## Slide 1: Loss of Mains Protection on DG Rectification Programme
ENFG
15 March 2017

## Slide 2: Agenda
Background
Emerging Vector Shift Issue
Benefit of making the change
Costs of Rectification
Funding Options
Implementation
Required Actions

## Slide 3: 1 - Background
Emerging and increasing risk of high RoCoF frequency excursion leading to RoCoF protection trips on Distributed Generation.
Phase 1 dealt with DG>5MW
Significant difficulty in completing this programme on about [200] sites.
There is a strong business case for phase 2 for all remaining DG - approximately 40 000 sites.
A different approach using dedicated and funded resource is proposed for Phase 2 –but will require DNO and NG expertise to initiate and manage

## Slide 4: 2 – Emerging Vector Shift Issue
Currently under detailed investigation
Langage incident (May 2016) has shown there could be a real issue with VS protection fitted to DG
Hitherto VS has been as an acceptable alternative to RoCoF
Worst case is that VS protection will trip inappropriately over a wide area for transmission faults – possibly exceeding the 1800MW maximum infeed loss.
New settings might be possible to avoid this risk, but would probably need applying on a regional or national basis
Final recommendations for settings or for replacement will be factored into the overall RoCoF update programme.

## Slide 5: 3 - Benefit of Making the Change (a)
Savings of > £50m per year will be made by completing the RoCoF settings programme
Savings are the avoided Balancing Service costs of
  managing the total system to a RoCoF limit of 0.125Hzs-1
  managing vector shift trip risks
Balancing Service costs flow through National Grid’s Balancing Service Incentive
  Savings go to consumers as targets take account of known changes with a 12 month or greater lead time

## Slide 6: 3 - Benefit of Making the Change (b)
The GC0079 workgroup has agreed it’s view of RoCoF costs
Cost comprises of two elements
  Trading to curtail interconnectors (from 1000MW)
  Synchronising extra generation when the minimum loss limit is reached (660MW)
The setting change programme is assumed to complete before the end of 2019/20, making savings available from 2020 onwards

## Slide 7: 4 - Rectification Costs (a)
DNOs collaborated in the summer of 2016 to build a model of implementation costs
There are approximately 40 000 generation sites of less than 5MW, excluding domestic installations.
From research undertaken by the WG, the inverters used in domestic generation are not sensitive to RoCoF. Their insensitivity to VS is being established.
Domestic inverters are not included in the proposals as it is not believed there is any issue with them.

## Slide 8: 4 - Rectification Costs (b)
A concentrated programme has been assumed, where there will be economies of scale and efficiencies.
The following costs are assumed * £
  Visit each site 200
  Perform simple risk assessment (synchronous sites) 125
  More detailed risk assessment (where required) 5 275
  Change protection setting only 200
  Change relay 7 700
Site visit costs include an allowance for DNO record keeping/updates etc
More significant network costs assume for risk mitigation on the network, eg synch-check or intertripping.
*Summarised/simplified for presentation purposes

## Slide 9: 4 - Rectification Costs (c)
Although numbers of sites is known reasonably accurately, the incidence of RoCoF protection or VS is not known, nor whether fitted to synch or asynch generation.
A best estimate has been made with high and low sensitivities to allow for errors in estimates etc.
To reset all relays on generation <5MW
RoCoF Only RoCoF and VS
  Best Estimate £16.1M £46.8M
  Low sensitivity £9.3M £22.1M
  High Sensitivity £46.7M £229.5M
The high sensitivities assume network modifications to minimise risk for synchronous generation; it is also assumed that these costs would be recharged directly to generators – so it is likely that they will be significantly overstated as generators will seek lower cost mitigations within their own control

## Slide 10: 5 - Funding Options
As directed by Ofgem the WG has considered and investigated the following funding options:
  Generators fund (and undertake) the work under a D Code obligation (as per the current >5MW programme)
  Centrally funded approach from BSUoS receipts
  DNO funded approach from DUoS receipts
  Centrally funded approach from TNUoS receipts
Ofgem instructed the WG to consider alternatives to generator self-funding, ie to (a) above.
Of these the centrally funded TNUoS receipts seems to be the most attractive option.
In all cases b, c, d it is end customers who eventually pay. Case (c) risks inequitable distribution of costs between DUoS payers of different DNOs.

## Slide 11: 6 – Implementation (a)
The programme is substantial and needs to benefit from economies of scale
Dedicated resources can be used to
  Research, contact and doorstep generators
  Perform screening and detailed risk assessments for synchronous sites
  Change relay settings
  Project manage any physical rectification actions for individual synchronous sites
  Update DNO records

## Slide 12: 6 - Implementation (b)
The WG will:
  Determine the necessary future proof RoCoF and VS settings
  Write up the business case for the changes
  Provide draft legal text for D Code changes.
  Consult on the proposals – date TBA
  Write a detailed technical specification for the work to be undertaken
Actions outside the WG
  Create an implementation project under ENFG governance
    Determine detail of TNUoS approach and suggest licence modifications to Ofgem
    Determine the contracting and commercial strategy for contracting in the necessary resources
    Develop the appropriate delivery incentives and assurance
    Agree a Project Management approach and timescale for completion

## Slide 13: 6 - Implementation (c)
Outsourcing options
  DNOs undertake with own staff, supplemented with contractors
  DNOs outsource it completely on an individual basis
  DNOs outsource it collectively
  NG outsource it, liaising with DNOs as necessary
Need to consider how to include IDNOs

## Slide 14: 8 - Next actions
ENFG discuss and advise on overall approach
  Agree to set up ENFG project to manage the programme
  Identify a PM
  Agree project ToRs
  Provide appropriate regulatory and commercial expertise to develop the contracting and commercial approach
WG
  Complete analysis
  Recommend how future synchronous risk assessments should be supported
  Complete draft legal text
  Write detailed technical specification for work to be done.
  Write consultation paper and determine when to consult and report to Ofgem