OPERATING CODE NO. 9

(OC9)

CONTINGENCY PLANNING

CONTENTS

GC0096 – STORAGE

20 MARCH 2019

(This contents page does not form part of the Grid Code)

Paragraph No/Title	Page Number

OC9.1   INTRODUCTION	2

OC9.2   OBJECTIVE	2

OC9.3   SCOPE	3

OC9.4   BLACK START	3

OC9.4.1 - OC9.4.4   Total Shutdown And Partial Shutdown	3

OC9.4.5   Black Start Stations	3

OC9.4.6   Black Start Situation	4

OC9.4.7   Black Start	4

OC9.5   RE-SYNCHRONISATION OF DE-SYNCHRONISED ISLANDS	12

OC9.5.2   Options	12

OC9.5.3   Choice Of Option	14

OC9.5.4   Agreeing Procedures	15

OC9.6   JOINT SYSTEM INCIDENT PROCEDURE	17

OC9.1	INTRODUCTION

Operating Code No.9 ("OC9") covers the following:

OC9.1.1	Black Starts

The implementation of recovery procedures following a Total Shutdown or Partial Shutdown.

OC9.1.2	Re-Synchronisation Of Islands

The Re-Synchronisation of parts of the Total System which have become Out of Synchronism with each other irrespective of whether or not a Total Shutdown or Partial Shutdown has occurred.

OC9.1.3	Joint System Incident Procedure

The establishment of a communication route and arrangements between senior management representatives of The Company and Users involved in, or who may be involved in, an actual or potential serious or widespread disruption to the Total System or a part of the Total System, which requires, or may require, urgent managerial response, day or night, but which does not fall within the provisions of OC9.1.4.

OC9.1.4	It should be noted that under section 96 of the Act the Secretary of State may give directions to The Company and/or any Generator and/or any Supplier, for the purpose of "mitigating the effects of any civil emergency which may occur" (ie. for the purposes of planning for a civil emergency); a civil emergency is defined in the Act as "any natural disaster or other emergency which, in the opinion of the Secretary of State, is or may be likely to disrupt electricity supplies".  Under the Energy Act 1976, the Secretary of State has powers to make orders and give directions controlling the production, supply, acquisition or use of electricity, where an Order in Council under section 3 is in force declaring that there is an actual or imminent emergency affecting electricity supplies.  In the event that any such directions are given, or orders made under the Energy Act 1976, the provisions of the Grid Code will be suspended in so far as they are inconsistent with them.

OC9.1.5	The Company shall procure that Relevant Scottish Transmission Licensees shall comply with OC9.4 and OC9.5 and any relevant Local Joint Restoration Plan or OC9 De-Synchronised Island Procedure where and to the extent that such matters apply to them.

OC9.2	OBJECTIVE

The overall objectives of OC9 are:

OC9.2.1	To achieve, as far as possible, restoration of the Total System and associated Demand in the shortest possible time, taking into account Power Station capabilities, including Embedded Generating Units, External Interconnections and the operational constraints of the Total System.

OC9.2.2	To achieve the Re-Synchronisation of parts of the Total System which have become Out of Synchronism with each other.

OC9.2.3	To ensure that communication routes and arrangements are available to enable senior management representatives of The Company and Users, who are authorised to make binding decisions on behalf of The Company or the relevant User, as the case may be, to communicate with each other in the situation described in OC9.1.3.

OC9.2.4	To describe the role that in respect of Scottish Transmission Systems, Relevant Scottish Transmission Licensees may have in the restoration processes as detailed in the relevant OC9 De-Synchronised Island Procedures and Local Joint Restoration Plans.

OC9.2.5	To identify and address as far as possible the events and processes necessary to enable the restoration of the Total System, after a Total Shutdown or Partial Shutdown.  This is likely to require the following key processes to be implemented, typically, but not necessarily, in the order given below:

(i) 	Selectively implement Local Joint Restoration Plans

(ii)	Expand Power Islands to supply Power Stations

(iii)	Expand and merge Power Islands leading to Total System energisation

(iv)	Selectively reconnect Demand

- Facilitate and co-ordinate returning the Total System back to normal operation

- Resumption of the Balancing Mechanism if suspended in accordance with the provisions of the BSC.

OC9.3	SCOPE

OC9.3.1	OC9 applies to The Company and to Users, which in OC9 means:-

(a)	Generators;

(b)	Network Operators; and

(c)	Non-Embedded Customers.

OC9.3.2	The procedure for the establishment of emergency support/contingency planning between The Company and Externally Interconnected System Operators is set out in the Interconnection Agreement with each Externally Interconnected System Operator.

OC9.3.3	In respect of Scottish Transmission Systems, OC9.4 and OC9.5 also apply to Relevant Scottish Transmission Licensees.

OC9.4	BLACK START

Total Shutdown And Partial Shutdown

OC9.4.1	A "Total Shutdown" is the situation existing when all generationhas ceased and there is no electricity supply from External Interconnections. Therefore, the Total System has shutdown with the result that it is not possible for the Total System to begin to function again without The Company 's directions relating to a Black Start.

OC9.4.2	A "Partial Shutdown" is the same as a Total Shutdown except that all generation has ceased in a separate part of the Total System and there is no electricity supply from External Interconnections or other parts of the Total System to that part of the Total System. Therefore, that part of the Total System is shutdown with the result that it is not possible for that part of the Total System to begin to function again without The Company's directions relating to a Black Start.

OC9.4.3	During a Total Shutdown or Partial Shutdown and during the subsequent recovery, the Licence Standards may not apply and the Total System may be operated outside normal voltage and Frequency standards.

OC9.4.4	In a Total Shutdown and in a Partial Shutdown and during the subsequent recovery, it is likely to be necessary for The Company  to issue Emergency Instructions in accordance with BC2.9.

OC9.4.5	Black Start Stations

OC9.4.5.1	Certain Power Stations ("Black Start Stations") are registered, 	pursuant to the Bilateral Agreement with a User, as having an ability for at least one of its Gensets to Start-Up from Shutdown and to energise a part of the Total System, or be Synchronised to the System, upon instruction from The Company  within two hours, without an external electrical power supply ("Black Start Capability").

OC9.4.5.2 	For each Black Start Station, a Local Joint Restoration Plan will be produced jointly by The Company, the relevant Generator and Network Operator in accordance with the provisions of OC9.4.7.12. The Local Joint Restoration Plan will detail the agreed method and procedure by which a Genset at a Black Start Station (possibly with other Gensets at that Black Start Station) will energise part of the Total System and meet complementary local Demand so as to form a Power Island.

OC9.4.5.3	In respect of Scottish Transmission Systems, a Local Joint Restoration Plan may cover more than one Black Start Station and may be produced with and include obligations on Relevant Scottish Transmission Licensees, Generators responsible for Gensets not at a Black Start Station and other Users.

OC9.4.6	Black Start Situation

In the event of a Total Shutdown or Partial Shutdown, The Company will, as soon as reasonably practical, inform Users (or, in the case of a Partial Shutdown, Users which in The Company's opinion need to be informed) and the BSCCo that a Total Shutdown, or, as the case may be, a Partial Shutdown, exists and that The Company intends to implement a Black Start. The Company  shall (as soon as is practicable) determine, in its reasonable opinion, the time and date with effect from which the Total Shutdown or Partial Shutdown commenced and notify BSCCo of that time and date.

In the event of a Total Shutdown and following such notification, in accordance with the provisions of the BSC, the BSCCo will determine the Settlement Period with effect from which the Balancing Mechanism is suspended.

In the event of a Partial Shutdown and following such notification, the Balancing Mechanism will not be suspended until such time and date that the Market Suspension Threshold has been met, or deemed to have been met, in accordance with the provisions of the BSC.  The Company shall carry out the monitoring activities required by paragraph G3.1 of the BSC.

Following determination by The Company pursuant to its obligations under the BSC that the Market Suspension Threshold has been met, or deemed to have been met, The Company shall (as soon as practicable) inform the BSCCo of that time and date at which the Market Suspension Threshold was met, or deemed to have been met, and the BSCCo will determine the Settlement Period in accordance with the provisions of the BSC with effect from which the Balancing Mechanism will be suspended.

Should The Company  determine that the Total System is capable of returning to normal operation without meeting the Market Suspension Threshold, The Company will follow the procedure given in OC9.4.7.9.

The Black Start will conclude with effect from the time and date determined in accordance with OC9.4.7.10.

In respect of Scottish Transmission Systems, in exceptional circumstances, as specified in the Local Joint Restoration Plan, SPT or SHETL, may invoke such Local Joint Restoration Plan for its own Transmission System and Scottish Offshore Transmission Systems connected to it and operate within its provisions.

OC9.4.7	Black Start

OC9.4.7.1	The procedure necessary for a recovery from a Total Shutdown or Partial Shutdown is known as a "Black Start".  The procedure for a Partial Shutdown is the same as that for a Total Shutdown except that it applies only to a part of the Total System.  It should be remembered that a Partial Shutdown may affect parts of the Total System which are not themselves shutdown.

OC9.4.7.2	The complexities and uncertainties of recovery from a Total Shutdown or Partial Shutdown require that OC9 is sufficiently flexible in order to accommodate the full range of Genset and Total System characteristics and operational possibilities, and this precludes the setting out in the Grid Code itself of concise chronological sequences.  The overall strategy will, in general, include the overlapping phases of establishment of Genset(s) at an isolated Power Station, together with complementary local Demand, termed "Power Islands", step by step integration of these Power Islands into larger sub-systems which includes utilising the procedures in OC9.5 (Re-Synchronisation of De-Synchronised Island) and eventually re-establishment of the complete Total System.

The Company Instructions

OC9.4.7.3	The procedures for a Black Start will, therefore, be those specified by The Company at the time.  These will normally recognise any applicable Local Joint Restoration Plan.  Users shall abide by The Company's instructions during a Black Start situation, even if these conflict with the general overall strategy outlined in OC9.4.7.2 or any applicable Local Joint Restoration Plan.  The Company 's instructions may (although this list should not be regarded as exhaustive) be to a Black Start Station relating to the commencement of generation, to a Network Operator or Non-Embedded Customer relating to the restoration of Demand, and to a Power Station relating to preparation for commencement of generation when an external power supply is made available to it, and in each case may include the requirement to undertake switching.

In respect of Scottish Transmission Systems SPT and SHETL will act on The Company’s behalf in accordance with its duties under the relevant Local Joint Restoration Plan.  Scottish Users shall abide by SPT’s or SHETL’s instructions given in accordance with the Local Joint Restoration Plan during a Black Start situation.

OC9.4.7.4	(a)	Black Start following a Total Shutdown or where the Balancing Mechanism has been suspended following a Partial Shutdown

During a Black Start situation where the Balancing Mechanism has been suspended, all instructions to Power Stations and to Network Operators will be deemed to be Emergency Instructions under BC2.9.2.2 (iii).  All such Emergency Instructions will recognise any differing Black Start operational capabilities (however termed) set out in the relevant Ancillary Services Agreement in preference to the declared operational capability as registered pursuant to BC1 (or as amended from time to time in accordance with the BC).  For the purposes of these instructions the Black Start will be an emergency circumstance under BC2.9.

In Scotland, Gensets that are not at Black Start Stations, but which are part of a Local Joint Restoration Plan, may be instructed in accordance with the provisions of that Local Joint Restoration Plan.

(b)	Black Start following a Partial Shutdown where the Balancing Mechanism has not been suspended

During a Black Start situation where the Balancing Mechanism has not been suspended, instructions in relation to Black Start Stations and to Network Operators which are part of an invoked Local Joint Restoration Plan will (unless The Company  specifies otherwise) be deemed to be Emergency Instructions under BC2.9.2.2 (iv) and will recognise any differing Black Start operational capabilities (however termed) set out in the relevant Ancillary Services Agreement in preference to the declared operational capability as registered pursuant to BC1 (or as amended from time to time in accordance with the BC). For the purposes of these instructions the Black Start will be an emergency circumstance under BC2.9.

During a Black Start situation where the Balancing Mechanism has not been suspended, The Company may issue instructions to Users other than Black Start Stations and Network Operators which are part of an invoked Local Joint Restoration Plan. Such instructions would be Emergency Instructions pursuant to BC2.9.1.2(e)(i) subject to the requirements of BC2.9.2.2 being met.

In Scotland, Gensets that are not at Black Start Stations, but which are part of an invoked Local Joint Restoration Plan, may be instructed in accordance with the provisions of that Local Joint Restoration Plan.

(c)  If during the Demand restoration process any Genset cannot, because of the Demand being experienced, keep within its safe operating parameters, the Generator shall, unless a Local Joint Restoration Plan is in operation, inform The Company. The Company will, where possible, either instruct Demand to be altered or will re-configure the National Electricity Transmission System or will instruct a User to re-configure its System in order to alleviate the problem being experienced by the Generator.  If a Local Joint Restoration Plan is in operation, then the arrangements set out therein shall apply.  However, The Company  accepts that any decision to keep a Genset operating, if outside its safe operating parameters, is one for the Generator concerned alone and accepts that the Generator may change generation on that Genset if it believes it is necessary for safety reasons (whether relating to personnel or Plant and/or Apparatus).  If such a change is made without prior notice, then the Generator shall inform The Company as soon as reasonably practical (unless a Local Joint Restoration Plan is in operation in which case the arrangements set out therein shall apply).

Embedded Power Stations

OC9.4.7.5	Without prejudice to the provisions of OC9.4.7.8, Network Operators with Embedded Power Stations will comply with any directions of The Company to restore Demand to be met by the Embedded Power Stations.

Local Joint Restoration Plan operation

OC9.4.7.6	(a)	The following provisions apply in relation to a Local Joint Restoration Plan.  As set out in OC9.4.7.3, The Company  may issue instructions which conflict with a Local Joint Restoration Plan.  In such cases, these instructions will take precedence over the requirements of the Local Joint Restoration Plan. When issuing such instructions, The Company shall state whether or not it wishes the remainder of the Local Joint Restoration Plan to apply.  If, not withstanding that The Company has stated that it wishes the remainder of the Local Joint Restoration Plan to apply, the Generator or the relevant Network Operator consider that The Company’s instructions mean that it is not possible to operate the Local Joint Restoration Plan as modified by those instructions, any of them may give notice to The Company and the other parties to the Local Joint Restoration Plan to this effect and The Company shall immediately consult with all parties to the Local Joint Restoration Plan.  Unless all parties to the Local Joint Restoration Plan reach an agreement forthwith as to how the Local Joint Restoration Plan shall operate in those circumstances, operation in accordance with the Local Joint Restoration Plan will terminate.

(b)	Where The Company, as part of a Black Start, has given an instruction to a Black Start Station to initiate Start-Up, the relevant Genset(s) at the Black Start Station will Start-Up in accordance with the Local Joint Restoration Plan.

(c)	The Company will advise the relevant Network Operator of the requirement to switch its User System so as to segregate its Demand and to carry out such other actions as set out in the Local Joint Restoration Plan.  The relevant Network Operator will then operate in accordance with the provisions of the Local Joint Restoration Plan.

(d)	The Company will ensure that switching carried out on the National Electricity Transmission System and other actions are as set out in the Local Joint Restoration Plan.

(e)	Following notification from the Generator that the Black Start Station is ready to accept load, The Company will instruct the Black Start Station to energise part of the Total System.  The Black Start Station and the relevant Network Operator will then, in accordance with the requirements of the Local Joint Restoration Plan, establish communication and agree the output of the relevant Genset(s) and the connection of Demand so as to establish a Power Island.  During this period, the Generator will be required to regulate the output of the relevant Genset(s) at its Black Start Station to the Demand prevailing in the Power Island in which it is situated, on the basis that it will (where practicable) seek to maintain the Target Frequency.  The Genset(s) at the Black Start Station will (where practical) also seek to follow the requirements relating to Reactive Power (which may include the requirement to maintain a target voltage) set out in the Local Joint Restoration Plan.

(f)	Operation in accordance with the Local Joint Restoration Plan will be terminated by The Company (by notifying the relevant Users) prior to connecting the Power Island to other Power Islands (other than, in Scotland, as allowed for in the Local Joint Restoration Plan), or to the User System of another Network Operator, or to the synchronising of Gensets at other Power Stations (other than, in Scotland, those forming part of the Local Joint Restoration Plan).  Operation in accordance with the Local Joint Restoration Plan will also terminate in the circumstances provided for in OC9.4.7.6(a) if an agreement is not reached or if The Company states that it does not wish the remainder of the Local Joint Restoration Plan to apply.  Users will then comply with the Bid-Offer Acceptances or Emergency Instructions of The Company

(g)	In Scotland, Gensets included in a Local Joint Restoration Plan, but not at a Black Start Station, will operate in accordance with the requirements of the Local Joint Restoration Plan.

Interconnection of Power Islands

OC9.4.7.7	The Company will instruct the relevant Users so as to interconnect Power Islands to achieve larger sub-systems, and subsequently the interconnection of these sub-systems to form an integrated system.  This should eventually achieve the re-establishment of the Total System or that part of the Total System subject to the Partial Shutdown, as the case may be.  The interconnection of Power Islands and sub-systems will utilise the provisions of all or part of OC9.5 (Re-Synchronisation of De-synchronised Islands) and in such a situation such provisions will be part of the Black Start.

OC9.4.7.8	As part of the Black Start strategy each Network Operator with either an Embedded Black Start Station which has established a Power Island within its User System or with any Embedded Power Stations within its User System which have become islanded, may in liaison with The Company  sustain and expand these islands in accordance with the relevant provisions of OC9.5 which shall apply to this OC9.4 as if set out here.  They will inform The Company of their actions and will not Re-Synchronise to the National Electricity Transmission System or any

User's System which is already Synchronised to the National Electricity Transmission System without The Company  's agreement.

Return the Total System Back to Normal Operation

OC9.4.7.9	The Company shall, as soon as reasonably practical, inform Users and the BSCCo when the Total System could return to normal operation.  Any such determination by The Company does not mean that the provisions of Section G paragraph 3 (Black Start) of the BSC shall cease to apply.

In making the determination that the Total System could return to normal operation, The Company, would consider, amongst other things, the following areas:

(a)	the extent to which the National Electricity Transmission System is contiguous and energised;

(b)	the integrity and stability of the National Electricity Transmission System and its ability to operate in accordance with the Licence Standards;

(c)	the impact that returning to normal may have on transmission constraints and the corresponding ability to maximise the Demand connected; and

(d)	the volume of generation, Electricity Storage or Demand not connected to the National Electricity Transmission System; and

(e)	the functionality of normal communication systems (i.e. electronic data communication facilities, Control Telephony, etc).

In the event that the Balancing Mechanism has been suspended, it will not resume until the start of the Settlement Period determined by the BSC Panel in accordance with paragraph G3.1.2(d)(i) of the BSC.

For the avoidance of doubt, until resumption of the Balancing Mechanism, The Company   is likely to continue to issue Emergency Instructions in accordance with BC2.9.

Users shall use reasonable endeavours to submit Physical notifications ten hours prior to the start of the Settlement Period determined by the BSC Panel in accordance with paragraph G3.1.2(d)(i) of the BSC and as notified by The Company  to Users, in preparation for a return to normal operations.

In the event that the Balancing Mechanism has not been suspended and The Company   has determined that the Total System has returned to normal operation, The Company   shall inform Users and the BSCCo as soon as possible of the time and date at which (in The Company’s determination) the Total System returned to normal operation.

Conclusion of Black Start

OC9.4.7.10	The provisions of this OC9 shall cease to apply with effect from either:

(a)   Where the Balancing Mechanism was suspended, the start of the Settlement Period that the Balancing Mechanism resumed normal operation, as determined by the BSC Panel and notified by the BSCCo in accordance with the provisions of the BSC; or

(b)  Where the Balancing Mechanism was not suspended, the end of the Settlement Period determined and notified by the BSCCo (in accordance with the provisions of the BSC) and corresponding  to  the time and date that The Company determined that the Total System had returned to normal operation.

Externally Interconnected System Operators

OC9.4.7.11	During a Black Start, The Company   will, pursuant to the Interconnection Agreement with Externally Interconnected System Operators, agree with Externally Interconnected System Operators when their transmission systems can be Re-Synchronised to the Total System, if they have become separated.

OC9.4.7.12	Local Joint Restoration Plan Establishment

(a)	In England and Wales, in relation to each Black Start Station, The Company, the Network Operator and the relevant Generator will discuss and agree a Local Joint Restoration Plan.  Where at the date of the first inclusion of this OC9.4.7.12 into the Grid Code a local plan covering the procedures to be covered in a Local Joint Restoration Plan is in existence and agreed, The Company will discuss this with the Network Operator and the relevant Generator to agree whether it is consistent with the principles set out in this OC9.4.  If it is agreed to be so consistent, then it shall become a Local Joint Restoration Plan under this OC9 and the relevant provisions of OC9.4.7.12(b) shall apply.  If it is not agreed to be so consistent, then the provisions of OC9.4.7.12(b) shall apply as if there is no Local Joint Restoration Plan in place.

In respect of Scottish Transmission Systems where a requirement for a Local Joint Restoration Plan is identified, The Company, the Relevant Scottish Transmission Licensee(s), the Network Operator and Black Start Station(s) will discuss and agree a Local Joint Restoration Plan. In addition other Users, including other Generators, may be reasonably required by The Company to discuss and agree a Local Joint Restoration Plan.

(b)	In England and Wales, where the need for a Local Joint Restoration Plan arises when there is none in place, the following provisions shall apply:

(i)	The Company, the Network Operator and the relevant Generator will discuss and agree the detail of the Local Joint Restoration Plan as soon as the requirement for a Local Joint Restoration Plan is identified by The Company. The Company will notify all affected Users, and will initiate these discussions.

(ii)	Each Local Joint Restoration Plan will be in relation to a specific Black Start Station.

(iii)	The Local Joint Restoration Plan will record which Users and which User Sites are covered by the Local Joint Restoration Plan and set out what is required from The Company and each User should a Black Start situation arise.

(iv)	Each Local Joint Restoration Plan shall be prepared by The Company to reflect the above discussions and agreement.

(v)	Each page of the Local Joint Restoration Plan shall bear a date of issue and the issue number.

(vi)	When a Local Joint Restoration Plan has been prepared, it shall be sent by The Company to the Users involved for confirmation of its accuracy.

(vii)	The Local Joint Restoration Plan shall then (if its accuracy has been confirmed) be signed on behalf of The Company and on behalf of each relevant User by way of written confirmation of its accuracy.

(viii)	Once agreed under this OC9.4.7.12, the procedure will become a Local Joint Restoration Plan under the Grid Code and (subject to any change pursuant to this OC9) will apply between The Company and the relevant Users as if it were part of the Grid Code.

(ix)	Once signed, a copy of the Local Joint Restoration Plan will be distributed by The Company to each User which is a party to it accompanied by a note indicating the date of implementation.

(x)	The Company and Users must make the Local Joint Restoration Plan readily available to the relevant operational staff.

(xi)	If The Company, or any User which is a party to a Local Joint Restoration Plan, becomes aware that a change is needed to that Local Joint Restoration Plan, it shall (in the case of The Company) initiate a discussion between The Company and the relevant Users to seek to agree the relevant change.  If a User becomes so aware, it shall contact The Company who will then initiate such discussions. The principles applying to establishing a new Local Joint Restoration Plan under this OC9.4.7.12 shall apply to such discussions and to any consequent changes.

(xii)	The Company, the Network Operator and the relevant Generator will conduct regular joint exercises of the Local Joint Restoration Plan to which they are parties.  The objectives of such exercises include:

To test the effectiveness of the Local Joint Restoration Plan;

To provide for joint training of the parties in respect of the Local Joint Restoration Plan;

To maintain the parties’ awareness and familiarity of the Local Joint Restoration Plan;

To promote understanding of each parties’ roles under a Local Joint Restoration Plan;

To identify any improvement areas which should be incorporated in to the Local Joint Restoration Plan.

The principles applying to the establishment of a new Local Joint Restoration Plan under this OC9.4.7.12 shall apply to any changes to the Local Joint Restoration Plan.

The Company will propose to the parties of a Local Joint Restoration Plan a date for the exercise to take place, to be agreed with the other parties.  All the Local Joint Restoration Plan parties will jointly share the task of planning, preparing, participating in and facilitating the exercises, which will normally be in desktop format or as otherwise agreed.  The precise timing of the exercise for each Local Joint Restoration Plan will be agreed by all parties, but will not be less than one every 8 years.

(c)	In respect of Scottish Transmission Systems, where the need for a Local Joint Restoration Plan arises, the following provisions shall apply:

(i)	The Company, the Relevant Scottish Transmission Licensee(s), the Network Operator and the relevant Generator will discuss and agree the detail of the Local Joint Restoration Plan as soon as the requirement for a Local Joint Restoration Plan is identified by The Company. In addition other Scottish Users, including other Generators, may be reasonably required by The Company to discuss and agree details of the Local Joint Restoration Plan as soon as the requirement for a Local Joint Restoration Plan is identified by The Company. The Company will notify the Relevant Scottish Transmission Licensee(s) and all affected Scottish Users, and will initiate these discussions.

(ii)	Each Local Joint Restoration Plan may be in relation to either  a specific Black Start Station or a number of Black Start Stations, and may include Gensets at Power Stations other than a Black Start Station.

(iii)	The Local Joint Restoration Plan will record which Scottish Users and which Scottish User Sites are covered by the Local Joint Restoration Plan and set out what is required from The Company, the Relevant Scottish Transmission Licensee(s) and each Scottish User should a Black Start situation arise.

(iv)	Each Local Joint Restoration Plan shall be prepared by The Company to reflect the above discussions and agreement.

(v)	Each page of the Local Joint Restoration Plan shall bear a date of issue and the issue number.

(vi)	When a Local Joint Restoration Plan has been prepared, it shall be sent by The Company to the Relevant Scottish Transmission Licensee(s) and Scottish Users involved for confirmation of its accuracy.

(vii)	The Local Joint Restoration Plan shall then (if its accuracy has been confirmed) be signed on behalf of The Company and on behalf of each relevant Scottish User and Relevant Scottish Transmission Licensee(s) by way of written confirmation of its accuracy.

(viii)	Once agreed under this OC9.4.7.12, the procedure will become a Local Joint Restoration Plan under the Grid Code and (subject to any change pursuant to this OC9) will apply between The Company, Relevant Scottish Transmission Licensee(s) and the relevant Scottish Users as if it were part of the Grid Code.

(ix)	Once signed, a copy of the Local Joint Restoration Plan will be distributed by The Company to the Relevant Scottish Transmission Licensee(s) and each Scottish User which is a party to it accompanied by a note indicating the date of implementation.

(x)	The Company, the Relevant Scottish Transmission Licensee(s) and Scottish Users must make the Local Joint Restoration Plan readily available to the relevant operational staff.

(xi)	If The Company, the Relevant Scottish Transmission Licensee(s) or any Scottish User which is a party to a Local Joint Restoration Plan, becomes aware that a change is needed to that Local Joint Restoration Plan, it shall (in the case of The Company) initiate a discussion between The Company, the Relevant Scottish Transmission Licensee(s) and the relevant Scottish Users to seek to agree the relevant change.  If a Scottish User or a Relevant Scottish Transmission Licensee becomes so aware, it shall contact The Company who will then initiate such discussions. The principles applying to establishing a new Local Joint Restoration Plan under this OC9.4.7.12 shall apply to such discussions and to any consequent changes.

(xii)	The Company, the Relevant Scottish Transmission Licensee(s), the Network Operator and the relevant Generator will conduct regular joint exercises of the Local Joint Restoration Plan to which they are parties.  The objectives of such exercises include:

To test the effectiveness of the Local Joint Restoration Plan;

To provide for joint training of the parties in respect of the Local Joint Restoration Plan;

To maintain the parties’ awareness and familiarity of the Local Joint Restoration Plan;

To promote understanding of each parties’ roles under a Local Joint Restoration Plan;

To identify any improvement areas which should be incorporated in to the Local Joint Restoration Plan.

The principles applying to the establishment of a new Local Joint Restoration Plan under this OC9.4.7.12 shall apply to any changes to the Local Joint Restoration Plan.

The Company will propose to the parties of a Local Joint Restoration Plan a date for the exercise to take place, to be agreed with the other parties.  All the Local Joint Restoration Plan parties will jointly share the task of planning, preparing, participating in and facilitating the exercises, which will normally be in desktop format or as otherwise agreed.  The precise timing of the exercise for each Local Joint Restoration Plan will be agreed by all parties, but will not be less than one every 8 years.

OC9.5	RE-SYNCHRONISATION OF DE-SYNCHRONISED ISLANDS

The provisions in this OC9.5 do not apply to the parts of the Total System that normally operate Out of Synchronism with the rest of the National Electricity Transmission System.

Further requirements, including the provision of information, applying to Re-synchronisation of De-synchronised Islands following any Total Shutdown or Partial Shutdown are detailed in OC9.5.6.

OC9.5.1	(a)	Where parts of the Total System are Out of Synchronism with each other (each such part being termed a "De-Synchronised Island"), but there is no Total Shutdown or Partial Shutdown, The Company will instruct Users to regulate generation or Demand, as the case may be, to enable the De-Synchronised Islands to be Re-Synchronised and The Company will inform those Users when Re-Synchronisation has taken place.

(b)	As part of that process, there may be a need to deal specifically with Embedded generation or storage in those De-Synchronised Islands.  This OC9.5 provides for how such Embedded generation or storage should be dealt with. In Scotland, this OC9.5 also provides for how Transmission connected generation in De-Synchronised Islands should be dealt with.

(c)	In accordance with the provisions of the BC, The Company may decide that, to enable Re-Synchronisation, it will issue Emergency Instructions in accordance with BC2.9 and it may be necessary to depart from normal Balancing Mechanism operation in accordance with BC2 in issuing Bid-Offer Acceptances.

(d)	The provisions of this OC9.5 shall also apply during a Black Start to the Re-Synchronising of parts of the System following a Total or Partial Shutdown, as indicated in OC9.4.  In such cases, the provisions of the OC9.5 shall apply following completion and/or termination of the relevant Local Joint Restoration Plan(s) process as referred to in OC9.4.7.6(f).

OC9.5.2	Options

Generation in those De-Synchronised Islands may be dealt with in three different ways, more than one of which may be utilised in relation to any particular incident:-

OC9.5.2.1	Indirect Data

(a)	The Company, each Generator with Synchronised (or connected and available to generate although not Synchronised) Genset(s) in the De-Synchronised Island and the Network Operator whose User System forms all or part of the De-Synchronised Island shall exchange information as set out in this OC9.5.2.1 to enable The Company to issue a Bid-Offer Acceptance or an Emergency Instruction to that Generator in relation to its Genset(s) in the De-Synchronised Island until Re-Synchronisation takes place, on the basis that it will (where practicable) seek to maintain the Target Frequency.

(b)	The information to The Company from the Generator will cover its relevant operational parameters as outlined in the BC and from The Company to the Generator will cover data on Demand and changes in Demand in the De-Synchronised Island.

(c)	The information from the Network Operator to The Company will comprise data on Demand in the De-Synchronised Island, including data on any constraints within the De-Synchronised Island.

(d)	The Company will keep the Network Operator informed of the Bid-Offer Acceptances or Emergency Instructions it is issuing to Embedded Genset(s) within the Network Operator’s User System forming part of the De-Synchronised Island.

OC9.5.2.2	Direct Data

(a)	The Company will issue an Emergency Instruction and/or a Bid-Offer Acceptance, to the Generator to "float" local Demand and maintain Frequency at Target Frequency.  Under this, the Generator will be required to regulate the output of its Genset(s) at the Power Station in question to the Demand prevailing in the De-Synchronised Island in which it is situated, until Re-Synchronisation takes place, on the basis that it will (where practicable) seek to maintain the Target Frequency.

(b)	The Network Operator is required to be in contact with the Generator at the Power Station to supply data on Demand changes within the De-Synchronised Island.

(c)	If more than one Genset is Synchronised on the De-Synchronised Island, or is connected to the De-Synchronised Island and available to generate although not Synchronised, the Network Operator will need to liaise with The Company to agree which Genset(s) will be utilised to accommodate changes in Demand in the De-Synchronised Island. The Network Operator will then maintain contact with the relevant Generator (or Generators) in relation to that Genset(s).

(d)	The Generator at the Power Station must contact the Network Operator if the level of Demand which it has been asked to meet as a result of the Emergency Instruction and/or Bid-Offer Acceptance to "float" and the detail on Demand passed on by the Network Operator, is likely to cause problems for safety reasons (whether relating to personnel or Plant and/or Apparatus) in the operation of its Genset(s), in order that the Network Operator can alter the level of Demand which that Generator needs to meet. Any decision to operate outside any relevant parameters is one entirely for the Generator.

OC9.5.2.3	Control Features

(a)	A system may be established in relation to a part of the National Electricity Transmission System and a  Network Operator’s User System, if agreed between The Company and the Network Operator and any relevant Generator(s), whereby upon a defined fault(s) occurring, manual or automatic control features will operate to protect the National Electricity Transmission System and relevant Network Operator’s User System and Genset(s) and simplify the restoration of Demand in the De-Synchronised Island.

(b)	In agreeing the establishment of such a system of control features The Company will need to consider its impact on the operation of the National Electricity Transmission System.

OC9.5.2.4	Absence of Control Features System

If a system of control features under OC9.5.2.3 has not been agreed as part of an OC9 De-Synchronised Island Procedure under OC9.5.4 below, The Company may choose to utilise the procedures set out in OC9.5.2.1 or OC9.5.2.2, or may instruct the Genset(s) (or some of them) in the De-Synchronised Island to De-Synchronise.

OC9.5.3	Choice Of Option

In relation to each of the methods set out in OC9.5.2, where a De-Synchronised Island has come into existence and where an OC9 De-Synchronised Island Procedure under OC9.5.4 has been agreed, The Company, the Network Operator and relevant Generator(s) will operate in accordance with that OC9 De-Synchronised Islands Procedure unless The Company considers that the nature of the De-Synchronised Island situation is such that either:-

(i)	the OC9 De-Synchronised Island Procedure does not cover the situation; or

(ii)	the provisions of the OC9 De-Synchronised Island Procedure are not appropriate,

in which case The Company will instruct the relevant Users and the Users will comply with The Company's instructions (which in the case of Generators will relate to generation and in the case of Network Operators will relate to Demand).

OC9.5.4	Agreeing Procedures

In relation to each relevant part of the Total System, The Company, the Network Operator and the relevant Generator will discuss and may agree a local procedure (an "OC9 De-Synchronised Island Procedure").

OC9.5.4.1	Where there is no relevant local procedure in place at 12th May 1997, or in the case where the need for an OC9 De-Synchronised Island Procedure arises for the first time, the following provisions shall apply:

(a)	The Company, the Network Operator(s) and the relevant Generator(s) will discuss the need for, and the detail of, the OC9 De-Synchronised Island Procedure.  As soon as the need for an OC9 De-Synchronised Island Procedure is identified by The Company or a User, and the party which identifies such a need will notify all affected Users (and The Company, if that party is a User), and The Company will initiate these discussions.

(b)	Each OC9 De-Synchronised Island Procedure will be in relation to a specific Grid Supply Point, but if there is more than one Grid Supply Point between The Company and the Network Operator then the OC9 De-Synchronised Island Procedure may cover all relevant Grid Supply Points. In Scotland, the OC9 De-Synchronised Island Procedure may also cover parts of the National Electricity Transmission System connected to the User’s System(s) and Power Stations directly connected to the National Electricity Transmission System which are also likely to form part of the Power Island.

(c)	The OC9 De-Synchronised Island Procedure will:

(i)	record which Users and which User Sites are covered by the OC9 De-Synchronised Island Procedure;

(ii)	record which of the three methods set out in OC9.5 (or combination of the three) shall apply, with any conditions as to applicability being set out as well;

(iii)	set out what is required from The Company and each User should a De-Synchronised Island arise;

(iv)	set out what action should be taken if the OC9 De-Synchronised Island Procedure does not cover a particular set of circumstances and will reflect that in the absence of any specified action, the provisions of OC9.5.3 will apply;

(v)	in respect of Scottish Transmission Systems, the OC9 De-Synchronised Island Procedure may be produced with and include obligations on the Relevant Scottish Transmission Licensee(s) ; and

(vi)	in respect of Scottish Transmission Systems, where the OC9 De-Synchronised Island Procedure includes the establishment of a De-synchronised Island, describe the route for establishment of the De-Synchronised Island.

(d)	Each OC9 De-Synchronised Island Procedure shall be prepared by The Company to reflect the above discussions.

(e)	Each page of the OC9 De-Synchronised Island Procedure shall bear a date of issue and the issue number.

(f)	When an OC9 De-Synchronised Island Procedure is prepared, it shall be sent by The Company to the Users involved for confirmation of its accuracy.

(g)	The OC9 De-Synchronised Island Procedure shall then be signed on behalf of The Company and on behalf of each relevant User by way of written confirmation of its accuracy.

(h)	Once agreed under this OC9.5.4.1, the procedure will become an OC9 De-Synchronised Island Procedure under the Grid Code and (subject to any change pursuant to this OC9) will apply between The Company, Relevant Transmission Licensee and the relevant Users as if it were part of the Grid Code.

(i)	Once signed, a copy will be distributed by The Company to each User which is a party accompanied by a note indicating the issue number and the date of implementation.

(j)	The Company and Users must make the OC9 De-Synchronised Island Procedure readily available to the relevant operational staff.

(k)	If a new User connects to the Total System and needs to be included with an existing OC9 De-Synchronised Island Procedure, The Company will initiate a discussion with that User and the Users which are parties to the relevant OC9 De-Synchronised Island Procedure.  The principles applying to a new OC9 De-Synchronised Island Procedure under this OC9.5.4.1 shall apply to such discussions and to any consequent changes.

(l)	If The Company, or any User which is a party to an OC9 De-Synchronised Island Procedure, becomes aware that a change is needed to that OC9 De-Synchronised Island Procedure, it shall (in the case of The Company) initiate a discussion between The Company and the relevant Users to seek to agree the relevant change.  The principles applying to establishing a new OC9 De-Synchronised Island Procedure under this OC9.5.4.1 shall apply to such discussions and to any consequent changes.  If a User becomes so aware, it shall contact The Company who will then initiate such discussions.

(m)	If in relation to any discussions, agreement cannot be reached between The Company and the relevant Users, The Company will operate the System on the basis that it will discuss which of the three methods set out in OC9.5.2.1 to OC9.5.2.3 would be most appropriate at the time, if practicable.  The complexities and uncertainties of recovery from a De-Synchronised Island means that The Company will decide, having discussed the situation with the relevant Users and taking into account the fact that the three methods may not cover the situation or be appropriate, the approach which is to be followed.  The Company will instruct the relevant Users and the Users will comply with The Company 's instructions as provided in OC9.5.3.

OC9.5.4.2	Where there is a relevant local procedure in place at 12th May 1997, the following provisions shall apply:

(a)	The Company and the Network Operator and the relevant Generator(s) will discuss the existing procedure to see whether it is consistent with the principles set out in this OC9.5.

(b)	If it is, then it shall become an OC9 De-Synchronised Island Procedure under this OC9, and the relevant provisions of OC9.5.4.1 shall apply.

(c)	If it is not, then the parties will discuss what changes are needed to ensure that it is consistent, and once agreed the procedure will become an OC9 De-Synchronised Island Procedure under this OC9, and the relevant provisions of OC9.5.4.1 shall apply.

(d)	If agreement cannot be reached between The Company and the relevant Users after a reasonable period of time, the existing procedure will cease to apply and The Company will operate the System on the basis that it will discuss which of the three methods set out in OC9.5.2.1 to OC9.5.2.3 would be most appropriate at the time, if practicable. The complexities and uncertainties of recovery from a De-Synchronised Island means that The Company will decide, having discussed the situation with the relevant Users and taking into account the fact that the three methods may not cover the situation or be appropriate, the approach which is to be followed.  The Company will instruct the relevant Users and the Users will comply with The Company 's instructions as provided in OC9.5.3.

OC9.5.5	Where the National Electricity Transmission System is Out of Synchronism with the Transmission System of an Externally Interconnected System Operator, The Company will, pursuant to the Interconnection Agreement with that Externally Interconnected System Operator, agree with that Externally Interconnected System Operator when its Transmission System can be Re-Synchronised to the National Electricity Transmission System.

OC9.5.6	Further requirements regarding Re-synchronisation of De-synchronised Islands following any Total Shutdown or Partial Shutdown

Following any Total Shutdown or Partial Shutdown, The Company expects that it will be necessary to interconnect Power Islands utilising the provisions of OC9.5.  The complexities and uncertainties of recovery from a Total Shutdown or Partial Shutdown requires the provisions of OC9.5 to be flexible, however, the strategies which The Company will, where practicable, be seeking to follow when Re-synchronising De-synchronised Islands following any Total Shutdown or Partial Shutdown, include the following:

(a)	the provision of supplies to appropriate Power Stations to facilitate their synchronisation as soon as practicable;

(b)	energisation of a skeletal National Electricity Transmission System;

(c)	the strategic restoration of Demand in co-ordination with relevant Network Operators.

As highlighted in OC9.4.3, during a Total Shutdown or Partial Shutdown and during the subsequent recovery, which includes any period during which the procedures in this OC9.5 apply, the Licence Standards may not apply and the Total System may be operated outside normal voltage and Frequency standards.

OC9.5.7	To manage effectively and co-ordinate the restoration strategies of the Total System (any Re-Synchronisation of De-Synchronised Islands) following any Total Shutdown or Partial Shutdown, requires The Company and relevant Users to undertake certain planning activities as set out below:

(a)	The Company and Network Operators shall review on a regular basis the processes by which each Power Island will be interconnected.  This is likely to cover an exchange of information regarding the typical size, location and timing requirements for Demand to be reconnected and also include details (ability to change/disable) of the low frequency trip relay settings of the Demand identified.

(b)	Each Generator shall provide to The Company information to assist The Company in the formulation of the restoration strategies of Power Island expansion.  This information shall be provided in accordance with PC.A.5.7.

OC9.6	JOINT SYSTEM INCIDENT PROCEDURE

OC9.6.1	A "Joint System Incident" is

(a)	an Event, wherever occurring (other than on an Embedded Small Power Station or Embedded Medium Power Station), which, in the opinion of The Company or a User, has or may have a serious and/or widespread effect.

(b)	In the case of an Event on a User(s) System(s) (other than on an Embedded Small Power Station or Embedded Medium Power Station), the effect must be on the National Electricity Transmission System, and in the case of an Event on the National Electricity Transmission System, the effect must be on a User(s) System(s) (other than on an Embedded Small Power Station or Embedded Medium Power Station).

Where an Event on a User(s) System(s) has or may have no effect on the National Electricity Transmission System, then such an Event does not fall within OC9 and accordingly OC9 shall not apply to it.

OC9.6.2	(a)	(i)	Each User (other than Generators which only have Embedded Small Power Stations and/or Embedded Medium Power Stations) will provide in writing to The Company, and

(ii)	The Company will provide in writing to each User (other than Generators which only have Embedded Small Power Stations and/or Embedded Medium Power Stations), a telephone number or numbers at which, or through which, senior management representatives nominated for this purpose and who are fully authorised to make binding decisions on behalf of The Company or the relevant User, as the case may be, can be contacted day or night when there is a Joint System Incident.

(b)	The lists of telephone numbers will be provided in accordance with the timing requirements of the Bilateral Agreement and/or Construction Agreement with that User, prior to the time that a User connects to the National Electricity Transmission System and must be up-dated (in writing) as often as the information contained in them changes.

OC9.6.3	Following notification of an Event under OC7, The Company or a User, as the case may be, will, if it considers necessary, telephone the User or The Company, as the case may be, on the telephone number referred to in OC9.6.2, to obtain such additional information as it requires.

OC9.6.4	Following notification of an Event under OC7, and/or the receipt of any additional information requested pursuant to OC9.6.3, The Company or a User, as the case may be, will determine whether or not the Event is a Joint System Incident, and, if so, The Company and/or the User may set up an Incident Centre in order to avoid overloading the existing The Company or that User's, as the case may be, operational/control arrangements.

OC9.6.5	Where The Company has determined that an Event is a Joint System Incident, The Company shall, as soon as possible, notify all relevant Users that a Joint System Incident has occurred and, if appropriate, that it has established an Incident Centre and the telephone number(s) of its Incident Centre if different from those already supplied pursuant to OC9.6.2.

OC9.6.6	If a User establishes an Incident Centre it shall, as soon as possible, notify The Company that it has been established and the telephone number(s) of the Incident Centre if different from those already supplied pursuant to OC9.6.2.

OC9.6.7	The Company's Incident Centre and/or the User's Incident Centre will not assume any responsibility for the operation of the National Electricity Transmission System or User's System, as the case may be, but will be the focal point in The Company or the User, as the case may be, for:

(a)	the communication and dissemination of information between The Company and the senior management representatives of User(s); or

(b)	between the User and the senior management representatives of The Company, as the case may be,

relating to the Joint System Incident.  The term "Incident Centre" does not imply a specially built centre for dealing with Joint System Incidents, but is a communications focal point.  During a Joint System Incident, the normal communication channels, for operational/control communication between The Company and Users will continue to be used.

OC9.6.8	All communications between the senior management representatives of the relevant parties with regard to The Company's role in the Joint System Incident shall be made via The Company's Incident Centre if it has been established.

OC9.6.9	All communications between the senior management representatives of The Company and a User with regard to that User's role in the Joint System Incident shall be made via that User's Incident Centre if it has been established.

OC9.6.10	The Company will decide when conditions no longer justify the need to use its Incident Centre and will inform all relevant Users of this decision.

OC9.6.11	Each User which has established an Incident Centre will decide when conditions no longer justify the need to use that Incident Centre and will inform The Company of this decision.

< END OF OPERATING CODE NO. 9 >