| Workgroup Consultation |  | At what stage is this document in the process? |
| --- | --- | --- |
| GC0125 Mod Title: EU Code Emergency & Restoration: Black Start testing requirements for Interconnectors |  | 02 Workgroup Consultation 01 Proposal form 03 Workgroup Report 05 Draft Grid Code Modification Report Consultation 06 Final Grid Code Modification Report 04 Code Administrator Consultation |
| Purpose of Modification: This modification seeks to align the GB Grid Code with the European Emergency and Restoration Code, specifically in relation to Black Start testing for Interconnectors. |  |  |
|  | This document contains the discussion of the Workgroup which formed in May 2019 to develop and assess the proposal. Any interested party is able to make a response in line with the guidance set out in the Governance Rules of the Grid Code. Published on: xx June 2019 Length of Consultation: 15 Working days Responses by: xx June 2019 |  |
|  | High Impact: Electricity System Operator (ESO), external Transmission System Operators (TSOs), Interconnectors wishing to provide Black Start. |  |
|  | Medium Impact: None. |  |
|  | Low Impact: None. |  |

| Contents 1 About this document 3 2 Original Proposal 4 3 Proposers Solution 6 4 Impacts & Other Considerations 7 5 Workgroup discussions 7 6 Relevant Objectives 10 7 Implementation 11 8 How to respond 11 Annex 1 – Extracts from European Network Codes 12 Annex 2 – Terms of Reference 13 Annex 3 – Draft legal text 14 Annex 4 – Attendance log 15 Timetable The Code Administrator recommends the following expedited timetable:. Initial consideration by Workgroup. Workgroup Consultation; June 2019. Modification concluded by Workgroup; 22 July 2019. Workgroup Report presented to Panel; 30 July 2019. Code Administration Consultation Report issued to the Industry; August 2019. Draft Final Modification Report presented to Panel; August 2019. Modification Panel recommendation; August 2019. Final Modification Report issued the Authority; September 2019. Authority decision (25WDs); October 2019. Decision implemented into the Grid Code; By 18 December 2019. May 2019. | Any questions? |
| --- | --- |
|  | Contact: Chrissie Brown Code Administrator |
|  | Christine.brown1@ntionalgrideso. com |
|  | 07866794568 |
|  | Proposer: Anthony Johnson |
|  | anthony.johnson@nationalgrideso.com |
|  | 07966 734856 |

# About this document

This Workgroup Consultation contains the discussion of the Workgroup which formed in May 2019 to develop and assess the proposal.

Section 2 (Original Proposal) and Section 3 (Proposer’s solution) are sourced directly from the Proposer and any statements or assertions have not been altered or substantiated/supported or refuted by the Workgroup. Section 5 of the Workgroup contains the discussion by the Workgroup on the Proposal and the potential solution.

The Grid Code Panel detailed in the Terms of Reference the scope of work for the GC0125 Workgroup and the specific areas that the Workgroup should consider.

The table below details these specific areas and where the Workgroup have covered them or will cover post Workgroup Consultation.

The full Terms of Reference can be found in Annex 2.

Terms of Reference

| Specific Area | Location in the report |
| --- | --- |
| Implementation and costs; | Page 11. |
| Review draft legal text should it have been provided. If legal text is not submitted within the Grid Code Modification Proposal the Workgroup should be instructed to assist in the developing of the legal text; | Annex 3 and Workgroup discussions section 5. |
| Consider whether any further Industry experts or stakeholders should be invited to participate within the Workgroup to ensure that all potentially affected stakeholders have the opportunity to be represented in the Workgroup. Demonstrate what has been done to cover this clearly in the report; | Following the first workgroup, members and the Code Administrator sought to source further membership. Further Interconnector members joined following this. |
| Introduce Black start testing requirements as a result of E&R; | Workgroup discussions section 5. |
| To introduce interconnectors as a source of Black start; | Workgroup discussions section 5. |
| Review all current Black start references for suitability; and | Workgroup discussions section 5. |
| Ensure all Black start providers are treated equally as far as practical in the scope of E&R | Workgroup discussions section 5. |

Acronym Table

| Acronym | Meaning |
| --- | --- |
| E&R | Emergency and Restoration Network Code |
| HVDC | High Voltage Direct Current |

# Original Proposal

Section 2 (Original Proposal) and Section 3 (Proposer’s solution) are sourced directly from the Proposer and any statements or assertions have not been altered or substantiated/supported or refuted by the Workgroup. Section 5 of the Workgroup Consultation contains the discussion by the Workgroup on the Proposal and the potential solution.

#### Defect

The Grid Code doesn’t currently include black start testing requirements for interconnectors, whereas the Emergency and Restoration Code (E&R) does. Therefore, the Grid Code needs to be aligned to the European Network Code to reflect these requirements.

#### What

The Grid Code currently has testing requirements for generators choosing to provide a black start service, which were aligned to E&R as a result of GC0108. This was approved by Ofgem on 21st November 2018. E&R also sets out testing requirements for interconnectors offering Black Start but these are not currently specified in the Grid Code. This modification seeks to add these requirements to facilitate alignment with E&R.

#### Why

The requirements need to be added to the Grid Code to reflect the testing requirements that will be necessary as of 18th December 2019.

#### How

This modification proposes to align the testing requirements set out in the E&R with GB frameworks by adding the requirements in OC.5.7 of the Operating Code within the Grid Code.

It will be specified that High Voltage Direct Current systems delivering a black start service will be required to execute a black start capability test at least every three years and will detail how this needs to be done.

#### Governance

#### Justification for Normal Procedure to apply

- Normal Governance procedures should apply as there will be a material impact on interconnectors who wish to deliver a black start service in future.

- There is no need for this modification to be treated as urgent as the requirements do not need to be in the Grid Code before 18th December 2019.

#### Requested Next Steps

This modification should:

- be assessed by a Workgroup

- Following the feedback received for modification GC0108 EU Code: Emergency & Restoration: Black start testing requirement and given that this modification is slightly more complex given that the requirements are new and do not currently exist in the Grid Code, we believe a workgroup should help to develop the final solution.

- The Grid Code Review Panel decided that this modification should follow the standard route by forming a Workgroup and the modification being submitted to the Authority for decision.

#### Why Change?

This Proposal is one of a number of Proposals which seek to implement relevant provisions of a number of new EU Network Codes/Guidelines which have been introduced in order to enable progress towards a competitive and efficient internal market in electricity. Some EU Network Guidelines are still in development and these may in due course require a review of the solutions developed for the Codes that come into force beforehand. The full set of EU network guidelines are:

- Regulation 2015/1222- Capacity Allocation and Congestion Management (CACM) which came into force 14 August 2015

- Regulation 2016/1719 – Forward Capacity Allocation (FCA) which came into force 17 October 2016

- Regulation 2016/631- Requirements for Generators (RfG) which came into force 17 May 2016

- Regulation 2016/1388 – Demand Connection Code (DCC) which came into force 7 September 2016

- Regulation 2016/1447 – High Voltage Direct Current (HVDC) which came into force 28 September 2016

- Transmission System Operation Guideline (SOGL) - which came into force 14 September 2017

- Regulation 2017/2196 - Emergency and Restoration (E&R) which came into force 18 December 2018.

The Regulation establishing an E&R came into force on 18 December 2017. The E&R sets out rules relating to the management of the electricity transmission system in the emergency, blackout and restoration states. The main objective of the relevant rules is to bring the system back to the normal state as quickly and efficiently as possible.

#### Code Specific Matters

#### Technical Skillsets

Understanding of black start arrangements

#### Reference Documents

Emergency and Restoration Code:

https://eur-lex.europa.eu/legal-content/EN/TXT/PDF/?uri=CELEX:32017R2196&from=EN

GC0108 Report:

https://www.nationalgrideso.com/codes/grid-code/modifications/gc0108-eu-code-emergency-restoration-black-start-testing-requirement

Emergency and Restoration consultation documents (including the System Restoration Plan):

https://www.nationalgrideso.com/codes/european-network-codes/meetings/emergency-and-restoration-consultation

# Proposers Solution

Section 2 (Original Proposal) and Section 3 (Proposer’s solution) are sourced directly from the Proposer and any statements or assertions have not been altered or substantiated/supported or refuted by the Workgroup. Section 5 of the Workgroup Consultation contains the discussion by the Workgroup on the Proposal and the potential solution.

E&R Article 46:

Each restoration service provider which is an HVDC system delivering a black start service shall execute a black start capability test, at least every three years.

HVDC Article 71(11):

With regard to the black start test, if applicable:

(a) the HVDC system shall demonstrate its technical capability to energise the busbar of the remote AC substation to which it is connected, within a time frame specified by the relevant TSO, according to Article 37(2);

(b) the test shall be carried out while the HVDC system starts from shut down;

(c) the test shall be deemed passed, provided that the following conditions are cumulatively fulfilled:

(i) the HVDC system has demonstrated being able to energise the busbar of the remote AC-substation to which it is connected;

(ii) the HVDC system operates from a stable operating point at agreed capacity, according to the procedure of Article 37(3).

Both the requirements from E&R and the methodology described in HVDC will need to be incorporated into the Grid Code.

- Impacts & Other Considerations

Interconnectors wishing to deliver a black start service will be affected as this will define how they must demonstrate compliance for this service and how often these tests will need to be completed. It should be noted that black start is not a mandatory service and so interconnectors not wishing to offer this service will not be affected.

Systems impacted include National Grid ESO Black Start testing.

#### Does this modification impact a Significant Code Review (SCR) or other significant industry change projects, if so, how?

No.

#### Consumer Impacts

This change will facilitate the implementation of the EU E&R which helps to facilitate a harmonised electricity system as part of the package of European Network Codes, and will help to deliver and facilitate a significant benefit to the end consumer by ensuring a coordinated security of supply across GB and Europe.

- Workgroup discussions

- The Workgroup convened xx times between May 2019 and June 2019 to discuss the perceived issue, detail the scope of the proposed defect, devise potential solutions and assess the proposal in terms of the Grid Code Objectives.  The Workgroup will in due course conclude these tasks after this consultation (taking account of responses to this consultation).

- The Workgroup discussed a number of the key attributes under GC0125 and these discussions are described below.

- Testing frequency, synchronisation and consistency

- The Proposer of GC0125 explained to the Workgroup that this modification has been raised to ensure that the requirements outlined in the E&R for HVDC systems are implemented into the Grid Code.  They outlined that there were two potential ways forward with regards to the legal text.  This would either be to create a new section for HVDC systems or to integrate the requirements in line with the Generator requirements.

- The Workgroup discussed this. The interconnector representative stated that ideally, they would like there to be a separate section whilst another Workgroup member stated that it would be of benefit to go through each clause of the legal text for Generators and assess whether it should be applicable for HVDC systems and added that this was part of the agreed Terms of Reference. This would then ensure consistency in the drafting of the legal text.  The Workgroup agreed that this would be the best way to proceed.  The Proposer stated that they wanted to ensure the legal text is as simple and easy to digest as possible whilst ensuring that the requirements are consistent between all Black Start providers where possible when considering the requirements as part of the E&R.

- The Workgroup went onto discuss whether the compliance testing was to also include synchronisation and not just the energisation of the busbar.  An example used by the Proposer when explaining Black Start testing was that if you had a car and needed to know whether it would be able to run in certain circumstances you wouldn’t simply ensure it turned on, you would also test whether it could run by attempting to complete the journey you would have to do.  This means fully simulating the black start situation.

- The Workgroup noted that there were some definitions that would not be relevant for HVDC such as shutdown.  The Proposer took an action to review these as part of the second iteration of the proposed legal text.

- A Workgroup member asked how often the tests would be carried out. The Proposer took an action to look into and clarify whether the tests would be required to be carried out every three or eight years. A Workgroup member stated that if this is every three years that this would in their view be difficult for the National Grid Electricity System Operator to complete. A Workgroup member stated that they thought that the testing of the energisation of the busbar would be every three years and the full test every eight years (that included synchronisation) as part of the Joint Restoration Plan.

- Blackstart Standard – new version 1 April 2020

- The Workgroup noted that there will be a new version of the Blackstart Standard in place from 1 April 2020.  The Workgroup discussed the fact that this may mean further amendments to the requirements on interconnectors in the future and that it was important that they were aware that these may change following the implementation of this modification (should it be approved by the Authority) The Workgroup decided that the best course of action was to note this given the fact that the draft of the document is not currently in the public domain for them to discuss. It was recognised that Interconnector parties had not been involved in these discussions and the interconnector representative has now contacted relevant people within National Grid Electricity System Operator to ascertain how interconnector parties can get involved.

- Notice ahead of testing

- Under Grid Code, National Grid Electricity System Operator are only required to provide seven days’ notice of requirement to carry out Black Start testing to Black Start Providers A Workgroup member enquired as to whether this is what happens in practice or whether it is just for emergency situations and would ideally prefer a longer notice period. The Proposer took an action to look into this and clarify.

- Cross modification considerations

- It was noted by the Workgroup that there were two Articles in the Emergency & Restoration plan that could lead to further amendments to the requirements on HVDC systems if not covered within the scope of this modification.  These were the following;

- Article 43 (2)

- By 18 December 2019 each TSO shall define a test plan in consultation with the DSOs, the SGUs identified pursuant to Articles 11(4) and 23(4), the defence service providers and the restoration service providers. The test plan shall identify the equipment and capabilities relevant for the system defence plan and the restoration plan that have to be tested.

- Article 51

- Compliance testing and periodic review of the restoration plan

- 1. Each TSO shall review the measures of its restoration plan using computer simulation tests, using data from the DSOs identified pursuant to Article 23(4) and the restoration service providers, at least every five years. The TSO shall define these simulation tests in a dedicated testing procedure covering at least:

- (a) the energising restoration path from restoration service providers with black start or island operation capabilities;

- (b) the supply of power generating modules main auxiliaries;

- (c) the demand reconnection process; and

- (d) the process for resynchronisation of networks in island operation. L 312/82 EN Official Journal of the European Union 28.11.2017 2.

- 2.In addition, where deemed necessary by the TSO for the effectiveness of the restoration plan, each TSO shall execute operational testing of parts of the restoration plan, in coordination with the DSOs identified pursuant to Article 23(4) and the restoration service providers. The TSO shall set out, in consultation with the DSOs and restoration service providers, those operational tests in a dedicated testing procedure.

- 3. Each TSO shall review its restoration plan to assess its effectiveness, at least every five years.

- 4. Each TSO shall review the relevant measures of its restoration plan in accordance with paragraph 1 and review their effectiveness before any substantial change in the configuration of the grid.

- 5. When the TSO identifies the need to adapt the restoration plan, it shall amend its restoration plan and implement these amendments in accordance with points (c) and (d) of Article 4(2) and Articles 23 and 24.

- The Proposer took an action to clarify whether these Articles would be addressed as part of this modification. It was noted that should it be covered in this modification that those impacted are not currently workgroup members and Proposer’s view is that these would be picked up as part of a different Modification.  It was also noted by the Workgroup that Interconnectors should be aware that these Articles will be addressed.

- The Workgroup agreed that they would be mindful of any other related modifications that were ongoing to ensure no overlap in legal text requirements and duplication of work.

- Relevant Objectives

| Impact of the modification on the Applicable Grid Code Objectives: |  |
| --- | --- |
| Relevant Objective | Identified impact |
| (a) To permit the development, maintenance and operation of an efficient, coordinated and economical system for the transmission of electricity | Positive - To permit the development, maintenance and operation of an efficient, coordinated and economical system for the transmission of electricity |
| (b) Facilitating effective competition in the generation and supply of electricity (and without limiting the foregoing, to facilitate the national electricity transmission system being made available to persons authorised to supply or generate electricity on terms which neither prevent nor restrict competition in the supply or generation of electricity); | Positive - Specifying these requirements will make it easier for interconnectors to offer black start as a service, thereby opening up the market to more participants and increasing competition. |
| (c) Subject to sub-paragraphs (i) and (ii), to promote the security and efficiency of the electricity generation, transmission and distribution systems in the national electricity transmission system operator area taken as a whole; | Positive - Encouraging more black start providers will allow for additional system security should a black start event ever occur. |
| (d) To efficiently discharge the obligations imposed upon the licensee by this license and to comply with the Electricity Regulation and any relevant legally binding decisions of the European Commission and/or the Agency; and | Positive - Discharges the obligations of the Emergency and Restoration code into GB frameworks. |
| (e) To promote efficiency in the implementation and administration of the Grid Code arrangements | None |

- Implementation

- GB is required to have implemented the System Defence and Restoration Plans by 18th December 2019; therefore this modification needs to have been approved and implemented by this deadline.

# How to respond

The GC0125 Workgroup is seeking the views of Grid Code Parties and other interested parties in relation to the issues noted in this document and specifically in response to the questions highlighted in the report and summarised below:

Standard Workgroup Consultation questions:

Q1:	Do you believe that GC0125 Original proposal better facilitates the Grid Code Objectives?

Q2:	Do you support the proposed implementation approach?

Q3:	Do you have any other comments?

Q4:	Do you wish to raise a Workgroup Consultation Alternative request for the Workgroup to consider?

Specific GC0125 Workgroup Consultations Questions:

Q5: 	.

Please send your response using the response proforma which can be found on the National Grid website via the following link:

https://www.nationalgrideso.com/codes/grid-code/modifications/gc0125-eu-code-emergency-restoration-black-start-testing-requirements

In accordance with the Grid Code Governance Rules of, Any Authorised Electricity Operator; the Citizens Advice or the Citizens Advice Scotland, The Company or a Materially Affected Party may also raise a Workgroup Consultation Alternative Request.  If you wish to raise such a request, please use the relevant form available at the weblink below:

http://www.nationalgrid.com/uk/Electricity/Codes/systemcode/amendments/forms_guidance/

Views are invited upon the proposals outlined in this report, which should be received by 5pm on xx June 2019.

Your formal responses may be emailed to: grid.code@nationalgrideso.com

If you wish to submit a confidential response, please note that information provided in response to this consultation will be published on National Grid’s website unless the response is clearly marked “Private & Confidential”, we will contact you to establish the extent of the confidentiality.  A response market “Private & Confidential” will be disclosed to the Authority in full but, unless agreed otherwise, will not be shared with the Grid Code Review Panel or the industry and may therefore not influence the debate to the same extent as a non-confidential response.

Please note an automatic confidentiality disclaimer generated by your IT System will not in itself, mean that your response is treated as if it had been marked “Private and Confidential”

# Annex 1 – extracts from European Network Codes

- Emergency & Restoration Code

Article 46

Compliance testing of HVDC capabilities

Each restoration service provider which is an HVDC system delivering a black start service shall execute a black start capability test, at least every three years, following the methodology laid down in Article 70(11) of Regulation (EU) 2016/1447.

HVDC

Article 71

Compliance testing for HVDC systems

11.   With regard to the black start test, if applicable:

| (a) | the HVDC system shall demonstrate its technical capability to energise the busbar of the remote AC substation to which it is connected, within a time frame specified by the relevant TSO, according to Article 37(2); |
| --- | --- |

| (b) | the test shall be carried out while the HVDC system starts from shut down; |
| --- | --- |

| (c) | the test shall be deemed passed, provided that the following conditions are cumulatively fulfilled: (i); the HVDC system has demonstrated being able to energise the busbar of the remote AC-substation to which it is connected;. (ii); the HVDC system operates from a stable operating point at agreed capacity, according to the procedure of Article 37(3).. |
| --- | --- |

Article 37

Black start

1.   The relevant TSO may obtain a quote for black start capability from an HVDC system owner.

2.   An HVDC system with black start capability shall be able, in case one converter station is energised, to energise the busbar of the AC-substation to which another converter station is connected, within a timeframe after shut down of the HVDC system determined by the relevant TSOs. The HVDC system shall be able to synchronise within the frequency limits set out in Article 11 and within the voltage limits specified by the relevant TSO or as provided for in Article 18, where applicable. Wider frequency and voltage ranges can be specified by the relevant TSO where needed in order to restore system security.

3.   The relevant TSO and the HVDC system owner shall agree on the capacity and availability of the black start capability and the operational procedure.

# Annex 2 – Terms of Reference

# Annex 3 – Draft legal text

# Annex 4 – Attendance log

- Key

A – Attended

X – Absent

O – Alternate

D – Dial-in

| Name | Organisation | Role | 09/05/2019 (informal meeting) |  |  |
| --- | --- | --- | --- | --- | --- |
| Paul Mullen | Code Administrator, NG Electricity System Operator | Chair | A |  |  |
| Chrissie Brown | Code Administrator, NG Electricity System Operator | Technical Secretary | A |  |  |
| Anthony Johnson | National Grid Electricity System Operator | Proposer/Workgroup member | A |  |  |
| Alastair Frew | Drax Generation Enterprise Ltd | Workgroup member | D |  |  |
| Garth Graham | SSE Generation Limited | Workgroup member | D |  |  |
| Russell Smalley | Viking Link | Workgroup member | A |  |  |
| Nigel Wood | Nemolink Limited | Workgroup member | X |  |  |