## OPMR
BMRS Surplus (SPLD) Breakdown & Total Contracted Availability
National Grid gathers generation availability information from Generators over a variety of timescales via information provision mechanisms established under OC2 of the Grid Code. In accordance with the BSC, this information is reflected back to the market in aggregate format predominantly via the Balancing Mechanism Reporting Service (BMRS).
When assessing and publishing generation availability information against system requirements, National Grid includes an Operational Planning Margin Requirement (OPMR) above demand forecast. This OPMR is the amount of generation, in excess of demand forecast, that is required to meet National Grid’s Day-Ahead Reserve Requirement.
The relevant provisions within the BSC do not provide for the explicit publication of OPMR, but rather describe the publication of a “Surplus”, being the difference between the overall system requirement (demand forecast + OPMR) and the aggregate available generation.
National Grid publishes OPMR, and its constituent parts, in a manner which complements the information currently on the BMRS and to meet Grid Code requirements. The intention is to assist Market Participants in understanding and interpreting the generation availability information.

## 29-Nov-2019
|  | Relevant Information |  |  |  |  | Calculated | OPMR Variables | [5 empty] | Total OPMR adjustors |  | Calculated |  | Wind |  | Negative Reserve at minimum demand
|  | a | b | c | d | e | f | g | h | i | j | k | l | m | n | o | p | q | r | s | t | u
Publish Date | Date | Peak Demand Forecast | Generator Availability | Contracted Availability | Maximum I/C Export | Maximum I/C Import | Generation Availability Margin | Contingency Requirement | STORR Requirement | Operating Reserve provided by I/Cs | Unavailable to Market & Commissioning Plant | Unavailable to National Grid | Available only to National Grid in exceptional circumstances | Reduction from additional availability (Not declared via OC2) | Reduction in Low Frequency Response Reserve Requirement (due to Contracted Response) | OPMR total | National Surplus (SPLD) | Effect of wind on surplus | Generation Availability Margin excluding wind | Minimum Demand Forecast | Total Negative Reserve Requirement for Minimum Demand | High Freq Response Requirement
2019-11-29 | 2019-12-01 | 42210 | 57964 | 3047.9144 | 3250 | 3250 | 15754 | 1200 | 4040.3743 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 4037.4599 | 11716.5401 | 6474 | 9280 | 22430 | 2249.7576 | 522.3667
2019-11-29 | 2019-12-02 | 46910 | 56651 | 3047.9144 | 3250 | 3250 | 9741 | 1200 | 3914.7059 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 3911.7914 | 5829.2086 | 5412 | 4329 | 23700 | 2535.5556 | 509.6667
2019-11-29 | 2019-12-03 | 46920 | 55803 | 3047.9144 | 3250 | 3250 | 8883 | 1200 | 3914.4385 | 181.8182 | 156 | 0 | 0 | -913 | -467.9144 | 3889.5241 | 4993.4759 | 4893 | 3990 | 24790 | 2509.1313 | 498.7667
2019-11-29 | 2019-12-04 | 46860 | 56177 | 3047.9144 | 3250 | 3250 | 9317 | 1200 | 3916.0428 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 3913.1283 | 5403.8717 | 5239 | 4078 | 24910 | 2506.2222 | 497.5667
2019-11-29 | 2019-12-05 | 44850 | 62222 | 3047.9144 | 3250 | 3250 | 17372 | 1200 | 3969.7861 | 181.8182 | 178 | 1010.7 | 0 | -913 | -467.9144 | 4977.5717 | 12394.4283 | 10684.3 | 6687.7 | 24910 | 2506.2222 | 497.5667
2019-11-29 | 2019-12-06 | 43130 | 59280 | 3047.9144 | 3250 | 3250 | 16150 | 1200 | 4015.7754 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 4012.861 | 12137.139 | 9206 | 6944 | 24910 | 2506.2222 | 497.5667
2019-11-29 | 2019-12-07 | 40320 | 56904 | 3047.9144 | 3250 | 3250 | 16584 | 1200 | 4090.9091 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 4087.9947 | 12496.0053 | 8166 | 8418 | 23700 | 2535.5556 | 509.6667
2019-11-29 | 2019-12-08 | 40940 | 57778 | 3047.9144 | 3250 | 3250 | 16838 | 1200 | 4074.3316 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 4071.4171 | 12766.5829 | 8875 | 7963 | 22730 | 2559.0707 | 519.3667
2019-11-29 | 2019-12-09 | 45380 | 59636 | 3047.9144 | 3250 | 3250 | 14256 | 1200 | 3955.615 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 3952.7005 | 10303.2995 | 8964 | 5292 | 24150 | 2524.6465 | 505.1667
2019-11-29 | 2019-12-10 | 45710 | 59289 | 3047.9144 | 3250 | 3250 | 13579 | 1200 | 3946.7914 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 3943.877 | 9635.123 | 8384 | 5195 | 25240 | 2498.2222 | 494.2667
2019-11-29 | 2019-12-11 | 46070 | 57053 | 3047.9144 | 3250 | 3250 | 10983 | 1200 | 3937.1658 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 3934.2513 | 7048.7487 | 6634 | 4349 | 25360 | 2495.3131 | 493.0667
2019-11-29 | 2019-12-12 | 46090 | 56201 | 3047.9144 | 3250 | 3250 | 10111 | 1200 | 3936.631 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 3933.7166 | 6177.2834 | 6157 | 3954 | 25360 | 2495.3131 | 493.0667
2019-11-29 | 2019-12-13 | 43940 | 58601 | 3047.9144 | 3250 | 3250 | 14661 | 1200 | 3994.1176 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 3991.2032 | 10669.7968 | 8467 | 6194 | 25360 | 2495.3131 | 493.0667
OPMR total (o) = (g) + (h) + (j) + (k) +(l) + (m) + (n)
Generation Plant Margin (f) = (b) - (a) ALIGNS WITH ELEXON WEBSITE
National Surplus (p) = (f) - (o) ALIGNS WITH BMRS

## 28-Nov-2019
|  | Relevant Information |  |  |  |  | Calculated | OPMR Variables | [5 empty] | Total OPMR adjustors |  | Calculated |  | Wind |  | Negative Reserve at minimum demand
|  | a | b | c | d | e | f | g | h | i | j | k | l | m | n | o | p | q | r | s | t | u
Publish Date | Date | Peak Demand Forecast | Generator Availability | Contracted Availability | Maximum I/C Export | Maximum I/C Import | Generation Availability Margin | Contingency Requirement | STORR Requirement | Operating Reserve provided by I/Cs | Unavailable to Market & Commissioning Plant | Unavailable to National Grid | Available only to National Grid in exceptional circumstances | Reduction from additional availability (Not declared via OC2) | Reduction in Low Frequency Response Reserve Requirement (due to Contracted Response) | OPMR total | National Surplus (SPLD) | Effect of wind on surplus | Generation Availability Margin excluding wind | Minimum Demand Forecast | Total Negative Reserve Requirement for Minimum Demand | High Freq Response Requirement
2019-11-28 | 2019-11-30 | 41290 | 53363 | 3047.9144 | 3250 | 3250 | 12073 | 1200 | 4064.9733 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 4062.0588 | 8010.9412 | 3697 | 8376 | 23400 | 2232.1212 | 512.6667
2019-11-28 | 2019-12-01 | 42220 | 57122 | 3047.9144 | 3250 | 3250 | 14902 | 1200 | 4040.107 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 4037.1925 | 10864.8075 | 6447 | 8455 | 22430 | 2566.3434 | 522.3667
2019-11-28 | 2019-12-02 | 46420 | 58567 | 3047.9144 | 3250 | 3250 | 12147 | 1200 | 3927.8075 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 3924.893 | 8222.107 | 7523 | 4624 | 23700 | 2535.5556 | 509.6667
2019-11-28 | 2019-12-03 | 46240 | 58727 | 3047.9144 | 3250 | 3250 | 12487 | 1200 | 3932.6203 | 181.8182 | 178 | 115.81 | 0 | -913 | -467.9144 | 4045.5159 | 8441.4841 | 7831.19 | 4655.81 | 24790 | 2509.1313 | 498.7667
2019-11-28 | 2019-12-04 | 45400 | 60135 | 3047.9144 | 3250 | 3250 | 14735 | 1200 | 3955.0802 | 181.8182 | 178 | 635.34 | 0 | -913 | -467.9144 | 4587.5058 | 10147.4942 | 9131.66 | 5603.34 | 24910 | 2506.2222 | 497.5667
2019-11-28 | 2019-12-05 | 43900 | 60190 | 3047.9144 | 3250 | 3250 | 16290 | 1200 | 3995.1872 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 3992.2727 | 12297.7273 | 10279 | 6011 | 24910 | 2506.2222 | 497.5667
2019-11-28 | 2019-12-06 | 42510 | 59271 | 3047.9144 | 3250 | 3250 | 16761 | 1200 | 4032.3529 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 4029.4385 | 12731.5615 | 9457 | 7304 | 24910 | 2506.2222 | 497.5667
2019-11-28 | 2019-12-07 | 39810 | 57278 | 3047.9144 | 3250 | 3250 | 17468 | 1200 | 4104.5455 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 4101.631 | 13366.369 | 8493 | 8975 | 23700 | 2535.5556 | 509.6667
2019-11-28 | 2019-12-08 | 41140 | 57108 | 3047.9144 | 3250 | 3250 | 15968 | 1200 | 4068.984 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 4066.0695 | 11901.9305 | 8169 | 7799 | 22730 | 2559.0707 | 519.3667
2019-11-28 | 2019-12-09 | 45530 | 57382 | 3047.9144 | 3250 | 3250 | 11852 | 1200 | 3951.6043 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 3948.6898 | 7903.3102 | 7112 | 4740 | 24150 | 2524.6465 | 505.1667
2019-11-28 | 2019-12-10 | 45830 | 58335 | 3047.9144 | 3250 | 3250 | 12505 | 1200 | 3943.5829 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 3940.6684 | 8564.3316 | 7799 | 4706 | 25240 | 2498.2222 | 494.2667
2019-11-28 | 2019-12-11 | 46070 | 57289 | 3047.9144 | 3250 | 3250 | 11219 | 1200 | 3937.1658 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 3934.2513 | 7284.7487 | 7226 | 3993 | 25360 | 2495.3131 | 493.0667
2019-11-28 | 2019-12-12 | 45270 | 58392 | 3047.9144 | 3250 | 3250 | 13122 | 1200 | 3958.5561 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 3955.6417 | 9166.3583 | 8454 | 4668 | 25360 | 2495.3131 | 493.0667
OPMR total (o) = (g) + (h) + (j) + (k) +(l) + (m) + (n)
Generation Plant Margin (f) = (b) - (a) ALIGNS WITH ELEXON WEBSITE
National Surplus (p) = (f) - (o) ALIGNS WITH BMRS

## 27-Nov-2019
|  | Relevant Information |  |  |  |  | Calculated | OPMR Variables | [5 empty] | Total OPMR adjustors |  | Calculated |  | Wind |  | Negative Reserve at minimum demand
|  | a | b | c | d | e | f | g | h | i | j | k | l | m | n | o | p | q | r | s | t | u
Publish Date | Date | Peak Demand Forecast | Generator Availability | Contracted Availability | Maximum I/C Export | Maximum I/C Import | Generation Availability Margin | Contingency Requirement | STORR Requirement | Operating Reserve provided by I/Cs | Unavailable to Market & Commissioning Plant | Unavailable to National Grid | Available only to National Grid in exceptional circumstances | Reduction from additional availability (Not declared via OC2) | Reduction in Low Frequency Response Reserve Requirement (due to Contracted Response) | OPMR total | National Surplus (SPLD) | Effect of wind on surplus | Generation Availability Margin excluding wind | Minimum Demand Forecast | Total Negative Reserve Requirement for Minimum Demand | High Freq Response Requirement
2019-11-27 | 2019-11-29 | 44640 | 52944 | 3047.9144 | 3250 | 3250 | 8304 | 1200 | 3975.4011 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 3972.4866 | 4331.5134 | 3227 | 5077 | 24600 | 2210.303 | 500.6667
2019-11-27 | 2019-11-30 | 41860 | 52395 | 3047.9144 | 3250 | 3250 | 10535 | 1200 | 4049.7326 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 4046.8182 | 6488.1818 | 2127 | 8408 | 23400 | 2542.8283 | 512.6667
2019-11-27 | 2019-12-01 | 42450 | 57842 | 3047.9144 | 3250 | 3250 | 15392 | 1200 | 4033.9572 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 4031.0428 | 11360.9572 | 6937 | 8455 | 22430 | 2566.3434 | 522.3667
2019-11-27 | 2019-12-02 | 47510 | 55983 | 3047.9144 | 3250 | 3250 | 8473 | 1200 | 3898.6631 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 3895.7487 | 4577.2513 | 5043 | 3430 | 23700 | 2535.5556 | 509.6667
2019-11-27 | 2019-12-03 | 46370 | 60319 | 3047.9144 | 3250 | 3250 | 13949 | 1200 | 3929.1444 | 181.8182 | 178 | 557.81 | 0 | -913 | -467.9144 | 4484.0399 | 9464.9601 | 9053.19 | 4895.81 | 24790 | 2509.1313 | 498.7667
2019-11-27 | 2019-12-04 | 46620 | 57066 | 3047.9144 | 3250 | 3250 | 10446 | 1200 | 3922.4599 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 3919.5455 | 6526.4545 | 6845 | 3601 | 24910 | 2506.2222 | 497.5667
2019-11-27 | 2019-12-05 | 45100 | 58893 | 3047.9144 | 3250 | 3250 | 13793 | 1200 | 3963.1016 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 3960.1872 | 9832.8128 | 8949 | 4844 | 24910 | 2506.2222 | 497.5667
2019-11-27 | 2019-12-06 | 43290 | 58946 | 3047.9144 | 3250 | 3250 | 15656 | 1200 | 4011.4973 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 4008.5829 | 11647.4171 | 9174 | 6482 | 24910 | 2506.2222 | 497.5667
2019-11-27 | 2019-12-07 | 40300 | 56789 | 3047.9144 | 3250 | 3250 | 16489 | 1200 | 4091.4439 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 4088.5294 | 12400.4706 | 8050 | 8439 | 23700 | 2535.5556 | 509.6667
2019-11-27 | 2019-12-08 | 41160 | 56817 | 3047.9144 | 3250 | 3250 | 15657 | 1200 | 4068.4492 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 4065.5348 | 11591.4652 | 7933 | 7724 | 22730 | 2559.0707 | 519.3667
2019-11-27 | 2019-12-09 | 45650 | 57743 | 3047.9144 | 3250 | 3250 | 12093 | 1200 | 3948.3957 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 3945.4813 | 8147.5187 | 7504 | 4589 | 24150 | 2524.6465 | 505.1667
2019-11-27 | 2019-12-10 | 45840 | 57675 | 3047.9144 | 3250 | 3250 | 11835 | 1200 | 3943.3155 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 3940.4011 | 7894.5989 | 7419 | 4416 | 25240 | 2498.2222 | 494.2667
2019-11-27 | 2019-12-11 | 45670 | 58847 | 3047.9144 | 3250 | 3250 | 13177 | 1200 | 3947.861 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 3944.9465 | 9232.0535 | 8556 | 4621 | 25360 | 2495.3131 | 493.0667
OPMR total (o) = (g) + (h) + (j) + (k) +(l) + (m) + (n)
Generation Plant Margin (f) = (b) - (a) ALIGNS WITH ELEXON WEBSITE
National Surplus (p) = (f) - (o) ALIGNS WITH BMRS

## 26-Nov-2019
|  | Relevant Information |  |  |  |  | Calculated | OPMR Variables | [5 empty] | Total OPMR adjustors |  | Calculated |  | Wind |  | Negative Reserve at minimum demand
|  | a | b | c | d | e | f | g | h | i | j | k | l | m | n | o | p | q | r | s | t | u
Publish Date | Date | Peak Demand Forecast | Generator Availability | Contracted Availability | Maximum I/C Export | Maximum I/C Import | Generation Availability Margin | Contingency Requirement | STORR Requirement | Operating Reserve provided by I/Cs | Unavailable to Market & Commissioning Plant | Unavailable to National Grid | Available only to National Grid in exceptional circumstances | Reduction from additional availability (Not declared via OC2) | Reduction in Low Frequency Response Reserve Requirement (due to Contracted Response) | OPMR total | National Surplus (SPLD) | Effect of wind on surplus | Generation Availability Margin excluding wind | Minimum Demand Forecast | Total Negative Reserve Requirement for Minimum Demand | High Freq Response Requirement
2019-11-26 | 2019-11-28 | 43640 | 59110 | 3047.9144 | 3250 | 3250 | 15470 | 1200 | 4002.139 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 3999.2246 | 11470.7754 | 9068 | 6402 | 24500 | 2212.1212 | 501.6667
2019-11-26 | 2019-11-29 | 44770 | 54646 | 3047.9144 | 3250 | 3250 | 9876 | 1200 | 3971.9251 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 3969.0107 | 5906.9893 | 4665 | 5211 | 24600 | 2513.7374 | 500.6667
2019-11-26 | 2019-11-30 | 42160 | 52224 | 3047.9144 | 3250 | 3250 | 10064 | 1200 | 4041.7112 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 4038.7968 | 6025.2032 | 2062 | 8002 | 23400 | 2542.8283 | 512.6667
2019-11-26 | 2019-12-01 | 42920 | 57081 | 3047.9144 | 3250 | 3250 | 14161 | 1200 | 4021.3904 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 4018.4759 | 10142.5241 | 6251 | 7910 | 22430 | 2566.3434 | 522.3667
2019-11-26 | 2019-12-02 | 47420 | 57016 | 3047.9144 | 3250 | 3250 | 9596 | 1200 | 3901.0695 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 3898.1551 | 5697.8449 | 6391 | 3205 | 23700 | 2535.5556 | 509.6667
2019-11-26 | 2019-12-03 | 47780 | 55214 | 3047.9144 | 3250 | 3250 | 7434 | 1200 | 3891.4439 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 3888.5294 | 3545.4706 | 4280 | 3154 | 24790 | 2509.1313 | 498.7667
2019-11-26 | 2019-12-04 | 46780 | 57256 | 3047.9144 | 3250 | 3250 | 10476 | 1200 | 3918.1818 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 3915.2674 | 6560.7326 | 6718 | 3758 | 24910 | 2506.2222 | 497.5667
2019-11-26 | 2019-12-05 | 45390 | 57544 | 3047.9144 | 3250 | 3250 | 12154 | 1200 | 3955.3476 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 3952.4332 | 8201.5668 | 7681 | 4473 | 24910 | 2506.2222 | 497.5667
2019-11-26 | 2019-12-06 | 43750 | 57507 | 3047.9144 | 3250 | 3250 | 13757 | 1200 | 3999.1979 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 3996.2834 | 9760.7166 | 7950 | 5807 | 24910 | 2506.2222 | 497.5667
2019-11-26 | 2019-12-07 | 40420 | 56533 | 3047.9144 | 3250 | 3250 | 16113 | 1200 | 4088.2353 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 4085.3209 | 12027.6791 | 8016 | 8097 | 23700 | 2535.5556 | 509.6667
2019-11-26 | 2019-12-08 | 41270 | 57431 | 3047.9144 | 3250 | 3250 | 16161 | 1200 | 4065.508 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 4062.5936 | 12098.4064 | 8208 | 7953 | 22730 | 2559.0707 | 519.3667
2019-11-26 | 2019-12-09 | 45760 | 58678 | 3047.9144 | 3250 | 3250 | 12918 | 1200 | 3945.4545 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 3942.5401 | 8975.4599 | 8242 | 4676 | 24150 | 2524.6465 | 505.1667
2019-11-26 | 2019-12-10 | 45620 | 59210 | 3047.9144 | 3250 | 3250 | 13590 | 1200 | 3949.1979 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 3946.2834 | 9643.7166 | 8534 | 5056 | 25240 | 2498.2222 | 494.2667
OPMR total (o) = (g) + (h) + (j) + (k) +(l) + (m) + (n)
Generation Plant Margin (f) = (b) - (a) ALIGNS WITH ELEXON WEBSITE
National Surplus (p) = (f) - (o) ALIGNS WITH BMRS

## 25-Nov-2019
|  | Relevant Information |  |  |  |  | Calculated | OPMR Variables | [5 empty] | Total OPMR adjustors |  | Calculated |  | Wind |  | Negative Reserve at minimum demand
|  | a | b | c | d | e | f | g | h | i | j | k | l | m | n | o | p | q | r | s | t | u
Publish Date | Date | Peak Demand Forecast | Generator Availability | Contracted Availability | Maximum I/C Export | Maximum I/C Import | Generation Availability Margin | Contingency Requirement | STORR Requirement | Operating Reserve provided by I/Cs | Unavailable to Market & Commissioning Plant | Unavailable to National Grid | Available only to National Grid in exceptional circumstances | Reduction from additional availability (Not declared via OC2) | Reduction in Low Frequency Response Reserve Requirement (due to Contracted Response) | OPMR total | National Surplus (SPLD) | Effect of wind on surplus | Generation Availability Margin excluding wind | Minimum Demand Forecast | Total Negative Reserve Requirement for Minimum Demand | High Freq Response Requirement
2019-11-25 | 2019-11-27 | 43630 | 55129 | 3047.9144 | 3250 | 3250 | 11499 | 1200 | 4002.4064 | 181.8182 | 22 | 0 | 0 | -913 | -467.9144 | 3843.492 | 7655.508 | 6098 | 5401 | 24400 | 2213.9394 | 502.6667
2019-11-25 | 2019-11-28 | 43590 | 58155 | 3047.9144 | 3250 | 3250 | 14565 | 1200 | 4003.4759 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 4000.5615 | 10564.4385 | 8389 | 6176 | 24500 | 2516.1616 | 501.6667
2019-11-25 | 2019-11-29 | 44540 | 52931 | 3047.9144 | 3250 | 3250 | 8391 | 1200 | 3978.0749 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 3975.1604 | 4415.8396 | 3199 | 5192 | 24600 | 2513.7374 | 500.6667
2019-11-25 | 2019-11-30 | 41890 | 52272 | 3047.9144 | 3250 | 3250 | 10382 | 1200 | 4048.9305 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 4046.016 | 6335.984 | 2273 | 8109 | 23400 | 2542.8283 | 512.6667
2019-11-25 | 2019-12-01 | 42810 | 55926 | 3047.9144 | 3250 | 3250 | 13116 | 1200 | 4024.3316 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 4021.4171 | 9094.5829 | 5402 | 7714 | 22430 | 2566.3434 | 522.3667
2019-11-25 | 2019-12-02 | 47420 | 57037 | 3047.9144 | 3250 | 3250 | 9617 | 1200 | 3901.0695 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 3898.1551 | 5718.8449 | 6029 | 3588 | 23700 | 2535.5556 | 509.6667
2019-11-25 | 2019-12-03 | 47340 | 57807 | 3047.9144 | 3250 | 3250 | 10467 | 1200 | 3903.2086 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 3900.2941 | 6566.7059 | 6204 | 4263 | 24790 | 2509.1313 | 498.7667
2019-11-25 | 2019-12-04 | 46440 | 58949 | 3047.9144 | 3250 | 3250 | 12509 | 1200 | 3927.2727 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 3924.3583 | 8584.6417 | 7759 | 4750 | 24910 | 2506.2222 | 497.5667
2019-11-25 | 2019-12-05 | 45410 | 58115 | 3047.9144 | 3250 | 3250 | 12705 | 1200 | 3954.8128 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 3951.8984 | 8753.1016 | 7811 | 4894 | 24910 | 2506.2222 | 497.5667
2019-11-25 | 2019-12-06 | 43660 | 58439 | 3047.9144 | 3250 | 3250 | 14779 | 1200 | 4001.6043 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 3998.6898 | 10780.3102 | 8454 | 6325 | 24910 | 2506.2222 | 497.5667
2019-11-25 | 2019-12-07 | 40480 | 56368 | 3047.9144 | 3250 | 3250 | 15888 | 1200 | 4086.631 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 4083.7166 | 11804.2834 | 7411 | 8477 | 23700 | 2535.5556 | 509.6667
2019-11-25 | 2019-12-08 | 41270 | 58354 | 3047.9144 | 3250 | 3250 | 17084 | 1200 | 4065.508 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 4062.5936 | 13021.4064 | 8686 | 8398 | 22730 | 2559.0707 | 519.3667
2019-11-25 | 2019-12-09 | 45560 | 59174 | 3047.9144 | 3250 | 3250 | 13614 | 1200 | 3950.8021 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 3947.8877 | 9666.1123 | 8524 | 5090 | 24150 | 2524.6465 | 505.1667
OPMR total (o) = (g) + (h) + (j) + (k) +(l) + (m) + (n)
Generation Plant Margin (f) = (b) - (a) ALIGNS WITH ELEXON WEBSITE
National Surplus (p) = (f) - (o) ALIGNS WITH BMRS

## 22-Nov-2019
|  | Relevant Information |  |  |  |  | Calculated | OPMR Variables | [5 empty] | Total OPMR adjustors |  | Calculated |  | Wind |  | Negative Reserve at minimum demand
|  | a | b | c | d | e | f | g | h | i | j | k | l | m | n | o | p | q | r | s | t | u
Publish Date | Date | Peak Demand Forecast | Generator Availability | Contracted Availability | Maximum I/C Export | Maximum I/C Import | Generation Availability Margin | Contingency Requirement | STORR Requirement | Operating Reserve provided by I/Cs | Unavailable to Market & Commissioning Plant | Unavailable to National Grid | Available only to National Grid in exceptional circumstances | Reduction from additional availability (Not declared via OC2) | Reduction in Low Frequency Response Reserve Requirement (due to Contracted Response) | OPMR total | National Surplus (SPLD) | Effect of wind on surplus | Generation Availability Margin excluding wind | Minimum Demand Forecast | Total Negative Reserve Requirement for Minimum Demand | High Freq Response Requirement
2019-11-22 | 2019-11-24 | 39940 | 49876 | 3047.9144 | 3250 | 3250 | 9936 | 1200 | 4101.0695 | 181.8182 | 22 | 0 | 0 | -913 | -467.9144 | 3942.1551 | 5993.8449 | 5227 | 4709 | 22170 | 2254.4848 | 524.9667
2019-11-22 | 2019-11-25 | 43510 | 55209 | 3047.9144 | 3250 | 3250 | 11699 | 1200 | 4005.615 | 181.8182 | 22 | 0 | 0 | -913 | -467.9144 | 3846.7005 | 7852.2995 | 6106 | 5593 | 23200 | 2547.6768 | 514.6667
2019-11-22 | 2019-11-26 | 43730 | 53829 | 3047.9144 | 3250 | 3250 | 10099 | 1200 | 3999.7326 | 181.8182 | 22 | 0 | 0 | -913 | -467.9144 | 3840.8182 | 6258.1818 | 4841 | 5258 | 24280 | 2521.4949 | 503.8667
2019-11-22 | 2019-11-27 | 43640 | 56342 | 3047.9144 | 3250 | 3250 | 12702 | 1200 | 4002.139 | 181.8182 | 22 | 0 | 0 | -913 | -467.9144 | 3843.2246 | 8858.7754 | 6822 | 5880 | 24400 | 2518.5859 | 502.6667
2019-11-22 | 2019-11-28 | 44260 | 55616 | 3047.9144 | 3250 | 3250 | 11356 | 1200 | 3985.5615 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 3982.6471 | 7373.3529 | 5761 | 5595 | 24500 | 2516.1616 | 501.6667
2019-11-22 | 2019-11-29 | 44160 | 53723 | 3047.9144 | 3250 | 3250 | 9563 | 1200 | 3988.2353 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 3985.3209 | 5577.6791 | 3960 | 5603 | 24600 | 2513.7374 | 500.6667
2019-11-22 | 2019-11-30 | 40860 | 55854 | 3047.9144 | 3250 | 3250 | 14994 | 1200 | 4076.4706 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 4073.5561 | 10920.4439 | 6051 | 8943 | 23400 | 2542.8283 | 512.6667
2019-11-22 | 2019-12-01 | 41770 | 57952 | 3047.9144 | 3250 | 3250 | 16182 | 1200 | 4052.139 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 4049.2246 | 12132.7754 | 6901 | 9281 | 22430 | 2566.3434 | 522.3667
2019-11-22 | 2019-12-02 | 46220 | 58662 | 3047.9144 | 3250 | 3250 | 12442 | 1200 | 3933.1551 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 3930.2406 | 8511.7594 | 7380 | 5062 | 23700 | 2535.5556 | 509.6667
2019-11-22 | 2019-12-03 | 45910 | 60296 | 3047.9144 | 3250 | 3250 | 14386 | 1200 | 3941.4439 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 3938.5294 | 10447.4706 | 8453 | 5933 | 24790 | 2509.1313 | 498.7667
2019-11-22 | 2019-12-04 | 45750 | 59633 | 3047.9144 | 3250 | 3250 | 13883 | 1200 | 3945.7219 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 3942.8075 | 9940.1925 | 8046 | 5837 | 24910 | 2506.2222 | 497.5667
2019-11-22 | 2019-12-05 | 45010 | 58886 | 3047.9144 | 3250 | 3250 | 13876 | 1200 | 3965.508 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 3962.5936 | 9913.4064 | 8132 | 5744 | 24910 | 2506.2222 | 497.5667
2019-11-22 | 2019-12-06 | 43610 | 59104 | 3047.9144 | 3250 | 3250 | 15494 | 1200 | 4002.9412 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 4000.0267 | 11493.9733 | 8468 | 7026 | 24910 | 2506.2222 | 497.5667
OPMR total (o) = (g) + (h) + (j) + (k) +(l) + (m) + (n)
Generation Plant Margin (f) = (b) - (a) ALIGNS WITH ELEXON WEBSITE
National Surplus (p) = (f) - (o) ALIGNS WITH BMRS

## 21-Nov-2019
|  | Relevant Information |  |  |  |  | Calculated | OPMR Variables | [5 empty] | Total OPMR adjustors |  | Calculated |  | Wind |  | Negative Reserve at minimum demand
|  | a | b | c | d | e | f | g | h | i | j | k | l | m | n | o | p | q | r | s | t | u
Publish Date | Date | Peak Demand Forecast | Generator Availability | Contracted Availability | Maximum I/C Export | Maximum I/C Import | Generation Availability Margin | Contingency Requirement | STORR Requirement | Operating Reserve provided by I/Cs | Unavailable to Market & Commissioning Plant | Unavailable to National Grid | Available only to National Grid in exceptional circumstances | Reduction from additional availability (Not declared via OC2) | Reduction in Low Frequency Response Reserve Requirement (due to Contracted Response) | OPMR total | National Surplus (SPLD) | Effect of wind on surplus | Generation Availability Margin excluding wind | Minimum Demand Forecast | Total Negative Reserve Requirement for Minimum Demand | High Freq Response Requirement
2019-11-21 | 2019-11-23 | 39320 | 52348 | 3047.9144 | 3250 | 3250 | 13028 | 1200 | 4117.6471 | 181.8182 | 22 | 168.52 | 0 | -913 | -467.9144 | 4127.2526 | 8900.7474 | 6763.48 | 6264.52 | 23150 | 2236.6667 | 515.1667
2019-11-21 | 2019-11-24 | 39940 | 51389 | 3047.9144 | 3250 | 3250 | 11449 | 1200 | 4101.0695 | 181.8182 | 22 | 0 | 0 | -913 | -467.9144 | 3942.1551 | 7506.8449 | 5419 | 6030 | 22170 | 2572.6465 | 524.9667
2019-11-21 | 2019-11-25 | 43830 | 54889 | 3047.9144 | 3250 | 3250 | 11059 | 1200 | 3997.0588 | 181.8182 | 22 | 0 | 0 | -913 | -467.9144 | 3838.1444 | 7220.8556 | 5374 | 5685 | 23200 | 2547.6768 | 514.6667
2019-11-21 | 2019-11-26 | 44370 | 53988 | 3047.9144 | 3250 | 3250 | 9618 | 1200 | 3982.6203 | 181.8182 | 22 | 0 | 0 | -913 | -467.9144 | 3823.7059 | 5794.2941 | 4586 | 5032 | 24280 | 2521.4949 | 503.8667
2019-11-21 | 2019-11-27 | 44230 | 56068 | 3047.9144 | 3250 | 3250 | 11838 | 1200 | 3986.3636 | 181.8182 | 22 | 0 | 0 | -913 | -467.9144 | 3827.4492 | 8010.5508 | 6091 | 5747 | 24400 | 2518.5859 | 502.6667
2019-11-21 | 2019-11-28 | 44910 | 55739 | 3047.9144 | 3250 | 3250 | 10829 | 1200 | 3968.1818 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 3965.2674 | 6863.7326 | 5503 | 5326 | 24500 | 2516.1616 | 501.6667
2019-11-21 | 2019-11-29 | 44160 | 55720 | 3047.9144 | 3250 | 3250 | 11560 | 1200 | 3988.2353 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 3985.3209 | 7574.6791 | 5479 | 6081 | 24600 | 2513.7374 | 500.6667
2019-11-21 | 2019-11-30 | 40980 | 55644 | 3047.9144 | 3250 | 3250 | 14664 | 1200 | 4073.262 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 4070.3476 | 10593.6524 | 5848 | 8816 | 23400 | 2542.8283 | 512.6667
2019-11-21 | 2019-12-01 | 41860 | 57694 | 3047.9144 | 3250 | 3250 | 15834 | 1200 | 4049.7326 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 4046.8182 | 11787.1818 | 6638 | 9196 | 22430 | 2566.3434 | 522.3667
2019-11-21 | 2019-12-02 | 45840 | 57940 | 3047.9144 | 3250 | 3250 | 12100 | 1200 | 3943.3155 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 3940.4011 | 8159.5989 | 6666 | 5434 | 23700 | 2535.5556 | 509.6667
2019-11-21 | 2019-12-03 | 45740 | 58231 | 3047.9144 | 3250 | 3250 | 12491 | 1200 | 3945.9893 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 3943.0749 | 8547.9251 | 6391 | 6100 | 24790 | 2509.1313 | 498.7667
2019-11-21 | 2019-12-04 | 45640 | 58363 | 3047.9144 | 3250 | 3250 | 12723 | 1200 | 3948.6631 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 3945.7487 | 8777.2513 | 6777 | 5946 | 24910 | 2506.2222 | 497.5667
2019-11-21 | 2019-12-05 | 44910 | 59653 | 3047.9144 | 3250 | 3250 | 14743 | 1200 | 3968.1818 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 3965.2674 | 10777.7326 | 8466 | 6277 | 24910 | 2506.2222 | 497.5667
OPMR total (o) = (g) + (h) + (j) + (k) +(l) + (m) + (n)
Generation Plant Margin (f) = (b) - (a) ALIGNS WITH ELEXON WEBSITE
National Surplus (p) = (f) - (o) ALIGNS WITH BMRS

## 20-Nov-2019
|  | Relevant Information |  |  |  |  | Calculated | OPMR Variables | [5 empty] | Total OPMR adjustors |  | Calculated |  | Wind |  | Negative Reserve at minimum demand
|  | a | b | c | d | e | f | g | h | i | j | k | l | m | n | o | p | q | r | s | t | u
Publish Date | Date | Peak Demand Forecast | Generator Availability | Contracted Availability | Maximum I/C Export | Maximum I/C Import | Generation Availability Margin | Contingency Requirement | STORR Requirement | Operating Reserve provided by I/Cs | Unavailable to Market & Commissioning Plant | Unavailable to National Grid | Available only to National Grid in exceptional circumstances | Reduction from additional availability (Not declared via OC2) | Reduction in Low Frequency Response Reserve Requirement (due to Contracted Response) | OPMR total | National Surplus (SPLD) | Effect of wind on surplus | Generation Availability Margin excluding wind | Minimum Demand Forecast | Total Negative Reserve Requirement for Minimum Demand | High Freq Response Requirement
2019-11-20 | 2019-11-22 | 43320 | 52693 | 3047.9144 | 3250 | 3250 | 9373 | 1200 | 4010.6952 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 4007.7807 | 5365.2193 | 5603 | 3770 | 24350 | 2214.8485 | 503.1667
2019-11-20 | 2019-11-23 | 40150 | 50147 | 3047.9144 | 3250 | 3250 | 9997 | 1200 | 4095.4545 | 181.8182 | 22 | 0 | 0 | -913 | -467.9144 | 3936.5401 | 6060.4599 | 3878 | 6119 | 23150 | 2548.8889 | 515.1667
2019-11-20 | 2019-11-24 | 40790 | 50303 | 3047.9144 | 3250 | 3250 | 9513 | 1200 | 4078.3422 | 181.8182 | 22 | 0 | 0 | -913 | -467.9144 | 3919.4278 | 5593.5722 | 3389 | 6124 | 22170 | 2572.6465 | 524.9667
2019-11-20 | 2019-11-25 | 44310 | 56038 | 3047.9144 | 3250 | 3250 | 11728 | 1200 | 3984.2246 | 181.8182 | 22 | 0 | 0 | -913 | -467.9144 | 3825.3102 | 7902.6898 | 6625 | 5103 | 23200 | 2547.6768 | 514.6667
2019-11-20 | 2019-11-26 | 44430 | 55083 | 3047.9144 | 3250 | 3250 | 10653 | 1200 | 3981.016 | 181.8182 | 22 | 0 | 0 | -913 | -467.9144 | 3822.1016 | 6830.8984 | 5825 | 4828 | 24280 | 2521.4949 | 503.8667
2019-11-20 | 2019-11-27 | 44580 | 55516 | 3047.9144 | 3250 | 3250 | 10936 | 1200 | 3977.0053 | 181.8182 | 22 | 0 | 0 | -913 | -467.9144 | 3818.0909 | 7117.9091 | 5721 | 5215 | 24400 | 2518.5859 | 502.6667
2019-11-20 | 2019-11-28 | 44330 | 56023 | 3047.9144 | 3250 | 3250 | 11693 | 1200 | 3983.6898 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 3980.7754 | 7712.2246 | 5952 | 5741 | 24500 | 2516.1616 | 501.6667
2019-11-20 | 2019-11-29 | 43280 | 55274 | 3047.9144 | 3250 | 3250 | 11994 | 1200 | 4011.7647 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 4008.8503 | 7985.1497 | 5204 | 6790 | 24600 | 2513.7374 | 500.6667
2019-11-20 | 2019-11-30 | 40020 | 55436 | 3047.9144 | 3250 | 3250 | 15416 | 1200 | 4098.9305 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 4096.016 | 11319.984 | 5805 | 9611 | 23400 | 2542.8283 | 512.6667
2019-11-20 | 2019-12-01 | 40540 | 57682 | 3047.9144 | 3250 | 3250 | 17142 | 1200 | 4085.0267 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 4082.1123 | 13059.8877 | 6676 | 10466 | 22430 | 2566.3434 | 522.3667
2019-11-20 | 2019-12-02 | 45030 | 57300 | 3047.9144 | 3250 | 3250 | 12270 | 1200 | 3964.9733 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 3962.0588 | 8307.9412 | 6065 | 6205 | 23700 | 2535.5556 | 509.6667
2019-11-20 | 2019-12-03 | 45220 | 58355 | 3047.9144 | 3250 | 3250 | 13135 | 1200 | 3959.893 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 3956.9786 | 9178.0214 | 6546 | 6589 | 24790 | 2509.1313 | 498.7667
2019-11-20 | 2019-12-04 | 45370 | 59946 | 3047.9144 | 3250 | 3250 | 14576 | 1200 | 3955.8824 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 3952.9679 | 10623.0321 | 8475 | 6101 | 24910 | 2506.2222 | 497.5667
OPMR total (o) = (g) + (h) + (j) + (k) +(l) + (m) + (n)
Generation Plant Margin (f) = (b) - (a) ALIGNS WITH ELEXON WEBSITE
National Surplus (p) = (f) - (o) ALIGNS WITH BMRS

## 19-Nov-2019
|  | Relevant Information |  |  |  |  | Calculated | OPMR Variables | [5 empty] | Total OPMR adjustors |  | Calculated |  | Wind |  | Negative Reserve at minimum demand
|  | a | b | c | d | e | f | g | h | i | j | k | l | m | n | o | p | q | r | s | t | u
Publish Date | Date | Peak Demand Forecast | Generator Availability | Contracted Availability | Maximum I/C Export | Maximum I/C Import | Generation Availability Margin | Contingency Requirement | STORR Requirement | Operating Reserve provided by I/Cs | Unavailable to Market & Commissioning Plant | Unavailable to National Grid | Available only to National Grid in exceptional circumstances | Reduction from additional availability (Not declared via OC2) | Reduction in Low Frequency Response Reserve Requirement (due to Contracted Response) | OPMR total | National Surplus (SPLD) | Effect of wind on surplus | Generation Availability Margin excluding wind | Minimum Demand Forecast | Total Negative Reserve Requirement for Minimum Demand | High Freq Response Requirement
2019-11-19 | 2019-11-21 | 44600 | 55842 | 3047.9144 | 3250 | 3250 | 11242 | 1200 | 3976.4706 | 181.8182 | 22 | 1365.15 | 0 | -913 | -467.9144 | 5182.7061 | 6059.2939 | 7473.85 | 3768.15 | 24350 | 2214.8485 | 503.1667
2019-11-19 | 2019-11-22 | 43110 | 53808 | 3047.9144 | 3250 | 3250 | 10698 | 1200 | 4016.3102 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 4013.3957 | 6684.6043 | 5807 | 4891 | 24350 | 2519.798 | 503.1667
2019-11-19 | 2019-11-23 | 39670 | 51208 | 3047.9144 | 3250 | 3250 | 11538 | 1200 | 4108.2888 | 181.8182 | 22 | 0 | 0 | -913 | -467.9144 | 3949.3743 | 7588.6257 | 4971 | 6567 | 23150 | 2548.8889 | 515.1667
2019-11-19 | 2019-11-24 | 40960 | 50027 | 3047.9144 | 3250 | 3250 | 9067 | 1200 | 4073.7968 | 181.8182 | 22 | 0 | 0 | -913 | -467.9144 | 3914.8824 | 5152.1176 | 2908 | 6159 | 22170 | 2572.6465 | 524.9667
2019-11-19 | 2019-11-25 | 44660 | 53923 | 3047.9144 | 3250 | 3250 | 9263 | 1200 | 3974.8663 | 181.8182 | 22 | 0 | 0 | -913 | -467.9144 | 3815.9519 | 5447.0481 | 4560 | 4703 | 23200 | 2547.6768 | 514.6667
2019-11-19 | 2019-11-26 | 44200 | 55959 | 3047.9144 | 3250 | 3250 | 11759 | 1200 | 3987.1658 | 181.8182 | 22 | 0 | 0 | -913 | -467.9144 | 3828.2513 | 7930.7487 | 6486 | 5273 | 24280 | 2521.4949 | 503.8667
2019-11-19 | 2019-11-27 | 44180 | 55409 | 3047.9144 | 3250 | 3250 | 11229 | 1200 | 3987.7005 | 181.8182 | 22 | 0 | 0 | -913 | -467.9144 | 3828.7861 | 7400.2139 | 6095 | 5134 | 24400 | 2518.5859 | 502.6667
2019-11-19 | 2019-11-28 | 43940 | 55041 | 3047.9144 | 3250 | 3250 | 11101 | 1200 | 3994.1176 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 3991.2032 | 7109.7968 | 5455 | 5646 | 24500 | 2516.1616 | 501.6667
2019-11-19 | 2019-11-29 | 42710 | 54999 | 3047.9144 | 3250 | 3250 | 12289 | 1200 | 4027.0053 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 4024.0909 | 8264.9091 | 5410 | 6879 | 24600 | 2513.7374 | 500.6667
2019-11-19 | 2019-11-30 | 39180 | 54720 | 3047.9144 | 3250 | 3250 | 15540 | 1200 | 4121.3904 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 4118.4759 | 11421.5241 | 5583 | 9957 | 23400 | 2542.8283 | 512.6667
2019-11-19 | 2019-12-01 | 40080 | 56266 | 3047.9144 | 3250 | 3250 | 16186 | 1200 | 4097.3262 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 4094.4118 | 12091.5882 | 5747 | 10439 | 22430 | 2566.3434 | 522.3667
2019-11-19 | 2019-12-02 | 44410 | 57593 | 3047.9144 | 3250 | 3250 | 13183 | 1200 | 3981.5508 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 3978.6364 | 9204.3636 | 6428 | 6755 | 23700 | 2535.5556 | 509.6667
2019-11-19 | 2019-12-03 | 45300 | 57555 | 3047.9144 | 3250 | 3250 | 12255 | 1200 | 3957.754 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 3954.8396 | 8300.1604 | 6428 | 5827 | 24790 | 2509.1313 | 498.7667
OPMR total (o) = (g) + (h) + (j) + (k) +(l) + (m) + (n)
Generation Plant Margin (f) = (b) - (a) ALIGNS WITH ELEXON WEBSITE
National Surplus (p) = (f) - (o) ALIGNS WITH BMRS

## 18-Nov-2019
|  | Relevant Information |  |  |  |  | Calculated | OPMR Variables | [5 empty] | Total OPMR adjustors |  | Calculated |  | Wind |  | Negative Reserve at minimum demand
|  | a | b | c | d | e | f | g | h | i | j | k | l | m | n | o | p | q | r | s | t | u
Publish Date | Date | Peak Demand Forecast | Generator Availability | Contracted Availability | Maximum I/C Export | Maximum I/C Import | Generation Availability Margin | Contingency Requirement | STORR Requirement | Operating Reserve provided by I/Cs | Unavailable to Market & Commissioning Plant | Unavailable to National Grid | Available only to National Grid in exceptional circumstances | Reduction from additional availability (Not declared via OC2) | Reduction in Low Frequency Response Reserve Requirement (due to Contracted Response) | OPMR total | National Surplus (SPLD) | Effect of wind on surplus | Generation Availability Margin excluding wind | Minimum Demand Forecast | Total Negative Reserve Requirement for Minimum Demand | High Freq Response Requirement
2019-11-18 | 2019-11-20 | 45470 | 55418 | 3047.9144 | 3250 | 3250 | 9948 | 1200 | 3953.2086 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 3950.2941 | 5997.7059 | 7547 | 2401 | 24350 | 2214.8485 | 503.1667
2019-11-18 | 2019-11-21 | 44950 | 55326 | 3047.9144 | 3250 | 3250 | 10376 | 1200 | 3967.1123 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 3964.1979 | 6411.8021 | 7743 | 2633 | 24350 | 2519.798 | 503.1667
2019-11-18 | 2019-11-22 | 43430 | 53434 | 3047.9144 | 3250 | 3250 | 10004 | 1200 | 4007.754 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 4004.8396 | 5999.1604 | 5129 | 4875 | 24350 | 2519.798 | 503.1667
2019-11-18 | 2019-11-23 | 40060 | 52708 | 3047.9144 | 3250 | 3250 | 12648 | 1200 | 4097.861 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 4094.9465 | 8553.0535 | 5474 | 7174 | 23150 | 2548.8889 | 515.1667
2019-11-18 | 2019-11-24 | 40080 | 55275 | 3047.9144 | 3250 | 3250 | 15195 | 1200 | 4097.3262 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 4094.4118 | 11100.5882 | 7162 | 8033 | 22170 | 2572.6465 | 524.9667
2019-11-18 | 2019-11-25 | 44690 | 54755 | 3047.9144 | 3250 | 3250 | 10065 | 1200 | 3974.0642 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 3971.1497 | 6093.8503 | 4739 | 5326 | 23200 | 2547.6768 | 514.6667
2019-11-18 | 2019-11-26 | 44590 | 55160 | 3047.9144 | 3250 | 3250 | 10570 | 1200 | 3976.738 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 3973.8235 | 6596.1765 | 5033 | 5537 | 24280 | 2521.4949 | 503.8667
2019-11-18 | 2019-11-27 | 44240 | 56142 | 3047.9144 | 3250 | 3250 | 11902 | 1200 | 3986.0963 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 3983.1818 | 7918.8182 | 6193 | 5709 | 24400 | 2518.5859 | 502.6667
2019-11-18 | 2019-11-28 | 43560 | 57245 | 3047.9144 | 3250 | 3250 | 13685 | 1200 | 4004.2781 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 4001.3636 | 9683.6364 | 7410 | 6275 | 24500 | 2516.1616 | 501.6667
2019-11-18 | 2019-11-29 | 42210 | 56700 | 3047.9144 | 3250 | 3250 | 14490 | 1200 | 4040.3743 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 4037.4599 | 10452.5401 | 6880 | 7610 | 24600 | 2513.7374 | 500.6667
2019-11-18 | 2019-11-30 | 39240 | 55890 | 3047.9144 | 3250 | 3250 | 16650 | 1200 | 4119.7861 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 4116.8717 | 12533.1283 | 6279 | 10371 | 23400 | 2542.8283 | 512.6667
2019-11-18 | 2019-12-01 | 40080 | 57805 | 3047.9144 | 3250 | 3250 | 17725 | 1200 | 4097.3262 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 4094.4118 | 13630.5882 | 6816 | 10909 | 22430 | 2566.3434 | 522.3667
2019-11-18 | 2019-12-02 | 45240 | 59897 | 3047.9144 | 3250 | 3250 | 14657 | 1200 | 3959.3583 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 3956.4439 | 10700.5561 | 8563 | 6094 | 23700 | 2535.5556 | 509.6667
OPMR total (o) = (g) + (h) + (j) + (k) +(l) + (m) + (n)
Generation Plant Margin (f) = (b) - (a) ALIGNS WITH ELEXON WEBSITE
National Surplus (p) = (f) - (o) ALIGNS WITH BMRS

## 15-Nov-2019
|  | Relevant Information |  |  |  |  | Calculated | OPMR Variables | [5 empty] | Total OPMR adjustors |  | Calculated |  | Wind |  | Negative Reserve at minimum demand
|  | a | b | c | d | e | f | g | h | i | j | k | l | m | n | o | p | q | r | s | t | u
Publish Date | Date | Peak Demand Forecast | Generator Availability | Contracted Availability | Maximum I/C Export | Maximum I/C Import | Generation Availability Margin | Contingency Requirement | STORR Requirement | Operating Reserve provided by I/Cs | Unavailable to Market & Commissioning Plant | Unavailable to National Grid | Available only to National Grid in exceptional circumstances | Reduction from additional availability (Not declared via OC2) | Reduction in Low Frequency Response Reserve Requirement (due to Contracted Response) | OPMR total | National Surplus (SPLD) | Effect of wind on surplus | Generation Availability Margin excluding wind | Minimum Demand Forecast | Total Negative Reserve Requirement for Minimum Demand | High Freq Response Requirement
2019-11-15 | 2019-11-17 | 41100 | 49159 | 3047.9144 | 3250 | 3250 | 8059 | 1200 | 4070.0535 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 4067.139 | 3991.861 | 2054 | 6005 | 21420 | 2268.1212 | 532.4667
2019-11-15 | 2019-11-18 | 46170 | 49580 | 3047.9144 | 3250 | 3250 | 3410 | 1200 | 3934.492 | 181.8182 | 156 | 0 | 0 | -913 | -467.9144 | 3909.5775 | -499.5775 | 1756 | 1654 | 23050 | 2551.3131 | 516.1667
2019-11-15 | 2019-11-19 | 44830 | 54783 | 3047.9144 | 3250 | 3250 | 9953 | 1200 | 3970.3209 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 3967.4064 | 5985.5936 | 6679 | 3274 | 24230 | 2522.7071 | 504.3667
2019-11-15 | 2019-11-20 | 44640 | 56652 | 3047.9144 | 3250 | 3250 | 12012 | 1200 | 3975.4011 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 3972.4866 | 8039.5134 | 8541 | 3471 | 24350 | 2519.798 | 503.1667
2019-11-15 | 2019-11-21 | 43540 | 58333 | 3047.9144 | 3250 | 3250 | 14793 | 1200 | 4004.8128 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 4001.8984 | 10791.1016 | 9625 | 5168 | 24350 | 2519.798 | 503.1667
2019-11-15 | 2019-11-22 | 42930 | 55084 | 3047.9144 | 3250 | 3250 | 12154 | 1200 | 4021.123 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 4018.2086 | 8135.7914 | 6074 | 6080 | 24350 | 2519.798 | 503.1667
2019-11-15 | 2019-11-23 | 39740 | 53356 | 3047.9144 | 3250 | 3250 | 13616 | 1200 | 4106.4171 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 4103.5027 | 9512.4973 | 5125 | 8491 | 23150 | 2548.8889 | 515.1667
2019-11-15 | 2019-11-24 | 40660 | 54080 | 3047.9144 | 3250 | 3250 | 13420 | 1200 | 4081.8182 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 4078.9037 | 9341.0963 | 4974 | 8446 | 22170 | 2572.6465 | 524.9667
2019-11-15 | 2019-11-25 | 44980 | 55370 | 3047.9144 | 3250 | 3250 | 10390 | 1200 | 3966.3102 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 3963.3957 | 6426.6043 | 3951 | 6439 | 23200 | 2547.6768 | 514.6667
2019-11-15 | 2019-11-26 | 44520 | 55369 | 3047.9144 | 3250 | 3250 | 10849 | 1200 | 3978.6096 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 3975.6952 | 6873.3048 | 3855 | 6994 | 24280 | 2521.4949 | 503.8667
2019-11-15 | 2019-11-27 | 44640 | 55239 | 3047.9144 | 3250 | 3250 | 10599 | 1200 | 3975.4011 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 3972.4866 | 6626.5134 | 3904 | 6695 | 24400 | 2518.5859 | 502.6667
2019-11-15 | 2019-11-28 | 44410 | 56081 | 3047.9144 | 3250 | 3250 | 11671 | 1200 | 3981.5508 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 3978.6364 | 7692.3636 | 4868 | 6803 | 24500 | 2516.1616 | 501.6667
2019-11-15 | 2019-11-29 | 43240 | 58522 | 3047.9144 | 3250 | 3250 | 15282 | 1200 | 4012.8342 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 4009.9198 | 11272.0802 | 6970 | 8312 | 24600 | 2513.7374 | 500.6667
OPMR total (o) = (g) + (h) + (j) + (k) +(l) + (m) + (n)
Generation Plant Margin (f) = (b) - (a) ALIGNS WITH ELEXON WEBSITE
National Surplus (p) = (f) - (o) ALIGNS WITH BMRS

## 14-Nov-2019
|  | Relevant Information |  |  |  |  | Calculated | OPMR Variables | [5 empty] | Total OPMR adjustors |  | Calculated |  | Wind |  | Negative Reserve at minimum demand
|  | a | b | c | d | e | f | g | h | i | j | k | l | m | n | o | p | q | r | s | t | u
Publish Date | Date | Peak Demand Forecast | Generator Availability | Contracted Availability | Maximum I/C Export | Maximum I/C Import | Generation Availability Margin | Contingency Requirement | STORR Requirement | Operating Reserve provided by I/Cs | Unavailable to Market & Commissioning Plant | Unavailable to National Grid | Available only to National Grid in exceptional circumstances | Reduction from additional availability (Not declared via OC2) | Reduction in Low Frequency Response Reserve Requirement (due to Contracted Response) | OPMR total | National Surplus (SPLD) | Effect of wind on surplus | Generation Availability Margin excluding wind | Minimum Demand Forecast | Total Negative Reserve Requirement for Minimum Demand | High Freq Response Requirement
2019-11-14 | 2019-11-16 | 40900 | 47198 | 3047.9144 | 3250 | 3250 | 6298 | 1200 | 4075.4011 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 4072.4866 | 2225.5134 | 1334 | 4964 | 22400 | 2250.303 | 522.6667
2019-11-14 | 2019-11-17 | 41400 | 49229 | 3047.9144 | 3250 | 3250 | 7829 | 1200 | 4062.0321 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 4059.1176 | 3769.8824 | 2431 | 5398 | 21420 | 2590.8283 | 532.4667
2019-11-14 | 2019-11-18 | 46300 | 49928 | 3047.9144 | 3250 | 3250 | 3628 | 1200 | 3931.016 | 181.8182 | 156 | 0 | 0 | -913 | -467.9144 | 3906.1016 | -278.1016 | 2051 | 1577 | 23050 | 2551.3131 | 516.1667
2019-11-14 | 2019-11-19 | 45310 | 54800 | 3047.9144 | 3250 | 3250 | 9490 | 1200 | 3957.4866 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 3954.5722 | 5535.4278 | 6810 | 2680 | 24230 | 2522.7071 | 504.3667
2019-11-14 | 2019-11-20 | 45010 | 55716 | 3047.9144 | 3250 | 3250 | 10706 | 1200 | 3965.508 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 3962.5936 | 6743.4064 | 7540 | 3166 | 24350 | 2519.798 | 503.1667
2019-11-14 | 2019-11-21 | 44530 | 56759 | 3047.9144 | 3250 | 3250 | 12229 | 1200 | 3978.3422 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 3975.4278 | 8253.5722 | 7490 | 4739 | 24350 | 2519.798 | 503.1667
2019-11-14 | 2019-11-22 | 42920 | 56704 | 3047.9144 | 3250 | 3250 | 13784 | 1200 | 4021.3904 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 4018.4759 | 9765.5241 | 7654 | 6130 | 24350 | 2519.798 | 503.1667
2019-11-14 | 2019-11-23 | 39820 | 55050 | 3047.9144 | 3250 | 3250 | 15230 | 1200 | 4104.2781 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 4101.3636 | 11128.6364 | 6411 | 8819 | 23150 | 2548.8889 | 515.1667
2019-11-14 | 2019-11-24 | 40620 | 55409 | 3047.9144 | 3250 | 3250 | 14789 | 1200 | 4082.8877 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 4079.9733 | 10709.0267 | 5423 | 9366 | 22170 | 2572.6465 | 524.9667
2019-11-14 | 2019-11-25 | 44410 | 56558 | 3047.9144 | 3250 | 3250 | 12148 | 1200 | 3981.5508 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 3978.6364 | 8169.3636 | 5184 | 6964 | 23200 | 2547.6768 | 514.6667
2019-11-14 | 2019-11-26 | 44630 | 56292 | 3047.9144 | 3250 | 3250 | 11662 | 1200 | 3975.6684 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 3972.754 | 7689.246 | 4812 | 6850 | 24280 | 2521.4949 | 503.8667
2019-11-14 | 2019-11-27 | 44810 | 56039 | 3047.9144 | 3250 | 3250 | 11229 | 1200 | 3970.8556 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 3967.9412 | 7261.0588 | 4736 | 6493 | 24400 | 2518.5859 | 502.6667
2019-11-14 | 2019-11-28 | 44540 | 58194 | 3047.9144 | 3250 | 3250 | 13654 | 1200 | 3978.0749 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 3975.1604 | 9678.8396 | 6972 | 6682 | 24500 | 2516.1616 | 501.6667
OPMR total (o) = (g) + (h) + (j) + (k) +(l) + (m) + (n)
Generation Plant Margin (f) = (b) - (a) ALIGNS WITH ELEXON WEBSITE
National Surplus (p) = (f) - (o) ALIGNS WITH BMRS

## 13-Nov-2019
|  | Relevant Information |  |  |  |  | Calculated | OPMR Variables | [5 empty] | Total OPMR adjustors |  | Calculated |  | Wind |  | Negative Reserve at minimum demand
|  | a | b | c | d | e | f | g | h | i | j | k | l | m | n | o | p | q | r | s | t | u
Publish Date | Date | Peak Demand Forecast | Generator Availability | Contracted Availability | Maximum I/C Export | Maximum I/C Import | Generation Availability Margin | Contingency Requirement | STORR Requirement | Operating Reserve provided by I/Cs | Unavailable to Market & Commissioning Plant | Unavailable to National Grid | Available only to National Grid in exceptional circumstances | Reduction from additional availability (Not declared via OC2) | Reduction in Low Frequency Response Reserve Requirement (due to Contracted Response) | OPMR total | National Surplus (SPLD) | Effect of wind on surplus | Generation Availability Margin excluding wind | Minimum Demand Forecast | Total Negative Reserve Requirement for Minimum Demand | High Freq Response Requirement
2019-11-13 | 2019-11-15 | 43030 | 53429 | 3047.9144 | 3250 | 3250 | 10399 | 1200 | 4018.4492 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 4015.5348 | 6383.4652 | 6834 | 3565 | 23610 | 2228.303 | 510.5667
2019-11-13 | 2019-11-16 | 41020 | 48980 | 3047.9144 | 3250 | 3250 | 7960 | 1200 | 4072.1925 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 4069.2781 | 3890.7219 | 2994 | 4966 | 22400 | 2567.0707 | 522.6667
2019-11-13 | 2019-11-17 | 41790 | 49080 | 3047.9144 | 3250 | 3250 | 7290 | 1200 | 4051.6043 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 4048.6898 | 3241.3102 | 2247 | 5043 | 21420 | 2590.8283 | 532.4667
2019-11-13 | 2019-11-18 | 46570 | 52207 | 3047.9144 | 3250 | 3250 | 5637 | 1200 | 3923.7968 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 3920.8824 | 1716.1176 | 2890 | 2747 | 23050 | 2551.3131 | 516.1667
2019-11-13 | 2019-11-19 | 45830 | 55130 | 3047.9144 | 3250 | 3250 | 9300 | 1200 | 3943.5829 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 3940.6684 | 5359.3316 | 5857 | 3443 | 24230 | 2522.7071 | 504.3667
2019-11-13 | 2019-11-20 | 46180 | 53610 | 3047.9144 | 3250 | 3250 | 7430 | 1200 | 3934.2246 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 3931.3102 | 3498.6898 | 4343 | 3087 | 24350 | 2519.798 | 503.1667
2019-11-13 | 2019-11-21 | 45220 | 56610 | 3047.9144 | 3250 | 3250 | 11390 | 1200 | 3959.893 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 3956.9786 | 7433.0214 | 6343 | 5047 | 24350 | 2519.798 | 503.1667
2019-11-13 | 2019-11-22 | 43650 | 55528 | 3047.9144 | 3250 | 3250 | 11878 | 1200 | 4001.8717 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 3998.9572 | 7879.0428 | 6266 | 5612 | 24350 | 2519.798 | 503.1667
2019-11-13 | 2019-11-23 | 40090 | 55405 | 3047.9144 | 3250 | 3250 | 15315 | 1200 | 4097.0588 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 4094.1444 | 11220.8556 | 6629 | 8686 | 23150 | 2548.8889 | 515.1667
2019-11-13 | 2019-11-24 | 40450 | 55718 | 3047.9144 | 3250 | 3250 | 15268 | 1200 | 4087.4332 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 4084.5187 | 11183.4813 | 5685 | 9583 | 22170 | 2572.6465 | 524.9667
2019-11-13 | 2019-11-25 | 44640 | 56170 | 3047.9144 | 3250 | 3250 | 11530 | 1200 | 3975.4011 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 3972.4866 | 7557.5134 | 4790 | 6740 | 23200 | 2547.6768 | 514.6667
2019-11-13 | 2019-11-26 | 44740 | 55975 | 3047.9144 | 3250 | 3250 | 11235 | 1200 | 3972.7273 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 3969.8128 | 7265.1872 | 4491 | 6744 | 24280 | 2521.4949 | 503.8667
2019-11-13 | 2019-11-27 | 44830 | 58173 | 3047.9144 | 3250 | 3250 | 13343 | 1200 | 3970.3209 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 3967.4064 | 9375.5936 | 6954 | 6389 | 24400 | 2518.5859 | 502.6667
OPMR total (o) = (g) + (h) + (j) + (k) +(l) + (m) + (n)
Generation Plant Margin (f) = (b) - (a) ALIGNS WITH ELEXON WEBSITE
National Surplus (p) = (f) - (o) ALIGNS WITH BMRS

## 12-Nov-2019
|  | Relevant Information |  |  |  |  | Calculated | OPMR Variables | [5 empty] | Total OPMR adjustors |  | Calculated |  | Wind |  | Negative Reserve at minimum demand
|  | a | b | c | d | e | f | g | h | i | j | k | l | m | n | o | p | q | r | s | t | u
Publish Date | Date | Peak Demand Forecast | Generator Availability | Contracted Availability | Maximum I/C Export | Maximum I/C Import | Generation Availability Margin | Contingency Requirement | STORR Requirement | Operating Reserve provided by I/Cs | Unavailable to Market & Commissioning Plant | Unavailable to National Grid | Available only to National Grid in exceptional circumstances | Reduction from additional availability (Not declared via OC2) | Reduction in Low Frequency Response Reserve Requirement (due to Contracted Response) | OPMR total | National Surplus (SPLD) | Effect of wind on surplus | Generation Availability Margin excluding wind | Minimum Demand Forecast | Total Negative Reserve Requirement for Minimum Demand | High Freq Response Requirement
2019-11-12 | 2019-11-14 | 44240 | 54741 | 3047.9144 | 3250 | 3250 | 10501 | 1200 | 3986.0963 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 3983.1818 | 6517.8182 | 7482 | 3019 | 23610 | 2228.303 | 510.5667
2019-11-12 | 2019-11-15 | 42990 | 54331 | 3047.9144 | 3250 | 3250 | 11341 | 1200 | 4019.5187 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 4016.6043 | 7324.3957 | 7369 | 3972 | 23610 | 2537.7374 | 510.5667
2019-11-12 | 2019-11-16 | 41280 | 48405 | 3047.9144 | 3250 | 3250 | 7125 | 1200 | 4065.2406 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 4062.3262 | 3062.6738 | 2361 | 4764 | 22400 | 2567.0707 | 522.6667
2019-11-12 | 2019-11-17 | 42570 | 48697 | 3047.9144 | 3250 | 3250 | 6127 | 1200 | 4030.7487 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 4027.8342 | 2099.1658 | 1741 | 4386 | 21420 | 2590.8283 | 532.4667
2019-11-12 | 2019-11-18 | 46720 | 52109 | 3047.9144 | 3250 | 3250 | 5389 | 1200 | 3919.7861 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 3916.8717 | 1472.1283 | 2685 | 2704 | 23050 | 2551.3131 | 516.1667
2019-11-12 | 2019-11-19 | 46660 | 53007 | 3047.9144 | 3250 | 3250 | 6347 | 1200 | 3921.3904 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 3918.4759 | 2428.5241 | 3998 | 2349 | 24230 | 2522.7071 | 504.3667
2019-11-12 | 2019-11-20 | 46580 | 53807 | 3047.9144 | 3250 | 3250 | 7227 | 1200 | 3923.5294 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 3920.615 | 3306.385 | 4474 | 2753 | 24350 | 2519.798 | 503.1667
2019-11-12 | 2019-11-21 | 45730 | 55944 | 3047.9144 | 3250 | 3250 | 10214 | 1200 | 3946.2567 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 3943.3422 | 6270.6578 | 5594 | 4620 | 24350 | 2519.798 | 503.1667
2019-11-12 | 2019-11-22 | 44130 | 55783 | 3047.9144 | 3250 | 3250 | 11653 | 1200 | 3989.0374 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 3986.123 | 7666.877 | 5692 | 5961 | 24350 | 2519.798 | 503.1667
2019-11-12 | 2019-11-23 | 40380 | 55349 | 3047.9144 | 3250 | 3250 | 14969 | 1200 | 4089.3048 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 4086.3904 | 10882.6096 | 6074 | 8895 | 23150 | 2548.8889 | 515.1667
2019-11-12 | 2019-11-24 | 41090 | 55678 | 3047.9144 | 3250 | 3250 | 14588 | 1200 | 4070.3209 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 4067.4064 | 10520.5936 | 5550 | 9038 | 22170 | 2572.6465 | 524.9667
2019-11-12 | 2019-11-25 | 45160 | 57399 | 3047.9144 | 3250 | 3250 | 12239 | 1200 | 3961.4973 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 3958.5829 | 8280.4171 | 5924 | 6315 | 23200 | 2547.6768 | 514.6667
2019-11-12 | 2019-11-26 | 44940 | 58547 | 3047.9144 | 3250 | 3250 | 13607 | 1200 | 3967.3797 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 3964.4652 | 9642.5348 | 7137 | 6470 | 24280 | 2521.4949 | 503.8667
OPMR total (o) = (g) + (h) + (j) + (k) +(l) + (m) + (n)
Generation Plant Margin (f) = (b) - (a) ALIGNS WITH ELEXON WEBSITE
National Surplus (p) = (f) - (o) ALIGNS WITH BMRS

## 11-Nov-2019
|  | Relevant Information |  |  |  |  | Calculated | OPMR Variables | [5 empty] | Total OPMR adjustors |  | Calculated |  | Wind |  | Negative Reserve at minimum demand
|  | a | b | c | d | e | f | g | h | i | j | k | l | m | n | o | p | q | r | s | t | u
Publish Date | Date | Peak Demand Forecast | Generator Availability | Contracted Availability | Maximum I/C Export | Maximum I/C Import | Generation Availability Margin | Contingency Requirement | STORR Requirement | Operating Reserve provided by I/Cs | Unavailable to Market & Commissioning Plant | Unavailable to National Grid | Available only to National Grid in exceptional circumstances | Reduction from additional availability (Not declared via OC2) | Reduction in Low Frequency Response Reserve Requirement (due to Contracted Response) | OPMR total | National Surplus (SPLD) | Effect of wind on surplus | Generation Availability Margin excluding wind | Minimum Demand Forecast | Total Negative Reserve Requirement for Minimum Demand | High Freq Response Requirement
2019-11-11 | 2019-11-13 | 45220 | 50491 | 3047.9144 | 3250 | 3250 | 5271 | 1200 | 3959.893 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 3956.9786 | 1314.0214 | 3597 | 1674 | 23610 | 2228.303 | 510.5667
2019-11-11 | 2019-11-14 | 44550 | 54521 | 3047.9144 | 3250 | 3250 | 9971 | 1200 | 3977.8075 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 3974.893 | 5996.107 | 6992 | 2979 | 23610 | 2537.7374 | 510.5667
2019-11-11 | 2019-11-15 | 43400 | 53517 | 3047.9144 | 3250 | 3250 | 10117 | 1200 | 4008.5561 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 4005.6417 | 6111.3583 | 6264 | 3853 | 23610 | 2537.7374 | 510.5667
2019-11-11 | 2019-11-16 | 41460 | 48952 | 3047.9144 | 3250 | 3250 | 7492 | 1200 | 4060.4278 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 4057.5134 | 3434.4866 | 2526 | 4966 | 22400 | 2567.0707 | 522.6667
2019-11-11 | 2019-11-17 | 42200 | 49377 | 3047.9144 | 3250 | 3250 | 7177 | 1200 | 4040.6417 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 4037.7273 | 3139.2727 | 2179 | 4998 | 21420 | 2590.8283 | 532.4667
2019-11-11 | 2019-11-18 | 46990 | 52094 | 3047.9144 | 3250 | 3250 | 5104 | 1200 | 3912.5668 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 3909.6524 | 1194.3476 | 2921 | 2183 | 23050 | 2551.3131 | 516.1667
2019-11-11 | 2019-11-19 | 46820 | 53389 | 3047.9144 | 3250 | 3250 | 6569 | 1200 | 3917.1123 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 3914.1979 | 2654.8021 | 4224 | 2345 | 24230 | 2522.7071 | 504.3667
2019-11-11 | 2019-11-20 | 46530 | 54238 | 3047.9144 | 3250 | 3250 | 7708 | 1200 | 3924.8663 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 3921.9519 | 3786.0481 | 4754 | 2954 | 24350 | 2519.798 | 503.1667
2019-11-11 | 2019-11-21 | 45610 | 56215 | 3047.9144 | 3250 | 3250 | 10605 | 1200 | 3949.4652 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 3946.5508 | 6658.4492 | 5712 | 4893 | 24350 | 2519.798 | 503.1667
2019-11-11 | 2019-11-22 | 43740 | 56720 | 3047.9144 | 3250 | 3250 | 12980 | 1200 | 3999.4652 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 3996.5508 | 8983.4492 | 6483 | 6497 | 24350 | 2519.798 | 503.1667
2019-11-11 | 2019-11-23 | 40370 | 55640 | 3047.9144 | 3250 | 3250 | 15270 | 1200 | 4089.5722 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 4086.6578 | 11183.3422 | 6209 | 9061 | 23150 | 2548.8889 | 515.1667
2019-11-11 | 2019-11-24 | 41080 | 55883 | 3047.9144 | 3250 | 3250 | 14803 | 1200 | 4070.5882 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 4067.6738 | 10735.3262 | 5605 | 9198 | 22170 | 2572.6465 | 524.9667
2019-11-11 | 2019-11-25 | 44890 | 58517 | 3047.9144 | 3250 | 3250 | 13627 | 1200 | 3968.7166 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 3965.8021 | 9661.1979 | 7104 | 6523 | 23200 | 2547.6768 | 514.6667
OPMR total (o) = (g) + (h) + (j) + (k) +(l) + (m) + (n)
Generation Plant Margin (f) = (b) - (a) ALIGNS WITH ELEXON WEBSITE
National Surplus (p) = (f) - (o) ALIGNS WITH BMRS

## 08-Nov-2019
|  | Relevant Information |  |  |  |  | Calculated | OPMR Variables | [5 empty] | Total OPMR adjustors |  | Calculated |  | Wind |  | Negative Reserve at minimum demand
|  | a | b | c | d | e | f | g | h | i | j | k | l | m | n | o | p | q | r | s | t | u
Publish Date | Date | Peak Demand Forecast | Generator Availability | Contracted Availability | Maximum I/C Export | Maximum I/C Import | Generation Availability Margin | Contingency Requirement | STORR Requirement | Operating Reserve provided by I/Cs | Unavailable to Market & Commissioning Plant | Unavailable to National Grid | Available only to National Grid in exceptional circumstances | Reduction from additional availability (Not declared via OC2) | Reduction in Low Frequency Response Reserve Requirement (due to Contracted Response) | OPMR total | National Surplus (SPLD) | Effect of wind on surplus | Generation Availability Margin excluding wind | Minimum Demand Forecast | Total Negative Reserve Requirement for Minimum Demand | High Freq Response Requirement
2019-11-08 | 2019-11-10 | 41630 | 50230 | 3047.9144 | 3250 | 3250 | 8600 | 1200 | 4055.8824 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 4052.9679 | 4547.0321 | 2487 | 6113 | 20970 | 2276.303 | 536.9667
2019-11-08 | 2019-11-11 | 44000 | 57755 | 3047.9144 | 3250 | 3250 | 13755 | 1200 | 3992.5134 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 3989.5989 | 9765.4011 | 9945 | 3810 | 22300 | 2569.4949 | 523.6667
2019-11-08 | 2019-11-12 | 44260 | 56679 | 3047.9144 | 3250 | 3250 | 12419 | 1200 | 3985.5615 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 3982.6471 | 8436.3529 | 8819 | 3600 | 23490 | 2540.6465 | 511.7667
2019-11-08 | 2019-11-13 | 44900 | 53447 | 3047.9144 | 3250 | 3250 | 8547 | 1200 | 3968.4492 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 3965.5348 | 4581.4652 | 5710 | 2837 | 23610 | 2537.7374 | 510.5667
2019-11-08 | 2019-11-14 | 44970 | 53511 | 3047.9144 | 3250 | 3250 | 8541 | 1200 | 3966.5775 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 3963.6631 | 4577.3369 | 5377 | 3164 | 23610 | 2537.7374 | 510.5667
2019-11-08 | 2019-11-15 | 44040 | 54064 | 3047.9144 | 3250 | 3250 | 10024 | 1200 | 3991.4439 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 3988.5294 | 6035.4706 | 6401 | 3623 | 23610 | 2537.7374 | 510.5667
2019-11-08 | 2019-11-16 | 41040 | 51195 | 3047.9144 | 3250 | 3250 | 10155 | 1200 | 4071.6578 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 4068.7433 | 6086.2567 | 4466 | 5689 | 22400 | 2567.0707 | 522.6667
2019-11-08 | 2019-11-17 | 42080 | 51105 | 3047.9144 | 3250 | 3250 | 9025 | 1200 | 4043.8503 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 4040.9358 | 4984.0642 | 3596 | 5429 | 21420 | 2590.8283 | 532.4667
2019-11-08 | 2019-11-18 | 46020 | 54615 | 3047.9144 | 3250 | 3250 | 8595 | 1200 | 3938.5027 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 3935.5882 | 4659.4118 | 5118 | 3477 | 23050 | 2551.3131 | 516.1667
2019-11-08 | 2019-11-19 | 45490 | 54778 | 3047.9144 | 3250 | 3250 | 9288 | 1200 | 3952.6738 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 3949.7594 | 5338.2406 | 5298 | 3990 | 24230 | 2522.7071 | 504.3667
2019-11-08 | 2019-11-20 | 45480 | 55117 | 3047.9144 | 3250 | 3250 | 9637 | 1200 | 3952.9412 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 3950.0267 | 5686.9733 | 5318 | 4319 | 24350 | 2519.798 | 503.1667
2019-11-08 | 2019-11-21 | 45190 | 55544 | 3047.9144 | 3250 | 3250 | 10354 | 1200 | 3960.6952 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 3957.7807 | 6396.2193 | 4733 | 5621 | 24350 | 2519.798 | 503.1667
2019-11-08 | 2019-11-22 | 42880 | 57609 | 3047.9144 | 3250 | 3250 | 14729 | 1200 | 4022.4599 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 4019.5455 | 10709.4545 | 6904 | 7825 | 24350 | 2519.798 | 503.1667
OPMR total (o) = (g) + (h) + (j) + (k) +(l) + (m) + (n)
Generation Plant Margin (f) = (b) - (a) ALIGNS WITH ELEXON WEBSITE
National Surplus (p) = (f) - (o) ALIGNS WITH BMRS

## 07-Nov-2019
|  | Relevant Information |  |  |  |  | Calculated | OPMR Variables | [5 empty] | Total OPMR adjustors |  | Calculated |  | Wind |  | Negative Reserve at minimum demand
|  | a | b | c | d | e | f | g | h | i | j | k | l | m | n | o | p | q | r | s | t | u
Publish Date | Date | Peak Demand Forecast | Generator Availability | Contracted Availability | Maximum I/C Export | Maximum I/C Import | Generation Availability Margin | Contingency Requirement | STORR Requirement | Operating Reserve provided by I/Cs | Unavailable to Market & Commissioning Plant | Unavailable to National Grid | Available only to National Grid in exceptional circumstances | Reduction from additional availability (Not declared via OC2) | Reduction in Low Frequency Response Reserve Requirement (due to Contracted Response) | OPMR total | National Surplus (SPLD) | Effect of wind on surplus | Generation Availability Margin excluding wind | Minimum Demand Forecast | Total Negative Reserve Requirement for Minimum Demand | High Freq Response Requirement
2019-11-07 | 2019-11-09 | 40010 | 51466 | 3047.9144 | 3250 | 3250 | 11456 | 1200 | 4099.1979 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 4096.2834 | 7359.7166 | 3660 | 7796 | 21950 | 2258.4848 | 527.1667
2019-11-07 | 2019-11-10 | 41360 | 50185 | 3047.9144 | 3250 | 3250 | 8825 | 1200 | 4063.1016 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 4060.1872 | 4764.8128 | 1962 | 6863 | 20970 | 2601.7374 | 536.9667
2019-11-07 | 2019-11-11 | 44230 | 56696 | 3047.9144 | 3250 | 3250 | 12466 | 1200 | 3986.3636 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 3983.4492 | 8482.5508 | 8319 | 4147 | 22300 | 2569.4949 | 523.6667
2019-11-07 | 2019-11-12 | 44610 | 56983 | 3047.9144 | 3250 | 3250 | 12373 | 1200 | 3976.2032 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 3973.2888 | 8399.7112 | 8538 | 3835 | 23490 | 2540.6465 | 511.7667
2019-11-07 | 2019-11-13 | 44800 | 55284 | 3047.9144 | 3250 | 3250 | 10484 | 1200 | 3971.123 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 3968.2086 | 6515.7914 | 7153 | 3331 | 23610 | 2537.7374 | 510.5667
2019-11-07 | 2019-11-14 | 45270 | 54741 | 3047.9144 | 3250 | 3250 | 9471 | 1200 | 3958.5561 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 3955.6417 | 5515.3583 | 6375 | 3096 | 23610 | 2537.7374 | 510.5667
2019-11-07 | 2019-11-15 | 44090 | 53281 | 3047.9144 | 3250 | 3250 | 9191 | 1200 | 3990.107 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 3987.1925 | 5203.8075 | 5770 | 3421 | 23610 | 2537.7374 | 510.5667
2019-11-07 | 2019-11-16 | 40980 | 53015 | 3047.9144 | 3250 | 3250 | 12035 | 1200 | 4073.262 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 4070.3476 | 7964.6524 | 6263 | 5772 | 22400 | 2567.0707 | 522.6667
2019-11-07 | 2019-11-17 | 41900 | 52198 | 3047.9144 | 3250 | 3250 | 10298 | 1200 | 4048.6631 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 4045.7487 | 6252.2513 | 4698 | 5600 | 21420 | 2590.8283 | 532.4667
2019-11-07 | 2019-11-18 | 45520 | 55234 | 3047.9144 | 3250 | 3250 | 9714 | 1200 | 3951.8717 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 3948.9572 | 5765.0428 | 5768 | 3946 | 23050 | 2551.3131 | 516.1667
2019-11-07 | 2019-11-19 | 45550 | 55068 | 3047.9144 | 3250 | 3250 | 9518 | 1200 | 3951.0695 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 3948.1551 | 5569.8449 | 5609 | 3909 | 24230 | 2522.7071 | 504.3667
2019-11-07 | 2019-11-20 | 45600 | 55680 | 3047.9144 | 3250 | 3250 | 10080 | 1200 | 3949.7326 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 3946.8182 | 6133.1818 | 5900 | 4180 | 24350 | 2519.798 | 503.1667
2019-11-07 | 2019-11-21 | 44160 | 57906 | 3047.9144 | 3250 | 3250 | 13746 | 1200 | 3988.2353 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 3985.3209 | 9760.6791 | 7200 | 6546 | 24350 | 2519.798 | 503.1667
OPMR total (o) = (g) + (h) + (j) + (k) +(l) + (m) + (n)
Generation Plant Margin (f) = (b) - (a) ALIGNS WITH ELEXON WEBSITE
National Surplus (p) = (f) - (o) ALIGNS WITH BMRS

## 06-Nov-2019
|  | Relevant Information |  |  |  |  | Calculated | OPMR Variables | [5 empty] | Total OPMR adjustors |  | Calculated |  | Wind |  | Negative Reserve at minimum demand
|  | a | b | c | d | e | f | g | h | i | j | k | l | m | n | o | p | q | r | s | t | u
Publish Date | Date | Peak Demand Forecast | Generator Availability | Contracted Availability | Maximum I/C Export | Maximum I/C Import | Generation Availability Margin | Contingency Requirement | STORR Requirement | Operating Reserve provided by I/Cs | Unavailable to Market & Commissioning Plant | Unavailable to National Grid | Available only to National Grid in exceptional circumstances | Reduction from additional availability (Not declared via OC2) | Reduction in Low Frequency Response Reserve Requirement (due to Contracted Response) | OPMR total | National Surplus (SPLD) | Effect of wind on surplus | Generation Availability Margin excluding wind | Minimum Demand Forecast | Total Negative Reserve Requirement for Minimum Demand | High Freq Response Requirement
2019-11-06 | 2019-11-08 | 43430 | 50692 | 3047.9144 | 3250 | 3250 | 7262 | 1200 | 4007.754 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 4004.8396 | 3257.1604 | 2759 | 4503 | 23060 | 2238.303 | 516.0667
2019-11-06 | 2019-11-09 | 40110 | 51262 | 3047.9144 | 3250 | 3250 | 11152 | 1200 | 4096.5241 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 4093.6096 | 7058.3904 | 4096 | 7056 | 21950 | 2577.9798 | 527.1667
2019-11-06 | 2019-11-10 | 41170 | 50213 | 3047.9144 | 3250 | 3250 | 9043 | 1200 | 4068.1818 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 4065.2674 | 4977.7326 | 2322 | 6721 | 20970 | 2601.7374 | 536.9667
2019-11-06 | 2019-11-11 | 44660 | 57493 | 3047.9144 | 3250 | 3250 | 12833 | 1200 | 3974.8663 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 3971.9519 | 8861.0481 | 8342 | 4491 | 22300 | 2569.4949 | 523.6667
2019-11-06 | 2019-11-12 | 45070 | 55744 | 3047.9144 | 3250 | 3250 | 10674 | 1200 | 3963.9037 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 3960.9893 | 6713.0107 | 6574 | 4100 | 23490 | 2540.6465 | 511.7667
2019-11-06 | 2019-11-13 | 45550 | 55871 | 3047.9144 | 3250 | 3250 | 10321 | 1200 | 3951.0695 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 3948.1551 | 6372.8449 | 6765 | 3556 | 23610 | 2537.7374 | 510.5667
2019-11-06 | 2019-11-14 | 45840 | 55225 | 3047.9144 | 3250 | 3250 | 9385 | 1200 | 3943.3155 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 3940.4011 | 5444.5989 | 6084 | 3301 | 23610 | 2537.7374 | 510.5667
2019-11-06 | 2019-11-15 | 44440 | 53949 | 3047.9144 | 3250 | 3250 | 9509 | 1200 | 3980.7487 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 3977.8342 | 5531.1658 | 5671 | 3838 | 23610 | 2537.7374 | 510.5667
2019-11-06 | 2019-11-16 | 41110 | 52757 | 3047.9144 | 3250 | 3250 | 11647 | 1200 | 4069.7861 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 4066.8717 | 7580.1283 | 4734 | 6913 | 22400 | 2567.0707 | 522.6667
2019-11-06 | 2019-11-17 | 41090 | 53881 | 3047.9144 | 3250 | 3250 | 12791 | 1200 | 4070.3209 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 4067.4064 | 8723.5936 | 5111 | 7680 | 21420 | 2590.8283 | 532.4667
2019-11-06 | 2019-11-18 | 45310 | 54710 | 3047.9144 | 3250 | 3250 | 9400 | 1200 | 3957.4866 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 3954.5722 | 5445.4278 | 4461 | 4939 | 23050 | 2551.3131 | 516.1667
2019-11-06 | 2019-11-19 | 45230 | 56056 | 3047.9144 | 3250 | 3250 | 10826 | 1200 | 3959.6257 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 3956.7112 | 6869.2888 | 5864 | 4962 | 24230 | 2522.7071 | 504.3667
2019-11-06 | 2019-11-20 | 44230 | 57629 | 3047.9144 | 3250 | 3250 | 13399 | 1200 | 3986.3636 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 3983.4492 | 9415.5508 | 7173 | 6226 | 24350 | 2519.798 | 503.1667
OPMR total (o) = (g) + (h) + (j) + (k) +(l) + (m) + (n)
Generation Plant Margin (f) = (b) - (a) ALIGNS WITH ELEXON WEBSITE
National Surplus (p) = (f) - (o) ALIGNS WITH BMRS

## 05-Nov-2019
|  | Relevant Information |  |  |  |  | Calculated | OPMR Variables | [5 empty] | Total OPMR adjustors |  | Calculated |  | Wind |  | Negative Reserve at minimum demand
|  | a | b | c | d | e | f | g | h | i | j | k | l | m | n | o | p | q | r | s | t | u
Publish Date | Date | Peak Demand Forecast | Generator Availability | Contracted Availability | Maximum I/C Export | Maximum I/C Import | Generation Availability Margin | Contingency Requirement | STORR Requirement | Operating Reserve provided by I/Cs | Unavailable to Market & Commissioning Plant | Unavailable to National Grid | Available only to National Grid in exceptional circumstances | Reduction from additional availability (Not declared via OC2) | Reduction in Low Frequency Response Reserve Requirement (due to Contracted Response) | OPMR total | National Surplus (SPLD) | Effect of wind on surplus | Generation Availability Margin excluding wind | Minimum Demand Forecast | Total Negative Reserve Requirement for Minimum Demand | High Freq Response Requirement
2019-11-05 | 2019-11-07 | 43570 | 55025 | 3047.9144 | 3250 | 3250 | 11455 | 1200 | 4004.0107 | 181.8182 | 178 | 2043.21 | 0 | -913 | -467.9144 | 6044.3063 | 5410.6937 | 4705.79 | 6749.21 | 22960 | 2240.1212 | 517.0667
2019-11-05 | 2019-11-08 | 43250 | 50587 | 3047.9144 | 3250 | 3250 | 7337 | 1200 | 4012.5668 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 4009.6524 | 3327.3476 | 2491 | 4846 | 23060 | 2551.0707 | 516.0667
2019-11-05 | 2019-11-09 | 39850 | 51802 | 3047.9144 | 3250 | 3250 | 11952 | 1200 | 4103.4759 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 4100.5615 | 7851.4385 | 4665 | 7287 | 21950 | 2577.9798 | 527.1667
2019-11-05 | 2019-11-10 | 40810 | 52768 | 3047.9144 | 3250 | 3250 | 11958 | 1200 | 4077.8075 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 4074.893 | 7883.107 | 4845 | 7113 | 20970 | 2601.7374 | 536.9667
2019-11-05 | 2019-11-11 | 44670 | 57411 | 3047.9144 | 3250 | 3250 | 12741 | 1200 | 3974.5989 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 3971.6845 | 8769.3155 | 8204 | 4537 | 22300 | 2569.4949 | 523.6667
2019-11-05 | 2019-11-12 | 45550 | 54877 | 3047.9144 | 3250 | 3250 | 9327 | 1200 | 3951.0695 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 3948.1551 | 5378.8449 | 5711 | 3616 | 23490 | 2540.6465 | 511.7667
2019-11-05 | 2019-11-13 | 45470 | 55391 | 3047.9144 | 3250 | 3250 | 9921 | 1200 | 3953.2086 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 3950.2941 | 5970.7059 | 6266 | 3655 | 23610 | 2537.7374 | 510.5667
2019-11-05 | 2019-11-14 | 45550 | 54212 | 3047.9144 | 3250 | 3250 | 8662 | 1200 | 3951.0695 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 3948.1551 | 4713.8449 | 5048 | 3614 | 23610 | 2537.7374 | 510.5667
2019-11-05 | 2019-11-15 | 44140 | 52746 | 3047.9144 | 3250 | 3250 | 8606 | 1200 | 3988.7701 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 3985.8556 | 4620.1444 | 4480 | 4126 | 23610 | 2537.7374 | 510.5667
2019-11-05 | 2019-11-16 | 40280 | 52896 | 3047.9144 | 3250 | 3250 | 12616 | 1200 | 4091.9786 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 4089.0642 | 8526.9358 | 4938 | 7678 | 22400 | 2567.0707 | 522.6667
2019-11-05 | 2019-11-17 | 40980 | 53672 | 3047.9144 | 3250 | 3250 | 12692 | 1200 | 4073.262 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 4070.3476 | 8621.6524 | 4961 | 7731 | 21420 | 2590.8283 | 532.4667
2019-11-05 | 2019-11-18 | 45310 | 54812 | 3047.9144 | 3250 | 3250 | 9502 | 1200 | 3957.4866 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 3954.5722 | 5547.4278 | 4631 | 4871 | 23050 | 2551.3131 | 516.1667
2019-11-05 | 2019-11-19 | 44100 | 57301 | 3047.9144 | 3250 | 3250 | 13201 | 1200 | 3989.8396 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 3986.9251 | 9214.0749 | 7211 | 5990 | 24230 | 2522.7071 | 504.3667
OPMR total (o) = (g) + (h) + (j) + (k) +(l) + (m) + (n)
Generation Plant Margin (f) = (b) - (a) ALIGNS WITH ELEXON WEBSITE
National Surplus (p) = (f) - (o) ALIGNS WITH BMRS

## 04-Nov-2019
|  | Relevant Information |  |  |  |  | Calculated | OPMR Variables | [5 empty] | Total OPMR adjustors |  | Calculated |  | Wind |  | Negative Reserve at minimum demand
|  | a | b | c | d | e | f | g | h | i | j | k | l | m | n | o | p | q | r | s | t | u
Publish Date | Date | Peak Demand Forecast | Generator Availability | Contracted Availability | Maximum I/C Export | Maximum I/C Import | Generation Availability Margin | Contingency Requirement | STORR Requirement | Operating Reserve provided by I/Cs | Unavailable to Market & Commissioning Plant | Unavailable to National Grid | Available only to National Grid in exceptional circumstances | Reduction from additional availability (Not declared via OC2) | Reduction in Low Frequency Response Reserve Requirement (due to Contracted Response) | OPMR total | National Surplus (SPLD) | Effect of wind on surplus | Generation Availability Margin excluding wind | Minimum Demand Forecast | Total Negative Reserve Requirement for Minimum Demand | High Freq Response Requirement
2019-11-04 | 2019-11-06 | 44410 | 51501 | 3047.9144 | 3250 | 3250 | 7091 | 1200 | 3981.5508 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 3978.6364 | 3112.3636 | 3602 | 3489 | 22860 | 2241.9394 | 518.0667
2019-11-04 | 2019-11-07 | 43590 | 56364 | 3047.9144 | 3250 | 3250 | 12774 | 1200 | 4003.4759 | 181.8182 | 178 | 675.73 | 0 | -913 | -467.9144 | 4676.2915 | 8097.7085 | 7212.27 | 5561.73 | 22960 | 2553.4949 | 517.0667
2019-11-04 | 2019-11-08 | 43480 | 50981 | 3047.9144 | 3250 | 3250 | 7501 | 1200 | 4006.4171 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 4003.5027 | 3497.4973 | 2679 | 4822 | 23060 | 2551.0707 | 516.0667
2019-11-04 | 2019-11-09 | 40180 | 53360 | 3047.9144 | 3250 | 3250 | 13180 | 1200 | 4094.6524 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 4091.738 | 9088.262 | 5328 | 7852 | 21950 | 2577.9798 | 527.1667
2019-11-04 | 2019-11-10 | 40980 | 53331 | 3047.9144 | 3250 | 3250 | 12351 | 1200 | 4073.262 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 4070.3476 | 8280.6524 | 5305 | 7046 | 20970 | 2601.7374 | 536.9667
2019-11-04 | 2019-11-11 | 45260 | 55342 | 3047.9144 | 3250 | 3250 | 10082 | 1200 | 3958.8235 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 3955.9091 | 6126.0909 | 5956 | 4126 | 22300 | 2569.4949 | 523.6667
2019-11-04 | 2019-11-12 | 45410 | 55129 | 3047.9144 | 3250 | 3250 | 9719 | 1200 | 3954.8128 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 3951.8984 | 5767.1016 | 5751 | 3968 | 23490 | 2540.6465 | 511.7667
2019-11-04 | 2019-11-13 | 45520 | 55383 | 3047.9144 | 3250 | 3250 | 9863 | 1200 | 3951.8717 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 3948.9572 | 5914.0428 | 6043 | 3820 | 23610 | 2537.7374 | 510.5667
2019-11-04 | 2019-11-14 | 45280 | 54639 | 3047.9144 | 3250 | 3250 | 9359 | 1200 | 3958.2888 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 3955.3743 | 5403.6257 | 5346 | 4013 | 23610 | 2537.7374 | 510.5667
2019-11-04 | 2019-11-15 | 43220 | 53733 | 3047.9144 | 3250 | 3250 | 10513 | 1200 | 4013.369 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 4010.4545 | 6502.5455 | 4822 | 5691 | 23610 | 2537.7374 | 510.5667
2019-11-04 | 2019-11-16 | 39940 | 54095 | 3047.9144 | 3250 | 3250 | 14155 | 1200 | 4101.0695 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 4098.1551 | 10056.8449 | 5482 | 8673 | 22400 | 2567.0707 | 522.6667
2019-11-04 | 2019-11-17 | 40700 | 55204 | 3047.9144 | 3250 | 3250 | 14504 | 1200 | 4080.7487 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 4077.8342 | 10426.1658 | 5841 | 8663 | 21420 | 2590.8283 | 532.4667
2019-11-04 | 2019-11-18 | 43990 | 57525 | 3047.9144 | 3250 | 3250 | 13535 | 1200 | 3992.7807 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 3989.8663 | 9545.1337 | 7213 | 6322 | 23050 | 2551.3131 | 516.1667
OPMR total (o) = (g) + (h) + (j) + (k) +(l) + (m) + (n)
Generation Plant Margin (f) = (b) - (a) ALIGNS WITH ELEXON WEBSITE
National Surplus (p) = (f) - (o) ALIGNS WITH BMRS

## 01-Nov-2019
|  | Relevant Information |  |  |  |  | Calculated | OPMR Variables | [5 empty] | Total OPMR adjustors |  | Calculated |  | Wind |  | Negative Reserve at minimum demand
|  | a | b | c | d | e | f | g | h | i | j | k | l | m | n | o | p | q | r | s | t | u
Publish Date | Date | Peak Demand Forecast | Generator Availability | Contracted Availability | Maximum I/C Export | Maximum I/C Import | Generation Availability Margin | Contingency Requirement | STORR Requirement | Operating Reserve provided by I/Cs | Unavailable to Market & Commissioning Plant | Unavailable to National Grid | Available only to National Grid in exceptional circumstances | Reduction from additional availability (Not declared via OC2) | Reduction in Low Frequency Response Reserve Requirement (due to Contracted Response) | OPMR total | National Surplus (SPLD) | Effect of wind on surplus | Generation Availability Margin excluding wind | Minimum Demand Forecast | Total Negative Reserve Requirement for Minimum Demand | High Freq Response Requirement
2019-11-01 | 2019-11-03 | 38100 | 52117 | 3047.9144 | 3250 | 3250 | 14017 | 1200 | 4150.2674 | 181.8182 | 178 | 404.49 | 0 | -913 | -467.9144 | 4551.8429 | 9465.1571 | 4795.51 | 9221.49 | 19720 | 2299.0303 | 549.4667
2019-11-01 | 2019-11-04 | 42720 | 55696 | 3047.9144 | 3250 | 3250 | 12976 | 1200 | 4026.738 | 181.8182 | 178 | 844.78 | 0 | -913 | -467.9144 | 4868.6035 | 8107.3965 | 5928.22 | 7047.78 | 21350 | 2592.5253 | 533.1667
2019-11-01 | 2019-11-05 | 43930 | 54040 | 3047.9144 | 3250 | 3250 | 10110 | 1200 | 3994.385 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 3991.4706 | 6118.5294 | 4705 | 5405 | 22640 | 2561.2525 | 520.2667
2019-11-01 | 2019-11-06 | 44360 | 54658 | 3047.9144 | 3250 | 3250 | 10298 | 1200 | 3982.8877 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 3979.9733 | 6318.0267 | 5299 | 4999 | 22860 | 2555.9192 | 518.0667
2019-11-01 | 2019-11-07 | 44290 | 55320 | 3047.9144 | 3250 | 3250 | 11030 | 1200 | 3984.7594 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 3981.8449 | 7048.1551 | 5556 | 5474 | 22960 | 2553.4949 | 517.0667
2019-11-01 | 2019-11-08 | 43900 | 52290 | 3047.9144 | 3250 | 3250 | 8390 | 1200 | 3995.1872 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 3992.2727 | 4397.7273 | 3225 | 5165 | 23060 | 2551.0707 | 516.0667
2019-11-01 | 2019-11-09 | 40820 | 52905 | 3047.9144 | 3250 | 3250 | 12085 | 1200 | 4077.5401 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 4074.6257 | 8010.3743 | 4243 | 7842 | 21950 | 2577.9798 | 527.1667
2019-11-01 | 2019-11-10 | 41570 | 53544 | 3047.9144 | 3250 | 3250 | 11974 | 1200 | 4057.4866 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 4054.5722 | 7919.4278 | 4978 | 6996 | 20970 | 2601.7374 | 536.9667
2019-11-01 | 2019-11-11 | 45720 | 54690 | 3047.9144 | 3250 | 3250 | 8970 | 1200 | 3946.5241 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 3943.6096 | 5026.3904 | 4808 | 4162 | 22300 | 2569.4949 | 523.6667
2019-11-01 | 2019-11-12 | 45140 | 55403 | 3047.9144 | 3250 | 3250 | 10263 | 1200 | 3962.0321 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 3959.1176 | 6303.8824 | 5503 | 4760 | 23490 | 2540.6465 | 511.7667
2019-11-01 | 2019-11-13 | 44920 | 55187 | 3047.9144 | 3250 | 3250 | 10267 | 1200 | 3967.9144 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 3965 | 6302 | 5288 | 4979 | 23610 | 2537.7374 | 510.5667
2019-11-01 | 2019-11-14 | 44540 | 54973 | 3047.9144 | 3250 | 3250 | 10433 | 1200 | 3978.0749 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 3975.1604 | 6457.8396 | 5122 | 5311 | 23610 | 2537.7374 | 510.5667
2019-11-01 | 2019-11-15 | 41810 | 57519 | 3047.9144 | 3250 | 3250 | 15709 | 1200 | 4051.0695 | 181.8182 | 178 | 0 | 0 | -913 | -467.9144 | 4048.1551 | 11660.8449 | 7022 | 8687 | 23610 | 2537.7374 | 510.5667
OPMR total (o) = (g) + (h) + (j) + (k) +(l) + (m) + (n)
Generation Plant Margin (f) = (b) - (a) ALIGNS WITH ELEXON WEBSITE
National Surplus (p) = (f) - (o) ALIGNS WITH BMRS