## Slide 1
GC0147
Last resort disconnection of Embedded Generation – enduring solution
Rob Wilson
Presentation to recap and summarise GC0147 proposal
1st Workgroup meeting - 8th Sept 2020

## Slide 2: The defect - recap of GC0143 background and urgency
Under emergency conditions the Electricity System Operator (ESO) may need to instruct a Distribution Network Operator (DNO) to disconnect embedded generators connected to its system
Existing ability under the Grid Code to do this was felt to lack detail and be legally ambiguous
GC0143 clarified the format of instructions and removed the ambiguity
The requirement for this was due to the unprecedented societal changes brought about by the COVID-19 pandemic which has led to demands out-turning up to 20% lower than predicted
During very low demand periods very few controllable larger generators will be running
Urgency was required to achieve a solution before the Bank Holiday weekend on 8 May 2020
Sunset clause included in solution times out on 25 Oct 2020 after which the original defect will return

## Slide 3: GC0143 Timeline
Milestone | Date
Raised at Grid Code panel | 1 May 2020
Ofgem agree urgency | 1 May 2020
Code Administrator Consultation | 1 May 2020 to 5pm on 5 May 2020
Panel meeting to approve Final Modification Report | 6 May 2020
Ofgem approval | 7 May 2020
Implementation | 7 May 2020
Notes: 18 March 2020 to 25 March 2020
31 March 2020
Workgroup Consultation (5 working days)
1 April 2020 to 7 April 2020
Workgroup 2 (to discuss Workgroup Consultation Responses and hold Workgroup Vote)
9 April 2020
Workgroup Report issued to Panel
16 April 2020
Workgroup Report presented to Panel
24 April 2020
Code Administrator Consultation
27 April 2020 to 19 May 2020
Draft Final Modification Report presented to Panel
20 May 2020
Modification Panel decision
29 May 2020
Final Modification Report issued to the Authority
9 June 2020
Decision implemented in CUSC
1 April 2021

## Slide 4: GC0143 Ofgem decision – key points
In approving GC0143 Ofgem’s decision noted the following key points:
The need for urgency
The time-limited nature of the GC0143 solution
Use of disconnections as a last resort only following the exhaustion of all commercial alternatives
The concerns of respondents on environmental impact, safety issues and impacts on industrial processes, and an expectation on the ESO and DNOs to consider the order in which generation could be disconnected to minimize risks
The need for an enduring solution which would:
    Be progressed imminently
    Allow for full engagement and consultation
    Take account of the responses received to the GC0143 consultation

## Slide 5: Consultation responses – summary & key themes
Most respondents stated that they understand the reasoning behind the modification being raised and the threat to Security of Supply that the current situation (COVID-19) poses for the GB National Electricity Transmission System (NETS).
Whilst there was broad understanding of the issue facing National Grid ESO there were concerns raised around the approach outlined in this modification. Questions were raised around the approach through urgency and whether there would be unintended consequences to the modification being implemented as a result, plus the need for a more considered enduring solution.

## Slide 6: Theme #1 - The development of modification GC0143
Concern | Detail
Time taken to raise the change | It was highlighted by some respondents that in their view the ESO could have raised this change earlier and that the ESO had the opportunity to do so in the lead up to the paper being raised on the 30 April 2020.
Use of urgency | Concerns were raised at the modification being treated as urgent, the limited opportunity for industry engagement, and whether there would be unintended consequences of the modification being implemented as a result. Although there was broad support that the defect needed addressing, many respondents felt that it should have be done in a more thorough, considered way ahead of implementation. Some respondents also stated that there was not enough time to get plans in place ahead of implementation on 7 May 2020.
Enduring solution required | Many respondents highlighted the need for an enduring solution to be developed as soon as possible. It should address the points raised in the GC0143 discussions and consultation responses, and should ensure that all relevant stakeholders are both made aware of the proposal and given suitable opportunity to engage in developing the solution. Some also stressed that the temporary solution, having been approved and implemented, should not set a precedent for the enduring solution.

## Slide 7: Theme #2 - Carrying out emergency instructions
Concern | Detail
Clarity required over order of disconnection | Clarity over the order in which generators would be disconnected, with some suggesting that certain generators, or types of generators, should not be subject to disconnection. Several factors were recommended as considerations that should be included: The government’s carbon net zero targets, with the view that renewable generation should not be disconnected ahead of fossil fuel generation. Security of connection - those power stations providing the greatest level of security of supply should be the last to be disconnected. The consequences for customers, particularly those for whom generation formed part of a more complex industrial site, or where deenergisation of generation would also mean cutting off local demand, or could have environmental impacts.
‘Last resort’ only | Assurance that use would only be in an emergency situation and as a last resort after all other options had been exhausted. Several suggested that this should be included in the legal text. It was also felt that there should be more transparency over the steps that would be taken ahead of any instructions being given, and that these details should be in the public domain.
DNOs’ visibility | Concern over the visibility that the DNOs have of the information required to carry out emergency instructions, and how they would know what to disconnect.
Clarity over instruction | Respondents wanted more clarity over the disconnection process, including what the instruction from the ESO would look like, how DNOs would comply with the instruction and how generators would be notified.
Notice period before disconnection | Clarity over how much notice generators could expect before disconnection.
Reporting requested | Responses included the request that reporting is made publicly available detailing any emergency instructions of this type that are given by the ESO, including the rationale.

## Slide 8: Theme #3 - Impacts of emergency disconnection
Concern | Detail
Commercial impact / lack of compensation | One of the most frequent concerns raised in the responses was the lack of compensation that would be provided to any embedded generators that were disconnected via this process. This was seen to be a financial risk to generators, with many believing this demonstrated the absence of a level playing field and that the process was detrimental to competition since, in contrast, transmission connected generators and those that are in the Balancing Mechanism would receive compensation should the instruction be enacted.
Damage to assets | Potential for emergency disconnection to cause health and safety risks, damage to assets and the need for significant maintenance intervention. In some cases, forced disconnection could lead to wider plant shutdowns and disruption to industrial processes. They could be followed by further shutdowns after the system was restored. Some respondents wanted assurance from DNOs that essential infrastructure sites would not be affected. Respondents wanted clarity over the reconnection process, and suggested that, where restarting plants would require a site visit, this would be more difficult now due to the COVID-19 restrictions.
Risk to network stability | There were concerns at the impact to network stability if certain generators that provide services such as inertia and voltage control were disconnected.

## Slide 9: What has been done to address concerns?
Action | Progress
Work with DNOs on communication that can be published to improve transparency | Joint guidance agreed and published*
Letter to be published from the ESO on their position on GC0143 | Published*
Review all responses ahead of raising a modification for the enduring solution involving all stakeholders in its development | Report required by Ofgem – completed and published*
Establish new ODFM service to provide commercial alternative to disconnection | In place
Repeat consultation to comply with EBGL A18 requirements | 1 month consultation ran from 21 May to 22 June.
Develop enduring solution following normal governance including engagement and consultation | Needs to be in place by Spring 2021; to be raised at July Grid Code Review Panel
*Documents published under the ‘decision’ tab on the GC0143 web page

## Slide 10: Optional Downwards Flexibility Management (ODFM)
The ESO balances balance generation and demand in real time.
To allow us to do this we need to hold enough reserve to turn generation up or down to meet demand second by second.
When demand is low, we would expect embedded generation to be running along with nuclear, any transmission connected renewable generation, interconnectors and some conventional generation running at minimum stable export limit (SEL).
With this profile, there may be a requirement for additional flexibility to balance generation and demand, as well as to achieve sufficient negative reserve and high frequency response.
ODFM is a new optional service for non-BM parties to allow the ESO to access flexibility that is not currently available in real time.
ODFM in its current form will time out on 25 October 2020.
A new product will be developed for use in 2021.
https://data.nationalgrideso.com/ancillary-services/optional-downward-flexibility-management-odfm1

## Slide 11: Use of Emergency Instructions and ODFM in May 2020
Use of Emergency Instructions:
None – EIs are a last resort to be used only when all commercial alternatives are exhausted
Use of ODFM:
Sunday 10 May
Demand of 15.5GW, 238MW used for 3 hours
Saturday 23 May
Demand of 14.8GW over 1B period (1GW of ODFM used)
Demand of 16.7MW over 3B period (1938MW of ODFM used)
Sunday 24 May
1B demand of 14.5GW (800MW of ODFM used)
3B demand of 17GW (no ODFM used)
Monday 25 May
1B demand of 16.8GW (no ODFM used)
3B demand of 16.45GW (1020MW of ODFM used)
1B – night/early morning minimum
(ie low demand but no solar)
3B – afternoon minimum
(slightly higher demand but with solar)

## Slide 12: Joint ESO/DNO Guidance - High Level Principles

## Slide 13: Joint ESO/DNO Guidance - Priorities for maintaining connection

## Slide 14: Areas to Address in Enduring Solution
Symmetry with demand control instructions and protocols in section OC6 of the Grid Code
System warnings as covered under section OC7.4 of the Grid Code
Compensation arrangements – not covered under the Grid Code but need to be considered. Also whether Article 13 paragraph 7 of the Clean Energy Package applies.
NB This requires that “where non-market based redispatching is used, it shall be subject to financial compensation by the system operator requesting the redispatching….except in the case of producers that have accepted a connection agreement under which there is no guarantee of firm delivery of energy”.
Definition of last resort. Although in an emergency the ESO and DNOs have to maintain some flexibility to avoid worse disruption for consumers.
Any other options such as turndown short of disconnections
How an instruction will be implemented. Including:
      Order of priority
      Considerations around damage to equipment/environmental impact
      Restoration process
Reporting post-event
Any cross-code impacts

## Slide 15: GC0147 Legal Text – proposed changes
The following sections have been updated in the proposed draft legal text for GC0147
Section | Changes
OC6B (new section) | New section added, OC6B: Embedded Generation Control, which outlines the procedures for Embedded Generation Control and Disconnection Broadly symmetrical with the current OC6: Demand Control
OC7 | New System Warnings added to cover Embedded Generation Control.
Glossary & Definitions | Various new and amended defined terms including the new System Warnings
BC2.6.3 Communication With Network Operators In Emergency Circumstances | Updated to include Embedded Generation Control (symmetry with Demand Control)
BC2.9.1 Emergency Actions | Timed out GC0143 solution with sunset clause removed Embedded Generation Control added to Emergency Actions

## Slide 16: Draft Timeline for Development of Enduring Solution
Milestone | Date
Raise modification at Grid Code Review Panel | 30 July 2020
Workgroup nominations sought | 19 August 2020
Workgroup meetings x 3 | Sep – Oct 2020
Workgroup consultation (normally 15 working days) | Oct 2020
Workgroup vote on solution | Nov 2020
Workgroup report presented to panel | 26 Nov 2020
Code Administrator consultation (1 month) | Dec 2020
Draft final modification report presented to panel & recommendation vote | Jan 2021
Submission of final modification report to Ofgem | Feb 2021
Ofgem decision (25 working day KPI) | March 2021
Implementation | + 10 days
NB The driver is that implementation is required in time for the May 2021 Bank Holiday anticipated low demand periods