## Notes
Subject | Notes
System inertia: method of calculation | H=(f*∆P)/(2*RoCoF) H is system inertia; f is the starting frequency; ∆P is the system imbalance; RoCoF is the rate of change of frequency; Note that smaller losses will have less accurate system inertia calculations
RoCoF: method of calculation | RoCoF=(f_500ms-f_0ms)/500ms RoCoF is calculated using 500ms sliding window. RoCoF is the rate of change of frequency; f is the frequency; Note that smaller losses will have less accurate ROCOF calculations
Voltage Dip | Transient Voltage Dip with loss % and duration measured at the local substation
'Immediately before the Significant Event' | The starting frequency indicated in the Frequency Event Report, for frequency excursions. Where there is no Frequency Event Report, NGESO will use its best judgement.
'Immediately after the Significant Event' | The maximum frequency deviation indicated in the Frequency Event Report, for frequency excursions. Where there is no Frequency Event Report, NGESO will use its best judgement.

## Report
|  |  |  | (i) the time(s) in hh.mm.ss of the Significant Event and any potentially related occurrences; | (ii) any known or reported loss of Embedded Power Station(s) with locations and ratings where available; | (iii) the Frequency record (in table and graphical format) at <=1 second intervals for 1 minute before and 1 minute after the Significant Event; | (iv) the Frequency (to 2 decimal places) immediately before the Significant Event; | (v) the Frequency (to 2 decimal places) immediately after the Significant Event; | (vi) the maximum rate of change of Frequency recorded during the Significant Event over a specified time period of 500ms; | (vii) where known, the MW of all individual losses or trips related to the Significant Event; |  | (viii) where known, the identity of the Users and Network Operator of all demand losses or trips related to the Significant Event; | (ix) the location of any reported Transmission fault on the network diagram and geographically; | (x) the extent of any voltage dip associated with the Significant Event; | (xi) an estimate of system inertia in MWs at the time of the Significant Event along with how it has been calculated; and | (xii) any other data available that is of value to gain a clearer understanding of the Significant Event and its potential implications; and
Event Ref | Event Name | Notes | Date (Local) | Time (Local) | Loss of Embedded Power Station | Frequency Record | Pre-Event Frequency | Post-Event Frequency | RoCoF over 500ms | Individual Loss | System Imbalance | Demand loss of Users/DNOs related to event | Location of transmission fault | Voltage Dip | System Inertia | Additional data
Event Date-Number | Text | Text | DD/MM/YYYY | hh:mm:ss | MW | Text | Hz | Hz | Hz/s | Text+MW | MW | Text+MW | Text | % | GWs | Text
Event 20200803-1 | Trip of PEMB-51 |  | 2020-08-03 | 1:29 | N/A | Refer to tab 'Event 20200803-1' | 49.89 | 49.694 | -0.03 | 422 | -422 | N/A | N/A | N/A | 350.893
Event 20200805-1 | Trip of Britned and BoA Deviation of WLNY-4 |  | 2020-08-05 | 0:03 | N/A | Refer to tab 'Event 20200805-1' | 49.98 | 50.302 | 0.078 | Britned 352MW GB to NE while ramping to 645MW, WLNY-4 221MW | 866 | N/A | N/A | N/A | 277.4531
Event 20200806-1 | Loss of MEDP-51 | GT tripped | 2020-08-06 | 19:25 | N/A | Refer to tab 'Event 20200806-1' | 50.025 | 49.933 | -0.017 | 350 | -350 | N/A | N/A | N/A | 514.9632
Event 20200807-1 | Trip of DRAX-3 | Coincident with Interconnector 2.5GW increase at combined rate of 300MW/min | 2020-08-07 | 22:51 | N/A | Refer to tab 'Event 20200807-1' | 49.92 | 49.742 | -0.029 | 300 | -300 | N/A | N/A | N/A | 258.2069
Event 20200810-1 | Trip of GRAI-8 |  | 2020-08-10 | 6:59 | N/A | Refer to tab 'Event 20200810-1' | 50.079 | 49.931 | -0.046 | 410 | -410 | N/A | N/A | N/A | 223.1782
Event 20200810-2 | Trip of DRAX-4 |  | 2020-08-10 | 20:58 | N/A | Refer to tab 'Event 20200810-2' | 50.039 | 49.759 | -0.045 | 645 | -645 | N/A | N/A | N/A | 358.6128
Event 20200812-1 | Trip of LAGA-1 |  | 2020-08-12 | 11:40 | N/A | Refer to tab 'Event 20200812-1' | 49.993 | 49.903 | -0.028 | 251 | -251 | N/A | N/A | N/A | 224.0758
Event 20200813-1 | Trip of DINO-8 | G6 tripped at 04:51, G2 tripped at 04:59, G1 tripped at 05:01, G4 tripped at 05:02, G5 tripped at 05:17 | 2020-08-13 | 4:51 | N/A | Refer to tab 'Event 20200813-1' | 49.969 | 50.142 | 0.013 | G6 267MW, G2 260MW, G1 269MW, G4 264MW, G5 265MW | 1325 | N/A | N/A | N/A | 513
Event 20200816-1 | Interconnectors ramping down import to GB | IFA -200MW, Britned -100MW and Nemo -500MW, at peak combined rate of 300MW/min | 2020-08-16 | 22:59 | N/A | Refer to tab 'Event 20200816-1' | 50 | 49.679 | -0.017 | IFA 200MW, Britned 100MW and Nemo 500MW | -800 | N/A | N/A | N/A | N/A
Event 20200817-1 | Trip of HEYM11 |  | 2020-08-17 | 10:53 | N/A | Refer to tab 'Event 20200817-1' | 49.979 | 49.751 | -0.047 | 486 | -486 | N/A | N/A | N/A | 258.4021
Event 20200821-1 | Trip of DINO-6 |  | 2020-08-21 | 7:04 | N/A | Refer to tab 'Event 20200821-1' | 49.95 | 50.074 | 0.035 | 287 | 287 | N/A | N/A | N/A | 204.795
Event 20200822-1 | Trip of SIZB-1 |  | 2020-08-22 | 1:34 | N/A | Refer to tab 'Event 20200822-1' | 50.095 | 49.875 | -0.091 | 606 | -606 | N/A | N/A | N/A | N/A
Event 20200822-2 | Trip of CDCL-1 | Output reduced from 394MW at 20:57 to 0MW at 21:18 | 2020-08-22 | 20:57 | N/A | Refer to tab 'Event 20200822-2' | 50.036 | 49.93 | N/A | 403 | -403 | N/A | N/A | N/A | N/A
Event 20200825-1 | Trip of STAY-4 |  | 2020-08-25 | 8:39 | N/A | Refer to tab 'Event 20200825-1' | 49.968 | 49.816 | -0.066 | 400 | -400 | N/A | N/A | N/A | N/A
Event 20200827-1 | Trip of CNQPS-2 |  | 2020-08-27 | 11:11 | N/A | Refer to tab 'Event 20200827-1' | 50.03 | 49.832 | -0.031 | 320 | -320 | N/A | N/A | N/A | 258.2194
Event 20200829-1 | Trip of SPLN-1 | Output reduced from 405MW at 06:52 to 0MW at 08:14 | 2020-08-29 | 6:52 | N/A | Refer to tab 'Event 20200829-1' | 50.043 | 49.812 | N/A | 405 | -405 | N/A | N/A | N/A | N/A
Event 20200830-1 | Trip of KEAD |  | 2020-08-30 | 12:17 | N/A | Refer to tab 'Event 20200830-1' | 49.906 | 49.868 | -0.017 | 402 | -402 | N/A | N/A | N/A | 590.0651
Event 20200831-1 | Loss of WBURB-2 | ST Tripped, GTs came off controlled, output reduced from 414MW at 18:50 to 0MW at 19:28 | 2020-08-31 | 18:50 | N/A | Refer to tab 'Event 20200831-1' | 50.146 | 49.874 | N/A | 414 | -414 | N/A | N/A | N/A | N/A

## Event 20200803-1
In UTC
Date | Time | Freq
2020-08-03 | 0:28 | 49.887
2020-08-03 | 0:28 | 49.884
2020-08-03 | 0:28 | 49.884
2020-08-03 | 0:28 | 49.882
2020-08-03 | 0:28 | 49.881
2020-08-03 | 1:28 | 49.883
2020-08-03 | 2:28 | 49.882
2020-08-03 | 3:28 | 49.88
2020-08-03 | 4:28 | 49.879
2020-08-03 | 5:28 | 49.879
2020-08-03 | 6:28 | 49.881
2020-08-03 | 7:28 | 49.879
2020-08-03 | 8:28 | 49.88
2020-08-03 | 9:28 | 49.88
2020-08-03 | 10:28 | 49.88
2020-08-03 | 11:28 | 49.88
2020-08-03 | 12:28 | 49.878
2020-08-03 | 13:28 | 49.876
2020-08-03 | 14:28 | 49.875
2020-08-03 | 15:28 | 49.87
2020-08-03 | 16:28 | 49.869
2020-08-03 | 17:28 | 49.868
2020-08-03 | 18:28 | 49.865
2020-08-03 | 19:28 | 49.862
2020-08-03 | 20:28 | 49.862
2020-08-03 | 21:28 | 49.857
2020-08-03 | 22:28 | 49.856
2020-08-03 | 23:28 | 49.855
2020-08-03 | 24:28 | 49.853
2020-08-03 | 25:28 | 49.851
2020-08-03 | 26:28 | 49.849
2020-08-03 | 27:28 | 49.848
2020-08-03 | 28:28 | 49.845
2020-08-03 | 29:28 | 49.844
2020-08-03 | 30:28 | 49.84
2020-08-03 | 31:28 | 49.836
2020-08-03 | 32:28 | 49.835
2020-08-03 | 33:28 | 49.83
2020-08-03 | 34:28 | 49.826
2020-08-03 | 35:28 | 49.824
2020-08-03 | 36:28 | 49.823
2020-08-03 | 37:28 | 49.82
2020-08-03 | 38:28 | 49.818
2020-08-03 | 39:28 | 49.816
2020-08-03 | 40:28 | 49.812
2020-08-03 | 41:28 | 49.807
2020-08-03 | 42:28 | 49.802
2020-08-03 | 43:28 | 49.796
2020-08-03 | 44:28 | 49.791
2020-08-03 | 45:28 | 49.784
2020-08-03 | 46:28 | 49.781
2020-08-03 | 47:28 | 49.779
2020-08-03 | 48:28 | 49.778
2020-08-03 | 49:28 | 49.778
2020-08-03 | 50:28 | 49.779
2020-08-03 | 51:28 | 49.78
2020-08-03 | 52:28 | 49.78
2020-08-03 | 53:28 | 49.78
2020-08-03 | 54:28 | 49.779
2020-08-03 | 55:28 | 49.779
2020-08-03 | 56:28 | 49.762
2020-08-03 | 57:28 | 49.743
2020-08-03 | 58:28 | 49.725
2020-08-03 | 59:28 | 49.711
2020-08-03 | 60:28 | 49.705
2020-08-03 | 61:28 | 49.702
2020-08-03 | 62:28 | 49.699
2020-08-03 | 63:28 | 49.7
2020-08-03 | 64:28 | 49.701
2020-08-03 | 65:28 | 49.705
2020-08-03 | 66:28 | 49.712
2020-08-03 | 67:28 | 49.715
2020-08-03 | 68:28 | 49.717
2020-08-03 | 69:28 | 49.72
2020-08-03 | 70:28 | 49.722
2020-08-03 | 71:28 | 49.724
2020-08-03 | 72:28 | 49.726
2020-08-03 | 73:28 | 49.727
2020-08-03 | 74:28 | 49.728
2020-08-03 | 75:28 | 49.73
2020-08-03 | 76:28 | 49.733
2020-08-03 | 77:28 | 49.733
2020-08-03 | 78:28 | 49.739
2020-08-03 | 79:28 | 49.743
2020-08-03 | 80:28 | 49.749
2020-08-03 | 81:28 | 49.751
2020-08-03 | 82:28 | 49.754
2020-08-03 | 83:28 | 49.76
2020-08-03 | 84:28 | 49.765
2020-08-03 | 85:28 | 49.771
2020-08-03 | 86:28 | 49.773
2020-08-03 | 87:28 | 49.773
2020-08-03 | 88:28 | 49.773
2020-08-03 | 89:28 | 49.773
2020-08-03 | 90:28 | 49.774
2020-08-03 | 91:28 | 49.777
2020-08-03 | 92:28 | 49.779
2020-08-03 | 93:28 | 49.781
2020-08-03 | 94:28 | 49.784
2020-08-03 | 95:28 | 49.784
2020-08-03 | 96:28 | 49.783
2020-08-03 | 97:28 | 49.782
2020-08-03 | 98:28 | 49.78
2020-08-03 | 99:28 | 49.781
2020-08-03 | 100:28 | 49.78
2020-08-03 | 101:28 | 49.782
2020-08-03 | 102:28 | 49.78
2020-08-03 | 103:28 | 49.779
2020-08-03 | 104:28 | 49.778
2020-08-03 | 105:28 | 49.779
2020-08-03 | 106:28 | 49.778
2020-08-03 | 107:28 | 49.781
2020-08-03 | 108:28 | 49.782
2020-08-03 | 109:28 | 49.78
2020-08-03 | 110:28 | 49.778
2020-08-03 | 111:28 | 49.776
2020-08-03 | 112:28 | 49.776
2020-08-03 | 113:28 | 49.776
2020-08-03 | 114:28 | 49.775
2020-08-03 | 115:28 | 49.772
2020-08-03 | 116:28 | 49.768
2020-08-03 | 117:28 | 49.762
2020-08-03 | 118:28 | 49.758
2020-08-03 | 119:28 | 49.758
2020-08-03 | 120:28 | 49.756
2020-08-03 | 121:28 | 49.756
2020-08-03 | 122:28 | 49.757
2020-08-03 | 123:28 | 49.757
2020-08-03 | 124:28 | 49.755
2020-08-03 | 125:28 | 49.755
2020-08-03 | 126:28 | 49.753
2020-08-03 | 127:28 | 49.751
2020-08-03 | 128:28 | 49.747
2020-08-03 | 129:28 | 49.749
2020-08-03 | 130:28 | 49.748
2020-08-03 | 131:28 | 49.748
2020-08-03 | 132:28 | 49.749
2020-08-03 | 133:28 | 49.75
2020-08-03 | 134:28 | 49.75
2020-08-03 | 135:28 | 49.75
2020-08-03 | 136:28 | 49.749
2020-08-03 | 137:28 | 49.748
2020-08-03 | 138:28 | 49.746
2020-08-03 | 139:28 | 49.743
2020-08-03 | 140:28 | 49.743
2020-08-03 | 141:28 | 49.744
2020-08-03 | 142:28 | 49.75
2020-08-03 | 143:28 | 49.757
2020-08-03 | 144:28 | 49.765
2020-08-03 | 145:28 | 49.772
2020-08-03 | 146:28 | 49.783
2020-08-03 | 147:28 | 49.792
2020-08-03 | 148:28 | 49.802
2020-08-03 | 149:28 | 49.81
2020-08-03 | 150:28 | 49.815
2020-08-03 | 151:28 | 49.818
2020-08-03 | 152:28 | 49.82
2020-08-03 | 153:28 | 49.819
2020-08-03 | 154:28 | 49.821
2020-08-03 | 155:28 | 49.821
2020-08-03 | 156:28 | 49.822
2020-08-03 | 157:28 | 49.821
2020-08-03 | 158:28 | 49.826
2020-08-03 | 159:28 | 49.83
2020-08-03 | 160:28 | 49.832
2020-08-03 | 161:28 | 49.835
2020-08-03 | 162:28 | 49.837
2020-08-03 | 163:28 | 49.838
2020-08-03 | 164:28 | 49.838
2020-08-03 | 165:28 | 49.837
2020-08-03 | 166:28 | 49.834
2020-08-03 | 167:28 | 49.831
2020-08-03 | 168:28 | 49.83
2020-08-03 | 169:28 | 49.829
2020-08-03 | 170:28 | 49.829
2020-08-03 | 171:28 | 49.83
2020-08-03 | 172:28 | 49.829
2020-08-03 | 173:28 | 49.831
2020-08-03 | 174:28 | 49.831
2020-08-03 | 175:28 | 49.831
2020-08-03 | 176:28 | 49.832
2020-08-03 | 177:28 | 49.832
2020-08-03 | 178:28 | 49.832
2020-08-03 | 179:28 | 49.832
2020-08-03 | 180:28 | 49.835
2020-08-03 | 181:28 | 49.84
2020-08-03 | 182:28 | 49.842
2020-08-03 | 183:28 | 49.844
2020-08-03 | 184:28 | 49.845
2020-08-03 | 185:28 | 49.846
2020-08-03 | 186:28 | 49.847
2020-08-03 | 187:28 | 49.849
2020-08-03 | 188:28 | 49.85
2020-08-03 | 189:28 | 49.851
2020-08-03 | 190:28 | 49.853
2020-08-03 | 191:28 | 49.854
2020-08-03 | 192:28 | 49.857
2020-08-03 | 193:28 | 49.859
2020-08-03 | 194:28 | 49.86
2020-08-03 | 195:28 | 49.861
2020-08-03 | 196:28 | 49.861
2020-08-03 | 197:28 | 49.862
2020-08-03 | 198:28 | 49.863
2020-08-03 | 199:28 | 49.865
2020-08-03 | 200:28 | 49.868
2020-08-03 | 201:28 | 49.87
2020-08-03 | 202:28 | 49.874
2020-08-03 | 203:28 | 49.876
2020-08-03 | 204:28 | 49.877
2020-08-03 | 205:28 | 49.879
2020-08-03 | 206:28 | 49.879
2020-08-03 | 207:28 | 49.88
2020-08-03 | 208:28 | 49.879
2020-08-03 | 209:28 | 49.881
2020-08-03 | 210:28 | 49.88
2020-08-03 | 211:28 | 49.88
2020-08-03 | 212:28 | 49.88
2020-08-03 | 213:28 | 49.879
2020-08-03 | 214:28 | 49.88
2020-08-03 | 215:28 | 49.88
2020-08-03 | 216:28 | 49.88
2020-08-03 | 217:28 | 49.881
2020-08-03 | 218:28 | 49.879
2020-08-03 | 219:28 | 49.878
2020-08-03 | 220:28 | 49.88
2020-08-03 | 221:28 | 49.879
2020-08-03 | 222:28 | 49.88
2020-08-03 | 223:28 | 49.881
2020-08-03 | 224:28 | 49.881
2020-08-03 | 225:28 | 49.882
2020-08-03 | 226:28 | 49.881
2020-08-03 | 227:28 | 49.882
2020-08-03 | 228:28 | 49.882
2020-08-03 | 229:28 | 49.883
2020-08-03 | 230:28 | 49.883
2020-08-03 | 231:28 | 49.882
2020-08-03 | 232:28 | 49.883
2020-08-03 | 233:28 | 49.882
2020-08-03 | 234:28 | 49.88
2020-08-03 | 235:28 | 49.876
2020-08-03 | 236:28 | 49.873
2020-08-03 | 237:28 | 49.87
2020-08-03 | 238:28 | 49.869
2020-08-03 | 239:28 | 49.87
2020-08-03 | 240:28 | 49.872
2020-08-03 | 241:28 | 49.873
2020-08-03 | 242:28 | 49.874
2020-08-03 | 243:28 | 49.874
2020-08-03 | 244:28 | 49.875
2020-08-03 | 245:28 | 49.874
2020-08-03 | 246:28 | 49.876
2020-08-03 | 247:28 | 49.876
2020-08-03 | 248:28 | 49.878
2020-08-03 | 249:28 | 49.878
2020-08-03 | 250:28 | 49.876
2020-08-03 | 251:28 | 49.875
2020-08-03 | 252:28 | 49.874
2020-08-03 | 253:28 | 49.876
2020-08-03 | 254:28 | 49.879
2020-08-03 | 255:28 | 49.881
2020-08-03 | 256:28 | 49.882
2020-08-03 | 257:28 | 49.882
2020-08-03 | 258:28 | 49.882
2020-08-03 | 259:28 | 49.883
2020-08-03 | 260:28 | 49.884
2020-08-03 | 261:28 | 49.884
2020-08-03 | 262:28 | 49.883
2020-08-03 | 263:28 | 49.881
2020-08-03 | 264:28 | 49.879
2020-08-03 | 265:28 | 49.879
2020-08-03 | 266:28 | 49.878
2020-08-03 | 267:28 | 49.877
2020-08-03 | 268:28 | 49.882
2020-08-03 | 269:28 | 49.887
2020-08-03 | 270:28 | 49.889
2020-08-03 | 271:28 | 49.889
2020-08-03 | 272:28 | 49.89
2020-08-03 | 273:28 | 49.892
2020-08-03 | 274:28 | 49.893
2020-08-03 | 275:28 | 49.892
2020-08-03 | 276:28 | 49.891
2020-08-03 | 277:28 | 49.889
2020-08-03 | 278:28 | 49.887
2020-08-03 | 279:28 | 49.886
2020-08-03 | 280:28 | 49.886
2020-08-03 | 281:28 | 49.888
2020-08-03 | 282:28 | 49.89
2020-08-03 | 283:28 | 49.892
2020-08-03 | 284:28 | 49.895
2020-08-03 | 285:28 | 49.898
2020-08-03 | 286:28 | 49.9
2020-08-03 | 287:28 | 49.902
2020-08-03 | 288:28 | 49.905
2020-08-03 | 289:28 | 49.908
2020-08-03 | 290:28 | 49.911
2020-08-03 | 291:28 | 49.913
2020-08-03 | 292:28 | 49.915
2020-08-03 | 293:28 | 49.916
2020-08-03 | 294:28 | 49.916
2020-08-03 | 295:28 | 49.918
2020-08-03 | 296:28 | 49.919
2020-08-03 | 297:28 | 49.919
2020-08-03 | 298:28 | 49.918
2020-08-03 | 299:28 | 49.919
2020-08-03 | 300:28 | 49.918
2020-08-03 | 301:28 | 49.919
2020-08-03 | 302:28 | 49.919
2020-08-03 | 303:28 | 49.92
2020-08-03 | 304:28 | 49.919
2020-08-03 | 305:28 | 49.921
2020-08-03 | 306:28 | 49.922
2020-08-03 | 307:28 | 49.924
2020-08-03 | 308:28 | 49.925
2020-08-03 | 309:28 | 49.925
2020-08-03 | 310:28 | 49.924
2020-08-03 | 311:28 | 49.923
2020-08-03 | 312:28 | 49.924
2020-08-03 | 313:28 | 49.924
2020-08-03 | 314:28 | 49.925
2020-08-03 | 315:28 | 49.925
2020-08-03 | 316:28 | 49.925
2020-08-03 | 317:28 | 49.925
2020-08-03 | 318:28 | 49.927
2020-08-03 | 319:28 | 49.929
2020-08-03 | 320:28 | 49.929
2020-08-03 | 321:28 | 49.928
2020-08-03 | 322:28 | 49.927
2020-08-03 | 323:28 | 49.927
2020-08-03 | 324:28 | 49.926
2020-08-03 | 325:28 | 49.925
2020-08-03 | 326:28 | 49.923
2020-08-03 | 327:28 | 49.922
2020-08-03 | 328:28 | 49.92
2020-08-03 | 329:28 | 49.919
2020-08-03 | 330:28 | 49.919
2020-08-03 | 331:28 | 49.92
2020-08-03 | 332:28 | 49.922
2020-08-03 | 333:28 | 49.922
2020-08-03 | 334:28 | 49.922
2020-08-03 | 335:28 | 49.924
2020-08-03 | 336:28 | 49.924
2020-08-03 | 337:28 | 49.925
2020-08-03 | 338:28 | 49.924
2020-08-03 | 339:28 | 49.922
2020-08-03 | 340:28 | 49.92
2020-08-03 | 341:28 | 49.916
2020-08-03 | 342:28 | 49.913
2020-08-03 | 343:28 | 49.912
2020-08-03 | 344:28 | 49.912
2020-08-03 | 345:28 | 49.914
2020-08-03 | 346:28 | 49.914
2020-08-03 | 347:28 | 49.915
2020-08-03 | 348:28 | 49.915
2020-08-03 | 349:28 | 49.917
2020-08-03 | 350:28 | 49.919
2020-08-03 | 351:28 | 49.917
2020-08-03 | 352:28 | 49.914
2020-08-03 | 353:28 | 49.912
2020-08-03 | 354:28 | 49.91
2020-08-03 | 355:28 | 49.911
2020-08-03 | 356:28 | 49.914
2020-08-03 | 357:28 | 49.918
2020-08-03 | 358:28 | 49.92
2020-08-03 | 359:28 | 49.922
2020-08-03 | 360:28 | 49.924
2020-08-03 | 361:28 | 49.925
2020-08-03 | 362:28 | 49.926
2020-08-03 | 363:28 | 49.928
2020-08-03 | 364:28 | 49.926
2020-08-03 | 365:28 | 49.924
2020-08-03 | 366:28 | 49.922
2020-08-03 | 367:28 | 49.921
2020-08-03 | 368:28 | 49.92
2020-08-03 | 369:28 | 49.92
2020-08-03 | 370:28 | 49.92
2020-08-03 | 371:28 | 49.925
2020-08-03 | 372:28 | 49.929
2020-08-03 | 373:28 | 49.933
2020-08-03 | 374:28 | 49.936
2020-08-03 | 375:28 | 49.938
2020-08-03 | 376:28 | 49.938
2020-08-03 | 377:28 | 49.938
2020-08-03 | 378:28 | 49.938
2020-08-03 | 379:28 | 49.935
2020-08-03 | 380:28 | 49.933
2020-08-03 | 381:28 | 49.933
2020-08-03 | 382:28 | 49.934
2020-08-03 | 383:28 | 49.935
2020-08-03 | 384:28 | 49.936
2020-08-03 | 385:28 | 49.937
2020-08-03 | 386:28 | 49.938
2020-08-03 | 387:28 | 49.94
2020-08-03 | 388:28 | 49.941
2020-08-03 | 389:28 | 49.944
2020-08-03 | 390:28 | 49.947
2020-08-03 | 391:28 | 49.949
2020-08-03 | 392:28 | 49.95
2020-08-03 | 393:28 | 49.953
2020-08-03 | 394:28 | 49.954
2020-08-03 | 395:28 | 49.957
2020-08-03 | 396:28 | 49.96
2020-08-03 | 397:28 | 49.961
2020-08-03 | 398:28 | 49.963
2020-08-03 | 399:28 | 49.964
2020-08-03 | 400:28 | 49.965
2020-08-03 | 401:28 | 49.967
2020-08-03 | 402:28 | 49.967
2020-08-03 | 403:28 | 49.967
2020-08-03 | 404:28 | 49.967
2020-08-03 | 405:28 | 49.967
2020-08-03 | 406:28 | 49.966
2020-08-03 | 407:28 | 49.966
2020-08-03 | 408:28 | 49.965
2020-08-03 | 409:28 | 49.964
2020-08-03 | 410:28 | 49.962
2020-08-03 | 411:28 | 49.963
2020-08-03 | 412:28 | 49.963
2020-08-03 | 413:28 | 49.962
2020-08-03 | 414:28 | 49.963
2020-08-03 | 415:28 | 49.965
2020-08-03 | 416:28 | 49.965
2020-08-03 | 417:28 | 49.966
2020-08-03 | 418:28 | 49.967
2020-08-03 | 419:28 | 49.968
2020-08-03 | 420:28 | 49.97
2020-08-03 | 421:28 | 49.971
2020-08-03 | 422:28 | 49.973
2020-08-03 | 423:28 | 49.974
2020-08-03 | 424:28 | 49.974
2020-08-03 | 425:28 | 49.974
2020-08-03 | 426:28 | 49.974
2020-08-03 | 427:28 | 49.974
2020-08-03 | 428:28 | 49.973
2020-08-03 | 429:28 | 49.973
2020-08-03 | 430:28 | 49.973
2020-08-03 | 431:28 | 49.973
2020-08-03 | 432:28 | 49.974
2020-08-03 | 433:28 | 49.974
2020-08-03 | 434:28 | 49.975
2020-08-03 | 435:28 | 49.976
2020-08-03 | 436:28 | 49.977
2020-08-03 | 437:28 | 49.979
2020-08-03 | 438:28 | 49.98
2020-08-03 | 439:28 | 49.982
2020-08-03 | 440:28 | 49.983
2020-08-03 | 441:28 | 49.984
2020-08-03 | 442:28 | 49.985
2020-08-03 | 443:28 | 49.984
2020-08-03 | 444:28 | 49.984
2020-08-03 | 445:28 | 49.983
2020-08-03 | 446:28 | 49.982
2020-08-03 | 447:28 | 49.981
2020-08-03 | 448:28 | 49.981
2020-08-03 | 449:28 | 49.98
2020-08-03 | 450:28 | 49.98
2020-08-03 | 451:28 | 49.98
2020-08-03 | 452:28 | 49.981
2020-08-03 | 453:28 | 49.983
2020-08-03 | 454:28 | 49.984
2020-08-03 | 455:28 | 49.985
2020-08-03 | 456:28 | 49.986
2020-08-03 | 457:28 | 49.988
2020-08-03 | 458:28 | 49.989
2020-08-03 | 459:28 | 49.989
2020-08-03 | 460:28 | 49.991
2020-08-03 | 461:28 | 49.991
2020-08-03 | 462:28 | 49.992
2020-08-03 | 463:28 | 49.991
2020-08-03 | 464:28 | 49.99
2020-08-03 | 465:28 | 49.987
2020-08-03 | 466:28 | 49.987
2020-08-03 | 467:28 | 49.984
2020-08-03 | 468:28 | 49.981
2020-08-03 | 469:28 | 49.978
2020-08-03 | 470:28 | 49.976
2020-08-03 | 471:28 | 49.974
2020-08-03 | 472:28 | 49.976
2020-08-03 | 473:28 | 49.976
2020-08-03 | 474:28 | 49.975
2020-08-03 | 475:28 | 49.974
2020-08-03 | 476:28 | 49.973
2020-08-03 | 477:28 | 49.972
2020-08-03 | 478:28 | 49.971
2020-08-03 | 479:28 | 49.97
2020-08-03 | 480:28 | 49.971
2020-08-03 | 481:28 | 49.974
2020-08-03 | 482:28 | 49.976
2020-08-03 | 483:28 | 49.978
2020-08-03 | 484:28 | 49.98
2020-08-03 | 485:28 | 49.981
2020-08-03 | 486:28 | 49.982
2020-08-03 | 487:28 | 49.984
2020-08-03 | 488:28 | 49.986
2020-08-03 | 489:28 | 49.984
2020-08-03 | 490:28 | 49.981
2020-08-03 | 491:28 | 49.978
2020-08-03 | 492:28 | 49.975
2020-08-03 | 493:28 | 49.978
2020-08-03 | 494:28 | 49.981
2020-08-03 | 495:28 | 49.984
2020-08-03 | 496:28 | 49.986
2020-08-03 | 497:28 | 49.988
2020-08-03 | 498:28 | 49.988
2020-08-03 | 499:28 | 49.987
2020-08-03 | 500:28 | 49.988
2020-08-03 | 501:28 | 49.988
2020-08-03 | 502:28 | 49.989
2020-08-03 | 503:28 | 49.989
2020-08-03 | 504:28 | 49.987
2020-08-03 | 505:28 | 49.985
2020-08-03 | 506:28 | 49.983
2020-08-03 | 507:28 | 49.984
2020-08-03 | 508:28 | 49.986
2020-08-03 | 509:28 | 49.989
2020-08-03 | 510:28 | 49.992
2020-08-03 | 511:28 | 49.994
2020-08-03 | 512:28 | 49.998
2020-08-03 | 513:28 | 50
2020-08-03 | 514:28 | 50.003
2020-08-03 | 515:28 | 50.005
2020-08-03 | 516:28 | 50.003
2020-08-03 | 517:28 | 50
2020-08-03 | 518:28 | 49.993
2020-08-03 | 519:28 | 49.989
2020-08-03 | 520:28 | 49.984
2020-08-03 | 521:28 | 49.98
2020-08-03 | 522:28 | 49.98
2020-08-03 | 523:28 | 49.985
2020-08-03 | 524:28 | 49.993
2020-08-03 | 525:28 | 49.999
2020-08-03 | 526:28 | 50.003
2020-08-03 | 527:28 | 50.005
2020-08-03 | 528:28 | 50.006
2020-08-03 | 529:28 | 50.004
2020-08-03 | 530:28 | 50.001
2020-08-03 | 531:28 | 50
2020-08-03 | 532:28 | 49.995
2020-08-03 | 533:28 | 49.992
2020-08-03 | 534:28 | 49.989
2020-08-03 | 535:28 | 49.985
536:28
537:28
538:28
539:28
540:28
541:28
542:28
543:28
544:28
545:28
546:28
547:28
548:28
549:28
550:28
551:28
552:28
553:28
554:28
555:28
556:28
557:28
558:28
559:28
560:28
561:28
562:28
563:28
564:28
565:28
566:28
567:28
568:28
569:28
570:28
571:28
572:28
573:28
574:28
575:28
576:28
577:28
578:28
579:28
580:28
581:28
582:28
583:28
584:28
585:28
586:28
587:28
588:28
589:28
590:28
591:28
592:28
593:28
594:28
595:28
596:28
597:28
598:28
599:28
600:28
601:28
602:28
603:28
604:28
605:28
606:28
607:28
608:28
609:28
610:28
611:28
612:28
613:28
614:28
615:28
616:28
617:28
618:28
619:28
620:28
621:28
622:28
623:28
624:28
625:28
626:28
627:28
628:28
629:28
630:28
631:28
632:28
633:28
634:28
635:28
636:28
637:28
638:28
639:28
640:28
641:28
642:28
643:28
644:28
645:28
646:28
647:28
648:28
649:28
650:28
651:28
652:28
653:28
654:28
655:28
656:28
657:28
658:28
659:28
660:28
661:28
662:28
663:28
664:28
665:28
666:28
667:28
668:28
669:28
670:28
671:28
672:28
673:28
674:28
675:28
676:28
677:28
678:28
679:28
680:28
681:28
682:28
683:28
684:28
685:28
686:28
687:28
688:28
689:28
690:28
691:28
692:28
693:28
694:28
695:28
696:28
697:28
698:28
699:28
700:28
701:28
702:28
703:28
704:28
705:28
706:28
707:28
708:28
709:28
710:28
711:28
712:28
713:28
714:28
715:28
716:28
717:28
718:28
719:28
720:28
721:28
722:28
723:28
724:28
725:28
726:28
727:28
728:28
729:28
730:28
731:28
732:28
733:28
734:28
735:28
736:28
737:28
738:28
739:28
740:28
741:28
742:28
743:28
744:28
745:28
746:28
747:28
748:28
749:28
750:28
751:28
752:28
753:28
754:28
755:28
756:28
757:28
758:28
759:28
760:28
761:28
762:28
763:28
764:28
765:28
766:28
767:28
768:28
769:28
770:28
771:28
772:28
773:28
774:28
775:28
776:28
777:28
778:28
779:28
780:28
781:28
782:28
783:28
784:28
785:28
786:28
787:28
788:28
789:28
790:28
791:28
792:28
793:28
794:28
795:28
796:28
797:28
798:28
799:28
800:28
801:28
802:28
803:28
804:28
805:28
806:28
807:28
808:28
809:28
810:28
811:28
812:28
813:28
814:28
815:28
816:28
817:28
818:28
819:28
820:28
821:28
822:28
823:28
824:28
825:28
826:28
827:28
828:28
829:28
830:28
831:28
832:28
833:28
834:28
835:28
836:28
837:28
838:28
839:28
840:28
841:28
842:28
843:28
844:28
845:28
846:28
847:28
848:28
849:28
850:28
851:28
852:28
853:28
854:28
855:28
856:28
857:28
858:28
859:28
860:28
861:28
862:28
863:28
864:28
865:28
866:28
867:28
868:28
869:28
870:28
871:28
872:28
873:28
874:28
875:28
876:28
877:28
878:28
879:28
880:28
881:28
882:28
883:28
884:28
885:28
886:28
887:28
888:28
889:28
890:28
891:28
892:28
893:28
894:28
895:28

## Event 20200805-1
In UTC
Date | Time | Freq
2020-08-04 | 23:02 | 49.954
2020-08-04 | 23:02 | 49.952
2020-08-04 | 23:02 | 49.95
2020-08-04 | 23:02 | 49.95
2020-08-04 | 23:02 | 49.949
2020-08-04 | 24:02 | 49.949
2020-08-04 | 25:02 | 49.95
2020-08-04 | 26:02 | 49.953
2020-08-04 | 27:02 | 49.952
2020-08-04 | 28:02 | 49.951
2020-08-04 | 29:02 | 49.948
2020-08-04 | 30:02 | 49.947
2020-08-04 | 31:02 | 49.944
2020-08-04 | 32:02 | 49.944
2020-08-04 | 33:02 | 49.943
2020-08-04 | 34:02 | 49.944
2020-08-04 | 35:02 | 49.946
2020-08-04 | 36:02 | 49.947
2020-08-04 | 37:02 | 49.948
2020-08-04 | 38:02 | 49.952
2020-08-04 | 39:02 | 49.957
2020-08-04 | 40:02 | 49.962
2020-08-04 | 41:02 | 49.963
2020-08-04 | 42:02 | 49.963
2020-08-04 | 43:02 | 49.96
2020-08-04 | 44:02 | 49.956
2020-08-04 | 45:02 | 49.952
2020-08-04 | 46:02 | 49.949
2020-08-04 | 47:02 | 49.949
2020-08-04 | 48:02 | 49.949
2020-08-04 | 49:02 | 49.949
2020-08-04 | 50:02 | 49.951
2020-08-04 | 51:02 | 49.95
2020-08-04 | 52:02 | 49.952
2020-08-04 | 53:02 | 49.953
2020-08-04 | 54:02 | 49.954
2020-08-04 | 55:02 | 49.954
2020-08-04 | 56:02 | 49.957
2020-08-04 | 57:02 | 49.958
2020-08-04 | 58:02 | 49.959
2020-08-04 | 59:02 | 49.96
2020-08-04 | 60:02 | 49.962
2020-08-04 | 61:02 | 49.963
2020-08-04 | 62:02 | 49.963
2020-08-04 | 63:02 | 49.965
2020-08-04 | 64:02 | 49.965
2020-08-04 | 65:02 | 49.963
2020-08-04 | 66:02 | 49.959
2020-08-04 | 67:02 | 49.957
2020-08-04 | 68:02 | 49.953
2020-08-04 | 69:02 | 49.951
2020-08-04 | 70:02 | 49.95
2020-08-04 | 71:02 | 49.955
2020-08-04 | 72:02 | 49.96
2020-08-04 | 73:02 | 49.968
2020-08-04 | 74:02 | 49.973
2020-08-04 | 75:02 | 49.976
2020-08-04 | 76:02 | 49.977
2020-08-04 | 77:02 | 49.976
2020-08-04 | 78:02 | 49.974
2020-08-04 | 79:02 | 49.972
2020-08-04 | 80:02 | 49.965
2020-08-04 | 81:02 | 49.959
2020-08-04 | 82:02 | 49.957
2020-08-04 | 83:02 | 49.958
2020-08-04 | 84:02 | 49.962
2020-08-04 | 85:02 | 49.967
2020-08-04 | 86:02 | 49.969
2020-08-04 | 87:02 | 49.973
2020-08-04 | 88:02 | 49.974
2020-08-04 | 89:02 | 49.976
2020-08-04 | 90:02 | 49.977
2020-08-04 | 91:02 | 49.977
2020-08-04 | 92:02 | 49.977
2020-08-04 | 93:02 | 49.974
2020-08-04 | 94:02 | 49.969
2020-08-04 | 95:02 | 49.966
2020-08-04 | 96:02 | 49.965
2020-08-04 | 97:02 | 49.964
2020-08-04 | 98:02 | 49.964
2020-08-04 | 99:02 | 49.965
2020-08-04 | 100:02 | 49.965
2020-08-04 | 101:02 | 49.964
2020-08-04 | 102:02 | 49.963
2020-08-04 | 103:02 | 49.964
2020-08-04 | 104:02 | 49.967
2020-08-04 | 105:02 | 49.968
2020-08-04 | 106:02 | 49.969
2020-08-04 | 107:02 | 50.019
2020-08-04 | 108:02 | 50.072
2020-08-04 | 109:02 | 50.106
2020-08-04 | 110:02 | 50.127
2020-08-04 | 111:02 | 50.139
2020-08-04 | 112:02 | 50.146
2020-08-04 | 113:02 | 50.145
2020-08-04 | 114:02 | 50.146
2020-08-04 | 115:02 | 50.146
2020-08-04 | 116:02 | 50.145
2020-08-04 | 117:02 | 50.145
2020-08-04 | 118:02 | 50.148
2020-08-04 | 119:02 | 50.155
2020-08-04 | 120:02 | 50.161
2020-08-04 | 121:02 | 50.164
2020-08-04 | 122:02 | 50.165
2020-08-04 | 123:02 | 50.165
2020-08-04 | 124:02 | 50.166
2020-08-04 | 125:02 | 50.168
2020-08-04 | 126:02 | 50.169
2020-08-04 | 127:02 | 50.171
2020-08-04 | 128:02 | 50.174
2020-08-04 | 129:02 | 50.177
2020-08-04 | 130:02 | 50.181
2020-08-04 | 131:02 | 50.183
2020-08-04 | 132:02 | 50.185
2020-08-04 | 133:02 | 50.184
2020-08-04 | 134:02 | 50.183
2020-08-04 | 135:02 | 50.182
2020-08-04 | 136:02 | 50.18
2020-08-04 | 137:02 | 50.18
2020-08-04 | 138:02 | 50.178
2020-08-04 | 139:02 | 50.178
2020-08-04 | 140:02 | 50.178
2020-08-04 | 141:02 | 50.179
2020-08-04 | 142:02 | 50.179
2020-08-04 | 143:02 | 50.181
2020-08-04 | 144:02 | 50.18
2020-08-04 | 145:02 | 50.179
2020-08-04 | 146:02 | 50.177
2020-08-04 | 147:02 | 50.175
2020-08-04 | 148:02 | 50.173
2020-08-04 | 149:02 | 50.173
2020-08-04 | 150:02 | 50.177
2020-08-04 | 151:02 | 50.179
2020-08-04 | 152:02 | 50.179
2020-08-04 | 153:02 | 50.172
2020-08-04 | 154:02 | 50.166
2020-08-04 | 155:02 | 50.163
2020-08-04 | 156:02 | 50.16
2020-08-04 | 157:02 | 50.159
2020-08-04 | 158:02 | 50.16
2020-08-04 | 159:02 | 50.16
2020-08-04 | 160:02 | 50.165
2020-08-04 | 161:02 | 50.173
2020-08-04 | 162:02 | 50.174
2020-08-04 | 163:02 | 50.175
2020-08-04 | 164:02 | 50.175
2020-08-04 | 165:02 | 50.173
2020-08-04 | 166:02 | 50.171
2020-08-04 | 167:02 | 50.172
2020-08-04 | 168:02 | 50.172
2020-08-04 | 169:02 | 50.173
2020-08-04 | 170:02 | 50.171
2020-08-04 | 171:02 | 50.171
2020-08-04 | 172:02 | 50.172
2020-08-04 | 173:02 | 50.17
2020-08-04 | 174:02 | 50.167
2020-08-04 | 175:02 | 50.165
2020-08-04 | 176:02 | 50.165
2020-08-04 | 177:02 | 50.166
2020-08-04 | 178:02 | 50.166
2020-08-04 | 179:02 | 50.169
2020-08-04 | 180:02 | 50.17
2020-08-04 | 181:02 | 50.17
2020-08-04 | 182:02 | 50.172
2020-08-04 | 183:02 | 50.178
2020-08-04 | 184:02 | 50.187
2020-08-04 | 185:02 | 50.194
2020-08-04 | 186:02 | 50.198
2020-08-04 | 187:02 | 50.201
2020-08-04 | 188:02 | 50.201
2020-08-04 | 189:02 | 50.201
2020-08-04 | 190:02 | 50.199
2020-08-04 | 191:02 | 50.199
2020-08-04 | 192:02 | 50.203
2020-08-04 | 193:02 | 50.207
2020-08-04 | 194:02 | 50.211
2020-08-04 | 195:02 | 50.215
2020-08-04 | 196:02 | 50.218
2020-08-04 | 197:02 | 50.221
2020-08-04 | 198:02 | 50.224
2020-08-04 | 199:02 | 50.228
2020-08-04 | 200:02 | 50.231
2020-08-04 | 201:02 | 50.231
2020-08-04 | 202:02 | 50.229
2020-08-04 | 203:02 | 50.228
2020-08-04 | 204:02 | 50.228
2020-08-04 | 205:02 | 50.227
2020-08-04 | 206:02 | 50.226
2020-08-04 | 207:02 | 50.226
2020-08-04 | 208:02 | 50.226
2020-08-04 | 209:02 | 50.223
2020-08-04 | 210:02 | 50.222
2020-08-04 | 211:02 | 50.223
2020-08-04 | 212:02 | 50.227
2020-08-04 | 213:02 | 50.23
2020-08-04 | 214:02 | 50.233
2020-08-04 | 215:02 | 50.237
2020-08-04 | 216:02 | 50.239
2020-08-04 | 217:02 | 50.24
2020-08-04 | 218:02 | 50.24
2020-08-04 | 219:02 | 50.24
2020-08-04 | 220:02 | 50.239
2020-08-04 | 221:02 | 50.241
2020-08-04 | 222:02 | 50.243
2020-08-04 | 223:02 | 50.247
2020-08-04 | 224:02 | 50.25
2020-08-04 | 225:02 | 50.253
2020-08-04 | 226:02 | 50.256
2020-08-04 | 227:02 | 50.256
2020-08-04 | 228:02 | 50.259
2020-08-04 | 229:02 | 50.26
2020-08-04 | 230:02 | 50.259
2020-08-04 | 231:02 | 50.26
2020-08-04 | 232:02 | 50.263
2020-08-04 | 233:02 | 50.265
2020-08-04 | 234:02 | 50.265
2020-08-04 | 235:02 | 50.265
2020-08-04 | 236:02 | 50.264
2020-08-04 | 237:02 | 50.262
2020-08-04 | 238:02 | 50.262
2020-08-04 | 239:02 | 50.262
2020-08-04 | 240:02 | 50.26
2020-08-04 | 241:02 | 50.26
2020-08-04 | 242:02 | 50.263
2020-08-04 | 243:02 | 50.266
2020-08-04 | 244:02 | 50.27
2020-08-04 | 245:02 | 50.275
2020-08-04 | 246:02 | 50.278
2020-08-04 | 247:02 | 50.28
2020-08-04 | 248:02 | 50.285
2020-08-04 | 249:02 | 50.287
2020-08-04 | 250:02 | 50.291
2020-08-04 | 251:02 | 50.294
2020-08-04 | 252:02 | 50.293
2020-08-04 | 253:02 | 50.289
2020-08-04 | 254:02 | 50.284
2020-08-04 | 255:02 | 50.282
2020-08-04 | 256:02 | 50.282
2020-08-04 | 257:02 | 50.28
2020-08-04 | 258:02 | 50.28
2020-08-04 | 259:02 | 50.279
2020-08-04 | 260:02 | 50.276
2020-08-04 | 261:02 | 50.272
2020-08-04 | 262:02 | 50.269
2020-08-04 | 263:02 | 50.271
2020-08-04 | 264:02 | 50.272
2020-08-04 | 265:02 | 50.273
2020-08-04 | 266:02 | 50.273
2020-08-04 | 267:02 | 50.275
2020-08-04 | 268:02 | 50.276
2020-08-04 | 269:02 | 50.277
2020-08-04 | 270:02 | 50.277
2020-08-04 | 271:02 | 50.279
2020-08-04 | 272:02 | 50.281
2020-08-04 | 273:02 | 50.282
2020-08-04 | 274:02 | 50.282
2020-08-04 | 275:02 | 50.286
2020-08-04 | 276:02 | 50.289
2020-08-04 | 277:02 | 50.291
2020-08-04 | 278:02 | 50.291
2020-08-04 | 279:02 | 50.288
2020-08-04 | 280:02 | 50.284
2020-08-04 | 281:02 | 50.281
2020-08-04 | 282:02 | 50.282
2020-08-04 | 283:02 | 50.284
2020-08-04 | 284:02 | 50.285
2020-08-04 | 285:02 | 50.285
2020-08-04 | 286:02 | 50.284
2020-08-04 | 287:02 | 50.285
2020-08-04 | 288:02 | 50.289
2020-08-04 | 289:02 | 50.294
2020-08-04 | 290:02 | 50.297
2020-08-04 | 291:02 | 50.298
2020-08-04 | 292:02 | 50.296
2020-08-04 | 293:02 | 50.293
2020-08-04 | 294:02 | 50.291
2020-08-04 | 295:02 | 50.288
2020-08-04 | 296:02 | 50.292
2020-08-04 | 297:02 | 50.295
2020-08-04 | 298:02 | 50.297
2020-08-04 | 299:02 | 50.296
2020-08-04 | 300:02 | 50.297
2020-08-04 | 301:02 | 50.296
2020-08-04 | 302:02 | 50.297
2020-08-04 | 303:02 | 50.298
2020-08-04 | 304:02 | 50.295
2020-08-04 | 305:02 | 50.291
2020-08-04 | 306:02 | 50.286
2020-08-04 | 307:02 | 50.283
2020-08-04 | 308:02 | 50.281
2020-08-04 | 309:02 | 50.279
2020-08-04 | 310:02 | 50.279
2020-08-04 | 311:02 | 50.28
2020-08-04 | 312:02 | 50.283
2020-08-04 | 313:02 | 50.285
2020-08-04 | 314:02 | 50.285
2020-08-04 | 315:02 | 50.284
2020-08-04 | 316:02 | 50.282
2020-08-04 | 317:02 | 50.28
2020-08-04 | 318:02 | 50.275
2020-08-04 | 319:02 | 50.268
2020-08-04 | 320:02 | 50.262
2020-08-04 | 321:02 | 50.255
2020-08-04 | 322:02 | 50.251
2020-08-04 | 323:02 | 50.247
2020-08-04 | 324:02 | 50.241
2020-08-04 | 325:02 | 50.229
2020-08-04 | 326:02 | 50.215
2020-08-04 | 327:02 | 50.202
2020-08-04 | 328:02 | 50.194
2020-08-04 | 329:02 | 50.187
2020-08-04 | 330:02 | 50.182
2020-08-04 | 331:02 | 50.18
2020-08-04 | 332:02 | 50.182
2020-08-04 | 333:02 | 50.18
2020-08-04 | 334:02 | 50.179
2020-08-04 | 335:02 | 50.171
2020-08-04 | 336:02 | 50.162
2020-08-04 | 337:02 | 50.151
2020-08-04 | 338:02 | 50.144
2020-08-04 | 339:02 | 50.138
2020-08-04 | 340:02 | 50.136
2020-08-04 | 341:02 | 50.134
2020-08-04 | 342:02 | 50.134
2020-08-04 | 343:02 | 50.136
2020-08-04 | 344:02 | 50.138
2020-08-04 | 345:02 | 50.14
2020-08-04 | 346:02 | 50.141
2020-08-04 | 347:02 | 50.141
2020-08-04 | 348:02 | 50.141
2020-08-04 | 349:02 | 50.139
2020-08-04 | 350:02 | 50.138
2020-08-04 | 351:02 | 50.136
2020-08-04 | 352:02 | 50.133
2020-08-04 | 353:02 | 50.13
2020-08-04 | 354:02 | 50.126
2020-08-04 | 355:02 | 50.122
2020-08-04 | 356:02 | 50.117
2020-08-04 | 357:02 | 50.113
2020-08-04 | 358:02 | 50.107
2020-08-04 | 359:02 | 50.102
2020-08-04 | 360:02 | 50.097
2020-08-04 | 361:02 | 50.094
2020-08-04 | 362:02 | 50.092
2020-08-04 | 363:02 | 50.089
2020-08-04 | 364:02 | 50.088
2020-08-04 | 365:02 | 50.087
2020-08-04 | 366:02 | 50.086
2020-08-04 | 367:02 | 50.084
2020-08-04 | 368:02 | 50.081
2020-08-04 | 369:02 | 50.077
2020-08-04 | 370:02 | 50.072
2020-08-04 | 371:02 | 50.068
2020-08-04 | 372:02 | 50.066
2020-08-04 | 373:02 | 50.065
2020-08-04 | 374:02 | 50.064
2020-08-04 | 375:02 | 50.063
2020-08-04 | 376:02 | 50.063
2020-08-04 | 377:02 | 50.062
2020-08-04 | 378:02 | 50.059
2020-08-04 | 379:02 | 50.055
2020-08-04 | 380:02 | 50.049
2020-08-04 | 381:02 | 50.044
2020-08-04 | 382:02 | 50.04
2020-08-04 | 383:02 | 50.036
2020-08-04 | 384:02 | 50.033
2020-08-04 | 385:02 | 50.03
2020-08-04 | 386:02 | 50.027
2020-08-04 | 387:02 | 50.024
2020-08-04 | 388:02 | 50.022
2020-08-04 | 389:02 | 50.023
2020-08-04 | 390:02 | 50.025
2020-08-04 | 391:02 | 50.027
2020-08-04 | 392:02 | 50.028
2020-08-04 | 393:02 | 50.03
2020-08-04 | 394:02 | 50.032
2020-08-04 | 395:02 | 50.036
2020-08-04 | 396:02 | 50.038
2020-08-04 | 397:02 | 50.04
2020-08-04 | 398:02 | 50.042
2020-08-04 | 399:02 | 50.045
2020-08-04 | 400:02 | 50.045
2020-08-04 | 401:02 | 50.046
2020-08-04 | 402:02 | 50.046
2020-08-04 | 403:02 | 50.046
2020-08-04 | 404:02 | 50.045
2020-08-04 | 405:02 | 50.045
2020-08-04 | 406:02 | 50.046
2020-08-04 | 407:02 | 50.044
2020-08-04 | 408:02 | 50.043
2020-08-04 | 409:02 | 50.042
2020-08-04 | 410:02 | 50.042
2020-08-04 | 411:02 | 50.043
2020-08-04 | 412:02 | 50.043
2020-08-04 | 413:02 | 50.042
2020-08-04 | 414:02 | 50.041
2020-08-04 | 415:02 | 50.04
2020-08-04 | 416:02 | 50.039
2020-08-04 | 417:02 | 50.038
2020-08-04 | 418:02 | 50.038
2020-08-04 | 419:02 | 50.04
2020-08-04 | 420:02 | 50.039
2020-08-04 | 421:02 | 50.039
2020-08-04 | 422:02 | 50.04
2020-08-04 | 423:02 | 50.042
2020-08-04 | 424:02 | 50.044
2020-08-04 | 425:02 | 50.044
2020-08-04 | 426:02 | 50.043
2020-08-04 | 427:02 | 50.045
2020-08-04 | 428:02 | 50.043
2020-08-04 | 429:02 | 50.04
2020-08-04 | 430:02 | 50.035
2020-08-04 | 431:02 | 50.031
2020-08-04 | 432:02 | 50.026
2020-08-04 | 433:02 | 50.023
2020-08-04 | 434:02 | 50.023
2020-08-04 | 435:02 | 50.017
2020-08-04 | 436:02 | 50.01
2020-08-04 | 437:02 | 49.998
2020-08-04 | 438:02 | 49.988
439:02
440:02
441:02
442:02
443:02
444:02
445:02
446:02
447:02
448:02
449:02
450:02
451:02
452:02
453:02
454:02
455:02
456:02
457:02
458:02
459:02
460:02
461:02
462:02
463:02
464:02
465:02
466:02
467:02
468:02
469:02
470:02
471:02
472:02
473:02
474:02
475:02
476:02
477:02
478:02
479:02
480:02
481:02
482:02
483:02
484:02
485:02
486:02
487:02
488:02
489:02
490:02
491:02
492:02
493:02
494:02
495:02
496:02
497:02
498:02
499:02
500:02
501:02
502:02
503:02
504:02
505:02
506:02
507:02
508:02
509:02
510:02
511:02
512:02
513:02
514:02
515:02
516:02
517:02
518:02
519:02
520:02
521:02
522:02
523:02
524:02
525:02
526:02
527:02
528:02
529:02
530:02
531:02
532:02
533:02
534:02
535:02
536:02
537:02
538:02
539:02
540:02
541:02
542:02
543:02
544:02
545:02
546:02
547:02
548:02
549:02
550:02
551:02
552:02
553:02
554:02
555:02
556:02
557:02
558:02
559:02
560:02
561:02
562:02
563:02
564:02
565:02
566:02
567:02
568:02
569:02
570:02
571:02
572:02
573:02
574:02
575:02
576:02
577:02
578:02
579:02
580:02
581:02
582:02
583:02
584:02
585:02
586:02
587:02
588:02
589:02
590:02
591:02
592:02
593:02
594:02
595:02
596:02
597:02
598:02
599:02
600:02
601:02
602:02
603:02
604:02
605:02
606:02
607:02
608:02
609:02
610:02
611:02
612:02
613:02
614:02
615:02
616:02
617:02
618:02
619:02
620:02
621:02
622:02
623:02
624:02
625:02
626:02
627:02
628:02
629:02
630:02
631:02
632:02
633:02
634:02
635:02
636:02
637:02
638:02
639:02
640:02
641:02
642:02
643:02
644:02
645:02
646:02
647:02
648:02
649:02
650:02
651:02
652:02
653:02
654:02
655:02
656:02
657:02
658:02
659:02
660:02
661:02
662:02
663:02
664:02
665:02
666:02
667:02
668:02
669:02
670:02
671:02
672:02
673:02
674:02
675:02
676:02
677:02
678:02
679:02
680:02
681:02
682:02
683:02
684:02
685:02
686:02
687:02
688:02
689:02
690:02
691:02
692:02
693:02
694:02
695:02
696:02
697:02
698:02
699:02
700:02
701:02
702:02
703:02
704:02
705:02
706:02
707:02
708:02
709:02
710:02
711:02
712:02
713:02
714:02
715:02
716:02
717:02
718:02
719:02
720:02
721:02
722:02
723:02
724:02
725:02
726:02
727:02
728:02
729:02
730:02
731:02
732:02
733:02
734:02
735:02
736:02
737:02
738:02
739:02
740:02
741:02
742:02
743:02
744:02
745:02
746:02
747:02
748:02
749:02
750:02
751:02
752:02
753:02
754:02
755:02
756:02
757:02
758:02
759:02
760:02
761:02
762:02
763:02
764:02
765:02
766:02
767:02
768:02
769:02
770:02
771:02
772:02
773:02
774:02
775:02
776:02
777:02
778:02
779:02
780:02
781:02
782:02
783:02
784:02
785:02
786:02
787:02
788:02
789:02
790:02
791:02
792:02
793:02
794:02
795:02
796:02
797:02
798:02
799:02
800:02
801:02
802:02
803:02
804:02
805:02
806:02
807:02
808:02
809:02
810:02
811:02
812:02
813:02
814:02
815:02
816:02
817:02
818:02
819:02
820:02
821:02
822:02
823:02
824:02
825:02
826:02
827:02
828:02
829:02
830:02
831:02
832:02
833:02
834:02
835:02
836:02
837:02
838:02
839:02
840:02
841:02
842:02
843:02
844:02
845:02
846:02
847:02
848:02
849:02
850:02
851:02
852:02
853:02
854:02
855:02
856:02
857:02
858:02
859:02
860:02
861:02
862:02
863:02
864:02
865:02
866:02
867:02
868:02
869:02
870:02
871:02
872:02
873:02
874:02
875:02
876:02
877:02
878:02
879:02
880:02
881:02
882:02
883:02
884:02
885:02
886:02
887:02
888:02
889:02
890:02
891:02
892:02
893:02
894:02
895:02
896:02
897:02
898:02
899:02
900:02
901:02
902:02
903:02
904:02
905:02
906:02
907:02
908:02
909:02
910:02
911:02
912:02
913:02
914:02
915:02
916:02
917:02
918:02

## Event 20200806-1
In UTC
Date | Time | Freq
2020-08-06 | 18:24 | 50.051
2020-08-06 | 18:24 | 50.047
2020-08-06 | 18:24 | 50.048
2020-08-06 | 18:24 | 50.048
2020-08-06 | 18:24 | 50.046
2020-08-06 | 19:24 | 50.046
2020-08-06 | 20:24 | 50.045
2020-08-06 | 21:24 | 50.044
2020-08-06 | 22:24 | 50.045
2020-08-06 | 23:24 | 50.042
2020-08-06 | 24:24 | 50.039
2020-08-06 | 25:24 | 50.039
2020-08-06 | 26:24 | 50.039
2020-08-06 | 27:24 | 50.039
2020-08-06 | 28:24 | 50.036
2020-08-06 | 29:24 | 50.034
2020-08-06 | 30:24 | 50.032
2020-08-06 | 31:24 | 50.032
2020-08-06 | 32:24 | 50.031
2020-08-06 | 33:24 | 50.031
2020-08-06 | 34:24 | 50.03
2020-08-06 | 35:24 | 50.029
2020-08-06 | 36:24 | 50.028
2020-08-06 | 37:24 | 50.027
2020-08-06 | 38:24 | 50.027
2020-08-06 | 39:24 | 50.025
2020-08-06 | 40:24 | 50.024
2020-08-06 | 41:24 | 50.023
2020-08-06 | 42:24 | 50.025
2020-08-06 | 43:24 | 50.025
2020-08-06 | 44:24 | 50.025
2020-08-06 | 45:24 | 50.024
2020-08-06 | 46:24 | 50.023
2020-08-06 | 47:24 | 50.022
2020-08-06 | 48:24 | 50.014
2020-08-06 | 49:24 | 50.005
2020-08-06 | 50:24 | 49.99
2020-08-06 | 51:24 | 49.977
2020-08-06 | 52:24 | 49.963
2020-08-06 | 53:24 | 49.949
2020-08-06 | 54:24 | 49.939
2020-08-06 | 55:24 | 49.933
2020-08-06 | 56:24 | 49.934
2020-08-06 | 57:24 | 49.942
2020-08-06 | 58:24 | 49.952
2020-08-06 | 59:24 | 49.962
2020-08-06 | 60:24 | 49.972
2020-08-06 | 61:24 | 49.974
2020-08-06 | 62:24 | 49.979
2020-08-06 | 63:24 | 49.982
2020-08-06 | 64:24 | 49.986
2020-08-06 | 65:24 | 49.989
2020-08-06 | 66:24 | 49.994
2020-08-06 | 67:24 | 49.998
2020-08-06 | 68:24 | 50.004
2020-08-06 | 69:24 | 50.006
2020-08-06 | 70:24 | 50.007
2020-08-06 | 71:24 | 50.005
2020-08-06 | 72:24 | 50.004
2020-08-06 | 73:24 | 50
2020-08-06 | 74:24 | 49.998
2020-08-06 | 75:24 | 49.997
2020-08-06 | 76:24 | 49.997
2020-08-06 | 77:24 | 49.998
2020-08-06 | 78:24 | 50.003
2020-08-06 | 79:24 | 50.008
2020-08-06 | 80:24 | 50.011
2020-08-06 | 81:24 | 50.014
2020-08-06 | 82:24 | 50.005
2020-08-06 | 83:24 | 49.995
2020-08-06 | 84:24 | 49.982
2020-08-06 | 85:24 | 49.97
2020-08-06 | 86:24 | 49.964
2020-08-06 | 87:24 | 49.959
2020-08-06 | 88:24 | 49.956
2020-08-06 | 89:24 | 49.952
2020-08-06 | 90:24 | 49.954
2020-08-06 | 91:24 | 49.954
2020-08-06 | 92:24 | 49.956
2020-08-06 | 93:24 | 49.957
2020-08-06 | 94:24 | 49.958
2020-08-06 | 95:24 | 49.96
2020-08-06 | 96:24 | 49.963
2020-08-06 | 97:24 | 49.966
2020-08-06 | 98:24 | 49.967
2020-08-06 | 99:24 | 49.968
2020-08-06 | 100:24 | 49.963
2020-08-06 | 101:24 | 49.961
2020-08-06 | 102:24 | 49.958
2020-08-06 | 103:24 | 49.953
2020-08-06 | 104:24 | 49.951
2020-08-06 | 105:24 | 49.946
2020-08-06 | 106:24 | 49.941
2020-08-06 | 107:24 | 49.939
2020-08-06 | 108:24 | 49.937
2020-08-06 | 109:24 | 49.937
2020-08-06 | 110:24 | 49.936
2020-08-06 | 111:24 | 49.937
2020-08-06 | 112:24 | 49.94
2020-08-06 | 113:24 | 49.943
2020-08-06 | 114:24 | 49.949
2020-08-06 | 115:24 | 49.952
2020-08-06 | 116:24 | 49.956
2020-08-06 | 117:24 | 49.959
2020-08-06 | 118:24 | 49.961
2020-08-06 | 119:24 | 49.96
2020-08-06 | 120:24 | 49.96
2020-08-06 | 121:24 | 49.959
2020-08-06 | 122:24 | 49.958
2020-08-06 | 123:24 | 49.956
2020-08-06 | 124:24 | 49.956
2020-08-06 | 125:24 | 49.954
2020-08-06 | 126:24 | 49.952
2020-08-06 | 127:24 | 49.953
2020-08-06 | 128:24 | 49.953
2020-08-06 | 129:24 | 49.955
2020-08-06 | 130:24 | 49.954
2020-08-06 | 131:24 | 49.954
2020-08-06 | 132:24 | 49.952
2020-08-06 | 133:24 | 49.949
2020-08-06 | 134:24 | 49.948
2020-08-06 | 135:24 | 49.944
2020-08-06 | 136:24 | 49.941
2020-08-06 | 137:24 | 49.938
2020-08-06 | 138:24 | 49.936
2020-08-06 | 139:24 | 49.933
2020-08-06 | 140:24 | 49.932
2020-08-06 | 141:24 | 49.93
2020-08-06 | 142:24 | 49.931
2020-08-06 | 143:24 | 49.93
2020-08-06 | 144:24 | 49.927
2020-08-06 | 145:24 | 49.924
2020-08-06 | 146:24 | 49.925
2020-08-06 | 147:24 | 49.925
2020-08-06 | 148:24 | 49.923
2020-08-06 | 149:24 | 49.922
2020-08-06 | 150:24 | 49.922
2020-08-06 | 151:24 | 49.922
2020-08-06 | 152:24 | 49.923
2020-08-06 | 153:24 | 49.925
2020-08-06 | 154:24 | 49.925
2020-08-06 | 155:24 | 49.923
2020-08-06 | 156:24 | 49.92
2020-08-06 | 157:24 | 49.919
2020-08-06 | 158:24 | 49.916
2020-08-06 | 159:24 | 49.913
2020-08-06 | 160:24 | 49.912
2020-08-06 | 161:24 | 49.914
2020-08-06 | 162:24 | 49.916
2020-08-06 | 163:24 | 49.915
2020-08-06 | 164:24 | 49.915
2020-08-06 | 165:24 | 49.916
2020-08-06 | 166:24 | 49.914
2020-08-06 | 167:24 | 49.915
2020-08-06 | 168:24 | 49.914
2020-08-06 | 169:24 | 49.912
2020-08-06 | 170:24 | 49.91
2020-08-06 | 171:24 | 49.911
2020-08-06 | 172:24 | 49.912
2020-08-06 | 173:24 | 49.914
2020-08-06 | 174:24 | 49.915
2020-08-06 | 175:24 | 49.918
2020-08-06 | 176:24 | 49.919
2020-08-06 | 177:24 | 49.919
2020-08-06 | 178:24 | 49.921
2020-08-06 | 179:24 | 49.918
2020-08-06 | 180:24 | 49.916
2020-08-06 | 181:24 | 49.915
2020-08-06 | 182:24 | 49.912
2020-08-06 | 183:24 | 49.912
2020-08-06 | 184:24 | 49.912
2020-08-06 | 185:24 | 49.915
2020-08-06 | 186:24 | 49.917
2020-08-06 | 187:24 | 49.92
2020-08-06 | 188:24 | 49.92
2020-08-06 | 189:24 | 49.922
2020-08-06 | 190:24 | 49.923
2020-08-06 | 191:24 | 49.92
2020-08-06 | 192:24 | 49.918
2020-08-06 | 193:24 | 49.917
2020-08-06 | 194:24 | 49.914
2020-08-06 | 195:24 | 49.912
2020-08-06 | 196:24 | 49.909
2020-08-06 | 197:24 | 49.904
2020-08-06 | 198:24 | 49.898
2020-08-06 | 199:24 | 49.896
2020-08-06 | 200:24 | 49.893
2020-08-06 | 201:24 | 49.891
2020-08-06 | 202:24 | 49.891
2020-08-06 | 203:24 | 49.892
2020-08-06 | 204:24 | 49.892
2020-08-06 | 205:24 | 49.891
2020-08-06 | 206:24 | 49.892
2020-08-06 | 207:24 | 49.892
2020-08-06 | 208:24 | 49.891
2020-08-06 | 209:24 | 49.892
2020-08-06 | 210:24 | 49.891
2020-08-06 | 211:24 | 49.889
2020-08-06 | 212:24 | 49.889
2020-08-06 | 213:24 | 49.888
2020-08-06 | 214:24 | 49.888
2020-08-06 | 215:24 | 49.89
2020-08-06 | 216:24 | 49.891
2020-08-06 | 217:24 | 49.893
2020-08-06 | 218:24 | 49.893
2020-08-06 | 219:24 | 49.891
2020-08-06 | 220:24 | 49.892
2020-08-06 | 221:24 | 49.894
2020-08-06 | 222:24 | 49.891
2020-08-06 | 223:24 | 49.889
2020-08-06 | 224:24 | 49.884
2020-08-06 | 225:24 | 49.881
2020-08-06 | 226:24 | 49.879
2020-08-06 | 227:24 | 49.877
2020-08-06 | 228:24 | 49.875
2020-08-06 | 229:24 | 49.874
2020-08-06 | 230:24 | 49.873
2020-08-06 | 231:24 | 49.873
2020-08-06 | 232:24 | 49.874
2020-08-06 | 233:24 | 49.873
2020-08-06 | 234:24 | 49.869
2020-08-06 | 235:24 | 49.868
2020-08-06 | 236:24 | 49.866
2020-08-06 | 237:24 | 49.865
2020-08-06 | 238:24 | 49.865
2020-08-06 | 239:24 | 49.865
2020-08-06 | 240:24 | 49.865
2020-08-06 | 241:24 | 49.867
2020-08-06 | 242:24 | 49.868
2020-08-06 | 243:24 | 49.872
2020-08-06 | 244:24 | 49.873
2020-08-06 | 245:24 | 49.877
2020-08-06 | 246:24 | 49.88
2020-08-06 | 247:24 | 49.88
2020-08-06 | 248:24 | 49.882
2020-08-06 | 249:24 | 49.884
2020-08-06 | 250:24 | 49.885
2020-08-06 | 251:24 | 49.884
2020-08-06 | 252:24 | 49.886
2020-08-06 | 253:24 | 49.885
2020-08-06 | 254:24 | 49.885
2020-08-06 | 255:24 | 49.882
2020-08-06 | 256:24 | 49.881
2020-08-06 | 257:24 | 49.881
2020-08-06 | 258:24 | 49.88
2020-08-06 | 259:24 | 49.878
2020-08-06 | 260:24 | 49.877
2020-08-06 | 261:24 | 49.873
2020-08-06 | 262:24 | 49.871
2020-08-06 | 263:24 | 49.864
2020-08-06 | 264:24 | 49.861
2020-08-06 | 265:24 | 49.858
2020-08-06 | 266:24 | 49.857
2020-08-06 | 267:24 | 49.855
2020-08-06 | 268:24 | 49.853
2020-08-06 | 269:24 | 49.85
2020-08-06 | 270:24 | 49.849
2020-08-06 | 271:24 | 49.848
2020-08-06 | 272:24 | 49.845
2020-08-06 | 273:24 | 49.844
2020-08-06 | 274:24 | 49.843
2020-08-06 | 275:24 | 49.842
2020-08-06 | 276:24 | 49.841
2020-08-06 | 277:24 | 49.84
2020-08-06 | 278:24 | 49.839
2020-08-06 | 279:24 | 49.843
2020-08-06 | 280:24 | 49.842
2020-08-06 | 281:24 | 49.839
2020-08-06 | 282:24 | 49.839
2020-08-06 | 283:24 | 49.841
2020-08-06 | 284:24 | 49.839
2020-08-06 | 285:24 | 49.84
2020-08-06 | 286:24 | 49.838
2020-08-06 | 287:24 | 49.84
2020-08-06 | 288:24 | 49.839
2020-08-06 | 289:24 | 49.839
2020-08-06 | 290:24 | 49.84
2020-08-06 | 291:24 | 49.841
2020-08-06 | 292:24 | 49.842
2020-08-06 | 293:24 | 49.847
2020-08-06 | 294:24 | 49.85
2020-08-06 | 295:24 | 49.85
2020-08-06 | 296:24 | 49.851
2020-08-06 | 297:24 | 49.852
2020-08-06 | 298:24 | 49.855
2020-08-06 | 299:24 | 49.858
2020-08-06 | 300:24 | 49.863
2020-08-06 | 301:24 | 49.864
2020-08-06 | 302:24 | 49.866
2020-08-06 | 303:24 | 49.865
2020-08-06 | 304:24 | 49.864
2020-08-06 | 305:24 | 49.861
2020-08-06 | 306:24 | 49.86
2020-08-06 | 307:24 | 49.858
2020-08-06 | 308:24 | 49.855
2020-08-06 | 309:24 | 49.851
2020-08-06 | 310:24 | 49.849
2020-08-06 | 311:24 | 49.848
2020-08-06 | 312:24 | 49.845
2020-08-06 | 313:24 | 49.846
2020-08-06 | 314:24 | 49.845
2020-08-06 | 315:24 | 49.841
2020-08-06 | 316:24 | 49.84
2020-08-06 | 317:24 | 49.84
2020-08-06 | 318:24 | 49.841
2020-08-06 | 319:24 | 49.844
2020-08-06 | 320:24 | 49.847
2020-08-06 | 321:24 | 49.85
2020-08-06 | 322:24 | 49.856
2020-08-06 | 323:24 | 49.862
2020-08-06 | 324:24 | 49.869
2020-08-06 | 325:24 | 49.874
2020-08-06 | 326:24 | 49.881
2020-08-06 | 327:24 | 49.885
2020-08-06 | 328:24 | 49.893
2020-08-06 | 329:24 | 49.902
2020-08-06 | 330:24 | 49.909
2020-08-06 | 331:24 | 49.917
2020-08-06 | 332:24 | 49.921
2020-08-06 | 333:24 | 49.925
2020-08-06 | 334:24 | 49.927
2020-08-06 | 335:24 | 49.927
2020-08-06 | 336:24 | 49.928
2020-08-06 | 337:24 | 49.929
2020-08-06 | 338:24 | 49.927
2020-08-06 | 339:24 | 49.925
2020-08-06 | 340:24 | 49.923
2020-08-06 | 341:24 | 49.925
2020-08-06 | 342:24 | 49.928
2020-08-06 | 343:24 | 49.932
2020-08-06 | 344:24 | 49.939
2020-08-06 | 345:24 | 49.942
2020-08-06 | 346:24 | 49.949
2020-08-06 | 347:24 | 49.953
2020-08-06 | 348:24 | 49.96
2020-08-06 | 349:24 | 49.963
2020-08-06 | 350:24 | 49.964
2020-08-06 | 351:24 | 49.966
2020-08-06 | 352:24 | 49.966
2020-08-06 | 353:24 | 49.966
2020-08-06 | 354:24 | 49.967
2020-08-06 | 355:24 | 49.967
2020-08-06 | 356:24 | 49.967
2020-08-06 | 357:24 | 49.969
2020-08-06 | 358:24 | 49.971
2020-08-06 | 359:24 | 49.973
2020-08-06 | 360:24 | 49.972
2020-08-06 | 361:24 | 49.972
2020-08-06 | 362:24 | 49.971
2020-08-06 | 363:24 | 49.972
2020-08-06 | 364:24 | 49.973
2020-08-06 | 365:24 | 49.975
2020-08-06 | 366:24 | 49.976
2020-08-06 | 367:24 | 49.976
2020-08-06 | 368:24 | 49.978
2020-08-06 | 369:24 | 49.981
2020-08-06 | 370:24 | 49.985
2020-08-06 | 371:24 | 49.983
2020-08-06 | 372:24 | 49.986
2020-08-06 | 373:24 | 49.988
2020-08-06 | 374:24 | 49.989
2020-08-06 | 375:24 | 49.99
2020-08-06 | 376:24 | 49.992
2020-08-06 | 377:24 | 49.994
2020-08-06 | 378:24 | 49.998
2020-08-06 | 379:24 | 50.002
2020-08-06 | 380:24 | 50.004
2020-08-06 | 381:24 | 50.005
2020-08-06 | 382:24 | 50.006
2020-08-06 | 383:24 | 50.005
2020-08-06 | 384:24 | 50.004
2020-08-06 | 385:24 | 50.004
2020-08-06 | 386:24 | 50.003
2020-08-06 | 387:24 | 50.002
2020-08-06 | 388:24 | 50.001
2020-08-06 | 389:24 | 50.001
2020-08-06 | 390:24 | 50
2020-08-06 | 391:24 | 49.999
2020-08-06 | 392:24 | 49.997
2020-08-06 | 393:24 | 49.995
2020-08-06 | 394:24 | 49.992
2020-08-06 | 395:24 | 49.991
2020-08-06 | 396:24 | 49.989
2020-08-06 | 397:24 | 49.988
2020-08-06 | 398:24 | 49.99
2020-08-06 | 399:24 | 49.992
2020-08-06 | 400:24 | 49.993
2020-08-06 | 401:24 | 49.996
2020-08-06 | 402:24 | 49.996
2020-08-06 | 403:24 | 49.999
2020-08-06 | 404:24 | 50.001
2020-08-06 | 405:24 | 50.003
2020-08-06 | 406:24 | 50.006
2020-08-06 | 407:24 | 50.01
2020-08-06 | 408:24 | 50.01
2020-08-06 | 409:24 | 50.009
2020-08-06 | 410:24 | 50.009
2020-08-06 | 411:24 | 50.007
2020-08-06 | 412:24 | 50.005
2020-08-06 | 413:24 | 50
2020-08-06 | 414:24 | 50
2020-08-06 | 415:24 | 49.997
2020-08-06 | 416:24 | 49.996
2020-08-06 | 417:24 | 49.996
2020-08-06 | 418:24 | 50
2020-08-06 | 419:24 | 50.001
2020-08-06 | 420:24 | 50.006
2020-08-06 | 421:24 | 50.005
2020-08-06 | 422:24 | 50.006
2020-08-06 | 423:24 | 50.003
2020-08-06 | 424:24 | 50
2020-08-06 | 425:24 | 49.995
2020-08-06 | 426:24 | 49.993
2020-08-06 | 427:24 | 49.989
2020-08-06 | 428:24 | 49.988
2020-08-06 | 429:24 | 49.986
2020-08-06 | 430:24 | 49.985
2020-08-06 | 431:24 | 49.985
2020-08-06 | 432:24 | 49.987
2020-08-06 | 433:24 | 49.988
434:24
435:24
436:24
437:24
438:24
439:24
440:24
441:24
442:24
443:24
444:24
445:24
446:24
447:24
448:24
449:24
450:24
451:24
452:24
453:24
454:24
455:24
456:24
457:24
458:24
459:24
460:24
461:24
462:24
463:24
464:24
465:24
466:24
467:24
468:24
469:24
470:24
471:24
472:24
473:24
474:24
475:24
476:24
477:24
478:24
479:24
480:24
481:24
482:24
483:24
484:24
485:24
486:24
487:24
488:24
489:24
490:24
491:24
492:24
493:24
494:24
495:24
496:24
497:24
498:24
499:24
500:24
501:24
502:24
503:24
504:24
505:24
506:24
507:24
508:24
509:24
510:24
511:24
512:24
513:24
514:24
515:24
516:24
517:24
518:24
519:24
520:24
521:24
522:24
523:24
524:24
525:24
526:24
527:24
528:24
529:24
530:24
531:24
532:24
533:24
534:24
535:24
536:24
537:24
538:24
539:24
540:24
541:24
542:24
543:24
544:24
545:24
546:24
547:24
548:24
549:24
550:24
551:24
552:24
553:24
554:24
555:24
556:24
557:24
558:24
559:24
560:24
561:24
562:24
563:24
564:24
565:24
566:24
567:24
568:24
569:24
570:24
571:24
572:24
573:24
574:24
575:24
576:24
577:24
578:24
579:24
580:24
581:24
582:24
583:24
584:24
585:24
586:24
587:24
588:24
589:24
590:24
591:24
592:24
593:24
594:24
595:24
596:24
597:24
598:24
599:24
600:24
601:24
602:24
603:24
604:24
605:24
606:24
607:24
608:24
609:24
610:24
611:24
612:24
613:24
614:24
615:24
616:24
617:24
618:24
619:24
620:24
621:24
622:24
623:24
624:24
625:24
626:24
627:24
628:24
629:24
630:24
631:24
632:24
633:24
634:24
635:24
636:24
637:24
638:24
639:24
640:24
641:24
642:24
643:24
644:24
645:24
646:24
647:24
648:24
649:24
650:24
651:24
652:24
653:24
654:24
655:24
656:24
657:24
658:24
659:24
660:24
661:24
662:24
663:24
664:24
665:24
666:24
667:24
668:24
669:24
670:24
671:24
672:24
673:24
674:24
675:24
676:24
677:24
678:24
679:24
680:24
681:24
682:24
683:24
684:24
685:24
686:24
687:24
688:24
689:24
690:24
691:24
692:24
693:24
694:24
695:24
696:24
697:24
698:24
699:24
700:24
701:24
702:24
703:24
704:24
705:24
706:24
707:24
708:24
709:24
710:24
711:24
712:24
713:24
714:24
715:24
716:24
717:24
718:24
719:24
720:24
721:24
722:24
723:24
724:24
725:24
726:24
727:24
728:24
729:24
730:24
731:24
732:24
733:24
734:24
735:24
736:24
737:24
738:24
739:24
740:24
741:24
742:24
743:24
744:24
745:24
746:24
747:24
748:24
749:24
750:24
751:24
752:24
753:24
754:24
755:24
756:24
757:24
758:24
759:24
760:24
761:24
762:24
763:24
764:24
765:24
766:24
767:24
768:24
769:24
770:24
771:24
772:24
773:24
774:24
775:24
776:24
777:24
778:24
779:24
780:24
781:24
782:24
783:24
784:24
785:24
786:24
787:24
788:24
789:24
790:24
791:24
792:24
793:24
794:24
795:24
796:24
797:24
798:24
799:24
800:24
801:24
802:24
803:24
804:24
805:24
806:24
807:24
808:24
809:24
810:24
811:24
812:24
813:24
814:24
815:24
816:24
817:24
818:24
819:24
820:24
821:24
822:24
823:24
824:24
825:24
826:24
827:24
828:24
829:24
830:24
831:24
832:24
833:24
834:24
835:24
836:24
837:24
838:24
839:24
840:24
841:24
842:24
843:24
844:24
845:24
846:24
847:24
848:24
849:24
850:24
851:24
852:24
853:24
854:24
855:24
856:24
857:24
858:24
859:24
860:24
861:24
862:24
863:24
864:24
865:24
866:24
867:24
868:24
869:24
870:24
871:24
872:24
873:24
874:24
875:24
876:24
877:24
878:24
879:24
880:24
881:24
882:24
883:24
884:24
885:24
886:24
887:24
888:24
889:24
890:24
891:24
892:24
893:24
894:24
895:24
896:24
897:24
898:24
899:24
900:24
901:24
902:24
903:24
904:24
905:24
906:24
907:24
908:24
909:24
910:24
911:24
912:24
913:24

## Event 20200807-1
In UTC
Date | Time | Freq
2020-08-07 | 21:51 | 49.931
2020-08-07 | 21:51 | 49.927
2020-08-07 | 21:51 | 49.925
2020-08-07 | 21:51 | 49.924
2020-08-07 | 21:51 | 49.92
2020-08-07 | 22:51 | 49.893
2020-08-07 | 23:51 | 49.869
2020-08-07 | 24:51 | 49.85
2020-08-07 | 25:51 | 49.837
2020-08-07 | 26:51 | 49.828
2020-08-07 | 27:51 | 49.82
2020-08-07 | 28:51 | 49.815
2020-08-07 | 29:51 | 49.811
2020-08-07 | 30:51 | 49.808
2020-08-07 | 31:51 | 49.806
2020-08-07 | 32:51 | 49.807
2020-08-07 | 33:51 | 49.807
2020-08-07 | 34:51 | 49.805
2020-08-07 | 35:51 | 49.806
2020-08-07 | 36:51 | 49.806
2020-08-07 | 37:51 | 49.805
2020-08-07 | 38:51 | 49.806
2020-08-07 | 39:51 | 49.806
2020-08-07 | 40:51 | 49.808
2020-08-07 | 41:51 | 49.809
2020-08-07 | 42:51 | 49.808
2020-08-07 | 43:51 | 49.808
2020-08-07 | 44:51 | 49.808
2020-08-07 | 45:51 | 49.807
2020-08-07 | 46:51 | 49.805
2020-08-07 | 47:51 | 49.805
2020-08-07 | 48:51 | 49.804
2020-08-07 | 49:51 | 49.801
2020-08-07 | 50:51 | 49.795
2020-08-07 | 51:51 | 49.789
2020-08-07 | 52:51 | 49.787
2020-08-07 | 53:51 | 49.786
2020-08-07 | 54:51 | 49.785
2020-08-07 | 55:51 | 49.781
2020-08-07 | 56:51 | 49.779
2020-08-07 | 57:51 | 49.779
2020-08-07 | 58:51 | 49.779
2020-08-07 | 59:51 | 49.779
2020-08-07 | 60:51 | 49.778
2020-08-07 | 61:51 | 49.78
2020-08-07 | 62:51 | 49.78
2020-08-07 | 63:51 | 49.781
2020-08-07 | 64:51 | 49.779
2020-08-07 | 65:51 | 49.777
2020-08-07 | 66:51 | 49.774
2020-08-07 | 67:51 | 49.773
2020-08-07 | 68:51 | 49.772
2020-08-07 | 69:51 | 49.773
2020-08-07 | 70:51 | 49.77
2020-08-07 | 71:51 | 49.768
2020-08-07 | 72:51 | 49.765
2020-08-07 | 73:51 | 49.764
2020-08-07 | 74:51 | 49.762
2020-08-07 | 75:51 | 49.759
2020-08-07 | 76:51 | 49.758
2020-08-07 | 77:51 | 49.756
2020-08-07 | 78:51 | 49.755
2020-08-07 | 79:51 | 49.754
2020-08-07 | 80:51 | 49.752
2020-08-07 | 81:51 | 49.751
2020-08-07 | 82:51 | 49.751
2020-08-07 | 83:51 | 49.752
2020-08-07 | 84:51 | 49.753
2020-08-07 | 85:51 | 49.753
2020-08-07 | 86:51 | 49.753
2020-08-07 | 87:51 | 49.752
2020-08-07 | 88:51 | 49.753
2020-08-07 | 89:51 | 49.751
2020-08-07 | 90:51 | 49.752
2020-08-07 | 91:51 | 49.752
2020-08-07 | 92:51 | 49.756
2020-08-07 | 93:51 | 49.76
2020-08-07 | 94:51 | 49.761
2020-08-07 | 95:51 | 49.764
2020-08-07 | 96:51 | 49.767
2020-08-07 | 97:51 | 49.769
2020-08-07 | 98:51 | 49.771
2020-08-07 | 99:51 | 49.77
2020-08-07 | 100:51 | 49.768
2020-08-07 | 101:51 | 49.766
2020-08-07 | 102:51 | 49.765
2020-08-07 | 103:51 | 49.762
2020-08-07 | 104:51 | 49.762
2020-08-07 | 105:51 | 49.76
2020-08-07 | 106:51 | 49.759
2020-08-07 | 107:51 | 49.759
2020-08-07 | 108:51 | 49.76
2020-08-07 | 109:51 | 49.76
2020-08-07 | 110:51 | 49.758
2020-08-07 | 111:51 | 49.758
2020-08-07 | 112:51 | 49.756
2020-08-07 | 113:51 | 49.755
2020-08-07 | 114:51 | 49.752
2020-08-07 | 115:51 | 49.75
2020-08-07 | 116:51 | 49.748
2020-08-07 | 117:51 | 49.75
2020-08-07 | 118:51 | 49.753
2020-08-07 | 119:51 | 49.758
2020-08-07 | 120:51 | 49.764
2020-08-07 | 121:51 | 49.771
2020-08-07 | 122:51 | 49.778
2020-08-07 | 123:51 | 49.785
2020-08-07 | 124:51 | 49.791
2020-08-07 | 125:51 | 49.795
2020-08-07 | 126:51 | 49.8
2020-08-07 | 127:51 | 49.805
2020-08-07 | 128:51 | 49.808
2020-08-07 | 129:51 | 49.809
2020-08-07 | 130:51 | 49.811
2020-08-07 | 131:51 | 49.812
2020-08-07 | 132:51 | 49.814
2020-08-07 | 133:51 | 49.816
2020-08-07 | 134:51 | 49.816
2020-08-07 | 135:51 | 49.816
2020-08-07 | 136:51 | 49.815
2020-08-07 | 137:51 | 49.814
2020-08-07 | 138:51 | 49.812
2020-08-07 | 139:51 | 49.81
2020-08-07 | 140:51 | 49.809
2020-08-07 | 141:51 | 49.809
2020-08-07 | 142:51 | 49.809
2020-08-07 | 143:51 | 49.808
2020-08-07 | 144:51 | 49.805
2020-08-07 | 145:51 | 49.803
2020-08-07 | 146:51 | 49.802
2020-08-07 | 147:51 | 49.801
2020-08-07 | 148:51 | 49.8
2020-08-07 | 149:51 | 49.801
2020-08-07 | 150:51 | 49.802
2020-08-07 | 151:51 | 49.806
2020-08-07 | 152:51 | 49.809
2020-08-07 | 153:51 | 49.81
2020-08-07 | 154:51 | 49.811
2020-08-07 | 155:51 | 49.813
2020-08-07 | 156:51 | 49.815
2020-08-07 | 157:51 | 49.815
2020-08-07 | 158:51 | 49.815
2020-08-07 | 159:51 | 49.814
2020-08-07 | 160:51 | 49.816
2020-08-07 | 161:51 | 49.818
2020-08-07 | 162:51 | 49.819
2020-08-07 | 163:51 | 49.819
2020-08-07 | 164:51 | 49.821
2020-08-07 | 165:51 | 49.824
2020-08-07 | 166:51 | 49.827
2020-08-07 | 167:51 | 49.83
2020-08-07 | 168:51 | 49.832
2020-08-07 | 169:51 | 49.835
2020-08-07 | 170:51 | 49.834
2020-08-07 | 171:51 | 49.832
2020-08-07 | 172:51 | 49.829
2020-08-07 | 173:51 | 49.829
2020-08-07 | 174:51 | 49.826
2020-08-07 | 175:51 | 49.824
2020-08-07 | 176:51 | 49.823
2020-08-07 | 177:51 | 49.82
2020-08-07 | 178:51 | 49.819
2020-08-07 | 179:51 | 49.817
2020-08-07 | 180:51 | 49.816
2020-08-07 | 181:51 | 49.815
2020-08-07 | 182:51 | 49.818
2020-08-07 | 183:51 | 49.82
2020-08-07 | 184:51 | 49.821
2020-08-07 | 185:51 | 49.821
2020-08-07 | 186:51 | 49.823
2020-08-07 | 187:51 | 49.824
2020-08-07 | 188:51 | 49.824
2020-08-07 | 189:51 | 49.827
2020-08-07 | 190:51 | 49.828
2020-08-07 | 191:51 | 49.833
2020-08-07 | 192:51 | 49.835
2020-08-07 | 193:51 | 49.836
2020-08-07 | 194:51 | 49.839
2020-08-07 | 195:51 | 49.839
2020-08-07 | 196:51 | 49.838
2020-08-07 | 197:51 | 49.837
2020-08-07 | 198:51 | 49.837
2020-08-07 | 199:51 | 49.835
2020-08-07 | 200:51 | 49.831
2020-08-07 | 201:51 | 49.829
2020-08-07 | 202:51 | 49.829
2020-08-07 | 203:51 | 49.83
2020-08-07 | 204:51 | 49.83
2020-08-07 | 205:51 | 49.831
2020-08-07 | 206:51 | 49.833
2020-08-07 | 207:51 | 49.834
2020-08-07 | 208:51 | 49.835
2020-08-07 | 209:51 | 49.835
2020-08-07 | 210:51 | 49.838
2020-08-07 | 211:51 | 49.839
2020-08-07 | 212:51 | 49.839
2020-08-07 | 213:51 | 49.838
2020-08-07 | 214:51 | 49.838
2020-08-07 | 215:51 | 49.837
2020-08-07 | 216:51 | 49.837
2020-08-07 | 217:51 | 49.836
2020-08-07 | 218:51 | 49.837
2020-08-07 | 219:51 | 49.838
2020-08-07 | 220:51 | 49.838
2020-08-07 | 221:51 | 49.838
2020-08-07 | 222:51 | 49.839
2020-08-07 | 223:51 | 49.84
2020-08-07 | 224:51 | 49.841
2020-08-07 | 225:51 | 49.839
2020-08-07 | 226:51 | 49.839
2020-08-07 | 227:51 | 49.838
2020-08-07 | 228:51 | 49.837
2020-08-07 | 229:51 | 49.834
2020-08-07 | 230:51 | 49.832
2020-08-07 | 231:51 | 49.831
2020-08-07 | 232:51 | 49.83
2020-08-07 | 233:51 | 49.829
2020-08-07 | 234:51 | 49.827
2020-08-07 | 235:51 | 49.821
2020-08-07 | 236:51 | 49.818
2020-08-07 | 237:51 | 49.816
2020-08-07 | 238:51 | 49.815
2020-08-07 | 239:51 | 49.814
2020-08-07 | 240:51 | 49.814
2020-08-07 | 241:51 | 49.817
2020-08-07 | 242:51 | 49.82
2020-08-07 | 243:51 | 49.822
2020-08-07 | 244:51 | 49.825
2020-08-07 | 245:51 | 49.828
2020-08-07 | 246:51 | 49.829
2020-08-07 | 247:51 | 49.831
2020-08-07 | 248:51 | 49.833
2020-08-07 | 249:51 | 49.834
2020-08-07 | 250:51 | 49.837
2020-08-07 | 251:51 | 49.837
2020-08-07 | 252:51 | 49.837
2020-08-07 | 253:51 | 49.839
2020-08-07 | 254:51 | 49.843
2020-08-07 | 255:51 | 49.848
2020-08-07 | 256:51 | 49.851
2020-08-07 | 257:51 | 49.855
2020-08-07 | 258:51 | 49.856
2020-08-07 | 259:51 | 49.858
2020-08-07 | 260:51 | 49.858
2020-08-07 | 261:51 | 49.855
2020-08-07 | 262:51 | 49.854
2020-08-07 | 263:51 | 49.852
2020-08-07 | 264:51 | 49.85
2020-08-07 | 265:51 | 49.847
2020-08-07 | 266:51 | 49.846
2020-08-07 | 267:51 | 49.846
2020-08-07 | 268:51 | 49.849
2020-08-07 | 269:51 | 49.851
2020-08-07 | 270:51 | 49.853
2020-08-07 | 271:51 | 49.856
2020-08-07 | 272:51 | 49.859
2020-08-07 | 273:51 | 49.864
2020-08-07 | 274:51 | 49.865
2020-08-07 | 275:51 | 49.867
2020-08-07 | 276:51 | 49.867
2020-08-07 | 277:51 | 49.867
2020-08-07 | 278:51 | 49.866
2020-08-07 | 279:51 | 49.867
2020-08-07 | 280:51 | 49.867
2020-08-07 | 281:51 | 49.869
2020-08-07 | 282:51 | 49.871
2020-08-07 | 283:51 | 49.873
2020-08-07 | 284:51 | 49.873
2020-08-07 | 285:51 | 49.875
2020-08-07 | 286:51 | 49.877
2020-08-07 | 287:51 | 49.878
2020-08-07 | 288:51 | 49.879
2020-08-07 | 289:51 | 49.879
2020-08-07 | 290:51 | 49.879
2020-08-07 | 291:51 | 49.88
2020-08-07 | 292:51 | 49.882
2020-08-07 | 293:51 | 49.886
2020-08-07 | 294:51 | 49.89
2020-08-07 | 295:51 | 49.892
2020-08-07 | 296:51 | 49.895
2020-08-07 | 297:51 | 49.897
2020-08-07 | 298:51 | 49.898
2020-08-07 | 299:51 | 49.901
2020-08-07 | 300:51 | 49.904
2020-08-07 | 301:51 | 49.906
2020-08-07 | 302:51 | 49.907
2020-08-07 | 303:51 | 49.906
2020-08-07 | 304:51 | 49.905
2020-08-07 | 305:51 | 49.905
2020-08-07 | 306:51 | 49.905
2020-08-07 | 307:51 | 49.908
2020-08-07 | 308:51 | 49.913
2020-08-07 | 309:51 | 49.917
2020-08-07 | 310:51 | 49.922
2020-08-07 | 311:51 | 49.926
2020-08-07 | 312:51 | 49.928
2020-08-07 | 313:51 | 49.929
2020-08-07 | 314:51 | 49.929
2020-08-07 | 315:51 | 49.929
2020-08-07 | 316:51 | 49.929
2020-08-07 | 317:51 | 49.925
2020-08-07 | 318:51 | 49.922
2020-08-07 | 319:51 | 49.918
2020-08-07 | 320:51 | 49.915
2020-08-07 | 321:51 | 49.914
2020-08-07 | 322:51 | 49.912
2020-08-07 | 323:51 | 49.91
2020-08-07 | 324:51 | 49.91
2020-08-07 | 325:51 | 49.909
2020-08-07 | 326:51 | 49.907
2020-08-07 | 327:51 | 49.907
2020-08-07 | 328:51 | 49.906
2020-08-07 | 329:51 | 49.907
2020-08-07 | 330:51 | 49.909
2020-08-07 | 331:51 | 49.914
2020-08-07 | 332:51 | 49.92
2020-08-07 | 333:51 | 49.925
2020-08-07 | 334:51 | 49.931
2020-08-07 | 335:51 | 49.936
2020-08-07 | 336:51 | 49.94
2020-08-07 | 337:51 | 49.944
2020-08-07 | 338:51 | 49.947
2020-08-07 | 339:51 | 49.949
2020-08-07 | 340:51 | 49.95
2020-08-07 | 341:51 | 49.951
2020-08-07 | 342:51 | 49.952
2020-08-07 | 343:51 | 49.952
2020-08-07 | 344:51 | 49.952
2020-08-07 | 345:51 | 49.95
2020-08-07 | 346:51 | 49.95
2020-08-07 | 347:51 | 49.949
2020-08-07 | 348:51 | 49.948
2020-08-07 | 349:51 | 49.949
2020-08-07 | 350:51 | 49.952
2020-08-07 | 351:51 | 49.954
2020-08-07 | 352:51 | 49.956
2020-08-07 | 353:51 | 49.959
2020-08-07 | 354:51 | 49.962
2020-08-07 | 355:51 | 49.961
2020-08-07 | 356:51 | 49.96
2020-08-07 | 357:51 | 49.961
2020-08-07 | 358:51 | 49.962
2020-08-07 | 359:51 | 49.964
2020-08-07 | 360:51 | 49.968
2020-08-07 | 361:51 | 49.971
2020-08-07 | 362:51 | 49.975
2020-08-07 | 363:51 | 49.977
2020-08-07 | 364:51 | 49.979
2020-08-07 | 365:51 | 49.982
2020-08-07 | 366:51 | 49.981
2020-08-07 | 367:51 | 49.981
2020-08-07 | 368:51 | 49.982
2020-08-07 | 369:51 | 49.985
2020-08-07 | 370:51 | 49.987
2020-08-07 | 371:51 | 49.99
2020-08-07 | 372:51 | 49.991
2020-08-07 | 373:51 | 49.995
2020-08-07 | 374:51 | 49.995
2020-08-07 | 375:51 | 49.993
2020-08-07 | 376:51 | 49.994
2020-08-07 | 377:51 | 49.995
2020-08-07 | 378:51 | 49.996
2020-08-07 | 379:51 | 49.997
2020-08-07 | 380:51 | 49.998
2020-08-07 | 381:51 | 49.999
2020-08-07 | 382:51 | 50.001
2020-08-07 | 383:51 | 50.004
2020-08-07 | 384:51 | 50.005
2020-08-07 | 385:51 | 50.006
2020-08-07 | 386:51 | 50.007
2020-08-07 | 387:51 | 50.009
2020-08-07 | 388:51 | 50.012
2020-08-07 | 389:51 | 50.014
2020-08-07 | 390:51 | 50.019
2020-08-07 | 391:51 | 50.024
2020-08-07 | 392:51 | 50.028
2020-08-07 | 393:51 | 50.031
2020-08-07 | 394:51 | 50.034
2020-08-07 | 395:51 | 50.035
2020-08-07 | 396:51 | 50.037
2020-08-07 | 397:51 | 50.039
2020-08-07 | 398:51 | 50.042
2020-08-07 | 399:51 | 50.045
2020-08-07 | 400:51 | 50.049
2020-08-07 | 401:51 | 50.052
2020-08-07 | 402:51 | 50.054
2020-08-07 | 403:51 | 50.054
2020-08-07 | 404:51 | 50.053
2020-08-07 | 405:51 | 50.054
2020-08-07 | 406:51 | 50.054
2020-08-07 | 407:51 | 50.056
2020-08-07 | 408:51 | 50.058
2020-08-07 | 409:51 | 50.062
2020-08-07 | 410:51 | 50.064
2020-08-07 | 411:51 | 50.064
2020-08-07 | 412:51 | 50.065
2020-08-07 | 413:51 | 50.069
2020-08-07 | 414:51 | 50.075
2020-08-07 | 415:51 | 50.079
2020-08-07 | 416:51 | 50.082
2020-08-07 | 417:51 | 50.085
2020-08-07 | 418:51 | 50.087
2020-08-07 | 419:51 | 50.092
2020-08-07 | 420:51 | 50.093
2020-08-07 | 421:51 | 50.096
2020-08-07 | 422:51 | 50.098
2020-08-07 | 423:51 | 50.1
2020-08-07 | 424:51 | 50.103
2020-08-07 | 425:51 | 50.105
2020-08-07 | 426:51 | 50.108
2020-08-07 | 427:51 | 50.11
2020-08-07 | 428:51 | 50.113
2020-08-07 | 429:51 | 50.115
2020-08-07 | 430:51 | 50.117
2020-08-07 | 431:51 | 50.117
2020-08-07 | 432:51 | 50.118
2020-08-07 | 433:51 | 50.12
2020-08-07 | 434:51 | 50.125
2020-08-07 | 435:51 | 50.13
2020-08-07 | 436:51 | 50.135
437:51
438:51
439:51
440:51
441:51
442:51
443:51
444:51
445:51
446:51
447:51
448:51
449:51
450:51
451:51
452:51
453:51
454:51
455:51
456:51
457:51
458:51
459:51
460:51
461:51
462:51
463:51
464:51
465:51
466:51
467:51
468:51
469:51
470:51
471:51
472:51
473:51
474:51
475:51
476:51
477:51
478:51
479:51
480:51
481:51
482:51
483:51
484:51
485:51
486:51
487:51
488:51
489:51
490:51
491:51
492:51
493:51
494:51
495:51
496:51
497:51
498:51
499:51
500:51
501:51
502:51
503:51
504:51
505:51
506:51
507:51
508:51
509:51
510:51
511:51
512:51
513:51
514:51
515:51
516:51
517:51
518:51
519:51
520:51
521:51
522:51
523:51
524:51
525:51
526:51
527:51
528:51
529:51
530:51
531:51
532:51
533:51
534:51
535:51
536:51
537:51
538:51
539:51
540:51
541:51
542:51
543:51
544:51
545:51
546:51
547:51
548:51
549:51
550:51
551:51
552:51
553:51
554:51
555:51
556:51
557:51
558:51
559:51
560:51
561:51
562:51
563:51
564:51
565:51
566:51
567:51
568:51
569:51
570:51
571:51
572:51
573:51
574:51
575:51
576:51
577:51
578:51
579:51
580:51
581:51
582:51
583:51
584:51
585:51
586:51
587:51
588:51
589:51
590:51
591:51
592:51
593:51
594:51
595:51
596:51
597:51
598:51
599:51
600:51
601:51
602:51
603:51
604:51
605:51
606:51
607:51
608:51
609:51
610:51
611:51
612:51
613:51
614:51
615:51
616:51
617:51
618:51
619:51
620:51
621:51
622:51
623:51
624:51
625:51
626:51
627:51
628:51
629:51
630:51
631:51
632:51
633:51
634:51
635:51
636:51
637:51
638:51
639:51
640:51
641:51
642:51
643:51
644:51
645:51
646:51
647:51
648:51
649:51
650:51
651:51
652:51
653:51
654:51
655:51
656:51
657:51
658:51
659:51
660:51
661:51
662:51
663:51
664:51
665:51
666:51
667:51
668:51
669:51
670:51
671:51
672:51
673:51
674:51
675:51
676:51
677:51
678:51
679:51
680:51
681:51
682:51
683:51
684:51
685:51
686:51
687:51
688:51
689:51
690:51
691:51
692:51
693:51
694:51
695:51
696:51
697:51
698:51
699:51
700:51
701:51
702:51
703:51
704:51
705:51
706:51
707:51
708:51
709:51
710:51
711:51
712:51
713:51
714:51
715:51
716:51
717:51
718:51
719:51
720:51
721:51
722:51
723:51
724:51
725:51
726:51
727:51
728:51
729:51
730:51
731:51
732:51
733:51
734:51
735:51
736:51
737:51
738:51
739:51
740:51
741:51
742:51
743:51
744:51
745:51
746:51
747:51
748:51
749:51
750:51
751:51
752:51
753:51
754:51
755:51
756:51
757:51
758:51
759:51
760:51
761:51
762:51
763:51
764:51
765:51
766:51
767:51
768:51
769:51
770:51
771:51
772:51
773:51
774:51
775:51
776:51
777:51
778:51
779:51
780:51
781:51
782:51
783:51
784:51
785:51
786:51
787:51
788:51
789:51
790:51
791:51
792:51
793:51
794:51
795:51
796:51
797:51
798:51
799:51
800:51
801:51
802:51
803:51
804:51
805:51
806:51
807:51
808:51
809:51
810:51
811:51
812:51
813:51
814:51
815:51
816:51
817:51
818:51
819:51
820:51
821:51
822:51
823:51
824:51
825:51
826:51
827:51
828:51
829:51
830:51
831:51
832:51
833:51
834:51
835:51
836:51
837:51
838:51
839:51
840:51
841:51
842:51
843:51
844:51
845:51
846:51
847:51
848:51
849:51
850:51
851:51
852:51
853:51
854:51
855:51
856:51
857:51
858:51
859:51
860:51
861:51
862:51
863:51
864:51
865:51
866:51
867:51
868:51
869:51
870:51
871:51
872:51
873:51
874:51
875:51
876:51
877:51
878:51
879:51
880:51
881:51
882:51
883:51
884:51
885:51
886:51
887:51
888:51
889:51
890:51
891:51
892:51
893:51
894:51
895:51
896:51
897:51
898:51
899:51
900:51
901:51
902:51
903:51
904:51
905:51
906:51
907:51
908:51
909:51
910:51
911:51
912:51
913:51
914:51
915:51
916:51

## Event 20200810-1
In UTC
Date | Time | Freq
2020-08-10 | 5:57 | 50.066
2020-08-10 | 5:57 | 50.064
2020-08-10 | 5:57 | 50.063
2020-08-10 | 5:57 | 50.06
2020-08-10 | 5:57 | 50.058
2020-08-10 | 6:57 | 50.057
2020-08-10 | 7:57 | 50.058
2020-08-10 | 8:57 | 50.06
2020-08-10 | 9:57 | 50.06
2020-08-10 | 10:57 | 50.061
2020-08-10 | 11:57 | 50.062
2020-08-10 | 12:57 | 50.062
2020-08-10 | 13:57 | 50.062
2020-08-10 | 14:57 | 50.062
2020-08-10 | 15:57 | 50.06
2020-08-10 | 16:57 | 50.059
2020-08-10 | 17:57 | 50.06
2020-08-10 | 18:57 | 50.061
2020-08-10 | 19:57 | 50.063
2020-08-10 | 20:57 | 50.064
2020-08-10 | 21:57 | 50.062
2020-08-10 | 22:57 | 50.062
2020-08-10 | 23:57 | 50.06
2020-08-10 | 24:57 | 50.06
2020-08-10 | 25:57 | 50.06
2020-08-10 | 26:57 | 50.057
2020-08-10 | 27:57 | 50.056
2020-08-10 | 28:57 | 50.054
2020-08-10 | 29:57 | 50.054
2020-08-10 | 30:57 | 50.054
2020-08-10 | 31:57 | 50.054
2020-08-10 | 32:57 | 50.055
2020-08-10 | 33:57 | 50.056
2020-08-10 | 34:57 | 50.056
2020-08-10 | 35:57 | 50.058
2020-08-10 | 36:57 | 50.059
2020-08-10 | 37:57 | 50.061
2020-08-10 | 38:57 | 50.062
2020-08-10 | 39:57 | 50.064
2020-08-10 | 40:57 | 50.066
2020-08-10 | 41:57 | 50.068
2020-08-10 | 42:57 | 50.069
2020-08-10 | 43:57 | 50.07
2020-08-10 | 44:57 | 50.067
2020-08-10 | 45:57 | 50.064
2020-08-10 | 46:57 | 50.059
2020-08-10 | 47:57 | 50.057
2020-08-10 | 48:57 | 50.056
2020-08-10 | 49:57 | 50.057
2020-08-10 | 50:57 | 50.059
2020-08-10 | 51:57 | 50.058
2020-08-10 | 52:57 | 50.059
2020-08-10 | 53:57 | 50.06
2020-08-10 | 54:57 | 50.061
2020-08-10 | 55:57 | 50.063
2020-08-10 | 56:57 | 50.065
2020-08-10 | 57:57 | 50.064
2020-08-10 | 58:57 | 50.062
2020-08-10 | 59:57 | 50.061
2020-08-10 | 60:57 | 50.059
2020-08-10 | 61:57 | 50.057
2020-08-10 | 62:57 | 50.056
2020-08-10 | 63:57 | 50.056
2020-08-10 | 64:57 | 50.054
2020-08-10 | 65:57 | 50.051
2020-08-10 | 66:57 | 50.049
2020-08-10 | 67:57 | 50.045
2020-08-10 | 68:57 | 50.043
2020-08-10 | 69:57 | 50.039
2020-08-10 | 70:57 | 50.032
2020-08-10 | 71:57 | 50.028
2020-08-10 | 72:57 | 50.024
2020-08-10 | 73:57 | 50.02
2020-08-10 | 74:57 | 50.021
2020-08-10 | 75:57 | 50.022
2020-08-10 | 76:57 | 50.026
2020-08-10 | 77:57 | 50.028
2020-08-10 | 78:57 | 50.028
2020-08-10 | 79:57 | 50.03
2020-08-10 | 80:57 | 50.031
2020-08-10 | 81:57 | 50.032
2020-08-10 | 82:57 | 50.033
2020-08-10 | 83:57 | 50.033
2020-08-10 | 84:57 | 50.034
2020-08-10 | 85:57 | 50.034
2020-08-10 | 86:57 | 50.036
2020-08-10 | 87:57 | 50.038
2020-08-10 | 88:57 | 50.039
2020-08-10 | 89:57 | 50.044
2020-08-10 | 90:57 | 50.051
2020-08-10 | 91:57 | 50.055
2020-08-10 | 92:57 | 50.059
2020-08-10 | 93:57 | 50.06
2020-08-10 | 94:57 | 50.061
2020-08-10 | 95:57 | 50.059
2020-08-10 | 96:57 | 50.058
2020-08-10 | 97:57 | 50.055
2020-08-10 | 98:57 | 50.054
2020-08-10 | 99:57 | 50.052
2020-08-10 | 100:57 | 50.048
2020-08-10 | 101:57 | 50.044
2020-08-10 | 102:57 | 50.041
2020-08-10 | 103:57 | 50.041
2020-08-10 | 104:57 | 50.043
2020-08-10 | 105:57 | 50.042
2020-08-10 | 106:57 | 50.045
2020-08-10 | 107:57 | 50.049
2020-08-10 | 108:57 | 50.054
2020-08-10 | 109:57 | 50.06
2020-08-10 | 110:57 | 50.067
2020-08-10 | 111:57 | 50.074
2020-08-10 | 112:57 | 50.078
2020-08-10 | 113:57 | 50.079
2020-08-10 | 114:57 | 50.065
2020-08-10 | 115:57 | 50.033
2020-08-10 | 116:57 | 50.003
2020-08-10 | 117:57 | 49.982
2020-08-10 | 118:57 | 49.97
2020-08-10 | 119:57 | 49.961
2020-08-10 | 120:57 | 49.955
2020-08-10 | 121:57 | 49.949
2020-08-10 | 122:57 | 49.944
2020-08-10 | 123:57 | 49.94
2020-08-10 | 124:57 | 49.938
2020-08-10 | 125:57 | 49.935
2020-08-10 | 126:57 | 49.936
2020-08-10 | 127:57 | 49.935
2020-08-10 | 128:57 | 49.935
2020-08-10 | 129:57 | 49.934
2020-08-10 | 130:57 | 49.933
2020-08-10 | 131:57 | 49.934
2020-08-10 | 132:57 | 49.933
2020-08-10 | 133:57 | 49.932
2020-08-10 | 134:57 | 49.931
2020-08-10 | 135:57 | 49.937
2020-08-10 | 136:57 | 49.945
2020-08-10 | 137:57 | 49.952
2020-08-10 | 138:57 | 49.958
2020-08-10 | 139:57 | 49.963
2020-08-10 | 140:57 | 49.966
2020-08-10 | 141:57 | 49.969
2020-08-10 | 142:57 | 49.973
2020-08-10 | 143:57 | 49.973
2020-08-10 | 144:57 | 49.974
2020-08-10 | 145:57 | 49.973
2020-08-10 | 146:57 | 49.972
2020-08-10 | 147:57 | 49.971
2020-08-10 | 148:57 | 49.972
2020-08-10 | 149:57 | 49.973
2020-08-10 | 150:57 | 49.973
2020-08-10 | 151:57 | 49.972
2020-08-10 | 152:57 | 49.972
2020-08-10 | 153:57 | 49.972
2020-08-10 | 154:57 | 49.973
2020-08-10 | 155:57 | 49.973
2020-08-10 | 156:57 | 49.972
2020-08-10 | 157:57 | 49.972
2020-08-10 | 158:57 | 49.974
2020-08-10 | 159:57 | 49.974
2020-08-10 | 160:57 | 49.972
2020-08-10 | 161:57 | 49.971
2020-08-10 | 162:57 | 49.97
2020-08-10 | 163:57 | 49.969
2020-08-10 | 164:57 | 49.969
2020-08-10 | 165:57 | 49.968
2020-08-10 | 166:57 | 49.965
2020-08-10 | 167:57 | 49.963
2020-08-10 | 168:57 | 49.96
2020-08-10 | 169:57 | 49.956
2020-08-10 | 170:57 | 49.951
2020-08-10 | 171:57 | 49.946
2020-08-10 | 172:57 | 49.946
2020-08-10 | 173:57 | 49.944
2020-08-10 | 174:57 | 49.943
2020-08-10 | 175:57 | 49.943
2020-08-10 | 176:57 | 49.942
2020-08-10 | 177:57 | 49.942
2020-08-10 | 178:57 | 49.943
2020-08-10 | 179:57 | 49.943
2020-08-10 | 180:57 | 49.942
2020-08-10 | 181:57 | 49.942
2020-08-10 | 182:57 | 49.942
2020-08-10 | 183:57 | 49.942
2020-08-10 | 184:57 | 49.94
2020-08-10 | 185:57 | 49.939
2020-08-10 | 186:57 | 49.942
2020-08-10 | 187:57 | 49.94
2020-08-10 | 188:57 | 49.94
2020-08-10 | 189:57 | 49.94
2020-08-10 | 190:57 | 49.938
2020-08-10 | 191:57 | 49.936
2020-08-10 | 192:57 | 49.937
2020-08-10 | 193:57 | 49.936
2020-08-10 | 194:57 | 49.932
2020-08-10 | 195:57 | 49.927
2020-08-10 | 196:57 | 49.922
2020-08-10 | 197:57 | 49.92
2020-08-10 | 198:57 | 49.921
2020-08-10 | 199:57 | 49.92
2020-08-10 | 200:57 | 49.919
2020-08-10 | 201:57 | 49.919
2020-08-10 | 202:57 | 49.919
2020-08-10 | 203:57 | 49.926
2020-08-10 | 204:57 | 49.937
2020-08-10 | 205:57 | 49.943
2020-08-10 | 206:57 | 49.95
2020-08-10 | 207:57 | 49.954
2020-08-10 | 208:57 | 49.958
2020-08-10 | 209:57 | 49.959
2020-08-10 | 210:57 | 49.963
2020-08-10 | 211:57 | 49.966
2020-08-10 | 212:57 | 49.967
2020-08-10 | 213:57 | 49.969
2020-08-10 | 214:57 | 49.97
2020-08-10 | 215:57 | 49.97
2020-08-10 | 216:57 | 49.968
2020-08-10 | 217:57 | 49.968
2020-08-10 | 218:57 | 49.965
2020-08-10 | 219:57 | 49.965
2020-08-10 | 220:57 | 49.966
2020-08-10 | 221:57 | 49.967
2020-08-10 | 222:57 | 49.97
2020-08-10 | 223:57 | 49.969
2020-08-10 | 224:57 | 49.969
2020-08-10 | 225:57 | 49.973
2020-08-10 | 226:57 | 49.976
2020-08-10 | 227:57 | 49.98
2020-08-10 | 228:57 | 49.984
2020-08-10 | 229:57 | 49.984
2020-08-10 | 230:57 | 49.983
2020-08-10 | 231:57 | 49.982
2020-08-10 | 232:57 | 49.982
2020-08-10 | 233:57 | 49.983
2020-08-10 | 234:57 | 49.984
2020-08-10 | 235:57 | 49.985
2020-08-10 | 236:57 | 49.985
2020-08-10 | 237:57 | 49.983
2020-08-10 | 238:57 | 49.981
2020-08-10 | 239:57 | 49.979
2020-08-10 | 240:57 | 49.974
2020-08-10 | 241:57 | 49.971
2020-08-10 | 242:57 | 49.969
2020-08-10 | 243:57 | 49.966
2020-08-10 | 244:57 | 49.966
2020-08-10 | 245:57 | 49.965
2020-08-10 | 246:57 | 49.965
2020-08-10 | 247:57 | 49.964
2020-08-10 | 248:57 | 49.965
2020-08-10 | 249:57 | 49.966
2020-08-10 | 250:57 | 49.966
2020-08-10 | 251:57 | 49.97
2020-08-10 | 252:57 | 49.97
2020-08-10 | 253:57 | 49.972
2020-08-10 | 254:57 | 49.971
2020-08-10 | 255:57 | 49.968
2020-08-10 | 256:57 | 49.964
2020-08-10 | 257:57 | 49.957
2020-08-10 | 258:57 | 49.951
2020-08-10 | 259:57 | 49.948
2020-08-10 | 260:57 | 49.945
2020-08-10 | 261:57 | 49.943
2020-08-10 | 262:57 | 49.942
2020-08-10 | 263:57 | 49.943
2020-08-10 | 264:57 | 49.943
2020-08-10 | 265:57 | 49.943
2020-08-10 | 266:57 | 49.945
2020-08-10 | 267:57 | 49.947
2020-08-10 | 268:57 | 49.948
2020-08-10 | 269:57 | 49.95
2020-08-10 | 270:57 | 49.948
2020-08-10 | 271:57 | 49.949
2020-08-10 | 272:57 | 49.95
2020-08-10 | 273:57 | 49.95
2020-08-10 | 274:57 | 49.953
2020-08-10 | 275:57 | 49.954
2020-08-10 | 276:57 | 49.956
2020-08-10 | 277:57 | 49.955
2020-08-10 | 278:57 | 49.955
2020-08-10 | 279:57 | 49.955
2020-08-10 | 280:57 | 49.953
2020-08-10 | 281:57 | 49.955
2020-08-10 | 282:57 | 49.953
2020-08-10 | 283:57 | 49.953
2020-08-10 | 284:57 | 49.952
2020-08-10 | 285:57 | 49.952
2020-08-10 | 286:57 | 49.953
2020-08-10 | 287:57 | 49.952
2020-08-10 | 288:57 | 49.953
2020-08-10 | 289:57 | 49.952
2020-08-10 | 290:57 | 49.953
2020-08-10 | 291:57 | 49.95
2020-08-10 | 292:57 | 49.948
2020-08-10 | 293:57 | 49.948
2020-08-10 | 294:57 | 49.946
2020-08-10 | 295:57 | 49.947
2020-08-10 | 296:57 | 49.948
2020-08-10 | 297:57 | 49.95
2020-08-10 | 298:57 | 49.95
2020-08-10 | 299:57 | 49.95
2020-08-10 | 300:57 | 49.953
2020-08-10 | 301:57 | 49.956
2020-08-10 | 302:57 | 49.958
2020-08-10 | 303:57 | 49.96
2020-08-10 | 304:57 | 49.963
2020-08-10 | 305:57 | 49.965
2020-08-10 | 306:57 | 49.968
2020-08-10 | 307:57 | 49.967
2020-08-10 | 308:57 | 49.968
2020-08-10 | 309:57 | 49.97
2020-08-10 | 310:57 | 49.969
2020-08-10 | 311:57 | 49.968
2020-08-10 | 312:57 | 49.968
2020-08-10 | 313:57 | 49.968
2020-08-10 | 314:57 | 49.968
2020-08-10 | 315:57 | 49.969
2020-08-10 | 316:57 | 49.966
2020-08-10 | 317:57 | 49.966
2020-08-10 | 318:57 | 49.966
2020-08-10 | 319:57 | 49.966
2020-08-10 | 320:57 | 49.966
2020-08-10 | 321:57 | 49.967
2020-08-10 | 322:57 | 49.97
2020-08-10 | 323:57 | 49.974
2020-08-10 | 324:57 | 49.976
2020-08-10 | 325:57 | 49.975
2020-08-10 | 326:57 | 49.974
2020-08-10 | 327:57 | 49.975
2020-08-10 | 328:57 | 49.976
2020-08-10 | 329:57 | 49.98
2020-08-10 | 330:57 | 49.983
2020-08-10 | 331:57 | 49.986
2020-08-10 | 332:57 | 49.989
2020-08-10 | 333:57 | 49.989
2020-08-10 | 334:57 | 49.992
2020-08-10 | 335:57 | 49.992
2020-08-10 | 336:57 | 49.991
2020-08-10 | 337:57 | 49.987
2020-08-10 | 338:57 | 49.983
2020-08-10 | 339:57 | 49.98
2020-08-10 | 340:57 | 49.982
2020-08-10 | 341:57 | 49.984
2020-08-10 | 342:57 | 49.984
2020-08-10 | 343:57 | 49.984
2020-08-10 | 344:57 | 49.984
2020-08-10 | 345:57 | 49.986
2020-08-10 | 346:57 | 49.988
2020-08-10 | 347:57 | 49.99
2020-08-10 | 348:57 | 49.99
2020-08-10 | 349:57 | 49.992
2020-08-10 | 350:57 | 49.989
2020-08-10 | 351:57 | 49.989
2020-08-10 | 352:57 | 49.986
2020-08-10 | 353:57 | 49.984
2020-08-10 | 354:57 | 49.979
2020-08-10 | 355:57 | 49.975
2020-08-10 | 356:57 | 49.973
2020-08-10 | 357:57 | 49.973
2020-08-10 | 358:57 | 49.972
2020-08-10 | 359:57 | 49.969
2020-08-10 | 360:57 | 49.967
2020-08-10 | 361:57 | 49.963
2020-08-10 | 362:57 | 49.962
2020-08-10 | 363:57 | 49.959
2020-08-10 | 364:57 | 49.959
2020-08-10 | 365:57 | 49.959
2020-08-10 | 366:57 | 49.957
2020-08-10 | 367:57 | 49.956
2020-08-10 | 368:57 | 49.955
2020-08-10 | 369:57 | 49.956
2020-08-10 | 370:57 | 49.958
2020-08-10 | 371:57 | 49.959
2020-08-10 | 372:57 | 49.963
2020-08-10 | 373:57 | 49.964
2020-08-10 | 374:57 | 49.967
2020-08-10 | 375:57 | 49.966
2020-08-10 | 376:57 | 49.965
2020-08-10 | 377:57 | 49.967
2020-08-10 | 378:57 | 49.966
2020-08-10 | 379:57 | 49.965
2020-08-10 | 380:57 | 49.964
2020-08-10 | 381:57 | 49.965
2020-08-10 | 382:57 | 49.966
2020-08-10 | 383:57 | 49.969
2020-08-10 | 384:57 | 49.971
2020-08-10 | 385:57 | 49.973
2020-08-10 | 386:57 | 49.974
2020-08-10 | 387:57 | 49.976
2020-08-10 | 388:57 | 49.978
2020-08-10 | 389:57 | 49.979
2020-08-10 | 390:57 | 49.98
2020-08-10 | 391:57 | 49.981
2020-08-10 | 392:57 | 49.983
2020-08-10 | 393:57 | 49.984
2020-08-10 | 394:57 | 49.987
2020-08-10 | 395:57 | 49.992
2020-08-10 | 396:57 | 49.995
2020-08-10 | 397:57 | 49.997
2020-08-10 | 398:57 | 49.998
2020-08-10 | 399:57 | 50
2020-08-10 | 400:57 | 50.002
2020-08-10 | 401:57 | 50.001
2020-08-10 | 402:57 | 50
2020-08-10 | 403:57 | 49.998
2020-08-10 | 404:57 | 49.996
2020-08-10 | 405:57 | 49.994
2020-08-10 | 406:57 | 49.991
2020-08-10 | 407:57 | 49.994
2020-08-10 | 408:57 | 49.994
2020-08-10 | 409:57 | 49.995
2020-08-10 | 410:57 | 49.993
2020-08-10 | 411:57 | 49.99
2020-08-10 | 412:57 | 49.985
2020-08-10 | 413:57 | 49.982
2020-08-10 | 414:57 | 49.981
2020-08-10 | 415:57 | 49.98
2020-08-10 | 416:57 | 49.98
2020-08-10 | 417:57 | 49.98
2020-08-10 | 418:57 | 49.982
2020-08-10 | 419:57 | 49.983
2020-08-10 | 420:57 | 49.982
421:57
422:57
423:57
424:57
425:57
426:57
427:57
428:57
429:57
430:57
431:57
432:57
433:57
434:57
435:57
436:57
437:57
438:57
439:57
440:57
441:57
442:57
443:57
444:57
445:57
446:57
447:57
448:57
449:57
450:57
451:57
452:57
453:57
454:57
455:57
456:57
457:57
458:57
459:57
460:57
461:57
462:57
463:57
464:57
465:57
466:57
467:57
468:57
469:57
470:57
471:57
472:57
473:57
474:57
475:57
476:57
477:57
478:57
479:57
480:57
481:57
482:57
483:57
484:57
485:57
486:57
487:57
488:57
489:57
490:57
491:57
492:57
493:57
494:57
495:57
496:57
497:57
498:57
499:57
500:57
501:57
502:57
503:57
504:57
505:57
506:57
507:57
508:57
509:57
510:57
511:57
512:57
513:57
514:57
515:57
516:57
517:57
518:57
519:57
520:57
521:57
522:57
523:57
524:57
525:57
526:57
527:57
528:57
529:57
530:57
531:57
532:57
533:57
534:57
535:57
536:57
537:57
538:57
539:57
540:57
541:57
542:57
543:57
544:57
545:57
546:57
547:57
548:57
549:57
550:57
551:57
552:57
553:57
554:57
555:57
556:57
557:57
558:57
559:57
560:57
561:57
562:57
563:57
564:57
565:57
566:57
567:57
568:57
569:57
570:57
571:57
572:57
573:57
574:57
575:57
576:57
577:57
578:57
579:57
580:57
581:57
582:57
583:57
584:57
585:57
586:57
587:57
588:57
589:57
590:57
591:57
592:57
593:57
594:57
595:57
596:57
597:57
598:57
599:57
600:57
601:57
602:57
603:57
604:57
605:57
606:57
607:57
608:57
609:57
610:57
611:57
612:57
613:57
614:57
615:57
616:57
617:57
618:57
619:57
620:57
621:57
622:57
623:57
624:57
625:57
626:57
627:57
628:57
629:57
630:57
631:57
632:57
633:57
634:57
635:57
636:57
637:57
638:57
639:57
640:57
641:57
642:57
643:57
644:57
645:57
646:57
647:57
648:57
649:57
650:57
651:57
652:57
653:57
654:57
655:57
656:57
657:57
658:57
659:57
660:57
661:57
662:57
663:57
664:57
665:57
666:57
667:57
668:57
669:57
670:57
671:57
672:57
673:57
674:57
675:57
676:57
677:57
678:57
679:57
680:57
681:57
682:57
683:57
684:57
685:57
686:57
687:57
688:57
689:57
690:57
691:57
692:57
693:57
694:57
695:57
696:57
697:57
698:57
699:57
700:57
701:57
702:57
703:57
704:57
705:57
706:57
707:57
708:57
709:57
710:57
711:57
712:57
713:57
714:57
715:57
716:57
717:57
718:57
719:57
720:57
721:57
722:57
723:57
724:57
725:57
726:57
727:57
728:57
729:57
730:57
731:57
732:57
733:57
734:57
735:57
736:57
737:57
738:57
739:57
740:57
741:57
742:57
743:57
744:57
745:57
746:57
747:57
748:57
749:57
750:57
751:57
752:57
753:57
754:57
755:57
756:57
757:57
758:57
759:57
760:57
761:57
762:57
763:57
764:57
765:57
766:57
767:57
768:57
769:57
770:57
771:57
772:57
773:57
774:57
775:57
776:57
777:57
778:57
779:57
780:57
781:57
782:57
783:57
784:57
785:57
786:57
787:57
788:57
789:57
790:57
791:57
792:57
793:57
794:57
795:57
796:57
797:57
798:57
799:57
800:57
801:57
802:57
803:57
804:57
805:57
806:57
807:57
808:57
809:57
810:57
811:57
812:57
813:57
814:57
815:57
816:57
817:57
818:57
819:57
820:57
821:57
822:57
823:57
824:57
825:57
826:57
827:57
828:57
829:57
830:57
831:57
832:57
833:57
834:57
835:57
836:57
837:57
838:57
839:57
840:57
841:57
842:57
843:57
844:57
845:57
846:57
847:57
848:57
849:57
850:57
851:57
852:57
853:57
854:57
855:57
856:57
857:57
858:57
859:57
860:57
861:57
862:57
863:57
864:57
865:57
866:57
867:57
868:57
869:57
870:57
871:57
872:57
873:57
874:57
875:57
876:57
877:57
878:57
879:57
880:57
881:57
882:57
883:57
884:57
885:57
886:57
887:57
888:57
889:57
890:57
891:57
892:57
893:57
894:57
895:57
896:57
897:57
898:57
899:57
900:57

## Event 20200810-2
In UTC
Date | Time | Freq
2020-08-10 | 19:57 | 50.027
2020-08-10 | 19:57 | 50.026
2020-08-10 | 19:57 | 50.025
2020-08-10 | 19:57 | 50.025
2020-08-10 | 19:57 | 50.022
2020-08-10 | 20:57 | 50.02
2020-08-10 | 21:57 | 50.016
2020-08-10 | 22:57 | 50.014
2020-08-10 | 23:57 | 50.013
2020-08-10 | 24:57 | 50.013
2020-08-10 | 25:57 | 50.013
2020-08-10 | 26:57 | 50.016
2020-08-10 | 27:57 | 50.019
2020-08-10 | 28:57 | 50.021
2020-08-10 | 29:57 | 50.023
2020-08-10 | 30:57 | 50.025
2020-08-10 | 31:57 | 50.025
2020-08-10 | 32:57 | 50.024
2020-08-10 | 33:57 | 50.022
2020-08-10 | 34:57 | 50.02
2020-08-10 | 35:57 | 50.018
2020-08-10 | 36:57 | 50.014
2020-08-10 | 37:57 | 50.012
2020-08-10 | 38:57 | 50.01
2020-08-10 | 39:57 | 50.009
2020-08-10 | 40:57 | 50.006
2020-08-10 | 41:57 | 50.002
2020-08-10 | 42:57 | 49.998
2020-08-10 | 43:57 | 49.998
2020-08-10 | 44:57 | 50
2020-08-10 | 45:57 | 50.003
2020-08-10 | 46:57 | 50.005
2020-08-10 | 47:57 | 50.006
2020-08-10 | 48:57 | 50.008
2020-08-10 | 49:57 | 50.008
2020-08-10 | 50:57 | 50.011
2020-08-10 | 51:57 | 50.012
2020-08-10 | 52:57 | 50.012
2020-08-10 | 53:57 | 50.012
2020-08-10 | 54:57 | 50.011
2020-08-10 | 55:57 | 50.01
2020-08-10 | 56:57 | 50.01
2020-08-10 | 57:57 | 50.011
2020-08-10 | 58:57 | 50.011
2020-08-10 | 59:57 | 50.013
2020-08-10 | 60:57 | 50.014
2020-08-10 | 61:57 | 50.014
2020-08-10 | 62:57 | 50.014
2020-08-10 | 63:57 | 50.015
2020-08-10 | 64:57 | 50.018
2020-08-10 | 65:57 | 50.016
2020-08-10 | 66:57 | 50.017
2020-08-10 | 67:57 | 50.016
2020-08-10 | 68:57 | 50.014
2020-08-10 | 69:57 | 50.012
2020-08-10 | 70:57 | 50.009
2020-08-10 | 71:57 | 50.007
2020-08-10 | 72:57 | 50.005
2020-08-10 | 73:57 | 50.006
2020-08-10 | 74:57 | 50.005
2020-08-10 | 75:57 | 50.005
2020-08-10 | 76:57 | 50.002
2020-08-10 | 77:57 | 50.002
2020-08-10 | 78:57 | 50.003
2020-08-10 | 79:57 | 50.002
2020-08-10 | 80:57 | 50.003
2020-08-10 | 81:57 | 50.004
2020-08-10 | 82:57 | 50.003
2020-08-10 | 83:57 | 50.002
2020-08-10 | 84:57 | 50.003
2020-08-10 | 85:57 | 50.005
2020-08-10 | 86:57 | 50.011
2020-08-10 | 87:57 | 50.015
2020-08-10 | 88:57 | 50.021
2020-08-10 | 89:57 | 50.027
2020-08-10 | 90:57 | 50.032
2020-08-10 | 91:57 | 50.036
2020-08-10 | 92:57 | 50.039
2020-08-10 | 93:57 | 50.037
2020-08-10 | 94:57 | 49.989
2020-08-10 | 95:57 | 49.958
2020-08-10 | 96:57 | 49.919
2020-08-10 | 97:57 | 49.898
2020-08-10 | 98:57 | 49.881
2020-08-10 | 99:57 | 49.867
2020-08-10 | 100:57 | 49.858
2020-08-10 | 101:57 | 49.851
2020-08-10 | 102:57 | 49.847
2020-08-10 | 103:57 | 49.845
2020-08-10 | 104:57 | 49.845
2020-08-10 | 105:57 | 49.843
2020-08-10 | 106:57 | 49.841
2020-08-10 | 107:57 | 49.838
2020-08-10 | 108:57 | 49.835
2020-08-10 | 109:57 | 49.832
2020-08-10 | 110:57 | 49.832
2020-08-10 | 111:57 | 49.83
2020-08-10 | 112:57 | 49.829
2020-08-10 | 113:57 | 49.829
2020-08-10 | 114:57 | 49.83
2020-08-10 | 115:57 | 49.833
2020-08-10 | 116:57 | 49.835
2020-08-10 | 117:57 | 49.837
2020-08-10 | 118:57 | 49.839
2020-08-10 | 119:57 | 49.842
2020-08-10 | 120:57 | 49.844
2020-08-10 | 121:57 | 49.843
2020-08-10 | 122:57 | 49.842
2020-08-10 | 123:57 | 49.841
2020-08-10 | 124:57 | 49.839
2020-08-10 | 125:57 | 49.837
2020-08-10 | 126:57 | 49.836
2020-08-10 | 127:57 | 49.834
2020-08-10 | 128:57 | 49.833
2020-08-10 | 129:57 | 49.834
2020-08-10 | 130:57 | 49.834
2020-08-10 | 131:57 | 49.836
2020-08-10 | 132:57 | 49.834
2020-08-10 | 133:57 | 49.831
2020-08-10 | 134:57 | 49.827
2020-08-10 | 135:57 | 49.822
2020-08-10 | 136:57 | 49.82
2020-08-10 | 137:57 | 49.818
2020-08-10 | 138:57 | 49.814
2020-08-10 | 139:57 | 49.812
2020-08-10 | 140:57 | 49.812
2020-08-10 | 141:57 | 49.812
2020-08-10 | 142:57 | 49.814
2020-08-10 | 143:57 | 49.816
2020-08-10 | 144:57 | 49.82
2020-08-10 | 145:57 | 49.824
2020-08-10 | 146:57 | 49.83
2020-08-10 | 147:57 | 49.834
2020-08-10 | 148:57 | 49.84
2020-08-10 | 149:57 | 49.845
2020-08-10 | 150:57 | 49.851
2020-08-10 | 151:57 | 49.856
2020-08-10 | 152:57 | 49.858
2020-08-10 | 153:57 | 49.859
2020-08-10 | 154:57 | 49.861
2020-08-10 | 155:57 | 49.861
2020-08-10 | 156:57 | 49.861
2020-08-10 | 157:57 | 49.859
2020-08-10 | 158:57 | 49.858
2020-08-10 | 159:57 | 49.856
2020-08-10 | 160:57 | 49.855
2020-08-10 | 161:57 | 49.854
2020-08-10 | 162:57 | 49.853
2020-08-10 | 163:57 | 49.855
2020-08-10 | 164:57 | 49.856
2020-08-10 | 165:57 | 49.857
2020-08-10 | 166:57 | 49.855
2020-08-10 | 167:57 | 49.854
2020-08-10 | 168:57 | 49.854
2020-08-10 | 169:57 | 49.855
2020-08-10 | 170:57 | 49.856
2020-08-10 | 171:57 | 49.859
2020-08-10 | 172:57 | 49.862
2020-08-10 | 173:57 | 49.869
2020-08-10 | 174:57 | 49.874
2020-08-10 | 175:57 | 49.878
2020-08-10 | 176:57 | 49.882
2020-08-10 | 177:57 | 49.884
2020-08-10 | 178:57 | 49.886
2020-08-10 | 179:57 | 49.887
2020-08-10 | 180:57 | 49.886
2020-08-10 | 181:57 | 49.884
2020-08-10 | 182:57 | 49.881
2020-08-10 | 183:57 | 49.877
2020-08-10 | 184:57 | 49.872
2020-08-10 | 185:57 | 49.866
2020-08-10 | 186:57 | 49.861
2020-08-10 | 187:57 | 49.857
2020-08-10 | 188:57 | 49.854
2020-08-10 | 189:57 | 49.853
2020-08-10 | 190:57 | 49.853
2020-08-10 | 191:57 | 49.853
2020-08-10 | 192:57 | 49.852
2020-08-10 | 193:57 | 49.852
2020-08-10 | 194:57 | 49.85
2020-08-10 | 195:57 | 49.846
2020-08-10 | 196:57 | 49.843
2020-08-10 | 197:57 | 49.842
2020-08-10 | 198:57 | 49.839
2020-08-10 | 199:57 | 49.838
2020-08-10 | 200:57 | 49.836
2020-08-10 | 201:57 | 49.834
2020-08-10 | 202:57 | 49.834
2020-08-10 | 203:57 | 49.833
2020-08-10 | 204:57 | 49.831
2020-08-10 | 205:57 | 49.828
2020-08-10 | 206:57 | 49.827
2020-08-10 | 207:57 | 49.826
2020-08-10 | 208:57 | 49.825
2020-08-10 | 209:57 | 49.824
2020-08-10 | 210:57 | 49.824
2020-08-10 | 211:57 | 49.824
2020-08-10 | 212:57 | 49.825
2020-08-10 | 213:57 | 49.826
2020-08-10 | 214:57 | 49.826
2020-08-10 | 215:57 | 49.825
2020-08-10 | 216:57 | 49.824
2020-08-10 | 217:57 | 49.821
2020-08-10 | 218:57 | 49.821
2020-08-10 | 219:57 | 49.82
2020-08-10 | 220:57 | 49.818
2020-08-10 | 221:57 | 49.815
2020-08-10 | 222:57 | 49.811
2020-08-10 | 223:57 | 49.81
2020-08-10 | 224:57 | 49.809
2020-08-10 | 225:57 | 49.809
2020-08-10 | 226:57 | 49.808
2020-08-10 | 227:57 | 49.806
2020-08-10 | 228:57 | 49.804
2020-08-10 | 229:57 | 49.803
2020-08-10 | 230:57 | 49.8
2020-08-10 | 231:57 | 49.799
2020-08-10 | 232:57 | 49.797
2020-08-10 | 233:57 | 49.794
2020-08-10 | 234:57 | 49.794
2020-08-10 | 235:57 | 49.793
2020-08-10 | 236:57 | 49.793
2020-08-10 | 237:57 | 49.792
2020-08-10 | 238:57 | 49.791
2020-08-10 | 239:57 | 49.788
2020-08-10 | 240:57 | 49.786
2020-08-10 | 241:57 | 49.783
2020-08-10 | 242:57 | 49.783
2020-08-10 | 243:57 | 49.782
2020-08-10 | 244:57 | 49.784
2020-08-10 | 245:57 | 49.785
2020-08-10 | 246:57 | 49.785
2020-08-10 | 247:57 | 49.783
2020-08-10 | 248:57 | 49.782
2020-08-10 | 249:57 | 49.782
2020-08-10 | 250:57 | 49.782
2020-08-10 | 251:57 | 49.782
2020-08-10 | 252:57 | 49.784
2020-08-10 | 253:57 | 49.784
2020-08-10 | 254:57 | 49.785
2020-08-10 | 255:57 | 49.785
2020-08-10 | 256:57 | 49.783
2020-08-10 | 257:57 | 49.779
2020-08-10 | 258:57 | 49.779
2020-08-10 | 259:57 | 49.779
2020-08-10 | 260:57 | 49.778
2020-08-10 | 261:57 | 49.779
2020-08-10 | 262:57 | 49.778
2020-08-10 | 263:57 | 49.778
2020-08-10 | 264:57 | 49.779
2020-08-10 | 265:57 | 49.779
2020-08-10 | 266:57 | 49.779
2020-08-10 | 267:57 | 49.778
2020-08-10 | 268:57 | 49.776
2020-08-10 | 269:57 | 49.772
2020-08-10 | 270:57 | 49.768
2020-08-10 | 271:57 | 49.768
2020-08-10 | 272:57 | 49.766
2020-08-10 | 273:57 | 49.765
2020-08-10 | 274:57 | 49.766
2020-08-10 | 275:57 | 49.768
2020-08-10 | 276:57 | 49.771
2020-08-10 | 277:57 | 49.773
2020-08-10 | 278:57 | 49.778
2020-08-10 | 279:57 | 49.78
2020-08-10 | 280:57 | 49.782
2020-08-10 | 281:57 | 49.785
2020-08-10 | 282:57 | 49.785
2020-08-10 | 283:57 | 49.783
2020-08-10 | 284:57 | 49.782
2020-08-10 | 285:57 | 49.782
2020-08-10 | 286:57 | 49.779
2020-08-10 | 287:57 | 49.778
2020-08-10 | 288:57 | 49.78
2020-08-10 | 289:57 | 49.784
2020-08-10 | 290:57 | 49.789
2020-08-10 | 291:57 | 49.797
2020-08-10 | 292:57 | 49.806
2020-08-10 | 293:57 | 49.813
2020-08-10 | 294:57 | 49.819
2020-08-10 | 295:57 | 49.825
2020-08-10 | 296:57 | 49.829
2020-08-10 | 297:57 | 49.834
2020-08-10 | 298:57 | 49.839
2020-08-10 | 299:57 | 49.844
2020-08-10 | 300:57 | 49.852
2020-08-10 | 301:57 | 49.857
2020-08-10 | 302:57 | 49.863
2020-08-10 | 303:57 | 49.866
2020-08-10 | 304:57 | 49.869
2020-08-10 | 305:57 | 49.871
2020-08-10 | 306:57 | 49.872
2020-08-10 | 307:57 | 49.872
2020-08-10 | 308:57 | 49.874
2020-08-10 | 309:57 | 49.876
2020-08-10 | 310:57 | 49.877
2020-08-10 | 311:57 | 49.877
2020-08-10 | 312:57 | 49.878
2020-08-10 | 313:57 | 49.877
2020-08-10 | 314:57 | 49.876
2020-08-10 | 315:57 | 49.875
2020-08-10 | 316:57 | 49.875
2020-08-10 | 317:57 | 49.873
2020-08-10 | 318:57 | 49.872
2020-08-10 | 319:57 | 49.87
2020-08-10 | 320:57 | 49.87
2020-08-10 | 321:57 | 49.869
2020-08-10 | 322:57 | 49.866
2020-08-10 | 323:57 | 49.865
2020-08-10 | 324:57 | 49.863
2020-08-10 | 325:57 | 49.863
2020-08-10 | 326:57 | 49.863
2020-08-10 | 327:57 | 49.863
2020-08-10 | 328:57 | 49.861
2020-08-10 | 329:57 | 49.86
2020-08-10 | 330:57 | 49.86
2020-08-10 | 331:57 | 49.861
2020-08-10 | 332:57 | 49.859
2020-08-10 | 333:57 | 49.859
2020-08-10 | 334:57 | 49.859
2020-08-10 | 335:57 | 49.861
2020-08-10 | 336:57 | 49.863
2020-08-10 | 337:57 | 49.866
2020-08-10 | 338:57 | 49.866
2020-08-10 | 339:57 | 49.866
2020-08-10 | 340:57 | 49.867
2020-08-10 | 341:57 | 49.868
2020-08-10 | 342:57 | 49.869
2020-08-10 | 343:57 | 49.871
2020-08-10 | 344:57 | 49.871
2020-08-10 | 345:57 | 49.87
2020-08-10 | 346:57 | 49.869
2020-08-10 | 347:57 | 49.871
2020-08-10 | 348:57 | 49.87
2020-08-10 | 349:57 | 49.872
2020-08-10 | 350:57 | 49.87
2020-08-10 | 351:57 | 49.87
2020-08-10 | 352:57 | 49.871
2020-08-10 | 353:57 | 49.873
2020-08-10 | 354:57 | 49.876
2020-08-10 | 355:57 | 49.878
2020-08-10 | 356:57 | 49.882
2020-08-10 | 357:57 | 49.884
2020-08-10 | 358:57 | 49.885
2020-08-10 | 359:57 | 49.885
2020-08-10 | 360:57 | 49.885
2020-08-10 | 361:57 | 49.885
2020-08-10 | 362:57 | 49.886
2020-08-10 | 363:57 | 49.889
2020-08-10 | 364:57 | 49.892
2020-08-10 | 365:57 | 49.894
2020-08-10 | 366:57 | 49.896
2020-08-10 | 367:57 | 49.899
2020-08-10 | 368:57 | 49.904
2020-08-10 | 369:57 | 49.906
2020-08-10 | 370:57 | 49.906
2020-08-10 | 371:57 | 49.907
2020-08-10 | 372:57 | 49.906
2020-08-10 | 373:57 | 49.904
2020-08-10 | 374:57 | 49.902
2020-08-10 | 375:57 | 49.901
2020-08-10 | 376:57 | 49.901
2020-08-10 | 377:57 | 49.903
2020-08-10 | 378:57 | 49.905
2020-08-10 | 379:57 | 49.905
2020-08-10 | 380:57 | 49.904
2020-08-10 | 381:57 | 49.904
2020-08-10 | 382:57 | 49.903
2020-08-10 | 383:57 | 49.903
2020-08-10 | 384:57 | 49.902
2020-08-10 | 385:57 | 49.903
2020-08-10 | 386:57 | 49.901
2020-08-10 | 387:57 | 49.9
2020-08-10 | 388:57 | 49.9
2020-08-10 | 389:57 | 49.9
2020-08-10 | 390:57 | 49.898
2020-08-10 | 391:57 | 49.899
2020-08-10 | 392:57 | 49.899
2020-08-10 | 393:57 | 49.898
2020-08-10 | 394:57 | 49.896
2020-08-10 | 395:57 | 49.893
2020-08-10 | 396:57 | 49.892
2020-08-10 | 397:57 | 49.889
2020-08-10 | 398:57 | 49.888
2020-08-10 | 399:57 | 49.886
2020-08-10 | 400:57 | 49.883
2020-08-10 | 401:57 | 49.879
2020-08-10 | 402:57 | 49.878
2020-08-10 | 403:57 | 49.875
2020-08-10 | 404:57 | 49.872
2020-08-10 | 405:57 | 49.871
2020-08-10 | 406:57 | 49.869
2020-08-10 | 407:57 | 49.867
2020-08-10 | 408:57 | 49.868
2020-08-10 | 409:57 | 49.868
2020-08-10 | 410:57 | 49.868
2020-08-10 | 411:57 | 49.867
2020-08-10 | 412:57 | 49.864
2020-08-10 | 413:57 | 49.862
2020-08-10 | 414:57 | 49.858
2020-08-10 | 415:57 | 49.854
2020-08-10 | 416:57 | 49.851
2020-08-10 | 417:57 | 49.847
2020-08-10 | 418:57 | 49.844
2020-08-10 | 419:57 | 49.843
2020-08-10 | 420:57 | 49.844
2020-08-10 | 421:57 | 49.843
2020-08-10 | 422:57 | 49.843
2020-08-10 | 423:57 | 49.843
2020-08-10 | 424:57 | 49.844
2020-08-10 | 425:57 | 49.843
2020-08-10 | 426:57 | 49.844
2020-08-10 | 427:57 | 49.845
2020-08-10 | 428:57 | 49.845
2020-08-10 | 429:57 | 49.845
2020-08-10 | 430:57 | 49.846
2020-08-10 | 431:57 | 49.845
2020-08-10 | 432:57 | 49.845
2020-08-10 | 433:57 | 49.845
2020-08-10 | 434:57 | 49.844
2020-08-10 | 435:57 | 49.842
2020-08-10 | 436:57 | 49.841
2020-08-10 | 437:57 | 49.838
2020-08-10 | 438:57 | 49.837
2020-08-10 | 439:57 | 49.837
2020-08-10 | 440:57 | 49.838
2020-08-10 | 441:57 | 49.84
2020-08-10 | 442:57 | 49.84
2020-08-10 | 443:57 | 49.84
2020-08-10 | 444:57 | 49.84
2020-08-10 | 445:57 | 49.84
2020-08-10 | 446:57 | 49.842
2020-08-10 | 447:57 | 49.844
2020-08-10 | 448:57 | 49.846
2020-08-10 | 449:57 | 49.85
2020-08-10 | 450:57 | 49.852
2020-08-10 | 451:57 | 49.854
2020-08-10 | 452:57 | 49.852
2020-08-10 | 453:57 | 49.852
2020-08-10 | 454:57 | 49.854
2020-08-10 | 455:57 | 49.854
2020-08-10 | 456:57 | 49.856
2020-08-10 | 457:57 | 49.857
2020-08-10 | 458:57 | 49.857
2020-08-10 | 459:57 | 49.859
2020-08-10 | 460:57 | 49.862
2020-08-10 | 461:57 | 49.87
2020-08-10 | 462:57 | 49.873
2020-08-10 | 463:57 | 49.88
2020-08-10 | 464:57 | 49.885
2020-08-10 | 465:57 | 49.888
2020-08-10 | 466:57 | 49.89
2020-08-10 | 467:57 | 49.893
2020-08-10 | 468:57 | 49.897
2020-08-10 | 469:57 | 49.9
2020-08-10 | 470:57 | 49.901
2020-08-10 | 471:57 | 49.903
2020-08-10 | 472:57 | 49.905
2020-08-10 | 473:57 | 49.908
2020-08-10 | 474:57 | 49.912
2020-08-10 | 475:57 | 49.915
2020-08-10 | 476:57 | 49.92
2020-08-10 | 477:57 | 49.92
2020-08-10 | 478:57 | 49.923
2020-08-10 | 479:57 | 49.926
2020-08-10 | 480:57 | 49.93
2020-08-10 | 481:57 | 49.935
2020-08-10 | 482:57 | 49.94
2020-08-10 | 483:57 | 49.944
2020-08-10 | 484:57 | 49.947
2020-08-10 | 485:57 | 49.95
2020-08-10 | 486:57 | 49.949
2020-08-10 | 487:57 | 49.948
2020-08-10 | 488:57 | 49.948
2020-08-10 | 489:57 | 49.946
2020-08-10 | 490:57 | 49.945
2020-08-10 | 491:57 | 49.945
2020-08-10 | 492:57 | 49.946
2020-08-10 | 493:57 | 49.947
2020-08-10 | 494:57 | 49.948
2020-08-10 | 495:57 | 49.949
2020-08-10 | 496:57 | 49.951
2020-08-10 | 497:57 | 49.952
2020-08-10 | 498:57 | 49.955
2020-08-10 | 499:57 | 49.957
2020-08-10 | 500:57 | 49.958
2020-08-10 | 501:57 | 49.959
2020-08-10 | 502:57 | 49.961
2020-08-10 | 503:57 | 49.962
2020-08-10 | 504:57 | 49.965
2020-08-10 | 505:57 | 49.965
2020-08-10 | 506:57 | 49.965
2020-08-10 | 507:57 | 49.966
2020-08-10 | 508:57 | 49.965
2020-08-10 | 509:57 | 49.967
2020-08-10 | 510:57 | 49.968
2020-08-10 | 511:57 | 49.97
2020-08-10 | 512:57 | 49.973
2020-08-10 | 513:57 | 49.975
2020-08-10 | 514:57 | 49.977
2020-08-10 | 515:57 | 49.978
2020-08-10 | 516:57 | 49.979
2020-08-10 | 517:57 | 49.982
2020-08-10 | 518:57 | 49.985
2020-08-10 | 519:57 | 49.987
2020-08-10 | 520:57 | 49.986
2020-08-10 | 521:57 | 49.987
2020-08-10 | 522:57 | 49.989
2020-08-10 | 523:57 | 49.991
2020-08-10 | 524:57 | 49.993
2020-08-10 | 525:57 | 49.997
2020-08-10 | 526:57 | 49.999
2020-08-10 | 527:57 | 50.002
2020-08-10 | 528:57 | 50.006
2020-08-10 | 529:57 | 50.01
2020-08-10 | 530:57 | 50.014
2020-08-10 | 531:57 | 50.018
2020-08-10 | 532:57 | 50.021
2020-08-10 | 533:57 | 50.023
2020-08-10 | 534:57 | 50.023
2020-08-10 | 535:57 | 50.021
2020-08-10 | 536:57 | 50.017
2020-08-10 | 537:57 | 50.015
2020-08-10 | 538:57 | 50.012
2020-08-10 | 539:57 | 50.014
2020-08-10 | 540:57 | 50.017
2020-08-10 | 541:57 | 50.018
2020-08-10 | 542:57 | 50.019
2020-08-10 | 543:57 | 50.019
2020-08-10 | 544:57 | 50.02
2020-08-10 | 545:57 | 50.02
2020-08-10 | 546:57 | 50.02
2020-08-10 | 547:57 | 50.02
2020-08-10 | 548:57 | 50.017
2020-08-10 | 549:57 | 50.014
2020-08-10 | 550:57 | 50.009
2020-08-10 | 551:57 | 50.007
2020-08-10 | 552:57 | 50.004
2020-08-10 | 553:57 | 50.003
2020-08-10 | 554:57 | 50
555:57
556:57
557:57
558:57
559:57
560:57
561:57
562:57
563:57
564:57
565:57
566:57
567:57
568:57
569:57
570:57
571:57
572:57
573:57
574:57
575:57
576:57
577:57
578:57
579:57
580:57
581:57
582:57
583:57
584:57
585:57
586:57
587:57
588:57
589:57
590:57
591:57
592:57
593:57
594:57
595:57
596:57
597:57
598:57
599:57
600:57
601:57
602:57
603:57
604:57
605:57
606:57
607:57
608:57
609:57
610:57
611:57
612:57
613:57
614:57
615:57
616:57
617:57
618:57
619:57
620:57
621:57
622:57
623:57
624:57
625:57
626:57
627:57
628:57
629:57
630:57
631:57
632:57
633:57
634:57
635:57
636:57
637:57
638:57
639:57
640:57
641:57
642:57
643:57
644:57
645:57
646:57
647:57
648:57
649:57
650:57
651:57
652:57
653:57
654:57
655:57
656:57
657:57
658:57
659:57
660:57
661:57
662:57
663:57
664:57
665:57
666:57
667:57
668:57
669:57
670:57
671:57
672:57
673:57
674:57
675:57
676:57
677:57
678:57
679:57
680:57
681:57
682:57
683:57
684:57
685:57
686:57
687:57
688:57
689:57
690:57
691:57
692:57
693:57
694:57
695:57
696:57
697:57
698:57
699:57
700:57
701:57
702:57
703:57
704:57
705:57
706:57
707:57
708:57
709:57
710:57
711:57
712:57
713:57
714:57
715:57
716:57
717:57
718:57
719:57
720:57
721:57
722:57
723:57
724:57
725:57
726:57
727:57
728:57
729:57
730:57
731:57
732:57
733:57
734:57
735:57
736:57
737:57
738:57
739:57
740:57
741:57
742:57
743:57
744:57
745:57
746:57
747:57
748:57
749:57
750:57
751:57
752:57
753:57
754:57
755:57
756:57
757:57
758:57
759:57
760:57
761:57
762:57
763:57
764:57
765:57
766:57
767:57
768:57
769:57
770:57
771:57
772:57
773:57
774:57
775:57
776:57
777:57
778:57
779:57
780:57
781:57
782:57
783:57
784:57
785:57
786:57
787:57
788:57
789:57
790:57
791:57
792:57
793:57
794:57
795:57
796:57
797:57
798:57
799:57
800:57
801:57
802:57
803:57
804:57
805:57
806:57
807:57
808:57
809:57
810:57
811:57
812:57
813:57
814:57
815:57
816:57
817:57
818:57
819:57
820:57
821:57
822:57
823:57
824:57
825:57
826:57
827:57
828:57
829:57
830:57
831:57
832:57
833:57
834:57
835:57
836:57
837:57
838:57
839:57
840:57
841:57
842:57
843:57
844:57
845:57
846:57
847:57
848:57
849:57
850:57
851:57
852:57
853:57
854:57
855:57
856:57
857:57
858:57
859:57
860:57
861:57
862:57
863:57
864:57
865:57
866:57
867:57
868:57
869:57
870:57
871:57
872:57
873:57
874:57
875:57
876:57
877:57
878:57
879:57
880:57
881:57
882:57
883:57
884:57
885:57
886:57
887:57
888:57
889:57
890:57
891:57
892:57
893:57
894:57
895:57
896:57
897:57
898:57
899:57
900:57
901:57
902:57
903:57
904:57
905:57
906:57
907:57
908:57
909:57
910:57
911:57
912:57
913:57
914:57

## Event 20200812-1
In UTC
Date | Time | Freq
2020-08-12 | 10:40 | 49.964
2020-08-12 | 10:40 | 49.965
2020-08-12 | 10:40 | 49.962
2020-08-12 | 10:40 | 49.963
2020-08-12 | 10:40 | 49.964
2020-08-12 | 11:40 | 49.966
2020-08-12 | 12:40 | 49.966
2020-08-12 | 13:40 | 49.969
2020-08-12 | 14:40 | 49.97
2020-08-12 | 15:40 | 49.97
2020-08-12 | 16:40 | 49.971
2020-08-12 | 17:40 | 49.971
2020-08-12 | 18:40 | 49.973
2020-08-12 | 19:40 | 49.971
2020-08-12 | 20:40 | 49.972
2020-08-12 | 21:40 | 49.976
2020-08-12 | 22:40 | 49.975
2020-08-12 | 23:40 | 49.977
2020-08-12 | 24:40 | 49.983
2020-08-12 | 25:40 | 49.982
2020-08-12 | 26:40 | 49.984
2020-08-12 | 27:40 | 49.985
2020-08-12 | 28:40 | 49.988
2020-08-12 | 29:40 | 49.986
2020-08-12 | 30:40 | 49.99
2020-08-12 | 31:40 | 49.992
2020-08-12 | 32:40 | 49.993
2020-08-12 | 33:40 | 49.992
2020-08-12 | 34:40 | 49.993
2020-08-12 | 35:40 | 49.981
2020-08-12 | 36:40 | 49.956
2020-08-12 | 37:40 | 49.941
2020-08-12 | 38:40 | 49.927
2020-08-12 | 39:40 | 49.919
2020-08-12 | 40:40 | 49.912
2020-08-12 | 41:40 | 49.907
2020-08-12 | 42:40 | 49.904
2020-08-12 | 43:40 | 49.904
2020-08-12 | 44:40 | 49.905
2020-08-12 | 45:40 | 49.906
2020-08-12 | 46:40 | 49.907
2020-08-12 | 47:40 | 49.905
2020-08-12 | 48:40 | 49.903
2020-08-12 | 49:40 | 49.903
2020-08-12 | 50:40 | 49.905
2020-08-12 | 51:40 | 49.908
2020-08-12 | 52:40 | 49.905
2020-08-12 | 53:40 | 49.907
2020-08-12 | 54:40 | 49.909
2020-08-12 | 55:40 | 49.905
2020-08-12 | 56:40 | 49.907
2020-08-12 | 57:40 | 49.906
2020-08-12 | 58:40 | 49.904
2020-08-12 | 59:40 | 49.906
2020-08-12 | 60:40 | 49.904
2020-08-12 | 61:40 | 49.904
2020-08-12 | 62:40 | 49.902
2020-08-12 | 63:40 | 49.903
2020-08-12 | 64:40 | 49.903
2020-08-12 | 65:40 | 49.903
2020-08-12 | 66:40 | 49.903
2020-08-12 | 67:40 | 49.903
2020-08-12 | 68:40 | 49.903
2020-08-12 | 69:40 | 49.903
2020-08-12 | 70:40 | 49.905
2020-08-12 | 71:40 | 49.903
2020-08-12 | 72:40 | 49.906
2020-08-12 | 73:40 | 49.904
2020-08-12 | 74:40 | 49.905
2020-08-12 | 75:40 | 49.904
2020-08-12 | 76:40 | 49.903
2020-08-12 | 77:40 | 49.908
2020-08-12 | 78:40 | 49.906
2020-08-12 | 79:40 | 49.91
2020-08-12 | 80:40 | 49.909
2020-08-12 | 81:40 | 49.909
2020-08-12 | 82:40 | 49.91
2020-08-12 | 83:40 | 49.909
2020-08-12 | 84:40 | 49.909
2020-08-12 | 85:40 | 49.911
2020-08-12 | 86:40 | 49.912
2020-08-12 | 87:40 | 49.909
2020-08-12 | 88:40 | 49.909
2020-08-12 | 89:40 | 49.908
2020-08-12 | 90:40 | 49.907
2020-08-12 | 91:40 | 49.908
2020-08-12 | 92:40 | 49.902
2020-08-12 | 93:40 | 49.9
2020-08-12 | 94:40 | 49.898
2020-08-12 | 95:40 | 49.897
2020-08-12 | 96:40 | 49.9
2020-08-12 | 97:40 | 49.899
2020-08-12 | 98:40 | 49.9
2020-08-12 | 99:40 | 49.903
2020-08-12 | 100:40 | 49.9
2020-08-12 | 101:40 | 49.9
2020-08-12 | 102:40 | 49.897
2020-08-12 | 103:40 | 49.893
2020-08-12 | 104:40 | 49.892
2020-08-12 | 105:40 | 49.887
2020-08-12 | 106:40 | 49.887
2020-08-12 | 107:40 | 49.887
2020-08-12 | 108:40 | 49.885
2020-08-12 | 109:40 | 49.883
2020-08-12 | 110:40 | 49.882
2020-08-12 | 111:40 | 49.882
2020-08-12 | 112:40 | 49.881
2020-08-12 | 113:40 | 49.884
2020-08-12 | 114:40 | 49.881
2020-08-12 | 115:40 | 49.884
2020-08-12 | 116:40 | 49.888
2020-08-12 | 117:40 | 49.884
2020-08-12 | 118:40 | 49.887
2020-08-12 | 119:40 | 49.884
2020-08-12 | 120:40 | 49.883
2020-08-12 | 121:40 | 49.884
2020-08-12 | 122:40 | 49.884
2020-08-12 | 123:40 | 49.884
2020-08-12 | 124:40 | 49.887
2020-08-12 | 125:40 | 49.888
2020-08-12 | 126:40 | 49.886
2020-08-12 | 127:40 | 49.889
2020-08-12 | 128:40 | 49.887
2020-08-12 | 129:40 | 49.888
2020-08-12 | 130:40 | 49.889
2020-08-12 | 131:40 | 49.888
2020-08-12 | 132:40 | 49.89
2020-08-12 | 133:40 | 49.888
2020-08-12 | 134:40 | 49.887
2020-08-12 | 135:40 | 49.891
2020-08-12 | 136:40 | 49.887
2020-08-12 | 137:40 | 49.883
2020-08-12 | 138:40 | 49.884
2020-08-12 | 139:40 | 49.883
2020-08-12 | 140:40 | 49.882
2020-08-12 | 141:40 | 49.883
2020-08-12 | 142:40 | 49.886
2020-08-12 | 143:40 | 49.883
2020-08-12 | 144:40 | 49.881
2020-08-12 | 145:40 | 49.88
2020-08-12 | 146:40 | 49.877
2020-08-12 | 147:40 | 49.876
2020-08-12 | 148:40 | 49.876
2020-08-12 | 149:40 | 49.877
2020-08-12 | 150:40 | 49.875
2020-08-12 | 151:40 | 49.875
2020-08-12 | 152:40 | 49.875
2020-08-12 | 153:40 | 49.876
2020-08-12 | 154:40 | 49.879
2020-08-12 | 155:40 | 49.878
2020-08-12 | 156:40 | 49.88
2020-08-12 | 157:40 | 49.88
2020-08-12 | 158:40 | 49.882
2020-08-12 | 159:40 | 49.883
2020-08-12 | 160:40 | 49.882
2020-08-12 | 161:40 | 49.886
2020-08-12 | 162:40 | 49.882
2020-08-12 | 163:40 | 49.878
2020-08-12 | 164:40 | 49.878
2020-08-12 | 165:40 | 49.877
2020-08-12 | 166:40 | 49.877
2020-08-12 | 167:40 | 49.881
2020-08-12 | 168:40 | 49.878
2020-08-12 | 169:40 | 49.874
2020-08-12 | 170:40 | 49.877
2020-08-12 | 171:40 | 49.878
2020-08-12 | 172:40 | 49.878
2020-08-12 | 173:40 | 49.882
2020-08-12 | 174:40 | 49.882
2020-08-12 | 175:40 | 49.885
2020-08-12 | 176:40 | 49.883
2020-08-12 | 177:40 | 49.886
2020-08-12 | 178:40 | 49.888
2020-08-12 | 179:40 | 49.887
2020-08-12 | 180:40 | 49.891
2020-08-12 | 181:40 | 49.89
2020-08-12 | 182:40 | 49.897
2020-08-12 | 183:40 | 49.898
2020-08-12 | 184:40 | 49.903
2020-08-12 | 185:40 | 49.906
2020-08-12 | 186:40 | 49.905
2020-08-12 | 187:40 | 49.908
2020-08-12 | 188:40 | 49.905
2020-08-12 | 189:40 | 49.905
2020-08-12 | 190:40 | 49.906
2020-08-12 | 191:40 | 49.903
2020-08-12 | 192:40 | 49.9
2020-08-12 | 193:40 | 49.9
2020-08-12 | 194:40 | 49.899
2020-08-12 | 195:40 | 49.899
2020-08-12 | 196:40 | 49.899
2020-08-12 | 197:40 | 49.899
2020-08-12 | 198:40 | 49.896
2020-08-12 | 199:40 | 49.901
2020-08-12 | 200:40 | 49.901
2020-08-12 | 201:40 | 49.901
2020-08-12 | 202:40 | 49.903
2020-08-12 | 203:40 | 49.907
2020-08-12 | 204:40 | 49.912
2020-08-12 | 205:40 | 49.913
2020-08-12 | 206:40 | 49.917
2020-08-12 | 207:40 | 49.918
2020-08-12 | 208:40 | 49.913
2020-08-12 | 209:40 | 49.916
2020-08-12 | 210:40 | 49.914
2020-08-12 | 211:40 | 49.914
2020-08-12 | 212:40 | 49.92
2020-08-12 | 213:40 | 49.922
2020-08-12 | 214:40 | 49.922
2020-08-12 | 215:40 | 49.925
2020-08-12 | 216:40 | 49.926
2020-08-12 | 217:40 | 49.926
2020-08-12 | 218:40 | 49.926
2020-08-12 | 219:40 | 49.921
2020-08-12 | 220:40 | 49.923
2020-08-12 | 221:40 | 49.92
2020-08-12 | 222:40 | 49.921
2020-08-12 | 223:40 | 49.922
2020-08-12 | 224:40 | 49.924
2020-08-12 | 225:40 | 49.932
2020-08-12 | 226:40 | 49.932
2020-08-12 | 227:40 | 49.934
2020-08-12 | 228:40 | 49.934
2020-08-12 | 229:40 | 49.934
2020-08-12 | 230:40 | 49.934
2020-08-12 | 231:40 | 49.936
2020-08-12 | 232:40 | 49.934
2020-08-12 | 233:40 | 49.932
2020-08-12 | 234:40 | 49.931
2020-08-12 | 235:40 | 49.93
2020-08-12 | 236:40 | 49.927
2020-08-12 | 237:40 | 49.927
2020-08-12 | 238:40 | 49.923
2020-08-12 | 239:40 | 49.919
2020-08-12 | 240:40 | 49.92
2020-08-12 | 241:40 | 49.919
2020-08-12 | 242:40 | 49.917
2020-08-12 | 243:40 | 49.917
2020-08-12 | 244:40 | 49.917
2020-08-12 | 245:40 | 49.913
2020-08-12 | 246:40 | 49.908
2020-08-12 | 247:40 | 49.905
2020-08-12 | 248:40 | 49.907
2020-08-12 | 249:40 | 49.905
2020-08-12 | 250:40 | 49.902
2020-08-12 | 251:40 | 49.901
2020-08-12 | 252:40 | 49.903
2020-08-12 | 253:40 | 49.903
2020-08-12 | 254:40 | 49.903
2020-08-12 | 255:40 | 49.902
2020-08-12 | 256:40 | 49.903
2020-08-12 | 257:40 | 49.906
2020-08-12 | 258:40 | 49.909
2020-08-12 | 259:40 | 49.913
2020-08-12 | 260:40 | 49.913
2020-08-12 | 261:40 | 49.912
2020-08-12 | 262:40 | 49.911
2020-08-12 | 263:40 | 49.91
2020-08-12 | 264:40 | 49.91
2020-08-12 | 265:40 | 49.908
2020-08-12 | 266:40 | 49.904
2020-08-12 | 267:40 | 49.902
2020-08-12 | 268:40 | 49.9
2020-08-12 | 269:40 | 49.901
2020-08-12 | 270:40 | 49.902
2020-08-12 | 271:40 | 49.902
2020-08-12 | 272:40 | 49.899
2020-08-12 | 273:40 | 49.897
2020-08-12 | 274:40 | 49.896
2020-08-12 | 275:40 | 49.895
2020-08-12 | 276:40 | 49.894
2020-08-12 | 277:40 | 49.895
2020-08-12 | 278:40 | 49.895
2020-08-12 | 279:40 | 49.894
2020-08-12 | 280:40 | 49.892
2020-08-12 | 281:40 | 49.889
2020-08-12 | 282:40 | 49.891
2020-08-12 | 283:40 | 49.893
2020-08-12 | 284:40 | 49.895
2020-08-12 | 285:40 | 49.894
2020-08-12 | 286:40 | 49.894
2020-08-12 | 287:40 | 49.895
2020-08-12 | 288:40 | 49.893
2020-08-12 | 289:40 | 49.893
2020-08-12 | 290:40 | 49.894
2020-08-12 | 291:40 | 49.892
2020-08-12 | 292:40 | 49.892
2020-08-12 | 293:40 | 49.89
2020-08-12 | 294:40 | 49.891
2020-08-12 | 295:40 | 49.892
2020-08-12 | 296:40 | 49.89
2020-08-12 | 297:40 | 49.891
2020-08-12 | 298:40 | 49.893
2020-08-12 | 299:40 | 49.896
2020-08-12 | 300:40 | 49.898
2020-08-12 | 301:40 | 49.897
2020-08-12 | 302:40 | 49.895
2020-08-12 | 303:40 | 49.894
2020-08-12 | 304:40 | 49.895
2020-08-12 | 305:40 | 49.893
2020-08-12 | 306:40 | 49.89
2020-08-12 | 307:40 | 49.893
2020-08-12 | 308:40 | 49.887
2020-08-12 | 309:40 | 49.885
2020-08-12 | 310:40 | 49.882
2020-08-12 | 311:40 | 49.881
2020-08-12 | 312:40 | 49.878
2020-08-12 | 313:40 | 49.876
2020-08-12 | 314:40 | 49.872
2020-08-12 | 315:40 | 49.87
2020-08-12 | 316:40 | 49.869
2020-08-12 | 317:40 | 49.869
2020-08-12 | 318:40 | 49.869
2020-08-12 | 319:40 | 49.871
2020-08-12 | 320:40 | 49.871
2020-08-12 | 321:40 | 49.869
2020-08-12 | 322:40 | 49.872
2020-08-12 | 323:40 | 49.873
2020-08-12 | 324:40 | 49.873
2020-08-12 | 325:40 | 49.877
2020-08-12 | 326:40 | 49.873
2020-08-12 | 327:40 | 49.875
2020-08-12 | 328:40 | 49.88
2020-08-12 | 329:40 | 49.879
2020-08-12 | 330:40 | 49.88
2020-08-12 | 331:40 | 49.884
2020-08-12 | 332:40 | 49.887
2020-08-12 | 333:40 | 49.891
2020-08-12 | 334:40 | 49.892
2020-08-12 | 335:40 | 49.889
2020-08-12 | 336:40 | 49.886
2020-08-12 | 337:40 | 49.892
2020-08-12 | 338:40 | 49.892
2020-08-12 | 339:40 | 49.888
2020-08-12 | 340:40 | 49.888
2020-08-12 | 341:40 | 49.89
2020-08-12 | 342:40 | 49.894
2020-08-12 | 343:40 | 49.89
2020-08-12 | 344:40 | 49.895
2020-08-12 | 345:40 | 49.894
2020-08-12 | 346:40 | 49.895
2020-08-12 | 347:40 | 49.894
2020-08-12 | 348:40 | 49.896
2020-08-12 | 349:40 | 49.893
2020-08-12 | 350:40 | 49.897
2020-08-12 | 351:40 | 49.894
2020-08-12 | 352:40 | 49.895
2020-08-12 | 353:40 | 49.894
2020-08-12 | 354:40 | 49.889
2020-08-12 | 355:40 | 49.891
2020-08-12 | 356:40 | 49.888
2020-08-12 | 357:40 | 49.888
2020-08-12 | 358:40 | 49.89
2020-08-12 | 359:40 | 49.891
2020-08-12 | 360:40 | 49.889
2020-08-12 | 361:40 | 49.893
2020-08-12 | 362:40 | 49.894
2020-08-12 | 363:40 | 49.899
2020-08-12 | 364:40 | 49.9
2020-08-12 | 365:40 | 49.899
2020-08-12 | 366:40 | 49.904
2020-08-12 | 367:40 | 49.902
2020-08-12 | 368:40 | 49.906
2020-08-12 | 369:40 | 49.904
2020-08-12 | 370:40 | 49.898
2020-08-12 | 371:40 | 49.895
2020-08-12 | 372:40 | 49.894
2020-08-12 | 373:40 | 49.892
2020-08-12 | 374:40 | 49.888
2020-08-12 | 375:40 | 49.891
2020-08-12 | 376:40 | 49.888
2020-08-12 | 377:40 | 49.887
2020-08-12 | 378:40 | 49.886
2020-08-12 | 379:40 | 49.887
2020-08-12 | 380:40 | 49.889
2020-08-12 | 381:40 | 49.891
2020-08-12 | 382:40 | 49.889
2020-08-12 | 383:40 | 49.894
2020-08-12 | 384:40 | 49.895
2020-08-12 | 385:40 | 49.897
2020-08-12 | 386:40 | 49.896
2020-08-12 | 387:40 | 49.896
2020-08-12 | 388:40 | 49.897
2020-08-12 | 389:40 | 49.896
2020-08-12 | 390:40 | 49.894
2020-08-12 | 391:40 | 49.892
2020-08-12 | 392:40 | 49.892
2020-08-12 | 393:40 | 49.892
2020-08-12 | 394:40 | 49.887
2020-08-12 | 395:40 | 49.887
2020-08-12 | 396:40 | 49.886
2020-08-12 | 397:40 | 49.884
2020-08-12 | 398:40 | 49.886
2020-08-12 | 399:40 | 49.887
2020-08-12 | 400:40 | 49.892
2020-08-12 | 401:40 | 49.889
2020-08-12 | 402:40 | 49.891
2020-08-12 | 403:40 | 49.891
2020-08-12 | 404:40 | 49.893
2020-08-12 | 405:40 | 49.893
2020-08-12 | 406:40 | 49.892
2020-08-12 | 407:40 | 49.893
2020-08-12 | 408:40 | 49.894
2020-08-12 | 409:40 | 49.896
2020-08-12 | 410:40 | 49.899
2020-08-12 | 411:40 | 49.897
2020-08-12 | 412:40 | 49.896
2020-08-12 | 413:40 | 49.898
2020-08-12 | 414:40 | 49.896
2020-08-12 | 415:40 | 49.897
2020-08-12 | 416:40 | 49.898
2020-08-12 | 417:40 | 49.896
2020-08-12 | 418:40 | 49.896
2020-08-12 | 419:40 | 49.894
2020-08-12 | 420:40 | 49.892
2020-08-12 | 421:40 | 49.894
2020-08-12 | 422:40 | 49.895
2020-08-12 | 423:40 | 49.902
2020-08-12 | 424:40 | 49.898
2020-08-12 | 425:40 | 49.897
2020-08-12 | 426:40 | 49.894
2020-08-12 | 427:40 | 49.894
2020-08-12 | 428:40 | 49.893
2020-08-12 | 429:40 | 49.891
2020-08-12 | 430:40 | 49.89
2020-08-12 | 431:40 | 49.886
2020-08-12 | 432:40 | 49.887
2020-08-12 | 433:40 | 49.884
2020-08-12 | 434:40 | 49.887
2020-08-12 | 435:40 | 49.888
2020-08-12 | 436:40 | 49.89
2020-08-12 | 437:40 | 49.893
2020-08-12 | 438:40 | 49.897
2020-08-12 | 439:40 | 49.898
2020-08-12 | 440:40 | 49.895
2020-08-12 | 441:40 | 49.902
2020-08-12 | 442:40 | 49.901
2020-08-12 | 443:40 | 49.9
2020-08-12 | 444:40 | 49.906
2020-08-12 | 445:40 | 49.908
2020-08-12 | 446:40 | 49.906
2020-08-12 | 447:40 | 49.907
2020-08-12 | 448:40 | 49.911
2020-08-12 | 449:40 | 49.911
2020-08-12 | 450:40 | 49.912
2020-08-12 | 451:40 | 49.91
2020-08-12 | 452:40 | 49.907
2020-08-12 | 453:40 | 49.908
2020-08-12 | 454:40 | 49.91
2020-08-12 | 455:40 | 49.912
2020-08-12 | 456:40 | 49.914
2020-08-12 | 457:40 | 49.913
2020-08-12 | 458:40 | 49.917
2020-08-12 | 459:40 | 49.917
2020-08-12 | 460:40 | 49.912
2020-08-12 | 461:40 | 49.911
2020-08-12 | 462:40 | 49.911
2020-08-12 | 463:40 | 49.905
2020-08-12 | 464:40 | 49.908
2020-08-12 | 465:40 | 49.907
2020-08-12 | 466:40 | 49.91
2020-08-12 | 467:40 | 49.911
2020-08-12 | 468:40 | 49.913
2020-08-12 | 469:40 | 49.911
2020-08-12 | 470:40 | 49.914
2020-08-12 | 471:40 | 49.909
2020-08-12 | 472:40 | 49.914
2020-08-12 | 473:40 | 49.915
2020-08-12 | 474:40 | 49.917
2020-08-12 | 475:40 | 49.916
2020-08-12 | 476:40 | 49.918
2020-08-12 | 477:40 | 49.918
2020-08-12 | 478:40 | 49.922
2020-08-12 | 479:40 | 49.925
2020-08-12 | 480:40 | 49.924
2020-08-12 | 481:40 | 49.925
2020-08-12 | 482:40 | 49.922
2020-08-12 | 483:40 | 49.924
2020-08-12 | 484:40 | 49.921
2020-08-12 | 485:40 | 49.917
2020-08-12 | 486:40 | 49.916
2020-08-12 | 487:40 | 49.91
2020-08-12 | 488:40 | 49.908
2020-08-12 | 489:40 | 49.907
2020-08-12 | 490:40 | 49.907
2020-08-12 | 491:40 | 49.905
2020-08-12 | 492:40 | 49.905
2020-08-12 | 493:40 | 49.903
2020-08-12 | 494:40 | 49.904
2020-08-12 | 495:40 | 49.906
2020-08-12 | 496:40 | 49.909
2020-08-12 | 497:40 | 49.913
2020-08-12 | 498:40 | 49.913
2020-08-12 | 499:40 | 49.915
2020-08-12 | 500:40 | 49.918
2020-08-12 | 501:40 | 49.92
2020-08-12 | 502:40 | 49.92
2020-08-12 | 503:40 | 49.925
2020-08-12 | 504:40 | 49.923
2020-08-12 | 505:40 | 49.924
2020-08-12 | 506:40 | 49.921
2020-08-12 | 507:40 | 49.921
2020-08-12 | 508:40 | 49.919
2020-08-12 | 509:40 | 49.922
2020-08-12 | 510:40 | 49.916
2020-08-12 | 511:40 | 49.919
2020-08-12 | 512:40 | 49.914
2020-08-12 | 513:40 | 49.911
2020-08-12 | 514:40 | 49.914
2020-08-12 | 515:40 | 49.911
2020-08-12 | 516:40 | 49.912
2020-08-12 | 517:40 | 49.912
2020-08-12 | 518:40 | 49.916
2020-08-12 | 519:40 | 49.916
2020-08-12 | 520:40 | 49.912
2020-08-12 | 521:40 | 49.918
2020-08-12 | 522:40 | 49.921
2020-08-12 | 523:40 | 49.923
2020-08-12 | 524:40 | 49.922
2020-08-12 | 525:40 | 49.921
2020-08-12 | 526:40 | 49.925
2020-08-12 | 527:40 | 49.928
2020-08-12 | 528:40 | 49.929
2020-08-12 | 529:40 | 49.929
2020-08-12 | 530:40 | 49.93
2020-08-12 | 531:40 | 49.932
2020-08-12 | 532:40 | 49.933
2020-08-12 | 533:40 | 49.935
2020-08-12 | 534:40 | 49.938
2020-08-12 | 535:40 | 49.937
2020-08-12 | 536:40 | 49.935
2020-08-12 | 537:40 | 49.936
2020-08-12 | 538:40 | 49.935
2020-08-12 | 539:40 | 49.934
2020-08-12 | 540:40 | 49.934
2020-08-12 | 541:40 | 49.937
2020-08-12 | 542:40 | 49.939
2020-08-12 | 543:40 | 49.94
2020-08-12 | 544:40 | 49.94
2020-08-12 | 545:40 | 49.945
2020-08-12 | 546:40 | 49.944
2020-08-12 | 547:40 | 49.943
2020-08-12 | 548:40 | 49.943
2020-08-12 | 549:40 | 49.942
2020-08-12 | 550:40 | 49.942
2020-08-12 | 551:40 | 49.941
2020-08-12 | 552:40 | 49.942
2020-08-12 | 553:40 | 49.943
2020-08-12 | 554:40 | 49.945
2020-08-12 | 555:40 | 49.944
2020-08-12 | 556:40 | 49.94
2020-08-12 | 557:40 | 49.938
2020-08-12 | 558:40 | 49.937
2020-08-12 | 559:40 | 49.938
2020-08-12 | 560:40 | 49.938
2020-08-12 | 561:40 | 49.939
2020-08-12 | 562:40 | 49.941
2020-08-12 | 563:40 | 49.941
2020-08-12 | 564:40 | 49.943
2020-08-12 | 565:40 | 49.947
2020-08-12 | 566:40 | 49.951
2020-08-12 | 567:40 | 49.952
2020-08-12 | 568:40 | 49.956
2020-08-12 | 569:40 | 49.958
2020-08-12 | 570:40 | 49.961
2020-08-12 | 571:40 | 49.962
2020-08-12 | 572:40 | 49.964
2020-08-12 | 573:40 | 49.963
2020-08-12 | 574:40 | 49.963
2020-08-12 | 575:40 | 49.965
2020-08-12 | 576:40 | 49.964
2020-08-12 | 577:40 | 49.965
2020-08-12 | 578:40 | 49.962
2020-08-12 | 579:40 | 49.961
2020-08-12 | 580:40 | 49.962
2020-08-12 | 581:40 | 49.964
2020-08-12 | 582:40 | 49.967
2020-08-12 | 583:40 | 49.97
2020-08-12 | 584:40 | 49.97
2020-08-12 | 585:40 | 49.971
2020-08-12 | 586:40 | 49.97
2020-08-12 | 587:40 | 49.969
2020-08-12 | 588:40 | 49.97
2020-08-12 | 589:40 | 49.97
2020-08-12 | 590:40 | 49.972
2020-08-12 | 591:40 | 49.974
2020-08-12 | 592:40 | 49.976
2020-08-12 | 593:40 | 49.98
2020-08-12 | 594:40 | 49.982
2020-08-12 | 595:40 | 49.985
2020-08-12 | 596:40 | 49.988
2020-08-12 | 597:40 | 49.986
2020-08-12 | 598:40 | 49.988
2020-08-12 | 599:40 | 49.99
2020-08-12 | 600:40 | 49.992
2020-08-12 | 601:40 | 49.993
2020-08-12 | 602:40 | 49.994
2020-08-12 | 603:40 | 49.995
2020-08-12 | 604:40 | 50
2020-08-12 | 605:40 | 50.001
606:40
607:40
608:40
609:40
610:40
611:40
612:40
613:40
614:40
615:40
616:40
617:40
618:40
619:40
620:40
621:40
622:40
623:40
624:40
625:40
626:40
627:40
628:40
629:40
630:40
631:40
632:40
633:40
634:40
635:40
636:40
637:40
638:40
639:40
640:40
641:40
642:40
643:40
644:40
645:40
646:40
647:40
648:40
649:40
650:40
651:40
652:40
653:40
654:40
655:40
656:40
657:40
658:40
659:40
660:40
661:40
662:40
663:40
664:40
665:40
666:40
667:40
668:40
669:40
670:40
671:40
672:40
673:40
674:40
675:40
676:40
677:40
678:40
679:40
680:40
681:40
682:40
683:40
684:40
685:40
686:40
687:40
688:40
689:40
690:40
691:40
692:40
693:40
694:40
695:40
696:40
697:40
698:40
699:40
700:40
701:40
702:40
703:40
704:40
705:40
706:40
707:40
708:40
709:40
710:40
711:40
712:40
713:40
714:40
715:40
716:40
717:40
718:40
719:40
720:40
721:40
722:40
723:40
724:40
725:40
726:40
727:40
728:40
729:40
730:40
731:40
732:40
733:40
734:40
735:40
736:40
737:40
738:40
739:40
740:40
741:40
742:40
743:40
744:40
745:40
746:40
747:40
748:40
749:40
750:40
751:40
752:40
753:40
754:40
755:40
756:40
757:40
758:40
759:40
760:40
761:40
762:40
763:40
764:40
765:40
766:40
767:40
768:40
769:40
770:40
771:40
772:40
773:40
774:40
775:40
776:40
777:40
778:40
779:40
780:40
781:40
782:40
783:40
784:40
785:40
786:40
787:40
788:40
789:40
790:40
791:40
792:40
793:40
794:40
795:40
796:40
797:40
798:40
799:40
800:40
801:40
802:40
803:40
804:40
805:40
806:40
807:40
808:40
809:40
810:40
811:40
812:40
813:40
814:40
815:40
816:40
817:40
818:40
819:40
820:40
821:40
822:40
823:40
824:40
825:40
826:40
827:40
828:40
829:40
830:40
831:40
832:40
833:40
834:40
835:40
836:40
837:40
838:40
839:40
840:40
841:40
842:40
843:40
844:40
845:40
846:40
847:40
848:40
849:40
850:40
851:40
852:40
853:40
854:40
855:40
856:40
857:40
858:40
859:40
860:40
861:40
862:40
863:40
864:40
865:40
866:40
867:40
868:40
869:40
870:40
871:40
872:40
873:40
874:40
875:40
876:40
877:40
878:40
879:40
880:40
881:40
882:40
883:40
884:40
885:40
886:40
887:40
888:40
889:40
890:40
891:40
892:40
893:40
894:40
895:40
896:40
897:40
898:40
899:40
900:40
901:40
902:40
903:40
904:40
905:40

## Event 20200813-1
In UTC
Date | Time | Freq
2020-08-13 | 4:50 | 49.976
2020-08-13 | 4:50 | 49.975
2020-08-13 | 4:50 | 49.975
2020-08-13 | 4:50 | 49.974
2020-08-13 | 4:50 | 49.974
2020-08-13 | 5:50 | 49.973
2020-08-13 | 6:50 | 49.974
2020-08-13 | 7:50 | 49.973
2020-08-13 | 8:50 | 49.972
2020-08-13 | 9:50 | 49.97
2020-08-13 | 10:50 | 49.97
2020-08-13 | 11:50 | 49.969
2020-08-13 | 12:50 | 49.97
2020-08-13 | 13:50 | 49.971
2020-08-13 | 14:50 | 49.973
2020-08-13 | 15:50 | 49.973
2020-08-13 | 16:50 | 49.973
2020-08-13 | 17:50 | 49.977
2020-08-13 | 18:50 | 49.976
2020-08-13 | 19:50 | 49.975
2020-08-13 | 20:50 | 49.976
2020-08-13 | 21:50 | 49.977
2020-08-13 | 22:50 | 49.977
2020-08-13 | 23:50 | 49.978
2020-08-13 | 24:50 | 49.975
2020-08-13 | 25:50 | 49.973
2020-08-13 | 26:50 | 49.971
2020-08-13 | 27:50 | 49.971
2020-08-13 | 28:50 | 49.973
2020-08-13 | 29:50 | 49.972
2020-08-13 | 30:50 | 49.973
2020-08-13 | 31:50 | 49.976
2020-08-13 | 32:50 | 49.979
2020-08-13 | 33:50 | 49.981
2020-08-13 | 34:50 | 49.985
2020-08-13 | 35:50 | 49.988
2020-08-13 | 36:50 | 49.991
2020-08-13 | 37:50 | 49.995
2020-08-13 | 38:50 | 49.997
2020-08-13 | 39:50 | 49.999
2020-08-13 | 40:50 | 49.999
2020-08-13 | 41:50 | 50
2020-08-13 | 42:50 | 50.002
2020-08-13 | 43:50 | 50.002
2020-08-13 | 44:50 | 50.006
2020-08-13 | 45:50 | 50.01
2020-08-13 | 46:50 | 50.013
2020-08-13 | 47:50 | 50.016
2020-08-13 | 48:50 | 50.018
2020-08-13 | 49:50 | 50.018
2020-08-13 | 50:50 | 50.018
2020-08-13 | 51:50 | 50.015
2020-08-13 | 52:50 | 50.014
2020-08-13 | 53:50 | 50.011
2020-08-13 | 54:50 | 50.01
2020-08-13 | 55:50 | 50.009
2020-08-13 | 56:50 | 50.007
2020-08-13 | 57:50 | 50.006
2020-08-13 | 58:50 | 50.001
2020-08-13 | 59:50 | 49.998
2020-08-13 | 60:50 | 49.993
2020-08-13 | 61:50 | 49.988
2020-08-13 | 62:50 | 49.987
2020-08-13 | 63:50 | 49.984
2020-08-13 | 64:50 | 49.983
2020-08-13 | 65:50 | 49.981
2020-08-13 | 66:50 | 49.982
2020-08-13 | 67:50 | 49.982
2020-08-13 | 68:50 | 49.982
2020-08-13 | 69:50 | 49.983
2020-08-13 | 70:50 | 49.982
2020-08-13 | 71:50 | 49.98
2020-08-13 | 72:50 | 49.98
2020-08-13 | 73:50 | 49.98
2020-08-13 | 74:50 | 49.98
2020-08-13 | 75:50 | 49.981
2020-08-13 | 76:50 | 49.981
2020-08-13 | 77:50 | 49.981
2020-08-13 | 78:50 | 49.982
2020-08-13 | 79:50 | 49.983
2020-08-13 | 80:50 | 49.985
2020-08-13 | 81:50 | 49.984
2020-08-13 | 82:50 | 49.986
2020-08-13 | 83:50 | 49.985
2020-08-13 | 84:50 | 49.986
2020-08-13 | 85:50 | 49.984
2020-08-13 | 86:50 | 49.984
2020-08-13 | 87:50 | 49.983
2020-08-13 | 88:50 | 49.981
2020-08-13 | 89:50 | 49.981
2020-08-13 | 90:50 | 49.979
2020-08-13 | 91:50 | 49.978
2020-08-13 | 92:50 | 49.979
2020-08-13 | 93:50 | 49.979
2020-08-13 | 94:50 | 49.98
2020-08-13 | 95:50 | 49.98
2020-08-13 | 96:50 | 49.98
2020-08-13 | 97:50 | 49.978
2020-08-13 | 98:50 | 49.977
2020-08-13 | 99:50 | 49.977
2020-08-13 | 100:50 | 49.977
2020-08-13 | 101:50 | 49.976
2020-08-13 | 102:50 | 49.974
2020-08-13 | 103:50 | 49.975
2020-08-13 | 104:50 | 49.978
2020-08-13 | 105:50 | 49.978
2020-08-13 | 106:50 | 49.98
2020-08-13 | 107:50 | 49.98
2020-08-13 | 108:50 | 49.98
2020-08-13 | 109:50 | 49.979
2020-08-13 | 110:50 | 49.977
2020-08-13 | 111:50 | 49.978
2020-08-13 | 112:50 | 49.978
2020-08-13 | 113:50 | 49.979
2020-08-13 | 114:50 | 49.98
2020-08-13 | 115:50 | 49.978
2020-08-13 | 116:50 | 49.981
2020-08-13 | 117:50 | 49.982
2020-08-13 | 118:50 | 49.98
2020-08-13 | 119:50 | 49.979
2020-08-13 | 120:50 | 49.979
2020-08-13 | 121:50 | 49.981
2020-08-13 | 122:50 | 49.98
2020-08-13 | 123:50 | 49.981
2020-08-13 | 124:50 | 49.985
2020-08-13 | 125:50 | 49.985
2020-08-13 | 126:50 | 49.987
2020-08-13 | 127:50 | 49.989
2020-08-13 | 128:50 | 49.988
2020-08-13 | 129:50 | 49.987
2020-08-13 | 130:50 | 49.986
2020-08-13 | 131:50 | 49.987
2020-08-13 | 132:50 | 49.989
2020-08-13 | 133:50 | 49.988
2020-08-13 | 134:50 | 49.986
2020-08-13 | 135:50 | 49.985
2020-08-13 | 136:50 | 49.983
2020-08-13 | 137:50 | 49.983
2020-08-13 | 138:50 | 49.982
2020-08-13 | 139:50 | 49.981
2020-08-13 | 140:50 | 49.978
2020-08-13 | 141:50 | 49.977
2020-08-13 | 142:50 | 49.973
2020-08-13 | 143:50 | 49.969
2020-08-13 | 144:50 | 49.971
2020-08-13 | 145:50 | 49.974
2020-08-13 | 146:50 | 49.977
2020-08-13 | 147:50 | 49.979
2020-08-13 | 148:50 | 49.98
2020-08-13 | 149:50 | 49.982
2020-08-13 | 150:50 | 49.981
2020-08-13 | 151:50 | 49.982
2020-08-13 | 152:50 | 49.98
2020-08-13 | 153:50 | 49.979
2020-08-13 | 154:50 | 49.978
2020-08-13 | 155:50 | 49.976
2020-08-13 | 156:50 | 49.976
2020-08-13 | 157:50 | 49.975
2020-08-13 | 158:50 | 49.977
2020-08-13 | 159:50 | 49.978
2020-08-13 | 160:50 | 49.979
2020-08-13 | 161:50 | 49.981
2020-08-13 | 162:50 | 49.983
2020-08-13 | 163:50 | 49.986
2020-08-13 | 164:50 | 49.987
2020-08-13 | 165:50 | 49.99
2020-08-13 | 166:50 | 49.991
2020-08-13 | 167:50 | 49.996
2020-08-13 | 168:50 | 49.997
2020-08-13 | 169:50 | 49.995
2020-08-13 | 170:50 | 49.996
2020-08-13 | 171:50 | 49.995
2020-08-13 | 172:50 | 49.994
2020-08-13 | 173:50 | 49.992
2020-08-13 | 174:50 | 49.991
2020-08-13 | 175:50 | 49.989
2020-08-13 | 176:50 | 49.989
2020-08-13 | 177:50 | 49.987
2020-08-13 | 178:50 | 49.988
2020-08-13 | 179:50 | 49.986
2020-08-13 | 180:50 | 49.981
2020-08-13 | 181:50 | 49.979
2020-08-13 | 182:50 | 49.98
2020-08-13 | 183:50 | 49.98
2020-08-13 | 184:50 | 49.983
2020-08-13 | 185:50 | 49.98
2020-08-13 | 186:50 | 49.979
2020-08-13 | 187:50 | 49.975
2020-08-13 | 188:50 | 49.974
2020-08-13 | 189:50 | 49.975
2020-08-13 | 190:50 | 49.977
2020-08-13 | 191:50 | 49.977
2020-08-13 | 192:50 | 49.976
2020-08-13 | 193:50 | 49.976
2020-08-13 | 194:50 | 49.979
2020-08-13 | 195:50 | 49.979
2020-08-13 | 196:50 | 49.983
2020-08-13 | 197:50 | 49.985
2020-08-13 | 198:50 | 49.988
2020-08-13 | 199:50 | 49.989
2020-08-13 | 200:50 | 49.987
2020-08-13 | 201:50 | 49.986
2020-08-13 | 202:50 | 49.985
2020-08-13 | 203:50 | 49.981
2020-08-13 | 204:50 | 49.98
2020-08-13 | 205:50 | 49.98
2020-08-13 | 206:50 | 49.979
2020-08-13 | 207:50 | 49.978
2020-08-13 | 208:50 | 49.977
2020-08-13 | 209:50 | 49.978
2020-08-13 | 210:50 | 49.978
2020-08-13 | 211:50 | 49.98
2020-08-13 | 212:50 | 49.981
2020-08-13 | 213:50 | 49.983
2020-08-13 | 214:50 | 49.986
2020-08-13 | 215:50 | 49.988
2020-08-13 | 216:50 | 49.99
2020-08-13 | 217:50 | 49.991
2020-08-13 | 218:50 | 49.992
2020-08-13 | 219:50 | 49.99
2020-08-13 | 220:50 | 49.992
2020-08-13 | 221:50 | 49.992
2020-08-13 | 222:50 | 49.99
2020-08-13 | 223:50 | 49.989
2020-08-13 | 224:50 | 49.989
2020-08-13 | 225:50 | 49.986
2020-08-13 | 226:50 | 49.982
2020-08-13 | 227:50 | 49.977
2020-08-13 | 228:50 | 49.975
2020-08-13 | 229:50 | 49.972
2020-08-13 | 230:50 | 49.971
2020-08-13 | 231:50 | 49.972
2020-08-13 | 232:50 | 49.974
2020-08-13 | 233:50 | 49.977
2020-08-13 | 234:50 | 49.979
2020-08-13 | 235:50 | 49.982
2020-08-13 | 236:50 | 49.982
2020-08-13 | 237:50 | 49.982
2020-08-13 | 238:50 | 49.981
2020-08-13 | 239:50 | 49.98
2020-08-13 | 240:50 | 49.977
2020-08-13 | 241:50 | 49.977
2020-08-13 | 242:50 | 49.979
2020-08-13 | 243:50 | 49.982
2020-08-13 | 244:50 | 49.985
2020-08-13 | 245:50 | 49.984
2020-08-13 | 246:50 | 49.983
2020-08-13 | 247:50 | 49.983
2020-08-13 | 248:50 | 49.983
2020-08-13 | 249:50 | 49.982
2020-08-13 | 250:50 | 49.982
2020-08-13 | 251:50 | 49.981
2020-08-13 | 252:50 | 49.98
2020-08-13 | 253:50 | 49.979
2020-08-13 | 254:50 | 49.979
2020-08-13 | 255:50 | 49.982
2020-08-13 | 256:50 | 49.982
2020-08-13 | 257:50 | 49.983
2020-08-13 | 258:50 | 49.985
2020-08-13 | 259:50 | 49.986
2020-08-13 | 260:50 | 49.987
2020-08-13 | 261:50 | 49.988
2020-08-13 | 262:50 | 49.988
2020-08-13 | 263:50 | 49.986
2020-08-13 | 264:50 | 49.986
2020-08-13 | 265:50 | 49.986
2020-08-13 | 266:50 | 49.986
2020-08-13 | 267:50 | 49.986
2020-08-13 | 268:50 | 49.987
2020-08-13 | 269:50 | 49.989
2020-08-13 | 270:50 | 49.988
2020-08-13 | 271:50 | 49.99
2020-08-13 | 272:50 | 49.992
2020-08-13 | 273:50 | 49.993
2020-08-13 | 274:50 | 49.995
2020-08-13 | 275:50 | 49.995
2020-08-13 | 276:50 | 49.994
2020-08-13 | 277:50 | 49.992
2020-08-13 | 278:50 | 49.989
2020-08-13 | 279:50 | 49.987
2020-08-13 | 280:50 | 49.986
2020-08-13 | 281:50 | 49.984
2020-08-13 | 282:50 | 49.983
2020-08-13 | 283:50 | 49.985
2020-08-13 | 284:50 | 49.987
2020-08-13 | 285:50 | 49.989
2020-08-13 | 286:50 | 49.989
2020-08-13 | 287:50 | 49.988
2020-08-13 | 288:50 | 49.987
2020-08-13 | 289:50 | 49.986
2020-08-13 | 290:50 | 49.983
2020-08-13 | 291:50 | 49.979
2020-08-13 | 292:50 | 49.976
2020-08-13 | 293:50 | 49.971
2020-08-13 | 294:50 | 49.969
2020-08-13 | 295:50 | 49.967
2020-08-13 | 296:50 | 49.967
2020-08-13 | 297:50 | 49.967
2020-08-13 | 298:50 | 49.968
2020-08-13 | 299:50 | 49.971
2020-08-13 | 300:50 | 49.971
2020-08-13 | 301:50 | 49.972
2020-08-13 | 302:50 | 49.971
2020-08-13 | 303:50 | 49.972
2020-08-13 | 304:50 | 49.974
2020-08-13 | 305:50 | 49.977
2020-08-13 | 306:50 | 49.982
2020-08-13 | 307:50 | 49.985
2020-08-13 | 308:50 | 49.986
2020-08-13 | 309:50 | 49.986
2020-08-13 | 310:50 | 49.985
2020-08-13 | 311:50 | 49.983
2020-08-13 | 312:50 | 49.982
2020-08-13 | 313:50 | 49.98
2020-08-13 | 314:50 | 49.981
2020-08-13 | 315:50 | 49.981
2020-08-13 | 316:50 | 49.982
2020-08-13 | 317:50 | 49.982
2020-08-13 | 318:50 | 49.984
2020-08-13 | 319:50 | 49.985
2020-08-13 | 320:50 | 49.985
2020-08-13 | 321:50 | 49.985
2020-08-13 | 322:50 | 49.986
2020-08-13 | 323:50 | 49.988
2020-08-13 | 324:50 | 49.989
2020-08-13 | 325:50 | 49.99
2020-08-13 | 326:50 | 49.988
2020-08-13 | 327:50 | 49.99
2020-08-13 | 328:50 | 49.991
2020-08-13 | 329:50 | 49.995
2020-08-13 | 330:50 | 49.997
2020-08-13 | 331:50 | 50
2020-08-13 | 332:50 | 50.001
2020-08-13 | 333:50 | 50.001
2020-08-13 | 334:50 | 50.002
2020-08-13 | 335:50 | 49.999
2020-08-13 | 336:50 | 49.995
2020-08-13 | 337:50 | 49.989
2020-08-13 | 338:50 | 49.985
2020-08-13 | 339:50 | 49.981
2020-08-13 | 340:50 | 49.98
2020-08-13 | 341:50 | 49.978
2020-08-13 | 342:50 | 49.976
2020-08-13 | 343:50 | 49.974
2020-08-13 | 344:50 | 49.973
2020-08-13 | 345:50 | 49.972
2020-08-13 | 346:50 | 49.972
2020-08-13 | 347:50 | 49.973
2020-08-13 | 348:50 | 49.974
2020-08-13 | 349:50 | 49.976
2020-08-13 | 350:50 | 49.98
2020-08-13 | 351:50 | 49.982
2020-08-13 | 352:50 | 49.984
2020-08-13 | 353:50 | 49.986
2020-08-13 | 354:50 | 49.987
2020-08-13 | 355:50 | 49.988
2020-08-13 | 356:50 | 49.987
2020-08-13 | 357:50 | 49.987
2020-08-13 | 358:50 | 49.986
2020-08-13 | 359:50 | 49.985
2020-08-13 | 360:50 | 49.984
2020-08-13 | 361:50 | 49.982
2020-08-13 | 362:50 | 49.979
2020-08-13 | 363:50 | 49.977
2020-08-13 | 364:50 | 49.977
2020-08-13 | 365:50 | 49.978
2020-08-13 | 366:50 | 49.981
2020-08-13 | 367:50 | 49.98
2020-08-13 | 368:50 | 49.982
2020-08-13 | 369:50 | 49.985
2020-08-13 | 370:50 | 49.984
2020-08-13 | 371:50 | 49.983
2020-08-13 | 372:50 | 49.982
2020-08-13 | 373:50 | 49.984
2020-08-13 | 374:50 | 49.985
2020-08-13 | 375:50 | 49.987
2020-08-13 | 376:50 | 49.987
2020-08-13 | 377:50 | 49.986
2020-08-13 | 378:50 | 49.985
2020-08-13 | 379:50 | 49.985
2020-08-13 | 380:50 | 49.984
2020-08-13 | 381:50 | 49.986
2020-08-13 | 382:50 | 49.986
2020-08-13 | 383:50 | 49.986
2020-08-13 | 384:50 | 49.986
2020-08-13 | 385:50 | 49.988
2020-08-13 | 386:50 | 49.989
2020-08-13 | 387:50 | 49.991
2020-08-13 | 388:50 | 49.993
2020-08-13 | 389:50 | 49.995
2020-08-13 | 390:50 | 49.997
2020-08-13 | 391:50 | 49.999
2020-08-13 | 392:50 | 50.002
2020-08-13 | 393:50 | 50.004
2020-08-13 | 394:50 | 50.006
2020-08-13 | 395:50 | 50.007
2020-08-13 | 396:50 | 50.01
2020-08-13 | 397:50 | 50.011
2020-08-13 | 398:50 | 50.009
2020-08-13 | 399:50 | 50.009
2020-08-13 | 400:50 | 50.009
2020-08-13 | 401:50 | 50.01
2020-08-13 | 402:50 | 50.013
2020-08-13 | 403:50 | 50.017
2020-08-13 | 404:50 | 50.019
2020-08-13 | 405:50 | 50.022
2020-08-13 | 406:50 | 50.025
2020-08-13 | 407:50 | 50.026
2020-08-13 | 408:50 | 50.027
2020-08-13 | 409:50 | 50.025
2020-08-13 | 410:50 | 50.024
2020-08-13 | 411:50 | 50.021
2020-08-13 | 412:50 | 50.018
2020-08-13 | 413:50 | 50.018
2020-08-13 | 414:50 | 50.016
2020-08-13 | 415:50 | 50.014
2020-08-13 | 416:50 | 50.011
2020-08-13 | 417:50 | 50.008
2020-08-13 | 418:50 | 50.006
2020-08-13 | 419:50 | 50.005
2020-08-13 | 420:50 | 50.005
2020-08-13 | 421:50 | 50.003
2020-08-13 | 422:50 | 50.004
2020-08-13 | 423:50 | 50.005
2020-08-13 | 424:50 | 50.006
2020-08-13 | 425:50 | 50.007
2020-08-13 | 426:50 | 50.007
2020-08-13 | 427:50 | 50.008
2020-08-13 | 428:50 | 50.01
2020-08-13 | 429:50 | 50.011
2020-08-13 | 430:50 | 50.012
2020-08-13 | 431:50 | 50.012
2020-08-13 | 432:50 | 50.011
2020-08-13 | 433:50 | 50.012
2020-08-13 | 434:50 | 50.014
2020-08-13 | 435:50 | 50.015
2020-08-13 | 436:50 | 50.016
2020-08-13 | 437:50 | 50.017
2020-08-13 | 438:50 | 50.018
2020-08-13 | 439:50 | 50.016
2020-08-13 | 440:50 | 50.014
2020-08-13 | 441:50 | 50.013
2020-08-13 | 442:50 | 50.014
2020-08-13 | 443:50 | 50.014
2020-08-13 | 444:50 | 50.014
2020-08-13 | 445:50 | 50.015
2020-08-13 | 446:50 | 50.015
2020-08-13 | 447:50 | 50.015
2020-08-13 | 448:50 | 50.016
2020-08-13 | 449:50 | 50.016
2020-08-13 | 450:50 | 50.016
2020-08-13 | 451:50 | 50.016
2020-08-13 | 452:50 | 50.013
2020-08-13 | 453:50 | 50.013
2020-08-13 | 454:50 | 50.013
2020-08-13 | 455:50 | 50.014
2020-08-13 | 456:50 | 50.016
2020-08-13 | 457:50 | 50.017
2020-08-13 | 458:50 | 50.019
2020-08-13 | 459:50 | 50.02
2020-08-13 | 460:50 | 50.02
2020-08-13 | 461:50 | 50.021
2020-08-13 | 462:50 | 50.022
2020-08-13 | 463:50 | 50.023
2020-08-13 | 464:50 | 50.024
2020-08-13 | 465:50 | 50.024
2020-08-13 | 466:50 | 50.023
2020-08-13 | 467:50 | 50.023
2020-08-13 | 468:50 | 50.022
2020-08-13 | 469:50 | 50.025
2020-08-13 | 470:50 | 50.025
2020-08-13 | 471:50 | 50.027
2020-08-13 | 472:50 | 50.028
2020-08-13 | 473:50 | 50.027
2020-08-13 | 474:50 | 50.025
2020-08-13 | 475:50 | 50.022
2020-08-13 | 476:50 | 50.02
2020-08-13 | 477:50 | 50.018
2020-08-13 | 478:50 | 50.019
2020-08-13 | 479:50 | 50.019
2020-08-13 | 480:50 | 50.021
2020-08-13 | 481:50 | 50.024
2020-08-13 | 482:50 | 50.027
2020-08-13 | 483:50 | 50.029
2020-08-13 | 484:50 | 50.029
2020-08-13 | 485:50 | 50.032
2020-08-13 | 486:50 | 50.034
2020-08-13 | 487:50 | 50.036
2020-08-13 | 488:50 | 50.033
2020-08-13 | 489:50 | 50.029
2020-08-13 | 490:50 | 50.023
2020-08-13 | 491:50 | 50.019
2020-08-13 | 492:50 | 50.017
2020-08-13 | 493:50 | 50.018
2020-08-13 | 494:50 | 50.02
2020-08-13 | 495:50 | 50.022
2020-08-13 | 496:50 | 50.025
2020-08-13 | 497:50 | 50.027
2020-08-13 | 498:50 | 50.031
2020-08-13 | 499:50 | 50.036
2020-08-13 | 500:50 | 50.04
2020-08-13 | 501:50 | 50.043
2020-08-13 | 502:50 | 50.046
2020-08-13 | 503:50 | 50.049
2020-08-13 | 504:50 | 50.052
2020-08-13 | 505:50 | 50.054
2020-08-13 | 506:50 | 50.059
2020-08-13 | 507:50 | 50.06
2020-08-13 | 508:50 | 50.059
2020-08-13 | 509:50 | 50.059
2020-08-13 | 510:50 | 50.057
2020-08-13 | 511:50 | 50.058
2020-08-13 | 512:50 | 50.059
2020-08-13 | 513:50 | 50.06
2020-08-13 | 514:50 | 50.061
2020-08-13 | 515:50 | 50.063
2020-08-13 | 516:50 | 50.064
2020-08-13 | 517:50 | 50.065
2020-08-13 | 518:50 | 50.068
2020-08-13 | 519:50 | 50.071
2020-08-13 | 520:50 | 50.072
2020-08-13 | 521:50 | 50.073
2020-08-13 | 522:50 | 50.074
2020-08-13 | 523:50 | 50.076
2020-08-13 | 524:50 | 50.077
2020-08-13 | 525:50 | 50.075
2020-08-13 | 526:50 | 50.074
2020-08-13 | 527:50 | 50.074
2020-08-13 | 528:50 | 50.073
2020-08-13 | 529:50 | 50.071
2020-08-13 | 530:50 | 50.071
2020-08-13 | 531:50 | 50.071
2020-08-13 | 532:50 | 50.07
2020-08-13 | 533:50 | 50.069
2020-08-13 | 534:50 | 50.069
2020-08-13 | 535:50 | 50.073
2020-08-13 | 536:50 | 50.075
2020-08-13 | 537:50 | 50.078
2020-08-13 | 538:50 | 50.077
2020-08-13 | 539:50 | 50.077
2020-08-13 | 540:50 | 50.075
2020-08-13 | 541:50 | 50.072
2020-08-13 | 542:50 | 50.068
2020-08-13 | 543:50 | 50.062
2020-08-13 | 544:50 | 50.058
2020-08-13 | 545:50 | 50.058
2020-08-13 | 546:50 | 50.059
2020-08-13 | 547:50 | 50.062
2020-08-13 | 548:50 | 50.067
2020-08-13 | 549:50 | 50.072
2020-08-13 | 550:50 | 50.081
2020-08-13 | 551:50 | 50.09
2020-08-13 | 552:50 | 50.096
2020-08-13 | 553:50 | 50.101
2020-08-13 | 554:50 | 50.104
2020-08-13 | 555:50 | 50.106
2020-08-13 | 556:50 | 50.106
2020-08-13 | 557:50 | 50.106
2020-08-13 | 558:50 | 50.106
2020-08-13 | 559:50 | 50.107
2020-08-13 | 560:50 | 50.108
2020-08-13 | 561:50 | 50.109
2020-08-13 | 562:50 | 50.11
2020-08-13 | 563:50 | 50.113
2020-08-13 | 564:50 | 50.115
2020-08-13 | 565:50 | 50.118
2020-08-13 | 566:50 | 50.118
2020-08-13 | 567:50 | 50.121
2020-08-13 | 568:50 | 50.123
2020-08-13 | 569:50 | 50.126
2020-08-13 | 570:50 | 50.13
2020-08-13 | 571:50 | 50.134
2020-08-13 | 572:50 | 50.137
2020-08-13 | 573:50 | 50.138
2020-08-13 | 574:50 | 50.139
2020-08-13 | 575:50 | 50.141
2020-08-13 | 576:50 | 50.142
2020-08-13 | 577:50 | 50.141
2020-08-13 | 578:50 | 50.14
2020-08-13 | 579:50 | 50.14
2020-08-13 | 580:50 | 50.14
2020-08-13 | 581:50 | 50.138
2020-08-13 | 582:50 | 50.138
2020-08-13 | 583:50 | 50.138
2020-08-13 | 584:50 | 50.138
2020-08-13 | 585:50 | 50.137
2020-08-13 | 586:50 | 50.136
2020-08-13 | 587:50 | 50.135
2020-08-13 | 588:50 | 50.134
2020-08-13 | 589:50 | 50.135
2020-08-13 | 590:50 | 50.136
2020-08-13 | 591:50 | 50.136
2020-08-13 | 592:50 | 50.136
2020-08-13 | 593:50 | 50.137
2020-08-13 | 594:50 | 50.138
2020-08-13 | 595:50 | 50.138
2020-08-13 | 596:50 | 50.138
2020-08-13 | 597:50 | 50.138
2020-08-13 | 598:50 | 50.136
2020-08-13 | 599:50 | 50.134
2020-08-13 | 600:50 | 50.133
2020-08-13 | 601:50 | 50.133
2020-08-13 | 602:50 | 50.128
2020-08-13 | 603:50 | 50.126
2020-08-13 | 604:50 | 50.124
2020-08-13 | 605:50 | 50.123
2020-08-13 | 606:50 | 50.123
2020-08-13 | 607:50 | 50.12
2020-08-13 | 608:50 | 50.118
2020-08-13 | 609:50 | 50.114
2020-08-13 | 610:50 | 50.111
2020-08-13 | 611:50 | 50.108
2020-08-13 | 612:50 | 50.106
2020-08-13 | 613:50 | 50.103
2020-08-13 | 614:50 | 50.102
2020-08-13 | 615:50 | 50.102
2020-08-13 | 616:50 | 50.103
2020-08-13 | 617:50 | 50.103
2020-08-13 | 618:50 | 50.103
2020-08-13 | 619:50 | 50.104
2020-08-13 | 620:50 | 50.104
2020-08-13 | 621:50 | 50.106
2020-08-13 | 622:50 | 50.106
2020-08-13 | 623:50 | 50.107
2020-08-13 | 624:50 | 50.108
2020-08-13 | 625:50 | 50.108
2020-08-13 | 626:50 | 50.108
2020-08-13 | 627:50 | 50.106
2020-08-13 | 628:50 | 50.106
2020-08-13 | 629:50 | 50.105
2020-08-13 | 630:50 | 50.104
2020-08-13 | 631:50 | 50.105
2020-08-13 | 632:50 | 50.105
2020-08-13 | 633:50 | 50.106
2020-08-13 | 634:50 | 50.106
2020-08-13 | 635:50 | 50.107
2020-08-13 | 636:50 | 50.108
2020-08-13 | 637:50 | 50.109
2020-08-13 | 638:50 | 50.109
2020-08-13 | 639:50 | 50.111
2020-08-13 | 640:50 | 50.11
2020-08-13 | 641:50 | 50.109
2020-08-13 | 642:50 | 50.106
2020-08-13 | 643:50 | 50.105
2020-08-13 | 644:50 | 50.105
2020-08-13 | 645:50 | 50.105
2020-08-13 | 646:50 | 50.105
2020-08-13 | 647:50 | 50.104
2020-08-13 | 648:50 | 50.104
2020-08-13 | 649:50 | 50.104
2020-08-13 | 650:50 | 50.104
2020-08-13 | 651:50 | 50.106
2020-08-13 | 652:50 | 50.109
2020-08-13 | 653:50 | 50.111
2020-08-13 | 654:50 | 50.113
2020-08-13 | 655:50 | 50.113
2020-08-13 | 656:50 | 50.112
2020-08-13 | 657:50 | 50.112
2020-08-13 | 658:50 | 50.11
2020-08-13 | 659:50 | 50.111
2020-08-13 | 660:50 | 50.111
2020-08-13 | 661:50 | 50.111
2020-08-13 | 662:50 | 50.111
2020-08-13 | 663:50 | 50.112
2020-08-13 | 664:50 | 50.112
2020-08-13 | 665:50 | 50.111
2020-08-13 | 666:50 | 50.111
2020-08-13 | 667:50 | 50.112
2020-08-13 | 668:50 | 50.113
2020-08-13 | 669:50 | 50.114
2020-08-13 | 670:50 | 50.114
2020-08-13 | 671:50 | 50.113
2020-08-13 | 672:50 | 50.109
2020-08-13 | 673:50 | 50.109
2020-08-13 | 674:50 | 50.102
2020-08-13 | 675:50 | 50.097
2020-08-13 | 676:50 | 50.091
2020-08-13 | 677:50 | 50.088
2020-08-13 | 678:50 | 50.084
2020-08-13 | 679:50 | 50.081
2020-08-13 | 680:50 | 50.078
2020-08-13 | 681:50 | 50.077
2020-08-13 | 682:50 | 50.075
2020-08-13 | 683:50 | 50.074
2020-08-13 | 684:50 | 50.075
2020-08-13 | 685:50 | 50.076
2020-08-13 | 686:50 | 50.075
2020-08-13 | 687:50 | 50.077
2020-08-13 | 688:50 | 50.078
2020-08-13 | 689:50 | 50.08
2020-08-13 | 690:50 | 50.081
2020-08-13 | 691:50 | 50.082
2020-08-13 | 692:50 | 50.083
2020-08-13 | 693:50 | 50.081
2020-08-13 | 694:50 | 50.083
2020-08-13 | 695:50 | 50.081
2020-08-13 | 696:50 | 50.081
2020-08-13 | 697:50 | 50.079
2020-08-13 | 698:50 | 50.079
2020-08-13 | 699:50 | 50.079
2020-08-13 | 700:50 | 50.079
2020-08-13 | 701:50 | 50.077
2020-08-13 | 702:50 | 50.076
2020-08-13 | 703:50 | 50.076
2020-08-13 | 704:50 | 50.076
2020-08-13 | 705:50 | 50.076
2020-08-13 | 706:50 | 50.078
2020-08-13 | 707:50 | 50.08
2020-08-13 | 708:50 | 50.083
2020-08-13 | 709:50 | 50.083
2020-08-13 | 710:50 | 50.085
2020-08-13 | 711:50 | 50.086
2020-08-13 | 712:50 | 50.083
2020-08-13 | 713:50 | 50.083
2020-08-13 | 714:50 | 50.081
2020-08-13 | 715:50 | 50.08
2020-08-13 | 716:50 | 50.075
2020-08-13 | 717:50 | 50.07
2020-08-13 | 718:50 | 50.066
2020-08-13 | 719:50 | 50.061
2020-08-13 | 720:50 | 50.058
2020-08-13 | 721:50 | 50.059
2020-08-13 | 722:50 | 50.06
2020-08-13 | 723:50 | 50.06
2020-08-13 | 724:50 | 50.06
2020-08-13 | 725:50 | 50.062
2020-08-13 | 726:50 | 50.063
2020-08-13 | 727:50 | 50.065
2020-08-13 | 728:50 | 50.068
2020-08-13 | 729:50 | 50.066
2020-08-13 | 730:50 | 50.066
2020-08-13 | 731:50 | 50.064
2020-08-13 | 732:50 | 50.063
2020-08-13 | 733:50 | 50.064
2020-08-13 | 734:50 | 50.065
2020-08-13 | 735:50 | 50.064
2020-08-13 | 736:50 | 50.064
2020-08-13 | 737:50 | 50.066
2020-08-13 | 738:50 | 50.063
2020-08-13 | 739:50 | 50.062
2020-08-13 | 740:50 | 50.061
2020-08-13 | 741:50 | 50.06
2020-08-13 | 742:50 | 50.059
2020-08-13 | 743:50 | 50.057
2020-08-13 | 744:50 | 50.055
2020-08-13 | 745:50 | 50.054
2020-08-13 | 746:50 | 50.056
2020-08-13 | 747:50 | 50.058
2020-08-13 | 748:50 | 50.06
2020-08-13 | 749:50 | 50.063
2020-08-13 | 750:50 | 50.065
2020-08-13 | 751:50 | 50.067
2020-08-13 | 752:50 | 50.068
2020-08-13 | 753:50 | 50.07
2020-08-13 | 754:50 | 50.071
2020-08-13 | 755:50 | 50.072
2020-08-13 | 756:50 | 50.072
2020-08-13 | 757:50 | 50.071
2020-08-13 | 758:50 | 50.069
2020-08-13 | 759:50 | 50.068
2020-08-13 | 760:50 | 50.069
2020-08-13 | 761:50 | 50.069
2020-08-13 | 762:50 | 50.07
2020-08-13 | 763:50 | 50.07
2020-08-13 | 764:50 | 50.071
2020-08-13 | 765:50 | 50.072
2020-08-13 | 766:50 | 50.073
2020-08-13 | 767:50 | 50.075
2020-08-13 | 768:50 | 50.076
2020-08-13 | 769:50 | 50.076
2020-08-13 | 770:50 | 50.076
2020-08-13 | 771:50 | 50.073
2020-08-13 | 772:50 | 50.068
2020-08-13 | 773:50 | 50.066
2020-08-13 | 774:50 | 50.067
2020-08-13 | 775:50 | 50.067
2020-08-13 | 776:50 | 50.067
2020-08-13 | 777:50 | 50.067
2020-08-13 | 778:50 | 50.066
2020-08-13 | 779:50 | 50.066
2020-08-13 | 780:50 | 50.069
2020-08-13 | 781:50 | 50.07
2020-08-13 | 782:50 | 50.069
2020-08-13 | 783:50 | 50.067
2020-08-13 | 784:50 | 50.062
2020-08-13 | 785:50 | 50.059
2020-08-13 | 786:50 | 50.055
2020-08-13 | 787:50 | 50.049
2020-08-13 | 788:50 | 50.045
2020-08-13 | 789:50 | 50.044
2020-08-13 | 790:50 | 50.044
2020-08-13 | 791:50 | 50.043
2020-08-13 | 792:50 | 50.041
2020-08-13 | 793:50 | 50.04
2020-08-13 | 794:50 | 50.039
2020-08-13 | 795:50 | 50.04
2020-08-13 | 796:50 | 50.04
2020-08-13 | 797:50 | 50.041
2020-08-13 | 798:50 | 50.041
2020-08-13 | 799:50 | 50.042
2020-08-13 | 800:50 | 50.043
2020-08-13 | 801:50 | 50.045
2020-08-13 | 802:50 | 50.049
2020-08-13 | 803:50 | 50.054
2020-08-13 | 804:50 | 50.056
2020-08-13 | 805:50 | 50.057
2020-08-13 | 806:50 | 50.059
2020-08-13 | 807:50 | 50.06
2020-08-13 | 808:50 | 50.061
2020-08-13 | 809:50 | 50.062
2020-08-13 | 810:50 | 50.064
2020-08-13 | 811:50 | 50.064
2020-08-13 | 812:50 | 50.063
2020-08-13 | 813:50 | 50.062
2020-08-13 | 814:50 | 50.06
2020-08-13 | 815:50 | 50.057
2020-08-13 | 816:50 | 50.055
2020-08-13 | 817:50 | 50.052
2020-08-13 | 818:50 | 50.053
2020-08-13 | 819:50 | 50.053
2020-08-13 | 820:50 | 50.053
2020-08-13 | 821:50 | 50.052
2020-08-13 | 822:50 | 50.052
2020-08-13 | 823:50 | 50.053
2020-08-13 | 824:50 | 50.054
2020-08-13 | 825:50 | 50.053
2020-08-13 | 826:50 | 50.052
2020-08-13 | 827:50 | 50.05
2020-08-13 | 828:50 | 50.05
2020-08-13 | 829:50 | 50.051
2020-08-13 | 830:50 | 50.05
2020-08-13 | 831:50 | 50.048
2020-08-13 | 832:50 | 50.048
2020-08-13 | 833:50 | 50.044
2020-08-13 | 834:50 | 50.042
2020-08-13 | 835:50 | 50.04
2020-08-13 | 836:50 | 50.038
2020-08-13 | 837:50 | 50.035
2020-08-13 | 838:50 | 50.033
2020-08-13 | 839:50 | 50.031
2020-08-13 | 840:50 | 50.028
2020-08-13 | 841:50 | 50.023
2020-08-13 | 842:50 | 50.024
2020-08-13 | 843:50 | 50.021
2020-08-13 | 844:50 | 50.021
2020-08-13 | 845:50 | 50.018
2020-08-13 | 846:50 | 50.017
2020-08-13 | 847:50 | 50.015
2020-08-13 | 848:50 | 50.013
2020-08-13 | 849:50 | 50.013
2020-08-13 | 850:50 | 50.014
2020-08-13 | 851:50 | 50.014
2020-08-13 | 852:50 | 50.014
2020-08-13 | 853:50 | 50.013
2020-08-13 | 854:50 | 50.013
2020-08-13 | 855:50 | 50.009
2020-08-13 | 856:50 | 50.007
2020-08-13 | 857:50 | 50.005
2020-08-13 | 858:50 | 50.003
2020-08-13 | 859:50 | 50.002
2020-08-13 | 860:50 | 49.999
2020-08-13 | 861:50 | 50
2020-08-13 | 862:50 | 49.997
2020-08-13 | 863:50 | 49.995
2020-08-13 | 864:50 | 49.992
2020-08-13 | 865:50 | 49.988
2020-08-13 | 866:50 | 49.982
2020-08-13 | 867:50 | 49.978
2020-08-13 | 868:50 | 49.976
2020-08-13 | 869:50 | 49.974
2020-08-13 | 870:50 | 49.973
2020-08-13 | 871:50 | 49.973
2020-08-13 | 872:50 | 49.973
2020-08-13 | 873:50 | 49.974
2020-08-13 | 874:50 | 49.973
2020-08-13 | 875:50 | 49.97
2020-08-13 | 876:50 | 49.969
2020-08-13 | 877:50 | 49.964
2020-08-13 | 878:50 | 49.964
2020-08-13 | 879:50 | 49.965
2020-08-13 | 880:50 | 49.966
2020-08-13 | 881:50 | 49.965
2020-08-13 | 882:50 | 49.966
2020-08-13 | 883:50 | 49.964
2020-08-13 | 884:50 | 49.962
2020-08-13 | 885:50 | 49.961
2020-08-13 | 886:50 | 49.96
2020-08-13 | 887:50 | 49.961
2020-08-13 | 888:50 | 49.963
2020-08-13 | 889:50 | 49.964
2020-08-13 | 890:50 | 49.966
2020-08-13 | 891:50 | 49.969
2020-08-13 | 892:50 | 49.972
2020-08-13 | 893:50 | 49.973
2020-08-13 | 894:50 | 49.974
2020-08-13 | 895:50 | 49.972
2020-08-13 | 896:50 | 49.97
2020-08-13 | 897:50 | 49.968
2020-08-13 | 898:50 | 49.967
2020-08-13 | 899:50 | 49.964
2020-08-13 | 5:05 | 49.964
2020-08-13 | 5:05 | 49.962
2020-08-13 | 5:05 | 49.96
2020-08-13 | 5:05 | 49.96
2020-08-13 | 5:05 | 49.958
2020-08-13 | 5:05 | 49.957
2020-08-13 | 5:05 | 49.955
2020-08-13 | 5:05 | 49.954
2020-08-13 | 5:05 | 49.955
2020-08-13 | 5:05 | 49.954
2020-08-13 | 5:05 | 49.957
2020-08-13 | 5:05 | 49.96
2020-08-13 | 5:05 | 49.962
2020-08-13 | 5:05 | 49.965
2020-08-13 | 5:05 | 49.966
2020-08-13 | 5:05 | 49.967
2020-08-13 | 5:05 | 49.966
2020-08-13 | 5:05 | 49.967
2020-08-13 | 5:05 | 49.967
2020-08-13 | 5:05 | 49.962
2020-08-13 | 5:05 | 49.959
2020-08-13 | 5:05 | 49.957
2020-08-13 | 5:05 | 49.957
2020-08-13 | 5:05 | 49.957
2020-08-13 | 5:05 | 49.958
2020-08-13 | 5:05 | 49.958
2020-08-13 | 5:05 | 49.959
2020-08-13 | 5:05 | 49.958
2020-08-13 | 5:05 | 49.957
2020-08-13 | 5:05 | 49.956
2020-08-13 | 5:06 | 49.956
2020-08-13 | 5:06 | 49.956
2020-08-13 | 5:06 | 49.959
2020-08-13 | 5:06 | 49.961
2020-08-13 | 5:06 | 49.965
2020-08-13 | 5:06 | 49.969
2020-08-13 | 5:06 | 49.974
2020-08-13 | 5:06 | 49.976
2020-08-13 | 5:06 | 49.975
2020-08-13 | 5:06 | 49.974
2020-08-13 | 5:06 | 49.972
2020-08-13 | 5:06 | 49.97
2020-08-13 | 5:06 | 49.97
2020-08-13 | 5:06 | 49.97
2020-08-13 | 5:06 | 49.972
2020-08-13 | 5:06 | 49.973
2020-08-13 | 5:06 | 49.974
2020-08-13 | 5:06 | 49.972
2020-08-13 | 5:06 | 49.975
2020-08-13 | 5:06 | 49.975
2020-08-13 | 5:06 | 49.976
2020-08-13 | 5:06 | 49.977
2020-08-13 | 5:06 | 49.975
2020-08-13 | 5:06 | 49.975
2020-08-13 | 5:06 | 49.975
2020-08-13 | 5:06 | 49.973
2020-08-13 | 5:06 | 49.973
2020-08-13 | 5:06 | 49.973
2020-08-13 | 5:06 | 49.974
2020-08-13 | 5:06 | 49.975
2020-08-13 | 5:06 | 49.974
2020-08-13 | 5:06 | 49.974
2020-08-13 | 5:06 | 49.973
2020-08-13 | 5:06 | 49.968
2020-08-13 | 5:06 | 49.964
2020-08-13 | 5:06 | 49.961
2020-08-13 | 5:06 | 49.958
2020-08-13 | 5:06 | 49.954
2020-08-13 | 5:06 | 49.95
2020-08-13 | 5:06 | 49.946
2020-08-13 | 5:06 | 49.944
2020-08-13 | 5:06 | 49.948
2020-08-13 | 5:06 | 49.952
2020-08-13 | 5:06 | 49.956
2020-08-13 | 5:06 | 49.958
2020-08-13 | 5:06 | 49.959
2020-08-13 | 5:06 | 49.959
2020-08-13 | 5:06 | 49.958
2020-08-13 | 5:06 | 49.958
2020-08-13 | 5:06 | 49.953
2020-08-13 | 5:06 | 49.95
2020-08-13 | 5:06 | 49.948
2020-08-13 | 5:06 | 49.948
2020-08-13 | 5:06 | 49.951
2020-08-13 | 5:06 | 49.952
2020-08-13 | 5:06 | 49.954
2020-08-13 | 5:06 | 49.955
2020-08-13 | 5:06 | 49.956
2020-08-13 | 5:06 | 49.957
2020-08-13 | 5:06 | 49.958
2020-08-13 | 5:06 | 49.959
2020-08-13 | 5:07 | 49.956
2020-08-13 | 5:07 | 49.953
2020-08-13 | 5:07 | 49.952
2020-08-13 | 5:07 | 49.95
2020-08-13 | 5:07 | 49.951
2020-08-13 | 5:07 | 49.952
2020-08-13 | 5:07 | 49.953
2020-08-13 | 5:07 | 49.953
2020-08-13 | 5:07 | 49.952
2020-08-13 | 5:07 | 49.951
2020-08-13 | 5:07 | 49.95
2020-08-13 | 5:07 | 49.949
2020-08-13 | 5:07 | 49.948
2020-08-13 | 5:07 | 49.947
2020-08-13 | 5:07 | 49.949
2020-08-13 | 5:07 | 49.95
2020-08-13 | 5:07 | 49.951
2020-08-13 | 5:07 | 49.953
2020-08-13 | 5:07 | 49.957
2020-08-13 | 5:07 | 49.96
2020-08-13 | 5:07 | 49.959
2020-08-13 | 5:07 | 49.96
2020-08-13 | 5:07 | 49.958
2020-08-13 | 5:07 | 49.958
2020-08-13 | 5:07 | 49.956
2020-08-13 | 5:07 | 49.952
2020-08-13 | 5:07 | 49.948
2020-08-13 | 5:07 | 49.945
2020-08-13 | 5:07 | 49.944
2020-08-13 | 5:07 | 49.939
2020-08-13 | 5:07 | 49.939
2020-08-13 | 5:07 | 49.942
2020-08-13 | 5:07 | 49.942
2020-08-13 | 5:07 | 49.945
2020-08-13 | 5:07 | 49.949
2020-08-13 | 5:07 | 49.95
2020-08-13 | 5:07 | 49.95
2020-08-13 | 5:07 | 49.948
2020-08-13 | 5:07 | 49.946
2020-08-13 | 5:07 | 49.947
2020-08-13 | 5:07 | 49.948
2020-08-13 | 5:07 | 49.947
2020-08-13 | 5:07 | 49.944
2020-08-13 | 5:07 | 49.942
2020-08-13 | 5:07 | 49.939
2020-08-13 | 5:07 | 49.938
2020-08-13 | 5:07 | 49.935
2020-08-13 | 5:07 | 49.934
2020-08-13 | 5:07 | 49.934
2020-08-13 | 5:07 | 49.935
2020-08-13 | 5:07 | 49.937
2020-08-13 | 5:07 | 49.94
2020-08-13 | 5:07 | 49.941
2020-08-13 | 5:07 | 49.942
2020-08-13 | 5:07 | 49.942
2020-08-13 | 5:07 | 49.944
2020-08-13 | 5:07 | 49.946
2020-08-13 | 5:07 | 49.95
2020-08-13 | 5:07 | 49.955
2020-08-13 | 5:08 | 49.961
2020-08-13 | 5:08 | 49.97
2020-08-13 | 5:08 | 49.976
2020-08-13 | 5:08 | 49.977
2020-08-13 | 5:08 | 49.98
2020-08-13 | 5:08 | 49.981
2020-08-13 | 5:08 | 49.98
2020-08-13 | 5:08 | 49.979
2020-08-13 | 5:08 | 49.979
2020-08-13 | 5:08 | 49.978
2020-08-13 | 5:08 | 49.976
2020-08-13 | 5:08 | 49.975
2020-08-13 | 5:08 | 49.973
2020-08-13 | 5:08 | 49.972
2020-08-13 | 5:08 | 49.972
2020-08-13 | 5:08 | 49.972
2020-08-13 | 5:08 | 49.973
2020-08-13 | 5:08 | 49.973
2020-08-13 | 5:08 | 49.973
2020-08-13 | 5:08 | 49.972
2020-08-13 | 5:08 | 49.972
2020-08-13 | 5:08 | 49.972
2020-08-13 | 5:08 | 49.972
2020-08-13 | 5:08 | 49.974
2020-08-13 | 5:08 | 49.976
2020-08-13 | 5:08 | 49.976
2020-08-13 | 5:08 | 49.98
2020-08-13 | 5:08 | 49.981
2020-08-13 | 5:08 | 49.982
2020-08-13 | 5:08 | 49.984
2020-08-13 | 5:08 | 49.983
2020-08-13 | 5:08 | 49.984
2020-08-13 | 5:08 | 49.983
2020-08-13 | 5:08 | 49.982
2020-08-13 | 5:08 | 49.984
2020-08-13 | 5:08 | 49.987
2020-08-13 | 5:08 | 49.989
2020-08-13 | 5:08 | 49.993
2020-08-13 | 5:08 | 49.995
2020-08-13 | 5:08 | 49.998
2020-08-13 | 5:08 | 50
2020-08-13 | 5:08 | 50.001
2020-08-13 | 5:08 | 50.001
2020-08-13 | 5:08 | 50.002
2020-08-13 | 5:08 | 50.001
2020-08-13 | 5:08 | 50
2020-08-13 | 5:08 | 49.999
2020-08-13 | 5:08 | 49.999
2020-08-13 | 5:08 | 49.998
2020-08-13 | 5:08 | 49.996
2020-08-13 | 5:08 | 49.994
2020-08-13 | 5:08 | 49.994
2020-08-13 | 5:08 | 49.993
2020-08-13 | 5:08 | 49.991
2020-08-13 | 5:08 | 49.988
2020-08-13 | 5:08 | 49.983
2020-08-13 | 5:08 | 49.98
2020-08-13 | 5:08 | 49.978
2020-08-13 | 5:08 | 49.974
2020-08-13 | 5:08 | 49.972
2020-08-13 | 5:08 | 49.969
2020-08-13 | 5:09 | 49.966
2020-08-13 | 5:09 | 49.966
2020-08-13 | 5:09 | 49.967
2020-08-13 | 5:09 | 49.966
2020-08-13 | 5:09 | 49.966
2020-08-13 | 5:09 | 49.966
2020-08-13 | 5:09 | 49.967
2020-08-13 | 5:09 | 49.967
2020-08-13 | 5:09 | 49.969
2020-08-13 | 5:09 | 49.968
2020-08-13 | 5:09 | 49.966
2020-08-13 | 5:09 | 49.964
2020-08-13 | 5:09 | 49.962
2020-08-13 | 5:09 | 49.959
2020-08-13 | 5:09 | 49.96
2020-08-13 | 5:09 | 49.959
2020-08-13 | 5:09 | 49.959
2020-08-13 | 5:09 | 49.959
2020-08-13 | 5:09 | 49.958
2020-08-13 | 5:09 | 49.958
2020-08-13 | 5:09 | 49.957
2020-08-13 | 5:09 | 49.957
2020-08-13 | 5:09 | 49.955
2020-08-13 | 5:09 | 49.956
2020-08-13 | 5:09 | 49.956
2020-08-13 | 5:09 | 49.956
2020-08-13 | 5:09 | 49.955
2020-08-13 | 5:09 | 49.954
2020-08-13 | 5:09 | 49.954
2020-08-13 | 5:09 | 49.952
2020-08-13 | 5:09 | 49.952
2020-08-13 | 5:09 | 49.953
2020-08-13 | 5:09 | 49.952
2020-08-13 | 5:09 | 49.95
2020-08-13 | 5:09 | 49.95
2020-08-13 | 5:09 | 49.947
2020-08-13 | 5:09 | 49.946
2020-08-13 | 5:09 | 49.945
2020-08-13 | 5:09 | 49.942
2020-08-13 | 5:09 | 49.944
2020-08-13 | 5:09 | 49.943
2020-08-13 | 5:09 | 49.945
2020-08-13 | 5:09 | 49.948
2020-08-13 | 5:09 | 49.95
2020-08-13 | 5:09 | 49.952
2020-08-13 | 5:09 | 49.956
2020-08-13 | 5:09 | 49.957
2020-08-13 | 5:09 | 49.96
2020-08-13 | 5:09 | 49.964
2020-08-13 | 5:09 | 49.966
2020-08-13 | 5:09 | 49.967
2020-08-13 | 5:09 | 49.969
2020-08-13 | 5:09 | 49.97
2020-08-13 | 5:09 | 49.971
2020-08-13 | 5:09 | 49.973
2020-08-13 | 5:09 | 49.974
2020-08-13 | 5:09 | 49.977
2020-08-13 | 5:09 | 49.979
2020-08-13 | 5:09 | 49.983
2020-08-13 | 5:10 | 49.983
2020-08-13 | 5:10 | 49.982
2020-08-13 | 5:10 | 49.979
2020-08-13 | 5:10 | 49.978
2020-08-13 | 5:10 | 49.974
2020-08-13 | 5:10 | 49.974
2020-08-13 | 5:10 | 49.972
2020-08-13 | 5:10 | 49.972
2020-08-13 | 5:10 | 49.972
2020-08-13 | 5:10 | 49.974
2020-08-13 | 5:10 | 49.976
2020-08-13 | 5:10 | 49.979
2020-08-13 | 5:10 | 49.979
2020-08-13 | 5:10 | 49.979
2020-08-13 | 5:10 | 49.981
2020-08-13 | 5:10 | 49.978
2020-08-13 | 5:10 | 49.98
2020-08-13 | 5:10 | 49.982
2020-08-13 | 5:10 | 49.985
2020-08-13 | 5:10 | 49.988
2020-08-13 | 5:10 | 49.988
2020-08-13 | 5:10 | 49.988
2020-08-13 | 5:10 | 49.988
2020-08-13 | 5:10 | 49.988
2020-08-13 | 5:10 | 49.988
2020-08-13 | 5:10 | 49.988
2020-08-13 | 5:10 | 49.985
2020-08-13 | 5:10 | 49.982
2020-08-13 | 5:10 | 49.982
2020-08-13 | 5:10 | 49.981
2020-08-13 | 5:10 | 49.979
2020-08-13 | 5:10 | 49.976
2020-08-13 | 5:10 | 49.973
2020-08-13 | 5:10 | 49.971
2020-08-13 | 5:10 | 49.971
2020-08-13 | 5:10 | 49.973
2020-08-13 | 5:10 | 49.973
2020-08-13 | 5:10 | 49.974
2020-08-13 | 5:10 | 49.973
2020-08-13 | 5:10 | 49.974
2020-08-13 | 5:10 | 49.973
2020-08-13 | 5:10 | 49.974
2020-08-13 | 5:10 | 49.977
2020-08-13 | 5:10 | 49.974
2020-08-13 | 5:10 | 49.967
2020-08-13 | 5:10 | 49.959
2020-08-13 | 5:10 | 49.953
2020-08-13 | 5:10 | 49.941
2020-08-13 | 5:10 | 49.93
2020-08-13 | 5:10 | 49.923
2020-08-13 | 5:10 | 49.916
2020-08-13 | 5:10 | 49.912
2020-08-13 | 5:10 | 49.911
2020-08-13 | 5:10 | 49.912
2020-08-13 | 5:10 | 49.908
2020-08-13 | 5:10 | 49.91
2020-08-13 | 5:10 | 49.914
2020-08-13 | 5:10 | 49.915
2020-08-13 | 5:10 | 49.92
2020-08-13 | 5:10 | 49.92
2020-08-13 | 5:10 | 49.921
2020-08-13 | 5:11 | 49.921
2020-08-13 | 5:11 | 49.92
2020-08-13 | 5:11 | 49.922
2020-08-13 | 5:11 | 49.922
2020-08-13 | 5:11 | 49.925
2020-08-13 | 5:11 | 49.923
2020-08-13 | 5:11 | 49.92
2020-08-13 | 5:11 | 49.92
2020-08-13 | 5:11 | 49.922
2020-08-13 | 5:11 | 49.921
2020-08-13 | 5:11 | 49.923
2020-08-13 | 5:11 | 49.926
2020-08-13 | 5:11 | 49.927
2020-08-13 | 5:11 | 49.926
2020-08-13 | 5:11 | 49.923
2020-08-13 | 5:11 | 49.921
2020-08-13 | 5:11 | 49.92
2020-08-13 | 5:11 | 49.922
2020-08-13 | 5:11 | 49.926
2020-08-13 | 5:11 | 49.929
2020-08-13 | 5:11 | 49.931
2020-08-13 | 5:11 | 49.933
2020-08-13 | 5:11 | 49.935
2020-08-13 | 5:11 | 49.935
2020-08-13 | 5:11 | 49.934
2020-08-13 | 5:11 | 49.933
2020-08-13 | 5:11 | 49.933
2020-08-13 | 5:11 | 49.932
2020-08-13 | 5:11 | 49.931
2020-08-13 | 5:11 | 49.93
2020-08-13 | 5:11 | 49.931
2020-08-13 | 5:11 | 49.93
2020-08-13 | 5:11 | 49.929
2020-08-13 | 5:11 | 49.929
2020-08-13 | 5:11 | 49.927
2020-08-13 | 5:11 | 49.928
2020-08-13 | 5:11 | 49.928
2020-08-13 | 5:11 | 49.926
2020-08-13 | 5:11 | 49.928
2020-08-13 | 5:11 | 49.926
2020-08-13 | 5:11 | 49.929
2020-08-13 | 5:11 | 49.93
2020-08-13 | 5:11 | 49.931
2020-08-13 | 5:11 | 49.932
2020-08-13 | 5:11 | 49.932
2020-08-13 | 5:11 | 49.931
2020-08-13 | 5:11 | 49.93
2020-08-13 | 5:11 | 49.931
2020-08-13 | 5:11 | 49.932
2020-08-13 | 5:11 | 49.931
2020-08-13 | 5:11 | 49.929
2020-08-13 | 5:11 | 49.928
2020-08-13 | 5:11 | 49.925
2020-08-13 | 5:11 | 49.922
2020-08-13 | 5:11 | 49.919
2020-08-13 | 5:11 | 49.919
2020-08-13 | 5:11 | 49.921
2020-08-13 | 5:11 | 49.921
2020-08-13 | 5:11 | 49.923
2020-08-13 | 5:11 | 49.923
2020-08-13 | 5:12 | 49.924
2020-08-13 | 5:12 | 49.923
2020-08-13 | 5:12 | 49.922
2020-08-13 | 5:12 | 49.92
2020-08-13 | 5:12 | 49.92
2020-08-13 | 5:12 | 49.924
2020-08-13 | 5:12 | 49.928
2020-08-13 | 5:12 | 49.931
2020-08-13 | 5:12 | 49.935
2020-08-13 | 5:12 | 49.936
2020-08-13 | 5:12 | 49.937
2020-08-13 | 5:12 | 49.941
2020-08-13 | 5:12 | 49.943
2020-08-13 | 5:12 | 49.947
2020-08-13 | 5:12 | 49.949
2020-08-13 | 5:12 | 49.949
2020-08-13 | 5:12 | 49.95
2020-08-13 | 5:12 | 49.95
2020-08-13 | 5:12 | 49.95
2020-08-13 | 5:12 | 49.949
2020-08-13 | 5:12 | 49.948
2020-08-13 | 5:12 | 49.947
2020-08-13 | 5:12 | 49.947
2020-08-13 | 5:12 | 49.946
2020-08-13 | 5:12 | 49.945
2020-08-13 | 5:12 | 49.943
2020-08-13 | 5:12 | 49.942
2020-08-13 | 5:12 | 49.938
2020-08-13 | 5:12 | 49.938
2020-08-13 | 5:12 | 49.938
2020-08-13 | 5:12 | 49.935
2020-08-13 | 5:12 | 49.933
2020-08-13 | 5:12 | 49.932
2020-08-13 | 5:12 | 49.929
2020-08-13 | 5:12 | 49.927
2020-08-13 | 5:12 | 49.927
2020-08-13 | 5:12 | 49.926
2020-08-13 | 5:12 | 49.925
2020-08-13 | 5:12 | 49.925
2020-08-13 | 5:12 | 49.922
2020-08-13 | 5:12 | 49.92
2020-08-13 | 5:12 | 49.921
2020-08-13 | 5:12 | 49.92
2020-08-13 | 5:12 | 49.919
2020-08-13 | 5:12 | 49.921
2020-08-13 | 5:12 | 49.924
2020-08-13 | 5:12 | 49.926
2020-08-13 | 5:12 | 49.928
2020-08-13 | 5:12 | 49.932
2020-08-13 | 5:12 | 49.932
2020-08-13 | 5:12 | 49.934
2020-08-13 | 5:12 | 49.935
2020-08-13 | 5:12 | 49.936
2020-08-13 | 5:12 | 49.94
2020-08-13 | 5:12 | 49.942
2020-08-13 | 5:12 | 49.947
2020-08-13 | 5:12 | 49.947
2020-08-13 | 5:12 | 49.949
2020-08-13 | 5:12 | 49.952
2020-08-13 | 5:13 | 49.953
2020-08-13 | 5:13 | 49.953
2020-08-13 | 5:13 | 49.954
2020-08-13 | 5:13 | 49.953
2020-08-13 | 5:13 | 49.954
2020-08-13 | 5:13 | 49.954
2020-08-13 | 5:13 | 49.957
2020-08-13 | 5:13 | 49.958
2020-08-13 | 5:13 | 49.956
2020-08-13 | 5:13 | 49.957
2020-08-13 | 5:13 | 49.954
2020-08-13 | 5:13 | 49.954
2020-08-13 | 5:13 | 49.954
2020-08-13 | 5:13 | 49.953
2020-08-13 | 5:13 | 49.95
2020-08-13 | 5:13 | 49.948
2020-08-13 | 5:13 | 49.945
2020-08-13 | 5:13 | 49.943
2020-08-13 | 5:13 | 49.942
2020-08-13 | 5:13 | 49.941
2020-08-13 | 5:13 | 49.94
2020-08-13 | 5:13 | 49.941
2020-08-13 | 5:13 | 49.94
2020-08-13 | 5:13 | 49.939
2020-08-13 | 5:13 | 49.939
2020-08-13 | 5:13 | 49.938
2020-08-13 | 5:13 | 49.936
2020-08-13 | 5:13 | 49.934
2020-08-13 | 5:13 | 49.935
2020-08-13 | 5:13 | 49.932
2020-08-13 | 5:13 | 49.93
2020-08-13 | 5:13 | 49.931
2020-08-13 | 5:13 | 49.931
2020-08-13 | 5:13 | 49.93
2020-08-13 | 5:13 | 49.93
2020-08-13 | 5:13 | 49.93
2020-08-13 | 5:13 | 49.928
2020-08-13 | 5:13 | 49.926
2020-08-13 | 5:13 | 49.927
2020-08-13 | 5:13 | 49.927
2020-08-13 | 5:13 | 49.927
2020-08-13 | 5:13 | 49.927
2020-08-13 | 5:13 | 49.929
2020-08-13 | 5:13 | 49.929
2020-08-13 | 5:13 | 49.928
2020-08-13 | 5:13 | 49.928
2020-08-13 | 5:13 | 49.926
2020-08-13 | 5:13 | 49.924
2020-08-13 | 5:13 | 49.923
2020-08-13 | 5:13 | 49.919
2020-08-13 | 5:13 | 49.915
2020-08-13 | 5:13 | 49.913
2020-08-13 | 5:13 | 49.912
2020-08-13 | 5:13 | 49.912
2020-08-13 | 5:13 | 49.913
2020-08-13 | 5:13 | 49.909
2020-08-13 | 5:13 | 49.91
2020-08-13 | 5:13 | 49.91
2020-08-13 | 5:13 | 49.909
2020-08-13 | 5:13 | 49.912
2020-08-13 | 5:13 | 49.911
2020-08-13 | 5:14 | 49.913
2020-08-13 | 5:14 | 49.916
2020-08-13 | 5:14 | 49.92
2020-08-13 | 5:14 | 49.924
2020-08-13 | 5:14 | 49.928
2020-08-13 | 5:14 | 49.927
2020-08-13 | 5:14 | 49.929
2020-08-13 | 5:14 | 49.932
2020-08-13 | 5:14 | 49.934
2020-08-13 | 5:14 | 49.935
2020-08-13 | 5:14 | 49.935
2020-08-13 | 5:14 | 49.935
2020-08-13 | 5:14 | 49.938
2020-08-13 | 5:14 | 49.943
2020-08-13 | 5:14 | 49.943
2020-08-13 | 5:14 | 49.944
2020-08-13 | 5:14 | 49.941
2020-08-13 | 5:14 | 49.944
2020-08-13 | 5:14 | 49.945
2020-08-13 | 5:14 | 49.947
2020-08-13 | 5:14 | 49.949
2020-08-13 | 5:14 | 49.949
2020-08-13 | 5:14 | 49.948
2020-08-13 | 5:14 | 49.947
2020-08-13 | 5:14 | 49.946
2020-08-13 | 5:14 | 49.946
2020-08-13 | 5:14 | 49.947
2020-08-13 | 5:14 | 49.949
2020-08-13 | 5:14 | 49.95
2020-08-13 | 5:14 | 49.95
2020-08-13 | 5:14 | 49.951
2020-08-13 | 5:14 | 49.949
2020-08-13 | 5:14 | 49.949
2020-08-13 | 5:14 | 49.946
2020-08-13 | 5:14 | 49.946
2020-08-13 | 5:14 | 49.946
2020-08-13 | 5:14 | 49.946
2020-08-13 | 5:14 | 49.948
2020-08-13 | 5:14 | 49.949
2020-08-13 | 5:14 | 49.95
2020-08-13 | 5:14 | 49.951
2020-08-13 | 5:14 | 49.95
2020-08-13 | 5:14 | 49.95
2020-08-13 | 5:14 | 49.953
2020-08-13 | 5:14 | 49.953
2020-08-13 | 5:14 | 49.955
2020-08-13 | 5:14 | 49.958
2020-08-13 | 5:14 | 49.958
2020-08-13 | 5:14 | 49.957
2020-08-13 | 5:14 | 49.956
2020-08-13 | 5:14 | 49.955
2020-08-13 | 5:14 | 49.951
2020-08-13 | 5:14 | 49.947
2020-08-13 | 5:14 | 49.943
2020-08-13 | 5:14 | 49.939
2020-08-13 | 5:14 | 49.936
2020-08-13 | 5:14 | 49.935
2020-08-13 | 5:14 | 49.933
2020-08-13 | 5:14 | 49.931
2020-08-13 | 5:15 | 49.932
2020-08-13 | 5:15 | 49.93
2020-08-13 | 5:15 | 49.931
2020-08-13 | 5:15 | 49.93
2020-08-13 | 5:15 | 49.931
2020-08-13 | 5:15 | 49.933
2020-08-13 | 5:15 | 49.935
2020-08-13 | 5:15 | 49.935
2020-08-13 | 5:15 | 49.936
2020-08-13 | 5:15 | 49.939
2020-08-13 | 5:15 | 49.938
2020-08-13 | 5:15 | 49.939
2020-08-13 | 5:15 | 49.939
2020-08-13 | 5:15 | 49.938
2020-08-13 | 5:15 | 49.939
2020-08-13 | 5:15 | 49.939
2020-08-13 | 5:15 | 49.94
2020-08-13 | 5:15 | 49.94
2020-08-13 | 5:15 | 49.94
2020-08-13 | 5:15 | 49.938
2020-08-13 | 5:15 | 49.936
2020-08-13 | 5:15 | 49.936
2020-08-13 | 5:15 | 49.935
2020-08-13 | 5:15 | 49.934
2020-08-13 | 5:15 | 49.933
2020-08-13 | 5:15 | 49.935
2020-08-13 | 5:15 | 49.936
2020-08-13 | 5:15 | 49.937
2020-08-13 | 5:15 | 49.94
2020-08-13 | 5:15 | 49.942
2020-08-13 | 5:15 | 49.943
2020-08-13 | 5:15 | 49.943
2020-08-13 | 5:15 | 49.946
2020-08-13 | 5:15 | 49.948
2020-08-13 | 5:15 | 49.948
2020-08-13 | 5:15 | 49.949
2020-08-13 | 5:15 | 49.948
2020-08-13 | 5:15 | 49.952
2020-08-13 | 5:15 | 49.955
2020-08-13 | 5:15 | 49.957
2020-08-13 | 5:15 | 49.956
2020-08-13 | 5:15 | 49.952
2020-08-13 | 5:15 | 49.95
2020-08-13 | 5:15 | 49.946
2020-08-13 | 5:15 | 49.944
2020-08-13 | 5:15 | 49.942
2020-08-13 | 5:15 | 49.941
2020-08-13 | 5:15 | 49.94
2020-08-13 | 5:15 | 49.939
2020-08-13 | 5:15 | 49.94
2020-08-13 | 5:15 | 49.941
2020-08-13 | 5:15 | 49.942
2020-08-13 | 5:15 | 49.944
2020-08-13 | 5:15 | 49.944
2020-08-13 | 5:15 | 49.947
2020-08-13 | 5:15 | 49.948
2020-08-13 | 5:15 | 49.951
2020-08-13 | 5:15 | 49.958
2020-08-13 | 5:15 | 49.964
2020-08-13 | 5:15 | 49.971
2020-08-13 | 5:15 | 49.974
2020-08-13 | 5:16 | 49.977
2020-08-13 | 5:16 | 49.977
2020-08-13 | 5:16 | 49.979
2020-08-13 | 5:16 | 49.98
2020-08-13 | 5:16 | 49.981
2020-08-13 | 5:16 | 49.981
2020-08-13 | 5:16 | 49.981
2020-08-13 | 5:16 | 49.979
2020-08-13 | 5:16 | 49.975
2020-08-13 | 5:16 | 49.974
2020-08-13 | 5:16 | 49.974
2020-08-13 | 5:16 | 49.975
2020-08-13 | 5:16 | 49.975
2020-08-13 | 5:16 | 49.975
2020-08-13 | 5:16 | 49.975
2020-08-13 | 5:16 | 49.976
2020-08-13 | 5:16 | 49.976
2020-08-13 | 5:16 | 49.975
2020-08-13 | 5:16 | 49.973
2020-08-13 | 5:16 | 49.969
2020-08-13 | 5:16 | 49.967
2020-08-13 | 5:16 | 49.963
2020-08-13 | 5:16 | 49.965
2020-08-13 | 5:16 | 49.965
2020-08-13 | 5:16 | 49.965
2020-08-13 | 5:16 | 49.964
2020-08-13 | 5:16 | 49.964
2020-08-13 | 5:16 | 49.963
2020-08-13 | 5:16 | 49.963
2020-08-13 | 5:16 | 49.963
2020-08-13 | 5:16 | 49.963
2020-08-13 | 5:16 | 49.963
2020-08-13 | 5:16 | 49.963
2020-08-13 | 5:16 | 49.962
2020-08-13 | 5:16 | 49.96
2020-08-13 | 5:16 | 49.961
2020-08-13 | 5:16 | 49.964
2020-08-13 | 5:16 | 49.966
2020-08-13 | 5:16 | 49.969
2020-08-13 | 5:16 | 49.971
2020-08-13 | 5:16 | 49.971
2020-08-13 | 5:16 | 49.971
2020-08-13 | 5:16 | 49.97
2020-08-13 | 5:16 | 49.968
2020-08-13 | 5:16 | 49.966
2020-08-13 | 5:16 | 49.962
2020-08-13 | 5:16 | 49.958
2020-08-13 | 5:16 | 49.955
2020-08-13 | 5:16 | 49.951
2020-08-13 | 5:16 | 49.947
2020-08-13 | 5:16 | 49.944
2020-08-13 | 5:16 | 49.945
2020-08-13 | 5:16 | 49.945
2020-08-13 | 5:16 | 49.947
2020-08-13 | 5:16 | 49.949
2020-08-13 | 5:16 | 49.95
2020-08-13 | 5:16 | 49.95
2020-08-13 | 5:16 | 49.95
2020-08-13 | 5:16 | 49.951
2020-08-13 | 5:17 | 49.951
2020-08-13 | 5:17 | 49.951
2020-08-13 | 5:17 | 49.952
2020-08-13 | 5:17 | 49.953
2020-08-13 | 5:17 | 49.952
2020-08-13 | 5:17 | 49.953
2020-08-13 | 5:17 | 49.952
2020-08-13 | 5:17 | 49.952
2020-08-13 | 5:17 | 49.952
2020-08-13 | 5:17 | 49.951
2020-08-13 | 5:17 | 49.949
2020-08-13 | 5:17 | 49.948
2020-08-13 | 5:17 | 49.949
2020-08-13 | 5:17 | 49.949
2020-08-13 | 5:17 | 49.949
2020-08-13 | 5:17 | 49.948
2020-08-13 | 5:17 | 49.949
2020-08-13 | 5:17 | 49.948
2020-08-13 | 5:17 | 49.948
2020-08-13 | 5:17 | 49.947
2020-08-13 | 5:17 | 49.944
2020-08-13 | 5:17 | 49.943
2020-08-13 | 5:17 | 49.941
2020-08-13 | 5:17 | 49.94
2020-08-13 | 5:17 | 49.939
2020-08-13 | 5:17 | 49.94
2020-08-13 | 5:17 | 49.94
2020-08-13 | 5:17 | 49.941
2020-08-13 | 5:17 | 49.941
2020-08-13 | 5:17 | 49.943
2020-08-13 | 5:17 | 49.943
2020-08-13 | 5:17 | 49.944
2020-08-13 | 5:17 | 49.945
2020-08-13 | 5:17 | 49.946
2020-08-13 | 5:17 | 49.948
2020-08-13 | 5:17 | 49.948
2020-08-13 | 5:17 | 49.949
2020-08-13 | 5:17 | 49.949
2020-08-13 | 5:17 | 49.948
2020-08-13 | 5:17 | 49.948
2020-08-13 | 5:17 | 49.945
2020-08-13 | 5:17 | 49.945
2020-08-13 | 5:17 | 49.942
2020-08-13 | 5:17 | 49.941
2020-08-13 | 5:17 | 49.939
2020-08-13 | 5:17 | 49.937
2020-08-13 | 5:17 | 49.935
2020-08-13 | 5:17 | 49.933
2020-08-13 | 5:17 | 49.933
2020-08-13 | 5:17 | 49.933
2020-08-13 | 5:17 | 49.932
2020-08-13 | 5:17 | 49.932
2020-08-13 | 5:17 | 49.932
2020-08-13 | 5:17 | 49.932
2020-08-13 | 5:17 | 49.933
2020-08-13 | 5:17 | 49.935
2020-08-13 | 5:17 | 49.938
2020-08-13 | 5:17 | 49.939
2020-08-13 | 5:17 | 49.94
2020-08-13 | 5:17 | 49.943
2020-08-13 | 5:17 | 49.942
2020-08-13 | 5:18 | 49.942
2020-08-13 | 5:18 | 49.939
2020-08-13 | 5:18 | 49.938
2020-08-13 | 5:18 | 49.938
2020-08-13 | 5:18 | 49.939
2020-08-13 | 5:18 | 49.941
2020-08-13 | 5:18 | 49.94
2020-08-13 | 5:18 | 49.939
2020-08-13 | 5:18 | 49.939
2020-08-13 | 5:18 | 49.937
2020-08-13 | 5:18 | 49.935
2020-08-13 | 5:18 | 49.934
2020-08-13 | 5:18 | 49.933
2020-08-13 | 5:18 | 49.932
2020-08-13 | 5:18 | 49.931
2020-08-13 | 5:18 | 49.931
2020-08-13 | 5:18 | 49.929
2020-08-13 | 5:18 | 49.928
2020-08-13 | 5:18 | 49.928
2020-08-13 | 5:18 | 49.928
2020-08-13 | 5:18 | 49.928
2020-08-13 | 5:18 | 49.927
2020-08-13 | 5:18 | 49.928
2020-08-13 | 5:18 | 49.929
2020-08-13 | 5:18 | 49.931
2020-08-13 | 5:18 | 49.934
2020-08-13 | 5:18 | 49.936
2020-08-13 | 5:18 | 49.937
2020-08-13 | 5:18 | 49.936
2020-08-13 | 5:18 | 49.939
2020-08-13 | 5:18 | 49.939
2020-08-13 | 5:18 | 49.939
2020-08-13 | 5:18 | 49.94
2020-08-13 | 5:18 | 49.943
2020-08-13 | 5:18 | 49.945
2020-08-13 | 5:18 | 49.945
2020-08-13 | 5:18 | 49.945
2020-08-13 | 5:18 | 49.945
2020-08-13 | 5:18 | 49.945
2020-08-13 | 5:18 | 49.945
2020-08-13 | 5:18 | 49.945
2020-08-13 | 5:18 | 49.945
2020-08-13 | 5:18 | 49.944
2020-08-13 | 5:18 | 49.945
2020-08-13 | 5:18 | 49.943
2020-08-13 | 5:18 | 49.943
2020-08-13 | 5:18 | 49.943
2020-08-13 | 5:18 | 49.941
2020-08-13 | 5:18 | 49.941
2020-08-13 | 5:18 | 49.939
2020-08-13 | 5:18 | 49.942
2020-08-13 | 5:18 | 49.943
2020-08-13 | 5:18 | 49.946
2020-08-13 | 5:18 | 49.949
2020-08-13 | 5:18 | 49.953
2020-08-13 | 5:18 | 49.954
2020-08-13 | 5:18 | 49.955
2020-08-13 | 5:18 | 49.957
2020-08-13 | 5:18 | 49.956
2020-08-13 | 5:19 | 49.955
2020-08-13 | 5:19 | 49.953
2020-08-13 | 5:19 | 49.952
2020-08-13 | 5:19 | 49.949
2020-08-13 | 5:19 | 49.947
2020-08-13 | 5:19 | 49.946
2020-08-13 | 5:19 | 49.943
2020-08-13 | 5:19 | 49.943
2020-08-13 | 5:19 | 49.943
2020-08-13 | 5:19 | 49.944
2020-08-13 | 5:19 | 49.944
2020-08-13 | 5:19 | 49.944
2020-08-13 | 5:19 | 49.944
2020-08-13 | 5:19 | 49.943
2020-08-13 | 5:19 | 49.945
2020-08-13 | 5:19 | 49.945
2020-08-13 | 5:19 | 49.945
2020-08-13 | 5:19 | 49.944
2020-08-13 | 5:19 | 49.943
2020-08-13 | 5:19 | 49.943
2020-08-13 | 5:19 | 49.943
2020-08-13 | 5:19 | 49.945
2020-08-13 | 5:19 | 49.948
2020-08-13 | 5:19 | 49.95
2020-08-13 | 5:19 | 49.952
2020-08-13 | 5:19 | 49.953
2020-08-13 | 5:19 | 49.952
2020-08-13 | 5:19 | 49.952
2020-08-13 | 5:19 | 49.953
2020-08-13 | 5:19 | 49.956
2020-08-13 | 5:19 | 49.954
2020-08-13 | 5:19 | 49.954
2020-08-13 | 5:19 | 49.953
2020-08-13 | 5:19 | 49.953
2020-08-13 | 5:19 | 49.953
2020-08-13 | 5:19 | 49.952
2020-08-13 | 5:19 | 49.95
2020-08-13 | 5:19 | 49.948
2020-08-13 | 5:19 | 49.945
2020-08-13 | 5:19 | 49.941
2020-08-13 | 5:19 | 49.937
2020-08-13 | 5:19 | 49.937
2020-08-13 | 5:19 | 49.935
2020-08-13 | 5:19 | 49.934
2020-08-13 | 5:19 | 49.935
2020-08-13 | 5:19 | 49.934
2020-08-13 | 5:19 | 49.936
2020-08-13 | 5:19 | 49.94
2020-08-13 | 5:19 | 49.942
2020-08-13 | 5:19 | 49.943
2020-08-13 | 5:19 | 49.943
2020-08-13 | 5:19 | 49.942
2020-08-13 | 5:19 | 49.942
2020-08-13 | 5:19 | 49.942
2020-08-13 | 5:19 | 49.942
2020-08-13 | 5:19 | 49.942
2020-08-13 | 5:19 | 49.942
2020-08-13 | 5:19 | 49.941
2020-08-13 | 5:19 | 49.942
2020-08-13 | 5:19 | 49.945
2020-08-13 | 5:20 | 49.943
2020-08-13 | 5:20 | 49.943
2020-08-13 | 5:20 | 49.944
2020-08-13 | 5:20 | 49.943
2020-08-13 | 5:20 | 49.943
2020-08-13 | 5:20 | 49.944
2020-08-13 | 5:20 | 49.944
2020-08-13 | 5:20 | 49.944
2020-08-13 | 5:20 | 49.941
2020-08-13 | 5:20 | 49.937
2020-08-13 | 5:20 | 49.933
2020-08-13 | 5:20 | 49.929
2020-08-13 | 5:20 | 49.924
2020-08-13 | 5:20 | 49.924
2020-08-13 | 5:20 | 49.924
2020-08-13 | 5:20 | 49.924
2020-08-13 | 5:20 | 49.926
2020-08-13 | 5:20 | 49.925
2020-08-13 | 5:20 | 49.927
2020-08-13 | 5:20 | 49.927
2020-08-13 | 5:20 | 49.927
2020-08-13 | 5:20 | 49.927
2020-08-13 | 5:20 | 49.926
2020-08-13 | 5:20 | 49.926
2020-08-13 | 5:20 | 49.926
2020-08-13 | 5:20 | 49.931
2020-08-13 | 5:20 | 49.935
2020-08-13 | 5:20 | 49.939
2020-08-13 | 5:20 | 49.942
2020-08-13 | 5:20 | 49.943
2020-08-13 | 5:20 | 49.943
2020-08-13 | 5:20 | 49.945
2020-08-13 | 5:20 | 49.942
2020-08-13 | 5:20 | 49.941
2020-08-13 | 5:20 | 49.939
2020-08-13 | 5:20 | 49.935
2020-08-13 | 5:20 | 49.936
2020-08-13 | 5:20 | 49.935
2020-08-13 | 5:20 | 49.933
2020-08-13 | 5:20 | 49.931
2020-08-13 | 5:20 | 49.929
2020-08-13 | 5:20 | 49.928
2020-08-13 | 5:20 | 49.929
2020-08-13 | 5:20 | 49.927
2020-08-13 | 5:20 | 49.926
2020-08-13 | 5:20 | 49.928
2020-08-13 | 5:20 | 49.928
2020-08-13 | 5:20 | 49.928
2020-08-13 | 5:20 | 49.927
2020-08-13 | 5:20 | 49.927
2020-08-13 | 5:20 | 49.926
2020-08-13 | 5:20 | 49.926
2020-08-13 | 5:20 | 49.925
2020-08-13 | 5:20 | 49.927
2020-08-13 | 5:20 | 49.929
2020-08-13 | 5:20 | 49.929
2020-08-13 | 5:20 | 49.931
2020-08-13 | 5:20 | 49.932
2020-08-13 | 5:20 | 49.932
2020-08-13 | 5:20 | 49.931
2020-08-13 | 5:20 | 49.932
2020-08-13 | 5:21 | 49.933
2020-08-13 | 5:21 | 49.934
2020-08-13 | 5:21 | 49.934
2020-08-13 | 5:21 | 49.934
2020-08-13 | 5:21 | 49.931
2020-08-13 | 5:21 | 49.927
2020-08-13 | 5:21 | 49.925
2020-08-13 | 5:21 | 49.925
2020-08-13 | 5:21 | 49.926
2020-08-13 | 5:21 | 49.926
2020-08-13 | 5:21 | 49.928
2020-08-13 | 5:21 | 49.929
2020-08-13 | 5:21 | 49.929
2020-08-13 | 5:21 | 49.929
2020-08-13 | 5:21 | 49.93
2020-08-13 | 5:21 | 49.931
2020-08-13 | 5:21 | 49.934
2020-08-13 | 5:21 | 49.935
2020-08-13 | 5:21 | 49.936
2020-08-13 | 5:21 | 49.936
2020-08-13 | 5:21 | 49.939
2020-08-13 | 5:21 | 49.942
2020-08-13 | 5:21 | 49.946
2020-08-13 | 5:21 | 49.949
2020-08-13 | 5:21 | 49.953
2020-08-13 | 5:21 | 49.958
2020-08-13 | 5:21 | 49.959
2020-08-13 | 5:21 | 49.961
2020-08-13 | 5:21 | 49.962

## Event 20200816-1
In UTC
Date | Time | Freq
2020-08-16 | 21:56 | 50.174
2020-08-16 | 21:56 | 50.175
2020-08-16 | 21:56 | 50.176
2020-08-16 | 21:56 | 50.178
2020-08-16 | 21:56 | 50.18
2020-08-16 | 22:56 | 50.183
2020-08-16 | 23:56 | 50.185
2020-08-16 | 24:56 | 50.187
2020-08-16 | 25:56 | 50.189
2020-08-16 | 26:56 | 50.192
2020-08-16 | 27:56 | 50.194
2020-08-16 | 28:56 | 50.196
2020-08-16 | 29:56 | 50.196
2020-08-16 | 30:56 | 50.197
2020-08-16 | 31:56 | 50.198
2020-08-16 | 32:56 | 50.198
2020-08-16 | 33:56 | 50.199
2020-08-16 | 34:56 | 50.199
2020-08-16 | 35:56 | 50.199
2020-08-16 | 36:56 | 50.198
2020-08-16 | 37:56 | 50.197
2020-08-16 | 38:56 | 50.196
2020-08-16 | 39:56 | 50.195
2020-08-16 | 40:56 | 50.194
2020-08-16 | 41:56 | 50.193
2020-08-16 | 42:56 | 50.193
2020-08-16 | 43:56 | 50.194
2020-08-16 | 44:56 | 50.194
2020-08-16 | 45:56 | 50.196
2020-08-16 | 46:56 | 50.198
2020-08-16 | 47:56 | 50.199
2020-08-16 | 48:56 | 50.201
2020-08-16 | 49:56 | 50.203
2020-08-16 | 50:56 | 50.205
2020-08-16 | 51:56 | 50.206
2020-08-16 | 52:56 | 50.207
2020-08-16 | 53:56 | 50.206
2020-08-16 | 54:56 | 50.207
2020-08-16 | 55:56 | 50.208
2020-08-16 | 56:56 | 50.208
2020-08-16 | 57:56 | 50.209
2020-08-16 | 58:56 | 50.21
2020-08-16 | 59:56 | 50.211
2020-08-16 | 60:56 | 50.211
2020-08-16 | 61:56 | 50.211
2020-08-16 | 62:56 | 50.212
2020-08-16 | 63:56 | 50.213
2020-08-16 | 64:56 | 50.21
2020-08-16 | 65:56 | 50.209
2020-08-16 | 66:56 | 50.206
2020-08-16 | 67:56 | 50.203
2020-08-16 | 68:56 | 50.201
2020-08-16 | 69:56 | 50.201
2020-08-16 | 70:56 | 50.201
2020-08-16 | 71:56 | 50.203
2020-08-16 | 72:56 | 50.203
2020-08-16 | 73:56 | 50.204
2020-08-16 | 74:56 | 50.206
2020-08-16 | 75:56 | 50.208
2020-08-16 | 76:56 | 50.21
2020-08-16 | 77:56 | 50.209
2020-08-16 | 78:56 | 50.211
2020-08-16 | 79:56 | 50.212
2020-08-16 | 80:56 | 50.214
2020-08-16 | 81:56 | 50.215
2020-08-16 | 82:56 | 50.217
2020-08-16 | 83:56 | 50.222
2020-08-16 | 84:56 | 50.227
2020-08-16 | 85:56 | 50.231
2020-08-16 | 86:56 | 50.235
2020-08-16 | 87:56 | 50.239
2020-08-16 | 88:56 | 50.241
2020-08-16 | 89:56 | 50.242
2020-08-16 | 90:56 | 50.241
2020-08-16 | 91:56 | 50.24
2020-08-16 | 92:56 | 50.24
2020-08-16 | 93:56 | 50.24
2020-08-16 | 94:56 | 50.24
2020-08-16 | 95:56 | 50.241
2020-08-16 | 96:56 | 50.241
2020-08-16 | 97:56 | 50.241
2020-08-16 | 98:56 | 50.239
2020-08-16 | 99:56 | 50.238
2020-08-16 | 100:56 | 50.237
2020-08-16 | 101:56 | 50.237
2020-08-16 | 102:56 | 50.237
2020-08-16 | 103:56 | 50.236
2020-08-16 | 104:56 | 50.235
2020-08-16 | 105:56 | 50.238
2020-08-16 | 106:56 | 50.239
2020-08-16 | 107:56 | 50.24
2020-08-16 | 108:56 | 50.243
2020-08-16 | 109:56 | 50.244
2020-08-16 | 110:56 | 50.247
2020-08-16 | 111:56 | 50.251
2020-08-16 | 112:56 | 50.251
2020-08-16 | 113:56 | 50.254
2020-08-16 | 114:56 | 50.255
2020-08-16 | 115:56 | 50.255
2020-08-16 | 116:56 | 50.255
2020-08-16 | 117:56 | 50.255
2020-08-16 | 118:56 | 50.252
2020-08-16 | 119:56 | 50.25
2020-08-16 | 120:56 | 50.248
2020-08-16 | 121:56 | 50.246
2020-08-16 | 122:56 | 50.244
2020-08-16 | 123:56 | 50.242
2020-08-16 | 124:56 | 50.24
2020-08-16 | 125:56 | 50.238
2020-08-16 | 126:56 | 50.237
2020-08-16 | 127:56 | 50.235
2020-08-16 | 128:56 | 50.234
2020-08-16 | 129:56 | 50.234
2020-08-16 | 130:56 | 50.233
2020-08-16 | 131:56 | 50.232
2020-08-16 | 132:56 | 50.229
2020-08-16 | 133:56 | 50.226
2020-08-16 | 134:56 | 50.225
2020-08-16 | 135:56 | 50.224
2020-08-16 | 136:56 | 50.224
2020-08-16 | 137:56 | 50.223
2020-08-16 | 138:56 | 50.223
2020-08-16 | 139:56 | 50.222
2020-08-16 | 140:56 | 50.221
2020-08-16 | 141:56 | 50.22
2020-08-16 | 142:56 | 50.219
2020-08-16 | 143:56 | 50.219
2020-08-16 | 144:56 | 50.219
2020-08-16 | 145:56 | 50.221
2020-08-16 | 146:56 | 50.223
2020-08-16 | 147:56 | 50.225
2020-08-16 | 148:56 | 50.227
2020-08-16 | 149:56 | 50.228
2020-08-16 | 150:56 | 50.227
2020-08-16 | 151:56 | 50.227
2020-08-16 | 152:56 | 50.226
2020-08-16 | 153:56 | 50.227
2020-08-16 | 154:56 | 50.226
2020-08-16 | 155:56 | 50.226
2020-08-16 | 156:56 | 50.224
2020-08-16 | 157:56 | 50.22
2020-08-16 | 158:56 | 50.218
2020-08-16 | 159:56 | 50.216
2020-08-16 | 160:56 | 50.212
2020-08-16 | 161:56 | 50.208
2020-08-16 | 162:56 | 50.204
2020-08-16 | 163:56 | 50.204
2020-08-16 | 164:56 | 50.205
2020-08-16 | 165:56 | 50.206
2020-08-16 | 166:56 | 50.208
2020-08-16 | 167:56 | 50.21
2020-08-16 | 168:56 | 50.211
2020-08-16 | 169:56 | 50.212
2020-08-16 | 170:56 | 50.21
2020-08-16 | 171:56 | 50.21
2020-08-16 | 172:56 | 50.208
2020-08-16 | 173:56 | 50.205
2020-08-16 | 174:56 | 50.203
2020-08-16 | 175:56 | 50.201
2020-08-16 | 176:56 | 50.199
2020-08-16 | 177:56 | 50.194
2020-08-16 | 178:56 | 50.19
2020-08-16 | 179:56 | 50.185
2020-08-16 | 180:56 | 50.179
2020-08-16 | 181:56 | 50.165
2020-08-16 | 182:56 | 50.15
2020-08-16 | 183:56 | 50.136
2020-08-16 | 184:56 | 50.124
2020-08-16 | 185:56 | 50.113
2020-08-16 | 186:56 | 50.102
2020-08-16 | 187:56 | 50.093
2020-08-16 | 188:56 | 50.086
2020-08-16 | 189:56 | 50.081
2020-08-16 | 190:56 | 50.078
2020-08-16 | 191:56 | 50.074
2020-08-16 | 192:56 | 50.07
2020-08-16 | 193:56 | 50.067
2020-08-16 | 194:56 | 50.064
2020-08-16 | 195:56 | 50.064
2020-08-16 | 196:56 | 50.064
2020-08-16 | 197:56 | 50.064
2020-08-16 | 198:56 | 50.063
2020-08-16 | 199:56 | 50.062
2020-08-16 | 200:56 | 50.058
2020-08-16 | 201:56 | 50.055
2020-08-16 | 202:56 | 50.051
2020-08-16 | 203:56 | 50.047
2020-08-16 | 204:56 | 50.043
2020-08-16 | 205:56 | 50.04
2020-08-16 | 206:56 | 50.038
2020-08-16 | 207:56 | 50.036
2020-08-16 | 208:56 | 50.031
2020-08-16 | 209:56 | 50.026
2020-08-16 | 210:56 | 50.021
2020-08-16 | 211:56 | 50.014
2020-08-16 | 212:56 | 50.006
2020-08-16 | 213:56 | 50
2020-08-16 | 214:56 | 49.992
2020-08-16 | 215:56 | 49.988
2020-08-16 | 216:56 | 49.981
2020-08-16 | 217:56 | 49.978
2020-08-16 | 218:56 | 49.975
2020-08-16 | 219:56 | 49.973
2020-08-16 | 220:56 | 49.971
2020-08-16 | 221:56 | 49.969
2020-08-16 | 222:56 | 49.967
2020-08-16 | 223:56 | 49.966
2020-08-16 | 224:56 | 49.964
2020-08-16 | 225:56 | 49.96
2020-08-16 | 226:56 | 49.957
2020-08-16 | 227:56 | 49.953
2020-08-16 | 228:56 | 49.95
2020-08-16 | 229:56 | 49.948
2020-08-16 | 230:56 | 49.948
2020-08-16 | 231:56 | 49.948
2020-08-16 | 232:56 | 49.949
2020-08-16 | 233:56 | 49.949
2020-08-16 | 234:56 | 49.948
2020-08-16 | 235:56 | 49.946
2020-08-16 | 236:56 | 49.943
2020-08-16 | 237:56 | 49.94
2020-08-16 | 238:56 | 49.938
2020-08-16 | 239:56 | 49.934
2020-08-16 | 240:56 | 49.931
2020-08-16 | 241:56 | 49.927
2020-08-16 | 242:56 | 49.926
2020-08-16 | 243:56 | 49.922
2020-08-16 | 244:56 | 49.92
2020-08-16 | 245:56 | 49.916
2020-08-16 | 246:56 | 49.913
2020-08-16 | 247:56 | 49.909
2020-08-16 | 248:56 | 49.905
2020-08-16 | 249:56 | 49.903
2020-08-16 | 250:56 | 49.901
2020-08-16 | 251:56 | 49.899
2020-08-16 | 252:56 | 49.898
2020-08-16 | 253:56 | 49.895
2020-08-16 | 254:56 | 49.89
2020-08-16 | 255:56 | 49.885
2020-08-16 | 256:56 | 49.879
2020-08-16 | 257:56 | 49.872
2020-08-16 | 258:56 | 49.865
2020-08-16 | 259:56 | 49.858
2020-08-16 | 260:56 | 49.853
2020-08-16 | 261:56 | 49.847
2020-08-16 | 262:56 | 49.843
2020-08-16 | 263:56 | 49.84
2020-08-16 | 264:56 | 49.836
2020-08-16 | 265:56 | 49.834
2020-08-16 | 266:56 | 49.831
2020-08-16 | 267:56 | 49.83
2020-08-16 | 268:56 | 49.83
2020-08-16 | 269:56 | 49.829
2020-08-16 | 270:56 | 49.83
2020-08-16 | 271:56 | 49.83
2020-08-16 | 272:56 | 49.827
2020-08-16 | 273:56 | 49.826
2020-08-16 | 274:56 | 49.824
2020-08-16 | 275:56 | 49.82
2020-08-16 | 276:56 | 49.819
2020-08-16 | 277:56 | 49.817
2020-08-16 | 278:56 | 49.815
2020-08-16 | 279:56 | 49.814
2020-08-16 | 280:56 | 49.812
2020-08-16 | 281:56 | 49.808
2020-08-16 | 282:56 | 49.803
2020-08-16 | 283:56 | 49.798
2020-08-16 | 284:56 | 49.794
2020-08-16 | 285:56 | 49.787
2020-08-16 | 286:56 | 49.78
2020-08-16 | 287:56 | 49.775
2020-08-16 | 288:56 | 49.768
2020-08-16 | 289:56 | 49.764
2020-08-16 | 290:56 | 49.759
2020-08-16 | 291:56 | 49.755
2020-08-16 | 292:56 | 49.752
2020-08-16 | 293:56 | 49.75
2020-08-16 | 294:56 | 49.748
2020-08-16 | 295:56 | 49.747
2020-08-16 | 296:56 | 49.744
2020-08-16 | 297:56 | 49.744
2020-08-16 | 298:56 | 49.742
2020-08-16 | 299:56 | 49.742
2020-08-16 | 300:56 | 49.742
2020-08-16 | 301:56 | 49.741
2020-08-16 | 302:56 | 49.741
2020-08-16 | 303:56 | 49.739
2020-08-16 | 304:56 | 49.739
2020-08-16 | 305:56 | 49.74
2020-08-16 | 306:56 | 49.738
2020-08-16 | 307:56 | 49.735
2020-08-16 | 308:56 | 49.732
2020-08-16 | 309:56 | 49.728
2020-08-16 | 310:56 | 49.724
2020-08-16 | 311:56 | 49.721
2020-08-16 | 312:56 | 49.72
2020-08-16 | 313:56 | 49.719
2020-08-16 | 314:56 | 49.72
2020-08-16 | 315:56 | 49.72
2020-08-16 | 316:56 | 49.719
2020-08-16 | 317:56 | 49.714
2020-08-16 | 318:56 | 49.71
2020-08-16 | 319:56 | 49.707
2020-08-16 | 320:56 | 49.706
2020-08-16 | 321:56 | 49.703
2020-08-16 | 322:56 | 49.7
2020-08-16 | 323:56 | 49.699
2020-08-16 | 324:56 | 49.697
2020-08-16 | 325:56 | 49.696
2020-08-16 | 326:56 | 49.695
2020-08-16 | 327:56 | 49.693
2020-08-16 | 328:56 | 49.69
2020-08-16 | 329:56 | 49.687
2020-08-16 | 330:56 | 49.686
2020-08-16 | 331:56 | 49.686
2020-08-16 | 332:56 | 49.686
2020-08-16 | 333:56 | 49.684
2020-08-16 | 334:56 | 49.683
2020-08-16 | 335:56 | 49.684
2020-08-16 | 336:56 | 49.684
2020-08-16 | 337:56 | 49.685
2020-08-16 | 338:56 | 49.688
2020-08-16 | 339:56 | 49.692
2020-08-16 | 340:56 | 49.697
2020-08-16 | 341:56 | 49.701
2020-08-16 | 342:56 | 49.708
2020-08-16 | 343:56 | 49.714
2020-08-16 | 344:56 | 49.721
2020-08-16 | 345:56 | 49.732
2020-08-16 | 346:56 | 49.741
2020-08-16 | 347:56 | 49.75
2020-08-16 | 348:56 | 49.761
2020-08-16 | 349:56 | 49.772
2020-08-16 | 350:56 | 49.786
2020-08-16 | 351:56 | 49.799
2020-08-16 | 352:56 | 49.816
2020-08-16 | 353:56 | 49.831
2020-08-16 | 354:56 | 49.842
2020-08-16 | 355:56 | 49.848
2020-08-16 | 356:56 | 49.852
2020-08-16 | 357:56 | 49.855
2020-08-16 | 358:56 | 49.856
2020-08-16 | 359:56 | 49.856
2020-08-16 | 360:56 | 49.856
2020-08-16 | 361:56 | 49.859
2020-08-16 | 362:56 | 49.859
2020-08-16 | 363:56 | 49.86
2020-08-16 | 364:56 | 49.862
2020-08-16 | 365:56 | 49.865
2020-08-16 | 366:56 | 49.866
2020-08-16 | 367:56 | 49.867
2020-08-16 | 368:56 | 49.869
2020-08-16 | 369:56 | 49.871
2020-08-16 | 370:56 | 49.872
2020-08-16 | 371:56 | 49.869
2020-08-16 | 372:56 | 49.867
2020-08-16 | 373:56 | 49.864
2020-08-16 | 374:56 | 49.863
2020-08-16 | 375:56 | 49.863
2020-08-16 | 376:56 | 49.861
2020-08-16 | 377:56 | 49.86
2020-08-16 | 378:56 | 49.859
2020-08-16 | 379:56 | 49.859
2020-08-16 | 380:56 | 49.86
2020-08-16 | 381:56 | 49.861
2020-08-16 | 382:56 | 49.864
2020-08-16 | 383:56 | 49.864
2020-08-16 | 384:56 | 49.866
2020-08-16 | 385:56 | 49.868
2020-08-16 | 386:56 | 49.869
2020-08-16 | 387:56 | 49.869
2020-08-16 | 388:56 | 49.868
2020-08-16 | 389:56 | 49.868
2020-08-16 | 390:56 | 49.869
2020-08-16 | 391:56 | 49.869
2020-08-16 | 392:56 | 49.869
2020-08-16 | 393:56 | 49.869
2020-08-16 | 394:56 | 49.868
2020-08-16 | 395:56 | 49.869
2020-08-16 | 396:56 | 49.869
2020-08-16 | 397:56 | 49.872
2020-08-16 | 398:56 | 49.874
2020-08-16 | 399:56 | 49.874
2020-08-16 | 400:56 | 49.876
2020-08-16 | 401:56 | 49.878
2020-08-16 | 402:56 | 49.882
2020-08-16 | 403:56 | 49.888
2020-08-16 | 404:56 | 49.892
2020-08-16 | 405:56 | 49.896
2020-08-16 | 406:56 | 49.898
2020-08-16 | 407:56 | 49.899
2020-08-16 | 408:56 | 49.898
2020-08-16 | 409:56 | 49.901
2020-08-16 | 410:56 | 49.9
2020-08-16 | 411:56 | 49.902
2020-08-16 | 412:56 | 49.903
2020-08-16 | 413:56 | 49.906
2020-08-16 | 414:56 | 49.907
2020-08-16 | 415:56 | 49.909
2020-08-16 | 416:56 | 49.912
2020-08-16 | 417:56 | 49.915
2020-08-16 | 418:56 | 49.917
2020-08-16 | 419:56 | 49.922
2020-08-16 | 420:56 | 49.924
2020-08-16 | 421:56 | 49.925
2020-08-16 | 422:56 | 49.926
2020-08-16 | 423:56 | 49.928
2020-08-16 | 424:56 | 49.929
2020-08-16 | 425:56 | 49.932
2020-08-16 | 426:56 | 49.934
2020-08-16 | 427:56 | 49.935
2020-08-16 | 428:56 | 49.939
2020-08-16 | 429:56 | 49.942
2020-08-16 | 430:56 | 49.943
2020-08-16 | 431:56 | 49.947
2020-08-16 | 432:56 | 49.949
2020-08-16 | 433:56 | 49.949
2020-08-16 | 434:56 | 49.95
2020-08-16 | 435:56 | 49.951
2020-08-16 | 436:56 | 49.948
2020-08-16 | 437:56 | 49.944
2020-08-16 | 438:56 | 49.941
2020-08-16 | 439:56 | 49.94
2020-08-16 | 440:56 | 49.94
2020-08-16 | 441:56 | 49.938
2020-08-16 | 442:56 | 49.938
2020-08-16 | 443:56 | 49.938
2020-08-16 | 444:56 | 49.938
2020-08-16 | 445:56 | 49.937
2020-08-16 | 446:56 | 49.936
2020-08-16 | 447:56 | 49.935
2020-08-16 | 448:56 | 49.935
2020-08-16 | 449:56 | 49.936
2020-08-16 | 450:56 | 49.935
2020-08-16 | 451:56 | 49.935
2020-08-16 | 452:56 | 49.934
2020-08-16 | 453:56 | 49.934
2020-08-16 | 454:56 | 49.936
2020-08-16 | 455:56 | 49.938
2020-08-16 | 456:56 | 49.941
2020-08-16 | 457:56 | 49.944
2020-08-16 | 458:56 | 49.945
2020-08-16 | 459:56 | 49.948
2020-08-16 | 460:56 | 49.949
2020-08-16 | 461:56 | 49.952
2020-08-16 | 462:56 | 49.953
2020-08-16 | 463:56 | 49.953
2020-08-16 | 464:56 | 49.955
2020-08-16 | 465:56 | 49.956
2020-08-16 | 466:56 | 49.957
2020-08-16 | 467:56 | 49.957
2020-08-16 | 468:56 | 49.958
2020-08-16 | 469:56 | 49.959
2020-08-16 | 470:56 | 49.96
2020-08-16 | 471:56 | 49.962
2020-08-16 | 472:56 | 49.963
2020-08-16 | 473:56 | 49.965
2020-08-16 | 474:56 | 49.968
2020-08-16 | 475:56 | 49.97
2020-08-16 | 476:56 | 49.972
2020-08-16 | 477:56 | 49.973
2020-08-16 | 478:56 | 49.975
2020-08-16 | 479:56 | 49.976
2020-08-16 | 480:56 | 49.976
2020-08-16 | 481:56 | 49.975
2020-08-16 | 482:56 | 49.973
2020-08-16 | 483:56 | 49.968
2020-08-16 | 484:56 | 49.967
2020-08-16 | 485:56 | 49.962
2020-08-16 | 486:56 | 49.96
2020-08-16 | 487:56 | 49.959
2020-08-16 | 488:56 | 49.959
2020-08-16 | 489:56 | 49.96
2020-08-16 | 490:56 | 49.961
2020-08-16 | 491:56 | 49.962
2020-08-16 | 492:56 | 49.965
2020-08-16 | 493:56 | 49.967
2020-08-16 | 494:56 | 49.969
2020-08-16 | 495:56 | 49.971
2020-08-16 | 496:56 | 49.973
2020-08-16 | 497:56 | 49.976
2020-08-16 | 498:56 | 49.978
2020-08-16 | 499:56 | 49.978
2020-08-16 | 500:56 | 49.979
2020-08-16 | 501:56 | 49.981
2020-08-16 | 502:56 | 49.98
2020-08-16 | 503:56 | 49.98
2020-08-16 | 504:56 | 49.978
2020-08-16 | 505:56 | 49.976
2020-08-16 | 506:56 | 49.976
2020-08-16 | 507:56 | 49.974
2020-08-16 | 508:56 | 49.972
2020-08-16 | 509:56 | 49.972
2020-08-16 | 510:56 | 49.97
2020-08-16 | 511:56 | 49.967
2020-08-16 | 512:56 | 49.964
2020-08-16 | 513:56 | 49.964
2020-08-16 | 514:56 | 49.963
2020-08-16 | 515:56 | 49.963
2020-08-16 | 516:56 | 49.965
2020-08-16 | 517:56 | 49.967
2020-08-16 | 518:56 | 49.968
2020-08-16 | 519:56 | 49.968
2020-08-16 | 520:56 | 49.969
2020-08-16 | 521:56 | 49.97
2020-08-16 | 522:56 | 49.972
2020-08-16 | 523:56 | 49.974
2020-08-16 | 524:56 | 49.973
2020-08-16 | 525:56 | 49.974
2020-08-16 | 526:56 | 49.976
2020-08-16 | 527:56 | 49.978
2020-08-16 | 528:56 | 49.982
2020-08-16 | 529:56 | 49.987
2020-08-16 | 530:56 | 49.991
2020-08-16 | 531:56 | 49.998
2020-08-16 | 532:56 | 50.004
2020-08-16 | 533:56 | 50.008
2020-08-16 | 534:56 | 50.011
2020-08-16 | 535:56 | 50.016
2020-08-16 | 536:56 | 50.016
2020-08-16 | 537:56 | 50.017
2020-08-16 | 538:56 | 50.016
2020-08-16 | 539:56 | 50.017
2020-08-16 | 540:56 | 50.016
2020-08-16 | 541:56 | 50.018
2020-08-16 | 542:56 | 50.019
2020-08-16 | 543:56 | 50.02
2020-08-16 | 544:56 | 50.021
2020-08-16 | 545:56 | 50.023
2020-08-16 | 546:56 | 50.023
2020-08-16 | 547:56 | 50.026
2020-08-16 | 548:56 | 50.026
2020-08-16 | 549:56 | 50.025
2020-08-16 | 550:56 | 50.024
2020-08-16 | 551:56 | 50.023
2020-08-16 | 552:56 | 50.023
2020-08-16 | 553:56 | 50.022
2020-08-16 | 554:56 | 50.022
2020-08-16 | 555:56 | 50.02
2020-08-16 | 556:56 | 50.02
2020-08-16 | 557:56 | 50.018
2020-08-16 | 558:56 | 50.017
2020-08-16 | 559:56 | 50.016
2020-08-16 | 560:56 | 50.016
2020-08-16 | 561:56 | 50.017
2020-08-16 | 562:56 | 50.022
2020-08-16 | 563:56 | 50.025
2020-08-16 | 564:56 | 50.029
2020-08-16 | 565:56 | 50.031
2020-08-16 | 566:56 | 50.035
2020-08-16 | 567:56 | 50.037
2020-08-16 | 568:56 | 50.037
2020-08-16 | 569:56 | 50.04
2020-08-16 | 570:56 | 50.042
2020-08-16 | 571:56 | 50.044
2020-08-16 | 572:56 | 50.048
2020-08-16 | 573:56 | 50.05
2020-08-16 | 574:56 | 50.05
2020-08-16 | 575:56 | 50.051
2020-08-16 | 576:56 | 50.05
2020-08-16 | 577:56 | 50.051
2020-08-16 | 578:56 | 50.05
2020-08-16 | 579:56 | 50.05
2020-08-16 | 580:56 | 50.05
2020-08-16 | 581:56 | 50.052
2020-08-16 | 582:56 | 50.055
2020-08-16 | 583:56 | 50.058
2020-08-16 | 584:56 | 50.059
2020-08-16 | 585:56 | 50.061
2020-08-16 | 586:56 | 50.061
2020-08-16 | 587:56 | 50.06
2020-08-16 | 588:56 | 50.06
2020-08-16 | 589:56 | 50.06
2020-08-16 | 590:56 | 50.061
2020-08-16 | 591:56 | 50.061
2020-08-16 | 592:56 | 50.064
2020-08-16 | 593:56 | 50.066
2020-08-16 | 594:56 | 50.067
2020-08-16 | 595:56 | 50.067
2020-08-16 | 596:56 | 50.067
2020-08-16 | 597:56 | 50.068
2020-08-16 | 598:56 | 50.068
2020-08-16 | 599:56 | 50.069
2020-08-16 | 600:56 | 50.071
2020-08-16 | 601:56 | 50.074
2020-08-16 | 602:56 | 50.074
2020-08-16 | 603:56 | 50.074
2020-08-16 | 604:56 | 50.074
2020-08-16 | 605:56 | 50.073
2020-08-16 | 606:56 | 50.072
2020-08-16 | 607:56 | 50.069
2020-08-16 | 608:56 | 50.066
2020-08-16 | 609:56 | 50.066
2020-08-16 | 610:56 | 50.063
2020-08-16 | 611:56 | 50.063
2020-08-16 | 612:56 | 50.063
2020-08-16 | 613:56 | 50.064
2020-08-16 | 614:56 | 50.068
2020-08-16 | 615:56 | 50.073
2020-08-16 | 616:56 | 50.077
617:56
618:56
619:56
620:56
621:56
622:56
623:56
624:56
625:56
626:56
627:56
628:56
629:56
630:56
631:56
632:56
633:56
634:56
635:56
636:56
637:56
638:56
639:56
640:56
641:56
642:56
643:56
644:56
645:56
646:56
647:56
648:56
649:56
650:56
651:56
652:56
653:56
654:56
655:56
656:56
657:56
658:56
659:56
660:56
661:56
662:56
663:56
664:56
665:56
666:56
667:56
668:56
669:56
670:56
671:56
672:56
673:56
674:56
675:56
676:56
677:56
678:56
679:56
680:56
681:56
682:56
683:56
684:56
685:56
686:56
687:56
688:56
689:56
690:56
691:56
692:56
693:56
694:56
695:56
696:56
697:56
698:56
699:56
700:56
701:56
702:56
703:56
704:56
705:56
706:56
707:56
708:56
709:56
710:56
711:56
712:56
713:56
714:56
715:56
716:56
717:56
718:56
719:56
720:56
721:56
722:56
723:56
724:56
725:56
726:56
727:56
728:56
729:56
730:56
731:56
732:56
733:56
734:56
735:56
736:56
737:56
738:56
739:56
740:56
741:56
742:56
743:56
744:56
745:56
746:56
747:56
748:56
749:56
750:56
751:56
752:56
753:56
754:56
755:56
756:56
757:56
758:56
759:56
760:56
761:56
762:56
763:56
764:56
765:56
766:56
767:56
768:56
769:56
770:56
771:56
772:56
773:56
774:56
775:56
776:56
777:56
778:56
779:56
780:56
781:56
782:56
783:56
784:56
785:56
786:56
787:56
788:56
789:56
790:56
791:56
792:56
793:56
794:56
795:56
796:56
797:56
798:56
799:56
800:56
801:56
802:56
803:56
804:56
805:56
806:56
807:56
808:56
809:56
810:56
811:56
812:56
813:56
814:56
815:56
816:56
817:56
818:56
819:56
820:56
821:56
822:56
823:56
824:56
825:56
826:56
827:56
828:56
829:56
830:56
831:56
832:56
833:56
834:56
835:56
836:56
837:56
838:56
839:56
840:56
841:56
842:56
843:56
844:56
845:56
846:56
847:56
848:56
849:56
850:56
851:56
852:56
853:56
854:56
855:56
856:56
857:56
858:56
859:56
860:56
861:56
862:56
863:56
864:56
865:56
866:56
867:56
868:56
869:56
870:56
871:56
872:56
873:56
874:56
875:56
876:56
877:56
878:56
879:56
880:56
881:56
882:56
883:56
884:56
885:56
886:56
887:56
888:56
889:56
890:56
891:56
892:56
893:56
894:56
895:56
896:56
897:56
898:56
899:56
900:56
901:56
902:56
903:56
904:56
905:56
906:56
907:56
908:56
909:56
910:56
911:56
912:56
913:56
914:56
915:56
916:56

## Event 20200817-1
In UTC
Date | Time | Freq
2020-08-17 | 9:52 | 50.034
2020-08-17 | 9:52 | 50.034
2020-08-17 | 9:52 | 50.031
2020-08-17 | 9:52 | 50.029
2020-08-17 | 9:52 | 50.026
2020-08-17 | 10:52 | 50.023
2020-08-17 | 11:52 | 50.02
2020-08-17 | 12:52 | 50.018
2020-08-17 | 13:52 | 50.018
2020-08-17 | 14:52 | 50.018
2020-08-17 | 15:52 | 50.016
2020-08-17 | 16:52 | 50.019
2020-08-17 | 17:52 | 50.018
2020-08-17 | 18:52 | 50.019
2020-08-17 | 19:52 | 50.018
2020-08-17 | 20:52 | 50.019
2020-08-17 | 21:52 | 50.02
2020-08-17 | 22:52 | 50.021
2020-08-17 | 23:52 | 50.021
2020-08-17 | 24:52 | 50.023
2020-08-17 | 25:52 | 50.021
2020-08-17 | 26:52 | 50.022
2020-08-17 | 27:52 | 50.019
2020-08-17 | 28:52 | 50.018
2020-08-17 | 29:52 | 50.017
2020-08-17 | 30:52 | 50.015
2020-08-17 | 31:52 | 50.014
2020-08-17 | 32:52 | 50.011
2020-08-17 | 33:52 | 50.009
2020-08-17 | 34:52 | 50.007
2020-08-17 | 35:52 | 50.003
2020-08-17 | 36:52 | 50.001
2020-08-17 | 37:52 | 49.998
2020-08-17 | 38:52 | 49.998
2020-08-17 | 39:52 | 49.997
2020-08-17 | 40:52 | 49.992
2020-08-17 | 41:52 | 49.992
2020-08-17 | 42:52 | 49.989
2020-08-17 | 43:52 | 49.986
2020-08-17 | 44:52 | 49.983
2020-08-17 | 45:52 | 49.98
2020-08-17 | 46:52 | 49.979
2020-08-17 | 47:52 | 49.98
2020-08-17 | 48:52 | 49.98
2020-08-17 | 49:52 | 49.98
2020-08-17 | 50:52 | 49.982
2020-08-17 | 51:52 | 49.984
2020-08-17 | 52:52 | 49.987
2020-08-17 | 53:52 | 49.988
2020-08-17 | 54:52 | 49.989
2020-08-17 | 55:52 | 49.99
2020-08-17 | 56:52 | 49.991
2020-08-17 | 57:52 | 49.991
2020-08-17 | 58:52 | 49.991
2020-08-17 | 59:52 | 49.991
2020-08-17 | 60:52 | 49.994
2020-08-17 | 61:52 | 49.998
2020-08-17 | 62:52 | 50.002
2020-08-17 | 63:52 | 50.006
2020-08-17 | 64:52 | 50.012
2020-08-17 | 65:52 | 50.017
2020-08-17 | 66:52 | 50.019
2020-08-17 | 67:52 | 50.019
2020-08-17 | 68:52 | 50.02
2020-08-17 | 69:52 | 50.019
2020-08-17 | 70:52 | 50.016
2020-08-17 | 71:52 | 50.014
2020-08-17 | 72:52 | 50.01
2020-08-17 | 73:52 | 50.008
2020-08-17 | 74:52 | 50.004
2020-08-17 | 75:52 | 50.001
2020-08-17 | 76:52 | 50.005
2020-08-17 | 77:52 | 50.005
2020-08-17 | 78:52 | 50.006
2020-08-17 | 79:52 | 50.007
2020-08-17 | 80:52 | 50.007
2020-08-17 | 81:52 | 50.006
2020-08-17 | 82:52 | 50.003
2020-08-17 | 83:52 | 50.002
2020-08-17 | 84:52 | 50
2020-08-17 | 85:52 | 49.996
2020-08-17 | 86:52 | 49.991
2020-08-17 | 87:52 | 49.988
2020-08-17 | 88:52 | 49.985
2020-08-17 | 89:52 | 49.982
2020-08-17 | 90:52 | 49.981
2020-08-17 | 91:52 | 49.98
2020-08-17 | 92:52 | 49.98
2020-08-17 | 93:52 | 49.979
2020-08-17 | 94:52 | 49.945
2020-08-17 | 95:52 | 49.911
2020-08-17 | 96:52 | 49.881
2020-08-17 | 97:52 | 49.859
2020-08-17 | 98:52 | 49.842
2020-08-17 | 99:52 | 49.829
2020-08-17 | 100:52 | 49.819
2020-08-17 | 101:52 | 49.81
2020-08-17 | 102:52 | 49.803
2020-08-17 | 103:52 | 49.794
2020-08-17 | 104:52 | 49.787
2020-08-17 | 105:52 | 49.782
2020-08-17 | 106:52 | 49.778
2020-08-17 | 107:52 | 49.773
2020-08-17 | 108:52 | 49.769
2020-08-17 | 109:52 | 49.765
2020-08-17 | 110:52 | 49.763
2020-08-17 | 111:52 | 49.76
2020-08-17 | 112:52 | 49.757
2020-08-17 | 113:52 | 49.754
2020-08-17 | 114:52 | 49.751
2020-08-17 | 115:52 | 49.75
2020-08-17 | 116:52 | 49.75
2020-08-17 | 117:52 | 49.751
2020-08-17 | 118:52 | 49.753
2020-08-17 | 119:52 | 49.754
2020-08-17 | 120:52 | 49.756
2020-08-17 | 121:52 | 49.76
2020-08-17 | 122:52 | 49.762
2020-08-17 | 123:52 | 49.764
2020-08-17 | 124:52 | 49.767
2020-08-17 | 125:52 | 49.768
2020-08-17 | 126:52 | 49.77
2020-08-17 | 127:52 | 49.769
2020-08-17 | 128:52 | 49.768
2020-08-17 | 129:52 | 49.767
2020-08-17 | 130:52 | 49.766
2020-08-17 | 131:52 | 49.765
2020-08-17 | 132:52 | 49.762
2020-08-17 | 133:52 | 49.759
2020-08-17 | 134:52 | 49.757
2020-08-17 | 135:52 | 49.755
2020-08-17 | 136:52 | 49.754
2020-08-17 | 137:52 | 49.753
2020-08-17 | 138:52 | 49.754
2020-08-17 | 139:52 | 49.754
2020-08-17 | 140:52 | 49.754
2020-08-17 | 141:52 | 49.754
2020-08-17 | 142:52 | 49.755
2020-08-17 | 143:52 | 49.758
2020-08-17 | 144:52 | 49.763
2020-08-17 | 145:52 | 49.767
2020-08-17 | 146:52 | 49.773
2020-08-17 | 147:52 | 49.779
2020-08-17 | 148:52 | 49.787
2020-08-17 | 149:52 | 49.794
2020-08-17 | 150:52 | 49.801
2020-08-17 | 151:52 | 49.811
2020-08-17 | 152:52 | 49.819
2020-08-17 | 153:52 | 49.828
2020-08-17 | 154:52 | 49.834
2020-08-17 | 155:52 | 49.839
2020-08-17 | 156:52 | 49.843
2020-08-17 | 157:52 | 49.849
2020-08-17 | 158:52 | 49.854
2020-08-17 | 159:52 | 49.86
2020-08-17 | 160:52 | 49.865
2020-08-17 | 161:52 | 49.869
2020-08-17 | 162:52 | 49.875
2020-08-17 | 163:52 | 49.882
2020-08-17 | 164:52 | 49.887
2020-08-17 | 165:52 | 49.891
2020-08-17 | 166:52 | 49.896
2020-08-17 | 167:52 | 49.899
2020-08-17 | 168:52 | 49.901
2020-08-17 | 169:52 | 49.902
2020-08-17 | 170:52 | 49.902
2020-08-17 | 171:52 | 49.901
2020-08-17 | 172:52 | 49.9
2020-08-17 | 173:52 | 49.901
2020-08-17 | 174:52 | 49.899
2020-08-17 | 175:52 | 49.896
2020-08-17 | 176:52 | 49.894
2020-08-17 | 177:52 | 49.895
2020-08-17 | 178:52 | 49.896
2020-08-17 | 179:52 | 49.897
2020-08-17 | 180:52 | 49.896
2020-08-17 | 181:52 | 49.898
2020-08-17 | 182:52 | 49.896
2020-08-17 | 183:52 | 49.894
2020-08-17 | 184:52 | 49.89
2020-08-17 | 185:52 | 49.886
2020-08-17 | 186:52 | 49.88
2020-08-17 | 187:52 | 49.876
2020-08-17 | 188:52 | 49.87
2020-08-17 | 189:52 | 49.866
2020-08-17 | 190:52 | 49.861
2020-08-17 | 191:52 | 49.854
2020-08-17 | 192:52 | 49.85
2020-08-17 | 193:52 | 49.846
2020-08-17 | 194:52 | 49.847
2020-08-17 | 195:52 | 49.844
2020-08-17 | 196:52 | 49.842
2020-08-17 | 197:52 | 49.84
2020-08-17 | 198:52 | 49.84
2020-08-17 | 199:52 | 49.841
2020-08-17 | 200:52 | 49.845
2020-08-17 | 201:52 | 49.85
2020-08-17 | 202:52 | 49.853
2020-08-17 | 203:52 | 49.858
2020-08-17 | 204:52 | 49.864
2020-08-17 | 205:52 | 49.867
2020-08-17 | 206:52 | 49.871
2020-08-17 | 207:52 | 49.874
2020-08-17 | 208:52 | 49.876
2020-08-17 | 209:52 | 49.877
2020-08-17 | 210:52 | 49.878
2020-08-17 | 211:52 | 49.879
2020-08-17 | 212:52 | 49.882
2020-08-17 | 213:52 | 49.883
2020-08-17 | 214:52 | 49.882
2020-08-17 | 215:52 | 49.884
2020-08-17 | 216:52 | 49.885
2020-08-17 | 217:52 | 49.887
2020-08-17 | 218:52 | 49.889
2020-08-17 | 219:52 | 49.892
2020-08-17 | 220:52 | 49.894
2020-08-17 | 221:52 | 49.895
2020-08-17 | 222:52 | 49.897
2020-08-17 | 223:52 | 49.897
2020-08-17 | 224:52 | 49.895
2020-08-17 | 225:52 | 49.894
2020-08-17 | 226:52 | 49.893
2020-08-17 | 227:52 | 49.892
2020-08-17 | 228:52 | 49.892
2020-08-17 | 229:52 | 49.892
2020-08-17 | 230:52 | 49.894
2020-08-17 | 231:52 | 49.895
2020-08-17 | 232:52 | 49.893
2020-08-17 | 233:52 | 49.891
2020-08-17 | 234:52 | 49.889
2020-08-17 | 235:52 | 49.887
2020-08-17 | 236:52 | 49.881
2020-08-17 | 237:52 | 49.879
2020-08-17 | 238:52 | 49.874
2020-08-17 | 239:52 | 49.87
2020-08-17 | 240:52 | 49.865
2020-08-17 | 241:52 | 49.862
2020-08-17 | 242:52 | 49.858
2020-08-17 | 243:52 | 49.853
2020-08-17 | 244:52 | 49.848
2020-08-17 | 245:52 | 49.844
2020-08-17 | 246:52 | 49.844
2020-08-17 | 247:52 | 49.842
2020-08-17 | 248:52 | 49.842
2020-08-17 | 249:52 | 49.843
2020-08-17 | 250:52 | 49.843
2020-08-17 | 251:52 | 49.843
2020-08-17 | 252:52 | 49.842
2020-08-17 | 253:52 | 49.838
2020-08-17 | 254:52 | 49.839
2020-08-17 | 255:52 | 49.838
2020-08-17 | 256:52 | 49.839
2020-08-17 | 257:52 | 49.838
2020-08-17 | 258:52 | 49.836
2020-08-17 | 259:52 | 49.834
2020-08-17 | 260:52 | 49.832
2020-08-17 | 261:52 | 49.831
2020-08-17 | 262:52 | 49.83
2020-08-17 | 263:52 | 49.827
2020-08-17 | 264:52 | 49.826
2020-08-17 | 265:52 | 49.828
2020-08-17 | 266:52 | 49.829
2020-08-17 | 267:52 | 49.829
2020-08-17 | 268:52 | 49.83
2020-08-17 | 269:52 | 49.828
2020-08-17 | 270:52 | 49.828
2020-08-17 | 271:52 | 49.828
2020-08-17 | 272:52 | 49.828
2020-08-17 | 273:52 | 49.83
2020-08-17 | 274:52 | 49.831
2020-08-17 | 275:52 | 49.832
2020-08-17 | 276:52 | 49.832
2020-08-17 | 277:52 | 49.832
2020-08-17 | 278:52 | 49.83
2020-08-17 | 279:52 | 49.834
2020-08-17 | 280:52 | 49.839
2020-08-17 | 281:52 | 49.843
2020-08-17 | 282:52 | 49.845
2020-08-17 | 283:52 | 49.85
2020-08-17 | 284:52 | 49.854
2020-08-17 | 285:52 | 49.855
2020-08-17 | 286:52 | 49.853
2020-08-17 | 287:52 | 49.853
2020-08-17 | 288:52 | 49.852
2020-08-17 | 289:52 | 49.851
2020-08-17 | 290:52 | 49.849
2020-08-17 | 291:52 | 49.85
2020-08-17 | 292:52 | 49.851
2020-08-17 | 293:52 | 49.851
2020-08-17 | 294:52 | 49.853
2020-08-17 | 295:52 | 49.854
2020-08-17 | 296:52 | 49.856
2020-08-17 | 297:52 | 49.86
2020-08-17 | 298:52 | 49.86
2020-08-17 | 299:52 | 49.857
2020-08-17 | 300:52 | 49.854
2020-08-17 | 301:52 | 49.852
2020-08-17 | 302:52 | 49.851
2020-08-17 | 303:52 | 49.848
2020-08-17 | 304:52 | 49.847
2020-08-17 | 305:52 | 49.847
2020-08-17 | 306:52 | 49.846
2020-08-17 | 307:52 | 49.845
2020-08-17 | 308:52 | 49.843
2020-08-17 | 309:52 | 49.842
2020-08-17 | 310:52 | 49.84
2020-08-17 | 311:52 | 49.838
2020-08-17 | 312:52 | 49.838
2020-08-17 | 313:52 | 49.838
2020-08-17 | 314:52 | 49.837
2020-08-17 | 315:52 | 49.839
2020-08-17 | 316:52 | 49.84
2020-08-17 | 317:52 | 49.843
2020-08-17 | 318:52 | 49.845
2020-08-17 | 319:52 | 49.844
2020-08-17 | 320:52 | 49.844
2020-08-17 | 321:52 | 49.845
2020-08-17 | 322:52 | 49.845
2020-08-17 | 323:52 | 49.846
2020-08-17 | 324:52 | 49.848
2020-08-17 | 325:52 | 49.852
2020-08-17 | 326:52 | 49.857
2020-08-17 | 327:52 | 49.86
2020-08-17 | 328:52 | 49.861
2020-08-17 | 329:52 | 49.862
2020-08-17 | 330:52 | 49.864
2020-08-17 | 331:52 | 49.864
2020-08-17 | 332:52 | 49.867
2020-08-17 | 333:52 | 49.868
2020-08-17 | 334:52 | 49.87
2020-08-17 | 335:52 | 49.873
2020-08-17 | 336:52 | 49.875
2020-08-17 | 337:52 | 49.875
2020-08-17 | 338:52 | 49.873
2020-08-17 | 339:52 | 49.871
2020-08-17 | 340:52 | 49.87
2020-08-17 | 341:52 | 49.869
2020-08-17 | 342:52 | 49.87
2020-08-17 | 343:52 | 49.867
2020-08-17 | 344:52 | 49.865
2020-08-17 | 345:52 | 49.862
2020-08-17 | 346:52 | 49.861
2020-08-17 | 347:52 | 49.86
2020-08-17 | 348:52 | 49.86
2020-08-17 | 349:52 | 49.861
2020-08-17 | 350:52 | 49.861
2020-08-17 | 351:52 | 49.863
2020-08-17 | 352:52 | 49.864
2020-08-17 | 353:52 | 49.865
2020-08-17 | 354:52 | 49.866
2020-08-17 | 355:52 | 49.866
2020-08-17 | 356:52 | 49.866
2020-08-17 | 357:52 | 49.868
2020-08-17 | 358:52 | 49.867
2020-08-17 | 359:52 | 49.87
2020-08-17 | 360:52 | 49.873
2020-08-17 | 361:52 | 49.872
2020-08-17 | 362:52 | 49.873
2020-08-17 | 363:52 | 49.873
2020-08-17 | 364:52 | 49.874
2020-08-17 | 365:52 | 49.873
2020-08-17 | 366:52 | 49.874
2020-08-17 | 367:52 | 49.874
2020-08-17 | 368:52 | 49.873
2020-08-17 | 369:52 | 49.873
2020-08-17 | 370:52 | 49.872
2020-08-17 | 371:52 | 49.871
2020-08-17 | 372:52 | 49.869
2020-08-17 | 373:52 | 49.869
2020-08-17 | 374:52 | 49.868
2020-08-17 | 375:52 | 49.868
2020-08-17 | 376:52 | 49.866
2020-08-17 | 377:52 | 49.864
2020-08-17 | 378:52 | 49.86
2020-08-17 | 379:52 | 49.861
2020-08-17 | 380:52 | 49.86
2020-08-17 | 381:52 | 49.863
2020-08-17 | 382:52 | 49.866
2020-08-17 | 383:52 | 49.869
2020-08-17 | 384:52 | 49.87
2020-08-17 | 385:52 | 49.871
2020-08-17 | 386:52 | 49.873
2020-08-17 | 387:52 | 49.874
2020-08-17 | 388:52 | 49.876
2020-08-17 | 389:52 | 49.877
2020-08-17 | 390:52 | 49.88
2020-08-17 | 391:52 | 49.88
2020-08-17 | 392:52 | 49.882
2020-08-17 | 393:52 | 49.884
2020-08-17 | 394:52 | 49.885
2020-08-17 | 395:52 | 49.888
2020-08-17 | 396:52 | 49.888
2020-08-17 | 397:52 | 49.893
2020-08-17 | 398:52 | 49.893
2020-08-17 | 399:52 | 49.897
2020-08-17 | 400:52 | 49.9
2020-08-17 | 401:52 | 49.9
2020-08-17 | 402:52 | 49.901
2020-08-17 | 403:52 | 49.901
2020-08-17 | 404:52 | 49.902
2020-08-17 | 405:52 | 49.903
2020-08-17 | 406:52 | 49.905
2020-08-17 | 407:52 | 49.906
2020-08-17 | 408:52 | 49.907
2020-08-17 | 409:52 | 49.908
2020-08-17 | 410:52 | 49.907
2020-08-17 | 411:52 | 49.905
2020-08-17 | 412:52 | 49.903
2020-08-17 | 413:52 | 49.905
2020-08-17 | 414:52 | 49.905
2020-08-17 | 415:52 | 49.907
2020-08-17 | 416:52 | 49.909
2020-08-17 | 417:52 | 49.91
2020-08-17 | 418:52 | 49.91
2020-08-17 | 419:52 | 49.91
2020-08-17 | 420:52 | 49.911
2020-08-17 | 421:52 | 49.911
2020-08-17 | 422:52 | 49.912
2020-08-17 | 423:52 | 49.915
2020-08-17 | 424:52 | 49.915
2020-08-17 | 425:52 | 49.915
2020-08-17 | 426:52 | 49.912
2020-08-17 | 427:52 | 49.91
2020-08-17 | 428:52 | 49.91
2020-08-17 | 429:52 | 49.909
2020-08-17 | 430:52 | 49.912
2020-08-17 | 431:52 | 49.913
2020-08-17 | 432:52 | 49.913
2020-08-17 | 433:52 | 49.915
2020-08-17 | 434:52 | 49.915
2020-08-17 | 435:52 | 49.916
2020-08-17 | 436:52 | 49.921
2020-08-17 | 437:52 | 49.924
2020-08-17 | 438:52 | 49.928
2020-08-17 | 439:52 | 49.933
2020-08-17 | 440:52 | 49.937
2020-08-17 | 441:52 | 49.939
2020-08-17 | 442:52 | 49.941
2020-08-17 | 443:52 | 49.945
2020-08-17 | 444:52 | 49.947
2020-08-17 | 445:52 | 49.95
2020-08-17 | 446:52 | 49.951
2020-08-17 | 447:52 | 49.95
2020-08-17 | 448:52 | 49.949
2020-08-17 | 449:52 | 49.95
2020-08-17 | 450:52 | 49.951
2020-08-17 | 451:52 | 49.952
2020-08-17 | 452:52 | 49.952
2020-08-17 | 453:52 | 49.952
2020-08-17 | 454:52 | 49.952
2020-08-17 | 455:52 | 49.952
2020-08-17 | 456:52 | 49.951
2020-08-17 | 457:52 | 49.951
2020-08-17 | 458:52 | 49.954
2020-08-17 | 459:52 | 49.954
2020-08-17 | 460:52 | 49.954
2020-08-17 | 461:52 | 49.953
2020-08-17 | 462:52 | 49.953
2020-08-17 | 463:52 | 49.954
2020-08-17 | 464:52 | 49.954
2020-08-17 | 465:52 | 49.956
2020-08-17 | 466:52 | 49.961
2020-08-17 | 467:52 | 49.963
2020-08-17 | 468:52 | 49.968
2020-08-17 | 469:52 | 49.971
2020-08-17 | 470:52 | 49.974
2020-08-17 | 471:52 | 49.976
2020-08-17 | 472:52 | 49.976
2020-08-17 | 473:52 | 49.975
2020-08-17 | 474:52 | 49.975
2020-08-17 | 475:52 | 49.974
2020-08-17 | 476:52 | 49.977
2020-08-17 | 477:52 | 49.979
2020-08-17 | 478:52 | 49.982
2020-08-17 | 479:52 | 49.985
2020-08-17 | 480:52 | 49.989
2020-08-17 | 481:52 | 49.993
2020-08-17 | 482:52 | 49.995
2020-08-17 | 483:52 | 49.999
2020-08-17 | 484:52 | 50.004
485:52
486:52
487:52
488:52
489:52
490:52
491:52
492:52
493:52
494:52
495:52
496:52
497:52
498:52
499:52
500:52
501:52
502:52
503:52
504:52
505:52
506:52
507:52
508:52
509:52
510:52
511:52
512:52
513:52
514:52
515:52
516:52
517:52
518:52
519:52
520:52
521:52
522:52
523:52
524:52
525:52
526:52
527:52
528:52
529:52
530:52
531:52
532:52
533:52
534:52
535:52
536:52
537:52
538:52
539:52
540:52
541:52
542:52
543:52
544:52
545:52
546:52
547:52
548:52
549:52
550:52
551:52
552:52
553:52
554:52
555:52
556:52
557:52
558:52
559:52
560:52
561:52
562:52
563:52
564:52
565:52
566:52
567:52
568:52
569:52
570:52
571:52
572:52
573:52
574:52
575:52
576:52
577:52
578:52
579:52
580:52
581:52
582:52
583:52
584:52
585:52
586:52
587:52
588:52
589:52
590:52
591:52
592:52
593:52
594:52
595:52
596:52
597:52
598:52
599:52
600:52
601:52
602:52
603:52
604:52
605:52
606:52
607:52
608:52
609:52
610:52
611:52
612:52
613:52
614:52
615:52
616:52
617:52
618:52
619:52
620:52
621:52
622:52
623:52
624:52
625:52
626:52
627:52
628:52
629:52
630:52
631:52
632:52
633:52
634:52
635:52
636:52
637:52
638:52
639:52
640:52
641:52
642:52
643:52
644:52
645:52
646:52
647:52
648:52
649:52
650:52
651:52
652:52
653:52
654:52
655:52
656:52
657:52
658:52
659:52
660:52
661:52
662:52
663:52
664:52
665:52
666:52
667:52
668:52
669:52
670:52
671:52
672:52
673:52
674:52
675:52
676:52
677:52
678:52
679:52
680:52
681:52
682:52
683:52
684:52
685:52
686:52
687:52
688:52
689:52
690:52
691:52
692:52
693:52
694:52
695:52
696:52
697:52
698:52
699:52
700:52
701:52
702:52
703:52
704:52
705:52
706:52
707:52
708:52
709:52
710:52
711:52
712:52
713:52
714:52
715:52
716:52
717:52
718:52
719:52
720:52
721:52
722:52
723:52
724:52
725:52
726:52
727:52
728:52
729:52
730:52
731:52
732:52
733:52
734:52
735:52
736:52
737:52
738:52
739:52
740:52
741:52
742:52
743:52
744:52
745:52
746:52
747:52
748:52
749:52
750:52
751:52
752:52
753:52
754:52
755:52
756:52
757:52
758:52
759:52
760:52
761:52
762:52
763:52
764:52
765:52
766:52
767:52
768:52
769:52
770:52
771:52
772:52
773:52
774:52
775:52
776:52
777:52
778:52
779:52
780:52
781:52
782:52
783:52
784:52
785:52
786:52
787:52
788:52
789:52
790:52
791:52
792:52
793:52
794:52
795:52
796:52
797:52
798:52
799:52
800:52
801:52
802:52
803:52
804:52
805:52
806:52
807:52
808:52
809:52
810:52
811:52
812:52
813:52
814:52
815:52
816:52
817:52
818:52
819:52
820:52
821:52
822:52
823:52
824:52
825:52
826:52
827:52
828:52
829:52
830:52
831:52
832:52
833:52
834:52
835:52
836:52
837:52
838:52
839:52
840:52
841:52
842:52
843:52
844:52
845:52
846:52
847:52
848:52
849:52
850:52
851:52
852:52
853:52
854:52
855:52
856:52
857:52
858:52
859:52
860:52
861:52
862:52
863:52
864:52
865:52
866:52
867:52
868:52
869:52
870:52
871:52
872:52
873:52
874:52
875:52
876:52
877:52
878:52
879:52
880:52
881:52
882:52
883:52
884:52
885:52
886:52
887:52
888:52
889:52
890:52
891:52
892:52
893:52
894:52
895:52
896:52
897:52
898:52
899:52
900:52
901:52
902:52
903:52
904:52

## Event 20200821-1
In UTC
Date | Time | Freq
2020-08-21 | 6:04 | 49.919
2020-08-21 | 6:04 | 49.92
2020-08-21 | 6:04 | 49.919
2020-08-21 | 6:04 | 49.918
2020-08-21 | 6:04 | 49.92
2020-08-21 | 7:04 | 49.922
2020-08-21 | 8:04 | 49.922
2020-08-21 | 9:04 | 49.921
2020-08-21 | 10:04 | 49.924
2020-08-21 | 11:04 | 49.926
2020-08-21 | 12:04 | 49.927
2020-08-21 | 13:04 | 49.93
2020-08-21 | 14:04 | 49.929
2020-08-21 | 15:04 | 49.933
2020-08-21 | 16:04 | 49.934
2020-08-21 | 17:04 | 49.936
2020-08-21 | 18:04 | 49.939
2020-08-21 | 19:04 | 49.944
2020-08-21 | 20:04 | 49.949
2020-08-21 | 21:04 | 49.952
2020-08-21 | 22:04 | 49.951
2020-08-21 | 23:04 | 49.95
2020-08-21 | 24:04 | 49.95
2020-08-21 | 25:04 | 49.95
2020-08-21 | 26:04 | 49.952
2020-08-21 | 27:04 | 49.973
2020-08-21 | 28:04 | 50.002
2020-08-21 | 29:04 | 50.028
2020-08-21 | 30:04 | 50.05
2020-08-21 | 31:04 | 50.062
2020-08-21 | 32:04 | 50.068
2020-08-21 | 33:04 | 50.073
2020-08-21 | 34:04 | 50.074
2020-08-21 | 35:04 | 50.071
2020-08-21 | 36:04 | 50.069
2020-08-21 | 37:04 | 50.066
2020-08-21 | 38:04 | 50.067
2020-08-21 | 39:04 | 50.061
2020-08-21 | 40:04 | 50.06
2020-08-21 | 41:04 | 50.059
2020-08-21 | 42:04 | 50.056
2020-08-21 | 43:04 | 50.054
2020-08-21 | 44:04 | 50.052
2020-08-21 | 45:04 | 50.05
2020-08-21 | 46:04 | 50.05
2020-08-21 | 47:04 | 50.048
2020-08-21 | 48:04 | 50.048
2020-08-21 | 49:04 | 50.047
2020-08-21 | 50:04 | 50.048
2020-08-21 | 51:04 | 50.046
2020-08-21 | 52:04 | 50.049
2020-08-21 | 53:04 | 50.05
2020-08-21 | 54:04 | 50.051
2020-08-21 | 55:04 | 50.052
2020-08-21 | 56:04 | 50.054
2020-08-21 | 57:04 | 50.059
2020-08-21 | 58:04 | 50.062
2020-08-21 | 59:04 | 50.066
2020-08-21 | 60:04 | 50.069
2020-08-21 | 61:04 | 50.071
2020-08-21 | 62:04 | 50.07
2020-08-21 | 63:04 | 50.07
2020-08-21 | 64:04 | 50.066
2020-08-21 | 65:04 | 50.062
2020-08-21 | 66:04 | 50.056
2020-08-21 | 67:04 | 50.054
2020-08-21 | 68:04 | 50.052
2020-08-21 | 69:04 | 50.048
2020-08-21 | 70:04 | 50.048
2020-08-21 | 71:04 | 50.046
2020-08-21 | 72:04 | 50.045
2020-08-21 | 73:04 | 50.045
2020-08-21 | 74:04 | 50.048
2020-08-21 | 75:04 | 50.05
2020-08-21 | 76:04 | 50.051
2020-08-21 | 77:04 | 50.051
2020-08-21 | 78:04 | 50.054
2020-08-21 | 79:04 | 50.053
2020-08-21 | 80:04 | 50.055
2020-08-21 | 81:04 | 50.057
2020-08-21 | 82:04 | 50.059
2020-08-21 | 83:04 | 50.059
2020-08-21 | 84:04 | 50.062
2020-08-21 | 85:04 | 50.071
2020-08-21 | 86:04 | 50.075
2020-08-21 | 87:04 | 50.075
2020-08-21 | 88:04 | 50.073
2020-08-21 | 89:04 | 50.072
2020-08-21 | 90:04 | 50.069
2020-08-21 | 91:04 | 50.067
2020-08-21 | 92:04 | 50.067
2020-08-21 | 93:04 | 50.065
2020-08-21 | 94:04 | 50.065
2020-08-21 | 95:04 | 50.066
2020-08-21 | 96:04 | 50.065
2020-08-21 | 97:04 | 50.064
2020-08-21 | 98:04 | 50.063
2020-08-21 | 99:04 | 50.065
2020-08-21 | 100:04 | 50.067
2020-08-21 | 101:04 | 50.068
2020-08-21 | 102:04 | 50.067
2020-08-21 | 103:04 | 50.065
2020-08-21 | 104:04 | 50.063
2020-08-21 | 105:04 | 50.064
2020-08-21 | 106:04 | 50.068
2020-08-21 | 107:04 | 50.07
2020-08-21 | 108:04 | 50.069
2020-08-21 | 109:04 | 50.066
2020-08-21 | 110:04 | 50.064
2020-08-21 | 111:04 | 50.062
2020-08-21 | 112:04 | 50.062
2020-08-21 | 113:04 | 50.066
2020-08-21 | 114:04 | 50.067
2020-08-21 | 115:04 | 50.07
2020-08-21 | 116:04 | 50.071
2020-08-21 | 117:04 | 50.073
2020-08-21 | 118:04 | 50.073
2020-08-21 | 119:04 | 50.074
2020-08-21 | 120:04 | 50.073
2020-08-21 | 121:04 | 50.069
2020-08-21 | 122:04 | 50.063
2020-08-21 | 123:04 | 50.056
2020-08-21 | 124:04 | 50.047
2020-08-21 | 125:04 | 50.039
2020-08-21 | 126:04 | 50.033
2020-08-21 | 127:04 | 50.029
2020-08-21 | 128:04 | 50.025
2020-08-21 | 129:04 | 50.023
2020-08-21 | 130:04 | 50.021
2020-08-21 | 131:04 | 50.02
2020-08-21 | 132:04 | 50.02
2020-08-21 | 133:04 | 50.024
2020-08-21 | 134:04 | 50.025
2020-08-21 | 135:04 | 50.029
2020-08-21 | 136:04 | 50.031
2020-08-21 | 137:04 | 50.035
2020-08-21 | 138:04 | 50.034
2020-08-21 | 139:04 | 50.034
2020-08-21 | 140:04 | 50.034
2020-08-21 | 141:04 | 50.031
2020-08-21 | 142:04 | 50.032
2020-08-21 | 143:04 | 50.035
2020-08-21 | 144:04 | 50.037
2020-08-21 | 145:04 | 50.036
2020-08-21 | 146:04 | 50.038
2020-08-21 | 147:04 | 50.038
2020-08-21 | 148:04 | 50.035
2020-08-21 | 149:04 | 50.032
2020-08-21 | 150:04 | 50.03
2020-08-21 | 151:04 | 50.026
2020-08-21 | 152:04 | 50.024
2020-08-21 | 153:04 | 50.021
2020-08-21 | 154:04 | 50.022
2020-08-21 | 155:04 | 50.024
2020-08-21 | 156:04 | 50.028
2020-08-21 | 157:04 | 50.032
2020-08-21 | 158:04 | 50.037
2020-08-21 | 159:04 | 50.042
2020-08-21 | 160:04 | 50.046
2020-08-21 | 161:04 | 50.046
2020-08-21 | 162:04 | 50.046
2020-08-21 | 163:04 | 50.044
2020-08-21 | 164:04 | 50.041
2020-08-21 | 165:04 | 50.042
2020-08-21 | 166:04 | 50.044
2020-08-21 | 167:04 | 50.045
2020-08-21 | 168:04 | 50.05
2020-08-21 | 169:04 | 50.053
2020-08-21 | 170:04 | 50.055
2020-08-21 | 171:04 | 50.054
2020-08-21 | 172:04 | 50.055
2020-08-21 | 173:04 | 50.056
2020-08-21 | 174:04 | 50.059
2020-08-21 | 175:04 | 50.061
2020-08-21 | 176:04 | 50.061
2020-08-21 | 177:04 | 50.06
2020-08-21 | 178:04 | 50.059
2020-08-21 | 179:04 | 50.062
2020-08-21 | 180:04 | 50.06
2020-08-21 | 181:04 | 50.059
2020-08-21 | 182:04 | 50.058
2020-08-21 | 183:04 | 50.057
2020-08-21 | 184:04 | 50.056
2020-08-21 | 185:04 | 50.052
2020-08-21 | 186:04 | 50.051
2020-08-21 | 187:04 | 50.048
2020-08-21 | 188:04 | 50.049
2020-08-21 | 189:04 | 50.05
2020-08-21 | 190:04 | 50.053
2020-08-21 | 191:04 | 50.057
2020-08-21 | 192:04 | 50.062
2020-08-21 | 193:04 | 50.068
2020-08-21 | 194:04 | 50.067
2020-08-21 | 195:04 | 50.064
2020-08-21 | 196:04 | 50.061
2020-08-21 | 197:04 | 50.06
2020-08-21 | 198:04 | 50.059
2020-08-21 | 199:04 | 50.054
2020-08-21 | 200:04 | 50.051
2020-08-21 | 201:04 | 50.052
2020-08-21 | 202:04 | 50.053
2020-08-21 | 203:04 | 50.055
2020-08-21 | 204:04 | 50.053
2020-08-21 | 205:04 | 50.052
2020-08-21 | 206:04 | 50.051
2020-08-21 | 207:04 | 50.051
2020-08-21 | 208:04 | 50.05
2020-08-21 | 209:04 | 50.052
2020-08-21 | 210:04 | 50.053
2020-08-21 | 211:04 | 50.052
2020-08-21 | 212:04 | 50.053
2020-08-21 | 213:04 | 50.059
2020-08-21 | 214:04 | 50.062
2020-08-21 | 215:04 | 50.062
2020-08-21 | 216:04 | 50.06
2020-08-21 | 217:04 | 50.06
2020-08-21 | 218:04 | 50.055
2020-08-21 | 219:04 | 50.054
2020-08-21 | 220:04 | 50.053
2020-08-21 | 221:04 | 50.051
2020-08-21 | 222:04 | 50.048
2020-08-21 | 223:04 | 50.05
2020-08-21 | 224:04 | 50.047
2020-08-21 | 225:04 | 50.048
2020-08-21 | 226:04 | 50.045
2020-08-21 | 227:04 | 50.044
2020-08-21 | 228:04 | 50.041
2020-08-21 | 229:04 | 50.041
2020-08-21 | 230:04 | 50.038
2020-08-21 | 231:04 | 50.036
2020-08-21 | 232:04 | 50.037
2020-08-21 | 233:04 | 50.035
2020-08-21 | 234:04 | 50.038
2020-08-21 | 235:04 | 50.04
2020-08-21 | 236:04 | 50.042
2020-08-21 | 237:04 | 50.045
2020-08-21 | 238:04 | 50.048
2020-08-21 | 239:04 | 50.05
2020-08-21 | 240:04 | 50.05
2020-08-21 | 241:04 | 50.046
2020-08-21 | 242:04 | 50.04
2020-08-21 | 243:04 | 50.034
2020-08-21 | 244:04 | 50.028
2020-08-21 | 245:04 | 50.021
2020-08-21 | 246:04 | 50.018
2020-08-21 | 247:04 | 50.015
2020-08-21 | 248:04 | 50.014
2020-08-21 | 249:04 | 50.015
2020-08-21 | 250:04 | 50.014
2020-08-21 | 251:04 | 50.011
2020-08-21 | 252:04 | 50.008
2020-08-21 | 253:04 | 50.007
2020-08-21 | 254:04 | 50.003
2020-08-21 | 255:04 | 50.001
2020-08-21 | 256:04 | 49.996
2020-08-21 | 257:04 | 49.994
2020-08-21 | 258:04 | 49.993
2020-08-21 | 259:04 | 49.992
2020-08-21 | 260:04 | 49.996
2020-08-21 | 261:04 | 50.001
2020-08-21 | 262:04 | 50.005
2020-08-21 | 263:04 | 50.009
2020-08-21 | 264:04 | 50.015
2020-08-21 | 265:04 | 50.02
2020-08-21 | 266:04 | 50.025
2020-08-21 | 267:04 | 50.031
2020-08-21 | 268:04 | 50.036
2020-08-21 | 269:04 | 50.037
2020-08-21 | 270:04 | 50.039
2020-08-21 | 271:04 | 50.04
2020-08-21 | 272:04 | 50.039
2020-08-21 | 273:04 | 50.036
2020-08-21 | 274:04 | 50.031
2020-08-21 | 275:04 | 50.026
2020-08-21 | 276:04 | 50.022
2020-08-21 | 277:04 | 50.022
2020-08-21 | 278:04 | 50.021
2020-08-21 | 279:04 | 50.022
2020-08-21 | 280:04 | 50.023
2020-08-21 | 281:04 | 50.025
2020-08-21 | 282:04 | 50.025
2020-08-21 | 283:04 | 50.028
2020-08-21 | 284:04 | 50.03
2020-08-21 | 285:04 | 50.03
2020-08-21 | 286:04 | 50.029
2020-08-21 | 287:04 | 50.03
2020-08-21 | 288:04 | 50.031
2020-08-21 | 289:04 | 50.031
2020-08-21 | 290:04 | 50.031
2020-08-21 | 291:04 | 50.031
2020-08-21 | 292:04 | 50.032
2020-08-21 | 293:04 | 50.034
2020-08-21 | 294:04 | 50.034
2020-08-21 | 295:04 | 50.034
2020-08-21 | 296:04 | 50.035
2020-08-21 | 297:04 | 50.036
2020-08-21 | 298:04 | 50.036
2020-08-21 | 299:04 | 50.037
2020-08-21 | 300:04 | 50.035
2020-08-21 | 301:04 | 50.034
302:04
303:04
304:04
305:04
306:04
307:04
308:04
309:04
310:04
311:04
312:04
313:04
314:04
315:04
316:04
317:04
318:04
319:04
320:04
321:04
322:04
323:04
324:04
325:04
326:04
327:04
328:04
329:04
330:04
331:04
332:04
333:04
334:04
335:04
336:04
337:04
338:04
339:04
340:04
341:04
342:04
343:04
344:04
345:04
346:04
347:04
348:04
349:04
350:04
351:04
352:04
353:04
354:04
355:04
356:04
357:04
358:04
359:04
360:04
361:04
362:04
363:04
364:04
365:04
366:04
367:04
368:04
369:04
370:04
371:04
372:04
373:04
374:04
375:04
376:04
377:04
378:04
379:04
380:04
381:04
382:04
383:04
384:04
385:04
386:04
387:04
388:04
389:04
390:04
391:04
392:04
393:04
394:04
395:04
396:04
397:04
398:04
399:04
400:04
401:04
402:04
403:04
404:04
405:04
406:04
407:04
408:04
409:04
410:04
411:04
412:04
413:04
414:04
415:04
416:04
417:04
418:04
419:04
420:04
421:04
422:04
423:04
424:04
425:04
426:04
427:04
428:04
429:04
430:04
431:04
432:04
433:04
434:04
435:04
436:04
437:04
438:04
439:04
440:04
441:04
442:04
443:04
444:04
445:04
446:04
447:04
448:04
449:04
450:04
451:04
452:04
453:04
454:04
455:04
456:04
457:04
458:04
459:04
460:04
461:04
462:04
463:04
464:04
465:04
466:04
467:04
468:04
469:04
470:04
471:04
472:04
473:04
474:04
475:04
476:04
477:04
478:04
479:04
480:04
481:04
482:04
483:04
484:04
485:04
486:04
487:04
488:04
489:04
490:04
491:04
492:04
493:04
494:04
495:04
496:04
497:04
498:04
499:04
500:04
501:04
502:04
503:04
504:04
505:04
506:04
507:04
508:04
509:04
510:04
511:04
512:04
513:04
514:04
515:04
516:04
517:04
518:04
519:04
520:04
521:04
522:04
523:04
524:04
525:04
526:04
527:04
528:04
529:04
530:04
531:04
532:04
533:04
534:04
535:04
536:04
537:04
538:04
539:04
540:04
541:04
542:04
543:04
544:04
545:04
546:04
547:04
548:04
549:04
550:04
551:04
552:04
553:04
554:04
555:04
556:04
557:04
558:04
559:04
560:04
561:04
562:04
563:04
564:04
565:04
566:04
567:04
568:04
569:04
570:04
571:04
572:04
573:04
574:04
575:04
576:04
577:04
578:04
579:04
580:04
581:04
582:04
583:04
584:04
585:04
586:04
587:04
588:04
589:04
590:04
591:04
592:04
593:04
594:04
595:04
596:04
597:04
598:04
599:04
600:04
601:04
602:04
603:04
604:04
605:04
606:04
607:04
608:04
609:04
610:04
611:04
612:04
613:04
614:04
615:04
616:04
617:04
618:04
619:04
620:04
621:04
622:04
623:04
624:04
625:04
626:04
627:04
628:04
629:04
630:04
631:04
632:04
633:04
634:04
635:04
636:04
637:04
638:04
639:04
640:04
641:04
642:04
643:04
644:04
645:04
646:04
647:04
648:04
649:04
650:04
651:04
652:04
653:04
654:04
655:04
656:04
657:04
658:04
659:04
660:04
661:04
662:04
663:04
664:04
665:04
666:04
667:04
668:04
669:04
670:04
671:04
672:04
673:04
674:04
675:04
676:04
677:04
678:04
679:04
680:04
681:04
682:04
683:04
684:04
685:04
686:04
687:04
688:04
689:04
690:04
691:04
692:04
693:04
694:04
695:04
696:04
697:04
698:04
699:04
700:04
701:04
702:04
703:04
704:04
705:04
706:04
707:04
708:04
709:04
710:04
711:04
712:04
713:04
714:04
715:04
716:04
717:04
718:04
719:04
720:04
721:04
722:04
723:04
724:04
725:04
726:04
727:04
728:04
729:04
730:04
731:04
732:04
733:04
734:04
735:04
736:04
737:04
738:04
739:04
740:04
741:04
742:04
743:04
744:04
745:04
746:04
747:04
748:04
749:04
750:04
751:04
752:04
753:04
754:04
755:04
756:04
757:04
758:04
759:04
760:04
761:04
762:04
763:04
764:04
765:04
766:04
767:04
768:04
769:04
770:04
771:04
772:04
773:04
774:04
775:04
776:04
777:04
778:04
779:04
780:04
781:04
782:04
783:04
784:04
785:04
786:04
787:04
788:04
789:04
790:04
791:04
792:04
793:04
794:04
795:04
796:04
797:04
798:04
799:04
800:04
801:04
802:04
803:04
804:04
805:04
806:04
807:04
808:04
809:04
810:04
811:04
812:04
813:04
814:04
815:04
816:04
817:04
818:04
819:04
820:04
821:04
822:04
823:04
824:04
825:04
826:04
827:04
828:04
829:04
830:04
831:04
832:04
833:04
834:04
835:04
836:04
837:04
838:04
839:04
840:04
841:04
842:04
843:04
844:04
845:04
846:04
847:04
848:04
849:04
850:04
851:04
852:04
853:04
854:04
855:04
856:04
857:04
858:04
859:04
860:04
861:04
862:04
863:04
864:04
865:04
866:04
867:04
868:04
869:04
870:04
871:04
872:04
873:04
874:04
875:04
876:04
877:04
878:04
879:04
880:04
881:04
882:04
883:04
884:04
885:04
886:04
887:04
888:04
889:04
890:04
891:04
892:04
893:04
894:04
895:04
896:04
897:04
898:04
899:04
900:04
901:04

## Event 20200822-1
In UTC
Date | Time | Freq
2020-08-22 | 0:32 | 50.077
2020-08-22 | 0:32 | 50.075
2020-08-22 | 0:32 | 50.073
2020-08-22 | 0:32 | 50.074
2020-08-22 | 0:32 | 50.074
2020-08-22 | 1:32 | 50.077
2020-08-22 | 2:32 | 50.077
2020-08-22 | 3:32 | 50.078
2020-08-22 | 4:32 | 50.077
2020-08-22 | 5:32 | 50.076
2020-08-22 | 6:32 | 50.079
2020-08-22 | 7:32 | 50.08
2020-08-22 | 8:32 | 50.081
2020-08-22 | 9:32 | 50.08
2020-08-22 | 10:32 | 50.083
2020-08-22 | 11:32 | 50.086
2020-08-22 | 12:32 | 50.09
2020-08-22 | 13:32 | 50.091
2020-08-22 | 14:32 | 50.091
2020-08-22 | 15:32 | 50.09
2020-08-22 | 16:32 | 50.089
2020-08-22 | 17:32 | 50.086
2020-08-22 | 18:32 | 50.086
2020-08-22 | 19:32 | 50.085
2020-08-22 | 20:32 | 50.085
2020-08-22 | 21:32 | 50.086
2020-08-22 | 22:32 | 50.085
2020-08-22 | 23:32 | 50.084
2020-08-22 | 24:32 | 50.082
2020-08-22 | 25:32 | 50.081
2020-08-22 | 26:32 | 50.079
2020-08-22 | 27:32 | 50.078
2020-08-22 | 28:32 | 50.076
2020-08-22 | 29:32 | 50.076
2020-08-22 | 30:32 | 50.077
2020-08-22 | 31:32 | 50.077
2020-08-22 | 32:32 | 50.078
2020-08-22 | 33:32 | 50.078
2020-08-22 | 34:32 | 50.081
2020-08-22 | 35:32 | 50.081
2020-08-22 | 36:32 | 50.08
2020-08-22 | 37:32 | 50.078
2020-08-22 | 38:32 | 50.079
2020-08-22 | 39:32 | 50.077
2020-08-22 | 40:32 | 50.077
2020-08-22 | 41:32 | 50.079
2020-08-22 | 42:32 | 50.077
2020-08-22 | 43:32 | 50.077
2020-08-22 | 44:32 | 50.077
2020-08-22 | 45:32 | 50.076
2020-08-22 | 46:32 | 50.075
2020-08-22 | 47:32 | 50.075
2020-08-22 | 48:32 | 50.076
2020-08-22 | 49:32 | 50.078
2020-08-22 | 50:32 | 50.077
2020-08-22 | 51:32 | 50.077
2020-08-22 | 52:32 | 50.079
2020-08-22 | 53:32 | 50.08
2020-08-22 | 54:32 | 50.08
2020-08-22 | 55:32 | 50.08
2020-08-22 | 56:32 | 50.079
2020-08-22 | 57:32 | 50.077
2020-08-22 | 58:32 | 50.077
2020-08-22 | 59:32 | 50.077
2020-08-22 | 60:32 | 50.078
2020-08-22 | 61:32 | 50.076
2020-08-22 | 62:32 | 50.079
2020-08-22 | 63:32 | 50.076
2020-08-22 | 64:32 | 50.076
2020-08-22 | 65:32 | 50.074
2020-08-22 | 66:32 | 50.073
2020-08-22 | 67:32 | 50.073
2020-08-22 | 68:32 | 50.073
2020-08-22 | 69:32 | 50.075
2020-08-22 | 70:32 | 50.075
2020-08-22 | 71:32 | 50.073
2020-08-22 | 72:32 | 50.072
2020-08-22 | 73:32 | 50.072
2020-08-22 | 74:32 | 50.073
2020-08-22 | 75:32 | 50.074
2020-08-22 | 76:32 | 50.077
2020-08-22 | 77:32 | 50.077
2020-08-22 | 78:32 | 50.079
2020-08-22 | 79:32 | 50.081
2020-08-22 | 80:32 | 50.084
2020-08-22 | 81:32 | 50.085
2020-08-22 | 82:32 | 50.087
2020-08-22 | 83:32 | 50.088
2020-08-22 | 84:32 | 50.088
2020-08-22 | 85:32 | 50.09
2020-08-22 | 86:32 | 50.092
2020-08-22 | 87:32 | 50.092
2020-08-22 | 88:32 | 50.094
2020-08-22 | 89:32 | 50.096
2020-08-22 | 90:32 | 50.095
2020-08-22 | 91:32 | 50.09
2020-08-22 | 92:32 | 50.008
2020-08-22 | 93:32 | 49.936
2020-08-22 | 94:32 | 49.894
2020-08-22 | 95:32 | 49.875
2020-08-22 | 96:32 | 49.879
2020-08-22 | 97:32 | 49.89
2020-08-22 | 98:32 | 49.901
2020-08-22 | 99:32 | 49.912
2020-08-22 | 100:32 | 49.921
2020-08-22 | 101:32 | 49.927
2020-08-22 | 102:32 | 49.933
2020-08-22 | 103:32 | 49.937
2020-08-22 | 104:32 | 49.939
2020-08-22 | 105:32 | 49.94
2020-08-22 | 106:32 | 49.941
2020-08-22 | 107:32 | 49.941
2020-08-22 | 108:32 | 49.941
2020-08-22 | 109:32 | 49.939
2020-08-22 | 110:32 | 49.935
2020-08-22 | 111:32 | 49.933
2020-08-22 | 112:32 | 49.93
2020-08-22 | 113:32 | 49.931
2020-08-22 | 114:32 | 49.932
2020-08-22 | 115:32 | 49.932
2020-08-22 | 116:32 | 49.932
2020-08-22 | 117:32 | 49.93
2020-08-22 | 118:32 | 49.928
2020-08-22 | 119:32 | 49.925
2020-08-22 | 120:32 | 49.922
2020-08-22 | 121:32 | 49.922
2020-08-22 | 122:32 | 49.921
2020-08-22 | 123:32 | 49.92
2020-08-22 | 124:32 | 49.919
2020-08-22 | 125:32 | 49.918
2020-08-22 | 126:32 | 49.916
2020-08-22 | 127:32 | 49.917
2020-08-22 | 128:32 | 49.916
2020-08-22 | 129:32 | 49.916
2020-08-22 | 130:32 | 49.916
2020-08-22 | 131:32 | 49.917
2020-08-22 | 132:32 | 49.917
2020-08-22 | 133:32 | 49.913
2020-08-22 | 134:32 | 49.912
2020-08-22 | 135:32 | 49.912
2020-08-22 | 136:32 | 49.912
2020-08-22 | 137:32 | 49.914
2020-08-22 | 138:32 | 49.916
2020-08-22 | 139:32 | 49.918
2020-08-22 | 140:32 | 49.92
2020-08-22 | 141:32 | 49.921
2020-08-22 | 142:32 | 49.919
2020-08-22 | 143:32 | 49.919
2020-08-22 | 144:32 | 49.917
2020-08-22 | 145:32 | 49.917
2020-08-22 | 146:32 | 49.918
2020-08-22 | 147:32 | 49.916
2020-08-22 | 148:32 | 49.914
2020-08-22 | 149:32 | 49.914
2020-08-22 | 150:32 | 49.913
2020-08-22 | 151:32 | 49.913
2020-08-22 | 152:32 | 49.914
2020-08-22 | 153:32 | 49.915
2020-08-22 | 154:32 | 49.918
2020-08-22 | 155:32 | 49.918
2020-08-22 | 156:32 | 49.919
2020-08-22 | 157:32 | 49.921
2020-08-22 | 158:32 | 49.921
2020-08-22 | 159:32 | 49.921
2020-08-22 | 160:32 | 49.919
2020-08-22 | 161:32 | 49.917
2020-08-22 | 162:32 | 49.915
2020-08-22 | 163:32 | 49.914
2020-08-22 | 164:32 | 49.914
2020-08-22 | 165:32 | 49.916
2020-08-22 | 166:32 | 49.917
2020-08-22 | 167:32 | 49.918
2020-08-22 | 168:32 | 49.92
2020-08-22 | 169:32 | 49.92
2020-08-22 | 170:32 | 49.919
2020-08-22 | 171:32 | 49.92
2020-08-22 | 172:32 | 49.919
2020-08-22 | 173:32 | 49.918
2020-08-22 | 174:32 | 49.917
2020-08-22 | 175:32 | 49.915
2020-08-22 | 176:32 | 49.914
2020-08-22 | 177:32 | 49.915
2020-08-22 | 178:32 | 49.916
2020-08-22 | 179:32 | 49.917
2020-08-22 | 180:32 | 49.921
2020-08-22 | 181:32 | 49.925
2020-08-22 | 182:32 | 49.926
2020-08-22 | 183:32 | 49.927
2020-08-22 | 184:32 | 49.925
2020-08-22 | 185:32 | 49.927
2020-08-22 | 186:32 | 49.926
2020-08-22 | 187:32 | 49.926
2020-08-22 | 188:32 | 49.926
2020-08-22 | 189:32 | 49.928
2020-08-22 | 190:32 | 49.929
2020-08-22 | 191:32 | 49.932
2020-08-22 | 192:32 | 49.934
2020-08-22 | 193:32 | 49.935
2020-08-22 | 194:32 | 49.937
2020-08-22 | 195:32 | 49.936
2020-08-22 | 196:32 | 49.933
2020-08-22 | 197:32 | 49.927
2020-08-22 | 198:32 | 49.924
2020-08-22 | 199:32 | 49.92
2020-08-22 | 200:32 | 49.918
2020-08-22 | 201:32 | 49.919
2020-08-22 | 202:32 | 49.92
2020-08-22 | 203:32 | 49.919
2020-08-22 | 204:32 | 49.919
2020-08-22 | 205:32 | 49.918
2020-08-22 | 206:32 | 49.919
2020-08-22 | 207:32 | 49.919
2020-08-22 | 208:32 | 49.918
2020-08-22 | 209:32 | 49.919
2020-08-22 | 210:32 | 49.92
2020-08-22 | 211:32 | 49.921
2020-08-22 | 212:32 | 49.92
2020-08-22 | 213:32 | 49.919
2020-08-22 | 214:32 | 49.92
2020-08-22 | 215:32 | 49.921
2020-08-22 | 216:32 | 49.92
2020-08-22 | 217:32 | 49.921
2020-08-22 | 218:32 | 49.921
2020-08-22 | 219:32 | 49.92
2020-08-22 | 220:32 | 49.919
2020-08-22 | 221:32 | 49.919
2020-08-22 | 222:32 | 49.918
2020-08-22 | 223:32 | 49.917
2020-08-22 | 224:32 | 49.916
2020-08-22 | 225:32 | 49.915
2020-08-22 | 226:32 | 49.915
2020-08-22 | 227:32 | 49.915
2020-08-22 | 228:32 | 49.915
2020-08-22 | 229:32 | 49.917
2020-08-22 | 230:32 | 49.917
2020-08-22 | 231:32 | 49.917
2020-08-22 | 232:32 | 49.916
2020-08-22 | 233:32 | 49.917
2020-08-22 | 234:32 | 49.917
2020-08-22 | 235:32 | 49.921
2020-08-22 | 236:32 | 49.92
2020-08-22 | 237:32 | 49.92
2020-08-22 | 238:32 | 49.92
2020-08-22 | 239:32 | 49.92
2020-08-22 | 240:32 | 49.921
2020-08-22 | 241:32 | 49.922
2020-08-22 | 242:32 | 49.923
2020-08-22 | 243:32 | 49.923
2020-08-22 | 244:32 | 49.923
2020-08-22 | 245:32 | 49.923
2020-08-22 | 246:32 | 49.922
2020-08-22 | 247:32 | 49.922
2020-08-22 | 248:32 | 49.921
2020-08-22 | 249:32 | 49.922
2020-08-22 | 250:32 | 49.924
2020-08-22 | 251:32 | 49.924
2020-08-22 | 252:32 | 49.924
2020-08-22 | 253:32 | 49.922
2020-08-22 | 254:32 | 49.922
2020-08-22 | 255:32 | 49.921
2020-08-22 | 256:32 | 49.92
2020-08-22 | 257:32 | 49.921
2020-08-22 | 258:32 | 49.918
2020-08-22 | 259:32 | 49.918
2020-08-22 | 260:32 | 49.917
2020-08-22 | 261:32 | 49.917
2020-08-22 | 262:32 | 49.917
2020-08-22 | 263:32 | 49.917
2020-08-22 | 264:32 | 49.919
2020-08-22 | 265:32 | 49.918
2020-08-22 | 266:32 | 49.918
2020-08-22 | 267:32 | 49.917
2020-08-22 | 268:32 | 49.916
2020-08-22 | 269:32 | 49.916
2020-08-22 | 270:32 | 49.915
2020-08-22 | 271:32 | 49.915
2020-08-22 | 272:32 | 49.914
2020-08-22 | 273:32 | 49.917
2020-08-22 | 274:32 | 49.915
2020-08-22 | 275:32 | 49.915
2020-08-22 | 276:32 | 49.916
2020-08-22 | 277:32 | 49.916
2020-08-22 | 278:32 | 49.915
2020-08-22 | 279:32 | 49.917
2020-08-22 | 280:32 | 49.917
2020-08-22 | 281:32 | 49.918
2020-08-22 | 282:32 | 49.917
2020-08-22 | 283:32 | 49.916
2020-08-22 | 284:32 | 49.913
2020-08-22 | 285:32 | 49.911
2020-08-22 | 286:32 | 49.907
2020-08-22 | 287:32 | 49.907
2020-08-22 | 288:32 | 49.905
2020-08-22 | 289:32 | 49.905
2020-08-22 | 290:32 | 49.905
2020-08-22 | 291:32 | 49.906
2020-08-22 | 292:32 | 49.906
2020-08-22 | 293:32 | 49.907
2020-08-22 | 294:32 | 49.909
2020-08-22 | 295:32 | 49.91
2020-08-22 | 296:32 | 49.911
2020-08-22 | 297:32 | 49.909
2020-08-22 | 298:32 | 49.908
2020-08-22 | 299:32 | 49.908
2020-08-22 | 300:32 | 49.909
2020-08-22 | 301:32 | 49.91
2020-08-22 | 302:32 | 49.912
2020-08-22 | 303:32 | 49.913
2020-08-22 | 304:32 | 49.912
2020-08-22 | 305:32 | 49.911
2020-08-22 | 306:32 | 49.908
2020-08-22 | 307:32 | 49.905
2020-08-22 | 308:32 | 49.903
2020-08-22 | 309:32 | 49.903
2020-08-22 | 310:32 | 49.903
2020-08-22 | 311:32 | 49.901
2020-08-22 | 312:32 | 49.899
2020-08-22 | 313:32 | 49.9
2020-08-22 | 314:32 | 49.899
2020-08-22 | 315:32 | 49.899
2020-08-22 | 316:32 | 49.898
2020-08-22 | 317:32 | 49.897
2020-08-22 | 318:32 | 49.898
2020-08-22 | 319:32 | 49.896
2020-08-22 | 320:32 | 49.896
2020-08-22 | 321:32 | 49.894
2020-08-22 | 322:32 | 49.895
2020-08-22 | 323:32 | 49.894
2020-08-22 | 324:32 | 49.894
2020-08-22 | 325:32 | 49.893
2020-08-22 | 326:32 | 49.894
2020-08-22 | 327:32 | 49.895
2020-08-22 | 328:32 | 49.895
2020-08-22 | 329:32 | 49.895
2020-08-22 | 330:32 | 49.894
2020-08-22 | 331:32 | 49.896
2020-08-22 | 332:32 | 49.895
2020-08-22 | 333:32 | 49.894
2020-08-22 | 334:32 | 49.893
2020-08-22 | 335:32 | 49.893
2020-08-22 | 336:32 | 49.896
2020-08-22 | 337:32 | 49.898
2020-08-22 | 338:32 | 49.899
2020-08-22 | 339:32 | 49.9
2020-08-22 | 340:32 | 49.899
2020-08-22 | 341:32 | 49.9
2020-08-22 | 342:32 | 49.899
2020-08-22 | 343:32 | 49.899
2020-08-22 | 344:32 | 49.897
2020-08-22 | 345:32 | 49.895
2020-08-22 | 346:32 | 49.894
2020-08-22 | 347:32 | 49.894
2020-08-22 | 348:32 | 49.894
2020-08-22 | 349:32 | 49.894
2020-08-22 | 350:32 | 49.895
2020-08-22 | 351:32 | 49.897
2020-08-22 | 352:32 | 49.896
2020-08-22 | 353:32 | 49.895
2020-08-22 | 354:32 | 49.895
2020-08-22 | 355:32 | 49.894
2020-08-22 | 356:32 | 49.892
2020-08-22 | 357:32 | 49.891
2020-08-22 | 358:32 | 49.889
2020-08-22 | 359:32 | 49.888
2020-08-22 | 360:32 | 49.887
2020-08-22 | 361:32 | 49.889
2020-08-22 | 362:32 | 49.891
2020-08-22 | 363:32 | 49.892
2020-08-22 | 364:32 | 49.893
2020-08-22 | 365:32 | 49.892
2020-08-22 | 366:32 | 49.892
2020-08-22 | 367:32 | 49.892
2020-08-22 | 368:32 | 49.892
2020-08-22 | 369:32 | 49.893
2020-08-22 | 370:32 | 49.893
2020-08-22 | 371:32 | 49.893
2020-08-22 | 372:32 | 49.895
2020-08-22 | 373:32 | 49.896
2020-08-22 | 374:32 | 49.897
2020-08-22 | 375:32 | 49.898
2020-08-22 | 376:32 | 49.895
2020-08-22 | 377:32 | 49.893
2020-08-22 | 378:32 | 49.894
2020-08-22 | 379:32 | 49.893
2020-08-22 | 380:32 | 49.893
2020-08-22 | 381:32 | 49.891
2020-08-22 | 382:32 | 49.89
2020-08-22 | 383:32 | 49.889
2020-08-22 | 384:32 | 49.888
2020-08-22 | 385:32 | 49.886
2020-08-22 | 386:32 | 49.887
2020-08-22 | 387:32 | 49.883
2020-08-22 | 388:32 | 49.883
2020-08-22 | 389:32 | 49.885
2020-08-22 | 390:32 | 49.888
2020-08-22 | 391:32 | 49.889
2020-08-22 | 392:32 | 49.892
2020-08-22 | 393:32 | 49.893
2020-08-22 | 394:32 | 49.894
2020-08-22 | 395:32 | 49.897
2020-08-22 | 396:32 | 49.9
2020-08-22 | 397:32 | 49.902
2020-08-22 | 398:32 | 49.901
2020-08-22 | 399:32 | 49.901
2020-08-22 | 400:32 | 49.898
2020-08-22 | 401:32 | 49.896
2020-08-22 | 402:32 | 49.896
2020-08-22 | 403:32 | 49.896
2020-08-22 | 404:32 | 49.897
2020-08-22 | 405:32 | 49.898
2020-08-22 | 406:32 | 49.899
2020-08-22 | 407:32 | 49.897
2020-08-22 | 408:32 | 49.896
2020-08-22 | 409:32 | 49.896
2020-08-22 | 410:32 | 49.895
2020-08-22 | 411:32 | 49.892
2020-08-22 | 412:32 | 49.892
2020-08-22 | 413:32 | 49.891
2020-08-22 | 414:32 | 49.893
2020-08-22 | 415:32 | 49.894
2020-08-22 | 416:32 | 49.894
2020-08-22 | 417:32 | 49.897
2020-08-22 | 418:32 | 49.898
2020-08-22 | 419:32 | 49.899
2020-08-22 | 420:32 | 49.903
2020-08-22 | 421:32 | 49.902
2020-08-22 | 422:32 | 49.9
2020-08-22 | 423:32 | 49.895
2020-08-22 | 424:32 | 49.892
2020-08-22 | 425:32 | 49.891
2020-08-22 | 426:32 | 49.891
2020-08-22 | 427:32 | 49.894
2020-08-22 | 428:32 | 49.892
2020-08-22 | 429:32 | 49.894
2020-08-22 | 430:32 | 49.895
2020-08-22 | 431:32 | 49.895
2020-08-22 | 432:32 | 49.894
2020-08-22 | 433:32 | 49.893
2020-08-22 | 434:32 | 49.893
2020-08-22 | 435:32 | 49.895
2020-08-22 | 436:32 | 49.896
2020-08-22 | 437:32 | 49.899
2020-08-22 | 438:32 | 49.901
2020-08-22 | 439:32 | 49.904
2020-08-22 | 440:32 | 49.903
2020-08-22 | 441:32 | 49.901
2020-08-22 | 442:32 | 49.9
2020-08-22 | 443:32 | 49.902
2020-08-22 | 444:32 | 49.903
2020-08-22 | 445:32 | 49.904
2020-08-22 | 446:32 | 49.906
2020-08-22 | 447:32 | 49.907
2020-08-22 | 448:32 | 49.906
2020-08-22 | 449:32 | 49.906
2020-08-22 | 450:32 | 49.907
2020-08-22 | 451:32 | 49.906
2020-08-22 | 452:32 | 49.907
2020-08-22 | 453:32 | 49.908
2020-08-22 | 454:32 | 49.909
2020-08-22 | 455:32 | 49.91
2020-08-22 | 456:32 | 49.909
2020-08-22 | 457:32 | 49.909
2020-08-22 | 458:32 | 49.906
2020-08-22 | 459:32 | 49.905
2020-08-22 | 460:32 | 49.903
2020-08-22 | 461:32 | 49.902
2020-08-22 | 462:32 | 49.901
2020-08-22 | 463:32 | 49.902
2020-08-22 | 464:32 | 49.901
2020-08-22 | 465:32 | 49.904
2020-08-22 | 466:32 | 49.908
2020-08-22 | 467:32 | 49.911
2020-08-22 | 468:32 | 49.914
2020-08-22 | 469:32 | 49.916
2020-08-22 | 470:32 | 49.917
2020-08-22 | 471:32 | 49.917
2020-08-22 | 472:32 | 49.917
2020-08-22 | 473:32 | 49.918
2020-08-22 | 474:32 | 49.919
2020-08-22 | 475:32 | 49.917
2020-08-22 | 476:32 | 49.916
2020-08-22 | 477:32 | 49.914
2020-08-22 | 478:32 | 49.912
2020-08-22 | 479:32 | 49.911
2020-08-22 | 480:32 | 49.91
2020-08-22 | 481:32 | 49.909
2020-08-22 | 482:32 | 49.907
2020-08-22 | 483:32 | 49.907
2020-08-22 | 484:32 | 49.908
2020-08-22 | 485:32 | 49.911
2020-08-22 | 486:32 | 49.91
2020-08-22 | 487:32 | 49.911
2020-08-22 | 488:32 | 49.909
2020-08-22 | 489:32 | 49.909
2020-08-22 | 490:32 | 49.911
2020-08-22 | 491:32 | 49.913
2020-08-22 | 492:32 | 49.914
2020-08-22 | 493:32 | 49.92
2020-08-22 | 494:32 | 49.93
2020-08-22 | 495:32 | 49.94
2020-08-22 | 496:32 | 49.945
2020-08-22 | 497:32 | 49.948
2020-08-22 | 498:32 | 49.946
2020-08-22 | 499:32 | 49.947
2020-08-22 | 500:32 | 49.949
2020-08-22 | 501:32 | 49.948
2020-08-22 | 502:32 | 49.947
2020-08-22 | 503:32 | 49.945
2020-08-22 | 504:32 | 49.942
2020-08-22 | 505:32 | 49.942
2020-08-22 | 506:32 | 49.942
2020-08-22 | 507:32 | 49.942
2020-08-22 | 508:32 | 49.942
2020-08-22 | 509:32 | 49.942
2020-08-22 | 510:32 | 49.941
2020-08-22 | 511:32 | 49.939
2020-08-22 | 512:32 | 49.939
2020-08-22 | 513:32 | 49.938
2020-08-22 | 514:32 | 49.938
2020-08-22 | 515:32 | 49.942
2020-08-22 | 516:32 | 49.943
2020-08-22 | 517:32 | 49.944
2020-08-22 | 518:32 | 49.946
2020-08-22 | 519:32 | 49.948
2020-08-22 | 520:32 | 49.948
2020-08-22 | 521:32 | 49.949
2020-08-22 | 522:32 | 49.951
2020-08-22 | 523:32 | 49.95
2020-08-22 | 524:32 | 49.949
2020-08-22 | 525:32 | 49.951
2020-08-22 | 526:32 | 49.949
2020-08-22 | 527:32 | 49.95
2020-08-22 | 528:32 | 49.95
2020-08-22 | 529:32 | 49.952
2020-08-22 | 530:32 | 49.953
2020-08-22 | 531:32 | 49.955
2020-08-22 | 532:32 | 49.956
2020-08-22 | 533:32 | 49.957
2020-08-22 | 534:32 | 49.96
2020-08-22 | 535:32 | 49.962
2020-08-22 | 536:32 | 49.961
2020-08-22 | 537:32 | 49.96
2020-08-22 | 538:32 | 49.959
2020-08-22 | 539:32 | 49.958
2020-08-22 | 540:32 | 49.958
2020-08-22 | 541:32 | 49.961
2020-08-22 | 542:32 | 49.964
2020-08-22 | 543:32 | 49.966
2020-08-22 | 544:32 | 49.967
2020-08-22 | 545:32 | 49.967
2020-08-22 | 546:32 | 49.97
2020-08-22 | 547:32 | 49.97
2020-08-22 | 548:32 | 49.97
2020-08-22 | 549:32 | 49.97
2020-08-22 | 550:32 | 49.968
2020-08-22 | 551:32 | 49.96
2020-08-22 | 552:32 | 49.951
2020-08-22 | 553:32 | 49.943
2020-08-22 | 554:32 | 49.938
2020-08-22 | 555:32 | 49.935
2020-08-22 | 556:32 | 49.932
2020-08-22 | 557:32 | 49.932
2020-08-22 | 558:32 | 49.935
2020-08-22 | 559:32 | 49.938
2020-08-22 | 560:32 | 49.941
2020-08-22 | 561:32 | 49.941
2020-08-22 | 562:32 | 49.943
2020-08-22 | 563:32 | 49.941
2020-08-22 | 564:32 | 49.941
2020-08-22 | 565:32 | 49.94
2020-08-22 | 566:32 | 49.94
2020-08-22 | 567:32 | 49.938
2020-08-22 | 568:32 | 49.939
2020-08-22 | 569:32 | 49.941
2020-08-22 | 570:32 | 49.944
2020-08-22 | 571:32 | 49.946
2020-08-22 | 572:32 | 49.948
2020-08-22 | 573:32 | 49.945
2020-08-22 | 574:32 | 49.942
2020-08-22 | 575:32 | 49.941
2020-08-22 | 576:32 | 49.941
2020-08-22 | 577:32 | 49.939
2020-08-22 | 578:32 | 49.938
2020-08-22 | 579:32 | 49.934
2020-08-22 | 580:32 | 49.932
2020-08-22 | 581:32 | 49.93
2020-08-22 | 582:32 | 49.928
2020-08-22 | 583:32 | 49.929
2020-08-22 | 584:32 | 49.931
2020-08-22 | 585:32 | 49.931
2020-08-22 | 586:32 | 49.933
2020-08-22 | 587:32 | 49.934
2020-08-22 | 588:32 | 49.936
2020-08-22 | 589:32 | 49.938
2020-08-22 | 590:32 | 49.938
2020-08-22 | 591:32 | 49.94
2020-08-22 | 592:32 | 49.94
2020-08-22 | 593:32 | 49.94
2020-08-22 | 594:32 | 49.94
2020-08-22 | 595:32 | 49.939
2020-08-22 | 596:32 | 49.938
2020-08-22 | 597:32 | 49.938
2020-08-22 | 598:32 | 49.938
2020-08-22 | 599:32 | 49.939
2020-08-22 | 600:32 | 49.939
2020-08-22 | 601:32 | 49.938
2020-08-22 | 602:32 | 49.937
2020-08-22 | 603:32 | 49.936
2020-08-22 | 604:32 | 49.938
2020-08-22 | 605:32 | 49.941
2020-08-22 | 606:32 | 49.939
2020-08-22 | 607:32 | 49.939
2020-08-22 | 608:32 | 49.941
2020-08-22 | 609:32 | 49.943
2020-08-22 | 610:32 | 49.944
2020-08-22 | 611:32 | 49.944
2020-08-22 | 612:32 | 49.944
2020-08-22 | 613:32 | 49.943
2020-08-22 | 614:32 | 49.942
2020-08-22 | 615:32 | 49.943
2020-08-22 | 616:32 | 49.942
2020-08-22 | 617:32 | 49.943
2020-08-22 | 618:32 | 49.944
2020-08-22 | 619:32 | 49.945
2020-08-22 | 620:32 | 49.947
2020-08-22 | 621:32 | 49.948
2020-08-22 | 622:32 | 49.947
2020-08-22 | 623:32 | 49.948
2020-08-22 | 624:32 | 49.947
2020-08-22 | 625:32 | 49.947
2020-08-22 | 626:32 | 49.947
2020-08-22 | 627:32 | 49.948
2020-08-22 | 628:32 | 49.948
2020-08-22 | 629:32 | 49.948
2020-08-22 | 630:32 | 49.946
2020-08-22 | 631:32 | 49.945
2020-08-22 | 632:32 | 49.943
2020-08-22 | 633:32 | 49.943
2020-08-22 | 634:32 | 49.941
2020-08-22 | 635:32 | 49.939
2020-08-22 | 636:32 | 49.937
2020-08-22 | 637:32 | 49.936
2020-08-22 | 638:32 | 49.935
2020-08-22 | 639:32 | 49.933
2020-08-22 | 640:32 | 49.933
2020-08-22 | 641:32 | 49.932
2020-08-22 | 642:32 | 49.929
2020-08-22 | 643:32 | 49.928
2020-08-22 | 644:32 | 49.925
2020-08-22 | 645:32 | 49.922
2020-08-22 | 646:32 | 49.922
2020-08-22 | 647:32 | 49.921
2020-08-22 | 648:32 | 49.921
2020-08-22 | 649:32 | 49.92
2020-08-22 | 650:32 | 49.921
2020-08-22 | 651:32 | 49.922
2020-08-22 | 652:32 | 49.92
2020-08-22 | 653:32 | 49.919
2020-08-22 | 654:32 | 49.918
2020-08-22 | 655:32 | 49.918
2020-08-22 | 656:32 | 49.918
2020-08-22 | 657:32 | 49.917
2020-08-22 | 658:32 | 49.917
2020-08-22 | 659:32 | 49.916
2020-08-22 | 660:32 | 49.916
2020-08-22 | 661:32 | 49.916
2020-08-22 | 662:32 | 49.916
2020-08-22 | 663:32 | 49.915
2020-08-22 | 664:32 | 49.916
2020-08-22 | 665:32 | 49.917
2020-08-22 | 666:32 | 49.92
2020-08-22 | 667:32 | 49.929
2020-08-22 | 668:32 | 49.937
2020-08-22 | 669:32 | 49.942
2020-08-22 | 670:32 | 49.945
2020-08-22 | 671:32 | 49.947
2020-08-22 | 672:32 | 49.946
2020-08-22 | 673:32 | 49.946
2020-08-22 | 674:32 | 49.945
2020-08-22 | 675:32 | 49.944
2020-08-22 | 676:32 | 49.942
2020-08-22 | 677:32 | 49.941
2020-08-22 | 678:32 | 49.938
2020-08-22 | 679:32 | 49.936
2020-08-22 | 680:32 | 49.933
2020-08-22 | 681:32 | 49.932
2020-08-22 | 682:32 | 49.929
2020-08-22 | 683:32 | 49.927
2020-08-22 | 684:32 | 49.926
2020-08-22 | 685:32 | 49.926
2020-08-22 | 686:32 | 49.926
2020-08-22 | 687:32 | 49.926
2020-08-22 | 688:32 | 49.927
2020-08-22 | 689:32 | 49.928
2020-08-22 | 690:32 | 49.93
2020-08-22 | 691:32 | 49.932
2020-08-22 | 692:32 | 49.932
2020-08-22 | 693:32 | 49.933
2020-08-22 | 694:32 | 49.935
2020-08-22 | 695:32 | 49.936
2020-08-22 | 696:32 | 49.937
2020-08-22 | 697:32 | 49.938
2020-08-22 | 698:32 | 49.938
2020-08-22 | 699:32 | 49.937
2020-08-22 | 700:32 | 49.938
2020-08-22 | 701:32 | 49.937
2020-08-22 | 702:32 | 49.938
2020-08-22 | 703:32 | 49.937
2020-08-22 | 704:32 | 49.937
2020-08-22 | 705:32 | 49.938
2020-08-22 | 706:32 | 49.937
2020-08-22 | 707:32 | 49.938
2020-08-22 | 708:32 | 49.938
2020-08-22 | 709:32 | 49.939
2020-08-22 | 710:32 | 49.939
2020-08-22 | 711:32 | 49.937
2020-08-22 | 712:32 | 49.938
2020-08-22 | 713:32 | 49.936
2020-08-22 | 714:32 | 49.935
2020-08-22 | 715:32 | 49.934
2020-08-22 | 716:32 | 49.934
2020-08-22 | 717:32 | 49.935
2020-08-22 | 718:32 | 49.933
2020-08-22 | 719:32 | 49.933
2020-08-22 | 720:32 | 49.933
2020-08-22 | 721:32 | 49.933
2020-08-22 | 722:32 | 49.932
2020-08-22 | 723:32 | 49.932
2020-08-22 | 724:32 | 49.933
2020-08-22 | 725:32 | 49.933
2020-08-22 | 726:32 | 49.932
2020-08-22 | 727:32 | 49.929
2020-08-22 | 728:32 | 49.928
2020-08-22 | 729:32 | 49.927
2020-08-22 | 730:32 | 49.929
2020-08-22 | 731:32 | 49.931
2020-08-22 | 732:32 | 49.933
2020-08-22 | 733:32 | 49.934
2020-08-22 | 734:32 | 49.935
2020-08-22 | 735:32 | 49.939
2020-08-22 | 736:32 | 49.94
2020-08-22 | 737:32 | 49.941
2020-08-22 | 738:32 | 49.943
2020-08-22 | 739:32 | 49.946
2020-08-22 | 740:32 | 49.948
2020-08-22 | 741:32 | 49.951
2020-08-22 | 742:32 | 49.957
2020-08-22 | 743:32 | 49.96
2020-08-22 | 744:32 | 49.965
2020-08-22 | 745:32 | 49.973
2020-08-22 | 746:32 | 49.98
2020-08-22 | 747:32 | 49.989
2020-08-22 | 748:32 | 49.998
2020-08-22 | 749:32 | 50.005
2020-08-22 | 750:32 | 50.013
2020-08-22 | 751:32 | 50.02
2020-08-22 | 752:32 | 50.024
2020-08-22 | 753:32 | 50.025
2020-08-22 | 754:32 | 50.027
2020-08-22 | 755:32 | 50.029
2020-08-22 | 756:32 | 50.033
2020-08-22 | 757:32 | 50.035
2020-08-22 | 758:32 | 50.035
2020-08-22 | 759:32 | 50.033
2020-08-22 | 760:32 | 50.033
2020-08-22 | 761:32 | 50.031
2020-08-22 | 762:32 | 50.029
2020-08-22 | 763:32 | 50.029
2020-08-22 | 764:32 | 50.027
2020-08-22 | 765:32 | 50.029
2020-08-22 | 766:32 | 50.029
2020-08-22 | 767:32 | 50.027
2020-08-22 | 768:32 | 50.025
2020-08-22 | 769:32 | 50.024
2020-08-22 | 770:32 | 50.024
2020-08-22 | 771:32 | 50.023
2020-08-22 | 772:32 | 50.025
2020-08-22 | 773:32 | 50.025
2020-08-22 | 774:32 | 50.026
2020-08-22 | 775:32 | 50.025
776:32
777:32
778:32
779:32
780:32
781:32
782:32
783:32
784:32
785:32
786:32
787:32
788:32
789:32
790:32
791:32
792:32
793:32
794:32
795:32
796:32
797:32
798:32
799:32
800:32
801:32
802:32
803:32
804:32
805:32
806:32
807:32
808:32
809:32
810:32
811:32
812:32
813:32
814:32
815:32
816:32
817:32
818:32
819:32
820:32
821:32
822:32
823:32
824:32
825:32
826:32
827:32
828:32
829:32
830:32
831:32
832:32
833:32
834:32
835:32
836:32
837:32
838:32
839:32
840:32
841:32
842:32
843:32
844:32
845:32
846:32
847:32
848:32
849:32
850:32
851:32
852:32
853:32
854:32
855:32
856:32
857:32
858:32
859:32
860:32
861:32
862:32
863:32
864:32
865:32
866:32
867:32
868:32
869:32
870:32
871:32
872:32
873:32
874:32
875:32
876:32
877:32
878:32
879:32
880:32
881:32
882:32
883:32
884:32
885:32
886:32
887:32
888:32
889:32
890:32
891:32
892:32
893:32
894:32
895:32

## Event 20200822-2
In UTC
Date | Time | Freq
2020-08-22 | 19:56 | 50.038
2020-08-22 | 19:56 | 50.035
2020-08-22 | 19:56 | 50.03
2020-08-22 | 19:56 | 50.027
2020-08-22 | 19:56 | 50.023
2020-08-22 | 20:56 | 50.02
2020-08-22 | 21:56 | 50.018
2020-08-22 | 22:56 | 50.017
2020-08-22 | 23:56 | 50.016
2020-08-22 | 24:56 | 50.015
2020-08-22 | 25:56 | 50.016
2020-08-22 | 26:56 | 50.018
2020-08-22 | 27:56 | 50.019
2020-08-22 | 28:56 | 50.021
2020-08-22 | 29:56 | 50.022
2020-08-22 | 30:56 | 50.023
2020-08-22 | 31:56 | 50.023
2020-08-22 | 32:56 | 50.023
2020-08-22 | 33:56 | 50.025
2020-08-22 | 34:56 | 50.025
2020-08-22 | 35:56 | 50.025
2020-08-22 | 36:56 | 50.025
2020-08-22 | 37:56 | 50.024
2020-08-22 | 38:56 | 50.02
2020-08-22 | 39:56 | 50.021
2020-08-22 | 40:56 | 50.021
2020-08-22 | 41:56 | 50.021
2020-08-22 | 42:56 | 50.021
2020-08-22 | 43:56 | 50.021
2020-08-22 | 44:56 | 50.02
2020-08-22 | 45:56 | 50.02
2020-08-22 | 46:56 | 50.019
2020-08-22 | 47:56 | 50.02
2020-08-22 | 48:56 | 50.021
2020-08-22 | 49:56 | 50.025
2020-08-22 | 50:56 | 50.027
2020-08-22 | 51:56 | 50.028
2020-08-22 | 52:56 | 50.031
2020-08-22 | 53:56 | 50.032
2020-08-22 | 54:56 | 50.031
2020-08-22 | 55:56 | 50.029
2020-08-22 | 56:56 | 50.027
2020-08-22 | 57:56 | 50.027
2020-08-22 | 58:56 | 50.027
2020-08-22 | 59:56 | 50.026
2020-08-22 | 60:56 | 50.025
2020-08-22 | 61:56 | 50.024
2020-08-22 | 62:56 | 50.022
2020-08-22 | 63:56 | 50.02
2020-08-22 | 64:56 | 50.018
2020-08-22 | 65:56 | 50.016
2020-08-22 | 66:56 | 50.014
2020-08-22 | 67:56 | 50.013
2020-08-22 | 68:56 | 50.014
2020-08-22 | 69:56 | 50.016
2020-08-22 | 70:56 | 50.015
2020-08-22 | 71:56 | 50.014
2020-08-22 | 72:56 | 50.014
2020-08-22 | 73:56 | 50.013
2020-08-22 | 74:56 | 50.011
2020-08-22 | 75:56 | 50.009
2020-08-22 | 76:56 | 50.008
2020-08-22 | 77:56 | 50.008
2020-08-22 | 78:56 | 50.011
2020-08-22 | 79:56 | 50.016
2020-08-22 | 80:56 | 50.02
2020-08-22 | 81:56 | 50.022
2020-08-22 | 82:56 | 50.022
2020-08-22 | 83:56 | 50.02
2020-08-22 | 84:56 | 50.021
2020-08-22 | 85:56 | 50.02
2020-08-22 | 86:56 | 50.021
2020-08-22 | 87:56 | 50.023
2020-08-22 | 88:56 | 50.027
2020-08-22 | 89:56 | 50.031
2020-08-22 | 90:56 | 50.032
2020-08-22 | 91:56 | 50.034
2020-08-22 | 92:56 | 50.036
2020-08-22 | 93:56 | 50.037
2020-08-22 | 94:56 | 50.035
2020-08-22 | 95:56 | 50.035
2020-08-22 | 96:56 | 50.034
2020-08-22 | 97:56 | 50.033
2020-08-22 | 98:56 | 50.033
2020-08-22 | 99:56 | 50.033
2020-08-22 | 100:56 | 50.033
2020-08-22 | 101:56 | 50.032
2020-08-22 | 102:56 | 50.032
2020-08-22 | 103:56 | 50.035
2020-08-22 | 104:56 | 50.034
2020-08-22 | 105:56 | 50.033
2020-08-22 | 106:56 | 50.031
2020-08-22 | 107:56 | 50.029
2020-08-22 | 108:56 | 50.026
2020-08-22 | 109:56 | 50.024
2020-08-22 | 110:56 | 50.025
2020-08-22 | 111:56 | 50.027
2020-08-22 | 112:56 | 50.029
2020-08-22 | 113:56 | 50.032
2020-08-22 | 114:56 | 50.036
2020-08-22 | 115:56 | 50.039
2020-08-22 | 116:56 | 50.04
2020-08-22 | 117:56 | 50.04
2020-08-22 | 118:56 | 50.04
2020-08-22 | 119:56 | 50.041
2020-08-22 | 120:56 | 50.043
2020-08-22 | 121:56 | 50.044
2020-08-22 | 122:56 | 50.044
2020-08-22 | 123:56 | 50.043
2020-08-22 | 124:56 | 50.045
2020-08-22 | 125:56 | 50.045
2020-08-22 | 126:56 | 50.046
2020-08-22 | 127:56 | 50.046
2020-08-22 | 128:56 | 50.045
2020-08-22 | 129:56 | 50.042
2020-08-22 | 130:56 | 50.042
2020-08-22 | 131:56 | 50.042
2020-08-22 | 132:56 | 50.041
2020-08-22 | 133:56 | 50.039
2020-08-22 | 134:56 | 50.039
2020-08-22 | 135:56 | 50.039
2020-08-22 | 136:56 | 50.039
2020-08-22 | 137:56 | 50.041
2020-08-22 | 138:56 | 50.042
2020-08-22 | 139:56 | 50.045
2020-08-22 | 140:56 | 50.049
2020-08-22 | 141:56 | 50.052
2020-08-22 | 142:56 | 50.054
2020-08-22 | 143:56 | 50.053
2020-08-22 | 144:56 | 50.051
2020-08-22 | 145:56 | 50.047
2020-08-22 | 146:56 | 50.042
2020-08-22 | 147:56 | 50.037
2020-08-22 | 148:56 | 50.033
2020-08-22 | 149:56 | 50.03
2020-08-22 | 150:56 | 50.028
2020-08-22 | 151:56 | 50.027
2020-08-22 | 152:56 | 50.027
2020-08-22 | 153:56 | 50.027
2020-08-22 | 154:56 | 50.028
2020-08-22 | 155:56 | 50.032
2020-08-22 | 156:56 | 50.036
2020-08-22 | 157:56 | 50.04
2020-08-22 | 158:56 | 50.042
2020-08-22 | 159:56 | 50.041
2020-08-22 | 160:56 | 50.041
2020-08-22 | 161:56 | 50.04
2020-08-22 | 162:56 | 50.038
2020-08-22 | 163:56 | 50.037
2020-08-22 | 164:56 | 50.035
2020-08-22 | 165:56 | 50.031
2020-08-22 | 166:56 | 50.028
2020-08-22 | 167:56 | 50.026
2020-08-22 | 168:56 | 50.026
2020-08-22 | 169:56 | 50.024
2020-08-22 | 170:56 | 50.022
2020-08-22 | 171:56 | 50.019
2020-08-22 | 172:56 | 50.017
2020-08-22 | 173:56 | 50.015
2020-08-22 | 174:56 | 50.015
2020-08-22 | 175:56 | 50.015
2020-08-22 | 176:56 | 50.015
2020-08-22 | 177:56 | 50.015
2020-08-22 | 178:56 | 50.019
2020-08-22 | 179:56 | 50.022
2020-08-22 | 180:56 | 50.024
2020-08-22 | 181:56 | 50.025
2020-08-22 | 182:56 | 50.025
2020-08-22 | 183:56 | 50.025
2020-08-22 | 184:56 | 50.026
2020-08-22 | 185:56 | 50.025
2020-08-22 | 186:56 | 50.024
2020-08-22 | 187:56 | 50.023
2020-08-22 | 188:56 | 50.021
2020-08-22 | 189:56 | 50.018
2020-08-22 | 190:56 | 50.018
2020-08-22 | 191:56 | 50.018
2020-08-22 | 192:56 | 50.019
2020-08-22 | 193:56 | 50.021
2020-08-22 | 194:56 | 50.023
2020-08-22 | 195:56 | 50.024
2020-08-22 | 196:56 | 50.026
2020-08-22 | 197:56 | 50.028
2020-08-22 | 198:56 | 50.031
2020-08-22 | 199:56 | 50.033
2020-08-22 | 200:56 | 50.034
2020-08-22 | 201:56 | 50.037
2020-08-22 | 202:56 | 50.04
2020-08-22 | 203:56 | 50.043
2020-08-22 | 204:56 | 50.047
2020-08-22 | 205:56 | 50.05
2020-08-22 | 206:56 | 50.052
2020-08-22 | 207:56 | 50.053
2020-08-22 | 208:56 | 50.052
2020-08-22 | 209:56 | 50.051
2020-08-22 | 210:56 | 50.053
2020-08-22 | 211:56 | 50.055
2020-08-22 | 212:56 | 50.056
2020-08-22 | 213:56 | 50.057
2020-08-22 | 214:56 | 50.059
2020-08-22 | 215:56 | 50.058
2020-08-22 | 216:56 | 50.057
2020-08-22 | 217:56 | 50.057
2020-08-22 | 218:56 | 50.058
2020-08-22 | 219:56 | 50.057
2020-08-22 | 220:56 | 50.055
2020-08-22 | 221:56 | 50.055
2020-08-22 | 222:56 | 50.056
2020-08-22 | 223:56 | 50.057
2020-08-22 | 224:56 | 50.058
2020-08-22 | 225:56 | 50.059
2020-08-22 | 226:56 | 50.058
2020-08-22 | 227:56 | 50.058
2020-08-22 | 228:56 | 50.057
2020-08-22 | 229:56 | 50.055
2020-08-22 | 230:56 | 50.053
2020-08-22 | 231:56 | 50.054
2020-08-22 | 232:56 | 50.053
2020-08-22 | 233:56 | 50.055
2020-08-22 | 234:56 | 50.056
2020-08-22 | 235:56 | 50.056
2020-08-22 | 236:56 | 50.056
2020-08-22 | 237:56 | 50.054
2020-08-22 | 238:56 | 50.052
2020-08-22 | 239:56 | 50.05
2020-08-22 | 240:56 | 50.046
2020-08-22 | 241:56 | 50.04
2020-08-22 | 242:56 | 50.034
2020-08-22 | 243:56 | 50.029
2020-08-22 | 244:56 | 50.027
2020-08-22 | 245:56 | 50.025
2020-08-22 | 246:56 | 50.025
2020-08-22 | 247:56 | 50.027
2020-08-22 | 248:56 | 50.028
2020-08-22 | 249:56 | 50.027
2020-08-22 | 250:56 | 50.026
2020-08-22 | 251:56 | 50.024
2020-08-22 | 252:56 | 50.023
2020-08-22 | 253:56 | 50.023
2020-08-22 | 254:56 | 50.024
2020-08-22 | 255:56 | 50.023
2020-08-22 | 256:56 | 50.021
2020-08-22 | 257:56 | 50.019
2020-08-22 | 258:56 | 50.017
2020-08-22 | 259:56 | 50.018
2020-08-22 | 260:56 | 50.018
2020-08-22 | 261:56 | 50.017
2020-08-22 | 262:56 | 50.017
2020-08-22 | 263:56 | 50.019
2020-08-22 | 264:56 | 50.021
2020-08-22 | 265:56 | 50.022
2020-08-22 | 266:56 | 50.022
2020-08-22 | 267:56 | 50.021
2020-08-22 | 268:56 | 50.019
2020-08-22 | 269:56 | 50.016
2020-08-22 | 270:56 | 50.013
2020-08-22 | 271:56 | 50.012
2020-08-22 | 272:56 | 50.013
2020-08-22 | 273:56 | 50.012
2020-08-22 | 274:56 | 50.014
2020-08-22 | 275:56 | 50.011
2020-08-22 | 276:56 | 50.012
2020-08-22 | 277:56 | 50.014
2020-08-22 | 278:56 | 50.013
2020-08-22 | 279:56 | 50.014
2020-08-22 | 280:56 | 50.015
2020-08-22 | 281:56 | 50.017
2020-08-22 | 282:56 | 50.018
2020-08-22 | 283:56 | 50.02
2020-08-22 | 284:56 | 50.018
2020-08-22 | 285:56 | 50.018
2020-08-22 | 286:56 | 50.017
2020-08-22 | 287:56 | 50.018
2020-08-22 | 288:56 | 50.019
2020-08-22 | 289:56 | 50.022
2020-08-22 | 290:56 | 50.025
2020-08-22 | 291:56 | 50.029
2020-08-22 | 292:56 | 50.032
2020-08-22 | 293:56 | 50.034
2020-08-22 | 294:56 | 50.034
2020-08-22 | 295:56 | 50.034
2020-08-22 | 296:56 | 50.035
2020-08-22 | 297:56 | 50.034
2020-08-22 | 298:56 | 50.033
2020-08-22 | 299:56 | 50.029
2020-08-22 | 300:56 | 50.027
2020-08-22 | 301:56 | 50.027
2020-08-22 | 302:56 | 50.027
2020-08-22 | 303:56 | 50.027
2020-08-22 | 304:56 | 50.027
2020-08-22 | 305:56 | 50.026
2020-08-22 | 306:56 | 50.025
2020-08-22 | 307:56 | 50.025
2020-08-22 | 308:56 | 50.025
2020-08-22 | 309:56 | 50.023
2020-08-22 | 310:56 | 50.021
2020-08-22 | 311:56 | 50.018
2020-08-22 | 312:56 | 50.015
2020-08-22 | 313:56 | 50.011
2020-08-22 | 314:56 | 50.011
2020-08-22 | 315:56 | 50.011
2020-08-22 | 316:56 | 50.012
2020-08-22 | 317:56 | 50.013
2020-08-22 | 318:56 | 50.013
2020-08-22 | 319:56 | 50.014
2020-08-22 | 320:56 | 50.014
2020-08-22 | 321:56 | 50.013
2020-08-22 | 322:56 | 50.011
2020-08-22 | 323:56 | 50.009
2020-08-22 | 324:56 | 50.006
2020-08-22 | 325:56 | 50.002
2020-08-22 | 326:56 | 49.997
2020-08-22 | 327:56 | 49.994
2020-08-22 | 328:56 | 49.991
2020-08-22 | 329:56 | 49.99
2020-08-22 | 330:56 | 49.987
2020-08-22 | 331:56 | 49.982
2020-08-22 | 332:56 | 49.981
2020-08-22 | 333:56 | 49.982
2020-08-22 | 334:56 | 49.98
2020-08-22 | 335:56 | 49.979
2020-08-22 | 336:56 | 49.976
2020-08-22 | 337:56 | 49.972
2020-08-22 | 338:56 | 49.97
2020-08-22 | 339:56 | 49.967
2020-08-22 | 340:56 | 49.965
2020-08-22 | 341:56 | 49.962
2020-08-22 | 342:56 | 49.962
2020-08-22 | 343:56 | 49.964
2020-08-22 | 344:56 | 49.966
2020-08-22 | 345:56 | 49.97
2020-08-22 | 346:56 | 49.976
2020-08-22 | 347:56 | 49.982
2020-08-22 | 348:56 | 49.986
2020-08-22 | 349:56 | 49.99
2020-08-22 | 350:56 | 49.992
2020-08-22 | 351:56 | 49.994
2020-08-22 | 352:56 | 49.996
2020-08-22 | 353:56 | 49.997
2020-08-22 | 354:56 | 49.996
2020-08-22 | 355:56 | 49.996
2020-08-22 | 356:56 | 49.995
2020-08-22 | 357:56 | 49.994
2020-08-22 | 358:56 | 49.992
2020-08-22 | 359:56 | 49.991
2020-08-22 | 360:56 | 49.989
2020-08-22 | 361:56 | 49.987
2020-08-22 | 362:56 | 49.985
2020-08-22 | 363:56 | 49.986
2020-08-22 | 364:56 | 49.989
2020-08-22 | 365:56 | 49.99
2020-08-22 | 366:56 | 49.99
2020-08-22 | 367:56 | 49.989
2020-08-22 | 368:56 | 49.987
2020-08-22 | 369:56 | 49.985
2020-08-22 | 370:56 | 49.983
2020-08-22 | 371:56 | 49.984
2020-08-22 | 372:56 | 49.985
2020-08-22 | 373:56 | 49.985
2020-08-22 | 374:56 | 49.987
2020-08-22 | 375:56 | 49.988
2020-08-22 | 376:56 | 49.987
2020-08-22 | 377:56 | 49.984
2020-08-22 | 378:56 | 49.984
2020-08-22 | 379:56 | 49.984
2020-08-22 | 380:56 | 49.984
2020-08-22 | 381:56 | 49.983
2020-08-22 | 382:56 | 49.985
2020-08-22 | 383:56 | 49.987
2020-08-22 | 384:56 | 49.988
2020-08-22 | 385:56 | 49.988
2020-08-22 | 386:56 | 49.988
2020-08-22 | 387:56 | 49.99
2020-08-22 | 388:56 | 49.994
2020-08-22 | 389:56 | 49.996
2020-08-22 | 390:56 | 49.995
2020-08-22 | 391:56 | 49.994
2020-08-22 | 392:56 | 49.992
2020-08-22 | 393:56 | 49.992
2020-08-22 | 394:56 | 49.994
2020-08-22 | 395:56 | 49.994
2020-08-22 | 396:56 | 49.995
2020-08-22 | 397:56 | 49.997
2020-08-22 | 398:56 | 49.999
2020-08-22 | 399:56 | 50
2020-08-22 | 400:56 | 50.002
2020-08-22 | 401:56 | 50.004
2020-08-22 | 402:56 | 50.007
2020-08-22 | 403:56 | 50.009
2020-08-22 | 404:56 | 50.011
2020-08-22 | 405:56 | 50.014
2020-08-22 | 406:56 | 50.016
2020-08-22 | 407:56 | 50.015
2020-08-22 | 408:56 | 50.014
2020-08-22 | 409:56 | 50.011
2020-08-22 | 410:56 | 50.011
2020-08-22 | 411:56 | 50.014
2020-08-22 | 412:56 | 50.017
2020-08-22 | 413:56 | 50.022
2020-08-22 | 414:56 | 50.026
2020-08-22 | 415:56 | 50.028
2020-08-22 | 416:56 | 50.029
2020-08-22 | 417:56 | 50.03
2020-08-22 | 418:56 | 50.028
2020-08-22 | 419:56 | 50.027
2020-08-22 | 420:56 | 50.027
2020-08-22 | 421:56 | 50.027
2020-08-22 | 422:56 | 50.028
2020-08-22 | 423:56 | 50.03
2020-08-22 | 424:56 | 50.033
2020-08-22 | 425:56 | 50.036
2020-08-22 | 426:56 | 50.039
2020-08-22 | 427:56 | 50.04
2020-08-22 | 428:56 | 50.044
2020-08-22 | 429:56 | 50.047
2020-08-22 | 430:56 | 50.049
2020-08-22 | 431:56 | 50.049
2020-08-22 | 432:56 | 50.049
2020-08-22 | 433:56 | 50.047
2020-08-22 | 434:56 | 50.045
2020-08-22 | 435:56 | 50.04
2020-08-22 | 436:56 | 50.04
2020-08-22 | 437:56 | 50.038
2020-08-22 | 438:56 | 50.035
2020-08-22 | 439:56 | 50.034
2020-08-22 | 440:56 | 50.033
2020-08-22 | 441:56 | 50.032
2020-08-22 | 442:56 | 50.033
2020-08-22 | 443:56 | 50.034
2020-08-22 | 444:56 | 50.035
2020-08-22 | 445:56 | 50.037
2020-08-22 | 446:56 | 50.038
2020-08-22 | 447:56 | 50.04
2020-08-22 | 448:56 | 50.041
2020-08-22 | 449:56 | 50.042
2020-08-22 | 450:56 | 50.041
2020-08-22 | 451:56 | 50.039
2020-08-22 | 452:56 | 50.039
2020-08-22 | 453:56 | 50.039
2020-08-22 | 454:56 | 50.04
2020-08-22 | 455:56 | 50.04
2020-08-22 | 456:56 | 50.04
2020-08-22 | 457:56 | 50.042
2020-08-22 | 458:56 | 50.046
2020-08-22 | 459:56 | 50.046
2020-08-22 | 460:56 | 50.049
2020-08-22 | 461:56 | 50.051
2020-08-22 | 462:56 | 50.052
2020-08-22 | 463:56 | 50.051
2020-08-22 | 464:56 | 50.048
2020-08-22 | 465:56 | 50.046
2020-08-22 | 466:56 | 50.045
2020-08-22 | 467:56 | 50.046
2020-08-22 | 468:56 | 50.045
2020-08-22 | 469:56 | 50.045
2020-08-22 | 470:56 | 50.042
2020-08-22 | 471:56 | 50.042
2020-08-22 | 472:56 | 50.042
2020-08-22 | 473:56 | 50.042
2020-08-22 | 474:56 | 50.043
2020-08-22 | 475:56 | 50.044
2020-08-22 | 476:56 | 50.045
2020-08-22 | 477:56 | 50.047
2020-08-22 | 478:56 | 50.046
2020-08-22 | 479:56 | 50.045
2020-08-22 | 480:56 | 50.046
2020-08-22 | 481:56 | 50.046
2020-08-22 | 482:56 | 50.046
2020-08-22 | 483:56 | 50.048
2020-08-22 | 484:56 | 50.05
2020-08-22 | 485:56 | 50.052
2020-08-22 | 486:56 | 50.053
2020-08-22 | 487:56 | 50.053
2020-08-22 | 488:56 | 50.051
2020-08-22 | 489:56 | 50.048
2020-08-22 | 490:56 | 50.046
2020-08-22 | 491:56 | 50.042
2020-08-22 | 492:56 | 50.039
2020-08-22 | 493:56 | 50.036
2020-08-22 | 494:56 | 50.035
2020-08-22 | 495:56 | 50.034
2020-08-22 | 496:56 | 50.033
2020-08-22 | 497:56 | 50.032
2020-08-22 | 498:56 | 50.029
2020-08-22 | 499:56 | 50.027
2020-08-22 | 500:56 | 50.027
2020-08-22 | 501:56 | 50.025
2020-08-22 | 502:56 | 50.022
2020-08-22 | 503:56 | 50.018
2020-08-22 | 504:56 | 50.014
2020-08-22 | 505:56 | 50.01
2020-08-22 | 506:56 | 50.001
2020-08-22 | 507:56 | 49.992
2020-08-22 | 508:56 | 49.98
2020-08-22 | 509:56 | 49.969
2020-08-22 | 510:56 | 49.961
2020-08-22 | 511:56 | 49.957
2020-08-22 | 512:56 | 49.954
2020-08-22 | 513:56 | 49.953
2020-08-22 | 514:56 | 49.953
2020-08-22 | 515:56 | 49.95
2020-08-22 | 516:56 | 49.948
2020-08-22 | 517:56 | 49.948
2020-08-22 | 518:56 | 49.95
2020-08-22 | 519:56 | 49.953
2020-08-22 | 520:56 | 49.954
2020-08-22 | 521:56 | 49.956
2020-08-22 | 522:56 | 49.958
2020-08-22 | 523:56 | 49.961
2020-08-22 | 524:56 | 49.966
2020-08-22 | 525:56 | 49.968
2020-08-22 | 526:56 | 49.969
2020-08-22 | 527:56 | 49.97
2020-08-22 | 528:56 | 49.971
2020-08-22 | 529:56 | 49.972
2020-08-22 | 530:56 | 49.976
2020-08-22 | 531:56 | 49.98
2020-08-22 | 532:56 | 49.984
2020-08-22 | 533:56 | 49.989
2020-08-22 | 534:56 | 49.993
2020-08-22 | 535:56 | 49.998
2020-08-22 | 536:56 | 50.001
2020-08-22 | 537:56 | 50.003
2020-08-22 | 538:56 | 50.006
2020-08-22 | 539:56 | 50.011
2020-08-22 | 540:56 | 50.016
2020-08-22 | 541:56 | 50.022
2020-08-22 | 542:56 | 50.025
2020-08-22 | 543:56 | 50.028
2020-08-22 | 544:56 | 50.031
2020-08-22 | 545:56 | 50.034
2020-08-22 | 546:56 | 50.033
2020-08-22 | 547:56 | 50.032
2020-08-22 | 548:56 | 50.031
2020-08-22 | 549:56 | 50.03
2020-08-22 | 550:56 | 50.028
2020-08-22 | 551:56 | 50.026
2020-08-22 | 552:56 | 50.024
2020-08-22 | 553:56 | 50.023
2020-08-22 | 554:56 | 50.022
2020-08-22 | 555:56 | 50.021
2020-08-22 | 556:56 | 50.017
2020-08-22 | 557:56 | 50.017
2020-08-22 | 558:56 | 50.018
2020-08-22 | 559:56 | 50.018
2020-08-22 | 560:56 | 50.016
2020-08-22 | 561:56 | 50.014
2020-08-22 | 562:56 | 50.013
2020-08-22 | 563:56 | 50.012
2020-08-22 | 564:56 | 50.012
2020-08-22 | 565:56 | 50.011
2020-08-22 | 566:56 | 50.009
2020-08-22 | 567:56 | 50.008
2020-08-22 | 568:56 | 50.005
2020-08-22 | 569:56 | 50.003
2020-08-22 | 570:56 | 50.004
2020-08-22 | 571:56 | 50.006
2020-08-22 | 572:56 | 50.008
2020-08-22 | 573:56 | 50.009
2020-08-22 | 574:56 | 50.011
2020-08-22 | 575:56 | 50.011
2020-08-22 | 576:56 | 50.011
2020-08-22 | 577:56 | 50.011
2020-08-22 | 578:56 | 50.009
2020-08-22 | 579:56 | 50.007
2020-08-22 | 580:56 | 50.003
2020-08-22 | 581:56 | 50
2020-08-22 | 582:56 | 49.998
2020-08-22 | 583:56 | 49.995
2020-08-22 | 584:56 | 49.993
2020-08-22 | 585:56 | 49.993
2020-08-22 | 586:56 | 49.992
2020-08-22 | 587:56 | 49.993
2020-08-22 | 588:56 | 49.995
2020-08-22 | 589:56 | 49.998
2020-08-22 | 590:56 | 50.001
2020-08-22 | 591:56 | 50.005
2020-08-22 | 592:56 | 50.008
2020-08-22 | 593:56 | 50.01
2020-08-22 | 594:56 | 50.011
2020-08-22 | 595:56 | 50.01
2020-08-22 | 596:56 | 50.01
2020-08-22 | 597:56 | 50.008
2020-08-22 | 598:56 | 50.007
2020-08-22 | 599:56 | 50.006
2020-08-22 | 600:56 | 50.005
2020-08-22 | 601:56 | 50.002
2020-08-22 | 602:56 | 49.997
2020-08-22 | 603:56 | 49.991
2020-08-22 | 604:56 | 49.986
2020-08-22 | 605:56 | 49.983
2020-08-22 | 606:56 | 49.98
2020-08-22 | 607:56 | 49.978
2020-08-22 | 608:56 | 49.975
2020-08-22 | 609:56 | 49.973
2020-08-22 | 610:56 | 49.969
2020-08-22 | 611:56 | 49.966
2020-08-22 | 612:56 | 49.963
2020-08-22 | 613:56 | 49.961
2020-08-22 | 614:56 | 49.958
2020-08-22 | 615:56 | 49.954
2020-08-22 | 616:56 | 49.951
2020-08-22 | 617:56 | 49.948
2020-08-22 | 618:56 | 49.946
2020-08-22 | 619:56 | 49.943
2020-08-22 | 620:56 | 49.94
2020-08-22 | 621:56 | 49.939
2020-08-22 | 622:56 | 49.937
2020-08-22 | 623:56 | 49.935
2020-08-22 | 624:56 | 49.934
2020-08-22 | 625:56 | 49.932
2020-08-22 | 626:56 | 49.933
2020-08-22 | 627:56 | 49.934
2020-08-22 | 628:56 | 49.934
2020-08-22 | 629:56 | 49.933
2020-08-22 | 630:56 | 49.933
2020-08-22 | 631:56 | 49.934
2020-08-22 | 632:56 | 49.935
2020-08-22 | 633:56 | 49.939
2020-08-22 | 634:56 | 49.944
2020-08-22 | 635:56 | 49.947
2020-08-22 | 636:56 | 49.95
2020-08-22 | 637:56 | 49.953
2020-08-22 | 638:56 | 49.957
2020-08-22 | 639:56 | 49.96
2020-08-22 | 640:56 | 49.963
2020-08-22 | 641:56 | 49.965
2020-08-22 | 642:56 | 49.964
2020-08-22 | 643:56 | 49.962
2020-08-22 | 644:56 | 49.959
2020-08-22 | 645:56 | 49.959
2020-08-22 | 646:56 | 49.958
2020-08-22 | 647:56 | 49.96
2020-08-22 | 648:56 | 49.961
2020-08-22 | 649:56 | 49.964
2020-08-22 | 650:56 | 49.967
2020-08-22 | 651:56 | 49.97
2020-08-22 | 652:56 | 49.973
2020-08-22 | 653:56 | 49.976
2020-08-22 | 654:56 | 49.978
2020-08-22 | 655:56 | 49.979
2020-08-22 | 656:56 | 49.978
2020-08-22 | 657:56 | 49.976
2020-08-22 | 658:56 | 49.976
2020-08-22 | 659:56 | 49.975
2020-08-22 | 660:56 | 49.973
2020-08-22 | 661:56 | 49.973
2020-08-22 | 662:56 | 49.975
2020-08-22 | 663:56 | 49.975
2020-08-22 | 664:56 | 49.976
2020-08-22 | 665:56 | 49.981
2020-08-22 | 666:56 | 49.986
2020-08-22 | 667:56 | 49.988
2020-08-22 | 668:56 | 49.991
2020-08-22 | 669:56 | 49.993
2020-08-22 | 670:56 | 49.995
2020-08-22 | 671:56 | 49.999
2020-08-22 | 672:56 | 50.005
2020-08-22 | 673:56 | 50.009
2020-08-22 | 674:56 | 50.013
2020-08-22 | 675:56 | 50.016
2020-08-22 | 676:56 | 50.02
2020-08-22 | 677:56 | 50.023
2020-08-22 | 678:56 | 50.025
2020-08-22 | 679:56 | 50.026
2020-08-22 | 680:56 | 50.024
2020-08-22 | 681:56 | 50.023
2020-08-22 | 682:56 | 50.021
2020-08-22 | 683:56 | 50.02
2020-08-22 | 684:56 | 50.018
2020-08-22 | 685:56 | 50.017
2020-08-22 | 686:56 | 50.018
2020-08-22 | 687:56 | 50.019
2020-08-22 | 688:56 | 50.019
2020-08-22 | 689:56 | 50.019
2020-08-22 | 690:56 | 50.025
2020-08-22 | 691:56 | 50.031
2020-08-22 | 692:56 | 50.039
2020-08-22 | 693:56 | 50.045
2020-08-22 | 694:56 | 50.049
2020-08-22 | 695:56 | 50.053
2020-08-22 | 696:56 | 50.056
2020-08-22 | 697:56 | 50.058
2020-08-22 | 698:56 | 50.061
2020-08-22 | 699:56 | 50.062
2020-08-22 | 700:56 | 50.063
2020-08-22 | 701:56 | 50.065
2020-08-22 | 702:56 | 50.067
2020-08-22 | 703:56 | 50.069
2020-08-22 | 704:56 | 50.071
2020-08-22 | 705:56 | 50.073
2020-08-22 | 706:56 | 50.077
2020-08-22 | 707:56 | 50.083
2020-08-22 | 708:56 | 50.09
2020-08-22 | 709:56 | 50.097
2020-08-22 | 710:56 | 50.103
2020-08-22 | 711:56 | 50.107
2020-08-22 | 712:56 | 50.11
2020-08-22 | 713:56 | 50.11
2020-08-22 | 714:56 | 50.108
2020-08-22 | 715:56 | 50.105
2020-08-22 | 716:56 | 50.102
2020-08-22 | 717:56 | 50.102
2020-08-22 | 718:56 | 50.099
2020-08-22 | 719:56 | 50.096
2020-08-22 | 720:56 | 50.093
2020-08-22 | 721:56 | 50.091
2020-08-22 | 722:56 | 50.088
2020-08-22 | 723:56 | 50.087
2020-08-22 | 724:56 | 50.085
2020-08-22 | 725:56 | 50.082
2020-08-22 | 726:56 | 50.079
2020-08-22 | 727:56 | 50.076
2020-08-22 | 728:56 | 50.076
2020-08-22 | 729:56 | 50.074
2020-08-22 | 730:56 | 50.071
2020-08-22 | 731:56 | 50.071
2020-08-22 | 732:56 | 50.07
2020-08-22 | 733:56 | 50.071
2020-08-22 | 734:56 | 50.072
2020-08-22 | 735:56 | 50.071
2020-08-22 | 736:56 | 50.072
2020-08-22 | 737:56 | 50.074
2020-08-22 | 738:56 | 50.076
2020-08-22 | 739:56 | 50.078
2020-08-22 | 740:56 | 50.079
2020-08-22 | 741:56 | 50.078
2020-08-22 | 742:56 | 50.077
2020-08-22 | 743:56 | 50.077
2020-08-22 | 744:56 | 50.076
2020-08-22 | 745:56 | 50.073
2020-08-22 | 746:56 | 50.069
2020-08-22 | 747:56 | 50.066
2020-08-22 | 748:56 | 50.064
2020-08-22 | 749:56 | 50.062
2020-08-22 | 750:56 | 50.062
2020-08-22 | 751:56 | 50.062
2020-08-22 | 752:56 | 50.062
2020-08-22 | 753:56 | 50.062
2020-08-22 | 754:56 | 50.06
2020-08-22 | 755:56 | 50.058
2020-08-22 | 756:56 | 50.056
2020-08-22 | 757:56 | 50.056
2020-08-22 | 758:56 | 50.056
2020-08-22 | 759:56 | 50.056
2020-08-22 | 760:56 | 50.062
2020-08-22 | 761:56 | 50.071
2020-08-22 | 762:56 | 50.077
2020-08-22 | 763:56 | 50.079
2020-08-22 | 764:56 | 50.077
2020-08-22 | 765:56 | 50.075
2020-08-22 | 766:56 | 50.073
2020-08-22 | 767:56 | 50.073
2020-08-22 | 768:56 | 50.073
2020-08-22 | 769:56 | 50.073
2020-08-22 | 770:56 | 50.073
2020-08-22 | 771:56 | 50.073
2020-08-22 | 772:56 | 50.072
2020-08-22 | 773:56 | 50.071
2020-08-22 | 774:56 | 50.07
2020-08-22 | 775:56 | 50.068
2020-08-22 | 776:56 | 50.066
2020-08-22 | 777:56 | 50.065
2020-08-22 | 778:56 | 50.066
2020-08-22 | 779:56 | 50.069
2020-08-22 | 780:56 | 50.07
2020-08-22 | 781:56 | 50.072
2020-08-22 | 782:56 | 50.074
2020-08-22 | 783:56 | 50.077
2020-08-22 | 784:56 | 50.08
2020-08-22 | 785:56 | 50.082
2020-08-22 | 786:56 | 50.082
2020-08-22 | 787:56 | 50.082
2020-08-22 | 788:56 | 50.083
2020-08-22 | 789:56 | 50.083
2020-08-22 | 790:56 | 50.081
2020-08-22 | 791:56 | 50.079
2020-08-22 | 792:56 | 50.077
2020-08-22 | 793:56 | 50.077
2020-08-22 | 794:56 | 50.078
2020-08-22 | 795:56 | 50.076
2020-08-22 | 796:56 | 50.074
2020-08-22 | 797:56 | 50.073
2020-08-22 | 798:56 | 50.073
2020-08-22 | 799:56 | 50.074
2020-08-22 | 800:56 | 50.074
2020-08-22 | 801:56 | 50.072
2020-08-22 | 802:56 | 50.07
2020-08-22 | 803:56 | 50.067
2020-08-22 | 804:56 | 50.066
2020-08-22 | 805:56 | 50.067
2020-08-22 | 806:56 | 50.069
2020-08-22 | 807:56 | 50.07
2020-08-22 | 808:56 | 50.069
2020-08-22 | 809:56 | 50.067
2020-08-22 | 810:56 | 50.065
2020-08-22 | 811:56 | 50.063
2020-08-22 | 812:56 | 50.061
2020-08-22 | 813:56 | 50.06
2020-08-22 | 814:56 | 50.056
2020-08-22 | 815:56 | 50.053
2020-08-22 | 816:56 | 50.049
2020-08-22 | 817:56 | 50.046
2020-08-22 | 818:56 | 50.042
2020-08-22 | 819:56 | 50.04
2020-08-22 | 820:56 | 50.042
2020-08-22 | 821:56 | 50.047
2020-08-22 | 822:56 | 50.052
2020-08-22 | 823:56 | 50.056
2020-08-22 | 824:56 | 50.059
2020-08-22 | 825:56 | 50.062
2020-08-22 | 826:56 | 50.066
2020-08-22 | 827:56 | 50.069
2020-08-22 | 828:56 | 50.072
2020-08-22 | 829:56 | 50.073
2020-08-22 | 830:56 | 50.074
2020-08-22 | 831:56 | 50.076
2020-08-22 | 832:56 | 50.078
2020-08-22 | 833:56 | 50.08
2020-08-22 | 834:56 | 50.081
2020-08-22 | 835:56 | 50.08
2020-08-22 | 836:56 | 50.073
2020-08-22 | 837:56 | 50.064
2020-08-22 | 838:56 | 50.06
2020-08-22 | 839:56 | 50.055
2020-08-22 | 840:56 | 50.051
2020-08-22 | 841:56 | 50.048
2020-08-22 | 842:56 | 50.046
2020-08-22 | 843:56 | 50.044
2020-08-22 | 844:56 | 50.044
2020-08-22 | 845:56 | 50.044
2020-08-22 | 846:56 | 50.044
2020-08-22 | 847:56 | 50.041
2020-08-22 | 848:56 | 50.041
2020-08-22 | 849:56 | 50.041
2020-08-22 | 850:56 | 50.042
2020-08-22 | 851:56 | 50.042
2020-08-22 | 852:56 | 50.042
2020-08-22 | 853:56 | 50.042
2020-08-22 | 854:56 | 50.041
2020-08-22 | 855:56 | 50.041
2020-08-22 | 856:56 | 50.041
2020-08-22 | 857:56 | 50.039
2020-08-22 | 858:56 | 50.036
2020-08-22 | 859:56 | 50.039
2020-08-22 | 860:56 | 50.046
2020-08-22 | 861:56 | 50.052
2020-08-22 | 862:56 | 50.059
2020-08-22 | 863:56 | 50.065
2020-08-22 | 864:56 | 50.07
2020-08-22 | 865:56 | 50.073
2020-08-22 | 866:56 | 50.075
2020-08-22 | 867:56 | 50.076
2020-08-22 | 868:56 | 50.078
2020-08-22 | 869:56 | 50.078
2020-08-22 | 870:56 | 50.078
2020-08-22 | 871:56 | 50.077
2020-08-22 | 872:56 | 50.076
2020-08-22 | 873:56 | 50.078
2020-08-22 | 874:56 | 50.079
2020-08-22 | 875:56 | 50.077
2020-08-22 | 876:56 | 50.074
2020-08-22 | 877:56 | 50.071
2020-08-22 | 878:56 | 50.067
2020-08-22 | 879:56 | 50.06
2020-08-22 | 880:56 | 50.057
2020-08-22 | 881:56 | 50.055
2020-08-22 | 882:56 | 50.054
2020-08-22 | 883:56 | 50.053
2020-08-22 | 884:56 | 50.053
2020-08-22 | 885:56 | 50.054
2020-08-22 | 886:56 | 50.053
2020-08-22 | 887:56 | 50.052
2020-08-22 | 888:56 | 50.051
2020-08-22 | 889:56 | 50.048
2020-08-22 | 890:56 | 50.044
2020-08-22 | 891:56 | 50.041
2020-08-22 | 892:56 | 50.038
2020-08-22 | 893:56 | 50.036
2020-08-22 | 894:56 | 50.034
2020-08-22 | 895:56 | 50.034
2020-08-22 | 896:56 | 50.037
2020-08-22 | 897:56 | 50.042
2020-08-22 | 898:56 | 50.047
2020-08-22 | 899:56 | 50.05
2020-08-22 | 900:56 | 50.053
2020-08-22 | 901:56 | 50.055
2020-08-22 | 902:56 | 50.056
2020-08-22 | 903:56 | 50.055
2020-08-22 | 904:56 | 50.055
2020-08-22 | 905:56 | 50.055
2020-08-22 | 906:56 | 50.056
2020-08-22 | 907:56 | 50.057
2020-08-22 | 908:56 | 50.058
2020-08-22 | 909:56 | 50.059
2020-08-22 | 910:56 | 50.059
2020-08-22 | 911:56 | 50.058
2020-08-22 | 912:56 | 50.06
2020-08-22 | 913:56 | 50.06
2020-08-22 | 914:56 | 50.063
2020-08-22 | 20:11 | 50.063
2020-08-22 | 20:11 | 50.063
2020-08-22 | 20:11 | 50.063
2020-08-22 | 20:11 | 50.062
2020-08-22 | 20:11 | 50.06
2020-08-22 | 20:11 | 50.057
2020-08-22 | 20:11 | 50.055
2020-08-22 | 20:11 | 50.056
2020-08-22 | 20:11 | 50.059
2020-08-22 | 20:11 | 50.064
2020-08-22 | 20:11 | 50.067
2020-08-22 | 20:11 | 50.069
2020-08-22 | 20:11 | 50.069
2020-08-22 | 20:11 | 50.071
2020-08-22 | 20:11 | 50.072
2020-08-22 | 20:11 | 50.073
2020-08-22 | 20:11 | 50.074
2020-08-22 | 20:11 | 50.074
2020-08-22 | 20:11 | 50.073
2020-08-22 | 20:11 | 50.072
2020-08-22 | 20:11 | 50.069
2020-08-22 | 20:11 | 50.07
2020-08-22 | 20:11 | 50.071
2020-08-22 | 20:11 | 50.072
2020-08-22 | 20:11 | 50.073
2020-08-22 | 20:11 | 50.074
2020-08-22 | 20:11 | 50.075
2020-08-22 | 20:11 | 50.075
2020-08-22 | 20:11 | 50.076
2020-08-22 | 20:11 | 50.077
2020-08-22 | 20:11 | 50.078
2020-08-22 | 20:12 | 50.079
2020-08-22 | 20:12 | 50.08
2020-08-22 | 20:12 | 50.079
2020-08-22 | 20:12 | 50.078
2020-08-22 | 20:12 | 50.077
2020-08-22 | 20:12 | 50.077
2020-08-22 | 20:12 | 50.077
2020-08-22 | 20:12 | 50.076
2020-08-22 | 20:12 | 50.076
2020-08-22 | 20:12 | 50.076
2020-08-22 | 20:12 | 50.077
2020-08-22 | 20:12 | 50.079
2020-08-22 | 20:12 | 50.083
2020-08-22 | 20:12 | 50.087
2020-08-22 | 20:12 | 50.087
2020-08-22 | 20:12 | 50.086
2020-08-22 | 20:12 | 50.083
2020-08-22 | 20:12 | 50.081
2020-08-22 | 20:12 | 50.08
2020-08-22 | 20:12 | 50.079
2020-08-22 | 20:12 | 50.079
2020-08-22 | 20:12 | 50.077
2020-08-22 | 20:12 | 50.074
2020-08-22 | 20:12 | 50.074
2020-08-22 | 20:12 | 50.073
2020-08-22 | 20:12 | 50.07
2020-08-22 | 20:12 | 50.067
2020-08-22 | 20:12 | 50.065
2020-08-22 | 20:12 | 50.065
2020-08-22 | 20:12 | 50.064
2020-08-22 | 20:12 | 50.065
2020-08-22 | 20:12 | 50.066
2020-08-22 | 20:12 | 50.068
2020-08-22 | 20:12 | 50.068
2020-08-22 | 20:12 | 50.068
2020-08-22 | 20:12 | 50.066
2020-08-22 | 20:12 | 50.064
2020-08-22 | 20:12 | 50.064
2020-08-22 | 20:12 | 50.064
2020-08-22 | 20:12 | 50.063
2020-08-22 | 20:12 | 50.063
2020-08-22 | 20:12 | 50.061
2020-08-22 | 20:12 | 50.058
2020-08-22 | 20:12 | 50.056
2020-08-22 | 20:12 | 50.053
2020-08-22 | 20:12 | 50.05
2020-08-22 | 20:12 | 50.045
2020-08-22 | 20:12 | 50.044
2020-08-22 | 20:12 | 50.044
2020-08-22 | 20:12 | 50.045
2020-08-22 | 20:12 | 50.045
2020-08-22 | 20:12 | 50.045
2020-08-22 | 20:12 | 50.044
2020-08-22 | 20:12 | 50.044
2020-08-22 | 20:12 | 50.044
2020-08-22 | 20:12 | 50.042
2020-08-22 | 20:12 | 50.041
2020-08-22 | 20:12 | 50.039
2020-08-22 | 20:12 | 50.037
2020-08-22 | 20:12 | 50.036
2020-08-22 | 20:13 | 50.035
2020-08-22 | 20:13 | 50.036
2020-08-22 | 20:13 | 50.038
2020-08-22 | 20:13 | 50.038
2020-08-22 | 20:13 | 50.038
2020-08-22 | 20:13 | 50.038
2020-08-22 | 20:13 | 50.038
2020-08-22 | 20:13 | 50.04
2020-08-22 | 20:13 | 50.045
2020-08-22 | 20:13 | 50.048
2020-08-22 | 20:13 | 50.051
2020-08-22 | 20:13 | 50.053
2020-08-22 | 20:13 | 50.057
2020-08-22 | 20:13 | 50.061
2020-08-22 | 20:13 | 50.065
2020-08-22 | 20:13 | 50.068
2020-08-22 | 20:13 | 50.071
2020-08-22 | 20:13 | 50.072
2020-08-22 | 20:13 | 50.074
2020-08-22 | 20:13 | 50.075
2020-08-22 | 20:13 | 50.075
2020-08-22 | 20:13 | 50.075
2020-08-22 | 20:13 | 50.076
2020-08-22 | 20:13 | 50.078
2020-08-22 | 20:13 | 50.08
2020-08-22 | 20:13 | 50.083
2020-08-22 | 20:13 | 50.085
2020-08-22 | 20:13 | 50.086
2020-08-22 | 20:13 | 50.085
2020-08-22 | 20:13 | 50.084
2020-08-22 | 20:13 | 50.084
2020-08-22 | 20:13 | 50.084
2020-08-22 | 20:13 | 50.084
2020-08-22 | 20:13 | 50.086
2020-08-22 | 20:13 | 50.089
2020-08-22 | 20:13 | 50.092
2020-08-22 | 20:13 | 50.094
2020-08-22 | 20:13 | 50.092
2020-08-22 | 20:13 | 50.093
2020-08-22 | 20:13 | 50.09
2020-08-22 | 20:13 | 50.091
2020-08-22 | 20:13 | 50.091
2020-08-22 | 20:13 | 50.091
2020-08-22 | 20:13 | 50.09
2020-08-22 | 20:13 | 50.089
2020-08-22 | 20:13 | 50.087
2020-08-22 | 20:13 | 50.085
2020-08-22 | 20:13 | 50.082
2020-08-22 | 20:13 | 50.08
2020-08-22 | 20:13 | 50.073
2020-08-22 | 20:13 | 50.067
2020-08-22 | 20:13 | 50.064
2020-08-22 | 20:13 | 50.062
2020-08-22 | 20:13 | 50.062
2020-08-22 | 20:13 | 50.061
2020-08-22 | 20:13 | 50.06
2020-08-22 | 20:13 | 50.059
2020-08-22 | 20:13 | 50.058
2020-08-22 | 20:13 | 50.057
2020-08-22 | 20:13 | 50.056
2020-08-22 | 20:14 | 50.054
2020-08-22 | 20:14 | 50.054
2020-08-22 | 20:14 | 50.056
2020-08-22 | 20:14 | 50.057
2020-08-22 | 20:14 | 50.056
2020-08-22 | 20:14 | 50.055
2020-08-22 | 20:14 | 50.054
2020-08-22 | 20:14 | 50.055
2020-08-22 | 20:14 | 50.055
2020-08-22 | 20:14 | 50.055
2020-08-22 | 20:14 | 50.055
2020-08-22 | 20:14 | 50.056
2020-08-22 | 20:14 | 50.056
2020-08-22 | 20:14 | 50.056
2020-08-22 | 20:14 | 50.056
2020-08-22 | 20:14 | 50.056
2020-08-22 | 20:14 | 50.056
2020-08-22 | 20:14 | 50.054
2020-08-22 | 20:14 | 50.05
2020-08-22 | 20:14 | 50.047
2020-08-22 | 20:14 | 50.045
2020-08-22 | 20:14 | 50.045
2020-08-22 | 20:14 | 50.046
2020-08-22 | 20:14 | 50.048
2020-08-22 | 20:14 | 50.049
2020-08-22 | 20:14 | 50.05
2020-08-22 | 20:14 | 50.05
2020-08-22 | 20:14 | 50.049
2020-08-22 | 20:14 | 50.049
2020-08-22 | 20:14 | 50.048
2020-08-22 | 20:14 | 50.048
2020-08-22 | 20:14 | 50.048
2020-08-22 | 20:14 | 50.05
2020-08-22 | 20:14 | 50.054
2020-08-22 | 20:14 | 50.056
2020-08-22 | 20:14 | 50.057
2020-08-22 | 20:14 | 50.059
2020-08-22 | 20:14 | 50.061
2020-08-22 | 20:14 | 50.06
2020-08-22 | 20:14 | 50.059
2020-08-22 | 20:14 | 50.057
2020-08-22 | 20:14 | 50.058
2020-08-22 | 20:14 | 50.06
2020-08-22 | 20:14 | 50.061
2020-08-22 | 20:14 | 50.063
2020-08-22 | 20:14 | 50.065
2020-08-22 | 20:14 | 50.067
2020-08-22 | 20:14 | 50.07
2020-08-22 | 20:14 | 50.07
2020-08-22 | 20:14 | 50.066
2020-08-22 | 20:14 | 50.064
2020-08-22 | 20:14 | 50.064
2020-08-22 | 20:14 | 50.067
2020-08-22 | 20:14 | 50.072
2020-08-22 | 20:14 | 50.075
2020-08-22 | 20:14 | 50.077
2020-08-22 | 20:14 | 50.079
2020-08-22 | 20:14 | 50.081
2020-08-22 | 20:14 | 50.082
2020-08-22 | 20:15 | 50.082
2020-08-22 | 20:15 | 50.082
2020-08-22 | 20:15 | 50.081
2020-08-22 | 20:15 | 50.079
2020-08-22 | 20:15 | 50.078
2020-08-22 | 20:15 | 50.075
2020-08-22 | 20:15 | 50.073
2020-08-22 | 20:15 | 50.072
2020-08-22 | 20:15 | 50.075
2020-08-22 | 20:15 | 50.076
2020-08-22 | 20:15 | 50.075
2020-08-22 | 20:15 | 50.073
2020-08-22 | 20:15 | 50.07
2020-08-22 | 20:15 | 50.066
2020-08-22 | 20:15 | 50.064
2020-08-22 | 20:15 | 50.058
2020-08-22 | 20:15 | 50.052
2020-08-22 | 20:15 | 50.046
2020-08-22 | 20:15 | 50.043
2020-08-22 | 20:15 | 50.041
2020-08-22 | 20:15 | 50.041
2020-08-22 | 20:15 | 50.039
2020-08-22 | 20:15 | 50.037
2020-08-22 | 20:15 | 50.035
2020-08-22 | 20:15 | 50.033
2020-08-22 | 20:15 | 50.035
2020-08-22 | 20:15 | 50.035
2020-08-22 | 20:15 | 50.037
2020-08-22 | 20:15 | 50.035
2020-08-22 | 20:15 | 50.031
2020-08-22 | 20:15 | 50.029
2020-08-22 | 20:15 | 50.025
2020-08-22 | 20:15 | 50.022
2020-08-22 | 20:15 | 50.02
2020-08-22 | 20:15 | 50.021
2020-08-22 | 20:15 | 50.019
2020-08-22 | 20:15 | 50.019
2020-08-22 | 20:15 | 50.019
2020-08-22 | 20:15 | 50.021
2020-08-22 | 20:15 | 50.023
2020-08-22 | 20:15 | 50.026
2020-08-22 | 20:15 | 50.027
2020-08-22 | 20:15 | 50.029
2020-08-22 | 20:15 | 50.03
2020-08-22 | 20:15 | 50.032
2020-08-22 | 20:15 | 50.035
2020-08-22 | 20:15 | 50.037
2020-08-22 | 20:15 | 50.039
2020-08-22 | 20:15 | 50.039
2020-08-22 | 20:15 | 50.038
2020-08-22 | 20:15 | 50.037
2020-08-22 | 20:15 | 50.036
2020-08-22 | 20:15 | 50.035
2020-08-22 | 20:15 | 50.035
2020-08-22 | 20:15 | 50.034
2020-08-22 | 20:15 | 50.034
2020-08-22 | 20:15 | 50.035
2020-08-22 | 20:15 | 50.037
2020-08-22 | 20:15 | 50.041
2020-08-22 | 20:15 | 50.045
2020-08-22 | 20:15 | 50.049
2020-08-22 | 20:16 | 50.051
2020-08-22 | 20:16 | 50.052
2020-08-22 | 20:16 | 50.051
2020-08-22 | 20:16 | 50.053
2020-08-22 | 20:16 | 50.055
2020-08-22 | 20:16 | 50.057
2020-08-22 | 20:16 | 50.059
2020-08-22 | 20:16 | 50.06
2020-08-22 | 20:16 | 50.064
2020-08-22 | 20:16 | 50.067
2020-08-22 | 20:16 | 50.068
2020-08-22 | 20:16 | 50.068
2020-08-22 | 20:16 | 50.067
2020-08-22 | 20:16 | 50.064
2020-08-22 | 20:16 | 50.06
2020-08-22 | 20:16 | 50.057
2020-08-22 | 20:16 | 50.054
2020-08-22 | 20:16 | 50.053
2020-08-22 | 20:16 | 50.054
2020-08-22 | 20:16 | 50.053
2020-08-22 | 20:16 | 50.054
2020-08-22 | 20:16 | 50.056
2020-08-22 | 20:16 | 50.055
2020-08-22 | 20:16 | 50.052
2020-08-22 | 20:16 | 50.051
2020-08-22 | 20:16 | 50.051
2020-08-22 | 20:16 | 50.051
2020-08-22 | 20:16 | 50.051
2020-08-22 | 20:16 | 50.051
2020-08-22 | 20:16 | 50.051
2020-08-22 | 20:16 | 50.052
2020-08-22 | 20:16 | 50.053
2020-08-22 | 20:16 | 50.054
2020-08-22 | 20:16 | 50.055
2020-08-22 | 20:16 | 50.055
2020-08-22 | 20:16 | 50.052
2020-08-22 | 20:16 | 50.049
2020-08-22 | 20:16 | 50.047
2020-08-22 | 20:16 | 50.046
2020-08-22 | 20:16 | 50.05
2020-08-22 | 20:16 | 50.051
2020-08-22 | 20:16 | 50.053
2020-08-22 | 20:16 | 50.055
2020-08-22 | 20:16 | 50.056
2020-08-22 | 20:16 | 50.057
2020-08-22 | 20:16 | 50.059
2020-08-22 | 20:16 | 50.06
2020-08-22 | 20:16 | 50.059
2020-08-22 | 20:16 | 50.059
2020-08-22 | 20:16 | 50.063
2020-08-22 | 20:16 | 50.064
2020-08-22 | 20:16 | 50.064
2020-08-22 | 20:16 | 50.062
2020-08-22 | 20:16 | 50.062
2020-08-22 | 20:16 | 50.062
2020-08-22 | 20:16 | 50.061
2020-08-22 | 20:16 | 50.063
2020-08-22 | 20:16 | 50.063
2020-08-22 | 20:16 | 50.064
2020-08-22 | 20:17 | 50.064
2020-08-22 | 20:17 | 50.063
2020-08-22 | 20:17 | 50.063
2020-08-22 | 20:17 | 50.064
2020-08-22 | 20:17 | 50.066
2020-08-22 | 20:17 | 50.065
2020-08-22 | 20:17 | 50.065
2020-08-22 | 20:17 | 50.063
2020-08-22 | 20:17 | 50.062
2020-08-22 | 20:17 | 50.061
2020-08-22 | 20:17 | 50.062
2020-08-22 | 20:17 | 50.062
2020-08-22 | 20:17 | 50.061
2020-08-22 | 20:17 | 50.062
2020-08-22 | 20:17 | 50.063
2020-08-22 | 20:17 | 50.067
2020-08-22 | 20:17 | 50.07
2020-08-22 | 20:17 | 50.073
2020-08-22 | 20:17 | 50.074
2020-08-22 | 20:17 | 50.073
2020-08-22 | 20:17 | 50.072
2020-08-22 | 20:17 | 50.07
2020-08-22 | 20:17 | 50.068
2020-08-22 | 20:17 | 50.067
2020-08-22 | 20:17 | 50.065
2020-08-22 | 20:17 | 50.064
2020-08-22 | 20:17 | 50.061
2020-08-22 | 20:17 | 50.058
2020-08-22 | 20:17 | 50.054
2020-08-22 | 20:17 | 50.05
2020-08-22 | 20:17 | 50.046
2020-08-22 | 20:17 | 50.044
2020-08-22 | 20:17 | 50.041
2020-08-22 | 20:17 | 50.037
2020-08-22 | 20:17 | 50.033
2020-08-22 | 20:17 | 50.031
2020-08-22 | 20:17 | 50.03
2020-08-22 | 20:17 | 50.032
2020-08-22 | 20:17 | 50.035
2020-08-22 | 20:17 | 50.037
2020-08-22 | 20:17 | 50.035
2020-08-22 | 20:17 | 50.038
2020-08-22 | 20:17 | 50.038
2020-08-22 | 20:17 | 50.041
2020-08-22 | 20:17 | 50.041
2020-08-22 | 20:17 | 50.043
2020-08-22 | 20:17 | 50.044
2020-08-22 | 20:17 | 50.042
2020-08-22 | 20:17 | 50.038
2020-08-22 | 20:17 | 50.035
2020-08-22 | 20:17 | 50.032
2020-08-22 | 20:17 | 50.031
2020-08-22 | 20:17 | 50.03
2020-08-22 | 20:17 | 50.03
2020-08-22 | 20:17 | 50.029
2020-08-22 | 20:17 | 50.029
2020-08-22 | 20:17 | 50.028
2020-08-22 | 20:17 | 50.027
2020-08-22 | 20:17 | 50.025
2020-08-22 | 20:17 | 50.02
2020-08-22 | 20:18 | 50.017
2020-08-22 | 20:18 | 50.014
2020-08-22 | 20:18 | 50.013
2020-08-22 | 20:18 | 50.012
2020-08-22 | 20:18 | 50.011
2020-08-22 | 20:18 | 50.009
2020-08-22 | 20:18 | 50.01
2020-08-22 | 20:18 | 50.012
2020-08-22 | 20:18 | 50.016
2020-08-22 | 20:18 | 50.02
2020-08-22 | 20:18 | 50.023
2020-08-22 | 20:18 | 50.024
2020-08-22 | 20:18 | 50.029
2020-08-22 | 20:18 | 50.037
2020-08-22 | 20:18 | 50.044
2020-08-22 | 20:18 | 50.049
2020-08-22 | 20:18 | 50.051
2020-08-22 | 20:18 | 50.054
2020-08-22 | 20:18 | 50.057
2020-08-22 | 20:18 | 50.059
2020-08-22 | 20:18 | 50.06
2020-08-22 | 20:18 | 50.061
2020-08-22 | 20:18 | 50.065
2020-08-22 | 20:18 | 50.069
2020-08-22 | 20:18 | 50.071
2020-08-22 | 20:18 | 50.075
2020-08-22 | 20:18 | 50.076
2020-08-22 | 20:18 | 50.078
2020-08-22 | 20:18 | 50.082
2020-08-22 | 20:18 | 50.084
2020-08-22 | 20:18 | 50.084
2020-08-22 | 20:18 | 50.082
2020-08-22 | 20:18 | 50.083
2020-08-22 | 20:18 | 50.082
2020-08-22 | 20:18 | 50.081
2020-08-22 | 20:18 | 50.077
2020-08-22 | 20:18 | 50.074
2020-08-22 | 20:18 | 50.071
2020-08-22 | 20:18 | 50.069
2020-08-22 | 20:18 | 50.066
2020-08-22 | 20:18 | 50.063
2020-08-22 | 20:18 | 50.06
2020-08-22 | 20:18 | 50.058
2020-08-22 | 20:18 | 50.057
2020-08-22 | 20:18 | 50.055
2020-08-22 | 20:18 | 50.053
2020-08-22 | 20:18 | 50.052
2020-08-22 | 20:18 | 50.051
2020-08-22 | 20:18 | 50.05
2020-08-22 | 20:18 | 50.047
2020-08-22 | 20:18 | 50.045
2020-08-22 | 20:18 | 50.044
2020-08-22 | 20:18 | 50.047
2020-08-22 | 20:18 | 50.05
2020-08-22 | 20:18 | 50.054
2020-08-22 | 20:18 | 50.058
2020-08-22 | 20:18 | 50.061
2020-08-22 | 20:18 | 50.066
2020-08-22 | 20:18 | 50.068
2020-08-22 | 20:18 | 50.069
2020-08-22 | 20:19 | 50.071
2020-08-22 | 20:19 | 50.07
2020-08-22 | 20:19 | 50.069
2020-08-22 | 20:19 | 50.065
2020-08-22 | 20:19 | 50.062
2020-08-22 | 20:19 | 50.059
2020-08-22 | 20:19 | 50.054
2020-08-22 | 20:19 | 50.054
2020-08-22 | 20:19 | 50.053
2020-08-22 | 20:19 | 50.052
2020-08-22 | 20:19 | 50.053
2020-08-22 | 20:19 | 50.051
2020-08-22 | 20:19 | 50.051
2020-08-22 | 20:19 | 50.051
2020-08-22 | 20:19 | 50.053
2020-08-22 | 20:19 | 50.058
2020-08-22 | 20:19 | 50.063
2020-08-22 | 20:19 | 50.069
2020-08-22 | 20:19 | 50.072
2020-08-22 | 20:19 | 50.076
2020-08-22 | 20:19 | 50.078
2020-08-22 | 20:19 | 50.081
2020-08-22 | 20:19 | 50.085
2020-08-22 | 20:19 | 50.088
2020-08-22 | 20:19 | 50.087
2020-08-22 | 20:19 | 50.089
2020-08-22 | 20:19 | 50.093
2020-08-22 | 20:19 | 50.094
2020-08-22 | 20:19 | 50.094
2020-08-22 | 20:19 | 50.094
2020-08-22 | 20:19 | 50.097
2020-08-22 | 20:19 | 50.097
2020-08-22 | 20:19 | 50.096
2020-08-22 | 20:19 | 50.095
2020-08-22 | 20:19 | 50.095
2020-08-22 | 20:19 | 50.096
2020-08-22 | 20:19 | 50.097
2020-08-22 | 20:19 | 50.095
2020-08-22 | 20:19 | 50.089
2020-08-22 | 20:19 | 50.085
2020-08-22 | 20:19 | 50.078
2020-08-22 | 20:19 | 50.073
2020-08-22 | 20:19 | 50.071
2020-08-22 | 20:19 | 50.069
2020-08-22 | 20:19 | 50.068
2020-08-22 | 20:19 | 50.068
2020-08-22 | 20:19 | 50.068
2020-08-22 | 20:19 | 50.066
2020-08-22 | 20:19 | 50.064
2020-08-22 | 20:19 | 50.063
2020-08-22 | 20:19 | 50.06
2020-08-22 | 20:19 | 50.058
2020-08-22 | 20:19 | 50.056
2020-08-22 | 20:19 | 50.052
2020-08-22 | 20:19 | 50.048
2020-08-22 | 20:19 | 50.047
2020-08-22 | 20:19 | 50.047
2020-08-22 | 20:19 | 50.047
2020-08-22 | 20:19 | 50.051
2020-08-22 | 20:19 | 50.053
2020-08-22 | 20:20 | 50.055
2020-08-22 | 20:20 | 50.056
2020-08-22 | 20:20 | 50.057
2020-08-22 | 20:20 | 50.058
2020-08-22 | 20:20 | 50.059
2020-08-22 | 20:20 | 50.058
2020-08-22 | 20:20 | 50.058
2020-08-22 | 20:20 | 50.057
2020-08-22 | 20:20 | 50.055
2020-08-22 | 20:20 | 50.056
2020-08-22 | 20:20 | 50.061
2020-08-22 | 20:20 | 50.063
2020-08-22 | 20:20 | 50.066
2020-08-22 | 20:20 | 50.068
2020-08-22 | 20:20 | 50.069
2020-08-22 | 20:20 | 50.072
2020-08-22 | 20:20 | 50.074
2020-08-22 | 20:20 | 50.076
2020-08-22 | 20:20 | 50.078
2020-08-22 | 20:20 | 50.075
2020-08-22 | 20:20 | 50.073
2020-08-22 | 20:20 | 50.072
2020-08-22 | 20:20 | 50.07
2020-08-22 | 20:20 | 50.069
2020-08-22 | 20:20 | 50.069
2020-08-22 | 20:20 | 50.071
2020-08-22 | 20:20 | 50.073
2020-08-22 | 20:20 | 50.077
2020-08-22 | 20:20 | 50.077
2020-08-22 | 20:20 | 50.078

## Event 20200825-1
In UTC
Date | Time | Freq
2020-08-25 | 7:38 | 49.976
2020-08-25 | 7:38 | 49.975
2020-08-25 | 7:38 | 49.976
2020-08-25 | 7:38 | 49.978
2020-08-25 | 7:38 | 49.979
2020-08-25 | 8:38 | 49.977
2020-08-25 | 9:38 | 49.971
2020-08-25 | 10:38 | 49.965
2020-08-25 | 11:38 | 49.96
2020-08-25 | 12:38 | 49.956
2020-08-25 | 13:38 | 49.952
2020-08-25 | 14:38 | 49.954
2020-08-25 | 15:38 | 49.954
2020-08-25 | 16:38 | 49.954
2020-08-25 | 17:38 | 49.958
2020-08-25 | 18:38 | 49.962
2020-08-25 | 19:38 | 49.968
2020-08-25 | 20:38 | 49.975
2020-08-25 | 21:38 | 49.981
2020-08-25 | 22:38 | 49.986
2020-08-25 | 23:38 | 49.987
2020-08-25 | 24:38 | 49.987
2020-08-25 | 25:38 | 49.986
2020-08-25 | 26:38 | 49.985
2020-08-25 | 27:38 | 49.982
2020-08-25 | 28:38 | 49.982
2020-08-25 | 29:38 | 49.979
2020-08-25 | 30:38 | 49.977
2020-08-25 | 31:38 | 49.974
2020-08-25 | 32:38 | 49.973
2020-08-25 | 33:38 | 49.973
2020-08-25 | 34:38 | 49.975
2020-08-25 | 35:38 | 49.979
2020-08-25 | 36:38 | 49.98
2020-08-25 | 37:38 | 49.984
2020-08-25 | 38:38 | 49.984
2020-08-25 | 39:38 | 49.986
2020-08-25 | 40:38 | 49.984
2020-08-25 | 41:38 | 49.982
2020-08-25 | 42:38 | 49.982
2020-08-25 | 43:38 | 49.979
2020-08-25 | 44:38 | 49.976
2020-08-25 | 45:38 | 49.974
2020-08-25 | 46:38 | 49.975
2020-08-25 | 47:38 | 49.976
2020-08-25 | 48:38 | 49.977
2020-08-25 | 49:38 | 49.979
2020-08-25 | 50:38 | 49.979
2020-08-25 | 51:38 | 49.981
2020-08-25 | 52:38 | 49.982
2020-08-25 | 53:38 | 49.984
2020-08-25 | 54:38 | 49.985
2020-08-25 | 55:38 | 49.986
2020-08-25 | 56:38 | 49.983
2020-08-25 | 57:38 | 49.977
2020-08-25 | 58:38 | 49.946
2020-08-25 | 59:38 | 49.9
2020-08-25 | 60:38 | 49.867
2020-08-25 | 61:38 | 49.848
2020-08-25 | 62:38 | 49.837
2020-08-25 | 63:38 | 49.832
2020-08-25 | 64:38 | 49.829
2020-08-25 | 65:38 | 49.827
2020-08-25 | 66:38 | 49.828
2020-08-25 | 67:38 | 49.825
2020-08-25 | 68:38 | 49.822
2020-08-25 | 69:38 | 49.82
2020-08-25 | 70:38 | 49.818
2020-08-25 | 71:38 | 49.816
2020-08-25 | 72:38 | 49.816
2020-08-25 | 73:38 | 49.817
2020-08-25 | 74:38 | 49.821
2020-08-25 | 75:38 | 49.819
2020-08-25 | 76:38 | 49.823
2020-08-25 | 77:38 | 49.825
2020-08-25 | 78:38 | 49.825
2020-08-25 | 79:38 | 49.826
2020-08-25 | 80:38 | 49.827
2020-08-25 | 81:38 | 49.827
2020-08-25 | 82:38 | 49.827
2020-08-25 | 83:38 | 49.825
2020-08-25 | 84:38 | 49.826
2020-08-25 | 85:38 | 49.824
2020-08-25 | 86:38 | 49.821
2020-08-25 | 87:38 | 49.82
2020-08-25 | 88:38 | 49.814
2020-08-25 | 89:38 | 49.815
2020-08-25 | 90:38 | 49.816
2020-08-25 | 91:38 | 49.815
2020-08-25 | 92:38 | 49.814
2020-08-25 | 93:38 | 49.813
2020-08-25 | 94:38 | 49.812
2020-08-25 | 95:38 | 49.813
2020-08-25 | 96:38 | 49.816
2020-08-25 | 97:38 | 49.817
2020-08-25 | 98:38 | 49.819
2020-08-25 | 99:38 | 49.822
2020-08-25 | 100:38 | 49.828
2020-08-25 | 101:38 | 49.834
2020-08-25 | 102:38 | 49.839
2020-08-25 | 103:38 | 49.843
2020-08-25 | 104:38 | 49.848
2020-08-25 | 105:38 | 49.853
2020-08-25 | 106:38 | 49.857
2020-08-25 | 107:38 | 49.857
2020-08-25 | 108:38 | 49.856
2020-08-25 | 109:38 | 49.854
2020-08-25 | 110:38 | 49.851
2020-08-25 | 111:38 | 49.846
2020-08-25 | 112:38 | 49.841
2020-08-25 | 113:38 | 49.836
2020-08-25 | 114:38 | 49.836
2020-08-25 | 115:38 | 49.835
2020-08-25 | 116:38 | 49.834
2020-08-25 | 117:38 | 49.832
2020-08-25 | 118:38 | 49.833
2020-08-25 | 119:38 | 49.838
2020-08-25 | 120:38 | 49.839
2020-08-25 | 121:38 | 49.842
2020-08-25 | 122:38 | 49.842
2020-08-25 | 123:38 | 49.843
2020-08-25 | 124:38 | 49.842
2020-08-25 | 125:38 | 49.84
2020-08-25 | 126:38 | 49.839
2020-08-25 | 127:38 | 49.838
2020-08-25 | 128:38 | 49.835
2020-08-25 | 129:38 | 49.834
2020-08-25 | 130:38 | 49.833
2020-08-25 | 131:38 | 49.836
2020-08-25 | 132:38 | 49.84
2020-08-25 | 133:38 | 49.844
2020-08-25 | 134:38 | 49.848
2020-08-25 | 135:38 | 49.856
2020-08-25 | 136:38 | 49.863
2020-08-25 | 137:38 | 49.868
2020-08-25 | 138:38 | 49.875
2020-08-25 | 139:38 | 49.881
2020-08-25 | 140:38 | 49.887
2020-08-25 | 141:38 | 49.891
2020-08-25 | 142:38 | 49.896
2020-08-25 | 143:38 | 49.9
2020-08-25 | 144:38 | 49.907
2020-08-25 | 145:38 | 49.914
2020-08-25 | 146:38 | 49.923
2020-08-25 | 147:38 | 49.932
2020-08-25 | 148:38 | 49.938
2020-08-25 | 149:38 | 49.944
2020-08-25 | 150:38 | 49.951
2020-08-25 | 151:38 | 49.957
2020-08-25 | 152:38 | 49.959
2020-08-25 | 153:38 | 49.963
2020-08-25 | 154:38 | 49.966
2020-08-25 | 155:38 | 49.964
2020-08-25 | 156:38 | 49.965
2020-08-25 | 157:38 | 49.963
2020-08-25 | 158:38 | 49.96
2020-08-25 | 159:38 | 49.956
2020-08-25 | 160:38 | 49.958
2020-08-25 | 161:38 | 49.956
2020-08-25 | 162:38 | 49.956
2020-08-25 | 163:38 | 49.951
2020-08-25 | 164:38 | 49.948
2020-08-25 | 165:38 | 49.944
2020-08-25 | 166:38 | 49.942
2020-08-25 | 167:38 | 49.943
2020-08-25 | 168:38 | 49.943
2020-08-25 | 169:38 | 49.946
2020-08-25 | 170:38 | 49.949
2020-08-25 | 171:38 | 49.953
2020-08-25 | 172:38 | 49.958
2020-08-25 | 173:38 | 49.958
2020-08-25 | 174:38 | 49.96
2020-08-25 | 175:38 | 49.964
2020-08-25 | 176:38 | 49.966
2020-08-25 | 177:38 | 49.971
2020-08-25 | 178:38 | 49.974
2020-08-25 | 179:38 | 49.976
2020-08-25 | 180:38 | 49.976
2020-08-25 | 181:38 | 49.978
2020-08-25 | 182:38 | 49.982
2020-08-25 | 183:38 | 49.984
2020-08-25 | 184:38 | 49.984
2020-08-25 | 185:38 | 49.986
2020-08-25 | 186:38 | 49.986
2020-08-25 | 187:38 | 49.988
2020-08-25 | 188:38 | 49.988
2020-08-25 | 189:38 | 49.988
2020-08-25 | 190:38 | 49.987
2020-08-25 | 191:38 | 49.988
2020-08-25 | 192:38 | 49.988
2020-08-25 | 193:38 | 49.99
2020-08-25 | 194:38 | 49.991
2020-08-25 | 195:38 | 49.992
2020-08-25 | 196:38 | 49.991
2020-08-25 | 197:38 | 49.99
2020-08-25 | 198:38 | 49.991
2020-08-25 | 199:38 | 49.988
2020-08-25 | 200:38 | 49.988
2020-08-25 | 201:38 | 49.984
2020-08-25 | 202:38 | 49.983
2020-08-25 | 203:38 | 49.983
2020-08-25 | 204:38 | 49.986
2020-08-25 | 205:38 | 49.986
2020-08-25 | 206:38 | 49.987
2020-08-25 | 207:38 | 49.988
2020-08-25 | 208:38 | 49.988
2020-08-25 | 209:38 | 49.992
2020-08-25 | 210:38 | 49.994
2020-08-25 | 211:38 | 49.996
2020-08-25 | 212:38 | 49.998
2020-08-25 | 213:38 | 49.998
2020-08-25 | 214:38 | 49.994
2020-08-25 | 215:38 | 49.991
2020-08-25 | 216:38 | 49.988
2020-08-25 | 217:38 | 49.986
2020-08-25 | 218:38 | 49.984
2020-08-25 | 219:38 | 49.981
2020-08-25 | 220:38 | 49.976
2020-08-25 | 221:38 | 49.974
2020-08-25 | 222:38 | 49.972
2020-08-25 | 223:38 | 49.972
2020-08-25 | 224:38 | 49.972
2020-08-25 | 225:38 | 49.973
2020-08-25 | 226:38 | 49.972
2020-08-25 | 227:38 | 49.971
2020-08-25 | 228:38 | 49.972
2020-08-25 | 229:38 | 49.973
2020-08-25 | 230:38 | 49.97
2020-08-25 | 231:38 | 49.972
2020-08-25 | 232:38 | 49.972
2020-08-25 | 233:38 | 49.973
2020-08-25 | 234:38 | 49.974
2020-08-25 | 235:38 | 49.975
2020-08-25 | 236:38 | 49.973
2020-08-25 | 237:38 | 49.972
2020-08-25 | 238:38 | 49.968
2020-08-25 | 239:38 | 49.967
2020-08-25 | 240:38 | 49.965
2020-08-25 | 241:38 | 49.968
2020-08-25 | 242:38 | 49.97
2020-08-25 | 243:38 | 49.971
2020-08-25 | 244:38 | 49.97
2020-08-25 | 245:38 | 49.968
2020-08-25 | 246:38 | 49.965
2020-08-25 | 247:38 | 49.964
2020-08-25 | 248:38 | 49.964
2020-08-25 | 249:38 | 49.963
2020-08-25 | 250:38 | 49.961
2020-08-25 | 251:38 | 49.961
2020-08-25 | 252:38 | 49.963
2020-08-25 | 253:38 | 49.966
2020-08-25 | 254:38 | 49.964
2020-08-25 | 255:38 | 49.963
2020-08-25 | 256:38 | 49.961
2020-08-25 | 257:38 | 49.96
2020-08-25 | 258:38 | 49.961
2020-08-25 | 259:38 | 49.962
2020-08-25 | 260:38 | 49.964
2020-08-25 | 261:38 | 49.967
2020-08-25 | 262:38 | 49.97
2020-08-25 | 263:38 | 49.972
2020-08-25 | 264:38 | 49.976
2020-08-25 | 265:38 | 49.976
2020-08-25 | 266:38 | 49.976
2020-08-25 | 267:38 | 49.978
2020-08-25 | 268:38 | 49.977
2020-08-25 | 269:38 | 49.977
2020-08-25 | 270:38 | 49.976
2020-08-25 | 271:38 | 49.977
2020-08-25 | 272:38 | 49.98
2020-08-25 | 273:38 | 49.981
2020-08-25 | 274:38 | 49.982
2020-08-25 | 275:38 | 49.984
2020-08-25 | 276:38 | 49.984
2020-08-25 | 277:38 | 49.982
2020-08-25 | 278:38 | 49.977
2020-08-25 | 279:38 | 49.975
2020-08-25 | 280:38 | 49.974
2020-08-25 | 281:38 | 49.973
2020-08-25 | 282:38 | 49.972
2020-08-25 | 283:38 | 49.971
2020-08-25 | 284:38 | 49.972
2020-08-25 | 285:38 | 49.973
2020-08-25 | 286:38 | 49.977
2020-08-25 | 287:38 | 49.976
2020-08-25 | 288:38 | 49.979
2020-08-25 | 289:38 | 49.981
2020-08-25 | 290:38 | 49.981
2020-08-25 | 291:38 | 49.982
2020-08-25 | 292:38 | 49.981
2020-08-25 | 293:38 | 49.98
2020-08-25 | 294:38 | 49.978
2020-08-25 | 295:38 | 49.978
2020-08-25 | 296:38 | 49.98
2020-08-25 | 297:38 | 49.981
2020-08-25 | 298:38 | 49.981
2020-08-25 | 299:38 | 49.98
2020-08-25 | 300:38 | 49.982
2020-08-25 | 301:38 | 49.98
2020-08-25 | 302:38 | 49.981
2020-08-25 | 303:38 | 49.98
2020-08-25 | 304:38 | 49.981
2020-08-25 | 305:38 | 49.981
2020-08-25 | 306:38 | 49.983
2020-08-25 | 307:38 | 49.982
2020-08-25 | 308:38 | 49.979
2020-08-25 | 309:38 | 49.976
2020-08-25 | 310:38 | 49.972
2020-08-25 | 311:38 | 49.967
2020-08-25 | 312:38 | 49.961
2020-08-25 | 313:38 | 49.957
2020-08-25 | 314:38 | 49.954
2020-08-25 | 315:38 | 49.954
2020-08-25 | 316:38 | 49.955
2020-08-25 | 317:38 | 49.958
2020-08-25 | 318:38 | 49.957
2020-08-25 | 319:38 | 49.956
2020-08-25 | 320:38 | 49.955
2020-08-25 | 321:38 | 49.954
2020-08-25 | 322:38 | 49.954
2020-08-25 | 323:38 | 49.955
2020-08-25 | 324:38 | 49.958
2020-08-25 | 325:38 | 49.958
2020-08-25 | 326:38 | 49.957
2020-08-25 | 327:38 | 49.96
2020-08-25 | 328:38 | 49.961
2020-08-25 | 329:38 | 49.961
2020-08-25 | 330:38 | 49.96
2020-08-25 | 331:38 | 49.962
2020-08-25 | 332:38 | 49.965
2020-08-25 | 333:38 | 49.967
2020-08-25 | 334:38 | 49.97
2020-08-25 | 335:38 | 49.972
2020-08-25 | 336:38 | 49.973
2020-08-25 | 337:38 | 49.972
2020-08-25 | 338:38 | 49.974
2020-08-25 | 339:38 | 49.971
2020-08-25 | 340:38 | 49.973
2020-08-25 | 341:38 | 49.975
2020-08-25 | 342:38 | 49.98
2020-08-25 | 343:38 | 49.983
2020-08-25 | 344:38 | 49.987
2020-08-25 | 345:38 | 49.991
2020-08-25 | 346:38 | 49.994
2020-08-25 | 347:38 | 49.995
2020-08-25 | 348:38 | 49.997
2020-08-25 | 349:38 | 49.998
2020-08-25 | 350:38 | 50
2020-08-25 | 351:38 | 50
2020-08-25 | 352:38 | 49.998
2020-08-25 | 353:38 | 49.997
2020-08-25 | 354:38 | 49.996
2020-08-25 | 355:38 | 49.995
2020-08-25 | 356:38 | 49.993
2020-08-25 | 357:38 | 49.987
2020-08-25 | 358:38 | 49.982
2020-08-25 | 359:38 | 49.981
2020-08-25 | 360:38 | 49.981
2020-08-25 | 361:38 | 49.982
2020-08-25 | 362:38 | 49.984
363:38
364:38
365:38
366:38
367:38
368:38
369:38
370:38
371:38
372:38
373:38
374:38
375:38
376:38
377:38
378:38
379:38
380:38
381:38
382:38
383:38
384:38
385:38
386:38
387:38
388:38
389:38
390:38
391:38
392:38
393:38
394:38
395:38
396:38
397:38
398:38
399:38
400:38
401:38
402:38
403:38
404:38
405:38
406:38
407:38
408:38
409:38
410:38
411:38
412:38
413:38
414:38
415:38
416:38
417:38
418:38
419:38
420:38
421:38
422:38
423:38
424:38
425:38
426:38
427:38
428:38
429:38
430:38
431:38
432:38
433:38
434:38
435:38
436:38
437:38
438:38
439:38
440:38
441:38
442:38
443:38
444:38
445:38
446:38
447:38
448:38
449:38
450:38
451:38
452:38
453:38
454:38
455:38
456:38
457:38
458:38
459:38
460:38
461:38
462:38
463:38
464:38
465:38
466:38
467:38
468:38
469:38
470:38
471:38
472:38
473:38
474:38
475:38
476:38
477:38
478:38
479:38
480:38
481:38
482:38
483:38
484:38
485:38
486:38
487:38
488:38
489:38
490:38
491:38
492:38
493:38
494:38
495:38
496:38
497:38
498:38
499:38
500:38
501:38
502:38
503:38
504:38
505:38
506:38
507:38
508:38
509:38
510:38
511:38
512:38
513:38
514:38
515:38
516:38
517:38
518:38
519:38
520:38
521:38
522:38
523:38
524:38
525:38
526:38
527:38
528:38
529:38
530:38
531:38
532:38
533:38
534:38
535:38
536:38
537:38
538:38
539:38
540:38
541:38
542:38
543:38
544:38
545:38
546:38
547:38
548:38
549:38
550:38
551:38
552:38
553:38
554:38
555:38
556:38
557:38
558:38
559:38
560:38
561:38
562:38
563:38
564:38
565:38
566:38
567:38
568:38
569:38
570:38
571:38
572:38
573:38
574:38
575:38
576:38
577:38
578:38
579:38
580:38
581:38
582:38
583:38
584:38
585:38
586:38
587:38
588:38
589:38
590:38
591:38
592:38
593:38
594:38
595:38
596:38
597:38
598:38
599:38
600:38
601:38
602:38
603:38
604:38
605:38
606:38
607:38
608:38
609:38
610:38
611:38
612:38
613:38
614:38
615:38
616:38
617:38
618:38
619:38
620:38
621:38
622:38
623:38
624:38
625:38
626:38
627:38
628:38
629:38
630:38
631:38
632:38
633:38
634:38
635:38
636:38
637:38
638:38
639:38
640:38
641:38
642:38
643:38
644:38
645:38
646:38
647:38
648:38
649:38
650:38
651:38
652:38
653:38
654:38
655:38
656:38
657:38
658:38
659:38
660:38
661:38
662:38
663:38
664:38
665:38
666:38
667:38
668:38
669:38
670:38
671:38
672:38
673:38
674:38
675:38
676:38
677:38
678:38
679:38
680:38
681:38
682:38
683:38
684:38
685:38
686:38
687:38
688:38
689:38
690:38
691:38
692:38
693:38
694:38
695:38
696:38
697:38
698:38
699:38
700:38
701:38
702:38
703:38
704:38
705:38
706:38
707:38
708:38
709:38
710:38
711:38
712:38
713:38
714:38
715:38
716:38
717:38
718:38
719:38
720:38
721:38
722:38
723:38
724:38
725:38
726:38
727:38
728:38
729:38
730:38
731:38
732:38
733:38
734:38
735:38
736:38
737:38
738:38
739:38
740:38
741:38
742:38
743:38
744:38
745:38
746:38
747:38
748:38
749:38
750:38
751:38
752:38
753:38
754:38
755:38
756:38
757:38
758:38
759:38
760:38
761:38
762:38
763:38
764:38
765:38
766:38
767:38
768:38
769:38
770:38
771:38
772:38
773:38
774:38
775:38
776:38
777:38
778:38
779:38
780:38
781:38
782:38
783:38
784:38
785:38
786:38
787:38
788:38
789:38
790:38
791:38
792:38
793:38
794:38
795:38
796:38
797:38
798:38
799:38
800:38
801:38
802:38
803:38
804:38
805:38
806:38
807:38
808:38
809:38
810:38
811:38
812:38
813:38
814:38
815:38
816:38
817:38
818:38
819:38
820:38
821:38
822:38
823:38
824:38
825:38
826:38
827:38
828:38
829:38
830:38
831:38
832:38
833:38
834:38
835:38
836:38
837:38
838:38
839:38
840:38
841:38
842:38
843:38
844:38
845:38
846:38
847:38
848:38
849:38
850:38
851:38
852:38
853:38
854:38
855:38
856:38
857:38
858:38
859:38
860:38
861:38
862:38
863:38
864:38
865:38
866:38
867:38
868:38
869:38
870:38
871:38
872:38
873:38
874:38
875:38
876:38
877:38
878:38
879:38
880:38
881:38
882:38
883:38
884:38
885:38
886:38
887:38
888:38
889:38
890:38
891:38
892:38
893:38
894:38
895:38
896:38
897:38
898:38
899:38
900:38
901:38
902:38

## Event 20200827-1
In UTC
Date | Time | Freq
2020-08-27 | 10:11 | 50.061
2020-08-27 | 10:11 | 50.059
2020-08-27 | 10:11 | 50.056
2020-08-27 | 10:11 | 50.055
2020-08-27 | 10:11 | 50.05
2020-08-27 | 11:11 | 50.046
2020-08-27 | 12:11 | 50.043
2020-08-27 | 13:11 | 50.041
2020-08-27 | 14:11 | 50.036
2020-08-27 | 15:11 | 50.034
2020-08-27 | 16:11 | 50.033
2020-08-27 | 17:11 | 50.033
2020-08-27 | 18:11 | 50.034
2020-08-27 | 19:11 | 50.034
2020-08-27 | 20:11 | 50.034
2020-08-27 | 21:11 | 50.033
2020-08-27 | 22:11 | 50.03
2020-08-27 | 23:11 | 50.028
2020-08-27 | 24:11 | 50.027
2020-08-27 | 25:11 | 50.025
2020-08-27 | 26:11 | 50.025
2020-08-27 | 27:11 | 50.027
2020-08-27 | 28:11 | 50.028
2020-08-27 | 29:11 | 50.027
2020-08-27 | 30:11 | 50.029
2020-08-27 | 31:11 | 50.029
2020-08-27 | 32:11 | 50.03
2020-08-27 | 33:11 | 50.014
2020-08-27 | 34:11 | 49.987
2020-08-27 | 35:11 | 49.963
2020-08-27 | 36:11 | 49.944
2020-08-27 | 37:11 | 49.925
2020-08-27 | 38:11 | 49.913
2020-08-27 | 39:11 | 49.904
2020-08-27 | 40:11 | 49.897
2020-08-27 | 41:11 | 49.89
2020-08-27 | 42:11 | 49.887
2020-08-27 | 43:11 | 49.884
2020-08-27 | 44:11 | 49.882
2020-08-27 | 45:11 | 49.881
2020-08-27 | 46:11 | 49.881
2020-08-27 | 47:11 | 49.88
2020-08-27 | 48:11 | 49.881
2020-08-27 | 49:11 | 49.881
2020-08-27 | 50:11 | 49.881
2020-08-27 | 51:11 | 49.881
2020-08-27 | 52:11 | 49.883
2020-08-27 | 53:11 | 49.884
2020-08-27 | 54:11 | 49.885
2020-08-27 | 55:11 | 49.886
2020-08-27 | 56:11 | 49.888
2020-08-27 | 57:11 | 49.889
2020-08-27 | 58:11 | 49.89
2020-08-27 | 59:11 | 49.89
2020-08-27 | 60:11 | 49.891
2020-08-27 | 61:11 | 49.889
2020-08-27 | 62:11 | 49.89
2020-08-27 | 63:11 | 49.888
2020-08-27 | 64:11 | 49.889
2020-08-27 | 65:11 | 49.889
2020-08-27 | 66:11 | 49.888
2020-08-27 | 67:11 | 49.889
2020-08-27 | 68:11 | 49.888
2020-08-27 | 69:11 | 49.888
2020-08-27 | 70:11 | 49.888
2020-08-27 | 71:11 | 49.888
2020-08-27 | 72:11 | 49.887
2020-08-27 | 73:11 | 49.887
2020-08-27 | 74:11 | 49.886
2020-08-27 | 75:11 | 49.883
2020-08-27 | 76:11 | 49.88
2020-08-27 | 77:11 | 49.876
2020-08-27 | 78:11 | 49.873
2020-08-27 | 79:11 | 49.867
2020-08-27 | 80:11 | 49.863
2020-08-27 | 81:11 | 49.858
2020-08-27 | 82:11 | 49.855
2020-08-27 | 83:11 | 49.849
2020-08-27 | 84:11 | 49.845
2020-08-27 | 85:11 | 49.841
2020-08-27 | 86:11 | 49.837
2020-08-27 | 87:11 | 49.834
2020-08-27 | 88:11 | 49.832
2020-08-27 | 89:11 | 49.831
2020-08-27 | 90:11 | 49.831
2020-08-27 | 91:11 | 49.832
2020-08-27 | 92:11 | 49.838
2020-08-27 | 93:11 | 49.843
2020-08-27 | 94:11 | 49.851
2020-08-27 | 95:11 | 49.857
2020-08-27 | 96:11 | 49.867
2020-08-27 | 97:11 | 49.878
2020-08-27 | 98:11 | 49.887
2020-08-27 | 99:11 | 49.899
2020-08-27 | 100:11 | 49.91
2020-08-27 | 101:11 | 49.92
2020-08-27 | 102:11 | 49.932
2020-08-27 | 103:11 | 49.938
2020-08-27 | 104:11 | 49.944
2020-08-27 | 105:11 | 49.95
2020-08-27 | 106:11 | 49.955
2020-08-27 | 107:11 | 49.959
2020-08-27 | 108:11 | 49.965
2020-08-27 | 109:11 | 49.97
2020-08-27 | 110:11 | 49.976
2020-08-27 | 111:11 | 49.981
2020-08-27 | 112:11 | 49.988
2020-08-27 | 113:11 | 49.993
2020-08-27 | 114:11 | 49.997
2020-08-27 | 115:11 | 50
2020-08-27 | 116:11 | 50.003
2020-08-27 | 117:11 | 50.005
2020-08-27 | 118:11 | 50.008
2020-08-27 | 119:11 | 50.011
2020-08-27 | 120:11 | 50.011
2020-08-27 | 121:11 | 50.01
2020-08-27 | 122:11 | 50.01
2020-08-27 | 123:11 | 50.01
2020-08-27 | 124:11 | 50.009
2020-08-27 | 125:11 | 50.008
2020-08-27 | 126:11 | 50.005
2020-08-27 | 127:11 | 50.001
2020-08-27 | 128:11 | 50
2020-08-27 | 129:11 | 49.992
2020-08-27 | 130:11 | 49.986
2020-08-27 | 131:11 | 49.98
2020-08-27 | 132:11 | 49.976
2020-08-27 | 133:11 | 49.972
2020-08-27 | 134:11 | 49.968
2020-08-27 | 135:11 | 49.964
2020-08-27 | 136:11 | 49.961
2020-08-27 | 137:11 | 49.959
2020-08-27 | 138:11 | 49.956
2020-08-27 | 139:11 | 49.955
2020-08-27 | 140:11 | 49.951
2020-08-27 | 141:11 | 49.95
2020-08-27 | 142:11 | 49.948
2020-08-27 | 143:11 | 49.946
2020-08-27 | 144:11 | 49.944
2020-08-27 | 145:11 | 49.943
2020-08-27 | 146:11 | 49.942
2020-08-27 | 147:11 | 49.938
2020-08-27 | 148:11 | 49.936
2020-08-27 | 149:11 | 49.935
2020-08-27 | 150:11 | 49.935
2020-08-27 | 151:11 | 49.936
2020-08-27 | 152:11 | 49.935
2020-08-27 | 153:11 | 49.939
2020-08-27 | 154:11 | 49.936
2020-08-27 | 155:11 | 49.937
2020-08-27 | 156:11 | 49.935
2020-08-27 | 157:11 | 49.935
2020-08-27 | 158:11 | 49.933
2020-08-27 | 159:11 | 49.934
2020-08-27 | 160:11 | 49.934
2020-08-27 | 161:11 | 49.933
2020-08-27 | 162:11 | 49.933
2020-08-27 | 163:11 | 49.933
2020-08-27 | 164:11 | 49.932
2020-08-27 | 165:11 | 49.933
2020-08-27 | 166:11 | 49.933
2020-08-27 | 167:11 | 49.935
2020-08-27 | 168:11 | 49.938
2020-08-27 | 169:11 | 49.938
2020-08-27 | 170:11 | 49.94
2020-08-27 | 171:11 | 49.94
2020-08-27 | 172:11 | 49.938
2020-08-27 | 173:11 | 49.938
2020-08-27 | 174:11 | 49.94
2020-08-27 | 175:11 | 49.937
2020-08-27 | 176:11 | 49.936
2020-08-27 | 177:11 | 49.935
2020-08-27 | 178:11 | 49.936
2020-08-27 | 179:11 | 49.939
2020-08-27 | 180:11 | 49.94
2020-08-27 | 181:11 | 49.943
2020-08-27 | 182:11 | 49.948
2020-08-27 | 183:11 | 49.953
2020-08-27 | 184:11 | 49.957
2020-08-27 | 185:11 | 49.959
186:11
187:11
188:11
189:11
190:11
191:11
192:11
193:11
194:11
195:11
196:11
197:11
198:11
199:11
200:11
201:11
202:11
203:11
204:11
205:11
206:11
207:11
208:11
209:11
210:11
211:11
212:11
213:11
214:11
215:11
216:11
217:11
218:11
219:11
220:11
221:11
222:11
223:11
224:11
225:11
226:11
227:11
228:11
229:11
230:11
231:11
232:11
233:11
234:11
235:11
236:11
237:11
238:11
239:11
240:11
241:11
242:11
243:11
244:11
245:11
246:11
247:11
248:11
249:11
250:11
251:11
252:11
253:11
254:11
255:11
256:11
257:11
258:11
259:11
260:11
261:11
262:11
263:11
264:11
265:11
266:11
267:11
268:11
269:11
270:11
271:11
272:11
273:11
274:11
275:11
276:11
277:11
278:11
279:11
280:11
281:11
282:11
283:11
284:11
285:11
286:11
287:11
288:11
289:11
290:11
291:11
292:11
293:11
294:11
295:11
296:11
297:11
298:11
299:11
300:11
301:11
302:11
303:11
304:11
305:11
306:11
307:11
308:11
309:11
310:11
311:11
312:11
313:11
314:11
315:11
316:11
317:11
318:11
319:11
320:11
321:11
322:11
323:11
324:11
325:11
326:11
327:11
328:11
329:11
330:11
331:11
332:11
333:11
334:11
335:11
336:11
337:11
338:11
339:11
340:11
341:11
342:11
343:11
344:11
345:11
346:11
347:11
348:11
349:11
350:11
351:11
352:11
353:11
354:11
355:11
356:11
357:11
358:11
359:11
360:11
361:11
362:11
363:11
364:11
365:11
366:11
367:11
368:11
369:11
370:11
371:11
372:11
373:11
374:11
375:11
376:11
377:11
378:11
379:11
380:11
381:11
382:11
383:11
384:11
385:11
386:11
387:11
388:11
389:11
390:11
391:11
392:11
393:11
394:11
395:11
396:11
397:11
398:11
399:11
400:11
401:11
402:11
403:11
404:11
405:11
406:11
407:11
408:11
409:11
410:11
411:11
412:11
413:11
414:11
415:11
416:11
417:11
418:11
419:11
420:11
421:11
422:11
423:11
424:11
425:11
426:11
427:11
428:11
429:11
430:11
431:11
432:11
433:11
434:11
435:11
436:11
437:11
438:11
439:11
440:11
441:11
442:11
443:11
444:11
445:11
446:11
447:11
448:11
449:11
450:11
451:11
452:11
453:11
454:11
455:11
456:11
457:11
458:11
459:11
460:11
461:11
462:11
463:11
464:11
465:11
466:11
467:11
468:11
469:11
470:11
471:11
472:11
473:11
474:11
475:11
476:11
477:11
478:11
479:11
480:11
481:11
482:11
483:11
484:11
485:11
486:11
487:11
488:11
489:11
490:11
491:11
492:11
493:11
494:11
495:11
496:11
497:11
498:11
499:11
500:11
501:11
502:11
503:11
504:11
505:11
506:11
507:11
508:11
509:11
510:11
511:11
512:11
513:11
514:11
515:11
516:11
517:11
518:11
519:11
520:11
521:11
522:11
523:11
524:11
525:11
526:11
527:11
528:11
529:11
530:11
531:11
532:11
533:11
534:11
535:11
536:11
537:11
538:11
539:11
540:11
541:11
542:11
543:11
544:11
545:11
546:11
547:11
548:11
549:11
550:11
551:11
552:11
553:11
554:11
555:11
556:11
557:11
558:11
559:11
560:11
561:11
562:11
563:11
564:11
565:11
566:11
567:11
568:11
569:11
570:11
571:11
572:11
573:11
574:11
575:11
576:11
577:11
578:11
579:11
580:11
581:11
582:11
583:11
584:11
585:11
586:11
587:11
588:11
589:11
590:11
591:11
592:11
593:11
594:11
595:11
596:11
597:11
598:11
599:11
600:11
601:11
602:11
603:11
604:11
605:11
606:11
607:11
608:11
609:11
610:11
611:11
612:11
613:11
614:11
615:11
616:11
617:11
618:11
619:11
620:11
621:11
622:11
623:11
624:11
625:11
626:11
627:11
628:11
629:11
630:11
631:11
632:11
633:11
634:11
635:11
636:11
637:11
638:11
639:11
640:11
641:11
642:11
643:11
644:11
645:11
646:11
647:11
648:11
649:11
650:11
651:11
652:11
653:11
654:11
655:11
656:11
657:11
658:11
659:11
660:11
661:11
662:11
663:11
664:11
665:11
666:11
667:11
668:11
669:11
670:11
671:11
672:11
673:11
674:11
675:11
676:11
677:11
678:11
679:11
680:11
681:11
682:11
683:11
684:11
685:11
686:11
687:11
688:11
689:11
690:11
691:11
692:11
693:11
694:11
695:11
696:11
697:11
698:11
699:11
700:11
701:11
702:11
703:11
704:11
705:11
706:11
707:11
708:11
709:11
710:11
711:11
712:11
713:11
714:11
715:11
716:11
717:11
718:11
719:11
720:11
721:11
722:11
723:11
724:11
725:11
726:11
727:11
728:11
729:11
730:11
731:11
732:11
733:11
734:11
735:11
736:11
737:11
738:11
739:11
740:11
741:11
742:11
743:11
744:11
745:11
746:11
747:11
748:11
749:11
750:11
751:11
752:11
753:11
754:11
755:11
756:11
757:11
758:11
759:11
760:11
761:11
762:11
763:11
764:11
765:11
766:11
767:11
768:11
769:11
770:11
771:11
772:11
773:11
774:11
775:11
776:11
777:11
778:11
779:11
780:11
781:11
782:11
783:11
784:11
785:11
786:11
787:11
788:11
789:11
790:11
791:11
792:11
793:11
794:11
795:11
796:11
797:11
798:11
799:11
800:11
801:11
802:11
803:11
804:11
805:11
806:11
807:11
808:11
809:11
810:11
811:11
812:11
813:11
814:11
815:11
816:11
817:11
818:11
819:11
820:11
821:11
822:11
823:11
824:11
825:11
826:11
827:11
828:11
829:11
830:11
831:11
832:11
833:11
834:11
835:11
836:11
837:11
838:11
839:11
840:11
841:11
842:11
843:11
844:11
845:11
846:11
847:11
848:11
849:11
850:11
851:11
852:11
853:11
854:11
855:11
856:11
857:11
858:11
859:11
860:11
861:11
862:11
863:11
864:11
865:11
866:11
867:11
868:11
869:11
870:11
871:11
872:11
873:11
874:11
875:11
876:11
877:11
878:11
879:11
880:11
881:11
882:11
883:11
884:11
885:11
886:11
887:11
888:11
889:11
890:11
891:11
892:11
893:11
894:11
895:11
896:11
897:11
898:11
899:11
900:11
901:11
902:11
903:11
904:11
905:11

## Event 20200829-1
In UTC
Date | Time | Freq
2020-08-29 | 5:51 | 50.045
2020-08-29 | 5:51 | 50.045
2020-08-29 | 5:51 | 50.044
2020-08-29 | 5:51 | 50.044
2020-08-29 | 5:51 | 50.045
2020-08-29 | 6:51 | 50.044
2020-08-29 | 7:51 | 50.045
2020-08-29 | 8:51 | 50.045
2020-08-29 | 9:51 | 50.043
2020-08-29 | 10:51 | 50.04
2020-08-29 | 11:51 | 50.034
2020-08-29 | 12:51 | 50.028
2020-08-29 | 13:51 | 50.023
2020-08-29 | 14:51 | 50.022
2020-08-29 | 15:51 | 50.021
2020-08-29 | 16:51 | 50.019
2020-08-29 | 17:51 | 50.021
2020-08-29 | 18:51 | 50.021
2020-08-29 | 19:51 | 50.023
2020-08-29 | 20:51 | 50.023
2020-08-29 | 21:51 | 50.019
2020-08-29 | 22:51 | 50.017
2020-08-29 | 23:51 | 50.014
2020-08-29 | 24:51 | 50.013
2020-08-29 | 25:51 | 50.014
2020-08-29 | 26:51 | 50.014
2020-08-29 | 27:51 | 50.015
2020-08-29 | 28:51 | 50.015
2020-08-29 | 29:51 | 50.015
2020-08-29 | 30:51 | 50.014
2020-08-29 | 31:51 | 50.011
2020-08-29 | 32:51 | 50.008
2020-08-29 | 33:51 | 50.003
2020-08-29 | 34:51 | 49.998
2020-08-29 | 35:51 | 49.991
2020-08-29 | 36:51 | 49.984
2020-08-29 | 37:51 | 49.982
2020-08-29 | 38:51 | 49.981
2020-08-29 | 39:51 | 49.982
2020-08-29 | 40:51 | 49.982
2020-08-29 | 41:51 | 49.983
2020-08-29 | 42:51 | 49.985
2020-08-29 | 43:51 | 49.986
2020-08-29 | 44:51 | 49.987
2020-08-29 | 45:51 | 49.991
2020-08-29 | 46:51 | 49.997
2020-08-29 | 47:51 | 50.008
2020-08-29 | 48:51 | 50.017
2020-08-29 | 49:51 | 50.025
2020-08-29 | 50:51 | 50.029
2020-08-29 | 51:51 | 50.029
2020-08-29 | 52:51 | 50.028
2020-08-29 | 53:51 | 50.026
2020-08-29 | 54:51 | 50.028
2020-08-29 | 55:51 | 50.028
2020-08-29 | 56:51 | 50.03
2020-08-29 | 57:51 | 50.032
2020-08-29 | 58:51 | 50.033
2020-08-29 | 59:51 | 50.032
2020-08-29 | 60:51 | 50.029
2020-08-29 | 61:51 | 50.027
2020-08-29 | 62:51 | 50.029
2020-08-29 | 63:51 | 50.027
2020-08-29 | 64:51 | 50.027
2020-08-29 | 65:51 | 50.03
2020-08-29 | 66:51 | 50.029
2020-08-29 | 67:51 | 50.029
2020-08-29 | 68:51 | 50.032
2020-08-29 | 69:51 | 50.033
2020-08-29 | 70:51 | 50.037
2020-08-29 | 71:51 | 50.042
2020-08-29 | 72:51 | 50.045
2020-08-29 | 73:51 | 50.049
2020-08-29 | 74:51 | 50.052
2020-08-29 | 75:51 | 50.053
2020-08-29 | 76:51 | 50.056
2020-08-29 | 77:51 | 50.058
2020-08-29 | 78:51 | 50.06
2020-08-29 | 79:51 | 50.062
2020-08-29 | 80:51 | 50.062
2020-08-29 | 81:51 | 50.065
2020-08-29 | 82:51 | 50.068
2020-08-29 | 83:51 | 50.073
2020-08-29 | 84:51 | 50.076
2020-08-29 | 85:51 | 50.075
2020-08-29 | 86:51 | 50.077
2020-08-29 | 87:51 | 50.077
2020-08-29 | 88:51 | 50.076
2020-08-29 | 89:51 | 50.075
2020-08-29 | 90:51 | 50.075
2020-08-29 | 91:51 | 50.075
2020-08-29 | 92:51 | 50.074
2020-08-29 | 93:51 | 50.074
2020-08-29 | 94:51 | 50.073
2020-08-29 | 95:51 | 50.068
2020-08-29 | 96:51 | 50.067
2020-08-29 | 97:51 | 50.066
2020-08-29 | 98:51 | 50.066
2020-08-29 | 99:51 | 50.065
2020-08-29 | 100:51 | 50.064
2020-08-29 | 101:51 | 50.059
2020-08-29 | 102:51 | 50.058
2020-08-29 | 103:51 | 50.057
2020-08-29 | 104:51 | 50.055
2020-08-29 | 105:51 | 50.054
2020-08-29 | 106:51 | 50.057
2020-08-29 | 107:51 | 50.057
2020-08-29 | 108:51 | 50.058
2020-08-29 | 109:51 | 50.058
2020-08-29 | 110:51 | 50.057
2020-08-29 | 111:51 | 50.056
2020-08-29 | 112:51 | 50.055
2020-08-29 | 113:51 | 50.054
2020-08-29 | 114:51 | 50.055
2020-08-29 | 115:51 | 50.055
2020-08-29 | 116:51 | 50.053
2020-08-29 | 117:51 | 50.055
2020-08-29 | 118:51 | 50.054
2020-08-29 | 119:51 | 50.053
2020-08-29 | 120:51 | 50.051
2020-08-29 | 121:51 | 50.048
2020-08-29 | 122:51 | 50.049
2020-08-29 | 123:51 | 50.051
2020-08-29 | 124:51 | 50.051
2020-08-29 | 125:51 | 50.051
2020-08-29 | 126:51 | 50.051
2020-08-29 | 127:51 | 50.051
2020-08-29 | 128:51 | 50.053
2020-08-29 | 129:51 | 50.05
2020-08-29 | 130:51 | 50.046
2020-08-29 | 131:51 | 50.044
2020-08-29 | 132:51 | 50.043
2020-08-29 | 133:51 | 50.045
2020-08-29 | 134:51 | 50.046
2020-08-29 | 135:51 | 50.046
2020-08-29 | 136:51 | 50.044
2020-08-29 | 137:51 | 50.043
2020-08-29 | 138:51 | 50.044
2020-08-29 | 139:51 | 50.045
2020-08-29 | 140:51 | 50.045
2020-08-29 | 141:51 | 50.048
2020-08-29 | 142:51 | 50.05
2020-08-29 | 143:51 | 50.054
2020-08-29 | 144:51 | 50.057
2020-08-29 | 145:51 | 50.058
2020-08-29 | 146:51 | 50.061
2020-08-29 | 147:51 | 50.063
2020-08-29 | 148:51 | 50.064
2020-08-29 | 149:51 | 50.065
2020-08-29 | 150:51 | 50.064
2020-08-29 | 151:51 | 50.065
2020-08-29 | 152:51 | 50.065
2020-08-29 | 153:51 | 50.064
2020-08-29 | 154:51 | 50.066
2020-08-29 | 155:51 | 50.067
2020-08-29 | 156:51 | 50.067
2020-08-29 | 157:51 | 50.066
2020-08-29 | 158:51 | 50.065
2020-08-29 | 159:51 | 50.063
2020-08-29 | 160:51 | 50.065
2020-08-29 | 161:51 | 50.067
2020-08-29 | 162:51 | 50.067
2020-08-29 | 163:51 | 50.068
2020-08-29 | 164:51 | 50.068
2020-08-29 | 165:51 | 50.067
2020-08-29 | 166:51 | 50.067
2020-08-29 | 167:51 | 50.066
2020-08-29 | 168:51 | 50.065
2020-08-29 | 169:51 | 50.061
2020-08-29 | 170:51 | 50.06
2020-08-29 | 171:51 | 50.058
2020-08-29 | 172:51 | 50.057
2020-08-29 | 173:51 | 50.055
2020-08-29 | 174:51 | 50.054
2020-08-29 | 175:51 | 50.054
2020-08-29 | 176:51 | 50.055
2020-08-29 | 177:51 | 50.055
2020-08-29 | 178:51 | 50.056
2020-08-29 | 179:51 | 50.058
2020-08-29 | 180:51 | 50.057
2020-08-29 | 181:51 | 50.058
2020-08-29 | 182:51 | 50.06
2020-08-29 | 183:51 | 50.057
2020-08-29 | 184:51 | 50.056
2020-08-29 | 185:51 | 50.055
2020-08-29 | 186:51 | 50.052
2020-08-29 | 187:51 | 50.05
2020-08-29 | 188:51 | 50.048
2020-08-29 | 189:51 | 50.048
2020-08-29 | 190:51 | 50.048
2020-08-29 | 191:51 | 50.049
2020-08-29 | 192:51 | 50.047
2020-08-29 | 193:51 | 50.046
2020-08-29 | 194:51 | 50.043
2020-08-29 | 195:51 | 50.04
2020-08-29 | 196:51 | 50.042
2020-08-29 | 197:51 | 50.046
2020-08-29 | 198:51 | 50.05
2020-08-29 | 199:51 | 50.055
2020-08-29 | 200:51 | 50.058
2020-08-29 | 201:51 | 50.059
2020-08-29 | 202:51 | 50.06
2020-08-29 | 203:51 | 50.058
2020-08-29 | 204:51 | 50.056
2020-08-29 | 205:51 | 50.058
2020-08-29 | 206:51 | 50.057
2020-08-29 | 207:51 | 50.057
2020-08-29 | 208:51 | 50.06
2020-08-29 | 209:51 | 50.06
2020-08-29 | 210:51 | 50.058
2020-08-29 | 211:51 | 50.057
2020-08-29 | 212:51 | 50.056
2020-08-29 | 213:51 | 50.054
2020-08-29 | 214:51 | 50.052
2020-08-29 | 215:51 | 50.051
2020-08-29 | 216:51 | 50.049
2020-08-29 | 217:51 | 50.049
2020-08-29 | 218:51 | 50.051
2020-08-29 | 219:51 | 50.052
2020-08-29 | 220:51 | 50.053
2020-08-29 | 221:51 | 50.055
2020-08-29 | 222:51 | 50.058
2020-08-29 | 223:51 | 50.062
2020-08-29 | 224:51 | 50.064
2020-08-29 | 225:51 | 50.065
2020-08-29 | 226:51 | 50.068
2020-08-29 | 227:51 | 50.072
2020-08-29 | 228:51 | 50.074
2020-08-29 | 229:51 | 50.074
2020-08-29 | 230:51 | 50.076
2020-08-29 | 231:51 | 50.077
2020-08-29 | 232:51 | 50.077
2020-08-29 | 233:51 | 50.077
2020-08-29 | 234:51 | 50.079
2020-08-29 | 235:51 | 50.082
2020-08-29 | 236:51 | 50.084
2020-08-29 | 237:51 | 50.086
2020-08-29 | 238:51 | 50.089
2020-08-29 | 239:51 | 50.091
2020-08-29 | 240:51 | 50.092
2020-08-29 | 241:51 | 50.093
2020-08-29 | 242:51 | 50.092
2020-08-29 | 243:51 | 50.088
2020-08-29 | 244:51 | 50.083
2020-08-29 | 245:51 | 50.081
2020-08-29 | 246:51 | 50.077
2020-08-29 | 247:51 | 50.076
2020-08-29 | 248:51 | 50.074
2020-08-29 | 249:51 | 50.074
2020-08-29 | 250:51 | 50.074
2020-08-29 | 251:51 | 50.077
2020-08-29 | 252:51 | 50.08
2020-08-29 | 253:51 | 50.081
2020-08-29 | 254:51 | 50.083
2020-08-29 | 255:51 | 50.084
2020-08-29 | 256:51 | 50.082
2020-08-29 | 257:51 | 50.082
2020-08-29 | 258:51 | 50.083
2020-08-29 | 259:51 | 50.084
2020-08-29 | 260:51 | 50.086
2020-08-29 | 261:51 | 50.084
2020-08-29 | 262:51 | 50.082
2020-08-29 | 263:51 | 50.079
2020-08-29 | 264:51 | 50.077
2020-08-29 | 265:51 | 50.074
2020-08-29 | 266:51 | 50.071
2020-08-29 | 267:51 | 50.073
2020-08-29 | 268:51 | 50.072
2020-08-29 | 269:51 | 50.072
2020-08-29 | 270:51 | 50.073
2020-08-29 | 271:51 | 50.073
2020-08-29 | 272:51 | 50.074
2020-08-29 | 273:51 | 50.073
2020-08-29 | 274:51 | 50.072
2020-08-29 | 275:51 | 50.075
2020-08-29 | 276:51 | 50.076
2020-08-29 | 277:51 | 50.076
2020-08-29 | 278:51 | 50.078
2020-08-29 | 279:51 | 50.081
2020-08-29 | 280:51 | 50.085
2020-08-29 | 281:51 | 50.089
2020-08-29 | 282:51 | 50.092
2020-08-29 | 283:51 | 50.096
2020-08-29 | 284:51 | 50.097
2020-08-29 | 285:51 | 50.1
2020-08-29 | 286:51 | 50.1
2020-08-29 | 287:51 | 50.102
2020-08-29 | 288:51 | 50.1
2020-08-29 | 289:51 | 50.099
2020-08-29 | 290:51 | 50.1
2020-08-29 | 291:51 | 50.1
2020-08-29 | 292:51 | 50.104
2020-08-29 | 293:51 | 50.106
2020-08-29 | 294:51 | 50.108
2020-08-29 | 295:51 | 50.109
2020-08-29 | 296:51 | 50.11
2020-08-29 | 297:51 | 50.109
2020-08-29 | 298:51 | 50.108
2020-08-29 | 299:51 | 50.107
2020-08-29 | 300:51 | 50.107
2020-08-29 | 301:51 | 50.105
2020-08-29 | 302:51 | 50.104
2020-08-29 | 303:51 | 50.104
2020-08-29 | 304:51 | 50.1
2020-08-29 | 305:51 | 50.099
2020-08-29 | 306:51 | 50.097
2020-08-29 | 307:51 | 50.094
2020-08-29 | 308:51 | 50.094
2020-08-29 | 309:51 | 50.091
2020-08-29 | 310:51 | 50.092
2020-08-29 | 311:51 | 50.093
2020-08-29 | 312:51 | 50.092
2020-08-29 | 313:51 | 50.091
2020-08-29 | 314:51 | 50.091
2020-08-29 | 315:51 | 50.091
2020-08-29 | 316:51 | 50.094
2020-08-29 | 317:51 | 50.095
2020-08-29 | 318:51 | 50.096
2020-08-29 | 319:51 | 50.097
2020-08-29 | 320:51 | 50.094
2020-08-29 | 321:51 | 50.097
2020-08-29 | 322:51 | 50.097
2020-08-29 | 323:51 | 50.096
2020-08-29 | 324:51 | 50.097
2020-08-29 | 325:51 | 50.097
2020-08-29 | 326:51 | 50.1
2020-08-29 | 327:51 | 50.104
2020-08-29 | 328:51 | 50.106
2020-08-29 | 329:51 | 50.109
2020-08-29 | 330:51 | 50.11
2020-08-29 | 331:51 | 50.111
2020-08-29 | 332:51 | 50.111
2020-08-29 | 333:51 | 50.114
2020-08-29 | 334:51 | 50.118
2020-08-29 | 335:51 | 50.12
2020-08-29 | 336:51 | 50.121
2020-08-29 | 337:51 | 50.121
2020-08-29 | 338:51 | 50.119
2020-08-29 | 339:51 | 50.117
2020-08-29 | 340:51 | 50.113
2020-08-29 | 341:51 | 50.113
2020-08-29 | 342:51 | 50.115
2020-08-29 | 343:51 | 50.113
2020-08-29 | 344:51 | 50.113
2020-08-29 | 345:51 | 50.113
2020-08-29 | 346:51 | 50.111
2020-08-29 | 347:51 | 50.109
2020-08-29 | 348:51 | 50.105
2020-08-29 | 349:51 | 50.104
2020-08-29 | 350:51 | 50.103
2020-08-29 | 351:51 | 50.1
2020-08-29 | 352:51 | 50.099
2020-08-29 | 353:51 | 50.098
2020-08-29 | 354:51 | 50.1
2020-08-29 | 355:51 | 50.104
2020-08-29 | 356:51 | 50.106
2020-08-29 | 357:51 | 50.108
2020-08-29 | 358:51 | 50.108
2020-08-29 | 359:51 | 50.107
2020-08-29 | 360:51 | 50.108
2020-08-29 | 361:51 | 50.106
2020-08-29 | 362:51 | 50.104
2020-08-29 | 363:51 | 50.102
2020-08-29 | 364:51 | 50.099
2020-08-29 | 365:51 | 50.101
2020-08-29 | 366:51 | 50.103
2020-08-29 | 367:51 | 50.104
2020-08-29 | 368:51 | 50.106
2020-08-29 | 369:51 | 50.106
2020-08-29 | 370:51 | 50.105
2020-08-29 | 371:51 | 50.104
2020-08-29 | 372:51 | 50.101
2020-08-29 | 373:51 | 50.099
2020-08-29 | 374:51 | 50.099
2020-08-29 | 375:51 | 50.098
2020-08-29 | 376:51 | 50.095
2020-08-29 | 377:51 | 50.094
2020-08-29 | 378:51 | 50.092
2020-08-29 | 379:51 | 50.089
2020-08-29 | 380:51 | 50.089
2020-08-29 | 381:51 | 50.089
2020-08-29 | 382:51 | 50.086
2020-08-29 | 383:51 | 50.085
2020-08-29 | 384:51 | 50.087
2020-08-29 | 385:51 | 50.094
2020-08-29 | 386:51 | 50.098
2020-08-29 | 387:51 | 50.1
2020-08-29 | 388:51 | 50.104
2020-08-29 | 389:51 | 50.103
2020-08-29 | 390:51 | 50.102
2020-08-29 | 391:51 | 50.101
2020-08-29 | 392:51 | 50.095
2020-08-29 | 393:51 | 50.092
2020-08-29 | 394:51 | 50.089
2020-08-29 | 395:51 | 50.087
2020-08-29 | 396:51 | 50.085
2020-08-29 | 397:51 | 50.082
2020-08-29 | 398:51 | 50.081
2020-08-29 | 399:51 | 50.081
2020-08-29 | 400:51 | 50.084
2020-08-29 | 401:51 | 50.086
2020-08-29 | 402:51 | 50.085
2020-08-29 | 403:51 | 50.087
2020-08-29 | 404:51 | 50.086
2020-08-29 | 405:51 | 50.085
2020-08-29 | 406:51 | 50.083
2020-08-29 | 407:51 | 50.081
2020-08-29 | 408:51 | 50.082
2020-08-29 | 409:51 | 50.081
2020-08-29 | 410:51 | 50.079
2020-08-29 | 411:51 | 50.079
2020-08-29 | 412:51 | 50.078
2020-08-29 | 413:51 | 50.075
2020-08-29 | 414:51 | 50.074
2020-08-29 | 415:51 | 50.07
2020-08-29 | 416:51 | 50.065
2020-08-29 | 417:51 | 50.063
2020-08-29 | 418:51 | 50.061
2020-08-29 | 419:51 | 50.064
2020-08-29 | 420:51 | 50.066
2020-08-29 | 421:51 | 50.071
2020-08-29 | 422:51 | 50.074
2020-08-29 | 423:51 | 50.075
2020-08-29 | 424:51 | 50.076
2020-08-29 | 425:51 | 50.077
2020-08-29 | 426:51 | 50.08
2020-08-29 | 427:51 | 50.081
2020-08-29 | 428:51 | 50.084
2020-08-29 | 429:51 | 50.084
2020-08-29 | 430:51 | 50.086
2020-08-29 | 431:51 | 50.087
2020-08-29 | 432:51 | 50.087
2020-08-29 | 433:51 | 50.087
2020-08-29 | 434:51 | 50.088
2020-08-29 | 435:51 | 50.091
2020-08-29 | 436:51 | 50.093
2020-08-29 | 437:51 | 50.092
2020-08-29 | 438:51 | 50.091
2020-08-29 | 439:51 | 50.086
2020-08-29 | 440:51 | 50.083
2020-08-29 | 441:51 | 50.078
2020-08-29 | 442:51 | 50.073
2020-08-29 | 443:51 | 50.072
2020-08-29 | 444:51 | 50.07
2020-08-29 | 445:51 | 50.071
2020-08-29 | 446:51 | 50.075
2020-08-29 | 447:51 | 50.074
2020-08-29 | 448:51 | 50.074
2020-08-29 | 449:51 | 50.075
2020-08-29 | 450:51 | 50.074
2020-08-29 | 451:51 | 50.077
2020-08-29 | 452:51 | 50.08
2020-08-29 | 453:51 | 50.082
2020-08-29 | 454:51 | 50.087
2020-08-29 | 455:51 | 50.088
2020-08-29 | 456:51 | 50.089
2020-08-29 | 457:51 | 50.089
2020-08-29 | 458:51 | 50.087
2020-08-29 | 459:51 | 50.087
2020-08-29 | 460:51 | 50.085
2020-08-29 | 461:51 | 50.087
2020-08-29 | 462:51 | 50.088
2020-08-29 | 463:51 | 50.091
2020-08-29 | 464:51 | 50.091
2020-08-29 | 465:51 | 50.091
2020-08-29 | 466:51 | 50.093
2020-08-29 | 467:51 | 50.094
2020-08-29 | 468:51 | 50.094
2020-08-29 | 469:51 | 50.09
2020-08-29 | 470:51 | 50.089
2020-08-29 | 471:51 | 50.088
2020-08-29 | 472:51 | 50.089
2020-08-29 | 473:51 | 50.091
2020-08-29 | 474:51 | 50.089
2020-08-29 | 475:51 | 50.089
2020-08-29 | 476:51 | 50.091
2020-08-29 | 477:51 | 50.09
2020-08-29 | 478:51 | 50.089
2020-08-29 | 479:51 | 50.084
2020-08-29 | 480:51 | 50.084
2020-08-29 | 481:51 | 50.083
2020-08-29 | 482:51 | 50.081
2020-08-29 | 483:51 | 50.08
2020-08-29 | 484:51 | 50.082
2020-08-29 | 485:51 | 50.083
2020-08-29 | 486:51 | 50.086
2020-08-29 | 487:51 | 50.087
2020-08-29 | 488:51 | 50.084
2020-08-29 | 489:51 | 50.067
2020-08-29 | 490:51 | 50.06
2020-08-29 | 491:51 | 50.054
2020-08-29 | 492:51 | 50.05
2020-08-29 | 493:51 | 50.048
2020-08-29 | 494:51 | 50.045
2020-08-29 | 495:51 | 50.047
2020-08-29 | 496:51 | 50.047
2020-08-29 | 497:51 | 50.046
2020-08-29 | 498:51 | 50.046
2020-08-29 | 499:51 | 50.044
2020-08-29 | 500:51 | 50.041
2020-08-29 | 501:51 | 50.039
2020-08-29 | 502:51 | 50.038
2020-08-29 | 503:51 | 50.039
2020-08-29 | 504:51 | 50.043
2020-08-29 | 505:51 | 50.049
2020-08-29 | 506:51 | 50.052
2020-08-29 | 507:51 | 50.053
2020-08-29 | 508:51 | 50.053
2020-08-29 | 509:51 | 50.055
2020-08-29 | 510:51 | 50.055
2020-08-29 | 511:51 | 50.057
2020-08-29 | 512:51 | 50.059
2020-08-29 | 513:51 | 50.06
2020-08-29 | 514:51 | 50.062
2020-08-29 | 515:51 | 50.062
2020-08-29 | 516:51 | 50.062
2020-08-29 | 517:51 | 50.063
2020-08-29 | 518:51 | 50.06
2020-08-29 | 519:51 | 50.06
2020-08-29 | 520:51 | 50.058
2020-08-29 | 521:51 | 50.059
2020-08-29 | 522:51 | 50.062
2020-08-29 | 523:51 | 50.062
2020-08-29 | 524:51 | 50.063
2020-08-29 | 525:51 | 50.062
2020-08-29 | 526:51 | 50.063
2020-08-29 | 527:51 | 50.063
2020-08-29 | 528:51 | 50.064
2020-08-29 | 529:51 | 50.063
2020-08-29 | 530:51 | 50.059
2020-08-29 | 531:51 | 50.056
2020-08-29 | 532:51 | 50.054
2020-08-29 | 533:51 | 50.057
2020-08-29 | 534:51 | 50.059
2020-08-29 | 535:51 | 50.064
2020-08-29 | 536:51 | 50.068
2020-08-29 | 537:51 | 50.068
2020-08-29 | 538:51 | 50.069
2020-08-29 | 539:51 | 50.064
2020-08-29 | 540:51 | 50.063
2020-08-29 | 541:51 | 50.059
2020-08-29 | 542:51 | 50.058
2020-08-29 | 543:51 | 50.053
2020-08-29 | 544:51 | 50.051
2020-08-29 | 545:51 | 50.051
2020-08-29 | 546:51 | 50.054
2020-08-29 | 547:51 | 50.05
2020-08-29 | 548:51 | 50.053
2020-08-29 | 549:51 | 50.048
2020-08-29 | 550:51 | 50.046
2020-08-29 | 551:51 | 50.046
2020-08-29 | 552:51 | 50.043
2020-08-29 | 553:51 | 50.041
2020-08-29 | 554:51 | 50.039
2020-08-29 | 555:51 | 50.037
2020-08-29 | 556:51 | 50.039
2020-08-29 | 557:51 | 50.041
2020-08-29 | 558:51 | 50.044
2020-08-29 | 559:51 | 50.042
2020-08-29 | 560:51 | 50.044
2020-08-29 | 561:51 | 50.031
2020-08-29 | 562:51 | 50.016
2020-08-29 | 563:51 | 50.008
2020-08-29 | 564:51 | 50.007
2020-08-29 | 565:51 | 50.001
2020-08-29 | 566:51 | 49.998
2020-08-29 | 567:51 | 49.996
2020-08-29 | 568:51 | 49.994
2020-08-29 | 569:51 | 49.989
2020-08-29 | 570:51 | 49.986
2020-08-29 | 571:51 | 49.986
2020-08-29 | 572:51 | 49.987
2020-08-29 | 573:51 | 49.987
2020-08-29 | 574:51 | 49.987
2020-08-29 | 575:51 | 49.985
2020-08-29 | 576:51 | 49.984
2020-08-29 | 577:51 | 49.987
2020-08-29 | 578:51 | 49.989
2020-08-29 | 579:51 | 49.996
2020-08-29 | 580:51 | 50
2020-08-29 | 581:51 | 50.004
2020-08-29 | 582:51 | 50.008
2020-08-29 | 583:51 | 50.013
2020-08-29 | 584:51 | 50.024
2020-08-29 | 585:51 | 50.028
2020-08-29 | 586:51 | 50.031
2020-08-29 | 587:51 | 50.033
2020-08-29 | 588:51 | 50.035
2020-08-29 | 589:51 | 50.038
2020-08-29 | 590:51 | 50.039
2020-08-29 | 591:51 | 50.041
2020-08-29 | 592:51 | 50.042
2020-08-29 | 593:51 | 50.044
2020-08-29 | 594:51 | 50.046
2020-08-29 | 595:51 | 50.047
2020-08-29 | 596:51 | 50.051
2020-08-29 | 597:51 | 50.052
2020-08-29 | 598:51 | 50.055
2020-08-29 | 599:51 | 50.054
2020-08-29 | 600:51 | 50.055
2020-08-29 | 601:51 | 50.052
2020-08-29 | 602:51 | 50.054
2020-08-29 | 603:51 | 50.054
2020-08-29 | 604:51 | 50.056
2020-08-29 | 605:51 | 50.053
2020-08-29 | 606:51 | 50.048
2020-08-29 | 607:51 | 50.044
2020-08-29 | 608:51 | 50.036
2020-08-29 | 609:51 | 50.032
2020-08-29 | 610:51 | 50.03
2020-08-29 | 611:51 | 50.025
2020-08-29 | 612:51 | 50.021
2020-08-29 | 613:51 | 50.015
2020-08-29 | 614:51 | 50.013
2020-08-29 | 615:51 | 50.014
2020-08-29 | 616:51 | 50.01
2020-08-29 | 617:51 | 50.008
2020-08-29 | 618:51 | 50.005
2020-08-29 | 619:51 | 50.004
2020-08-29 | 620:51 | 50.002
2020-08-29 | 621:51 | 49.998
2020-08-29 | 622:51 | 49.994
2020-08-29 | 623:51 | 49.992
2020-08-29 | 624:51 | 49.992
2020-08-29 | 625:51 | 49.993
2020-08-29 | 626:51 | 49.991
2020-08-29 | 627:51 | 49.99
2020-08-29 | 628:51 | 49.987
2020-08-29 | 629:51 | 49.982
2020-08-29 | 630:51 | 49.981
2020-08-29 | 631:51 | 49.981
2020-08-29 | 632:51 | 49.977
2020-08-29 | 633:51 | 49.976
2020-08-29 | 634:51 | 49.977
2020-08-29 | 635:51 | 49.977
2020-08-29 | 636:51 | 49.975
2020-08-29 | 637:51 | 49.975
2020-08-29 | 638:51 | 49.973
2020-08-29 | 639:51 | 49.97
2020-08-29 | 640:51 | 49.97
2020-08-29 | 641:51 | 49.969
2020-08-29 | 642:51 | 49.969
2020-08-29 | 643:51 | 49.973
2020-08-29 | 644:51 | 49.976
2020-08-29 | 645:51 | 49.98
2020-08-29 | 646:51 | 49.984
2020-08-29 | 647:51 | 49.99
2020-08-29 | 648:51 | 49.991
2020-08-29 | 649:51 | 49.991
2020-08-29 | 650:51 | 49.988
2020-08-29 | 651:51 | 49.989
2020-08-29 | 652:51 | 49.989
2020-08-29 | 653:51 | 49.986
2020-08-29 | 654:51 | 49.985
2020-08-29 | 655:51 | 49.983
2020-08-29 | 656:51 | 49.982
2020-08-29 | 657:51 | 49.976
2020-08-29 | 658:51 | 49.973
2020-08-29 | 659:51 | 49.97
2020-08-29 | 660:51 | 49.966
2020-08-29 | 661:51 | 49.964
2020-08-29 | 662:51 | 49.965
2020-08-29 | 663:51 | 49.961
2020-08-29 | 664:51 | 49.961
2020-08-29 | 665:51 | 49.965
2020-08-29 | 666:51 | 49.967
2020-08-29 | 667:51 | 49.965
2020-08-29 | 668:51 | 49.965
2020-08-29 | 669:51 | 49.965
2020-08-29 | 670:51 | 49.966
2020-08-29 | 671:51 | 49.962
2020-08-29 | 672:51 | 49.961
2020-08-29 | 673:51 | 49.95
2020-08-29 | 674:51 | 49.944
2020-08-29 | 675:51 | 49.941
2020-08-29 | 676:51 | 49.936
2020-08-29 | 677:51 | 49.936
2020-08-29 | 678:51 | 49.935
2020-08-29 | 679:51 | 49.933
2020-08-29 | 680:51 | 49.933
2020-08-29 | 681:51 | 49.932
2020-08-29 | 682:51 | 49.932
2020-08-29 | 683:51 | 49.932
2020-08-29 | 684:51 | 49.934
2020-08-29 | 685:51 | 49.937
2020-08-29 | 686:51 | 49.94
2020-08-29 | 687:51 | 49.942
2020-08-29 | 688:51 | 49.945
2020-08-29 | 689:51 | 49.949
2020-08-29 | 690:51 | 49.95
2020-08-29 | 691:51 | 49.944
2020-08-29 | 692:51 | 49.941
2020-08-29 | 693:51 | 49.939
2020-08-29 | 694:51 | 49.937
2020-08-29 | 695:51 | 49.937
2020-08-29 | 696:51 | 49.938
2020-08-29 | 697:51 | 49.94
2020-08-29 | 698:51 | 49.941
2020-08-29 | 699:51 | 49.942
2020-08-29 | 700:51 | 49.944
2020-08-29 | 701:51 | 49.943
2020-08-29 | 702:51 | 49.945
2020-08-29 | 703:51 | 49.94
2020-08-29 | 704:51 | 49.937
2020-08-29 | 705:51 | 49.934
2020-08-29 | 706:51 | 49.932
2020-08-29 | 707:51 | 49.929
2020-08-29 | 708:51 | 49.927
2020-08-29 | 709:51 | 49.924
2020-08-29 | 710:51 | 49.927
2020-08-29 | 711:51 | 49.928
2020-08-29 | 712:51 | 49.928
2020-08-29 | 713:51 | 49.928
2020-08-29 | 714:51 | 49.929
2020-08-29 | 715:51 | 49.929
2020-08-29 | 716:51 | 49.928
2020-08-29 | 717:51 | 49.929
2020-08-29 | 718:51 | 49.93
2020-08-29 | 719:51 | 49.929
2020-08-29 | 720:51 | 49.925
2020-08-29 | 721:51 | 49.926
2020-08-29 | 722:51 | 49.925
2020-08-29 | 723:51 | 49.926
2020-08-29 | 724:51 | 49.928
2020-08-29 | 725:51 | 49.929
2020-08-29 | 726:51 | 49.927
2020-08-29 | 727:51 | 49.925
2020-08-29 | 728:51 | 49.926
2020-08-29 | 729:51 | 49.928
2020-08-29 | 730:51 | 49.93
2020-08-29 | 731:51 | 49.931
2020-08-29 | 732:51 | 49.925
2020-08-29 | 733:51 | 49.922
2020-08-29 | 734:51 | 49.921
2020-08-29 | 735:51 | 49.924
2020-08-29 | 736:51 | 49.92
2020-08-29 | 737:51 | 49.919
2020-08-29 | 738:51 | 49.913
2020-08-29 | 739:51 | 49.914
2020-08-29 | 740:51 | 49.918
2020-08-29 | 741:51 | 49.924
2020-08-29 | 742:51 | 49.928
2020-08-29 | 743:51 | 49.934
2020-08-29 | 744:51 | 49.936
2020-08-29 | 745:51 | 49.938
2020-08-29 | 746:51 | 49.936
2020-08-29 | 747:51 | 49.933
2020-08-29 | 748:51 | 49.928
2020-08-29 | 749:51 | 49.922
2020-08-29 | 750:51 | 49.917
2020-08-29 | 751:51 | 49.91
2020-08-29 | 752:51 | 49.909
2020-08-29 | 753:51 | 49.91
2020-08-29 | 754:51 | 49.909
2020-08-29 | 755:51 | 49.912
2020-08-29 | 756:51 | 49.913
2020-08-29 | 757:51 | 49.916
2020-08-29 | 758:51 | 49.917
2020-08-29 | 759:51 | 49.923
2020-08-29 | 760:51 | 49.924
2020-08-29 | 761:51 | 49.923
2020-08-29 | 762:51 | 49.929
2020-08-29 | 763:51 | 49.932
2020-08-29 | 764:51 | 49.931
2020-08-29 | 765:51 | 49.934
2020-08-29 | 766:51 | 49.937
2020-08-29 | 767:51 | 49.938
2020-08-29 | 768:51 | 49.941
2020-08-29 | 769:51 | 49.943
2020-08-29 | 770:51 | 49.943
2020-08-29 | 771:51 | 49.941
2020-08-29 | 772:51 | 49.942
2020-08-29 | 773:51 | 49.943
2020-08-29 | 774:51 | 49.946
2020-08-29 | 775:51 | 49.949
2020-08-29 | 776:51 | 49.95
2020-08-29 | 777:51 | 49.949
2020-08-29 | 778:51 | 49.945
2020-08-29 | 779:51 | 49.941
2020-08-29 | 780:51 | 49.94
2020-08-29 | 781:51 | 49.939
2020-08-29 | 782:51 | 49.931
2020-08-29 | 783:51 | 49.924
2020-08-29 | 784:51 | 49.92
2020-08-29 | 785:51 | 49.918
2020-08-29 | 786:51 | 49.919
2020-08-29 | 787:51 | 49.921
2020-08-29 | 788:51 | 49.926
2020-08-29 | 789:51 | 49.929
2020-08-29 | 790:51 | 49.935
2020-08-29 | 791:51 | 49.939
2020-08-29 | 792:51 | 49.938
2020-08-29 | 793:51 | 49.94
2020-08-29 | 794:51 | 49.942
2020-08-29 | 795:51 | 49.939
2020-08-29 | 796:51 | 49.938
2020-08-29 | 797:51 | 49.933
2020-08-29 | 798:51 | 49.927
2020-08-29 | 799:51 | 49.927
2020-08-29 | 800:51 | 49.924
2020-08-29 | 801:51 | 49.923
2020-08-29 | 802:51 | 49.921
2020-08-29 | 803:51 | 49.918
2020-08-29 | 804:51 | 49.916
2020-08-29 | 805:51 | 49.917
2020-08-29 | 806:51 | 49.917
2020-08-29 | 807:51 | 49.919
2020-08-29 | 808:51 | 49.919
2020-08-29 | 809:51 | 49.917
2020-08-29 | 810:51 | 49.919
2020-08-29 | 811:51 | 49.916
2020-08-29 | 812:51 | 49.911
2020-08-29 | 813:51 | 49.913
2020-08-29 | 814:51 | 49.919
2020-08-29 | 815:51 | 49.923
2020-08-29 | 816:51 | 49.925
2020-08-29 | 817:51 | 49.925
2020-08-29 | 818:51 | 49.923
2020-08-29 | 819:51 | 49.924
2020-08-29 | 820:51 | 49.923
2020-08-29 | 821:51 | 49.924
2020-08-29 | 822:51 | 49.929
2020-08-29 | 823:51 | 49.93
2020-08-29 | 824:51 | 49.934
2020-08-29 | 825:51 | 49.936
2020-08-29 | 826:51 | 49.936
2020-08-29 | 827:51 | 49.935
2020-08-29 | 828:51 | 49.934
2020-08-29 | 829:51 | 49.934
2020-08-29 | 830:51 | 49.933
2020-08-29 | 831:51 | 49.931
2020-08-29 | 832:51 | 49.929
2020-08-29 | 833:51 | 49.929
2020-08-29 | 834:51 | 49.926
2020-08-29 | 835:51 | 49.926
2020-08-29 | 836:51 | 49.926
2020-08-29 | 837:51 | 49.922
2020-08-29 | 838:51 | 49.925
2020-08-29 | 839:51 | 49.924
2020-08-29 | 840:51 | 49.922
2020-08-29 | 841:51 | 49.921
2020-08-29 | 842:51 | 49.916
2020-08-29 | 843:51 | 49.912
2020-08-29 | 844:51 | 49.911
2020-08-29 | 845:51 | 49.912
2020-08-29 | 846:51 | 49.913
2020-08-29 | 847:51 | 49.913
2020-08-29 | 848:51 | 49.919
2020-08-29 | 849:51 | 49.927
2020-08-29 | 850:51 | 49.933
2020-08-29 | 851:51 | 49.933
2020-08-29 | 852:51 | 49.935
2020-08-29 | 853:51 | 49.938
2020-08-29 | 854:51 | 49.939
2020-08-29 | 855:51 | 49.94
2020-08-29 | 856:51 | 49.94
2020-08-29 | 857:51 | 49.94
2020-08-29 | 858:51 | 49.939
2020-08-29 | 859:51 | 49.937
2020-08-29 | 860:51 | 49.931
2020-08-29 | 861:51 | 49.929
2020-08-29 | 862:51 | 49.927
2020-08-29 | 863:51 | 49.923
2020-08-29 | 864:51 | 49.919
2020-08-29 | 865:51 | 49.916
2020-08-29 | 866:51 | 49.913
2020-08-29 | 867:51 | 49.91
2020-08-29 | 868:51 | 49.908
2020-08-29 | 869:51 | 49.907
2020-08-29 | 870:51 | 49.907
2020-08-29 | 871:51 | 49.907
2020-08-29 | 872:51 | 49.909
2020-08-29 | 873:51 | 49.911
2020-08-29 | 874:51 | 49.913
2020-08-29 | 875:51 | 49.914
2020-08-29 | 876:51 | 49.915
2020-08-29 | 877:51 | 49.917
2020-08-29 | 878:51 | 49.918
2020-08-29 | 879:51 | 49.918
2020-08-29 | 880:51 | 49.912
2020-08-29 | 881:51 | 49.911
2020-08-29 | 882:51 | 49.907
2020-08-29 | 883:51 | 49.907
2020-08-29 | 884:51 | 49.909
2020-08-29 | 885:51 | 49.913
2020-08-29 | 886:51 | 49.914
2020-08-29 | 887:51 | 49.921
2020-08-29 | 888:51 | 49.923
2020-08-29 | 889:51 | 49.927
2020-08-29 | 890:51 | 49.932
2020-08-29 | 891:51 | 49.932
2020-08-29 | 892:51 | 49.929
2020-08-29 | 893:51 | 49.929
2020-08-29 | 894:51 | 49.929
2020-08-29 | 895:51 | 49.927
2020-08-29 | 896:51 | 49.927
2020-08-29 | 897:51 | 49.926
2020-08-29 | 898:51 | 49.924
2020-08-29 | 899:51 | 49.926
2020-08-29 | 900:51 | 49.926
2020-08-29 | 6:06 | 49.926
2020-08-29 | 6:06 | 49.925
2020-08-29 | 6:06 | 49.919
2020-08-29 | 6:06 | 49.919
2020-08-29 | 6:06 | 49.915
2020-08-29 | 6:06 | 49.912
2020-08-29 | 6:06 | 49.91
2020-08-29 | 6:06 | 49.909
2020-08-29 | 6:06 | 49.91
2020-08-29 | 6:06 | 49.918
2020-08-29 | 6:06 | 49.922
2020-08-29 | 6:06 | 49.925
2020-08-29 | 6:06 | 49.924
2020-08-29 | 6:06 | 49.922
2020-08-29 | 6:06 | 49.924
2020-08-29 | 6:06 | 49.927
2020-08-29 | 6:06 | 49.931
2020-08-29 | 6:06 | 49.935
2020-08-29 | 6:06 | 49.935
2020-08-29 | 6:06 | 49.939
2020-08-29 | 6:06 | 49.939
2020-08-29 | 6:06 | 49.939
2020-08-29 | 6:06 | 49.935
2020-08-29 | 6:06 | 49.932
2020-08-29 | 6:06 | 49.931
2020-08-29 | 6:06 | 49.929
2020-08-29 | 6:06 | 49.93
2020-08-29 | 6:06 | 49.934
2020-08-29 | 6:06 | 49.937
2020-08-29 | 6:06 | 49.938
2020-08-29 | 6:07 | 49.938
2020-08-29 | 6:07 | 49.939
2020-08-29 | 6:07 | 49.943
2020-08-29 | 6:07 | 49.946
2020-08-29 | 6:07 | 49.95
2020-08-29 | 6:07 | 49.951
2020-08-29 | 6:07 | 49.953
2020-08-29 | 6:07 | 49.958
2020-08-29 | 6:07 | 49.961
2020-08-29 | 6:07 | 49.961
2020-08-29 | 6:07 | 49.96
2020-08-29 | 6:07 | 49.959
2020-08-29 | 6:07 | 49.958
2020-08-29 | 6:07 | 49.958
2020-08-29 | 6:07 | 49.957
2020-08-29 | 6:07 | 49.953
2020-08-29 | 6:07 | 49.949
2020-08-29 | 6:07 | 49.949
2020-08-29 | 6:07 | 49.949
2020-08-29 | 6:07 | 49.95
2020-08-29 | 6:07 | 49.952
2020-08-29 | 6:07 | 49.957
2020-08-29 | 6:07 | 49.96
2020-08-29 | 6:07 | 49.96
2020-08-29 | 6:07 | 49.961
2020-08-29 | 6:07 | 49.962
2020-08-29 | 6:07 | 49.961
2020-08-29 | 6:07 | 49.961
2020-08-29 | 6:07 | 49.96
2020-08-29 | 6:07 | 49.961
2020-08-29 | 6:07 | 49.96
2020-08-29 | 6:07 | 49.957
2020-08-29 | 6:07 | 49.958
2020-08-29 | 6:07 | 49.955
2020-08-29 | 6:07 | 49.953
2020-08-29 | 6:07 | 49.947
2020-08-29 | 6:07 | 49.943
2020-08-29 | 6:07 | 49.94
2020-08-29 | 6:07 | 49.941
2020-08-29 | 6:07 | 49.941
2020-08-29 | 6:07 | 49.942
2020-08-29 | 6:07 | 49.94
2020-08-29 | 6:07 | 49.94
2020-08-29 | 6:07 | 49.94
2020-08-29 | 6:07 | 49.938
2020-08-29 | 6:07 | 49.936
2020-08-29 | 6:07 | 49.936
2020-08-29 | 6:07 | 49.932
2020-08-29 | 6:07 | 49.929
2020-08-29 | 6:07 | 49.929
2020-08-29 | 6:07 | 49.929
2020-08-29 | 6:07 | 49.929
2020-08-29 | 6:07 | 49.93
2020-08-29 | 6:07 | 49.931
2020-08-29 | 6:07 | 49.932
2020-08-29 | 6:07 | 49.934
2020-08-29 | 6:07 | 49.939
2020-08-29 | 6:07 | 49.945
2020-08-29 | 6:07 | 49.952
2020-08-29 | 6:07 | 49.959
2020-08-29 | 6:07 | 49.964
2020-08-29 | 6:08 | 49.968
2020-08-29 | 6:08 | 49.969
2020-08-29 | 6:08 | 49.97
2020-08-29 | 6:08 | 49.969
2020-08-29 | 6:08 | 49.968
2020-08-29 | 6:08 | 49.966
2020-08-29 | 6:08 | 49.962
2020-08-29 | 6:08 | 49.961
2020-08-29 | 6:08 | 49.961
2020-08-29 | 6:08 | 49.962
2020-08-29 | 6:08 | 49.963
2020-08-29 | 6:08 | 49.963
2020-08-29 | 6:08 | 49.966
2020-08-29 | 6:08 | 49.968
2020-08-29 | 6:08 | 49.97
2020-08-29 | 6:08 | 49.968
2020-08-29 | 6:08 | 49.969
2020-08-29 | 6:08 | 49.969
2020-08-29 | 6:08 | 49.967
2020-08-29 | 6:08 | 49.964
2020-08-29 | 6:08 | 49.963
2020-08-29 | 6:08 | 49.961
2020-08-29 | 6:08 | 49.962
2020-08-29 | 6:08 | 49.962
2020-08-29 | 6:08 | 49.962
2020-08-29 | 6:08 | 49.962
2020-08-29 | 6:08 | 49.961
2020-08-29 | 6:08 | 49.96
2020-08-29 | 6:08 | 49.961
2020-08-29 | 6:08 | 49.961
2020-08-29 | 6:08 | 49.962
2020-08-29 | 6:08 | 49.961
2020-08-29 | 6:08 | 49.962
2020-08-29 | 6:08 | 49.961
2020-08-29 | 6:08 | 49.964
2020-08-29 | 6:08 | 49.972
2020-08-29 | 6:08 | 49.975
2020-08-29 | 6:08 | 49.978
2020-08-29 | 6:08 | 49.981
2020-08-29 | 6:08 | 49.981
2020-08-29 | 6:08 | 49.979
2020-08-29 | 6:08 | 49.978
2020-08-29 | 6:08 | 49.979
2020-08-29 | 6:08 | 49.981
2020-08-29 | 6:08 | 49.984
2020-08-29 | 6:08 | 49.99
2020-08-29 | 6:08 | 49.993
2020-08-29 | 6:08 | 49.998
2020-08-29 | 6:08 | 50.004
2020-08-29 | 6:08 | 50.008
2020-08-29 | 6:08 | 50.011
2020-08-29 | 6:08 | 50.011
2020-08-29 | 6:08 | 50.013
2020-08-29 | 6:08 | 50.014
2020-08-29 | 6:08 | 50.016
2020-08-29 | 6:08 | 50.015
2020-08-29 | 6:08 | 50.015
2020-08-29 | 6:08 | 50.015
2020-08-29 | 6:08 | 50.017
2020-08-29 | 6:09 | 50.016
2020-08-29 | 6:09 | 50.013
2020-08-29 | 6:09 | 50.011
2020-08-29 | 6:09 | 50.012
2020-08-29 | 6:09 | 50.011
2020-08-29 | 6:09 | 50.012
2020-08-29 | 6:09 | 50.014
2020-08-29 | 6:09 | 50.016
2020-08-29 | 6:09 | 50.015
2020-08-29 | 6:09 | 50.014
2020-08-29 | 6:09 | 50.013
2020-08-29 | 6:09 | 50.013
2020-08-29 | 6:09 | 50.012
2020-08-29 | 6:09 | 50.005
2020-08-29 | 6:09 | 50
2020-08-29 | 6:09 | 49.998
2020-08-29 | 6:09 | 49.997
2020-08-29 | 6:09 | 49.996
2020-08-29 | 6:09 | 49.994
2020-08-29 | 6:09 | 49.994
2020-08-29 | 6:09 | 49.993
2020-08-29 | 6:09 | 49.992
2020-08-29 | 6:09 | 49.989
2020-08-29 | 6:09 | 49.989
2020-08-29 | 6:09 | 49.984
2020-08-29 | 6:09 | 49.982
2020-08-29 | 6:09 | 49.978
2020-08-29 | 6:09 | 49.976
2020-08-29 | 6:09 | 49.973
2020-08-29 | 6:09 | 49.974
2020-08-29 | 6:09 | 49.978
2020-08-29 | 6:09 | 49.981
2020-08-29 | 6:09 | 49.99
2020-08-29 | 6:09 | 49.993
2020-08-29 | 6:09 | 50.002
2020-08-29 | 6:09 | 50.006
2020-08-29 | 6:09 | 50.008
2020-08-29 | 6:09 | 50.008
2020-08-29 | 6:09 | 50.011
2020-08-29 | 6:09 | 50.012
2020-08-29 | 6:09 | 50.011
2020-08-29 | 6:09 | 50.011
2020-08-29 | 6:09 | 50.007
2020-08-29 | 6:09 | 50.009
2020-08-29 | 6:09 | 50.008
2020-08-29 | 6:09 | 50.011
2020-08-29 | 6:09 | 50.014
2020-08-29 | 6:09 | 50.015
2020-08-29 | 6:09 | 50.018
2020-08-29 | 6:09 | 50.021
2020-08-29 | 6:09 | 50.023
2020-08-29 | 6:09 | 50.024
2020-08-29 | 6:09 | 50.021
2020-08-29 | 6:09 | 50.017
2020-08-29 | 6:09 | 50.013
2020-08-29 | 6:09 | 50.011
2020-08-29 | 6:09 | 50.008
2020-08-29 | 6:09 | 50.005
2020-08-29 | 6:09 | 49.999
2020-08-29 | 6:09 | 50
2020-08-29 | 6:09 | 49.998
2020-08-29 | 6:10 | 49.997
2020-08-29 | 6:10 | 49.998
2020-08-29 | 6:10 | 49.999
2020-08-29 | 6:10 | 49.996
2020-08-29 | 6:10 | 49.996
2020-08-29 | 6:10 | 49.996
2020-08-29 | 6:10 | 49.996
2020-08-29 | 6:10 | 50
2020-08-29 | 6:10 | 49.999
2020-08-29 | 6:10 | 49.995
2020-08-29 | 6:10 | 49.995
2020-08-29 | 6:10 | 49.996
2020-08-29 | 6:10 | 49.998
2020-08-29 | 6:10 | 50.001
2020-08-29 | 6:10 | 50.004
2020-08-29 | 6:10 | 50.004
2020-08-29 | 6:10 | 50.006
2020-08-29 | 6:10 | 50.005
2020-08-29 | 6:10 | 50
2020-08-29 | 6:10 | 49.992
2020-08-29 | 6:10 | 49.984
2020-08-29 | 6:10 | 49.977
2020-08-29 | 6:10 | 49.972
2020-08-29 | 6:10 | 49.969
2020-08-29 | 6:10 | 49.967
2020-08-29 | 6:10 | 49.963
2020-08-29 | 6:10 | 49.961
2020-08-29 | 6:10 | 49.96
2020-08-29 | 6:10 | 49.961
2020-08-29 | 6:10 | 49.961
2020-08-29 | 6:10 | 49.961
2020-08-29 | 6:10 | 49.961
2020-08-29 | 6:10 | 49.959
2020-08-29 | 6:10 | 49.96
2020-08-29 | 6:10 | 49.961
2020-08-29 | 6:10 | 49.96
2020-08-29 | 6:10 | 49.959
2020-08-29 | 6:10 | 49.959
2020-08-29 | 6:10 | 49.958
2020-08-29 | 6:10 | 49.96
2020-08-29 | 6:10 | 49.961
2020-08-29 | 6:10 | 49.961
2020-08-29 | 6:10 | 49.964
2020-08-29 | 6:10 | 49.966
2020-08-29 | 6:10 | 49.966
2020-08-29 | 6:10 | 49.965
2020-08-29 | 6:10 | 49.962
2020-08-29 | 6:10 | 49.962
2020-08-29 | 6:10 | 49.964
2020-08-29 | 6:10 | 49.962
2020-08-29 | 6:10 | 49.962
2020-08-29 | 6:10 | 49.959
2020-08-29 | 6:10 | 49.954
2020-08-29 | 6:10 | 49.95
2020-08-29 | 6:10 | 49.946
2020-08-29 | 6:10 | 49.942
2020-08-29 | 6:10 | 49.942
2020-08-29 | 6:10 | 49.94
2020-08-29 | 6:10 | 49.941
2020-08-29 | 6:11 | 49.94
2020-08-29 | 6:11 | 49.937
2020-08-29 | 6:11 | 49.939
2020-08-29 | 6:11 | 49.938
2020-08-29 | 6:11 | 49.937
2020-08-29 | 6:11 | 49.937
2020-08-29 | 6:11 | 49.934
2020-08-29 | 6:11 | 49.931
2020-08-29 | 6:11 | 49.93
2020-08-29 | 6:11 | 49.928
2020-08-29 | 6:11 | 49.925
2020-08-29 | 6:11 | 49.926
2020-08-29 | 6:11 | 49.929
2020-08-29 | 6:11 | 49.931
2020-08-29 | 6:11 | 49.932
2020-08-29 | 6:11 | 49.931
2020-08-29 | 6:11 | 49.928
2020-08-29 | 6:11 | 49.927
2020-08-29 | 6:11 | 49.926
2020-08-29 | 6:11 | 49.925
2020-08-29 | 6:11 | 49.925
2020-08-29 | 6:11 | 49.925
2020-08-29 | 6:11 | 49.925
2020-08-29 | 6:11 | 49.927
2020-08-29 | 6:11 | 49.927
2020-08-29 | 6:11 | 49.927
2020-08-29 | 6:11 | 49.925
2020-08-29 | 6:11 | 49.924
2020-08-29 | 6:11 | 49.923
2020-08-29 | 6:11 | 49.92
2020-08-29 | 6:11 | 49.917
2020-08-29 | 6:11 | 49.916
2020-08-29 | 6:11 | 49.913
2020-08-29 | 6:11 | 49.911
2020-08-29 | 6:11 | 49.906
2020-08-29 | 6:11 | 49.903
2020-08-29 | 6:11 | 49.9
2020-08-29 | 6:11 | 49.896
2020-08-29 | 6:11 | 49.894
2020-08-29 | 6:11 | 49.894
2020-08-29 | 6:11 | 49.894
2020-08-29 | 6:11 | 49.893
2020-08-29 | 6:11 | 49.895
2020-08-29 | 6:11 | 49.894
2020-08-29 | 6:11 | 49.892
2020-08-29 | 6:11 | 49.89
2020-08-29 | 6:11 | 49.889
2020-08-29 | 6:11 | 49.887
2020-08-29 | 6:11 | 49.888
2020-08-29 | 6:11 | 49.887
2020-08-29 | 6:11 | 49.884
2020-08-29 | 6:11 | 49.883
2020-08-29 | 6:11 | 49.883
2020-08-29 | 6:11 | 49.884
2020-08-29 | 6:11 | 49.887
2020-08-29 | 6:11 | 49.889
2020-08-29 | 6:11 | 49.892
2020-08-29 | 6:11 | 49.893
2020-08-29 | 6:11 | 49.893
2020-08-29 | 6:11 | 49.896
2020-08-29 | 6:11 | 49.898
2020-08-29 | 6:12 | 49.898
2020-08-29 | 6:12 | 49.902
2020-08-29 | 6:12 | 49.906
2020-08-29 | 6:12 | 49.911
2020-08-29 | 6:12 | 49.914
2020-08-29 | 6:12 | 49.916
2020-08-29 | 6:12 | 49.917
2020-08-29 | 6:12 | 49.919
2020-08-29 | 6:12 | 49.921
2020-08-29 | 6:12 | 49.924
2020-08-29 | 6:12 | 49.925
2020-08-29 | 6:12 | 49.926
2020-08-29 | 6:12 | 49.925
2020-08-29 | 6:12 | 49.921
2020-08-29 | 6:12 | 49.92
2020-08-29 | 6:12 | 49.919
2020-08-29 | 6:12 | 49.918
2020-08-29 | 6:12 | 49.922
2020-08-29 | 6:12 | 49.925
2020-08-29 | 6:12 | 49.926
2020-08-29 | 6:12 | 49.928
2020-08-29 | 6:12 | 49.93
2020-08-29 | 6:12 | 49.931
2020-08-29 | 6:12 | 49.935
2020-08-29 | 6:12 | 49.93
2020-08-29 | 6:12 | 49.925
2020-08-29 | 6:12 | 49.92
2020-08-29 | 6:12 | 49.916
2020-08-29 | 6:12 | 49.915
2020-08-29 | 6:12 | 49.912
2020-08-29 | 6:12 | 49.911
2020-08-29 | 6:12 | 49.912
2020-08-29 | 6:12 | 49.914
2020-08-29 | 6:12 | 49.912
2020-08-29 | 6:12 | 49.908
2020-08-29 | 6:12 | 49.908
2020-08-29 | 6:12 | 49.909
2020-08-29 | 6:12 | 49.909
2020-08-29 | 6:12 | 49.907
2020-08-29 | 6:12 | 49.907
2020-08-29 | 6:12 | 49.904
2020-08-29 | 6:12 | 49.905
2020-08-29 | 6:12 | 49.905
2020-08-29 | 6:12 | 49.906
2020-08-29 | 6:12 | 49.905
2020-08-29 | 6:12 | 49.908
2020-08-29 | 6:12 | 49.907
2020-08-29 | 6:12 | 49.907
2020-08-29 | 6:12 | 49.909
2020-08-29 | 6:12 | 49.912
2020-08-29 | 6:12 | 49.913
2020-08-29 | 6:12 | 49.913
2020-08-29 | 6:12 | 49.915
2020-08-29 | 6:12 | 49.915
2020-08-29 | 6:12 | 49.916
2020-08-29 | 6:12 | 49.917
2020-08-29 | 6:12 | 49.919
2020-08-29 | 6:12 | 49.919
2020-08-29 | 6:12 | 49.918
2020-08-29 | 6:13 | 49.919
2020-08-29 | 6:13 | 49.919
2020-08-29 | 6:13 | 49.917
2020-08-29 | 6:13 | 49.919
2020-08-29 | 6:13 | 49.919
2020-08-29 | 6:13 | 49.918
2020-08-29 | 6:13 | 49.918
2020-08-29 | 6:13 | 49.915
2020-08-29 | 6:13 | 49.915
2020-08-29 | 6:13 | 49.917
2020-08-29 | 6:13 | 49.916
2020-08-29 | 6:13 | 49.915
2020-08-29 | 6:13 | 49.915
2020-08-29 | 6:13 | 49.914
2020-08-29 | 6:13 | 49.912
2020-08-29 | 6:13 | 49.914
2020-08-29 | 6:13 | 49.912
2020-08-29 | 6:13 | 49.912
2020-08-29 | 6:13 | 49.913
2020-08-29 | 6:13 | 49.915
2020-08-29 | 6:13 | 49.917
2020-08-29 | 6:13 | 49.919
2020-08-29 | 6:13 | 49.918
2020-08-29 | 6:13 | 49.916
2020-08-29 | 6:13 | 49.914
2020-08-29 | 6:13 | 49.911
2020-08-29 | 6:13 | 49.908
2020-08-29 | 6:13 | 49.908
2020-08-29 | 6:13 | 49.908
2020-08-29 | 6:13 | 49.906
2020-08-29 | 6:13 | 49.908
2020-08-29 | 6:13 | 49.908
2020-08-29 | 6:13 | 49.906
2020-08-29 | 6:13 | 49.906
2020-08-29 | 6:13 | 49.906
2020-08-29 | 6:13 | 49.905
2020-08-29 | 6:13 | 49.906
2020-08-29 | 6:13 | 49.905
2020-08-29 | 6:13 | 49.906
2020-08-29 | 6:13 | 49.907
2020-08-29 | 6:13 | 49.908
2020-08-29 | 6:13 | 49.907
2020-08-29 | 6:13 | 49.906
2020-08-29 | 6:13 | 49.905
2020-08-29 | 6:13 | 49.902
2020-08-29 | 6:13 | 49.903
2020-08-29 | 6:13 | 49.905
2020-08-29 | 6:13 | 49.907
2020-08-29 | 6:13 | 49.908
2020-08-29 | 6:13 | 49.909
2020-08-29 | 6:13 | 49.912
2020-08-29 | 6:13 | 49.913
2020-08-29 | 6:13 | 49.916
2020-08-29 | 6:13 | 49.919
2020-08-29 | 6:13 | 49.923
2020-08-29 | 6:13 | 49.925
2020-08-29 | 6:13 | 49.925
2020-08-29 | 6:13 | 49.923
2020-08-29 | 6:13 | 49.921
2020-08-29 | 6:13 | 49.917
2020-08-29 | 6:14 | 49.916
2020-08-29 | 6:14 | 49.915
2020-08-29 | 6:14 | 49.911
2020-08-29 | 6:14 | 49.907
2020-08-29 | 6:14 | 49.904
2020-08-29 | 6:14 | 49.905
2020-08-29 | 6:14 | 49.901
2020-08-29 | 6:14 | 49.899
2020-08-29 | 6:14 | 49.899
2020-08-29 | 6:14 | 49.901
2020-08-29 | 6:14 | 49.907
2020-08-29 | 6:14 | 49.911
2020-08-29 | 6:14 | 49.915
2020-08-29 | 6:14 | 49.918
2020-08-29 | 6:14 | 49.922
2020-08-29 | 6:14 | 49.926
2020-08-29 | 6:14 | 49.925
2020-08-29 | 6:14 | 49.924
2020-08-29 | 6:14 | 49.921
2020-08-29 | 6:14 | 49.918
2020-08-29 | 6:14 | 49.914
2020-08-29 | 6:14 | 49.911
2020-08-29 | 6:14 | 49.91
2020-08-29 | 6:14 | 49.908
2020-08-29 | 6:14 | 49.907
2020-08-29 | 6:14 | 49.906
2020-08-29 | 6:14 | 49.905
2020-08-29 | 6:14 | 49.902
2020-08-29 | 6:14 | 49.903
2020-08-29 | 6:14 | 49.901
2020-08-29 | 6:14 | 49.902
2020-08-29 | 6:14 | 49.901
2020-08-29 | 6:14 | 49.9
2020-08-29 | 6:14 | 49.898
2020-08-29 | 6:14 | 49.9
2020-08-29 | 6:14 | 49.9
2020-08-29 | 6:14 | 49.898
2020-08-29 | 6:14 | 49.897
2020-08-29 | 6:14 | 49.897
2020-08-29 | 6:14 | 49.895
2020-08-29 | 6:14 | 49.895
2020-08-29 | 6:14 | 49.894
2020-08-29 | 6:14 | 49.891
2020-08-29 | 6:14 | 49.888
2020-08-29 | 6:14 | 49.887
2020-08-29 | 6:14 | 49.885
2020-08-29 | 6:14 | 49.883
2020-08-29 | 6:14 | 49.883
2020-08-29 | 6:14 | 49.884
2020-08-29 | 6:14 | 49.887
2020-08-29 | 6:14 | 49.887
2020-08-29 | 6:14 | 49.887
2020-08-29 | 6:14 | 49.886
2020-08-29 | 6:14 | 49.884
2020-08-29 | 6:14 | 49.884
2020-08-29 | 6:14 | 49.885
2020-08-29 | 6:14 | 49.887
2020-08-29 | 6:14 | 49.889
2020-08-29 | 6:14 | 49.891
2020-08-29 | 6:14 | 49.893
2020-08-29 | 6:14 | 49.896
2020-08-29 | 6:15 | 49.901
2020-08-29 | 6:15 | 49.906
2020-08-29 | 6:15 | 49.91
2020-08-29 | 6:15 | 49.915
2020-08-29 | 6:15 | 49.92
2020-08-29 | 6:15 | 49.923
2020-08-29 | 6:15 | 49.928
2020-08-29 | 6:15 | 49.931
2020-08-29 | 6:15 | 49.935
2020-08-29 | 6:15 | 49.939
2020-08-29 | 6:15 | 49.94
2020-08-29 | 6:15 | 49.941
2020-08-29 | 6:15 | 49.94
2020-08-29 | 6:15 | 49.941
2020-08-29 | 6:15 | 49.941
2020-08-29 | 6:15 | 49.94
2020-08-29 | 6:15 | 49.938
2020-08-29 | 6:15 | 49.935
2020-08-29 | 6:15 | 49.933
2020-08-29 | 6:15 | 49.932
2020-08-29 | 6:15 | 49.932
2020-08-29 | 6:15 | 49.933
2020-08-29 | 6:15 | 49.934
2020-08-29 | 6:15 | 49.934
2020-08-29 | 6:15 | 49.929
2020-08-29 | 6:15 | 49.924
2020-08-29 | 6:15 | 49.923
2020-08-29 | 6:15 | 49.92
2020-08-29 | 6:15 | 49.918
2020-08-29 | 6:15 | 49.914
2020-08-29 | 6:15 | 49.915
2020-08-29 | 6:15 | 49.916
2020-08-29 | 6:15 | 49.921
2020-08-29 | 6:15 | 49.927
2020-08-29 | 6:15 | 49.936
2020-08-29 | 6:15 | 49.942
2020-08-29 | 6:15 | 49.945
2020-08-29 | 6:15 | 49.947
2020-08-29 | 6:15 | 49.947
2020-08-29 | 6:15 | 49.949
2020-08-29 | 6:15 | 49.95
2020-08-29 | 6:15 | 49.949
2020-08-29 | 6:15 | 49.945
2020-08-29 | 6:15 | 49.943
2020-08-29 | 6:15 | 49.941
2020-08-29 | 6:15 | 49.94
2020-08-29 | 6:15 | 49.941
2020-08-29 | 6:15 | 49.943
2020-08-29 | 6:15 | 49.949
2020-08-29 | 6:15 | 49.953
2020-08-29 | 6:15 | 49.956
2020-08-29 | 6:15 | 49.962
2020-08-29 | 6:15 | 49.967
2020-08-29 | 6:15 | 49.968
2020-08-29 | 6:15 | 49.968
2020-08-29 | 6:15 | 49.966
2020-08-29 | 6:15 | 49.966
2020-08-29 | 6:15 | 49.97
2020-08-29 | 6:15 | 49.972
2020-08-29 | 6:16 | 49.97
2020-08-29 | 6:16 | 49.969
2020-08-29 | 6:16 | 49.969
2020-08-29 | 6:16 | 49.968
2020-08-29 | 6:16 | 49.968
2020-08-29 | 6:16 | 49.965
2020-08-29 | 6:16 | 49.963
2020-08-29 | 6:16 | 49.964
2020-08-29 | 6:16 | 49.964
2020-08-29 | 6:16 | 49.962
2020-08-29 | 6:16 | 49.961
2020-08-29 | 6:16 | 49.959
2020-08-29 | 6:16 | 49.958
2020-08-29 | 6:16 | 49.958
2020-08-29 | 6:16 | 49.961
2020-08-29 | 6:16 | 49.964
2020-08-29 | 6:16 | 49.965
2020-08-29 | 6:16 | 49.968
2020-08-29 | 6:16 | 49.972
2020-08-29 | 6:16 | 49.976
2020-08-29 | 6:16 | 49.98
2020-08-29 | 6:16 | 49.983
2020-08-29 | 6:16 | 49.986
2020-08-29 | 6:16 | 49.985
2020-08-29 | 6:16 | 49.986
2020-08-29 | 6:16 | 49.986
2020-08-29 | 6:16 | 49.985
2020-08-29 | 6:16 | 49.983
2020-08-29 | 6:16 | 49.983
2020-08-29 | 6:16 | 49.984
2020-08-29 | 6:16 | 49.985
2020-08-29 | 6:16 | 49.984
2020-08-29 | 6:16 | 49.982
2020-08-29 | 6:16 | 49.979
2020-08-29 | 6:16 | 49.976
2020-08-29 | 6:16 | 49.977
2020-08-29 | 6:16 | 49.975
2020-08-29 | 6:16 | 49.976
2020-08-29 | 6:16 | 49.975
2020-08-29 | 6:16 | 49.975
2020-08-29 | 6:16 | 49.977
2020-08-29 | 6:16 | 49.977
2020-08-29 | 6:16 | 49.978
2020-08-29 | 6:16 | 49.978
2020-08-29 | 6:16 | 49.982
2020-08-29 | 6:16 | 49.987
2020-08-29 | 6:16 | 49.991
2020-08-29 | 6:16 | 49.994
2020-08-29 | 6:16 | 49.997
2020-08-29 | 6:16 | 50
2020-08-29 | 6:16 | 50.002
2020-08-29 | 6:16 | 50.003
2020-08-29 | 6:16 | 50.003
2020-08-29 | 6:16 | 50.002
2020-08-29 | 6:16 | 50.002
2020-08-29 | 6:16 | 50
2020-08-29 | 6:16 | 49.998
2020-08-29 | 6:16 | 49.997
2020-08-29 | 6:16 | 49.998
2020-08-29 | 6:16 | 49.997
2020-08-29 | 6:16 | 49.994
2020-08-29 | 6:17 | 49.989
2020-08-29 | 6:17 | 49.982
2020-08-29 | 6:17 | 49.979
2020-08-29 | 6:17 | 49.975
2020-08-29 | 6:17 | 49.971
2020-08-29 | 6:17 | 49.968
2020-08-29 | 6:17 | 49.965
2020-08-29 | 6:17 | 49.963
2020-08-29 | 6:17 | 49.964
2020-08-29 | 6:17 | 49.965
2020-08-29 | 6:17 | 49.967
2020-08-29 | 6:17 | 49.969
2020-08-29 | 6:17 | 49.971
2020-08-29 | 6:17 | 49.974
2020-08-29 | 6:17 | 49.978
2020-08-29 | 6:17 | 49.981
2020-08-29 | 6:17 | 49.982
2020-08-29 | 6:17 | 49.983
2020-08-29 | 6:17 | 49.984
2020-08-29 | 6:17 | 49.982
2020-08-29 | 6:17 | 49.979
2020-08-29 | 6:17 | 49.973
2020-08-29 | 6:17 | 49.967
2020-08-29 | 6:17 | 49.964
2020-08-29 | 6:17 | 49.962
2020-08-29 | 6:17 | 49.959
2020-08-29 | 6:17 | 49.959
2020-08-29 | 6:17 | 49.96
2020-08-29 | 6:17 | 49.96
2020-08-29 | 6:17 | 49.96
2020-08-29 | 6:17 | 49.961
2020-08-29 | 6:17 | 49.964
2020-08-29 | 6:17 | 49.965
2020-08-29 | 6:17 | 49.97
2020-08-29 | 6:17 | 49.964
2020-08-29 | 6:17 | 49.962
2020-08-29 | 6:17 | 49.955
2020-08-29 | 6:17 | 49.953
2020-08-29 | 6:17 | 49.949
2020-08-29 | 6:17 | 49.941
2020-08-29 | 6:17 | 49.936
2020-08-29 | 6:17 | 49.934
2020-08-29 | 6:17 | 49.93
2020-08-29 | 6:17 | 49.93
2020-08-29 | 6:17 | 49.93
2020-08-29 | 6:17 | 49.933
2020-08-29 | 6:17 | 49.937
2020-08-29 | 6:17 | 49.94
2020-08-29 | 6:17 | 49.942
2020-08-29 | 6:17 | 49.942
2020-08-29 | 6:17 | 49.944
2020-08-29 | 6:17 | 49.945
2020-08-29 | 6:17 | 49.945
2020-08-29 | 6:17 | 49.948
2020-08-29 | 6:17 | 49.95
2020-08-29 | 6:17 | 49.949
2020-08-29 | 6:17 | 49.948
2020-08-29 | 6:17 | 49.949
2020-08-29 | 6:17 | 49.95
2020-08-29 | 6:18 | 49.948
2020-08-29 | 6:18 | 49.945
2020-08-29 | 6:18 | 49.942
2020-08-29 | 6:18 | 49.941
2020-08-29 | 6:18 | 49.94
2020-08-29 | 6:18 | 49.943
2020-08-29 | 6:18 | 49.944
2020-08-29 | 6:18 | 49.946
2020-08-29 | 6:18 | 49.952
2020-08-29 | 6:18 | 49.958
2020-08-29 | 6:18 | 49.961
2020-08-29 | 6:18 | 49.96
2020-08-29 | 6:18 | 49.959
2020-08-29 | 6:18 | 49.957
2020-08-29 | 6:18 | 49.954
2020-08-29 | 6:18 | 49.951
2020-08-29 | 6:18 | 49.946
2020-08-29 | 6:18 | 49.941
2020-08-29 | 6:18 | 49.936
2020-08-29 | 6:18 | 49.935
2020-08-29 | 6:18 | 49.939
2020-08-29 | 6:18 | 49.942
2020-08-29 | 6:18 | 49.947
2020-08-29 | 6:18 | 49.948
2020-08-29 | 6:18 | 49.948
2020-08-29 | 6:18 | 49.948
2020-08-29 | 6:18 | 49.944
2020-08-29 | 6:18 | 49.939
2020-08-29 | 6:18 | 49.934
2020-08-29 | 6:18 | 49.933
2020-08-29 | 6:18 | 49.93
2020-08-29 | 6:18 | 49.925
2020-08-29 | 6:18 | 49.925
2020-08-29 | 6:18 | 49.929
2020-08-29 | 6:18 | 49.936
2020-08-29 | 6:18 | 49.938
2020-08-29 | 6:18 | 49.938
2020-08-29 | 6:18 | 49.939
2020-08-29 | 6:18 | 49.94
2020-08-29 | 6:18 | 49.938
2020-08-29 | 6:18 | 49.937
2020-08-29 | 6:18 | 49.932
2020-08-29 | 6:18 | 49.93
2020-08-29 | 6:18 | 49.925
2020-08-29 | 6:18 | 49.923
2020-08-29 | 6:18 | 49.92
2020-08-29 | 6:18 | 49.917
2020-08-29 | 6:18 | 49.913
2020-08-29 | 6:18 | 49.912
2020-08-29 | 6:18 | 49.911
2020-08-29 | 6:18 | 49.909
2020-08-29 | 6:18 | 49.912
2020-08-29 | 6:18 | 49.912
2020-08-29 | 6:18 | 49.914
2020-08-29 | 6:18 | 49.915
2020-08-29 | 6:18 | 49.915
2020-08-29 | 6:18 | 49.914
2020-08-29 | 6:18 | 49.915
2020-08-29 | 6:18 | 49.914
2020-08-29 | 6:18 | 49.914
2020-08-29 | 6:18 | 49.915
2020-08-29 | 6:19 | 49.922
2020-08-29 | 6:19 | 49.924
2020-08-29 | 6:19 | 49.932
2020-08-29 | 6:19 | 49.935
2020-08-29 | 6:19 | 49.939
2020-08-29 | 6:19 | 49.942
2020-08-29 | 6:19 | 49.944
2020-08-29 | 6:19 | 49.944
2020-08-29 | 6:19 | 49.947
2020-08-29 | 6:19 | 49.946
2020-08-29 | 6:19 | 49.945
2020-08-29 | 6:19 | 49.945
2020-08-29 | 6:19 | 49.944
2020-08-29 | 6:19 | 49.94
2020-08-29 | 6:19 | 49.936
2020-08-29 | 6:19 | 49.935
2020-08-29 | 6:19 | 49.937
2020-08-29 | 6:19 | 49.934
2020-08-29 | 6:19 | 49.935
2020-08-29 | 6:19 | 49.933
2020-08-29 | 6:19 | 49.931
2020-08-29 | 6:19 | 49.928
2020-08-29 | 6:19 | 49.925
2020-08-29 | 6:19 | 49.922
2020-08-29 | 6:19 | 49.915
2020-08-29 | 6:19 | 49.912
2020-08-29 | 6:19 | 49.911
2020-08-29 | 6:19 | 49.913
2020-08-29 | 6:19 | 49.915
2020-08-29 | 6:19 | 49.917
2020-08-29 | 6:19 | 49.92
2020-08-29 | 6:19 | 49.923
2020-08-29 | 6:19 | 49.925
2020-08-29 | 6:19 | 49.926
2020-08-29 | 6:19 | 49.926
2020-08-29 | 6:19 | 49.925
2020-08-29 | 6:19 | 49.925
2020-08-29 | 6:19 | 49.927
2020-08-29 | 6:19 | 49.926
2020-08-29 | 6:19 | 49.922
2020-08-29 | 6:19 | 49.92
2020-08-29 | 6:19 | 49.919
2020-08-29 | 6:19 | 49.917
2020-08-29 | 6:19 | 49.915
2020-08-29 | 6:19 | 49.91
2020-08-29 | 6:19 | 49.909
2020-08-29 | 6:19 | 49.904
2020-08-29 | 6:19 | 49.9
2020-08-29 | 6:19 | 49.899
2020-08-29 | 6:19 | 49.898
2020-08-29 | 6:19 | 49.895
2020-08-29 | 6:19 | 49.896
2020-08-29 | 6:19 | 49.897
2020-08-29 | 6:19 | 49.897
2020-08-29 | 6:19 | 49.9
2020-08-29 | 6:19 | 49.901
2020-08-29 | 6:19 | 49.902
2020-08-29 | 6:19 | 49.902
2020-08-29 | 6:19 | 49.904
2020-08-29 | 6:20 | 49.907
2020-08-29 | 6:20 | 49.907
2020-08-29 | 6:20 | 49.911
2020-08-29 | 6:20 | 49.913
2020-08-29 | 6:20 | 49.912
2020-08-29 | 6:20 | 49.911
2020-08-29 | 6:20 | 49.911
2020-08-29 | 6:20 | 49.91
2020-08-29 | 6:20 | 49.909
2020-08-29 | 6:20 | 49.907
2020-08-29 | 6:20 | 49.905
2020-08-29 | 6:20 | 49.91
2020-08-29 | 6:20 | 49.912
2020-08-29 | 6:20 | 49.913
2020-08-29 | 6:20 | 49.912
2020-08-29 | 6:20 | 49.909
2020-08-29 | 6:20 | 49.905
2020-08-29 | 6:20 | 49.905
2020-08-29 | 6:20 | 49.904
2020-08-29 | 6:20 | 49.901
2020-08-29 | 6:20 | 49.897
2020-08-29 | 6:20 | 49.895
2020-08-29 | 6:20 | 49.893
2020-08-29 | 6:20 | 49.894
2020-08-29 | 6:20 | 49.893
2020-08-29 | 6:20 | 49.893
2020-08-29 | 6:20 | 49.888
2020-08-29 | 6:20 | 49.89
2020-08-29 | 6:20 | 49.895
2020-08-29 | 6:20 | 49.894
2020-08-29 | 6:20 | 49.892
2020-08-29 | 6:20 | 49.894
2020-08-29 | 6:20 | 49.893
2020-08-29 | 6:20 | 49.893
2020-08-29 | 6:20 | 49.895
2020-08-29 | 6:20 | 49.9
2020-08-29 | 6:20 | 49.901
2020-08-29 | 6:20 | 49.897
2020-08-29 | 6:20 | 49.899
2020-08-29 | 6:20 | 49.898
2020-08-29 | 6:20 | 49.895
2020-08-29 | 6:20 | 49.889
2020-08-29 | 6:20 | 49.882
2020-08-29 | 6:20 | 49.881
2020-08-29 | 6:20 | 49.88
2020-08-29 | 6:20 | 49.877
2020-08-29 | 6:20 | 49.876
2020-08-29 | 6:20 | 49.876
2020-08-29 | 6:20 | 49.877
2020-08-29 | 6:20 | 49.88
2020-08-29 | 6:20 | 49.883
2020-08-29 | 6:20 | 49.884
2020-08-29 | 6:20 | 49.887
2020-08-29 | 6:20 | 49.888
2020-08-29 | 6:20 | 49.888
2020-08-29 | 6:20 | 49.887
2020-08-29 | 6:20 | 49.888
2020-08-29 | 6:20 | 49.894
2020-08-29 | 6:20 | 49.896
2020-08-29 | 6:20 | 49.899
2020-08-29 | 6:20 | 49.903
2020-08-29 | 6:21 | 49.905
2020-08-29 | 6:21 | 49.908
2020-08-29 | 6:21 | 49.91
2020-08-29 | 6:21 | 49.91
2020-08-29 | 6:21 | 49.91
2020-08-29 | 6:21 | 49.909
2020-08-29 | 6:21 | 49.908
2020-08-29 | 6:21 | 49.908
2020-08-29 | 6:21 | 49.909
2020-08-29 | 6:21 | 49.908
2020-08-29 | 6:21 | 49.907
2020-08-29 | 6:21 | 49.911
2020-08-29 | 6:21 | 49.916
2020-08-29 | 6:21 | 49.92
2020-08-29 | 6:21 | 49.92
2020-08-29 | 6:21 | 49.923
2020-08-29 | 6:21 | 49.926
2020-08-29 | 6:21 | 49.925
2020-08-29 | 6:21 | 49.925
2020-08-29 | 6:21 | 49.921
2020-08-29 | 6:21 | 49.917
2020-08-29 | 6:21 | 49.911
2020-08-29 | 6:21 | 49.911
2020-08-29 | 6:21 | 49.908
2020-08-29 | 6:21 | 49.908
2020-08-29 | 6:21 | 49.909
2020-08-29 | 6:21 | 49.915
2020-08-29 | 6:21 | 49.921
2020-08-29 | 6:21 | 49.924
2020-08-29 | 6:21 | 49.931
2020-08-29 | 6:21 | 49.933
2020-08-29 | 6:21 | 49.934
2020-08-29 | 6:21 | 49.936
2020-08-29 | 6:21 | 49.939
2020-08-29 | 6:21 | 49.937
2020-08-29 | 6:21 | 49.933
2020-08-29 | 6:21 | 49.93
2020-08-29 | 6:21 | 49.927
2020-08-29 | 6:21 | 49.922
2020-08-29 | 6:21 | 49.92
2020-08-29 | 6:21 | 49.919
2020-08-29 | 6:21 | 49.919
2020-08-29 | 6:21 | 49.919
2020-08-29 | 6:21 | 49.918
2020-08-29 | 6:21 | 49.918
2020-08-29 | 6:21 | 49.918
2020-08-29 | 6:21 | 49.919
2020-08-29 | 6:21 | 49.918
2020-08-29 | 6:21 | 49.916
2020-08-29 | 6:21 | 49.914
2020-08-29 | 6:21 | 49.914
2020-08-29 | 6:21 | 49.912
2020-08-29 | 6:21 | 49.913
2020-08-29 | 6:21 | 49.916
2020-08-29 | 6:21 | 49.92
2020-08-29 | 6:21 | 49.928
2020-08-29 | 6:21 | 49.932
2020-08-29 | 6:21 | 49.933
2020-08-29 | 6:21 | 49.934
2020-08-29 | 6:22 | 49.931
2020-08-29 | 6:22 | 49.929
2020-08-29 | 6:22 | 49.928
2020-08-29 | 6:22 | 49.925
2020-08-29 | 6:22 | 49.921
2020-08-29 | 6:22 | 49.917
2020-08-29 | 6:22 | 49.917
2020-08-29 | 6:22 | 49.913
2020-08-29 | 6:22 | 49.913
2020-08-29 | 6:22 | 49.911
2020-08-29 | 6:22 | 49.911
2020-08-29 | 6:22 | 49.913
2020-08-29 | 6:22 | 49.916
2020-08-29 | 6:22 | 49.918
2020-08-29 | 6:22 | 49.923
2020-08-29 | 6:22 | 49.929
2020-08-29 | 6:22 | 49.935
2020-08-29 | 6:22 | 49.938
2020-08-29 | 6:22 | 49.94
2020-08-29 | 6:22 | 49.939
2020-08-29 | 6:22 | 49.937
2020-08-29 | 6:22 | 49.937
2020-08-29 | 6:22 | 49.934
2020-08-29 | 6:22 | 49.935
2020-08-29 | 6:22 | 49.935
2020-08-29 | 6:22 | 49.936
2020-08-29 | 6:22 | 49.935
2020-08-29 | 6:22 | 49.937
2020-08-29 | 6:22 | 49.937
2020-08-29 | 6:22 | 49.936
2020-08-29 | 6:22 | 49.934
2020-08-29 | 6:22 | 49.93
2020-08-29 | 6:22 | 49.927
2020-08-29 | 6:22 | 49.922
2020-08-29 | 6:22 | 49.919
2020-08-29 | 6:22 | 49.918
2020-08-29 | 6:22 | 49.923
2020-08-29 | 6:22 | 49.925
2020-08-29 | 6:22 | 49.926
2020-08-29 | 6:22 | 49.928
2020-08-29 | 6:22 | 49.931
2020-08-29 | 6:22 | 49.933
2020-08-29 | 6:22 | 49.935
2020-08-29 | 6:22 | 49.935
2020-08-29 | 6:22 | 49.934
2020-08-29 | 6:22 | 49.931
2020-08-29 | 6:22 | 49.929
2020-08-29 | 6:22 | 49.929
2020-08-29 | 6:22 | 49.926
2020-08-29 | 6:22 | 49.926
2020-08-29 | 6:22 | 49.925
2020-08-29 | 6:22 | 49.925
2020-08-29 | 6:22 | 49.924
2020-08-29 | 6:22 | 49.923
2020-08-29 | 6:22 | 49.926
2020-08-29 | 6:22 | 49.926
2020-08-29 | 6:22 | 49.928
2020-08-29 | 6:22 | 49.929
2020-08-29 | 6:22 | 49.932
2020-08-29 | 6:22 | 49.936
2020-08-29 | 6:22 | 49.942
2020-08-29 | 6:23 | 49.944
2020-08-29 | 6:23 | 49.946
2020-08-29 | 6:23 | 49.947
2020-08-29 | 6:23 | 49.95
2020-08-29 | 6:23 | 49.951
2020-08-29 | 6:23 | 49.953
2020-08-29 | 6:23 | 49.953
2020-08-29 | 6:23 | 49.953
2020-08-29 | 6:23 | 49.952
2020-08-29 | 6:23 | 49.949
2020-08-29 | 6:23 | 49.948
2020-08-29 | 6:23 | 49.947
2020-08-29 | 6:23 | 49.949
2020-08-29 | 6:23 | 49.949
2020-08-29 | 6:23 | 49.947
2020-08-29 | 6:23 | 49.947
2020-08-29 | 6:23 | 49.946
2020-08-29 | 6:23 | 49.943
2020-08-29 | 6:23 | 49.941
2020-08-29 | 6:23 | 49.943
2020-08-29 | 6:23 | 49.948
2020-08-29 | 6:23 | 49.95
2020-08-29 | 6:23 | 49.954
2020-08-29 | 6:23 | 49.959
2020-08-29 | 6:23 | 49.963
2020-08-29 | 6:23 | 49.966
2020-08-29 | 6:23 | 49.966
2020-08-29 | 6:23 | 49.966
2020-08-29 | 6:23 | 49.968
2020-08-29 | 6:23 | 49.969
2020-08-29 | 6:23 | 49.969
2020-08-29 | 6:23 | 49.975
2020-08-29 | 6:23 | 49.976
2020-08-29 | 6:23 | 49.977
2020-08-29 | 6:23 | 49.978
2020-08-29 | 6:23 | 49.976
2020-08-29 | 6:23 | 49.976
2020-08-29 | 6:23 | 49.977
2020-08-29 | 6:23 | 49.979
2020-08-29 | 6:23 | 49.982
2020-08-29 | 6:23 | 49.985
2020-08-29 | 6:23 | 49.987
2020-08-29 | 6:23 | 49.985
2020-08-29 | 6:23 | 49.983
2020-08-29 | 6:23 | 49.979
2020-08-29 | 6:23 | 49.975
2020-08-29 | 6:23 | 49.972
2020-08-29 | 6:23 | 49.967
2020-08-29 | 6:23 | 49.963
2020-08-29 | 6:23 | 49.962
2020-08-29 | 6:23 | 49.962
2020-08-29 | 6:23 | 49.958
2020-08-29 | 6:23 | 49.957
2020-08-29 | 6:23 | 49.958
2020-08-29 | 6:23 | 49.959
2020-08-29 | 6:23 | 49.958
2020-08-29 | 6:23 | 49.956
2020-08-29 | 6:23 | 49.955
2020-08-29 | 6:23 | 49.956
2020-08-29 | 6:23 | 49.951
2020-08-29 | 6:24 | 49.952
2020-08-29 | 6:24 | 49.955
2020-08-29 | 6:24 | 49.959
2020-08-29 | 6:24 | 49.959
2020-08-29 | 6:24 | 49.958
2020-08-29 | 6:24 | 49.957
2020-08-29 | 6:24 | 49.958
2020-08-29 | 6:24 | 49.961
2020-08-29 | 6:24 | 49.963
2020-08-29 | 6:24 | 49.968
2020-08-29 | 6:24 | 49.971
2020-08-29 | 6:24 | 49.973
2020-08-29 | 6:24 | 49.976
2020-08-29 | 6:24 | 49.979
2020-08-29 | 6:24 | 49.987
2020-08-29 | 6:24 | 49.99
2020-08-29 | 6:24 | 49.994
2020-08-29 | 6:24 | 49.998
2020-08-29 | 6:24 | 50.002
2020-08-29 | 6:24 | 50.003
2020-08-29 | 6:24 | 50.003
2020-08-29 | 6:24 | 50.004
2020-08-29 | 6:24 | 50.006
2020-08-29 | 6:24 | 50.006
2020-08-29 | 6:24 | 50.005
2020-08-29 | 6:24 | 50.003
2020-08-29 | 6:24 | 50.001
2020-08-29 | 6:24 | 50.002
2020-08-29 | 6:24 | 49.998
2020-08-29 | 6:24 | 49.993
2020-08-29 | 6:24 | 49.988
2020-08-29 | 6:24 | 49.987
2020-08-29 | 6:24 | 49.987
2020-08-29 | 6:24 | 49.986
2020-08-29 | 6:24 | 49.987
2020-08-29 | 6:24 | 49.987
2020-08-29 | 6:24 | 49.983
2020-08-29 | 6:24 | 49.982
2020-08-29 | 6:24 | 49.98
2020-08-29 | 6:24 | 49.984
2020-08-29 | 6:24 | 49.987
2020-08-29 | 6:24 | 49.988
2020-08-29 | 6:24 | 49.988
2020-08-29 | 6:24 | 49.987
2020-08-29 | 6:24 | 49.985
2020-08-29 | 6:24 | 49.983
2020-08-29 | 6:24 | 49.985
2020-08-29 | 6:24 | 49.991
2020-08-29 | 6:24 | 49.996
2020-08-29 | 6:24 | 50.001
2020-08-29 | 6:24 | 50.002
2020-08-29 | 6:24 | 50.006
2020-08-29 | 6:24 | 50.008
2020-08-29 | 6:24 | 50.011
2020-08-29 | 6:24 | 50.014
2020-08-29 | 6:24 | 50.015
2020-08-29 | 6:24 | 50.013
2020-08-29 | 6:24 | 50.015
2020-08-29 | 6:24 | 50.017
2020-08-29 | 6:25 | 50.018
2020-08-29 | 6:25 | 50.023
2020-08-29 | 6:25 | 50.028
2020-08-29 | 6:25 | 50.032
2020-08-29 | 6:25 | 50.031
2020-08-29 | 6:25 | 50.031
2020-08-29 | 6:25 | 50.028
2020-08-29 | 6:25 | 50.027
2020-08-29 | 6:25 | 50.026
2020-08-29 | 6:25 | 50.027
2020-08-29 | 6:25 | 50.024
2020-08-29 | 6:25 | 50.022
2020-08-29 | 6:25 | 50.021
2020-08-29 | 6:25 | 50.024
2020-08-29 | 6:25 | 50.023
2020-08-29 | 6:25 | 50.02
2020-08-29 | 6:25 | 50.016
2020-08-29 | 6:25 | 50.015
2020-08-29 | 6:25 | 50.013
2020-08-29 | 6:25 | 50.014
2020-08-29 | 6:25 | 50.016
2020-08-29 | 6:25 | 50.017
2020-08-29 | 6:25 | 50.017
2020-08-29 | 6:25 | 50.017
2020-08-29 | 6:25 | 50.016
2020-08-29 | 6:25 | 50.017
2020-08-29 | 6:25 | 50.016
2020-08-29 | 6:25 | 50.015
2020-08-29 | 6:25 | 50.012
2020-08-29 | 6:25 | 50.012
2020-08-29 | 6:25 | 50.01
2020-08-29 | 6:25 | 50.007
2020-08-29 | 6:25 | 50.004
2020-08-29 | 6:25 | 50.002
2020-08-29 | 6:25 | 50.009
2020-08-29 | 6:25 | 50.016
2020-08-29 | 6:25 | 50.023
2020-08-29 | 6:25 | 50.024
2020-08-29 | 6:25 | 50.025
2020-08-29 | 6:25 | 50.024
2020-08-29 | 6:25 | 50.023
2020-08-29 | 6:25 | 50.021
2020-08-29 | 6:25 | 50.017
2020-08-29 | 6:25 | 50.012
2020-08-29 | 6:25 | 50.008
2020-08-29 | 6:25 | 50.003
2020-08-29 | 6:25 | 50
2020-08-29 | 6:25 | 49.993
2020-08-29 | 6:25 | 49.988
2020-08-29 | 6:25 | 49.983
2020-08-29 | 6:25 | 49.978
2020-08-29 | 6:25 | 49.975
2020-08-29 | 6:25 | 49.977
2020-08-29 | 6:25 | 49.979
2020-08-29 | 6:25 | 49.979
2020-08-29 | 6:25 | 49.979
2020-08-29 | 6:25 | 49.983
2020-08-29 | 6:25 | 49.985
2020-08-29 | 6:25 | 49.985
2020-08-29 | 6:25 | 49.984
2020-08-29 | 6:25 | 49.981
2020-08-29 | 6:26 | 49.977
2020-08-29 | 6:26 | 49.974
2020-08-29 | 6:26 | 49.972
2020-08-29 | 6:26 | 49.971
2020-08-29 | 6:26 | 49.968
2020-08-29 | 6:26 | 49.967
2020-08-29 | 6:26 | 49.965
2020-08-29 | 6:26 | 49.964
2020-08-29 | 6:26 | 49.965
2020-08-29 | 6:26 | 49.966
2020-08-29 | 6:26 | 49.968
2020-08-29 | 6:26 | 49.968
2020-08-29 | 6:26 | 49.968
2020-08-29 | 6:26 | 49.968
2020-08-29 | 6:26 | 49.97
2020-08-29 | 6:26 | 49.973
2020-08-29 | 6:26 | 49.977
2020-08-29 | 6:26 | 49.979
2020-08-29 | 6:26 | 49.982
2020-08-29 | 6:26 | 49.983
2020-08-29 | 6:26 | 49.985
2020-08-29 | 6:26 | 49.986
2020-08-29 | 6:26 | 49.985
2020-08-29 | 6:26 | 49.985
2020-08-29 | 6:26 | 49.984
2020-08-29 | 6:26 | 49.981
2020-08-29 | 6:26 | 49.981
2020-08-29 | 6:26 | 49.981
2020-08-29 | 6:26 | 49.979
2020-08-29 | 6:26 | 49.979
2020-08-29 | 6:26 | 49.978
2020-08-29 | 6:26 | 49.975
2020-08-29 | 6:26 | 49.975
2020-08-29 | 6:26 | 49.973
2020-08-29 | 6:26 | 49.972
2020-08-29 | 6:26 | 49.97
2020-08-29 | 6:26 | 49.97
2020-08-29 | 6:26 | 49.97
2020-08-29 | 6:26 | 49.972
2020-08-29 | 6:26 | 49.975
2020-08-29 | 6:26 | 49.978
2020-08-29 | 6:26 | 49.977
2020-08-29 | 6:26 | 49.972
2020-08-29 | 6:26 | 49.971
2020-08-29 | 6:26 | 49.971
2020-08-29 | 6:26 | 49.968
2020-08-29 | 6:26 | 49.965
2020-08-29 | 6:26 | 49.96
2020-08-29 | 6:26 | 49.958
2020-08-29 | 6:26 | 49.956
2020-08-29 | 6:26 | 49.95
2020-08-29 | 6:26 | 49.948
2020-08-29 | 6:26 | 49.948
2020-08-29 | 6:26 | 49.948
2020-08-29 | 6:26 | 49.947
2020-08-29 | 6:26 | 49.947
2020-08-29 | 6:26 | 49.948
2020-08-29 | 6:26 | 49.948
2020-08-29 | 6:26 | 49.949
2020-08-29 | 6:27 | 49.947
2020-08-29 | 6:27 | 49.944
2020-08-29 | 6:27 | 49.942
2020-08-29 | 6:27 | 49.943
2020-08-29 | 6:27 | 49.943
2020-08-29 | 6:27 | 49.944
2020-08-29 | 6:27 | 49.944
2020-08-29 | 6:27 | 49.943
2020-08-29 | 6:27 | 49.945
2020-08-29 | 6:27 | 49.944
2020-08-29 | 6:27 | 49.941
2020-08-29 | 6:27 | 49.939
2020-08-29 | 6:27 | 49.94
2020-08-29 | 6:27 | 49.939
2020-08-29 | 6:27 | 49.938
2020-08-29 | 6:27 | 49.937
2020-08-29 | 6:27 | 49.938
2020-08-29 | 6:27 | 49.94
2020-08-29 | 6:27 | 49.94
2020-08-29 | 6:27 | 49.939
2020-08-29 | 6:27 | 49.941
2020-08-29 | 6:27 | 49.944
2020-08-29 | 6:27 | 49.946
2020-08-29 | 6:27 | 49.951
2020-08-29 | 6:27 | 49.962
2020-08-29 | 6:27 | 49.971
2020-08-29 | 6:27 | 49.976
2020-08-29 | 6:27 | 49.978
2020-08-29 | 6:27 | 49.982
2020-08-29 | 6:27 | 49.983
2020-08-29 | 6:27 | 49.98
2020-08-29 | 6:27 | 49.98
2020-08-29 | 6:27 | 49.979
2020-08-29 | 6:27 | 49.98
2020-08-29 | 6:27 | 49.982
2020-08-29 | 6:27 | 49.983
2020-08-29 | 6:27 | 49.981
2020-08-29 | 6:27 | 49.979
2020-08-29 | 6:27 | 49.977
2020-08-29 | 6:27 | 49.974
2020-08-29 | 6:27 | 49.972
2020-08-29 | 6:27 | 49.969
2020-08-29 | 6:27 | 49.966
2020-08-29 | 6:27 | 49.964
2020-08-29 | 6:27 | 49.964
2020-08-29 | 6:27 | 49.966
2020-08-29 | 6:27 | 49.968
2020-08-29 | 6:27 | 49.969
2020-08-29 | 6:27 | 49.971
2020-08-29 | 6:27 | 49.975
2020-08-29 | 6:27 | 49.977
2020-08-29 | 6:27 | 49.978
2020-08-29 | 6:27 | 49.978
2020-08-29 | 6:27 | 49.98
2020-08-29 | 6:27 | 49.98
2020-08-29 | 6:27 | 49.98
2020-08-29 | 6:27 | 49.98
2020-08-29 | 6:27 | 49.982
2020-08-29 | 6:27 | 49.982
2020-08-29 | 6:27 | 49.982
2020-08-29 | 6:27 | 49.982
2020-08-29 | 6:28 | 49.982
2020-08-29 | 6:28 | 49.984
2020-08-29 | 6:28 | 49.985
2020-08-29 | 6:28 | 49.985
2020-08-29 | 6:28 | 49.984
2020-08-29 | 6:28 | 49.983
2020-08-29 | 6:28 | 49.982
2020-08-29 | 6:28 | 49.982
2020-08-29 | 6:28 | 49.981
2020-08-29 | 6:28 | 49.982
2020-08-29 | 6:28 | 49.984
2020-08-29 | 6:28 | 49.983
2020-08-29 | 6:28 | 49.984
2020-08-29 | 6:28 | 49.984
2020-08-29 | 6:28 | 49.984
2020-08-29 | 6:28 | 49.983
2020-08-29 | 6:28 | 49.982
2020-08-29 | 6:28 | 49.981
2020-08-29 | 6:28 | 49.978
2020-08-29 | 6:28 | 49.974
2020-08-29 | 6:28 | 49.97
2020-08-29 | 6:28 | 49.969
2020-08-29 | 6:28 | 49.97
2020-08-29 | 6:28 | 49.973
2020-08-29 | 6:28 | 49.977
2020-08-29 | 6:28 | 49.979
2020-08-29 | 6:28 | 49.979
2020-08-29 | 6:28 | 49.978
2020-08-29 | 6:28 | 49.981
2020-08-29 | 6:28 | 49.982
2020-08-29 | 6:28 | 49.98
2020-08-29 | 6:28 | 49.979
2020-08-29 | 6:28 | 49.977
2020-08-29 | 6:28 | 49.978
2020-08-29 | 6:28 | 49.978
2020-08-29 | 6:28 | 49.98
2020-08-29 | 6:28 | 49.984
2020-08-29 | 6:28 | 49.984
2020-08-29 | 6:28 | 49.985
2020-08-29 | 6:28 | 49.985
2020-08-29 | 6:28 | 49.985
2020-08-29 | 6:28 | 49.987
2020-08-29 | 6:28 | 49.991
2020-08-29 | 6:28 | 49.995
2020-08-29 | 6:28 | 50
2020-08-29 | 6:28 | 50.002
2020-08-29 | 6:28 | 50.006
2020-08-29 | 6:28 | 50.011
2020-08-29 | 6:28 | 50.018
2020-08-29 | 6:28 | 50.022
2020-08-29 | 6:28 | 50.021
2020-08-29 | 6:28 | 50.021
2020-08-29 | 6:28 | 50.019
2020-08-29 | 6:28 | 50.017
2020-08-29 | 6:28 | 50.016
2020-08-29 | 6:28 | 50.016
2020-08-29 | 6:28 | 50.016
2020-08-29 | 6:28 | 50.011
2020-08-29 | 6:28 | 50.008
2020-08-29 | 6:29 | 50.003
2020-08-29 | 6:29 | 50.001
2020-08-29 | 6:29 | 49.997
2020-08-29 | 6:29 | 49.993
2020-08-29 | 6:29 | 49.988
2020-08-29 | 6:29 | 49.987
2020-08-29 | 6:29 | 49.983
2020-08-29 | 6:29 | 49.98
2020-08-29 | 6:29 | 49.983
2020-08-29 | 6:29 | 49.984
2020-08-29 | 6:29 | 49.985
2020-08-29 | 6:29 | 49.984
2020-08-29 | 6:29 | 49.982
2020-08-29 | 6:29 | 49.981
2020-08-29 | 6:29 | 49.98
2020-08-29 | 6:29 | 49.978
2020-08-29 | 6:29 | 49.975
2020-08-29 | 6:29 | 49.972
2020-08-29 | 6:29 | 49.965
2020-08-29 | 6:29 | 49.961
2020-08-29 | 6:29 | 49.954
2020-08-29 | 6:29 | 49.95
2020-08-29 | 6:29 | 49.943
2020-08-29 | 6:29 | 49.941
2020-08-29 | 6:29 | 49.941
2020-08-29 | 6:29 | 49.94
2020-08-29 | 6:29 | 49.94
2020-08-29 | 6:29 | 49.942
2020-08-29 | 6:29 | 49.943
2020-08-29 | 6:29 | 49.94
2020-08-29 | 6:29 | 49.938
2020-08-29 | 6:29 | 49.932
2020-08-29 | 6:29 | 49.928
2020-08-29 | 6:29 | 49.923
2020-08-29 | 6:29 | 49.921
2020-08-29 | 6:29 | 49.917
2020-08-29 | 6:29 | 49.917
2020-08-29 | 6:29 | 49.916
2020-08-29 | 6:29 | 49.915
2020-08-29 | 6:29 | 49.912
2020-08-29 | 6:29 | 49.912
2020-08-29 | 6:29 | 49.908
2020-08-29 | 6:29 | 49.905
2020-08-29 | 6:29 | 49.904
2020-08-29 | 6:29 | 49.905
2020-08-29 | 6:29 | 49.906
2020-08-29 | 6:29 | 49.907
2020-08-29 | 6:29 | 49.914
2020-08-29 | 6:29 | 49.919
2020-08-29 | 6:29 | 49.923
2020-08-29 | 6:29 | 49.926
2020-08-29 | 6:29 | 49.929
2020-08-29 | 6:29 | 49.933
2020-08-29 | 6:29 | 49.935
2020-08-29 | 6:29 | 49.934
2020-08-29 | 6:29 | 49.934
2020-08-29 | 6:29 | 49.933
2020-08-29 | 6:29 | 49.93
2020-08-29 | 6:29 | 49.927
2020-08-29 | 6:29 | 49.925
2020-08-29 | 6:29 | 49.923
2020-08-29 | 6:30 | 49.922
2020-08-29 | 6:30 | 49.921
2020-08-29 | 6:30 | 49.92
2020-08-29 | 6:30 | 49.923
2020-08-29 | 6:30 | 49.924
2020-08-29 | 6:30 | 49.923
2020-08-29 | 6:30 | 49.922
2020-08-29 | 6:30 | 49.92
2020-08-29 | 6:30 | 49.92
2020-08-29 | 6:30 | 49.919
2020-08-29 | 6:30 | 49.921
2020-08-29 | 6:30 | 49.921
2020-08-29 | 6:30 | 49.92
2020-08-29 | 6:30 | 49.92
2020-08-29 | 6:30 | 49.921
2020-08-29 | 6:30 | 49.919
2020-08-29 | 6:30 | 49.919
2020-08-29 | 6:30 | 49.918
2020-08-29 | 6:30 | 49.917
2020-08-29 | 6:30 | 49.917
2020-08-29 | 6:30 | 49.918
2020-08-29 | 6:30 | 49.919
2020-08-29 | 6:30 | 49.919
2020-08-29 | 6:30 | 49.919
2020-08-29 | 6:30 | 49.917
2020-08-29 | 6:30 | 49.92
2020-08-29 | 6:30 | 49.923
2020-08-29 | 6:30 | 49.925
2020-08-29 | 6:30 | 49.924
2020-08-29 | 6:30 | 49.923
2020-08-29 | 6:30 | 49.923
2020-08-29 | 6:30 | 49.924
2020-08-29 | 6:30 | 49.919
2020-08-29 | 6:30 | 49.918
2020-08-29 | 6:30 | 49.917
2020-08-29 | 6:30 | 49.917
2020-08-29 | 6:30 | 49.92
2020-08-29 | 6:30 | 49.921
2020-08-29 | 6:30 | 49.918
2020-08-29 | 6:30 | 49.916
2020-08-29 | 6:30 | 49.917
2020-08-29 | 6:30 | 49.914
2020-08-29 | 6:30 | 49.913
2020-08-29 | 6:30 | 49.913
2020-08-29 | 6:30 | 49.912
2020-08-29 | 6:30 | 49.916
2020-08-29 | 6:30 | 49.918
2020-08-29 | 6:30 | 49.923
2020-08-29 | 6:30 | 49.926
2020-08-29 | 6:30 | 49.929
2020-08-29 | 6:30 | 49.93
2020-08-29 | 6:30 | 49.932
2020-08-29 | 6:30 | 49.932
2020-08-29 | 6:30 | 49.935
2020-08-29 | 6:30 | 49.935
2020-08-29 | 6:30 | 49.938
2020-08-29 | 6:30 | 49.94
2020-08-29 | 6:30 | 49.944
2020-08-29 | 6:30 | 49.947
2020-08-29 | 6:31 | 49.948
2020-08-29 | 6:31 | 49.951
2020-08-29 | 6:31 | 49.955
2020-08-29 | 6:31 | 49.959
2020-08-29 | 6:31 | 49.959
2020-08-29 | 6:31 | 49.956
2020-08-29 | 6:31 | 49.957
2020-08-29 | 6:31 | 49.955
2020-08-29 | 6:31 | 49.954
2020-08-29 | 6:31 | 49.954
2020-08-29 | 6:31 | 49.952
2020-08-29 | 6:31 | 49.953
2020-08-29 | 6:31 | 49.951
2020-08-29 | 6:31 | 49.948
2020-08-29 | 6:31 | 49.946
2020-08-29 | 6:31 | 49.945
2020-08-29 | 6:31 | 49.944
2020-08-29 | 6:31 | 49.943
2020-08-29 | 6:31 | 49.943
2020-08-29 | 6:31 | 49.942
2020-08-29 | 6:31 | 49.941
2020-08-29 | 6:31 | 49.938
2020-08-29 | 6:31 | 49.937
2020-08-29 | 6:31 | 49.938
2020-08-29 | 6:31 | 49.936
2020-08-29 | 6:31 | 49.932
2020-08-29 | 6:31 | 49.933
2020-08-29 | 6:31 | 49.933
2020-08-29 | 6:31 | 49.931
2020-08-29 | 6:31 | 49.934
2020-08-29 | 6:31 | 49.937
2020-08-29 | 6:31 | 49.937
2020-08-29 | 6:31 | 49.937
2020-08-29 | 6:31 | 49.932
2020-08-29 | 6:31 | 49.931
2020-08-29 | 6:31 | 49.93
2020-08-29 | 6:31 | 49.929
2020-08-29 | 6:31 | 49.927
2020-08-29 | 6:31 | 49.926
2020-08-29 | 6:31 | 49.923
2020-08-29 | 6:31 | 49.922
2020-08-29 | 6:31 | 49.919
2020-08-29 | 6:31 | 49.917
2020-08-29 | 6:31 | 49.914
2020-08-29 | 6:31 | 49.911
2020-08-29 | 6:31 | 49.906
2020-08-29 | 6:31 | 49.903
2020-08-29 | 6:31 | 49.903
2020-08-29 | 6:31 | 49.903
2020-08-29 | 6:31 | 49.904
2020-08-29 | 6:31 | 49.903
2020-08-29 | 6:31 | 49.902
2020-08-29 | 6:31 | 49.902
2020-08-29 | 6:31 | 49.899
2020-08-29 | 6:31 | 49.901
2020-08-29 | 6:31 | 49.896
2020-08-29 | 6:31 | 49.897
2020-08-29 | 6:31 | 49.892
2020-08-29 | 6:31 | 49.887
2020-08-29 | 6:31 | 49.884
2020-08-29 | 6:31 | 49.884
2020-08-29 | 6:32 | 49.88
2020-08-29 | 6:32 | 49.878
2020-08-29 | 6:32 | 49.877
2020-08-29 | 6:32 | 49.874
2020-08-29 | 6:32 | 49.87
2020-08-29 | 6:32 | 49.866
2020-08-29 | 6:32 | 49.866
2020-08-29 | 6:32 | 49.863
2020-08-29 | 6:32 | 49.863
2020-08-29 | 6:32 | 49.866
2020-08-29 | 6:32 | 49.87
2020-08-29 | 6:32 | 49.867
2020-08-29 | 6:32 | 49.868
2020-08-29 | 6:32 | 49.871
2020-08-29 | 6:32 | 49.875
2020-08-29 | 6:32 | 49.881
2020-08-29 | 6:32 | 49.885
2020-08-29 | 6:32 | 49.886
2020-08-29 | 6:32 | 49.888
2020-08-29 | 6:32 | 49.891
2020-08-29 | 6:32 | 49.89
2020-08-29 | 6:32 | 49.894
2020-08-29 | 6:32 | 49.898
2020-08-29 | 6:32 | 49.902
2020-08-29 | 6:32 | 49.903
2020-08-29 | 6:32 | 49.903
2020-08-29 | 6:32 | 49.907
2020-08-29 | 6:32 | 49.906
2020-08-29 | 6:32 | 49.909
2020-08-29 | 6:32 | 49.908
2020-08-29 | 6:32 | 49.91
2020-08-29 | 6:32 | 49.908
2020-08-29 | 6:32 | 49.91
2020-08-29 | 6:32 | 49.908
2020-08-29 | 6:32 | 49.905
2020-08-29 | 6:32 | 49.904
2020-08-29 | 6:32 | 49.898
2020-08-29 | 6:32 | 49.892
2020-08-29 | 6:32 | 49.882
2020-08-29 | 6:32 | 49.876
2020-08-29 | 6:32 | 49.873
2020-08-29 | 6:32 | 49.875
2020-08-29 | 6:32 | 49.876
2020-08-29 | 6:32 | 49.877
2020-08-29 | 6:32 | 49.877
2020-08-29 | 6:32 | 49.875
2020-08-29 | 6:32 | 49.871
2020-08-29 | 6:32 | 49.868
2020-08-29 | 6:32 | 49.866
2020-08-29 | 6:32 | 49.862
2020-08-29 | 6:32 | 49.866
2020-08-29 | 6:32 | 49.864
2020-08-29 | 6:32 | 49.865
2020-08-29 | 6:32 | 49.866
2020-08-29 | 6:32 | 49.867
2020-08-29 | 6:32 | 49.863
2020-08-29 | 6:32 | 49.86
2020-08-29 | 6:32 | 49.855
2020-08-29 | 6:32 | 49.852
2020-08-29 | 6:33 | 49.85
2020-08-29 | 6:33 | 49.852
2020-08-29 | 6:33 | 49.853
2020-08-29 | 6:33 | 49.856
2020-08-29 | 6:33 | 49.857
2020-08-29 | 6:33 | 49.857
2020-08-29 | 6:33 | 49.857
2020-08-29 | 6:33 | 49.859
2020-08-29 | 6:33 | 49.858
2020-08-29 | 6:33 | 49.862
2020-08-29 | 6:33 | 49.864
2020-08-29 | 6:33 | 49.866
2020-08-29 | 6:33 | 49.866
2020-08-29 | 6:33 | 49.865
2020-08-29 | 6:33 | 49.866
2020-08-29 | 6:33 | 49.867
2020-08-29 | 6:33 | 49.871
2020-08-29 | 6:33 | 49.872
2020-08-29 | 6:33 | 49.872
2020-08-29 | 6:33 | 49.87
2020-08-29 | 6:33 | 49.865
2020-08-29 | 6:33 | 49.865
2020-08-29 | 6:33 | 49.864
2020-08-29 | 6:33 | 49.861
2020-08-29 | 6:33 | 49.863
2020-08-29 | 6:33 | 49.864
2020-08-29 | 6:33 | 49.867
2020-08-29 | 6:33 | 49.867
2020-08-29 | 6:33 | 49.865
2020-08-29 | 6:33 | 49.863
2020-08-29 | 6:33 | 49.859
2020-08-29 | 6:33 | 49.858
2020-08-29 | 6:33 | 49.856
2020-08-29 | 6:33 | 49.856
2020-08-29 | 6:33 | 49.86
2020-08-29 | 6:33 | 49.867
2020-08-29 | 6:33 | 49.873
2020-08-29 | 6:33 | 49.88
2020-08-29 | 6:33 | 49.883
2020-08-29 | 6:33 | 49.885
2020-08-29 | 6:33 | 49.885
2020-08-29 | 6:33 | 49.888
2020-08-29 | 6:33 | 49.891
2020-08-29 | 6:33 | 49.898
2020-08-29 | 6:33 | 49.901
2020-08-29 | 6:33 | 49.905
2020-08-29 | 6:33 | 49.912
2020-08-29 | 6:33 | 49.918
2020-08-29 | 6:33 | 49.929
2020-08-29 | 6:33 | 49.937
2020-08-29 | 6:33 | 49.942
2020-08-29 | 6:33 | 49.944
2020-08-29 | 6:33 | 49.945
2020-08-29 | 6:33 | 49.942
2020-08-29 | 6:33 | 49.938
2020-08-29 | 6:33 | 49.934
2020-08-29 | 6:33 | 49.931
2020-08-29 | 6:33 | 49.933
2020-08-29 | 6:33 | 49.933
2020-08-29 | 6:33 | 49.936
2020-08-29 | 6:34 | 49.936
2020-08-29 | 6:34 | 49.933
2020-08-29 | 6:34 | 49.93
2020-08-29 | 6:34 | 49.927
2020-08-29 | 6:34 | 49.922
2020-08-29 | 6:34 | 49.919
2020-08-29 | 6:34 | 49.918
2020-08-29 | 6:34 | 49.919
2020-08-29 | 6:34 | 49.922
2020-08-29 | 6:34 | 49.926
2020-08-29 | 6:34 | 49.928
2020-08-29 | 6:34 | 49.927
2020-08-29 | 6:34 | 49.926
2020-08-29 | 6:34 | 49.923
2020-08-29 | 6:34 | 49.922
2020-08-29 | 6:34 | 49.916
2020-08-29 | 6:34 | 49.914
2020-08-29 | 6:34 | 49.914
2020-08-29 | 6:34 | 49.913
2020-08-29 | 6:34 | 49.912
2020-08-29 | 6:34 | 49.91
2020-08-29 | 6:34 | 49.905
2020-08-29 | 6:34 | 49.905
2020-08-29 | 6:34 | 49.901
2020-08-29 | 6:34 | 49.896
2020-08-29 | 6:34 | 49.898
2020-08-29 | 6:34 | 49.899
2020-08-29 | 6:34 | 49.9
2020-08-29 | 6:34 | 49.899
2020-08-29 | 6:34 | 49.901
2020-08-29 | 6:34 | 49.902
2020-08-29 | 6:34 | 49.906
2020-08-29 | 6:34 | 49.909
2020-08-29 | 6:34 | 49.91
2020-08-29 | 6:34 | 49.909
2020-08-29 | 6:34 | 49.91
2020-08-29 | 6:34 | 49.903
2020-08-29 | 6:34 | 49.901
2020-08-29 | 6:34 | 49.9
2020-08-29 | 6:34 | 49.9
2020-08-29 | 6:34 | 49.9
2020-08-29 | 6:34 | 49.9
2020-08-29 | 6:34 | 49.9
2020-08-29 | 6:34 | 49.901
2020-08-29 | 6:34 | 49.906
2020-08-29 | 6:34 | 49.909
2020-08-29 | 6:34 | 49.91
2020-08-29 | 6:34 | 49.911
2020-08-29 | 6:34 | 49.908
2020-08-29 | 6:34 | 49.907
2020-08-29 | 6:34 | 49.903
2020-08-29 | 6:34 | 49.901
2020-08-29 | 6:34 | 49.899
2020-08-29 | 6:34 | 49.897
2020-08-29 | 6:34 | 49.896
2020-08-29 | 6:34 | 49.896
2020-08-29 | 6:34 | 49.894
2020-08-29 | 6:34 | 49.895
2020-08-29 | 6:34 | 49.895
2020-08-29 | 6:34 | 49.895
2020-08-29 | 6:34 | 49.898
2020-08-29 | 6:35 | 49.903
2020-08-29 | 6:35 | 49.903
2020-08-29 | 6:35 | 49.905
2020-08-29 | 6:35 | 49.907
2020-08-29 | 6:35 | 49.91
2020-08-29 | 6:35 | 49.91
2020-08-29 | 6:35 | 49.91
2020-08-29 | 6:35 | 49.913
2020-08-29 | 6:35 | 49.915
2020-08-29 | 6:35 | 49.917
2020-08-29 | 6:35 | 49.918
2020-08-29 | 6:35 | 49.918
2020-08-29 | 6:35 | 49.919
2020-08-29 | 6:35 | 49.919
2020-08-29 | 6:35 | 49.921
2020-08-29 | 6:35 | 49.918
2020-08-29 | 6:35 | 49.917
2020-08-29 | 6:35 | 49.917
2020-08-29 | 6:35 | 49.919
2020-08-29 | 6:35 | 49.919
2020-08-29 | 6:35 | 49.92
2020-08-29 | 6:35 | 49.917
2020-08-29 | 6:35 | 49.917
2020-08-29 | 6:35 | 49.921
2020-08-29 | 6:35 | 49.924
2020-08-29 | 6:35 | 49.922
2020-08-29 | 6:35 | 49.921
2020-08-29 | 6:35 | 49.918
2020-08-29 | 6:35 | 49.917
2020-08-29 | 6:35 | 49.917
2020-08-29 | 6:35 | 49.916
2020-08-29 | 6:35 | 49.913
2020-08-29 | 6:35 | 49.914
2020-08-29 | 6:35 | 49.913
2020-08-29 | 6:35 | 49.912
2020-08-29 | 6:35 | 49.911
2020-08-29 | 6:35 | 49.908
2020-08-29 | 6:35 | 49.905
2020-08-29 | 6:35 | 49.905
2020-08-29 | 6:35 | 49.906
2020-08-29 | 6:35 | 49.905
2020-08-29 | 6:35 | 49.906
2020-08-29 | 6:35 | 49.908
2020-08-29 | 6:35 | 49.909
2020-08-29 | 6:35 | 49.909
2020-08-29 | 6:35 | 49.909
2020-08-29 | 6:35 | 49.909
2020-08-29 | 6:35 | 49.907
2020-08-29 | 6:35 | 49.906
2020-08-29 | 6:35 | 49.906
2020-08-29 | 6:35 | 49.908
2020-08-29 | 6:35 | 49.906
2020-08-29 | 6:35 | 49.906
2020-08-29 | 6:35 | 49.905
2020-08-29 | 6:35 | 49.908
2020-08-29 | 6:35 | 49.909
2020-08-29 | 6:35 | 49.913
2020-08-29 | 6:35 | 49.916
2020-08-29 | 6:35 | 49.919
2020-08-29 | 6:36 | 49.92
2020-08-29 | 6:36 | 49.922
2020-08-29 | 6:36 | 49.925
2020-08-29 | 6:36 | 49.926
2020-08-29 | 6:36 | 49.924
2020-08-29 | 6:36 | 49.923
2020-08-29 | 6:36 | 49.922
2020-08-29 | 6:36 | 49.923
2020-08-29 | 6:36 | 49.923
2020-08-29 | 6:36 | 49.921
2020-08-29 | 6:36 | 49.92
2020-08-29 | 6:36 | 49.92
2020-08-29 | 6:36 | 49.919
2020-08-29 | 6:36 | 49.919
2020-08-29 | 6:36 | 49.916
2020-08-29 | 6:36 | 49.916
2020-08-29 | 6:36 | 49.918
2020-08-29 | 6:36 | 49.924
2020-08-29 | 6:36 | 49.927
2020-08-29 | 6:36 | 49.931
2020-08-29 | 6:36 | 49.932
2020-08-29 | 6:36 | 49.931
2020-08-29 | 6:36 | 49.926
2020-08-29 | 6:36 | 49.924
2020-08-29 | 6:36 | 49.921
2020-08-29 | 6:36 | 49.921
2020-08-29 | 6:36 | 49.921
2020-08-29 | 6:36 | 49.921
2020-08-29 | 6:36 | 49.922
2020-08-29 | 6:36 | 49.926
2020-08-29 | 6:36 | 49.929
2020-08-29 | 6:36 | 49.929
2020-08-29 | 6:36 | 49.926
2020-08-29 | 6:36 | 49.928
2020-08-29 | 6:36 | 49.928
2020-08-29 | 6:36 | 49.928
2020-08-29 | 6:36 | 49.928
2020-08-29 | 6:36 | 49.927
2020-08-29 | 6:36 | 49.929
2020-08-29 | 6:36 | 49.932
2020-08-29 | 6:36 | 49.935
2020-08-29 | 6:36 | 49.937
2020-08-29 | 6:36 | 49.938
2020-08-29 | 6:36 | 49.938
2020-08-29 | 6:36 | 49.938
2020-08-29 | 6:36 | 49.938
2020-08-29 | 6:36 | 49.936
2020-08-29 | 6:36 | 49.934
2020-08-29 | 6:36 | 49.933
2020-08-29 | 6:36 | 49.932
2020-08-29 | 6:36 | 49.929
2020-08-29 | 6:36 | 49.93
2020-08-29 | 6:36 | 49.928
2020-08-29 | 6:36 | 49.924
2020-08-29 | 6:36 | 49.923
2020-08-29 | 6:36 | 49.923
2020-08-29 | 6:36 | 49.923
2020-08-29 | 6:36 | 49.923
2020-08-29 | 6:36 | 49.924
2020-08-29 | 6:36 | 49.926
2020-08-29 | 6:36 | 49.926
2020-08-29 | 6:37 | 49.927
2020-08-29 | 6:37 | 49.93
2020-08-29 | 6:37 | 49.934
2020-08-29 | 6:37 | 49.936
2020-08-29 | 6:37 | 49.937
2020-08-29 | 6:37 | 49.937
2020-08-29 | 6:37 | 49.937
2020-08-29 | 6:37 | 49.937
2020-08-29 | 6:37 | 49.937
2020-08-29 | 6:37 | 49.936
2020-08-29 | 6:37 | 49.935
2020-08-29 | 6:37 | 49.937
2020-08-29 | 6:37 | 49.94
2020-08-29 | 6:37 | 49.945
2020-08-29 | 6:37 | 49.948
2020-08-29 | 6:37 | 49.949
2020-08-29 | 6:37 | 49.949
2020-08-29 | 6:37 | 49.949
2020-08-29 | 6:37 | 49.951
2020-08-29 | 6:37 | 49.953
2020-08-29 | 6:37 | 49.952
2020-08-29 | 6:37 | 49.949
2020-08-29 | 6:37 | 49.948
2020-08-29 | 6:37 | 49.948
2020-08-29 | 6:37 | 49.948
2020-08-29 | 6:37 | 49.947
2020-08-29 | 6:37 | 49.949
2020-08-29 | 6:37 | 49.953
2020-08-29 | 6:37 | 49.951
2020-08-29 | 6:37 | 49.946
2020-08-29 | 6:37 | 49.94
2020-08-29 | 6:37 | 49.934
2020-08-29 | 6:37 | 49.933
2020-08-29 | 6:37 | 49.932
2020-08-29 | 6:37 | 49.93
2020-08-29 | 6:37 | 49.932
2020-08-29 | 6:37 | 49.935
2020-08-29 | 6:37 | 49.939
2020-08-29 | 6:37 | 49.945
2020-08-29 | 6:37 | 49.947
2020-08-29 | 6:37 | 49.947
2020-08-29 | 6:37 | 49.949
2020-08-29 | 6:37 | 49.95
2020-08-29 | 6:37 | 49.95
2020-08-29 | 6:37 | 49.953
2020-08-29 | 6:37 | 49.958
2020-08-29 | 6:37 | 49.96
2020-08-29 | 6:37 | 49.962
2020-08-29 | 6:37 | 49.965
2020-08-29 | 6:37 | 49.967
2020-08-29 | 6:37 | 49.967
2020-08-29 | 6:37 | 49.967
2020-08-29 | 6:37 | 49.964
2020-08-29 | 6:37 | 49.961
2020-08-29 | 6:37 | 49.959
2020-08-29 | 6:37 | 49.959
2020-08-29 | 6:37 | 49.96
2020-08-29 | 6:37 | 49.959
2020-08-29 | 6:37 | 49.96
2020-08-29 | 6:38 | 49.96
2020-08-29 | 6:38 | 49.96
2020-08-29 | 6:38 | 49.96
2020-08-29 | 6:38 | 49.959
2020-08-29 | 6:38 | 49.961
2020-08-29 | 6:38 | 49.959
2020-08-29 | 6:38 | 49.958
2020-08-29 | 6:38 | 49.958
2020-08-29 | 6:38 | 49.958
2020-08-29 | 6:38 | 49.96
2020-08-29 | 6:38 | 49.965
2020-08-29 | 6:38 | 49.969
2020-08-29 | 6:38 | 49.972
2020-08-29 | 6:38 | 49.974
2020-08-29 | 6:38 | 49.975
2020-08-29 | 6:38 | 49.973
2020-08-29 | 6:38 | 49.974
2020-08-29 | 6:38 | 49.974
2020-08-29 | 6:38 | 49.975
2020-08-29 | 6:38 | 49.976
2020-08-29 | 6:38 | 49.977
2020-08-29 | 6:38 | 49.976
2020-08-29 | 6:38 | 49.98
2020-08-29 | 6:38 | 49.985
2020-08-29 | 6:38 | 49.986
2020-08-29 | 6:38 | 49.989
2020-08-29 | 6:38 | 49.991
2020-08-29 | 6:38 | 49.994
2020-08-29 | 6:38 | 49.995
2020-08-29 | 6:38 | 49.993
2020-08-29 | 6:38 | 49.99
2020-08-29 | 6:38 | 49.99
2020-08-29 | 6:38 | 49.989
2020-08-29 | 6:38 | 49.987
2020-08-29 | 6:38 | 49.987
2020-08-29 | 6:38 | 49.983
2020-08-29 | 6:38 | 49.98
2020-08-29 | 6:38 | 49.98
2020-08-29 | 6:38 | 49.978
2020-08-29 | 6:38 | 49.976
2020-08-29 | 6:38 | 49.976
2020-08-29 | 6:38 | 49.976
2020-08-29 | 6:38 | 49.977
2020-08-29 | 6:38 | 49.979
2020-08-29 | 6:38 | 49.979
2020-08-29 | 6:38 | 49.978
2020-08-29 | 6:38 | 49.981
2020-08-29 | 6:38 | 49.981
2020-08-29 | 6:38 | 49.981
2020-08-29 | 6:38 | 49.98
2020-08-29 | 6:38 | 49.977
2020-08-29 | 6:38 | 49.975
2020-08-29 | 6:38 | 49.976
2020-08-29 | 6:38 | 49.977
2020-08-29 | 6:38 | 49.978
2020-08-29 | 6:38 | 49.979
2020-08-29 | 6:38 | 49.979
2020-08-29 | 6:38 | 49.978
2020-08-29 | 6:38 | 49.976
2020-08-29 | 6:38 | 49.976
2020-08-29 | 6:38 | 49.977
2020-08-29 | 6:39 | 49.977
2020-08-29 | 6:39 | 49.978
2020-08-29 | 6:39 | 49.979
2020-08-29 | 6:39 | 49.978
2020-08-29 | 6:39 | 49.979
2020-08-29 | 6:39 | 49.98
2020-08-29 | 6:39 | 49.98
2020-08-29 | 6:39 | 49.977
2020-08-29 | 6:39 | 49.974
2020-08-29 | 6:39 | 49.971
2020-08-29 | 6:39 | 49.967
2020-08-29 | 6:39 | 49.965
2020-08-29 | 6:39 | 49.962
2020-08-29 | 6:39 | 49.96
2020-08-29 | 6:39 | 49.954
2020-08-29 | 6:39 | 49.949
2020-08-29 | 6:39 | 49.947
2020-08-29 | 6:39 | 49.947
2020-08-29 | 6:39 | 49.947
2020-08-29 | 6:39 | 49.95
2020-08-29 | 6:39 | 49.953
2020-08-29 | 6:39 | 49.953
2020-08-29 | 6:39 | 49.949
2020-08-29 | 6:39 | 49.943
2020-08-29 | 6:39 | 49.937
2020-08-29 | 6:39 | 49.927
2020-08-29 | 6:39 | 49.918
2020-08-29 | 6:39 | 49.91
2020-08-29 | 6:39 | 49.902
2020-08-29 | 6:39 | 49.893
2020-08-29 | 6:39 | 49.888
2020-08-29 | 6:39 | 49.89
2020-08-29 | 6:39 | 49.891
2020-08-29 | 6:39 | 49.891
2020-08-29 | 6:39 | 49.893
2020-08-29 | 6:39 | 49.896
2020-08-29 | 6:39 | 49.896
2020-08-29 | 6:39 | 49.894
2020-08-29 | 6:39 | 49.895
2020-08-29 | 6:39 | 49.895
2020-08-29 | 6:39 | 49.893
2020-08-29 | 6:39 | 49.892
2020-08-29 | 6:39 | 49.892
2020-08-29 | 6:39 | 49.894
2020-08-29 | 6:39 | 49.893
2020-08-29 | 6:39 | 49.895
2020-08-29 | 6:39 | 49.898
2020-08-29 | 6:39 | 49.896
2020-08-29 | 6:39 | 49.9
2020-08-29 | 6:39 | 49.901
2020-08-29 | 6:39 | 49.9
2020-08-29 | 6:39 | 49.901
2020-08-29 | 6:39 | 49.903
2020-08-29 | 6:39 | 49.904
2020-08-29 | 6:39 | 49.905
2020-08-29 | 6:39 | 49.905
2020-08-29 | 6:39 | 49.905
2020-08-29 | 6:39 | 49.907
2020-08-29 | 6:39 | 49.906
2020-08-29 | 6:40 | 49.906
2020-08-29 | 6:40 | 49.907
2020-08-29 | 6:40 | 49.906
2020-08-29 | 6:40 | 49.905
2020-08-29 | 6:40 | 49.906
2020-08-29 | 6:40 | 49.905
2020-08-29 | 6:40 | 49.904
2020-08-29 | 6:40 | 49.905
2020-08-29 | 6:40 | 49.905
2020-08-29 | 6:40 | 49.908
2020-08-29 | 6:40 | 49.912
2020-08-29 | 6:40 | 49.913
2020-08-29 | 6:40 | 49.916
2020-08-29 | 6:40 | 49.915
2020-08-29 | 6:40 | 49.91
2020-08-29 | 6:40 | 49.907
2020-08-29 | 6:40 | 49.905
2020-08-29 | 6:40 | 49.905
2020-08-29 | 6:40 | 49.904
2020-08-29 | 6:40 | 49.904
2020-08-29 | 6:40 | 49.907
2020-08-29 | 6:40 | 49.913
2020-08-29 | 6:40 | 49.917
2020-08-29 | 6:40 | 49.917
2020-08-29 | 6:40 | 49.919
2020-08-29 | 6:40 | 49.924
2020-08-29 | 6:40 | 49.926
2020-08-29 | 6:40 | 49.933
2020-08-29 | 6:40 | 49.932
2020-08-29 | 6:40 | 49.931
2020-08-29 | 6:40 | 49.929
2020-08-29 | 6:40 | 49.927
2020-08-29 | 6:40 | 49.923
2020-08-29 | 6:40 | 49.926
2020-08-29 | 6:40 | 49.932
2020-08-29 | 6:40 | 49.936
2020-08-29 | 6:40 | 49.939
2020-08-29 | 6:40 | 49.937
2020-08-29 | 6:40 | 49.934
2020-08-29 | 6:40 | 49.936
2020-08-29 | 6:40 | 49.935
2020-08-29 | 6:40 | 49.934
2020-08-29 | 6:40 | 49.931
2020-08-29 | 6:40 | 49.925
2020-08-29 | 6:40 | 49.92
2020-08-29 | 6:40 | 49.918
2020-08-29 | 6:40 | 49.911
2020-08-29 | 6:40 | 49.909
2020-08-29 | 6:40 | 49.911
2020-08-29 | 6:40 | 49.91
2020-08-29 | 6:40 | 49.911
2020-08-29 | 6:40 | 49.912
2020-08-29 | 6:40 | 49.909
2020-08-29 | 6:40 | 49.91
2020-08-29 | 6:40 | 49.91
2020-08-29 | 6:40 | 49.911
2020-08-29 | 6:40 | 49.911
2020-08-29 | 6:40 | 49.909
2020-08-29 | 6:40 | 49.915
2020-08-29 | 6:40 | 49.914
2020-08-29 | 6:40 | 49.917
2020-08-29 | 6:41 | 49.919
2020-08-29 | 6:41 | 49.922
2020-08-29 | 6:41 | 49.927
2020-08-29 | 6:41 | 49.929
2020-08-29 | 6:41 | 49.934
2020-08-29 | 6:41 | 49.937
2020-08-29 | 6:41 | 49.939
2020-08-29 | 6:41 | 49.941
2020-08-29 | 6:41 | 49.94
2020-08-29 | 6:41 | 49.942
2020-08-29 | 6:41 | 49.939
2020-08-29 | 6:41 | 49.935
2020-08-29 | 6:41 | 49.928
2020-08-29 | 6:41 | 49.921
2020-08-29 | 6:41 | 49.917
2020-08-29 | 6:41 | 49.915
2020-08-29 | 6:41 | 49.915
2020-08-29 | 6:41 | 49.918
2020-08-29 | 6:41 | 49.921
2020-08-29 | 6:41 | 49.922
2020-08-29 | 6:41 | 49.926
2020-08-29 | 6:41 | 49.926
2020-08-29 | 6:41 | 49.925
2020-08-29 | 6:41 | 49.925
2020-08-29 | 6:41 | 49.923
2020-08-29 | 6:41 | 49.922
2020-08-29 | 6:41 | 49.921
2020-08-29 | 6:41 | 49.921
2020-08-29 | 6:41 | 49.921
2020-08-29 | 6:41 | 49.924
2020-08-29 | 6:41 | 49.924
2020-08-29 | 6:41 | 49.922
2020-08-29 | 6:41 | 49.923
2020-08-29 | 6:41 | 49.922
2020-08-29 | 6:41 | 49.92
2020-08-29 | 6:41 | 49.92
2020-08-29 | 6:41 | 49.919
2020-08-29 | 6:41 | 49.917
2020-08-29 | 6:41 | 49.917
2020-08-29 | 6:41 | 49.919
2020-08-29 | 6:41 | 49.92
2020-08-29 | 6:41 | 49.921
2020-08-29 | 6:41 | 49.92
2020-08-29 | 6:41 | 49.923
2020-08-29 | 6:41 | 49.924
2020-08-29 | 6:41 | 49.924
2020-08-29 | 6:41 | 49.922
2020-08-29 | 6:41 | 49.921
2020-08-29 | 6:41 | 49.918
2020-08-29 | 6:41 | 49.917
2020-08-29 | 6:41 | 49.92
2020-08-29 | 6:41 | 49.923
2020-08-29 | 6:41 | 49.925
2020-08-29 | 6:41 | 49.927
2020-08-29 | 6:41 | 49.929
2020-08-29 | 6:41 | 49.93
2020-08-29 | 6:41 | 49.931
2020-08-29 | 6:41 | 49.931
2020-08-29 | 6:41 | 49.932
2020-08-29 | 6:41 | 49.932
2020-08-29 | 6:42 | 49.931
2020-08-29 | 6:42 | 49.932
2020-08-29 | 6:42 | 49.932
2020-08-29 | 6:42 | 49.932
2020-08-29 | 6:42 | 49.932
2020-08-29 | 6:42 | 49.931
2020-08-29 | 6:42 | 49.932
2020-08-29 | 6:42 | 49.932
2020-08-29 | 6:42 | 49.931
2020-08-29 | 6:42 | 49.929
2020-08-29 | 6:42 | 49.93
2020-08-29 | 6:42 | 49.93
2020-08-29 | 6:42 | 49.928
2020-08-29 | 6:42 | 49.926
2020-08-29 | 6:42 | 49.923
2020-08-29 | 6:42 | 49.923
2020-08-29 | 6:42 | 49.926
2020-08-29 | 6:42 | 49.925
2020-08-29 | 6:42 | 49.927
2020-08-29 | 6:42 | 49.929
2020-08-29 | 6:42 | 49.929
2020-08-29 | 6:42 | 49.929
2020-08-29 | 6:42 | 49.928
2020-08-29 | 6:42 | 49.926
2020-08-29 | 6:42 | 49.928
2020-08-29 | 6:42 | 49.927
2020-08-29 | 6:42 | 49.923
2020-08-29 | 6:42 | 49.922
2020-08-29 | 6:42 | 49.919
2020-08-29 | 6:42 | 49.913
2020-08-29 | 6:42 | 49.906
2020-08-29 | 6:42 | 49.899
2020-08-29 | 6:42 | 49.893
2020-08-29 | 6:42 | 49.893
2020-08-29 | 6:42 | 49.895
2020-08-29 | 6:42 | 49.895
2020-08-29 | 6:42 | 49.897
2020-08-29 | 6:42 | 49.9
2020-08-29 | 6:42 | 49.9
2020-08-29 | 6:42 | 49.897
2020-08-29 | 6:42 | 49.895
2020-08-29 | 6:42 | 49.895
2020-08-29 | 6:42 | 49.893
2020-08-29 | 6:42 | 49.895
2020-08-29 | 6:42 | 49.9
2020-08-29 | 6:42 | 49.903
2020-08-29 | 6:42 | 49.908
2020-08-29 | 6:42 | 49.911
2020-08-29 | 6:42 | 49.91
2020-08-29 | 6:42 | 49.909
2020-08-29 | 6:42 | 49.909
2020-08-29 | 6:42 | 49.91
2020-08-29 | 6:42 | 49.911
2020-08-29 | 6:42 | 49.911
2020-08-29 | 6:42 | 49.912
2020-08-29 | 6:42 | 49.911
2020-08-29 | 6:42 | 49.911
2020-08-29 | 6:42 | 49.914
2020-08-29 | 6:42 | 49.913
2020-08-29 | 6:43 | 49.914
2020-08-29 | 6:43 | 49.914
2020-08-29 | 6:43 | 49.913
2020-08-29 | 6:43 | 49.912
2020-08-29 | 6:43 | 49.911
2020-08-29 | 6:43 | 49.91
2020-08-29 | 6:43 | 49.91
2020-08-29 | 6:43 | 49.911
2020-08-29 | 6:43 | 49.91
2020-08-29 | 6:43 | 49.907
2020-08-29 | 6:43 | 49.904
2020-08-29 | 6:43 | 49.902
2020-08-29 | 6:43 | 49.897
2020-08-29 | 6:43 | 49.894
2020-08-29 | 6:43 | 49.893
2020-08-29 | 6:43 | 49.892
2020-08-29 | 6:43 | 49.892
2020-08-29 | 6:43 | 49.894
2020-08-29 | 6:43 | 49.892
2020-08-29 | 6:43 | 49.888
2020-08-29 | 6:43 | 49.886
2020-08-29 | 6:43 | 49.884
2020-08-29 | 6:43 | 49.883
2020-08-29 | 6:43 | 49.881
2020-08-29 | 6:43 | 49.881
2020-08-29 | 6:43 | 49.88
2020-08-29 | 6:43 | 49.879
2020-08-29 | 6:43 | 49.88
2020-08-29 | 6:43 | 49.882
2020-08-29 | 6:43 | 49.883
2020-08-29 | 6:43 | 49.884
2020-08-29 | 6:43 | 49.883
2020-08-29 | 6:43 | 49.881
2020-08-29 | 6:43 | 49.88
2020-08-29 | 6:43 | 49.879
2020-08-29 | 6:43 | 49.879
2020-08-29 | 6:43 | 49.881
2020-08-29 | 6:43 | 49.884
2020-08-29 | 6:43 | 49.887
2020-08-29 | 6:43 | 49.887
2020-08-29 | 6:43 | 49.888
2020-08-29 | 6:43 | 49.888
2020-08-29 | 6:43 | 49.886
2020-08-29 | 6:43 | 49.883
2020-08-29 | 6:43 | 49.881
2020-08-29 | 6:43 | 49.878
2020-08-29 | 6:43 | 49.875
2020-08-29 | 6:43 | 49.872
2020-08-29 | 6:43 | 49.874
2020-08-29 | 6:43 | 49.875
2020-08-29 | 6:43 | 49.874
2020-08-29 | 6:43 | 49.876
2020-08-29 | 6:43 | 49.877
2020-08-29 | 6:43 | 49.88
2020-08-29 | 6:43 | 49.885
2020-08-29 | 6:43 | 49.891
2020-08-29 | 6:43 | 49.897
2020-08-29 | 6:43 | 49.901
2020-08-29 | 6:43 | 49.902
2020-08-29 | 6:43 | 49.904
2020-08-29 | 6:43 | 49.906
2020-08-29 | 6:44 | 49.905
2020-08-29 | 6:44 | 49.903
2020-08-29 | 6:44 | 49.9
2020-08-29 | 6:44 | 49.9
2020-08-29 | 6:44 | 49.899
2020-08-29 | 6:44 | 49.897
2020-08-29 | 6:44 | 49.896
2020-08-29 | 6:44 | 49.897
2020-08-29 | 6:44 | 49.895
2020-08-29 | 6:44 | 49.889
2020-08-29 | 6:44 | 49.888
2020-08-29 | 6:44 | 49.888
2020-08-29 | 6:44 | 49.885
2020-08-29 | 6:44 | 49.886
2020-08-29 | 6:44 | 49.889
2020-08-29 | 6:44 | 49.89
2020-08-29 | 6:44 | 49.889
2020-08-29 | 6:44 | 49.89
2020-08-29 | 6:44 | 49.888
2020-08-29 | 6:44 | 49.888
2020-08-29 | 6:44 | 49.89
2020-08-29 | 6:44 | 49.888
2020-08-29 | 6:44 | 49.887
2020-08-29 | 6:44 | 49.887
2020-08-29 | 6:44 | 49.889
2020-08-29 | 6:44 | 49.895
2020-08-29 | 6:44 | 49.899
2020-08-29 | 6:44 | 49.898
2020-08-29 | 6:44 | 49.897
2020-08-29 | 6:44 | 49.896
2020-08-29 | 6:44 | 49.893
2020-08-29 | 6:44 | 49.893
2020-08-29 | 6:44 | 49.891
2020-08-29 | 6:44 | 49.887
2020-08-29 | 6:44 | 49.883
2020-08-29 | 6:44 | 49.88
2020-08-29 | 6:44 | 49.875
2020-08-29 | 6:44 | 49.872
2020-08-29 | 6:44 | 49.871
2020-08-29 | 6:44 | 49.871
2020-08-29 | 6:44 | 49.872
2020-08-29 | 6:44 | 49.874
2020-08-29 | 6:44 | 49.876
2020-08-29 | 6:44 | 49.878
2020-08-29 | 6:44 | 49.876
2020-08-29 | 6:44 | 49.872
2020-08-29 | 6:44 | 49.871
2020-08-29 | 6:44 | 49.871
2020-08-29 | 6:44 | 49.876
2020-08-29 | 6:44 | 49.882
2020-08-29 | 6:44 | 49.888
2020-08-29 | 6:44 | 49.896
2020-08-29 | 6:44 | 49.9
2020-08-29 | 6:44 | 49.905
2020-08-29 | 6:44 | 49.909
2020-08-29 | 6:44 | 49.909
2020-08-29 | 6:44 | 49.909
2020-08-29 | 6:44 | 49.91
2020-08-29 | 6:44 | 49.911
2020-08-29 | 6:45 | 49.91
2020-08-29 | 6:45 | 49.908
2020-08-29 | 6:45 | 49.909
2020-08-29 | 6:45 | 49.91
2020-08-29 | 6:45 | 49.912
2020-08-29 | 6:45 | 49.915
2020-08-29 | 6:45 | 49.916
2020-08-29 | 6:45 | 49.914
2020-08-29 | 6:45 | 49.915
2020-08-29 | 6:45 | 49.914
2020-08-29 | 6:45 | 49.913
2020-08-29 | 6:45 | 49.913
2020-08-29 | 6:45 | 49.912
2020-08-29 | 6:45 | 49.911
2020-08-29 | 6:45 | 49.91
2020-08-29 | 6:45 | 49.912
2020-08-29 | 6:45 | 49.911
2020-08-29 | 6:45 | 49.91
2020-08-29 | 6:45 | 49.905
2020-08-29 | 6:45 | 49.903
2020-08-29 | 6:45 | 49.899
2020-08-29 | 6:45 | 49.899
2020-08-29 | 6:45 | 49.9
2020-08-29 | 6:45 | 49.9
2020-08-29 | 6:45 | 49.899
2020-08-29 | 6:45 | 49.9
2020-08-29 | 6:45 | 49.9
2020-08-29 | 6:45 | 49.901
2020-08-29 | 6:45 | 49.899
2020-08-29 | 6:45 | 49.899
2020-08-29 | 6:45 | 49.898
2020-08-29 | 6:45 | 49.895
2020-08-29 | 6:45 | 49.895
2020-08-29 | 6:45 | 49.896
2020-08-29 | 6:45 | 49.896
2020-08-29 | 6:45 | 49.896
2020-08-29 | 6:45 | 49.895
2020-08-29 | 6:45 | 49.892
2020-08-29 | 6:45 | 49.89
2020-08-29 | 6:45 | 49.889
2020-08-29 | 6:45 | 49.885
2020-08-29 | 6:45 | 49.884
2020-08-29 | 6:45 | 49.881
2020-08-29 | 6:45 | 49.882
2020-08-29 | 6:45 | 49.885
2020-08-29 | 6:45 | 49.886
2020-08-29 | 6:45 | 49.887
2020-08-29 | 6:45 | 49.887
2020-08-29 | 6:45 | 49.887
2020-08-29 | 6:45 | 49.884
2020-08-29 | 6:45 | 49.878
2020-08-29 | 6:45 | 49.872
2020-08-29 | 6:45 | 49.866
2020-08-29 | 6:45 | 49.859
2020-08-29 | 6:45 | 49.857
2020-08-29 | 6:45 | 49.855
2020-08-29 | 6:45 | 49.85
2020-08-29 | 6:45 | 49.848
2020-08-29 | 6:45 | 49.846
2020-08-29 | 6:45 | 49.844
2020-08-29 | 6:45 | 49.846
2020-08-29 | 6:46 | 49.847
2020-08-29 | 6:46 | 49.847
2020-08-29 | 6:46 | 49.848
2020-08-29 | 6:46 | 49.845
2020-08-29 | 6:46 | 49.843
2020-08-29 | 6:46 | 49.841
2020-08-29 | 6:46 | 49.838
2020-08-29 | 6:46 | 49.836
2020-08-29 | 6:46 | 49.834
2020-08-29 | 6:46 | 49.831
2020-08-29 | 6:46 | 49.831
2020-08-29 | 6:46 | 49.83
2020-08-29 | 6:46 | 49.828
2020-08-29 | 6:46 | 49.827
2020-08-29 | 6:46 | 49.825
2020-08-29 | 6:46 | 49.822
2020-08-29 | 6:46 | 49.818
2020-08-29 | 6:46 | 49.816
2020-08-29 | 6:46 | 49.815
2020-08-29 | 6:46 | 49.816
2020-08-29 | 6:46 | 49.818
2020-08-29 | 6:46 | 49.815
2020-08-29 | 6:46 | 49.812
2020-08-29 | 6:46 | 49.813
2020-08-29 | 6:46 | 49.817
2020-08-29 | 6:46 | 49.82
2020-08-29 | 6:46 | 49.826
2020-08-29 | 6:46 | 49.831
2020-08-29 | 6:46 | 49.834
2020-08-29 | 6:46 | 49.838
2020-08-29 | 6:46 | 49.84
2020-08-29 | 6:46 | 49.841
2020-08-29 | 6:46 | 49.844
2020-08-29 | 6:46 | 49.846
2020-08-29 | 6:46 | 49.846
2020-08-29 | 6:46 | 49.848
2020-08-29 | 6:46 | 49.852
2020-08-29 | 6:46 | 49.856
2020-08-29 | 6:46 | 49.861
2020-08-29 | 6:46 | 49.866
2020-08-29 | 6:46 | 49.87
2020-08-29 | 6:46 | 49.877
2020-08-29 | 6:46 | 49.888
2020-08-29 | 6:46 | 49.896
2020-08-29 | 6:46 | 49.904
2020-08-29 | 6:46 | 49.908
2020-08-29 | 6:46 | 49.912
2020-08-29 | 6:46 | 49.916
2020-08-29 | 6:46 | 49.917
2020-08-29 | 6:46 | 49.917
2020-08-29 | 6:46 | 49.916
2020-08-29 | 6:46 | 49.912
2020-08-29 | 6:46 | 49.911
2020-08-29 | 6:46 | 49.91
2020-08-29 | 6:46 | 49.91
2020-08-29 | 6:46 | 49.908
2020-08-29 | 6:46 | 49.908
2020-08-29 | 6:46 | 49.909
2020-08-29 | 6:46 | 49.913
2020-08-29 | 6:47 | 49.916
2020-08-29 | 6:47 | 49.918
2020-08-29 | 6:47 | 49.919
2020-08-29 | 6:47 | 49.921
2020-08-29 | 6:47 | 49.92
2020-08-29 | 6:47 | 49.918
2020-08-29 | 6:47 | 49.918
2020-08-29 | 6:47 | 49.915
2020-08-29 | 6:47 | 49.913
2020-08-29 | 6:47 | 49.912
2020-08-29 | 6:47 | 49.91
2020-08-29 | 6:47 | 49.91
2020-08-29 | 6:47 | 49.914
2020-08-29 | 6:47 | 49.917
2020-08-29 | 6:47 | 49.92
2020-08-29 | 6:47 | 49.922
2020-08-29 | 6:47 | 49.921
2020-08-29 | 6:47 | 49.926
2020-08-29 | 6:47 | 49.931
2020-08-29 | 6:47 | 49.933
2020-08-29 | 6:47 | 49.937
2020-08-29 | 6:47 | 49.942
2020-08-29 | 6:47 | 49.949
2020-08-29 | 6:47 | 49.955
2020-08-29 | 6:47 | 49.96
2020-08-29 | 6:47 | 49.965
2020-08-29 | 6:47 | 49.971
2020-08-29 | 6:47 | 49.976
2020-08-29 | 6:47 | 49.977
2020-08-29 | 6:47 | 49.979
2020-08-29 | 6:47 | 49.977
2020-08-29 | 6:47 | 49.976
2020-08-29 | 6:47 | 49.974
2020-08-29 | 6:47 | 49.974
2020-08-29 | 6:47 | 49.972
2020-08-29 | 6:47 | 49.973
2020-08-29 | 6:47 | 49.976
2020-08-29 | 6:47 | 49.98
2020-08-29 | 6:47 | 49.984
2020-08-29 | 6:47 | 49.988
2020-08-29 | 6:47 | 49.991
2020-08-29 | 6:47 | 49.993
2020-08-29 | 6:47 | 49.997
2020-08-29 | 6:47 | 49.998
2020-08-29 | 6:47 | 50
2020-08-29 | 6:47 | 50.006
2020-08-29 | 6:47 | 50.011
2020-08-29 | 6:47 | 50.018
2020-08-29 | 6:47 | 50.025
2020-08-29 | 6:47 | 50.032
2020-08-29 | 6:47 | 50.038
2020-08-29 | 6:47 | 50.04
2020-08-29 | 6:47 | 50.039
2020-08-29 | 6:47 | 50.037
2020-08-29 | 6:47 | 50.035
2020-08-29 | 6:47 | 50.031
2020-08-29 | 6:47 | 50.031
2020-08-29 | 6:47 | 50.031
2020-08-29 | 6:47 | 50.029
2020-08-29 | 6:47 | 50.029
2020-08-29 | 6:47 | 50.031
2020-08-29 | 6:48 | 50.035
2020-08-29 | 6:48 | 50.039
2020-08-29 | 6:48 | 50.043
2020-08-29 | 6:48 | 50.044
2020-08-29 | 6:48 | 50.049
2020-08-29 | 6:48 | 50.049
2020-08-29 | 6:48 | 50.048
2020-08-29 | 6:48 | 50.051
2020-08-29 | 6:48 | 50.053
2020-08-29 | 6:48 | 50.056
2020-08-29 | 6:48 | 50.059
2020-08-29 | 6:48 | 50.062
2020-08-29 | 6:48 | 50.065
2020-08-29 | 6:48 | 50.066
2020-08-29 | 6:48 | 50.067
2020-08-29 | 6:48 | 50.069
2020-08-29 | 6:48 | 50.066
2020-08-29 | 6:48 | 50.063
2020-08-29 | 6:48 | 50.06
2020-08-29 | 6:48 | 50.06
2020-08-29 | 6:48 | 50.059
2020-08-29 | 6:48 | 50.056
2020-08-29 | 6:48 | 50.056
2020-08-29 | 6:48 | 50.059
2020-08-29 | 6:48 | 50.058
2020-08-29 | 6:48 | 50.057
2020-08-29 | 6:48 | 50.059
2020-08-29 | 6:48 | 50.059
2020-08-29 | 6:48 | 50.061
2020-08-29 | 6:48 | 50.061
2020-08-29 | 6:48 | 50.059
2020-08-29 | 6:48 | 50.059
2020-08-29 | 6:48 | 50.059
2020-08-29 | 6:48 | 50.056
2020-08-29 | 6:48 | 50.054
2020-08-29 | 6:48 | 50.056
2020-08-29 | 6:48 | 50.055
2020-08-29 | 6:48 | 50.055
2020-08-29 | 6:48 | 50.054
2020-08-29 | 6:48 | 50.054
2020-08-29 | 6:48 | 50.054
2020-08-29 | 6:48 | 50.055
2020-08-29 | 6:48 | 50.055
2020-08-29 | 6:48 | 50.053
2020-08-29 | 6:48 | 50.05
2020-08-29 | 6:48 | 50.048
2020-08-29 | 6:48 | 50.049
2020-08-29 | 6:48 | 50.052
2020-08-29 | 6:48 | 50.053
2020-08-29 | 6:48 | 50.054
2020-08-29 | 6:48 | 50.052
2020-08-29 | 6:48 | 50.052
2020-08-29 | 6:48 | 50.052
2020-08-29 | 6:48 | 50.05
2020-08-29 | 6:48 | 50.051
2020-08-29 | 6:48 | 50.049
2020-08-29 | 6:48 | 50.051
2020-08-29 | 6:48 | 50.052
2020-08-29 | 6:48 | 50.05
2020-08-29 | 6:49 | 50.047
2020-08-29 | 6:49 | 50.045
2020-08-29 | 6:49 | 50.046
2020-08-29 | 6:49 | 50.048
2020-08-29 | 6:49 | 50.053
2020-08-29 | 6:49 | 50.055
2020-08-29 | 6:49 | 50.056
2020-08-29 | 6:49 | 50.055
2020-08-29 | 6:49 | 50.054
2020-08-29 | 6:49 | 50.052
2020-08-29 | 6:49 | 50.05
2020-08-29 | 6:49 | 50.049
2020-08-29 | 6:49 | 50.046
2020-08-29 | 6:49 | 50.043
2020-08-29 | 6:49 | 50.046
2020-08-29 | 6:49 | 50.047
2020-08-29 | 6:49 | 50.05
2020-08-29 | 6:49 | 50.053
2020-08-29 | 6:49 | 50.054
2020-08-29 | 6:49 | 50.052
2020-08-29 | 6:49 | 50.051
2020-08-29 | 6:49 | 50.053
2020-08-29 | 6:49 | 50.054
2020-08-29 | 6:49 | 50.053
2020-08-29 | 6:49 | 50.054
2020-08-29 | 6:49 | 50.055
2020-08-29 | 6:49 | 50.055
2020-08-29 | 6:49 | 50.056
2020-08-29 | 6:49 | 50.054
2020-08-29 | 6:49 | 50.054
2020-08-29 | 6:49 | 50.054
2020-08-29 | 6:49 | 50.052
2020-08-29 | 6:49 | 50.05
2020-08-29 | 6:49 | 50.047
2020-08-29 | 6:49 | 50.042
2020-08-29 | 6:49 | 50.039
2020-08-29 | 6:49 | 50.04
2020-08-29 | 6:49 | 50.04
2020-08-29 | 6:49 | 50.04
2020-08-29 | 6:49 | 50.041
2020-08-29 | 6:49 | 50.04
2020-08-29 | 6:49 | 50.035
2020-08-29 | 6:49 | 50.032
2020-08-29 | 6:49 | 50.027
2020-08-29 | 6:49 | 50.021
2020-08-29 | 6:49 | 50.017
2020-08-29 | 6:49 | 50.013
2020-08-29 | 6:49 | 50.009
2020-08-29 | 6:49 | 50.008
2020-08-29 | 6:49 | 50.007
2020-08-29 | 6:49 | 50.006
2020-08-29 | 6:49 | 50.008
2020-08-29 | 6:49 | 50.013
2020-08-29 | 6:49 | 50.016
2020-08-29 | 6:49 | 50.019
2020-08-29 | 6:49 | 50.025
2020-08-29 | 6:49 | 50.027
2020-08-29 | 6:49 | 50.025
2020-08-29 | 6:49 | 50.025
2020-08-29 | 6:49 | 50.027
2020-08-29 | 6:50 | 50.028
2020-08-29 | 6:50 | 50.028
2020-08-29 | 6:50 | 50.031
2020-08-29 | 6:50 | 50.033
2020-08-29 | 6:50 | 50.033
2020-08-29 | 6:50 | 50.032
2020-08-29 | 6:50 | 50.032
2020-08-29 | 6:50 | 50.029
2020-08-29 | 6:50 | 50.029
2020-08-29 | 6:50 | 50.025
2020-08-29 | 6:50 | 50.024
2020-08-29 | 6:50 | 50.021
2020-08-29 | 6:50 | 50.019
2020-08-29 | 6:50 | 50.014
2020-08-29 | 6:50 | 50.011
2020-08-29 | 6:50 | 50.01
2020-08-29 | 6:50 | 50.009
2020-08-29 | 6:50 | 50.008
2020-08-29 | 6:50 | 50.01
2020-08-29 | 6:50 | 50.014
2020-08-29 | 6:50 | 50.018
2020-08-29 | 6:50 | 50.021
2020-08-29 | 6:50 | 50.024
2020-08-29 | 6:50 | 50.027
2020-08-29 | 6:50 | 50.029
2020-08-29 | 6:50 | 50.033
2020-08-29 | 6:50 | 50.033
2020-08-29 | 6:50 | 50.033
2020-08-29 | 6:50 | 50.033
2020-08-29 | 6:50 | 50.031
2020-08-29 | 6:50 | 50.027
2020-08-29 | 6:50 | 50.025
2020-08-29 | 6:50 | 50.026
2020-08-29 | 6:50 | 50.028
2020-08-29 | 6:50 | 50.032
2020-08-29 | 6:50 | 50.036
2020-08-29 | 6:50 | 50.04
2020-08-29 | 6:50 | 50.045
2020-08-29 | 6:50 | 50.05
2020-08-29 | 6:50 | 50.056
2020-08-29 | 6:50 | 50.06
2020-08-29 | 6:50 | 50.061
2020-08-29 | 6:50 | 50.061
2020-08-29 | 6:50 | 50.058
2020-08-29 | 6:50 | 50.054
2020-08-29 | 6:50 | 50.053
2020-08-29 | 6:50 | 50.054
2020-08-29 | 6:50 | 50.056
2020-08-29 | 6:50 | 50.057
2020-08-29 | 6:50 | 50.057
2020-08-29 | 6:50 | 50.058
2020-08-29 | 6:50 | 50.057
2020-08-29 | 6:50 | 50.054
2020-08-29 | 6:50 | 50.052
2020-08-29 | 6:50 | 50.052
2020-08-29 | 6:50 | 50.049
2020-08-29 | 6:50 | 50.048
2020-08-29 | 6:50 | 50.046
2020-08-29 | 6:50 | 50.047
2020-08-29 | 6:50 | 50.048
2020-08-29 | 6:50 | 50.047
2020-08-29 | 6:51 | 50.047
2020-08-29 | 6:51 | 50.048
2020-08-29 | 6:51 | 50.047
2020-08-29 | 6:51 | 50.049
2020-08-29 | 6:51 | 50.05
2020-08-29 | 6:51 | 50.052
2020-08-29 | 6:51 | 50.051
2020-08-29 | 6:51 | 50.053
2020-08-29 | 6:51 | 50.054
2020-08-29 | 6:51 | 50.052
2020-08-29 | 6:51 | 50.049
2020-08-29 | 6:51 | 50.048
2020-08-29 | 6:51 | 50.047
2020-08-29 | 6:51 | 50.048
2020-08-29 | 6:51 | 50.051
2020-08-29 | 6:51 | 50.052
2020-08-29 | 6:51 | 50.053
2020-08-29 | 6:51 | 50.055
2020-08-29 | 6:51 | 50.056
2020-08-29 | 6:51 | 50.056
2020-08-29 | 6:51 | 50.055
2020-08-29 | 6:51 | 50.051
2020-08-29 | 6:51 | 50.049
2020-08-29 | 6:51 | 50.051
2020-08-29 | 6:51 | 50.05
2020-08-29 | 6:51 | 50.046
2020-08-29 | 6:51 | 50.049
2020-08-29 | 6:51 | 50.053
2020-08-29 | 6:51 | 50.054
2020-08-29 | 6:51 | 50.055
2020-08-29 | 6:51 | 50.052
2020-08-29 | 6:51 | 50.051
2020-08-29 | 6:51 | 50.053
2020-08-29 | 6:51 | 50.054
2020-08-29 | 6:51 | 50.054
2020-08-29 | 6:51 | 50.054
2020-08-29 | 6:51 | 50.052
2020-08-29 | 6:51 | 50.052
2020-08-29 | 6:51 | 50.052
2020-08-29 | 6:51 | 50.051
2020-08-29 | 6:51 | 50.05
2020-08-29 | 6:51 | 50.046
2020-08-29 | 6:51 | 50.042
2020-08-29 | 6:51 | 50.039
2020-08-29 | 6:51 | 50.037
2020-08-29 | 6:51 | 50.036
2020-08-29 | 6:51 | 50.034
2020-08-29 | 6:51 | 50.032
2020-08-29 | 6:51 | 50.034
2020-08-29 | 6:51 | 50.032
2020-08-29 | 6:51 | 50.028
2020-08-29 | 6:51 | 50.026
2020-08-29 | 6:51 | 50.021
2020-08-29 | 6:51 | 50.016
2020-08-29 | 6:51 | 50.015
2020-08-29 | 6:51 | 50.014
2020-08-29 | 6:51 | 50.016
2020-08-29 | 6:51 | 50.019
2020-08-29 | 6:51 | 50.019
2020-08-29 | 6:52 | 50.021
2020-08-29 | 6:52 | 50.022
2020-08-29 | 6:52 | 50.021
2020-08-29 | 6:52 | 50.02
2020-08-29 | 6:52 | 50.018
2020-08-29 | 6:52 | 50.018
2020-08-29 | 6:52 | 50.019
2020-08-29 | 6:52 | 50.019
2020-08-29 | 6:52 | 50.022
2020-08-29 | 6:52 | 50.024
2020-08-29 | 6:52 | 50.024
2020-08-29 | 6:52 | 50.028
2020-08-29 | 6:52 | 50.032
2020-08-29 | 6:52 | 50.032
2020-08-29 | 6:52 | 50.032
2020-08-29 | 6:52 | 50.031
2020-08-29 | 6:52 | 50.03
2020-08-29 | 6:52 | 50.032
2020-08-29 | 6:52 | 50.035
2020-08-29 | 6:52 | 50.036
2020-08-29 | 6:52 | 50.035
2020-08-29 | 6:52 | 50.031
2020-08-29 | 6:52 | 50.027
2020-08-29 | 6:52 | 50.026
2020-08-29 | 6:52 | 50.027
2020-08-29 | 6:52 | 50.026
2020-08-29 | 6:52 | 50.031
2020-08-29 | 6:52 | 50.035
2020-08-29 | 6:52 | 50.033
2020-08-29 | 6:52 | 50.031
2020-08-29 | 6:52 | 50.03
2020-08-29 | 6:52 | 50.03
2020-08-29 | 6:52 | 50.03
2020-08-29 | 6:52 | 50.031
2020-08-29 | 6:52 | 50.03
2020-08-29 | 6:52 | 50.029
2020-08-29 | 6:52 | 50.032
2020-08-29 | 6:52 | 50.035
2020-08-29 | 6:52 | 50.037
2020-08-29 | 6:52 | 50.036
2020-08-29 | 6:52 | 50.037
2020-08-29 | 6:52 | 50.035
2020-08-29 | 6:52 | 50.033
2020-08-29 | 6:52 | 50.033
2020-08-29 | 6:52 | 50.03
2020-08-29 | 6:52 | 50.026
2020-08-29 | 6:52 | 50.022
2020-08-29 | 6:52 | 50.017
2020-08-29 | 6:52 | 50.012
2020-08-29 | 6:52 | 50.008
2020-08-29 | 6:52 | 50.003
2020-08-29 | 6:52 | 49.999
2020-08-29 | 6:52 | 49.997
2020-08-29 | 6:52 | 49.992
2020-08-29 | 6:52 | 49.99
2020-08-29 | 6:52 | 49.989
2020-08-29 | 6:52 | 49.989
2020-08-29 | 6:52 | 49.988
2020-08-29 | 6:52 | 49.989
2020-08-29 | 6:52 | 49.99
2020-08-29 | 6:52 | 49.988
2020-08-29 | 6:53 | 49.988
2020-08-29 | 6:53 | 49.986
2020-08-29 | 6:53 | 49.984
2020-08-29 | 6:53 | 49.984
2020-08-29 | 6:53 | 49.984
2020-08-29 | 6:53 | 49.98
2020-08-29 | 6:53 | 49.976
2020-08-29 | 6:53 | 49.967
2020-08-29 | 6:53 | 49.967
2020-08-29 | 6:53 | 49.963
2020-08-29 | 6:53 | 49.961
2020-08-29 | 6:53 | 49.963
2020-08-29 | 6:53 | 49.963
2020-08-29 | 6:53 | 49.965
2020-08-29 | 6:53 | 49.97
2020-08-29 | 6:53 | 49.975
2020-08-29 | 6:53 | 49.978
2020-08-29 | 6:53 | 49.982
2020-08-29 | 6:53 | 49.986
2020-08-29 | 6:53 | 49.986
2020-08-29 | 6:53 | 49.983
2020-08-29 | 6:53 | 49.982
2020-08-29 | 6:53 | 49.98
2020-08-29 | 6:53 | 49.983
2020-08-29 | 6:53 | 49.983
2020-08-29 | 6:53 | 49.981
2020-08-29 | 6:53 | 49.978
2020-08-29 | 6:53 | 49.977
2020-08-29 | 6:53 | 49.977
2020-08-29 | 6:53 | 49.976
2020-08-29 | 6:53 | 49.972
2020-08-29 | 6:53 | 49.973
2020-08-29 | 6:53 | 49.977
2020-08-29 | 6:53 | 49.981
2020-08-29 | 6:53 | 49.984
2020-08-29 | 6:53 | 49.984
2020-08-29 | 6:53 | 49.982
2020-08-29 | 6:53 | 49.98
2020-08-29 | 6:53 | 49.978
2020-08-29 | 6:53 | 49.978
2020-08-29 | 6:53 | 49.977
2020-08-29 | 6:53 | 49.973
2020-08-29 | 6:53 | 49.971
2020-08-29 | 6:53 | 49.968
2020-08-29 | 6:53 | 49.969
2020-08-29 | 6:53 | 49.967
2020-08-29 | 6:53 | 49.965
2020-08-29 | 6:53 | 49.961
2020-08-29 | 6:53 | 49.961
2020-08-29 | 6:53 | 49.961
2020-08-29 | 6:53 | 49.966
2020-08-29 | 6:53 | 49.973
2020-08-29 | 6:53 | 49.978
2020-08-29 | 6:53 | 49.983
2020-08-29 | 6:53 | 49.988
2020-08-29 | 6:53 | 49.992
2020-08-29 | 6:53 | 49.997
2020-08-29 | 6:53 | 49.998
2020-08-29 | 6:53 | 50
2020-08-29 | 6:54 | 50.001
2020-08-29 | 6:54 | 50
2020-08-29 | 6:54 | 49.995
2020-08-29 | 6:54 | 49.994
2020-08-29 | 6:54 | 49.993
2020-08-29 | 6:54 | 49.995
2020-08-29 | 6:54 | 49.995
2020-08-29 | 6:54 | 49.997
2020-08-29 | 6:54 | 50
2020-08-29 | 6:54 | 50.003
2020-08-29 | 6:54 | 50.01
2020-08-29 | 6:54 | 50.02
2020-08-29 | 6:54 | 50.021
2020-08-29 | 6:54 | 50.022
2020-08-29 | 6:54 | 50.024
2020-08-29 | 6:54 | 50.025
2020-08-29 | 6:54 | 50.023
2020-08-29 | 6:54 | 50.023
2020-08-29 | 6:54 | 50.026
2020-08-29 | 6:54 | 50.028
2020-08-29 | 6:54 | 50.029
2020-08-29 | 6:54 | 50.027
2020-08-29 | 6:54 | 50.024
2020-08-29 | 6:54 | 50.027
2020-08-29 | 6:54 | 50.028
2020-08-29 | 6:54 | 50.027
2020-08-29 | 6:54 | 50.029
2020-08-29 | 6:54 | 50.025
2020-08-29 | 6:54 | 50.02
2020-08-29 | 6:54 | 50.017
2020-08-29 | 6:54 | 50.017
2020-08-29 | 6:54 | 50.018
2020-08-29 | 6:54 | 50.016
2020-08-29 | 6:54 | 50.014
2020-08-29 | 6:54 | 50.014
2020-08-29 | 6:54 | 50.014
2020-08-29 | 6:54 | 50.012
2020-08-29 | 6:54 | 50.01
2020-08-29 | 6:54 | 50.01
2020-08-29 | 6:54 | 50.009
2020-08-29 | 6:54 | 50.01
2020-08-29 | 6:54 | 50.007
2020-08-29 | 6:54 | 50.005
2020-08-29 | 6:54 | 50.005
2020-08-29 | 6:54 | 49.999
2020-08-29 | 6:54 | 49.999
2020-08-29 | 6:54 | 49.998
2020-08-29 | 6:54 | 49.999
2020-08-29 | 6:54 | 50
2020-08-29 | 6:54 | 50.002
2020-08-29 | 6:54 | 50.006
2020-08-29 | 6:54 | 50.009
2020-08-29 | 6:54 | 50.011
2020-08-29 | 6:54 | 50.013
2020-08-29 | 6:54 | 50.014
2020-08-29 | 6:54 | 50.013
2020-08-29 | 6:54 | 50.016
2020-08-29 | 6:54 | 50.016
2020-08-29 | 6:54 | 50.016
2020-08-29 | 6:54 | 50.017
2020-08-29 | 6:54 | 50.017
2020-08-29 | 6:55 | 50.018
2020-08-29 | 6:55 | 50.02
2020-08-29 | 6:55 | 50.02
2020-08-29 | 6:55 | 50.025
2020-08-29 | 6:55 | 50.028
2020-08-29 | 6:55 | 50.027
2020-08-29 | 6:55 | 50.024
2020-08-29 | 6:55 | 50.019
2020-08-29 | 6:55 | 50.017
2020-08-29 | 6:55 | 50.011
2020-08-29 | 6:55 | 50.003
2020-08-29 | 6:55 | 49.998
2020-08-29 | 6:55 | 49.993
2020-08-29 | 6:55 | 49.99
2020-08-29 | 6:55 | 49.988
2020-08-29 | 6:55 | 49.982
2020-08-29 | 6:55 | 49.981
2020-08-29 | 6:55 | 49.982
2020-08-29 | 6:55 | 49.981
2020-08-29 | 6:55 | 49.982
2020-08-29 | 6:55 | 49.982
2020-08-29 | 6:55 | 49.982
2020-08-29 | 6:55 | 49.983
2020-08-29 | 6:55 | 49.982
2020-08-29 | 6:55 | 49.98
2020-08-29 | 6:55 | 49.983
2020-08-29 | 6:55 | 49.979
2020-08-29 | 6:55 | 49.978
2020-08-29 | 6:55 | 49.98
2020-08-29 | 6:55 | 49.983
2020-08-29 | 6:55 | 49.985
2020-08-29 | 6:55 | 49.985
2020-08-29 | 6:55 | 49.985
2020-08-29 | 6:55 | 49.988
2020-08-29 | 6:55 | 49.986
2020-08-29 | 6:55 | 49.982
2020-08-29 | 6:55 | 49.978
2020-08-29 | 6:55 | 49.977
2020-08-29 | 6:55 | 49.975
2020-08-29 | 6:55 | 49.971
2020-08-29 | 6:55 | 49.968
2020-08-29 | 6:55 | 49.965
2020-08-29 | 6:55 | 49.962
2020-08-29 | 6:55 | 49.96
2020-08-29 | 6:55 | 49.959
2020-08-29 | 6:55 | 49.957
2020-08-29 | 6:55 | 49.961
2020-08-29 | 6:55 | 49.961
2020-08-29 | 6:55 | 49.964
2020-08-29 | 6:55 | 49.968
2020-08-29 | 6:55 | 49.97
2020-08-29 | 6:55 | 49.97
2020-08-29 | 6:55 | 49.971
2020-08-29 | 6:55 | 49.97
2020-08-29 | 6:55 | 49.965
2020-08-29 | 6:55 | 49.96
2020-08-29 | 6:55 | 49.956
2020-08-29 | 6:55 | 49.953
2020-08-29 | 6:55 | 49.953
2020-08-29 | 6:56 | 49.956
2020-08-29 | 6:56 | 49.955
2020-08-29 | 6:56 | 49.957
2020-08-29 | 6:56 | 49.959
2020-08-29 | 6:56 | 49.962
2020-08-29 | 6:56 | 49.963
2020-08-29 | 6:56 | 49.964
2020-08-29 | 6:56 | 49.966
2020-08-29 | 6:56 | 49.966
2020-08-29 | 6:56 | 49.968
2020-08-29 | 6:56 | 49.968
2020-08-29 | 6:56 | 49.968
2020-08-29 | 6:56 | 49.968
2020-08-29 | 6:56 | 49.967
2020-08-29 | 6:56 | 49.966
2020-08-29 | 6:56 | 49.97
2020-08-29 | 6:56 | 49.967
2020-08-29 | 6:56 | 49.965
2020-08-29 | 6:56 | 49.969
2020-08-29 | 6:56 | 49.97
2020-08-29 | 6:56 | 49.974
2020-08-29 | 6:56 | 49.978
2020-08-29 | 6:56 | 49.981
2020-08-29 | 6:56 | 49.98
2020-08-29 | 6:56 | 49.972
2020-08-29 | 6:56 | 49.963
2020-08-29 | 6:56 | 49.953
2020-08-29 | 6:56 | 49.936
2020-08-29 | 6:56 | 49.921
2020-08-29 | 6:56 | 49.906
2020-08-29 | 6:56 | 49.893
2020-08-29 | 6:56 | 49.883
2020-08-29 | 6:56 | 49.879
2020-08-29 | 6:56 | 49.875
2020-08-29 | 6:56 | 49.875
2020-08-29 | 6:56 | 49.879
2020-08-29 | 6:56 | 49.887
2020-08-29 | 6:56 | 49.888
2020-08-29 | 6:56 | 49.892
2020-08-29 | 6:56 | 49.894
2020-08-29 | 6:56 | 49.898
2020-08-29 | 6:56 | 49.899
2020-08-29 | 6:56 | 49.903
2020-08-29 | 6:56 | 49.905
2020-08-29 | 6:56 | 49.905
2020-08-29 | 6:56 | 49.907
2020-08-29 | 6:56 | 49.909
2020-08-29 | 6:56 | 49.913
2020-08-29 | 6:56 | 49.911
2020-08-29 | 6:56 | 49.912
2020-08-29 | 6:56 | 49.909
2020-08-29 | 6:56 | 49.908
2020-08-29 | 6:56 | 49.906
2020-08-29 | 6:56 | 49.902
2020-08-29 | 6:56 | 49.902
2020-08-29 | 6:56 | 49.904
2020-08-29 | 6:56 | 49.904
2020-08-29 | 6:56 | 49.904
2020-08-29 | 6:56 | 49.906
2020-08-29 | 6:56 | 49.911
2020-08-29 | 6:56 | 49.912
2020-08-29 | 6:57 | 49.916
2020-08-29 | 6:57 | 49.919
2020-08-29 | 6:57 | 49.922
2020-08-29 | 6:57 | 49.925
2020-08-29 | 6:57 | 49.932
2020-08-29 | 6:57 | 49.94
2020-08-29 | 6:57 | 49.945
2020-08-29 | 6:57 | 49.946
2020-08-29 | 6:57 | 49.947
2020-08-29 | 6:57 | 49.946
2020-08-29 | 6:57 | 49.952
2020-08-29 | 6:57 | 49.958
2020-08-29 | 6:57 | 49.962
2020-08-29 | 6:57 | 49.967
2020-08-29 | 6:57 | 49.964
2020-08-29 | 6:57 | 49.964
2020-08-29 | 6:57 | 49.961
2020-08-29 | 6:57 | 49.958
2020-08-29 | 6:57 | 49.954
2020-08-29 | 6:57 | 49.951
2020-08-29 | 6:57 | 49.945
2020-08-29 | 6:57 | 49.942
2020-08-29 | 6:57 | 49.941
2020-08-29 | 6:57 | 49.943
2020-08-29 | 6:57 | 49.942
2020-08-29 | 6:57 | 49.943
2020-08-29 | 6:57 | 49.941
2020-08-29 | 6:57 | 49.94
2020-08-29 | 6:57 | 49.938
2020-08-29 | 6:57 | 49.937
2020-08-29 | 6:57 | 49.937
2020-08-29 | 6:57 | 49.939
2020-08-29 | 6:57 | 49.936
2020-08-29 | 6:57 | 49.938
2020-08-29 | 6:57 | 49.938
2020-08-29 | 6:57 | 49.939
2020-08-29 | 6:57 | 49.945
2020-08-29 | 6:57 | 49.946
2020-08-29 | 6:57 | 49.943
2020-08-29 | 6:57 | 49.946
2020-08-29 | 6:57 | 49.947
2020-08-29 | 6:57 | 49.952
2020-08-29 | 6:57 | 49.959
2020-08-29 | 6:57 | 49.963
2020-08-29 | 6:57 | 49.965
2020-08-29 | 6:57 | 49.969
2020-08-29 | 6:57 | 49.975
2020-08-29 | 6:57 | 49.981
2020-08-29 | 6:57 | 49.986
2020-08-29 | 6:57 | 49.986
2020-08-29 | 6:57 | 49.988
2020-08-29 | 6:57 | 49.987
2020-08-29 | 6:57 | 49.989
2020-08-29 | 6:57 | 49.99
2020-08-29 | 6:57 | 49.992
2020-08-29 | 6:57 | 49.994
2020-08-29 | 6:57 | 49.993
2020-08-29 | 6:57 | 49.994
2020-08-29 | 6:57 | 49.995
2020-08-29 | 6:58 | 50.002
2020-08-29 | 6:58 | 50.006
2020-08-29 | 6:58 | 50.011
2020-08-29 | 6:58 | 50.016
2020-08-29 | 6:58 | 50.017
2020-08-29 | 6:58 | 50.016
2020-08-29 | 6:58 | 50.017
2020-08-29 | 6:58 | 50.016
2020-08-29 | 6:58 | 50.015
2020-08-29 | 6:58 | 50.014
2020-08-29 | 6:58 | 50.02
2020-08-29 | 6:58 | 50.019
2020-08-29 | 6:58 | 50.023
2020-08-29 | 6:58 | 50.023
2020-08-29 | 6:58 | 50.026
2020-08-29 | 6:58 | 50.029
2020-08-29 | 6:58 | 50.03
2020-08-29 | 6:58 | 50.029
2020-08-29 | 6:58 | 50.027
2020-08-29 | 6:58 | 50.026
2020-08-29 | 6:58 | 50.026
2020-08-29 | 6:58 | 50.022
2020-08-29 | 6:58 | 50.02
2020-08-29 | 6:58 | 50.018
2020-08-29 | 6:58 | 50.011
2020-08-29 | 6:58 | 50.006
2020-08-29 | 6:58 | 49.999
2020-08-29 | 6:58 | 49.995
2020-08-29 | 6:58 | 49.99
2020-08-29 | 6:58 | 49.984
2020-08-29 | 6:58 | 49.978
2020-08-29 | 6:58 | 49.97
2020-08-29 | 6:58 | 49.963
2020-08-29 | 6:58 | 49.958
2020-08-29 | 6:58 | 49.955
2020-08-29 | 6:58 | 49.952
2020-08-29 | 6:58 | 49.955
2020-08-29 | 6:58 | 49.957
2020-08-29 | 6:58 | 49.959
2020-08-29 | 6:58 | 49.957
2020-08-29 | 6:58 | 49.958
2020-08-29 | 6:58 | 49.956
2020-08-29 | 6:58 | 49.955
2020-08-29 | 6:58 | 49.957
2020-08-29 | 6:58 | 49.961
2020-08-29 | 6:58 | 49.963
2020-08-29 | 6:58 | 49.964
2020-08-29 | 6:58 | 49.963
2020-08-29 | 6:58 | 49.963
2020-08-29 | 6:58 | 49.962
2020-08-29 | 6:58 | 49.958
2020-08-29 | 6:58 | 49.957
2020-08-29 | 6:58 | 49.951
2020-08-29 | 6:58 | 49.949
2020-08-29 | 6:58 | 49.947
2020-08-29 | 6:58 | 49.949
2020-08-29 | 6:58 | 49.949
2020-08-29 | 6:58 | 49.95
2020-08-29 | 6:58 | 49.949
2020-08-29 | 6:58 | 49.947
2020-08-29 | 6:59 | 49.944
2020-08-29 | 6:59 | 49.94
2020-08-29 | 6:59 | 49.937
2020-08-29 | 6:59 | 49.938
2020-08-29 | 6:59 | 49.939
2020-08-29 | 6:59 | 49.94
2020-08-29 | 6:59 | 49.939
2020-08-29 | 6:59 | 49.943
2020-08-29 | 6:59 | 49.947
2020-08-29 | 6:59 | 49.949
2020-08-29 | 6:59 | 49.954
2020-08-29 | 6:59 | 49.958
2020-08-29 | 6:59 | 49.962
2020-08-29 | 6:59 | 49.969
2020-08-29 | 6:59 | 49.975
2020-08-29 | 6:59 | 49.982
2020-08-29 | 6:59 | 49.986
2020-08-29 | 6:59 | 49.985
2020-08-29 | 6:59 | 49.985
2020-08-29 | 6:59 | 49.983
2020-08-29 | 6:59 | 49.981
2020-08-29 | 6:59 | 49.981
2020-08-29 | 6:59 | 49.979
2020-08-29 | 6:59 | 49.976
2020-08-29 | 6:59 | 49.973
2020-08-29 | 6:59 | 49.972
2020-08-29 | 6:59 | 49.974
2020-08-29 | 6:59 | 49.974
2020-08-29 | 6:59 | 49.974
2020-08-29 | 6:59 | 49.975
2020-08-29 | 6:59 | 49.974
2020-08-29 | 6:59 | 49.974
2020-08-29 | 6:59 | 49.973
2020-08-29 | 6:59 | 49.975
2020-08-29 | 6:59 | 49.976
2020-08-29 | 6:59 | 49.977
2020-08-29 | 6:59 | 49.978
2020-08-29 | 6:59 | 49.977
2020-08-29 | 6:59 | 49.977
2020-08-29 | 6:59 | 49.982
2020-08-29 | 6:59 | 49.996
2020-08-29 | 6:59 | 50.01
2020-08-29 | 6:59 | 50.021
2020-08-29 | 6:59 | 50.028
2020-08-29 | 6:59 | 50.032
2020-08-29 | 6:59 | 50.034
2020-08-29 | 6:59 | 50.032
2020-08-29 | 6:59 | 50.027
2020-08-29 | 6:59 | 50.024
2020-08-29 | 6:59 | 50.021
2020-08-29 | 6:59 | 50.017
2020-08-29 | 6:59 | 50.014
2020-08-29 | 6:59 | 50.014
2020-08-29 | 6:59 | 50.015
2020-08-29 | 6:59 | 50.015
2020-08-29 | 6:59 | 50.015
2020-08-29 | 6:59 | 50.015
2020-08-29 | 6:59 | 50.014
2020-08-29 | 6:59 | 50.011
2020-08-29 | 6:59 | 50.012
2020-08-29 | 6:59 | 50.017
2020-08-29 | 7:00 | 50.021
2020-08-29 | 7:00 | 50.022
2020-08-29 | 7:00 | 50.026
2020-08-29 | 7:00 | 50.035
2020-08-29 | 7:00 | 50.039
2020-08-29 | 7:00 | 50.041
2020-08-29 | 7:00 | 50.04
2020-08-29 | 7:00 | 50.042
2020-08-29 | 7:00 | 50.043
2020-08-29 | 7:00 | 50.043
2020-08-29 | 7:00 | 50.042
2020-08-29 | 7:00 | 50.042
2020-08-29 | 7:00 | 50.04
2020-08-29 | 7:00 | 50.037
2020-08-29 | 7:00 | 50.034
2020-08-29 | 7:00 | 50.033
2020-08-29 | 7:00 | 50.032
2020-08-29 | 7:00 | 50.033
2020-08-29 | 7:00 | 50.033
2020-08-29 | 7:00 | 50.036
2020-08-29 | 7:00 | 50.04
2020-08-29 | 7:00 | 50.042
2020-08-29 | 7:00 | 50.044
2020-08-29 | 7:00 | 50.049
2020-08-29 | 7:00 | 50.057
2020-08-29 | 7:00 | 50.054
2020-08-29 | 7:00 | 50.054
2020-08-29 | 7:00 | 50.054
2020-08-29 | 7:00 | 50.057
2020-08-29 | 7:00 | 50.058
2020-08-29 | 7:00 | 50.057
2020-08-29 | 7:00 | 50.057
2020-08-29 | 7:00 | 50.055
2020-08-29 | 7:00 | 50.057
2020-08-29 | 7:00 | 50.055
2020-08-29 | 7:00 | 50.054
2020-08-29 | 7:00 | 50.053
2020-08-29 | 7:00 | 50.049
2020-08-29 | 7:00 | 50.042
2020-08-29 | 7:00 | 50.032
2020-08-29 | 7:00 | 50.023
2020-08-29 | 7:00 | 50.016
2020-08-29 | 7:00 | 50.013
2020-08-29 | 7:00 | 50.01
2020-08-29 | 7:00 | 50.008
2020-08-29 | 7:00 | 50.01
2020-08-29 | 7:00 | 50.011
2020-08-29 | 7:00 | 50.01
2020-08-29 | 7:00 | 50.01
2020-08-29 | 7:00 | 50.009
2020-08-29 | 7:00 | 50.02
2020-08-29 | 7:00 | 50.036
2020-08-29 | 7:00 | 50.047
2020-08-29 | 7:00 | 50.049
2020-08-29 | 7:00 | 50.05
2020-08-29 | 7:00 | 50.051
2020-08-29 | 7:00 | 50.052
2020-08-29 | 7:00 | 50.054
2020-08-29 | 7:00 | 50.055
2020-08-29 | 7:01 | 50.057
2020-08-29 | 7:01 | 50.056
2020-08-29 | 7:01 | 50.056
2020-08-29 | 7:01 | 50.057
2020-08-29 | 7:01 | 50.059
2020-08-29 | 7:01 | 50.058
2020-08-29 | 7:01 | 50.058
2020-08-29 | 7:01 | 50.06
2020-08-29 | 7:01 | 50.062
2020-08-29 | 7:01 | 50.062
2020-08-29 | 7:01 | 50.061
2020-08-29 | 7:01 | 50.062
2020-08-29 | 7:01 | 50.062
2020-08-29 | 7:01 | 50.062
2020-08-29 | 7:01 | 50.059
2020-08-29 | 7:01 | 50.057
2020-08-29 | 7:01 | 50.056
2020-08-29 | 7:01 | 50.057
2020-08-29 | 7:01 | 50.062
2020-08-29 | 7:01 | 50.063
2020-08-29 | 7:01 | 50.062
2020-08-29 | 7:01 | 50.063
2020-08-29 | 7:01 | 50.064
2020-08-29 | 7:01 | 50.065
2020-08-29 | 7:01 | 50.067
2020-08-29 | 7:01 | 50.069
2020-08-29 | 7:01 | 50.068
2020-08-29 | 7:01 | 50.071
2020-08-29 | 7:01 | 50.07
2020-08-29 | 7:01 | 50.069
2020-08-29 | 7:01 | 50.067
2020-08-29 | 7:01 | 50.066
2020-08-29 | 7:01 | 50.064
2020-08-29 | 7:01 | 50.063
2020-08-29 | 7:01 | 50.063
2020-08-29 | 7:01 | 50.065
2020-08-29 | 7:01 | 50.066
2020-08-29 | 7:01 | 50.069
2020-08-29 | 7:01 | 50.074
2020-08-29 | 7:01 | 50.074
2020-08-29 | 7:01 | 50.075
2020-08-29 | 7:01 | 50.076
2020-08-29 | 7:01 | 50.076
2020-08-29 | 7:01 | 50.08
2020-08-29 | 7:01 | 50.08
2020-08-29 | 7:01 | 50.077
2020-08-29 | 7:01 | 50.071
2020-08-29 | 7:01 | 50.071
2020-08-29 | 7:01 | 50.071
2020-08-29 | 7:01 | 50.072
2020-08-29 | 7:01 | 50.072
2020-08-29 | 7:01 | 50.07
2020-08-29 | 7:01 | 50.07
2020-08-29 | 7:01 | 50.068
2020-08-29 | 7:01 | 50.066
2020-08-29 | 7:01 | 50.063
2020-08-29 | 7:01 | 50.06
2020-08-29 | 7:01 | 50.058
2020-08-29 | 7:01 | 50.061
2020-08-29 | 7:01 | 50.063
2020-08-29 | 7:01 | 50.063
2020-08-29 | 7:02 | 50.063
2020-08-29 | 7:02 | 50.062
2020-08-29 | 7:02 | 50.061
2020-08-29 | 7:02 | 50.06
2020-08-29 | 7:02 | 50.059
2020-08-29 | 7:02 | 50.057
2020-08-29 | 7:02 | 50.057
2020-08-29 | 7:02 | 50.057
2020-08-29 | 7:02 | 50.055
2020-08-29 | 7:02 | 50.053
2020-08-29 | 7:02 | 50.052
2020-08-29 | 7:02 | 50.051
2020-08-29 | 7:02 | 50.051
2020-08-29 | 7:02 | 50.051
2020-08-29 | 7:02 | 50.049
2020-08-29 | 7:02 | 50.048
2020-08-29 | 7:02 | 50.047
2020-08-29 | 7:02 | 50.049
2020-08-29 | 7:02 | 50.051
2020-08-29 | 7:02 | 50.053
2020-08-29 | 7:02 | 50.058
2020-08-29 | 7:02 | 50.064
2020-08-29 | 7:02 | 50.067
2020-08-29 | 7:02 | 50.071
2020-08-29 | 7:02 | 50.074
2020-08-29 | 7:02 | 50.077
2020-08-29 | 7:02 | 50.079
2020-08-29 | 7:02 | 50.079
2020-08-29 | 7:02 | 50.075
2020-08-29 | 7:02 | 50.072
2020-08-29 | 7:02 | 50.069
2020-08-29 | 7:02 | 50.066
2020-08-29 | 7:02 | 50.065
2020-08-29 | 7:02 | 50.064
2020-08-29 | 7:02 | 50.061
2020-08-29 | 7:02 | 50.06
2020-08-29 | 7:02 | 50.062
2020-08-29 | 7:02 | 50.063
2020-08-29 | 7:02 | 50.064
2020-08-29 | 7:02 | 50.063
2020-08-29 | 7:02 | 50.059
2020-08-29 | 7:02 | 50.055
2020-08-29 | 7:02 | 50.052
2020-08-29 | 7:02 | 50.053
2020-08-29 | 7:02 | 50.051
2020-08-29 | 7:02 | 50.049
2020-08-29 | 7:02 | 50.049
2020-08-29 | 7:02 | 50.048
2020-08-29 | 7:02 | 50.046
2020-08-29 | 7:02 | 50.045
2020-08-29 | 7:02 | 50.046
2020-08-29 | 7:02 | 50.045
2020-08-29 | 7:02 | 50.044
2020-08-29 | 7:02 | 50.046
2020-08-29 | 7:02 | 50.049
2020-08-29 | 7:02 | 50.048
2020-08-29 | 7:02 | 50.048
2020-08-29 | 7:02 | 50.052
2020-08-29 | 7:02 | 50.056
2020-08-29 | 7:03 | 50.059
2020-08-29 | 7:03 | 50.062
2020-08-29 | 7:03 | 50.064
2020-08-29 | 7:03 | 50.064
2020-08-29 | 7:03 | 50.063
2020-08-29 | 7:03 | 50.063
2020-08-29 | 7:03 | 50.058
2020-08-29 | 7:03 | 50.055
2020-08-29 | 7:03 | 50.053
2020-08-29 | 7:03 | 50.052
2020-08-29 | 7:03 | 50.051
2020-08-29 | 7:03 | 50.049
2020-08-29 | 7:03 | 50.048
2020-08-29 | 7:03 | 50.046
2020-08-29 | 7:03 | 50.046
2020-08-29 | 7:03 | 50.048
2020-08-29 | 7:03 | 50.052
2020-08-29 | 7:03 | 50.056
2020-08-29 | 7:03 | 50.058
2020-08-29 | 7:03 | 50.058
2020-08-29 | 7:03 | 50.058
2020-08-29 | 7:03 | 50.058
2020-08-29 | 7:03 | 50.058
2020-08-29 | 7:03 | 50.059
2020-08-29 | 7:03 | 50.062
2020-08-29 | 7:03 | 50.066
2020-08-29 | 7:03 | 50.067
2020-08-29 | 7:03 | 50.067
2020-08-29 | 7:03 | 50.068
2020-08-29 | 7:03 | 50.068
2020-08-29 | 7:03 | 50.066
2020-08-29 | 7:03 | 50.063
2020-08-29 | 7:03 | 50.062
2020-08-29 | 7:03 | 50.06
2020-08-29 | 7:03 | 50.062
2020-08-29 | 7:03 | 50.066
2020-08-29 | 7:03 | 50.068
2020-08-29 | 7:03 | 50.07
2020-08-29 | 7:03 | 50.074
2020-08-29 | 7:03 | 50.074
2020-08-29 | 7:03 | 50.073
2020-08-29 | 7:03 | 50.072
2020-08-29 | 7:03 | 50.07
2020-08-29 | 7:03 | 50.07
2020-08-29 | 7:03 | 50.07
2020-08-29 | 7:03 | 50.07
2020-08-29 | 7:03 | 50.072
2020-08-29 | 7:03 | 50.072
2020-08-29 | 7:03 | 50.073
2020-08-29 | 7:03 | 50.074
2020-08-29 | 7:03 | 50.075
2020-08-29 | 7:03 | 50.081
2020-08-29 | 7:03 | 50.084
2020-08-29 | 7:03 | 50.086
2020-08-29 | 7:03 | 50.085
2020-08-29 | 7:03 | 50.08
2020-08-29 | 7:03 | 50.076
2020-08-29 | 7:03 | 50.074
2020-08-29 | 7:03 | 50.07
2020-08-29 | 7:03 | 50.067
2020-08-29 | 7:03 | 50.066
2020-08-29 | 7:04 | 50.068
2020-08-29 | 7:04 | 50.071
2020-08-29 | 7:04 | 50.076
2020-08-29 | 7:04 | 50.083
2020-08-29 | 7:04 | 50.091
2020-08-29 | 7:04 | 50.096
2020-08-29 | 7:04 | 50.099
2020-08-29 | 7:04 | 50.101
2020-08-29 | 7:04 | 50.105
2020-08-29 | 7:04 | 50.106
2020-08-29 | 7:04 | 50.104
2020-08-29 | 7:04 | 50.102
2020-08-29 | 7:04 | 50.101
2020-08-29 | 7:04 | 50.098
2020-08-29 | 7:04 | 50.097
2020-08-29 | 7:04 | 50.097
2020-08-29 | 7:04 | 50.097
2020-08-29 | 7:04 | 50.098
2020-08-29 | 7:04 | 50.095
2020-08-29 | 7:04 | 50.095
2020-08-29 | 7:04 | 50.096
2020-08-29 | 7:04 | 50.098
2020-08-29 | 7:04 | 50.1
2020-08-29 | 7:04 | 50.101
2020-08-29 | 7:04 | 50.1
2020-08-29 | 7:04 | 50.101
2020-08-29 | 7:04 | 50.098
2020-08-29 | 7:04 | 50.099
2020-08-29 | 7:04 | 50.098
2020-08-29 | 7:04 | 50.093
2020-08-29 | 7:04 | 50.088
2020-08-29 | 7:04 | 50.084
2020-08-29 | 7:04 | 50.081
2020-08-29 | 7:04 | 50.081
2020-08-29 | 7:04 | 50.078
2020-08-29 | 7:04 | 50.076
2020-08-29 | 7:04 | 50.068
2020-08-29 | 7:04 | 50.064
2020-08-29 | 7:04 | 50.061
2020-08-29 | 7:04 | 50.059
2020-08-29 | 7:04 | 50.055
2020-08-29 | 7:04 | 50.055
2020-08-29 | 7:04 | 50.052
2020-08-29 | 7:04 | 50.052
2020-08-29 | 7:04 | 50.054
2020-08-29 | 7:04 | 50.061
2020-08-29 | 7:04 | 50.064
2020-08-29 | 7:04 | 50.069
2020-08-29 | 7:04 | 50.071
2020-08-29 | 7:04 | 50.071
2020-08-29 | 7:04 | 50.073
2020-08-29 | 7:04 | 50.071
2020-08-29 | 7:04 | 50.072
2020-08-29 | 7:04 | 50.069
2020-08-29 | 7:04 | 50.066
2020-08-29 | 7:04 | 50.062
2020-08-29 | 7:04 | 50.06
2020-08-29 | 7:04 | 50.059
2020-08-29 | 7:04 | 50.056
2020-08-29 | 7:05 | 50.055
2020-08-29 | 7:05 | 50.052
2020-08-29 | 7:05 | 50.051
2020-08-29 | 7:05 | 50.055
2020-08-29 | 7:05 | 50.062
2020-08-29 | 7:05 | 50.067
2020-08-29 | 7:05 | 50.071
2020-08-29 | 7:05 | 50.075
2020-08-29 | 7:05 | 50.075
2020-08-29 | 7:05 | 50.075
2020-08-29 | 7:05 | 50.077
2020-08-29 | 7:05 | 50.074
2020-08-29 | 7:05 | 50.073
2020-08-29 | 7:05 | 50.073
2020-08-29 | 7:05 | 50.078
2020-08-29 | 7:05 | 50.081
2020-08-29 | 7:05 | 50.085
2020-08-29 | 7:05 | 50.083
2020-08-29 | 7:05 | 50.079
2020-08-29 | 7:05 | 50.074
2020-08-29 | 7:05 | 50.068
2020-08-29 | 7:05 | 50.064
2020-08-29 | 7:05 | 50.065
2020-08-29 | 7:05 | 50.063
2020-08-29 | 7:05 | 50.06
2020-08-29 | 7:05 | 50.058
2020-08-29 | 7:05 | 50.056
2020-08-29 | 7:05 | 50.056
2020-08-29 | 7:05 | 50.056
2020-08-29 | 7:05 | 50.053
2020-08-29 | 7:05 | 50.054
2020-08-29 | 7:05 | 50.053
2020-08-29 | 7:05 | 50.052
2020-08-29 | 7:05 | 50.051
2020-08-29 | 7:05 | 50.049
2020-08-29 | 7:05 | 50.046
2020-08-29 | 7:05 | 50.042
2020-08-29 | 7:05 | 50.042
2020-08-29 | 7:05 | 50.04
2020-08-29 | 7:05 | 50.039
2020-08-29 | 7:05 | 50.036
2020-08-29 | 7:05 | 50.032
2020-08-29 | 7:05 | 50.034
2020-08-29 | 7:05 | 50.036
2020-08-29 | 7:05 | 50.04
2020-08-29 | 7:05 | 50.042
2020-08-29 | 7:05 | 50.048
2020-08-29 | 7:05 | 50.054
2020-08-29 | 7:05 | 50.059
2020-08-29 | 7:05 | 50.059
2020-08-29 | 7:05 | 50.06
2020-08-29 | 7:05 | 50.062
2020-08-29 | 7:05 | 50.061
2020-08-29 | 7:05 | 50.058
2020-08-29 | 7:05 | 50.053
2020-08-29 | 7:05 | 50.048
2020-08-29 | 7:05 | 50.042
2020-08-29 | 7:05 | 50.037
2020-08-29 | 7:05 | 50.035
2020-08-29 | 7:05 | 50.034
2020-08-29 | 7:05 | 50.03
2020-08-29 | 7:06 | 50.024
2020-08-29 | 7:06 | 50.022
2020-08-29 | 7:06 | 50.017
2020-08-29 | 7:06 | 50.019
2020-08-29 | 7:06 | 50.019
2020-08-29 | 7:06 | 50.021
2020-08-29 | 7:06 | 50.024
2020-08-29 | 7:06 | 50.024
2020-08-29 | 7:06 | 50.027
2020-08-29 | 7:06 | 50.031
2020-08-29 | 7:06 | 50.04
2020-08-29 | 7:06 | 50.045
2020-08-29 | 7:06 | 50.046
2020-08-29 | 7:06 | 50.043
2020-08-29 | 7:06 | 50.039
2020-08-29 | 7:06 | 50.032
2020-08-29 | 7:06 | 50.026
2020-08-29 | 7:06 | 50.024
2020-08-29 | 7:06 | 50.022
2020-08-29 | 7:06 | 50.022
2020-08-29 | 7:06 | 50.021
2020-08-29 | 7:06 | 50.022
2020-08-29 | 7:06 | 50.02
2020-08-29 | 7:06 | 50.018
2020-08-29 | 7:06 | 50.019
2020-08-29 | 7:06 | 50.019
2020-08-29 | 7:06 | 50.021
2020-08-29 | 7:06 | 50.022
2020-08-29 | 7:06 | 50.019
2020-08-29 | 7:06 | 50.016
2020-08-29 | 7:06 | 50.015
2020-08-29 | 7:06 | 50.017
2020-08-29 | 7:06 | 50.019
2020-08-29 | 7:06 | 50.018
2020-08-29 | 7:06 | 50.02
2020-08-29 | 7:06 | 50.016
2020-08-29 | 7:06 | 50.016
2020-08-29 | 7:06 | 50.011
2020-08-29 | 7:06 | 50.006
2020-08-29 | 7:06 | 50
2020-08-29 | 7:06 | 49.994
2020-08-29 | 7:06 | 49.988
2020-08-29 | 7:06 | 49.983
2020-08-29 | 7:06 | 49.978
2020-08-29 | 7:06 | 49.976
2020-08-29 | 7:06 | 49.975
2020-08-29 | 7:06 | 49.976
2020-08-29 | 7:06 | 49.976
2020-08-29 | 7:06 | 49.977
2020-08-29 | 7:06 | 49.979
2020-08-29 | 7:06 | 49.98
2020-08-29 | 7:06 | 49.984
2020-08-29 | 7:06 | 49.988
2020-08-29 | 7:06 | 49.989
2020-08-29 | 7:06 | 49.995
2020-08-29 | 7:06 | 49.997
2020-08-29 | 7:06 | 50.001
2020-08-29 | 7:06 | 50.004
2020-08-29 | 7:06 | 50.008
2020-08-29 | 7:07 | 50.01
2020-08-29 | 7:07 | 50.012
2020-08-29 | 7:07 | 50.013
2020-08-29 | 7:07 | 50.013
2020-08-29 | 7:07 | 50.012
2020-08-29 | 7:07 | 50.015
2020-08-29 | 7:07 | 50.011
2020-08-29 | 7:07 | 50.012
2020-08-29 | 7:07 | 50.012
2020-08-29 | 7:07 | 50.01
2020-08-29 | 7:07 | 50.012
2020-08-29 | 7:07 | 50.016
2020-08-29 | 7:07 | 50.018
2020-08-29 | 7:07 | 50.017
2020-08-29 | 7:07 | 50.018
2020-08-29 | 7:07 | 50.019
2020-08-29 | 7:07 | 50.017
2020-08-29 | 7:07 | 50.014
2020-08-29 | 7:07 | 50.008
2020-08-29 | 7:07 | 50.004
2020-08-29 | 7:07 | 50
2020-08-29 | 7:07 | 50
2020-08-29 | 7:07 | 50
2020-08-29 | 7:07 | 50.006
2020-08-29 | 7:07 | 50.011
2020-08-29 | 7:07 | 50.012
2020-08-29 | 7:07 | 50.011
2020-08-29 | 7:07 | 50.009
2020-08-29 | 7:07 | 50.008
2020-08-29 | 7:07 | 50.006
2020-08-29 | 7:07 | 50.007
2020-08-29 | 7:07 | 50.007
2020-08-29 | 7:07 | 50.006
2020-08-29 | 7:07 | 50.005
2020-08-29 | 7:07 | 50.007
2020-08-29 | 7:07 | 50.004
2020-08-29 | 7:07 | 50.003
2020-08-29 | 7:07 | 50.004
2020-08-29 | 7:07 | 50.001
2020-08-29 | 7:07 | 50
2020-08-29 | 7:07 | 50
2020-08-29 | 7:07 | 50.002
2020-08-29 | 7:07 | 50.006
2020-08-29 | 7:07 | 50.008
2020-08-29 | 7:07 | 50.008
2020-08-29 | 7:07 | 50.009
2020-08-29 | 7:07 | 50.012
2020-08-29 | 7:07 | 50.013
2020-08-29 | 7:07 | 50.011
2020-08-29 | 7:07 | 50.004
2020-08-29 | 7:07 | 49.999
2020-08-29 | 7:07 | 49.991
2020-08-29 | 7:07 | 49.979
2020-08-29 | 7:07 | 49.973
2020-08-29 | 7:07 | 49.969
2020-08-29 | 7:07 | 49.967
2020-08-29 | 7:07 | 49.968
2020-08-29 | 7:07 | 49.968
2020-08-29 | 7:07 | 49.971
2020-08-29 | 7:07 | 49.976
2020-08-29 | 7:08 | 49.981
2020-08-29 | 7:08 | 49.985
2020-08-29 | 7:08 | 49.988
2020-08-29 | 7:08 | 49.988
2020-08-29 | 7:08 | 49.987
2020-08-29 | 7:08 | 49.987
2020-08-29 | 7:08 | 49.991
2020-08-29 | 7:08 | 49.993
2020-08-29 | 7:08 | 49.995
2020-08-29 | 7:08 | 49.997
2020-08-29 | 7:08 | 49.999
2020-08-29 | 7:08 | 49.999
2020-08-29 | 7:08 | 50.002
2020-08-29 | 7:08 | 50.006
2020-08-29 | 7:08 | 50.004
2020-08-29 | 7:08 | 50
2020-08-29 | 7:08 | 49.996
2020-08-29 | 7:08 | 49.993
2020-08-29 | 7:08 | 49.988
2020-08-29 | 7:08 | 49.983
2020-08-29 | 7:08 | 49.982
2020-08-29 | 7:08 | 49.983
2020-08-29 | 7:08 | 49.982
2020-08-29 | 7:08 | 49.98
2020-08-29 | 7:08 | 49.979
2020-08-29 | 7:08 | 49.977
2020-08-29 | 7:08 | 49.973
2020-08-29 | 7:08 | 49.97
2020-08-29 | 7:08 | 49.971
2020-08-29 | 7:08 | 49.97
2020-08-29 | 7:08 | 49.97
2020-08-29 | 7:08 | 49.968
2020-08-29 | 7:08 | 49.967
2020-08-29 | 7:08 | 49.969
2020-08-29 | 7:08 | 49.971
2020-08-29 | 7:08 | 49.973
2020-08-29 | 7:08 | 49.973
2020-08-29 | 7:08 | 49.973
2020-08-29 | 7:08 | 49.972
2020-08-29 | 7:08 | 49.97
2020-08-29 | 7:08 | 49.97
2020-08-29 | 7:08 | 49.97
2020-08-29 | 7:08 | 49.971
2020-08-29 | 7:08 | 49.972
2020-08-29 | 7:08 | 49.974
2020-08-29 | 7:08 | 49.975
2020-08-29 | 7:08 | 49.977
2020-08-29 | 7:08 | 49.98
2020-08-29 | 7:08 | 49.983
2020-08-29 | 7:08 | 49.987
2020-08-29 | 7:08 | 49.987
2020-08-29 | 7:08 | 49.99
2020-08-29 | 7:08 | 49.993
2020-08-29 | 7:08 | 49.992
2020-08-29 | 7:08 | 49.993
2020-08-29 | 7:08 | 49.996
2020-08-29 | 7:08 | 50.002
2020-08-29 | 7:08 | 50.006
2020-08-29 | 7:08 | 50.013
2020-08-29 | 7:08 | 50.018
2020-08-29 | 7:08 | 50.023
2020-08-29 | 7:09 | 50.025
2020-08-29 | 7:09 | 50.025
2020-08-29 | 7:09 | 50.026
2020-08-29 | 7:09 | 50.027
2020-08-29 | 7:09 | 50.028
2020-08-29 | 7:09 | 50.031
2020-08-29 | 7:09 | 50.037
2020-08-29 | 7:09 | 50.04
2020-08-29 | 7:09 | 50.043
2020-08-29 | 7:09 | 50.045
2020-08-29 | 7:09 | 50.045
2020-08-29 | 7:09 | 50.04
2020-08-29 | 7:09 | 50.037
2020-08-29 | 7:09 | 50.032
2020-08-29 | 7:09 | 50.031
2020-08-29 | 7:09 | 50.029
2020-08-29 | 7:09 | 50.027
2020-08-29 | 7:09 | 50.027
2020-08-29 | 7:09 | 50.025
2020-08-29 | 7:09 | 50.025
2020-08-29 | 7:09 | 50.027
2020-08-29 | 7:09 | 50.026
2020-08-29 | 7:09 | 50.025
2020-08-29 | 7:09 | 50.025
2020-08-29 | 7:09 | 50.024
2020-08-29 | 7:09 | 50.022
2020-08-29 | 7:09 | 50.02
2020-08-29 | 7:09 | 50.02
2020-08-29 | 7:09 | 50.022
2020-08-29 | 7:09 | 50.02
2020-08-29 | 7:09 | 50.018
2020-08-29 | 7:09 | 50.014
2020-08-29 | 7:09 | 50.012
2020-08-29 | 7:09 | 50.01
2020-08-29 | 7:09 | 50.008
2020-08-29 | 7:09 | 50.006
2020-08-29 | 7:09 | 50.004
2020-08-29 | 7:09 | 50.001
2020-08-29 | 7:09 | 49.997
2020-08-29 | 7:09 | 49.993
2020-08-29 | 7:09 | 49.988
2020-08-29 | 7:09 | 49.983
2020-08-29 | 7:09 | 49.979
2020-08-29 | 7:09 | 49.976
2020-08-29 | 7:09 | 49.977
2020-08-29 | 7:09 | 49.978
2020-08-29 | 7:09 | 49.976
2020-08-29 | 7:09 | 49.975
2020-08-29 | 7:09 | 49.976
2020-08-29 | 7:09 | 49.977
2020-08-29 | 7:09 | 49.981
2020-08-29 | 7:09 | 49.983
2020-08-29 | 7:09 | 49.984
2020-08-29 | 7:09 | 49.984
2020-08-29 | 7:09 | 49.986
2020-08-29 | 7:09 | 49.989
2020-08-29 | 7:09 | 49.991
2020-08-29 | 7:09 | 49.992
2020-08-29 | 7:09 | 49.994
2020-08-29 | 7:10 | 49.998
2020-08-29 | 7:10 | 50.002
2020-08-29 | 7:10 | 50.006
2020-08-29 | 7:10 | 50.009
2020-08-29 | 7:10 | 50.011
2020-08-29 | 7:10 | 50.012
2020-08-29 | 7:10 | 50.01
2020-08-29 | 7:10 | 50.007
2020-08-29 | 7:10 | 50.008
2020-08-29 | 7:10 | 50.006
2020-08-29 | 7:10 | 50.006
2020-08-29 | 7:10 | 50.007
2020-08-29 | 7:10 | 50.008
2020-08-29 | 7:10 | 50.007
2020-08-29 | 7:10 | 50.006
2020-08-29 | 7:10 | 50.006
2020-08-29 | 7:10 | 50.012
2020-08-29 | 7:10 | 50.015
2020-08-29 | 7:10 | 50.016
2020-08-29 | 7:10 | 50.014
2020-08-29 | 7:10 | 50.012
2020-08-29 | 7:10 | 50.009
2020-08-29 | 7:10 | 50.006
2020-08-29 | 7:10 | 50.002
2020-08-29 | 7:10 | 50
2020-08-29 | 7:10 | 49.998
2020-08-29 | 7:10 | 49.998
2020-08-29 | 7:10 | 49.997
2020-08-29 | 7:10 | 49.997
2020-08-29 | 7:10 | 49.998
2020-08-29 | 7:10 | 49.997
2020-08-29 | 7:10 | 49.994
2020-08-29 | 7:10 | 49.991
2020-08-29 | 7:10 | 49.99
2020-08-29 | 7:10 | 49.988
2020-08-29 | 7:10 | 49.987
2020-08-29 | 7:10 | 49.983
2020-08-29 | 7:10 | 49.979
2020-08-29 | 7:10 | 49.977
2020-08-29 | 7:10 | 49.975
2020-08-29 | 7:10 | 49.976
2020-08-29 | 7:10 | 49.979
2020-08-29 | 7:10 | 49.979
2020-08-29 | 7:10 | 49.985
2020-08-29 | 7:10 | 49.988
2020-08-29 | 7:10 | 49.99
2020-08-29 | 7:10 | 49.993
2020-08-29 | 7:10 | 49.996
2020-08-29 | 7:10 | 49.998
2020-08-29 | 7:10 | 50
2020-08-29 | 7:10 | 50.001
2020-08-29 | 7:10 | 50.001
2020-08-29 | 7:10 | 49.998
2020-08-29 | 7:10 | 49.996
2020-08-29 | 7:10 | 49.993
2020-08-29 | 7:10 | 49.989
2020-08-29 | 7:10 | 49.986
2020-08-29 | 7:10 | 49.979
2020-08-29 | 7:10 | 49.979
2020-08-29 | 7:10 | 49.977
2020-08-29 | 7:10 | 49.978
2020-08-29 | 7:11 | 49.982
2020-08-29 | 7:11 | 49.987
2020-08-29 | 7:11 | 49.987
2020-08-29 | 7:11 | 49.984
2020-08-29 | 7:11 | 49.984
2020-08-29 | 7:11 | 49.985
2020-08-29 | 7:11 | 49.983
2020-08-29 | 7:11 | 49.98
2020-08-29 | 7:11 | 49.977
2020-08-29 | 7:11 | 49.975
2020-08-29 | 7:11 | 49.974
2020-08-29 | 7:11 | 49.972
2020-08-29 | 7:11 | 49.97
2020-08-29 | 7:11 | 49.965
2020-08-29 | 7:11 | 49.96
2020-08-29 | 7:11 | 49.958
2020-08-29 | 7:11 | 49.958
2020-08-29 | 7:11 | 49.96
2020-08-29 | 7:11 | 49.959
2020-08-29 | 7:11 | 49.96
2020-08-29 | 7:11 | 49.963
2020-08-29 | 7:11 | 49.966
2020-08-29 | 7:11 | 49.969
2020-08-29 | 7:11 | 49.972
2020-08-29 | 7:11 | 49.975
2020-08-29 | 7:11 | 49.976
2020-08-29 | 7:11 | 49.978
2020-08-29 | 7:11 | 49.98
2020-08-29 | 7:11 | 49.981
2020-08-29 | 7:11 | 49.981
2020-08-29 | 7:11 | 49.978
2020-08-29 | 7:11 | 49.975
2020-08-29 | 7:11 | 49.971
2020-08-29 | 7:11 | 49.969
2020-08-29 | 7:11 | 49.973
2020-08-29 | 7:11 | 49.975
2020-08-29 | 7:11 | 49.975
2020-08-29 | 7:11 | 49.975
2020-08-29 | 7:11 | 49.972
2020-08-29 | 7:11 | 49.971
2020-08-29 | 7:11 | 49.968
2020-08-29 | 7:11 | 49.966
2020-08-29 | 7:11 | 49.962
2020-08-29 | 7:11 | 49.96
2020-08-29 | 7:11 | 49.956
2020-08-29 | 7:11 | 49.953
2020-08-29 | 7:11 | 49.955
2020-08-29 | 7:11 | 49.955
2020-08-29 | 7:11 | 49.956
2020-08-29 | 7:11 | 49.951
2020-08-29 | 7:11 | 49.949
2020-08-29 | 7:11 | 49.945
2020-08-29 | 7:11 | 49.947
2020-08-29 | 7:11 | 49.945
2020-08-29 | 7:11 | 49.945
2020-08-29 | 7:11 | 49.944
2020-08-29 | 7:11 | 49.945
2020-08-29 | 7:11 | 49.943
2020-08-29 | 7:11 | 49.943
2020-08-29 | 7:12 | 49.94
2020-08-29 | 7:12 | 49.94
2020-08-29 | 7:12 | 49.939
2020-08-29 | 7:12 | 49.938
2020-08-29 | 7:12 | 49.935
2020-08-29 | 7:12 | 49.934
2020-08-29 | 7:12 | 49.932
2020-08-29 | 7:12 | 49.931
2020-08-29 | 7:12 | 49.933
2020-08-29 | 7:12 | 49.937
2020-08-29 | 7:12 | 49.941
2020-08-29 | 7:12 | 49.944
2020-08-29 | 7:12 | 49.946
2020-08-29 | 7:12 | 49.946
2020-08-29 | 7:12 | 49.947
2020-08-29 | 7:12 | 49.948
2020-08-29 | 7:12 | 49.947
2020-08-29 | 7:12 | 49.946
2020-08-29 | 7:12 | 49.942
2020-08-29 | 7:12 | 49.937
2020-08-29 | 7:12 | 49.932
2020-08-29 | 7:12 | 49.929
2020-08-29 | 7:12 | 49.926
2020-08-29 | 7:12 | 49.924
2020-08-29 | 7:12 | 49.922
2020-08-29 | 7:12 | 49.921
2020-08-29 | 7:12 | 49.918
2020-08-29 | 7:12 | 49.917
2020-08-29 | 7:12 | 49.916
2020-08-29 | 7:12 | 49.913
2020-08-29 | 7:12 | 49.91
2020-08-29 | 7:12 | 49.912
2020-08-29 | 7:12 | 49.911
2020-08-29 | 7:12 | 49.911
2020-08-29 | 7:12 | 49.911
2020-08-29 | 7:12 | 49.911
2020-08-29 | 7:12 | 49.912
2020-08-29 | 7:12 | 49.913
2020-08-29 | 7:12 | 49.913
2020-08-29 | 7:12 | 49.91
2020-08-29 | 7:12 | 49.909
2020-08-29 | 7:12 | 49.907
2020-08-29 | 7:12 | 49.908
2020-08-29 | 7:12 | 49.906
2020-08-29 | 7:12 | 49.903
2020-08-29 | 7:12 | 49.905
2020-08-29 | 7:12 | 49.909
2020-08-29 | 7:12 | 49.911
2020-08-29 | 7:12 | 49.911
2020-08-29 | 7:12 | 49.911
2020-08-29 | 7:12 | 49.911
2020-08-29 | 7:12 | 49.908
2020-08-29 | 7:12 | 49.908
2020-08-29 | 7:12 | 49.906
2020-08-29 | 7:12 | 49.903
2020-08-29 | 7:12 | 49.9
2020-08-29 | 7:12 | 49.901
2020-08-29 | 7:12 | 49.903
2020-08-29 | 7:12 | 49.902
2020-08-29 | 7:12 | 49.902
2020-08-29 | 7:12 | 49.904
2020-08-29 | 7:13 | 49.903
2020-08-29 | 7:13 | 49.904
2020-08-29 | 7:13 | 49.904
2020-08-29 | 7:13 | 49.903
2020-08-29 | 7:13 | 49.903
2020-08-29 | 7:13 | 49.901
2020-08-29 | 7:13 | 49.9
2020-08-29 | 7:13 | 49.9
2020-08-29 | 7:13 | 49.903
2020-08-29 | 7:13 | 49.904
2020-08-29 | 7:13 | 49.902
2020-08-29 | 7:13 | 49.903
2020-08-29 | 7:13 | 49.903
2020-08-29 | 7:13 | 49.902
2020-08-29 | 7:13 | 49.903
2020-08-29 | 7:13 | 49.906
2020-08-29 | 7:13 | 49.908
2020-08-29 | 7:13 | 49.906
2020-08-29 | 7:13 | 49.907
2020-08-29 | 7:13 | 49.912
2020-08-29 | 7:13 | 49.915
2020-08-29 | 7:13 | 49.917
2020-08-29 | 7:13 | 49.919
2020-08-29 | 7:13 | 49.921
2020-08-29 | 7:13 | 49.917
2020-08-29 | 7:13 | 49.914
2020-08-29 | 7:13 | 49.91
2020-08-29 | 7:13 | 49.907
2020-08-29 | 7:13 | 49.909
2020-08-29 | 7:13 | 49.912
2020-08-29 | 7:13 | 49.915
2020-08-29 | 7:13 | 49.916
2020-08-29 | 7:13 | 49.916
2020-08-29 | 7:13 | 49.91
2020-08-29 | 7:13 | 49.908
2020-08-29 | 7:13 | 49.905
2020-08-29 | 7:13 | 49.903
2020-08-29 | 7:13 | 49.9
2020-08-29 | 7:13 | 49.896
2020-08-29 | 7:13 | 49.891
2020-08-29 | 7:13 | 49.889
2020-08-29 | 7:13 | 49.889
2020-08-29 | 7:13 | 49.892
2020-08-29 | 7:13 | 49.899
2020-08-29 | 7:13 | 49.908
2020-08-29 | 7:13 | 49.914
2020-08-29 | 7:13 | 49.915
2020-08-29 | 7:13 | 49.916
2020-08-29 | 7:13 | 49.915
2020-08-29 | 7:13 | 49.914
2020-08-29 | 7:13 | 49.914
2020-08-29 | 7:13 | 49.911
2020-08-29 | 7:13 | 49.907
2020-08-29 | 7:13 | 49.904
2020-08-29 | 7:13 | 49.903
2020-08-29 | 7:13 | 49.904
2020-08-29 | 7:13 | 49.905
2020-08-29 | 7:13 | 49.907
2020-08-29 | 7:13 | 49.907
2020-08-29 | 7:14 | 49.908
2020-08-29 | 7:14 | 49.906
2020-08-29 | 7:14 | 49.91
2020-08-29 | 7:14 | 49.911
2020-08-29 | 7:14 | 49.915
2020-08-29 | 7:14 | 49.915
2020-08-29 | 7:14 | 49.914
2020-08-29 | 7:14 | 49.914
2020-08-29 | 7:14 | 49.913
2020-08-29 | 7:14 | 49.914
2020-08-29 | 7:14 | 49.916
2020-08-29 | 7:14 | 49.917
2020-08-29 | 7:14 | 49.918
2020-08-29 | 7:14 | 49.917
2020-08-29 | 7:14 | 49.917
2020-08-29 | 7:14 | 49.914
2020-08-29 | 7:14 | 49.911
2020-08-29 | 7:14 | 49.909
2020-08-29 | 7:14 | 49.907
2020-08-29 | 7:14 | 49.908
2020-08-29 | 7:14 | 49.91
2020-08-29 | 7:14 | 49.908
2020-08-29 | 7:14 | 49.909
2020-08-29 | 7:14 | 49.91
2020-08-29 | 7:14 | 49.91
2020-08-29 | 7:14 | 49.907
2020-08-29 | 7:14 | 49.903
2020-08-29 | 7:14 | 49.899
2020-08-29 | 7:14 | 49.898
2020-08-29 | 7:14 | 49.895
2020-08-29 | 7:14 | 49.892
2020-08-29 | 7:14 | 49.889
2020-08-29 | 7:14 | 49.886
2020-08-29 | 7:14 | 49.885
2020-08-29 | 7:14 | 49.885
2020-08-29 | 7:14 | 49.883
2020-08-29 | 7:14 | 49.88
2020-08-29 | 7:14 | 49.878
2020-08-29 | 7:14 | 49.879
2020-08-29 | 7:14 | 49.877
2020-08-29 | 7:14 | 49.877
2020-08-29 | 7:14 | 49.877
2020-08-29 | 7:14 | 49.879
2020-08-29 | 7:14 | 49.879
2020-08-29 | 7:14 | 49.88
2020-08-29 | 7:14 | 49.882
2020-08-29 | 7:14 | 49.883
2020-08-29 | 7:14 | 49.884
2020-08-29 | 7:14 | 49.887
2020-08-29 | 7:14 | 49.889
2020-08-29 | 7:14 | 49.893
2020-08-29 | 7:14 | 49.9
2020-08-29 | 7:14 | 49.907
2020-08-29 | 7:14 | 49.912
2020-08-29 | 7:14 | 49.916
2020-08-29 | 7:14 | 49.918
2020-08-29 | 7:14 | 49.922
2020-08-29 | 7:14 | 49.922
2020-08-29 | 7:14 | 49.921
2020-08-29 | 7:14 | 49.92
2020-08-29 | 7:14 | 49.92
2020-08-29 | 7:15 | 49.919
2020-08-29 | 7:15 | 49.919
2020-08-29 | 7:15 | 49.917
2020-08-29 | 7:15 | 49.915
2020-08-29 | 7:15 | 49.915
2020-08-29 | 7:15 | 49.918
2020-08-29 | 7:15 | 49.92
2020-08-29 | 7:15 | 49.925
2020-08-29 | 7:15 | 49.926
2020-08-29 | 7:15 | 49.927
2020-08-29 | 7:15 | 49.932
2020-08-29 | 7:15 | 49.935
2020-08-29 | 7:15 | 49.939
2020-08-29 | 7:15 | 49.943
2020-08-29 | 7:15 | 49.945
2020-08-29 | 7:15 | 49.946
2020-08-29 | 7:15 | 49.948
2020-08-29 | 7:15 | 49.947
2020-08-29 | 7:15 | 49.947
2020-08-29 | 7:15 | 49.949
2020-08-29 | 7:15 | 49.951
2020-08-29 | 7:15 | 49.952
2020-08-29 | 7:15 | 49.95
2020-08-29 | 7:15 | 49.953
2020-08-29 | 7:15 | 49.955
2020-08-29 | 7:15 | 49.957
2020-08-29 | 7:15 | 49.958
2020-08-29 | 7:15 | 49.96
2020-08-29 | 7:15 | 49.963
2020-08-29 | 7:15 | 49.964
2020-08-29 | 7:15 | 49.962
2020-08-29 | 7:15 | 49.961
2020-08-29 | 7:15 | 49.96
2020-08-29 | 7:15 | 49.959
2020-08-29 | 7:15 | 49.958
2020-08-29 | 7:15 | 49.956
2020-08-29 | 7:15 | 49.954
2020-08-29 | 7:15 | 49.956
2020-08-29 | 7:15 | 49.96
2020-08-29 | 7:15 | 49.962
2020-08-29 | 7:15 | 49.966
2020-08-29 | 7:15 | 49.97
2020-08-29 | 7:15 | 49.973
2020-08-29 | 7:15 | 49.975
2020-08-29 | 7:15 | 49.976
2020-08-29 | 7:15 | 49.977
2020-08-29 | 7:15 | 49.977
2020-08-29 | 7:15 | 49.98
2020-08-29 | 7:15 | 49.979
2020-08-29 | 7:15 | 49.977
2020-08-29 | 7:15 | 49.979
2020-08-29 | 7:15 | 49.984
2020-08-29 | 7:15 | 49.986
2020-08-29 | 7:15 | 49.988
2020-08-29 | 7:15 | 49.989
2020-08-29 | 7:15 | 49.99
2020-08-29 | 7:15 | 49.99
2020-08-29 | 7:15 | 49.989
2020-08-29 | 7:15 | 49.991
2020-08-29 | 7:16 | 49.994
2020-08-29 | 7:16 | 49.996
2020-08-29 | 7:16 | 50
2020-08-29 | 7:16 | 50.002
2020-08-29 | 7:16 | 50.001
2020-08-29 | 7:16 | 49.999
2020-08-29 | 7:16 | 49.997
2020-08-29 | 7:16 | 49.995
2020-08-29 | 7:16 | 49.995
2020-08-29 | 7:16 | 49.993
2020-08-29 | 7:16 | 49.991
2020-08-29 | 7:16 | 49.99
2020-08-29 | 7:16 | 49.986
2020-08-29 | 7:16 | 49.987
2020-08-29 | 7:16 | 49.988
2020-08-29 | 7:16 | 49.988
2020-08-29 | 7:16 | 49.986
2020-08-29 | 7:16 | 49.985
2020-08-29 | 7:16 | 49.981
2020-08-29 | 7:16 | 49.981
2020-08-29 | 7:16 | 49.984
2020-08-29 | 7:16 | 49.985
2020-08-29 | 7:16 | 49.988
2020-08-29 | 7:16 | 49.993
2020-08-29 | 7:16 | 49.992
2020-08-29 | 7:16 | 49.991
2020-08-29 | 7:16 | 49.989
2020-08-29 | 7:16 | 49.984
2020-08-29 | 7:16 | 49.982
2020-08-29 | 7:16 | 49.979
2020-08-29 | 7:16 | 49.976
2020-08-29 | 7:16 | 49.974
2020-08-29 | 7:16 | 49.974
2020-08-29 | 7:16 | 49.972
2020-08-29 | 7:16 | 49.973
2020-08-29 | 7:16 | 49.977
2020-08-29 | 7:16 | 49.973
2020-08-29 | 7:16 | 49.967
2020-08-29 | 7:16 | 49.963
2020-08-29 | 7:16 | 49.961
2020-08-29 | 7:16 | 49.961
2020-08-29 | 7:16 | 49.961
2020-08-29 | 7:16 | 49.959
2020-08-29 | 7:16 | 49.956
2020-08-29 | 7:16 | 49.954
2020-08-29 | 7:16 | 49.956
2020-08-29 | 7:16 | 49.954
2020-08-29 | 7:16 | 49.958
2020-08-29 | 7:16 | 49.962
2020-08-29 | 7:16 | 49.967
2020-08-29 | 7:16 | 49.972
2020-08-29 | 7:16 | 49.978
2020-08-29 | 7:16 | 49.98
2020-08-29 | 7:16 | 49.979
2020-08-29 | 7:16 | 49.975
2020-08-29 | 7:16 | 49.975
2020-08-29 | 7:16 | 49.972
2020-08-29 | 7:16 | 49.965
2020-08-29 | 7:16 | 49.959
2020-08-29 | 7:16 | 49.959
2020-08-29 | 7:16 | 49.962
2020-08-29 | 7:17 | 49.965
2020-08-29 | 7:17 | 49.966
2020-08-29 | 7:17 | 49.97
2020-08-29 | 7:17 | 49.973
2020-08-29 | 7:17 | 49.974
2020-08-29 | 7:17 | 49.98
2020-08-29 | 7:17 | 49.985
2020-08-29 | 7:17 | 49.989
2020-08-29 | 7:17 | 49.988
2020-08-29 | 7:17 | 49.988
2020-08-29 | 7:17 | 49.988
2020-08-29 | 7:17 | 49.989
2020-08-29 | 7:17 | 49.989
2020-08-29 | 7:17 | 49.991
2020-08-29 | 7:17 | 49.991
2020-08-29 | 7:17 | 49.991
2020-08-29 | 7:17 | 49.991
2020-08-29 | 7:17 | 49.989
2020-08-29 | 7:17 | 49.988
2020-08-29 | 7:17 | 49.988
2020-08-29 | 7:17 | 49.986
2020-08-29 | 7:17 | 49.986
2020-08-29 | 7:17 | 49.985
2020-08-29 | 7:17 | 49.987
2020-08-29 | 7:17 | 49.991
2020-08-29 | 7:17 | 49.993
2020-08-29 | 7:17 | 49.996
2020-08-29 | 7:17 | 49.997
2020-08-29 | 7:17 | 49.997

## Event 20200830-1
In UTC
Date | Time | Freq
2020-08-30 | 11:16 | 49.88
2020-08-30 | 11:16 | 49.88
2020-08-30 | 11:16 | 49.88
2020-08-30 | 11:16 | 49.877
2020-08-30 | 11:16 | 49.876
2020-08-30 | 12:16 | 49.873
2020-08-30 | 13:16 | 49.872
2020-08-30 | 14:16 | 49.873
2020-08-30 | 15:16 | 49.874
2020-08-30 | 16:16 | 49.875
2020-08-30 | 17:16 | 49.874
2020-08-30 | 18:16 | 49.873
2020-08-30 | 19:16 | 49.871
2020-08-30 | 20:16 | 49.87
2020-08-30 | 21:16 | 49.87
2020-08-30 | 22:16 | 49.87
2020-08-30 | 23:16 | 49.869
2020-08-30 | 24:16 | 49.87
2020-08-30 | 25:16 | 49.869
2020-08-30 | 26:16 | 49.87
2020-08-30 | 27:16 | 49.872
2020-08-30 | 28:16 | 49.872
2020-08-30 | 29:16 | 49.871
2020-08-30 | 30:16 | 49.871
2020-08-30 | 31:16 | 49.871
2020-08-30 | 32:16 | 49.87
2020-08-30 | 33:16 | 49.87
2020-08-30 | 34:16 | 49.873
2020-08-30 | 35:16 | 49.875
2020-08-30 | 36:16 | 49.877
2020-08-30 | 37:16 | 49.88
2020-08-30 | 38:16 | 49.884
2020-08-30 | 39:16 | 49.887
2020-08-30 | 40:16 | 49.887
2020-08-30 | 41:16 | 49.886
2020-08-30 | 42:16 | 49.883
2020-08-30 | 43:16 | 49.88
2020-08-30 | 44:16 | 49.877
2020-08-30 | 45:16 | 49.875
2020-08-30 | 46:16 | 49.872
2020-08-30 | 47:16 | 49.872
2020-08-30 | 48:16 | 49.876
2020-08-30 | 49:16 | 49.879
2020-08-30 | 50:16 | 49.884
2020-08-30 | 51:16 | 49.885
2020-08-30 | 52:16 | 49.886
2020-08-30 | 53:16 | 49.886
2020-08-30 | 54:16 | 49.885
2020-08-30 | 55:16 | 49.886
2020-08-30 | 56:16 | 49.887
2020-08-30 | 57:16 | 49.888
2020-08-30 | 58:16 | 49.888
2020-08-30 | 59:16 | 49.889
2020-08-30 | 60:16 | 49.891
2020-08-30 | 61:16 | 49.894
2020-08-30 | 62:16 | 49.897
2020-08-30 | 63:16 | 49.9
2020-08-30 | 64:16 | 49.902
2020-08-30 | 65:16 | 49.904
2020-08-30 | 66:16 | 49.902
2020-08-30 | 67:16 | 49.904
2020-08-30 | 68:16 | 49.903
2020-08-30 | 69:16 | 49.903
2020-08-30 | 70:16 | 49.904
2020-08-30 | 71:16 | 49.904
2020-08-30 | 72:16 | 49.906
2020-08-30 | 73:16 | 49.895
2020-08-30 | 74:16 | 49.886
2020-08-30 | 75:16 | 49.875
2020-08-30 | 76:16 | 49.868
2020-08-30 | 77:16 | 49.868
2020-08-30 | 78:16 | 49.87
2020-08-30 | 79:16 | 49.872
2020-08-30 | 80:16 | 49.874
2020-08-30 | 81:16 | 49.875
2020-08-30 | 82:16 | 49.877
2020-08-30 | 83:16 | 49.877
2020-08-30 | 84:16 | 49.876
2020-08-30 | 85:16 | 49.876
2020-08-30 | 86:16 | 49.876
2020-08-30 | 87:16 | 49.876
2020-08-30 | 88:16 | 49.878
2020-08-30 | 89:16 | 49.882
2020-08-30 | 90:16 | 49.884
2020-08-30 | 91:16 | 49.888
2020-08-30 | 92:16 | 49.892
2020-08-30 | 93:16 | 49.894
2020-08-30 | 94:16 | 49.898
2020-08-30 | 95:16 | 49.899
2020-08-30 | 96:16 | 49.903
2020-08-30 | 97:16 | 49.909
2020-08-30 | 98:16 | 49.912
2020-08-30 | 99:16 | 49.913
2020-08-30 | 100:16 | 49.914
2020-08-30 | 101:16 | 49.915
2020-08-30 | 102:16 | 49.913
2020-08-30 | 103:16 | 49.911
2020-08-30 | 104:16 | 49.906
2020-08-30 | 105:16 | 49.904
2020-08-30 | 106:16 | 49.904
2020-08-30 | 107:16 | 49.907
2020-08-30 | 108:16 | 49.909
2020-08-30 | 109:16 | 49.909
2020-08-30 | 110:16 | 49.907
2020-08-30 | 111:16 | 49.905
2020-08-30 | 112:16 | 49.903
2020-08-30 | 113:16 | 49.902
2020-08-30 | 114:16 | 49.902
2020-08-30 | 115:16 | 49.9
2020-08-30 | 116:16 | 49.897
2020-08-30 | 117:16 | 49.894
2020-08-30 | 118:16 | 49.891
2020-08-30 | 119:16 | 49.891
2020-08-30 | 120:16 | 49.892
2020-08-30 | 121:16 | 49.893
2020-08-30 | 122:16 | 49.897
2020-08-30 | 123:16 | 49.898
2020-08-30 | 124:16 | 49.896
2020-08-30 | 125:16 | 49.897
2020-08-30 | 126:16 | 49.898
2020-08-30 | 127:16 | 49.898
2020-08-30 | 128:16 | 49.895
2020-08-30 | 129:16 | 49.894
2020-08-30 | 130:16 | 49.892
2020-08-30 | 131:16 | 49.891
2020-08-30 | 132:16 | 49.893
2020-08-30 | 133:16 | 49.893
2020-08-30 | 134:16 | 49.893
2020-08-30 | 135:16 | 49.889
2020-08-30 | 136:16 | 49.887
2020-08-30 | 137:16 | 49.882
2020-08-30 | 138:16 | 49.877
2020-08-30 | 139:16 | 49.875
2020-08-30 | 140:16 | 49.873
2020-08-30 | 141:16 | 49.87
2020-08-30 | 142:16 | 49.868
2020-08-30 | 143:16 | 49.867
2020-08-30 | 144:16 | 49.865
2020-08-30 | 145:16 | 49.865
2020-08-30 | 146:16 | 49.866
2020-08-30 | 147:16 | 49.87
2020-08-30 | 148:16 | 49.874
2020-08-30 | 149:16 | 49.877
2020-08-30 | 150:16 | 49.881
2020-08-30 | 151:16 | 49.886
2020-08-30 | 152:16 | 49.89
2020-08-30 | 153:16 | 49.893
2020-08-30 | 154:16 | 49.893
2020-08-30 | 155:16 | 49.892
2020-08-30 | 156:16 | 49.893
2020-08-30 | 157:16 | 49.891
2020-08-30 | 158:16 | 49.89
2020-08-30 | 159:16 | 49.888
2020-08-30 | 160:16 | 49.886
2020-08-30 | 161:16 | 49.885
2020-08-30 | 162:16 | 49.883
2020-08-30 | 163:16 | 49.881
2020-08-30 | 164:16 | 49.882
2020-08-30 | 165:16 | 49.881
2020-08-30 | 166:16 | 49.879
2020-08-30 | 167:16 | 49.88
2020-08-30 | 168:16 | 49.879
2020-08-30 | 169:16 | 49.878
2020-08-30 | 170:16 | 49.878
2020-08-30 | 171:16 | 49.876
2020-08-30 | 172:16 | 49.874
2020-08-30 | 173:16 | 49.872
2020-08-30 | 174:16 | 49.87
2020-08-30 | 175:16 | 49.869
2020-08-30 | 176:16 | 49.87
2020-08-30 | 177:16 | 49.869
2020-08-30 | 178:16 | 49.867
2020-08-30 | 179:16 | 49.866
2020-08-30 | 180:16 | 49.865
2020-08-30 | 181:16 | 49.864
2020-08-30 | 182:16 | 49.863
2020-08-30 | 183:16 | 49.862
2020-08-30 | 184:16 | 49.862
2020-08-30 | 185:16 | 49.863
2020-08-30 | 186:16 | 49.863
2020-08-30 | 187:16 | 49.863
2020-08-30 | 188:16 | 49.863
2020-08-30 | 189:16 | 49.864
2020-08-30 | 190:16 | 49.864
2020-08-30 | 191:16 | 49.866
2020-08-30 | 192:16 | 49.864
2020-08-30 | 193:16 | 49.861
2020-08-30 | 194:16 | 49.859
2020-08-30 | 195:16 | 49.857
2020-08-30 | 196:16 | 49.854
2020-08-30 | 197:16 | 49.848
2020-08-30 | 198:16 | 49.842
2020-08-30 | 199:16 | 49.836
2020-08-30 | 200:16 | 49.834
2020-08-30 | 201:16 | 49.83
2020-08-30 | 202:16 | 49.827
2020-08-30 | 203:16 | 49.824
2020-08-30 | 204:16 | 49.823
2020-08-30 | 205:16 | 49.824
2020-08-30 | 206:16 | 49.824
2020-08-30 | 207:16 | 49.825
2020-08-30 | 208:16 | 49.824
2020-08-30 | 209:16 | 49.825
2020-08-30 | 210:16 | 49.826
2020-08-30 | 211:16 | 49.829
2020-08-30 | 212:16 | 49.833
2020-08-30 | 213:16 | 49.834
2020-08-30 | 214:16 | 49.835
2020-08-30 | 215:16 | 49.837
2020-08-30 | 216:16 | 49.837
2020-08-30 | 217:16 | 49.839
2020-08-30 | 218:16 | 49.839
2020-08-30 | 219:16 | 49.84
2020-08-30 | 220:16 | 49.842
2020-08-30 | 221:16 | 49.843
2020-08-30 | 222:16 | 49.845
2020-08-30 | 223:16 | 49.847
2020-08-30 | 224:16 | 49.85
2020-08-30 | 225:16 | 49.85
2020-08-30 | 226:16 | 49.85
2020-08-30 | 227:16 | 49.851
2020-08-30 | 228:16 | 49.851
2020-08-30 | 229:16 | 49.85
2020-08-30 | 230:16 | 49.849
2020-08-30 | 231:16 | 49.848
2020-08-30 | 232:16 | 49.848
2020-08-30 | 233:16 | 49.85
2020-08-30 | 234:16 | 49.854
2020-08-30 | 235:16 | 49.861
2020-08-30 | 236:16 | 49.865
2020-08-30 | 237:16 | 49.865
2020-08-30 | 238:16 | 49.862
2020-08-30 | 239:16 | 49.859
2020-08-30 | 240:16 | 49.856
2020-08-30 | 241:16 | 49.853
2020-08-30 | 242:16 | 49.85
2020-08-30 | 243:16 | 49.847
2020-08-30 | 244:16 | 49.842
2020-08-30 | 245:16 | 49.84
2020-08-30 | 246:16 | 49.835
2020-08-30 | 247:16 | 49.831
2020-08-30 | 248:16 | 49.828
2020-08-30 | 249:16 | 49.829
2020-08-30 | 250:16 | 49.832
2020-08-30 | 251:16 | 49.838
2020-08-30 | 252:16 | 49.847
2020-08-30 | 253:16 | 49.854
2020-08-30 | 254:16 | 49.862
2020-08-30 | 255:16 | 49.868
2020-08-30 | 256:16 | 49.875
2020-08-30 | 257:16 | 49.882
2020-08-30 | 258:16 | 49.89
2020-08-30 | 259:16 | 49.896
2020-08-30 | 260:16 | 49.902
2020-08-30 | 261:16 | 49.905
2020-08-30 | 262:16 | 49.912
2020-08-30 | 263:16 | 49.918
2020-08-30 | 264:16 | 49.922
2020-08-30 | 265:16 | 49.924
2020-08-30 | 266:16 | 49.923
2020-08-30 | 267:16 | 49.92
2020-08-30 | 268:16 | 49.918
2020-08-30 | 269:16 | 49.919
2020-08-30 | 270:16 | 49.918
2020-08-30 | 271:16 | 49.917
2020-08-30 | 272:16 | 49.916
2020-08-30 | 273:16 | 49.916
2020-08-30 | 274:16 | 49.917
2020-08-30 | 275:16 | 49.918
2020-08-30 | 276:16 | 49.92
2020-08-30 | 277:16 | 49.923
2020-08-30 | 278:16 | 49.923
2020-08-30 | 279:16 | 49.926
2020-08-30 | 280:16 | 49.928
2020-08-30 | 281:16 | 49.933
2020-08-30 | 282:16 | 49.94
2020-08-30 | 283:16 | 49.947
2020-08-30 | 284:16 | 49.953
2020-08-30 | 285:16 | 49.958
2020-08-30 | 286:16 | 49.963
2020-08-30 | 287:16 | 49.967
2020-08-30 | 288:16 | 49.969
2020-08-30 | 289:16 | 49.97
2020-08-30 | 290:16 | 49.971
2020-08-30 | 291:16 | 49.971
2020-08-30 | 292:16 | 49.972
2020-08-30 | 293:16 | 49.973
2020-08-30 | 294:16 | 49.972
2020-08-30 | 295:16 | 49.971
2020-08-30 | 296:16 | 49.968
2020-08-30 | 297:16 | 49.968
2020-08-30 | 298:16 | 49.969
2020-08-30 | 299:16 | 49.969
2020-08-30 | 300:16 | 49.968
2020-08-30 | 301:16 | 49.967
2020-08-30 | 302:16 | 49.965
2020-08-30 | 303:16 | 49.961
2020-08-30 | 304:16 | 49.96
2020-08-30 | 305:16 | 49.958
2020-08-30 | 306:16 | 49.956
2020-08-30 | 307:16 | 49.953
2020-08-30 | 308:16 | 49.952
2020-08-30 | 309:16 | 49.952
2020-08-30 | 310:16 | 49.953
2020-08-30 | 311:16 | 49.954
2020-08-30 | 312:16 | 49.956
2020-08-30 | 313:16 | 49.961
2020-08-30 | 314:16 | 49.965
2020-08-30 | 315:16 | 49.968
2020-08-30 | 316:16 | 49.97
2020-08-30 | 317:16 | 49.969
2020-08-30 | 318:16 | 49.967
2020-08-30 | 319:16 | 49.965
2020-08-30 | 320:16 | 49.961
2020-08-30 | 321:16 | 49.958
2020-08-30 | 322:16 | 49.956
2020-08-30 | 323:16 | 49.955
2020-08-30 | 324:16 | 49.953
2020-08-30 | 325:16 | 49.955
2020-08-30 | 326:16 | 49.953
2020-08-30 | 327:16 | 49.952
2020-08-30 | 328:16 | 49.951
2020-08-30 | 329:16 | 49.948
2020-08-30 | 330:16 | 49.946
2020-08-30 | 331:16 | 49.945
2020-08-30 | 332:16 | 49.945
2020-08-30 | 333:16 | 49.945
2020-08-30 | 334:16 | 49.946
2020-08-30 | 335:16 | 49.945
2020-08-30 | 336:16 | 49.943
2020-08-30 | 337:16 | 49.94
2020-08-30 | 338:16 | 49.939
2020-08-30 | 339:16 | 49.939
2020-08-30 | 340:16 | 49.937
2020-08-30 | 341:16 | 49.939
2020-08-30 | 342:16 | 49.939
2020-08-30 | 343:16 | 49.941
2020-08-30 | 344:16 | 49.94
2020-08-30 | 345:16 | 49.941
2020-08-30 | 346:16 | 49.942
2020-08-30 | 347:16 | 49.944
2020-08-30 | 348:16 | 49.947
2020-08-30 | 349:16 | 49.949
2020-08-30 | 350:16 | 49.949
2020-08-30 | 351:16 | 49.949
2020-08-30 | 352:16 | 49.946
2020-08-30 | 353:16 | 49.943
2020-08-30 | 354:16 | 49.942
2020-08-30 | 355:16 | 49.944
2020-08-30 | 356:16 | 49.949
2020-08-30 | 357:16 | 49.954
2020-08-30 | 358:16 | 49.96
2020-08-30 | 359:16 | 49.966
2020-08-30 | 360:16 | 49.972
2020-08-30 | 361:16 | 49.974
2020-08-30 | 362:16 | 49.977
2020-08-30 | 363:16 | 49.978
2020-08-30 | 364:16 | 49.978
2020-08-30 | 365:16 | 49.978
2020-08-30 | 366:16 | 49.979
2020-08-30 | 367:16 | 49.979
2020-08-30 | 368:16 | 49.979
2020-08-30 | 369:16 | 49.978
2020-08-30 | 370:16 | 49.977
2020-08-30 | 371:16 | 49.978
2020-08-30 | 372:16 | 49.979
2020-08-30 | 373:16 | 49.979
2020-08-30 | 374:16 | 49.981
2020-08-30 | 375:16 | 49.984
2020-08-30 | 376:16 | 49.986
2020-08-30 | 377:16 | 49.985
2020-08-30 | 378:16 | 49.984
2020-08-30 | 379:16 | 49.985
2020-08-30 | 380:16 | 49.985
2020-08-30 | 381:16 | 49.986
2020-08-30 | 382:16 | 49.985
2020-08-30 | 383:16 | 49.984
2020-08-30 | 384:16 | 49.983
2020-08-30 | 385:16 | 49.982
2020-08-30 | 386:16 | 49.983
2020-08-30 | 387:16 | 49.984
2020-08-30 | 388:16 | 49.987
2020-08-30 | 389:16 | 49.99
2020-08-30 | 390:16 | 49.991
2020-08-30 | 391:16 | 49.994
2020-08-30 | 392:16 | 49.996
2020-08-30 | 393:16 | 49.998
2020-08-30 | 394:16 | 49.998
2020-08-30 | 395:16 | 49.999
2020-08-30 | 396:16 | 50
2020-08-30 | 397:16 | 50.001
2020-08-30 | 398:16 | 50.003
2020-08-30 | 399:16 | 50.002
2020-08-30 | 400:16 | 50.001
2020-08-30 | 401:16 | 50.002
2020-08-30 | 402:16 | 50.001
2020-08-30 | 403:16 | 50
2020-08-30 | 404:16 | 50.002
2020-08-30 | 405:16 | 50.003
2020-08-30 | 406:16 | 50.005
2020-08-30 | 407:16 | 50.006
2020-08-30 | 408:16 | 50.006
2020-08-30 | 409:16 | 50.005
2020-08-30 | 410:16 | 50.005
2020-08-30 | 411:16 | 50.002
2020-08-30 | 412:16 | 50
2020-08-30 | 413:16 | 49.995
2020-08-30 | 414:16 | 49.989
2020-08-30 | 415:16 | 49.984
2020-08-30 | 416:16 | 49.981
2020-08-30 | 417:16 | 49.98
2020-08-30 | 418:16 | 49.978
2020-08-30 | 419:16 | 49.98
2020-08-30 | 420:16 | 49.982
2020-08-30 | 421:16 | 49.982
2020-08-30 | 422:16 | 49.982
2020-08-30 | 423:16 | 49.981
2020-08-30 | 424:16 | 49.98
2020-08-30 | 425:16 | 49.978
2020-08-30 | 426:16 | 49.975
427:16
428:16
429:16
430:16
431:16
432:16
433:16
434:16
435:16
436:16
437:16
438:16
439:16
440:16
441:16
442:16
443:16
444:16
445:16
446:16
447:16
448:16
449:16
450:16
451:16
452:16
453:16
454:16
455:16
456:16
457:16
458:16
459:16
460:16
461:16
462:16
463:16
464:16
465:16
466:16
467:16
468:16
469:16
470:16
471:16
472:16
473:16
474:16
475:16
476:16
477:16
478:16
479:16
480:16
481:16
482:16
483:16
484:16
485:16
486:16
487:16
488:16
489:16
490:16
491:16
492:16
493:16
494:16
495:16
496:16
497:16
498:16
499:16
500:16
501:16
502:16
503:16
504:16
505:16
506:16
507:16
508:16
509:16
510:16
511:16
512:16
513:16
514:16
515:16
516:16
517:16
518:16
519:16
520:16
521:16
522:16
523:16
524:16
525:16
526:16
527:16
528:16
529:16
530:16
531:16
532:16
533:16
534:16
535:16
536:16
537:16
538:16
539:16
540:16
541:16
542:16
543:16
544:16
545:16
546:16
547:16
548:16
549:16
550:16
551:16
552:16
553:16
554:16
555:16
556:16
557:16
558:16
559:16
560:16
561:16
562:16
563:16
564:16
565:16
566:16
567:16
568:16
569:16
570:16
571:16
572:16
573:16
574:16
575:16
576:16
577:16
578:16
579:16
580:16
581:16
582:16
583:16
584:16
585:16
586:16
587:16
588:16
589:16
590:16
591:16
592:16
593:16
594:16
595:16
596:16
597:16
598:16
599:16
600:16
601:16
602:16
603:16
604:16
605:16
606:16
607:16
608:16
609:16
610:16
611:16
612:16
613:16
614:16
615:16
616:16
617:16
618:16
619:16
620:16
621:16
622:16
623:16
624:16
625:16
626:16
627:16
628:16
629:16
630:16
631:16
632:16
633:16
634:16
635:16
636:16
637:16
638:16
639:16
640:16
641:16
642:16
643:16
644:16
645:16
646:16
647:16
648:16
649:16
650:16
651:16
652:16
653:16
654:16
655:16
656:16
657:16
658:16
659:16
660:16
661:16
662:16
663:16
664:16
665:16
666:16
667:16
668:16
669:16
670:16
671:16
672:16
673:16
674:16
675:16
676:16
677:16
678:16
679:16
680:16
681:16
682:16
683:16
684:16
685:16
686:16
687:16
688:16
689:16
690:16
691:16
692:16
693:16
694:16
695:16
696:16
697:16
698:16
699:16
700:16
701:16
702:16
703:16
704:16
705:16
706:16
707:16
708:16
709:16
710:16
711:16
712:16
713:16
714:16
715:16
716:16
717:16
718:16
719:16
720:16
721:16
722:16
723:16
724:16
725:16
726:16
727:16
728:16
729:16
730:16
731:16
732:16
733:16
734:16
735:16
736:16
737:16
738:16
739:16
740:16
741:16
742:16
743:16
744:16
745:16
746:16
747:16
748:16
749:16
750:16
751:16
752:16
753:16
754:16
755:16
756:16
757:16
758:16
759:16
760:16
761:16
762:16
763:16
764:16
765:16
766:16
767:16
768:16
769:16
770:16
771:16
772:16
773:16
774:16
775:16
776:16
777:16
778:16
779:16
780:16
781:16
782:16
783:16
784:16
785:16
786:16
787:16
788:16
789:16
790:16
791:16
792:16
793:16
794:16
795:16
796:16
797:16
798:16
799:16
800:16
801:16
802:16
803:16
804:16
805:16
806:16
807:16
808:16
809:16
810:16
811:16
812:16
813:16
814:16
815:16
816:16
817:16
818:16
819:16
820:16
821:16
822:16
823:16
824:16
825:16
826:16
827:16
828:16
829:16
830:16
831:16
832:16
833:16
834:16
835:16
836:16
837:16
838:16
839:16
840:16
841:16
842:16
843:16
844:16
845:16
846:16
847:16
848:16
849:16
850:16
851:16
852:16
853:16
854:16
855:16
856:16
857:16
858:16
859:16
860:16
861:16
862:16
863:16
864:16
865:16
866:16
867:16
868:16
869:16
870:16
871:16
872:16
873:16
874:16
875:16
876:16
877:16
878:16
879:16
880:16
881:16
882:16
883:16
884:16
885:16
886:16
887:16
888:16
889:16
890:16
891:16
892:16
893:16
894:16
895:16
896:16
897:16
898:16
899:16
900:16
901:16
902:16
903:16
904:16
905:16
906:16

## Event 20200831-1
In UTC
Date | Time | Freq
2020-08-31 | 17:49 | 50.145
2020-08-31 | 17:49 | 50.146
2020-08-31 | 17:49 | 50.149
2020-08-31 | 17:49 | 50.151
2020-08-31 | 17:49 | 50.15
2020-08-31 | 18:49 | 50.151
2020-08-31 | 19:49 | 50.15
2020-08-31 | 20:49 | 50.148
2020-08-31 | 21:49 | 50.147
2020-08-31 | 22:49 | 50.145
2020-08-31 | 23:49 | 50.144
2020-08-31 | 24:49 | 50.146
2020-08-31 | 25:49 | 50.147
2020-08-31 | 26:49 | 50.147
2020-08-31 | 27:49 | 50.147
2020-08-31 | 28:49 | 50.148
2020-08-31 | 29:49 | 50.146
2020-08-31 | 30:49 | 50.146
2020-08-31 | 31:49 | 50.146
2020-08-31 | 32:49 | 50.146
2020-08-31 | 33:49 | 50.146
2020-08-31 | 34:49 | 50.144
2020-08-31 | 35:49 | 50.143
2020-08-31 | 36:49 | 50.144
2020-08-31 | 37:49 | 50.145
2020-08-31 | 38:49 | 50.146
2020-08-31 | 39:49 | 50.146
2020-08-31 | 40:49 | 50.147
2020-08-31 | 41:49 | 50.146
2020-08-31 | 42:49 | 50.146
2020-08-31 | 43:49 | 50.145
2020-08-31 | 44:49 | 50.145
2020-08-31 | 45:49 | 50.144
2020-08-31 | 46:49 | 50.144
2020-08-31 | 47:49 | 50.146
2020-08-31 | 48:49 | 50.146
2020-08-31 | 49:49 | 50.143
2020-08-31 | 50:49 | 50.141
2020-08-31 | 51:49 | 50.137
2020-08-31 | 52:49 | 50.138
2020-08-31 | 53:49 | 50.136
2020-08-31 | 54:49 | 50.134
2020-08-31 | 55:49 | 50.134
2020-08-31 | 56:49 | 50.13
2020-08-31 | 57:49 | 50.126
2020-08-31 | 58:49 | 50.118
2020-08-31 | 59:49 | 50.112
2020-08-31 | 60:49 | 50.105
2020-08-31 | 61:49 | 50.101
2020-08-31 | 62:49 | 50.099
2020-08-31 | 63:49 | 50.094
2020-08-31 | 64:49 | 50.09
2020-08-31 | 65:49 | 50.084
2020-08-31 | 66:49 | 50.079
2020-08-31 | 67:49 | 50.074
2020-08-31 | 68:49 | 50.07
2020-08-31 | 69:49 | 50.069
2020-08-31 | 70:49 | 50.068
2020-08-31 | 71:49 | 50.068
2020-08-31 | 72:49 | 50.065
2020-08-31 | 73:49 | 50.065
2020-08-31 | 74:49 | 50.062
2020-08-31 | 75:49 | 50.062
2020-08-31 | 76:49 | 50.06
2020-08-31 | 77:49 | 50.057
2020-08-31 | 78:49 | 50.055
2020-08-31 | 79:49 | 50.053
2020-08-31 | 80:49 | 50.052
2020-08-31 | 81:49 | 50.05
2020-08-31 | 82:49 | 50.048
2020-08-31 | 83:49 | 50.047
2020-08-31 | 84:49 | 50.046
2020-08-31 | 85:49 | 50.044
2020-08-31 | 86:49 | 50.043
2020-08-31 | 87:49 | 50.04
2020-08-31 | 88:49 | 50.039
2020-08-31 | 89:49 | 50.04
2020-08-31 | 90:49 | 50.041
2020-08-31 | 91:49 | 50.041
2020-08-31 | 92:49 | 50.042
2020-08-31 | 93:49 | 50.045
2020-08-31 | 94:49 | 50.045
2020-08-31 | 95:49 | 50.045
2020-08-31 | 96:49 | 50.045
2020-08-31 | 97:49 | 50.042
2020-08-31 | 98:49 | 50.041
2020-08-31 | 99:49 | 50.038
2020-08-31 | 100:49 | 50.035
2020-08-31 | 101:49 | 50.03
2020-08-31 | 102:49 | 50.026
2020-08-31 | 103:49 | 50.023
2020-08-31 | 104:49 | 50.02
2020-08-31 | 105:49 | 50.017
2020-08-31 | 106:49 | 50.015
2020-08-31 | 107:49 | 50.013
2020-08-31 | 108:49 | 50.013
2020-08-31 | 109:49 | 50.014
2020-08-31 | 110:49 | 50.015
2020-08-31 | 111:49 | 50.014
2020-08-31 | 112:49 | 50.016
2020-08-31 | 113:49 | 50.017
2020-08-31 | 114:49 | 50.021
2020-08-31 | 115:49 | 50.024
2020-08-31 | 116:49 | 50.029
2020-08-31 | 117:49 | 50.033
2020-08-31 | 118:49 | 50.039
2020-08-31 | 119:49 | 50.039
2020-08-31 | 120:49 | 50.041
2020-08-31 | 121:49 | 50.043
2020-08-31 | 122:49 | 50.044
2020-08-31 | 123:49 | 50.048
2020-08-31 | 124:49 | 50.05
2020-08-31 | 125:49 | 50.053
2020-08-31 | 126:49 | 50.057
2020-08-31 | 127:49 | 50.059
2020-08-31 | 128:49 | 50.063
2020-08-31 | 129:49 | 50.063
2020-08-31 | 130:49 | 50.065
2020-08-31 | 131:49 | 50.063
2020-08-31 | 132:49 | 50.063
2020-08-31 | 133:49 | 50.063
2020-08-31 | 134:49 | 50.059
2020-08-31 | 135:49 | 50.055
2020-08-31 | 136:49 | 50.051
2020-08-31 | 137:49 | 50.047
2020-08-31 | 138:49 | 50.046
2020-08-31 | 139:49 | 50.042
2020-08-31 | 140:49 | 50.04
2020-08-31 | 141:49 | 50.04
2020-08-31 | 142:49 | 50.039
2020-08-31 | 143:49 | 50.039
2020-08-31 | 144:49 | 50.041
2020-08-31 | 145:49 | 50.042
2020-08-31 | 146:49 | 50.043
2020-08-31 | 147:49 | 50.034
2020-08-31 | 148:49 | 50.027
2020-08-31 | 149:49 | 50.021
2020-08-31 | 150:49 | 50.015
2020-08-31 | 151:49 | 50.013
2020-08-31 | 152:49 | 50.011
2020-08-31 | 153:49 | 50.01
2020-08-31 | 154:49 | 50.008
2020-08-31 | 155:49 | 50.008
2020-08-31 | 156:49 | 50.008
2020-08-31 | 157:49 | 50.008
2020-08-31 | 158:49 | 50.009
2020-08-31 | 159:49 | 50.009
2020-08-31 | 160:49 | 50.013
2020-08-31 | 161:49 | 50.015
2020-08-31 | 162:49 | 50.016
2020-08-31 | 163:49 | 50.018
2020-08-31 | 164:49 | 50.02
2020-08-31 | 165:49 | 50.02
2020-08-31 | 166:49 | 50.022
2020-08-31 | 167:49 | 50.022
2020-08-31 | 168:49 | 50.022
2020-08-31 | 169:49 | 50.023
2020-08-31 | 170:49 | 50.023
2020-08-31 | 171:49 | 50.023
2020-08-31 | 172:49 | 50.025
2020-08-31 | 173:49 | 50.022
2020-08-31 | 174:49 | 50.021
2020-08-31 | 175:49 | 50.018
2020-08-31 | 176:49 | 50.018
2020-08-31 | 177:49 | 50.019
2020-08-31 | 178:49 | 50.021
2020-08-31 | 179:49 | 50.024
2020-08-31 | 180:49 | 50.026
2020-08-31 | 181:49 | 50.029
2020-08-31 | 182:49 | 50.03
2020-08-31 | 183:49 | 50.032
2020-08-31 | 184:49 | 50.031
2020-08-31 | 185:49 | 50.03
2020-08-31 | 186:49 | 50.027
2020-08-31 | 187:49 | 50.027
2020-08-31 | 188:49 | 50.023
2020-08-31 | 189:49 | 50.022
2020-08-31 | 190:49 | 50.022
2020-08-31 | 191:49 | 50.02
2020-08-31 | 192:49 | 50.019
2020-08-31 | 193:49 | 50.019
2020-08-31 | 194:49 | 50.018
2020-08-31 | 195:49 | 50.017
2020-08-31 | 196:49 | 50.017
2020-08-31 | 197:49 | 50.016
2020-08-31 | 198:49 | 50.014
2020-08-31 | 199:49 | 50.009
2020-08-31 | 200:49 | 50.006
2020-08-31 | 201:49 | 50.002
2020-08-31 | 202:49 | 49.999
2020-08-31 | 203:49 | 49.994
2020-08-31 | 204:49 | 49.992
2020-08-31 | 205:49 | 49.991
2020-08-31 | 206:49 | 49.99
2020-08-31 | 207:49 | 49.987
2020-08-31 | 208:49 | 49.986
2020-08-31 | 209:49 | 49.985
2020-08-31 | 210:49 | 49.983
2020-08-31 | 211:49 | 49.98
2020-08-31 | 212:49 | 49.976
2020-08-31 | 213:49 | 49.973
2020-08-31 | 214:49 | 49.971
2020-08-31 | 215:49 | 49.97
2020-08-31 | 216:49 | 49.972
2020-08-31 | 217:49 | 49.974
2020-08-31 | 218:49 | 49.973
2020-08-31 | 219:49 | 49.973
2020-08-31 | 220:49 | 49.972
2020-08-31 | 221:49 | 49.973
2020-08-31 | 222:49 | 49.974
2020-08-31 | 223:49 | 49.975
2020-08-31 | 224:49 | 49.974
2020-08-31 | 225:49 | 49.975
2020-08-31 | 226:49 | 49.972
2020-08-31 | 227:49 | 49.973
2020-08-31 | 228:49 | 49.972
2020-08-31 | 229:49 | 49.972
2020-08-31 | 230:49 | 49.971
2020-08-31 | 231:49 | 49.972
2020-08-31 | 232:49 | 49.972
2020-08-31 | 233:49 | 49.975
2020-08-31 | 234:49 | 49.977
2020-08-31 | 235:49 | 49.978
2020-08-31 | 236:49 | 49.978
2020-08-31 | 237:49 | 49.98
2020-08-31 | 238:49 | 49.982
2020-08-31 | 239:49 | 49.985
2020-08-31 | 240:49 | 49.989
2020-08-31 | 241:49 | 49.994
2020-08-31 | 242:49 | 50
2020-08-31 | 243:49 | 50.005
2020-08-31 | 244:49 | 50.01
2020-08-31 | 245:49 | 50.013
2020-08-31 | 246:49 | 50.017
2020-08-31 | 247:49 | 50.022
2020-08-31 | 248:49 | 50.024
2020-08-31 | 249:49 | 50.026
2020-08-31 | 250:49 | 50.026
2020-08-31 | 251:49 | 50.026
2020-08-31 | 252:49 | 50.025
2020-08-31 | 253:49 | 50.024
2020-08-31 | 254:49 | 50.022
2020-08-31 | 255:49 | 50.022
2020-08-31 | 256:49 | 50.021
2020-08-31 | 257:49 | 50.021
2020-08-31 | 258:49 | 50.021
2020-08-31 | 259:49 | 50.022
2020-08-31 | 260:49 | 50.022
2020-08-31 | 261:49 | 50.022
2020-08-31 | 262:49 | 50.02
2020-08-31 | 263:49 | 50.02
2020-08-31 | 264:49 | 50.02
2020-08-31 | 265:49 | 50.019
2020-08-31 | 266:49 | 50.019
2020-08-31 | 267:49 | 50.019
2020-08-31 | 268:49 | 50.02
2020-08-31 | 269:49 | 50.021
2020-08-31 | 270:49 | 50.023
2020-08-31 | 271:49 | 50.025
2020-08-31 | 272:49 | 50.028
2020-08-31 | 273:49 | 50.033
2020-08-31 | 274:49 | 50.035
2020-08-31 | 275:49 | 50.037
2020-08-31 | 276:49 | 50.039
2020-08-31 | 277:49 | 50.042
2020-08-31 | 278:49 | 50.042
2020-08-31 | 279:49 | 50.043
2020-08-31 | 280:49 | 50.042
2020-08-31 | 281:49 | 50.04
2020-08-31 | 282:49 | 50.037
2020-08-31 | 283:49 | 50.035
2020-08-31 | 284:49 | 50.033
2020-08-31 | 285:49 | 50.032
2020-08-31 | 286:49 | 50.03
2020-08-31 | 287:49 | 50.029
2020-08-31 | 288:49 | 50.027
2020-08-31 | 289:49 | 50.026
2020-08-31 | 290:49 | 50.024
2020-08-31 | 291:49 | 50.023
2020-08-31 | 292:49 | 50.021
2020-08-31 | 293:49 | 50.02
2020-08-31 | 294:49 | 50.019
2020-08-31 | 295:49 | 50.017
2020-08-31 | 296:49 | 50.016
2020-08-31 | 297:49 | 50.015
2020-08-31 | 298:49 | 50.014
2020-08-31 | 299:49 | 50.014
2020-08-31 | 300:49 | 50.016
2020-08-31 | 301:49 | 50.015
2020-08-31 | 302:49 | 50.017
2020-08-31 | 303:49 | 50.017
2020-08-31 | 304:49 | 50.018
2020-08-31 | 305:49 | 50.018
2020-08-31 | 306:49 | 50.017
2020-08-31 | 307:49 | 50.015
2020-08-31 | 308:49 | 50.014
2020-08-31 | 309:49 | 50.014
2020-08-31 | 310:49 | 50.016
2020-08-31 | 311:49 | 50.015
2020-08-31 | 312:49 | 50.016
2020-08-31 | 313:49 | 50.015
2020-08-31 | 314:49 | 50.017
2020-08-31 | 315:49 | 50.016
2020-08-31 | 316:49 | 50.015
2020-08-31 | 317:49 | 50.011
2020-08-31 | 318:49 | 50.008
2020-08-31 | 319:49 | 50.006
2020-08-31 | 320:49 | 50.006
2020-08-31 | 321:49 | 50.003
2020-08-31 | 322:49 | 50.001
2020-08-31 | 323:49 | 49.999
2020-08-31 | 324:49 | 49.996
2020-08-31 | 325:49 | 49.994
2020-08-31 | 326:49 | 49.992
2020-08-31 | 327:49 | 49.992
2020-08-31 | 328:49 | 49.991
2020-08-31 | 329:49 | 49.991
2020-08-31 | 330:49 | 49.992
2020-08-31 | 331:49 | 49.993
2020-08-31 | 332:49 | 49.997
2020-08-31 | 333:49 | 50
2020-08-31 | 334:49 | 50.005
2020-08-31 | 335:49 | 50.009
2020-08-31 | 336:49 | 50.013
2020-08-31 | 337:49 | 50.016
2020-08-31 | 338:49 | 50.015
2020-08-31 | 339:49 | 50.014
2020-08-31 | 340:49 | 50.015
2020-08-31 | 341:49 | 50.015
2020-08-31 | 342:49 | 50.015
2020-08-31 | 343:49 | 50.016
2020-08-31 | 344:49 | 50.018
2020-08-31 | 345:49 | 50.02
2020-08-31 | 346:49 | 50.021
2020-08-31 | 347:49 | 50.023
2020-08-31 | 348:49 | 50.024
2020-08-31 | 349:49 | 50.024
2020-08-31 | 350:49 | 50.025
2020-08-31 | 351:49 | 50.025
2020-08-31 | 352:49 | 50.027
2020-08-31 | 353:49 | 50.03
2020-08-31 | 354:49 | 50.031
2020-08-31 | 355:49 | 50.035
2020-08-31 | 356:49 | 50.037
2020-08-31 | 357:49 | 50.038
2020-08-31 | 358:49 | 50.041
2020-08-31 | 359:49 | 50.042
2020-08-31 | 360:49 | 50.043
2020-08-31 | 361:49 | 50.044
2020-08-31 | 362:49 | 50.047
2020-08-31 | 363:49 | 50.047
2020-08-31 | 364:49 | 50.049
2020-08-31 | 365:49 | 50.049
2020-08-31 | 366:49 | 50.048
2020-08-31 | 367:49 | 50.046
2020-08-31 | 368:49 | 50.046
2020-08-31 | 369:49 | 50.044
2020-08-31 | 370:49 | 50.042
2020-08-31 | 371:49 | 50.04
2020-08-31 | 372:49 | 50.039
2020-08-31 | 373:49 | 50.038
2020-08-31 | 374:49 | 50.037
2020-08-31 | 375:49 | 50.035
2020-08-31 | 376:49 | 50.034
2020-08-31 | 377:49 | 50.034
2020-08-31 | 378:49 | 50.033
2020-08-31 | 379:49 | 50.033
2020-08-31 | 380:49 | 50.035
2020-08-31 | 381:49 | 50.036
2020-08-31 | 382:49 | 50.035
2020-08-31 | 383:49 | 50.035
2020-08-31 | 384:49 | 50.035
2020-08-31 | 385:49 | 50.034
2020-08-31 | 386:49 | 50.035
2020-08-31 | 387:49 | 50.035
2020-08-31 | 388:49 | 50.033
2020-08-31 | 389:49 | 50.033
2020-08-31 | 390:49 | 50.035
2020-08-31 | 391:49 | 50.035
2020-08-31 | 392:49 | 50.039
2020-08-31 | 393:49 | 50.041
2020-08-31 | 394:49 | 50.041
2020-08-31 | 395:49 | 50.041
2020-08-31 | 396:49 | 50.041
2020-08-31 | 397:49 | 50.04
2020-08-31 | 398:49 | 50.038
2020-08-31 | 399:49 | 50.039
2020-08-31 | 400:49 | 50.039
2020-08-31 | 401:49 | 50.039
2020-08-31 | 402:49 | 50.037
2020-08-31 | 403:49 | 50.036
2020-08-31 | 404:49 | 50.034
2020-08-31 | 405:49 | 50.029
2020-08-31 | 406:49 | 50.025
2020-08-31 | 407:49 | 50.021
2020-08-31 | 408:49 | 50.021
2020-08-31 | 409:49 | 50.02
2020-08-31 | 410:49 | 50.02
2020-08-31 | 411:49 | 50.018
2020-08-31 | 412:49 | 50.017
2020-08-31 | 413:49 | 50.014
2020-08-31 | 414:49 | 50.014
2020-08-31 | 415:49 | 50.012
2020-08-31 | 416:49 | 50.012
2020-08-31 | 417:49 | 50.011
2020-08-31 | 418:49 | 50.011
2020-08-31 | 419:49 | 50.011
2020-08-31 | 420:49 | 50.013
2020-08-31 | 421:49 | 50.012
2020-08-31 | 422:49 | 50.013
2020-08-31 | 423:49 | 50.013
2020-08-31 | 424:49 | 50.01
2020-08-31 | 425:49 | 50.008
2020-08-31 | 426:49 | 50.005
2020-08-31 | 427:49 | 50
2020-08-31 | 428:49 | 49.996
2020-08-31 | 429:49 | 49.991
2020-08-31 | 430:49 | 49.988
2020-08-31 | 431:49 | 49.987
2020-08-31 | 432:49 | 49.986
2020-08-31 | 433:49 | 49.985
2020-08-31 | 434:49 | 49.985
2020-08-31 | 435:49 | 49.986
2020-08-31 | 436:49 | 49.987
2020-08-31 | 437:49 | 49.989
2020-08-31 | 438:49 | 49.992
2020-08-31 | 439:49 | 49.993
2020-08-31 | 440:49 | 49.996
2020-08-31 | 441:49 | 49.997
2020-08-31 | 442:49 | 50
2020-08-31 | 443:49 | 50.002
2020-08-31 | 444:49 | 50.006
2020-08-31 | 445:49 | 50.011
2020-08-31 | 446:49 | 50.013
2020-08-31 | 447:49 | 50.017
2020-08-31 | 448:49 | 50.019
2020-08-31 | 449:49 | 50.018
2020-08-31 | 450:49 | 50.019
2020-08-31 | 451:49 | 50.019
2020-08-31 | 452:49 | 50.018
2020-08-31 | 453:49 | 50.019
2020-08-31 | 454:49 | 50.02
2020-08-31 | 455:49 | 50.019
2020-08-31 | 456:49 | 50.019
2020-08-31 | 457:49 | 50.02
2020-08-31 | 458:49 | 50.021
2020-08-31 | 459:49 | 50.022
2020-08-31 | 460:49 | 50.023
2020-08-31 | 461:49 | 50.021
2020-08-31 | 462:49 | 50.02
2020-08-31 | 463:49 | 50.02
2020-08-31 | 464:49 | 50.019
2020-08-31 | 465:49 | 50.02
2020-08-31 | 466:49 | 50.021
2020-08-31 | 467:49 | 50.021
2020-08-31 | 468:49 | 50.023
2020-08-31 | 469:49 | 50.022
2020-08-31 | 470:49 | 50.024
2020-08-31 | 471:49 | 50.024
2020-08-31 | 472:49 | 50.025
2020-08-31 | 473:49 | 50.028
2020-08-31 | 474:49 | 50.029
2020-08-31 | 475:49 | 50.029
2020-08-31 | 476:49 | 50.03
2020-08-31 | 477:49 | 50.028
2020-08-31 | 478:49 | 50.03
2020-08-31 | 479:49 | 50.031
2020-08-31 | 480:49 | 50.033
2020-08-31 | 481:49 | 50.034
2020-08-31 | 482:49 | 50.035
2020-08-31 | 483:49 | 50.035
2020-08-31 | 484:49 | 50.034
2020-08-31 | 485:49 | 50.031
2020-08-31 | 486:49 | 50.029
2020-08-31 | 487:49 | 50.027
2020-08-31 | 488:49 | 50.025
2020-08-31 | 489:49 | 50.023
2020-08-31 | 490:49 | 50.021
2020-08-31 | 491:49 | 50.019
2020-08-31 | 492:49 | 50.018
2020-08-31 | 493:49 | 50.016
2020-08-31 | 494:49 | 50.013
2020-08-31 | 495:49 | 50.011
2020-08-31 | 496:49 | 50.009
2020-08-31 | 497:49 | 50.006
2020-08-31 | 498:49 | 50.003
2020-08-31 | 499:49 | 49.997
2020-08-31 | 500:49 | 49.995
2020-08-31 | 501:49 | 49.991
2020-08-31 | 502:49 | 49.988
2020-08-31 | 503:49 | 49.984
2020-08-31 | 504:49 | 49.981
2020-08-31 | 505:49 | 49.978
2020-08-31 | 506:49 | 49.976
2020-08-31 | 507:49 | 49.973
2020-08-31 | 508:49 | 49.97
2020-08-31 | 509:49 | 49.968
2020-08-31 | 510:49 | 49.965
2020-08-31 | 511:49 | 49.965
2020-08-31 | 512:49 | 49.964
2020-08-31 | 513:49 | 49.962
2020-08-31 | 514:49 | 49.961
2020-08-31 | 515:49 | 49.96
2020-08-31 | 516:49 | 49.959
2020-08-31 | 517:49 | 49.96
2020-08-31 | 518:49 | 49.959
2020-08-31 | 519:49 | 49.955
2020-08-31 | 520:49 | 49.953
2020-08-31 | 521:49 | 49.951
2020-08-31 | 522:49 | 49.948
2020-08-31 | 523:49 | 49.947
2020-08-31 | 524:49 | 49.948
2020-08-31 | 525:49 | 49.948
2020-08-31 | 526:49 | 49.949
2020-08-31 | 527:49 | 49.949
2020-08-31 | 528:49 | 49.95
2020-08-31 | 529:49 | 49.951
2020-08-31 | 530:49 | 49.953
2020-08-31 | 531:49 | 49.954
2020-08-31 | 532:49 | 49.954
2020-08-31 | 533:49 | 49.953
2020-08-31 | 534:49 | 49.953
2020-08-31 | 535:49 | 49.955
2020-08-31 | 536:49 | 49.955
2020-08-31 | 537:49 | 49.958
2020-08-31 | 538:49 | 49.956
2020-08-31 | 539:49 | 49.958
2020-08-31 | 540:49 | 49.957
2020-08-31 | 541:49 | 49.956
2020-08-31 | 542:49 | 49.955
2020-08-31 | 543:49 | 49.954
2020-08-31 | 544:49 | 49.951
2020-08-31 | 545:49 | 49.949
2020-08-31 | 546:49 | 49.947
2020-08-31 | 547:49 | 49.944
2020-08-31 | 548:49 | 49.94
2020-08-31 | 549:49 | 49.936
2020-08-31 | 550:49 | 49.932
2020-08-31 | 551:49 | 49.929
2020-08-31 | 552:49 | 49.926
2020-08-31 | 553:49 | 49.924
2020-08-31 | 554:49 | 49.921
2020-08-31 | 555:49 | 49.917
2020-08-31 | 556:49 | 49.915
2020-08-31 | 557:49 | 49.913
2020-08-31 | 558:49 | 49.912
2020-08-31 | 559:49 | 49.911
2020-08-31 | 560:49 | 49.911
2020-08-31 | 561:49 | 49.91
2020-08-31 | 562:49 | 49.912
2020-08-31 | 563:49 | 49.912
2020-08-31 | 564:49 | 49.914
2020-08-31 | 565:49 | 49.913
2020-08-31 | 566:49 | 49.911
2020-08-31 | 567:49 | 49.909
2020-08-31 | 568:49 | 49.91
2020-08-31 | 569:49 | 49.911
2020-08-31 | 570:49 | 49.912
2020-08-31 | 571:49 | 49.914
2020-08-31 | 572:49 | 49.915
2020-08-31 | 573:49 | 49.916
2020-08-31 | 574:49 | 49.916
2020-08-31 | 575:49 | 49.915
2020-08-31 | 576:49 | 49.916
2020-08-31 | 577:49 | 49.919
2020-08-31 | 578:49 | 49.921
2020-08-31 | 579:49 | 49.925
2020-08-31 | 580:49 | 49.928
2020-08-31 | 581:49 | 49.932
2020-08-31 | 582:49 | 49.935
2020-08-31 | 583:49 | 49.937
2020-08-31 | 584:49 | 49.938
2020-08-31 | 585:49 | 49.939
2020-08-31 | 586:49 | 49.939
2020-08-31 | 587:49 | 49.939
2020-08-31 | 588:49 | 49.941
2020-08-31 | 589:49 | 49.94
2020-08-31 | 590:49 | 49.941
2020-08-31 | 591:49 | 49.941
2020-08-31 | 592:49 | 49.944
2020-08-31 | 593:49 | 49.948
2020-08-31 | 594:49 | 49.95
2020-08-31 | 595:49 | 49.951
2020-08-31 | 596:49 | 49.953
2020-08-31 | 597:49 | 49.952
2020-08-31 | 598:49 | 49.952
2020-08-31 | 599:49 | 49.95
2020-08-31 | 600:49 | 49.948
2020-08-31 | 601:49 | 49.944
2020-08-31 | 602:49 | 49.942
2020-08-31 | 603:49 | 49.941
2020-08-31 | 604:49 | 49.941
2020-08-31 | 605:49 | 49.94
2020-08-31 | 606:49 | 49.941
2020-08-31 | 607:49 | 49.943
2020-08-31 | 608:49 | 49.945
2020-08-31 | 609:49 | 49.946
2020-08-31 | 610:49 | 49.946
2020-08-31 | 611:49 | 49.946
2020-08-31 | 612:49 | 49.946
2020-08-31 | 613:49 | 49.944
2020-08-31 | 614:49 | 49.941
2020-08-31 | 615:49 | 49.938
2020-08-31 | 616:49 | 49.937
2020-08-31 | 617:49 | 49.937
2020-08-31 | 618:49 | 49.935
2020-08-31 | 619:49 | 49.936
2020-08-31 | 620:49 | 49.933
2020-08-31 | 621:49 | 49.933
2020-08-31 | 622:49 | 49.93
2020-08-31 | 623:49 | 49.922
2020-08-31 | 624:49 | 49.916
2020-08-31 | 625:49 | 49.912
2020-08-31 | 626:49 | 49.91
2020-08-31 | 627:49 | 49.91
2020-08-31 | 628:49 | 49.908
2020-08-31 | 629:49 | 49.908
2020-08-31 | 630:49 | 49.907
2020-08-31 | 631:49 | 49.909
2020-08-31 | 632:49 | 49.911
2020-08-31 | 633:49 | 49.912
2020-08-31 | 634:49 | 49.914
2020-08-31 | 635:49 | 49.918
2020-08-31 | 636:49 | 49.92
2020-08-31 | 637:49 | 49.922
2020-08-31 | 638:49 | 49.923
2020-08-31 | 639:49 | 49.922
2020-08-31 | 640:49 | 49.922
2020-08-31 | 641:49 | 49.922
2020-08-31 | 642:49 | 49.921
2020-08-31 | 643:49 | 49.922
2020-08-31 | 644:49 | 49.921
2020-08-31 | 645:49 | 49.923
2020-08-31 | 646:49 | 49.923
2020-08-31 | 647:49 | 49.925
2020-08-31 | 648:49 | 49.927
2020-08-31 | 649:49 | 49.929
2020-08-31 | 650:49 | 49.932
2020-08-31 | 651:49 | 49.935
2020-08-31 | 652:49 | 49.938
2020-08-31 | 653:49 | 49.942
2020-08-31 | 654:49 | 49.944
2020-08-31 | 655:49 | 49.946
2020-08-31 | 656:49 | 49.948
2020-08-31 | 657:49 | 49.953
2020-08-31 | 658:49 | 49.956
2020-08-31 | 659:49 | 49.96
2020-08-31 | 660:49 | 49.963
2020-08-31 | 661:49 | 49.965
2020-08-31 | 662:49 | 49.968
2020-08-31 | 663:49 | 49.97
2020-08-31 | 664:49 | 49.972
2020-08-31 | 665:49 | 49.972
2020-08-31 | 666:49 | 49.974
2020-08-31 | 667:49 | 49.975
2020-08-31 | 668:49 | 49.977
2020-08-31 | 669:49 | 49.979
2020-08-31 | 670:49 | 49.979
2020-08-31 | 671:49 | 49.979
2020-08-31 | 672:49 | 49.98
2020-08-31 | 673:49 | 49.981
2020-08-31 | 674:49 | 49.981
2020-08-31 | 675:49 | 49.981
2020-08-31 | 676:49 | 49.979
2020-08-31 | 677:49 | 49.981
2020-08-31 | 678:49 | 49.983
2020-08-31 | 679:49 | 49.987
2020-08-31 | 680:49 | 49.991
2020-08-31 | 681:49 | 49.993
2020-08-31 | 682:49 | 49.995
2020-08-31 | 683:49 | 49.996
2020-08-31 | 684:49 | 49.996
2020-08-31 | 685:49 | 49.997
2020-08-31 | 686:49 | 49.995
2020-08-31 | 687:49 | 49.993
2020-08-31 | 688:49 | 49.994
2020-08-31 | 689:49 | 49.996
2020-08-31 | 690:49 | 49.995
2020-08-31 | 691:49 | 49.995
2020-08-31 | 692:49 | 49.995
2020-08-31 | 693:49 | 49.992
2020-08-31 | 694:49 | 49.989
2020-08-31 | 695:49 | 49.984
2020-08-31 | 696:49 | 49.981
2020-08-31 | 697:49 | 49.98
2020-08-31 | 698:49 | 49.978
2020-08-31 | 699:49 | 49.977
2020-08-31 | 700:49 | 49.976
2020-08-31 | 701:49 | 49.975
2020-08-31 | 702:49 | 49.972
2020-08-31 | 703:49 | 49.969
2020-08-31 | 704:49 | 49.97
2020-08-31 | 705:49 | 49.969
2020-08-31 | 706:49 | 49.968
2020-08-31 | 707:49 | 49.967
2020-08-31 | 708:49 | 49.964
2020-08-31 | 709:49 | 49.964
2020-08-31 | 710:49 | 49.963
2020-08-31 | 711:49 | 49.963
2020-08-31 | 712:49 | 49.961
2020-08-31 | 713:49 | 49.961
2020-08-31 | 714:49 | 49.96
2020-08-31 | 715:49 | 49.96
2020-08-31 | 716:49 | 49.959
2020-08-31 | 717:49 | 49.96
2020-08-31 | 718:49 | 49.962
2020-08-31 | 719:49 | 49.967
2020-08-31 | 720:49 | 49.971
2020-08-31 | 721:49 | 49.975
2020-08-31 | 722:49 | 49.979
2020-08-31 | 723:49 | 49.983
2020-08-31 | 724:49 | 49.987
2020-08-31 | 725:49 | 49.991
2020-08-31 | 726:49 | 49.994
2020-08-31 | 727:49 | 49.998
2020-08-31 | 728:49 | 50.002
2020-08-31 | 729:49 | 50.007
2020-08-31 | 730:49 | 50.015
2020-08-31 | 731:49 | 50.022
2020-08-31 | 732:49 | 50.027
2020-08-31 | 733:49 | 50.028
2020-08-31 | 734:49 | 50.028
2020-08-31 | 735:49 | 50.028
2020-08-31 | 736:49 | 50.032
2020-08-31 | 737:49 | 50.034
2020-08-31 | 738:49 | 50.035
2020-08-31 | 739:49 | 50.038
2020-08-31 | 740:49 | 50.039
2020-08-31 | 741:49 | 50.041
2020-08-31 | 742:49 | 50.043
2020-08-31 | 743:49 | 50.043
2020-08-31 | 744:49 | 50.044
2020-08-31 | 745:49 | 50.043
2020-08-31 | 746:49 | 50.045
2020-08-31 | 747:49 | 50.044
2020-08-31 | 748:49 | 50.042
2020-08-31 | 749:49 | 50.041
2020-08-31 | 750:49 | 50.041
2020-08-31 | 751:49 | 50.039
2020-08-31 | 752:49 | 50.039
2020-08-31 | 753:49 | 50.039
2020-08-31 | 754:49 | 50.039
2020-08-31 | 755:49 | 50.043
2020-08-31 | 756:49 | 50.048
2020-08-31 | 757:49 | 50.051
2020-08-31 | 758:49 | 50.052
2020-08-31 | 759:49 | 50.054
2020-08-31 | 760:49 | 50.054
2020-08-31 | 761:49 | 50.054
2020-08-31 | 762:49 | 50.054
2020-08-31 | 763:49 | 50.057
2020-08-31 | 764:49 | 50.057
2020-08-31 | 765:49 | 50.058
2020-08-31 | 766:49 | 50.059
2020-08-31 | 767:49 | 50.059
2020-08-31 | 768:49 | 50.059
2020-08-31 | 769:49 | 50.061
2020-08-31 | 770:49 | 50.065
2020-08-31 | 771:49 | 50.07
2020-08-31 | 772:49 | 50.073
2020-08-31 | 773:49 | 50.075
2020-08-31 | 774:49 | 50.078
2020-08-31 | 775:49 | 50.08
2020-08-31 | 776:49 | 50.082
2020-08-31 | 777:49 | 50.087
2020-08-31 | 778:49 | 50.091
2020-08-31 | 779:49 | 50.097
2020-08-31 | 780:49 | 50.101
2020-08-31 | 781:49 | 50.106
2020-08-31 | 782:49 | 50.106
2020-08-31 | 783:49 | 50.106
2020-08-31 | 784:49 | 50.107
2020-08-31 | 785:49 | 50.108
2020-08-31 | 786:49 | 50.111
2020-08-31 | 787:49 | 50.113
2020-08-31 | 788:49 | 50.113
2020-08-31 | 789:49 | 50.111
2020-08-31 | 790:49 | 50.109
2020-08-31 | 791:49 | 50.107
2020-08-31 | 792:49 | 50.108
2020-08-31 | 793:49 | 50.109
2020-08-31 | 794:49 | 50.107
2020-08-31 | 795:49 | 50.107
2020-08-31 | 796:49 | 50.106
2020-08-31 | 797:49 | 50.106
2020-08-31 | 798:49 | 50.105
2020-08-31 | 799:49 | 50.105
2020-08-31 | 800:49 | 50.106
2020-08-31 | 801:49 | 50.107
2020-08-31 | 802:49 | 50.107
2020-08-31 | 803:49 | 50.106
2020-08-31 | 804:49 | 50.104
2020-08-31 | 805:49 | 50.104
2020-08-31 | 806:49 | 50.104
2020-08-31 | 807:49 | 50.107
2020-08-31 | 808:49 | 50.109
2020-08-31 | 809:49 | 50.113
2020-08-31 | 810:49 | 50.115
2020-08-31 | 811:49 | 50.117
2020-08-31 | 812:49 | 50.118
2020-08-31 | 813:49 | 50.117
2020-08-31 | 814:49 | 50.118
2020-08-31 | 815:49 | 50.118
2020-08-31 | 816:49 | 50.118
2020-08-31 | 817:49 | 50.118
2020-08-31 | 818:49 | 50.115
2020-08-31 | 819:49 | 50.112
2020-08-31 | 820:49 | 50.109
2020-08-31 | 821:49 | 50.108
2020-08-31 | 822:49 | 50.108
2020-08-31 | 823:49 | 50.107
2020-08-31 | 824:49 | 50.102
2020-08-31 | 825:49 | 50.097
2020-08-31 | 826:49 | 50.092
2020-08-31 | 827:49 | 50.086
2020-08-31 | 828:49 | 50.08
2020-08-31 | 829:49 | 50.073
2020-08-31 | 830:49 | 50.07
2020-08-31 | 831:49 | 50.066
2020-08-31 | 832:49 | 50.065
2020-08-31 | 833:49 | 50.066
2020-08-31 | 834:49 | 50.068
2020-08-31 | 835:49 | 50.067
2020-08-31 | 836:49 | 50.067
2020-08-31 | 837:49 | 50.069
2020-08-31 | 838:49 | 50.072
2020-08-31 | 839:49 | 50.076
2020-08-31 | 840:49 | 50.081
2020-08-31 | 841:49 | 50.086
2020-08-31 | 842:49 | 50.091
2020-08-31 | 843:49 | 50.094
2020-08-31 | 844:49 | 50.096
2020-08-31 | 845:49 | 50.096
2020-08-31 | 846:49 | 50.097
2020-08-31 | 847:49 | 50.097
2020-08-31 | 848:49 | 50.097
2020-08-31 | 849:49 | 50.096
2020-08-31 | 850:49 | 50.096
2020-08-31 | 851:49 | 50.097
2020-08-31 | 852:49 | 50.101
2020-08-31 | 853:49 | 50.103
2020-08-31 | 854:49 | 50.107
2020-08-31 | 855:49 | 50.108
2020-08-31 | 856:49 | 50.11
2020-08-31 | 857:49 | 50.113
2020-08-31 | 858:49 | 50.113
2020-08-31 | 859:49 | 50.113
2020-08-31 | 860:49 | 50.111
2020-08-31 | 861:49 | 50.113
2020-08-31 | 862:49 | 50.114
2020-08-31 | 863:49 | 50.114
2020-08-31 | 864:49 | 50.112
2020-08-31 | 865:49 | 50.109
2020-08-31 | 866:49 | 50.106
2020-08-31 | 867:49 | 50.102
2020-08-31 | 868:49 | 50.098
2020-08-31 | 869:49 | 50.095
2020-08-31 | 870:49 | 50.091
2020-08-31 | 871:49 | 50.09
2020-08-31 | 872:49 | 50.088
2020-08-31 | 873:49 | 50.087
2020-08-31 | 874:49 | 50.087
2020-08-31 | 875:49 | 50.087
2020-08-31 | 876:49 | 50.089
2020-08-31 | 877:49 | 50.089
2020-08-31 | 878:49 | 50.09
2020-08-31 | 879:49 | 50.09
2020-08-31 | 880:49 | 50.09
2020-08-31 | 881:49 | 50.092
2020-08-31 | 882:49 | 50.093
2020-08-31 | 883:49 | 50.095
2020-08-31 | 884:49 | 50.097
2020-08-31 | 885:49 | 50.099
2020-08-31 | 886:49 | 50.101
2020-08-31 | 887:49 | 50.103
2020-08-31 | 888:49 | 50.105
2020-08-31 | 889:49 | 50.106
2020-08-31 | 890:49 | 50.108
2020-08-31 | 891:49 | 50.11
2020-08-31 | 892:49 | 50.112
2020-08-31 | 893:49 | 50.112
2020-08-31 | 894:49 | 50.111
2020-08-31 | 895:49 | 50.109
2020-08-31 | 896:49 | 50.106
2020-08-31 | 897:49 | 50.1
2020-08-31 | 898:49 | 50.095
2020-08-31 | 899:49 | 50.09
2020-08-31 | 900:49 | 50.084
2020-08-31 | 901:49 | 50.082
2020-08-31 | 902:49 | 50.083
2020-08-31 | 903:49 | 50.083
2020-08-31 | 904:49 | 50.083
2020-08-31 | 905:49 | 50.084
2020-08-31 | 906:49 | 50.085
2020-08-31 | 907:49 | 50.083
2020-08-31 | 908:49 | 50.079
2020-08-31 | 909:49 | 50.074
2020-08-31 | 910:49 | 50.069
2020-08-31 | 911:49 | 50.064
2020-08-31 | 912:49 | 50.06
2020-08-31 | 18:04 | 50.059
2020-08-31 | 18:04 | 50.06
2020-08-31 | 18:04 | 50.063
2020-08-31 | 18:04 | 50.065
2020-08-31 | 18:04 | 50.067
2020-08-31 | 18:04 | 50.069
2020-08-31 | 18:04 | 50.068
2020-08-31 | 18:04 | 50.066
2020-08-31 | 18:04 | 50.065
2020-08-31 | 18:04 | 50.062
2020-08-31 | 18:04 | 50.058
2020-08-31 | 18:04 | 50.054
2020-08-31 | 18:04 | 50.053
2020-08-31 | 18:04 | 50.053
2020-08-31 | 18:04 | 50.053
2020-08-31 | 18:04 | 50.056
2020-08-31 | 18:04 | 50.057
2020-08-31 | 18:04 | 50.057
2020-08-31 | 18:04 | 50.057
2020-08-31 | 18:04 | 50.057
2020-08-31 | 18:04 | 50.055
2020-08-31 | 18:04 | 50.055
2020-08-31 | 18:04 | 50.054
2020-08-31 | 18:04 | 50.055
2020-08-31 | 18:04 | 50.056
2020-08-31 | 18:04 | 50.055
2020-08-31 | 18:04 | 50.057
2020-08-31 | 18:04 | 50.057
2020-08-31 | 18:04 | 50.06
2020-08-31 | 18:04 | 50.062
2020-08-31 | 18:04 | 50.065
2020-08-31 | 18:05 | 50.067
2020-08-31 | 18:05 | 50.07
2020-08-31 | 18:05 | 50.07
2020-08-31 | 18:05 | 50.073
2020-08-31 | 18:05 | 50.075
2020-08-31 | 18:05 | 50.077
2020-08-31 | 18:05 | 50.077
2020-08-31 | 18:05 | 50.079
2020-08-31 | 18:05 | 50.082
2020-08-31 | 18:05 | 50.085
2020-08-31 | 18:05 | 50.089
2020-08-31 | 18:05 | 50.092
2020-08-31 | 18:05 | 50.093
2020-08-31 | 18:05 | 50.094
2020-08-31 | 18:05 | 50.095
2020-08-31 | 18:05 | 50.097
2020-08-31 | 18:05 | 50.097
2020-08-31 | 18:05 | 50.098
2020-08-31 | 18:05 | 50.095
2020-08-31 | 18:05 | 50.094
2020-08-31 | 18:05 | 50.09
2020-08-31 | 18:05 | 50.087
2020-08-31 | 18:05 | 50.084
2020-08-31 | 18:05 | 50.083
2020-08-31 | 18:05 | 50.085
2020-08-31 | 18:05 | 50.089
2020-08-31 | 18:05 | 50.092
2020-08-31 | 18:05 | 50.095
2020-08-31 | 18:05 | 50.097
2020-08-31 | 18:05 | 50.098
2020-08-31 | 18:05 | 50.097
2020-08-31 | 18:05 | 50.096
2020-08-31 | 18:05 | 50.095
2020-08-31 | 18:05 | 50.094
2020-08-31 | 18:05 | 50.094
2020-08-31 | 18:05 | 50.092
2020-08-31 | 18:05 | 50.091
2020-08-31 | 18:05 | 50.086
2020-08-31 | 18:05 | 50.084
2020-08-31 | 18:05 | 50.08
2020-08-31 | 18:05 | 50.078
2020-08-31 | 18:05 | 50.076
2020-08-31 | 18:05 | 50.078
2020-08-31 | 18:05 | 50.077
2020-08-31 | 18:05 | 50.079
2020-08-31 | 18:05 | 50.08
2020-08-31 | 18:05 | 50.082
2020-08-31 | 18:05 | 50.084
2020-08-31 | 18:05 | 50.085
2020-08-31 | 18:05 | 50.086
2020-08-31 | 18:05 | 50.086
2020-08-31 | 18:05 | 50.088
2020-08-31 | 18:05 | 50.09
2020-08-31 | 18:05 | 50.092
2020-08-31 | 18:05 | 50.091
2020-08-31 | 18:05 | 50.092
2020-08-31 | 18:05 | 50.091
2020-08-31 | 18:05 | 50.091
2020-08-31 | 18:05 | 50.089
2020-08-31 | 18:05 | 50.086
2020-08-31 | 18:06 | 50.081
2020-08-31 | 18:06 | 50.079
2020-08-31 | 18:06 | 50.077
2020-08-31 | 18:06 | 50.077
2020-08-31 | 18:06 | 50.074
2020-08-31 | 18:06 | 50.075
2020-08-31 | 18:06 | 50.076
2020-08-31 | 18:06 | 50.078
2020-08-31 | 18:06 | 50.078
2020-08-31 | 18:06 | 50.078
2020-08-31 | 18:06 | 50.076
2020-08-31 | 18:06 | 50.075
2020-08-31 | 18:06 | 50.072
2020-08-31 | 18:06 | 50.07
2020-08-31 | 18:06 | 50.068
2020-08-31 | 18:06 | 50.068
2020-08-31 | 18:06 | 50.069
2020-08-31 | 18:06 | 50.071
2020-08-31 | 18:06 | 50.073
2020-08-31 | 18:06 | 50.075
2020-08-31 | 18:06 | 50.075
2020-08-31 | 18:06 | 50.076
2020-08-31 | 18:06 | 50.076
2020-08-31 | 18:06 | 50.077
2020-08-31 | 18:06 | 50.076
2020-08-31 | 18:06 | 50.076
2020-08-31 | 18:06 | 50.073
2020-08-31 | 18:06 | 50.071
2020-08-31 | 18:06 | 50.069
2020-08-31 | 18:06 | 50.067
2020-08-31 | 18:06 | 50.067
2020-08-31 | 18:06 | 50.068
2020-08-31 | 18:06 | 50.067
2020-08-31 | 18:06 | 50.07
2020-08-31 | 18:06 | 50.074
2020-08-31 | 18:06 | 50.076
2020-08-31 | 18:06 | 50.077
2020-08-31 | 18:06 | 50.076
2020-08-31 | 18:06 | 50.074
2020-08-31 | 18:06 | 50.071
2020-08-31 | 18:06 | 50.068
2020-08-31 | 18:06 | 50.066
2020-08-31 | 18:06 | 50.065
2020-08-31 | 18:06 | 50.066
2020-08-31 | 18:06 | 50.07
2020-08-31 | 18:06 | 50.075
2020-08-31 | 18:06 | 50.079
2020-08-31 | 18:06 | 50.082
2020-08-31 | 18:06 | 50.084
2020-08-31 | 18:06 | 50.086
2020-08-31 | 18:06 | 50.091
2020-08-31 | 18:06 | 50.095
2020-08-31 | 18:06 | 50.098
2020-08-31 | 18:06 | 50.1
2020-08-31 | 18:06 | 50.101
2020-08-31 | 18:06 | 50.102
2020-08-31 | 18:06 | 50.103
2020-08-31 | 18:06 | 50.103
2020-08-31 | 18:06 | 50.103
2020-08-31 | 18:07 | 50.101
2020-08-31 | 18:07 | 50.097
2020-08-31 | 18:07 | 50.093
2020-08-31 | 18:07 | 50.089
2020-08-31 | 18:07 | 50.085
2020-08-31 | 18:07 | 50.082
2020-08-31 | 18:07 | 50.079
2020-08-31 | 18:07 | 50.076
2020-08-31 | 18:07 | 50.072
2020-08-31 | 18:07 | 50.071
2020-08-31 | 18:07 | 50.07
2020-08-31 | 18:07 | 50.069
2020-08-31 | 18:07 | 50.069
2020-08-31 | 18:07 | 50.07
2020-08-31 | 18:07 | 50.071
2020-08-31 | 18:07 | 50.073
2020-08-31 | 18:07 | 50.074
2020-08-31 | 18:07 | 50.076
2020-08-31 | 18:07 | 50.077
2020-08-31 | 18:07 | 50.077
2020-08-31 | 18:07 | 50.076
2020-08-31 | 18:07 | 50.076
2020-08-31 | 18:07 | 50.075
2020-08-31 | 18:07 | 50.074
2020-08-31 | 18:07 | 50.072
2020-08-31 | 18:07 | 50.071
2020-08-31 | 18:07 | 50.07
2020-08-31 | 18:07 | 50.069
2020-08-31 | 18:07 | 50.068
2020-08-31 | 18:07 | 50.068
2020-08-31 | 18:07 | 50.065
2020-08-31 | 18:07 | 50.063
2020-08-31 | 18:07 | 50.06
2020-08-31 | 18:07 | 50.058
2020-08-31 | 18:07 | 50.057
2020-08-31 | 18:07 | 50.055
2020-08-31 | 18:07 | 50.053
2020-08-31 | 18:07 | 50.051
2020-08-31 | 18:07 | 50.051
2020-08-31 | 18:07 | 50.05
2020-08-31 | 18:07 | 50.049
2020-08-31 | 18:07 | 50.047
2020-08-31 | 18:07 | 50.046
2020-08-31 | 18:07 | 50.046
2020-08-31 | 18:07 | 50.048
2020-08-31 | 18:07 | 50.051
2020-08-31 | 18:07 | 50.053
2020-08-31 | 18:07 | 50.053
2020-08-31 | 18:07 | 50.053
2020-08-31 | 18:07 | 50.054
2020-08-31 | 18:07 | 50.053
2020-08-31 | 18:07 | 50.053
2020-08-31 | 18:07 | 50.053
2020-08-31 | 18:07 | 50.051
2020-08-31 | 18:07 | 50.049
2020-08-31 | 18:07 | 50.046
2020-08-31 | 18:07 | 50.044
2020-08-31 | 18:07 | 50.042
2020-08-31 | 18:07 | 50.04
2020-08-31 | 18:07 | 50.041
2020-08-31 | 18:07 | 50.04
2020-08-31 | 18:08 | 50.039
2020-08-31 | 18:08 | 50.04
2020-08-31 | 18:08 | 50.038
2020-08-31 | 18:08 | 50.038
2020-08-31 | 18:08 | 50.039
2020-08-31 | 18:08 | 50.04
2020-08-31 | 18:08 | 50.043
2020-08-31 | 18:08 | 50.045
2020-08-31 | 18:08 | 50.048
2020-08-31 | 18:08 | 50.049
2020-08-31 | 18:08 | 50.049
2020-08-31 | 18:08 | 50.05
2020-08-31 | 18:08 | 50.048
2020-08-31 | 18:08 | 50.048
2020-08-31 | 18:08 | 50.047
2020-08-31 | 18:08 | 50.044
2020-08-31 | 18:08 | 50.045
2020-08-31 | 18:08 | 50.044
2020-08-31 | 18:08 | 50.042
2020-08-31 | 18:08 | 50.041
2020-08-31 | 18:08 | 50.039
2020-08-31 | 18:08 | 50.038
2020-08-31 | 18:08 | 50.038
2020-08-31 | 18:08 | 50.038
2020-08-31 | 18:08 | 50.038
2020-08-31 | 18:08 | 50.038
2020-08-31 | 18:08 | 50.038
2020-08-31 | 18:08 | 50.04
2020-08-31 | 18:08 | 50.042
2020-08-31 | 18:08 | 50.043
2020-08-31 | 18:08 | 50.043
2020-08-31 | 18:08 | 50.044
2020-08-31 | 18:08 | 50.045
2020-08-31 | 18:08 | 50.046
2020-08-31 | 18:08 | 50.047
2020-08-31 | 18:08 | 50.047
2020-08-31 | 18:08 | 50.044
2020-08-31 | 18:08 | 50.043
2020-08-31 | 18:08 | 50.04
2020-08-31 | 18:08 | 50.037
2020-08-31 | 18:08 | 50.036
2020-08-31 | 18:08 | 50.036
2020-08-31 | 18:08 | 50.036
2020-08-31 | 18:08 | 50.036
2020-08-31 | 18:08 | 50.036
2020-08-31 | 18:08 | 50.037
2020-08-31 | 18:08 | 50.038
2020-08-31 | 18:08 | 50.039
2020-08-31 | 18:08 | 50.04
2020-08-31 | 18:08 | 50.041
2020-08-31 | 18:08 | 50.042
2020-08-31 | 18:08 | 50.042
2020-08-31 | 18:08 | 50.041
2020-08-31 | 18:08 | 50.04
2020-08-31 | 18:08 | 50.039
2020-08-31 | 18:08 | 50.04
2020-08-31 | 18:08 | 50.04
2020-08-31 | 18:08 | 50.04
2020-08-31 | 18:08 | 50.04
2020-08-31 | 18:09 | 50.039
2020-08-31 | 18:09 | 50.038
2020-08-31 | 18:09 | 50.038
2020-08-31 | 18:09 | 50.038
2020-08-31 | 18:09 | 50.037
2020-08-31 | 18:09 | 50.038
2020-08-31 | 18:09 | 50.038
2020-08-31 | 18:09 | 50.039
2020-08-31 | 18:09 | 50.04
2020-08-31 | 18:09 | 50.04
2020-08-31 | 18:09 | 50.042
2020-08-31 | 18:09 | 50.042
2020-08-31 | 18:09 | 50.042
2020-08-31 | 18:09 | 50.041
2020-08-31 | 18:09 | 50.041
2020-08-31 | 18:09 | 50.039
2020-08-31 | 18:09 | 50.036
2020-08-31 | 18:09 | 50.032
2020-08-31 | 18:09 | 50.032
2020-08-31 | 18:09 | 50.031
2020-08-31 | 18:09 | 50.032
2020-08-31 | 18:09 | 50.033
2020-08-31 | 18:09 | 50.033
2020-08-31 | 18:09 | 50.034
2020-08-31 | 18:09 | 50.032
2020-08-31 | 18:09 | 50.032
2020-08-31 | 18:09 | 50.033
2020-08-31 | 18:09 | 50.035
2020-08-31 | 18:09 | 50.038
2020-08-31 | 18:09 | 50.039
2020-08-31 | 18:09 | 50.039
2020-08-31 | 18:09 | 50.036
2020-08-31 | 18:09 | 50.034
2020-08-31 | 18:09 | 50.032
2020-08-31 | 18:09 | 50.029
2020-08-31 | 18:09 | 50.027
2020-08-31 | 18:09 | 50.025
2020-08-31 | 18:09 | 50.023
2020-08-31 | 18:09 | 50.02
2020-08-31 | 18:09 | 50.018
2020-08-31 | 18:09 | 50.016
2020-08-31 | 18:09 | 50.014
2020-08-31 | 18:09 | 50.013
2020-08-31 | 18:09 | 50.013
2020-08-31 | 18:09 | 50.013
2020-08-31 | 18:09 | 50.015
2020-08-31 | 18:09 | 50.015
2020-08-31 | 18:09 | 50.013
2020-08-31 | 18:09 | 50.013
2020-08-31 | 18:09 | 50.013
2020-08-31 | 18:09 | 50.014
2020-08-31 | 18:09 | 50.015
2020-08-31 | 18:09 | 50.016
2020-08-31 | 18:09 | 50.019
2020-08-31 | 18:09 | 50.021
2020-08-31 | 18:09 | 50.025
2020-08-31 | 18:09 | 50.03
2020-08-31 | 18:09 | 50.033
2020-08-31 | 18:09 | 50.037
2020-08-31 | 18:09 | 50.039
2020-08-31 | 18:09 | 50.04
2020-08-31 | 18:10 | 50.039
2020-08-31 | 18:10 | 50.04
2020-08-31 | 18:10 | 50.04
2020-08-31 | 18:10 | 50.041
2020-08-31 | 18:10 | 50.042
2020-08-31 | 18:10 | 50.043
2020-08-31 | 18:10 | 50.044
2020-08-31 | 18:10 | 50.044
2020-08-31 | 18:10 | 50.045
2020-08-31 | 18:10 | 50.047
2020-08-31 | 18:10 | 50.048
2020-08-31 | 18:10 | 50.047
2020-08-31 | 18:10 | 50.046
2020-08-31 | 18:10 | 50.045
2020-08-31 | 18:10 | 50.045
2020-08-31 | 18:10 | 50.044
2020-08-31 | 18:10 | 50.042
2020-08-31 | 18:10 | 50.04
2020-08-31 | 18:10 | 50.039
2020-08-31 | 18:10 | 50.037
2020-08-31 | 18:10 | 50.036
2020-08-31 | 18:10 | 50.037
2020-08-31 | 18:10 | 50.037
2020-08-31 | 18:10 | 50.036
2020-08-31 | 18:10 | 50.036
2020-08-31 | 18:10 | 50.035
2020-08-31 | 18:10 | 50.036
2020-08-31 | 18:10 | 50.034
2020-08-31 | 18:10 | 50.03
2020-08-31 | 18:10 | 50.025
2020-08-31 | 18:10 | 50.022
2020-08-31 | 18:10 | 50.02
2020-08-31 | 18:10 | 50.02
2020-08-31 | 18:10 | 50.023
2020-08-31 | 18:10 | 50.025
2020-08-31 | 18:10 | 50.027
2020-08-31 | 18:10 | 50.028
2020-08-31 | 18:10 | 50.03
2020-08-31 | 18:10 | 50.034
2020-08-31 | 18:10 | 50.037
2020-08-31 | 18:10 | 50.039
2020-08-31 | 18:10 | 50.041
2020-08-31 | 18:10 | 50.044
2020-08-31 | 18:10 | 50.046
2020-08-31 | 18:10 | 50.046
2020-08-31 | 18:10 | 50.046
2020-08-31 | 18:10 | 50.048
2020-08-31 | 18:10 | 50.048
2020-08-31 | 18:10 | 50.048
2020-08-31 | 18:10 | 50.046
2020-08-31 | 18:10 | 50.044
2020-08-31 | 18:10 | 50.042
2020-08-31 | 18:10 | 50.039
2020-08-31 | 18:10 | 50.039
2020-08-31 | 18:10 | 50.039
2020-08-31 | 18:10 | 50.04
2020-08-31 | 18:10 | 50.04
2020-08-31 | 18:10 | 50.039
2020-08-31 | 18:10 | 50.039
2020-08-31 | 18:11 | 50.038
2020-08-31 | 18:11 | 50.036
2020-08-31 | 18:11 | 50.034
2020-08-31 | 18:11 | 50.033
2020-08-31 | 18:11 | 50.031
2020-08-31 | 18:11 | 50.029
2020-08-31 | 18:11 | 50.026
2020-08-31 | 18:11 | 50.023
2020-08-31 | 18:11 | 50.021
2020-08-31 | 18:11 | 50.021
2020-08-31 | 18:11 | 50.019
2020-08-31 | 18:11 | 50.02
2020-08-31 | 18:11 | 50.021
2020-08-31 | 18:11 | 50.022
2020-08-31 | 18:11 | 50.025
2020-08-31 | 18:11 | 50.026
2020-08-31 | 18:11 | 50.027
2020-08-31 | 18:11 | 50.029
2020-08-31 | 18:11 | 50.029
2020-08-31 | 18:11 | 50.029
2020-08-31 | 18:11 | 50.029
2020-08-31 | 18:11 | 50.028
2020-08-31 | 18:11 | 50.027
2020-08-31 | 18:11 | 50.027
2020-08-31 | 18:11 | 50.03
2020-08-31 | 18:11 | 50.032
2020-08-31 | 18:11 | 50.034
2020-08-31 | 18:11 | 50.037
2020-08-31 | 18:11 | 50.04
2020-08-31 | 18:11 | 50.042
2020-08-31 | 18:11 | 50.041
2020-08-31 | 18:11 | 50.042
2020-08-31 | 18:11 | 50.041
2020-08-31 | 18:11 | 50.04
2020-08-31 | 18:11 | 50.039
2020-08-31 | 18:11 | 50.039
2020-08-31 | 18:11 | 50.039
2020-08-31 | 18:11 | 50.04
2020-08-31 | 18:11 | 50.038
2020-08-31 | 18:11 | 50.037
2020-08-31 | 18:11 | 50.035
2020-08-31 | 18:11 | 50.034
2020-08-31 | 18:11 | 50.032
2020-08-31 | 18:11 | 50.03
2020-08-31 | 18:11 | 50.028
2020-08-31 | 18:11 | 50.026
2020-08-31 | 18:11 | 50.025
2020-08-31 | 18:11 | 50.023
2020-08-31 | 18:11 | 50.022
2020-08-31 | 18:11 | 50.021
2020-08-31 | 18:11 | 50.019
2020-08-31 | 18:11 | 50.016
2020-08-31 | 18:11 | 50.015
2020-08-31 | 18:11 | 50.014
2020-08-31 | 18:11 | 50.013
2020-08-31 | 18:11 | 50.013
2020-08-31 | 18:11 | 50.012
2020-08-31 | 18:11 | 50.011
2020-08-31 | 18:11 | 50.01
2020-08-31 | 18:11 | 50.01
2020-08-31 | 18:11 | 50.013
2020-08-31 | 18:12 | 50.016
2020-08-31 | 18:12 | 50.017
2020-08-31 | 18:12 | 50.02
2020-08-31 | 18:12 | 50.021
2020-08-31 | 18:12 | 50.021
2020-08-31 | 18:12 | 50.022
2020-08-31 | 18:12 | 50.021
2020-08-31 | 18:12 | 50.021
2020-08-31 | 18:12 | 50.021
2020-08-31 | 18:12 | 50.021
2020-08-31 | 18:12 | 50.02
2020-08-31 | 18:12 | 50.02
2020-08-31 | 18:12 | 50.017
2020-08-31 | 18:12 | 50.012
2020-08-31 | 18:12 | 50.01
2020-08-31 | 18:12 | 50.007
2020-08-31 | 18:12 | 50.003
2020-08-31 | 18:12 | 49.999
2020-08-31 | 18:12 | 49.996
2020-08-31 | 18:12 | 49.995
2020-08-31 | 18:12 | 49.994
2020-08-31 | 18:12 | 49.992
2020-08-31 | 18:12 | 49.989
2020-08-31 | 18:12 | 49.986
2020-08-31 | 18:12 | 49.983
2020-08-31 | 18:12 | 49.98
2020-08-31 | 18:12 | 49.977
2020-08-31 | 18:12 | 49.977
2020-08-31 | 18:12 | 49.976
2020-08-31 | 18:12 | 49.976
2020-08-31 | 18:12 | 49.976
2020-08-31 | 18:12 | 49.978
2020-08-31 | 18:12 | 49.978
2020-08-31 | 18:12 | 49.978
2020-08-31 | 18:12 | 49.976
2020-08-31 | 18:12 | 49.975
2020-08-31 | 18:12 | 49.975
2020-08-31 | 18:12 | 49.976
2020-08-31 | 18:12 | 49.976
2020-08-31 | 18:12 | 49.978
2020-08-31 | 18:12 | 49.979
2020-08-31 | 18:12 | 49.981
2020-08-31 | 18:12 | 49.983
2020-08-31 | 18:12 | 49.984
2020-08-31 | 18:12 | 49.985
2020-08-31 | 18:12 | 49.987
2020-08-31 | 18:12 | 49.99
2020-08-31 | 18:12 | 49.993
2020-08-31 | 18:12 | 49.996
2020-08-31 | 18:12 | 50
2020-08-31 | 18:12 | 50.002
2020-08-31 | 18:12 | 50.005
2020-08-31 | 18:12 | 50.007
2020-08-31 | 18:12 | 50.008
2020-08-31 | 18:12 | 50.008
2020-08-31 | 18:12 | 50.01
2020-08-31 | 18:12 | 50.01
2020-08-31 | 18:12 | 50.011
2020-08-31 | 18:12 | 50.012
2020-08-31 | 18:13 | 50.013
2020-08-31 | 18:13 | 50.014
2020-08-31 | 18:13 | 50.014
2020-08-31 | 18:13 | 50.013
2020-08-31 | 18:13 | 50.013
2020-08-31 | 18:13 | 50.014
2020-08-31 | 18:13 | 50.015
2020-08-31 | 18:13 | 50.016
2020-08-31 | 18:13 | 50.016
2020-08-31 | 18:13 | 50.017
2020-08-31 | 18:13 | 50.018
2020-08-31 | 18:13 | 50.02
2020-08-31 | 18:13 | 50.021
2020-08-31 | 18:13 | 50.02
2020-08-31 | 18:13 | 50.021
2020-08-31 | 18:13 | 50.02
2020-08-31 | 18:13 | 50.019
2020-08-31 | 18:13 | 50.022
2020-08-31 | 18:13 | 50.023
2020-08-31 | 18:13 | 50.026
2020-08-31 | 18:13 | 50.027
2020-08-31 | 18:13 | 50.031
2020-08-31 | 18:13 | 50.031
2020-08-31 | 18:13 | 50.032
2020-08-31 | 18:13 | 50.033
2020-08-31 | 18:13 | 50.033
2020-08-31 | 18:13 | 50.033
2020-08-31 | 18:13 | 50.033
2020-08-31 | 18:13 | 50.034
2020-08-31 | 18:13 | 50.036
2020-08-31 | 18:13 | 50.038
2020-08-31 | 18:13 | 50.04
2020-08-31 | 18:13 | 50.043
2020-08-31 | 18:13 | 50.045
2020-08-31 | 18:13 | 50.046
2020-08-31 | 18:13 | 50.046
2020-08-31 | 18:13 | 50.047
2020-08-31 | 18:13 | 50.048
2020-08-31 | 18:13 | 50.049
2020-08-31 | 18:13 | 50.048
2020-08-31 | 18:13 | 50.049
2020-08-31 | 18:13 | 50.045
2020-08-31 | 18:13 | 50.043
2020-08-31 | 18:13 | 50.041
2020-08-31 | 18:13 | 50.04
2020-08-31 | 18:13 | 50.038
2020-08-31 | 18:13 | 50.035
2020-08-31 | 18:13 | 50.034
2020-08-31 | 18:13 | 50.034
2020-08-31 | 18:13 | 50.034
2020-08-31 | 18:13 | 50.034
2020-08-31 | 18:13 | 50.034
2020-08-31 | 18:13 | 50.035
2020-08-31 | 18:13 | 50.036
2020-08-31 | 18:13 | 50.035
2020-08-31 | 18:13 | 50.034
2020-08-31 | 18:13 | 50.032
2020-08-31 | 18:13 | 50.032
2020-08-31 | 18:13 | 50.027
2020-08-31 | 18:13 | 50.026
2020-08-31 | 18:14 | 50.022
2020-08-31 | 18:14 | 50.019
2020-08-31 | 18:14 | 50.015
2020-08-31 | 18:14 | 50.013
2020-08-31 | 18:14 | 50.01
2020-08-31 | 18:14 | 50.009
2020-08-31 | 18:14 | 50.008
2020-08-31 | 18:14 | 50.011
2020-08-31 | 18:14 | 50.01
2020-08-31 | 18:14 | 50.011
2020-08-31 | 18:14 | 50.01
2020-08-31 | 18:14 | 50.012
2020-08-31 | 18:14 | 50.012
2020-08-31 | 18:14 | 50.01
2020-08-31 | 18:14 | 50.008
2020-08-31 | 18:14 | 50.006
2020-08-31 | 18:14 | 50.003
2020-08-31 | 18:14 | 50.002
2020-08-31 | 18:14 | 50
2020-08-31 | 18:14 | 50
2020-08-31 | 18:14 | 50
2020-08-31 | 18:14 | 49.999
2020-08-31 | 18:14 | 49.998
2020-08-31 | 18:14 | 49.995
2020-08-31 | 18:14 | 49.994
2020-08-31 | 18:14 | 49.991
2020-08-31 | 18:14 | 49.99
2020-08-31 | 18:14 | 49.989
2020-08-31 | 18:14 | 49.989
2020-08-31 | 18:14 | 49.988
2020-08-31 | 18:14 | 49.986
2020-08-31 | 18:14 | 49.983
2020-08-31 | 18:14 | 49.98
2020-08-31 | 18:14 | 49.977
2020-08-31 | 18:14 | 49.975
2020-08-31 | 18:14 | 49.971
2020-08-31 | 18:14 | 49.97
2020-08-31 | 18:14 | 49.967
2020-08-31 | 18:14 | 49.969
2020-08-31 | 18:14 | 49.967
2020-08-31 | 18:14 | 49.969
2020-08-31 | 18:14 | 49.966
2020-08-31 | 18:14 | 49.966
2020-08-31 | 18:14 | 49.963
2020-08-31 | 18:14 | 49.963
2020-08-31 | 18:14 | 49.96
2020-08-31 | 18:14 | 49.959
2020-08-31 | 18:14 | 49.958
2020-08-31 | 18:14 | 49.958
2020-08-31 | 18:14 | 49.958
2020-08-31 | 18:14 | 49.958
2020-08-31 | 18:14 | 49.956
2020-08-31 | 18:14 | 49.956
2020-08-31 | 18:14 | 49.955
2020-08-31 | 18:14 | 49.953
2020-08-31 | 18:14 | 49.95
2020-08-31 | 18:14 | 49.951
2020-08-31 | 18:14 | 49.95
2020-08-31 | 18:14 | 49.95
2020-08-31 | 18:14 | 49.949
2020-08-31 | 18:15 | 49.949
2020-08-31 | 18:15 | 49.949
2020-08-31 | 18:15 | 49.951
2020-08-31 | 18:15 | 49.949
2020-08-31 | 18:15 | 49.947
2020-08-31 | 18:15 | 49.945
2020-08-31 | 18:15 | 49.943
2020-08-31 | 18:15 | 49.941
2020-08-31 | 18:15 | 49.942
2020-08-31 | 18:15 | 49.942
2020-08-31 | 18:15 | 49.941
2020-08-31 | 18:15 | 49.939
2020-08-31 | 18:15 | 49.938
2020-08-31 | 18:15 | 49.935
2020-08-31 | 18:15 | 49.934
2020-08-31 | 18:15 | 49.934
2020-08-31 | 18:15 | 49.932
2020-08-31 | 18:15 | 49.931
2020-08-31 | 18:15 | 49.928
2020-08-31 | 18:15 | 49.925
2020-08-31 | 18:15 | 49.921
2020-08-31 | 18:15 | 49.919
2020-08-31 | 18:15 | 49.917
2020-08-31 | 18:15 | 49.916
2020-08-31 | 18:15 | 49.916
2020-08-31 | 18:15 | 49.917
2020-08-31 | 18:15 | 49.919
2020-08-31 | 18:15 | 49.922
2020-08-31 | 18:15 | 49.926
2020-08-31 | 18:15 | 49.929
2020-08-31 | 18:15 | 49.932
2020-08-31 | 18:15 | 49.932
2020-08-31 | 18:15 | 49.933
2020-08-31 | 18:15 | 49.933
2020-08-31 | 18:15 | 49.933
2020-08-31 | 18:15 | 49.934
2020-08-31 | 18:15 | 49.932
2020-08-31 | 18:15 | 49.933
2020-08-31 | 18:15 | 49.933
2020-08-31 | 18:15 | 49.934
2020-08-31 | 18:15 | 49.936
2020-08-31 | 18:15 | 49.936
2020-08-31 | 18:15 | 49.937
2020-08-31 | 18:15 | 49.937
2020-08-31 | 18:15 | 49.936
2020-08-31 | 18:15 | 49.936
2020-08-31 | 18:15 | 49.937
2020-08-31 | 18:15 | 49.935
2020-08-31 | 18:15 | 49.935
2020-08-31 | 18:15 | 49.934
2020-08-31 | 18:15 | 49.933
2020-08-31 | 18:15 | 49.932
2020-08-31 | 18:15 | 49.933
2020-08-31 | 18:15 | 49.931
2020-08-31 | 18:15 | 49.932
2020-08-31 | 18:15 | 49.931
2020-08-31 | 18:15 | 49.931
2020-08-31 | 18:15 | 49.93
2020-08-31 | 18:15 | 49.928
2020-08-31 | 18:15 | 49.927
2020-08-31 | 18:16 | 49.926
2020-08-31 | 18:16 | 49.923
2020-08-31 | 18:16 | 49.921
2020-08-31 | 18:16 | 49.919
2020-08-31 | 18:16 | 49.918
2020-08-31 | 18:16 | 49.919
2020-08-31 | 18:16 | 49.916
2020-08-31 | 18:16 | 49.916
2020-08-31 | 18:16 | 49.915
2020-08-31 | 18:16 | 49.913
2020-08-31 | 18:16 | 49.911
2020-08-31 | 18:16 | 49.91
2020-08-31 | 18:16 | 49.909
2020-08-31 | 18:16 | 49.911
2020-08-31 | 18:16 | 49.909
2020-08-31 | 18:16 | 49.91
2020-08-31 | 18:16 | 49.912
2020-08-31 | 18:16 | 49.914
2020-08-31 | 18:16 | 49.916
2020-08-31 | 18:16 | 49.917
2020-08-31 | 18:16 | 49.916
2020-08-31 | 18:16 | 49.916
2020-08-31 | 18:16 | 49.917
2020-08-31 | 18:16 | 49.918
2020-08-31 | 18:16 | 49.919
2020-08-31 | 18:16 | 49.923
2020-08-31 | 18:16 | 49.926
2020-08-31 | 18:16 | 49.929
2020-08-31 | 18:16 | 49.931
2020-08-31 | 18:16 | 49.931
2020-08-31 | 18:16 | 49.93
2020-08-31 | 18:16 | 49.931
2020-08-31 | 18:16 | 49.932
2020-08-31 | 18:16 | 49.934
2020-08-31 | 18:16 | 49.934
2020-08-31 | 18:16 | 49.932
2020-08-31 | 18:16 | 49.931
2020-08-31 | 18:16 | 49.929
2020-08-31 | 18:16 | 49.93
2020-08-31 | 18:16 | 49.931
2020-08-31 | 18:16 | 49.932
2020-08-31 | 18:16 | 49.935
2020-08-31 | 18:16 | 49.94
2020-08-31 | 18:16 | 49.941
2020-08-31 | 18:16 | 49.943
2020-08-31 | 18:16 | 49.945
2020-08-31 | 18:16 | 49.946
2020-08-31 | 18:16 | 49.944
2020-08-31 | 18:16 | 49.944
2020-08-31 | 18:16 | 49.944
2020-08-31 | 18:16 | 49.942
2020-08-31 | 18:16 | 49.94
2020-08-31 | 18:16 | 49.937
2020-08-31 | 18:16 | 49.934
2020-08-31 | 18:16 | 49.931
2020-08-31 | 18:16 | 49.929
2020-08-31 | 18:16 | 49.927
2020-08-31 | 18:16 | 49.926
2020-08-31 | 18:16 | 49.928
2020-08-31 | 18:16 | 49.926
2020-08-31 | 18:16 | 49.925
2020-08-31 | 18:17 | 49.924
2020-08-31 | 18:17 | 49.921
2020-08-31 | 18:17 | 49.92
2020-08-31 | 18:17 | 49.918
2020-08-31 | 18:17 | 49.917
2020-08-31 | 18:17 | 49.919
2020-08-31 | 18:17 | 49.922
2020-08-31 | 18:17 | 49.922
2020-08-31 | 18:17 | 49.924
2020-08-31 | 18:17 | 49.927
2020-08-31 | 18:17 | 49.928
2020-08-31 | 18:17 | 49.931
2020-08-31 | 18:17 | 49.933
2020-08-31 | 18:17 | 49.935
2020-08-31 | 18:17 | 49.939
2020-08-31 | 18:17 | 49.938
2020-08-31 | 18:17 | 49.937
2020-08-31 | 18:17 | 49.937
2020-08-31 | 18:17 | 49.934
2020-08-31 | 18:17 | 49.929
2020-08-31 | 18:17 | 49.926
2020-08-31 | 18:17 | 49.925
2020-08-31 | 18:17 | 49.922
2020-08-31 | 18:17 | 49.923
2020-08-31 | 18:17 | 49.923
2020-08-31 | 18:17 | 49.923
2020-08-31 | 18:17 | 49.927
2020-08-31 | 18:17 | 49.93
2020-08-31 | 18:17 | 49.935
2020-08-31 | 18:17 | 49.938
2020-08-31 | 18:17 | 49.944
2020-08-31 | 18:17 | 49.946
2020-08-31 | 18:17 | 49.948
2020-08-31 | 18:17 | 49.951
2020-08-31 | 18:17 | 49.953
2020-08-31 | 18:17 | 49.955
2020-08-31 | 18:17 | 49.957
2020-08-31 | 18:17 | 49.955
2020-08-31 | 18:17 | 49.953
2020-08-31 | 18:17 | 49.953
2020-08-31 | 18:17 | 49.954
2020-08-31 | 18:17 | 49.956
2020-08-31 | 18:17 | 49.957
2020-08-31 | 18:17 | 49.959
2020-08-31 | 18:17 | 49.958
2020-08-31 | 18:17 | 49.956
2020-08-31 | 18:17 | 49.953
2020-08-31 | 18:17 | 49.953
2020-08-31 | 18:17 | 49.952
2020-08-31 | 18:17 | 49.953
2020-08-31 | 18:17 | 49.956
2020-08-31 | 18:17 | 49.958
2020-08-31 | 18:17 | 49.962
2020-08-31 | 18:17 | 49.963
2020-08-31 | 18:17 | 49.965
2020-08-31 | 18:17 | 49.968
2020-08-31 | 18:17 | 49.97
2020-08-31 | 18:17 | 49.972
2020-08-31 | 18:17 | 49.975
2020-08-31 | 18:18 | 49.977
2020-08-31 | 18:18 | 49.978
2020-08-31 | 18:18 | 49.977
2020-08-31 | 18:18 | 49.976
2020-08-31 | 18:18 | 49.975
2020-08-31 | 18:18 | 49.976
2020-08-31 | 18:18 | 49.976
2020-08-31 | 18:18 | 49.976
2020-08-31 | 18:18 | 49.975
2020-08-31 | 18:18 | 49.974
2020-08-31 | 18:18 | 49.973
2020-08-31 | 18:18 | 49.97
2020-08-31 | 18:18 | 49.97
2020-08-31 | 18:18 | 49.968
2020-08-31 | 18:18 | 49.968
2020-08-31 | 18:18 | 49.971
2020-08-31 | 18:18 | 49.972
2020-08-31 | 18:18 | 49.974
2020-08-31 | 18:18 | 49.977
2020-08-31 | 18:18 | 49.979
2020-08-31 | 18:18 | 49.981
2020-08-31 | 18:18 | 49.983
2020-08-31 | 18:18 | 49.984
2020-08-31 | 18:18 | 49.986
2020-08-31 | 18:18 | 49.986
2020-08-31 | 18:18 | 49.987
2020-08-31 | 18:18 | 49.988
2020-08-31 | 18:18 | 49.987
2020-08-31 | 18:18 | 49.984
2020-08-31 | 18:18 | 49.982
2020-08-31 | 18:18 | 49.978
2020-08-31 | 18:18 | 49.975
2020-08-31 | 18:18 | 49.971
2020-08-31 | 18:18 | 49.969
2020-08-31 | 18:18 | 49.966
2020-08-31 | 18:18 | 49.962
2020-08-31 | 18:18 | 49.96
2020-08-31 | 18:18 | 49.96
2020-08-31 | 18:18 | 49.961
2020-08-31 | 18:18 | 49.962
2020-08-31 | 18:18 | 49.96
2020-08-31 | 18:18 | 49.961
2020-08-31 | 18:18 | 49.96
2020-08-31 | 18:18 | 49.961
2020-08-31 | 18:18 | 49.96
2020-08-31 | 18:18 | 49.959
2020-08-31 | 18:18 | 49.959
2020-08-31 | 18:18 | 49.958
2020-08-31 | 18:18 | 49.954
2020-08-31 | 18:18 | 49.952
2020-08-31 | 18:18 | 49.95
2020-08-31 | 18:18 | 49.948
2020-08-31 | 18:18 | 49.945
2020-08-31 | 18:18 | 49.943
2020-08-31 | 18:18 | 49.944
2020-08-31 | 18:18 | 49.942
2020-08-31 | 18:18 | 49.943
2020-08-31 | 18:18 | 49.943
2020-08-31 | 18:18 | 49.948
2020-08-31 | 18:18 | 49.951
2020-08-31 | 18:18 | 49.953
2020-08-31 | 18:19 | 49.957
2020-08-31 | 18:19 | 49.957
2020-08-31 | 18:19 | 49.96
2020-08-31 | 18:19 | 49.961
2020-08-31 | 18:19 | 49.964
2020-08-31 | 18:19 | 49.967
2020-08-31 | 18:19 | 49.97
2020-08-31 | 18:19 | 49.972
2020-08-31 | 18:19 | 49.971
2020-08-31 | 18:19 | 49.97
2020-08-31 | 18:19 | 49.969
2020-08-31 | 18:19 | 49.969
2020-08-31 | 18:19 | 49.969
2020-08-31 | 18:19 | 49.969
2020-08-31 | 18:19 | 49.966
2020-08-31 | 18:19 | 49.964
2020-08-31 | 18:19 | 49.962
2020-08-31 | 18:19 | 49.959
2020-08-31 | 18:19 | 49.956
2020-08-31 | 18:19 | 49.951
2020-08-31 | 18:19 | 49.948
2020-08-31 | 18:19 | 49.945
2020-08-31 | 18:19 | 49.94
2020-08-31 | 18:19 | 49.937
2020-08-31 | 18:19 | 49.934
2020-08-31 | 18:19 | 49.932
2020-08-31 | 18:19 | 49.929
2020-08-31 | 18:19 | 49.926
2020-08-31 | 18:19 | 49.923
2020-08-31 | 18:19 | 49.92
2020-08-31 | 18:19 | 49.919
2020-08-31 | 18:19 | 49.919
2020-08-31 | 18:19 | 49.919
2020-08-31 | 18:19 | 49.918
2020-08-31 | 18:19 | 49.918
2020-08-31 | 18:19 | 49.915
2020-08-31 | 18:19 | 49.916
2020-08-31 | 18:19 | 49.915
2020-08-31 | 18:19 | 49.915
2020-08-31 | 18:19 | 49.915
2020-08-31 | 18:19 | 49.916
2020-08-31 | 18:19 | 49.915
2020-08-31 | 18:19 | 49.914
2020-08-31 | 18:19 | 49.913
2020-08-31 | 18:19 | 49.913
2020-08-31 | 18:19 | 49.913
2020-08-31 | 18:19 | 49.914
2020-08-31 | 18:19 | 49.913
2020-08-31 | 18:19 | 49.909
2020-08-31 | 18:19 | 49.908
2020-08-31 | 18:19 | 49.903
2020-08-31 | 18:19 | 49.901
2020-08-31 | 18:19 | 49.899
2020-08-31 | 18:19 | 49.898
2020-08-31 | 18:19 | 49.896
2020-08-31 | 18:19 | 49.898
2020-08-31 | 18:19 | 49.898
2020-08-31 | 18:19 | 49.899
2020-08-31 | 18:19 | 49.9
2020-08-31 | 18:20 | 49.902
2020-08-31 | 18:20 | 49.906
2020-08-31 | 18:20 | 49.91
2020-08-31 | 18:20 | 49.912
2020-08-31 | 18:20 | 49.914
2020-08-31 | 18:20 | 49.918
2020-08-31 | 18:20 | 49.921
2020-08-31 | 18:20 | 49.926
2020-08-31 | 18:20 | 49.929
2020-08-31 | 18:20 | 49.931
2020-08-31 | 18:20 | 49.935
2020-08-31 | 18:20 | 49.938
2020-08-31 | 18:20 | 49.937
2020-08-31 | 18:20 | 49.936
2020-08-31 | 18:20 | 49.932
2020-08-31 | 18:20 | 49.929
2020-08-31 | 18:20 | 49.924
2020-08-31 | 18:20 | 49.92
2020-08-31 | 18:20 | 49.916
2020-08-31 | 18:20 | 49.914
2020-08-31 | 18:20 | 49.913
2020-08-31 | 18:20 | 49.912
2020-08-31 | 18:20 | 49.911
2020-08-31 | 18:20 | 49.912
2020-08-31 | 18:20 | 49.912
2020-08-31 | 18:20 | 49.913
2020-08-31 | 18:20 | 49.912
2020-08-31 | 18:20 | 49.909
2020-08-31 | 18:20 | 49.907
2020-08-31 | 18:20 | 49.905
2020-08-31 | 18:20 | 49.903
2020-08-31 | 18:20 | 49.9
2020-08-31 | 18:20 | 49.896
2020-08-31 | 18:20 | 49.893
2020-08-31 | 18:20 | 49.891
2020-08-31 | 18:20 | 49.89
2020-08-31 | 18:20 | 49.888
2020-08-31 | 18:20 | 49.887
2020-08-31 | 18:20 | 49.889
2020-08-31 | 18:20 | 49.892
2020-08-31 | 18:20 | 49.896
2020-08-31 | 18:20 | 49.903
2020-08-31 | 18:20 | 49.907
2020-08-31 | 18:20 | 49.912
2020-08-31 | 18:20 | 49.92
2020-08-31 | 18:20 | 49.924
2020-08-31 | 18:20 | 49.934
2020-08-31 | 18:20 | 49.938
2020-08-31 | 18:20 | 49.943
2020-08-31 | 18:20 | 49.945
2020-08-31 | 18:20 | 49.946
2020-08-31 | 18:20 | 49.946
2020-08-31 | 18:20 | 49.947
2020-08-31 | 18:20 | 49.945
2020-08-31 | 18:20 | 49.946
2020-08-31 | 18:20 | 49.947
2020-08-31 | 18:20 | 49.945
2020-08-31 | 18:20 | 49.947
2020-08-31 | 18:20 | 49.947
2020-08-31 | 18:20 | 49.945
2020-08-31 | 18:20 | 49.946
2020-08-31 | 18:21 | 49.944
2020-08-31 | 18:21 | 49.944
2020-08-31 | 18:21 | 49.945
2020-08-31 | 18:21 | 49.947
2020-08-31 | 18:21 | 49.95
2020-08-31 | 18:21 | 49.952
2020-08-31 | 18:21 | 49.955
2020-08-31 | 18:21 | 49.958
2020-08-31 | 18:21 | 49.96
2020-08-31 | 18:21 | 49.96
2020-08-31 | 18:21 | 49.961
2020-08-31 | 18:21 | 49.962
2020-08-31 | 18:21 | 49.962
2020-08-31 | 18:21 | 49.962
2020-08-31 | 18:21 | 49.963
2020-08-31 | 18:21 | 49.965
2020-08-31 | 18:21 | 49.967
2020-08-31 | 18:21 | 49.967
2020-08-31 | 18:21 | 49.966
2020-08-31 | 18:21 | 49.967
2020-08-31 | 18:21 | 49.966
2020-08-31 | 18:21 | 49.964
2020-08-31 | 18:21 | 49.962
2020-08-31 | 18:21 | 49.961
2020-08-31 | 18:21 | 49.96
2020-08-31 | 18:21 | 49.959
2020-08-31 | 18:21 | 49.959
2020-08-31 | 18:21 | 49.959
2020-08-31 | 18:21 | 49.958
2020-08-31 | 18:21 | 49.96
2020-08-31 | 18:21 | 49.964
2020-08-31 | 18:21 | 49.967
2020-08-31 | 18:21 | 49.969
2020-08-31 | 18:21 | 49.971
2020-08-31 | 18:21 | 49.969
2020-08-31 | 18:21 | 49.965
2020-08-31 | 18:21 | 49.962
2020-08-31 | 18:21 | 49.958
2020-08-31 | 18:21 | 49.954
2020-08-31 | 18:21 | 49.951
2020-08-31 | 18:21 | 49.948
2020-08-31 | 18:21 | 49.947
2020-08-31 | 18:21 | 49.947
2020-08-31 | 18:21 | 49.947
2020-08-31 | 18:21 | 49.948
2020-08-31 | 18:21 | 49.949
2020-08-31 | 18:21 | 49.948
2020-08-31 | 18:21 | 49.949
2020-08-31 | 18:21 | 49.949
2020-08-31 | 18:21 | 49.949
2020-08-31 | 18:21 | 49.947
2020-08-31 | 18:21 | 49.947
2020-08-31 | 18:21 | 49.946
2020-08-31 | 18:21 | 49.946
2020-08-31 | 18:21 | 49.945
2020-08-31 | 18:21 | 49.944
2020-08-31 | 18:21 | 49.943
2020-08-31 | 18:21 | 49.941
2020-08-31 | 18:21 | 49.939
2020-08-31 | 18:22 | 49.938
2020-08-31 | 18:22 | 49.939
2020-08-31 | 18:22 | 49.94
2020-08-31 | 18:22 | 49.943
2020-08-31 | 18:22 | 49.945
2020-08-31 | 18:22 | 49.947
2020-08-31 | 18:22 | 49.949
2020-08-31 | 18:22 | 49.95
2020-08-31 | 18:22 | 49.95
2020-08-31 | 18:22 | 49.95
2020-08-31 | 18:22 | 49.95
2020-08-31 | 18:22 | 49.949
2020-08-31 | 18:22 | 49.949
2020-08-31 | 18:22 | 49.949
2020-08-31 | 18:22 | 49.949
2020-08-31 | 18:22 | 49.949
2020-08-31 | 18:22 | 49.949
2020-08-31 | 18:22 | 49.948
2020-08-31 | 18:22 | 49.945
2020-08-31 | 18:22 | 49.943
2020-08-31 | 18:22 | 49.941
2020-08-31 | 18:22 | 49.941
2020-08-31 | 18:22 | 49.942
2020-08-31 | 18:22 | 49.944
2020-08-31 | 18:22 | 49.944
2020-08-31 | 18:22 | 49.945
2020-08-31 | 18:22 | 49.947
2020-08-31 | 18:22 | 49.947
2020-08-31 | 18:22 | 49.949
2020-08-31 | 18:22 | 49.95
2020-08-31 | 18:22 | 49.951
2020-08-31 | 18:22 | 49.95
2020-08-31 | 18:22 | 49.951
2020-08-31 | 18:22 | 49.95
2020-08-31 | 18:22 | 49.95
2020-08-31 | 18:22 | 49.949
2020-08-31 | 18:22 | 49.947
2020-08-31 | 18:22 | 49.945
2020-08-31 | 18:22 | 49.947
2020-08-31 | 18:22 | 49.948
2020-08-31 | 18:22 | 49.949
2020-08-31 | 18:22 | 49.951
2020-08-31 | 18:22 | 49.953
2020-08-31 | 18:22 | 49.956
2020-08-31 | 18:22 | 49.956
2020-08-31 | 18:22 | 49.957
2020-08-31 | 18:22 | 49.956
2020-08-31 | 18:22 | 49.954
2020-08-31 | 18:22 | 49.951
2020-08-31 | 18:22 | 49.95
2020-08-31 | 18:22 | 49.948
2020-08-31 | 18:22 | 49.947
2020-08-31 | 18:22 | 49.947
2020-08-31 | 18:22 | 49.947
2020-08-31 | 18:22 | 49.947
2020-08-31 | 18:22 | 49.948
2020-08-31 | 18:22 | 49.949
2020-08-31 | 18:22 | 49.951
2020-08-31 | 18:22 | 49.954
2020-08-31 | 18:22 | 49.957
2020-08-31 | 18:22 | 49.956
2020-08-31 | 18:23 | 49.955
2020-08-31 | 18:23 | 49.954
2020-08-31 | 18:23 | 49.953
2020-08-31 | 18:23 | 49.953
2020-08-31 | 18:23 | 49.95
2020-08-31 | 18:23 | 49.948
2020-08-31 | 18:23 | 49.946
2020-08-31 | 18:23 | 49.947
2020-08-31 | 18:23 | 49.949
2020-08-31 | 18:23 | 49.953
2020-08-31 | 18:23 | 49.956
2020-08-31 | 18:23 | 49.959
2020-08-31 | 18:23 | 49.963
2020-08-31 | 18:23 | 49.969
2020-08-31 | 18:23 | 49.973
2020-08-31 | 18:23 | 49.978
2020-08-31 | 18:23 | 49.982
2020-08-31 | 18:23 | 49.984
2020-08-31 | 18:23 | 49.985
2020-08-31 | 18:23 | 49.987
2020-08-31 | 18:23 | 49.986
2020-08-31 | 18:23 | 49.985
2020-08-31 | 18:23 | 49.983
2020-08-31 | 18:23 | 49.981
2020-08-31 | 18:23 | 49.979
2020-08-31 | 18:23 | 49.978
2020-08-31 | 18:23 | 49.978
2020-08-31 | 18:23 | 49.978
2020-08-31 | 18:23 | 49.977
2020-08-31 | 18:23 | 49.976
2020-08-31 | 18:23 | 49.975
2020-08-31 | 18:23 | 49.972
2020-08-31 | 18:23 | 49.971
2020-08-31 | 18:23 | 49.969
2020-08-31 | 18:23 | 49.966
2020-08-31 | 18:23 | 49.964
2020-08-31 | 18:23 | 49.961
2020-08-31 | 18:23 | 49.96
2020-08-31 | 18:23 | 49.96
2020-08-31 | 18:23 | 49.961
2020-08-31 | 18:23 | 49.962
2020-08-31 | 18:23 | 49.964
2020-08-31 | 18:23 | 49.965
2020-08-31 | 18:23 | 49.967
2020-08-31 | 18:23 | 49.97
2020-08-31 | 18:23 | 49.973
2020-08-31 | 18:23 | 49.976
2020-08-31 | 18:23 | 49.979
2020-08-31 | 18:23 | 49.981
2020-08-31 | 18:23 | 49.983
2020-08-31 | 18:23 | 49.986
2020-08-31 | 18:23 | 49.985
2020-08-31 | 18:23 | 49.984
2020-08-31 | 18:23 | 49.982
2020-08-31 | 18:23 | 49.981
2020-08-31 | 18:23 | 49.978
2020-08-31 | 18:23 | 49.975
2020-08-31 | 18:23 | 49.973
2020-08-31 | 18:23 | 49.971
2020-08-31 | 18:23 | 49.969
2020-08-31 | 18:24 | 49.969
2020-08-31 | 18:24 | 49.97
2020-08-31 | 18:24 | 49.973
2020-08-31 | 18:24 | 49.973
2020-08-31 | 18:24 | 49.972
2020-08-31 | 18:24 | 49.971
2020-08-31 | 18:24 | 49.971
2020-08-31 | 18:24 | 49.971
2020-08-31 | 18:24 | 49.969
2020-08-31 | 18:24 | 49.968
2020-08-31 | 18:24 | 49.967
2020-08-31 | 18:24 | 49.968
2020-08-31 | 18:24 | 49.967
2020-08-31 | 18:24 | 49.966
2020-08-31 | 18:24 | 49.964
2020-08-31 | 18:24 | 49.962
2020-08-31 | 18:24 | 49.96
2020-08-31 | 18:24 | 49.957
2020-08-31 | 18:24 | 49.955
2020-08-31 | 18:24 | 49.955
2020-08-31 | 18:24 | 49.957
2020-08-31 | 18:24 | 49.956
2020-08-31 | 18:24 | 49.96
2020-08-31 | 18:24 | 49.963
2020-08-31 | 18:24 | 49.966
2020-08-31 | 18:24 | 49.972
2020-08-31 | 18:24 | 49.976
2020-08-31 | 18:24 | 49.979
2020-08-31 | 18:24 | 49.984
2020-08-31 | 18:24 | 49.985
2020-08-31 | 18:24 | 49.988
2020-08-31 | 18:24 | 49.989
2020-08-31 | 18:24 | 49.987
2020-08-31 | 18:24 | 49.987
2020-08-31 | 18:24 | 49.987
2020-08-31 | 18:24 | 49.987
2020-08-31 | 18:24 | 49.987
2020-08-31 | 18:24 | 49.987
2020-08-31 | 18:24 | 49.986
2020-08-31 | 18:24 | 49.985
2020-08-31 | 18:24 | 49.983
2020-08-31 | 18:24 | 49.98
2020-08-31 | 18:24 | 49.979
2020-08-31 | 18:24 | 49.979
2020-08-31 | 18:24 | 49.981
2020-08-31 | 18:24 | 49.982
2020-08-31 | 18:24 | 49.98
2020-08-31 | 18:24 | 49.979
2020-08-31 | 18:24 | 49.978
2020-08-31 | 18:24 | 49.976
2020-08-31 | 18:24 | 49.976
2020-08-31 | 18:24 | 49.976
2020-08-31 | 18:24 | 49.977
2020-08-31 | 18:24 | 49.977
2020-08-31 | 18:24 | 49.978
2020-08-31 | 18:24 | 49.977
2020-08-31 | 18:24 | 49.979
2020-08-31 | 18:24 | 49.979
2020-08-31 | 18:24 | 49.981
2020-08-31 | 18:25 | 49.983
2020-08-31 | 18:25 | 49.985
2020-08-31 | 18:25 | 49.986
2020-08-31 | 18:25 | 49.986
2020-08-31 | 18:25 | 49.985
2020-08-31 | 18:25 | 49.983
2020-08-31 | 18:25 | 49.982
2020-08-31 | 18:25 | 49.981
2020-08-31 | 18:25 | 49.979
2020-08-31 | 18:25 | 49.981
2020-08-31 | 18:25 | 49.98
2020-08-31 | 18:25 | 49.98
2020-08-31 | 18:25 | 49.981
2020-08-31 | 18:25 | 49.983
2020-08-31 | 18:25 | 49.983
2020-08-31 | 18:25 | 49.982
2020-08-31 | 18:25 | 49.98
2020-08-31 | 18:25 | 49.978
2020-08-31 | 18:25 | 49.974
2020-08-31 | 18:25 | 49.97
2020-08-31 | 18:25 | 49.965
2020-08-31 | 18:25 | 49.96
2020-08-31 | 18:25 | 49.957
2020-08-31 | 18:25 | 49.956
2020-08-31 | 18:25 | 49.955
2020-08-31 | 18:25 | 49.956
2020-08-31 | 18:25 | 49.958
2020-08-31 | 18:25 | 49.96
2020-08-31 | 18:25 | 49.959
2020-08-31 | 18:25 | 49.958
2020-08-31 | 18:25 | 49.953
2020-08-31 | 18:25 | 49.946
2020-08-31 | 18:25 | 49.937
2020-08-31 | 18:25 | 49.93
2020-08-31 | 18:25 | 49.919
2020-08-31 | 18:25 | 49.912
2020-08-31 | 18:25 | 49.904
2020-08-31 | 18:25 | 49.897
2020-08-31 | 18:25 | 49.893
2020-08-31 | 18:25 | 49.89
2020-08-31 | 18:25 | 49.887
2020-08-31 | 18:25 | 49.887
2020-08-31 | 18:25 | 49.887
2020-08-31 | 18:25 | 49.887
2020-08-31 | 18:25 | 49.887
2020-08-31 | 18:25 | 49.887
2020-08-31 | 18:25 | 49.886
2020-08-31 | 18:25 | 49.883
2020-08-31 | 18:25 | 49.88
2020-08-31 | 18:25 | 49.88
2020-08-31 | 18:25 | 49.879
2020-08-31 | 18:25 | 49.879
2020-08-31 | 18:25 | 49.878
2020-08-31 | 18:25 | 49.877
2020-08-31 | 18:25 | 49.878
2020-08-31 | 18:25 | 49.879
2020-08-31 | 18:25 | 49.879
2020-08-31 | 18:25 | 49.876
2020-08-31 | 18:25 | 49.876
2020-08-31 | 18:25 | 49.874
2020-08-31 | 18:25 | 49.876
2020-08-31 | 18:26 | 49.877
2020-08-31 | 18:26 | 49.879
2020-08-31 | 18:26 | 49.879
2020-08-31 | 18:26 | 49.879
2020-08-31 | 18:26 | 49.878
2020-08-31 | 18:26 | 49.879
2020-08-31 | 18:26 | 49.876
2020-08-31 | 18:26 | 49.876
2020-08-31 | 18:26 | 49.878
2020-08-31 | 18:26 | 49.881
2020-08-31 | 18:26 | 49.885
2020-08-31 | 18:26 | 49.889
2020-08-31 | 18:26 | 49.893
2020-08-31 | 18:26 | 49.895
2020-08-31 | 18:26 | 49.897
2020-08-31 | 18:26 | 49.896
2020-08-31 | 18:26 | 49.899
2020-08-31 | 18:26 | 49.899
2020-08-31 | 18:26 | 49.9
2020-08-31 | 18:26 | 49.898
2020-08-31 | 18:26 | 49.898
2020-08-31 | 18:26 | 49.895
2020-08-31 | 18:26 | 49.897
2020-08-31 | 18:26 | 49.895
2020-08-31 | 18:26 | 49.895
2020-08-31 | 18:26 | 49.891
2020-08-31 | 18:26 | 49.89
2020-08-31 | 18:26 | 49.888
2020-08-31 | 18:26 | 49.888
2020-08-31 | 18:26 | 49.888
2020-08-31 | 18:26 | 49.888
2020-08-31 | 18:26 | 49.888
2020-08-31 | 18:26 | 49.888
2020-08-31 | 18:26 | 49.889
2020-08-31 | 18:26 | 49.888
2020-08-31 | 18:26 | 49.89
2020-08-31 | 18:26 | 49.891
2020-08-31 | 18:26 | 49.893
2020-08-31 | 18:26 | 49.894
2020-08-31 | 18:26 | 49.897
2020-08-31 | 18:26 | 49.898
2020-08-31 | 18:26 | 49.896
2020-08-31 | 18:26 | 49.897
2020-08-31 | 18:26 | 49.898
2020-08-31 | 18:26 | 49.899
2020-08-31 | 18:26 | 49.9
2020-08-31 | 18:26 | 49.903
2020-08-31 | 18:26 | 49.904
2020-08-31 | 18:26 | 49.903
2020-08-31 | 18:26 | 49.904
2020-08-31 | 18:26 | 49.902
2020-08-31 | 18:26 | 49.901
2020-08-31 | 18:26 | 49.898
2020-08-31 | 18:26 | 49.897
2020-08-31 | 18:26 | 49.897
2020-08-31 | 18:26 | 49.898
2020-08-31 | 18:26 | 49.9
2020-08-31 | 18:26 | 49.899
2020-08-31 | 18:26 | 49.899
2020-08-31 | 18:27 | 49.899
2020-08-31 | 18:27 | 49.898
2020-08-31 | 18:27 | 49.897
2020-08-31 | 18:27 | 49.897
2020-08-31 | 18:27 | 49.898
2020-08-31 | 18:27 | 49.901
2020-08-31 | 18:27 | 49.904
2020-08-31 | 18:27 | 49.905
2020-08-31 | 18:27 | 49.904
2020-08-31 | 18:27 | 49.904
2020-08-31 | 18:27 | 49.901
2020-08-31 | 18:27 | 49.9
2020-08-31 | 18:27 | 49.897
2020-08-31 | 18:27 | 49.895
2020-08-31 | 18:27 | 49.892
2020-08-31 | 18:27 | 49.89
2020-08-31 | 18:27 | 49.89
2020-08-31 | 18:27 | 49.89
2020-08-31 | 18:27 | 49.893
2020-08-31 | 18:27 | 49.895
2020-08-31 | 18:27 | 49.9
2020-08-31 | 18:27 | 49.902
2020-08-31 | 18:27 | 49.906
2020-08-31 | 18:27 | 49.909
2020-08-31 | 18:27 | 49.911
2020-08-31 | 18:27 | 49.911
2020-08-31 | 18:27 | 49.91
2020-08-31 | 18:27 | 49.907
2020-08-31 | 18:27 | 49.906
2020-08-31 | 18:27 | 49.904
2020-08-31 | 18:27 | 49.902
2020-08-31 | 18:27 | 49.899
2020-08-31 | 18:27 | 49.896
2020-08-31 | 18:27 | 49.894
2020-08-31 | 18:27 | 49.891
2020-08-31 | 18:27 | 49.89
2020-08-31 | 18:27 | 49.888
2020-08-31 | 18:27 | 49.89
2020-08-31 | 18:27 | 49.892
2020-08-31 | 18:27 | 49.896
2020-08-31 | 18:27 | 49.902
2020-08-31 | 18:27 | 49.908
2020-08-31 | 18:27 | 49.914
2020-08-31 | 18:27 | 49.921
2020-08-31 | 18:27 | 49.928
2020-08-31 | 18:27 | 49.936
2020-08-31 | 18:27 | 49.941
2020-08-31 | 18:27 | 49.944
2020-08-31 | 18:27 | 49.946
2020-08-31 | 18:27 | 49.949
2020-08-31 | 18:27 | 49.949
2020-08-31 | 18:27 | 49.95
2020-08-31 | 18:27 | 49.953
2020-08-31 | 18:27 | 49.953
2020-08-31 | 18:27 | 49.955
2020-08-31 | 18:27 | 49.954
2020-08-31 | 18:27 | 49.954
2020-08-31 | 18:27 | 49.954
2020-08-31 | 18:27 | 49.954
2020-08-31 | 18:27 | 49.954
2020-08-31 | 18:27 | 49.955
2020-08-31 | 18:28 | 49.956
2020-08-31 | 18:28 | 49.958
2020-08-31 | 18:28 | 49.96
2020-08-31 | 18:28 | 49.961
2020-08-31 | 18:28 | 49.964
2020-08-31 | 18:28 | 49.967
2020-08-31 | 18:28 | 49.968
2020-08-31 | 18:28 | 49.971
2020-08-31 | 18:28 | 49.973
2020-08-31 | 18:28 | 49.975
2020-08-31 | 18:28 | 49.975
2020-08-31 | 18:28 | 49.975
2020-08-31 | 18:28 | 49.975
2020-08-31 | 18:28 | 49.975
2020-08-31 | 18:28 | 49.977
2020-08-31 | 18:28 | 49.977
2020-08-31 | 18:28 | 49.978
2020-08-31 | 18:28 | 49.98
2020-08-31 | 18:28 | 49.98
2020-08-31 | 18:28 | 49.98
2020-08-31 | 18:28 | 49.978
2020-08-31 | 18:28 | 49.977
2020-08-31 | 18:28 | 49.974
2020-08-31 | 18:28 | 49.969
2020-08-31 | 18:28 | 49.966
2020-08-31 | 18:28 | 49.964
2020-08-31 | 18:28 | 49.963
2020-08-31 | 18:28 | 49.962
2020-08-31 | 18:28 | 49.962
2020-08-31 | 18:28 | 49.962
2020-08-31 | 18:28 | 49.961
2020-08-31 | 18:28 | 49.961
2020-08-31 | 18:28 | 49.96
2020-08-31 | 18:28 | 49.958
2020-08-31 | 18:28 | 49.956
2020-08-31 | 18:28 | 49.954
2020-08-31 | 18:28 | 49.952
2020-08-31 | 18:28 | 49.951
2020-08-31 | 18:28 | 49.951
2020-08-31 | 18:28 | 49.95
2020-08-31 | 18:28 | 49.95
2020-08-31 | 18:28 | 49.951
2020-08-31 | 18:28 | 49.95
2020-08-31 | 18:28 | 49.95
2020-08-31 | 18:28 | 49.95
2020-08-31 | 18:28 | 49.951
2020-08-31 | 18:28 | 49.95
2020-08-31 | 18:28 | 49.949
2020-08-31 | 18:28 | 49.95
2020-08-31 | 18:28 | 49.95
2020-08-31 | 18:28 | 49.951
2020-08-31 | 18:28 | 49.949
2020-08-31 | 18:28 | 49.948
2020-08-31 | 18:28 | 49.946
2020-08-31 | 18:28 | 49.946
2020-08-31 | 18:28 | 49.946
2020-08-31 | 18:28 | 49.946
2020-08-31 | 18:28 | 49.944
2020-08-31 | 18:28 | 49.944
2020-08-31 | 18:29 | 49.945
2020-08-31 | 18:29 | 49.945
2020-08-31 | 18:29 | 49.944
2020-08-31 | 18:29 | 49.944
2020-08-31 | 18:29 | 49.945
2020-08-31 | 18:29 | 49.947
2020-08-31 | 18:29 | 49.947
2020-08-31 | 18:29 | 49.948
2020-08-31 | 18:29 | 49.948
2020-08-31 | 18:29 | 49.947
2020-08-31 | 18:29 | 49.947
2020-08-31 | 18:29 | 49.946
2020-08-31 | 18:29 | 49.944
2020-08-31 | 18:29 | 49.942
2020-08-31 | 18:29 | 49.941
2020-08-31 | 18:29 | 49.94
2020-08-31 | 18:29 | 49.939
2020-08-31 | 18:29 | 49.94
2020-08-31 | 18:29 | 49.94
2020-08-31 | 18:29 | 49.942
2020-08-31 | 18:29 | 49.942
2020-08-31 | 18:29 | 49.942
2020-08-31 | 18:29 | 49.94
2020-08-31 | 18:29 | 49.94
2020-08-31 | 18:29 | 49.94
2020-08-31 | 18:29 | 49.939
2020-08-31 | 18:29 | 49.938
2020-08-31 | 18:29 | 49.937
2020-08-31 | 18:29 | 49.934
2020-08-31 | 18:29 | 49.934
2020-08-31 | 18:29 | 49.93
2020-08-31 | 18:29 | 49.929
2020-08-31 | 18:29 | 49.924
2020-08-31 | 18:29 | 49.923
2020-08-31 | 18:29 | 49.92
2020-08-31 | 18:29 | 49.92
2020-08-31 | 18:29 | 49.919
2020-08-31 | 18:29 | 49.918
2020-08-31 | 18:29 | 49.917
2020-08-31 | 18:29 | 49.916
2020-08-31 | 18:29 | 49.918
2020-08-31 | 18:29 | 49.918
2020-08-31 | 18:29 | 49.919
2020-08-31 | 18:29 | 49.917
2020-08-31 | 18:29 | 49.917
2020-08-31 | 18:29 | 49.917
2020-08-31 | 18:29 | 49.915
2020-08-31 | 18:29 | 49.913
2020-08-31 | 18:29 | 49.912
2020-08-31 | 18:29 | 49.914
2020-08-31 | 18:29 | 49.917
2020-08-31 | 18:29 | 49.921
2020-08-31 | 18:29 | 49.925
2020-08-31 | 18:29 | 49.929
2020-08-31 | 18:29 | 49.933
2020-08-31 | 18:29 | 49.937
2020-08-31 | 18:29 | 49.94
2020-08-31 | 18:29 | 49.944
2020-08-31 | 18:29 | 49.947
2020-08-31 | 18:29 | 49.95
2020-08-31 | 18:29 | 49.956
2020-08-31 | 18:30 | 49.962
2020-08-31 | 18:30 | 49.967
2020-08-31 | 18:30 | 49.97
2020-08-31 | 18:30 | 49.973
2020-08-31 | 18:30 | 49.975
2020-08-31 | 18:30 | 49.977
2020-08-31 | 18:30 | 49.98
2020-08-31 | 18:30 | 49.98
2020-08-31 | 18:30 | 49.98
2020-08-31 | 18:30 | 49.982
2020-08-31 | 18:30 | 49.986
2020-08-31 | 18:30 | 49.988
2020-08-31 | 18:30 | 49.993
2020-08-31 | 18:30 | 49.995
2020-08-31 | 18:30 | 49.996
2020-08-31 | 18:30 | 49.999
2020-08-31 | 18:30 | 50
2020-08-31 | 18:30 | 50.003
2020-08-31 | 18:30 | 50.006
2020-08-31 | 18:30 | 50.006
2020-08-31 | 18:30 | 50.009
2020-08-31 | 18:30 | 50.012
2020-08-31 | 18:30 | 50.014
2020-08-31 | 18:30 | 50.017
2020-08-31 | 18:30 | 50.02
2020-08-31 | 18:30 | 50.021
2020-08-31 | 18:30 | 50.02
2020-08-31 | 18:30 | 50.022
2020-08-31 | 18:30 | 50.025
2020-08-31 | 18:30 | 50.028
2020-08-31 | 18:30 | 50.03
2020-08-31 | 18:30 | 50.03
2020-08-31 | 18:30 | 50.031
2020-08-31 | 18:30 | 50.032
2020-08-31 | 18:30 | 50.033
2020-08-31 | 18:30 | 50.034
2020-08-31 | 18:30 | 50.034
2020-08-31 | 18:30 | 50.034
2020-08-31 | 18:30 | 50.031
2020-08-31 | 18:30 | 50.032
2020-08-31 | 18:30 | 50.032
2020-08-31 | 18:30 | 50.033
2020-08-31 | 18:30 | 50.032
2020-08-31 | 18:30 | 50.034
2020-08-31 | 18:30 | 50.035
2020-08-31 | 18:30 | 50.035
2020-08-31 | 18:30 | 50.036
2020-08-31 | 18:30 | 50.035
2020-08-31 | 18:30 | 50.036
2020-08-31 | 18:30 | 50.036
2020-08-31 | 18:30 | 50.036
2020-08-31 | 18:30 | 50.035
2020-08-31 | 18:30 | 50.034
2020-08-31 | 18:30 | 50.033
2020-08-31 | 18:30 | 50.034
2020-08-31 | 18:30 | 50.036
2020-08-31 | 18:30 | 50.036
2020-08-31 | 18:30 | 50.036
2020-08-31 | 18:30 | 50.036
2020-08-31 | 18:31 | 50.035
2020-08-31 | 18:31 | 50.034
2020-08-31 | 18:31 | 50.035
2020-08-31 | 18:31 | 50.034
2020-08-31 | 18:31 | 50.035
2020-08-31 | 18:31 | 50.036
2020-08-31 | 18:31 | 50.038
2020-08-31 | 18:31 | 50.038
2020-08-31 | 18:31 | 50.039
2020-08-31 | 18:31 | 50.041
2020-08-31 | 18:31 | 50.043
2020-08-31 | 18:31 | 50.042
2020-08-31 | 18:31 | 50.042
2020-08-31 | 18:31 | 50.039
2020-08-31 | 18:31 | 50.038
2020-08-31 | 18:31 | 50.034
2020-08-31 | 18:31 | 50.032
2020-08-31 | 18:31 | 50.03
2020-08-31 | 18:31 | 50.027
2020-08-31 | 18:31 | 50.026
2020-08-31 | 18:31 | 50.023
2020-08-31 | 18:31 | 50.02
2020-08-31 | 18:31 | 50.019
2020-08-31 | 18:31 | 50.018
2020-08-31 | 18:31 | 50.016
2020-08-31 | 18:31 | 50.017
2020-08-31 | 18:31 | 50.015
2020-08-31 | 18:31 | 50.015
2020-08-31 | 18:31 | 50.015
2020-08-31 | 18:31 | 50.016