BALANCING CODE NO. 5

(BC5)

PREQUALIFICATION PROCESSES

CONTENTS

(This contents page does not form part of the Grid Code)

Paragraph No/Title	Page Number

BC5.1  PREQUALIFICATION	2

BC5.1.1   Prequalification Timelines	3

BC5.2  FCR PREQUALIFICATION PROCESS	3

BC5.2.1  FCR Minimum Technical Requirements	3

BC5.3   FRR PREEQUALIFICATION PROCESS	5

BC5.3.1   FRR Minimum Technical Requirements	5

BC5.4   RR PREQUALIFICATION PROCESS	5

BC5.4.1   RR Minimum Technical Requirements	5

BC5.1	PREQUALIFCATION

The Company shall list the current status and dates of potential status changes of Balancing Services as Frequency Containment Reserves (FCR), Frequency Restoration Reserves (FRR) or Replacement Reserves (RR) or existing GB.

Where a Balancing Service has been approved as a Standard Product or Specific Product providing FCR, FRR or RR, The Company shall ensure that prequalification processes for that Balancing Service follows the processes as set out here. The Company shall ensure that each relevant Balancing Service requires a formal application from the FCR, FRR or RR provider to prequalify.

Where the Connection Conditions or European Connection Conditions require the capability as a condition of connection, the connection application may be understood to fulfil this formal application if so requested by the connecting party. For the avoidance of doubt, this does not compel a party to pre-qualify as part of their connection conditions.

BC5.1.1        Prequalification Timelines

BC5.1.1.1    The following minimum timescales shall be apply to the FCR, FRR and RR

prequalification processes;

- Within 8 weeks of a formal application from the FCR, FRR or RR provider The Company shall confirm the application is complete or incomplete (from the perspective of information provision)

- If the application is incomplete the FCR, FRR, or RR provider shall submit the additional required information within 4 weeks of a request from The Company or it will be presumed that the application has been withdrawn.

- For units connected to distribution networks, The Company shall liaise with the relevant DNO(s) to identify potential limitations imposed on the proposed Balancing Services Provider by the distribution networks.

- Within 3 months of confirming that all information has been provided, The Company shall confirm if the potential FCR, FRR or RR provider meets the requirements in BC5.2.1, BC5.3.1 or BC5.4.1 respectively.

BC5.1.1.2	The Company shall re-assess the qualification of FCR, FRR or RR

providing units or groups:

- at least once every 5 years;

- in case the technical or availability requirements or the equipment has changed; and

- in the case of FCR providing units or groups, in case of modernisation of the equipment related to FCR activation.

BC5.2	FCR PREQUALIFICATION PROCESS

The Company shall ensure that each relevant Balancing Service prequalification process shall, as a minimum, require the FCR provider to submit a self-certification of the FCR Minimum Technical Requirements as defined in BC5.2.1.

A transitional period for the introduction of FCR Minimum Technical Requirements, as defined in BC5.2.1 and BC5.2.2, shall apply for those FCR providers who are not an EU Code User.

BC5.2.1 	FCR Minimum Technical Requirements

Each FCR provider shall have the right to aggregate the respective data for more than one FCR providing unit if the maximum power of the aggregated units is below 1.5 MW and a clear verification of activation of FCR is possible.

Each FCR providing unit and each FCR providing group shall;

    - activate the agreed FCR by means of a proportional governor or load controller   reacting to Frequency deviations or alternatively based on a monotonic piecewise linear power-frequency characteristic in case of relay activated FCR.

    - be capable of activating FCR within the Frequency ranges specified in the in CC.6.1.3 or ECC.6.1.2.1.2.

    - and comply with the following properties

- Maximum combined effect of inherent Frequency Response Insensitivity and possible intentional Frequency Response Deadband of the governor or load controller of the FCR providing units or FCR providing groups of ±15 mHz

- FCR full activation time of 10 s

- FCR full activation Frequency deviation of ± 500 mHz

(d)     Specify the limitations of the energy reservoir of its FCR providing units or FCR.

(e)     Each FCR provider shall be capable of making available to The Company, for each of its FCR providing units and FCR providing groups, at least the following information:

- time-stamped status indicating if FCR is on or off;

- time-stamped active power data needed to verify FCR activation, including time-stamped instantaneous Active Power; and

- droop of the governor or load controller for Type C Power Generating Modules and Type D Power Generating Modules acting as FCR providing units, or its equivalent parameter for FCR providing groups consisting of Type A Power-Generating Modules and/or Type B Power Generating Modules, and/or Demand Units with Demand Response Active Power.

(f)        An FCR provider shall guarantee the continuous availability of FCR, with the exception of a forced outage of a FCR providing unit, during the period of time in which it is obliged to provide FCR.

(g)    Each FCR provider shall inform The Company, as soon as possible, about any changes in the actual availability of its FCR providing unit and/or its FCR providing group, in whole or in part, relevant for the results of this prequalification.

BC5.2.2         In addition to the requirements in BC5.2.1, where a relevant Balancing

Service is provided by reserve providing groups or units located in the distribution systems, The Company shall ensure that the prequalification process requires the following to be specified;

- voltage levels and connection points of the reserve providing units or groups;

- the DNO(s) who operate the distribution systems to which the reserve providing units or groups are connected;

- the type of Active Power reserves;

- the maximum reserve capacity provided by the reserve providing units or groups at each connection point; and

- the maximum rate of change of Active Power for the reserve providing units or groups.

The relevant DNOs will identify potential distribution network restrictions,  based on technical reasons, on the provision of the proposed Balancing Service by the reserve providing groups or units.

BC 5.3	FRR PREQUALIFICATION PROCESS

The Company shall ensure that each relevant Balancing Service prequalification process shall, as a minimum, require the FRR provider to submit a self-certification of the FRR Minimum Technical Requirements as defined in BC5.3.1 and BC5.3.2.

BC5.3.1	FRR Minimum Technical Requirements

Each FRR providing unit and each FRR providing group shall;

    - activate FRR in accordance with the setpoint received from The Company;

    - ensure that the FRR activation of the FRR providing units within a reserve  	providing group can be monitored. For that purpose the FRR provider shall be 	capable of supplying to The Company real-time measurements of the 	connection point or another point of interaction agreed with The Company  	concerning:

- time-stamped scheduled Active Power output;

- time-stamped instantaneous Active Power for: 
— each FRR providing unit,

— each FRR providing group, and

— each Power Generating Module or Demand unit of a FRR providing group with a maximum Active Power output larger than or equal to 1.5 MW;

(c) a FRR providing unit or FRR providing group for automatic FRR shall have an automatic FRR activation delay not exceeding 30 seconds;

(d) be capable of activating its complete manual reserve capacity on FRR within the FRR full activation time;

(e) fulfil the FRR availability requirements;

(f) fulfil the ramping rate requirements

(g) inform The Company about a reduction of the actual availability of its FRR providing unit or its FRR providing group or a part of its FRR providing group as soon as possible.

BC5.3.2	In addition to the requirements in BC5.3.1, where a relevant Balancing

Service is provided by reserve providing groups or units located in the distribution 			systems, The Company shall ensure that the prequalification process requires the 			following to be specified;

- voltage levels and connection points of the reserve providing units or groups;

- the DNO(s) who operate the distribution systems to which the reserve providing units or groups are connected;

- the type of Active Power reserves;

- themaximum reserve capacity provided by the reserve providing units or groups at each connection point; and

- the maximum rate of change of Active Power for the reserve providing units or group

The relevant DNOs will identify potential distribution network restrictions, based on technical reasons, on the provision of the proposed Balancing Service by the reserve providing groups or units.

BC5.4                RR PREQUALIFICATION PROCESS

The Company shall ensure that each relevant Balancing Service prequalification process shall, as a minimum, require the RR provider to submit a self-certification of the RR Minimum Technical Requirements as defined in BC5.4.1 and BC5.4.2.

BC5.4.1	RR Minimum Technical Requirements

Each RR providing unit and each RR providing group shall;

- activate RR in accordance with the setpoint received from The Company;

- ensure activation of complete reserve capacity on RR within the activation  time defined by The Company;

- ensure de-activation of RR according to the setpoint received from The Company;

- ensure that the RR activation of the RR providing units within a reserve providing group can be monitored. For that purpose, the RR provider shall  be capable of supplying to The Company real-time measurements of the connection point or another point of interaction agreed with The Company: 

(i)  	the time-stamped scheduled a Active Power output, for each RR providing unit 	and   group and for each Power Generating Module or Demand unit of 	a RR providing group with maximum Active Power output larger than or equal 

	to 1.5 MW;

(ii) 	the time-stamped instantaneous Active Power, for each RR providing  unit 	and group, and for each Power Generating Module or Demand unit of 	a RR providing group with a maximum Active Power output greater than or 	equal to 1.5 MW;

- ensure fulfilment of the RR availablity requirements

- inform The Company about a reduction of the actual availability or a forced outage of its RR providing unit or its RR providing group or a part of its RR providing group as soon as possible.

BC5.4.2	In addition to the requirements in BC5.4.1, where a relevant Balancing Service

is provided by a reserve providing groups or units located in the distribution systems, The Company shall ensure that the prequalification process requires the following to be specified;

- voltage levels and connection points of the reserve providing units or groups;

- the DNO(s) who operate the distribution systems to which the reserve providing units or groups are connected;

- the type of Active Power reserves;

- the maximum reserve capacity provided by the reserve providing units or groups at each connection point; and

- the maximum rate of change of Active Power for the reserve providing units or groups.

The relevant DNOs will identify potential distribution network restrictions on the provision of the proposed Balancing Service by the reserve providing groups or units.

< END OF BALANCING CODE 5 >