## Notes
Stability Pathfinder Phase Two
Short circuit level effectiveness factors V6
February 2021
Notes:
1 | Effectiveness factors show how effective a solution will be based on its location to provide short circuit current contribution to the ESO locations of need
2 | Short circuit current contribution is based on RMS transient value
3 | Effectiveness values for sites at voltages 132kV and above not covered by this list will be provided on request
4 | Compared to V1, V2 contains these key changes:
4a | Additional sites added based on RFI requests
4b | Some effectiveness values/sites are updated based on RFI feedback and consideration of network owner developments
Removed ROTI2, NEDE2 and added ROTI4, NEDE4, PEHE4
Updated Longannet and nearby area values
Updated some 132kV nodes near Moffat/ Elvanfoot 400kV
4c | Column L heading updated to 'Moffat/ Elvanfoot 400kV and nearby area' - previoulsy 275kV was stated incorrectly.
5 | Compared to V2, V3 contains these key changes:
5a | Updated Example sheet
6 | Compared to V3, V4 contains additional sheet on retained voltage values
6a | Example sheet updated to link with retained voltage values
7 | Compared to V4, V5 contains these key changes:
7a | Updated SCL effectiveness factors and retained voltage values for PEHE,ROTI,NEDE. We have updated these as we have discovered a modelling discrepancy.
The discrepency was caused due to the use of a different network model to calculate SCL effectiveness and retained voltage for these 3 sites, as our original model didn't have this 400kV network reinforcement. The model had some additional SCL injection/generation in the nearby area which caused the discrepency. No other sites or values are impacted by this.
7b | New Cumnock 132kV site added to SCL and retained voltage sheet.
8 | Compared to V5, V6 contains additional sites for effectiveness and retained voltages. There is no change to values from V5.

## Example
Example:
The following is an interactive example of how the effectiveness factors should be considered.
The Retained Voltage worksheet will provides each solution with 8 retained voltage values for their point of stability (POS)* corresponding to a fault at each of the 8 ESO locations of need. The provider should calculate the short circuit current contribution for the given retained voltage values. Each of the short circuit contributions will be multiplied by the effectiveness factors in this document to get the effective SCL that will be used in the commercial assessment. The example below shows this calculation.
The assessment methodology contains a full description of the commercial assessment.
| ESO to provide |  | How to use:
| Provider to provide |  | Enter the substation code of your solution here (refer to column C of effectiveness factors sheet)
Contribution to requirement
The substation where the solution has its POS | Connection Substation | LOAN2
The voltage of that substation (lookup cell) | Connection Substation Voltage (kV) | 275
|  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8
| Effectiveness Location Name | Blackhillock | Eccles | Hunterston | Logannet | Peterhead | Spittal | Mark Hill | Moffatt
| Effectiveness Location voltage | 400 | 400 | 400 | 275 | 275 | 275 | 275 | 400
From Retaind voltage table (v4) | Retained Voltage at POS for a fault at given effectiveness location (p.u.) | 0.75 | 0.65 | 0.48 | 0 | 0.76 | 0.92 | 0.7 | 0.52
Provider to provide fault contribution at its point of Stability, for the given retained voltage. | Fault current in kA in response to a fault at given effectiveness location | 0.06 | 2.02 | 2.02 | 3.36 | 1.34 | 0.67 | 0.33 | 2.02
From Effectiveness Factors table (v4) | Effectiveness factor based on solution substation | 12% | 13% | 23% | 100% | 15% | 2% | 13% | 23%
| MVA Contribution | 4.9883 | 181.9346 | 321.8843 | 1600.4149 | 95.7391 | 6.3826 | 20.4339 | 321.8843
*Point of Stability is defined in the technical specification

## Effectiveness Factors
Effectiveness Location
Substation Location | Substation Code | Voltage Level | Blackhillock 400kV | Eccles 400kV | Hunterston 400kV | Longannet 275kV and nearby area | Peterhead 275kV | Spittal 275kV | Mark Hill/ Coylton 275kV and nearby area | Moffat/ Elvanfoot 400kV and nearby area
Arecleoch | AREC1 | 132 | 6% | 6% | 19% | 16% | 7% | 1% | 44% | 17%
Auchencrosh | AUCH2 | 275 | 7% | 14% | 43% | 35% | 9% | 1% | 100% | 39%
Auchenwynd | AUCW1 | 132 | 6% | 6% | 19% | 16% | 7% | 1% | 34% | 16%
Beatrice | BEAT4 | 400 | 100% | 8% | 13% | 60% | 71% | 6% | 8% | 13%
Beauly | BEAU1 | 132 | 13% | 2% | 4% | 16% | 14% | 6% | 3% | 4%
Beauly | BEAU2 | 275 | 23% | 5% | 9% | 38% | 24% | 12% | 6% | 9%
Blackhill | BLAH1 | 132 | 6% | 6% | 18% | 16% | 7% | 1% | 43% | 17%
Blackhillock | BLHI1 | 132 | 25% | 3% | 5% | 22% | 25% | 3% | 3% | 5%
Blackhillock | BLHI2 | 275 | 48% | 6% | 10% | 44% | 48% | 5% | 6% | 10%
Blackhillock | BLHI4 | 400 | 100% | 8% | 13% | 60% | 71% | 6% | 8% | 13%
Blacklaw Windfarm | BLKL1 | 132 | 6% | 6% | 10% | 17% | 7% | 1% | 7% | 13%
Blacklaw Extension | BLLX1 | 132 | 6% | 5% | 9% | 11% | 6% | 1% | 7% | 22%
Bonnybridge | BONN1 | 132 | 8% | 6% | 11% | 39% | 10% | 1% | 6% | 10%
Braehead Park | BRAP1 | 132 | 7% | 6% | 20% | 22% | 7% | 1% | 10% | 14%
Branxton | BRNX4 | 400 | 6% | 45% | 12% | 22% | 7% | 1% | 9% | 19%
Busby | BUSB2 | 275 | 8% | 13% | 34% | 48% | 10% | 1% | 20% | 32%
Chapelcross | CHAP1 | 132 | 5% | 3% | 4% | 6% | 6% | 1% | 3% | 15%
Charleston | CHAR1 | 132 | 10% | 4% | 7% | 27% | 14% | 2% | 4% | 6%
Clyde's Mill | CLYM2 | 275 | 9% | 13% | 29% | 55% | 11% | 2% | 18% | 32%
Clyde North | CLYN2 | 275 | 6% | 9% | 14% | 17% | 7% | 1% | 11% | 59%
Clyde South | CLYS2 | 275 | 6% | 9% | 14% | 17% | 7% | 1% | 11% | 58%
Coalburn | COAL1 | 132 | 6% | 6% | 10% | 12% | 6% | 1% | 7% | 31%
Coalburn | COAL4 | 400 | 7% | 17% | 31% | 34% | 9% | 1% | 22% | 100%
Coatbridge | COAT2 | 275 | 8% | 14% | 26% | 49% | 10% | 1% | 17% | 31%
Cockenzie | COCK2 | 275 | 7% | 29% | 12% | 35% | 9% | 1% | 8% | 16%
Coylton | COYL1 | 132 | 6% | 6% | 20% | 17% | 7% | 1% | 37% | 17%
Coylton | COYL2 | 275 | 7% | 13% | 41% | 34% | 9% | 1% | 100% | 38%
Craigiebuckler | CRAI1 | 132 | 19% | 3% | 5% | 23% | 30% | 2% | 3% | 5%
Crookston | CROO1 | 132 | 6% | 6% | 20% | 21% | 7% | 1% | 10% | 14%
Crystal Rigg | CRYR4 | 400 | 7% | 42% | 13% | 24% | 8% | 1% | 10% | 21%
Currie | CURR2 | 275 | 8% | 24% | 13% | 48% | 10% | 1% | 9% | 17%
Dalmally | DALL2 | 275 | 9% | 10% | 29% | 51% | 11% | 2% | 15% | 22%
Denny North | DENN2 | 275 | 12% | 12% | 24% | 100% | 14% | 2% | 14% | 22%
Denny North | DENN4 | 400 | 17% | 13% | 26% | 100% | 20% | 5% | 15% | 24%
Devol Moor | DEVM4 | 400 | 10% | 17% | 66% | 66% | 13% | 2% | 30% | 42%
Devonside | DEVO1 | 132 | 8% | 5% | 10% | 38% | 10% | 1% | 6% | 10%
Dounreay | DOUN1 | 132 | 10% | 2% | 3% | 12% | 11% | 34% | 2% | 3%
Dounreay | DOUN2 | 275 | 16% | 3% | 6% | 25% | 17% | 78% | 4% | 6%
Eccles | ECCL1 | 132 | 5% | 18% | 4% | 9% | 6% | 1% | 3% | 6%
Eccles | ECCL4 | 400 | 6% | 100% | 10% | 20% | 7% | 1% | 7% | 16%
Easterhouse | EERH2 | 275 | 9% | 14% | 27% | 58% | 11% | 2% | 17% | 31%
East Kilbride South | EKIS2 | 275 | 8% | 13% | 32% | 48% | 10% | 1% | 19% | 33%
Elvanfoot | ELVA1 | 132 | 5% | 4% | 7% | 9% | 6% | 1% | 5% | 27%
Elvanfoot | ELVA2 | 275 | 6% | 9% | 14% | 17% | 7% | 1% | 11% | 58%
Elvanfoot | ELVA4 | 400 | 7% | 14% | 24% | 28% | 8% | 1% | 18% | 100%
Errochty | ERRO1 | 132 | 9% | 4% | 7% | 23% | 11% | 2% | 4% | 6%
Fallago | FALL4 | 400 | 7% | 39% | 15% | 28% | 8% | 1% | 11% | 23%
Fort Augustus | FAUG1 | 132 | 10% | 3% | 5% | 17% | 11% | 4% | 3% | 4%
Fort Augustus | FAUG2 | 275 | 18% | 6% | 11% | 41% | 19% | 8% | 6% | 10%
Fort Augustus | FAUG4 | 400 | 22% | 8% | 15% | 59% | 24% | 10% | 9% | 14%
Fettereso | FETT2 | 275 | 32% | 8% | 12% | 56% | 48% | 3% | 7% | 12%
Foyers | FOYE2 | 275 | 25% | 5% | 9% | 37% | 26% | 10% | 5% | 9%
Fyrish | FYRI1 | 132 | 13% | 2% | 4% | 17% | 13% | 10% | 3% | 4%
Fyrish | FYRI2 | 275 | 21% | 5% | 8% | 33% | 21% | 20% | 5% | 8%
Galashields | GALA1 | 132 | 6% | 17% | 4% | 10% | 6% | 1% | 3% | 6%
Glenglass | GLGL1 | 132 | 6% | 6% | 18% | 15% | 7% | 1% | 42% | 16%
Glenlee | GLLE1 | 132 | 6% | 5% | 14% | 12% | 6% | 1% | 33% | 13%
Glenrothes | GLRO2 | 275 | 15% | 11% | 19% | 82% | 19% | 2% | 11% | 19%
Gordonbush | GORW2 | 275 | 17.87% | 3.745% | 6.776% | 27.54% | 18.5% | 43.89% | 4.111% | 6.367%
Grangemouth | GRMO2 | 275 | 11% | 17% | 15% | 78% | 14% | 2% | 10% | 18%
Gretna | GRNA1 | 132 | 5% | 4% | 4% | 6% | 6% | 1% | 4% | 22%
Gretna | GRNA4 | 400 | 6% | 12% | 17% | 20% | 7% | 1% | 13% | 100%
Harestanes | HARE1 | 132 | 5% | 4% | 6% | 7% | 6% | 1% | 4% | 21%
Hunterston | HUER1 | 132 | 6% | 6% | 26% | 18% | 7% | 1% | 19% | 16%
Hunterston | HUER4 | 400 | 9% | 19% | 100% | 56% | 11% | 2% | 40% | 50%
Hunterston East | HUNE4 | 400 | 9% | 19% | 100% | 56% | 11% | 2% | 40% | 50%
Inveraray | INVE1 | 132 | 7% | 5% | 14% | 22% | 8% | 1% | 7% | 10%
Inverarnan | INVR2 | 275 | 9% | 10% | 29% | 51% | 11% | 2% | 15% | 22%
Kaimes | KAIM2 | 275 | 8% | 25% | 13% | 43% | 10% | 1% | 9% | 17%
Keith | KEIT1 | 132 | 20% | 3% | 4% | 19% | 21% | 3% | 3% | 4%
Keith | KEIT2 | 275 | 48% | 6% | 10% | 44% | 48% | 5% | 6% | 10%
Kendoon | KEOO1 | 132 | 6% | 5% | 14% | 13% | 6% | 1% | 33% | 13%
Killin | KIIN1 | 132 | 7% | 3% | 9% | 18% | 8% | 1% | 5% | 7%
Kilgalleoch | KILG2 | 275 | 7% | 13% | 42% | 35% | 9% | 1% | 100% | 39%
Kilmarnock South | KILS2 | 275 | 7% | 13% | 41% | 34% | 9% | 1% | 73% | 38%
Kilmarnock South | KILS4 | 400 | 9% | 19% | 59% | 50% | 10% | 1% | 53% | 55%
Kilmarnock Town | KILT2 | 275 | 7% | 13% | 41% | 34% | 9% | 1% | 72% | 38%
Kilwinning | KILW1 | 132 | 6% | 6% | 24% | 17% | 7% | 1% | 20% | 16%
Kincardine | KINC2 | 275 | 12% | 15% | 17% | 100% | 15% | 2% | 11% | 19%
Kintore | KINT2 | 275 | 38% | 7% | 11% | 50% | 59% | 4% | 7% | 11%
Knocknagael | KNOC2 | 275 | 25% | 5% | 9% | 38% | 26% | 11% | 6% | 9%
Lambhill | LAMB2 | 275 | 10% | 12% | 29% | 68% | 13% | 2% | 16% | 24%
Longannet | LOAN2 | 275 | 12% | 13% | 23% | 100% | 15% | 2% | 13% | 23%
Loch Buidhe | LOCB2 | 275 | 19% | 4% | 7% | 30% | 20% | 32% | 4% | 7%
Mark Hill | MAHI2 | 275 | 7% | 14% | 43% | 35% | 9% | 1% | 100% | 39%
Maybole | MAYB1 | 132 | 6% | 6% | 19% | 16% | 7% | 1% | 34% | 16%
Melgrave | MELG1 | 132 | 11% | 3% | 6% | 22% | 11% | 4% | 4% | 6%
Melgrave | MELG4 | 400 | 21% | 9% | 16% | 63% | 24% | 9% | 9% | 16%
Moffat | MOFF1 | 132 | 5% | 4% | 6% | 8% | 6% | 1% | 4% | 30%
Moffat | MOFF4 | 400 | 6% | 12% | 18% | 21% | 7% | 1% | 13% | 100%
Mossmorran | MOSM2 | 275 | 13% | 12% | 20% | 100% | 17% | 2% | 12% | 20%
Mybster | MYBS1 | 132 | 10% | 2% | 3% | 11% | 10% | 44% | 2% | 3%
Newarthill | NEAR2 | 275 | 8% | 14% | 26% | 49% | 10% | 1% | 17% | 32%
New Cumnock | NECU1 | 132 | 6% | 6% | 19% | 16% | 7% | 1% | 43% | 17%
New Cumnock | NECU2 | 275 | 7% | 13% | 41% | 33% | 9% | 1% | 100% | 37%
New Deer | NEDE4 | 400 | 83% | 12% | 19% | 61% | 100% | 7% | 11% | 19%
Neilston | NEIL1 | 132 | 7% | 6% | 21% | 22% | 7% | 1% | 10% | 15%
Neilston | NEIL2 | 275 | 8% | 13% | 41% | 48% | 10% | 1% | 21% | 32%
Neilston | NEIL4 | 400 | 9% | 18% | 83% | 58% | 11% | 2% | 36% | 48%
Newton Stewart | NETS1 | 132 | 6% | 4% | 13% | 12% | 6% | 1% | 30% | 12%
Partick | PART1 | 132 | 7% | 5% | 14% | 25% | 8% | 1% | 7% | 11%
Peterhead | PEHE1 | 132 | 23% | 4% | 7% | 21% | 44% | 2% | 4% | 7%
Peterhead | PEHE2 | 275 | 51% | 9% | 14% | 44% | 100% | 5% | 8% | 14%
Peterhead | PEHE4 | 400 | 80% | 12% | 19% | 61% | 100% | 7% | 11% | 19%
Redhouse | REDH1 | 132 | 9% | 5% | 10% | 39% | 11% | 1% | 6% | 9%
Rothienorman | ROTI4 | 400 | 86% | 12% | 19% | 62% | 92% | 7% | 11% | 19%
Shin | SHIN1 | 132 | 11% | 2% | 3% | 13% | 11% | 13% | 2% | 3%
Sloy | SLOY1 | 132 | 7% | 5% | 13% | 23% | 8% | 1% | 7% | 10%
Smeaton | SMEA2 | 275 | 8% | 27% | 12% | 37% | 9% | 1% | 9% | 17%
Spittal | SPIT1 | 132 | 10% | 2% | 3% | 12% | 10% | 43% | 2% | 3%
Spittal | SPIT2 | 275 | 16% | 3% | 6% | 24% | 16% | 100% | 4% | 5%
Strathaven | STHA2 | 275 | 8% | 13% | 31% | 50% | 10% | 1% | 19% | 33%
Strathaven | STHA4 | 400 | 8% | 20% | 38% | 47% | 10% | 1% | 30% | 59%
Tealing | TEAL1 | 132 | 11% | 4% | 7% | 27% | 14% | 2% | 4% | 6%
Tealing | TEAL2 | 275 | 20% | 10% | 15% | 71% | 28% | 3% | 9% | 16%
Thurso South | THUS1 | 132 | 10% | 2% | 3% | 12% | 11% | 41% | 2% | 3%
Thurso South | THUS2 | 275 | 16% | 3% | 6% | 24% | 17% | 89% | 4% | 5%
Tongland | TONG1 | 132 | 6% | 4% | 12% | 11% | 6% | 1% | 28% | 11%
Torness | TORN4 | 400 | 6% | 45% | 12% | 22% | 7% | 1% | 9% | 19%
Tummel | TUMM2 | 275 | 14% | 8% | 15% | 54% | 17% | 4% | 9% | 14%
Westfield | WFIE1 | 132 | 9% | 6% | 10% | 40% | 11% | 1% | 6% | 10%
Westfield | WFIE2 | 275 | 14% | 12% | 20% | 100% | 18% | 2% | 12% | 20%
Wishaw (Gowkthrapple) | WISH4 | 400 | 8% | 22% | 35% | 48% | 10% | 1% | 26% | 52%
Windyhill | WIYH1 | 132 | 7% | 5% | 14% | 26% | 8% | 1% | 8% | 11%
Windyhill | WIYH2 | 275 | 10% | 12% | 33% | 60% | 12% | 2% | 17% | 25%
Whitelee | WLEE2 | 275 | 8% | 13% | 32% | 48% | 10% | 1% | 19% | 33%
Whitelee Extension | WLEX2 | 275 | 8% | 13% | 32% | 48% | 10% | 1% | 19% | 33%

## Retained Voltages
Fault Location
Substation Location | Substation Code | Voltage Level | Blackhillock 400kV | Eccles 400kV | Hunterston 400kV | Longannet 275kV and nearby area | Peterhead 275kV | Spittal 275kV | Mark Hill/ Coylton 275kV and nearby area | Moffat/ Elvanfoot 400kV and nearby area
Arecleoch | AREC1 | 132 | 0.89 | 0.62 | 0.24 | 0.5 | 0.89 | 0.97 | 0.14 | 0.27
Auchencrosh | AUCH2 | 275 | 0.89 | 0.62 | 0.25 | 0.49 | 0.89 | 0.97 | 0 | 0.26
Auchenwynd | AUCW1 | 132 | 0.9 | 0.71 | 0.35 | 0.58 | 0.91 | 0.98 | 0.24 | 0.44
Beatrice | BEAT4 | 400 | 0 | 0.74 | 0.64 | 0.3 | 0.29 | 0.81 | 0.79 | 0.67
Beauly | BEAU1 | 132 | 0.51 | 0.79 | 0.7 | 0.44 | 0.58 | 0.69 | 0.83 | 0.73
Beauly | BEAU2 | 275 | 0.5 | 0.78 | 0.67 | 0.4 | 0.58 | 0.68 | 0.81 | 0.7
Blackhill | BLAH1 | 132 | 0.89 | 0.65 | 0.27 | 0.51 | 0.89 | 0.97 | 0 | 0.33
Blackhillock | BLHI1 | 132 | 0.21 | 0.74 | 0.65 | 0.32 | 0.34 | 0.79 | 0.79 | 0.67
Blackhillock | BLHI2 | 275 | 0.2 | 0.75 | 0.65 | 0.31 | 0.33 | 0.8 | 0.79 | 0.67
Blackhillock | BLHI4 | 400 | 0 | 0.73 | 0.64 | 0.3 | 0.29 | 0.8 | 0.78 | 0.66
Blacklaw Windfarm | BLKL1 | 132 | 0.9 | 0.73 | 0.6 | 0.58 | 0.9 | 0.98 | 0.74 | 0.55
Blacklaw Extension | BLLX1 | 132 | 0.91 | 0.66 | 0.49 | 0.59 | 0.91 | 0.98 | 0.66 | 0.15
Bonnybridge | BONN1 | 132 | 0.75 | 0.69 | 0.51 | 0.14 | 0.76 | 0.91 | 0.71 | 0.56
Braehead Park | BRAP1 | 132 | 0.85 | 0.67 | 0.23 | 0.39 | 0.85 | 0.95 | 0.6 | 0.42
Branxton | BRNX4 | 400 | 0.92 | 0.35 | 0.69 | 0.67 | 0.92 | 0.97 | 0.79 | 0.61
Busby | BUSB2 | 275 | 0.85 | 0.65 | 0.33 | 0.37 | 0.85 | 0.95 | 0.61 | 0.39
Chapelcross | CHAP1 | 132 | 0.94 | 0.74 | 0.7 | 0.75 | 0.94 | 0.98 | 0.79 | 0.33
Charleston | CHAR1 | 132 | 0.61 | 0.72 | 0.6 | 0.26 | 0.6 | 0.87 | 0.76 | 0.63
Clyde's Mill | CLYM2 | 275 | 0.84 | 0.65 | 0.41 | 0.32 | 0.84 | 0.95 | 0.64 | 0.41
Clyde North | CLYN2 | 275 | 0.92 | 0.69 | 0.56 | 0.64 | 0.92 | 0.98 | 0.7 | 0
Clyde South | CLYS2 | 275 | 0.9 | 0.68 | 0.55 | 0.63 | 0.9 | 0.96 | 0.68 | 0
Coalburn | COAL1 | 132 | 0.9 | 0.65 | 0.48 | 0.59 | 0.9 | 0.97 | 0.65 | 0
Coalburn | COAL4 | 400 | 0.91 | 0.66 | 0.48 | 0.59 | 0.91 | 0.98 | 0.65 | 0
Coatbridge | COAT2 | 275 | 0.85 | 0.64 | 0.44 | 0.36 | 0.85 | 0.95 | 0.64 | 0.4
Cockenzie | COCK2 | 275 | 0.88 | 0.41 | 0.65 | 0.47 | 0.88 | 0.97 | 0.78 | 0.59
Coylton | COYL1 | 132 | 0.9 | 0.69 | 0.31 | 0.55 | 0.9 | 0.98 | 0.19 | 0.4
Coylton | COYL2 | 275 | 0.89 | 0.65 | 0.26 | 0.51 | 0.89 | 0.97 | 0 | 0.33
Craigiebuckler | CRAI1 | 132 | 0.33 | 0.73 | 0.63 | 0.28 | 0.26 | 0.84 | 0.78 | 0.66
Crookston | CROO1 | 132 | 0.85 | 0.67 | 0.23 | 0.4 | 0.85 | 0.95 | 0.59 | 0.41
Crystal Rigg | CRYR4 | 400 | 0.91 | 0.37 | 0.67 | 0.64 | 0.91 | 0.97 | 0.78 | 0.59
Currie | CURR2 | 275 | 0.84 | 0.48 | 0.62 | 0.35 | 0.84 | 0.95 | 0.76 | 0.58
Dalmally | DALL2 | 275 | 0.83 | 0.71 | 0.39 | 0.33 | 0.83 | 0.95 | 0.68 | 0.52
Denny North | DENN2 | 275 | 0.75 | 0.67 | 0.47 | 0 | 0.76 | 0.91 | 0.7 | 0.53
Denny North | DENN4 | 400 | 0.69 | 0.7 | 0.52 | 0 | 0.71 | 0.85 | 0.72 | 0.57
Devol Moor | DEVM4 | 400 | 0.85 | 0.67 | 0.2 | 0.37 | 0.85 | 0.96 | 0.59 | 0.43
Devonside | DEVO1 | 132 | 0.75 | 0.69 | 0.53 | 0.14 | 0.75 | 0.92 | 0.72 | 0.57
Dounreay | DOUN1 | 132 | 0.6 | 0.83 | 0.75 | 0.52 | 0.66 | 0.13 | 0.86 | 0.77
Dounreay | DOUN2 | 275 | 0.57 | 0.81 | 0.73 | 0.5 | 0.64 | 0.11 | 0.84 | 0.75
Eccles | ECCL1 | 132 | 0.92 | 0.26 | 0.72 | 0.65 | 0.92 | 0.98 | 0.82 | 0.64
Eccles | ECCL4 | 400 | 0.92 | 0 | 0.73 | 0.68 | 0.92 | 0.98 | 0.82 | 0.64
Easterhouse | EERH2 | 275 | 0.83 | 0.65 | 0.43 | 0.29 | 0.83 | 0.95 | 0.65 | 0.42
East Kilbride South | EKIS2 | 275 | 0.86 | 0.65 | 0.36 | 0.37 | 0.86 | 0.96 | 0.63 | 0.39
Elvanfoot | ELVA1 | 132 | 0.9 | 0.68 | 0.55 | 0.63 | 0.9 | 0.95 | 0.68 | 0
Elvanfoot | ELVA2 | 275 | 0.92 | 0.69 | 0.56 | 0.64 | 0.92 | 0.98 | 0.7 | 0
Elvanfoot | ELVA4 | 400 | 0.92 | 0.69 | 0.56 | 0.64 | 0.92 | 0.98 | 0.7 | 0
Errochty | ERRO1 | 132 | 0.7 | 0.76 | 0.61 | 0.34 | 0.71 | 0.88 | 0.78 | 0.66
Fallago | FALL4 | 400 | 0.91 | 0.4 | 0.65 | 0.62 | 0.91 | 0.97 | 0.76 | 0.56
Fort Augustus | FAUG1 | 132 | 0.63 | 0.8 | 0.69 | 0.43 | 0.68 | 0.78 | 0.82 | 0.72
Fort Augustus | FAUG2 | 275 | 0.58 | 0.77 | 0.65 | 0.37 | 0.63 | 0.75 | 0.8 | 0.68
Fort Augustus | FAUG4 | 400 | 0.58 | 0.76 | 0.64 | 0.36 | 0.64 | 0.75 | 0.79 | 0.68
Fettereso | FETT2 | 275 | 0.37 | 0.71 | 0.61 | 0.23 | 0.34 | 0.85 | 0.77 | 0.63
Foyers | FOYE2 | 275 | 0.46 | 0.78 | 0.67 | 0.39 | 0.54 | 0.7 | 0.81 | 0.71
Fyrish | FYRI1 | 132 | 0.53 | 0.8 | 0.7 | 0.44 | 0.61 | 0.58 | 0.84 | 0.73
Fyrish | FYRI2 | 275 | 0.52 | 0.79 | 0.69 | 0.43 | 0.59 | 0.57 | 0.82 | 0.72
Galashields | GALA1 | 132 | 0.92 | 0.3 | 0.71 | 0.62 | 0.92 | 0.98 | 0.81 | 0.64
Glenglass | GLGL1 | 132 | 0.89 | 0.65 | 0.27 | 0.51 | 0.89 | 0.97 | 0 | 0.33
Glenlee | GLLE1 | 132 | 0.9 | 0.69 | 0.35 | 0.56 | 0.9 | 0.97 | 0.13 | 0.41
Glenrothes | GLRO2 | 275 | 0.68 | 0.67 | 0.53 | 0.09 | 0.67 | 0.9 | 0.72 | 0.56
Gordonbush | GORW2 | 275 | 0.56 | 0.81 | 0.72 | 0.48 | 0.62 | 0.34 | 0.84 | 0.75
Grangemouth | GRMO2 | 275 | 0.77 | 0.57 | 0.58 | 0.12 | 0.76 | 0.93 | 0.74 | 0.57
Gretna | GRNA1 | 132 | 0.94 | 0.74 | 0.69 | 0.74 | 0.94 | 0.98 | 0.78 | 0.18
Gretna | GRNA4 | 400 | 0.93 | 0.72 | 0.64 | 0.7 | 0.93 | 0.98 | 0.75 | 0
Harestanes | HARE1 | 132 | 0.94 | 0.73 | 0.63 | 0.7 | 0.94 | 0.99 | 0.75 | 0
Hunterston | HUER1 | 132 | 0.9 | 0.7 | 0.19 | 0.53 | 0.9 | 0.98 | 0.47 | 0.44
Hunterston | HUER4 | 400 | 0.87 | 0.66 | 0 | 0.45 | 0.87 | 0.97 | 0.52 | 0.36
Hunterston East | HUNE4 | 400 | 0.87 | 0.66 | 0 | 0.45 | 0.87 | 0.97 | 0.52 | 0.36
Inveraray | INVE1 | 132 | 0.84 | 0.72 | 0.4 | 0.39 | 0.84 | 0.95 | 0.69 | 0.55
Inverarnan | INVR2 | 275 | 0.82 | 0.71 | 0.4 | 0.33 | 0.83 | 0.95 | 0.68 | 0.52
Kaimes | KAIM2 | 275 | 0.85 | 0.46 | 0.63 | 0.4 | 0.85 | 0.96 | 0.77 | 0.58
Keith | KEIT1 | 132 | 0.3 | 0.77 | 0.68 | 0.37 | 0.42 | 0.78 | 0.81 | 0.7
Keith | KEIT2 | 275 | 0.2 | 0.75 | 0.65 | 0.32 | 0.34 | 0.8 | 0.8 | 0.68
Kendoon | KEOO1 | 132 | 0.9 | 0.69 | 0.35 | 0.56 | 0.9 | 0.97 | 0.12 | 0.4
Killin | KIIN1 | 132 | 0.82 | 0.76 | 0.54 | 0.44 | 0.83 | 0.94 | 0.75 | 0.63
Kilgalleoch | KILG2 | 275 | 0.89 | 0.62 | 0.24 | 0.5 | 0.89 | 0.97 | 0 | 0.27
Kilmarnock South | KILS2 | 275 | 0.89 | 0.65 | 0.26 | 0.51 | 0.89 | 0.97 | 0.16 | 0.32
Kilmarnock South | KILS4 | 400 | 0.88 | 0.64 | 0.26 | 0.49 | 0.89 | 0.97 | 0.43 | 0.32
Kilmarnock Town | KILT2 | 275 | 0.89 | 0.65 | 0.26 | 0.51 | 0.89 | 0.97 | 0.16 | 0.32
Kilwinning | KILW1 | 132 | 0.9 | 0.71 | 0.22 | 0.54 | 0.9 | 0.98 | 0.44 | 0.44
Kincardine | KINC2 | 275 | 0.74 | 0.6 | 0.55 | 0 | 0.74 | 0.92 | 0.73 | 0.56
Kintore | KINT2 | 275 | 0.29 | 0.72 | 0.62 | 0.26 | 0.26 | 0.83 | 0.78 | 0.65
Knocknagael | KNOC2 | 275 | 0.46 | 0.78 | 0.67 | 0.39 | 0.54 | 0.7 | 0.81 | 0.7
Lambhill | LAMB2 | 275 | 0.79 | 0.68 | 0.4 | 0.21 | 0.8 | 0.93 | 0.67 | 0.5
Longannet | LOAN2 | 275 | 0.75 | 0.65 | 0.48 | 0 | 0.76 | 0.92 | 0.7 | 0.52
Loch Buidhe | LOCB2 | 275 | 0.54 | 0.8 | 0.71 | 0.46 | 0.61 | 0.44 | 0.83 | 0.73
Mark Hill | MAHI2 | 275 | 0.89 | 0.62 | 0.24 | 0.49 | 0.89 | 0.97 | 0 | 0.27
Maybole | MAYB1 | 132 | 0.9 | 0.71 | 0.35 | 0.58 | 0.91 | 0.98 | 0.24 | 0.44
Melgrave | MELG1 | 132 | 0.6 | 0.76 | 0.63 | 0.34 | 0.65 | 0.77 | 0.79 | 0.67
Melgrave | MELG4 | 400 | 0.6 | 0.75 | 0.62 | 0.33 | 0.65 | 0.77 | 0.78 | 0.66
Moffat | MOFF1 | 132 | 0.94 | 0.73 | 0.63 | 0.7 | 0.94 | 0.99 | 0.75 | 0
Moffat | MOFF4 | 400 | 0.93 | 0.72 | 0.63 | 0.69 | 0.93 | 0.98 | 0.74 | 0
Mossmorran | MOSM2 | 275 | 0.71 | 0.67 | 0.51 | 0 | 0.71 | 0.91 | 0.71 | 0.54
Mybster | MYBS1 | 132 | 0.6 | 0.83 | 0.75 | 0.52 | 0.66 | 0.17 | 0.86 | 0.77
Newarthill | NEAR2 | 275 | 0.85 | 0.64 | 0.44 | 0.36 | 0.85 | 0.95 | 0.64 | 0.4
New Cumnock | NECU1 | 132 | 0.89 | 0.65 | 0.27 | 0.51 | 0.89 | 0.97 | 0 | 0.27
New Cumnock | NECU2 | 275 | 0.89 | 0.65 | 0.27 | 0.51 | 0.89 | 0.97 | 0 | 0.33
New Deer | NEDE4 | 400 | 0.09 | 0.75 | 0.67 | 0.26 | 0.17 | 0.82 | 0.81 | 0.68
Neilston | NEIL1 | 132 | 0.85 | 0.66 | 0.22 | 0.4 | 0.85 | 0.95 | 0.59 | 0.41
Neilston | NEIL2 | 275 | 0.85 | 0.66 | 0.26 | 0.37 | 0.85 | 0.96 | 0.6 | 0.4
Neilston | NEIL4 | 400 | 0.86 | 0.66 | 0.08 | 0.43 | 0.87 | 0.96 | 0.54 | 0.38
Newton Stewart | NETS1 | 132 | 0.9 | 0.7 | 0.36 | 0.57 | 0.9 | 0.97 | 0.14 | 0.42
Partick | PART1 | 132 | 0.83 | 0.71 | 0.41 | 0.34 | 0.83 | 0.94 | 0.69 | 0.54
Peterhead | PEHE1 | 132 | 0.2 | 0.76 | 0.68 | 0.3 | 0.05 | 0.83 | 0.82 | 0.69
Peterhead | PEHE2 | 275 | 0.15 | 0.75 | 0.67 | 0.26 | 0 | 0.82 | 0.81 | 0.68
Peterhead | PEHE4 | 400 | 0.11 | 0.75 | 0.67 | 0.26 | 0.13 | 0.82 | 0.81 | 0.68
Redhouse | REDH1 | 132 | 0.73 | 0.69 | 0.54 | 0.13 | 0.73 | 0.91 | 0.73 | 0.57
Rothienorman | ROTI4 | 400 | 0.08 | 0.75 | 0.66 | 0.26 | 0.21 | 0.81 | 0.81 | 0.68
Shin | SHIN1 | 132 | 0.58 | 0.83 | 0.74 | 0.51 | 0.65 | 0.51 | 0.86 | 0.77
Sloy | SLOY1 | 132 | 0.84 | 0.73 | 0.43 | 0.38 | 0.84 | 0.95 | 0.7 | 0.56
Smeaton | SMEA2 | 275 | 0.87 | 0.44 | 0.64 | 0.45 | 0.87 | 0.97 | 0.77 | 0.58
Spittal | SPIT1 | 132 | 0.6 | 0.83 | 0.75 | 0.53 | 0.66 | 0.16 | 0.86 | 0.77
Spittal | SPIT2 | 275 | 0.58 | 0.81 | 0.73 | 0.51 | 0.64 | 0 | 0.84 | 0.76
Strathaven | STHA2 | 275 | 0.85 | 0.65 | 0.38 | 0.36 | 0.85 | 0.95 | 0.62 | 0.39
Strathaven | STHA4 | 400 | 0.89 | 0.63 | 0.42 | 0.51 | 0.89 | 0.97 | 0.59 | 0.28
Tealing | TEAL1 | 132 | 0.6 | 0.71 | 0.59 | 0.25 | 0.59 | 0.87 | 0.75 | 0.62
Tealing | TEAL2 | 275 | 0.57 | 0.68 | 0.57 | 0.15 | 0.55 | 0.88 | 0.74 | 0.59
Thurso South | THUS1 | 132 | 0.6 | 0.84 | 0.75 | 0.53 | 0.66 | 0.07 | 0.86 | 0.78
Thurso South | THUS2 | 275 | 0.58 | 0.81 | 0.73 | 0.5 | 0.64 | 0.05 | 0.84 | 0.75
Tongland | TONG1 | 132 | 0.9 | 0.7 | 0.38 | 0.58 | 0.9 | 0.96 | 0.17 | 0.44
Torness | TORN4 | 400 | 0.92 | 0.35 | 0.69 | 0.67 | 0.92 | 0.97 | 0.79 | 0.61
Tummel | TUMM2 | 275 | 0.66 | 0.73 | 0.57 | 0.27 | 0.69 | 0.83 | 0.75 | 0.62
Westfield | WFIE1 | 132 | 0.73 | 0.69 | 0.53 | 0.12 | 0.73 | 0.91 | 0.73 | 0.57
Westfield | WFIE2 | 275 | 0.7 | 0.67 | 0.52 | 0 | 0.69 | 0.91 | 0.72 | 0.55
Wishaw (Gowkthrapple) | WISH4 | 400 | 0.88 | 0.61 | 0.46 | 0.5 | 0.88 | 0.97 | 0.62 | 0.34
Windyhill | WIYH1 | 132 | 0.83 | 0.71 | 0.41 | 0.34 | 0.83 | 0.94 | 0.69 | 0.54
Windyhill | WIYH2 | 275 | 0.81 | 0.68 | 0.36 | 0.27 | 0.82 | 0.94 | 0.66 | 0.49
Whitelee | WLEE2 | 275 | 0.86 | 0.65 | 0.36 | 0.37 | 0.86 | 0.96 | 0.63 | 0.39
Whitelee Extension | WLEX2 | 275 | 0.86 | 0.65 | 0.36 | 0.37 | 0.86 | 0.96 | 0.63 | 0.39