## Notes
Subject | Notes
System inertia: method of calculation | H=(f*∆P)/(2*RoCoF) H is system inertia; f is the starting frequency; ∆P is the system imbalance; RoCoF is the rate of change of frequency; Note that smaller losses will have less accurate system inertia calculations
RoCoF: method of calculation | RoCoF=(f_500ms-f_0ms)/500ms RoCoF is calculated using 500ms sliding window. RoCoF is the rate of change of frequency; f is the frequency; Note that smaller losses will have less accurate ROCOF calculations The RoCoF figure in this report is from external service
Voltage Dip | Transient Voltage Dip with loss % and duration measured at the local substation
'Immediately before the Significant Event' | The starting frequency indicated in the Frequency Event Report, for frequency excursions. Where there is no Frequency Event Report, NGESO will use its best judgement.
'Immediately after the Significant Event' | The maximum frequency deviation indicated in the Frequency Event Report, for frequency excursions. Where there is no Frequency Event Report, NGESO will use its best judgement.
Data 'N/A' | N/A: data not applicable or potentially unreliable. For example, there maybe events when the loss of infeed or exfeed is not instantaneous (over long time period), the calculated RoCoF value may not be indicative. For some events, during a disturbance the data may potentially be unreliable. NGESO will apply engineering judgement to determine whether the derived/calculated data is suitable for sharing.

## Report
|  |  |  | (i) the time(s) in hh.mm.ss of the Significant Event and any potentially related occurrences; | (ii) any known or reported loss of Embedded Power Station(s) with locations and ratings where available; | (iii) the Frequency record (in table and graphical format) at <=1 second intervals for 1 minute before and 1 minute after the Significant Event; | (iv) the Frequency (to 2 decimal places) immediately before the Significant Event; | (v) the Frequency (to 2 decimal places) immediately after the Significant Event; | (vi) the maximum rate of change of Frequency recorded during the Significant Event over a specified time period of 500ms; | (vii) where known, the MW of all individual losses or trips related to the Significant Event; |  | (viii) where known, the identity of the Users and Network Operator of all demand losses or trips related to the Significant Event; | (ix) the location of any reported Transmission fault on the network diagram and geographically; | (x) the extent of any voltage dip associated with the Significant Event; | (xi) an estimate of system inertia in GWs at the time of the Significant Event along with how it has been calculated; and | (xii) any other data available that is of value to gain a clearer understanding of the Significant Event and its potential implications; and
Event Ref | Event Name | Notes | Date (Local) | Time (Local) | Loss of Embedded Power Station | Frequency Record | Pre-Event Frequency | Post-Event Frequency | RoCoF over 500ms | Individual Loss | System Imbalance | Demand loss of Users/DNOs related to event | Location of transmission fault | Voltage Dip | System Inertia | Additional data
Event Date-Number | Text | Text | DD/MM/YYYY | hh:mm:ss | MW | Text | Hz | Hz | Hz/s | Text+MW | MW | Text+MW | Text | % | GWs | Text
Event 20210102-1 | Trip of SHOS-1 |  | 2021-01-02 | 9:30 | N/A | Refer to tab 'Event 20210102-1' | 49.976 | 49.833 | -0.0517 | 395 | -395 | N/A | N/A | N/A | 190.3678
Event 20210106-1 | Trip of SHBA-1 |  | 2021-01-06 | 2:20 | N/A | Refer to tab 'Event 20210106-1' | 50.11 | 49.868 | -0.06543 | 786 | -786 | N/A | N/A | N/A | 299.5281
Event 20210110-1 | Trip of DAMC-1 |  | 2021-01-10 | 10:25 | N/A | Refer to tab 'Event 20210110-1' | 49.889 | 49.795 | -0.02839 | 270 | -270 | N/A | N/A | N/A | 236.785
Event 20210115-1 | Trip of WBURB-1 |  | 2021-01-15 | 18:18 | N/A | Refer to tab 'Event 20210115-1' | 50.069 | 49.807 | -0.0189 | 250 | -250 | N/A | N/A | N/A | 329.4114
Event 20210116-1 | Trip of IFA 2 | tripped four times from 08:00 to 16:30 | 2021-01-16 | 08:00 to 16:30 | N/A | Refer to tab 'Event 20210116-1' | N/A | N/A | N/A | 500 and 710 and 500 and 1017 | -500 and 710 and 500 and 1017 | N/A | N/A | N/A | N/A
Event 20210123-1 | Trip of KEAD-1 |  | 2021-01-23 | 11:59 | N/A | Refer to tab 'Event 20210123-1' | 50.35 | 49.806 | -0.04935 | 292 | -292 | N/A | N/A | N/A | 147.3491
Event 20210129-1 | Trip of IFA 2 |  | 2021-01-29 | 6:08 | N/A | Refer to tab 'Event 20210129-1' | 49.9 | 49.631 | -0.12479 | 880 | -880 | N/A | N/A | N/A | 174.9951

## Event 20210102-1
In UTC
Date | Time | Freq
2021-01-02 | 9:28 | 50.045
2021-01-02 | 9:28 | 50.042
2021-01-02 | 9:28 | 50.041
2021-01-02 | 9:28 | 50.04
2021-01-02 | 9:28 | 50.039
2021-01-02 | 9:28 | 50.039
2021-01-02 | 9:28 | 50.04
2021-01-02 | 9:28 | 50.042
2021-01-02 | 9:28 | 50.043
2021-01-02 | 9:28 | 50.043
2021-01-02 | 9:28 | 50.045
2021-01-02 | 9:28 | 50.047
2021-01-02 | 9:28 | 50.048
2021-01-02 | 9:28 | 50.047
2021-01-02 | 9:28 | 50.047
2021-01-02 | 9:28 | 50.048
2021-01-02 | 9:28 | 50.047
2021-01-02 | 9:28 | 50.047
2021-01-02 | 9:28 | 50.048
2021-01-02 | 9:28 | 50.047
2021-01-02 | 9:28 | 50.046
2021-01-02 | 9:28 | 50.045
2021-01-02 | 9:28 | 50.045
2021-01-02 | 9:28 | 50.048
2021-01-02 | 9:28 | 50.049
2021-01-02 | 9:28 | 50.052
2021-01-02 | 9:28 | 50.053
2021-01-02 | 9:28 | 50.053
2021-01-02 | 9:28 | 50.054
2021-01-02 | 9:28 | 50.055
2021-01-02 | 9:28 | 50.053
2021-01-02 | 9:29 | 50.051
2021-01-02 | 9:29 | 50.049
2021-01-02 | 9:29 | 50.047
2021-01-02 | 9:29 | 50.043
2021-01-02 | 9:29 | 50.04
2021-01-02 | 9:29 | 50.039
2021-01-02 | 9:29 | 50.036
2021-01-02 | 9:29 | 50.032
2021-01-02 | 9:29 | 50.026
2021-01-02 | 9:29 | 50.018
2021-01-02 | 9:29 | 50.014
2021-01-02 | 9:29 | 50.007
2021-01-02 | 9:29 | 50.006
2021-01-02 | 9:29 | 50.004
2021-01-02 | 9:29 | 50.005
2021-01-02 | 9:29 | 50.005
2021-01-02 | 9:29 | 50.008
2021-01-02 | 9:29 | 50.009
2021-01-02 | 9:29 | 50.013
2021-01-02 | 9:29 | 50.014
2021-01-02 | 9:29 | 50.012
2021-01-02 | 9:29 | 50.011
2021-01-02 | 9:29 | 50.007
2021-01-02 | 9:29 | 50.005
2021-01-02 | 9:29 | 50.001
2021-01-02 | 9:29 | 49.998
2021-01-02 | 9:29 | 49.995
2021-01-02 | 9:29 | 49.994
2021-01-02 | 9:29 | 49.993
2021-01-02 | 9:29 | 49.992
2021-01-02 | 9:29 | 49.991
2021-01-02 | 9:29 | 49.99
2021-01-02 | 9:29 | 49.991
2021-01-02 | 9:29 | 49.991
2021-01-02 | 9:29 | 49.994
2021-01-02 | 9:29 | 49.998
2021-01-02 | 9:29 | 50
2021-01-02 | 9:29 | 50.002
2021-01-02 | 9:29 | 50.003
2021-01-02 | 9:29 | 50.002
2021-01-02 | 9:29 | 50
2021-01-02 | 9:29 | 50
2021-01-02 | 9:29 | 49.999
2021-01-02 | 9:29 | 49.997
2021-01-02 | 9:29 | 49.995
2021-01-02 | 9:29 | 49.994
2021-01-02 | 9:29 | 49.995
2021-01-02 | 9:29 | 49.995
2021-01-02 | 9:29 | 49.997
2021-01-02 | 9:29 | 49.998
2021-01-02 | 9:29 | 49.999
2021-01-02 | 9:29 | 50
2021-01-02 | 9:29 | 50.001
2021-01-02 | 9:29 | 50.002
2021-01-02 | 9:29 | 50.004
2021-01-02 | 9:29 | 50.007
2021-01-02 | 9:29 | 50.009
2021-01-02 | 9:29 | 50.011
2021-01-02 | 9:29 | 50.012
2021-01-02 | 9:30 | 50.01
2021-01-02 | 9:30 | 50.011
2021-01-02 | 9:30 | 50.01
2021-01-02 | 9:30 | 50.01
2021-01-02 | 9:30 | 50.008
2021-01-02 | 9:30 | 50.005
2021-01-02 | 9:30 | 50.003
2021-01-02 | 9:30 | 50.003
2021-01-02 | 9:30 | 50.004
2021-01-02 | 9:30 | 50.005
2021-01-02 | 9:30 | 50.006
2021-01-02 | 9:30 | 50.006
2021-01-02 | 9:30 | 50.005
2021-01-02 | 9:30 | 50.003
2021-01-02 | 9:30 | 49.997
2021-01-02 | 9:30 | 49.997
2021-01-02 | 9:30 | 49.994
2021-01-02 | 9:30 | 49.99
2021-01-02 | 9:30 | 49.986
2021-01-02 | 9:30 | 49.983
2021-01-02 | 9:30 | 49.98
2021-01-02 | 9:30 | 49.98
2021-01-02 | 9:30 | 49.98
2021-01-02 | 9:30 | 49.979
2021-01-02 | 9:30 | 49.98
2021-01-02 | 9:30 | 49.979
2021-01-02 | 9:30 | 49.976
2021-01-02 | 9:30 | 49.965
2021-01-02 | 9:30 | 49.945
2021-01-02 | 9:30 | 49.919
2021-01-02 | 9:30 | 49.893
2021-01-02 | 9:30 | 49.876
2021-01-02 | 9:30 | 49.864
2021-01-02 | 9:30 | 49.858
2021-01-02 | 9:30 | 49.853
2021-01-02 | 9:30 | 49.851
2021-01-02 | 9:30 | 49.846
2021-01-02 | 9:30 | 49.847
2021-01-02 | 9:30 | 49.847
2021-01-02 | 9:30 | 49.848
2021-01-02 | 9:30 | 49.847
2021-01-02 | 9:30 | 49.849
2021-01-02 | 9:30 | 49.847
2021-01-02 | 9:30 | 49.847
2021-01-02 | 9:30 | 49.848
2021-01-02 | 9:30 | 49.85
2021-01-02 | 9:30 | 49.851
2021-01-02 | 9:30 | 49.846
2021-01-02 | 9:30 | 49.845
2021-01-02 | 9:30 | 49.845
2021-01-02 | 9:30 | 49.846
2021-01-02 | 9:30 | 49.845
2021-01-02 | 9:30 | 49.844
2021-01-02 | 9:30 | 49.845
2021-01-02 | 9:30 | 49.845
2021-01-02 | 9:30 | 49.843
2021-01-02 | 9:30 | 49.842
2021-01-02 | 9:30 | 49.841
2021-01-02 | 9:30 | 49.839
2021-01-02 | 9:30 | 49.836
2021-01-02 | 9:30 | 49.836
2021-01-02 | 9:31 | 49.84
2021-01-02 | 9:31 | 49.835
2021-01-02 | 9:31 | 49.836
2021-01-02 | 9:31 | 49.837
2021-01-02 | 9:31 | 49.834
2021-01-02 | 9:31 | 49.835
2021-01-02 | 9:31 | 49.833
2021-01-02 | 9:31 | 49.834
2021-01-02 | 9:31 | 49.836
2021-01-02 | 9:31 | 49.84
2021-01-02 | 9:31 | 49.842
2021-01-02 | 9:31 | 49.845
2021-01-02 | 9:31 | 49.843
2021-01-02 | 9:31 | 49.844
2021-01-02 | 9:31 | 49.845
2021-01-02 | 9:31 | 49.843
2021-01-02 | 9:31 | 49.843
2021-01-02 | 9:31 | 49.842
2021-01-02 | 9:31 | 49.841
2021-01-02 | 9:31 | 49.843
2021-01-02 | 9:31 | 49.841
2021-01-02 | 9:31 | 49.84
2021-01-02 | 9:31 | 49.84
2021-01-02 | 9:31 | 49.84
2021-01-02 | 9:31 | 49.841
2021-01-02 | 9:31 | 49.842
2021-01-02 | 9:31 | 49.845
2021-01-02 | 9:31 | 49.846
2021-01-02 | 9:31 | 49.846
2021-01-02 | 9:31 | 49.844
2021-01-02 | 9:31 | 49.842
2021-01-02 | 9:31 | 49.84
2021-01-02 | 9:31 | 49.839
2021-01-02 | 9:31 | 49.839
2021-01-02 | 9:31 | 49.838
2021-01-02 | 9:31 | 49.838
2021-01-02 | 9:31 | 49.842
2021-01-02 | 9:31 | 49.841
2021-01-02 | 9:31 | 49.843
2021-01-02 | 9:31 | 49.843
2021-01-02 | 9:31 | 49.849
2021-01-02 | 9:31 | 49.854
2021-01-02 | 9:31 | 49.858
2021-01-02 | 9:31 | 49.863
2021-01-02 | 9:31 | 49.868
2021-01-02 | 9:31 | 49.871
2021-01-02 | 9:31 | 49.874
2021-01-02 | 9:31 | 49.877
2021-01-02 | 9:31 | 49.879
2021-01-02 | 9:31 | 49.882
2021-01-02 | 9:31 | 49.881
2021-01-02 | 9:31 | 49.882
2021-01-02 | 9:31 | 49.883
2021-01-02 | 9:31 | 49.884
2021-01-02 | 9:31 | 49.883
2021-01-02 | 9:31 | 49.882
2021-01-02 | 9:31 | 49.881
2021-01-02 | 9:31 | 49.881
2021-01-02 | 9:31 | 49.879
2021-01-02 | 9:32 | 49.877
2021-01-02 | 9:32 | 49.875
2021-01-02 | 9:32 | 49.873
2021-01-02 | 9:32 | 49.873
2021-01-02 | 9:32 | 49.874
2021-01-02 | 9:32 | 49.873
2021-01-02 | 9:32 | 49.873
2021-01-02 | 9:32 | 49.872
2021-01-02 | 9:32 | 49.87
2021-01-02 | 9:32 | 49.869
2021-01-02 | 9:32 | 49.87
2021-01-02 | 9:32 | 49.869
2021-01-02 | 9:32 | 49.87
2021-01-02 | 9:32 | 49.87
2021-01-02 | 9:32 | 49.869
2021-01-02 | 9:32 | 49.868
2021-01-02 | 9:32 | 49.866
2021-01-02 | 9:32 | 49.864
2021-01-02 | 9:32 | 49.864
2021-01-02 | 9:32 | 49.865
2021-01-02 | 9:32 | 49.864
2021-01-02 | 9:32 | 49.867
2021-01-02 | 9:32 | 49.87
2021-01-02 | 9:32 | 49.872
2021-01-02 | 9:32 | 49.872
2021-01-02 | 9:32 | 49.874
2021-01-02 | 9:32 | 49.873
2021-01-02 | 9:32 | 49.869
2021-01-02 | 9:32 | 49.87
2021-01-02 | 9:32 | 49.868
2021-01-02 | 9:32 | 49.862
2021-01-02 | 9:32 | 49.858
2021-01-02 | 9:32 | 49.855
2021-01-02 | 9:32 | 49.854
2021-01-02 | 9:32 | 49.849
2021-01-02 | 9:32 | 49.849
2021-01-02 | 9:32 | 49.845
2021-01-02 | 9:32 | 49.845
2021-01-02 | 9:32 | 49.844
2021-01-02 | 9:32 | 49.844
2021-01-02 | 9:32 | 49.842
2021-01-02 | 9:32 | 49.841
2021-01-02 | 9:32 | 49.84
2021-01-02 | 9:32 | 49.841
2021-01-02 | 9:32 | 49.845
2021-01-02 | 9:32 | 49.85
2021-01-02 | 9:32 | 49.851
2021-01-02 | 9:32 | 49.853
2021-01-02 | 9:32 | 49.852
2021-01-02 | 9:32 | 49.853
2021-01-02 | 9:32 | 49.851
2021-01-02 | 9:32 | 49.851
2021-01-02 | 9:32 | 49.847
2021-01-02 | 9:32 | 49.847
2021-01-02 | 9:32 | 49.844
2021-01-02 | 9:32 | 49.844
2021-01-02 | 9:32 | 49.846
2021-01-02 | 9:32 | 49.848
2021-01-02 | 9:32 | 49.851
2021-01-02 | 9:32 | 49.852
2021-01-02 | 9:32 | 49.854
2021-01-02 | 9:33 | 49.858
2021-01-02 | 9:33 | 49.862
2021-01-02 | 9:33 | 49.867
2021-01-02 | 9:33 | 49.871
2021-01-02 | 9:33 | 49.877
2021-01-02 | 9:33 | 49.878
2021-01-02 | 9:33 | 49.883
2021-01-02 | 9:33 | 49.891
2021-01-02 | 9:33 | 49.895
2021-01-02 | 9:33 | 49.901
2021-01-02 | 9:33 | 49.906
2021-01-02 | 9:33 | 49.91
2021-01-02 | 9:33 | 49.915
2021-01-02 | 9:33 | 49.919
2021-01-02 | 9:33 | 49.921
2021-01-02 | 9:33 | 49.922
2021-01-02 | 9:33 | 49.923
2021-01-02 | 9:33 | 49.925
2021-01-02 | 9:33 | 49.926
2021-01-02 | 9:33 | 49.927
2021-01-02 | 9:33 | 49.926
2021-01-02 | 9:33 | 49.926
2021-01-02 | 9:33 | 49.925
2021-01-02 | 9:33 | 49.924
2021-01-02 | 9:33 | 49.923
2021-01-02 | 9:33 | 49.925
2021-01-02 | 9:33 | 49.924
2021-01-02 | 9:33 | 49.925
2021-01-02 | 9:33 | 49.925
2021-01-02 | 9:33 | 49.924
2021-01-02 | 9:33 | 49.924
2021-01-02 | 9:33 | 49.923
2021-01-02 | 9:33 | 49.927
2021-01-02 | 9:33 | 49.925
2021-01-02 | 9:33 | 49.925
2021-01-02 | 9:33 | 49.928
2021-01-02 | 9:33 | 49.926
2021-01-02 | 9:33 | 49.927
2021-01-02 | 9:33 | 49.927
2021-01-02 | 9:33 | 49.93
2021-01-02 | 9:33 | 49.931
2021-01-02 | 9:33 | 49.931
2021-01-02 | 9:33 | 49.933
2021-01-02 | 9:33 | 49.934
2021-01-02 | 9:33 | 49.935
2021-01-02 | 9:33 | 49.936
2021-01-02 | 9:33 | 49.938
2021-01-02 | 9:33 | 49.938
2021-01-02 | 9:33 | 49.943
2021-01-02 | 9:33 | 49.943
2021-01-02 | 9:33 | 49.944
2021-01-02 | 9:33 | 49.943
2021-01-02 | 9:33 | 49.942
2021-01-02 | 9:33 | 49.943
2021-01-02 | 9:33 | 49.943
2021-01-02 | 9:33 | 49.943
2021-01-02 | 9:33 | 49.944
2021-01-02 | 9:33 | 49.945
2021-01-02 | 9:33 | 49.946
2021-01-02 | 9:34 | 49.947
2021-01-02 | 9:34 | 49.944
2021-01-02 | 9:34 | 49.942
2021-01-02 | 9:34 | 49.943
2021-01-02 | 9:34 | 49.943
2021-01-02 | 9:34 | 49.94
2021-01-02 | 9:34 | 49.937
2021-01-02 | 9:34 | 49.933
2021-01-02 | 9:34 | 49.93
2021-01-02 | 9:34 | 49.926
2021-01-02 | 9:34 | 49.924
2021-01-02 | 9:34 | 49.921
2021-01-02 | 9:34 | 49.92
2021-01-02 | 9:34 | 49.92
2021-01-02 | 9:34 | 49.919
2021-01-02 | 9:34 | 49.919
2021-01-02 | 9:34 | 49.917
2021-01-02 | 9:34 | 49.915
2021-01-02 | 9:34 | 49.913
2021-01-02 | 9:34 | 49.912
2021-01-02 | 9:34 | 49.91
2021-01-02 | 9:34 | 49.912
2021-01-02 | 9:34 | 49.911
2021-01-02 | 9:34 | 49.912
2021-01-02 | 9:34 | 49.911
2021-01-02 | 9:34 | 49.911
2021-01-02 | 9:34 | 49.912
2021-01-02 | 9:34 | 49.908
2021-01-02 | 9:34 | 49.906
2021-01-02 | 9:34 | 49.903
2021-01-02 | 9:34 | 49.898
2021-01-02 | 9:34 | 49.893
2021-01-02 | 9:34 | 49.889
2021-01-02 | 9:34 | 49.886
2021-01-02 | 9:34 | 49.888
2021-01-02 | 9:34 | 49.886
2021-01-02 | 9:34 | 49.884
2021-01-02 | 9:34 | 49.885
2021-01-02 | 9:34 | 49.886
2021-01-02 | 9:34 | 49.887
2021-01-02 | 9:34 | 49.889
2021-01-02 | 9:34 | 49.889
2021-01-02 | 9:34 | 49.89
2021-01-02 | 9:34 | 49.891
2021-01-02 | 9:34 | 49.891
2021-01-02 | 9:34 | 49.891
2021-01-02 | 9:34 | 49.89
2021-01-02 | 9:34 | 49.889
2021-01-02 | 9:34 | 49.887
2021-01-02 | 9:34 | 49.885
2021-01-02 | 9:34 | 49.882
2021-01-02 | 9:34 | 49.882
2021-01-02 | 9:34 | 49.881
2021-01-02 | 9:34 | 49.882
2021-01-02 | 9:34 | 49.88
2021-01-02 | 9:34 | 49.879
2021-01-02 | 9:34 | 49.879
2021-01-02 | 9:34 | 49.879
2021-01-02 | 9:34 | 49.881
2021-01-02 | 9:34 | 49.88
2021-01-02 | 9:34 | 49.882
2021-01-02 | 9:35 | 49.882
2021-01-02 | 9:35 | 49.884
2021-01-02 | 9:35 | 49.888
2021-01-02 | 9:35 | 49.891
2021-01-02 | 9:35 | 49.892
2021-01-02 | 9:35 | 49.894
2021-01-02 | 9:35 | 49.896
2021-01-02 | 9:35 | 49.896
2021-01-02 | 9:35 | 49.896
2021-01-02 | 9:35 | 49.895
2021-01-02 | 9:35 | 49.895
2021-01-02 | 9:35 | 49.894
2021-01-02 | 9:35 | 49.893
2021-01-02 | 9:35 | 49.893
2021-01-02 | 9:35 | 49.892
2021-01-02 | 9:35 | 49.893
2021-01-02 | 9:35 | 49.892
2021-01-02 | 9:35 | 49.892
2021-01-02 | 9:35 | 49.891
2021-01-02 | 9:35 | 49.891
2021-01-02 | 9:35 | 49.89
2021-01-02 | 9:35 | 49.892
2021-01-02 | 9:35 | 49.888
2021-01-02 | 9:35 | 49.887
2021-01-02 | 9:35 | 49.884
2021-01-02 | 9:35 | 49.881
2021-01-02 | 9:35 | 49.882
2021-01-02 | 9:35 | 49.884
2021-01-02 | 9:35 | 49.886
2021-01-02 | 9:35 | 49.888
2021-01-02 | 9:35 | 49.892
2021-01-02 | 9:35 | 49.895
2021-01-02 | 9:35 | 49.896
2021-01-02 | 9:35 | 49.9
2021-01-02 | 9:35 | 49.9
2021-01-02 | 9:35 | 49.901
2021-01-02 | 9:35 | 49.9
2021-01-02 | 9:35 | 49.898
2021-01-02 | 9:35 | 49.896
2021-01-02 | 9:35 | 49.897
2021-01-02 | 9:35 | 49.895
2021-01-02 | 9:35 | 49.897
2021-01-02 | 9:35 | 49.898
2021-01-02 | 9:35 | 49.901
2021-01-02 | 9:35 | 49.902
2021-01-02 | 9:35 | 49.903
2021-01-02 | 9:35 | 49.904
2021-01-02 | 9:35 | 49.906
2021-01-02 | 9:35 | 49.907
2021-01-02 | 9:35 | 49.91
2021-01-02 | 9:35 | 49.911
2021-01-02 | 9:35 | 49.912
2021-01-02 | 9:35 | 49.911
2021-01-02 | 9:35 | 49.909
2021-01-02 | 9:35 | 49.909
2021-01-02 | 9:35 | 49.907
2021-01-02 | 9:35 | 49.904
2021-01-02 | 9:35 | 49.902
2021-01-02 | 9:35 | 49.903
2021-01-02 | 9:36 | 49.907
2021-01-02 | 9:36 | 49.908
2021-01-02 | 9:36 | 49.909
2021-01-02 | 9:36 | 49.912
2021-01-02 | 9:36 | 49.914
2021-01-02 | 9:36 | 49.919
2021-01-02 | 9:36 | 49.921
2021-01-02 | 9:36 | 49.923
2021-01-02 | 9:36 | 49.924
2021-01-02 | 9:36 | 49.923
2021-01-02 | 9:36 | 49.922
2021-01-02 | 9:36 | 49.923
2021-01-02 | 9:36 | 49.925
2021-01-02 | 9:36 | 49.925
2021-01-02 | 9:36 | 49.924
2021-01-02 | 9:36 | 49.924
2021-01-02 | 9:36 | 49.925
2021-01-02 | 9:36 | 49.923
2021-01-02 | 9:36 | 49.922
2021-01-02 | 9:36 | 49.922
2021-01-02 | 9:36 | 49.921
2021-01-02 | 9:36 | 49.92
2021-01-02 | 9:36 | 49.919
2021-01-02 | 9:36 | 49.921
2021-01-02 | 9:36 | 49.921
2021-01-02 | 9:36 | 49.922
2021-01-02 | 9:36 | 49.92
2021-01-02 | 9:36 | 49.919
2021-01-02 | 9:36 | 49.918
2021-01-02 | 9:36 | 49.915
2021-01-02 | 9:36 | 49.917
2021-01-02 | 9:36 | 49.915
2021-01-02 | 9:36 | 49.915
2021-01-02 | 9:36 | 49.917
2021-01-02 | 9:36 | 49.919
2021-01-02 | 9:36 | 49.922
2021-01-02 | 9:36 | 49.923
2021-01-02 | 9:36 | 49.928
2021-01-02 | 9:36 | 49.927
2021-01-02 | 9:36 | 49.929
2021-01-02 | 9:36 | 49.93
2021-01-02 | 9:36 | 49.931
2021-01-02 | 9:36 | 49.935
2021-01-02 | 9:36 | 49.934
2021-01-02 | 9:36 | 49.936
2021-01-02 | 9:36 | 49.936
2021-01-02 | 9:36 | 49.937
2021-01-02 | 9:36 | 49.936
2021-01-02 | 9:36 | 49.935
2021-01-02 | 9:36 | 49.934
2021-01-02 | 9:36 | 49.933
2021-01-02 | 9:36 | 49.934
2021-01-02 | 9:36 | 49.934
2021-01-02 | 9:36 | 49.933
2021-01-02 | 9:36 | 49.932
2021-01-02 | 9:36 | 49.934
2021-01-02 | 9:36 | 49.931
2021-01-02 | 9:36 | 49.93
2021-01-02 | 9:36 | 49.926
2021-01-02 | 9:36 | 49.923
2021-01-02 | 9:36 | 49.922
2021-01-02 | 9:37 | 49.924
2021-01-02 | 9:37 | 49.924
2021-01-02 | 9:37 | 49.923
2021-01-02 | 9:37 | 49.924
2021-01-02 | 9:37 | 49.925
2021-01-02 | 9:37 | 49.929
2021-01-02 | 9:37 | 49.929
2021-01-02 | 9:37 | 49.929
2021-01-02 | 9:37 | 49.931
2021-01-02 | 9:37 | 49.93
2021-01-02 | 9:37 | 49.931
2021-01-02 | 9:37 | 49.933
2021-01-02 | 9:37 | 49.933
2021-01-02 | 9:37 | 49.93
2021-01-02 | 9:37 | 49.926
2021-01-02 | 9:37 | 49.924
2021-01-02 | 9:37 | 49.922
2021-01-02 | 9:37 | 49.921
2021-01-02 | 9:37 | 49.919
2021-01-02 | 9:37 | 49.921
2021-01-02 | 9:37 | 49.919
2021-01-02 | 9:37 | 49.92
2021-01-02 | 9:37 | 49.919
2021-01-02 | 9:37 | 49.918
2021-01-02 | 9:37 | 49.918
2021-01-02 | 9:37 | 49.916
2021-01-02 | 9:37 | 49.919
2021-01-02 | 9:37 | 49.919
2021-01-02 | 9:37 | 49.919
2021-01-02 | 9:37 | 49.923
2021-01-02 | 9:37 | 49.926
2021-01-02 | 9:37 | 49.928
2021-01-02 | 9:37 | 49.931
2021-01-02 | 9:37 | 49.932
2021-01-02 | 9:37 | 49.931
2021-01-02 | 9:37 | 49.933
2021-01-02 | 9:37 | 49.933
2021-01-02 | 9:37 | 49.932
2021-01-02 | 9:37 | 49.931
2021-01-02 | 9:37 | 49.932
2021-01-02 | 9:37 | 49.93
2021-01-02 | 9:37 | 49.931
2021-01-02 | 9:37 | 49.932
2021-01-02 | 9:37 | 49.932
2021-01-02 | 9:37 | 49.931
2021-01-02 | 9:37 | 49.93
2021-01-02 | 9:37 | 49.929
2021-01-02 | 9:37 | 49.93
2021-01-02 | 9:37 | 49.93
2021-01-02 | 9:37 | 49.928
2021-01-02 | 9:37 | 49.927
2021-01-02 | 9:37 | 49.927
2021-01-02 | 9:37 | 49.924
2021-01-02 | 9:37 | 49.926
2021-01-02 | 9:37 | 49.929
2021-01-02 | 9:37 | 49.932
2021-01-02 | 9:37 | 49.938
2021-01-02 | 9:37 | 49.945
2021-01-02 | 9:37 | 49.95
2021-01-02 | 9:38 | 49.953
2021-01-02 | 9:38 | 49.956
2021-01-02 | 9:38 | 49.959
2021-01-02 | 9:38 | 49.959
2021-01-02 | 9:38 | 49.963
2021-01-02 | 9:38 | 49.963
2021-01-02 | 9:38 | 49.964
2021-01-02 | 9:38 | 49.964
2021-01-02 | 9:38 | 49.963
2021-01-02 | 9:38 | 49.963
2021-01-02 | 9:38 | 49.962
2021-01-02 | 9:38 | 49.963
2021-01-02 | 9:38 | 49.961
2021-01-02 | 9:38 | 49.962
2021-01-02 | 9:38 | 49.962
2021-01-02 | 9:38 | 49.962
2021-01-02 | 9:38 | 49.962
2021-01-02 | 9:38 | 49.963
2021-01-02 | 9:38 | 49.967
2021-01-02 | 9:38 | 49.966
2021-01-02 | 9:38 | 49.969
2021-01-02 | 9:38 | 49.969
2021-01-02 | 9:38 | 49.968
2021-01-02 | 9:38 | 49.968
2021-01-02 | 9:38 | 49.968
2021-01-02 | 9:38 | 49.969
2021-01-02 | 9:38 | 49.969
2021-01-02 | 9:38 | 49.971
2021-01-02 | 9:38 | 49.971
2021-01-02 | 9:38 | 49.972
2021-01-02 | 9:38 | 49.97
2021-01-02 | 9:38 | 49.972
2021-01-02 | 9:38 | 49.973
2021-01-02 | 9:38 | 49.972
2021-01-02 | 9:38 | 49.971
2021-01-02 | 9:38 | 49.972
2021-01-02 | 9:38 | 49.971
2021-01-02 | 9:38 | 49.971
2021-01-02 | 9:38 | 49.971
2021-01-02 | 9:38 | 49.971
2021-01-02 | 9:38 | 49.97
2021-01-02 | 9:38 | 49.968
2021-01-02 | 9:38 | 49.964
2021-01-02 | 9:38 | 49.961
2021-01-02 | 9:38 | 49.957
2021-01-02 | 9:38 | 49.954
2021-01-02 | 9:38 | 49.954
2021-01-02 | 9:38 | 49.95
2021-01-02 | 9:38 | 49.948
2021-01-02 | 9:38 | 49.944
2021-01-02 | 9:38 | 49.945
2021-01-02 | 9:38 | 49.942
2021-01-02 | 9:38 | 49.942
2021-01-02 | 9:38 | 49.942
2021-01-02 | 9:38 | 49.942
2021-01-02 | 9:38 | 49.943
2021-01-02 | 9:38 | 49.942
2021-01-02 | 9:38 | 49.943
2021-01-02 | 9:38 | 49.94
2021-01-02 | 9:38 | 49.94
2021-01-02 | 9:38 | 49.941
2021-01-02 | 9:39 | 49.938
2021-01-02 | 9:39 | 49.937
2021-01-02 | 9:39 | 49.936
2021-01-02 | 9:39 | 49.936
2021-01-02 | 9:39 | 49.937
2021-01-02 | 9:39 | 49.935
2021-01-02 | 9:39 | 49.935
2021-01-02 | 9:39 | 49.937
2021-01-02 | 9:39 | 49.935
2021-01-02 | 9:39 | 49.936
2021-01-02 | 9:39 | 49.938
2021-01-02 | 9:39 | 49.937
2021-01-02 | 9:39 | 49.937
2021-01-02 | 9:39 | 49.935
2021-01-02 | 9:39 | 49.935
2021-01-02 | 9:39 | 49.936
2021-01-02 | 9:39 | 49.937
2021-01-02 | 9:39 | 49.936
2021-01-02 | 9:39 | 49.933
2021-01-02 | 9:39 | 49.935
2021-01-02 | 9:39 | 49.935
2021-01-02 | 9:39 | 49.934
2021-01-02 | 9:39 | 49.934
2021-01-02 | 9:39 | 49.935
2021-01-02 | 9:39 | 49.933
2021-01-02 | 9:39 | 49.934
2021-01-02 | 9:39 | 49.938
2021-01-02 | 9:39 | 49.939
2021-01-02 | 9:39 | 49.939
2021-01-02 | 9:39 | 49.939
2021-01-02 | 9:39 | 49.941
2021-01-02 | 9:39 | 49.942
2021-01-02 | 9:39 | 49.942
2021-01-02 | 9:39 | 49.941
2021-01-02 | 9:39 | 49.939
2021-01-02 | 9:39 | 49.938
2021-01-02 | 9:39 | 49.936
2021-01-02 | 9:39 | 49.94
2021-01-02 | 9:39 | 49.941
2021-01-02 | 9:39 | 49.943
2021-01-02 | 9:39 | 49.943
2021-01-02 | 9:39 | 49.944
2021-01-02 | 9:39 | 49.944
2021-01-02 | 9:39 | 49.946
2021-01-02 | 9:39 | 49.945
2021-01-02 | 9:39 | 49.943
2021-01-02 | 9:39 | 49.941
2021-01-02 | 9:39 | 49.941
2021-01-02 | 9:39 | 49.942
2021-01-02 | 9:39 | 49.944
2021-01-02 | 9:39 | 49.943
2021-01-02 | 9:39 | 49.944
2021-01-02 | 9:39 | 49.941
2021-01-02 | 9:39 | 49.942
2021-01-02 | 9:39 | 49.941
2021-01-02 | 9:39 | 49.939
2021-01-02 | 9:39 | 49.94
2021-01-02 | 9:39 | 49.939
2021-01-02 | 9:39 | 49.937
2021-01-02 | 9:40 | 49.934
2021-01-02 | 9:40 | 49.932
2021-01-02 | 9:40 | 49.93
2021-01-02 | 9:40 | 49.931
2021-01-02 | 9:40 | 49.933
2021-01-02 | 9:40 | 49.935
2021-01-02 | 9:40 | 49.935
2021-01-02 | 9:40 | 49.934
2021-01-02 | 9:40 | 49.934
2021-01-02 | 9:40 | 49.935
2021-01-02 | 9:40 | 49.935
2021-01-02 | 9:40 | 49.935
2021-01-02 | 9:40 | 49.935
2021-01-02 | 9:40 | 49.934
2021-01-02 | 9:40 | 49.935
2021-01-02 | 9:40 | 49.938
2021-01-02 | 9:40 | 49.936
2021-01-02 | 9:40 | 49.938
2021-01-02 | 9:40 | 49.938
2021-01-02 | 9:40 | 49.938
2021-01-02 | 9:40 | 49.937
2021-01-02 | 9:40 | 49.936
2021-01-02 | 9:40 | 49.939
2021-01-02 | 9:40 | 49.941
2021-01-02 | 9:40 | 49.942
2021-01-02 | 9:40 | 49.944
2021-01-02 | 9:40 | 49.944
2021-01-02 | 9:40 | 49.947
2021-01-02 | 9:40 | 49.946
2021-01-02 | 9:40 | 49.947
2021-01-02 | 9:40 | 49.951
2021-01-02 | 9:40 | 49.95
2021-01-02 | 9:40 | 49.95
2021-01-02 | 9:40 | 49.95
2021-01-02 | 9:40 | 49.949
2021-01-02 | 9:40 | 49.951
2021-01-02 | 9:40 | 49.946
2021-01-02 | 9:40 | 49.947
2021-01-02 | 9:40 | 49.941
2021-01-02 | 9:40 | 49.941
2021-01-02 | 9:40 | 49.941
2021-01-02 | 9:40 | 49.942
2021-01-02 | 9:40 | 49.942
2021-01-02 | 9:40 | 49.939
2021-01-02 | 9:40 | 49.939
2021-01-02 | 9:40 | 49.937
2021-01-02 | 9:40 | 49.936
2021-01-02 | 9:40 | 49.935
2021-01-02 | 9:40 | 49.933
2021-01-02 | 9:40 | 49.935
2021-01-02 | 9:40 | 49.933
2021-01-02 | 9:40 | 49.934
2021-01-02 | 9:40 | 49.932
2021-01-02 | 9:40 | 49.931
2021-01-02 | 9:40 | 49.929
2021-01-02 | 9:40 | 49.931
2021-01-02 | 9:40 | 49.929
2021-01-02 | 9:40 | 49.93
2021-01-02 | 9:40 | 49.929
2021-01-02 | 9:40 | 49.93
2021-01-02 | 9:40 | 49.931
2021-01-02 | 9:41 | 49.93
2021-01-02 | 9:41 | 49.93
2021-01-02 | 9:41 | 49.929
2021-01-02 | 9:41 | 49.929
2021-01-02 | 9:41 | 49.929
2021-01-02 | 9:41 | 49.925
2021-01-02 | 9:41 | 49.922
2021-01-02 | 9:41 | 49.919
2021-01-02 | 9:41 | 49.912
2021-01-02 | 9:41 | 49.909
2021-01-02 | 9:41 | 49.902
2021-01-02 | 9:41 | 49.897
2021-01-02 | 9:41 | 49.891
2021-01-02 | 9:41 | 49.885
2021-01-02 | 9:41 | 49.881
2021-01-02 | 9:41 | 49.875
2021-01-02 | 9:41 | 49.872
2021-01-02 | 9:41 | 49.871
2021-01-02 | 9:41 | 49.868
2021-01-02 | 9:41 | 49.869
2021-01-02 | 9:41 | 49.867
2021-01-02 | 9:41 | 49.867
2021-01-02 | 9:41 | 49.865
2021-01-02 | 9:41 | 49.864
2021-01-02 | 9:41 | 49.862
2021-01-02 | 9:41 | 49.86
2021-01-02 | 9:41 | 49.86
2021-01-02 | 9:41 | 49.859
2021-01-02 | 9:41 | 49.86
2021-01-02 | 9:41 | 49.859
2021-01-02 | 9:41 | 49.858
2021-01-02 | 9:41 | 49.857
2021-01-02 | 9:41 | 49.857
2021-01-02 | 9:41 | 49.855
2021-01-02 | 9:41 | 49.853
2021-01-02 | 9:41 | 49.853
2021-01-02 | 9:41 | 49.85
2021-01-02 | 9:41 | 49.849
2021-01-02 | 9:41 | 49.845
2021-01-02 | 9:41 | 49.847
2021-01-02 | 9:41 | 49.845
2021-01-02 | 9:41 | 49.846
2021-01-02 | 9:41 | 49.845
2021-01-02 | 9:41 | 49.845
2021-01-02 | 9:41 | 49.843
2021-01-02 | 9:41 | 49.844
2021-01-02 | 9:41 | 49.842
2021-01-02 | 9:41 | 49.84
2021-01-02 | 9:41 | 49.838
2021-01-02 | 9:41 | 49.839
2021-01-02 | 9:41 | 49.84
2021-01-02 | 9:41 | 49.844
2021-01-02 | 9:41 | 49.846
2021-01-02 | 9:41 | 49.852
2021-01-02 | 9:41 | 49.854
2021-01-02 | 9:41 | 49.855
2021-01-02 | 9:41 | 49.855
2021-01-02 | 9:41 | 49.857
2021-01-02 | 9:41 | 49.857
2021-01-02 | 9:42 | 49.858
2021-01-02 | 9:42 | 49.86
2021-01-02 | 9:42 | 49.86
2021-01-02 | 9:42 | 49.86
2021-01-02 | 9:42 | 49.86
2021-01-02 | 9:42 | 49.86
2021-01-02 | 9:42 | 49.86
2021-01-02 | 9:42 | 49.864
2021-01-02 | 9:42 | 49.867
2021-01-02 | 9:42 | 49.869
2021-01-02 | 9:42 | 49.871
2021-01-02 | 9:42 | 49.872
2021-01-02 | 9:42 | 49.874
2021-01-02 | 9:42 | 49.876
2021-01-02 | 9:42 | 49.877
2021-01-02 | 9:42 | 49.876
2021-01-02 | 9:42 | 49.876
2021-01-02 | 9:42 | 49.874
2021-01-02 | 9:42 | 49.874
2021-01-02 | 9:42 | 49.875
2021-01-02 | 9:42 | 49.875
2021-01-02 | 9:42 | 49.874
2021-01-02 | 9:42 | 49.877
2021-01-02 | 9:42 | 49.877
2021-01-02 | 9:42 | 49.879
2021-01-02 | 9:42 | 49.882
2021-01-02 | 9:42 | 49.883
2021-01-02 | 9:42 | 49.885
2021-01-02 | 9:42 | 49.885
2021-01-02 | 9:42 | 49.886
2021-01-02 | 9:42 | 49.888
2021-01-02 | 9:42 | 49.891
2021-01-02 | 9:42 | 49.891
2021-01-02 | 9:42 | 49.891
2021-01-02 | 9:42 | 49.893
2021-01-02 | 9:42 | 49.893
2021-01-02 | 9:42 | 49.893
2021-01-02 | 9:42 | 49.893
2021-01-02 | 9:42 | 49.894
2021-01-02 | 9:42 | 49.893
2021-01-02 | 9:42 | 49.895
2021-01-02 | 9:42 | 49.894
2021-01-02 | 9:42 | 49.896
2021-01-02 | 9:42 | 49.896
2021-01-02 | 9:42 | 49.894
2021-01-02 | 9:42 | 49.894
2021-01-02 | 9:42 | 49.894
2021-01-02 | 9:42 | 49.897
2021-01-02 | 9:42 | 49.897
2021-01-02 | 9:42 | 49.896
2021-01-02 | 9:42 | 49.898
2021-01-02 | 9:42 | 49.898
2021-01-02 | 9:42 | 49.9
2021-01-02 | 9:42 | 49.901
2021-01-02 | 9:42 | 49.905
2021-01-02 | 9:42 | 49.906
2021-01-02 | 9:42 | 49.907
2021-01-02 | 9:42 | 49.908
2021-01-02 | 9:42 | 49.912
2021-01-02 | 9:42 | 49.914
2021-01-02 | 9:42 | 49.914
2021-01-02 | 9:43 | 49.915
2021-01-02 | 9:43 | 49.914
2021-01-02 | 9:43 | 49.915
2021-01-02 | 9:43 | 49.916
2021-01-02 | 9:43 | 49.923
2021-01-02 | 9:43 | 49.929
2021-01-02 | 9:43 | 49.934
2021-01-02 | 9:43 | 49.939
2021-01-02 | 9:43 | 49.939
2021-01-02 | 9:43 | 49.946
2021-01-02 | 9:43 | 49.95
2021-01-02 | 9:43 | 49.954
2021-01-02 | 9:43 | 49.958
2021-01-02 | 9:43 | 49.962
2021-01-02 | 9:43 | 49.966
2021-01-02 | 9:43 | 49.966
2021-01-02 | 9:43 | 49.965
2021-01-02 | 9:43 | 49.964
2021-01-02 | 9:43 | 49.961
2021-01-02 | 9:43 | 49.958
2021-01-02 | 9:43 | 49.956
2021-01-02 | 9:43 | 49.953
2021-01-02 | 9:43 | 49.948
2021-01-02 | 9:43 | 49.946
2021-01-02 | 9:43 | 49.944
2021-01-02 | 9:43 | 49.941
2021-01-02 | 9:43 | 49.938
2021-01-02 | 9:43 | 49.937
2021-01-02 | 9:43 | 49.936
2021-01-02 | 9:43 | 49.934
2021-01-02 | 9:43 | 49.932
2021-01-02 | 9:43 | 49.931
2021-01-02 | 9:43 | 49.931
2021-01-02 | 9:43 | 49.93
2021-01-02 | 9:43 | 49.931
2021-01-02 | 9:43 | 49.93
2021-01-02 | 9:43 | 49.928
2021-01-02 | 9:43 | 49.929
2021-01-02 | 9:43 | 49.928
2021-01-02 | 9:43 | 49.926
2021-01-02 | 9:43 | 49.926
2021-01-02 | 9:43 | 49.924
2021-01-02 | 9:43 | 49.924
2021-01-02 | 9:43 | 49.922
2021-01-02 | 9:43 | 49.919
2021-01-02 | 9:43 | 49.919
2021-01-02 | 9:43 | 49.921
2021-01-02 | 9:43 | 49.919
2021-01-02 | 9:43 | 49.924
2021-01-02 | 9:43 | 49.926
2021-01-02 | 9:43 | 49.925
2021-01-02 | 9:43 | 49.927
2021-01-02 | 9:43 | 49.924
2021-01-02 | 9:43 | 49.925
2021-01-02 | 9:43 | 49.924
2021-01-02 | 9:43 | 49.922
2021-01-02 | 9:43 | 49.923
2021-01-02 | 9:43 | 49.923
2021-01-02 | 9:43 | 49.923
2021-01-02 | 9:44 | 49.923
2021-01-02 | 9:44 | 49.924
2021-01-02 | 9:44 | 49.922
2021-01-02 | 9:44 | 49.922
2021-01-02 | 9:44 | 49.92
2021-01-02 | 9:44 | 49.921
2021-01-02 | 9:44 | 49.922
2021-01-02 | 9:44 | 49.922
2021-01-02 | 9:44 | 49.922
2021-01-02 | 9:44 | 49.922
2021-01-02 | 9:44 | 49.919
2021-01-02 | 9:44 | 49.919
2021-01-02 | 9:44 | 49.919
2021-01-02 | 9:44 | 49.92
2021-01-02 | 9:44 | 49.923
2021-01-02 | 9:44 | 49.925
2021-01-02 | 9:44 | 49.929
2021-01-02 | 9:44 | 49.928
2021-01-02 | 9:44 | 49.931
2021-01-02 | 9:44 | 49.929
2021-01-02 | 9:44 | 49.93
2021-01-02 | 9:44 | 49.927
2021-01-02 | 9:44 | 49.927
2021-01-02 | 9:44 | 49.928
2021-01-02 | 9:44 | 49.927
2021-01-02 | 9:44 | 49.929
2021-01-02 | 9:44 | 49.93
2021-01-02 | 9:44 | 49.931
2021-01-02 | 9:44 | 49.933
2021-01-02 | 9:44 | 49.935
2021-01-02 | 9:44 | 49.938
2021-01-02 | 9:44 | 49.938
2021-01-02 | 9:44 | 49.941
2021-01-02 | 9:44 | 49.942
2021-01-02 | 9:44 | 49.944
2021-01-02 | 9:44 | 49.944
2021-01-02 | 9:44 | 49.946
2021-01-02 | 9:44 | 49.943
2021-01-02 | 9:44 | 49.946
2021-01-02 | 9:44 | 49.946
2021-01-02 | 9:44 | 49.946
2021-01-02 | 9:44 | 49.947
2021-01-02 | 9:44 | 49.946
2021-01-02 | 9:44 | 49.948
2021-01-02 | 9:44 | 49.948
2021-01-02 | 9:44 | 49.948
2021-01-02 | 9:44 | 49.948
2021-01-02 | 9:44 | 49.949
2021-01-02 | 9:44 | 49.951
2021-01-02 | 9:44 | 49.95
2021-01-02 | 9:44 | 49.952
2021-01-02 | 9:44 | 49.953
2021-01-02 | 9:44 | 49.956
2021-01-02 | 9:44 | 49.957
2021-01-02 | 9:44 | 49.959
2021-01-02 | 9:44 | 49.959
2021-01-02 | 9:44 | 49.959
2021-01-02 | 9:44 | 49.96
2021-01-02 | 9:44 | 49.961
2021-01-02 | 9:44 | 49.964
2021-01-02 | 9:44 | 49.964
2021-01-02 | 9:45 | 49.966
2021-01-02 | 9:45 | 49.965
2021-01-02 | 9:45 | 49.964
2021-01-02 | 9:45 | 49.966
2021-01-02 | 9:45 | 49.967
2021-01-02 | 9:45 | 49.966
2021-01-02 | 9:45 | 49.964
2021-01-02 | 9:45 | 49.963
2021-01-02 | 9:45 | 49.959
2021-01-02 | 9:45 | 49.957
2021-01-02 | 9:45 | 49.956
2021-01-02 | 9:45 | 49.955
2021-01-02 | 9:45 | 49.954
2021-01-02 | 9:45 | 49.954
2021-01-02 | 9:45 | 49.954
2021-01-02 | 9:45 | 49.954
2021-01-02 | 9:45 | 49.958
2021-01-02 | 9:45 | 49.96
2021-01-02 | 9:45 | 49.962
2021-01-02 | 9:45 | 49.965
2021-01-02 | 9:45 | 49.966
2021-01-02 | 9:45 | 49.968
2021-01-02 | 9:45 | 49.967
2021-01-02 | 9:45 | 49.968
2021-01-02 | 9:45 | 49.967
2021-01-02 | 9:45 | 49.967
2021-01-02 | 9:45 | 49.966
2021-01-02 | 9:45 | 49.966
2021-01-02 | 9:45 | 49.966
2021-01-02 | 9:45 | 49.966
2021-01-02 | 9:45 | 49.964
2021-01-02 | 9:45 | 49.96
2021-01-02 | 9:45 | 49.959
2021-01-02 | 9:45 | 49.958
2021-01-02 | 9:45 | 49.959
2021-01-02 | 9:45 | 49.958
2021-01-02 | 9:45 | 49.96
2021-01-02 | 9:45 | 49.96
2021-01-02 | 9:45 | 49.959
2021-01-02 | 9:45 | 49.959
2021-01-02 | 9:45 | 49.959
2021-01-02 | 9:45 | 49.959
2021-01-02 | 9:45 | 49.959
2021-01-02 | 9:45 | 49.96
2021-01-02 | 9:45 | 49.962
2021-01-02 | 9:45 | 49.963
2021-01-02 | 9:45 | 49.963
2021-01-02 | 9:45 | 49.964
2021-01-02 | 9:45 | 49.965
2021-01-02 | 9:45 | 49.965
2021-01-02 | 9:45 | 49.966
2021-01-02 | 9:45 | 49.965
2021-01-02 | 9:45 | 49.965
2021-01-02 | 9:45 | 49.966
2021-01-02 | 9:45 | 49.967
2021-01-02 | 9:45 | 49.968
2021-01-02 | 9:45 | 49.969
2021-01-02 | 9:45 | 49.968
2021-01-02 | 9:45 | 49.967
2021-01-02 | 9:46 | 49.967
2021-01-02 | 9:46 | 49.966
2021-01-02 | 9:46 | 49.964
2021-01-02 | 9:46 | 49.962
2021-01-02 | 9:46 | 49.961
2021-01-02 | 9:46 | 49.96
2021-01-02 | 9:46 | 49.961
2021-01-02 | 9:46 | 49.962
2021-01-02 | 9:46 | 49.962
2021-01-02 | 9:46 | 49.96
2021-01-02 | 9:46 | 49.961
2021-01-02 | 9:46 | 49.961
2021-01-02 | 9:46 | 49.962
2021-01-02 | 9:46 | 49.961
2021-01-02 | 9:46 | 49.961
2021-01-02 | 9:46 | 49.962
2021-01-02 | 9:46 | 49.959
2021-01-02 | 9:46 | 49.96
2021-01-02 | 9:46 | 49.963
2021-01-02 | 9:46 | 49.964
2021-01-02 | 9:46 | 49.965
2021-01-02 | 9:46 | 49.968
2021-01-02 | 9:46 | 49.973
2021-01-02 | 9:46 | 49.976
2021-01-02 | 9:46 | 49.976
2021-01-02 | 9:46 | 49.976
2021-01-02 | 9:46 | 49.978
2021-01-02 | 9:46 | 49.979
2021-01-02 | 9:46 | 49.977
2021-01-02 | 9:46 | 49.976
2021-01-02 | 9:46 | 49.972
2021-01-02 | 9:46 | 49.968
2021-01-02 | 9:46 | 49.966
2021-01-02 | 9:46 | 49.962
2021-01-02 | 9:46 | 49.96
2021-01-02 | 9:46 | 49.958
2021-01-02 | 9:46 | 49.954
2021-01-02 | 9:46 | 49.95
2021-01-02 | 9:46 | 49.948
2021-01-02 | 9:46 | 49.945
2021-01-02 | 9:46 | 49.947
2021-01-02 | 9:46 | 49.947
2021-01-02 | 9:46 | 49.949
2021-01-02 | 9:46 | 49.948
2021-01-02 | 9:46 | 49.948
2021-01-02 | 9:46 | 49.948
2021-01-02 | 9:46 | 49.949
2021-01-02 | 9:46 | 49.95
2021-01-02 | 9:46 | 49.953
2021-01-02 | 9:46 | 49.955
2021-01-02 | 9:46 | 49.955
2021-01-02 | 9:46 | 49.955
2021-01-02 | 9:46 | 49.955
2021-01-02 | 9:46 | 49.956
2021-01-02 | 9:46 | 49.959
2021-01-02 | 9:46 | 49.962
2021-01-02 | 9:46 | 49.966
2021-01-02 | 9:46 | 49.969
2021-01-02 | 9:46 | 49.971
2021-01-02 | 9:46 | 49.974
2021-01-02 | 9:46 | 49.976
2021-01-02 | 9:47 | 49.978
2021-01-02 | 9:47 | 49.981
2021-01-02 | 9:47 | 49.981
2021-01-02 | 9:47 | 49.982
2021-01-02 | 9:47 | 49.981
2021-01-02 | 9:47 | 49.983
2021-01-02 | 9:47 | 49.984
2021-01-02 | 9:47 | 49.984
2021-01-02 | 9:47 | 49.986
2021-01-02 | 9:47 | 49.985
2021-01-02 | 9:47 | 49.985
2021-01-02 | 9:47 | 49.984
2021-01-02 | 9:47 | 49.982
2021-01-02 | 9:47 | 49.981
2021-01-02 | 9:47 | 49.982
2021-01-02 | 9:47 | 49.983
2021-01-02 | 9:47 | 49.983
2021-01-02 | 9:47 | 49.984
2021-01-02 | 9:47 | 49.983
2021-01-02 | 9:47 | 49.984
2021-01-02 | 9:47 | 49.983
2021-01-02 | 9:47 | 49.983
2021-01-02 | 9:47 | 49.981
2021-01-02 | 9:47 | 49.981
2021-01-02 | 9:47 | 49.979
2021-01-02 | 9:47 | 49.98
2021-01-02 | 9:47 | 49.978
2021-01-02 | 9:47 | 49.976
2021-01-02 | 9:47 | 49.975
2021-01-02 | 9:47 | 49.972
2021-01-02 | 9:47 | 49.972
2021-01-02 | 9:47 | 49.971
2021-01-02 | 9:47 | 49.968
2021-01-02 | 9:47 | 49.968
2021-01-02 | 9:47 | 49.968
2021-01-02 | 9:47 | 49.966
2021-01-02 | 9:47 | 49.964
2021-01-02 | 9:47 | 49.961
2021-01-02 | 9:47 | 49.957
2021-01-02 | 9:47 | 49.954
2021-01-02 | 9:47 | 49.952
2021-01-02 | 9:47 | 49.951
2021-01-02 | 9:47 | 49.951
2021-01-02 | 9:47 | 49.951
2021-01-02 | 9:47 | 49.95
2021-01-02 | 9:47 | 49.949
2021-01-02 | 9:47 | 49.947
2021-01-02 | 9:47 | 49.946
2021-01-02 | 9:47 | 49.944
2021-01-02 | 9:47 | 49.942
2021-01-02 | 9:47 | 49.943
2021-01-02 | 9:47 | 49.944
2021-01-02 | 9:47 | 49.946
2021-01-02 | 9:47 | 49.947
2021-01-02 | 9:47 | 49.948
2021-01-02 | 9:47 | 49.949
2021-01-02 | 9:47 | 49.947
2021-01-02 | 9:47 | 49.948
2021-01-02 | 9:47 | 49.948
2021-01-02 | 9:48 | 49.947
2021-01-02 | 9:48 | 49.945
2021-01-02 | 9:48 | 49.944
2021-01-02 | 9:48 | 49.943
2021-01-02 | 9:48 | 49.943
2021-01-02 | 9:48 | 49.943
2021-01-02 | 9:48 | 49.943
2021-01-02 | 9:48 | 49.944
2021-01-02 | 9:48 | 49.945
2021-01-02 | 9:48 | 49.945
2021-01-02 | 9:48 | 49.944
2021-01-02 | 9:48 | 49.947
2021-01-02 | 9:48 | 49.948
2021-01-02 | 9:48 | 49.947
2021-01-02 | 9:48 | 49.947
2021-01-02 | 9:48 | 49.948
2021-01-02 | 9:48 | 49.95
2021-01-02 | 9:48 | 49.952
2021-01-02 | 9:48 | 49.956
2021-01-02 | 9:48 | 49.956
2021-01-02 | 9:48 | 49.956
2021-01-02 | 9:48 | 49.955
2021-01-02 | 9:48 | 49.952
2021-01-02 | 9:48 | 49.954
2021-01-02 | 9:48 | 49.951
2021-01-02 | 9:48 | 49.945
2021-01-02 | 9:48 | 49.942
2021-01-02 | 9:48 | 49.939
2021-01-02 | 9:48 | 49.934
2021-01-02 | 9:48 | 49.931
2021-01-02 | 9:48 | 49.93
2021-01-02 | 9:48 | 49.927
2021-01-02 | 9:48 | 49.931
2021-01-02 | 9:48 | 49.935
2021-01-02 | 9:48 | 49.936
2021-01-02 | 9:48 | 49.939
2021-01-02 | 9:48 | 49.939
2021-01-02 | 9:48 | 49.94
2021-01-02 | 9:48 | 49.94
2021-01-02 | 9:48 | 49.94
2021-01-02 | 9:48 | 49.941
2021-01-02 | 9:48 | 49.941
2021-01-02 | 9:48 | 49.94
2021-01-02 | 9:48 | 49.939
2021-01-02 | 9:48 | 49.937
2021-01-02 | 9:48 | 49.936
2021-01-02 | 9:48 | 49.936
2021-01-02 | 9:48 | 49.936
2021-01-02 | 9:48 | 49.936
2021-01-02 | 9:48 | 49.939
2021-01-02 | 9:48 | 49.943
2021-01-02 | 9:48 | 49.946
2021-01-02 | 9:48 | 49.949
2021-01-02 | 9:48 | 49.954
2021-01-02 | 9:48 | 49.959
2021-01-02 | 9:48 | 49.964
2021-01-02 | 9:48 | 49.97
2021-01-02 | 9:48 | 49.972
2021-01-02 | 9:48 | 49.976
2021-01-02 | 9:48 | 49.979
2021-01-02 | 9:48 | 49.979
2021-01-02 | 9:49 | 49.981
2021-01-02 | 9:49 | 49.98
2021-01-02 | 9:49 | 49.98
2021-01-02 | 9:49 | 49.979
2021-01-02 | 9:49 | 49.977
2021-01-02 | 9:49 | 49.978
2021-01-02 | 9:49 | 49.978
2021-01-02 | 9:49 | 49.98
2021-01-02 | 9:49 | 49.979
2021-01-02 | 9:49 | 49.982
2021-01-02 | 9:49 | 49.983
2021-01-02 | 9:49 | 49.983
2021-01-02 | 9:49 | 49.982
2021-01-02 | 9:49 | 49.983
2021-01-02 | 9:49 | 49.982
2021-01-02 | 9:49 | 49.982
2021-01-02 | 9:49 | 49.983
2021-01-02 | 9:49 | 49.985
2021-01-02 | 9:49 | 49.986
2021-01-02 | 9:49 | 49.988
2021-01-02 | 9:49 | 49.991
2021-01-02 | 9:49 | 49.994
2021-01-02 | 9:49 | 50.001
2021-01-02 | 9:49 | 50.005
2021-01-02 | 9:49 | 50.012
2021-01-02 | 9:49 | 50.014
2021-01-02 | 9:49 | 50.017
2021-01-02 | 9:49 | 50.018
2021-01-02 | 9:49 | 50.019

## Event 20210106-1
In UTC
Date | Time | Freq
2021-01-06 | 2:18 | 50.106
2021-01-06 | 2:18 | 50.106
2021-01-06 | 2:18 | 50.105
2021-01-06 | 2:18 | 50.106
2021-01-06 | 2:18 | 50.106
2021-01-06 | 2:18 | 50.108
2021-01-06 | 2:18 | 50.106
2021-01-06 | 2:18 | 50.106
2021-01-06 | 2:18 | 50.106
2021-01-06 | 2:18 | 50.106
2021-01-06 | 2:18 | 50.106
2021-01-06 | 2:18 | 50.105
2021-01-06 | 2:18 | 50.105
2021-01-06 | 2:18 | 50.105
2021-01-06 | 2:18 | 50.105
2021-01-06 | 2:18 | 50.104
2021-01-06 | 2:18 | 50.103
2021-01-06 | 2:18 | 50.103
2021-01-06 | 2:18 | 50.102
2021-01-06 | 2:18 | 50.101
2021-01-06 | 2:18 | 50.102
2021-01-06 | 2:18 | 50.1
2021-01-06 | 2:18 | 50.099
2021-01-06 | 2:18 | 50.097
2021-01-06 | 2:18 | 50.096
2021-01-06 | 2:18 | 50.096
2021-01-06 | 2:18 | 50.097
2021-01-06 | 2:18 | 50.098
2021-01-06 | 2:18 | 50.097
2021-01-06 | 2:18 | 50.097
2021-01-06 | 2:18 | 50.095
2021-01-06 | 2:19 | 50.094
2021-01-06 | 2:19 | 50.094
2021-01-06 | 2:19 | 50.093
2021-01-06 | 2:19 | 50.093
2021-01-06 | 2:19 | 50.093
2021-01-06 | 2:19 | 50.095
2021-01-06 | 2:19 | 50.094
2021-01-06 | 2:19 | 50.095
2021-01-06 | 2:19 | 50.094
2021-01-06 | 2:19 | 50.094
2021-01-06 | 2:19 | 50.094
2021-01-06 | 2:19 | 50.093
2021-01-06 | 2:19 | 50.093
2021-01-06 | 2:19 | 50.092
2021-01-06 | 2:19 | 50.093
2021-01-06 | 2:19 | 50.093
2021-01-06 | 2:19 | 50.095
2021-01-06 | 2:19 | 50.096
2021-01-06 | 2:19 | 50.096
2021-01-06 | 2:19 | 50.098
2021-01-06 | 2:19 | 50.098
2021-01-06 | 2:19 | 50.099
2021-01-06 | 2:19 | 50.1
2021-01-06 | 2:19 | 50.1
2021-01-06 | 2:19 | 50.1
2021-01-06 | 2:19 | 50.1
2021-01-06 | 2:19 | 50.101
2021-01-06 | 2:19 | 50.102
2021-01-06 | 2:19 | 50.102
2021-01-06 | 2:19 | 50.103
2021-01-06 | 2:19 | 50.102
2021-01-06 | 2:19 | 50.102
2021-01-06 | 2:19 | 50.1
2021-01-06 | 2:19 | 50.102
2021-01-06 | 2:19 | 50.102
2021-01-06 | 2:19 | 50.101
2021-01-06 | 2:19 | 50.102
2021-01-06 | 2:19 | 50.102
2021-01-06 | 2:19 | 50.102
2021-01-06 | 2:19 | 50.1
2021-01-06 | 2:19 | 50.1
2021-01-06 | 2:19 | 50.099
2021-01-06 | 2:19 | 50.099
2021-01-06 | 2:19 | 50.1
2021-01-06 | 2:19 | 50.1
2021-01-06 | 2:19 | 50.101
2021-01-06 | 2:19 | 50.101
2021-01-06 | 2:19 | 50.1
2021-01-06 | 2:19 | 50.101
2021-01-06 | 2:19 | 50.1
2021-01-06 | 2:19 | 50.1
2021-01-06 | 2:19 | 50.1
2021-01-06 | 2:19 | 50.1
2021-01-06 | 2:19 | 50.101
2021-01-06 | 2:19 | 50.103
2021-01-06 | 2:19 | 50.102
2021-01-06 | 2:19 | 50.102
2021-01-06 | 2:19 | 50.102
2021-01-06 | 2:19 | 50.103
2021-01-06 | 2:20 | 50.102
2021-01-06 | 2:20 | 50.102
2021-01-06 | 2:20 | 50.105
2021-01-06 | 2:20 | 50.107
2021-01-06 | 2:20 | 50.107
2021-01-06 | 2:20 | 50.109
2021-01-06 | 2:20 | 50.11
2021-01-06 | 2:20 | 50.11
2021-01-06 | 2:20 | 50.11
2021-01-06 | 2:20 | 50.109
2021-01-06 | 2:20 | 50.108
2021-01-06 | 2:20 | 50.106
2021-01-06 | 2:20 | 50.105
2021-01-06 | 2:20 | 50.105
2021-01-06 | 2:20 | 50.105
2021-01-06 | 2:20 | 50.106
2021-01-06 | 2:20 | 50.109
2021-01-06 | 2:20 | 50.11
2021-01-06 | 2:20 | 50.097
2021-01-06 | 2:20 | 50.089
2021-01-06 | 2:20 | 50.034
2021-01-06 | 2:20 | 49.986
2021-01-06 | 2:20 | 49.948
2021-01-06 | 2:20 | 49.919
2021-01-06 | 2:20 | 49.896
2021-01-06 | 2:20 | 49.883
2021-01-06 | 2:20 | 49.875
2021-01-06 | 2:20 | 49.871
2021-01-06 | 2:20 | 49.869
2021-01-06 | 2:20 | 49.868
2021-01-06 | 2:20 | 49.869
2021-01-06 | 2:20 | 49.87
2021-01-06 | 2:20 | 49.87
2021-01-06 | 2:20 | 49.872
2021-01-06 | 2:20 | 49.875
2021-01-06 | 2:20 | 49.88
2021-01-06 | 2:20 | 49.883
2021-01-06 | 2:20 | 49.886
2021-01-06 | 2:20 | 49.888
2021-01-06 | 2:20 | 49.89
2021-01-06 | 2:20 | 49.891
2021-01-06 | 2:20 | 49.891
2021-01-06 | 2:20 | 49.888
2021-01-06 | 2:20 | 49.885
2021-01-06 | 2:20 | 49.884
2021-01-06 | 2:20 | 49.883
2021-01-06 | 2:20 | 49.882
2021-01-06 | 2:20 | 49.882
2021-01-06 | 2:20 | 49.881
2021-01-06 | 2:20 | 49.881
2021-01-06 | 2:20 | 49.88
2021-01-06 | 2:20 | 49.881
2021-01-06 | 2:20 | 49.88
2021-01-06 | 2:20 | 49.88
2021-01-06 | 2:20 | 49.879
2021-01-06 | 2:20 | 49.879
2021-01-06 | 2:20 | 49.88
2021-01-06 | 2:20 | 49.878
2021-01-06 | 2:20 | 49.879
2021-01-06 | 2:20 | 49.881
2021-01-06 | 2:20 | 49.882
2021-01-06 | 2:21 | 49.883
2021-01-06 | 2:21 | 49.883
2021-01-06 | 2:21 | 49.882
2021-01-06 | 2:21 | 49.882
2021-01-06 | 2:21 | 49.881
2021-01-06 | 2:21 | 49.88
2021-01-06 | 2:21 | 49.88
2021-01-06 | 2:21 | 49.879
2021-01-06 | 2:21 | 49.879
2021-01-06 | 2:21 | 49.879
2021-01-06 | 2:21 | 49.878
2021-01-06 | 2:21 | 49.877
2021-01-06 | 2:21 | 49.875
2021-01-06 | 2:21 | 49.873
2021-01-06 | 2:21 | 49.871
2021-01-06 | 2:21 | 49.87
2021-01-06 | 2:21 | 49.868
2021-01-06 | 2:21 | 49.867
2021-01-06 | 2:21 | 49.866
2021-01-06 | 2:21 | 49.866
2021-01-06 | 2:21 | 49.865
2021-01-06 | 2:21 | 49.865
2021-01-06 | 2:21 | 49.865
2021-01-06 | 2:21 | 49.864
2021-01-06 | 2:21 | 49.863
2021-01-06 | 2:21 | 49.863
2021-01-06 | 2:21 | 49.862
2021-01-06 | 2:21 | 49.861
2021-01-06 | 2:21 | 49.86
2021-01-06 | 2:21 | 49.859
2021-01-06 | 2:21 | 49.858
2021-01-06 | 2:21 | 49.857
2021-01-06 | 2:21 | 49.857
2021-01-06 | 2:21 | 49.856
2021-01-06 | 2:21 | 49.857
2021-01-06 | 2:21 | 49.858
2021-01-06 | 2:21 | 49.858
2021-01-06 | 2:21 | 49.859
2021-01-06 | 2:21 | 49.859
2021-01-06 | 2:21 | 49.859
2021-01-06 | 2:21 | 49.86
2021-01-06 | 2:21 | 49.86
2021-01-06 | 2:21 | 49.86
2021-01-06 | 2:21 | 49.858
2021-01-06 | 2:21 | 49.857
2021-01-06 | 2:21 | 49.86
2021-01-06 | 2:21 | 49.86
2021-01-06 | 2:21 | 49.86
2021-01-06 | 2:21 | 49.86
2021-01-06 | 2:21 | 49.86
2021-01-06 | 2:21 | 49.859
2021-01-06 | 2:21 | 49.859
2021-01-06 | 2:21 | 49.861
2021-01-06 | 2:21 | 49.86
2021-01-06 | 2:21 | 49.861
2021-01-06 | 2:21 | 49.858
2021-01-06 | 2:21 | 49.857
2021-01-06 | 2:21 | 49.856
2021-01-06 | 2:21 | 49.854
2021-01-06 | 2:22 | 49.856
2021-01-06 | 2:22 | 49.857
2021-01-06 | 2:22 | 49.855
2021-01-06 | 2:22 | 49.854
2021-01-06 | 2:22 | 49.856
2021-01-06 | 2:22 | 49.854
2021-01-06 | 2:22 | 49.854
2021-01-06 | 2:22 | 49.855
2021-01-06 | 2:22 | 49.855
2021-01-06 | 2:22 | 49.856
2021-01-06 | 2:22 | 49.856
2021-01-06 | 2:22 | 49.856
2021-01-06 | 2:22 | 49.857
2021-01-06 | 2:22 | 49.858
2021-01-06 | 2:22 | 49.858
2021-01-06 | 2:22 | 49.858
2021-01-06 | 2:22 | 49.859
2021-01-06 | 2:22 | 49.86
2021-01-06 | 2:22 | 49.861
2021-01-06 | 2:22 | 49.862
2021-01-06 | 2:22 | 49.861
2021-01-06 | 2:22 | 49.861
2021-01-06 | 2:22 | 49.862
2021-01-06 | 2:22 | 49.863
2021-01-06 | 2:22 | 49.863
2021-01-06 | 2:22 | 49.865
2021-01-06 | 2:22 | 49.867
2021-01-06 | 2:22 | 49.867
2021-01-06 | 2:22 | 49.868
2021-01-06 | 2:22 | 49.869
2021-01-06 | 2:22 | 49.872
2021-01-06 | 2:22 | 49.873
2021-01-06 | 2:22 | 49.874
2021-01-06 | 2:22 | 49.874
2021-01-06 | 2:22 | 49.874
2021-01-06 | 2:22 | 49.874
2021-01-06 | 2:22 | 49.874
2021-01-06 | 2:22 | 49.874
2021-01-06 | 2:22 | 49.874
2021-01-06 | 2:22 | 49.876
2021-01-06 | 2:22 | 49.877
2021-01-06 | 2:22 | 49.877
2021-01-06 | 2:22 | 49.879
2021-01-06 | 2:22 | 49.883
2021-01-06 | 2:22 | 49.882
2021-01-06 | 2:22 | 49.883
2021-01-06 | 2:22 | 49.881
2021-01-06 | 2:22 | 49.882
2021-01-06 | 2:22 | 49.882
2021-01-06 | 2:22 | 49.881
2021-01-06 | 2:22 | 49.881
2021-01-06 | 2:22 | 49.88
2021-01-06 | 2:22 | 49.88
2021-01-06 | 2:22 | 49.88
2021-01-06 | 2:22 | 49.88
2021-01-06 | 2:22 | 49.881
2021-01-06 | 2:22 | 49.881
2021-01-06 | 2:22 | 49.88
2021-01-06 | 2:22 | 49.88
2021-01-06 | 2:22 | 49.88
2021-01-06 | 2:22 | 49.884
2021-01-06 | 2:23 | 49.889
2021-01-06 | 2:23 | 49.894
2021-01-06 | 2:23 | 49.899
2021-01-06 | 2:23 | 49.903
2021-01-06 | 2:23 | 49.905
2021-01-06 | 2:23 | 49.908
2021-01-06 | 2:23 | 49.91
2021-01-06 | 2:23 | 49.911
2021-01-06 | 2:23 | 49.912
2021-01-06 | 2:23 | 49.912
2021-01-06 | 2:23 | 49.913
2021-01-06 | 2:23 | 49.912
2021-01-06 | 2:23 | 49.914
2021-01-06 | 2:23 | 49.916
2021-01-06 | 2:23 | 49.915
2021-01-06 | 2:23 | 49.917
2021-01-06 | 2:23 | 49.918
2021-01-06 | 2:23 | 49.919
2021-01-06 | 2:23 | 49.92
2021-01-06 | 2:23 | 49.92
2021-01-06 | 2:23 | 49.924
2021-01-06 | 2:23 | 49.924
2021-01-06 | 2:23 | 49.926
2021-01-06 | 2:23 | 49.928
2021-01-06 | 2:23 | 49.928
2021-01-06 | 2:23 | 49.929
2021-01-06 | 2:23 | 49.929
2021-01-06 | 2:23 | 49.93
2021-01-06 | 2:23 | 49.934
2021-01-06 | 2:23 | 49.936
2021-01-06 | 2:23 | 49.939
2021-01-06 | 2:23 | 49.942
2021-01-06 | 2:23 | 49.942
2021-01-06 | 2:23 | 49.944
2021-01-06 | 2:23 | 49.945
2021-01-06 | 2:23 | 49.947
2021-01-06 | 2:23 | 49.949
2021-01-06 | 2:23 | 49.95
2021-01-06 | 2:23 | 49.951
2021-01-06 | 2:23 | 49.953
2021-01-06 | 2:23 | 49.954
2021-01-06 | 2:23 | 49.956
2021-01-06 | 2:23 | 49.959
2021-01-06 | 2:23 | 49.962
2021-01-06 | 2:23 | 49.965
2021-01-06 | 2:23 | 49.966
2021-01-06 | 2:23 | 49.966
2021-01-06 | 2:23 | 49.965
2021-01-06 | 2:23 | 49.965
2021-01-06 | 2:23 | 49.965
2021-01-06 | 2:23 | 49.964
2021-01-06 | 2:23 | 49.965
2021-01-06 | 2:23 | 49.965
2021-01-06 | 2:23 | 49.965
2021-01-06 | 2:23 | 49.966
2021-01-06 | 2:23 | 49.967
2021-01-06 | 2:23 | 49.968
2021-01-06 | 2:23 | 49.969
2021-01-06 | 2:23 | 49.968
2021-01-06 | 2:24 | 49.968
2021-01-06 | 2:24 | 49.969
2021-01-06 | 2:24 | 49.971
2021-01-06 | 2:24 | 49.976
2021-01-06 | 2:24 | 49.978
2021-01-06 | 2:24 | 49.98
2021-01-06 | 2:24 | 49.979
2021-01-06 | 2:24 | 49.981
2021-01-06 | 2:24 | 49.982
2021-01-06 | 2:24 | 49.983
2021-01-06 | 2:24 | 49.982
2021-01-06 | 2:24 | 49.982
2021-01-06 | 2:24 | 49.983
2021-01-06 | 2:24 | 49.984
2021-01-06 | 2:24 | 49.986
2021-01-06 | 2:24 | 49.987
2021-01-06 | 2:24 | 49.987
2021-01-06 | 2:24 | 49.988
2021-01-06 | 2:24 | 49.99
2021-01-06 | 2:24 | 49.992
2021-01-06 | 2:24 | 49.994
2021-01-06 | 2:24 | 49.997
2021-01-06 | 2:24 | 49.999
2021-01-06 | 2:24 | 50.002
2021-01-06 | 2:24 | 50.005
2021-01-06 | 2:24 | 50.009
2021-01-06 | 2:24 | 50.013
2021-01-06 | 2:24 | 50.017
2021-01-06 | 2:24 | 50.019
2021-01-06 | 2:24 | 50.022

## Event 20210110-1
In UTC
Date | Time | Freq
2021-01-10 | 10:23 | 49.88
2021-01-10 | 10:23 | 49.879
2021-01-10 | 10:23 | 49.88
2021-01-10 | 10:23 | 49.881
2021-01-10 | 10:23 | 49.88
2021-01-10 | 10:23 | 49.881
2021-01-10 | 10:23 | 49.881
2021-01-10 | 10:23 | 49.881
2021-01-10 | 10:23 | 49.884
2021-01-10 | 10:23 | 49.885
2021-01-10 | 10:23 | 49.886
2021-01-10 | 10:23 | 49.888
2021-01-10 | 10:23 | 49.887
2021-01-10 | 10:23 | 49.89
2021-01-10 | 10:23 | 49.891
2021-01-10 | 10:23 | 49.893
2021-01-10 | 10:23 | 49.895
2021-01-10 | 10:23 | 49.898
2021-01-10 | 10:23 | 49.899
2021-01-10 | 10:23 | 49.901
2021-01-10 | 10:23 | 49.902
2021-01-10 | 10:23 | 49.903
2021-01-10 | 10:23 | 49.905
2021-01-10 | 10:23 | 49.907
2021-01-10 | 10:23 | 49.909
2021-01-10 | 10:23 | 49.902
2021-01-10 | 10:23 | 49.893
2021-01-10 | 10:23 | 49.888
2021-01-10 | 10:23 | 49.886
2021-01-10 | 10:23 | 49.884
2021-01-10 | 10:24 | 49.883
2021-01-10 | 10:24 | 49.882
2021-01-10 | 10:24 | 49.882
2021-01-10 | 10:24 | 49.883
2021-01-10 | 10:24 | 49.883
2021-01-10 | 10:24 | 49.884
2021-01-10 | 10:24 | 49.885
2021-01-10 | 10:24 | 49.886
2021-01-10 | 10:24 | 49.886
2021-01-10 | 10:24 | 49.886
2021-01-10 | 10:24 | 49.884
2021-01-10 | 10:24 | 49.885
2021-01-10 | 10:24 | 49.885
2021-01-10 | 10:24 | 49.888
2021-01-10 | 10:24 | 49.891
2021-01-10 | 10:24 | 49.893
2021-01-10 | 10:24 | 49.898
2021-01-10 | 10:24 | 49.899
2021-01-10 | 10:24 | 49.9
2021-01-10 | 10:24 | 49.9
2021-01-10 | 10:24 | 49.898
2021-01-10 | 10:24 | 49.896
2021-01-10 | 10:24 | 49.894
2021-01-10 | 10:24 | 49.892
2021-01-10 | 10:24 | 49.888
2021-01-10 | 10:24 | 49.886
2021-01-10 | 10:24 | 49.884
2021-01-10 | 10:24 | 49.884
2021-01-10 | 10:24 | 49.882
2021-01-10 | 10:24 | 49.88
2021-01-10 | 10:24 | 49.877
2021-01-10 | 10:24 | 49.875
2021-01-10 | 10:24 | 49.873
2021-01-10 | 10:24 | 49.873
2021-01-10 | 10:24 | 49.873
2021-01-10 | 10:24 | 49.873
2021-01-10 | 10:24 | 49.873
2021-01-10 | 10:24 | 49.874
2021-01-10 | 10:24 | 49.873
2021-01-10 | 10:24 | 49.874
2021-01-10 | 10:24 | 49.874
2021-01-10 | 10:24 | 49.875
2021-01-10 | 10:24 | 49.874
2021-01-10 | 10:24 | 49.875
2021-01-10 | 10:24 | 49.875
2021-01-10 | 10:24 | 49.875
2021-01-10 | 10:24 | 49.877
2021-01-10 | 10:24 | 49.876
2021-01-10 | 10:24 | 49.876
2021-01-10 | 10:24 | 49.874
2021-01-10 | 10:24 | 49.875
2021-01-10 | 10:24 | 49.875
2021-01-10 | 10:24 | 49.875
2021-01-10 | 10:24 | 49.877
2021-01-10 | 10:24 | 49.878
2021-01-10 | 10:24 | 49.878
2021-01-10 | 10:24 | 49.881
2021-01-10 | 10:24 | 49.884
2021-01-10 | 10:24 | 49.887
2021-01-10 | 10:24 | 49.889
2021-01-10 | 10:24 | 49.89
2021-01-10 | 10:25 | 49.889
2021-01-10 | 10:25 | 49.881
2021-01-10 | 10:25 | 49.861
2021-01-10 | 10:25 | 49.84
2021-01-10 | 10:25 | 49.823
2021-01-10 | 10:25 | 49.811
2021-01-10 | 10:25 | 49.802
2021-01-10 | 10:25 | 49.798
2021-01-10 | 10:25 | 49.795
2021-01-10 | 10:25 | 49.795
2021-01-10 | 10:25 | 49.798
2021-01-10 | 10:25 | 49.801
2021-01-10 | 10:25 | 49.804
2021-01-10 | 10:25 | 49.808
2021-01-10 | 10:25 | 49.811
2021-01-10 | 10:25 | 49.814
2021-01-10 | 10:25 | 49.817
2021-01-10 | 10:25 | 49.82
2021-01-10 | 10:25 | 49.823
2021-01-10 | 10:25 | 49.825
2021-01-10 | 10:25 | 49.828
2021-01-10 | 10:25 | 49.831
2021-01-10 | 10:25 | 49.833
2021-01-10 | 10:25 | 49.833
2021-01-10 | 10:25 | 49.834
2021-01-10 | 10:25 | 49.835
2021-01-10 | 10:25 | 49.835
2021-01-10 | 10:25 | 49.835
2021-01-10 | 10:25 | 49.833
2021-01-10 | 10:25 | 49.834
2021-01-10 | 10:25 | 49.834
2021-01-10 | 10:25 | 49.832
2021-01-10 | 10:25 | 49.831
2021-01-10 | 10:25 | 49.83
2021-01-10 | 10:25 | 49.831
2021-01-10 | 10:25 | 49.83
2021-01-10 | 10:25 | 49.832
2021-01-10 | 10:25 | 49.831
2021-01-10 | 10:25 | 49.831
2021-01-10 | 10:25 | 49.829
2021-01-10 | 10:25 | 49.829
2021-01-10 | 10:25 | 49.83
2021-01-10 | 10:25 | 49.831
2021-01-10 | 10:25 | 49.833
2021-01-10 | 10:25 | 49.832
2021-01-10 | 10:25 | 49.831
2021-01-10 | 10:25 | 49.832
2021-01-10 | 10:25 | 49.834
2021-01-10 | 10:25 | 49.836
2021-01-10 | 10:25 | 49.837
2021-01-10 | 10:25 | 49.84
2021-01-10 | 10:25 | 49.839
2021-01-10 | 10:25 | 49.841
2021-01-10 | 10:25 | 49.84
2021-01-10 | 10:25 | 49.842
2021-01-10 | 10:25 | 49.844
2021-01-10 | 10:25 | 49.845
2021-01-10 | 10:25 | 49.846
2021-01-10 | 10:25 | 49.848
2021-01-10 | 10:26 | 49.848
2021-01-10 | 10:26 | 49.848
2021-01-10 | 10:26 | 49.85
2021-01-10 | 10:26 | 49.85
2021-01-10 | 10:26 | 49.852
2021-01-10 | 10:26 | 49.852
2021-01-10 | 10:26 | 49.852
2021-01-10 | 10:26 | 49.85
2021-01-10 | 10:26 | 49.849
2021-01-10 | 10:26 | 49.847
2021-01-10 | 10:26 | 49.849
2021-01-10 | 10:26 | 49.848
2021-01-10 | 10:26 | 49.85
2021-01-10 | 10:26 | 49.85
2021-01-10 | 10:26 | 49.849
2021-01-10 | 10:26 | 49.848
2021-01-10 | 10:26 | 49.849
2021-01-10 | 10:26 | 49.85
2021-01-10 | 10:26 | 49.851
2021-01-10 | 10:26 | 49.852
2021-01-10 | 10:26 | 49.852
2021-01-10 | 10:26 | 49.851
2021-01-10 | 10:26 | 49.85
2021-01-10 | 10:26 | 49.849
2021-01-10 | 10:26 | 49.847
2021-01-10 | 10:26 | 49.845
2021-01-10 | 10:26 | 49.843
2021-01-10 | 10:26 | 49.842
2021-01-10 | 10:26 | 49.839
2021-01-10 | 10:26 | 49.837
2021-01-10 | 10:26 | 49.837
2021-01-10 | 10:26 | 49.833
2021-01-10 | 10:26 | 49.83
2021-01-10 | 10:26 | 49.829
2021-01-10 | 10:26 | 49.827
2021-01-10 | 10:26 | 49.825
2021-01-10 | 10:26 | 49.823
2021-01-10 | 10:26 | 49.822
2021-01-10 | 10:26 | 49.821
2021-01-10 | 10:26 | 49.82
2021-01-10 | 10:26 | 49.82
2021-01-10 | 10:26 | 49.821
2021-01-10 | 10:26 | 49.82
2021-01-10 | 10:26 | 49.821
2021-01-10 | 10:26 | 49.817
2021-01-10 | 10:26 | 49.818
2021-01-10 | 10:26 | 49.816
2021-01-10 | 10:26 | 49.817
2021-01-10 | 10:26 | 49.815
2021-01-10 | 10:26 | 49.815
2021-01-10 | 10:26 | 49.813
2021-01-10 | 10:26 | 49.814
2021-01-10 | 10:26 | 49.815
2021-01-10 | 10:26 | 49.816
2021-01-10 | 10:26 | 49.816
2021-01-10 | 10:26 | 49.816
2021-01-10 | 10:26 | 49.819
2021-01-10 | 10:26 | 49.82
2021-01-10 | 10:26 | 49.818
2021-01-10 | 10:26 | 49.817
2021-01-10 | 10:26 | 49.817
2021-01-10 | 10:27 | 49.816
2021-01-10 | 10:27 | 49.818
2021-01-10 | 10:27 | 49.818
2021-01-10 | 10:27 | 49.82
2021-01-10 | 10:27 | 49.821
2021-01-10 | 10:27 | 49.822
2021-01-10 | 10:27 | 49.823
2021-01-10 | 10:27 | 49.824
2021-01-10 | 10:27 | 49.824
2021-01-10 | 10:27 | 49.825
2021-01-10 | 10:27 | 49.828
2021-01-10 | 10:27 | 49.829
2021-01-10 | 10:27 | 49.829
2021-01-10 | 10:27 | 49.828
2021-01-10 | 10:27 | 49.828
2021-01-10 | 10:27 | 49.827
2021-01-10 | 10:27 | 49.825
2021-01-10 | 10:27 | 49.824
2021-01-10 | 10:27 | 49.822
2021-01-10 | 10:27 | 49.823
2021-01-10 | 10:27 | 49.822
2021-01-10 | 10:27 | 49.821
2021-01-10 | 10:27 | 49.821
2021-01-10 | 10:27 | 49.821
2021-01-10 | 10:27 | 49.821
2021-01-10 | 10:27 | 49.822
2021-01-10 | 10:27 | 49.823
2021-01-10 | 10:27 | 49.824
2021-01-10 | 10:27 | 49.826
2021-01-10 | 10:27 | 49.826
2021-01-10 | 10:27 | 49.825
2021-01-10 | 10:27 | 49.824
2021-01-10 | 10:27 | 49.824
2021-01-10 | 10:27 | 49.823
2021-01-10 | 10:27 | 49.823
2021-01-10 | 10:27 | 49.823
2021-01-10 | 10:27 | 49.823
2021-01-10 | 10:27 | 49.823
2021-01-10 | 10:27 | 49.825
2021-01-10 | 10:27 | 49.825
2021-01-10 | 10:27 | 49.823
2021-01-10 | 10:27 | 49.823
2021-01-10 | 10:27 | 49.822
2021-01-10 | 10:27 | 49.822
2021-01-10 | 10:27 | 49.822
2021-01-10 | 10:27 | 49.823
2021-01-10 | 10:27 | 49.822
2021-01-10 | 10:27 | 49.822
2021-01-10 | 10:27 | 49.823
2021-01-10 | 10:27 | 49.824
2021-01-10 | 10:27 | 49.826
2021-01-10 | 10:27 | 49.822
2021-01-10 | 10:27 | 49.821
2021-01-10 | 10:27 | 49.823
2021-01-10 | 10:27 | 49.824
2021-01-10 | 10:27 | 49.824
2021-01-10 | 10:27 | 49.826
2021-01-10 | 10:27 | 49.827
2021-01-10 | 10:27 | 49.827
2021-01-10 | 10:28 | 49.829
2021-01-10 | 10:28 | 49.83
2021-01-10 | 10:28 | 49.832
2021-01-10 | 10:28 | 49.832
2021-01-10 | 10:28 | 49.834
2021-01-10 | 10:28 | 49.835
2021-01-10 | 10:28 | 49.836
2021-01-10 | 10:28 | 49.835
2021-01-10 | 10:28 | 49.836
2021-01-10 | 10:28 | 49.837
2021-01-10 | 10:28 | 49.837
2021-01-10 | 10:28 | 49.842
2021-01-10 | 10:28 | 49.844
2021-01-10 | 10:28 | 49.845
2021-01-10 | 10:28 | 49.847
2021-01-10 | 10:28 | 49.85
2021-01-10 | 10:28 | 49.852
2021-01-10 | 10:28 | 49.856
2021-01-10 | 10:28 | 49.859
2021-01-10 | 10:28 | 49.862
2021-01-10 | 10:28 | 49.864
2021-01-10 | 10:28 | 49.866
2021-01-10 | 10:28 | 49.868
2021-01-10 | 10:28 | 49.869
2021-01-10 | 10:28 | 49.869
2021-01-10 | 10:28 | 49.868
2021-01-10 | 10:28 | 49.865
2021-01-10 | 10:28 | 49.866
2021-01-10 | 10:28 | 49.863
2021-01-10 | 10:28 | 49.863
2021-01-10 | 10:28 | 49.863
2021-01-10 | 10:28 | 49.864
2021-01-10 | 10:28 | 49.863
2021-01-10 | 10:28 | 49.864
2021-01-10 | 10:28 | 49.863
2021-01-10 | 10:28 | 49.861
2021-01-10 | 10:28 | 49.86
2021-01-10 | 10:28 | 49.857
2021-01-10 | 10:28 | 49.856
2021-01-10 | 10:28 | 49.854
2021-01-10 | 10:28 | 49.851
2021-01-10 | 10:28 | 49.848
2021-01-10 | 10:28 | 49.848
2021-01-10 | 10:28 | 49.848
2021-01-10 | 10:28 | 49.85
2021-01-10 | 10:28 | 49.853
2021-01-10 | 10:28 | 49.858
2021-01-10 | 10:28 | 49.866
2021-01-10 | 10:28 | 49.873
2021-01-10 | 10:28 | 49.88
2021-01-10 | 10:28 | 49.884
2021-01-10 | 10:28 | 49.887
2021-01-10 | 10:28 | 49.89
2021-01-10 | 10:28 | 49.892
2021-01-10 | 10:28 | 49.894
2021-01-10 | 10:28 | 49.896
2021-01-10 | 10:28 | 49.896
2021-01-10 | 10:28 | 49.897
2021-01-10 | 10:28 | 49.895
2021-01-10 | 10:28 | 49.895
2021-01-10 | 10:28 | 49.893
2021-01-10 | 10:29 | 49.892
2021-01-10 | 10:29 | 49.891
2021-01-10 | 10:29 | 49.89
2021-01-10 | 10:29 | 49.889
2021-01-10 | 10:29 | 49.89
2021-01-10 | 10:29 | 49.89
2021-01-10 | 10:29 | 49.893
2021-01-10 | 10:29 | 49.895
2021-01-10 | 10:29 | 49.896
2021-01-10 | 10:29 | 49.898
2021-01-10 | 10:29 | 49.9
2021-01-10 | 10:29 | 49.902
2021-01-10 | 10:29 | 49.902
2021-01-10 | 10:29 | 49.906
2021-01-10 | 10:29 | 49.908
2021-01-10 | 10:29 | 49.908
2021-01-10 | 10:29 | 49.91
2021-01-10 | 10:29 | 49.914
2021-01-10 | 10:29 | 49.917
2021-01-10 | 10:29 | 49.919
2021-01-10 | 10:29 | 49.92
2021-01-10 | 10:29 | 49.919
2021-01-10 | 10:29 | 49.918
2021-01-10 | 10:29 | 49.916
2021-01-10 | 10:29 | 49.916
2021-01-10 | 10:29 | 49.915
2021-01-10 | 10:29 | 49.914
2021-01-10 | 10:29 | 49.914
2021-01-10 | 10:29 | 49.915
2021-01-10 | 10:29 | 49.915
2021-01-10 | 10:29 | 49.915
2021-01-10 | 10:29 | 49.914
2021-01-10 | 10:29 | 49.914
2021-01-10 | 10:29 | 49.913
2021-01-10 | 10:29 | 49.913
2021-01-10 | 10:29 | 49.913
2021-01-10 | 10:29 | 49.913
2021-01-10 | 10:29 | 49.916
2021-01-10 | 10:29 | 49.916
2021-01-10 | 10:29 | 49.916
2021-01-10 | 10:29 | 49.917
2021-01-10 | 10:29 | 49.918
2021-01-10 | 10:29 | 49.92
2021-01-10 | 10:29 | 49.92
2021-01-10 | 10:29 | 49.92
2021-01-10 | 10:29 | 49.92
2021-01-10 | 10:29 | 49.92
2021-01-10 | 10:29 | 49.918
2021-01-10 | 10:29 | 49.917
2021-01-10 | 10:29 | 49.917
2021-01-10 | 10:29 | 49.918
2021-01-10 | 10:29 | 49.919
2021-01-10 | 10:29 | 49.919
2021-01-10 | 10:29 | 49.921
2021-01-10 | 10:29 | 49.923
2021-01-10 | 10:29 | 49.922
2021-01-10 | 10:29 | 49.925
2021-01-10 | 10:29 | 49.925
2021-01-10 | 10:29 | 49.927
2021-01-10 | 10:30 | 49.927
2021-01-10 | 10:30 | 49.928
2021-01-10 | 10:30 | 49.927
2021-01-10 | 10:30 | 49.926
2021-01-10 | 10:30 | 49.924
2021-01-10 | 10:30 | 49.921
2021-01-10 | 10:30 | 49.918
2021-01-10 | 10:30 | 49.917
2021-01-10 | 10:30 | 49.915
2021-01-10 | 10:30 | 49.912
2021-01-10 | 10:30 | 49.908
2021-01-10 | 10:30 | 49.905
2021-01-10 | 10:30 | 49.901
2021-01-10 | 10:30 | 49.899
2021-01-10 | 10:30 | 49.898
2021-01-10 | 10:30 | 49.9
2021-01-10 | 10:30 | 49.901
2021-01-10 | 10:30 | 49.903
2021-01-10 | 10:30 | 49.906
2021-01-10 | 10:30 | 49.908
2021-01-10 | 10:30 | 49.913
2021-01-10 | 10:30 | 49.916
2021-01-10 | 10:30 | 49.921
2021-01-10 | 10:30 | 49.923
2021-01-10 | 10:30 | 49.926
2021-01-10 | 10:30 | 49.93
2021-01-10 | 10:30 | 49.933
2021-01-10 | 10:30 | 49.936
2021-01-10 | 10:30 | 49.938
2021-01-10 | 10:30 | 49.939
2021-01-10 | 10:30 | 49.939
2021-01-10 | 10:30 | 49.937
2021-01-10 | 10:30 | 49.934
2021-01-10 | 10:30 | 49.934
2021-01-10 | 10:30 | 49.93
2021-01-10 | 10:30 | 49.929
2021-01-10 | 10:30 | 49.929
2021-01-10 | 10:30 | 49.93
2021-01-10 | 10:30 | 49.932
2021-01-10 | 10:30 | 49.931
2021-01-10 | 10:30 | 49.932
2021-01-10 | 10:30 | 49.934
2021-01-10 | 10:30 | 49.934
2021-01-10 | 10:30 | 49.936
2021-01-10 | 10:30 | 49.935
2021-01-10 | 10:30 | 49.936
2021-01-10 | 10:30 | 49.935
2021-01-10 | 10:30 | 49.934
2021-01-10 | 10:30 | 49.934
2021-01-10 | 10:30 | 49.934
2021-01-10 | 10:30 | 49.932
2021-01-10 | 10:30 | 49.934
2021-01-10 | 10:30 | 49.935
2021-01-10 | 10:30 | 49.936
2021-01-10 | 10:30 | 49.936
2021-01-10 | 10:30 | 49.934
2021-01-10 | 10:30 | 49.934
2021-01-10 | 10:30 | 49.935
2021-01-10 | 10:30 | 49.934
2021-01-10 | 10:30 | 49.934
2021-01-10 | 10:30 | 49.934
2021-01-10 | 10:31 | 49.934
2021-01-10 | 10:31 | 49.933
2021-01-10 | 10:31 | 49.933
2021-01-10 | 10:31 | 49.934
2021-01-10 | 10:31 | 49.935
2021-01-10 | 10:31 | 49.934
2021-01-10 | 10:31 | 49.935
2021-01-10 | 10:31 | 49.935
2021-01-10 | 10:31 | 49.936
2021-01-10 | 10:31 | 49.934
2021-01-10 | 10:31 | 49.933
2021-01-10 | 10:31 | 49.931
2021-01-10 | 10:31 | 49.929
2021-01-10 | 10:31 | 49.928
2021-01-10 | 10:31 | 49.924
2021-01-10 | 10:31 | 49.922
2021-01-10 | 10:31 | 49.919
2021-01-10 | 10:31 | 49.918
2021-01-10 | 10:31 | 49.919
2021-01-10 | 10:31 | 49.918
2021-01-10 | 10:31 | 49.919
2021-01-10 | 10:31 | 49.919
2021-01-10 | 10:31 | 49.92
2021-01-10 | 10:31 | 49.921
2021-01-10 | 10:31 | 49.923
2021-01-10 | 10:31 | 49.926
2021-01-10 | 10:31 | 49.926
2021-01-10 | 10:31 | 49.925
2021-01-10 | 10:31 | 49.928
2021-01-10 | 10:31 | 49.929
2021-01-10 | 10:31 | 49.93
2021-01-10 | 10:31 | 49.931
2021-01-10 | 10:31 | 49.931
2021-01-10 | 10:31 | 49.931
2021-01-10 | 10:31 | 49.93
2021-01-10 | 10:31 | 49.929
2021-01-10 | 10:31 | 49.928
2021-01-10 | 10:31 | 49.926
2021-01-10 | 10:31 | 49.924
2021-01-10 | 10:31 | 49.921
2021-01-10 | 10:31 | 49.92
2021-01-10 | 10:31 | 49.921
2021-01-10 | 10:31 | 49.921
2021-01-10 | 10:31 | 49.922
2021-01-10 | 10:31 | 49.923
2021-01-10 | 10:31 | 49.923
2021-01-10 | 10:31 | 49.924
2021-01-10 | 10:31 | 49.924
2021-01-10 | 10:31 | 49.926
2021-01-10 | 10:31 | 49.927
2021-01-10 | 10:31 | 49.926
2021-01-10 | 10:31 | 49.926
2021-01-10 | 10:31 | 49.927
2021-01-10 | 10:31 | 49.928
2021-01-10 | 10:31 | 49.928
2021-01-10 | 10:31 | 49.93
2021-01-10 | 10:31 | 49.93
2021-01-10 | 10:31 | 49.931
2021-01-10 | 10:31 | 49.931
2021-01-10 | 10:32 | 49.931
2021-01-10 | 10:32 | 49.932
2021-01-10 | 10:32 | 49.931
2021-01-10 | 10:32 | 49.931
2021-01-10 | 10:32 | 49.932
2021-01-10 | 10:32 | 49.932
2021-01-10 | 10:32 | 49.933
2021-01-10 | 10:32 | 49.932
2021-01-10 | 10:32 | 49.932
2021-01-10 | 10:32 | 49.933
2021-01-10 | 10:32 | 49.934
2021-01-10 | 10:32 | 49.934
2021-01-10 | 10:32 | 49.935
2021-01-10 | 10:32 | 49.937
2021-01-10 | 10:32 | 49.94
2021-01-10 | 10:32 | 49.942
2021-01-10 | 10:32 | 49.946
2021-01-10 | 10:32 | 49.949
2021-01-10 | 10:32 | 49.951
2021-01-10 | 10:32 | 49.954
2021-01-10 | 10:32 | 49.954
2021-01-10 | 10:32 | 49.955
2021-01-10 | 10:32 | 49.956
2021-01-10 | 10:32 | 49.957
2021-01-10 | 10:32 | 49.957
2021-01-10 | 10:32 | 49.957
2021-01-10 | 10:32 | 49.958
2021-01-10 | 10:32 | 49.956
2021-01-10 | 10:32 | 49.956
2021-01-10 | 10:32 | 49.955
2021-01-10 | 10:32 | 49.956
2021-01-10 | 10:32 | 49.956
2021-01-10 | 10:32 | 49.957
2021-01-10 | 10:32 | 49.957
2021-01-10 | 10:32 | 49.96
2021-01-10 | 10:32 | 49.964
2021-01-10 | 10:32 | 49.967
2021-01-10 | 10:32 | 49.97
2021-01-10 | 10:32 | 49.972
2021-01-10 | 10:32 | 49.974
2021-01-10 | 10:32 | 49.973
2021-01-10 | 10:32 | 49.973
2021-01-10 | 10:32 | 49.975
2021-01-10 | 10:32 | 49.974
2021-01-10 | 10:32 | 49.976
2021-01-10 | 10:32 | 49.977
2021-01-10 | 10:32 | 49.977
2021-01-10 | 10:32 | 49.979
2021-01-10 | 10:32 | 49.98
2021-01-10 | 10:32 | 49.982
2021-01-10 | 10:32 | 49.985
2021-01-10 | 10:32 | 49.988
2021-01-10 | 10:32 | 49.99
2021-01-10 | 10:32 | 49.993
2021-01-10 | 10:32 | 49.997
2021-01-10 | 10:32 | 49.998
2021-01-10 | 10:32 | 49.998
2021-01-10 | 10:32 | 49.999
2021-01-10 | 10:32 | 50
2021-01-10 | 10:32 | 49.999
2021-01-10 | 10:32 | 50
2021-01-10 | 10:33 | 49.999
2021-01-10 | 10:33 | 50
2021-01-10 | 10:33 | 50
2021-01-10 | 10:33 | 50.002
2021-01-10 | 10:33 | 50.005
2021-01-10 | 10:33 | 50.006
2021-01-10 | 10:33 | 50.009
2021-01-10 | 10:33 | 50.011
2021-01-10 | 10:33 | 50.015
2021-01-10 | 10:33 | 50.019
2021-01-10 | 10:33 | 50.021
2021-01-10 | 10:33 | 50.025
2021-01-10 | 10:33 | 50.029
2021-01-10 | 10:33 | 50.034
2021-01-10 | 10:33 | 50.037
2021-01-10 | 10:33 | 50.04
2021-01-10 | 10:33 | 50.042
2021-01-10 | 10:33 | 50.044
2021-01-10 | 10:33 | 50.046
2021-01-10 | 10:33 | 50.048
2021-01-10 | 10:33 | 50.049
2021-01-10 | 10:33 | 50.05
2021-01-10 | 10:33 | 50.051
2021-01-10 | 10:33 | 50.052
2021-01-10 | 10:33 | 50.054
2021-01-10 | 10:33 | 50.055
2021-01-10 | 10:33 | 50.057
2021-01-10 | 10:33 | 50.059
2021-01-10 | 10:33 | 50.059

## Event 20210115-1
In UTC
Date | Time | Freq
2021-01-15 | 18:17 | 50.104
2021-01-15 | 18:17 | 50.104
2021-01-15 | 18:17 | 50.106
2021-01-15 | 18:17 | 50.107
2021-01-15 | 18:17 | 50.108
2021-01-15 | 18:17 | 50.109
2021-01-15 | 18:17 | 50.11
2021-01-15 | 18:17 | 50.112
2021-01-15 | 18:17 | 50.105
2021-01-15 | 18:17 | 50.115
2021-01-15 | 18:17 | 50.116
2021-01-15 | 18:17 | 50.115
2021-01-15 | 18:17 | 50.112
2021-01-15 | 18:17 | 50.107
2021-01-15 | 18:17 | 50.101
2021-01-15 | 18:17 | 50.095
2021-01-15 | 18:17 | 50.092
2021-01-15 | 18:17 | 50.091
2021-01-15 | 18:17 | 50.089
2021-01-15 | 18:17 | 50.088
2021-01-15 | 18:17 | 50.087
2021-01-15 | 18:17 | 50.089
2021-01-15 | 18:17 | 50.091
2021-01-15 | 18:17 | 50.093
2021-01-15 | 18:17 | 50.094
2021-01-15 | 18:17 | 50.096
2021-01-15 | 18:17 | 50.1
2021-01-15 | 18:17 | 50.102
2021-01-15 | 18:17 | 50.104
2021-01-15 | 18:17 | 50.106
2021-01-15 | 18:18 | 50.108
2021-01-15 | 18:18 | 50.107
2021-01-15 | 18:18 | 50.108
2021-01-15 | 18:18 | 50.107
2021-01-15 | 18:18 | 50.103
2021-01-15 | 18:18 | 50.103
2021-01-15 | 18:18 | 50.1
2021-01-15 | 18:18 | 50.098
2021-01-15 | 18:18 | 50.096
2021-01-15 | 18:18 | 50.092
2021-01-15 | 18:18 | 50.089
2021-01-15 | 18:18 | 50.088
2021-01-15 | 18:18 | 50.086
2021-01-15 | 18:18 | 50.085
2021-01-15 | 18:18 | 50.082
2021-01-15 | 18:18 | 50.082
2021-01-15 | 18:18 | 50.082
2021-01-15 | 18:18 | 50.084
2021-01-15 | 18:18 | 50.087
2021-01-15 | 18:18 | 50.09
2021-01-15 | 18:18 | 50.095
2021-01-15 | 18:18 | 50.096
2021-01-15 | 18:18 | 50.1
2021-01-15 | 18:18 | 50.101
2021-01-15 | 18:18 | 50.102
2021-01-15 | 18:18 | 50.104
2021-01-15 | 18:18 | 50.104
2021-01-15 | 18:18 | 50.106
2021-01-15 | 18:18 | 50.105
2021-01-15 | 18:18 | 50.103
2021-01-15 | 18:18 | 50.099
2021-01-15 | 18:18 | 50.095
2021-01-15 | 18:18 | 50.093
2021-01-15 | 18:18 | 50.089
2021-01-15 | 18:18 | 50.086
2021-01-15 | 18:18 | 50.081
2021-01-15 | 18:18 | 50.079
2021-01-15 | 18:18 | 50.078
2021-01-15 | 18:18 | 50.079
2021-01-15 | 18:18 | 50.079
2021-01-15 | 18:18 | 50.081
2021-01-15 | 18:18 | 50.08
2021-01-15 | 18:18 | 50.077
2021-01-15 | 18:18 | 50.076
2021-01-15 | 18:18 | 50.074
2021-01-15 | 18:18 | 50.072
2021-01-15 | 18:18 | 50.07
2021-01-15 | 18:18 | 50.069
2021-01-15 | 18:18 | 50.068
2021-01-15 | 18:18 | 50.059
2021-01-15 | 18:18 | 50.046
2021-01-15 | 18:18 | 50.034
2021-01-15 | 18:18 | 50.018
2021-01-15 | 18:18 | 50.007
2021-01-15 | 18:18 | 49.995
2021-01-15 | 18:18 | 49.985
2021-01-15 | 18:18 | 49.974
2021-01-15 | 18:18 | 49.968
2021-01-15 | 18:18 | 49.962
2021-01-15 | 18:18 | 49.957
2021-01-15 | 18:18 | 49.952
2021-01-15 | 18:19 | 49.946
2021-01-15 | 18:19 | 49.941
2021-01-15 | 18:19 | 49.936
2021-01-15 | 18:19 | 49.933
2021-01-15 | 18:19 | 49.929
2021-01-15 | 18:19 | 49.927
2021-01-15 | 18:19 | 49.925
2021-01-15 | 18:19 | 49.925
2021-01-15 | 18:19 | 49.927
2021-01-15 | 18:19 | 49.924
2021-01-15 | 18:19 | 49.923
2021-01-15 | 18:19 | 49.92
2021-01-15 | 18:19 | 49.918
2021-01-15 | 18:19 | 49.913
2021-01-15 | 18:19 | 49.907
2021-01-15 | 18:19 | 49.9
2021-01-15 | 18:19 | 49.893
2021-01-15 | 18:19 | 49.888
2021-01-15 | 18:19 | 49.882
2021-01-15 | 18:19 | 49.877
2021-01-15 | 18:19 | 49.877
2021-01-15 | 18:19 | 49.873
2021-01-15 | 18:19 | 49.874
2021-01-15 | 18:19 | 49.875
2021-01-15 | 18:19 | 49.874
2021-01-15 | 18:19 | 49.876
2021-01-15 | 18:19 | 49.877
2021-01-15 | 18:19 | 49.877
2021-01-15 | 18:19 | 49.881
2021-01-15 | 18:19 | 49.882
2021-01-15 | 18:19 | 49.885
2021-01-15 | 18:19 | 49.885
2021-01-15 | 18:19 | 49.884
2021-01-15 | 18:19 | 49.882
2021-01-15 | 18:19 | 49.883
2021-01-15 | 18:19 | 49.883
2021-01-15 | 18:19 | 49.881
2021-01-15 | 18:19 | 49.881
2021-01-15 | 18:19 | 49.878
2021-01-15 | 18:19 | 49.876
2021-01-15 | 18:19 | 49.874
2021-01-15 | 18:19 | 49.873
2021-01-15 | 18:19 | 49.875
2021-01-15 | 18:19 | 49.874
2021-01-15 | 18:19 | 49.875
2021-01-15 | 18:19 | 49.876
2021-01-15 | 18:19 | 49.877
2021-01-15 | 18:19 | 49.878
2021-01-15 | 18:19 | 49.876
2021-01-15 | 18:19 | 49.879
2021-01-15 | 18:19 | 49.881
2021-01-15 | 18:19 | 49.885
2021-01-15 | 18:19 | 49.887
2021-01-15 | 18:19 | 49.89
2021-01-15 | 18:19 | 49.893
2021-01-15 | 18:19 | 49.895
2021-01-15 | 18:19 | 49.898
2021-01-15 | 18:19 | 49.9
2021-01-15 | 18:19 | 49.904
2021-01-15 | 18:20 | 49.906
2021-01-15 | 18:20 | 49.908
2021-01-15 | 18:20 | 49.91
2021-01-15 | 18:20 | 49.913
2021-01-15 | 18:20 | 49.913
2021-01-15 | 18:20 | 49.914
2021-01-15 | 18:20 | 49.913
2021-01-15 | 18:20 | 49.913
2021-01-15 | 18:20 | 49.911
2021-01-15 | 18:20 | 49.911
2021-01-15 | 18:20 | 49.909
2021-01-15 | 18:20 | 49.908
2021-01-15 | 18:20 | 49.908
2021-01-15 | 18:20 | 49.907
2021-01-15 | 18:20 | 49.906
2021-01-15 | 18:20 | 49.906
2021-01-15 | 18:20 | 49.906
2021-01-15 | 18:20 | 49.905
2021-01-15 | 18:20 | 49.904
2021-01-15 | 18:20 | 49.902
2021-01-15 | 18:20 | 49.901
2021-01-15 | 18:20 | 49.899
2021-01-15 | 18:20 | 49.898
2021-01-15 | 18:20 | 49.895
2021-01-15 | 18:20 | 49.89
2021-01-15 | 18:20 | 49.886
2021-01-15 | 18:20 | 49.883
2021-01-15 | 18:20 | 49.877
2021-01-15 | 18:20 | 49.876
2021-01-15 | 18:20 | 49.871
2021-01-15 | 18:20 | 49.868
2021-01-15 | 18:20 | 49.868
2021-01-15 | 18:20 | 49.867
2021-01-15 | 18:20 | 49.867
2021-01-15 | 18:20 | 49.865
2021-01-15 | 18:20 | 49.864
2021-01-15 | 18:20 | 49.863
2021-01-15 | 18:20 | 49.864
2021-01-15 | 18:20 | 49.861
2021-01-15 | 18:20 | 49.859
2021-01-15 | 18:20 | 49.858
2021-01-15 | 18:20 | 49.855
2021-01-15 | 18:20 | 49.852
2021-01-15 | 18:20 | 49.849
2021-01-15 | 18:20 | 49.848
2021-01-15 | 18:20 | 49.848
2021-01-15 | 18:20 | 49.844
2021-01-15 | 18:20 | 49.843
2021-01-15 | 18:20 | 49.841
2021-01-15 | 18:20 | 49.838
2021-01-15 | 18:20 | 49.838
2021-01-15 | 18:20 | 49.834
2021-01-15 | 18:20 | 49.831
2021-01-15 | 18:20 | 49.828
2021-01-15 | 18:20 | 49.826
2021-01-15 | 18:20 | 49.825
2021-01-15 | 18:20 | 49.825
2021-01-15 | 18:20 | 49.827
2021-01-15 | 18:20 | 49.831
2021-01-15 | 18:20 | 49.832
2021-01-15 | 18:20 | 49.834
2021-01-15 | 18:21 | 49.835
2021-01-15 | 18:21 | 49.835
2021-01-15 | 18:21 | 49.837
2021-01-15 | 18:21 | 49.836
2021-01-15 | 18:21 | 49.838
2021-01-15 | 18:21 | 49.838
2021-01-15 | 18:21 | 49.838
2021-01-15 | 18:21 | 49.838
2021-01-15 | 18:21 | 49.838
2021-01-15 | 18:21 | 49.84
2021-01-15 | 18:21 | 49.836
2021-01-15 | 18:21 | 49.835
2021-01-15 | 18:21 | 49.834
2021-01-15 | 18:21 | 49.834
2021-01-15 | 18:21 | 49.833
2021-01-15 | 18:21 | 49.833
2021-01-15 | 18:21 | 49.833
2021-01-15 | 18:21 | 49.834
2021-01-15 | 18:21 | 49.835
2021-01-15 | 18:21 | 49.836
2021-01-15 | 18:21 | 49.835
2021-01-15 | 18:21 | 49.835
2021-01-15 | 18:21 | 49.836
2021-01-15 | 18:21 | 49.837
2021-01-15 | 18:21 | 49.838
2021-01-15 | 18:21 | 49.839
2021-01-15 | 18:21 | 49.841
2021-01-15 | 18:21 | 49.84
2021-01-15 | 18:21 | 49.842
2021-01-15 | 18:21 | 49.842
2021-01-15 | 18:21 | 49.839
2021-01-15 | 18:21 | 49.837
2021-01-15 | 18:21 | 49.836
2021-01-15 | 18:21 | 49.834
2021-01-15 | 18:21 | 49.831
2021-01-15 | 18:21 | 49.827
2021-01-15 | 18:21 | 49.825
2021-01-15 | 18:21 | 49.823
2021-01-15 | 18:21 | 49.819
2021-01-15 | 18:21 | 49.816
2021-01-15 | 18:21 | 49.812
2021-01-15 | 18:21 | 49.811
2021-01-15 | 18:21 | 49.809
2021-01-15 | 18:21 | 49.807
2021-01-15 | 18:21 | 49.809
2021-01-15 | 18:21 | 49.807
2021-01-15 | 18:21 | 49.808
2021-01-15 | 18:21 | 49.81
2021-01-15 | 18:21 | 49.814
2021-01-15 | 18:21 | 49.819
2021-01-15 | 18:21 | 49.826
2021-01-15 | 18:21 | 49.836
2021-01-15 | 18:21 | 49.845
2021-01-15 | 18:21 | 49.856
2021-01-15 | 18:21 | 49.864
2021-01-15 | 18:21 | 49.877
2021-01-15 | 18:21 | 49.887
2021-01-15 | 18:21 | 49.898
2021-01-15 | 18:21 | 49.908
2021-01-15 | 18:22 | 49.92
2021-01-15 | 18:22 | 49.929
2021-01-15 | 18:22 | 49.937
2021-01-15 | 18:22 | 49.943
2021-01-15 | 18:22 | 49.947
2021-01-15 | 18:22 | 49.952
2021-01-15 | 18:22 | 49.954
2021-01-15 | 18:22 | 49.96
2021-01-15 | 18:22 | 49.962
2021-01-15 | 18:22 | 49.963
2021-01-15 | 18:22 | 49.962
2021-01-15 | 18:22 | 49.959
2021-01-15 | 18:22 | 49.96
2021-01-15 | 18:22 | 49.959
2021-01-15 | 18:22 | 49.96
2021-01-15 | 18:22 | 49.957
2021-01-15 | 18:22 | 49.957
2021-01-15 | 18:22 | 49.958
2021-01-15 | 18:22 | 49.957
2021-01-15 | 18:22 | 49.96
2021-01-15 | 18:22 | 49.961
2021-01-15 | 18:22 | 49.964
2021-01-15 | 18:22 | 49.965
2021-01-15 | 18:22 | 49.964
2021-01-15 | 18:22 | 49.965
2021-01-15 | 18:22 | 49.966
2021-01-15 | 18:22 | 49.966
2021-01-15 | 18:22 | 49.966
2021-01-15 | 18:22 | 49.966
2021-01-15 | 18:22 | 49.965
2021-01-15 | 18:22 | 49.964
2021-01-15 | 18:22 | 49.964
2021-01-15 | 18:22 | 49.959
2021-01-15 | 18:22 | 49.957
2021-01-15 | 18:22 | 49.957
2021-01-15 | 18:22 | 49.953
2021-01-15 | 18:22 | 49.953
2021-01-15 | 18:22 | 49.951
2021-01-15 | 18:22 | 49.949
2021-01-15 | 18:22 | 49.947
2021-01-15 | 18:22 | 49.947
2021-01-15 | 18:22 | 49.947
2021-01-15 | 18:22 | 49.949
2021-01-15 | 18:22 | 49.948
2021-01-15 | 18:22 | 49.948
2021-01-15 | 18:22 | 49.949
2021-01-15 | 18:22 | 49.951
2021-01-15 | 18:22 | 49.95
2021-01-15 | 18:22 | 49.952
2021-01-15 | 18:22 | 49.952
2021-01-15 | 18:22 | 49.952
2021-01-15 | 18:22 | 49.951
2021-01-15 | 18:22 | 49.953
2021-01-15 | 18:22 | 49.954
2021-01-15 | 18:22 | 49.954
2021-01-15 | 18:22 | 49.955
2021-01-15 | 18:22 | 49.957
2021-01-15 | 18:22 | 49.958
2021-01-15 | 18:22 | 49.96
2021-01-15 | 18:22 | 49.962
2021-01-15 | 18:22 | 49.963
2021-01-15 | 18:23 | 49.964
2021-01-15 | 18:23 | 49.965
2021-01-15 | 18:23 | 49.969
2021-01-15 | 18:23 | 49.975
2021-01-15 | 18:23 | 49.98
2021-01-15 | 18:23 | 49.982
2021-01-15 | 18:23 | 49.984
2021-01-15 | 18:23 | 49.985
2021-01-15 | 18:23 | 49.987
2021-01-15 | 18:23 | 49.987
2021-01-15 | 18:23 | 49.988
2021-01-15 | 18:23 | 49.989
2021-01-15 | 18:23 | 49.988
2021-01-15 | 18:23 | 49.988
2021-01-15 | 18:23 | 49.984
2021-01-15 | 18:23 | 49.984
2021-01-15 | 18:23 | 49.981
2021-01-15 | 18:23 | 49.977
2021-01-15 | 18:23 | 49.977
2021-01-15 | 18:23 | 49.976
2021-01-15 | 18:23 | 49.976
2021-01-15 | 18:23 | 49.976
2021-01-15 | 18:23 | 49.978
2021-01-15 | 18:23 | 49.981
2021-01-15 | 18:23 | 49.986
2021-01-15 | 18:23 | 49.993
2021-01-15 | 18:23 | 49.997
2021-01-15 | 18:23 | 50.003
2021-01-15 | 18:23 | 50.006

## Event 20210116-1
In UTC
Date | Time | Freq
2021-01-16 | 8:00 | 50.094
2021-01-16 | 8:00 | 50.093
2021-01-16 | 8:00 | 50.09
2021-01-16 | 8:00 | 50.09
2021-01-16 | 8:00 | 50.09
2021-01-16 | 8:00 | 50.089
2021-01-16 | 8:00 | 50.088
2021-01-16 | 8:00 | 50.087
2021-01-16 | 8:00 | 50.087
2021-01-16 | 8:00 | 50.086
2021-01-16 | 8:00 | 50.085
2021-01-16 | 8:00 | 50.084
2021-01-16 | 8:00 | 50.083
2021-01-16 | 8:00 | 50.083
2021-01-16 | 8:00 | 50.085
2021-01-16 | 8:00 | 50.087
2021-01-16 | 8:00 | 50.089
2021-01-16 | 8:00 | 50.088
2021-01-16 | 8:00 | 50.089
2021-01-16 | 8:00 | 50.088
2021-01-16 | 8:00 | 50.089
2021-01-16 | 8:00 | 50.087
2021-01-16 | 8:00 | 50.089
2021-01-16 | 8:00 | 50.092
2021-01-16 | 8:00 | 50.097
2021-01-16 | 8:00 | 50.102
2021-01-16 | 8:00 | 50.109
2021-01-16 | 8:00 | 50.115
2021-01-16 | 8:00 | 50.118
2021-01-16 | 8:00 | 50.123
2021-01-16 | 8:00 | 50.125
2021-01-16 | 8:01 | 50.129
2021-01-16 | 8:01 | 50.13
2021-01-16 | 8:01 | 50.131
2021-01-16 | 8:01 | 50.13
2021-01-16 | 8:01 | 50.133
2021-01-16 | 8:01 | 50.133
2021-01-16 | 8:01 | 50.132
2021-01-16 | 8:01 | 50.129
2021-01-16 | 8:01 | 50.126
2021-01-16 | 8:01 | 50.125
2021-01-16 | 8:01 | 50.123
2021-01-16 | 8:01 | 50.119
2021-01-16 | 8:01 | 50.119
2021-01-16 | 8:01 | 50.12
2021-01-16 | 8:01 | 50.123
2021-01-16 | 8:01 | 50.127
2021-01-16 | 8:01 | 50.127
2021-01-16 | 8:01 | 50.127
2021-01-16 | 8:01 | 50.127
2021-01-16 | 8:01 | 50.126
2021-01-16 | 8:01 | 50.128
2021-01-16 | 8:01 | 50.125
2021-01-16 | 8:01 | 50.126
2021-01-16 | 8:01 | 50.123
2021-01-16 | 8:01 | 50.122
2021-01-16 | 8:01 | 50.12
2021-01-16 | 8:01 | 50.119
2021-01-16 | 8:01 | 50.118
2021-01-16 | 8:01 | 50.116
2021-01-16 | 8:01 | 50.118
2021-01-16 | 8:01 | 50.118
2021-01-16 | 8:01 | 50.118
2021-01-16 | 8:01 | 50.12
2021-01-16 | 8:01 | 50.121
2021-01-16 | 8:01 | 50.122
2021-01-16 | 8:01 | 50.124
2021-01-16 | 8:01 | 50.125
2021-01-16 | 8:01 | 50.128
2021-01-16 | 8:01 | 50.132
2021-01-16 | 8:01 | 50.135
2021-01-16 | 8:01 | 50.139
2021-01-16 | 8:01 | 50.141
2021-01-16 | 8:01 | 50.144
2021-01-16 | 8:01 | 50.148
2021-01-16 | 8:01 | 50.147
2021-01-16 | 8:01 | 50.15
2021-01-16 | 8:01 | 50.152
2021-01-16 | 8:01 | 50.153
2021-01-16 | 8:01 | 50.153
2021-01-16 | 8:01 | 50.156
2021-01-16 | 8:01 | 50.154
2021-01-16 | 8:01 | 50.153
2021-01-16 | 8:01 | 50.152
2021-01-16 | 8:01 | 50.149
2021-01-16 | 8:01 | 50.15
2021-01-16 | 8:01 | 50.148
2021-01-16 | 8:01 | 50.146
2021-01-16 | 8:01 | 50.143
2021-01-16 | 8:01 | 50.142
2021-01-16 | 8:02 | 50.142
2021-01-16 | 8:02 | 50.143
2021-01-16 | 8:02 | 50.143
2021-01-16 | 8:02 | 50.144
2021-01-16 | 8:02 | 50.146
2021-01-16 | 8:02 | 50.15
2021-01-16 | 8:02 | 50.15
2021-01-16 | 8:02 | 50.151
2021-01-16 | 8:02 | 50.151
2021-01-16 | 8:02 | 50.151
2021-01-16 | 8:02 | 50.15
2021-01-16 | 8:02 | 50.15
2021-01-16 | 8:02 | 50.152
2021-01-16 | 8:02 | 50.156
2021-01-16 | 8:02 | 50.158
2021-01-16 | 8:02 | 50.159
2021-01-16 | 8:02 | 50.159
2021-01-16 | 8:02 | 50.155
2021-01-16 | 8:02 | 50.149
2021-01-16 | 8:02 | 50.138
2021-01-16 | 8:02 | 50.127
2021-01-16 | 8:02 | 50.115
2021-01-16 | 8:02 | 50.105
2021-01-16 | 8:02 | 50.097
2021-01-16 | 8:02 | 50.09
2021-01-16 | 8:02 | 50.085
2021-01-16 | 8:02 | 50.077
2021-01-16 | 8:02 | 50.076
2021-01-16 | 8:02 | 50.075
2021-01-16 | 8:02 | 50.076
2021-01-16 | 8:02 | 50.075
2021-01-16 | 8:02 | 50.08
2021-01-16 | 8:02 | 50.081
2021-01-16 | 8:02 | 50.086
2021-01-16 | 8:02 | 50.086
2021-01-16 | 8:02 | 50.088
2021-01-16 | 8:02 | 50.089
2021-01-16 | 8:02 | 50.092
2021-01-16 | 8:02 | 50.093
2021-01-16 | 8:02 | 50.094
2021-01-16 | 8:02 | 50.092
2021-01-16 | 8:02 | 50.092
2021-01-16 | 8:02 | 50.091
2021-01-16 | 8:02 | 50.092
2021-01-16 | 8:02 | 50.088
2021-01-16 | 8:02 | 50.089
2021-01-16 | 8:02 | 50.085
2021-01-16 | 8:02 | 50.083
2021-01-16 | 8:02 | 50.079
2021-01-16 | 8:02 | 50.079
2021-01-16 | 8:02 | 50.079
2021-01-16 | 8:02 | 50.082
2021-01-16 | 8:02 | 50.083
2021-01-16 | 8:02 | 50.086
2021-01-16 | 8:02 | 50.087
2021-01-16 | 8:02 | 50.091
2021-01-16 | 8:02 | 50.091
2021-01-16 | 8:02 | 50.092
2021-01-16 | 8:02 | 50.09
2021-01-16 | 8:02 | 50.091
2021-01-16 | 8:02 | 50.087
2021-01-16 | 8:03 | 50.085
2021-01-16 | 8:03 | 50.081
2021-01-16 | 8:03 | 50.076
2021-01-16 | 8:03 | 50.072
2021-01-16 | 8:03 | 50.067
2021-01-16 | 8:03 | 50.068
2021-01-16 | 8:03 | 50.069
2021-01-16 | 8:03 | 50.072
2021-01-16 | 8:03 | 50.073
2021-01-16 | 8:03 | 50.073
2021-01-16 | 8:03 | 50.075
2021-01-16 | 8:03 | 50.074
2021-01-16 | 8:03 | 50.073
2021-01-16 | 8:03 | 50.069
2021-01-16 | 8:03 | 50.07
2021-01-16 | 8:03 | 50.069
2021-01-16 | 8:03 | 50.072
2021-01-16 | 8:03 | 50.074
2021-01-16 | 8:03 | 50.075
2021-01-16 | 8:03 | 50.078
2021-01-16 | 8:03 | 50.078
2021-01-16 | 8:03 | 50.078
2021-01-16 | 8:03 | 50.077
2021-01-16 | 8:03 | 50.075
2021-01-16 | 8:03 | 50.072
2021-01-16 | 8:03 | 50.065
2021-01-16 | 8:03 | 50.06
2021-01-16 | 8:03 | 50.053
2021-01-16 | 8:03 | 50.051
2021-01-16 | 8:03 | 50.049
2021-01-16 | 8:03 | 50.048
2021-01-16 | 8:03 | 50.047
2021-01-16 | 8:03 | 50.046
2021-01-16 | 8:03 | 50.048
2021-01-16 | 8:03 | 50.047
2021-01-16 | 8:03 | 50.05
2021-01-16 | 8:03 | 50.051
2021-01-16 | 8:03 | 50.048
2021-01-16 | 8:03 | 50.048
2021-01-16 | 8:03 | 50.047
2021-01-16 | 8:03 | 50.051
2021-01-16 | 8:03 | 50.054
2021-01-16 | 8:03 | 50.055
2021-01-16 | 8:03 | 50.056
2021-01-16 | 8:03 | 50.059
2021-01-16 | 8:03 | 50.06
2021-01-16 | 8:03 | 50.06
2021-01-16 | 8:03 | 50.058
2021-01-16 | 8:03 | 50.057
2021-01-16 | 8:03 | 50.054
2021-01-16 | 8:03 | 50.05
2021-01-16 | 8:03 | 50.05
2021-01-16 | 8:03 | 50.045
2021-01-16 | 8:03 | 50.045
2021-01-16 | 8:03 | 50.044
2021-01-16 | 8:03 | 50.041
2021-01-16 | 8:03 | 50.042
2021-01-16 | 8:03 | 50.045
2021-01-16 | 8:03 | 50.05
2021-01-16 | 8:04 | 50.054
2021-01-16 | 8:04 | 50.056
2021-01-16 | 8:04 | 50.059
2021-01-16 | 8:04 | 50.056
2021-01-16 | 8:04 | 50.053
2021-01-16 | 8:04 | 50.053
2021-01-16 | 8:04 | 50.05
2021-01-16 | 8:04 | 50.048
2021-01-16 | 8:04 | 50.046
2021-01-16 | 8:04 | 50.043
2021-01-16 | 8:04 | 50.041
2021-01-16 | 8:04 | 50.038
2021-01-16 | 8:04 | 50.036
2021-01-16 | 8:04 | 50.038
2021-01-16 | 8:04 | 50.037
2021-01-16 | 8:04 | 50.04
2021-01-16 | 8:04 | 50.041
2021-01-16 | 8:04 | 50.043
2021-01-16 | 8:04 | 50.044
2021-01-16 | 8:04 | 50.042
2021-01-16 | 8:04 | 50.044
2021-01-16 | 8:04 | 50.041
2021-01-16 | 8:04 | 50.04
2021-01-16 | 8:04 | 50.039
2021-01-16 | 8:04 | 50.038
2021-01-16 | 8:04 | 50.037
2021-01-16 | 8:04 | 50.036
2021-01-16 | 8:04 | 50.031
2021-01-16 | 8:04 | 50.019
2021-01-16 | 8:04 | 50.004
2021-01-16 | 8:04 | 49.992
2021-01-16 | 8:04 | 49.983
2021-01-16 | 8:04 | 49.978
2021-01-16 | 8:04 | 49.972
2021-01-16 | 8:04 | 49.97
2021-01-16 | 8:04 | 49.967
2021-01-16 | 8:04 | 49.97
2021-01-16 | 8:04 | 49.973
2021-01-16 | 8:04 | 49.971
2021-01-16 | 8:04 | 49.969
2021-01-16 | 8:04 | 49.964
2021-01-16 | 8:04 | 49.963
2021-01-16 | 8:04 | 49.958
2021-01-16 | 8:04 | 49.957
2021-01-16 | 8:04 | 49.956
2021-01-16 | 8:04 | 49.956
2021-01-16 | 8:04 | 49.956
2021-01-16 | 8:04 | 49.954
2021-01-16 | 8:04 | 49.951
2021-01-16 | 8:04 | 49.948
2021-01-16 | 8:04 | 49.944
2021-01-16 | 8:04 | 49.941
2021-01-16 | 8:04 | 49.938
2021-01-16 | 8:04 | 49.935
2021-01-16 | 8:04 | 49.932
2021-01-16 | 8:04 | 49.934
2021-01-16 | 8:04 | 49.934
2021-01-16 | 8:04 | 49.937
2021-01-16 | 8:04 | 49.935
2021-01-16 | 8:04 | 49.936
2021-01-16 | 8:04 | 49.936
2021-01-16 | 8:05 | 49.938
2021-01-16 | 8:05 | 49.939
2021-01-16 | 8:05 | 49.941
2021-01-16 | 8:05 | 49.943
2021-01-16 | 8:05 | 49.944
2021-01-16 | 8:05 | 49.946
2021-01-16 | 8:05 | 49.946
2021-01-16 | 8:05 | 49.947
2021-01-16 | 8:05 | 49.944
2021-01-16 | 8:05 | 49.946
2021-01-16 | 8:05 | 49.944
2021-01-16 | 8:05 | 49.942
2021-01-16 | 8:05 | 49.941
2021-01-16 | 8:05 | 49.939
2021-01-16 | 8:05 | 49.94
2021-01-16 | 8:05 | 49.942
2021-01-16 | 8:05 | 49.945
2021-01-16 | 8:05 | 49.945
2021-01-16 | 8:05 | 49.945
2021-01-16 | 8:05 | 49.945
2021-01-16 | 8:05 | 49.946
2021-01-16 | 8:05 | 49.945
2021-01-16 | 8:05 | 49.946
2021-01-16 | 8:05 | 49.945
2021-01-16 | 8:05 | 49.947
2021-01-16 | 8:05 | 49.948
2021-01-16 | 8:05 | 49.948
2021-01-16 | 8:05 | 49.947
2021-01-16 | 8:05 | 49.946
2021-01-16 | 8:05 | 49.944
2021-01-16 | 8:05 | 49.943
2021-01-16 | 8:05 | 49.941
2021-01-16 | 8:05 | 49.94
2021-01-16 | 8:05 | 49.938
2021-01-16 | 8:05 | 49.937
2021-01-16 | 8:05 | 49.935
2021-01-16 | 8:05 | 49.933
2021-01-16 | 8:05 | 49.928
2021-01-16 | 8:05 | 49.928
2021-01-16 | 8:05 | 49.924
2021-01-16 | 8:05 | 49.924
2021-01-16 | 8:05 | 49.924
2021-01-16 | 8:05 | 49.925
2021-01-16 | 8:05 | 49.923
2021-01-16 | 8:05 | 49.925
2021-01-16 | 8:05 | 49.926
2021-01-16 | 8:05 | 49.928
2021-01-16 | 8:05 | 49.926
2021-01-16 | 8:05 | 49.926
2021-01-16 | 8:05 | 49.925
2021-01-16 | 8:05 | 49.926
2021-01-16 | 8:05 | 49.926
2021-01-16 | 8:05 | 49.927
2021-01-16 | 8:05 | 49.929
2021-01-16 | 8:05 | 49.931
2021-01-16 | 8:05 | 49.929
2021-01-16 | 8:05 | 49.929
2021-01-16 | 8:05 | 49.926
2021-01-16 | 8:05 | 49.925
2021-01-16 | 8:06 | 49.92
2021-01-16 | 8:06 | 49.918
2021-01-16 | 8:06 | 49.916
2021-01-16 | 8:06 | 49.917
2021-01-16 | 8:06 | 49.916
2021-01-16 | 8:06 | 49.918
2021-01-16 | 8:06 | 49.918
2021-01-16 | 8:06 | 49.916
2021-01-16 | 8:06 | 49.918
2021-01-16 | 8:06 | 49.918
2021-01-16 | 8:06 | 49.916
2021-01-16 | 8:06 | 49.917
2021-01-16 | 8:06 | 49.916
2021-01-16 | 8:06 | 49.915
2021-01-16 | 8:06 | 49.915
2021-01-16 | 8:06 | 49.914
2021-01-16 | 8:06 | 49.915
2021-01-16 | 8:06 | 49.914
2021-01-16 | 8:06 | 49.915
2021-01-16 | 8:06 | 49.916
2021-01-16 | 8:06 | 49.916
2021-01-16 | 8:06 | 49.916
2021-01-16 | 8:06 | 49.914
2021-01-16 | 8:06 | 49.913
2021-01-16 | 8:06 | 49.91
2021-01-16 | 8:06 | 49.908
2021-01-16 | 8:06 | 49.904
2021-01-16 | 8:06 | 49.902
2021-01-16 | 8:06 | 49.901
2021-01-16 | 8:06 | 49.905
2021-01-16 | 8:06 | 49.905
2021-01-16 | 8:06 | 49.904
2021-01-16 | 8:06 | 49.902
2021-01-16 | 8:06 | 49.898
2021-01-16 | 8:06 | 49.899
2021-01-16 | 8:06 | 49.897
2021-01-16 | 8:06 | 49.896
2021-01-16 | 8:06 | 49.896
2021-01-16 | 8:06 | 49.896
2021-01-16 | 8:06 | 49.896
2021-01-16 | 8:06 | 49.893
2021-01-16 | 8:06 | 49.896
2021-01-16 | 8:06 | 49.896
2021-01-16 | 8:06 | 49.899
2021-01-16 | 8:06 | 49.899
2021-01-16 | 8:06 | 49.902
2021-01-16 | 8:06 | 49.901
2021-01-16 | 8:06 | 49.904
2021-01-16 | 8:06 | 49.902
2021-01-16 | 8:06 | 49.902
2021-01-16 | 8:06 | 49.899
2021-01-16 | 8:06 | 49.899
2021-01-16 | 8:06 | 49.898
2021-01-16 | 8:06 | 49.897
2021-01-16 | 8:06 | 49.899
2021-01-16 | 8:06 | 49.898
2021-01-16 | 8:06 | 49.899
2021-01-16 | 8:06 | 49.901
2021-01-16 | 8:06 | 49.904
2021-01-16 | 8:06 | 49.911
2021-01-16 | 8:06 | 49.918
2021-01-16 | 8:07 | 49.924
2021-01-16 | 8:07 | 49.931
2021-01-16 | 8:07 | 49.935
2021-01-16 | 8:07 | 49.938
2021-01-16 | 8:07 | 49.939
2021-01-16 | 8:07 | 49.941
2021-01-16 | 8:07 | 49.94
2021-01-16 | 8:07 | 49.943
2021-01-16 | 8:07 | 49.943
2021-01-16 | 8:07 | 49.946
2021-01-16 | 8:07 | 49.946
2021-01-16 | 8:07 | 49.946
2021-01-16 | 8:07 | 49.94
2021-01-16 | 8:07 | 49.938
2021-01-16 | 8:07 | 49.937
2021-01-16 | 8:07 | 49.939
2021-01-16 | 8:07 | 49.939
2021-01-16 | 8:07 | 49.943
2021-01-16 | 8:07 | 49.947
2021-01-16 | 8:07 | 49.949
2021-01-16 | 8:07 | 49.95
2021-01-16 | 8:07 | 49.95
2021-01-16 | 8:07 | 49.949
2021-01-16 | 8:07 | 49.944
2021-01-16 | 8:07 | 49.945
2021-01-16 | 8:07 | 49.943
2021-01-16 | 8:07 | 49.941
2021-01-16 | 8:07 | 49.941
2021-01-16 | 8:07 | 49.939
2021-01-16 | 8:07 | 49.94
2021-01-16 | 8:07 | 49.938
2021-01-16 | 8:07 | 49.94
2021-01-16 | 8:07 | 49.941
2021-01-16 | 8:07 | 49.943
2021-01-16 | 8:07 | 49.941
2021-01-16 | 8:07 | 49.938
2021-01-16 | 8:07 | 49.938
2021-01-16 | 8:07 | 49.941
2021-01-16 | 8:07 | 49.945
2021-01-16 | 8:07 | 49.944
2021-01-16 | 8:07 | 49.946
2021-01-16 | 8:07 | 49.948
2021-01-16 | 8:07 | 49.95
2021-01-16 | 8:07 | 49.949
2021-01-16 | 8:07 | 49.95
2021-01-16 | 8:07 | 49.947
2021-01-16 | 8:07 | 49.949
2021-01-16 | 8:07 | 49.947
2021-01-16 | 8:07 | 49.947
2021-01-16 | 8:07 | 49.948
2021-01-16 | 8:07 | 49.949
2021-01-16 | 8:07 | 49.951
2021-01-16 | 8:07 | 49.953
2021-01-16 | 8:07 | 49.953
2021-01-16 | 8:07 | 49.955
2021-01-16 | 8:07 | 49.958
2021-01-16 | 8:07 | 49.963
2021-01-16 | 8:07 | 49.966
2021-01-16 | 8:07 | 49.97
2021-01-16 | 8:08 | 49.97
2021-01-16 | 8:08 | 49.973
2021-01-16 | 8:08 | 49.976
2021-01-16 | 8:08 | 49.98
2021-01-16 | 8:08 | 49.983
2021-01-16 | 8:08 | 49.99
2021-01-16 | 8:08 | 49.996
2021-01-16 | 8:08 | 50.006
2021-01-16 | 8:08 | 50.015
2021-01-16 | 8:08 | 50.02
2021-01-16 | 8:08 | 50.024
2021-01-16 | 8:08 | 50.028
2021-01-16 | 8:08 | 50.029
2021-01-16 | 8:08 | 50.028
2021-01-16 | 8:08 | 50.029
2021-01-16 | 8:08 | 50.03
2021-01-16 | 8:08 | 50.031
2021-01-16 | 8:08 | 50.034
2021-01-16 | 8:08 | 50.039
2021-01-16 | 8:08 | 50.041
2021-01-16 | 8:08 | 50.039
2021-01-16 | 8:08 | 50.041
2021-01-16 | 8:08 | 50.039
2021-01-16 | 8:08 | 50.041
2021-01-16 | 8:08 | 50.036
2021-01-16 | 8:08 | 50.035
2021-01-16 | 8:08 | 50.034
2021-01-16 | 8:08 | 50.033
2021-01-16 | 8:08 | 50.034
2021-01-16 | 8:08 | 50.036
2021-01-16 | 8:08 | 50.037
2021-01-16 | 8:08 | 50.036
2021-01-16 | 8:08 | 50.036
2021-01-16 | 8:08 | 50.036
2021-01-16 | 8:08 | 50.036
2021-01-16 | 8:08 | 50.039
2021-01-16 | 8:08 | 50.038
2021-01-16 | 8:08 | 50.04
2021-01-16 | 8:08 | 50.038
2021-01-16 | 8:08 | 50.035
2021-01-16 | 8:08 | 50.036
2021-01-16 | 8:08 | 50.034
2021-01-16 | 8:08 | 50.033
2021-01-16 | 8:08 | 50.035
2021-01-16 | 8:08 | 50.034
2021-01-16 | 8:08 | 50.035
2021-01-16 | 8:08 | 50.034
2021-01-16 | 8:08 | 50.036
2021-01-16 | 8:08 | 50.035
2021-01-16 | 8:08 | 50.037
2021-01-16 | 8:08 | 50.038
2021-01-16 | 8:08 | 50.04
2021-01-16 | 8:08 | 50.043
2021-01-16 | 8:08 | 50.042
2021-01-16 | 8:08 | 50.042
2021-01-16 | 8:08 | 50.042
2021-01-16 | 8:08 | 50.043
2021-01-16 | 8:08 | 50.044
2021-01-16 | 8:08 | 50.046
2021-01-16 | 8:08 | 50.045
2021-01-16 | 8:08 | 50.048
2021-01-16 | 8:09 | 50.047
2021-01-16 | 8:09 | 50.048
2021-01-16 | 8:09 | 50.048
2021-01-16 | 8:09 | 50.046
2021-01-16 | 8:09 | 50.048
2021-01-16 | 8:09 | 50.044
2021-01-16 | 8:09 | 50.044
2021-01-16 | 8:09 | 50.043
2021-01-16 | 8:09 | 50.043
2021-01-16 | 8:09 | 50.044
2021-01-16 | 8:09 | 50.048
2021-01-16 | 8:09 | 50.051
2021-01-16 | 8:09 | 50.052
2021-01-16 | 8:09 | 50.055
2021-01-16 | 8:09 | 50.057
2021-01-16 | 8:09 | 50.06
2021-01-16 | 8:09 | 50.062
2021-01-16 | 8:09 | 50.062
2021-01-16 | 8:09 | 50.064
2021-01-16 | 8:09 | 50.062
2021-01-16 | 8:09 | 50.06
2021-01-16 | 8:09 | 50.058
2021-01-16 | 8:09 | 50.055
2021-01-16 | 8:09 | 50.055
2021-01-16 | 8:09 | 50.051
2021-01-16 | 8:09 | 50.048
2021-01-16 | 8:09 | 50.044
2021-01-16 | 8:09 | 50.04
2021-01-16 | 8:09 | 50.041
2021-01-16 | 8:09 | 50.04
2021-01-16 | 8:09 | 50.041
2021-01-16 | 8:09 | 50.043
2021-01-16 | 8:09 | 50.041
2021-01-16 | 8:09 | 50.043
2021-01-16 | 8:09 | 50.043
2021-01-16 | 8:09 | 50.041
2021-01-16 | 8:09 | 50.04
2021-01-16 | 8:09 | 50.04
2021-01-16 | 8:09 | 50.041
2021-01-16 | 8:09 | 50.043
2021-01-16 | 8:09 | 50.045
2021-01-16 | 8:09 | 50.044
2021-01-16 | 8:09 | 50.044
2021-01-16 | 8:09 | 50.046
2021-01-16 | 8:09 | 50.045
2021-01-16 | 8:09 | 50.047
2021-01-16 | 8:09 | 50.049
2021-01-16 | 8:09 | 50.052
2021-01-16 | 8:09 | 50.055
2021-01-16 | 8:09 | 50.053
2021-01-16 | 8:09 | 50.052
2021-01-16 | 8:09 | 50.051
2021-01-16 | 8:09 | 50.049
2021-01-16 | 8:09 | 50.048
2021-01-16 | 8:09 | 50.047
2021-01-16 | 8:09 | 50.042
2021-01-16 | 8:09 | 50.041
2021-01-16 | 8:09 | 50.037
2021-01-16 | 8:09 | 50.044
2021-01-16 | 8:10 | 50.041
2021-01-16 | 8:10 | 50.042
2021-01-16 | 8:10 | 50.044
2021-01-16 | 8:10 | 50.046
2021-01-16 | 8:10 | 50.047
2021-01-16 | 8:10 | 50.048
2021-01-16 | 8:10 | 50.049
2021-01-16 | 8:10 | 50.047
2021-01-16 | 8:10 | 50.045
2021-01-16 | 8:10 | 50.042
2021-01-16 | 8:10 | 50.042
2021-01-16 | 8:10 | 50.036
2021-01-16 | 8:10 | 50.034
2021-01-16 | 8:10 | 50.035
2021-01-16 | 8:10 | 50.034
2021-01-16 | 8:10 | 50.037
2021-01-16 | 8:10 | 50.037
2021-01-16 | 8:10 | 50.037
2021-01-16 | 8:10 | 50.036
2021-01-16 | 8:10 | 50.036
2021-01-16 | 8:10 | 50.034
2021-01-16 | 8:10 | 50.033
2021-01-16 | 8:10 | 50.033
2021-01-16 | 8:10 | 50.033
2021-01-16 | 8:10 | 50.033
2021-01-16 | 8:10 | 50.034
2021-01-16 | 8:10 | 50.034
2021-01-16 | 8:10 | 50.032
2021-01-16 | 8:10 | 50.033
2021-01-16 | 8:10 | 50.033
2021-01-16 | 8:10 | 50.033
2021-01-16 | 8:10 | 50.03
2021-01-16 | 8:10 | 50.028
2021-01-16 | 8:10 | 50.027
2021-01-16 | 8:10 | 50.028
2021-01-16 | 8:10 | 50.027
2021-01-16 | 8:10 | 50.028
2021-01-16 | 8:10 | 50.028
2021-01-16 | 8:10 | 50.024
2021-01-16 | 8:10 | 50.023
2021-01-16 | 8:10 | 50.021
2021-01-16 | 8:10 | 50.025
2021-01-16 | 8:10 | 50.026
2021-01-16 | 8:10 | 50.03
2021-01-16 | 8:10 | 50.033
2021-01-16 | 8:10 | 50.033
2021-01-16 | 8:10 | 50.034
2021-01-16 | 8:10 | 50.035
2021-01-16 | 8:10 | 50.035
2021-01-16 | 8:10 | 50.036
2021-01-16 | 8:10 | 50.04
2021-01-16 | 8:10 | 50.044
2021-01-16 | 8:10 | 50.048
2021-01-16 | 8:10 | 50.051
2021-01-16 | 8:10 | 50.051
2021-01-16 | 8:10 | 50.051
2021-01-16 | 8:10 | 50.05
2021-01-16 | 8:10 | 50.049
2021-01-16 | 8:10 | 50.05
2021-01-16 | 8:10 | 50.05
2021-01-16 | 8:10 | 50.047
2021-01-16 | 8:11 | 50.046
2021-01-16 | 8:11 | 50.044
2021-01-16 | 8:11 | 50.043
2021-01-16 | 8:11 | 50.046
2021-01-16 | 8:11 | 50.05
2021-01-16 | 8:11 | 50.052
2021-01-16 | 8:11 | 50.053
2021-01-16 | 8:11 | 50.055
2021-01-16 | 8:11 | 50.055
2021-01-16 | 8:11 | 50.056
2021-01-16 | 8:11 | 50.058
2021-01-16 | 8:11 | 50.056
2021-01-16 | 8:11 | 50.054
2021-01-16 | 8:11 | 50.054
2021-01-16 | 8:11 | 50.055
2021-01-16 | 8:11 | 50.057
2021-01-16 | 8:11 | 50.059
2021-01-16 | 8:11 | 50.059
2021-01-16 | 8:11 | 50.056
2021-01-16 | 8:11 | 50.057
2021-01-16 | 8:11 | 50.055
2021-01-16 | 8:11 | 50.053
2021-01-16 | 8:11 | 50.054
2021-01-16 | 8:11 | 50.056
2021-01-16 | 8:11 | 50.054
2021-01-16 | 8:11 | 50.057
2021-01-16 | 8:11 | 50.059
2021-01-16 | 8:11 | 50.06
2021-01-16 | 8:11 | 50.06
2021-01-16 | 8:11 | 50.06
2021-01-16 | 8:11 | 50.057
2021-01-16 | 8:11 | 50.054
2021-01-16 | 8:11 | 50.056
2021-01-16 | 8:11 | 50.06
2021-01-16 | 8:11 | 50.064
2021-01-16 | 8:11 | 50.067
2021-01-16 | 8:11 | 50.065
2021-01-16 | 8:11 | 50.063
2021-01-16 | 8:11 | 50.062
2021-01-16 | 8:11 | 50.062
2021-01-16 | 8:11 | 50.063
2021-01-16 | 8:11 | 50.064
2021-01-16 | 8:11 | 50.066
2021-01-16 | 8:11 | 50.07
2021-01-16 | 8:11 | 50.07
2021-01-16 | 8:11 | 50.07
2021-01-16 | 8:11 | 50.072
2021-01-16 | 8:11 | 50.07
2021-01-16 | 8:11 | 50.069
2021-01-16 | 8:11 | 50.07
2021-01-16 | 8:11 | 50.069
2021-01-16 | 8:11 | 50.069
2021-01-16 | 8:11 | 50.07
2021-01-16 | 8:11 | 50.067
2021-01-16 | 8:11 | 50.07
2021-01-16 | 8:11 | 50.069
2021-01-16 | 8:11 | 50.067
2021-01-16 | 8:11 | 50.068
2021-01-16 | 8:11 | 50.067
2021-01-16 | 8:12 | 50.067
2021-01-16 | 8:12 | 50.067
2021-01-16 | 8:12 | 50.066
2021-01-16 | 8:12 | 50.066
2021-01-16 | 8:12 | 50.067
2021-01-16 | 8:12 | 50.067
2021-01-16 | 8:12 | 50.069
2021-01-16 | 8:12 | 50.07
2021-01-16 | 8:12 | 50.072
2021-01-16 | 8:12 | 50.075
2021-01-16 | 8:12 | 50.071
2021-01-16 | 8:12 | 50.072
2021-01-16 | 8:12 | 50.073
2021-01-16 | 8:12 | 50.071
2021-01-16 | 8:12 | 50.071
2021-01-16 | 8:12 | 50.072
2021-01-16 | 8:12 | 50.071
2021-01-16 | 8:12 | 50.073
2021-01-16 | 8:12 | 50.073
2021-01-16 | 8:12 | 50.07
2021-01-16 | 8:12 | 50.071
2021-01-16 | 8:12 | 50.071
2021-01-16 | 8:12 | 50.071
2021-01-16 | 8:12 | 50.071
2021-01-16 | 8:12 | 50.072
2021-01-16 | 8:12 | 50.069
2021-01-16 | 8:12 | 50.07
2021-01-16 | 8:12 | 50.068
2021-01-16 | 8:12 | 50.065
2021-01-16 | 8:12 | 50.066
2021-01-16 | 8:12 | 50.065
2021-01-16 | 8:12 | 50.066
2021-01-16 | 8:12 | 50.066
2021-01-16 | 8:12 | 50.064
2021-01-16 | 8:12 | 50.063
2021-01-16 | 8:12 | 50.066
2021-01-16 | 8:12 | 50.068
2021-01-16 | 8:12 | 50.07
2021-01-16 | 8:12 | 50.073
2021-01-16 | 8:12 | 50.074
2021-01-16 | 8:12 | 50.076
2021-01-16 | 8:12 | 50.075
2021-01-16 | 8:12 | 50.073
2021-01-16 | 8:12 | 50.071
2021-01-16 | 8:12 | 50.07
2021-01-16 | 8:12 | 50.067
2021-01-16 | 8:12 | 50.067
2021-01-16 | 8:12 | 50.067
2021-01-16 | 8:12 | 50.066
2021-01-16 | 8:12 | 50.068
2021-01-16 | 8:12 | 50.067
2021-01-16 | 8:12 | 50.064
2021-01-16 | 8:12 | 50.064
2021-01-16 | 8:12 | 50.064
2021-01-16 | 8:12 | 50.064
2021-01-16 | 8:12 | 50.064
2021-01-16 | 8:12 | 50.063
2021-01-16 | 8:12 | 50.062
2021-01-16 | 8:12 | 50.06
2021-01-16 | 8:12 | 50.061
2021-01-16 | 8:12 | 50.062
2021-01-16 | 8:13 | 50.061
2021-01-16 | 8:13 | 50.061
2021-01-16 | 8:13 | 50.062
2021-01-16 | 8:13 | 50.065
2021-01-16 | 8:13 | 50.068
2021-01-16 | 8:13 | 50.072
2021-01-16 | 8:13 | 50.075
2021-01-16 | 8:13 | 50.075
2021-01-16 | 8:13 | 50.072
2021-01-16 | 8:13 | 50.068
2021-01-16 | 8:13 | 50.062
2021-01-16 | 8:13 | 50.061
2021-01-16 | 8:13 | 50.061
2021-01-16 | 8:13 | 50.058
2021-01-16 | 8:13 | 50.057
2021-01-16 | 8:13 | 50.058
2021-01-16 | 8:13 | 50.059
2021-01-16 | 8:13 | 50.06
2021-01-16 | 8:13 | 50.06
2021-01-16 | 8:13 | 50.062
2021-01-16 | 8:13 | 50.062
2021-01-16 | 8:13 | 50.063
2021-01-16 | 8:13 | 50.068
2021-01-16 | 8:13 | 50.069
2021-01-16 | 8:13 | 50.07
2021-01-16 | 8:13 | 50.07
2021-01-16 | 8:13 | 50.069
2021-01-16 | 8:13 | 50.068
2021-01-16 | 8:13 | 50.067
2021-01-16 | 8:13 | 50.066
2021-01-16 | 8:13 | 50.062
2021-01-16 | 8:13 | 50.059
2021-01-16 | 8:13 | 50.056
2021-01-16 | 8:13 | 50.057
2021-01-16 | 8:13 | 50.058
2021-01-16 | 8:13 | 50.059
2021-01-16 | 8:13 | 50.06
2021-01-16 | 8:13 | 50.064
2021-01-16 | 8:13 | 50.065
2021-01-16 | 8:13 | 50.064
2021-01-16 | 8:13 | 50.066
2021-01-16 | 8:13 | 50.068
2021-01-16 | 8:13 | 50.072
2021-01-16 | 8:13 | 50.071
2021-01-16 | 8:13 | 50.071
2021-01-16 | 8:13 | 50.071
2021-01-16 | 8:13 | 50.072
2021-01-16 | 8:13 | 50.076
2021-01-16 | 8:13 | 50.079
2021-01-16 | 8:13 | 50.078
2021-01-16 | 8:13 | 50.077
2021-01-16 | 8:13 | 50.075
2021-01-16 | 8:13 | 50.075
2021-01-16 | 8:13 | 50.075
2021-01-16 | 8:13 | 50.072
2021-01-16 | 8:13 | 50.073
2021-01-16 | 8:13 | 50.07
2021-01-16 | 8:13 | 50.067
2021-01-16 | 8:13 | 50.066
2021-01-16 | 8:14 | 50.065
2021-01-16 | 8:14 | 50.064
2021-01-16 | 8:14 | 50.063
2021-01-16 | 8:14 | 50.064
2021-01-16 | 8:14 | 50.065
2021-01-16 | 8:14 | 50.068
2021-01-16 | 8:14 | 50.069
2021-01-16 | 8:14 | 50.072
2021-01-16 | 8:14 | 50.074
2021-01-16 | 8:14 | 50.076
2021-01-16 | 8:14 | 50.077
2021-01-16 | 8:14 | 50.076
2021-01-16 | 8:14 | 50.074
2021-01-16 | 8:14 | 50.073
2021-01-16 | 8:14 | 50.071
2021-01-16 | 8:14 | 50.069
2021-01-16 | 8:14 | 50.066
2021-01-16 | 8:14 | 50.066
2021-01-16 | 8:14 | 50.067
2021-01-16 | 8:14 | 50.068
2021-01-16 | 8:14 | 50.063
2021-01-16 | 8:14 | 50.06
2021-01-16 | 8:14 | 50.06
2021-01-16 | 8:14 | 50.061
2021-01-16 | 8:14 | 50.063
2021-01-16 | 8:14 | 50.065
2021-01-16 | 8:14 | 50.066
2021-01-16 | 8:14 | 50.068
2021-01-16 | 8:14 | 50.072
2021-01-16 | 8:14 | 50.07
2021-01-16 | 8:14 | 50.072
2021-01-16 | 8:14 | 50.074
2021-01-16 | 8:14 | 50.074
2021-01-16 | 8:14 | 50.074
2021-01-16 | 8:14 | 50.072
2021-01-16 | 8:14 | 50.069
2021-01-16 | 8:14 | 50.067
2021-01-16 | 8:14 | 50.066
2021-01-16 | 8:14 | 50.064
2021-01-16 | 8:14 | 50.061
2021-01-16 | 8:14 | 50.055
2021-01-16 | 8:14 | 50.051
2021-01-16 | 8:14 | 50.046
2021-01-16 | 8:14 | 50.043
2021-01-16 | 8:14 | 50.04
2021-01-16 | 8:14 | 50.039
2021-01-16 | 8:14 | 50.039
2021-01-16 | 8:14 | 50.04
2021-01-16 | 8:14 | 50.04
2021-01-16 | 8:14 | 50.039
2021-01-16 | 8:14 | 50.037
2021-01-16 | 8:14 | 50.034
2021-01-16 | 8:14 | 50.032
2021-01-16 | 8:14 | 50.031
2021-01-16 | 8:14 | 50.029
2021-01-16 | 8:14 | 50.03
2021-01-16 | 8:14 | 50.029
2021-01-16 | 8:14 | 50.029
2021-01-16 | 8:14 | 50.029
2021-01-16 | 8:14 | 50.027
2021-01-16 | 8:14 | 50.024
2021-01-16 | 8:15 | 50.023
2021-01-16 | 8:15 | 50.022
2021-01-16 | 8:15 | 50.02
2021-01-16 | 8:15 | 50.019
2021-01-16 | 8:15 | 50.021
2021-01-16 | 8:15 | 50.022
2021-01-16 | 8:15 | 50.023
2021-01-16 | 8:15 | 50.029
2021-01-16 | 8:15 | 50.033
2021-01-16 | 8:15 | 50.036
2021-01-16 | 8:15 | 50.037
2021-01-16 | 8:15 | 50.036
2021-01-16 | 8:15 | 50.034
2021-01-16 | 8:15 | 50.032
2021-01-16 | 8:15 | 50.032
2021-01-16 | 8:15 | 50.032
2021-01-16 | 8:15 | 50.028
2021-01-16 | 8:15 | 50.027
2021-01-16 | 8:15 | 50.025
2021-01-16 | 8:15 | 50.023
2021-01-16 | 8:15 | 50.022
2021-01-16 | 8:15 | 50.021
2021-01-16 | 8:15 | 50.018
2021-01-16 | 8:15 | 50.016
2021-01-16 | 8:15 | 50.018
2021-01-16 | 8:15 | 50.016
2021-01-16 | 8:15 | 50.016
2021-01-16 | 8:15 | 50.018
2021-01-16 | 8:15 | 50.018
2021-01-16 | 8:15 | 50.016
2021-01-16 | 8:15 | 50.016
2021-01-16 | 8:15 | 50.014
2021-01-16 | 8:15 | 50.011
2021-01-16 | 8:15 | 50.011
2021-01-16 | 8:15 | 50.01
2021-01-16 | 8:15 | 50.012
2021-01-16 | 8:15 | 50.012
2021-01-16 | 8:15 | 50.011
2021-01-16 | 8:15 | 50.01
2021-01-16 | 8:15 | 50.01
2021-01-16 | 8:15 | 50.009
2021-01-16 | 8:15 | 50.011
2021-01-16 | 8:15 | 50.01
2021-01-16 | 8:15 | 50.016
2021-01-16 | 8:15 | 50.018
2021-01-16 | 8:15 | 50.021
2021-01-16 | 8:15 | 50.022
2021-01-16 | 8:15 | 50.02
2021-01-16 | 8:15 | 50.02
2021-01-16 | 8:15 | 50.018
2021-01-16 | 8:15 | 50.018
2021-01-16 | 8:15 | 50.018
2021-01-16 | 8:15 | 50.019
2021-01-16 | 8:15 | 50.021
2021-01-16 | 8:15 | 50.019
2021-01-16 | 8:15 | 50.017
2021-01-16 | 8:15 | 50.015
2021-01-16 | 8:15 | 50.014
2021-01-16 | 8:15 | 50.014
2021-01-16 | 8:16 | 50.014
2021-01-16 | 8:16 | 50.015
2021-01-16 | 8:16 | 50.016
2021-01-16 | 8:16 | 50.015
2021-01-16 | 8:16 | 50.016
2021-01-16 | 8:16 | 50.016
2021-01-16 | 8:16 | 50.016
2021-01-16 | 8:16 | 50.021
2021-01-16 | 8:16 | 50.022
2021-01-16 | 8:16 | 50.025
2021-01-16 | 8:16 | 50.025
2021-01-16 | 8:16 | 50.026
2021-01-16 | 8:16 | 50.024
2021-01-16 | 8:16 | 50.022
2021-01-16 | 8:16 | 50.019
2021-01-16 | 8:16 | 50.018
2021-01-16 | 8:16 | 50.016
2021-01-16 | 8:16 | 50.014
2021-01-16 | 8:16 | 50.011
2021-01-16 | 8:16 | 50.012
2021-01-16 | 8:16 | 50.011
2021-01-16 | 8:16 | 50.013
2021-01-16 | 8:16 | 50.017
2021-01-16 | 8:16 | 50.018
2021-01-16 | 8:16 | 50.02
2021-01-16 | 8:16 | 50.019
2021-01-16 | 8:16 | 50.021
2021-01-16 | 8:16 | 50.023
2021-01-16 | 8:16 | 50.023
2021-01-16 | 8:16 | 50.023
2021-01-16 | 8:16 | 50.019
2021-01-16 | 8:16 | 50.017
2021-01-16 | 8:16 | 50.014
2021-01-16 | 8:16 | 50.016
2021-01-16 | 8:16 | 50.017
2021-01-16 | 8:16 | 50.016
2021-01-16 | 8:16 | 50.014
2021-01-16 | 8:16 | 50.009
2021-01-16 | 8:16 | 50.009
2021-01-16 | 8:16 | 50.009
2021-01-16 | 8:16 | 50.011
2021-01-16 | 8:16 | 50.012
2021-01-16 | 8:16 | 50.012
2021-01-16 | 8:16 | 50.013
2021-01-16 | 8:16 | 50.011
2021-01-16 | 8:16 | 50.009
2021-01-16 | 8:16 | 50.004
2021-01-16 | 8:16 | 49.997
2021-01-16 | 8:16 | 49.993
2021-01-16 | 8:16 | 49.99
2021-01-16 | 8:16 | 49.991
2021-01-16 | 8:16 | 49.991
2021-01-16 | 8:16 | 49.996
2021-01-16 | 8:16 | 50.001
2021-01-16 | 8:16 | 50.008
2021-01-16 | 8:16 | 50.015
2021-01-16 | 8:16 | 50.021
2021-01-16 | 8:16 | 50.026
2021-01-16 | 8:16 | 50.029
2021-01-16 | 8:16 | 50.029
2021-01-16 | 8:16 | 50.028
2021-01-16 | 8:17 | 50.027
2021-01-16 | 8:17 | 50.027
2021-01-16 | 8:17 | 50.025
2021-01-16 | 8:17 | 50.027
2021-01-16 | 8:17 | 50.027
2021-01-16 | 8:17 | 50.029
2021-01-16 | 8:17 | 50.031
2021-01-16 | 8:17 | 50.031
2021-01-16 | 8:17 | 50.033
2021-01-16 | 8:17 | 50.032
2021-01-16 | 8:17 | 50.031
2021-01-16 | 8:17 | 50.028
2021-01-16 | 8:17 | 50.026
2021-01-16 | 8:17 | 50.029
2021-01-16 | 8:17 | 50.032
2021-01-16 | 8:17 | 50.035
2021-01-16 | 8:17 | 50.037
2021-01-16 | 8:17 | 50.04
2021-01-16 | 8:17 | 50.042
2021-01-16 | 8:17 | 50.043
2021-01-16 | 8:17 | 50.042
2021-01-16 | 8:17 | 50.043
2021-01-16 | 8:17 | 50.041
2021-01-16 | 8:17 | 50.04
2021-01-16 | 8:17 | 50.04
2021-01-16 | 8:17 | 50.037
2021-01-16 | 8:17 | 50.037
2021-01-16 | 8:17 | 50.034
2021-01-16 | 8:17 | 50.033
2021-01-16 | 8:17 | 50.033
2021-01-16 | 8:17 | 50.029
2021-01-16 | 8:17 | 50.026
2021-01-16 | 8:17 | 50.025
2021-01-16 | 8:17 | 50.023
2021-01-16 | 8:17 | 50.022
2021-01-16 | 8:17 | 50.02
2021-01-16 | 8:17 | 50.02
2021-01-16 | 8:17 | 50.021
2021-01-16 | 8:17 | 50.021
2021-01-16 | 8:17 | 50.021
2021-01-16 | 8:17 | 50.024
2021-01-16 | 8:17 | 50.024
2021-01-16 | 8:17 | 50.027
2021-01-16 | 8:17 | 50.027
2021-01-16 | 8:17 | 50.027
2021-01-16 | 8:17 | 50.028
2021-01-16 | 8:17 | 50.027
2021-01-16 | 8:17 | 50.024
2021-01-16 | 8:17 | 50.023
2021-01-16 | 8:17 | 50.02
2021-01-16 | 8:17 | 50.018
2021-01-16 | 8:17 | 50.016
2021-01-16 | 8:17 | 50.016
2021-01-16 | 8:17 | 50.016
2021-01-16 | 8:17 | 50.016
2021-01-16 | 8:17 | 50.015
2021-01-16 | 8:17 | 50.016
2021-01-16 | 8:17 | 50.017
2021-01-16 | 8:17 | 50.021
2021-01-16 | 8:18 | 50.023
2021-01-16 | 8:18 | 50.026
2021-01-16 | 8:18 | 50.026
2021-01-16 | 8:18 | 50.025
2021-01-16 | 8:18 | 50.025
2021-01-16 | 8:18 | 50.024
2021-01-16 | 8:18 | 50.022
2021-01-16 | 8:18 | 50.022
2021-01-16 | 8:18 | 50.02
2021-01-16 | 8:18 | 50.021
2021-01-16 | 8:18 | 50.023
2021-01-16 | 8:18 | 50.024
2021-01-16 | 8:18 | 50.026
2021-01-16 | 8:18 | 50.027
2021-01-16 | 8:18 | 50.028
2021-01-16 | 8:18 | 50.029
2021-01-16 | 8:18 | 50.03
2021-01-16 | 8:18 | 50.03
2021-01-16 | 8:18 | 50.028
2021-01-16 | 8:18 | 50.024
2021-01-16 | 8:18 | 50.022
2021-01-16 | 8:18 | 50.021
2021-01-16 | 8:18 | 50.019
2021-01-16 | 8:18 | 50.019
2021-01-16 | 8:18 | 50.021
2021-01-16 | 8:18 | 50.021
2021-01-16 | 8:18 | 50.025
2021-01-16 | 8:18 | 50.029
2021-01-16 | 8:18 | 50.033
2021-01-16 | 8:18 | 50.043
2021-01-16 | 8:18 | 50.05
2021-01-16 | 8:18 | 50.052
2021-01-16 | 8:18 | 50.052
2021-01-16 | 8:18 | 50.053
2021-01-16 | 8:18 | 50.055
2021-01-16 | 8:18 | 50.056
2021-01-16 | 8:18 | 50.056
2021-01-16 | 8:18 | 50.057
2021-01-16 | 8:18 | 50.055
2021-01-16 | 8:18 | 50.055
2021-01-16 | 8:18 | 50.055
2021-01-16 | 8:18 | 50.055
2021-01-16 | 8:18 | 50.055
2021-01-16 | 8:18 | 50.053
2021-01-16 | 8:18 | 50.054
2021-01-16 | 8:18 | 50.053
2021-01-16 | 8:18 | 50.051
2021-01-16 | 8:18 | 50.05
2021-01-16 | 8:18 | 50.049
2021-01-16 | 8:18 | 50.051
2021-01-16 | 8:18 | 50.051
2021-01-16 | 8:18 | 50.048
2021-01-16 | 8:18 | 50.049
2021-01-16 | 8:18 | 50.047
2021-01-16 | 8:18 | 50.052
2021-01-16 | 8:18 | 50.054
2021-01-16 | 8:18 | 50.054
2021-01-16 | 8:18 | 50.056
2021-01-16 | 8:18 | 50.056
2021-01-16 | 8:18 | 50.058
2021-01-16 | 8:18 | 50.061
2021-01-16 | 8:19 | 50.063
2021-01-16 | 8:19 | 50.066
2021-01-16 | 8:19 | 50.067
2021-01-16 | 8:19 | 50.07
2021-01-16 | 8:19 | 50.07
2021-01-16 | 8:19 | 50.066
2021-01-16 | 8:19 | 50.065
2021-01-16 | 8:19 | 50.064
2021-01-16 | 8:19 | 50.063
2021-01-16 | 8:19 | 50.067
2021-01-16 | 8:19 | 50.067
2021-01-16 | 8:19 | 50.068
2021-01-16 | 8:19 | 50.07
2021-01-16 | 8:19 | 50.071
2021-01-16 | 8:19 | 50.072
2021-01-16 | 8:19 | 50.073
2021-01-16 | 8:19 | 50.07
2021-01-16 | 8:19 | 50.069
2021-01-16 | 8:19 | 50.069
2021-01-16 | 8:19 | 50.067
2021-01-16 | 8:19 | 50.068
2021-01-16 | 8:19 | 50.067
2021-01-16 | 8:19 | 50.066
2021-01-16 | 8:19 | 50.068
2021-01-16 | 8:19 | 50.065
2021-01-16 | 8:19 | 50.065
2021-01-16 | 8:19 | 50.066
2021-01-16 | 8:19 | 50.066
2021-01-16 | 8:19 | 50.067
2021-01-16 | 8:19 | 50.069
2021-01-16 | 8:19 | 50.069
2021-01-16 | 8:19 | 50.071
2021-01-16 | 8:19 | 50.069
2021-01-16 | 8:19 | 50.064
2021-01-16 | 8:19 | 50.063
2021-01-16 | 8:19 | 50.06
2021-01-16 | 8:19 | 50.057
2021-01-16 | 8:19 | 50.055
2021-01-16 | 8:19 | 50.056
2021-01-16 | 8:19 | 50.054
2021-01-16 | 8:19 | 50.053
2021-01-16 | 8:19 | 50.056
2021-01-16 | 8:19 | 50.057
2021-01-16 | 8:19 | 50.058
2021-01-16 | 8:19 | 50.06
2021-01-16 | 8:19 | 50.06
2021-01-16 | 8:19 | 50.062
2021-01-16 | 8:19 | 50.064
2021-01-16 | 8:19 | 50.066
2021-01-16 | 8:19 | 50.067
2021-01-16 | 8:19 | 50.068
2021-01-16 | 8:19 | 50.069
2021-01-16 | 8:19 | 50.07
2021-01-16 | 8:19 | 50.07
2021-01-16 | 8:19 | 50.073
2021-01-16 | 8:19 | 50.075
2021-01-16 | 8:19 | 50.072
2021-01-16 | 8:19 | 50.07
2021-01-16 | 8:19 | 50.066
2021-01-16 | 8:20 | 50.062
2021-01-16 | 8:20 | 50.06
2021-01-16 | 8:20 | 50.06
2021-01-16 | 8:20 | 50.059
2021-01-16 | 8:20 | 50.059
2021-01-16 | 8:20 | 50.058
2021-01-16 | 8:20 | 50.056
2021-01-16 | 8:20 | 50.057
2021-01-16 | 8:20 | 50.059
2021-01-16 | 8:20 | 50.062
2021-01-16 | 8:20 | 50.063
2021-01-16 | 8:20 | 50.059
2021-01-16 | 8:20 | 50.056
2021-01-16 | 8:20 | 50.057
2021-01-16 | 8:20 | 50.057
2021-01-16 | 8:20 | 50.055
2021-01-16 | 8:20 | 50.052
2021-01-16 | 8:20 | 50.051
2021-01-16 | 8:20 | 50.046
2021-01-16 | 8:20 | 50.043
2021-01-16 | 8:20 | 50.046
2021-01-16 | 8:20 | 50.044
2021-01-16 | 8:20 | 50.043
2021-01-16 | 8:20 | 50.042
2021-01-16 | 8:20 | 50.042
2021-01-16 | 8:20 | 50.041
2021-01-16 | 8:20 | 50.042
2021-01-16 | 8:20 | 50.044
2021-01-16 | 8:20 | 50.046
2021-01-16 | 8:20 | 50.046
2021-01-16 | 8:20 | 50.047
2021-01-16 | 8:20 | 50.045
2021-01-16 | 8:20 | 50.045
2021-01-16 | 8:20 | 50.045
2021-01-16 | 8:20 | 50.043
2021-01-16 | 8:20 | 50.042
2021-01-16 | 8:20 | 50.039
2021-01-16 | 8:20 | 50.037
2021-01-16 | 8:20 | 50.037
2021-01-16 | 8:20 | 50.034
2021-01-16 | 8:20 | 50.032
2021-01-16 | 8:20 | 50.032
2021-01-16 | 8:20 | 50.032
2021-01-16 | 8:20 | 50.031
2021-01-16 | 8:20 | 50.032
2021-01-16 | 8:20 | 50.035
2021-01-16 | 8:20 | 50.038
2021-01-16 | 8:20 | 50.043
2021-01-16 | 8:20 | 50.045
2021-01-16 | 8:20 | 50.049
2021-01-16 | 8:20 | 50.055
2021-01-16 | 8:20 | 50.06
2021-01-16 | 8:20 | 50.064
2021-01-16 | 8:20 | 50.064
2021-01-16 | 8:20 | 50.065
2021-01-16 | 8:20 | 50.064
2021-01-16 | 8:20 | 50.063
2021-01-16 | 8:20 | 50.063
2021-01-16 | 8:20 | 50.062
2021-01-16 | 8:20 | 50.061
2021-01-16 | 8:20 | 50.06
2021-01-16 | 8:21 | 50.058
2021-01-16 | 8:21 | 50.055
2021-01-16 | 8:21 | 50.056
2021-01-16 | 8:21 | 50.059
2021-01-16 | 8:21 | 50.061
2021-01-16 | 8:21 | 50.067
2021-01-16 | 8:21 | 50.072
2021-01-16 | 8:21 | 50.075
2021-01-16 | 8:21 | 50.075
2021-01-16 | 8:21 | 50.077
2021-01-16 | 8:21 | 50.073
2021-01-16 | 8:21 | 50.072
2021-01-16 | 8:21 | 50.072
2021-01-16 | 8:21 | 50.07
2021-01-16 | 8:21 | 50.07
2021-01-16 | 8:21 | 50.068
2021-01-16 | 8:21 | 50.066
2021-01-16 | 8:21 | 50.064
2021-01-16 | 8:21 | 50.061
2021-01-16 | 8:21 | 50.059
2021-01-16 | 8:21 | 50.059
2021-01-16 | 8:21 | 50.057
2021-01-16 | 8:21 | 50.056
2021-01-16 | 8:21 | 50.055
2021-01-16 | 8:21 | 50.051
2021-01-16 | 8:21 | 50.05
2021-01-16 | 8:21 | 50.047
2021-01-16 | 8:21 | 50.047
2021-01-16 | 8:21 | 50.048
2021-01-16 | 8:21 | 50.05
2021-01-16 | 8:21 | 50.049
2021-01-16 | 8:21 | 50.05
2021-01-16 | 8:21 | 50.05
2021-01-16 | 8:21 | 50.048
2021-01-16 | 8:21 | 50.049
2021-01-16 | 8:21 | 50.048
2021-01-16 | 8:21 | 50.046
2021-01-16 | 8:21 | 50.047
2021-01-16 | 8:21 | 50.045
2021-01-16 | 8:21 | 50.047
2021-01-16 | 8:21 | 50.05
2021-01-16 | 8:21 | 50.049
2021-01-16 | 8:21 | 50.05
2021-01-16 | 8:21 | 50.051
2021-01-16 | 8:21 | 50.051
2021-01-16 | 8:21 | 50.052
2021-01-16 | 8:21 | 50.051
2021-01-16 | 8:21 | 50.052
2021-01-16 | 8:21 | 50.052
2021-01-16 | 8:21 | 50.053
2021-01-16 | 8:21 | 50.052
2021-01-16 | 8:21 | 50.048
2021-01-16 | 8:21 | 50.045
2021-01-16 | 8:21 | 50.044
2021-01-16 | 8:21 | 50.046
2021-01-16 | 8:21 | 50.049
2021-01-16 | 8:21 | 50.051
2021-01-16 | 8:21 | 50.053
2021-01-16 | 8:21 | 50.057
2021-01-16 | 8:22 | 50.058
2021-01-16 | 8:22 | 50.059
2021-01-16 | 8:22 | 50.058
2021-01-16 | 8:22 | 50.057
2021-01-16 | 8:22 | 50.058
2021-01-16 | 8:22 | 50.059
2021-01-16 | 8:22 | 50.062
2021-01-16 | 8:22 | 50.064
2021-01-16 | 8:22 | 50.064
2021-01-16 | 8:22 | 50.064
2021-01-16 | 8:22 | 50.065
2021-01-16 | 8:22 | 50.065
2021-01-16 | 8:22 | 50.06
2021-01-16 | 8:22 | 50.057
2021-01-16 | 8:22 | 50.051
2021-01-16 | 8:22 | 50.045
2021-01-16 | 8:22 | 50.042
2021-01-16 | 8:22 | 50.039
2021-01-16 | 8:22 | 50.04
2021-01-16 | 8:22 | 50.039
2021-01-16 | 8:22 | 50.04
2021-01-16 | 8:22 | 50.041
2021-01-16 | 8:22 | 50.04
2021-01-16 | 8:22 | 50.044
2021-01-16 | 8:22 | 50.046
2021-01-16 | 8:22 | 50.047
2021-01-16 | 8:22 | 50.05
2021-01-16 | 8:22 | 50.05
2021-01-16 | 8:22 | 50.052
2021-01-16 | 8:22 | 50.054
2021-01-16 | 8:22 | 50.053
2021-01-16 | 8:22 | 50.055
2021-01-16 | 8:22 | 50.054
2021-01-16 | 8:22 | 50.054
2021-01-16 | 8:22 | 50.054
2021-01-16 | 8:22 | 50.055
2021-01-16 | 8:22 | 50.055
2021-01-16 | 8:22 | 50.053
2021-01-16 | 8:22 | 50.053
2021-01-16 | 8:22 | 50.05
2021-01-16 | 8:22 | 50.049
2021-01-16 | 8:22 | 50.044
2021-01-16 | 8:22 | 50.042
2021-01-16 | 8:22 | 50.04
2021-01-16 | 8:22 | 50.038
2021-01-16 | 8:22 | 50.036
2021-01-16 | 8:22 | 50.036
2021-01-16 | 8:22 | 50.035
2021-01-16 | 8:22 | 50.031
2021-01-16 | 8:22 | 50.03
2021-01-16 | 8:22 | 50.028
2021-01-16 | 8:22 | 50.03
2021-01-16 | 8:22 | 50.03
2021-01-16 | 8:22 | 50.031
2021-01-16 | 8:22 | 50.029
2021-01-16 | 8:22 | 50.031
2021-01-16 | 8:22 | 50.03
2021-01-16 | 8:22 | 50.032
2021-01-16 | 8:22 | 50.033
2021-01-16 | 8:22 | 50.037
2021-01-16 | 8:22 | 50.04
2021-01-16 | 8:23 | 50.045
2021-01-16 | 8:23 | 50.044
2021-01-16 | 8:23 | 50.043
2021-01-16 | 8:23 | 50.039
2021-01-16 | 8:23 | 50.035
2021-01-16 | 8:23 | 50.031
2021-01-16 | 8:23 | 50.027
2021-01-16 | 8:23 | 50.024
2021-01-16 | 8:23 | 50.027
2021-01-16 | 8:23 | 50.029
2021-01-16 | 8:23 | 50.035
2021-01-16 | 8:23 | 50.038
2021-01-16 | 8:23 | 50.041
2021-01-16 | 8:23 | 50.043
2021-01-16 | 8:23 | 50.043
2021-01-16 | 8:23 | 50.043
2021-01-16 | 8:23 | 50.042
2021-01-16 | 8:23 | 50.04
2021-01-16 | 8:23 | 50.04
2021-01-16 | 8:23 | 50.041
2021-01-16 | 8:23 | 50.039
2021-01-16 | 8:23 | 50.039
2021-01-16 | 8:23 | 50.034
2021-01-16 | 8:23 | 50.033
2021-01-16 | 8:23 | 50.03
2021-01-16 | 8:23 | 50.029
2021-01-16 | 8:23 | 50.029
2021-01-16 | 8:23 | 50.03
2021-01-16 | 8:23 | 50.03
2021-01-16 | 8:23 | 50.029
2021-01-16 | 8:23 | 50.026
2021-01-16 | 8:23 | 50.024
2021-01-16 | 8:23 | 50.022
2021-01-16 | 8:23 | 50.021
2021-01-16 | 8:23 | 50.019
2021-01-16 | 8:23 | 50.018
2021-01-16 | 8:23 | 50.017
2021-01-16 | 8:23 | 50.016
2021-01-16 | 8:23 | 50.017
2021-01-16 | 8:23 | 50.018
2021-01-16 | 8:23 | 50.02
2021-01-16 | 8:23 | 50.02
2021-01-16 | 8:23 | 50.022
2021-01-16 | 8:23 | 50.022
2021-01-16 | 8:23 | 50.021
2021-01-16 | 8:23 | 50.022
2021-01-16 | 8:23 | 50.027
2021-01-16 | 8:23 | 50.027
2021-01-16 | 8:23 | 50.025
2021-01-16 | 8:23 | 50.023
2021-01-16 | 8:23 | 50.022
2021-01-16 | 8:23 | 50.02
2021-01-16 | 8:23 | 50.019
2021-01-16 | 8:23 | 50.018
2021-01-16 | 8:23 | 50.018
2021-01-16 | 8:23 | 50.019
2021-01-16 | 8:23 | 50.019
2021-01-16 | 8:23 | 50.019
2021-01-16 | 8:23 | 50.017
2021-01-16 | 8:24 | 50.018
2021-01-16 | 8:24 | 50.018
2021-01-16 | 8:24 | 50.019
2021-01-16 | 8:24 | 50.02
2021-01-16 | 8:24 | 50.019
2021-01-16 | 8:24 | 50.016
2021-01-16 | 8:24 | 50.015
2021-01-16 | 8:24 | 50.011
2021-01-16 | 8:24 | 50.007
2021-01-16 | 8:24 | 50.004
2021-01-16 | 8:24 | 50
2021-01-16 | 8:24 | 49.999
2021-01-16 | 8:24 | 49.994
2021-01-16 | 8:24 | 49.995
2021-01-16 | 8:24 | 49.995
2021-01-16 | 8:24 | 49.996
2021-01-16 | 8:24 | 49.998
2021-01-16 | 8:24 | 49.998
2021-01-16 | 8:24 | 49.997
2021-01-16 | 8:24 | 49.998
2021-01-16 | 8:24 | 50.001
2021-01-16 | 8:24 | 50.001
2021-01-16 | 8:24 | 50.005
2021-01-16 | 8:24 | 50.008
2021-01-16 | 8:24 | 50.012
2021-01-16 | 8:24 | 50.015
2021-01-16 | 8:24 | 50.016
2021-01-16 | 8:24 | 50.014
2021-01-16 | 8:24 | 50.012
2021-01-16 | 8:24 | 50.011
2021-01-16 | 8:24 | 50.005
2021-01-16 | 8:24 | 50.002
2021-01-16 | 8:24 | 49.997
2021-01-16 | 8:24 | 49.992
2021-01-16 | 8:24 | 49.986
2021-01-16 | 8:24 | 49.98
2021-01-16 | 8:24 | 49.977
2021-01-16 | 8:24 | 49.975
2021-01-16 | 8:24 | 49.973
2021-01-16 | 8:24 | 49.973
2021-01-16 | 8:24 | 49.973
2021-01-16 | 8:24 | 49.975
2021-01-16 | 8:24 | 49.974
2021-01-16 | 8:24 | 49.975
2021-01-16 | 8:24 | 49.975
2021-01-16 | 8:24 | 49.977
2021-01-16 | 8:24 | 49.977
2021-01-16 | 8:24 | 49.976
2021-01-16 | 8:24 | 49.976
2021-01-16 | 8:24 | 49.974
2021-01-16 | 8:24 | 49.972
2021-01-16 | 8:24 | 49.971
2021-01-16 | 8:24 | 49.965
2021-01-16 | 8:24 | 49.963
2021-01-16 | 8:24 | 49.959
2021-01-16 | 8:24 | 49.96
2021-01-16 | 8:24 | 49.958
2021-01-16 | 8:24 | 49.963
2021-01-16 | 8:24 | 49.963
2021-01-16 | 8:24 | 49.964
2021-01-16 | 8:24 | 49.966
2021-01-16 | 8:25 | 49.967
2021-01-16 | 8:25 | 49.965
2021-01-16 | 8:25 | 49.967
2021-01-16 | 8:25 | 49.965
2021-01-16 | 8:25 | 49.963
2021-01-16 | 8:25 | 49.962
2021-01-16 | 8:25 | 49.96
2021-01-16 | 8:25 | 49.956
2021-01-16 | 8:25 | 49.953
2021-01-16 | 8:25 | 49.954
2021-01-16 | 8:25 | 49.951
2021-01-16 | 8:25 | 49.951
2021-01-16 | 8:25 | 49.95
2021-01-16 | 8:25 | 49.951
2021-01-16 | 8:25 | 49.951
2021-01-16 | 8:25 | 49.954
2021-01-16 | 8:25 | 49.957
2021-01-16 | 8:25 | 49.955
2021-01-16 | 8:25 | 49.955
2021-01-16 | 8:25 | 49.952
2021-01-16 | 8:25 | 49.951
2021-01-16 | 8:25 | 49.948
2021-01-16 | 8:25 | 49.95
2021-01-16 | 8:25 | 49.95
2021-01-16 | 8:25 | 49.949
2021-01-16 | 8:25 | 49.949
2021-01-16 | 8:25 | 49.95
2021-01-16 | 8:25 | 49.948
2021-01-16 | 8:25 | 49.952
2021-01-16 | 8:25 | 49.95
2021-01-16 | 8:25 | 49.953
2021-01-16 | 8:25 | 49.951
2021-01-16 | 8:25 | 49.947
2021-01-16 | 8:25 | 49.944
2021-01-16 | 8:25 | 49.943
2021-01-16 | 8:25 | 49.942
2021-01-16 | 8:25 | 49.94
2021-01-16 | 8:25 | 49.937
2021-01-16 | 8:25 | 49.934
2021-01-16 | 8:25 | 49.934
2021-01-16 | 8:25 | 49.93
2021-01-16 | 8:25 | 49.932
2021-01-16 | 8:25 | 49.932
2021-01-16 | 8:25 | 49.933
2021-01-16 | 8:25 | 49.933
2021-01-16 | 8:25 | 49.934
2021-01-16 | 8:25 | 49.939
2021-01-16 | 8:25 | 49.938
2021-01-16 | 8:25 | 49.941
2021-01-16 | 8:25 | 49.937
2021-01-16 | 8:25 | 49.932
2021-01-16 | 8:25 | 49.929
2021-01-16 | 8:25 | 49.929
2021-01-16 | 8:25 | 49.926
2021-01-16 | 8:25 | 49.926
2021-01-16 | 8:25 | 49.925
2021-01-16 | 8:25 | 49.927
2021-01-16 | 8:25 | 49.929
2021-01-16 | 8:25 | 49.929
2021-01-16 | 8:26 | 49.931
2021-01-16 | 8:26 | 49.931
2021-01-16 | 8:26 | 49.931
2021-01-16 | 8:26 | 49.932
2021-01-16 | 8:26 | 49.931
2021-01-16 | 8:26 | 49.931
2021-01-16 | 8:26 | 49.931
2021-01-16 | 8:26 | 49.93
2021-01-16 | 8:26 | 49.93
2021-01-16 | 8:26 | 49.93
2021-01-16 | 8:26 | 49.931
2021-01-16 | 8:26 | 49.93
2021-01-16 | 8:26 | 49.929
2021-01-16 | 8:26 | 49.928
2021-01-16 | 8:26 | 49.928
2021-01-16 | 8:26 | 49.926
2021-01-16 | 8:26 | 49.929
2021-01-16 | 8:26 | 49.929
2021-01-16 | 8:26 | 49.933
2021-01-16 | 8:26 | 49.938
2021-01-16 | 8:26 | 49.94
2021-01-16 | 8:26 | 49.942
2021-01-16 | 8:26 | 49.943
2021-01-16 | 8:26 | 49.941
2021-01-16 | 8:26 | 49.943
2021-01-16 | 8:26 | 49.943
2021-01-16 | 8:26 | 49.942
2021-01-16 | 8:26 | 49.942
2021-01-16 | 8:26 | 49.944
2021-01-16 | 8:26 | 49.943
2021-01-16 | 8:26 | 49.942
2021-01-16 | 8:26 | 49.941
2021-01-16 | 8:26 | 49.939
2021-01-16 | 8:26 | 49.938
2021-01-16 | 8:26 | 49.938
2021-01-16 | 8:26 | 49.935
2021-01-16 | 8:26 | 49.934
2021-01-16 | 8:26 | 49.93
2021-01-16 | 8:26 | 49.929
2021-01-16 | 8:26 | 49.926
2021-01-16 | 8:26 | 49.927
2021-01-16 | 8:26 | 49.925
2021-01-16 | 8:26 | 49.925
2021-01-16 | 8:26 | 49.924
2021-01-16 | 8:26 | 49.926
2021-01-16 | 8:26 | 49.928
2021-01-16 | 8:26 | 49.93
2021-01-16 | 8:26 | 49.929
2021-01-16 | 8:26 | 49.93
2021-01-16 | 8:26 | 49.928
2021-01-16 | 8:26 | 49.928
2021-01-16 | 8:26 | 49.926
2021-01-16 | 8:26 | 49.923
2021-01-16 | 8:26 | 49.917
2021-01-16 | 8:26 | 49.913
2021-01-16 | 8:26 | 49.909
2021-01-16 | 8:26 | 49.907
2021-01-16 | 8:26 | 49.908
2021-01-16 | 8:26 | 49.91
2021-01-16 | 8:26 | 49.908
2021-01-16 | 8:26 | 49.912
2021-01-16 | 8:27 | 49.914
2021-01-16 | 8:27 | 49.918
2021-01-16 | 8:27 | 49.922
2021-01-16 | 8:27 | 49.921
2021-01-16 | 8:27 | 49.923
2021-01-16 | 8:27 | 49.925
2021-01-16 | 8:27 | 49.923
2021-01-16 | 8:27 | 49.925
2021-01-16 | 8:27 | 49.924
2021-01-16 | 8:27 | 49.925
2021-01-16 | 8:27 | 49.925
2021-01-16 | 8:27 | 49.924
2021-01-16 | 8:27 | 49.927
2021-01-16 | 8:27 | 49.928
2021-01-16 | 8:27 | 49.929
2021-01-16 | 8:27 | 49.928
2021-01-16 | 8:27 | 49.925
2021-01-16 | 8:27 | 49.922
2021-01-16 | 8:27 | 49.92
2021-01-16 | 8:27 | 49.92
2021-01-16 | 8:27 | 49.921
2021-01-16 | 8:27 | 49.922
2021-01-16 | 8:27 | 49.921
2021-01-16 | 8:27 | 49.917
2021-01-16 | 8:27 | 49.915
2021-01-16 | 8:27 | 49.914
2021-01-16 | 8:27 | 49.916
2021-01-16 | 8:27 | 49.916
2021-01-16 | 8:27 | 49.918
2021-01-16 | 8:27 | 49.92
2021-01-16 | 8:27 | 49.918
2021-01-16 | 8:27 | 49.917
2021-01-16 | 8:27 | 49.917
2021-01-16 | 8:27 | 49.917
2021-01-16 | 8:27 | 49.919
2021-01-16 | 8:27 | 49.918
2021-01-16 | 8:27 | 49.919
2021-01-16 | 8:27 | 49.917
2021-01-16 | 8:27 | 49.918
2021-01-16 | 8:27 | 49.922
2021-01-16 | 8:27 | 49.921
2021-01-16 | 8:27 | 49.923
2021-01-16 | 8:27 | 49.921
2021-01-16 | 8:27 | 49.92
2021-01-16 | 8:27 | 49.919
2021-01-16 | 8:27 | 49.917
2021-01-16 | 8:27 | 49.913
2021-01-16 | 8:27 | 49.91
2021-01-16 | 8:27 | 49.905
2021-01-16 | 8:27 | 49.904
2021-01-16 | 8:27 | 49.902
2021-01-16 | 8:27 | 49.904
2021-01-16 | 8:27 | 49.906
2021-01-16 | 8:27 | 49.906
2021-01-16 | 8:27 | 49.91
2021-01-16 | 8:27 | 49.913
2021-01-16 | 8:27 | 49.914
2021-01-16 | 8:27 | 49.914
2021-01-16 | 8:27 | 49.915
2021-01-16 | 8:28 | 49.912
2021-01-16 | 8:28 | 49.912
2021-01-16 | 8:28 | 49.911
2021-01-16 | 8:28 | 49.915
2021-01-16 | 8:28 | 49.919
2021-01-16 | 8:28 | 49.919
2021-01-16 | 8:28 | 49.919
2021-01-16 | 8:28 | 49.917
2021-01-16 | 8:28 | 49.919
2021-01-16 | 8:28 | 49.916
2021-01-16 | 8:28 | 49.915
2021-01-16 | 8:28 | 49.915
2021-01-16 | 8:28 | 49.912
2021-01-16 | 8:28 | 49.91
2021-01-16 | 8:28 | 49.908
2021-01-16 | 8:28 | 49.907
2021-01-16 | 8:28 | 49.906
2021-01-16 | 8:28 | 49.905
2021-01-16 | 8:28 | 49.903
2021-01-16 | 8:28 | 49.904
2021-01-16 | 8:28 | 49.906
2021-01-16 | 8:28 | 49.904
2021-01-16 | 8:28 | 49.907
2021-01-16 | 8:28 | 49.908
2021-01-16 | 8:28 | 49.907
2021-01-16 | 8:28 | 49.909
2021-01-16 | 8:28 | 49.908
2021-01-16 | 8:28 | 49.909
2021-01-16 | 8:28 | 49.911
2021-01-16 | 8:28 | 49.909
2021-01-16 | 8:28 | 49.909
2021-01-16 | 8:28 | 49.906
2021-01-16 | 8:28 | 49.904
2021-01-16 | 8:28 | 49.902
2021-01-16 | 8:28 | 49.9
2021-01-16 | 8:28 | 49.903
2021-01-16 | 8:28 | 49.904
2021-01-16 | 8:28 | 49.908
2021-01-16 | 8:28 | 49.907
2021-01-16 | 8:28 | 49.905
2021-01-16 | 8:28 | 49.905
2021-01-16 | 8:28 | 49.901
2021-01-16 | 8:28 | 49.901
2021-01-16 | 8:28 | 49.9
2021-01-16 | 8:28 | 49.898
2021-01-16 | 8:28 | 49.896
2021-01-16 | 8:28 | 49.891
2021-01-16 | 8:28 | 49.89
2021-01-16 | 8:28 | 49.89
2021-01-16 | 8:28 | 49.887
2021-01-16 | 8:28 | 49.883
2021-01-16 | 8:28 | 49.882
2021-01-16 | 8:28 | 49.882
2021-01-16 | 8:28 | 49.882
2021-01-16 | 8:28 | 49.882
2021-01-16 | 8:28 | 49.884
2021-01-16 | 8:28 | 49.884
2021-01-16 | 8:28 | 49.886
2021-01-16 | 8:28 | 49.884
2021-01-16 | 8:28 | 49.885
2021-01-16 | 8:28 | 49.884
2021-01-16 | 8:29 | 49.886
2021-01-16 | 8:29 | 49.884
2021-01-16 | 8:29 | 49.885
2021-01-16 | 8:29 | 49.885
2021-01-16 | 8:29 | 49.886
2021-01-16 | 8:29 | 49.882
2021-01-16 | 8:29 | 49.884
2021-01-16 | 8:29 | 49.881
2021-01-16 | 8:29 | 49.881
2021-01-16 | 8:29 | 49.879
2021-01-16 | 8:29 | 49.877
2021-01-16 | 8:29 | 49.873
2021-01-16 | 8:29 | 49.873
2021-01-16 | 8:29 | 49.868
2021-01-16 | 8:29 | 49.87
2021-01-16 | 8:29 | 49.871
2021-01-16 | 8:29 | 49.874
2021-01-16 | 8:29 | 49.876
2021-01-16 | 8:29 | 49.881
2021-01-16 | 8:29 | 49.883
2021-01-16 | 8:29 | 49.885
2021-01-16 | 8:29 | 49.885
2021-01-16 | 8:29 | 49.888
2021-01-16 | 8:29 | 49.889
2021-01-16 | 8:29 | 49.895
2021-01-16 | 8:29 | 49.895
2021-01-16 | 8:29 | 49.895
2021-01-16 | 8:29 | 49.897
2021-01-16 | 8:29 | 49.898
2021-01-16 | 8:29 | 49.9
2021-01-16 | 8:29 | 49.902
2021-01-16 | 8:29 | 49.905
2021-01-16 | 8:29 | 49.907
2021-01-16 | 8:29 | 49.911
2021-01-16 | 8:29 | 49.913
2021-01-16 | 8:29 | 49.915
2021-01-16 | 8:29 | 49.915
2021-01-16 | 8:29 | 49.919
2021-01-16 | 8:29 | 49.925
2021-01-16 | 8:29 | 49.932
2021-01-16 | 8:29 | 49.937
2021-01-16 | 8:29 | 49.943
2021-01-16 | 8:29 | 49.95
2021-01-16 | 8:29 | 49.955
2021-01-16 | 8:29 | 49.961
2021-01-16 | 8:29 | 49.967
2021-01-16 | 8:29 | 49.971
2021-01-16 | 8:29 | 49.972
2021-01-16 | 8:29 | 49.973
2021-01-16 | 8:29 | 49.971
2021-01-16 | 8:29 | 49.97
2021-01-16 | 8:29 | 49.967
2021-01-16 | 8:29 | 49.965
2021-01-16 | 8:29 | 49.961
2021-01-16 | 8:29 | 49.963
2021-01-16 | 8:29 | 49.964
2021-01-16 | 8:29 | 49.964
2021-01-16 | 8:29 | 49.962
2021-01-16 | 8:29 | 49.962
2021-01-16 | 8:30 | 49.957
2021-01-16 | 8:30 | 49.96
2021-01-16 | 8:30 | 49.962
2021-01-16 | 8:30 | 49.963
2021-01-16 | 8:30 | 49.963
2021-01-16 | 8:30 | 49.964
2021-01-16 | 8:30 | 49.969
2021-01-16 | 8:30 | 49.973
2021-01-16 | 8:30 | 49.975
2021-01-16 | 8:30 | 49.973
2021-01-16 | 8:30 | 49.973
2021-01-16 | 8:30 | 49.971
2021-01-16 | 8:30 | 49.972
2021-01-16 | 8:30 | 49.971
2021-01-16 | 8:30 | 49.968
2021-01-16 | 8:30 | 49.963
2021-01-16 | 8:30 | 49.963
2021-01-16 | 8:30 | 49.959
2021-01-16 | 8:30 | 49.958
2021-01-16 | 8:30 | 49.957
2021-01-16 | 8:30 | 49.955
2021-01-16 | 8:30 | 49.956
2021-01-16 | 8:30 | 49.955
2021-01-16 | 8:30 | 49.954
2021-01-16 | 8:30 | 49.954
2021-01-16 | 8:30 | 49.954
2021-01-16 | 8:30 | 49.952
2021-01-16 | 8:30 | 49.95
2021-01-16 | 8:30 | 49.954
2021-01-16 | 8:30 | 49.954
2021-01-16 | 8:30 | 49.957
2021-01-16 | 8:30 | 49.958
2021-01-16 | 8:30 | 49.962
2021-01-16 | 8:30 | 49.963
2021-01-16 | 8:30 | 49.965
2021-01-16 | 8:30 | 49.963
2021-01-16 | 8:30 | 49.962
2021-01-16 | 8:30 | 49.964
2021-01-16 | 8:30 | 49.966
2021-01-16 | 8:30 | 49.968
2021-01-16 | 8:30 | 49.968
2021-01-16 | 8:30 | 49.967
2021-01-16 | 8:30 | 49.965
2021-01-16 | 8:30 | 49.967
2021-01-16 | 8:30 | 49.965
2021-01-16 | 8:30 | 49.967
2021-01-16 | 8:30 | 49.966
2021-01-16 | 8:30 | 49.967
2021-01-16 | 8:30 | 49.968
2021-01-16 | 8:30 | 49.97
2021-01-16 | 8:30 | 49.971
2021-01-16 | 8:30 | 49.97
2021-01-16 | 8:30 | 49.97
2021-01-16 | 8:30 | 49.968
2021-01-16 | 8:30 | 49.972
2021-01-16 | 8:30 | 49.977
2021-01-16 | 8:30 | 49.982
2021-01-16 | 8:30 | 49.985
2021-01-16 | 8:30 | 49.987
2021-01-16 | 8:30 | 49.985
2021-01-16 | 8:30 | 49.986
2021-01-16 | 8:31 | 49.984
2021-01-16 | 8:31 | 49.984
2021-01-16 | 8:31 | 49.981
2021-01-16 | 8:31 | 49.978
2021-01-16 | 8:31 | 49.972
2021-01-16 | 8:31 | 49.969
2021-01-16 | 8:31 | 49.965
2021-01-16 | 8:31 | 49.964
2021-01-16 | 8:31 | 49.961
2021-01-16 | 8:31 | 49.959
2021-01-16 | 8:31 | 49.961
2021-01-16 | 8:31 | 49.962
2021-01-16 | 8:31 | 49.967
2021-01-16 | 8:31 | 49.966
2021-01-16 | 8:31 | 49.968
2021-01-16 | 8:31 | 49.97
2021-01-16 | 8:31 | 49.972
2021-01-16 | 8:31 | 49.972
2021-01-16 | 8:31 | 49.976
2021-01-16 | 8:31 | 49.977
2021-01-16 | 8:31 | 49.979
2021-01-16 | 8:31 | 49.981
2021-01-16 | 8:31 | 49.982
2021-01-16 | 8:31 | 49.985
2021-01-16 | 8:31 | 49.989
2021-01-16 | 8:31 | 49.991
2021-01-16 | 8:31 | 49.991
2021-01-16 | 8:31 | 49.993
2021-01-16 | 8:31 | 49.991
2021-01-16 | 8:31 | 49.99
2021-01-16 | 8:31 | 49.988
2021-01-16 | 8:31 | 49.986
2021-01-16 | 8:31 | 49.982
2021-01-16 | 8:31 | 49.981
2021-01-16 | 8:31 | 49.978
2021-01-16 | 8:31 | 49.977
2021-01-16 | 8:31 | 49.977
2021-01-16 | 8:31 | 49.975
2021-01-16 | 8:31 | 49.975
2021-01-16 | 8:31 | 49.975
2021-01-16 | 8:31 | 49.974
2021-01-16 | 8:31 | 49.972
2021-01-16 | 8:31 | 49.973
2021-01-16 | 8:31 | 49.973
2021-01-16 | 8:31 | 49.974
2021-01-16 | 8:31 | 49.972
2021-01-16 | 8:31 | 49.973
2021-01-16 | 8:31 | 49.973
2021-01-16 | 8:31 | 49.977
2021-01-16 | 8:31 | 49.977
2021-01-16 | 8:31 | 49.977
2021-01-16 | 8:31 | 49.977
2021-01-16 | 8:31 | 49.977
2021-01-16 | 8:31 | 49.975
2021-01-16 | 8:31 | 49.973
2021-01-16 | 8:31 | 49.972
2021-01-16 | 8:31 | 49.971
2021-01-16 | 8:31 | 49.97
2021-01-16 | 8:31 | 49.971
2021-01-16 | 8:32 | 49.973
2021-01-16 | 8:32 | 49.972
2021-01-16 | 8:32 | 49.975
2021-01-16 | 8:32 | 49.974
2021-01-16 | 8:32 | 49.976
2021-01-16 | 8:32 | 49.976
2021-01-16 | 8:32 | 49.978
2021-01-16 | 8:32 | 49.978
2021-01-16 | 8:32 | 49.981
2021-01-16 | 8:32 | 49.98
2021-01-16 | 8:32 | 49.98
2021-01-16 | 8:32 | 49.978
2021-01-16 | 8:32 | 49.979
2021-01-16 | 8:32 | 49.979
2021-01-16 | 8:32 | 49.982
2021-01-16 | 8:32 | 49.984
2021-01-16 | 8:32 | 49.985
2021-01-16 | 8:32 | 49.985
2021-01-16 | 8:32 | 49.985
2021-01-16 | 8:32 | 49.986
2021-01-16 | 8:32 | 49.987
2021-01-16 | 8:32 | 49.986
2021-01-16 | 8:32 | 49.984
2021-01-16 | 8:32 | 49.983
2021-01-16 | 8:32 | 49.982
2021-01-16 | 8:32 | 49.985
2021-01-16 | 8:32 | 49.983
2021-01-16 | 8:32 | 49.981
2021-01-16 | 8:32 | 49.978
2021-01-16 | 8:32 | 49.974
2021-01-16 | 8:32 | 49.973
2021-01-16 | 8:32 | 49.971
2021-01-16 | 8:32 | 49.97
2021-01-16 | 8:32 | 49.968
2021-01-16 | 8:32 | 49.966
2021-01-16 | 8:32 | 49.966
2021-01-16 | 8:32 | 49.964
2021-01-16 | 8:32 | 49.962
2021-01-16 | 8:32 | 49.959
2021-01-16 | 8:32 | 49.958
2021-01-16 | 8:32 | 49.957
2021-01-16 | 8:32 | 49.96
2021-01-16 | 8:32 | 49.964
2021-01-16 | 8:32 | 49.967
2021-01-16 | 8:32 | 49.973
2021-01-16 | 8:32 | 49.977
2021-01-16 | 8:32 | 49.984
2021-01-16 | 8:32 | 49.988
2021-01-16 | 8:32 | 49.991
2021-01-16 | 8:32 | 49.993
2021-01-16 | 8:32 | 49.998
2021-01-16 | 8:32 | 49.997
2021-01-16 | 8:32 | 50.003
2021-01-16 | 8:32 | 50.004
2021-01-16 | 8:32 | 50.007
2021-01-16 | 8:32 | 50.007
2021-01-16 | 8:32 | 50.008
2021-01-16 | 8:32 | 50.008
2021-01-16 | 8:32 | 50.007
2021-01-16 | 8:32 | 50.007
2021-01-16 | 8:32 | 50.008
2021-01-16 | 8:33 | 50.013
2021-01-16 | 8:33 | 50.012
2021-01-16 | 8:33 | 50.015
2021-01-16 | 8:33 | 50.015
2021-01-16 | 8:33 | 50.015
2021-01-16 | 8:33 | 50.015
2021-01-16 | 8:33 | 50.016
2021-01-16 | 8:33 | 50.015
2021-01-16 | 8:33 | 50.013
2021-01-16 | 8:33 | 50.011
2021-01-16 | 8:33 | 50.007
2021-01-16 | 8:33 | 50.011
2021-01-16 | 8:33 | 50.013
2021-01-16 | 8:33 | 50.017
2021-01-16 | 8:33 | 50.024
2021-01-16 | 8:33 | 50.028
2021-01-16 | 8:33 | 50.029
2021-01-16 | 8:33 | 50.032
2021-01-16 | 8:33 | 50.032
2021-01-16 | 8:33 | 50.032
2021-01-16 | 8:33 | 50.032
2021-01-16 | 8:33 | 50.03
2021-01-16 | 8:33 | 50.028
2021-01-16 | 8:33 | 50.025
2021-01-16 | 8:33 | 50.024
2021-01-16 | 8:33 | 50.017
2021-01-16 | 8:33 | 50.008
2021-01-16 | 8:33 | 49.998
2021-01-16 | 8:33 | 49.988
2021-01-16 | 8:33 | 49.976
2021-01-16 | 8:33 | 49.968
2021-01-16 | 8:33 | 49.96
2021-01-16 | 8:33 | 49.952
2021-01-16 | 8:33 | 49.945
2021-01-16 | 8:33 | 49.94
2021-01-16 | 8:33 | 49.934
2021-01-16 | 8:33 | 49.93
2021-01-16 | 8:33 | 49.931
2021-01-16 | 8:33 | 49.932
2021-01-16 | 8:33 | 49.932
2021-01-16 | 8:33 | 49.934
2021-01-16 | 8:33 | 49.934
2021-01-16 | 8:33 | 49.934
2021-01-16 | 8:33 | 49.934
2021-01-16 | 8:33 | 49.934
2021-01-16 | 8:33 | 49.932
2021-01-16 | 8:33 | 49.933
2021-01-16 | 8:33 | 49.934
2021-01-16 | 8:33 | 49.935
2021-01-16 | 8:33 | 49.935
2021-01-16 | 8:33 | 49.935
2021-01-16 | 8:33 | 49.938
2021-01-16 | 8:33 | 49.939
2021-01-16 | 8:33 | 49.939
2021-01-16 | 8:33 | 49.939
2021-01-16 | 8:33 | 49.938
2021-01-16 | 8:33 | 49.937
2021-01-16 | 8:33 | 49.935
2021-01-16 | 8:33 | 49.935
2021-01-16 | 8:34 | 49.932
2021-01-16 | 8:34 | 49.931
2021-01-16 | 8:34 | 49.93
2021-01-16 | 8:34 | 49.934
2021-01-16 | 8:34 | 49.934
2021-01-16 | 8:34 | 49.939
2021-01-16 | 8:34 | 49.941
2021-01-16 | 8:34 | 49.946
2021-01-16 | 8:34 | 49.947
2021-01-16 | 8:34 | 49.95
2021-01-16 | 8:34 | 49.95
2021-01-16 | 8:34 | 49.949
2021-01-16 | 8:34 | 49.952
2021-01-16 | 8:34 | 49.954
2021-01-16 | 8:34 | 49.958
2021-01-16 | 8:34 | 49.958
2021-01-16 | 8:34 | 49.959
2021-01-16 | 8:34 | 49.959
2021-01-16 | 8:34 | 49.963
2021-01-16 | 8:34 | 49.964
2021-01-16 | 8:34 | 49.965
2021-01-16 | 8:34 | 49.964
2021-01-16 | 8:34 | 49.962
2021-01-16 | 8:34 | 49.958
2021-01-16 | 8:34 | 49.959
2021-01-16 | 8:34 | 49.957
2021-01-16 | 8:34 | 49.955
2021-01-16 | 8:34 | 49.952
2021-01-16 | 8:34 | 49.95
2021-01-16 | 8:34 | 49.954
2021-01-16 | 8:34 | 49.954
2021-01-16 | 8:34 | 49.955
2021-01-16 | 8:34 | 49.954
2021-01-16 | 8:34 | 49.954
2021-01-16 | 8:34 | 49.953
2021-01-16 | 8:34 | 49.953
2021-01-16 | 8:34 | 49.952
2021-01-16 | 8:34 | 49.952
2021-01-16 | 8:34 | 49.953
2021-01-16 | 8:34 | 49.954
2021-01-16 | 8:34 | 49.953
2021-01-16 | 8:34 | 49.95
2021-01-16 | 8:34 | 49.954
2021-01-16 | 8:34 | 49.954
2021-01-16 | 8:34 | 49.959
2021-01-16 | 8:34 | 49.963
2021-01-16 | 8:34 | 49.965
2021-01-16 | 8:34 | 49.966
2021-01-16 | 8:34 | 49.966
2021-01-16 | 8:34 | 49.968
2021-01-16 | 8:34 | 49.967
2021-01-16 | 8:34 | 49.967
2021-01-16 | 8:34 | 49.965
2021-01-16 | 8:34 | 49.963
2021-01-16 | 8:34 | 49.961
2021-01-16 | 8:34 | 49.958
2021-01-16 | 8:34 | 49.959
2021-01-16 | 8:34 | 49.957
2021-01-16 | 8:34 | 49.957
2021-01-16 | 8:34 | 49.956
2021-01-16 | 8:34 | 49.957
2021-01-16 | 8:35 | 49.958
2021-01-16 | 8:35 | 49.958
2021-01-16 | 8:35 | 49.961
2021-01-16 | 8:35 | 49.958
2021-01-16 | 8:35 | 49.959
2021-01-16 | 8:35 | 49.956
2021-01-16 | 8:35 | 49.956
2021-01-16 | 8:35 | 49.955
2021-01-16 | 8:35 | 49.952
2021-01-16 | 8:35 | 49.949
2021-01-16 | 8:35 | 49.944
2021-01-16 | 8:35 | 49.944
2021-01-16 | 8:35 | 49.942
2021-01-16 | 8:35 | 49.94
2021-01-16 | 8:35 | 49.939
2021-01-16 | 8:35 | 49.938
2021-01-16 | 8:35 | 49.939
2021-01-16 | 8:35 | 49.938
2021-01-16 | 8:35 | 49.94
2021-01-16 | 8:35 | 49.939
2021-01-16 | 8:35 | 49.941
2021-01-16 | 8:35 | 49.941
2021-01-16 | 8:35 | 49.942
2021-01-16 | 8:35 | 49.941
2021-01-16 | 8:35 | 49.941
2021-01-16 | 8:35 | 49.939
2021-01-16 | 8:35 | 49.935
2021-01-16 | 8:35 | 49.931
2021-01-16 | 8:35 | 49.926
2021-01-16 | 8:35 | 49.923
2021-01-16 | 8:35 | 49.92
2021-01-16 | 8:35 | 49.917
2021-01-16 | 8:35 | 49.916
2021-01-16 | 8:35 | 49.914
2021-01-16 | 8:35 | 49.915
2021-01-16 | 8:35 | 49.915
2021-01-16 | 8:35 | 49.914
2021-01-16 | 8:35 | 49.916
2021-01-16 | 8:35 | 49.915
2021-01-16 | 8:35 | 49.917
2021-01-16 | 8:35 | 49.916
2021-01-16 | 8:35 | 49.917
2021-01-16 | 8:35 | 49.918
2021-01-16 | 8:35 | 49.92
2021-01-16 | 8:35 | 49.922
2021-01-16 | 8:35 | 49.92
2021-01-16 | 8:35 | 49.92
2021-01-16 | 8:35 | 49.917
2021-01-16 | 8:35 | 49.917
2021-01-16 | 8:35 | 49.916
2021-01-16 | 8:35 | 49.912
2021-01-16 | 8:35 | 49.909
2021-01-16 | 8:35 | 49.904
2021-01-16 | 8:35 | 49.896
2021-01-16 | 8:35 | 49.893
2021-01-16 | 8:35 | 49.899
2021-01-16 | 8:35 | 49.901
2021-01-16 | 8:35 | 49.909
2021-01-16 | 8:35 | 49.912
2021-01-16 | 8:36 | 49.913
2021-01-16 | 8:36 | 49.915
2021-01-16 | 8:36 | 49.914
2021-01-16 | 8:36 | 49.912
2021-01-16 | 8:36 | 49.909
2021-01-16 | 8:36 | 49.905
2021-01-16 | 8:36 | 49.906
2021-01-16 | 8:36 | 49.902
2021-01-16 | 8:36 | 49.895
2021-01-16 | 8:36 | 49.889
2021-01-16 | 8:36 | 49.886
2021-01-16 | 8:36 | 49.887
2021-01-16 | 8:36 | 49.89
2021-01-16 | 8:36 | 49.892
2021-01-16 | 8:36 | 49.895
2021-01-16 | 8:36 | 49.897
2021-01-16 | 8:36 | 49.898
2021-01-16 | 8:36 | 49.899
2021-01-16 | 8:36 | 49.901
2021-01-16 | 8:36 | 49.903
2021-01-16 | 8:36 | 49.903
2021-01-16 | 8:36 | 49.901
2021-01-16 | 8:36 | 49.901
2021-01-16 | 8:36 | 49.9
2021-01-16 | 8:36 | 49.9
2021-01-16 | 8:36 | 49.902
2021-01-16 | 8:36 | 49.899
2021-01-16 | 8:36 | 49.899
2021-01-16 | 8:36 | 49.899
2021-01-16 | 8:36 | 49.903
2021-01-16 | 8:36 | 49.906
2021-01-16 | 8:36 | 49.911
2021-01-16 | 8:36 | 49.914
2021-01-16 | 8:36 | 49.918
2021-01-16 | 8:36 | 49.918
2021-01-16 | 8:36 | 49.919
2021-01-16 | 8:36 | 49.918
2021-01-16 | 8:36 | 49.917
2021-01-16 | 8:36 | 49.914
2021-01-16 | 8:36 | 49.91
2021-01-16 | 8:36 | 49.907
2021-01-16 | 8:36 | 49.905
2021-01-16 | 8:36 | 49.903
2021-01-16 | 8:36 | 49.901
2021-01-16 | 8:36 | 49.898
2021-01-16 | 8:36 | 49.896
2021-01-16 | 8:36 | 49.896
2021-01-16 | 8:36 | 49.898
2021-01-16 | 8:36 | 49.899
2021-01-16 | 8:36 | 49.903
2021-01-16 | 8:36 | 49.902
2021-01-16 | 8:36 | 49.902
2021-01-16 | 8:36 | 49.9
2021-01-16 | 8:36 | 49.898
2021-01-16 | 8:36 | 49.899
2021-01-16 | 8:36 | 49.899
2021-01-16 | 8:36 | 49.9
2021-01-16 | 8:36 | 49.901
2021-01-16 | 8:36 | 49.902
2021-01-16 | 8:36 | 49.904
2021-01-16 | 8:36 | 49.906
2021-01-16 | 8:37 | 49.908
2021-01-16 | 8:37 | 49.909
2021-01-16 | 8:37 | 49.913
2021-01-16 | 8:37 | 49.914
2021-01-16 | 8:37 | 49.918
2021-01-16 | 8:37 | 49.918
2021-01-16 | 8:37 | 49.921
2021-01-16 | 8:37 | 49.922
2021-01-16 | 8:37 | 49.921
2021-01-16 | 8:37 | 49.92
2021-01-16 | 8:37 | 49.92
2021-01-16 | 8:37 | 49.919
2021-01-16 | 8:37 | 49.921
2021-01-16 | 8:37 | 49.921
2021-01-16 | 8:37 | 49.923
2021-01-16 | 8:37 | 49.925
2021-01-16 | 8:37 | 49.927
2021-01-16 | 8:37 | 49.927
2021-01-16 | 8:37 | 49.929
2021-01-16 | 8:37 | 49.928
2021-01-16 | 8:37 | 49.926
2021-01-16 | 8:37 | 49.922
2021-01-16 | 8:37 | 49.921
2021-01-16 | 8:37 | 49.916
2021-01-16 | 8:37 | 49.913
2021-01-16 | 8:37 | 49.91
2021-01-16 | 8:37 | 49.91
2021-01-16 | 8:37 | 49.906
2021-01-16 | 8:37 | 49.904
2021-01-16 | 8:37 | 49.902
2021-01-16 | 8:37 | 49.902
2021-01-16 | 8:37 | 49.901
2021-01-16 | 8:37 | 49.901
2021-01-16 | 8:37 | 49.899
2021-01-16 | 8:37 | 49.899
2021-01-16 | 8:37 | 49.902
2021-01-16 | 8:37 | 49.902
2021-01-16 | 8:37 | 49.903
2021-01-16 | 8:37 | 49.901
2021-01-16 | 8:37 | 49.904
2021-01-16 | 8:37 | 49.902
2021-01-16 | 8:37 | 49.902
2021-01-16 | 8:37 | 49.901
2021-01-16 | 8:37 | 49.902
2021-01-16 | 8:37 | 49.902
2021-01-16 | 8:37 | 49.902
2021-01-16 | 8:37 | 49.903
2021-01-16 | 8:37 | 49.903
2021-01-16 | 8:37 | 49.904
2021-01-16 | 8:37 | 49.902
2021-01-16 | 8:37 | 49.902
2021-01-16 | 8:37 | 49.899
2021-01-16 | 8:37 | 49.898
2021-01-16 | 8:37 | 49.898
2021-01-16 | 8:37 | 49.898
2021-01-16 | 8:37 | 49.899
2021-01-16 | 8:37 | 49.903
2021-01-16 | 8:37 | 49.903
2021-01-16 | 8:37 | 49.905
2021-01-16 | 8:38 | 49.907
2021-01-16 | 8:38 | 49.907
2021-01-16 | 8:38 | 49.907
2021-01-16 | 8:38 | 49.906
2021-01-16 | 8:38 | 49.907
2021-01-16 | 8:38 | 49.906
2021-01-16 | 8:38 | 49.904
2021-01-16 | 8:38 | 49.903
2021-01-16 | 8:38 | 49.904
2021-01-16 | 8:38 | 49.901
2021-01-16 | 8:38 | 49.899
2021-01-16 | 8:38 | 49.896
2021-01-16 | 8:38 | 49.893
2021-01-16 | 8:38 | 49.891
2021-01-16 | 8:38 | 49.889
2021-01-16 | 8:38 | 49.885
2021-01-16 | 8:38 | 49.88
2021-01-16 | 8:38 | 49.88
2021-01-16 | 8:38 | 49.881
2021-01-16 | 8:38 | 49.88
2021-01-16 | 8:38 | 49.88
2021-01-16 | 8:38 | 49.881
2021-01-16 | 8:38 | 49.888
2021-01-16 | 8:38 | 49.89
2021-01-16 | 8:38 | 49.892
2021-01-16 | 8:38 | 49.891
2021-01-16 | 8:38 | 49.894
2021-01-16 | 8:38 | 49.895
2021-01-16 | 8:38 | 49.895
2021-01-16 | 8:38 | 49.891
2021-01-16 | 8:38 | 49.891
2021-01-16 | 8:38 | 49.89
2021-01-16 | 8:38 | 49.888
2021-01-16 | 8:38 | 49.888
2021-01-16 | 8:38 | 49.887
2021-01-16 | 8:38 | 49.888
2021-01-16 | 8:38 | 49.886
2021-01-16 | 8:38 | 49.885
2021-01-16 | 8:38 | 49.882
2021-01-16 | 8:38 | 49.883
2021-01-16 | 8:38 | 49.881
2021-01-16 | 8:38 | 49.882
2021-01-16 | 8:38 | 49.883
2021-01-16 | 8:38 | 49.882
2021-01-16 | 8:38 | 49.885
2021-01-16 | 8:38 | 49.884
2021-01-16 | 8:38 | 49.883
2021-01-16 | 8:38 | 49.879
2021-01-16 | 8:38 | 49.877
2021-01-16 | 8:38 | 49.877
2021-01-16 | 8:38 | 49.875
2021-01-16 | 8:38 | 49.879
2021-01-16 | 8:38 | 49.881
2021-01-16 | 8:38 | 49.885
2021-01-16 | 8:38 | 49.886
2021-01-16 | 8:38 | 49.887
2021-01-16 | 8:38 | 49.887
2021-01-16 | 8:38 | 49.891
2021-01-16 | 8:38 | 49.89
2021-01-16 | 8:38 | 49.89
2021-01-16 | 8:39 | 49.886
2021-01-16 | 8:39 | 49.886
2021-01-16 | 8:39 | 49.884
2021-01-16 | 8:39 | 49.882
2021-01-16 | 8:39 | 49.879
2021-01-16 | 8:39 | 49.879
2021-01-16 | 8:39 | 49.876
2021-01-16 | 8:39 | 49.876
2021-01-16 | 8:39 | 49.879
2021-01-16 | 8:39 | 49.885
2021-01-16 | 8:39 | 49.888
2021-01-16 | 8:39 | 49.892
2021-01-16 | 8:39 | 49.891
2021-01-16 | 8:39 | 49.893
2021-01-16 | 8:39 | 49.891
2021-01-16 | 8:39 | 49.892
2021-01-16 | 8:39 | 49.891
2021-01-16 | 8:39 | 49.896
2021-01-16 | 8:39 | 49.897
2021-01-16 | 8:39 | 49.898
2021-01-16 | 8:39 | 49.897
2021-01-16 | 8:39 | 49.896
2021-01-16 | 8:39 | 49.9
2021-01-16 | 8:39 | 49.896
2021-01-16 | 8:39 | 49.893
2021-01-16 | 8:39 | 49.895
2021-01-16 | 8:39 | 49.896
2021-01-16 | 8:39 | 49.896
2021-01-16 | 8:39 | 49.897
2021-01-16 | 8:39 | 49.899
2021-01-16 | 8:39 | 49.898
2021-01-16 | 8:39 | 49.897
2021-01-16 | 8:39 | 49.895
2021-01-16 | 8:39 | 49.895
2021-01-16 | 8:39 | 49.897
2021-01-16 | 8:39 | 49.894
2021-01-16 | 8:39 | 49.892
2021-01-16 | 8:39 | 49.89
2021-01-16 | 8:39 | 49.891
2021-01-16 | 8:39 | 49.89
2021-01-16 | 8:39 | 49.886
2021-01-16 | 8:39 | 49.885
2021-01-16 | 8:39 | 49.887
2021-01-16 | 8:39 | 49.89
2021-01-16 | 8:39 | 49.891
2021-01-16 | 8:39 | 49.893
2021-01-16 | 8:39 | 49.893
2021-01-16 | 8:39 | 49.89
2021-01-16 | 8:39 | 49.891
2021-01-16 | 8:39 | 49.887
2021-01-16 | 8:39 | 49.887
2021-01-16 | 8:39 | 49.885
2021-01-16 | 8:39 | 49.887
2021-01-16 | 8:39 | 49.884
2021-01-16 | 8:39 | 49.882
2021-01-16 | 8:39 | 49.881
2021-01-16 | 8:39 | 49.882
2021-01-16 | 8:39 | 49.88
2021-01-16 | 8:39 | 49.877
2021-01-16 | 8:39 | 49.877
2021-01-16 | 8:40 | 49.873
2021-01-16 | 8:40 | 49.877
2021-01-16 | 8:40 | 49.878
2021-01-16 | 8:40 | 49.884
2021-01-16 | 8:40 | 49.886
2021-01-16 | 8:40 | 49.888
2021-01-16 | 8:40 | 49.894
2021-01-16 | 8:40 | 49.897
2021-01-16 | 8:40 | 49.899
2021-01-16 | 8:40 | 49.903
2021-01-16 | 8:40 | 49.9
2021-01-16 | 8:40 | 49.901
2021-01-16 | 8:40 | 49.897
2021-01-16 | 8:40 | 49.895
2021-01-16 | 8:40 | 49.893
2021-01-16 | 8:40 | 49.891
2021-01-16 | 8:40 | 49.889
2021-01-16 | 8:40 | 49.887
2021-01-16 | 8:40 | 49.885
2021-01-16 | 8:40 | 49.882
2021-01-16 | 8:40 | 49.882
2021-01-16 | 8:40 | 49.881
2021-01-16 | 8:40 | 49.883
2021-01-16 | 8:40 | 49.884
2021-01-16 | 8:40 | 49.889
2021-01-16 | 8:40 | 49.889
2021-01-16 | 8:40 | 49.888
2021-01-16 | 8:40 | 49.886
2021-01-16 | 8:40 | 49.886
2021-01-16 | 8:40 | 49.886
2021-01-16 | 8:40 | 49.883
2021-01-16 | 8:40 | 49.883
2021-01-16 | 8:40 | 49.88
2021-01-16 | 8:40 | 49.878
2021-01-16 | 8:40 | 49.876
2021-01-16 | 8:40 | 49.871
2021-01-16 | 8:40 | 49.87
2021-01-16 | 8:40 | 49.866
2021-01-16 | 8:40 | 49.865
2021-01-16 | 8:40 | 49.866
2021-01-16 | 8:40 | 49.869
2021-01-16 | 8:40 | 49.871
2021-01-16 | 8:40 | 49.873
2021-01-16 | 8:40 | 49.874
2021-01-16 | 8:40 | 49.874
2021-01-16 | 8:40 | 49.872
2021-01-16 | 8:40 | 49.871
2021-01-16 | 8:40 | 49.873
2021-01-16 | 8:40 | 49.878
2021-01-16 | 8:40 | 49.882
2021-01-16 | 8:40 | 49.883
2021-01-16 | 8:40 | 49.886
2021-01-16 | 8:40 | 49.887
2021-01-16 | 8:40 | 49.889
2021-01-16 | 8:40 | 49.887
2021-01-16 | 8:40 | 49.884
2021-01-16 | 8:40 | 49.88
2021-01-16 | 8:40 | 49.878
2021-01-16 | 8:40 | 49.878
2021-01-16 | 8:40 | 49.877
2021-01-16 | 8:41 | 49.875
2021-01-16 | 8:41 | 49.869
2021-01-16 | 8:41 | 49.869
2021-01-16 | 8:41 | 49.865
2021-01-16 | 8:41 | 49.862
2021-01-16 | 8:41 | 49.86
2021-01-16 | 8:41 | 49.859
2021-01-16 | 8:41 | 49.86
2021-01-16 | 8:41 | 49.864
2021-01-16 | 8:41 | 49.864
2021-01-16 | 8:41 | 49.866
2021-01-16 | 8:41 | 49.867
2021-01-16 | 8:41 | 49.868
2021-01-16 | 8:41 | 49.867
2021-01-16 | 8:41 | 49.866
2021-01-16 | 8:41 | 49.863
2021-01-16 | 8:41 | 49.862
2021-01-16 | 8:41 | 49.862
2021-01-16 | 8:41 | 49.861
2021-01-16 | 8:41 | 49.862
2021-01-16 | 8:41 | 49.861
2021-01-16 | 8:41 | 49.859
2021-01-16 | 8:41 | 49.858
2021-01-16 | 8:41 | 49.857
2021-01-16 | 8:41 | 49.857
2021-01-16 | 8:41 | 49.855
2021-01-16 | 8:41 | 49.853
2021-01-16 | 8:41 | 49.854
2021-01-16 | 8:41 | 49.851
2021-01-16 | 8:41 | 49.851
2021-01-16 | 8:41 | 49.851
2021-01-16 | 8:41 | 49.847
2021-01-16 | 8:41 | 49.848
2021-01-16 | 8:41 | 49.852
2021-01-16 | 8:41 | 49.858
2021-01-16 | 8:41 | 49.863
2021-01-16 | 8:41 | 49.866
2021-01-16 | 8:41 | 49.869
2021-01-16 | 8:41 | 49.871
2021-01-16 | 8:41 | 49.871
2021-01-16 | 8:41 | 49.871
2021-01-16 | 8:41 | 49.867
2021-01-16 | 8:41 | 49.867
2021-01-16 | 8:41 | 49.864
2021-01-16 | 8:41 | 49.861
2021-01-16 | 8:41 | 49.856
2021-01-16 | 8:41 | 49.854
2021-01-16 | 8:41 | 49.854
2021-01-16 | 8:41 | 49.854
2021-01-16 | 8:41 | 49.858
2021-01-16 | 8:41 | 49.861
2021-01-16 | 8:41 | 49.861
2021-01-16 | 8:41 | 49.863
2021-01-16 | 8:41 | 49.864
2021-01-16 | 8:41 | 49.864
2021-01-16 | 8:41 | 49.862
2021-01-16 | 8:41 | 49.861
2021-01-16 | 8:41 | 49.859
2021-01-16 | 8:41 | 49.858
2021-01-16 | 8:41 | 49.859
2021-01-16 | 8:42 | 49.856
2021-01-16 | 8:42 | 49.855
2021-01-16 | 8:42 | 49.853
2021-01-16 | 8:42 | 49.852
2021-01-16 | 8:42 | 49.855
2021-01-16 | 8:42 | 49.854
2021-01-16 | 8:42 | 49.854
2021-01-16 | 8:42 | 49.858
2021-01-16 | 8:42 | 49.857
2021-01-16 | 8:42 | 49.862
2021-01-16 | 8:42 | 49.862
2021-01-16 | 8:42 | 49.865
2021-01-16 | 8:42 | 49.868
2021-01-16 | 8:42 | 49.867
2021-01-16 | 8:42 | 49.867
2021-01-16 | 8:42 | 49.865
2021-01-16 | 8:42 | 49.866
2021-01-16 | 8:42 | 49.866
2021-01-16 | 8:42 | 49.868
2021-01-16 | 8:42 | 49.871
2021-01-16 | 8:42 | 49.874
2021-01-16 | 8:42 | 49.876
2021-01-16 | 8:42 | 49.879
2021-01-16 | 8:42 | 49.877
2021-01-16 | 8:42 | 49.879
2021-01-16 | 8:42 | 49.875
2021-01-16 | 8:42 | 49.874
2021-01-16 | 8:42 | 49.872
2021-01-16 | 8:42 | 49.872
2021-01-16 | 8:42 | 49.871
2021-01-16 | 8:42 | 49.872
2021-01-16 | 8:42 | 49.87
2021-01-16 | 8:42 | 49.868
2021-01-16 | 8:42 | 49.864
2021-01-16 | 8:42 | 49.863
2021-01-16 | 8:42 | 49.861
2021-01-16 | 8:42 | 49.864
2021-01-16 | 8:42 | 49.863
2021-01-16 | 8:42 | 49.863
2021-01-16 | 8:42 | 49.863
2021-01-16 | 8:42 | 49.867
2021-01-16 | 8:42 | 49.871
2021-01-16 | 8:42 | 49.876
2021-01-16 | 8:42 | 49.878
2021-01-16 | 8:42 | 49.879
2021-01-16 | 8:42 | 49.877
2021-01-16 | 8:42 | 49.877
2021-01-16 | 8:42 | 49.874
2021-01-16 | 8:42 | 49.874
2021-01-16 | 8:42 | 49.873
2021-01-16 | 8:42 | 49.875
2021-01-16 | 8:42 | 49.874
2021-01-16 | 8:42 | 49.876
2021-01-16 | 8:42 | 49.877
2021-01-16 | 8:42 | 49.88
2021-01-16 | 8:42 | 49.881
2021-01-16 | 8:42 | 49.882
2021-01-16 | 8:42 | 49.883
2021-01-16 | 8:42 | 49.887
2021-01-16 | 8:42 | 49.887
2021-01-16 | 8:43 | 49.886
2021-01-16 | 8:43 | 49.886
2021-01-16 | 8:43 | 49.886
2021-01-16 | 8:43 | 49.884
2021-01-16 | 8:43 | 49.884
2021-01-16 | 8:43 | 49.882
2021-01-16 | 8:43 | 49.881
2021-01-16 | 8:43 | 49.88
2021-01-16 | 8:43 | 49.878
2021-01-16 | 8:43 | 49.877
2021-01-16 | 8:43 | 49.88
2021-01-16 | 8:43 | 49.878
2021-01-16 | 8:43 | 49.88
2021-01-16 | 8:43 | 49.88
2021-01-16 | 8:43 | 49.88
2021-01-16 | 8:43 | 49.878
2021-01-16 | 8:43 | 49.88
2021-01-16 | 8:43 | 49.881
2021-01-16 | 8:43 | 49.885
2021-01-16 | 8:43 | 49.887
2021-01-16 | 8:43 | 49.887
2021-01-16 | 8:43 | 49.888
2021-01-16 | 8:43 | 49.889
2021-01-16 | 8:43 | 49.892
2021-01-16 | 8:43 | 49.893
2021-01-16 | 8:43 | 49.892
2021-01-16 | 8:43 | 49.889
2021-01-16 | 8:43 | 49.887
2021-01-16 | 8:43 | 49.885
2021-01-16 | 8:43 | 49.885
2021-01-16 | 8:43 | 49.885
2021-01-16 | 8:43 | 49.887
2021-01-16 | 8:43 | 49.885
2021-01-16 | 8:43 | 49.885
2021-01-16 | 8:43 | 49.883
2021-01-16 | 8:43 | 49.883
2021-01-16 | 8:43 | 49.882
2021-01-16 | 8:43 | 49.884
2021-01-16 | 8:43 | 49.884
2021-01-16 | 8:43 | 49.888
2021-01-16 | 8:43 | 49.892
2021-01-16 | 8:43 | 49.894
2021-01-16 | 8:43 | 49.896
2021-01-16 | 8:43 | 49.898
2021-01-16 | 8:43 | 49.905
2021-01-16 | 8:43 | 49.909
2021-01-16 | 8:43 | 49.913
2021-01-16 | 8:43 | 49.912
2021-01-16 | 8:43 | 49.913
2021-01-16 | 8:43 | 49.915
2021-01-16 | 8:43 | 49.917
2021-01-16 | 8:43 | 49.92
2021-01-16 | 8:43 | 49.918
2021-01-16 | 8:43 | 49.92
2021-01-16 | 8:43 | 49.917
2021-01-16 | 8:43 | 49.917
2021-01-16 | 8:43 | 49.912
2021-01-16 | 8:43 | 49.912
2021-01-16 | 8:43 | 49.91
2021-01-16 | 8:43 | 49.91
2021-01-16 | 8:44 | 49.908
2021-01-16 | 8:44 | 49.906
2021-01-16 | 8:44 | 49.907
2021-01-16 | 8:44 | 49.909
2021-01-16 | 8:44 | 49.912
2021-01-16 | 8:44 | 49.912
2021-01-16 | 8:44 | 49.915
2021-01-16 | 8:44 | 49.912
2021-01-16 | 8:44 | 49.913
2021-01-16 | 8:44 | 49.913
2021-01-16 | 8:44 | 49.912
2021-01-16 | 8:44 | 49.91
2021-01-16 | 8:44 | 49.909
2021-01-16 | 8:44 | 49.91
2021-01-16 | 8:44 | 49.907
2021-01-16 | 8:44 | 49.905
2021-01-16 | 8:44 | 49.903
2021-01-16 | 8:44 | 49.904
2021-01-16 | 8:44 | 49.903
2021-01-16 | 8:44 | 49.902
2021-01-16 | 8:44 | 49.9
2021-01-16 | 8:44 | 49.901
2021-01-16 | 8:44 | 49.904
2021-01-16 | 8:44 | 49.905
2021-01-16 | 8:44 | 49.907
2021-01-16 | 8:44 | 49.909
2021-01-16 | 8:44 | 49.91
2021-01-16 | 8:44 | 49.914
2021-01-16 | 8:44 | 49.916
2021-01-16 | 8:44 | 49.919
2021-01-16 | 8:44 | 49.917
2021-01-16 | 8:44 | 49.916
2021-01-16 | 8:44 | 49.915
2021-01-16 | 8:44 | 49.914
2021-01-16 | 8:44 | 49.914
2021-01-16 | 8:44 | 49.914
2021-01-16 | 8:44 | 49.915
2021-01-16 | 8:44 | 49.914
2021-01-16 | 8:44 | 49.915
2021-01-16 | 8:44 | 49.919
2021-01-16 | 8:44 | 49.921
2021-01-16 | 8:44 | 49.924
2021-01-16 | 8:44 | 49.926
2021-01-16 | 8:44 | 49.928
2021-01-16 | 8:44 | 49.928
2021-01-16 | 8:44 | 49.927
2021-01-16 | 8:44 | 49.926
2021-01-16 | 8:44 | 49.921
2021-01-16 | 8:44 | 49.923
2021-01-16 | 8:44 | 49.923
2021-01-16 | 8:44 | 49.922
2021-01-16 | 8:44 | 49.922
2021-01-16 | 8:44 | 49.92
2021-01-16 | 8:44 | 49.922
2021-01-16 | 8:44 | 49.92
2021-01-16 | 8:44 | 49.921
2021-01-16 | 8:44 | 49.922
2021-01-16 | 8:44 | 49.922
2021-01-16 | 8:44 | 49.924
2021-01-16 | 8:44 | 49.921
2021-01-16 | 8:44 | 49.921
2021-01-16 | 8:45 | 49.918
2021-01-16 | 8:45 | 49.916
2021-01-16 | 8:45 | 49.914
2021-01-16 | 8:45 | 49.912
2021-01-16 | 8:45 | 49.907
2021-01-16 | 8:45 | 49.904
2021-01-16 | 8:45 | 49.902
2021-01-16 | 8:45 | 49.9
2021-01-16 | 8:45 | 49.903
2021-01-16 | 8:45 | 49.901
2021-01-16 | 8:45 | 49.905
2021-01-16 | 8:45 | 49.9
2021-01-16 | 8:45 | 49.902
2021-01-16 | 8:45 | 49.899
2021-01-16 | 8:45 | 49.899
2021-01-16 | 8:45 | 49.898
2021-01-16 | 8:45 | 49.898
2021-01-16 | 8:45 | 49.898
2021-01-16 | 8:45 | 49.895
2021-01-16 | 8:45 | 49.889
2021-01-16 | 8:45 | 49.886
2021-01-16 | 8:45 | 49.886
2021-01-16 | 8:45 | 49.882
2021-01-16 | 8:45 | 49.883
2021-01-16 | 8:45 | 49.884
2021-01-16 | 8:45 | 49.887
2021-01-16 | 8:45 | 49.89
2021-01-16 | 8:45 | 49.894
2021-01-16 | 8:45 | 49.897
2021-01-16 | 8:45 | 49.899
2021-01-16 | 8:45 | 49.9
2021-01-16 | 8:45 | 49.9
2021-01-16 | 8:45 | 49.901
2021-01-16 | 8:45 | 49.901
2021-01-16 | 8:45 | 49.903
2021-01-16 | 8:45 | 49.903
2021-01-16 | 8:45 | 49.903
2021-01-16 | 8:45 | 49.902
2021-01-16 | 8:45 | 49.899
2021-01-16 | 8:45 | 49.897
2021-01-16 | 8:45 | 49.894
2021-01-16 | 8:45 | 49.893
2021-01-16 | 8:45 | 49.891
2021-01-16 | 8:45 | 49.89
2021-01-16 | 8:45 | 49.887
2021-01-16 | 8:45 | 49.885
2021-01-16 | 8:45 | 49.881
2021-01-16 | 8:45 | 49.88
2021-01-16 | 8:45 | 49.877
2021-01-16 | 8:45 | 49.877
2021-01-16 | 8:45 | 49.874
2021-01-16 | 8:45 | 49.876
2021-01-16 | 8:45 | 49.874
2021-01-16 | 8:45 | 49.875
2021-01-16 | 8:45 | 49.878
2021-01-16 | 8:45 | 49.878
2021-01-16 | 8:45 | 49.881
2021-01-16 | 8:45 | 49.879
2021-01-16 | 8:45 | 49.879
2021-01-16 | 8:46 | 49.877
2021-01-16 | 8:46 | 49.877
2021-01-16 | 8:46 | 49.873
2021-01-16 | 8:46 | 49.871
2021-01-16 | 8:46 | 49.87
2021-01-16 | 8:46 | 49.869
2021-01-16 | 8:46 | 49.87
2021-01-16 | 8:46 | 49.87
2021-01-16 | 8:46 | 49.871
2021-01-16 | 8:46 | 49.869
2021-01-16 | 8:46 | 49.87
2021-01-16 | 8:46 | 49.869
2021-01-16 | 8:46 | 49.869
2021-01-16 | 8:46 | 49.867
2021-01-16 | 8:46 | 49.866
2021-01-16 | 8:46 | 49.862
2021-01-16 | 8:46 | 49.862
2021-01-16 | 8:46 | 49.86
2021-01-16 | 8:46 | 49.86
2021-01-16 | 8:46 | 49.859
2021-01-16 | 8:46 | 49.864
2021-01-16 | 8:46 | 49.864
2021-01-16 | 8:46 | 49.866
2021-01-16 | 8:46 | 49.866
2021-01-16 | 8:46 | 49.872
2021-01-16 | 8:46 | 49.875
2021-01-16 | 8:46 | 49.88
2021-01-16 | 8:46 | 49.879
2021-01-16 | 8:46 | 49.88
2021-01-16 | 8:46 | 49.882
2021-01-16 | 8:46 | 49.884
2021-01-16 | 8:46 | 49.881
2021-01-16 | 8:46 | 49.882
2021-01-16 | 8:46 | 49.879
2021-01-16 | 8:46 | 49.879
2021-01-16 | 8:46 | 49.878
2021-01-16 | 8:46 | 49.875
2021-01-16 | 8:46 | 49.874
2021-01-16 | 8:46 | 49.871
2021-01-16 | 8:46 | 49.87
2021-01-16 | 8:46 | 49.865
2021-01-16 | 8:46 | 49.864
2021-01-16 | 8:46 | 49.862
2021-01-16 | 8:46 | 49.864
2021-01-16 | 8:46 | 49.861
2021-01-16 | 8:46 | 49.86
2021-01-16 | 8:46 | 49.861
2021-01-16 | 8:46 | 49.862
2021-01-16 | 8:46 | 49.866
2021-01-16 | 8:46 | 49.866
2021-01-16 | 8:46 | 49.867
2021-01-16 | 8:46 | 49.864
2021-01-16 | 8:46 | 49.863
2021-01-16 | 8:46 | 49.865
2021-01-16 | 8:46 | 49.864
2021-01-16 | 8:46 | 49.863
2021-01-16 | 8:46 | 49.864
2021-01-16 | 8:46 | 49.862
2021-01-16 | 8:46 | 49.864
2021-01-16 | 8:46 | 49.864
2021-01-16 | 8:46 | 49.864
2021-01-16 | 8:47 | 49.863
2021-01-16 | 8:47 | 49.86
2021-01-16 | 8:47 | 49.859
2021-01-16 | 8:47 | 49.858
2021-01-16 | 8:47 | 49.857
2021-01-16 | 8:47 | 49.857
2021-01-16 | 8:47 | 49.854
2021-01-16 | 8:47 | 49.852
2021-01-16 | 8:47 | 49.85
2021-01-16 | 8:47 | 49.848
2021-01-16 | 8:47 | 49.848
2021-01-16 | 8:47 | 49.849
2021-01-16 | 8:47 | 49.852
2021-01-16 | 8:47 | 49.854
2021-01-16 | 8:47 | 49.856
2021-01-16 | 8:47 | 49.858
2021-01-16 | 8:47 | 49.856
2021-01-16 | 8:47 | 49.857
2021-01-16 | 8:47 | 49.854
2021-01-16 | 8:47 | 49.85
2021-01-16 | 8:47 | 49.848
2021-01-16 | 8:47 | 49.845
2021-01-16 | 8:47 | 49.846
2021-01-16 | 8:47 | 49.845
2021-01-16 | 8:47 | 49.846
2021-01-16 | 8:47 | 49.847
2021-01-16 | 8:47 | 49.849
2021-01-16 | 8:47 | 49.854
2021-01-16 | 8:47 | 49.853
2021-01-16 | 8:47 | 49.858
2021-01-16 | 8:47 | 49.859
2021-01-16 | 8:47 | 49.863
2021-01-16 | 8:47 | 49.866
2021-01-16 | 8:47 | 49.868
2021-01-16 | 8:47 | 49.87
2021-01-16 | 8:47 | 49.87
2021-01-16 | 8:47 | 49.87
2021-01-16 | 8:47 | 49.868
2021-01-16 | 8:47 | 49.867
2021-01-16 | 8:47 | 49.866
2021-01-16 | 8:47 | 49.865
2021-01-16 | 8:47 | 49.866
2021-01-16 | 8:47 | 49.863
2021-01-16 | 8:47 | 49.863
2021-01-16 | 8:47 | 49.861
2021-01-16 | 8:47 | 49.862
2021-01-16 | 8:47 | 49.863
2021-01-16 | 8:47 | 49.865
2021-01-16 | 8:47 | 49.865
2021-01-16 | 8:47 | 49.863
2021-01-16 | 8:47 | 49.862
2021-01-16 | 8:47 | 49.862
2021-01-16 | 8:47 | 49.861
2021-01-16 | 8:47 | 49.863
2021-01-16 | 8:47 | 49.862
2021-01-16 | 8:47 | 49.866
2021-01-16 | 8:47 | 49.867
2021-01-16 | 8:47 | 49.868
2021-01-16 | 8:47 | 49.869
2021-01-16 | 8:48 | 49.871
2021-01-16 | 8:48 | 49.872
2021-01-16 | 8:48 | 49.874
2021-01-16 | 8:48 | 49.876
2021-01-16 | 8:48 | 49.878
2021-01-16 | 8:48 | 49.88
2021-01-16 | 8:48 | 49.884
2021-01-16 | 8:48 | 49.886
2021-01-16 | 8:48 | 49.888
2021-01-16 | 8:48 | 49.887
2021-01-16 | 8:48 | 49.885
2021-01-16 | 8:48 | 49.884
2021-01-16 | 8:48 | 49.885
2021-01-16 | 8:48 | 49.886
2021-01-16 | 8:48 | 49.892
2021-01-16 | 8:48 | 49.894
2021-01-16 | 8:48 | 49.896
2021-01-16 | 8:48 | 49.895
2021-01-16 | 8:48 | 49.893
2021-01-16 | 8:48 | 49.89
2021-01-16 | 8:48 | 49.888
2021-01-16 | 8:48 | 49.885
2021-01-16 | 8:48 | 49.884
2021-01-16 | 8:48 | 49.885
2021-01-16 | 8:48 | 49.883
2021-01-16 | 8:48 | 49.885
2021-01-16 | 8:48 | 49.883
2021-01-16 | 8:48 | 49.883
2021-01-16 | 8:48 | 49.883
2021-01-16 | 8:48 | 49.887
2021-01-16 | 8:48 | 49.888
2021-01-16 | 8:48 | 49.888
2021-01-16 | 8:48 | 49.889
2021-01-16 | 8:48 | 49.89
2021-01-16 | 8:48 | 49.893
2021-01-16 | 8:48 | 49.895
2021-01-16 | 8:48 | 49.898
2021-01-16 | 8:48 | 49.894
2021-01-16 | 8:48 | 49.893
2021-01-16 | 8:48 | 49.89
2021-01-16 | 8:48 | 49.891
2021-01-16 | 8:48 | 49.892
2021-01-16 | 8:48 | 49.895
2021-01-16 | 8:48 | 49.896
2021-01-16 | 8:48 | 49.894
2021-01-16 | 8:48 | 49.896
2021-01-16 | 8:48 | 49.899
2021-01-16 | 8:48 | 49.901
2021-01-16 | 8:48 | 49.899
2021-01-16 | 8:48 | 49.899
2021-01-16 | 8:48 | 49.896
2021-01-16 | 8:48 | 49.896
2021-01-16 | 8:48 | 49.897
2021-01-16 | 8:48 | 49.898
2021-01-16 | 8:48 | 49.899
2021-01-16 | 8:48 | 49.902
2021-01-16 | 8:48 | 49.903
2021-01-16 | 8:48 | 49.901
2021-01-16 | 8:48 | 49.901
2021-01-16 | 8:48 | 49.901
2021-01-16 | 8:48 | 49.901
2021-01-16 | 8:49 | 49.904
2021-01-16 | 8:49 | 49.907
2021-01-16 | 8:49 | 49.914
2021-01-16 | 8:49 | 49.919
2021-01-16 | 8:49 | 49.927
2021-01-16 | 8:49 | 49.934
2021-01-16 | 8:49 | 49.938
2021-01-16 | 8:49 | 49.943
2021-01-16 | 8:49 | 49.947
2021-01-16 | 8:49 | 49.952
2021-01-16 | 8:49 | 49.953
2021-01-16 | 8:49 | 49.956
2021-01-16 | 8:49 | 49.959
2021-01-16 | 8:49 | 49.958
2021-01-16 | 8:49 | 49.958
2021-01-16 | 8:49 | 49.957
2021-01-16 | 8:49 | 49.958
2021-01-16 | 8:49 | 49.955
2021-01-16 | 8:49 | 49.954
2021-01-16 | 8:49 | 49.954
2021-01-16 | 8:49 | 49.954
2021-01-16 | 8:49 | 49.956
2021-01-16 | 8:49 | 49.959
2021-01-16 | 8:49 | 49.959
2021-01-16 | 8:49 | 49.961
2021-01-16 | 8:49 | 49.96
2021-01-16 | 8:49 | 49.96
2021-01-16 | 8:49 | 49.959
2021-01-16 | 8:49 | 49.956
2021-01-16 | 8:49 | 49.956
2021-01-16 | 8:49 | 49.951
2021-01-16 | 8:49 | 49.949
2021-01-16 | 8:49 | 49.95
2021-01-16 | 8:49 | 49.949
2021-01-16 | 8:49 | 49.949
2021-01-16 | 8:49 | 49.951
2021-01-16 | 8:49 | 49.955
2021-01-16 | 8:49 | 49.96
2021-01-16 | 8:49 | 49.966
2021-01-16 | 8:49 | 49.967
2021-01-16 | 8:49 | 49.968
2021-01-16 | 8:49 | 49.966
2021-01-16 | 8:49 | 49.967
2021-01-16 | 8:49 | 49.967
2021-01-16 | 8:49 | 49.966
2021-01-16 | 8:49 | 49.967
2021-01-16 | 8:49 | 49.966
2021-01-16 | 8:49 | 49.966
2021-01-16 | 8:49 | 49.968
2021-01-16 | 8:49 | 49.969
2021-01-16 | 8:49 | 49.971
2021-01-16 | 8:49 | 49.969
2021-01-16 | 8:49 | 49.969
2021-01-16 | 8:49 | 49.968
2021-01-16 | 8:49 | 49.962
2021-01-16 | 8:49 | 49.962
2021-01-16 | 8:49 | 49.963
2021-01-16 | 8:49 | 49.969
2021-01-16 | 8:49 | 49.973
2021-01-16 | 8:50 | 49.975
2021-01-16 | 8:50 | 49.981
2021-01-16 | 8:50 | 49.984
2021-01-16 | 8:50 | 49.988
2021-01-16 | 8:50 | 49.988
2021-01-16 | 8:50 | 49.987
2021-01-16 | 8:50 | 49.988
2021-01-16 | 8:50 | 49.985
2021-01-16 | 8:50 | 49.985
2021-01-16 | 8:50 | 49.982
2021-01-16 | 8:50 | 49.979
2021-01-16 | 8:50 | 49.978
2021-01-16 | 8:50 | 49.974
2021-01-16 | 8:50 | 49.973
2021-01-16 | 8:50 | 49.971
2021-01-16 | 8:50 | 49.97
2021-01-16 | 8:50 | 49.969
2021-01-16 | 8:50 | 49.972
2021-01-16 | 8:50 | 49.971
2021-01-16 | 8:50 | 49.974
2021-01-16 | 8:50 | 49.972
2021-01-16 | 8:50 | 49.971
2021-01-16 | 8:50 | 49.972
2021-01-16 | 8:50 | 49.969
2021-01-16 | 8:50 | 49.97
2021-01-16 | 8:50 | 49.969
2021-01-16 | 8:50 | 49.965
2021-01-16 | 8:50 | 49.964
2021-01-16 | 8:50 | 49.964
2021-01-16 | 8:50 | 49.964
2021-01-16 | 8:50 | 49.968
2021-01-16 | 8:50 | 49.971
2021-01-16 | 8:50 | 49.974
2021-01-16 | 8:50 | 49.977
2021-01-16 | 8:50 | 49.978
2021-01-16 | 8:50 | 49.979
2021-01-16 | 8:50 | 49.979
2021-01-16 | 8:50 | 49.979
2021-01-16 | 8:50 | 49.979
2021-01-16 | 8:50 | 49.98
2021-01-16 | 8:50 | 49.979
2021-01-16 | 8:50 | 49.979
2021-01-16 | 8:50 | 49.978
2021-01-16 | 8:50 | 49.976
2021-01-16 | 8:50 | 49.977
2021-01-16 | 8:50 | 49.977
2021-01-16 | 8:50 | 49.977
2021-01-16 | 8:50 | 49.976
2021-01-16 | 8:50 | 49.975
2021-01-16 | 8:50 | 49.975
2021-01-16 | 8:50 | 49.974
2021-01-16 | 8:50 | 49.978
2021-01-16 | 8:50 | 49.98
2021-01-16 | 8:50 | 49.979
2021-01-16 | 8:50 | 49.978
2021-01-16 | 8:50 | 49.977
2021-01-16 | 8:50 | 49.976
2021-01-16 | 8:50 | 49.976
2021-01-16 | 8:50 | 49.978
2021-01-16 | 8:50 | 49.98
2021-01-16 | 8:50 | 49.981
2021-01-16 | 8:51 | 49.984
2021-01-16 | 8:51 | 49.986
2021-01-16 | 8:51 | 49.986
2021-01-16 | 8:51 | 49.988
2021-01-16 | 8:51 | 49.989
2021-01-16 | 8:51 | 49.989
2021-01-16 | 8:51 | 49.99
2021-01-16 | 8:51 | 49.991
2021-01-16 | 8:51 | 49.993
2021-01-16 | 8:51 | 49.994
2021-01-16 | 8:51 | 49.993
2021-01-16 | 8:51 | 49.993
2021-01-16 | 8:51 | 49.989
2021-01-16 | 8:51 | 49.983
2021-01-16 | 8:51 | 49.982
2021-01-16 | 8:51 | 49.98
2021-01-16 | 8:51 | 49.975
2021-01-16 | 8:51 | 49.968
2021-01-16 | 8:51 | 49.964
2021-01-16 | 8:51 | 49.965
2021-01-16 | 8:51 | 49.966
2021-01-16 | 8:51 | 49.963
2021-01-16 | 8:51 | 49.964
2021-01-16 | 8:51 | 49.964
2021-01-16 | 8:51 | 49.962
2021-01-16 | 8:51 | 49.963
2021-01-16 | 8:51 | 49.964
2021-01-16 | 8:51 | 49.966
2021-01-16 | 8:51 | 49.968
2021-01-16 | 8:51 | 49.967
2021-01-16 | 8:51 | 49.967
2021-01-16 | 8:51 | 49.969
2021-01-16 | 8:51 | 49.967
2021-01-16 | 8:51 | 49.966
2021-01-16 | 8:51 | 49.966
2021-01-16 | 8:51 | 49.964
2021-01-16 | 8:51 | 49.959
2021-01-16 | 8:51 | 49.958
2021-01-16 | 8:51 | 49.954
2021-01-16 | 8:51 | 49.953
2021-01-16 | 8:51 | 49.953
2021-01-16 | 8:51 | 49.956
2021-01-16 | 8:51 | 49.956
2021-01-16 | 8:51 | 49.957
2021-01-16 | 8:51 | 49.958
2021-01-16 | 8:51 | 49.959
2021-01-16 | 8:51 | 49.958
2021-01-16 | 8:51 | 49.959
2021-01-16 | 8:51 | 49.958
2021-01-16 | 8:51 | 49.958
2021-01-16 | 8:51 | 49.957
2021-01-16 | 8:51 | 49.956
2021-01-16 | 8:51 | 49.957
2021-01-16 | 8:51 | 49.958
2021-01-16 | 8:51 | 49.957
2021-01-16 | 8:51 | 49.959
2021-01-16 | 8:51 | 49.96
2021-01-16 | 8:51 | 49.961
2021-01-16 | 8:51 | 49.959
2021-01-16 | 8:52 | 49.961
2021-01-16 | 8:52 | 49.959
2021-01-16 | 8:52 | 49.958
2021-01-16 | 8:52 | 49.957
2021-01-16 | 8:52 | 49.959
2021-01-16 | 8:52 | 49.958
2021-01-16 | 8:52 | 49.96
2021-01-16 | 8:52 | 49.964
2021-01-16 | 8:52 | 49.965
2021-01-16 | 8:52 | 49.967
2021-01-16 | 8:52 | 49.974
2021-01-16 | 8:52 | 49.976
2021-01-16 | 8:52 | 49.977
2021-01-16 | 8:52 | 49.979
2021-01-16 | 8:52 | 49.982
2021-01-16 | 8:52 | 49.979
2021-01-16 | 8:52 | 49.977
2021-01-16 | 8:52 | 49.978
2021-01-16 | 8:52 | 49.974
2021-01-16 | 8:52 | 49.974
2021-01-16 | 8:52 | 49.972
2021-01-16 | 8:52 | 49.971
2021-01-16 | 8:52 | 49.973
2021-01-16 | 8:52 | 49.974
2021-01-16 | 8:52 | 49.976
2021-01-16 | 8:52 | 49.977
2021-01-16 | 8:52 | 49.98
2021-01-16 | 8:52 | 49.981
2021-01-16 | 8:52 | 49.98
2021-01-16 | 8:52 | 49.98
2021-01-16 | 8:52 | 49.98
2021-01-16 | 8:52 | 49.978
2021-01-16 | 8:52 | 49.978
2021-01-16 | 8:52 | 49.978
2021-01-16 | 8:52 | 49.978
2021-01-16 | 8:52 | 49.98
2021-01-16 | 8:52 | 49.979
2021-01-16 | 8:52 | 49.979
2021-01-16 | 8:52 | 49.982
2021-01-16 | 8:52 | 49.983
2021-01-16 | 8:52 | 49.981
2021-01-16 | 8:52 | 49.982
2021-01-16 | 8:52 | 49.982
2021-01-16 | 8:52 | 49.981
2021-01-16 | 8:52 | 49.98
2021-01-16 | 8:52 | 49.981
2021-01-16 | 8:52 | 49.978
2021-01-16 | 8:52 | 49.978
2021-01-16 | 8:52 | 49.974
2021-01-16 | 8:52 | 49.971
2021-01-16 | 8:52 | 49.97
2021-01-16 | 8:52 | 49.972
2021-01-16 | 8:52 | 49.974
2021-01-16 | 8:52 | 49.976
2021-01-16 | 8:52 | 49.977
2021-01-16 | 8:52 | 49.979
2021-01-16 | 8:52 | 49.982
2021-01-16 | 8:52 | 49.981
2021-01-16 | 8:52 | 49.982
2021-01-16 | 8:52 | 49.982
2021-01-16 | 8:52 | 49.981
2021-01-16 | 8:53 | 49.98
2021-01-16 | 8:53 | 49.982
2021-01-16 | 8:53 | 49.98
2021-01-16 | 8:53 | 49.978
2021-01-16 | 8:53 | 49.977
2021-01-16 | 8:53 | 49.973
2021-01-16 | 8:53 | 49.972
2021-01-16 | 8:53 | 49.97
2021-01-16 | 8:53 | 49.966
2021-01-16 | 8:53 | 49.965
2021-01-16 | 8:53 | 49.965
2021-01-16 | 8:53 | 49.968
2021-01-16 | 8:53 | 49.973
2021-01-16 | 8:53 | 49.977
2021-01-16 | 8:53 | 49.978
2021-01-16 | 8:53 | 49.981
2021-01-16 | 8:53 | 49.98
2021-01-16 | 8:53 | 49.979
2021-01-16 | 8:53 | 49.978
2021-01-16 | 8:53 | 49.975
2021-01-16 | 8:53 | 49.975
2021-01-16 | 8:53 | 49.971
2021-01-16 | 8:53 | 49.967
2021-01-16 | 8:53 | 49.964
2021-01-16 | 8:53 | 49.962
2021-01-16 | 8:53 | 49.96
2021-01-16 | 8:53 | 49.958
2021-01-16 | 8:53 | 49.959
2021-01-16 | 8:53 | 49.957
2021-01-16 | 8:53 | 49.956
2021-01-16 | 8:53 | 49.96
2021-01-16 | 8:53 | 49.964
2021-01-16 | 8:53 | 49.968
2021-01-16 | 8:53 | 49.972
2021-01-16 | 8:53 | 49.973
2021-01-16 | 8:53 | 49.974
2021-01-16 | 8:53 | 49.974
2021-01-16 | 8:53 | 49.97
2021-01-16 | 8:53 | 49.968
2021-01-16 | 8:53 | 49.966
2021-01-16 | 8:53 | 49.964
2021-01-16 | 8:53 | 49.964
2021-01-16 | 8:53 | 49.964
2021-01-16 | 8:53 | 49.962
2021-01-16 | 8:53 | 49.96
2021-01-16 | 8:53 | 49.957
2021-01-16 | 8:53 | 49.953
2021-01-16 | 8:53 | 49.95
2021-01-16 | 8:53 | 49.948
2021-01-16 | 8:53 | 49.948
2021-01-16 | 8:53 | 49.948
2021-01-16 | 8:53 | 49.949
2021-01-16 | 8:53 | 49.95
2021-01-16 | 8:53 | 49.954
2021-01-16 | 8:53 | 49.958
2021-01-16 | 8:53 | 49.959
2021-01-16 | 8:53 | 49.962
2021-01-16 | 8:53 | 49.962
2021-01-16 | 8:53 | 49.962
2021-01-16 | 8:54 | 49.962
2021-01-16 | 8:54 | 49.962
2021-01-16 | 8:54 | 49.962
2021-01-16 | 8:54 | 49.966
2021-01-16 | 8:54 | 49.967
2021-01-16 | 8:54 | 49.967
2021-01-16 | 8:54 | 49.964
2021-01-16 | 8:54 | 49.958
2021-01-16 | 8:54 | 49.954
2021-01-16 | 8:54 | 49.951
2021-01-16 | 8:54 | 49.943
2021-01-16 | 8:54 | 49.939
2021-01-16 | 8:54 | 49.936
2021-01-16 | 8:54 | 49.933
2021-01-16 | 8:54 | 49.932
2021-01-16 | 8:54 | 49.929
2021-01-16 | 8:54 | 49.927
2021-01-16 | 8:54 | 49.927
2021-01-16 | 8:54 | 49.928
2021-01-16 | 8:54 | 49.93
2021-01-16 | 8:54 | 49.933
2021-01-16 | 8:54 | 49.936
2021-01-16 | 8:54 | 49.939
2021-01-16 | 8:54 | 49.939
2021-01-16 | 8:54 | 49.943
2021-01-16 | 8:54 | 49.943
2021-01-16 | 8:54 | 49.94
2021-01-16 | 8:54 | 49.939
2021-01-16 | 8:54 | 49.937
2021-01-16 | 8:54 | 49.935
2021-01-16 | 8:54 | 49.934
2021-01-16 | 8:54 | 49.931
2021-01-16 | 8:54 | 49.932
2021-01-16 | 8:54 | 49.932
2021-01-16 | 8:54 | 49.935
2021-01-16 | 8:54 | 49.936
2021-01-16 | 8:54 | 49.937
2021-01-16 | 8:54 | 49.936
2021-01-16 | 8:54 | 49.937
2021-01-16 | 8:54 | 49.937
2021-01-16 | 8:54 | 49.937
2021-01-16 | 8:54 | 49.939
2021-01-16 | 8:54 | 49.937
2021-01-16 | 8:54 | 49.937
2021-01-16 | 8:54 | 49.936
2021-01-16 | 8:54 | 49.936
2021-01-16 | 8:54 | 49.936
2021-01-16 | 8:54 | 49.934
2021-01-16 | 8:54 | 49.931
2021-01-16 | 8:54 | 49.928
2021-01-16 | 8:54 | 49.929
2021-01-16 | 8:54 | 49.93
2021-01-16 | 8:54 | 49.93
2021-01-16 | 8:54 | 49.931
2021-01-16 | 8:54 | 49.93
2021-01-16 | 8:54 | 49.932
2021-01-16 | 8:54 | 49.932
2021-01-16 | 8:54 | 49.933
2021-01-16 | 8:54 | 49.934
2021-01-16 | 8:54 | 49.936
2021-01-16 | 8:54 | 49.938
2021-01-16 | 8:55 | 49.94
2021-01-16 | 8:55 | 49.941
2021-01-16 | 8:55 | 49.939
2021-01-16 | 8:55 | 49.94
2021-01-16 | 8:55 | 49.938
2021-01-16 | 8:55 | 49.932
2021-01-16 | 8:55 | 49.93
2021-01-16 | 8:55 | 49.928
2021-01-16 | 8:55 | 49.925
2021-01-16 | 8:55 | 49.924
2021-01-16 | 8:55 | 49.923
2021-01-16 | 8:55 | 49.924
2021-01-16 | 8:55 | 49.925
2021-01-16 | 8:55 | 49.925
2021-01-16 | 8:55 | 49.925
2021-01-16 | 8:55 | 49.925
2021-01-16 | 8:55 | 49.925
2021-01-16 | 8:55 | 49.926
2021-01-16 | 8:55 | 49.927
2021-01-16 | 8:55 | 49.925
2021-01-16 | 8:55 | 49.924
2021-01-16 | 8:55 | 49.924
2021-01-16 | 8:55 | 49.923
2021-01-16 | 8:55 | 49.924
2021-01-16 | 8:55 | 49.926
2021-01-16 | 8:55 | 49.927
2021-01-16 | 8:55 | 49.926
2021-01-16 | 8:55 | 49.928
2021-01-16 | 8:55 | 49.927
2021-01-16 | 8:55 | 49.923
2021-01-16 | 8:55 | 49.924
2021-01-16 | 8:55 | 49.921
2021-01-16 | 8:55 | 49.918
2021-01-16 | 8:55 | 49.916
2021-01-16 | 8:55 | 49.916
2021-01-16 | 8:55 | 49.917
2021-01-16 | 8:55 | 49.917
2021-01-16 | 8:55 | 49.918
2021-01-16 | 8:55 | 49.92
2021-01-16 | 8:55 | 49.918
2021-01-16 | 8:55 | 49.917
2021-01-16 | 8:55 | 49.918
2021-01-16 | 8:55 | 49.917
2021-01-16 | 8:55 | 49.918
2021-01-16 | 8:55 | 49.918
2021-01-16 | 8:55 | 49.918
2021-01-16 | 8:55 | 49.918
2021-01-16 | 8:55 | 49.92
2021-01-16 | 8:55 | 49.924
2021-01-16 | 8:55 | 49.926
2021-01-16 | 8:55 | 49.931
2021-01-16 | 8:55 | 49.932
2021-01-16 | 8:55 | 49.933
2021-01-16 | 8:55 | 49.934
2021-01-16 | 8:55 | 49.934
2021-01-16 | 8:55 | 49.933
2021-01-16 | 8:55 | 49.932
2021-01-16 | 8:55 | 49.927
2021-01-16 | 8:55 | 49.922
2021-01-16 | 8:56 | 49.922
2021-01-16 | 8:56 | 49.923
2021-01-16 | 8:56 | 49.928
2021-01-16 | 8:56 | 49.931
2021-01-16 | 8:56 | 49.933
2021-01-16 | 8:56 | 49.936
2021-01-16 | 8:56 | 49.936
2021-01-16 | 8:56 | 49.938
2021-01-16 | 8:56 | 49.939
2021-01-16 | 8:56 | 49.939
2021-01-16 | 8:56 | 49.938
2021-01-16 | 8:56 | 49.936
2021-01-16 | 8:56 | 49.934
2021-01-16 | 8:56 | 49.931
2021-01-16 | 8:56 | 49.931
2021-01-16 | 8:56 | 49.931
2021-01-16 | 8:56 | 49.93
2021-01-16 | 8:56 | 49.928
2021-01-16 | 8:56 | 49.929
2021-01-16 | 8:56 | 49.931
2021-01-16 | 8:56 | 49.933
2021-01-16 | 8:56 | 49.935
2021-01-16 | 8:56 | 49.935
2021-01-16 | 8:56 | 49.937
2021-01-16 | 8:56 | 49.935
2021-01-16 | 8:56 | 49.934
2021-01-16 | 8:56 | 49.937
2021-01-16 | 8:56 | 49.938
2021-01-16 | 8:56 | 49.937
2021-01-16 | 8:56 | 49.938
2021-01-16 | 8:56 | 49.938
2021-01-16 | 8:56 | 49.938
2021-01-16 | 8:56 | 49.937
2021-01-16 | 8:56 | 49.938
2021-01-16 | 8:56 | 49.939
2021-01-16 | 8:56 | 49.936
2021-01-16 | 8:56 | 49.932
2021-01-16 | 8:56 | 49.932
2021-01-16 | 8:56 | 49.931
2021-01-16 | 8:56 | 49.927
2021-01-16 | 8:56 | 49.924
2021-01-16 | 8:56 | 49.924
2021-01-16 | 8:56 | 49.925
2021-01-16 | 8:56 | 49.927
2021-01-16 | 8:56 | 49.929
2021-01-16 | 8:56 | 49.932
2021-01-16 | 8:56 | 49.932
2021-01-16 | 8:56 | 49.932
2021-01-16 | 8:56 | 49.931
2021-01-16 | 8:56 | 49.933
2021-01-16 | 8:56 | 49.933
2021-01-16 | 8:56 | 49.93
2021-01-16 | 8:56 | 49.929
2021-01-16 | 8:56 | 49.932
2021-01-16 | 8:56 | 49.933
2021-01-16 | 8:56 | 49.935
2021-01-16 | 8:56 | 49.935
2021-01-16 | 8:56 | 49.937
2021-01-16 | 8:56 | 49.939
2021-01-16 | 8:56 | 49.937
2021-01-16 | 8:56 | 49.932
2021-01-16 | 8:57 | 49.93
2021-01-16 | 8:57 | 49.928
2021-01-16 | 8:57 | 49.927
2021-01-16 | 8:57 | 49.922
2021-01-16 | 8:57 | 49.919
2021-01-16 | 8:57 | 49.916
2021-01-16 | 8:57 | 49.916
2021-01-16 | 8:57 | 49.915
2021-01-16 | 8:57 | 49.914
2021-01-16 | 8:57 | 49.917
2021-01-16 | 8:57 | 49.919
2021-01-16 | 8:57 | 49.92
2021-01-16 | 8:57 | 49.923
2021-01-16 | 8:57 | 49.925
2021-01-16 | 8:57 | 49.928
2021-01-16 | 8:57 | 49.928
2021-01-16 | 8:57 | 49.928
2021-01-16 | 8:57 | 49.93
2021-01-16 | 8:57 | 49.93
2021-01-16 | 8:57 | 49.929
2021-01-16 | 8:57 | 49.929
2021-01-16 | 8:57 | 49.925
2021-01-16 | 8:57 | 49.922
2021-01-16 | 8:57 | 49.921
2021-01-16 | 8:57 | 49.924
2021-01-16 | 8:57 | 49.925
2021-01-16 | 8:57 | 49.927
2021-01-16 | 8:57 | 49.928
2021-01-16 | 8:57 | 49.928
2021-01-16 | 8:57 | 49.928
2021-01-16 | 8:57 | 49.928
2021-01-16 | 8:57 | 49.925
2021-01-16 | 8:57 | 49.923
2021-01-16 | 8:57 | 49.923
2021-01-16 | 8:57 | 49.922
2021-01-16 | 8:57 | 49.923
2021-01-16 | 8:57 | 49.924
2021-01-16 | 8:57 | 49.926
2021-01-16 | 8:57 | 49.925
2021-01-16 | 8:57 | 49.926
2021-01-16 | 8:57 | 49.928
2021-01-16 | 8:57 | 49.929
2021-01-16 | 8:57 | 49.926
2021-01-16 | 8:57 | 49.927
2021-01-16 | 8:57 | 49.927
2021-01-16 | 8:57 | 49.928
2021-01-16 | 8:57 | 49.928
2021-01-16 | 8:57 | 49.927
2021-01-16 | 8:57 | 49.925
2021-01-16 | 8:57 | 49.925
2021-01-16 | 8:57 | 49.922
2021-01-16 | 8:57 | 49.919
2021-01-16 | 8:57 | 49.919
2021-01-16 | 8:57 | 49.92
2021-01-16 | 8:57 | 49.919
2021-01-16 | 8:57 | 49.921
2021-01-16 | 8:57 | 49.923
2021-01-16 | 8:57 | 49.924
2021-01-16 | 8:57 | 49.926
2021-01-16 | 8:58 | 49.931
2021-01-16 | 8:58 | 49.937
2021-01-16 | 8:58 | 49.944
2021-01-16 | 8:58 | 49.949
2021-01-16 | 8:58 | 49.947
2021-01-16 | 8:58 | 49.944
2021-01-16 | 8:58 | 49.944
2021-01-16 | 8:58 | 49.943
2021-01-16 | 8:58 | 49.942
2021-01-16 | 8:58 | 49.942
2021-01-16 | 8:58 | 49.941
2021-01-16 | 8:58 | 49.94
2021-01-16 | 8:58 | 49.94
2021-01-16 | 8:58 | 49.943
2021-01-16 | 8:58 | 49.947
2021-01-16 | 8:58 | 49.95
2021-01-16 | 8:58 | 49.955
2021-01-16 | 8:58 | 49.957
2021-01-16 | 8:58 | 49.956
2021-01-16 | 8:58 | 49.958
2021-01-16 | 8:58 | 49.96
2021-01-16 | 8:58 | 49.96
2021-01-16 | 8:58 | 49.96
2021-01-16 | 8:58 | 49.96
2021-01-16 | 8:58 | 49.958
2021-01-16 | 8:58 | 49.956
2021-01-16 | 8:58 | 49.953
2021-01-16 | 8:58 | 49.951
2021-01-16 | 8:58 | 49.95
2021-01-16 | 8:58 | 49.949
2021-01-16 | 8:58 | 49.948
2021-01-16 | 8:58 | 49.947
2021-01-16 | 8:58 | 49.948
2021-01-16 | 8:58 | 49.948
2021-01-16 | 8:58 | 49.947
2021-01-16 | 8:58 | 49.946
2021-01-16 | 8:58 | 49.944
2021-01-16 | 8:58 | 49.942
2021-01-16 | 8:58 | 49.941
2021-01-16 | 8:58 | 49.938
2021-01-16 | 8:58 | 49.936
2021-01-16 | 8:58 | 49.937
2021-01-16 | 8:58 | 49.937
2021-01-16 | 8:58 | 49.936
2021-01-16 | 8:58 | 49.935
2021-01-16 | 8:58 | 49.936
2021-01-16 | 8:58 | 49.933
2021-01-16 | 8:58 | 49.931
2021-01-16 | 8:58 | 49.929
2021-01-16 | 8:58 | 49.929
2021-01-16 | 8:58 | 49.927
2021-01-16 | 8:58 | 49.924
2021-01-16 | 8:58 | 49.924
2021-01-16 | 8:58 | 49.924
2021-01-16 | 8:58 | 49.925
2021-01-16 | 8:58 | 49.925
2021-01-16 | 8:58 | 49.926
2021-01-16 | 8:58 | 49.927
2021-01-16 | 8:58 | 49.927
2021-01-16 | 8:58 | 49.929
2021-01-16 | 8:58 | 49.932
2021-01-16 | 8:59 | 49.932
2021-01-16 | 8:59 | 49.933
2021-01-16 | 8:59 | 49.932
2021-01-16 | 8:59 | 49.931
2021-01-16 | 8:59 | 49.932
2021-01-16 | 8:59 | 49.929
2021-01-16 | 8:59 | 49.927
2021-01-16 | 8:59 | 49.925
2021-01-16 | 8:59 | 49.924
2021-01-16 | 8:59 | 49.924
2021-01-16 | 8:59 | 49.924
2021-01-16 | 8:59 | 49.924
2021-01-16 | 8:59 | 49.925
2021-01-16 | 8:59 | 49.925
2021-01-16 | 8:59 | 49.929
2021-01-16 | 8:59 | 49.931
2021-01-16 | 8:59 | 49.932
2021-01-16 | 8:59 | 49.936
2021-01-16 | 8:59 | 49.94
2021-01-16 | 8:59 | 49.943
2021-01-16 | 8:59 | 49.945
2021-01-16 | 8:59 | 49.944
2021-01-16 | 8:59 | 49.94
2021-01-16 | 8:59 | 49.938
2021-01-16 | 8:59 | 49.938
2021-01-16 | 8:59 | 49.935
2021-01-16 | 8:59 | 49.929
2021-01-16 | 8:59 | 49.928
2021-01-16 | 8:59 | 49.93
2021-01-16 | 8:59 | 49.928
2021-01-16 | 8:59 | 49.927
2021-01-16 | 8:59 | 49.927
2021-01-16 | 8:59 | 49.926
2021-01-16 | 8:59 | 49.923
2021-01-16 | 8:59 | 49.921
2021-01-16 | 8:59 | 49.921
2021-01-16 | 8:59 | 49.921
2021-01-16 | 8:59 | 49.921
2021-01-16 | 8:59 | 49.922
2021-01-16 | 8:59 | 49.925
2021-01-16 | 8:59 | 49.928
2021-01-16 | 8:59 | 49.93
2021-01-16 | 8:59 | 49.935
2021-01-16 | 8:59 | 49.939
2021-01-16 | 8:59 | 49.942
2021-01-16 | 8:59 | 49.941
2021-01-16 | 8:59 | 49.939
2021-01-16 | 8:59 | 49.938
2021-01-16 | 8:59 | 49.938
2021-01-16 | 8:59 | 49.937
2021-01-16 | 8:59 | 49.938
2021-01-16 | 8:59 | 49.943
2021-01-16 | 8:59 | 49.948
2021-01-16 | 8:59 | 49.951
2021-01-16 | 8:59 | 49.951
2021-01-16 | 8:59 | 49.951
2021-01-16 | 8:59 | 49.951
2021-01-16 | 8:59 | 49.949
2021-01-16 | 8:59 | 49.945
2021-01-16 | 9:00 | 49.941
2021-01-16 | 9:00 | 49.94
2021-01-16 | 9:00 | 49.94
2021-01-16 | 9:00 | 49.938
2021-01-16 | 9:00 | 49.937
2021-01-16 | 9:00 | 49.936
2021-01-16 | 9:00 | 49.938
2021-01-16 | 9:00 | 49.938
2021-01-16 | 9:00 | 49.939
2021-01-16 | 9:00 | 49.94
2021-01-16 | 9:00 | 49.942
2021-01-16 | 9:00 | 49.942
2021-01-16 | 9:00 | 49.944
2021-01-16 | 9:00 | 49.947
2021-01-16 | 9:00 | 49.949
2021-01-16 | 9:00 | 49.949
2021-01-16 | 9:00 | 49.95
2021-01-16 | 9:00 | 49.951
2021-01-16 | 9:00 | 49.95
2021-01-16 | 9:00 | 49.95
2021-01-16 | 9:00 | 49.951
2021-01-16 | 9:00 | 49.951
2021-01-16 | 9:00 | 49.951
2021-01-16 | 9:00 | 49.95
2021-01-16 | 9:00 | 49.947
2021-01-16 | 9:00 | 49.944
2021-01-16 | 9:00 | 49.943
2021-01-16 | 9:00 | 49.941
2021-01-16 | 9:00 | 49.939
2021-01-16 | 9:00 | 49.941
2021-01-16 | 9:00 | 49.937
2021-01-16 | 9:00 | 49.934
2021-01-16 | 9:00 | 49.93
2021-01-16 | 9:00 | 49.927
2021-01-16 | 9:00 | 49.929
2021-01-16 | 9:00 | 49.927
2021-01-16 | 9:00 | 49.928
2021-01-16 | 9:00 | 49.929
2021-01-16 | 9:00 | 49.928
2021-01-16 | 9:00 | 49.931
2021-01-16 | 9:00 | 49.931
2021-01-16 | 9:00 | 49.933
2021-01-16 | 9:00 | 49.933
2021-01-16 | 9:00 | 49.932
2021-01-16 | 9:00 | 49.934
2021-01-16 | 9:00 | 49.934
2021-01-16 | 9:00 | 49.934
2021-01-16 | 9:00 | 49.936
2021-01-16 | 9:00 | 49.938
2021-01-16 | 9:00 | 49.94
2021-01-16 | 9:00 | 49.942
2021-01-16 | 9:00 | 49.94
2021-01-16 | 9:00 | 49.939
2021-01-16 | 9:00 | 49.937
2021-01-16 | 9:00 | 49.935
2021-01-16 | 9:00 | 49.935
2021-01-16 | 9:00 | 49.935
2021-01-16 | 9:00 | 49.934
2021-01-16 | 9:00 | 49.937
2021-01-16 | 9:00 | 49.94
2021-01-16 | 9:00 | 49.94
2021-01-16 | 9:01 | 49.938
2021-01-16 | 9:01 | 49.936
2021-01-16 | 9:01 | 49.936
2021-01-16 | 9:01 | 49.936
2021-01-16 | 9:01 | 49.936
2021-01-16 | 9:01 | 49.933
2021-01-16 | 9:01 | 49.932
2021-01-16 | 9:01 | 49.931
2021-01-16 | 9:01 | 49.93
2021-01-16 | 9:01 | 49.928
2021-01-16 | 9:01 | 49.928
2021-01-16 | 9:01 | 49.929
2021-01-16 | 9:01 | 49.932
2021-01-16 | 9:01 | 49.937
2021-01-16 | 9:01 | 49.94
2021-01-16 | 9:01 | 49.94
2021-01-16 | 9:01 | 49.938
2021-01-16 | 9:01 | 49.94
2021-01-16 | 9:01 | 49.939
2021-01-16 | 9:01 | 49.938
2021-01-16 | 9:01 | 49.937
2021-01-16 | 9:01 | 49.935
2021-01-16 | 9:01 | 49.931
2021-01-16 | 9:01 | 49.931
2021-01-16 | 9:01 | 49.935
2021-01-16 | 9:01 | 49.936
2021-01-16 | 9:01 | 49.934
2021-01-16 | 9:01 | 49.936
2021-01-16 | 9:01 | 49.936
2021-01-16 | 9:01 | 49.935
2021-01-16 | 9:01 | 49.934
2021-01-16 | 9:01 | 49.932
2021-01-16 | 9:01 | 49.929
2021-01-16 | 9:01 | 49.928
2021-01-16 | 9:01 | 49.928
2021-01-16 | 9:01 | 49.926
2021-01-16 | 9:01 | 49.928
2021-01-16 | 9:01 | 49.929
2021-01-16 | 9:01 | 49.932
2021-01-16 | 9:01 | 49.932
2021-01-16 | 9:01 | 49.933
2021-01-16 | 9:01 | 49.934
2021-01-16 | 9:01 | 49.937
2021-01-16 | 9:01 | 49.937
2021-01-16 | 9:01 | 49.939
2021-01-16 | 9:01 | 49.942
2021-01-16 | 9:01 | 49.941
2021-01-16 | 9:01 | 49.941
2021-01-16 | 9:01 | 49.942
2021-01-16 | 9:01 | 49.943
2021-01-16 | 9:01 | 49.945
2021-01-16 | 9:01 | 49.946
2021-01-16 | 9:01 | 49.946
2021-01-16 | 9:01 | 49.947
2021-01-16 | 9:01 | 49.949
2021-01-16 | 9:01 | 49.95
2021-01-16 | 9:01 | 49.951
2021-01-16 | 9:01 | 49.949
2021-01-16 | 9:01 | 49.95
2021-01-16 | 9:02 | 49.95
2021-01-16 | 9:02 | 49.951
2021-01-16 | 9:02 | 49.952
2021-01-16 | 9:02 | 49.952
2021-01-16 | 9:02 | 49.949
2021-01-16 | 9:02 | 49.945
2021-01-16 | 9:02 | 49.942
2021-01-16 | 9:02 | 49.939
2021-01-16 | 9:02 | 49.938
2021-01-16 | 9:02 | 49.941
2021-01-16 | 9:02 | 49.942
2021-01-16 | 9:02 | 49.942
2021-01-16 | 9:02 | 49.944
2021-01-16 | 9:02 | 49.946
2021-01-16 | 9:02 | 49.948
2021-01-16 | 9:02 | 49.949
2021-01-16 | 9:02 | 49.95
2021-01-16 | 9:02 | 49.951
2021-01-16 | 9:02 | 49.95
2021-01-16 | 9:02 | 49.951
2021-01-16 | 9:02 | 49.95
2021-01-16 | 9:02 | 49.952
2021-01-16 | 9:02 | 49.953
2021-01-16 | 9:02 | 49.953
2021-01-16 | 9:02 | 49.955
2021-01-16 | 9:02 | 49.96
2021-01-16 | 9:02 | 49.965
2021-01-16 | 9:02 | 49.965
2021-01-16 | 9:02 | 49.961
2021-01-16 | 9:02 | 49.96
2021-01-16 | 9:02 | 49.957
2021-01-16 | 9:02 | 49.954
2021-01-16 | 9:02 | 49.952
2021-01-16 | 9:02 | 49.95
2021-01-16 | 9:02 | 49.949
2021-01-16 | 9:02 | 49.947
2021-01-16 | 9:02 | 49.948
2021-01-16 | 9:02 | 49.948
2021-01-16 | 9:02 | 49.949
2021-01-16 | 9:02 | 49.95
2021-01-16 | 9:02 | 49.952
2021-01-16 | 9:02 | 49.954
2021-01-16 | 9:02 | 49.956
2021-01-16 | 9:02 | 49.956
2021-01-16 | 9:02 | 49.958
2021-01-16 | 9:02 | 49.961
2021-01-16 | 9:02 | 49.962
2021-01-16 | 9:02 | 49.962
2021-01-16 | 9:02 | 49.963
2021-01-16 | 9:02 | 49.963
2021-01-16 | 9:02 | 49.962
2021-01-16 | 9:02 | 49.958
2021-01-16 | 9:02 | 49.957
2021-01-16 | 9:02 | 49.959
2021-01-16 | 9:02 | 49.96
2021-01-16 | 9:02 | 49.963
2021-01-16 | 9:02 | 49.965
2021-01-16 | 9:02 | 49.969
2021-01-16 | 9:02 | 49.973
2021-01-16 | 9:02 | 49.975
2021-01-16 | 9:02 | 49.977
2021-01-16 | 9:03 | 49.976
2021-01-16 | 9:03 | 49.978
2021-01-16 | 9:03 | 49.981
2021-01-16 | 9:03 | 49.983
2021-01-16 | 9:03 | 49.986
2021-01-16 | 9:03 | 49.988
2021-01-16 | 9:03 | 49.989
2021-01-16 | 9:03 | 49.987
2021-01-16 | 9:03 | 49.986
2021-01-16 | 9:03 | 49.988
2021-01-16 | 9:03 | 49.989
2021-01-16 | 9:03 | 49.991
2021-01-16 | 9:03 | 49.992
2021-01-16 | 9:03 | 49.995
2021-01-16 | 9:03 | 49.999
2021-01-16 | 9:03 | 50.001
2021-01-16 | 9:03 | 50.005
2021-01-16 | 9:03 | 50.01
2021-01-16 | 9:03 | 50.015
2021-01-16 | 9:03 | 50.02
2021-01-16 | 9:03 | 50.022
2021-01-16 | 9:03 | 50.022
2021-01-16 | 9:03 | 50.024
2021-01-16 | 9:03 | 50.028
2021-01-16 | 9:03 | 50.03
2021-01-16 | 9:03 | 50.03
2021-01-16 | 9:03 | 50.031
2021-01-16 | 9:03 | 50.032
2021-01-16 | 9:03 | 50.033
2021-01-16 | 9:03 | 50.032
2021-01-16 | 9:03 | 50.028
2021-01-16 | 9:03 | 50.022
2021-01-16 | 9:03 | 50.02
2021-01-16 | 9:03 | 50.02
2021-01-16 | 9:03 | 50.021
2021-01-16 | 9:03 | 50.022
2021-01-16 | 9:03 | 50.02
2021-01-16 | 9:03 | 50.02
2021-01-16 | 9:03 | 50.019
2021-01-16 | 9:03 | 50.018
2021-01-16 | 9:03 | 50.018
2021-01-16 | 9:03 | 50.017
2021-01-16 | 9:03 | 50.016
2021-01-16 | 9:03 | 50.014
2021-01-16 | 9:03 | 50.015
2021-01-16 | 9:03 | 50.017
2021-01-16 | 9:03 | 50.016
2021-01-16 | 9:03 | 50.017
2021-01-16 | 9:03 | 50.015
2021-01-16 | 9:03 | 50.014
2021-01-16 | 9:03 | 50.013
2021-01-16 | 9:03 | 50.012
2021-01-16 | 9:03 | 50.014
2021-01-16 | 9:03 | 50.015
2021-01-16 | 9:03 | 50.016
2021-01-16 | 9:03 | 50.019
2021-01-16 | 9:03 | 50.021
2021-01-16 | 9:03 | 50.025
2021-01-16 | 9:03 | 50.028
2021-01-16 | 9:04 | 50.033
2021-01-16 | 9:04 | 50.036
2021-01-16 | 9:04 | 50.041
2021-01-16 | 9:04 | 50.045
2021-01-16 | 9:04 | 50.045
2021-01-16 | 9:04 | 50.046
2021-01-16 | 9:04 | 50.047
2021-01-16 | 9:04 | 50.049
2021-01-16 | 9:04 | 50.052
2021-01-16 | 9:04 | 50.053
2021-01-16 | 9:04 | 50.053
2021-01-16 | 9:04 | 50.054
2021-01-16 | 9:04 | 50.056
2021-01-16 | 9:04 | 50.057
2021-01-16 | 9:04 | 50.056
2021-01-16 | 9:04 | 50.053
2021-01-16 | 9:04 | 50.051
2021-01-16 | 9:04 | 50.047
2021-01-16 | 9:04 | 50.045
2021-01-16 | 9:04 | 50.042
2021-01-16 | 9:04 | 50.042
2021-01-16 | 9:04 | 50.042
2021-01-16 | 9:04 | 50.045
2021-01-16 | 9:04 | 50.049
2021-01-16 | 9:04 | 50.051
2021-01-16 | 9:04 | 50.052
2021-01-16 | 9:04 | 50.049
2021-01-16 | 9:04 | 50.049
2021-01-16 | 9:04 | 50.048
2021-01-16 | 9:04 | 50.049
2021-01-16 | 9:04 | 50.047
2021-01-16 | 9:04 | 50.044
2021-01-16 | 9:04 | 50.041
2021-01-16 | 9:04 | 50.037
2021-01-16 | 9:04 | 50.035
2021-01-16 | 9:04 | 50.036
2021-01-16 | 9:04 | 50.037
2021-01-16 | 9:04 | 50.04
2021-01-16 | 9:04 | 50.042
2021-01-16 | 9:04 | 50.043
2021-01-16 | 9:04 | 50.044
2021-01-16 | 9:04 | 50.042
2021-01-16 | 9:04 | 50.043
2021-01-16 | 9:04 | 50.044
2021-01-16 | 9:04 | 50.045
2021-01-16 | 9:04 | 50.044
2021-01-16 | 9:04 | 50.044
2021-01-16 | 9:04 | 50.045
2021-01-16 | 9:04 | 50.046
2021-01-16 | 9:04 | 50.047
2021-01-16 | 9:04 | 50.048
2021-01-16 | 9:04 | 50.047
2021-01-16 | 9:04 | 50.047
2021-01-16 | 9:04 | 50.045
2021-01-16 | 9:04 | 50.043
2021-01-16 | 9:04 | 50.042
2021-01-16 | 9:04 | 50.04
2021-01-16 | 9:04 | 50.039
2021-01-16 | 9:04 | 50.04
2021-01-16 | 9:04 | 50.04
2021-01-16 | 9:04 | 50.041
2021-01-16 | 9:05 | 50.04
2021-01-16 | 9:05 | 50.038
2021-01-16 | 9:05 | 50.037
2021-01-16 | 9:05 | 50.038
2021-01-16 | 9:05 | 50.04
2021-01-16 | 9:05 | 50.043
2021-01-16 | 9:05 | 50.044
2021-01-16 | 9:05 | 50.045
2021-01-16 | 9:05 | 50.045
2021-01-16 | 9:05 | 50.043
2021-01-16 | 9:05 | 50.043
2021-01-16 | 9:05 | 50.04
2021-01-16 | 9:05 | 50.039
2021-01-16 | 9:05 | 50.04
2021-01-16 | 9:05 | 50.039
2021-01-16 | 9:05 | 50.036
2021-01-16 | 9:05 | 50.034
2021-01-16 | 9:05 | 50.033
2021-01-16 | 9:05 | 50.032
2021-01-16 | 9:05 | 50.029
2021-01-16 | 9:05 | 50.028
2021-01-16 | 9:05 | 50.027
2021-01-16 | 9:05 | 50.029
2021-01-16 | 9:05 | 50.032
2021-01-16 | 9:05 | 50.035
2021-01-16 | 9:05 | 50.035
2021-01-16 | 9:05 | 50.034
2021-01-16 | 9:05 | 50.033
2021-01-16 | 9:05 | 50.032
2021-01-16 | 9:05 | 50.032
2021-01-16 | 9:05 | 50.03
2021-01-16 | 9:05 | 50.026
2021-01-16 | 9:05 | 50.023
2021-01-16 | 9:05 | 50.022
2021-01-16 | 9:05 | 50.023
2021-01-16 | 9:05 | 50.021
2021-01-16 | 9:05 | 50.02
2021-01-16 | 9:05 | 50.019
2021-01-16 | 9:05 | 50.02
2021-01-16 | 9:05 | 50.02
2021-01-16 | 9:05 | 50.019
2021-01-16 | 9:05 | 50.019
2021-01-16 | 9:05 | 50.017
2021-01-16 | 9:05 | 50.016
2021-01-16 | 9:05 | 50.015
2021-01-16 | 9:05 | 50.015
2021-01-16 | 9:05 | 50.014
2021-01-16 | 9:05 | 50.011
2021-01-16 | 9:05 | 50.011
2021-01-16 | 9:05 | 50.009
2021-01-16 | 9:05 | 50.006
2021-01-16 | 9:05 | 50.003
2021-01-16 | 9:05 | 50.004
2021-01-16 | 9:05 | 50.006
2021-01-16 | 9:05 | 50.007
2021-01-16 | 9:05 | 50.008
2021-01-16 | 9:05 | 50.009
2021-01-16 | 9:05 | 50.009
2021-01-16 | 9:05 | 50.01
2021-01-16 | 9:06 | 50.011
2021-01-16 | 9:06 | 50.012
2021-01-16 | 9:06 | 50.011
2021-01-16 | 9:06 | 50.013
2021-01-16 | 9:06 | 50.015
2021-01-16 | 9:06 | 50.018
2021-01-16 | 9:06 | 50.017
2021-01-16 | 9:06 | 50.015
2021-01-16 | 9:06 | 50.013
2021-01-16 | 9:06 | 50.01
2021-01-16 | 9:06 | 50.008
2021-01-16 | 9:06 | 50.008
2021-01-16 | 9:06 | 50.009
2021-01-16 | 9:06 | 50.01
2021-01-16 | 9:06 | 50.012
2021-01-16 | 9:06 | 50.014
2021-01-16 | 9:06 | 50.017
2021-01-16 | 9:06 | 50.019
2021-01-16 | 9:06 | 50.021
2021-01-16 | 9:06 | 50.02
2021-01-16 | 9:06 | 50.021
2021-01-16 | 9:06 | 50.019
2021-01-16 | 9:06 | 50.018
2021-01-16 | 9:06 | 50.02
2021-01-16 | 9:06 | 50.02
2021-01-16 | 9:06 | 50.017
2021-01-16 | 9:06 | 50.015
2021-01-16 | 9:06 | 50.013
2021-01-16 | 9:06 | 50.014
2021-01-16 | 9:06 | 50.017
2021-01-16 | 9:06 | 50.02
2021-01-16 | 9:06 | 50.02
2021-01-16 | 9:06 | 50.021
2021-01-16 | 9:06 | 50.023
2021-01-16 | 9:06 | 50.024
2021-01-16 | 9:06 | 50.026
2021-01-16 | 9:06 | 50.026
2021-01-16 | 9:06 | 50.025
2021-01-16 | 9:06 | 50.025
2021-01-16 | 9:06 | 50.025
2021-01-16 | 9:06 | 50.025
2021-01-16 | 9:06 | 50.025
2021-01-16 | 9:06 | 50.023
2021-01-16 | 9:06 | 50.02
2021-01-16 | 9:06 | 50.018
2021-01-16 | 9:06 | 50.014
2021-01-16 | 9:06 | 50.01
2021-01-16 | 9:06 | 50.005
2021-01-16 | 9:06 | 50
2021-01-16 | 9:06 | 49.997
2021-01-16 | 9:06 | 49.995
2021-01-16 | 9:06 | 49.998
2021-01-16 | 9:06 | 49.999
2021-01-16 | 9:06 | 50.002
2021-01-16 | 9:06 | 50.008
2021-01-16 | 9:06 | 50.011
2021-01-16 | 9:06 | 50.011
2021-01-16 | 9:06 | 50.014
2021-01-16 | 9:06 | 50.014
2021-01-16 | 9:06 | 50.015
2021-01-16 | 9:06 | 50.015
2021-01-16 | 9:07 | 50.014
2021-01-16 | 9:07 | 50.016
2021-01-16 | 9:07 | 50.017
2021-01-16 | 9:07 | 50.017
2021-01-16 | 9:07 | 50.015
2021-01-16 | 9:07 | 50.015
2021-01-16 | 9:07 | 50.014
2021-01-16 | 9:07 | 50.013
2021-01-16 | 9:07 | 50.012
2021-01-16 | 9:07 | 50.012
2021-01-16 | 9:07 | 50.012
2021-01-16 | 9:07 | 50.008
2021-01-16 | 9:07 | 50.005
2021-01-16 | 9:07 | 50.002
2021-01-16 | 9:07 | 50
2021-01-16 | 9:07 | 49.997
2021-01-16 | 9:07 | 49.996
2021-01-16 | 9:07 | 49.993
2021-01-16 | 9:07 | 49.992
2021-01-16 | 9:07 | 49.989
2021-01-16 | 9:07 | 49.987
2021-01-16 | 9:07 | 49.988
2021-01-16 | 9:07 | 49.988
2021-01-16 | 9:07 | 49.987
2021-01-16 | 9:07 | 49.984
2021-01-16 | 9:07 | 49.985
2021-01-16 | 9:07 | 49.983
2021-01-16 | 9:07 | 49.982
2021-01-16 | 9:07 | 49.98
2021-01-16 | 9:07 | 49.978
2021-01-16 | 9:07 | 49.976
2021-01-16 | 9:07 | 49.969
2021-01-16 | 9:07 | 49.963
2021-01-16 | 9:07 | 49.956
2021-01-16 | 9:07 | 49.948
2021-01-16 | 9:07 | 49.94
2021-01-16 | 9:07 | 49.934
2021-01-16 | 9:07 | 49.927
2021-01-16 | 9:07 | 49.924
2021-01-16 | 9:07 | 49.924
2021-01-16 | 9:07 | 49.923
2021-01-16 | 9:07 | 49.924
2021-01-16 | 9:07 | 49.927
2021-01-16 | 9:07 | 49.929
2021-01-16 | 9:07 | 49.93
2021-01-16 | 9:07 | 49.931
2021-01-16 | 9:07 | 49.931
2021-01-16 | 9:07 | 49.93
2021-01-16 | 9:07 | 49.93
2021-01-16 | 9:07 | 49.929
2021-01-16 | 9:07 | 49.927
2021-01-16 | 9:07 | 49.925
2021-01-16 | 9:07 | 49.924
2021-01-16 | 9:07 | 49.924
2021-01-16 | 9:07 | 49.922
2021-01-16 | 9:07 | 49.922
2021-01-16 | 9:07 | 49.919
2021-01-16 | 9:07 | 49.918
2021-01-16 | 9:07 | 49.916
2021-01-16 | 9:08 | 49.917
2021-01-16 | 9:08 | 49.918
2021-01-16 | 9:08 | 49.923
2021-01-16 | 9:08 | 49.925
2021-01-16 | 9:08 | 49.925
2021-01-16 | 9:08 | 49.925
2021-01-16 | 9:08 | 49.924
2021-01-16 | 9:08 | 49.923
2021-01-16 | 9:08 | 49.919
2021-01-16 | 9:08 | 49.919
2021-01-16 | 9:08 | 49.917
2021-01-16 | 9:08 | 49.915
2021-01-16 | 9:08 | 49.916
2021-01-16 | 9:08 | 49.916
2021-01-16 | 9:08 | 49.918
2021-01-16 | 9:08 | 49.918
2021-01-16 | 9:08 | 49.919
2021-01-16 | 9:08 | 49.919
2021-01-16 | 9:08 | 49.919
2021-01-16 | 9:08 | 49.917
2021-01-16 | 9:08 | 49.916
2021-01-16 | 9:08 | 49.917
2021-01-16 | 9:08 | 49.918
2021-01-16 | 9:08 | 49.919
2021-01-16 | 9:08 | 49.922
2021-01-16 | 9:08 | 49.924
2021-01-16 | 9:08 | 49.925
2021-01-16 | 9:08 | 49.925
2021-01-16 | 9:08 | 49.923
2021-01-16 | 9:08 | 49.922
2021-01-16 | 9:08 | 49.921
2021-01-16 | 9:08 | 49.92
2021-01-16 | 9:08 | 49.918
2021-01-16 | 9:08 | 49.915
2021-01-16 | 9:08 | 49.911
2021-01-16 | 9:08 | 49.909
2021-01-16 | 9:08 | 49.909
2021-01-16 | 9:08 | 49.91
2021-01-16 | 9:08 | 49.912
2021-01-16 | 9:08 | 49.91
2021-01-16 | 9:08 | 49.909
2021-01-16 | 9:08 | 49.907
2021-01-16 | 9:08 | 49.907
2021-01-16 | 9:08 | 49.908
2021-01-16 | 9:08 | 49.906
2021-01-16 | 9:08 | 49.906
2021-01-16 | 9:08 | 49.908
2021-01-16 | 9:08 | 49.909
2021-01-16 | 9:08 | 49.91
2021-01-16 | 9:08 | 49.912
2021-01-16 | 9:08 | 49.91
2021-01-16 | 9:08 | 49.909
2021-01-16 | 9:08 | 49.909
2021-01-16 | 9:08 | 49.914
2021-01-16 | 9:08 | 49.914
2021-01-16 | 9:08 | 49.913
2021-01-16 | 9:08 | 49.91
2021-01-16 | 9:08 | 49.909
2021-01-16 | 9:08 | 49.908
2021-01-16 | 9:08 | 49.905
2021-01-16 | 9:08 | 49.902
2021-01-16 | 9:09 | 49.901
2021-01-16 | 9:09 | 49.899
2021-01-16 | 9:09 | 49.897
2021-01-16 | 9:09 | 49.901
2021-01-16 | 9:09 | 49.901
2021-01-16 | 9:09 | 49.901
2021-01-16 | 9:09 | 49.9
2021-01-16 | 9:09 | 49.898
2021-01-16 | 9:09 | 49.896
2021-01-16 | 9:09 | 49.894
2021-01-16 | 9:09 | 49.896
2021-01-16 | 9:09 | 49.899
2021-01-16 | 9:09 | 49.901
2021-01-16 | 9:09 | 49.903
2021-01-16 | 9:09 | 49.902
2021-01-16 | 9:09 | 49.901
2021-01-16 | 9:09 | 49.899
2021-01-16 | 9:09 | 49.9
2021-01-16 | 9:09 | 49.903
2021-01-16 | 9:09 | 49.902
2021-01-16 | 9:09 | 49.901
2021-01-16 | 9:09 | 49.899
2021-01-16 | 9:09 | 49.898
2021-01-16 | 9:09 | 49.9
2021-01-16 | 9:09 | 49.901
2021-01-16 | 9:09 | 49.902
2021-01-16 | 9:09 | 49.9
2021-01-16 | 9:09 | 49.898
2021-01-16 | 9:09 | 49.898
2021-01-16 | 9:09 | 49.899
2021-01-16 | 9:09 | 49.899
2021-01-16 | 9:09 | 49.899
2021-01-16 | 9:09 | 49.9
2021-01-16 | 9:09 | 49.9
2021-01-16 | 9:09 | 49.9
2021-01-16 | 9:09 | 49.899
2021-01-16 | 9:09 | 49.9
2021-01-16 | 9:09 | 49.898
2021-01-16 | 9:09 | 49.899
2021-01-16 | 9:09 | 49.9
2021-01-16 | 9:09 | 49.902
2021-01-16 | 9:09 | 49.903
2021-01-16 | 9:09 | 49.906
2021-01-16 | 9:09 | 49.909
2021-01-16 | 9:09 | 49.91
2021-01-16 | 9:09 | 49.913
2021-01-16 | 9:09 | 49.915
2021-01-16 | 9:09 | 49.917
2021-01-16 | 9:09 | 49.917
2021-01-16 | 9:09 | 49.916
2021-01-16 | 9:09 | 49.912
2021-01-16 | 9:09 | 49.912
2021-01-16 | 9:09 | 49.912
2021-01-16 | 9:09 | 49.911
2021-01-16 | 9:09 | 49.908
2021-01-16 | 9:09 | 49.904
2021-01-16 | 9:09 | 49.902
2021-01-16 | 9:09 | 49.903
2021-01-16 | 9:09 | 49.907
2021-01-16 | 9:10 | 49.908
2021-01-16 | 9:10 | 49.907
2021-01-16 | 9:10 | 49.908
2021-01-16 | 9:10 | 49.91
2021-01-16 | 9:10 | 49.91
2021-01-16 | 9:10 | 49.91
2021-01-16 | 9:10 | 49.909
2021-01-16 | 9:10 | 49.909
2021-01-16 | 9:10 | 49.909
2021-01-16 | 9:10 | 49.912
2021-01-16 | 9:10 | 49.913
2021-01-16 | 9:10 | 49.917
2021-01-16 | 9:10 | 49.919
2021-01-16 | 9:10 | 49.919
2021-01-16 | 9:10 | 49.919
2021-01-16 | 9:10 | 49.916
2021-01-16 | 9:10 | 49.914
2021-01-16 | 9:10 | 49.913
2021-01-16 | 9:10 | 49.912
2021-01-16 | 9:10 | 49.913
2021-01-16 | 9:10 | 49.914
2021-01-16 | 9:10 | 49.913
2021-01-16 | 9:10 | 49.913
2021-01-16 | 9:10 | 49.912
2021-01-16 | 9:10 | 49.914
2021-01-16 | 9:10 | 49.916
2021-01-16 | 9:10 | 49.92
2021-01-16 | 9:10 | 49.921
2021-01-16 | 9:10 | 49.921
2021-01-16 | 9:10 | 49.923
2021-01-16 | 9:10 | 49.922
2021-01-16 | 9:10 | 49.921
2021-01-16 | 9:10 | 49.919
2021-01-16 | 9:10 | 49.918
2021-01-16 | 9:10 | 49.921
2021-01-16 | 9:10 | 49.922
2021-01-16 | 9:10 | 49.923
2021-01-16 | 9:10 | 49.923
2021-01-16 | 9:10 | 49.924
2021-01-16 | 9:10 | 49.924
2021-01-16 | 9:10 | 49.924
2021-01-16 | 9:10 | 49.924
2021-01-16 | 9:10 | 49.924
2021-01-16 | 9:10 | 49.924
2021-01-16 | 9:10 | 49.924
2021-01-16 | 9:10 | 49.927
2021-01-16 | 9:10 | 49.928
2021-01-16 | 9:10 | 49.929
2021-01-16 | 9:10 | 49.928
2021-01-16 | 9:10 | 49.93
2021-01-16 | 9:10 | 49.932
2021-01-16 | 9:10 | 49.931
2021-01-16 | 9:10 | 49.932
2021-01-16 | 9:10 | 49.932
2021-01-16 | 9:10 | 49.933
2021-01-16 | 9:10 | 49.934
2021-01-16 | 9:10 | 49.936
2021-01-16 | 9:10 | 49.936
2021-01-16 | 9:10 | 49.938
2021-01-16 | 9:10 | 49.939
2021-01-16 | 9:10 | 49.938
2021-01-16 | 9:11 | 49.939
2021-01-16 | 9:11 | 49.937
2021-01-16 | 9:11 | 49.939
2021-01-16 | 9:11 | 49.939
2021-01-16 | 9:11 | 49.941
2021-01-16 | 9:11 | 49.94
2021-01-16 | 9:11 | 49.939
2021-01-16 | 9:11 | 49.938
2021-01-16 | 9:11 | 49.935
2021-01-16 | 9:11 | 49.936
2021-01-16 | 9:11 | 49.936
2021-01-16 | 9:11 | 49.938
2021-01-16 | 9:11 | 49.938
2021-01-16 | 9:11 | 49.941
2021-01-16 | 9:11 | 49.941
2021-01-16 | 9:11 | 49.941
2021-01-16 | 9:11 | 49.94
2021-01-16 | 9:11 | 49.94
2021-01-16 | 9:11 | 49.942
2021-01-16 | 9:11 | 49.943
2021-01-16 | 9:11 | 49.944
2021-01-16 | 9:11 | 49.943
2021-01-16 | 9:11 | 49.942
2021-01-16 | 9:11 | 49.938
2021-01-16 | 9:11 | 49.934
2021-01-16 | 9:11 | 49.932
2021-01-16 | 9:11 | 49.929
2021-01-16 | 9:11 | 49.928
2021-01-16 | 9:11 | 49.927
2021-01-16 | 9:11 | 49.928
2021-01-16 | 9:11 | 49.927
2021-01-16 | 9:11 | 49.927
2021-01-16 | 9:11 | 49.929
2021-01-16 | 9:11 | 49.931
2021-01-16 | 9:11 | 49.931
2021-01-16 | 9:11 | 49.93
2021-01-16 | 9:11 | 49.928
2021-01-16 | 9:11 | 49.929
2021-01-16 | 9:11 | 49.929
2021-01-16 | 9:11 | 49.93
2021-01-16 | 9:11 | 49.931
2021-01-16 | 9:11 | 49.931
2021-01-16 | 9:11 | 49.932
2021-01-16 | 9:11 | 49.934
2021-01-16 | 9:11 | 49.935
2021-01-16 | 9:11 | 49.936
2021-01-16 | 9:11 | 49.937
2021-01-16 | 9:11 | 49.937
2021-01-16 | 9:11 | 49.939
2021-01-16 | 9:11 | 49.939
2021-01-16 | 9:11 | 49.939
2021-01-16 | 9:11 | 49.94
2021-01-16 | 9:11 | 49.942
2021-01-16 | 9:11 | 49.945
2021-01-16 | 9:11 | 49.948
2021-01-16 | 9:11 | 49.948
2021-01-16 | 9:11 | 49.947
2021-01-16 | 9:11 | 49.944
2021-01-16 | 9:11 | 49.942
2021-01-16 | 9:12 | 49.941
2021-01-16 | 9:12 | 49.94
2021-01-16 | 9:12 | 49.939
2021-01-16 | 9:12 | 49.94
2021-01-16 | 9:12 | 49.941
2021-01-16 | 9:12 | 49.944
2021-01-16 | 9:12 | 49.945
2021-01-16 | 9:12 | 49.948
2021-01-16 | 9:12 | 49.95
2021-01-16 | 9:12 | 49.953
2021-01-16 | 9:12 | 49.954
2021-01-16 | 9:12 | 49.956
2021-01-16 | 9:12 | 49.958
2021-01-16 | 9:12 | 49.959
2021-01-16 | 9:12 | 49.955
2021-01-16 | 9:12 | 49.952
2021-01-16 | 9:12 | 49.948
2021-01-16 | 9:12 | 49.945
2021-01-16 | 9:12 | 49.942
2021-01-16 | 9:12 | 49.937
2021-01-16 | 9:12 | 49.934
2021-01-16 | 9:12 | 49.932
2021-01-16 | 9:12 | 49.93
2021-01-16 | 9:12 | 49.929
2021-01-16 | 9:12 | 49.93
2021-01-16 | 9:12 | 49.928
2021-01-16 | 9:12 | 49.928
2021-01-16 | 9:12 | 49.926
2021-01-16 | 9:12 | 49.928
2021-01-16 | 9:12 | 49.93
2021-01-16 | 9:12 | 49.933
2021-01-16 | 9:12 | 49.933
2021-01-16 | 9:12 | 49.932
2021-01-16 | 9:12 | 49.931
2021-01-16 | 9:12 | 49.93
2021-01-16 | 9:12 | 49.93
2021-01-16 | 9:12 | 49.929
2021-01-16 | 9:12 | 49.929
2021-01-16 | 9:12 | 49.931
2021-01-16 | 9:12 | 49.934
2021-01-16 | 9:12 | 49.939
2021-01-16 | 9:12 | 49.944
2021-01-16 | 9:12 | 49.946
2021-01-16 | 9:12 | 49.949
2021-01-16 | 9:12 | 49.949
2021-01-16 | 9:12 | 49.948
2021-01-16 | 9:12 | 49.946
2021-01-16 | 9:12 | 49.944
2021-01-16 | 9:12 | 49.94
2021-01-16 | 9:12 | 49.939
2021-01-16 | 9:12 | 49.939
2021-01-16 | 9:12 | 49.938
2021-01-16 | 9:12 | 49.938
2021-01-16 | 9:12 | 49.94
2021-01-16 | 9:12 | 49.94
2021-01-16 | 9:12 | 49.941
2021-01-16 | 9:12 | 49.942
2021-01-16 | 9:12 | 49.943
2021-01-16 | 9:12 | 49.945
2021-01-16 | 9:12 | 49.945
2021-01-16 | 9:12 | 49.943
2021-01-16 | 9:13 | 49.943
2021-01-16 | 9:13 | 49.943
2021-01-16 | 9:13 | 49.943
2021-01-16 | 9:13 | 49.943
2021-01-16 | 9:13 | 49.941
2021-01-16 | 9:13 | 49.94
2021-01-16 | 9:13 | 49.939
2021-01-16 | 9:13 | 49.939
2021-01-16 | 9:13 | 49.938
2021-01-16 | 9:13 | 49.936
2021-01-16 | 9:13 | 49.934
2021-01-16 | 9:13 | 49.932
2021-01-16 | 9:13 | 49.932
2021-01-16 | 9:13 | 49.932
2021-01-16 | 9:13 | 49.934
2021-01-16 | 9:13 | 49.937
2021-01-16 | 9:13 | 49.936
2021-01-16 | 9:13 | 49.939
2021-01-16 | 9:13 | 49.944
2021-01-16 | 9:13 | 49.948
2021-01-16 | 9:13 | 49.949
2021-01-16 | 9:13 | 49.951
2021-01-16 | 9:13 | 49.952
2021-01-16 | 9:13 | 49.952
2021-01-16 | 9:13 | 49.954
2021-01-16 | 9:13 | 49.954
2021-01-16 | 9:13 | 49.953
2021-01-16 | 9:13 | 49.955
2021-01-16 | 9:13 | 49.954
2021-01-16 | 9:13 | 49.953
2021-01-16 | 9:13 | 49.949
2021-01-16 | 9:13 | 49.947
2021-01-16 | 9:13 | 49.945
2021-01-16 | 9:13 | 49.943
2021-01-16 | 9:13 | 49.938
2021-01-16 | 9:13 | 49.937
2021-01-16 | 9:13 | 49.936
2021-01-16 | 9:13 | 49.937
2021-01-16 | 9:13 | 49.936
2021-01-16 | 9:13 | 49.934
2021-01-16 | 9:13 | 49.932
2021-01-16 | 9:13 | 49.93
2021-01-16 | 9:13 | 49.931
2021-01-16 | 9:13 | 49.93
2021-01-16 | 9:13 | 49.928
2021-01-16 | 9:13 | 49.922
2021-01-16 | 9:13 | 49.921
2021-01-16 | 9:13 | 49.918
2021-01-16 | 9:13 | 49.916
2021-01-16 | 9:13 | 49.915
2021-01-16 | 9:13 | 49.916
2021-01-16 | 9:13 | 49.914
2021-01-16 | 9:13 | 49.917
2021-01-16 | 9:13 | 49.918
2021-01-16 | 9:13 | 49.92
2021-01-16 | 9:13 | 49.92
2021-01-16 | 9:13 | 49.92
2021-01-16 | 9:13 | 49.922
2021-01-16 | 9:13 | 49.923
2021-01-16 | 9:14 | 49.924
2021-01-16 | 9:14 | 49.924
2021-01-16 | 9:14 | 49.923
2021-01-16 | 9:14 | 49.925
2021-01-16 | 9:14 | 49.926
2021-01-16 | 9:14 | 49.925
2021-01-16 | 9:14 | 49.924
2021-01-16 | 9:14 | 49.925
2021-01-16 | 9:14 | 49.926
2021-01-16 | 9:14 | 49.928
2021-01-16 | 9:14 | 49.929
2021-01-16 | 9:14 | 49.933
2021-01-16 | 9:14 | 49.937
2021-01-16 | 9:14 | 49.941
2021-01-16 | 9:14 | 49.944
2021-01-16 | 9:14 | 49.944
2021-01-16 | 9:14 | 49.94
2021-01-16 | 9:14 | 49.938
2021-01-16 | 9:14 | 49.938
2021-01-16 | 9:14 | 49.937
2021-01-16 | 9:14 | 49.939
2021-01-16 | 9:14 | 49.94
2021-01-16 | 9:14 | 49.936
2021-01-16 | 9:14 | 49.932
2021-01-16 | 9:14 | 49.93
2021-01-16 | 9:14 | 49.926
2021-01-16 | 9:14 | 49.926
2021-01-16 | 9:14 | 49.924
2021-01-16 | 9:14 | 49.923
2021-01-16 | 9:14 | 49.925
2021-01-16 | 9:14 | 49.927
2021-01-16 | 9:14 | 49.926
2021-01-16 | 9:14 | 49.925
2021-01-16 | 9:14 | 49.926
2021-01-16 | 9:14 | 49.922
2021-01-16 | 9:14 | 49.921
2021-01-16 | 9:14 | 49.92
2021-01-16 | 9:14 | 49.923
2021-01-16 | 9:14 | 49.921
2021-01-16 | 9:14 | 49.923
2021-01-16 | 9:14 | 49.92
2021-01-16 | 9:14 | 49.918
2021-01-16 | 9:14 | 49.916
2021-01-16 | 9:14 | 49.919
2021-01-16 | 9:14 | 49.92
2021-01-16 | 9:14 | 49.921
2021-01-16 | 9:14 | 49.922
2021-01-16 | 9:14 | 49.925
2021-01-16 | 9:14 | 49.927
2021-01-16 | 9:14 | 49.928
2021-01-16 | 9:14 | 49.93
2021-01-16 | 9:14 | 49.928
2021-01-16 | 9:14 | 49.929
2021-01-16 | 9:14 | 49.931
2021-01-16 | 9:14 | 49.935
2021-01-16 | 9:14 | 49.936
2021-01-16 | 9:14 | 49.934
2021-01-16 | 9:14 | 49.934
2021-01-16 | 9:14 | 49.93
2021-01-16 | 9:14 | 49.931
2021-01-16 | 9:14 | 49.928
2021-01-16 | 9:15 | 49.927
2021-01-16 | 9:15 | 49.924
2021-01-16 | 9:15 | 49.922
2021-01-16 | 9:15 | 49.92
2021-01-16 | 9:15 | 49.915
2021-01-16 | 9:15 | 49.916
2021-01-16 | 9:15 | 49.916
2021-01-16 | 9:15 | 49.917
2021-01-16 | 9:15 | 49.916
2021-01-16 | 9:15 | 49.917
2021-01-16 | 9:15 | 49.918
2021-01-16 | 9:15 | 49.918
2021-01-16 | 9:15 | 49.918
2021-01-16 | 9:15 | 49.92
2021-01-16 | 9:15 | 49.92
2021-01-16 | 9:15 | 49.92
2021-01-16 | 9:15 | 49.922
2021-01-16 | 9:15 | 49.923
2021-01-16 | 9:15 | 49.925
2021-01-16 | 9:15 | 49.927
2021-01-16 | 9:15 | 49.93
2021-01-16 | 9:15 | 49.929
2021-01-16 | 9:15 | 49.93
2021-01-16 | 9:15 | 49.932
2021-01-16 | 9:15 | 49.935
2021-01-16 | 9:15 | 49.938
2021-01-16 | 9:15 | 49.941
2021-01-16 | 9:15 | 49.941
2021-01-16 | 9:15 | 49.939
2021-01-16 | 9:15 | 49.938
2021-01-16 | 9:15 | 49.933
2021-01-16 | 9:15 | 49.928
2021-01-16 | 9:15 | 49.926
2021-01-16 | 9:15 | 49.925
2021-01-16 | 9:15 | 49.923
2021-01-16 | 9:15 | 49.923
2021-01-16 | 9:15 | 49.922
2021-01-16 | 9:15 | 49.919
2021-01-16 | 9:15 | 49.917
2021-01-16 | 9:15 | 49.917
2021-01-16 | 9:15 | 49.916
2021-01-16 | 9:15 | 49.915
2021-01-16 | 9:15 | 49.919
2021-01-16 | 9:15 | 49.923
2021-01-16 | 9:15 | 49.925
2021-01-16 | 9:15 | 49.927
2021-01-16 | 9:15 | 49.927
2021-01-16 | 9:15 | 49.926
2021-01-16 | 9:15 | 49.928
2021-01-16 | 9:15 | 49.928
2021-01-16 | 9:15 | 49.928
2021-01-16 | 9:15 | 49.929
2021-01-16 | 9:15 | 49.929
2021-01-16 | 9:15 | 49.93
2021-01-16 | 9:15 | 49.933
2021-01-16 | 9:15 | 49.931
2021-01-16 | 9:15 | 49.93
2021-01-16 | 9:15 | 49.926
2021-01-16 | 9:15 | 49.924
2021-01-16 | 9:16 | 49.922
2021-01-16 | 9:16 | 49.925
2021-01-16 | 9:16 | 49.925
2021-01-16 | 9:16 | 49.926
2021-01-16 | 9:16 | 49.922
2021-01-16 | 9:16 | 49.921
2021-01-16 | 9:16 | 49.92
2021-01-16 | 9:16 | 49.92
2021-01-16 | 9:16 | 49.919
2021-01-16 | 9:16 | 49.918
2021-01-16 | 9:16 | 49.918
2021-01-16 | 9:16 | 49.919
2021-01-16 | 9:16 | 49.921
2021-01-16 | 9:16 | 49.922
2021-01-16 | 9:16 | 49.923
2021-01-16 | 9:16 | 49.921
2021-01-16 | 9:16 | 49.922
2021-01-16 | 9:16 | 49.92
2021-01-16 | 9:16 | 49.919
2021-01-16 | 9:16 | 49.918
2021-01-16 | 9:16 | 49.915
2021-01-16 | 9:16 | 49.914
2021-01-16 | 9:16 | 49.914
2021-01-16 | 9:16 | 49.914
2021-01-16 | 9:16 | 49.915
2021-01-16 | 9:16 | 49.915
2021-01-16 | 9:16 | 49.914
2021-01-16 | 9:16 | 49.911
2021-01-16 | 9:16 | 49.909
2021-01-16 | 9:16 | 49.907
2021-01-16 | 9:16 | 49.909
2021-01-16 | 9:16 | 49.909
2021-01-16 | 9:16 | 49.908
2021-01-16 | 9:16 | 49.909
2021-01-16 | 9:16 | 49.91
2021-01-16 | 9:16 | 49.911
2021-01-16 | 9:16 | 49.909
2021-01-16 | 9:16 | 49.908
2021-01-16 | 9:16 | 49.906
2021-01-16 | 9:16 | 49.907
2021-01-16 | 9:16 | 49.906
2021-01-16 | 9:16 | 49.903
2021-01-16 | 9:16 | 49.901
2021-01-16 | 9:16 | 49.899
2021-01-16 | 9:16 | 49.899
2021-01-16 | 9:16 | 49.899
2021-01-16 | 9:16 | 49.901
2021-01-16 | 9:16 | 49.9
2021-01-16 | 9:16 | 49.898
2021-01-16 | 9:16 | 49.898
2021-01-16 | 9:16 | 49.897
2021-01-16 | 9:16 | 49.897
2021-01-16 | 9:16 | 49.899
2021-01-16 | 9:16 | 49.9
2021-01-16 | 9:16 | 49.898
2021-01-16 | 9:16 | 49.899
2021-01-16 | 9:16 | 49.9
2021-01-16 | 9:16 | 49.898
2021-01-16 | 9:16 | 49.896
2021-01-16 | 9:16 | 49.896
2021-01-16 | 9:16 | 49.893
2021-01-16 | 9:17 | 49.891
2021-01-16 | 9:17 | 49.891
2021-01-16 | 9:17 | 49.888
2021-01-16 | 9:17 | 49.888
2021-01-16 | 9:17 | 49.886
2021-01-16 | 9:17 | 49.886
2021-01-16 | 9:17 | 49.885
2021-01-16 | 9:17 | 49.885
2021-01-16 | 9:17 | 49.887
2021-01-16 | 9:17 | 49.89
2021-01-16 | 9:17 | 49.892
2021-01-16 | 9:17 | 49.891
2021-01-16 | 9:17 | 49.892
2021-01-16 | 9:17 | 49.892
2021-01-16 | 9:17 | 49.892
2021-01-16 | 9:17 | 49.89
2021-01-16 | 9:17 | 49.89
2021-01-16 | 9:17 | 49.891
2021-01-16 | 9:17 | 49.891
2021-01-16 | 9:17 | 49.893
2021-01-16 | 9:17 | 49.895
2021-01-16 | 9:17 | 49.897
2021-01-16 | 9:17 | 49.899
2021-01-16 | 9:17 | 49.901
2021-01-16 | 9:17 | 49.901
2021-01-16 | 9:17 | 49.891
2021-01-16 | 9:17 | 49.896
2021-01-16 | 9:17 | 49.896
2021-01-16 | 9:17 | 49.894
2021-01-16 | 9:17 | 49.89
2021-01-16 | 9:17 | 49.888
2021-01-16 | 9:17 | 49.888
2021-01-16 | 9:17 | 49.889
2021-01-16 | 9:17 | 49.892
2021-01-16 | 9:17 | 49.893
2021-01-16 | 9:17 | 49.894
2021-01-16 | 9:17 | 49.892
2021-01-16 | 9:17 | 49.893
2021-01-16 | 9:17 | 49.894
2021-01-16 | 9:17 | 49.893
2021-01-16 | 9:17 | 49.894
2021-01-16 | 9:17 | 49.894
2021-01-16 | 9:17 | 49.895
2021-01-16 | 9:17 | 49.895
2021-01-16 | 9:17 | 49.896
2021-01-16 | 9:17 | 49.894
2021-01-16 | 9:17 | 49.895
2021-01-16 | 9:17 | 49.893
2021-01-16 | 9:17 | 49.893
2021-01-16 | 9:17 | 49.893
2021-01-16 | 9:17 | 49.894
2021-01-16 | 9:17 | 49.894
2021-01-16 | 9:17 | 49.896
2021-01-16 | 9:17 | 49.898
2021-01-16 | 9:17 | 49.9
2021-01-16 | 9:17 | 49.902
2021-01-16 | 9:17 | 49.903
2021-01-16 | 9:17 | 49.905
2021-01-16 | 9:17 | 49.905
2021-01-16 | 9:17 | 49.907
2021-01-16 | 9:18 | 49.909
2021-01-16 | 9:18 | 49.909
2021-01-16 | 9:18 | 49.909
2021-01-16 | 9:18 | 49.91
2021-01-16 | 9:18 | 49.907
2021-01-16 | 9:18 | 49.906
2021-01-16 | 9:18 | 49.907
2021-01-16 | 9:18 | 49.906
2021-01-16 | 9:18 | 49.903
2021-01-16 | 9:18 | 49.902
2021-01-16 | 9:18 | 49.901
2021-01-16 | 9:18 | 49.902
2021-01-16 | 9:18 | 49.905
2021-01-16 | 9:18 | 49.909
2021-01-16 | 9:18 | 49.912
2021-01-16 | 9:18 | 49.915
2021-01-16 | 9:18 | 49.918
2021-01-16 | 9:18 | 49.918
2021-01-16 | 9:18 | 49.919
2021-01-16 | 9:18 | 49.917
2021-01-16 | 9:18 | 49.916
2021-01-16 | 9:18 | 49.915
2021-01-16 | 9:18 | 49.916
2021-01-16 | 9:18 | 49.916
2021-01-16 | 9:18 | 49.913
2021-01-16 | 9:18 | 49.911
2021-01-16 | 9:18 | 49.909
2021-01-16 | 9:18 | 49.906
2021-01-16 | 9:18 | 49.906
2021-01-16 | 9:18 | 49.906
2021-01-16 | 9:18 | 49.904
2021-01-16 | 9:18 | 49.904
2021-01-16 | 9:18 | 49.905
2021-01-16 | 9:18 | 49.908
2021-01-16 | 9:18 | 49.908
2021-01-16 | 9:18 | 49.909
2021-01-16 | 9:18 | 49.91
2021-01-16 | 9:18 | 49.91
2021-01-16 | 9:18 | 49.911
2021-01-16 | 9:18 | 49.911
2021-01-16 | 9:18 | 49.91
2021-01-16 | 9:18 | 49.911
2021-01-16 | 9:18 | 49.911
2021-01-16 | 9:18 | 49.912
2021-01-16 | 9:18 | 49.912
2021-01-16 | 9:18 | 49.913
2021-01-16 | 9:18 | 49.913
2021-01-16 | 9:18 | 49.914
2021-01-16 | 9:18 | 49.917
2021-01-16 | 9:18 | 49.919
2021-01-16 | 9:18 | 49.92
2021-01-16 | 9:18 | 49.92
2021-01-16 | 9:18 | 49.921
2021-01-16 | 9:18 | 49.921
2021-01-16 | 9:18 | 49.923
2021-01-16 | 9:18 | 49.924
2021-01-16 | 9:18 | 49.926
2021-01-16 | 9:18 | 49.924
2021-01-16 | 9:18 | 49.922
2021-01-16 | 9:18 | 49.921
2021-01-16 | 9:19 | 49.92
2021-01-16 | 9:19 | 49.921
2021-01-16 | 9:19 | 49.923
2021-01-16 | 9:19 | 49.924
2021-01-16 | 9:19 | 49.923
2021-01-16 | 9:19 | 49.92
2021-01-16 | 9:19 | 49.92
2021-01-16 | 9:19 | 49.92
2021-01-16 | 9:19 | 49.918
2021-01-16 | 9:19 | 49.916
2021-01-16 | 9:19 | 49.917
2021-01-16 | 9:19 | 49.921
2021-01-16 | 9:19 | 49.924
2021-01-16 | 9:19 | 49.927
2021-01-16 | 9:19 | 49.927
2021-01-16 | 9:19 | 49.927
2021-01-16 | 9:19 | 49.926
2021-01-16 | 9:19 | 49.924
2021-01-16 | 9:19 | 49.924
2021-01-16 | 9:19 | 49.924
2021-01-16 | 9:19 | 49.921
2021-01-16 | 9:19 | 49.919
2021-01-16 | 9:19 | 49.919
2021-01-16 | 9:19 | 49.92
2021-01-16 | 9:19 | 49.921
2021-01-16 | 9:19 | 49.924
2021-01-16 | 9:19 | 49.923
2021-01-16 | 9:19 | 49.924
2021-01-16 | 9:19 | 49.925
2021-01-16 | 9:19 | 49.924
2021-01-16 | 9:19 | 49.923
2021-01-16 | 9:19 | 49.923
2021-01-16 | 9:19 | 49.923
2021-01-16 | 9:19 | 49.923
2021-01-16 | 9:19 | 49.921
2021-01-16 | 9:19 | 49.918
2021-01-16 | 9:19 | 49.916
2021-01-16 | 9:19 | 49.917
2021-01-16 | 9:19 | 49.919
2021-01-16 | 9:19 | 49.919
2021-01-16 | 9:19 | 49.918
2021-01-16 | 9:19 | 49.918
2021-01-16 | 9:19 | 49.92
2021-01-16 | 9:19 | 49.924
2021-01-16 | 9:19 | 49.926
2021-01-16 | 9:19 | 49.925
2021-01-16 | 9:19 | 49.927
2021-01-16 | 9:19 | 49.928
2021-01-16 | 9:19 | 49.928
2021-01-16 | 9:19 | 49.932
2021-01-16 | 9:19 | 49.935
2021-01-16 | 9:19 | 49.937
2021-01-16 | 9:19 | 49.938
2021-01-16 | 9:19 | 49.939
2021-01-16 | 9:19 | 49.937
2021-01-16 | 9:19 | 49.939
2021-01-16 | 9:19 | 49.94
2021-01-16 | 9:19 | 49.941
2021-01-16 | 9:19 | 49.941
2021-01-16 | 9:19 | 49.943
2021-01-16 | 9:20 | 49.941
2021-01-16 | 9:20 | 49.938
2021-01-16 | 9:20 | 49.938
2021-01-16 | 9:20 | 49.936
2021-01-16 | 9:20 | 49.936
2021-01-16 | 9:20 | 49.936
2021-01-16 | 9:20 | 49.936
2021-01-16 | 9:20 | 49.937
2021-01-16 | 9:20 | 49.937
2021-01-16 | 9:20 | 49.936
2021-01-16 | 9:20 | 49.936
2021-01-16 | 9:20 | 49.938
2021-01-16 | 9:20 | 49.938
2021-01-16 | 9:20 | 49.937
2021-01-16 | 9:20 | 49.938
2021-01-16 | 9:20 | 49.937
2021-01-16 | 9:20 | 49.934
2021-01-16 | 9:20 | 49.935
2021-01-16 | 9:20 | 49.933
2021-01-16 | 9:20 | 49.934
2021-01-16 | 9:20 | 49.936
2021-01-16 | 9:20 | 49.934
2021-01-16 | 9:20 | 49.934
2021-01-16 | 9:20 | 49.936
2021-01-16 | 9:20 | 49.939
2021-01-16 | 9:20 | 49.939
2021-01-16 | 9:20 | 49.939
2021-01-16 | 9:20 | 49.939
2021-01-16 | 9:20 | 49.938
2021-01-16 | 9:20 | 49.938
2021-01-16 | 9:20 | 49.936
2021-01-16 | 9:20 | 49.932
2021-01-16 | 9:20 | 49.927
2021-01-16 | 9:20 | 49.926
2021-01-16 | 9:20 | 49.926
2021-01-16 | 9:20 | 49.929
2021-01-16 | 9:20 | 49.933
2021-01-16 | 9:20 | 49.934
2021-01-16 | 9:20 | 49.933
2021-01-16 | 9:20 | 49.933
2021-01-16 | 9:20 | 49.932
2021-01-16 | 9:20 | 49.932
2021-01-16 | 9:20 | 49.931
2021-01-16 | 9:20 | 49.93
2021-01-16 | 9:20 | 49.93
2021-01-16 | 9:20 | 49.93
2021-01-16 | 9:20 | 49.933
2021-01-16 | 9:20 | 49.934
2021-01-16 | 9:20 | 49.937
2021-01-16 | 9:20 | 49.939
2021-01-16 | 9:20 | 49.94
2021-01-16 | 9:20 | 49.943
2021-01-16 | 9:20 | 49.942
2021-01-16 | 9:20 | 49.944
2021-01-16 | 9:20 | 49.943
2021-01-16 | 9:20 | 49.942
2021-01-16 | 9:20 | 49.942
2021-01-16 | 9:20 | 49.941
2021-01-16 | 9:20 | 49.94
2021-01-16 | 9:20 | 49.942
2021-01-16 | 9:21 | 49.943
2021-01-16 | 9:21 | 49.943
2021-01-16 | 9:21 | 49.943
2021-01-16 | 9:21 | 49.942
2021-01-16 | 9:21 | 49.943
2021-01-16 | 9:21 | 49.942
2021-01-16 | 9:21 | 49.942
2021-01-16 | 9:21 | 49.944
2021-01-16 | 9:21 | 49.947
2021-01-16 | 9:21 | 49.95
2021-01-16 | 9:21 | 49.95
2021-01-16 | 9:21 | 49.951
2021-01-16 | 9:21 | 49.952
2021-01-16 | 9:21 | 49.952
2021-01-16 | 9:21 | 49.952
2021-01-16 | 9:21 | 49.956
2021-01-16 | 9:21 | 49.959
2021-01-16 | 9:21 | 49.962
2021-01-16 | 9:21 | 49.962
2021-01-16 | 9:21 | 49.961
2021-01-16 | 9:21 | 49.956
2021-01-16 | 9:21 | 49.953
2021-01-16 | 9:21 | 49.95
2021-01-16 | 9:21 | 49.947
2021-01-16 | 9:21 | 49.944
2021-01-16 | 9:21 | 49.942
2021-01-16 | 9:21 | 49.942
2021-01-16 | 9:21 | 49.939
2021-01-16 | 9:21 | 49.934
2021-01-16 | 9:21 | 49.932
2021-01-16 | 9:21 | 49.929
2021-01-16 | 9:21 | 49.928
2021-01-16 | 9:21 | 49.929
2021-01-16 | 9:21 | 49.933
2021-01-16 | 9:21 | 49.933
2021-01-16 | 9:21 | 49.932
2021-01-16 | 9:21 | 49.933
2021-01-16 | 9:21 | 49.933
2021-01-16 | 9:21 | 49.933
2021-01-16 | 9:21 | 49.932
2021-01-16 | 9:21 | 49.934
2021-01-16 | 9:21 | 49.935
2021-01-16 | 9:21 | 49.935
2021-01-16 | 9:21 | 49.935
2021-01-16 | 9:21 | 49.938
2021-01-16 | 9:21 | 49.94
2021-01-16 | 9:21 | 49.945
2021-01-16 | 9:21 | 49.946
2021-01-16 | 9:21 | 49.949
2021-01-16 | 9:21 | 49.949
2021-01-16 | 9:21 | 49.95
2021-01-16 | 9:21 | 49.948
2021-01-16 | 9:21 | 49.95
2021-01-16 | 9:21 | 49.949
2021-01-16 | 9:21 | 49.948
2021-01-16 | 9:21 | 49.948
2021-01-16 | 9:21 | 49.95
2021-01-16 | 9:21 | 49.951
2021-01-16 | 9:21 | 49.954
2021-01-16 | 9:21 | 49.954
2021-01-16 | 9:22 | 49.955
2021-01-16 | 9:22 | 49.955
2021-01-16 | 9:22 | 49.955
2021-01-16 | 9:22 | 49.956
2021-01-16 | 9:22 | 49.956
2021-01-16 | 9:22 | 49.957
2021-01-16 | 9:22 | 49.96
2021-01-16 | 9:22 | 49.961
2021-01-16 | 9:22 | 49.961
2021-01-16 | 9:22 | 49.964
2021-01-16 | 9:22 | 49.966
2021-01-16 | 9:22 | 49.965
2021-01-16 | 9:22 | 49.966
2021-01-16 | 9:22 | 49.963
2021-01-16 | 9:22 | 49.962
2021-01-16 | 9:22 | 49.961
2021-01-16 | 9:22 | 49.96
2021-01-16 | 9:22 | 49.959
2021-01-16 | 9:22 | 49.958
2021-01-16 | 9:22 | 49.956
2021-01-16 | 9:22 | 49.955
2021-01-16 | 9:22 | 49.955
2021-01-16 | 9:22 | 49.957
2021-01-16 | 9:22 | 49.959
2021-01-16 | 9:22 | 49.962
2021-01-16 | 9:22 | 49.961
2021-01-16 | 9:22 | 49.962
2021-01-16 | 9:22 | 49.963
2021-01-16 | 9:22 | 49.963
2021-01-16 | 9:22 | 49.965
2021-01-16 | 9:22 | 49.964
2021-01-16 | 9:22 | 49.962
2021-01-16 | 9:22 | 49.959
2021-01-16 | 9:22 | 49.954
2021-01-16 | 9:22 | 49.952
2021-01-16 | 9:22 | 49.948
2021-01-16 | 9:22 | 49.945
2021-01-16 | 9:22 | 49.942
2021-01-16 | 9:22 | 49.942
2021-01-16 | 9:22 | 49.94
2021-01-16 | 9:22 | 49.938
2021-01-16 | 9:22 | 49.937
2021-01-16 | 9:22 | 49.936
2021-01-16 | 9:22 | 49.933
2021-01-16 | 9:22 | 49.935
2021-01-16 | 9:22 | 49.936
2021-01-16 | 9:22 | 49.94
2021-01-16 | 9:22 | 49.943
2021-01-16 | 9:22 | 49.944
2021-01-16 | 9:22 | 49.944
2021-01-16 | 9:22 | 49.947
2021-01-16 | 9:22 | 49.951
2021-01-16 | 9:22 | 49.952
2021-01-16 | 9:22 | 49.951
2021-01-16 | 9:22 | 49.952
2021-01-16 | 9:22 | 49.951
2021-01-16 | 9:22 | 49.951
2021-01-16 | 9:22 | 49.952
2021-01-16 | 9:22 | 49.953
2021-01-16 | 9:22 | 49.955
2021-01-16 | 9:23 | 49.957
2021-01-16 | 9:23 | 49.96
2021-01-16 | 9:23 | 49.96
2021-01-16 | 9:23 | 49.961
2021-01-16 | 9:23 | 49.963
2021-01-16 | 9:23 | 49.962
2021-01-16 | 9:23 | 49.963
2021-01-16 | 9:23 | 49.96
2021-01-16 | 9:23 | 49.959
2021-01-16 | 9:23 | 49.96
2021-01-16 | 9:23 | 49.958
2021-01-16 | 9:23 | 49.959
2021-01-16 | 9:23 | 49.958
2021-01-16 | 9:23 | 49.958
2021-01-16 | 9:23 | 49.957
2021-01-16 | 9:23 | 49.956
2021-01-16 | 9:23 | 49.953
2021-01-16 | 9:23 | 49.954
2021-01-16 | 9:23 | 49.958
2021-01-16 | 9:23 | 49.96
2021-01-16 | 9:23 | 49.963
2021-01-16 | 9:23 | 49.967
2021-01-16 | 9:23 | 49.966
2021-01-16 | 9:23 | 49.963
2021-01-16 | 9:23 | 49.963
2021-01-16 | 9:23 | 49.96
2021-01-16 | 9:23 | 49.956
2021-01-16 | 9:23 | 49.955
2021-01-16 | 9:23 | 49.955
2021-01-16 | 9:23 | 49.953
2021-01-16 | 9:23 | 49.951
2021-01-16 | 9:23 | 49.95
2021-01-16 | 9:23 | 49.952
2021-01-16 | 9:23 | 49.954
2021-01-16 | 9:23 | 49.957
2021-01-16 | 9:23 | 49.958
2021-01-16 | 9:23 | 49.96
2021-01-16 | 9:23 | 49.959
2021-01-16 | 9:23 | 49.959
2021-01-16 | 9:23 | 49.96
2021-01-16 | 9:23 | 49.96
2021-01-16 | 9:23 | 49.96
2021-01-16 | 9:23 | 49.96
2021-01-16 | 9:23 | 49.96
2021-01-16 | 9:23 | 49.961
2021-01-16 | 9:23 | 49.959
2021-01-16 | 9:23 | 49.96
2021-01-16 | 9:23 | 49.963
2021-01-16 | 9:23 | 49.963
2021-01-16 | 9:23 | 49.962
2021-01-16 | 9:23 | 49.962
2021-01-16 | 9:23 | 49.96
2021-01-16 | 9:23 | 49.96
2021-01-16 | 9:23 | 49.96
2021-01-16 | 9:23 | 49.96
2021-01-16 | 9:23 | 49.959
2021-01-16 | 9:23 | 49.96
2021-01-16 | 9:23 | 49.961
2021-01-16 | 9:23 | 49.962
2021-01-16 | 9:24 | 49.961
2021-01-16 | 9:24 | 49.96
2021-01-16 | 9:24 | 49.961
2021-01-16 | 9:24 | 49.961
2021-01-16 | 9:24 | 49.96
2021-01-16 | 9:24 | 49.961
2021-01-16 | 9:24 | 49.96
2021-01-16 | 9:24 | 49.96
2021-01-16 | 9:24 | 49.961
2021-01-16 | 9:24 | 49.961
2021-01-16 | 9:24 | 49.96
2021-01-16 | 9:24 | 49.959
2021-01-16 | 9:24 | 49.959
2021-01-16 | 9:24 | 49.958
2021-01-16 | 9:24 | 49.959
2021-01-16 | 9:24 | 49.96
2021-01-16 | 9:24 | 49.963
2021-01-16 | 9:24 | 49.965
2021-01-16 | 9:24 | 49.966
2021-01-16 | 9:24 | 49.965
2021-01-16 | 9:24 | 49.965
2021-01-16 | 9:24 | 49.965
2021-01-16 | 9:24 | 49.965
2021-01-16 | 9:24 | 49.965
2021-01-16 | 9:24 | 49.966
2021-01-16 | 9:24 | 49.968
2021-01-16 | 9:24 | 49.967
2021-01-16 | 9:24 | 49.967
2021-01-16 | 9:24 | 49.965
2021-01-16 | 9:24 | 49.963
2021-01-16 | 9:24 | 49.959
2021-01-16 | 9:24 | 49.955
2021-01-16 | 9:24 | 49.951
2021-01-16 | 9:24 | 49.948
2021-01-16 | 9:24 | 49.944
2021-01-16 | 9:24 | 49.941
2021-01-16 | 9:24 | 49.942
2021-01-16 | 9:24 | 49.941
2021-01-16 | 9:24 | 49.943
2021-01-16 | 9:24 | 49.946
2021-01-16 | 9:24 | 49.948
2021-01-16 | 9:24 | 49.948
2021-01-16 | 9:24 | 49.951
2021-01-16 | 9:24 | 49.952
2021-01-16 | 9:24 | 49.951
2021-01-16 | 9:24 | 49.949
2021-01-16 | 9:24 | 49.948
2021-01-16 | 9:24 | 49.945
2021-01-16 | 9:24 | 49.943
2021-01-16 | 9:24 | 49.943
2021-01-16 | 9:24 | 49.943
2021-01-16 | 9:24 | 49.944
2021-01-16 | 9:24 | 49.945
2021-01-16 | 9:24 | 49.945
2021-01-16 | 9:24 | 49.945
2021-01-16 | 9:24 | 49.943
2021-01-16 | 9:24 | 49.944
2021-01-16 | 9:24 | 49.944
2021-01-16 | 9:24 | 49.944
2021-01-16 | 9:24 | 49.943
2021-01-16 | 9:24 | 49.942
2021-01-16 | 9:25 | 49.941
2021-01-16 | 9:25 | 49.939
2021-01-16 | 9:25 | 49.936
2021-01-16 | 9:25 | 49.932
2021-01-16 | 9:25 | 49.93
2021-01-16 | 9:25 | 49.928
2021-01-16 | 9:25 | 49.927
2021-01-16 | 9:25 | 49.925
2021-01-16 | 9:25 | 49.925
2021-01-16 | 9:25 | 49.926
2021-01-16 | 9:25 | 49.924
2021-01-16 | 9:25 | 49.924
2021-01-16 | 9:25 | 49.926
2021-01-16 | 9:25 | 49.929
2021-01-16 | 9:25 | 49.929
2021-01-16 | 9:25 | 49.929
2021-01-16 | 9:25 | 49.928
2021-01-16 | 9:25 | 49.928
2021-01-16 | 9:25 | 49.93
2021-01-16 | 9:25 | 49.931
2021-01-16 | 9:25 | 49.934
2021-01-16 | 9:25 | 49.938
2021-01-16 | 9:25 | 49.94
2021-01-16 | 9:25 | 49.941
2021-01-16 | 9:25 | 49.945
2021-01-16 | 9:25 | 49.949
2021-01-16 | 9:25 | 49.95
2021-01-16 | 9:25 | 49.948
2021-01-16 | 9:25 | 49.947
2021-01-16 | 9:25 | 49.948
2021-01-16 | 9:25 | 49.948
2021-01-16 | 9:25 | 49.946
2021-01-16 | 9:25 | 49.947
2021-01-16 | 9:25 | 49.947
2021-01-16 | 9:25 | 49.949
2021-01-16 | 9:25 | 49.95
2021-01-16 | 9:25 | 49.951
2021-01-16 | 9:25 | 49.95
2021-01-16 | 9:25 | 49.949
2021-01-16 | 9:25 | 49.949
2021-01-16 | 9:25 | 49.948
2021-01-16 | 9:25 | 49.947
2021-01-16 | 9:25 | 49.945
2021-01-16 | 9:25 | 49.945
2021-01-16 | 9:25 | 49.943
2021-01-16 | 9:25 | 49.941
2021-01-16 | 9:25 | 49.941
2021-01-16 | 9:25 | 49.941
2021-01-16 | 9:25 | 49.942
2021-01-16 | 9:25 | 49.945
2021-01-16 | 9:25 | 49.948
2021-01-16 | 9:25 | 49.949
2021-01-16 | 9:25 | 49.95
2021-01-16 | 9:25 | 49.952
2021-01-16 | 9:25 | 49.952
2021-01-16 | 9:25 | 49.954
2021-01-16 | 9:25 | 49.955
2021-01-16 | 9:25 | 49.955
2021-01-16 | 9:25 | 49.953
2021-01-16 | 9:26 | 49.953
2021-01-16 | 9:26 | 49.954
2021-01-16 | 9:26 | 49.957
2021-01-16 | 9:26 | 49.959
2021-01-16 | 9:26 | 49.963
2021-01-16 | 9:26 | 49.964
2021-01-16 | 9:26 | 49.966
2021-01-16 | 9:26 | 49.969
2021-01-16 | 9:26 | 49.969
2021-01-16 | 9:26 | 49.97
2021-01-16 | 9:26 | 49.969
2021-01-16 | 9:26 | 49.967
2021-01-16 | 9:26 | 49.965
2021-01-16 | 9:26 | 49.964
2021-01-16 | 9:26 | 49.962
2021-01-16 | 9:26 | 49.959
2021-01-16 | 9:26 | 49.956
2021-01-16 | 9:26 | 49.953
2021-01-16 | 9:26 | 49.952
2021-01-16 | 9:26 | 49.952
2021-01-16 | 9:26 | 49.952
2021-01-16 | 9:26 | 49.95
2021-01-16 | 9:26 | 49.949
2021-01-16 | 9:26 | 49.948
2021-01-16 | 9:26 | 49.947
2021-01-16 | 9:26 | 49.948
2021-01-16 | 9:26 | 49.951
2021-01-16 | 9:26 | 49.952
2021-01-16 | 9:26 | 49.955
2021-01-16 | 9:26 | 49.957
2021-01-16 | 9:26 | 49.959
2021-01-16 | 9:26 | 49.961
2021-01-16 | 9:26 | 49.963
2021-01-16 | 9:26 | 49.963
2021-01-16 | 9:26 | 49.963
2021-01-16 | 9:26 | 49.965
2021-01-16 | 9:26 | 49.967
2021-01-16 | 9:26 | 49.97
2021-01-16 | 9:26 | 49.972
2021-01-16 | 9:26 | 49.972
2021-01-16 | 9:26 | 49.973
2021-01-16 | 9:26 | 49.973
2021-01-16 | 9:26 | 49.971
2021-01-16 | 9:26 | 49.97
2021-01-16 | 9:26 | 49.968
2021-01-16 | 9:26 | 49.965
2021-01-16 | 9:26 | 49.963
2021-01-16 | 9:26 | 49.959
2021-01-16 | 9:26 | 49.956
2021-01-16 | 9:26 | 49.955
2021-01-16 | 9:26 | 49.953
2021-01-16 | 9:26 | 49.949
2021-01-16 | 9:26 | 49.947
2021-01-16 | 9:26 | 49.945
2021-01-16 | 9:26 | 49.945
2021-01-16 | 9:26 | 49.945
2021-01-16 | 9:26 | 49.948
2021-01-16 | 9:26 | 49.946
2021-01-16 | 9:26 | 49.949
2021-01-16 | 9:26 | 49.948
2021-01-16 | 9:26 | 49.946
2021-01-16 | 9:27 | 49.945
2021-01-16 | 9:27 | 49.942
2021-01-16 | 9:27 | 49.941
2021-01-16 | 9:27 | 49.939
2021-01-16 | 9:27 | 49.941
2021-01-16 | 9:27 | 49.941
2021-01-16 | 9:27 | 49.942
2021-01-16 | 9:27 | 49.943
2021-01-16 | 9:27 | 49.942
2021-01-16 | 9:27 | 49.94
2021-01-16 | 9:27 | 49.937
2021-01-16 | 9:27 | 49.934
2021-01-16 | 9:27 | 49.936
2021-01-16 | 9:27 | 49.938
2021-01-16 | 9:27 | 49.939
2021-01-16 | 9:27 | 49.941
2021-01-16 | 9:27 | 49.944
2021-01-16 | 9:27 | 49.944
2021-01-16 | 9:27 | 49.945
2021-01-16 | 9:27 | 49.942
2021-01-16 | 9:27 | 49.939
2021-01-16 | 9:27 | 49.936
2021-01-16 | 9:27 | 49.935
2021-01-16 | 9:27 | 49.936
2021-01-16 | 9:27 | 49.936
2021-01-16 | 9:27 | 49.936
2021-01-16 | 9:27 | 49.939
2021-01-16 | 9:27 | 49.939
2021-01-16 | 9:27 | 49.939
2021-01-16 | 9:27 | 49.937
2021-01-16 | 9:27 | 49.934
2021-01-16 | 9:27 | 49.933
2021-01-16 | 9:27 | 49.93
2021-01-16 | 9:27 | 49.929
2021-01-16 | 9:27 | 49.929
2021-01-16 | 9:27 | 49.93
2021-01-16 | 9:27 | 49.931
2021-01-16 | 9:27 | 49.93
2021-01-16 | 9:27 | 49.932
2021-01-16 | 9:27 | 49.932
2021-01-16 | 9:27 | 49.933
2021-01-16 | 9:27 | 49.932
2021-01-16 | 9:27 | 49.934
2021-01-16 | 9:27 | 49.935
2021-01-16 | 9:27 | 49.931
2021-01-16 | 9:27 | 49.929
2021-01-16 | 9:27 | 49.929
2021-01-16 | 9:27 | 49.928
2021-01-16 | 9:27 | 49.929
2021-01-16 | 9:27 | 49.927
2021-01-16 | 9:27 | 49.927
2021-01-16 | 9:27 | 49.929
2021-01-16 | 9:27 | 49.931
2021-01-16 | 9:27 | 49.935
2021-01-16 | 9:27 | 49.935
2021-01-16 | 9:27 | 49.934
2021-01-16 | 9:27 | 49.936
2021-01-16 | 9:27 | 49.937
2021-01-16 | 9:27 | 49.939
2021-01-16 | 9:28 | 49.941
2021-01-16 | 9:28 | 49.941
2021-01-16 | 9:28 | 49.941
2021-01-16 | 9:28 | 49.942
2021-01-16 | 9:28 | 49.943
2021-01-16 | 9:28 | 49.945
2021-01-16 | 9:28 | 49.948
2021-01-16 | 9:28 | 49.95
2021-01-16 | 9:28 | 49.951
2021-01-16 | 9:28 | 49.953
2021-01-16 | 9:28 | 49.953
2021-01-16 | 9:28 | 49.951
2021-01-16 | 9:28 | 49.948
2021-01-16 | 9:28 | 49.945
2021-01-16 | 9:28 | 49.942
2021-01-16 | 9:28 | 49.942
2021-01-16 | 9:28 | 49.941
2021-01-16 | 9:28 | 49.94
2021-01-16 | 9:28 | 49.94
2021-01-16 | 9:28 | 49.939
2021-01-16 | 9:28 | 49.939
2021-01-16 | 9:28 | 49.94
2021-01-16 | 9:28 | 49.94
2021-01-16 | 9:28 | 49.941
2021-01-16 | 9:28 | 49.94
2021-01-16 | 9:28 | 49.94
2021-01-16 | 9:28 | 49.94
2021-01-16 | 9:28 | 49.937
2021-01-16 | 9:28 | 49.934
2021-01-16 | 9:28 | 49.932
2021-01-16 | 9:28 | 49.93
2021-01-16 | 9:28 | 49.928
2021-01-16 | 9:28 | 49.927
2021-01-16 | 9:28 | 49.926
2021-01-16 | 9:28 | 49.923
2021-01-16 | 9:28 | 49.921
2021-01-16 | 9:28 | 49.919
2021-01-16 | 9:28 | 49.916
2021-01-16 | 9:28 | 49.915
2021-01-16 | 9:28 | 49.913
2021-01-16 | 9:28 | 49.914
2021-01-16 | 9:28 | 49.915
2021-01-16 | 9:28 | 49.915
2021-01-16 | 9:28 | 49.915
2021-01-16 | 9:28 | 49.915
2021-01-16 | 9:28 | 49.915
2021-01-16 | 9:28 | 49.916
2021-01-16 | 9:28 | 49.922
2021-01-16 | 9:28 | 49.93
2021-01-16 | 9:28 | 49.935
2021-01-16 | 9:28 | 49.937
2021-01-16 | 9:28 | 49.939
2021-01-16 | 9:28 | 49.94
2021-01-16 | 9:28 | 49.937
2021-01-16 | 9:28 | 49.937
2021-01-16 | 9:28 | 49.934
2021-01-16 | 9:28 | 49.935
2021-01-16 | 9:28 | 49.934
2021-01-16 | 9:28 | 49.932
2021-01-16 | 9:28 | 49.93
2021-01-16 | 9:28 | 49.929
2021-01-16 | 9:29 | 49.93
2021-01-16 | 9:29 | 49.933
2021-01-16 | 9:29 | 49.937
2021-01-16 | 9:29 | 49.939
2021-01-16 | 9:29 | 49.94
2021-01-16 | 9:29 | 49.943
2021-01-16 | 9:29 | 49.943
2021-01-16 | 9:29 | 49.947
2021-01-16 | 9:29 | 49.95
2021-01-16 | 9:29 | 49.953
2021-01-16 | 9:29 | 49.955
2021-01-16 | 9:29 | 49.957
2021-01-16 | 9:29 | 49.958
2021-01-16 | 9:29 | 49.958
2021-01-16 | 9:29 | 49.958
2021-01-16 | 9:29 | 49.959
2021-01-16 | 9:29 | 49.956
2021-01-16 | 9:29 | 49.953
2021-01-16 | 9:29 | 49.949
2021-01-16 | 9:29 | 49.943
2021-01-16 | 9:29 | 49.941
2021-01-16 | 9:29 | 49.938
2021-01-16 | 9:29 | 49.936
2021-01-16 | 9:29 | 49.937
2021-01-16 | 9:29 | 49.935
2021-01-16 | 9:29 | 49.936
2021-01-16 | 9:29 | 49.938
2021-01-16 | 9:29 | 49.937
2021-01-16 | 9:29 | 49.939
2021-01-16 | 9:29 | 49.939
2021-01-16 | 9:29 | 49.939
2021-01-16 | 9:29 | 49.938
2021-01-16 | 9:29 | 49.938
2021-01-16 | 9:29 | 49.938
2021-01-16 | 9:29 | 49.939
2021-01-16 | 9:29 | 49.94
2021-01-16 | 9:29 | 49.942
2021-01-16 | 9:29 | 49.941
2021-01-16 | 9:29 | 49.941
2021-01-16 | 9:29 | 49.94
2021-01-16 | 9:29 | 49.939
2021-01-16 | 9:29 | 49.94
2021-01-16 | 9:29 | 49.939
2021-01-16 | 9:29 | 49.938
2021-01-16 | 9:29 | 49.937
2021-01-16 | 9:29 | 49.936
2021-01-16 | 9:29 | 49.935
2021-01-16 | 9:29 | 49.934
2021-01-16 | 9:29 | 49.934
2021-01-16 | 9:29 | 49.932
2021-01-16 | 9:29 | 49.934
2021-01-16 | 9:29 | 49.935
2021-01-16 | 9:29 | 49.935
2021-01-16 | 9:29 | 49.936
2021-01-16 | 9:29 | 49.935
2021-01-16 | 9:29 | 49.935
2021-01-16 | 9:29 | 49.936
2021-01-16 | 9:29 | 49.936
2021-01-16 | 9:29 | 49.935
2021-01-16 | 9:30 | 49.936
2021-01-16 | 9:30 | 49.937
2021-01-16 | 9:30 | 49.938
2021-01-16 | 9:30 | 49.941
2021-01-16 | 9:30 | 49.941
2021-01-16 | 9:30 | 49.944
2021-01-16 | 9:30 | 49.946
2021-01-16 | 9:30 | 49.951
2021-01-16 | 9:30 | 49.951
2021-01-16 | 9:30 | 49.955
2021-01-16 | 9:30 | 49.955
2021-01-16 | 9:30 | 49.955
2021-01-16 | 9:30 | 49.954
2021-01-16 | 9:30 | 49.955
2021-01-16 | 9:30 | 49.956
2021-01-16 | 9:30 | 49.957
2021-01-16 | 9:30 | 49.958
2021-01-16 | 9:30 | 49.958
2021-01-16 | 9:30 | 49.959
2021-01-16 | 9:30 | 49.957
2021-01-16 | 9:30 | 49.954
2021-01-16 | 9:30 | 49.951
2021-01-16 | 9:30 | 49.949
2021-01-16 | 9:30 | 49.949
2021-01-16 | 9:30 | 49.947
2021-01-16 | 9:30 | 49.945
2021-01-16 | 9:30 | 49.945
2021-01-16 | 9:30 | 49.947
2021-01-16 | 9:30 | 49.949
2021-01-16 | 9:30 | 49.953
2021-01-16 | 9:30 | 49.956
2021-01-16 | 9:30 | 49.96
2021-01-16 | 9:30 | 49.962
2021-01-16 | 9:30 | 49.963
2021-01-16 | 9:30 | 49.964
2021-01-16 | 9:30 | 49.966
2021-01-16 | 9:30 | 49.966
2021-01-16 | 9:30 | 49.967
2021-01-16 | 9:30 | 49.966
2021-01-16 | 9:30 | 49.963
2021-01-16 | 9:30 | 49.962
2021-01-16 | 9:30 | 49.958
2021-01-16 | 9:30 | 49.957
2021-01-16 | 9:30 | 49.954
2021-01-16 | 9:30 | 49.951
2021-01-16 | 9:30 | 49.948
2021-01-16 | 9:30 | 49.946
2021-01-16 | 9:30 | 49.947
2021-01-16 | 9:30 | 49.945
2021-01-16 | 9:30 | 49.944
2021-01-16 | 9:30 | 49.942
2021-01-16 | 9:30 | 49.94
2021-01-16 | 9:30 | 49.941
2021-01-16 | 9:30 | 49.942
2021-01-16 | 9:30 | 49.943
2021-01-16 | 9:30 | 49.944
2021-01-16 | 9:30 | 49.946
2021-01-16 | 9:30 | 49.946
2021-01-16 | 9:30 | 49.945
2021-01-16 | 9:30 | 49.946
2021-01-16 | 9:30 | 49.945
2021-01-16 | 9:31 | 49.945
2021-01-16 | 9:31 | 49.942
2021-01-16 | 9:31 | 49.939
2021-01-16 | 9:31 | 49.937
2021-01-16 | 9:31 | 49.936
2021-01-16 | 9:31 | 49.938
2021-01-16 | 9:31 | 49.938
2021-01-16 | 9:31 | 49.938
2021-01-16 | 9:31 | 49.936
2021-01-16 | 9:31 | 49.934
2021-01-16 | 9:31 | 49.934
2021-01-16 | 9:31 | 49.933
2021-01-16 | 9:31 | 49.933
2021-01-16 | 9:31 | 49.933
2021-01-16 | 9:31 | 49.932
2021-01-16 | 9:31 | 49.931
2021-01-16 | 9:31 | 49.931
2021-01-16 | 9:31 | 49.932
2021-01-16 | 9:31 | 49.935
2021-01-16 | 9:31 | 49.936
2021-01-16 | 9:31 | 49.937
2021-01-16 | 9:31 | 49.938
2021-01-16 | 9:31 | 49.938
2021-01-16 | 9:31 | 49.937
2021-01-16 | 9:31 | 49.934
2021-01-16 | 9:31 | 49.931
2021-01-16 | 9:31 | 49.928
2021-01-16 | 9:31 | 49.926
2021-01-16 | 9:31 | 49.927
2021-01-16 | 9:31 | 49.925
2021-01-16 | 9:31 | 49.924
2021-01-16 | 9:31 | 49.924
2021-01-16 | 9:31 | 49.926
2021-01-16 | 9:31 | 49.929
2021-01-16 | 9:31 | 49.932
2021-01-16 | 9:31 | 49.934
2021-01-16 | 9:31 | 49.937
2021-01-16 | 9:31 | 49.936
2021-01-16 | 9:31 | 49.937
2021-01-16 | 9:31 | 49.935
2021-01-16 | 9:31 | 49.935
2021-01-16 | 9:31 | 49.934
2021-01-16 | 9:31 | 49.934
2021-01-16 | 9:31 | 49.931
2021-01-16 | 9:31 | 49.933
2021-01-16 | 9:31 | 49.931
2021-01-16 | 9:31 | 49.928
2021-01-16 | 9:31 | 49.927
2021-01-16 | 9:31 | 49.926
2021-01-16 | 9:31 | 49.927
2021-01-16 | 9:31 | 49.93
2021-01-16 | 9:31 | 49.934
2021-01-16 | 9:31 | 49.939
2021-01-16 | 9:31 | 49.941
2021-01-16 | 9:31 | 49.942
2021-01-16 | 9:31 | 49.943
2021-01-16 | 9:31 | 49.943
2021-01-16 | 9:31 | 49.943
2021-01-16 | 9:31 | 49.943
2021-01-16 | 9:32 | 49.942
2021-01-16 | 9:32 | 49.941
2021-01-16 | 9:32 | 49.942
2021-01-16 | 9:32 | 49.942
2021-01-16 | 9:32 | 49.94
2021-01-16 | 9:32 | 49.941
2021-01-16 | 9:32 | 49.939
2021-01-16 | 9:32 | 49.937
2021-01-16 | 9:32 | 49.937
2021-01-16 | 9:32 | 49.936
2021-01-16 | 9:32 | 49.934
2021-01-16 | 9:32 | 49.931
2021-01-16 | 9:32 | 49.929
2021-01-16 | 9:32 | 49.928
2021-01-16 | 9:32 | 49.927
2021-01-16 | 9:32 | 49.929
2021-01-16 | 9:32 | 49.931
2021-01-16 | 9:32 | 49.932
2021-01-16 | 9:32 | 49.933
2021-01-16 | 9:32 | 49.933
2021-01-16 | 9:32 | 49.932
2021-01-16 | 9:32 | 49.93
2021-01-16 | 9:32 | 49.93
2021-01-16 | 9:32 | 49.927
2021-01-16 | 9:32 | 49.926
2021-01-16 | 9:32 | 49.924
2021-01-16 | 9:32 | 49.924
2021-01-16 | 9:32 | 49.921
2021-01-16 | 9:32 | 49.919
2021-01-16 | 9:32 | 49.918
2021-01-16 | 9:32 | 49.917
2021-01-16 | 9:32 | 49.915
2021-01-16 | 9:32 | 49.914
2021-01-16 | 9:32 | 49.916
2021-01-16 | 9:32 | 49.915
2021-01-16 | 9:32 | 49.917
2021-01-16 | 9:32 | 49.916
2021-01-16 | 9:32 | 49.918
2021-01-16 | 9:32 | 49.923
2021-01-16 | 9:32 | 49.926
2021-01-16 | 9:32 | 49.926
2021-01-16 | 9:32 | 49.925
2021-01-16 | 9:32 | 49.923
2021-01-16 | 9:32 | 49.923
2021-01-16 | 9:32 | 49.923
2021-01-16 | 9:32 | 49.923
2021-01-16 | 9:32 | 49.923
2021-01-16 | 9:32 | 49.921
2021-01-16 | 9:32 | 49.923
2021-01-16 | 9:32 | 49.923
2021-01-16 | 9:32 | 49.921
2021-01-16 | 9:32 | 49.92
2021-01-16 | 9:32 | 49.918
2021-01-16 | 9:32 | 49.918
2021-01-16 | 9:32 | 49.919
2021-01-16 | 9:32 | 49.922
2021-01-16 | 9:32 | 49.922
2021-01-16 | 9:32 | 49.923
2021-01-16 | 9:32 | 49.926
2021-01-16 | 9:32 | 49.929
2021-01-16 | 9:32 | 49.929
2021-01-16 | 9:33 | 49.929
2021-01-16 | 9:33 | 49.93
2021-01-16 | 9:33 | 49.93
2021-01-16 | 9:33 | 49.929
2021-01-16 | 9:33 | 49.928
2021-01-16 | 9:33 | 49.93
2021-01-16 | 9:33 | 49.934
2021-01-16 | 9:33 | 49.934
2021-01-16 | 9:33 | 49.934
2021-01-16 | 9:33 | 49.931
2021-01-16 | 9:33 | 49.928
2021-01-16 | 9:33 | 49.926
2021-01-16 | 9:33 | 49.924
2021-01-16 | 9:33 | 49.923
2021-01-16 | 9:33 | 49.925
2021-01-16 | 9:33 | 49.924
2021-01-16 | 9:33 | 49.924
2021-01-16 | 9:33 | 49.926
2021-01-16 | 9:33 | 49.928
2021-01-16 | 9:33 | 49.932
2021-01-16 | 9:33 | 49.93
2021-01-16 | 9:33 | 49.929
2021-01-16 | 9:33 | 49.927
2021-01-16 | 9:33 | 49.926
2021-01-16 | 9:33 | 49.925
2021-01-16 | 9:33 | 49.925
2021-01-16 | 9:33 | 49.924
2021-01-16 | 9:33 | 49.923
2021-01-16 | 9:33 | 49.919
2021-01-16 | 9:33 | 49.915
2021-01-16 | 9:33 | 49.913
2021-01-16 | 9:33 | 49.91
2021-01-16 | 9:33 | 49.909
2021-01-16 | 9:33 | 49.905
2021-01-16 | 9:33 | 49.906
2021-01-16 | 9:33 | 49.907
2021-01-16 | 9:33 | 49.904
2021-01-16 | 9:33 | 49.905
2021-01-16 | 9:33 | 49.903
2021-01-16 | 9:33 | 49.904
2021-01-16 | 9:33 | 49.904
2021-01-16 | 9:33 | 49.902
2021-01-16 | 9:33 | 49.902
2021-01-16 | 9:33 | 49.902
2021-01-16 | 9:33 | 49.904
2021-01-16 | 9:33 | 49.904
2021-01-16 | 9:33 | 49.904
2021-01-16 | 9:33 | 49.903
2021-01-16 | 9:33 | 49.901
2021-01-16 | 9:33 | 49.899
2021-01-16 | 9:33 | 49.898
2021-01-16 | 9:33 | 49.898
2021-01-16 | 9:33 | 49.897
2021-01-16 | 9:33 | 49.893
2021-01-16 | 9:33 | 49.89
2021-01-16 | 9:33 | 49.889
2021-01-16 | 9:33 | 49.89
2021-01-16 | 9:33 | 49.894
2021-01-16 | 9:33 | 49.899
2021-01-16 | 9:34 | 49.902
2021-01-16 | 9:34 | 49.905
2021-01-16 | 9:34 | 49.91
2021-01-16 | 9:34 | 49.911
2021-01-16 | 9:34 | 49.912
2021-01-16 | 9:34 | 49.913
2021-01-16 | 9:34 | 49.913
2021-01-16 | 9:34 | 49.91
2021-01-16 | 9:34 | 49.911
2021-01-16 | 9:34 | 49.911
2021-01-16 | 9:34 | 49.912
2021-01-16 | 9:34 | 49.912
2021-01-16 | 9:34 | 49.912
2021-01-16 | 9:34 | 49.911
2021-01-16 | 9:34 | 49.913
2021-01-16 | 9:34 | 49.914
2021-01-16 | 9:34 | 49.913
2021-01-16 | 9:34 | 49.913
2021-01-16 | 9:34 | 49.913
2021-01-16 | 9:34 | 49.911
2021-01-16 | 9:34 | 49.913
2021-01-16 | 9:34 | 49.912
2021-01-16 | 9:34 | 49.912
2021-01-16 | 9:34 | 49.91
2021-01-16 | 9:34 | 49.906
2021-01-16 | 9:34 | 49.905
2021-01-16 | 9:34 | 49.903
2021-01-16 | 9:34 | 49.902
2021-01-16 | 9:34 | 49.901
2021-01-16 | 9:34 | 49.9
2021-01-16 | 9:34 | 49.899
2021-01-16 | 9:34 | 49.9
2021-01-16 | 9:34 | 49.902
2021-01-16 | 9:34 | 49.904
2021-01-16 | 9:34 | 49.905
2021-01-16 | 9:34 | 49.904
2021-01-16 | 9:34 | 49.908
2021-01-16 | 9:34 | 49.909
2021-01-16 | 9:34 | 49.908
2021-01-16 | 9:34 | 49.909
2021-01-16 | 9:34 | 49.908
2021-01-16 | 9:34 | 49.909
2021-01-16 | 9:34 | 49.906
2021-01-16 | 9:34 | 49.904
2021-01-16 | 9:34 | 49.901
2021-01-16 | 9:34 | 49.901
2021-01-16 | 9:34 | 49.901
2021-01-16 | 9:34 | 49.901
2021-01-16 | 9:34 | 49.901
2021-01-16 | 9:34 | 49.903
2021-01-16 | 9:34 | 49.906
2021-01-16 | 9:34 | 49.908
2021-01-16 | 9:34 | 49.909
2021-01-16 | 9:34 | 49.911
2021-01-16 | 9:34 | 49.909
2021-01-16 | 9:34 | 49.91
2021-01-16 | 9:34 | 49.91
2021-01-16 | 9:34 | 49.909
2021-01-16 | 9:34 | 49.909
2021-01-16 | 9:34 | 49.907
2021-01-16 | 9:34 | 49.906
2021-01-16 | 9:35 | 49.905
2021-01-16 | 9:35 | 49.905
2021-01-16 | 9:35 | 49.905
2021-01-16 | 9:35 | 49.904
2021-01-16 | 9:35 | 49.904
2021-01-16 | 9:35 | 49.906
2021-01-16 | 9:35 | 49.909
2021-01-16 | 9:35 | 49.909
2021-01-16 | 9:35 | 49.91
2021-01-16 | 9:35 | 49.913
2021-01-16 | 9:35 | 49.913
2021-01-16 | 9:35 | 49.915
2021-01-16 | 9:35 | 49.915
2021-01-16 | 9:35 | 49.915
2021-01-16 | 9:35 | 49.916
2021-01-16 | 9:35 | 49.915
2021-01-16 | 9:35 | 49.916
2021-01-16 | 9:35 | 49.917
2021-01-16 | 9:35 | 49.919
2021-01-16 | 9:35 | 49.921
2021-01-16 | 9:35 | 49.924
2021-01-16 | 9:35 | 49.924
2021-01-16 | 9:35 | 49.923
2021-01-16 | 9:35 | 49.928
2021-01-16 | 9:35 | 49.93
2021-01-16 | 9:35 | 49.931
2021-01-16 | 9:35 | 49.933
2021-01-16 | 9:35 | 49.93
2021-01-16 | 9:35 | 49.929
2021-01-16 | 9:35 | 49.925
2021-01-16 | 9:35 | 49.924
2021-01-16 | 9:35 | 49.925
2021-01-16 | 9:35 | 49.923
2021-01-16 | 9:35 | 49.922
2021-01-16 | 9:35 | 49.922
2021-01-16 | 9:35 | 49.922
2021-01-16 | 9:35 | 49.923
2021-01-16 | 9:35 | 49.925
2021-01-16 | 9:35 | 49.928
2021-01-16 | 9:35 | 49.93
2021-01-16 | 9:35 | 49.93
2021-01-16 | 9:35 | 49.932
2021-01-16 | 9:35 | 49.931
2021-01-16 | 9:35 | 49.93
2021-01-16 | 9:35 | 49.928
2021-01-16 | 9:35 | 49.927
2021-01-16 | 9:35 | 49.93
2021-01-16 | 9:35 | 49.932
2021-01-16 | 9:35 | 49.933
2021-01-16 | 9:35 | 49.932
2021-01-16 | 9:35 | 49.928
2021-01-16 | 9:35 | 49.925
2021-01-16 | 9:35 | 49.923
2021-01-16 | 9:35 | 49.926
2021-01-16 | 9:35 | 49.928
2021-01-16 | 9:35 | 49.926
2021-01-16 | 9:35 | 49.927
2021-01-16 | 9:35 | 49.927
2021-01-16 | 9:35 | 49.927
2021-01-16 | 9:36 | 49.929
2021-01-16 | 9:36 | 49.93
2021-01-16 | 9:36 | 49.931
2021-01-16 | 9:36 | 49.93
2021-01-16 | 9:36 | 49.931
2021-01-16 | 9:36 | 49.931
2021-01-16 | 9:36 | 49.933
2021-01-16 | 9:36 | 49.934
2021-01-16 | 9:36 | 49.933
2021-01-16 | 9:36 | 49.929
2021-01-16 | 9:36 | 49.928
2021-01-16 | 9:36 | 49.929
2021-01-16 | 9:36 | 49.931
2021-01-16 | 9:36 | 49.935
2021-01-16 | 9:36 | 49.936
2021-01-16 | 9:36 | 49.936
2021-01-16 | 9:36 | 49.934
2021-01-16 | 9:36 | 49.934
2021-01-16 | 9:36 | 49.935
2021-01-16 | 9:36 | 49.934
2021-01-16 | 9:36 | 49.933
2021-01-16 | 9:36 | 49.932
2021-01-16 | 9:36 | 49.931
2021-01-16 | 9:36 | 49.93
2021-01-16 | 9:36 | 49.928
2021-01-16 | 9:36 | 49.927
2021-01-16 | 9:36 | 49.924
2021-01-16 | 9:36 | 49.924
2021-01-16 | 9:36 | 49.922
2021-01-16 | 9:36 | 49.92
2021-01-16 | 9:36 | 49.918
2021-01-16 | 9:36 | 49.916
2021-01-16 | 9:36 | 49.915
2021-01-16 | 9:36 | 49.911
2021-01-16 | 9:36 | 49.912
2021-01-16 | 9:36 | 49.915
2021-01-16 | 9:36 | 49.918
2021-01-16 | 9:36 | 49.921
2021-01-16 | 9:36 | 49.924
2021-01-16 | 9:36 | 49.927
2021-01-16 | 9:36 | 49.925
2021-01-16 | 9:36 | 49.926
2021-01-16 | 9:36 | 49.925
2021-01-16 | 9:36 | 49.924
2021-01-16 | 9:36 | 49.922
2021-01-16 | 9:36 | 49.921
2021-01-16 | 9:36 | 49.917
2021-01-16 | 9:36 | 49.914
2021-01-16 | 9:36 | 49.916
2021-01-16 | 9:36 | 49.914
2021-01-16 | 9:36 | 49.913
2021-01-16 | 9:36 | 49.912
2021-01-16 | 9:36 | 49.91
2021-01-16 | 9:36 | 49.91
2021-01-16 | 9:36 | 49.91
2021-01-16 | 9:36 | 49.908
2021-01-16 | 9:36 | 49.911
2021-01-16 | 9:36 | 49.911
2021-01-16 | 9:36 | 49.911
2021-01-16 | 9:36 | 49.912
2021-01-16 | 9:36 | 49.91
2021-01-16 | 9:37 | 49.906
2021-01-16 | 9:37 | 49.905
2021-01-16 | 9:37 | 49.9
2021-01-16 | 9:37 | 49.895
2021-01-16 | 9:37 | 49.892
2021-01-16 | 9:37 | 49.89
2021-01-16 | 9:37 | 49.891
2021-01-16 | 9:37 | 49.891
2021-01-16 | 9:37 | 49.896
2021-01-16 | 9:37 | 49.899
2021-01-16 | 9:37 | 49.899
2021-01-16 | 9:37 | 49.901
2021-01-16 | 9:37 | 49.9
2021-01-16 | 9:37 | 49.9
2021-01-16 | 9:37 | 49.899
2021-01-16 | 9:37 | 49.9
2021-01-16 | 9:37 | 49.903
2021-01-16 | 9:37 | 49.903
2021-01-16 | 9:37 | 49.904
2021-01-16 | 9:37 | 49.906
2021-01-16 | 9:37 | 49.907
2021-01-16 | 9:37 | 49.907
2021-01-16 | 9:37 | 49.909
2021-01-16 | 9:37 | 49.912
2021-01-16 | 9:37 | 49.913
2021-01-16 | 9:37 | 49.912
2021-01-16 | 9:37 | 49.908
2021-01-16 | 9:37 | 49.906
2021-01-16 | 9:37 | 49.907
2021-01-16 | 9:37 | 49.908
2021-01-16 | 9:37 | 49.911
2021-01-16 | 9:37 | 49.912
2021-01-16 | 9:37 | 49.909
2021-01-16 | 9:37 | 49.908
2021-01-16 | 9:37 | 49.907
2021-01-16 | 9:37 | 49.902
2021-01-16 | 9:37 | 49.9
2021-01-16 | 9:37 | 49.9
2021-01-16 | 9:37 | 49.9
2021-01-16 | 9:37 | 49.9
2021-01-16 | 9:37 | 49.902
2021-01-16 | 9:37 | 49.904
2021-01-16 | 9:37 | 49.906
2021-01-16 | 9:37 | 49.903
2021-01-16 | 9:37 | 49.902
2021-01-16 | 9:37 | 49.899
2021-01-16 | 9:37 | 49.898
2021-01-16 | 9:37 | 49.901
2021-01-16 | 9:37 | 49.903
2021-01-16 | 9:37 | 49.903
2021-01-16 | 9:37 | 49.904
2021-01-16 | 9:37 | 49.903
2021-01-16 | 9:37 | 49.901
2021-01-16 | 9:37 | 49.901
2021-01-16 | 9:37 | 49.901
2021-01-16 | 9:37 | 49.899
2021-01-16 | 9:37 | 49.899
2021-01-16 | 9:37 | 49.899
2021-01-16 | 9:37 | 49.901
2021-01-16 | 9:38 | 49.903
2021-01-16 | 9:38 | 49.906
2021-01-16 | 9:38 | 49.904
2021-01-16 | 9:38 | 49.909
2021-01-16 | 9:38 | 49.91
2021-01-16 | 9:38 | 49.911
2021-01-16 | 9:38 | 49.911
2021-01-16 | 9:38 | 49.911
2021-01-16 | 9:38 | 49.909
2021-01-16 | 9:38 | 49.909
2021-01-16 | 9:38 | 49.906
2021-01-16 | 9:38 | 49.908
2021-01-16 | 9:38 | 49.904
2021-01-16 | 9:38 | 49.904
2021-01-16 | 9:38 | 49.908
2021-01-16 | 9:38 | 49.908
2021-01-16 | 9:38 | 49.904
2021-01-16 | 9:38 | 49.904
2021-01-16 | 9:38 | 49.904
2021-01-16 | 9:38 | 49.904
2021-01-16 | 9:38 | 49.903
2021-01-16 | 9:38 | 49.901
2021-01-16 | 9:38 | 49.899
2021-01-16 | 9:38 | 49.897
2021-01-16 | 9:38 | 49.896
2021-01-16 | 9:38 | 49.895
2021-01-16 | 9:38 | 49.893
2021-01-16 | 9:38 | 49.894
2021-01-16 | 9:38 | 49.899
2021-01-16 | 9:38 | 49.899
2021-01-16 | 9:38 | 49.896
2021-01-16 | 9:38 | 49.891
2021-01-16 | 9:38 | 49.885
2021-01-16 | 9:38 | 49.884
2021-01-16 | 9:38 | 49.883
2021-01-16 | 9:38 | 49.887
2021-01-16 | 9:38 | 49.888
2021-01-16 | 9:38 | 49.887
2021-01-16 | 9:38 | 49.887
2021-01-16 | 9:38 | 49.888
2021-01-16 | 9:38 | 49.888
2021-01-16 | 9:38 | 49.892
2021-01-16 | 9:38 | 49.897
2021-01-16 | 9:38 | 49.904
2021-01-16 | 9:38 | 49.905
2021-01-16 | 9:38 | 49.906
2021-01-16 | 9:38 | 49.905
2021-01-16 | 9:38 | 49.902
2021-01-16 | 9:38 | 49.9
2021-01-16 | 9:38 | 49.896
2021-01-16 | 9:38 | 49.892
2021-01-16 | 9:38 | 49.892
2021-01-16 | 9:38 | 49.893
2021-01-16 | 9:38 | 49.895
2021-01-16 | 9:38 | 49.896
2021-01-16 | 9:38 | 49.897
2021-01-16 | 9:38 | 49.898
2021-01-16 | 9:38 | 49.899
2021-01-16 | 9:38 | 49.896
2021-01-16 | 9:38 | 49.897
2021-01-16 | 9:38 | 49.895
2021-01-16 | 9:39 | 49.89
2021-01-16 | 9:39 | 49.889
2021-01-16 | 9:39 | 49.89
2021-01-16 | 9:39 | 49.89
2021-01-16 | 9:39 | 49.889
2021-01-16 | 9:39 | 49.889
2021-01-16 | 9:39 | 49.886
2021-01-16 | 9:39 | 49.888
2021-01-16 | 9:39 | 49.889
2021-01-16 | 9:39 | 49.89
2021-01-16 | 9:39 | 49.89
2021-01-16 | 9:39 | 49.892
2021-01-16 | 9:39 | 49.894
2021-01-16 | 9:39 | 49.895
2021-01-16 | 9:39 | 49.898
2021-01-16 | 9:39 | 49.899
2021-01-16 | 9:39 | 49.899
2021-01-16 | 9:39 | 49.9
2021-01-16 | 9:39 | 49.901
2021-01-16 | 9:39 | 49.902
2021-01-16 | 9:39 | 49.906
2021-01-16 | 9:39 | 49.906
2021-01-16 | 9:39 | 49.911
2021-01-16 | 9:39 | 49.915
2021-01-16 | 9:39 | 49.916
2021-01-16 | 9:39 | 49.914
2021-01-16 | 9:39 | 49.912
2021-01-16 | 9:39 | 49.912
2021-01-16 | 9:39 | 49.912
2021-01-16 | 9:39 | 49.911
2021-01-16 | 9:39 | 49.908
2021-01-16 | 9:39 | 49.908
2021-01-16 | 9:39 | 49.907
2021-01-16 | 9:39 | 49.911
2021-01-16 | 9:39 | 49.913
2021-01-16 | 9:39 | 49.92
2021-01-16 | 9:39 | 49.923
2021-01-16 | 9:39 | 49.926
2021-01-16 | 9:39 | 49.925
2021-01-16 | 9:39 | 49.925
2021-01-16 | 9:39 | 49.924
2021-01-16 | 9:39 | 49.926
2021-01-16 | 9:39 | 49.925
2021-01-16 | 9:39 | 49.926
2021-01-16 | 9:39 | 49.926
2021-01-16 | 9:39 | 49.926
2021-01-16 | 9:39 | 49.924
2021-01-16 | 9:39 | 49.922
2021-01-16 | 9:39 | 49.92
2021-01-16 | 9:39 | 49.919
2021-01-16 | 9:39 | 49.916
2021-01-16 | 9:39 | 49.917
2021-01-16 | 9:39 | 49.916
2021-01-16 | 9:39 | 49.917
2021-01-16 | 9:39 | 49.917
2021-01-16 | 9:39 | 49.917
2021-01-16 | 9:39 | 49.92
2021-01-16 | 9:39 | 49.922
2021-01-16 | 9:39 | 49.924
2021-01-16 | 9:40 | 49.928
2021-01-16 | 9:40 | 49.927
2021-01-16 | 9:40 | 49.928
2021-01-16 | 9:40 | 49.928
2021-01-16 | 9:40 | 49.927
2021-01-16 | 9:40 | 49.928
2021-01-16 | 9:40 | 49.931
2021-01-16 | 9:40 | 49.933
2021-01-16 | 9:40 | 49.936
2021-01-16 | 9:40 | 49.94
2021-01-16 | 9:40 | 49.941
2021-01-16 | 9:40 | 49.944
2021-01-16 | 9:40 | 49.946
2021-01-16 | 9:40 | 49.944
2021-01-16 | 9:40 | 49.944
2021-01-16 | 9:40 | 49.945
2021-01-16 | 9:40 | 49.946
2021-01-16 | 9:40 | 49.944
2021-01-16 | 9:40 | 49.943
2021-01-16 | 9:40 | 49.941
2021-01-16 | 9:40 | 49.938
2021-01-16 | 9:40 | 49.934
2021-01-16 | 9:40 | 49.93
2021-01-16 | 9:40 | 49.93
2021-01-16 | 9:40 | 49.931
2021-01-16 | 9:40 | 49.931
2021-01-16 | 9:40 | 49.932
2021-01-16 | 9:40 | 49.931
2021-01-16 | 9:40 | 49.929
2021-01-16 | 9:40 | 49.928
2021-01-16 | 9:40 | 49.929
2021-01-16 | 9:40 | 49.929
2021-01-16 | 9:40 | 49.928
2021-01-16 | 9:40 | 49.928
2021-01-16 | 9:40 | 49.927
2021-01-16 | 9:40 | 49.927
2021-01-16 | 9:40 | 49.927
2021-01-16 | 9:40 | 49.925
2021-01-16 | 9:40 | 49.921
2021-01-16 | 9:40 | 49.921
2021-01-16 | 9:40 | 49.92
2021-01-16 | 9:40 | 49.92
2021-01-16 | 9:40 | 49.92
2021-01-16 | 9:40 | 49.921
2021-01-16 | 9:40 | 49.922
2021-01-16 | 9:40 | 49.922
2021-01-16 | 9:40 | 49.923
2021-01-16 | 9:40 | 49.922
2021-01-16 | 9:40 | 49.921
2021-01-16 | 9:40 | 49.919
2021-01-16 | 9:40 | 49.916
2021-01-16 | 9:40 | 49.912
2021-01-16 | 9:40 | 49.909
2021-01-16 | 9:40 | 49.904
2021-01-16 | 9:40 | 49.903
2021-01-16 | 9:40 | 49.902
2021-01-16 | 9:40 | 49.903
2021-01-16 | 9:40 | 49.905
2021-01-16 | 9:40 | 49.904
2021-01-16 | 9:40 | 49.904
2021-01-16 | 9:40 | 49.904
2021-01-16 | 9:41 | 49.907
2021-01-16 | 9:41 | 49.909
2021-01-16 | 9:41 | 49.909
2021-01-16 | 9:41 | 49.907
2021-01-16 | 9:41 | 49.908
2021-01-16 | 9:41 | 49.91
2021-01-16 | 9:41 | 49.912
2021-01-16 | 9:41 | 49.911
2021-01-16 | 9:41 | 49.913
2021-01-16 | 9:41 | 49.914
2021-01-16 | 9:41 | 49.916
2021-01-16 | 9:41 | 49.917
2021-01-16 | 9:41 | 49.916
2021-01-16 | 9:41 | 49.916
2021-01-16 | 9:41 | 49.914
2021-01-16 | 9:41 | 49.913
2021-01-16 | 9:41 | 49.911
2021-01-16 | 9:41 | 49.909
2021-01-16 | 9:41 | 49.908
2021-01-16 | 9:41 | 49.908
2021-01-16 | 9:41 | 49.909
2021-01-16 | 9:41 | 49.91
2021-01-16 | 9:41 | 49.908
2021-01-16 | 9:41 | 49.908
2021-01-16 | 9:41 | 49.908
2021-01-16 | 9:41 | 49.909
2021-01-16 | 9:41 | 49.908
2021-01-16 | 9:41 | 49.907
2021-01-16 | 9:41 | 49.907
2021-01-16 | 9:41 | 49.905
2021-01-16 | 9:41 | 49.902
2021-01-16 | 9:41 | 49.899
2021-01-16 | 9:41 | 49.894
2021-01-16 | 9:41 | 49.896
2021-01-16 | 9:41 | 49.895
2021-01-16 | 9:41 | 49.898
2021-01-16 | 9:41 | 49.896
2021-01-16 | 9:41 | 49.896
2021-01-16 | 9:41 | 49.896
2021-01-16 | 9:41 | 49.896
2021-01-16 | 9:41 | 49.895
2021-01-16 | 9:41 | 49.894
2021-01-16 | 9:41 | 49.893
2021-01-16 | 9:41 | 49.895
2021-01-16 | 9:41 | 49.896
2021-01-16 | 9:41 | 49.896
2021-01-16 | 9:41 | 49.897
2021-01-16 | 9:41 | 49.896
2021-01-16 | 9:41 | 49.895
2021-01-16 | 9:41 | 49.896
2021-01-16 | 9:41 | 49.896
2021-01-16 | 9:41 | 49.897
2021-01-16 | 9:41 | 49.898
2021-01-16 | 9:41 | 49.902
2021-01-16 | 9:41 | 49.899
2021-01-16 | 9:41 | 49.9
2021-01-16 | 9:41 | 49.9
2021-01-16 | 9:41 | 49.898
2021-01-16 | 9:41 | 49.894
2021-01-16 | 9:42 | 49.892
2021-01-16 | 9:42 | 49.89
2021-01-16 | 9:42 | 49.886
2021-01-16 | 9:42 | 49.886
2021-01-16 | 9:42 | 49.888
2021-01-16 | 9:42 | 49.889
2021-01-16 | 9:42 | 49.888
2021-01-16 | 9:42 | 49.89
2021-01-16 | 9:42 | 49.888
2021-01-16 | 9:42 | 49.889
2021-01-16 | 9:42 | 49.889
2021-01-16 | 9:42 | 49.889
2021-01-16 | 9:42 | 49.888
2021-01-16 | 9:42 | 49.887
2021-01-16 | 9:42 | 49.885
2021-01-16 | 9:42 | 49.884
2021-01-16 | 9:42 | 49.887
2021-01-16 | 9:42 | 49.888
2021-01-16 | 9:42 | 49.889
2021-01-16 | 9:42 | 49.891
2021-01-16 | 9:42 | 49.894
2021-01-16 | 9:42 | 49.896
2021-01-16 | 9:42 | 49.898
2021-01-16 | 9:42 | 49.897
2021-01-16 | 9:42 | 49.899
2021-01-16 | 9:42 | 49.899
2021-01-16 | 9:42 | 49.899
2021-01-16 | 9:42 | 49.9
2021-01-16 | 9:42 | 49.902
2021-01-16 | 9:42 | 49.899
2021-01-16 | 9:42 | 49.897
2021-01-16 | 9:42 | 49.894
2021-01-16 | 9:42 | 49.893
2021-01-16 | 9:42 | 49.892
2021-01-16 | 9:42 | 49.892
2021-01-16 | 9:42 | 49.892
2021-01-16 | 9:42 | 49.892
2021-01-16 | 9:42 | 49.889
2021-01-16 | 9:42 | 49.886
2021-01-16 | 9:42 | 49.885
2021-01-16 | 9:42 | 49.886
2021-01-16 | 9:42 | 49.885
2021-01-16 | 9:42 | 49.885
2021-01-16 | 9:42 | 49.885
2021-01-16 | 9:42 | 49.886
2021-01-16 | 9:42 | 49.888
2021-01-16 | 9:42 | 49.891
2021-01-16 | 9:42 | 49.896
2021-01-16 | 9:42 | 49.898
2021-01-16 | 9:42 | 49.902
2021-01-16 | 9:42 | 49.902
2021-01-16 | 9:42 | 49.904
2021-01-16 | 9:42 | 49.904
2021-01-16 | 9:42 | 49.901
2021-01-16 | 9:42 | 49.901
2021-01-16 | 9:42 | 49.898
2021-01-16 | 9:42 | 49.899
2021-01-16 | 9:42 | 49.903
2021-01-16 | 9:42 | 49.906
2021-01-16 | 9:42 | 49.906
2021-01-16 | 9:42 | 49.908
2021-01-16 | 9:43 | 49.906
2021-01-16 | 9:43 | 49.904
2021-01-16 | 9:43 | 49.904
2021-01-16 | 9:43 | 49.903
2021-01-16 | 9:43 | 49.902
2021-01-16 | 9:43 | 49.903
2021-01-16 | 9:43 | 49.9
2021-01-16 | 9:43 | 49.899
2021-01-16 | 9:43 | 49.898
2021-01-16 | 9:43 | 49.895
2021-01-16 | 9:43 | 49.894
2021-01-16 | 9:43 | 49.895
2021-01-16 | 9:43 | 49.894
2021-01-16 | 9:43 | 49.894
2021-01-16 | 9:43 | 49.895
2021-01-16 | 9:43 | 49.896
2021-01-16 | 9:43 | 49.897
2021-01-16 | 9:43 | 49.896
2021-01-16 | 9:43 | 49.895
2021-01-16 | 9:43 | 49.895
2021-01-16 | 9:43 | 49.898
2021-01-16 | 9:43 | 49.899
2021-01-16 | 9:43 | 49.898
2021-01-16 | 9:43 | 49.9
2021-01-16 | 9:43 | 49.9
2021-01-16 | 9:43 | 49.899
2021-01-16 | 9:43 | 49.899
2021-01-16 | 9:43 | 49.898
2021-01-16 | 9:43 | 49.895
2021-01-16 | 9:43 | 49.892
2021-01-16 | 9:43 | 49.893
2021-01-16 | 9:43 | 49.891
2021-01-16 | 9:43 | 49.89
2021-01-16 | 9:43 | 49.889
2021-01-16 | 9:43 | 49.887
2021-01-16 | 9:43 | 49.889
2021-01-16 | 9:43 | 49.892
2021-01-16 | 9:43 | 49.891
2021-01-16 | 9:43 | 49.889
2021-01-16 | 9:43 | 49.888
2021-01-16 | 9:43 | 49.889
2021-01-16 | 9:43 | 49.891
2021-01-16 | 9:43 | 49.89
2021-01-16 | 9:43 | 49.889
2021-01-16 | 9:43 | 49.888
2021-01-16 | 9:43 | 49.887
2021-01-16 | 9:43 | 49.888
2021-01-16 | 9:43 | 49.889
2021-01-16 | 9:43 | 49.89
2021-01-16 | 9:43 | 49.886
2021-01-16 | 9:43 | 49.885
2021-01-16 | 9:43 | 49.882
2021-01-16 | 9:43 | 49.879
2021-01-16 | 9:43 | 49.876
2021-01-16 | 9:43 | 49.874
2021-01-16 | 9:43 | 49.872
2021-01-16 | 9:43 | 49.872
2021-01-16 | 9:43 | 49.875
2021-01-16 | 9:43 | 49.877
2021-01-16 | 9:44 | 49.879
2021-01-16 | 9:44 | 49.883
2021-01-16 | 9:44 | 49.884
2021-01-16 | 9:44 | 49.885
2021-01-16 | 9:44 | 49.889
2021-01-16 | 9:44 | 49.89
2021-01-16 | 9:44 | 49.89
2021-01-16 | 9:44 | 49.889
2021-01-16 | 9:44 | 49.886
2021-01-16 | 9:44 | 49.889
2021-01-16 | 9:44 | 49.89
2021-01-16 | 9:44 | 49.891
2021-01-16 | 9:44 | 49.891
2021-01-16 | 9:44 | 49.886
2021-01-16 | 9:44 | 49.883
2021-01-16 | 9:44 | 49.886
2021-01-16 | 9:44 | 49.884
2021-01-16 | 9:44 | 49.884
2021-01-16 | 9:44 | 49.883
2021-01-16 | 9:44 | 49.881
2021-01-16 | 9:44 | 49.878
2021-01-16 | 9:44 | 49.879
2021-01-16 | 9:44 | 49.88
2021-01-16 | 9:44 | 49.881
2021-01-16 | 9:44 | 49.884
2021-01-16 | 9:44 | 49.883
2021-01-16 | 9:44 | 49.886
2021-01-16 | 9:44 | 49.89
2021-01-16 | 9:44 | 49.896
2021-01-16 | 9:44 | 49.899
2021-01-16 | 9:44 | 49.9
2021-01-16 | 9:44 | 49.901
2021-01-16 | 9:44 | 49.9
2021-01-16 | 9:44 | 49.901
2021-01-16 | 9:44 | 49.9
2021-01-16 | 9:44 | 49.9
2021-01-16 | 9:44 | 49.899
2021-01-16 | 9:44 | 49.893
2021-01-16 | 9:44 | 49.895
2021-01-16 | 9:44 | 49.892
2021-01-16 | 9:44 | 49.89
2021-01-16 | 9:44 | 49.892
2021-01-16 | 9:44 | 49.893
2021-01-16 | 9:44 | 49.893
2021-01-16 | 9:44 | 49.894
2021-01-16 | 9:44 | 49.896
2021-01-16 | 9:44 | 49.896
2021-01-16 | 9:44 | 49.897
2021-01-16 | 9:44 | 49.897
2021-01-16 | 9:44 | 49.899
2021-01-16 | 9:44 | 49.903
2021-01-16 | 9:44 | 49.907
2021-01-16 | 9:44 | 49.91
2021-01-16 | 9:44 | 49.912
2021-01-16 | 9:44 | 49.914
2021-01-16 | 9:44 | 49.915
2021-01-16 | 9:44 | 49.913
2021-01-16 | 9:44 | 49.911
2021-01-16 | 9:44 | 49.906
2021-01-16 | 9:44 | 49.906
2021-01-16 | 9:44 | 49.905
2021-01-16 | 9:45 | 49.904
2021-01-16 | 9:45 | 49.903
2021-01-16 | 9:45 | 49.902
2021-01-16 | 9:45 | 49.902
2021-01-16 | 9:45 | 49.901
2021-01-16 | 9:45 | 49.902
2021-01-16 | 9:45 | 49.902
2021-01-16 | 9:45 | 49.901
2021-01-16 | 9:45 | 49.9
2021-01-16 | 9:45 | 49.9
2021-01-16 | 9:45 | 49.899
2021-01-16 | 9:45 | 49.896
2021-01-16 | 9:45 | 49.898
2021-01-16 | 9:45 | 49.899
2021-01-16 | 9:45 | 49.897
2021-01-16 | 9:45 | 49.892
2021-01-16 | 9:45 | 49.891
2021-01-16 | 9:45 | 49.89
2021-01-16 | 9:45 | 49.889
2021-01-16 | 9:45 | 49.887
2021-01-16 | 9:45 | 49.888
2021-01-16 | 9:45 | 49.89
2021-01-16 | 9:45 | 49.888
2021-01-16 | 9:45 | 49.888
2021-01-16 | 9:45 | 49.889
2021-01-16 | 9:45 | 49.889
2021-01-16 | 9:45 | 49.888
2021-01-16 | 9:45 | 49.888
2021-01-16 | 9:45 | 49.89
2021-01-16 | 9:45 | 49.892
2021-01-16 | 9:45 | 49.892
2021-01-16 | 9:45 | 49.892
2021-01-16 | 9:45 | 49.893
2021-01-16 | 9:45 | 49.894
2021-01-16 | 9:45 | 49.897
2021-01-16 | 9:45 | 49.898
2021-01-16 | 9:45 | 49.898
2021-01-16 | 9:45 | 49.9
2021-01-16 | 9:45 | 49.903
2021-01-16 | 9:45 | 49.905
2021-01-16 | 9:45 | 49.908
2021-01-16 | 9:45 | 49.91
2021-01-16 | 9:45 | 49.909
2021-01-16 | 9:45 | 49.908
2021-01-16 | 9:45 | 49.907
2021-01-16 | 9:45 | 49.908
2021-01-16 | 9:45 | 49.907
2021-01-16 | 9:45 | 49.905
2021-01-16 | 9:45 | 49.905
2021-01-16 | 9:45 | 49.904
2021-01-16 | 9:45 | 49.901
2021-01-16 | 9:45 | 49.9
2021-01-16 | 9:45 | 49.899
2021-01-16 | 9:45 | 49.899
2021-01-16 | 9:45 | 49.897
2021-01-16 | 9:45 | 49.898
2021-01-16 | 9:45 | 49.9
2021-01-16 | 9:45 | 49.9
2021-01-16 | 9:45 | 49.901
2021-01-16 | 9:46 | 49.901
2021-01-16 | 9:46 | 49.904
2021-01-16 | 9:46 | 49.903
2021-01-16 | 9:46 | 49.904
2021-01-16 | 9:46 | 49.906
2021-01-16 | 9:46 | 49.907
2021-01-16 | 9:46 | 49.908
2021-01-16 | 9:46 | 49.909
2021-01-16 | 9:46 | 49.912
2021-01-16 | 9:46 | 49.915
2021-01-16 | 9:46 | 49.914
2021-01-16 | 9:46 | 49.913
2021-01-16 | 9:46 | 49.916
2021-01-16 | 9:46 | 49.917
2021-01-16 | 9:46 | 49.913
2021-01-16 | 9:46 | 49.909
2021-01-16 | 9:46 | 49.906
2021-01-16 | 9:46 | 49.902
2021-01-16 | 9:46 | 49.898
2021-01-16 | 9:46 | 49.896
2021-01-16 | 9:46 | 49.897
2021-01-16 | 9:46 | 49.9
2021-01-16 | 9:46 | 49.9
2021-01-16 | 9:46 | 49.9
2021-01-16 | 9:46 | 49.903
2021-01-16 | 9:46 | 49.904
2021-01-16 | 9:46 | 49.902
2021-01-16 | 9:46 | 49.902
2021-01-16 | 9:46 | 49.905
2021-01-16 | 9:46 | 49.905
2021-01-16 | 9:46 | 49.906
2021-01-16 | 9:46 | 49.909
2021-01-16 | 9:46 | 49.911
2021-01-16 | 9:46 | 49.911
2021-01-16 | 9:46 | 49.91
2021-01-16 | 9:46 | 49.909
2021-01-16 | 9:46 | 49.909
2021-01-16 | 9:46 | 49.906
2021-01-16 | 9:46 | 49.902
2021-01-16 | 9:46 | 49.9
2021-01-16 | 9:46 | 49.898
2021-01-16 | 9:46 | 49.898
2021-01-16 | 9:46 | 49.898
2021-01-16 | 9:46 | 49.895
2021-01-16 | 9:46 | 49.895
2021-01-16 | 9:46 | 49.895
2021-01-16 | 9:46 | 49.894
2021-01-16 | 9:46 | 49.895
2021-01-16 | 9:46 | 49.896
2021-01-16 | 9:46 | 49.897
2021-01-16 | 9:46 | 49.897
2021-01-16 | 9:46 | 49.9
2021-01-16 | 9:46 | 49.899
2021-01-16 | 9:46 | 49.898
2021-01-16 | 9:46 | 49.895
2021-01-16 | 9:46 | 49.898
2021-01-16 | 9:46 | 49.898
2021-01-16 | 9:46 | 49.898
2021-01-16 | 9:46 | 49.898
2021-01-16 | 9:46 | 49.901
2021-01-16 | 9:46 | 49.903
2021-01-16 | 9:47 | 49.906
2021-01-16 | 9:47 | 49.906
2021-01-16 | 9:47 | 49.906
2021-01-16 | 9:47 | 49.906
2021-01-16 | 9:47 | 49.907
2021-01-16 | 9:47 | 49.908
2021-01-16 | 9:47 | 49.908
2021-01-16 | 9:47 | 49.907
2021-01-16 | 9:47 | 49.904
2021-01-16 | 9:47 | 49.902
2021-01-16 | 9:47 | 49.902
2021-01-16 | 9:47 | 49.905
2021-01-16 | 9:47 | 49.908
2021-01-16 | 9:47 | 49.909
2021-01-16 | 9:47 | 49.91
2021-01-16 | 9:47 | 49.909
2021-01-16 | 9:47 | 49.911
2021-01-16 | 9:47 | 49.911
2021-01-16 | 9:47 | 49.906
2021-01-16 | 9:47 | 49.906
2021-01-16 | 9:47 | 49.907
2021-01-16 | 9:47 | 49.908
2021-01-16 | 9:47 | 49.907
2021-01-16 | 9:47 | 49.908
2021-01-16 | 9:47 | 49.909
2021-01-16 | 9:47 | 49.909
2021-01-16 | 9:47 | 49.909
2021-01-16 | 9:47 | 49.911
2021-01-16 | 9:47 | 49.915
2021-01-16 | 9:47 | 49.917
2021-01-16 | 9:47 | 49.916
2021-01-16 | 9:47 | 49.915
2021-01-16 | 9:47 | 49.915
2021-01-16 | 9:47 | 49.915
2021-01-16 | 9:47 | 49.914
2021-01-16 | 9:47 | 49.915
2021-01-16 | 9:47 | 49.918
2021-01-16 | 9:47 | 49.919
2021-01-16 | 9:47 | 49.916
2021-01-16 | 9:47 | 49.915
2021-01-16 | 9:47 | 49.914
2021-01-16 | 9:47 | 49.913
2021-01-16 | 9:47 | 49.911
2021-01-16 | 9:47 | 49.91
2021-01-16 | 9:47 | 49.909
2021-01-16 | 9:47 | 49.907
2021-01-16 | 9:47 | 49.907
2021-01-16 | 9:47 | 49.909
2021-01-16 | 9:47 | 49.909
2021-01-16 | 9:47 | 49.908
2021-01-16 | 9:47 | 49.905
2021-01-16 | 9:47 | 49.905
2021-01-16 | 9:47 | 49.903
2021-01-16 | 9:47 | 49.903
2021-01-16 | 9:47 | 49.904
2021-01-16 | 9:47 | 49.903
2021-01-16 | 9:47 | 49.904
2021-01-16 | 9:47 | 49.906
2021-01-16 | 9:47 | 49.91
2021-01-16 | 9:48 | 49.913
2021-01-16 | 9:48 | 49.913
2021-01-16 | 9:48 | 49.915
2021-01-16 | 9:48 | 49.915
2021-01-16 | 9:48 | 49.915
2021-01-16 | 9:48 | 49.915
2021-01-16 | 9:48 | 49.914
2021-01-16 | 9:48 | 49.917
2021-01-16 | 9:48 | 49.917
2021-01-16 | 9:48 | 49.919
2021-01-16 | 9:48 | 49.92
2021-01-16 | 9:48 | 49.919
2021-01-16 | 9:48 | 49.919
2021-01-16 | 9:48 | 49.919
2021-01-16 | 9:48 | 49.918
2021-01-16 | 9:48 | 49.921
2021-01-16 | 9:48 | 49.924
2021-01-16 | 9:48 | 49.928
2021-01-16 | 9:48 | 49.928
2021-01-16 | 9:48 | 49.927
2021-01-16 | 9:48 | 49.925
2021-01-16 | 9:48 | 49.923
2021-01-16 | 9:48 | 49.924
2021-01-16 | 9:48 | 49.924
2021-01-16 | 9:48 | 49.923
2021-01-16 | 9:48 | 49.923
2021-01-16 | 9:48 | 49.923
2021-01-16 | 9:48 | 49.923
2021-01-16 | 9:48 | 49.925
2021-01-16 | 9:48 | 49.926
2021-01-16 | 9:48 | 49.927
2021-01-16 | 9:48 | 49.931
2021-01-16 | 9:48 | 49.924
2021-01-16 | 9:48 | 49.924
2021-01-16 | 9:48 | 49.925
2021-01-16 | 9:48 | 49.924
2021-01-16 | 9:48 | 49.921
2021-01-16 | 9:48 | 49.921
2021-01-16 | 9:48 | 49.92
2021-01-16 | 9:48 | 49.92
2021-01-16 | 9:48 | 49.918
2021-01-16 | 9:48 | 49.919
2021-01-16 | 9:48 | 49.919
2021-01-16 | 9:48 | 49.92
2021-01-16 | 9:48 | 49.92
2021-01-16 | 9:48 | 49.922
2021-01-16 | 9:48 | 49.925
2021-01-16 | 9:48 | 49.926
2021-01-16 | 9:48 | 49.926
2021-01-16 | 9:48 | 49.924
2021-01-16 | 9:48 | 49.925
2021-01-16 | 9:48 | 49.924
2021-01-16 | 9:48 | 49.922
2021-01-16 | 9:48 | 49.921
2021-01-16 | 9:48 | 49.921
2021-01-16 | 9:48 | 49.922
2021-01-16 | 9:48 | 49.919
2021-01-16 | 9:48 | 49.917
2021-01-16 | 9:48 | 49.917
2021-01-16 | 9:48 | 49.919
2021-01-16 | 9:48 | 49.921
2021-01-16 | 9:49 | 49.922
2021-01-16 | 9:49 | 49.926
2021-01-16 | 9:49 | 49.931
2021-01-16 | 9:49 | 49.935
2021-01-16 | 9:49 | 49.936
2021-01-16 | 9:49 | 49.939
2021-01-16 | 9:49 | 49.942
2021-01-16 | 9:49 | 49.945
2021-01-16 | 9:49 | 49.946
2021-01-16 | 9:49 | 49.949
2021-01-16 | 9:49 | 49.948
2021-01-16 | 9:49 | 49.947
2021-01-16 | 9:49 | 49.946
2021-01-16 | 9:49 | 49.947
2021-01-16 | 9:49 | 49.947
2021-01-16 | 9:49 | 49.946
2021-01-16 | 9:49 | 49.944
2021-01-16 | 9:49 | 49.944
2021-01-16 | 9:49 | 49.942
2021-01-16 | 9:49 | 49.942
2021-01-16 | 9:49 | 49.944
2021-01-16 | 9:49 | 49.942
2021-01-16 | 9:49 | 49.945
2021-01-16 | 9:49 | 49.944
2021-01-16 | 9:49 | 49.943
2021-01-16 | 9:49 | 49.942
2021-01-16 | 9:49 | 49.94
2021-01-16 | 9:49 | 49.939
2021-01-16 | 9:49 | 49.939
2021-01-16 | 9:49 | 49.938
2021-01-16 | 9:49 | 49.938
2021-01-16 | 9:49 | 49.94
2021-01-16 | 9:49 | 49.94
2021-01-16 | 9:49 | 49.942
2021-01-16 | 9:49 | 49.943
2021-01-16 | 9:49 | 49.943
2021-01-16 | 9:49 | 49.942
2021-01-16 | 9:49 | 49.942
2021-01-16 | 9:49 | 49.942
2021-01-16 | 9:49 | 49.941
2021-01-16 | 9:49 | 49.942
2021-01-16 | 9:49 | 49.943
2021-01-16 | 9:49 | 49.944
2021-01-16 | 9:49 | 49.944
2021-01-16 | 9:49 | 49.947
2021-01-16 | 9:49 | 49.948
2021-01-16 | 9:49 | 49.948
2021-01-16 | 9:49 | 49.95
2021-01-16 | 9:49 | 49.951
2021-01-16 | 9:49 | 49.95
2021-01-16 | 9:49 | 49.947
2021-01-16 | 9:49 | 49.945
2021-01-16 | 9:49 | 49.943
2021-01-16 | 9:49 | 49.944
2021-01-16 | 9:49 | 49.941
2021-01-16 | 9:49 | 49.941
2021-01-16 | 9:49 | 49.942
2021-01-16 | 9:49 | 49.944
2021-01-16 | 9:49 | 49.943
2021-01-16 | 9:50 | 49.942
2021-01-16 | 9:50 | 49.939
2021-01-16 | 9:50 | 49.939
2021-01-16 | 9:50 | 49.937
2021-01-16 | 9:50 | 49.935
2021-01-16 | 9:50 | 49.936
2021-01-16 | 9:50 | 49.934
2021-01-16 | 9:50 | 49.934
2021-01-16 | 9:50 | 49.933
2021-01-16 | 9:50 | 49.934
2021-01-16 | 9:50 | 49.936
2021-01-16 | 9:50 | 49.937
2021-01-16 | 9:50 | 49.939
2021-01-16 | 9:50 | 49.942
2021-01-16 | 9:50 | 49.943
2021-01-16 | 9:50 | 49.943
2021-01-16 | 9:50 | 49.943
2021-01-16 | 9:50 | 49.941
2021-01-16 | 9:50 | 49.941
2021-01-16 | 9:50 | 49.938
2021-01-16 | 9:50 | 49.936
2021-01-16 | 9:50 | 49.934
2021-01-16 | 9:50 | 49.933
2021-01-16 | 9:50 | 49.933
2021-01-16 | 9:50 | 49.932
2021-01-16 | 9:50 | 49.931
2021-01-16 | 9:50 | 49.93
2021-01-16 | 9:50 | 49.93
2021-01-16 | 9:50 | 49.929
2021-01-16 | 9:50 | 49.929
2021-01-16 | 9:50 | 49.928
2021-01-16 | 9:50 | 49.927
2021-01-16 | 9:50 | 49.927
2021-01-16 | 9:50 | 49.928
2021-01-16 | 9:50 | 49.928
2021-01-16 | 9:50 | 49.929
2021-01-16 | 9:50 | 49.931
2021-01-16 | 9:50 | 49.931
2021-01-16 | 9:50 | 49.933
2021-01-16 | 9:50 | 49.935
2021-01-16 | 9:50 | 49.939
2021-01-16 | 9:50 | 49.94
2021-01-16 | 9:50 | 49.942
2021-01-16 | 9:50 | 49.942
2021-01-16 | 9:50 | 49.939
2021-01-16 | 9:50 | 49.939
2021-01-16 | 9:50 | 49.939
2021-01-16 | 9:50 | 49.939
2021-01-16 | 9:50 | 49.938
2021-01-16 | 9:50 | 49.938
2021-01-16 | 9:50 | 49.938
2021-01-16 | 9:50 | 49.939
2021-01-16 | 9:50 | 49.941
2021-01-16 | 9:50 | 49.945
2021-01-16 | 9:50 | 49.95
2021-01-16 | 9:50 | 49.954
2021-01-16 | 9:50 | 49.955
2021-01-16 | 9:50 | 49.956
2021-01-16 | 9:50 | 49.958
2021-01-16 | 9:50 | 49.96
2021-01-16 | 9:50 | 49.959
2021-01-16 | 9:51 | 49.959
2021-01-16 | 9:51 | 49.96
2021-01-16 | 9:51 | 49.958
2021-01-16 | 9:51 | 49.955
2021-01-16 | 9:51 | 49.952
2021-01-16 | 9:51 | 49.948
2021-01-16 | 9:51 | 49.945
2021-01-16 | 9:51 | 49.94
2021-01-16 | 9:51 | 49.938
2021-01-16 | 9:51 | 49.937
2021-01-16 | 9:51 | 49.939
2021-01-16 | 9:51 | 49.939
2021-01-16 | 9:51 | 49.941
2021-01-16 | 9:51 | 49.946
2021-01-16 | 9:51 | 49.95
2021-01-16 | 9:51 | 49.952
2021-01-16 | 9:51 | 49.954
2021-01-16 | 9:51 | 49.96
2021-01-16 | 9:51 | 49.959
2021-01-16 | 9:51 | 49.96
2021-01-16 | 9:51 | 49.957
2021-01-16 | 9:51 | 49.958
2021-01-16 | 9:51 | 49.956
2021-01-16 | 9:51 | 49.956
2021-01-16 | 9:51 | 49.954
2021-01-16 | 9:51 | 49.953
2021-01-16 | 9:51 | 49.952
2021-01-16 | 9:51 | 49.952
2021-01-16 | 9:51 | 49.953
2021-01-16 | 9:51 | 49.952
2021-01-16 | 9:51 | 49.952
2021-01-16 | 9:51 | 49.953
2021-01-16 | 9:51 | 49.953
2021-01-16 | 9:51 | 49.953
2021-01-16 | 9:51 | 49.956
2021-01-16 | 9:51 | 49.958
2021-01-16 | 9:51 | 49.957
2021-01-16 | 9:51 | 49.957
2021-01-16 | 9:51 | 49.956
2021-01-16 | 9:51 | 49.954
2021-01-16 | 9:51 | 49.954
2021-01-16 | 9:51 | 49.956
2021-01-16 | 9:51 | 49.958
2021-01-16 | 9:51 | 49.96
2021-01-16 | 9:51 | 49.964
2021-01-16 | 9:51 | 49.963
2021-01-16 | 9:51 | 49.963
2021-01-16 | 9:51 | 49.968
2021-01-16 | 9:51 | 49.969
2021-01-16 | 9:51 | 49.972
2021-01-16 | 9:51 | 49.973
2021-01-16 | 9:51 | 49.973
2021-01-16 | 9:51 | 49.974
2021-01-16 | 9:51 | 49.974
2021-01-16 | 9:51 | 49.971
2021-01-16 | 9:51 | 49.969
2021-01-16 | 9:51 | 49.967
2021-01-16 | 9:51 | 49.962
2021-01-16 | 9:51 | 49.959
2021-01-16 | 9:52 | 49.957
2021-01-16 | 9:52 | 49.954
2021-01-16 | 9:52 | 49.954
2021-01-16 | 9:52 | 49.951
2021-01-16 | 9:52 | 49.952
2021-01-16 | 9:52 | 49.951
2021-01-16 | 9:52 | 49.953
2021-01-16 | 9:52 | 49.952
2021-01-16 | 9:52 | 49.952
2021-01-16 | 9:52 | 49.956
2021-01-16 | 9:52 | 49.955
2021-01-16 | 9:52 | 49.956
2021-01-16 | 9:52 | 49.954
2021-01-16 | 9:52 | 49.954
2021-01-16 | 9:52 | 49.953
2021-01-16 | 9:52 | 49.952
2021-01-16 | 9:52 | 49.954
2021-01-16 | 9:52 | 49.954
2021-01-16 | 9:52 | 49.955
2021-01-16 | 9:52 | 49.952
2021-01-16 | 9:52 | 49.951
2021-01-16 | 9:52 | 49.949
2021-01-16 | 9:52 | 49.946
2021-01-16 | 9:52 | 49.947
2021-01-16 | 9:52 | 49.945
2021-01-16 | 9:52 | 49.946
2021-01-16 | 9:52 | 49.945
2021-01-16 | 9:52 | 49.945
2021-01-16 | 9:52 | 49.95
2021-01-16 | 9:52 | 49.954
2021-01-16 | 9:52 | 49.956
2021-01-16 | 9:52 | 49.958
2021-01-16 | 9:52 | 49.958
2021-01-16 | 9:52 | 49.959
2021-01-16 | 9:52 | 49.959
2021-01-16 | 9:52 | 49.957
2021-01-16 | 9:52 | 49.958
2021-01-16 | 9:52 | 49.957
2021-01-16 | 9:52 | 49.954
2021-01-16 | 9:52 | 49.955
2021-01-16 | 9:52 | 49.953
2021-01-16 | 9:52 | 49.952
2021-01-16 | 9:52 | 49.953
2021-01-16 | 9:52 | 49.953
2021-01-16 | 9:52 | 49.952
2021-01-16 | 9:52 | 49.952
2021-01-16 | 9:52 | 49.954
2021-01-16 | 9:52 | 49.953
2021-01-16 | 9:52 | 49.952
2021-01-16 | 9:52 | 49.952
2021-01-16 | 9:52 | 49.949
2021-01-16 | 9:52 | 49.948
2021-01-16 | 9:52 | 49.946
2021-01-16 | 9:52 | 49.945
2021-01-16 | 9:52 | 49.947
2021-01-16 | 9:52 | 49.947
2021-01-16 | 9:52 | 49.945
2021-01-16 | 9:52 | 49.945
2021-01-16 | 9:52 | 49.947
2021-01-16 | 9:52 | 49.947
2021-01-16 | 9:52 | 49.952
2021-01-16 | 9:53 | 49.959
2021-01-16 | 9:53 | 49.964
2021-01-16 | 9:53 | 49.969
2021-01-16 | 9:53 | 49.972
2021-01-16 | 9:53 | 49.975
2021-01-16 | 9:53 | 49.981
2021-01-16 | 9:53 | 49.986
2021-01-16 | 9:53 | 49.988
2021-01-16 | 9:53 | 49.987
2021-01-16 | 9:53 | 49.987
2021-01-16 | 9:53 | 49.986
2021-01-16 | 9:53 | 49.985
2021-01-16 | 9:53 | 49.986
2021-01-16 | 9:53 | 49.985
2021-01-16 | 9:53 | 49.984
2021-01-16 | 9:53 | 49.984
2021-01-16 | 9:53 | 49.984
2021-01-16 | 9:53 | 49.987
2021-01-16 | 9:53 | 49.989
2021-01-16 | 9:53 | 49.989
2021-01-16 | 9:53 | 49.99
2021-01-16 | 9:53 | 49.992
2021-01-16 | 9:53 | 49.992
2021-01-16 | 9:53 | 49.992
2021-01-16 | 9:53 | 49.995
2021-01-16 | 9:53 | 49.996
2021-01-16 | 9:53 | 49.997
2021-01-16 | 9:53 | 49.999
2021-01-16 | 9:53 | 50
2021-01-16 | 9:53 | 50.003
2021-01-16 | 9:53 | 50.006
2021-01-16 | 9:53 | 50.008
2021-01-16 | 9:53 | 50.011
2021-01-16 | 9:53 | 50.014
2021-01-16 | 9:53 | 50.015
2021-01-16 | 9:53 | 50.017
2021-01-16 | 9:53 | 50.018
2021-01-16 | 9:53 | 50.018
2021-01-16 | 9:53 | 50.017
2021-01-16 | 9:53 | 50.017
2021-01-16 | 9:53 | 50.014
2021-01-16 | 9:53 | 50.013
2021-01-16 | 9:53 | 50.013
2021-01-16 | 9:53 | 50.012
2021-01-16 | 9:53 | 50.011
2021-01-16 | 9:53 | 50.011
2021-01-16 | 9:53 | 50.008
2021-01-16 | 9:53 | 50.006
2021-01-16 | 9:53 | 50.004
2021-01-16 | 9:53 | 50.001
2021-01-16 | 9:53 | 50.001
2021-01-16 | 9:53 | 50.001
2021-01-16 | 9:53 | 49.998
2021-01-16 | 9:53 | 49.997
2021-01-16 | 9:53 | 49.996
2021-01-16 | 9:53 | 49.991
2021-01-16 | 9:53 | 49.988
2021-01-16 | 9:53 | 49.986
2021-01-16 | 9:53 | 49.984
2021-01-16 | 9:54 | 49.983
2021-01-16 | 9:54 | 49.983
2021-01-16 | 9:54 | 49.984
2021-01-16 | 9:54 | 49.989
2021-01-16 | 9:54 | 49.991
2021-01-16 | 9:54 | 49.994
2021-01-16 | 9:54 | 49.999
2021-01-16 | 9:54 | 50.004
2021-01-16 | 9:54 | 50.009
2021-01-16 | 9:54 | 50.014
2021-01-16 | 9:54 | 50.014
2021-01-16 | 9:54 | 50.013
2021-01-16 | 9:54 | 50.009
2021-01-16 | 9:54 | 50.008
2021-01-16 | 9:54 | 50.007
2021-01-16 | 9:54 | 50.006
2021-01-16 | 9:54 | 50.002
2021-01-16 | 9:54 | 50
2021-01-16 | 9:54 | 49.998
2021-01-16 | 9:54 | 49.996
2021-01-16 | 9:54 | 49.994
2021-01-16 | 9:54 | 49.994
2021-01-16 | 9:54 | 49.992
2021-01-16 | 9:54 | 49.995
2021-01-16 | 9:54 | 49.998
2021-01-16 | 9:54 | 49.996
2021-01-16 | 9:54 | 49.995
2021-01-16 | 9:54 | 49.997
2021-01-16 | 9:54 | 49.994
2021-01-16 | 9:54 | 49.995
2021-01-16 | 9:54 | 49.995
2021-01-16 | 9:54 | 49.993
2021-01-16 | 9:54 | 49.992
2021-01-16 | 9:54 | 49.993
2021-01-16 | 9:54 | 49.993
2021-01-16 | 9:54 | 49.995
2021-01-16 | 9:54 | 49.997
2021-01-16 | 9:54 | 49.997
2021-01-16 | 9:54 | 49.996
2021-01-16 | 9:54 | 49.998
2021-01-16 | 9:54 | 49.999
2021-01-16 | 9:54 | 49.997
2021-01-16 | 9:54 | 49.997
2021-01-16 | 9:54 | 49.998
2021-01-16 | 9:54 | 49.998
2021-01-16 | 9:54 | 49.999
2021-01-16 | 9:54 | 50
2021-01-16 | 9:54 | 50.002
2021-01-16 | 9:54 | 50.001
2021-01-16 | 9:54 | 50.001
2021-01-16 | 9:54 | 49.999
2021-01-16 | 9:54 | 49.997
2021-01-16 | 9:54 | 49.995
2021-01-16 | 9:54 | 49.992
2021-01-16 | 9:54 | 49.989
2021-01-16 | 9:54 | 49.989
2021-01-16 | 9:54 | 49.986
2021-01-16 | 9:54 | 49.984
2021-01-16 | 9:54 | 49.983
2021-01-16 | 9:54 | 49.982
2021-01-16 | 9:54 | 49.981
2021-01-16 | 9:55 | 49.978
2021-01-16 | 9:55 | 49.975
2021-01-16 | 9:55 | 49.975
2021-01-16 | 9:55 | 49.977
2021-01-16 | 9:55 | 49.982
2021-01-16 | 9:55 | 49.984
2021-01-16 | 9:55 | 49.986
2021-01-16 | 9:55 | 49.988
2021-01-16 | 9:55 | 49.99
2021-01-16 | 9:55 | 49.989
2021-01-16 | 9:55 | 49.991
2021-01-16 | 9:55 | 49.988
2021-01-16 | 9:55 | 49.984
2021-01-16 | 9:55 | 49.981
2021-01-16 | 9:55 | 49.978
2021-01-16 | 9:55 | 49.977
2021-01-16 | 9:55 | 49.978
2021-01-16 | 9:55 | 49.976
2021-01-16 | 9:55 | 49.976
2021-01-16 | 9:55 | 49.977
2021-01-16 | 9:55 | 49.978
2021-01-16 | 9:55 | 49.981
2021-01-16 | 9:55 | 49.984
2021-01-16 | 9:55 | 49.987
2021-01-16 | 9:55 | 49.992
2021-01-16 | 9:55 | 49.996
2021-01-16 | 9:55 | 49.998
2021-01-16 | 9:55 | 50.002
2021-01-16 | 9:55 | 50.006
2021-01-16 | 9:55 | 50.009
2021-01-16 | 9:55 | 50.011
2021-01-16 | 9:55 | 50.013
2021-01-16 | 9:55 | 50.013
2021-01-16 | 9:55 | 50.015
2021-01-16 | 9:55 | 50.015
2021-01-16 | 9:55 | 50.016
2021-01-16 | 9:55 | 50.015
2021-01-16 | 9:55 | 50.012
2021-01-16 | 9:55 | 50.008
2021-01-16 | 9:55 | 50.008
2021-01-16 | 9:55 | 50.007
2021-01-16 | 9:55 | 50.005
2021-01-16 | 9:55 | 50.003
2021-01-16 | 9:55 | 50.001
2021-01-16 | 9:55 | 49.999
2021-01-16 | 9:55 | 49.998
2021-01-16 | 9:55 | 49.995
2021-01-16 | 9:55 | 49.992
2021-01-16 | 9:55 | 49.991
2021-01-16 | 9:55 | 49.989
2021-01-16 | 9:55 | 49.99
2021-01-16 | 9:55 | 49.99
2021-01-16 | 9:55 | 49.99
2021-01-16 | 9:55 | 49.99
2021-01-16 | 9:55 | 49.991
2021-01-16 | 9:55 | 49.989
2021-01-16 | 9:55 | 49.987
2021-01-16 | 9:55 | 49.986
2021-01-16 | 9:55 | 49.986
2021-01-16 | 9:56 | 49.987
2021-01-16 | 9:56 | 49.985
2021-01-16 | 9:56 | 49.982
2021-01-16 | 9:56 | 49.979
2021-01-16 | 9:56 | 49.979
2021-01-16 | 9:56 | 49.977
2021-01-16 | 9:56 | 49.976
2021-01-16 | 9:56 | 49.976
2021-01-16 | 9:56 | 49.977
2021-01-16 | 9:56 | 49.975
2021-01-16 | 9:56 | 49.974
2021-01-16 | 9:56 | 49.973
2021-01-16 | 9:56 | 49.971
2021-01-16 | 9:56 | 49.971
2021-01-16 | 9:56 | 49.972
2021-01-16 | 9:56 | 49.972
2021-01-16 | 9:56 | 49.974
2021-01-16 | 9:56 | 49.971
2021-01-16 | 9:56 | 49.97
2021-01-16 | 9:56 | 49.972
2021-01-16 | 9:56 | 49.971
2021-01-16 | 9:56 | 49.97
2021-01-16 | 9:56 | 49.966
2021-01-16 | 9:56 | 49.967
2021-01-16 | 9:56 | 49.967
2021-01-16 | 9:56 | 49.968
2021-01-16 | 9:56 | 49.97
2021-01-16 | 9:56 | 49.974
2021-01-16 | 9:56 | 49.978
2021-01-16 | 9:56 | 49.978
2021-01-16 | 9:56 | 49.98
2021-01-16 | 9:56 | 49.976
2021-01-16 | 9:56 | 49.973
2021-01-16 | 9:56 | 49.971
2021-01-16 | 9:56 | 49.971
2021-01-16 | 9:56 | 49.969
2021-01-16 | 9:56 | 49.968
2021-01-16 | 9:56 | 49.967
2021-01-16 | 9:56 | 49.971
2021-01-16 | 9:56 | 49.972
2021-01-16 | 9:56 | 49.973
2021-01-16 | 9:56 | 49.978
2021-01-16 | 9:56 | 49.98
2021-01-16 | 9:56 | 49.979
2021-01-16 | 9:56 | 49.978
2021-01-16 | 9:56 | 49.974
2021-01-16 | 9:56 | 49.967
2021-01-16 | 9:56 | 49.963
2021-01-16 | 9:56 | 49.962
2021-01-16 | 9:56 | 49.96
2021-01-16 | 9:56 | 49.957
2021-01-16 | 9:56 | 49.956
2021-01-16 | 9:56 | 49.955
2021-01-16 | 9:56 | 49.953
2021-01-16 | 9:56 | 49.954
2021-01-16 | 9:56 | 49.957
2021-01-16 | 9:56 | 49.955
2021-01-16 | 9:56 | 49.954
2021-01-16 | 9:56 | 49.958
2021-01-16 | 9:56 | 49.962
2021-01-16 | 9:56 | 49.964
2021-01-16 | 9:57 | 49.967
2021-01-16 | 9:57 | 49.968
2021-01-16 | 9:57 | 49.968
2021-01-16 | 9:57 | 49.966
2021-01-16 | 9:57 | 49.965
2021-01-16 | 9:57 | 49.962
2021-01-16 | 9:57 | 49.958
2021-01-16 | 9:57 | 49.957
2021-01-16 | 9:57 | 49.957
2021-01-16 | 9:57 | 49.958
2021-01-16 | 9:57 | 49.964
2021-01-16 | 9:57 | 49.967
2021-01-16 | 9:57 | 49.971
2021-01-16 | 9:57 | 49.975
2021-01-16 | 9:57 | 49.976
2021-01-16 | 9:57 | 49.979
2021-01-16 | 9:57 | 49.979
2021-01-16 | 9:57 | 49.979
2021-01-16 | 9:57 | 49.977
2021-01-16 | 9:57 | 49.98
2021-01-16 | 9:57 | 49.979
2021-01-16 | 9:57 | 49.982
2021-01-16 | 9:57 | 49.984
2021-01-16 | 9:57 | 49.987
2021-01-16 | 9:57 | 49.99
2021-01-16 | 9:57 | 49.998
2021-01-16 | 9:57 | 50.002
2021-01-16 | 9:57 | 50.004
2021-01-16 | 9:57 | 50.008
2021-01-16 | 9:57 | 50.01
2021-01-16 | 9:57 | 50.008
2021-01-16 | 9:57 | 50.009
2021-01-16 | 9:57 | 50.01
2021-01-16 | 9:57 | 50.013
2021-01-16 | 9:57 | 50.016
2021-01-16 | 9:57 | 50.019
2021-01-16 | 9:57 | 50.018
2021-01-16 | 9:57 | 50.017
2021-01-16 | 9:57 | 50.018
2021-01-16 | 9:57 | 50.014
2021-01-16 | 9:57 | 50.013
2021-01-16 | 9:57 | 50.01
2021-01-16 | 9:57 | 50.007
2021-01-16 | 9:57 | 50.005
2021-01-16 | 9:57 | 50.006
2021-01-16 | 9:57 | 50.005
2021-01-16 | 9:57 | 50.002
2021-01-16 | 9:57 | 50.003
2021-01-16 | 9:57 | 50.002
2021-01-16 | 9:57 | 50.002
2021-01-16 | 9:57 | 50.001
2021-01-16 | 9:57 | 50
2021-01-16 | 9:57 | 49.998
2021-01-16 | 9:57 | 49.997
2021-01-16 | 9:57 | 49.995
2021-01-16 | 9:57 | 49.991
2021-01-16 | 9:57 | 49.988
2021-01-16 | 9:57 | 49.987
2021-01-16 | 9:57 | 49.987
2021-01-16 | 9:58 | 49.989
2021-01-16 | 9:58 | 49.99
2021-01-16 | 9:58 | 49.99
2021-01-16 | 9:58 | 49.99
2021-01-16 | 9:58 | 49.989
2021-01-16 | 9:58 | 49.987
2021-01-16 | 9:58 | 49.99
2021-01-16 | 9:58 | 49.992
2021-01-16 | 9:58 | 49.994
2021-01-16 | 9:58 | 49.997
2021-01-16 | 9:58 | 50
2021-01-16 | 9:58 | 50
2021-01-16 | 9:58 | 50
2021-01-16 | 9:58 | 49.998
2021-01-16 | 9:58 | 49.996
2021-01-16 | 9:58 | 49.995
2021-01-16 | 9:58 | 49.992
2021-01-16 | 9:58 | 49.99
2021-01-16 | 9:58 | 49.991
2021-01-16 | 9:58 | 49.995
2021-01-16 | 9:58 | 49.999
2021-01-16 | 9:58 | 50
2021-01-16 | 9:58 | 50.003
2021-01-16 | 9:58 | 50.002
2021-01-16 | 9:58 | 50
2021-01-16 | 9:58 | 49.998
2021-01-16 | 9:58 | 49.994
2021-01-16 | 9:58 | 49.992
2021-01-16 | 9:58 | 49.992
2021-01-16 | 9:58 | 49.989
2021-01-16 | 9:58 | 49.987
2021-01-16 | 9:58 | 49.984
2021-01-16 | 9:58 | 49.982
2021-01-16 | 9:58 | 49.982
2021-01-16 | 9:58 | 49.982
2021-01-16 | 9:58 | 49.978
2021-01-16 | 9:58 | 49.977
2021-01-16 | 9:58 | 49.976
2021-01-16 | 9:58 | 49.974
2021-01-16 | 9:58 | 49.976
2021-01-16 | 9:58 | 49.976
2021-01-16 | 9:58 | 49.973
2021-01-16 | 9:58 | 49.972
2021-01-16 | 9:58 | 49.97
2021-01-16 | 9:58 | 49.966
2021-01-16 | 9:58 | 49.965
2021-01-16 | 9:58 | 49.963
2021-01-16 | 9:58 | 49.958
2021-01-16 | 9:58 | 49.956
2021-01-16 | 9:58 | 49.954
2021-01-16 | 9:58 | 49.951
2021-01-16 | 9:58 | 49.95
2021-01-16 | 9:58 | 49.945
2021-01-16 | 9:58 | 49.941
2021-01-16 | 9:58 | 49.94
2021-01-16 | 9:58 | 49.939
2021-01-16 | 9:58 | 49.94
2021-01-16 | 9:58 | 49.939
2021-01-16 | 9:58 | 49.94
2021-01-16 | 9:58 | 49.94
2021-01-16 | 9:58 | 49.936
2021-01-16 | 9:59 | 49.937
2021-01-16 | 9:59 | 49.937
2021-01-16 | 9:59 | 49.936
2021-01-16 | 9:59 | 49.935
2021-01-16 | 9:59 | 49.933
2021-01-16 | 9:59 | 49.93
2021-01-16 | 9:59 | 49.928
2021-01-16 | 9:59 | 49.926
2021-01-16 | 9:59 | 49.923
2021-01-16 | 9:59 | 49.924
2021-01-16 | 9:59 | 49.92
2021-01-16 | 9:59 | 49.92
2021-01-16 | 9:59 | 49.921
2021-01-16 | 9:59 | 49.92
2021-01-16 | 9:59 | 49.921
2021-01-16 | 9:59 | 49.922
2021-01-16 | 9:59 | 49.919
2021-01-16 | 9:59 | 49.918
2021-01-16 | 9:59 | 49.915
2021-01-16 | 9:59 | 49.912
2021-01-16 | 9:59 | 49.908
2021-01-16 | 9:59 | 49.903
2021-01-16 | 9:59 | 49.899
2021-01-16 | 9:59 | 49.897
2021-01-16 | 9:59 | 49.897
2021-01-16 | 9:59 | 49.896
2021-01-16 | 9:59 | 49.899
2021-01-16 | 9:59 | 49.897
2021-01-16 | 9:59 | 49.899
2021-01-16 | 9:59 | 49.9
2021-01-16 | 9:59 | 49.899
2021-01-16 | 9:59 | 49.901
2021-01-16 | 9:59 | 49.903
2021-01-16 | 9:59 | 49.905
2021-01-16 | 9:59 | 49.908
2021-01-16 | 9:59 | 49.906
2021-01-16 | 9:59 | 49.909
2021-01-16 | 9:59 | 49.912
2021-01-16 | 9:59 | 49.912
2021-01-16 | 9:59 | 49.913
2021-01-16 | 9:59 | 49.915
2021-01-16 | 9:59 | 49.915
2021-01-16 | 9:59 | 49.916
2021-01-16 | 9:59 | 49.916
2021-01-16 | 9:59 | 49.913
2021-01-16 | 9:59 | 49.915
2021-01-16 | 9:59 | 49.914
2021-01-16 | 9:59 | 49.912
2021-01-16 | 9:59 | 49.911
2021-01-16 | 9:59 | 49.911
2021-01-16 | 9:59 | 49.909
2021-01-16 | 9:59 | 49.91
2021-01-16 | 9:59 | 49.911
2021-01-16 | 9:59 | 49.911
2021-01-16 | 9:59 | 49.91
2021-01-16 | 9:59 | 49.908
2021-01-16 | 9:59 | 49.906
2021-01-16 | 9:59 | 49.906
2021-01-16 | 9:59 | 49.907
2021-01-16 | 10:00 | 49.906
2021-01-16 | 10:00 | 49.906
2021-01-16 | 10:00 | 49.908
2021-01-16 | 10:00 | 49.908
2021-01-16 | 10:00 | 49.908
2021-01-16 | 10:00 | 49.906
2021-01-16 | 10:00 | 49.904
2021-01-16 | 10:00 | 49.902
2021-01-16 | 10:00 | 49.901
2021-01-16 | 10:00 | 49.9
2021-01-16 | 10:00 | 49.903
2021-01-16 | 10:00 | 49.904
2021-01-16 | 10:00 | 49.906
2021-01-16 | 10:00 | 49.907
2021-01-16 | 10:00 | 49.909
2021-01-16 | 10:00 | 49.909
2021-01-16 | 10:00 | 49.907
2021-01-16 | 10:00 | 49.905
2021-01-16 | 10:00 | 49.904
2021-01-16 | 10:00 | 49.902
2021-01-16 | 10:00 | 49.903
2021-01-16 | 10:00 | 49.904
2021-01-16 | 10:00 | 49.904
2021-01-16 | 10:00 | 49.904
2021-01-16 | 10:00 | 49.907
2021-01-16 | 10:00 | 49.906
2021-01-16 | 10:00 | 49.905
2021-01-16 | 10:00 | 49.903
2021-01-16 | 10:00 | 49.9
2021-01-16 | 10:00 | 49.897
2021-01-16 | 10:00 | 49.893
2021-01-16 | 10:00 | 49.887
2021-01-16 | 10:00 | 49.879
2021-01-16 | 10:00 | 49.87
2021-01-16 | 10:00 | 49.866
2021-01-16 | 10:00 | 49.86
2021-01-16 | 10:00 | 49.857
2021-01-16 | 10:00 | 49.86
2021-01-16 | 10:00 | 49.857
2021-01-16 | 10:00 | 49.859
2021-01-16 | 10:00 | 49.858
2021-01-16 | 10:00 | 49.861
2021-01-16 | 10:00 | 49.865
2021-01-16 | 10:00 | 49.865
2021-01-16 | 10:00 | 49.864
2021-01-16 | 10:00 | 49.863
2021-01-16 | 10:00 | 49.861
2021-01-16 | 10:00 | 49.859
2021-01-16 | 10:00 | 49.857
2021-01-16 | 10:00 | 49.855
2021-01-16 | 10:00 | 49.852
2021-01-16 | 10:00 | 49.854
2021-01-16 | 10:00 | 49.856
2021-01-16 | 10:00 | 49.854
2021-01-16 | 10:00 | 49.856
2021-01-16 | 10:00 | 49.855
2021-01-16 | 10:00 | 49.856
2021-01-16 | 10:00 | 49.858
2021-01-16 | 10:00 | 49.857
2021-01-16 | 10:00 | 49.857
2021-01-16 | 10:00 | 49.857
2021-01-16 | 10:01 | 49.855
2021-01-16 | 10:01 | 49.852
2021-01-16 | 10:01 | 49.85
2021-01-16 | 10:01 | 49.848
2021-01-16 | 10:01 | 49.846
2021-01-16 | 10:01 | 49.842
2021-01-16 | 10:01 | 49.837
2021-01-16 | 10:01 | 49.836
2021-01-16 | 10:01 | 49.834
2021-01-16 | 10:01 | 49.831
2021-01-16 | 10:01 | 49.832
2021-01-16 | 10:01 | 49.837
2021-01-16 | 10:01 | 49.841
2021-01-16 | 10:01 | 49.844
2021-01-16 | 10:01 | 49.848
2021-01-16 | 10:01 | 49.849
2021-01-16 | 10:01 | 49.849
2021-01-16 | 10:01 | 49.85
2021-01-16 | 10:01 | 49.853
2021-01-16 | 10:01 | 49.854
2021-01-16 | 10:01 | 49.85
2021-01-16 | 10:01 | 49.847
2021-01-16 | 10:01 | 49.844
2021-01-16 | 10:01 | 49.841
2021-01-16 | 10:01 | 49.841
2021-01-16 | 10:01 | 49.842
2021-01-16 | 10:01 | 49.841
2021-01-16 | 10:01 | 49.84
2021-01-16 | 10:01 | 49.841
2021-01-16 | 10:01 | 49.846
2021-01-16 | 10:01 | 49.848
2021-01-16 | 10:01 | 49.851
2021-01-16 | 10:01 | 49.853
2021-01-16 | 10:01 | 49.856
2021-01-16 | 10:01 | 49.857
2021-01-16 | 10:01 | 49.86
2021-01-16 | 10:01 | 49.864
2021-01-16 | 10:01 | 49.865
2021-01-16 | 10:01 | 49.869
2021-01-16 | 10:01 | 49.872
2021-01-16 | 10:01 | 49.873
2021-01-16 | 10:01 | 49.873
2021-01-16 | 10:01 | 49.872
2021-01-16 | 10:01 | 49.872
2021-01-16 | 10:01 | 49.874
2021-01-16 | 10:01 | 49.874
2021-01-16 | 10:01 | 49.871
2021-01-16 | 10:01 | 49.869
2021-01-16 | 10:01 | 49.869
2021-01-16 | 10:01 | 49.866
2021-01-16 | 10:01 | 49.864
2021-01-16 | 10:01 | 49.863
2021-01-16 | 10:01 | 49.864
2021-01-16 | 10:01 | 49.863
2021-01-16 | 10:01 | 49.863
2021-01-16 | 10:01 | 49.862
2021-01-16 | 10:01 | 49.861
2021-01-16 | 10:01 | 49.859
2021-01-16 | 10:01 | 49.859
2021-01-16 | 10:02 | 49.858
2021-01-16 | 10:02 | 49.855
2021-01-16 | 10:02 | 49.854
2021-01-16 | 10:02 | 49.851
2021-01-16 | 10:02 | 49.848
2021-01-16 | 10:02 | 49.848
2021-01-16 | 10:02 | 49.846
2021-01-16 | 10:02 | 49.845
2021-01-16 | 10:02 | 49.847
2021-01-16 | 10:02 | 49.847
2021-01-16 | 10:02 | 49.848
2021-01-16 | 10:02 | 49.849
2021-01-16 | 10:02 | 49.847
2021-01-16 | 10:02 | 49.847
2021-01-16 | 10:02 | 49.851
2021-01-16 | 10:02 | 49.853
2021-01-16 | 10:02 | 49.855
2021-01-16 | 10:02 | 49.857
2021-01-16 | 10:02 | 49.858
2021-01-16 | 10:02 | 49.86
2021-01-16 | 10:02 | 49.862
2021-01-16 | 10:02 | 49.866
2021-01-16 | 10:02 | 49.863
2021-01-16 | 10:02 | 49.861
2021-01-16 | 10:02 | 49.861
2021-01-16 | 10:02 | 49.861
2021-01-16 | 10:02 | 49.857
2021-01-16 | 10:02 | 49.859
2021-01-16 | 10:02 | 49.86
2021-01-16 | 10:02 | 49.863
2021-01-16 | 10:02 | 49.865
2021-01-16 | 10:02 | 49.864
2021-01-16 | 10:02 | 49.865
2021-01-16 | 10:02 | 49.864
2021-01-16 | 10:02 | 49.866
2021-01-16 | 10:02 | 49.864
2021-01-16 | 10:02 | 49.862
2021-01-16 | 10:02 | 49.863
2021-01-16 | 10:02 | 49.861
2021-01-16 | 10:02 | 49.865
2021-01-16 | 10:02 | 49.865
2021-01-16 | 10:02 | 49.867
2021-01-16 | 10:02 | 49.867
2021-01-16 | 10:02 | 49.868
2021-01-16 | 10:02 | 49.868
2021-01-16 | 10:02 | 49.872
2021-01-16 | 10:02 | 49.875
2021-01-16 | 10:02 | 49.877
2021-01-16 | 10:02 | 49.878
2021-01-16 | 10:02 | 49.877
2021-01-16 | 10:02 | 49.877
2021-01-16 | 10:02 | 49.879
2021-01-16 | 10:02 | 49.881
2021-01-16 | 10:02 | 49.882
2021-01-16 | 10:02 | 49.885
2021-01-16 | 10:02 | 49.886
2021-01-16 | 10:02 | 49.891
2021-01-16 | 10:02 | 49.892
2021-01-16 | 10:02 | 49.895
2021-01-16 | 10:02 | 49.898
2021-01-16 | 10:02 | 49.901
2021-01-16 | 10:03 | 49.907
2021-01-16 | 10:03 | 49.911
2021-01-16 | 10:03 | 49.917
2021-01-16 | 10:03 | 49.92
2021-01-16 | 10:03 | 49.924
2021-01-16 | 10:03 | 49.927
2021-01-16 | 10:03 | 49.931
2021-01-16 | 10:03 | 49.937
2021-01-16 | 10:03 | 49.941
2021-01-16 | 10:03 | 49.944
2021-01-16 | 10:03 | 49.945
2021-01-16 | 10:03 | 49.945
2021-01-16 | 10:03 | 49.949
2021-01-16 | 10:03 | 49.949
2021-01-16 | 10:03 | 49.951
2021-01-16 | 10:03 | 49.953
2021-01-16 | 10:03 | 49.953
2021-01-16 | 10:03 | 49.952
2021-01-16 | 10:03 | 49.949
2021-01-16 | 10:03 | 49.948
2021-01-16 | 10:03 | 49.949
2021-01-16 | 10:03 | 49.951
2021-01-16 | 10:03 | 49.953
2021-01-16 | 10:03 | 49.957
2021-01-16 | 10:03 | 49.959
2021-01-16 | 10:03 | 49.963
2021-01-16 | 10:03 | 49.964
2021-01-16 | 10:03 | 49.964
2021-01-16 | 10:03 | 49.964
2021-01-16 | 10:03 | 49.961
2021-01-16 | 10:03 | 49.96
2021-01-16 | 10:03 | 49.957
2021-01-16 | 10:03 | 49.955
2021-01-16 | 10:03 | 49.954
2021-01-16 | 10:03 | 49.951
2021-01-16 | 10:03 | 49.947
2021-01-16 | 10:03 | 49.944
2021-01-16 | 10:03 | 49.944
2021-01-16 | 10:03 | 49.943
2021-01-16 | 10:03 | 49.946
2021-01-16 | 10:03 | 49.945
2021-01-16 | 10:03 | 49.943
2021-01-16 | 10:03 | 49.944
2021-01-16 | 10:03 | 49.944
2021-01-16 | 10:03 | 49.943
2021-01-16 | 10:03 | 49.944
2021-01-16 | 10:03 | 49.944
2021-01-16 | 10:03 | 49.944
2021-01-16 | 10:03 | 49.947
2021-01-16 | 10:03 | 49.945
2021-01-16 | 10:03 | 49.949
2021-01-16 | 10:03 | 49.948
2021-01-16 | 10:03 | 49.951
2021-01-16 | 10:03 | 49.952
2021-01-16 | 10:03 | 49.951
2021-01-16 | 10:03 | 49.952
2021-01-16 | 10:03 | 49.952
2021-01-16 | 10:03 | 49.951
2021-01-16 | 10:03 | 49.952
2021-01-16 | 10:04 | 49.953
2021-01-16 | 10:04 | 49.953
2021-01-16 | 10:04 | 49.95
2021-01-16 | 10:04 | 49.95
2021-01-16 | 10:04 | 49.948
2021-01-16 | 10:04 | 49.949
2021-01-16 | 10:04 | 49.947
2021-01-16 | 10:04 | 49.946
2021-01-16 | 10:04 | 49.947
2021-01-16 | 10:04 | 49.946
2021-01-16 | 10:04 | 49.948
2021-01-16 | 10:04 | 49.945
2021-01-16 | 10:04 | 49.946
2021-01-16 | 10:04 | 49.945
2021-01-16 | 10:04 | 49.946
2021-01-16 | 10:04 | 49.946
2021-01-16 | 10:04 | 49.948
2021-01-16 | 10:04 | 49.948
2021-01-16 | 10:04 | 49.95
2021-01-16 | 10:04 | 49.949
2021-01-16 | 10:04 | 49.952
2021-01-16 | 10:04 | 49.952
2021-01-16 | 10:04 | 49.956
2021-01-16 | 10:04 | 49.957
2021-01-16 | 10:04 | 49.961
2021-01-16 | 10:04 | 49.963
2021-01-16 | 10:04 | 49.965
2021-01-16 | 10:04 | 49.968
2021-01-16 | 10:04 | 49.971
2021-01-16 | 10:04 | 49.973
2021-01-16 | 10:04 | 49.972
2021-01-16 | 10:04 | 49.973
2021-01-16 | 10:04 | 49.972
2021-01-16 | 10:04 | 49.974
2021-01-16 | 10:04 | 49.973
2021-01-16 | 10:04 | 49.973
2021-01-16 | 10:04 | 49.97
2021-01-16 | 10:04 | 49.969
2021-01-16 | 10:04 | 49.967
2021-01-16 | 10:04 | 49.967
2021-01-16 | 10:04 | 49.965
2021-01-16 | 10:04 | 49.966
2021-01-16 | 10:04 | 49.965
2021-01-16 | 10:04 | 49.965
2021-01-16 | 10:04 | 49.963
2021-01-16 | 10:04 | 49.964
2021-01-16 | 10:04 | 49.963
2021-01-16 | 10:04 | 49.963
2021-01-16 | 10:04 | 49.963
2021-01-16 | 10:04 | 49.964
2021-01-16 | 10:04 | 49.964
2021-01-16 | 10:04 | 49.964
2021-01-16 | 10:04 | 49.964
2021-01-16 | 10:04 | 49.963
2021-01-16 | 10:04 | 49.963
2021-01-16 | 10:04 | 49.961
2021-01-16 | 10:04 | 49.96
2021-01-16 | 10:04 | 49.96
2021-01-16 | 10:04 | 49.96
2021-01-16 | 10:04 | 49.959
2021-01-16 | 10:04 | 49.959
2021-01-16 | 10:05 | 49.958
2021-01-16 | 10:05 | 49.961
2021-01-16 | 10:05 | 49.961
2021-01-16 | 10:05 | 49.962
2021-01-16 | 10:05 | 49.96
2021-01-16 | 10:05 | 49.958
2021-01-16 | 10:05 | 49.955
2021-01-16 | 10:05 | 49.953
2021-01-16 | 10:05 | 49.952
2021-01-16 | 10:05 | 49.951
2021-01-16 | 10:05 | 49.952
2021-01-16 | 10:05 | 49.946
2021-01-16 | 10:05 | 49.945
2021-01-16 | 10:05 | 49.945
2021-01-16 | 10:05 | 49.948
2021-01-16 | 10:05 | 49.951
2021-01-16 | 10:05 | 49.951
2021-01-16 | 10:05 | 49.953
2021-01-16 | 10:05 | 49.955
2021-01-16 | 10:05 | 49.955
2021-01-16 | 10:05 | 49.953
2021-01-16 | 10:05 | 49.952
2021-01-16 | 10:05 | 49.948
2021-01-16 | 10:05 | 49.943
2021-01-16 | 10:05 | 49.943
2021-01-16 | 10:05 | 49.941
2021-01-16 | 10:05 | 49.942
2021-01-16 | 10:05 | 49.94
2021-01-16 | 10:05 | 49.941
2021-01-16 | 10:05 | 49.942
2021-01-16 | 10:05 | 49.942
2021-01-16 | 10:05 | 49.945
2021-01-16 | 10:05 | 49.949
2021-01-16 | 10:05 | 49.954
2021-01-16 | 10:05 | 49.953
2021-01-16 | 10:05 | 49.952
2021-01-16 | 10:05 | 49.951
2021-01-16 | 10:05 | 49.95
2021-01-16 | 10:05 | 49.948
2021-01-16 | 10:05 | 49.946
2021-01-16 | 10:05 | 49.945
2021-01-16 | 10:05 | 49.943
2021-01-16 | 10:05 | 49.943
2021-01-16 | 10:05 | 49.941
2021-01-16 | 10:05 | 49.943
2021-01-16 | 10:05 | 49.945
2021-01-16 | 10:05 | 49.948
2021-01-16 | 10:05 | 49.952
2021-01-16 | 10:05 | 49.954
2021-01-16 | 10:05 | 49.957
2021-01-16 | 10:05 | 49.959
2021-01-16 | 10:05 | 49.96
2021-01-16 | 10:05 | 49.961
2021-01-16 | 10:05 | 49.961
2021-01-16 | 10:05 | 49.959
2021-01-16 | 10:05 | 49.962
2021-01-16 | 10:05 | 49.963
2021-01-16 | 10:05 | 49.963
2021-01-16 | 10:05 | 49.962
2021-01-16 | 10:06 | 49.96
2021-01-16 | 10:06 | 49.955
2021-01-16 | 10:06 | 49.954
2021-01-16 | 10:06 | 49.95
2021-01-16 | 10:06 | 49.945
2021-01-16 | 10:06 | 49.94
2021-01-16 | 10:06 | 49.933
2021-01-16 | 10:06 | 49.93
2021-01-16 | 10:06 | 49.925
2021-01-16 | 10:06 | 49.923
2021-01-16 | 10:06 | 49.921
2021-01-16 | 10:06 | 49.918
2021-01-16 | 10:06 | 49.918
2021-01-16 | 10:06 | 49.916
2021-01-16 | 10:06 | 49.918
2021-01-16 | 10:06 | 49.917
2021-01-16 | 10:06 | 49.918
2021-01-16 | 10:06 | 49.918
2021-01-16 | 10:06 | 49.921
2021-01-16 | 10:06 | 49.919
2021-01-16 | 10:06 | 49.919
2021-01-16 | 10:06 | 49.92
2021-01-16 | 10:06 | 49.921
2021-01-16 | 10:06 | 49.919
2021-01-16 | 10:06 | 49.919
2021-01-16 | 10:06 | 49.916
2021-01-16 | 10:06 | 49.915
2021-01-16 | 10:06 | 49.913
2021-01-16 | 10:06 | 49.914
2021-01-16 | 10:06 | 49.91
2021-01-16 | 10:06 | 49.911
2021-01-16 | 10:06 | 49.91
2021-01-16 | 10:06 | 49.908
2021-01-16 | 10:06 | 49.906
2021-01-16 | 10:06 | 49.904
2021-01-16 | 10:06 | 49.906
2021-01-16 | 10:06 | 49.905
2021-01-16 | 10:06 | 49.908
2021-01-16 | 10:06 | 49.909
2021-01-16 | 10:06 | 49.912
2021-01-16 | 10:06 | 49.912
2021-01-16 | 10:06 | 49.914
2021-01-16 | 10:06 | 49.913
2021-01-16 | 10:06 | 49.915
2021-01-16 | 10:06 | 49.913
2021-01-16 | 10:06 | 49.914
2021-01-16 | 10:06 | 49.912
2021-01-16 | 10:06 | 49.913
2021-01-16 | 10:06 | 49.913
2021-01-16 | 10:06 | 49.912
2021-01-16 | 10:06 | 49.911
2021-01-16 | 10:06 | 49.91
2021-01-16 | 10:06 | 49.91
2021-01-16 | 10:06 | 49.911
2021-01-16 | 10:06 | 49.909
2021-01-16 | 10:06 | 49.905
2021-01-16 | 10:06 | 49.905
2021-01-16 | 10:06 | 49.906
2021-01-16 | 10:06 | 49.908
2021-01-16 | 10:06 | 49.91
2021-01-16 | 10:06 | 49.914
2021-01-16 | 10:07 | 49.915
2021-01-16 | 10:07 | 49.918
2021-01-16 | 10:07 | 49.922
2021-01-16 | 10:07 | 49.924
2021-01-16 | 10:07 | 49.924
2021-01-16 | 10:07 | 49.922
2021-01-16 | 10:07 | 49.922
2021-01-16 | 10:07 | 49.921
2021-01-16 | 10:07 | 49.921
2021-01-16 | 10:07 | 49.92
2021-01-16 | 10:07 | 49.918
2021-01-16 | 10:07 | 49.917
2021-01-16 | 10:07 | 49.918
2021-01-16 | 10:07 | 49.918
2021-01-16 | 10:07 | 49.918
2021-01-16 | 10:07 | 49.918
2021-01-16 | 10:07 | 49.916
2021-01-16 | 10:07 | 49.918
2021-01-16 | 10:07 | 49.918
2021-01-16 | 10:07 | 49.924
2021-01-16 | 10:07 | 49.929
2021-01-16 | 10:07 | 49.932
2021-01-16 | 10:07 | 49.935
2021-01-16 | 10:07 | 49.938
2021-01-16 | 10:07 | 49.939
2021-01-16 | 10:07 | 49.94
2021-01-16 | 10:07 | 49.94
2021-01-16 | 10:07 | 49.942
2021-01-16 | 10:07 | 49.942
2021-01-16 | 10:07 | 49.941
2021-01-16 | 10:07 | 49.94
2021-01-16 | 10:07 | 49.938
2021-01-16 | 10:07 | 49.939
2021-01-16 | 10:07 | 49.938
2021-01-16 | 10:07 | 49.938
2021-01-16 | 10:07 | 49.936
2021-01-16 | 10:07 | 49.933
2021-01-16 | 10:07 | 49.933
2021-01-16 | 10:07 | 49.935
2021-01-16 | 10:07 | 49.94
2021-01-16 | 10:07 | 49.94
2021-01-16 | 10:07 | 49.94
2021-01-16 | 10:07 | 49.94
2021-01-16 | 10:07 | 49.939
2021-01-16 | 10:07 | 49.943
2021-01-16 | 10:07 | 49.945
2021-01-16 | 10:07 | 49.947
2021-01-16 | 10:07 | 49.946
2021-01-16 | 10:07 | 49.948
2021-01-16 | 10:07 | 49.948
2021-01-16 | 10:07 | 49.948
2021-01-16 | 10:07 | 49.947
2021-01-16 | 10:07 | 49.946
2021-01-16 | 10:07 | 49.945
2021-01-16 | 10:07 | 49.945
2021-01-16 | 10:07 | 49.945
2021-01-16 | 10:07 | 49.944
2021-01-16 | 10:07 | 49.944
2021-01-16 | 10:07 | 49.944
2021-01-16 | 10:08 | 49.944
2021-01-16 | 10:08 | 49.942
2021-01-16 | 10:08 | 49.939
2021-01-16 | 10:08 | 49.938
2021-01-16 | 10:08 | 49.936
2021-01-16 | 10:08 | 49.935
2021-01-16 | 10:08 | 49.932
2021-01-16 | 10:08 | 49.931
2021-01-16 | 10:08 | 49.93
2021-01-16 | 10:08 | 49.931
2021-01-16 | 10:08 | 49.93
2021-01-16 | 10:08 | 49.932
2021-01-16 | 10:08 | 49.931
2021-01-16 | 10:08 | 49.936
2021-01-16 | 10:08 | 49.938
2021-01-16 | 10:08 | 49.942
2021-01-16 | 10:08 | 49.942
2021-01-16 | 10:08 | 49.944
2021-01-16 | 10:08 | 49.944
2021-01-16 | 10:08 | 49.945
2021-01-16 | 10:08 | 49.947
2021-01-16 | 10:08 | 49.949
2021-01-16 | 10:08 | 49.947
2021-01-16 | 10:08 | 49.947
2021-01-16 | 10:08 | 49.945
2021-01-16 | 10:08 | 49.943
2021-01-16 | 10:08 | 49.944
2021-01-16 | 10:08 | 49.945
2021-01-16 | 10:08 | 49.945
2021-01-16 | 10:08 | 49.943
2021-01-16 | 10:08 | 49.942
2021-01-16 | 10:08 | 49.938
2021-01-16 | 10:08 | 49.934
2021-01-16 | 10:08 | 49.931
2021-01-16 | 10:08 | 49.927
2021-01-16 | 10:08 | 49.923
2021-01-16 | 10:08 | 49.923
2021-01-16 | 10:08 | 49.922
2021-01-16 | 10:08 | 49.923
2021-01-16 | 10:08 | 49.926
2021-01-16 | 10:08 | 49.929
2021-01-16 | 10:08 | 49.931
2021-01-16 | 10:08 | 49.929
2021-01-16 | 10:08 | 49.929
2021-01-16 | 10:08 | 49.926
2021-01-16 | 10:08 | 49.925
2021-01-16 | 10:08 | 49.926
2021-01-16 | 10:08 | 49.925
2021-01-16 | 10:08 | 49.926
2021-01-16 | 10:08 | 49.927
2021-01-16 | 10:08 | 49.93
2021-01-16 | 10:08 | 49.932
2021-01-16 | 10:08 | 49.934
2021-01-16 | 10:08 | 49.938
2021-01-16 | 10:08 | 49.938
2021-01-16 | 10:08 | 49.94
2021-01-16 | 10:08 | 49.943
2021-01-16 | 10:08 | 49.948
2021-01-16 | 10:08 | 49.952
2021-01-16 | 10:08 | 49.955
2021-01-16 | 10:09 | 49.957
2021-01-16 | 10:09 | 49.956
2021-01-16 | 10:09 | 49.956
2021-01-16 | 10:09 | 49.955
2021-01-16 | 10:09 | 49.956
2021-01-16 | 10:09 | 49.953
2021-01-16 | 10:09 | 49.952
2021-01-16 | 10:09 | 49.951
2021-01-16 | 10:09 | 49.952
2021-01-16 | 10:09 | 49.952
2021-01-16 | 10:09 | 49.951
2021-01-16 | 10:09 | 49.951
2021-01-16 | 10:09 | 49.95
2021-01-16 | 10:09 | 49.954
2021-01-16 | 10:09 | 49.953
2021-01-16 | 10:09 | 49.953
2021-01-16 | 10:09 | 49.95
2021-01-16 | 10:09 | 49.948
2021-01-16 | 10:09 | 49.947
2021-01-16 | 10:09 | 49.948
2021-01-16 | 10:09 | 49.949
2021-01-16 | 10:09 | 49.952
2021-01-16 | 10:09 | 49.954
2021-01-16 | 10:09 | 49.956
2021-01-16 | 10:09 | 49.959
2021-01-16 | 10:09 | 49.961
2021-01-16 | 10:09 | 49.964
2021-01-16 | 10:09 | 49.964
2021-01-16 | 10:09 | 49.965
2021-01-16 | 10:09 | 49.965
2021-01-16 | 10:09 | 49.966
2021-01-16 | 10:09 | 49.964
2021-01-16 | 10:09 | 49.963
2021-01-16 | 10:09 | 49.961
2021-01-16 | 10:09 | 49.964
2021-01-16 | 10:09 | 49.964
2021-01-16 | 10:09 | 49.967
2021-01-16 | 10:09 | 49.97
2021-01-16 | 10:09 | 49.973
2021-01-16 | 10:09 | 49.974
2021-01-16 | 10:09 | 49.976
2021-01-16 | 10:09 | 49.974
2021-01-16 | 10:09 | 49.975
2021-01-16 | 10:09 | 49.977
2021-01-16 | 10:09 | 49.977
2021-01-16 | 10:09 | 49.978
2021-01-16 | 10:09 | 49.98
2021-01-16 | 10:09 | 49.98
2021-01-16 | 10:09 | 49.974
2021-01-16 | 10:09 | 49.973
2021-01-16 | 10:09 | 49.973
2021-01-16 | 10:09 | 49.97
2021-01-16 | 10:09 | 49.969
2021-01-16 | 10:09 | 49.969
2021-01-16 | 10:09 | 49.969
2021-01-16 | 10:09 | 49.971
2021-01-16 | 10:09 | 49.97
2021-01-16 | 10:09 | 49.969
2021-01-16 | 10:09 | 49.969
2021-01-16 | 10:09 | 49.97
2021-01-16 | 10:10 | 49.969
2021-01-16 | 10:10 | 49.97
2021-01-16 | 10:10 | 49.972
2021-01-16 | 10:10 | 49.97
2021-01-16 | 10:10 | 49.97
2021-01-16 | 10:10 | 49.97
2021-01-16 | 10:10 | 49.972
2021-01-16 | 10:10 | 49.97
2021-01-16 | 10:10 | 49.97
2021-01-16 | 10:10 | 49.97
2021-01-16 | 10:10 | 49.967
2021-01-16 | 10:10 | 49.964
2021-01-16 | 10:10 | 49.963
2021-01-16 | 10:10 | 49.964
2021-01-16 | 10:10 | 49.965
2021-01-16 | 10:10 | 49.967
2021-01-16 | 10:10 | 49.97
2021-01-16 | 10:10 | 49.975
2021-01-16 | 10:10 | 49.978
2021-01-16 | 10:10 | 49.981
2021-01-16 | 10:10 | 49.98
2021-01-16 | 10:10 | 49.98
2021-01-16 | 10:10 | 49.976
2021-01-16 | 10:10 | 49.974
2021-01-16 | 10:10 | 49.972
2021-01-16 | 10:10 | 49.969
2021-01-16 | 10:10 | 49.97
2021-01-16 | 10:10 | 49.968
2021-01-16 | 10:10 | 49.969
2021-01-16 | 10:10 | 49.968
2021-01-16 | 10:10 | 49.967
2021-01-16 | 10:10 | 49.964
2021-01-16 | 10:10 | 49.964
2021-01-16 | 10:10 | 49.965
2021-01-16 | 10:10 | 49.967
2021-01-16 | 10:10 | 49.97
2021-01-16 | 10:10 | 49.97
2021-01-16 | 10:10 | 49.971
2021-01-16 | 10:10 | 49.969
2021-01-16 | 10:10 | 49.971
2021-01-16 | 10:10 | 49.97
2021-01-16 | 10:10 | 49.967
2021-01-16 | 10:10 | 49.964
2021-01-16 | 10:10 | 49.961
2021-01-16 | 10:10 | 49.958
2021-01-16 | 10:10 | 49.957
2021-01-16 | 10:10 | 49.957
2021-01-16 | 10:10 | 49.962
2021-01-16 | 10:10 | 49.961
2021-01-16 | 10:10 | 49.966
2021-01-16 | 10:10 | 49.968
2021-01-16 | 10:10 | 49.968
2021-01-16 | 10:10 | 49.971
2021-01-16 | 10:10 | 49.97
2021-01-16 | 10:10 | 49.972
2021-01-16 | 10:10 | 49.974
2021-01-16 | 10:10 | 49.973
2021-01-16 | 10:10 | 49.974
2021-01-16 | 10:10 | 49.975
2021-01-16 | 10:10 | 49.977
2021-01-16 | 10:11 | 49.975
2021-01-16 | 10:11 | 49.975
2021-01-16 | 10:11 | 49.978
2021-01-16 | 10:11 | 49.98
2021-01-16 | 10:11 | 49.981
2021-01-16 | 10:11 | 49.98
2021-01-16 | 10:11 | 49.981
2021-01-16 | 10:11 | 49.981
2021-01-16 | 10:11 | 49.982
2021-01-16 | 10:11 | 49.982
2021-01-16 | 10:11 | 49.981
2021-01-16 | 10:11 | 49.981
2021-01-16 | 10:11 | 49.979
2021-01-16 | 10:11 | 49.98
2021-01-16 | 10:11 | 49.982
2021-01-16 | 10:11 | 49.983
2021-01-16 | 10:11 | 49.985
2021-01-16 | 10:11 | 49.987
2021-01-16 | 10:11 | 49.99
2021-01-16 | 10:11 | 49.993
2021-01-16 | 10:11 | 49.995
2021-01-16 | 10:11 | 49.996
2021-01-16 | 10:11 | 49.997
2021-01-16 | 10:11 | 49.997
2021-01-16 | 10:11 | 49.998
2021-01-16 | 10:11 | 49.997
2021-01-16 | 10:11 | 49.995
2021-01-16 | 10:11 | 49.992
2021-01-16 | 10:11 | 49.989
2021-01-16 | 10:11 | 49.988
2021-01-16 | 10:11 | 49.986
2021-01-16 | 10:11 | 49.983
2021-01-16 | 10:11 | 49.982
2021-01-16 | 10:11 | 49.98
2021-01-16 | 10:11 | 49.977
2021-01-16 | 10:11 | 49.973
2021-01-16 | 10:11 | 49.972
2021-01-16 | 10:11 | 49.971
2021-01-16 | 10:11 | 49.973
2021-01-16 | 10:11 | 49.975
2021-01-16 | 10:11 | 49.978
2021-01-16 | 10:11 | 49.977
2021-01-16 | 10:11 | 49.977
2021-01-16 | 10:11 | 49.973
2021-01-16 | 10:11 | 49.974
2021-01-16 | 10:11 | 49.973
2021-01-16 | 10:11 | 49.975
2021-01-16 | 10:11 | 49.976
2021-01-16 | 10:11 | 49.978
2021-01-16 | 10:11 | 49.976
2021-01-16 | 10:11 | 49.976
2021-01-16 | 10:11 | 49.977
2021-01-16 | 10:11 | 49.975
2021-01-16 | 10:11 | 49.97
2021-01-16 | 10:11 | 49.969
2021-01-16 | 10:11 | 49.966
2021-01-16 | 10:11 | 49.963
2021-01-16 | 10:11 | 49.963
2021-01-16 | 10:11 | 49.962
2021-01-16 | 10:11 | 49.965
2021-01-16 | 10:12 | 49.966
2021-01-16 | 10:12 | 49.969
2021-01-16 | 10:12 | 49.974
2021-01-16 | 10:12 | 49.976
2021-01-16 | 10:12 | 49.978
2021-01-16 | 10:12 | 49.978
2021-01-16 | 10:12 | 49.98
2021-01-16 | 10:12 | 49.982
2021-01-16 | 10:12 | 49.983
2021-01-16 | 10:12 | 49.981
2021-01-16 | 10:12 | 49.982
2021-01-16 | 10:12 | 49.977
2021-01-16 | 10:12 | 49.977
2021-01-16 | 10:12 | 49.975
2021-01-16 | 10:12 | 49.976
2021-01-16 | 10:12 | 49.975
2021-01-16 | 10:12 | 49.975
2021-01-16 | 10:12 | 49.972
2021-01-16 | 10:12 | 49.973
2021-01-16 | 10:12 | 49.979
2021-01-16 | 10:12 | 49.981
2021-01-16 | 10:12 | 49.983
2021-01-16 | 10:12 | 49.989
2021-01-16 | 10:12 | 49.992
2021-01-16 | 10:12 | 49.991
2021-01-16 | 10:12 | 49.993
2021-01-16 | 10:12 | 49.994
2021-01-16 | 10:12 | 49.993
2021-01-16 | 10:12 | 49.992
2021-01-16 | 10:12 | 49.989
2021-01-16 | 10:12 | 49.989
2021-01-16 | 10:12 | 49.987
2021-01-16 | 10:12 | 49.986
2021-01-16 | 10:12 | 49.988
2021-01-16 | 10:12 | 49.989
2021-01-16 | 10:12 | 49.992
2021-01-16 | 10:12 | 49.993
2021-01-16 | 10:12 | 49.994
2021-01-16 | 10:12 | 49.997
2021-01-16 | 10:12 | 49.997
2021-01-16 | 10:12 | 49.998
2021-01-16 | 10:12 | 49.997
2021-01-16 | 10:12 | 49.996
2021-01-16 | 10:12 | 49.998
2021-01-16 | 10:12 | 49.998
2021-01-16 | 10:12 | 50.001
2021-01-16 | 10:12 | 50.003
2021-01-16 | 10:12 | 50.004
2021-01-16 | 10:12 | 50.009
2021-01-16 | 10:12 | 50.011
2021-01-16 | 10:12 | 50.01
2021-01-16 | 10:12 | 50.01
2021-01-16 | 10:12 | 50.01
2021-01-16 | 10:12 | 50.009
2021-01-16 | 10:12 | 50.008
2021-01-16 | 10:12 | 50.005
2021-01-16 | 10:12 | 50.004
2021-01-16 | 10:12 | 50.005
2021-01-16 | 10:12 | 50.006
2021-01-16 | 10:12 | 50.007
2021-01-16 | 10:13 | 50.008
2021-01-16 | 10:13 | 50.009
2021-01-16 | 10:13 | 50.009
2021-01-16 | 10:13 | 50.008
2021-01-16 | 10:13 | 50.008
2021-01-16 | 10:13 | 50.007
2021-01-16 | 10:13 | 50.004
2021-01-16 | 10:13 | 50.002
2021-01-16 | 10:13 | 49.998
2021-01-16 | 10:13 | 49.998
2021-01-16 | 10:13 | 49.996
2021-01-16 | 10:13 | 50.003
2021-01-16 | 10:13 | 50.004
2021-01-16 | 10:13 | 50.008
2021-01-16 | 10:13 | 50.011
2021-01-16 | 10:13 | 50.016
2021-01-16 | 10:13 | 50.019
2021-01-16 | 10:13 | 50.022
2021-01-16 | 10:13 | 50.026
2021-01-16 | 10:13 | 50.028
2021-01-16 | 10:13 | 50.03
2021-01-16 | 10:13 | 50.034
2021-01-16 | 10:13 | 50.036
2021-01-16 | 10:13 | 50.034
2021-01-16 | 10:13 | 50.032
2021-01-16 | 10:13 | 50.025
2021-01-16 | 10:13 | 50.017
2021-01-16 | 10:13 | 50.009
2021-01-16 | 10:13 | 50.001
2021-01-16 | 10:13 | 49.992
2021-01-16 | 10:13 | 49.979
2021-01-16 | 10:13 | 49.967
2021-01-16 | 10:13 | 49.958
2021-01-16 | 10:13 | 49.956
2021-01-16 | 10:13 | 49.955
2021-01-16 | 10:13 | 49.955
2021-01-16 | 10:13 | 49.954
2021-01-16 | 10:13 | 49.95
2021-01-16 | 10:13 | 49.947
2021-01-16 | 10:13 | 49.942
2021-01-16 | 10:13 | 49.939
2021-01-16 | 10:13 | 49.934
2021-01-16 | 10:13 | 49.932
2021-01-16 | 10:13 | 49.929
2021-01-16 | 10:13 | 49.927
2021-01-16 | 10:13 | 49.926
2021-01-16 | 10:13 | 49.928
2021-01-16 | 10:13 | 49.928
2021-01-16 | 10:13 | 49.929
2021-01-16 | 10:13 | 49.929
2021-01-16 | 10:13 | 49.931
2021-01-16 | 10:13 | 49.933
2021-01-16 | 10:13 | 49.937
2021-01-16 | 10:13 | 49.94
2021-01-16 | 10:13 | 49.943
2021-01-16 | 10:13 | 49.946
2021-01-16 | 10:13 | 49.945
2021-01-16 | 10:13 | 49.947
2021-01-16 | 10:13 | 49.946
2021-01-16 | 10:13 | 49.948
2021-01-16 | 10:14 | 49.949
2021-01-16 | 10:14 | 49.951
2021-01-16 | 10:14 | 49.95
2021-01-16 | 10:14 | 49.952
2021-01-16 | 10:14 | 49.954
2021-01-16 | 10:14 | 49.954
2021-01-16 | 10:14 | 49.955
2021-01-16 | 10:14 | 49.954
2021-01-16 | 10:14 | 49.956
2021-01-16 | 10:14 | 49.955
2021-01-16 | 10:14 | 49.955
2021-01-16 | 10:14 | 49.953
2021-01-16 | 10:14 | 49.951
2021-01-16 | 10:14 | 49.95
2021-01-16 | 10:14 | 49.947
2021-01-16 | 10:14 | 49.946
2021-01-16 | 10:14 | 49.942
2021-01-16 | 10:14 | 49.938
2021-01-16 | 10:14 | 49.935
2021-01-16 | 10:14 | 49.931
2021-01-16 | 10:14 | 49.932
2021-01-16 | 10:14 | 49.932
2021-01-16 | 10:14 | 49.935
2021-01-16 | 10:14 | 49.937
2021-01-16 | 10:14 | 49.94
2021-01-16 | 10:14 | 49.943
2021-01-16 | 10:14 | 49.946
2021-01-16 | 10:14 | 49.948
2021-01-16 | 10:14 | 49.951
2021-01-16 | 10:14 | 49.953
2021-01-16 | 10:14 | 49.952
2021-01-16 | 10:14 | 49.949
2021-01-16 | 10:14 | 49.951
2021-01-16 | 10:14 | 49.949
2021-01-16 | 10:14 | 49.946
2021-01-16 | 10:14 | 49.942
2021-01-16 | 10:14 | 49.939
2021-01-16 | 10:14 | 49.935
2021-01-16 | 10:14 | 49.937
2021-01-16 | 10:14 | 49.937
2021-01-16 | 10:14 | 49.939
2021-01-16 | 10:14 | 49.938
2021-01-16 | 10:14 | 49.941
2021-01-16 | 10:14 | 49.943
2021-01-16 | 10:14 | 49.945
2021-01-16 | 10:14 | 49.947
2021-01-16 | 10:14 | 49.95
2021-01-16 | 10:14 | 49.949
2021-01-16 | 10:14 | 49.95
2021-01-16 | 10:14 | 49.948
2021-01-16 | 10:14 | 49.948
2021-01-16 | 10:14 | 49.948
2021-01-16 | 10:14 | 49.949
2021-01-16 | 10:14 | 49.949
2021-01-16 | 10:14 | 49.952
2021-01-16 | 10:14 | 49.951
2021-01-16 | 10:14 | 49.95
2021-01-16 | 10:14 | 49.948
2021-01-16 | 10:14 | 49.949
2021-01-16 | 10:14 | 49.95
2021-01-16 | 10:14 | 49.949
2021-01-16 | 10:15 | 49.952
2021-01-16 | 10:15 | 49.955
2021-01-16 | 10:15 | 49.957
2021-01-16 | 10:15 | 49.96
2021-01-16 | 10:15 | 49.961
2021-01-16 | 10:15 | 49.961
2021-01-16 | 10:15 | 49.962
2021-01-16 | 10:15 | 49.964
2021-01-16 | 10:15 | 49.964
2021-01-16 | 10:15 | 49.964
2021-01-16 | 10:15 | 49.964
2021-01-16 | 10:15 | 49.963
2021-01-16 | 10:15 | 49.962
2021-01-16 | 10:15 | 49.963
2021-01-16 | 10:15 | 49.961
2021-01-16 | 10:15 | 49.959
2021-01-16 | 10:15 | 49.957
2021-01-16 | 10:15 | 49.955
2021-01-16 | 10:15 | 49.952
2021-01-16 | 10:15 | 49.952
2021-01-16 | 10:15 | 49.951
2021-01-16 | 10:15 | 49.95
2021-01-16 | 10:15 | 49.949
2021-01-16 | 10:15 | 49.949
2021-01-16 | 10:15 | 49.951
2021-01-16 | 10:15 | 49.953
2021-01-16 | 10:15 | 49.958
2021-01-16 | 10:15 | 49.957
2021-01-16 | 10:15 | 49.958
2021-01-16 | 10:15 | 49.954
2021-01-16 | 10:15 | 49.955
2021-01-16 | 10:15 | 49.953
2021-01-16 | 10:15 | 49.957
2021-01-16 | 10:15 | 49.958
2021-01-16 | 10:15 | 49.959
2021-01-16 | 10:15 | 49.953
2021-01-16 | 10:15 | 49.95
2021-01-16 | 10:15 | 49.949
2021-01-16 | 10:15 | 49.948
2021-01-16 | 10:15 | 49.947
2021-01-16 | 10:15 | 49.947
2021-01-16 | 10:15 | 49.946
2021-01-16 | 10:15 | 49.944
2021-01-16 | 10:15 | 49.942
2021-01-16 | 10:15 | 49.94
2021-01-16 | 10:15 | 49.939
2021-01-16 | 10:15 | 49.937
2021-01-16 | 10:15 | 49.94
2021-01-16 | 10:15 | 49.942
2021-01-16 | 10:15 | 49.945
2021-01-16 | 10:15 | 49.947
2021-01-16 | 10:15 | 49.948
2021-01-16 | 10:15 | 49.949
2021-01-16 | 10:15 | 49.948
2021-01-16 | 10:15 | 49.95
2021-01-16 | 10:15 | 49.95
2021-01-16 | 10:15 | 49.951
2021-01-16 | 10:15 | 49.948
2021-01-16 | 10:15 | 49.944
2021-01-16 | 10:16 | 49.942
2021-01-16 | 10:16 | 49.939
2021-01-16 | 10:16 | 49.938
2021-01-16 | 10:16 | 49.941
2021-01-16 | 10:16 | 49.941
2021-01-16 | 10:16 | 49.945
2021-01-16 | 10:16 | 49.946
2021-01-16 | 10:16 | 49.946
2021-01-16 | 10:16 | 49.948
2021-01-16 | 10:16 | 49.948
2021-01-16 | 10:16 | 49.949
2021-01-16 | 10:16 | 49.948
2021-01-16 | 10:16 | 49.95
2021-01-16 | 10:16 | 49.95
2021-01-16 | 10:16 | 49.952
2021-01-16 | 10:16 | 49.952
2021-01-16 | 10:16 | 49.952
2021-01-16 | 10:16 | 49.951
2021-01-16 | 10:16 | 49.954
2021-01-16 | 10:16 | 49.954
2021-01-16 | 10:16 | 49.955
2021-01-16 | 10:16 | 49.954
2021-01-16 | 10:16 | 49.955
2021-01-16 | 10:16 | 49.952
2021-01-16 | 10:16 | 49.954
2021-01-16 | 10:16 | 49.955
2021-01-16 | 10:16 | 49.956
2021-01-16 | 10:16 | 49.957
2021-01-16 | 10:16 | 49.957
2021-01-16 | 10:16 | 49.959
2021-01-16 | 10:16 | 49.96
2021-01-16 | 10:16 | 49.958
2021-01-16 | 10:16 | 49.955
2021-01-16 | 10:16 | 49.954
2021-01-16 | 10:16 | 49.954
2021-01-16 | 10:16 | 49.954
2021-01-16 | 10:16 | 49.954
2021-01-16 | 10:16 | 49.957
2021-01-16 | 10:16 | 49.957
2021-01-16 | 10:16 | 49.955
2021-01-16 | 10:16 | 49.953
2021-01-16 | 10:16 | 49.95
2021-01-16 | 10:16 | 49.951
2021-01-16 | 10:16 | 49.95
2021-01-16 | 10:16 | 49.951
2021-01-16 | 10:16 | 49.954
2021-01-16 | 10:16 | 49.953
2021-01-16 | 10:16 | 49.954
2021-01-16 | 10:16 | 49.955
2021-01-16 | 10:16 | 49.957
2021-01-16 | 10:16 | 49.958
2021-01-16 | 10:16 | 49.958
2021-01-16 | 10:16 | 49.959
2021-01-16 | 10:16 | 49.961
2021-01-16 | 10:16 | 49.965
2021-01-16 | 10:16 | 49.965
2021-01-16 | 10:16 | 49.964
2021-01-16 | 10:16 | 49.961
2021-01-16 | 10:16 | 49.958
2021-01-16 | 10:16 | 49.954
2021-01-16 | 10:16 | 49.952
2021-01-16 | 10:17 | 49.954
2021-01-16 | 10:17 | 49.953
2021-01-16 | 10:17 | 49.955
2021-01-16 | 10:17 | 49.955
2021-01-16 | 10:17 | 49.958
2021-01-16 | 10:17 | 49.958
2021-01-16 | 10:17 | 49.959
2021-01-16 | 10:17 | 49.959
2021-01-16 | 10:17 | 49.96
2021-01-16 | 10:17 | 49.96
2021-01-16 | 10:17 | 49.959
2021-01-16 | 10:17 | 49.958
2021-01-16 | 10:17 | 49.96
2021-01-16 | 10:17 | 49.959
2021-01-16 | 10:17 | 49.957
2021-01-16 | 10:17 | 49.955
2021-01-16 | 10:17 | 49.955
2021-01-16 | 10:17 | 49.954
2021-01-16 | 10:17 | 49.954
2021-01-16 | 10:17 | 49.952
2021-01-16 | 10:17 | 49.951
2021-01-16 | 10:17 | 49.951
2021-01-16 | 10:17 | 49.949
2021-01-16 | 10:17 | 49.948
2021-01-16 | 10:17 | 49.947
2021-01-16 | 10:17 | 49.946
2021-01-16 | 10:17 | 49.944
2021-01-16 | 10:17 | 49.947
2021-01-16 | 10:17 | 49.947
2021-01-16 | 10:17 | 49.947
2021-01-16 | 10:17 | 49.946
2021-01-16 | 10:17 | 49.945
2021-01-16 | 10:17 | 49.944
2021-01-16 | 10:17 | 49.941
2021-01-16 | 10:17 | 49.939
2021-01-16 | 10:17 | 49.939
2021-01-16 | 10:17 | 49.942
2021-01-16 | 10:17 | 49.941
2021-01-16 | 10:17 | 49.94
2021-01-16 | 10:17 | 49.938
2021-01-16 | 10:17 | 49.938
2021-01-16 | 10:17 | 49.939
2021-01-16 | 10:17 | 49.942
2021-01-16 | 10:17 | 49.944
2021-01-16 | 10:17 | 49.944
2021-01-16 | 10:17 | 49.94
2021-01-16 | 10:17 | 49.938
2021-01-16 | 10:17 | 49.936
2021-01-16 | 10:17 | 49.933
2021-01-16 | 10:17 | 49.933
2021-01-16 | 10:17 | 49.931
2021-01-16 | 10:17 | 49.927
2021-01-16 | 10:17 | 49.924
2021-01-16 | 10:17 | 49.922
2021-01-16 | 10:17 | 49.92
2021-01-16 | 10:17 | 49.916
2021-01-16 | 10:17 | 49.916
2021-01-16 | 10:17 | 49.914
2021-01-16 | 10:17 | 49.914
2021-01-16 | 10:18 | 49.916
2021-01-16 | 10:18 | 49.915
2021-01-16 | 10:18 | 49.917
2021-01-16 | 10:18 | 49.918
2021-01-16 | 10:18 | 49.919
2021-01-16 | 10:18 | 49.919
2021-01-16 | 10:18 | 49.92
2021-01-16 | 10:18 | 49.919
2021-01-16 | 10:18 | 49.921
2021-01-16 | 10:18 | 49.922
2021-01-16 | 10:18 | 49.923
2021-01-16 | 10:18 | 49.923
2021-01-16 | 10:18 | 49.924
2021-01-16 | 10:18 | 49.923
2021-01-16 | 10:18 | 49.924
2021-01-16 | 10:18 | 49.926
2021-01-16 | 10:18 | 49.927
2021-01-16 | 10:18 | 49.93
2021-01-16 | 10:18 | 49.93
2021-01-16 | 10:18 | 49.931
2021-01-16 | 10:18 | 49.93
2021-01-16 | 10:18 | 49.927
2021-01-16 | 10:18 | 49.923
2021-01-16 | 10:18 | 49.922
2021-01-16 | 10:18 | 49.919
2021-01-16 | 10:18 | 49.919
2021-01-16 | 10:18 | 49.919
2021-01-16 | 10:18 | 49.919
2021-01-16 | 10:18 | 49.917
2021-01-16 | 10:18 | 49.916
2021-01-16 | 10:18 | 49.912
2021-01-16 | 10:18 | 49.91
2021-01-16 | 10:18 | 49.908
2021-01-16 | 10:18 | 49.91
2021-01-16 | 10:18 | 49.908
2021-01-16 | 10:18 | 49.908
2021-01-16 | 10:18 | 49.906
2021-01-16 | 10:18 | 49.908
2021-01-16 | 10:18 | 49.908
2021-01-16 | 10:18 | 49.909
2021-01-16 | 10:18 | 49.911
2021-01-16 | 10:18 | 49.912
2021-01-16 | 10:18 | 49.91
2021-01-16 | 10:18 | 49.909
2021-01-16 | 10:18 | 49.908
2021-01-16 | 10:18 | 49.908
2021-01-16 | 10:18 | 49.909
2021-01-16 | 10:18 | 49.912
2021-01-16 | 10:18 | 49.91
2021-01-16 | 10:18 | 49.909
2021-01-16 | 10:18 | 49.909
2021-01-16 | 10:18 | 49.908
2021-01-16 | 10:18 | 49.909
2021-01-16 | 10:18 | 49.908
2021-01-16 | 10:18 | 49.905
2021-01-16 | 10:18 | 49.903
2021-01-16 | 10:18 | 49.901
2021-01-16 | 10:18 | 49.899
2021-01-16 | 10:18 | 49.898
2021-01-16 | 10:18 | 49.898
2021-01-16 | 10:18 | 49.898
2021-01-16 | 10:19 | 49.896
2021-01-16 | 10:19 | 49.894
2021-01-16 | 10:19 | 49.89
2021-01-16 | 10:19 | 49.893
2021-01-16 | 10:19 | 49.895
2021-01-16 | 10:19 | 49.897
2021-01-16 | 10:19 | 49.896
2021-01-16 | 10:19 | 49.901
2021-01-16 | 10:19 | 49.904
2021-01-16 | 10:19 | 49.907
2021-01-16 | 10:19 | 49.907
2021-01-16 | 10:19 | 49.907
2021-01-16 | 10:19 | 49.906
2021-01-16 | 10:19 | 49.906
2021-01-16 | 10:19 | 49.905
2021-01-16 | 10:19 | 49.907
2021-01-16 | 10:19 | 49.904
2021-01-16 | 10:19 | 49.903
2021-01-16 | 10:19 | 49.902
2021-01-16 | 10:19 | 49.902
2021-01-16 | 10:19 | 49.902
2021-01-16 | 10:19 | 49.904
2021-01-16 | 10:19 | 49.902
2021-01-16 | 10:19 | 49.901
2021-01-16 | 10:19 | 49.897
2021-01-16 | 10:19 | 49.895
2021-01-16 | 10:19 | 49.893
2021-01-16 | 10:19 | 49.889
2021-01-16 | 10:19 | 49.889
2021-01-16 | 10:19 | 49.888
2021-01-16 | 10:19 | 49.886
2021-01-16 | 10:19 | 49.884
2021-01-16 | 10:19 | 49.884
2021-01-16 | 10:19 | 49.882
2021-01-16 | 10:19 | 49.877
2021-01-16 | 10:19 | 49.875
2021-01-16 | 10:19 | 49.87
2021-01-16 | 10:19 | 49.867
2021-01-16 | 10:19 | 49.867
2021-01-16 | 10:19 | 49.868
2021-01-16 | 10:19 | 49.87
2021-01-16 | 10:19 | 49.875
2021-01-16 | 10:19 | 49.878
2021-01-16 | 10:19 | 49.88
2021-01-16 | 10:19 | 49.883
2021-01-16 | 10:19 | 49.886
2021-01-16 | 10:19 | 49.887
2021-01-16 | 10:19 | 49.887
2021-01-16 | 10:19 | 49.887
2021-01-16 | 10:19 | 49.886
2021-01-16 | 10:19 | 49.886
2021-01-16 | 10:19 | 49.887
2021-01-16 | 10:19 | 49.885
2021-01-16 | 10:19 | 49.885
2021-01-16 | 10:19 | 49.883
2021-01-16 | 10:19 | 49.882
2021-01-16 | 10:19 | 49.881
2021-01-16 | 10:19 | 49.885
2021-01-16 | 10:19 | 49.891
2021-01-16 | 10:20 | 49.892
2021-01-16 | 10:20 | 49.895
2021-01-16 | 10:20 | 49.894
2021-01-16 | 10:20 | 49.897
2021-01-16 | 10:20 | 49.896
2021-01-16 | 10:20 | 49.897
2021-01-16 | 10:20 | 49.891
2021-01-16 | 10:20 | 49.888
2021-01-16 | 10:20 | 49.888
2021-01-16 | 10:20 | 49.887
2021-01-16 | 10:20 | 49.888
2021-01-16 | 10:20 | 49.889
2021-01-16 | 10:20 | 49.892
2021-01-16 | 10:20 | 49.895
2021-01-16 | 10:20 | 49.897
2021-01-16 | 10:20 | 49.899
2021-01-16 | 10:20 | 49.9
2021-01-16 | 10:20 | 49.903
2021-01-16 | 10:20 | 49.904
2021-01-16 | 10:20 | 49.905
2021-01-16 | 10:20 | 49.903
2021-01-16 | 10:20 | 49.902
2021-01-16 | 10:20 | 49.901
2021-01-16 | 10:20 | 49.901
2021-01-16 | 10:20 | 49.902
2021-01-16 | 10:20 | 49.902
2021-01-16 | 10:20 | 49.904
2021-01-16 | 10:20 | 49.905
2021-01-16 | 10:20 | 49.907
2021-01-16 | 10:20 | 49.912
2021-01-16 | 10:20 | 49.916
2021-01-16 | 10:20 | 49.915
2021-01-16 | 10:20 | 49.914
2021-01-16 | 10:20 | 49.912
2021-01-16 | 10:20 | 49.911
2021-01-16 | 10:20 | 49.911
2021-01-16 | 10:20 | 49.912
2021-01-16 | 10:20 | 49.911
2021-01-16 | 10:20 | 49.911
2021-01-16 | 10:20 | 49.91
2021-01-16 | 10:20 | 49.908
2021-01-16 | 10:20 | 49.906
2021-01-16 | 10:20 | 49.907
2021-01-16 | 10:20 | 49.905
2021-01-16 | 10:20 | 49.905
2021-01-16 | 10:20 | 49.905
2021-01-16 | 10:20 | 49.906
2021-01-16 | 10:20 | 49.905
2021-01-16 | 10:20 | 49.905
2021-01-16 | 10:20 | 49.904
2021-01-16 | 10:20 | 49.908
2021-01-16 | 10:20 | 49.908
2021-01-16 | 10:20 | 49.906
2021-01-16 | 10:20 | 49.908
2021-01-16 | 10:20 | 49.911
2021-01-16 | 10:20 | 49.91
2021-01-16 | 10:20 | 49.91
2021-01-16 | 10:20 | 49.91
2021-01-16 | 10:20 | 49.908
2021-01-16 | 10:20 | 49.906
2021-01-16 | 10:20 | 49.905
2021-01-16 | 10:21 | 49.901
2021-01-16 | 10:21 | 49.897
2021-01-16 | 10:21 | 49.896
2021-01-16 | 10:21 | 49.893
2021-01-16 | 10:21 | 49.897
2021-01-16 | 10:21 | 49.897
2021-01-16 | 10:21 | 49.9
2021-01-16 | 10:21 | 49.902
2021-01-16 | 10:21 | 49.905
2021-01-16 | 10:21 | 49.911
2021-01-16 | 10:21 | 49.911
2021-01-16 | 10:21 | 49.913
2021-01-16 | 10:21 | 49.914
2021-01-16 | 10:21 | 49.916
2021-01-16 | 10:21 | 49.917
2021-01-16 | 10:21 | 49.916
2021-01-16 | 10:21 | 49.918
2021-01-16 | 10:21 | 49.917
2021-01-16 | 10:21 | 49.918
2021-01-16 | 10:21 | 49.917
2021-01-16 | 10:21 | 49.916
2021-01-16 | 10:21 | 49.914
2021-01-16 | 10:21 | 49.914
2021-01-16 | 10:21 | 49.913
2021-01-16 | 10:21 | 49.914
2021-01-16 | 10:21 | 49.914
2021-01-16 | 10:21 | 49.915
2021-01-16 | 10:21 | 49.916
2021-01-16 | 10:21 | 49.917
2021-01-16 | 10:21 | 49.917
2021-01-16 | 10:21 | 49.914
2021-01-16 | 10:21 | 49.913
2021-01-16 | 10:21 | 49.914
2021-01-16 | 10:21 | 49.915
2021-01-16 | 10:21 | 49.914
2021-01-16 | 10:21 | 49.917
2021-01-16 | 10:21 | 49.914
2021-01-16 | 10:21 | 49.914
2021-01-16 | 10:21 | 49.91
2021-01-16 | 10:21 | 49.912
2021-01-16 | 10:21 | 49.91
2021-01-16 | 10:21 | 49.911
2021-01-16 | 10:21 | 49.911
2021-01-16 | 10:21 | 49.909
2021-01-16 | 10:21 | 49.908
2021-01-16 | 10:21 | 49.907
2021-01-16 | 10:21 | 49.91
2021-01-16 | 10:21 | 49.911
2021-01-16 | 10:21 | 49.913
2021-01-16 | 10:21 | 49.914
2021-01-16 | 10:21 | 49.915
2021-01-16 | 10:21 | 49.916
2021-01-16 | 10:21 | 49.919
2021-01-16 | 10:21 | 49.921
2021-01-16 | 10:21 | 49.922
2021-01-16 | 10:21 | 49.916
2021-01-16 | 10:21 | 49.914
2021-01-16 | 10:21 | 49.912
2021-01-16 | 10:21 | 49.913
2021-01-16 | 10:22 | 49.912
2021-01-16 | 10:22 | 49.911
2021-01-16 | 10:22 | 49.913
2021-01-16 | 10:22 | 49.914
2021-01-16 | 10:22 | 49.91
2021-01-16 | 10:22 | 49.904
2021-01-16 | 10:22 | 49.902
2021-01-16 | 10:22 | 49.899
2021-01-16 | 10:22 | 49.9
2021-01-16 | 10:22 | 49.902
2021-01-16 | 10:22 | 49.902
2021-01-16 | 10:22 | 49.904
2021-01-16 | 10:22 | 49.902
2021-01-16 | 10:22 | 49.901
2021-01-16 | 10:22 | 49.9
2021-01-16 | 10:22 | 49.904
2021-01-16 | 10:22 | 49.904
2021-01-16 | 10:22 | 49.903
2021-01-16 | 10:22 | 49.902
2021-01-16 | 10:22 | 49.9
2021-01-16 | 10:22 | 49.9
2021-01-16 | 10:22 | 49.898
2021-01-16 | 10:22 | 49.901
2021-01-16 | 10:22 | 49.901
2021-01-16 | 10:22 | 49.905
2021-01-16 | 10:22 | 49.907
2021-01-16 | 10:22 | 49.908
2021-01-16 | 10:22 | 49.908
2021-01-16 | 10:22 | 49.907
2021-01-16 | 10:22 | 49.906
2021-01-16 | 10:22 | 49.901
2021-01-16 | 10:22 | 49.901
2021-01-16 | 10:22 | 49.898
2021-01-16 | 10:22 | 49.896
2021-01-16 | 10:22 | 49.896
2021-01-16 | 10:22 | 49.899
2021-01-16 | 10:22 | 49.899
2021-01-16 | 10:22 | 49.899
2021-01-16 | 10:22 | 49.897
2021-01-16 | 10:22 | 49.897
2021-01-16 | 10:22 | 49.895
2021-01-16 | 10:22 | 49.898
2021-01-16 | 10:22 | 49.898
2021-01-16 | 10:22 | 49.897
2021-01-16 | 10:22 | 49.898
2021-01-16 | 10:22 | 49.9
2021-01-16 | 10:22 | 49.901
2021-01-16 | 10:22 | 49.905
2021-01-16 | 10:22 | 49.905
2021-01-16 | 10:22 | 49.905
2021-01-16 | 10:22 | 49.904
2021-01-16 | 10:22 | 49.907
2021-01-16 | 10:22 | 49.908
2021-01-16 | 10:22 | 49.91
2021-01-16 | 10:22 | 49.911
2021-01-16 | 10:22 | 49.914
2021-01-16 | 10:22 | 49.916
2021-01-16 | 10:22 | 49.917
2021-01-16 | 10:22 | 49.915
2021-01-16 | 10:22 | 49.915
2021-01-16 | 10:22 | 49.906
2021-01-16 | 10:23 | 49.903
2021-01-16 | 10:23 | 49.896
2021-01-16 | 10:23 | 49.894
2021-01-16 | 10:23 | 49.893
2021-01-16 | 10:23 | 49.896
2021-01-16 | 10:23 | 49.898
2021-01-16 | 10:23 | 49.899
2021-01-16 | 10:23 | 49.902
2021-01-16 | 10:23 | 49.902
2021-01-16 | 10:23 | 49.903
2021-01-16 | 10:23 | 49.906
2021-01-16 | 10:23 | 49.909
2021-01-16 | 10:23 | 49.91
2021-01-16 | 10:23 | 49.909
2021-01-16 | 10:23 | 49.908
2021-01-16 | 10:23 | 49.908
2021-01-16 | 10:23 | 49.908
2021-01-16 | 10:23 | 49.909
2021-01-16 | 10:23 | 49.91
2021-01-16 | 10:23 | 49.91
2021-01-16 | 10:23 | 49.91
2021-01-16 | 10:23 | 49.91
2021-01-16 | 10:23 | 49.913
2021-01-16 | 10:23 | 49.914
2021-01-16 | 10:23 | 49.918
2021-01-16 | 10:23 | 49.92
2021-01-16 | 10:23 | 49.922
2021-01-16 | 10:23 | 49.922
2021-01-16 | 10:23 | 49.925
2021-01-16 | 10:23 | 49.922
2021-01-16 | 10:23 | 49.923
2021-01-16 | 10:23 | 49.92
2021-01-16 | 10:23 | 49.919
2021-01-16 | 10:23 | 49.917
2021-01-16 | 10:23 | 49.917
2021-01-16 | 10:23 | 49.917
2021-01-16 | 10:23 | 49.916
2021-01-16 | 10:23 | 49.916
2021-01-16 | 10:23 | 49.912
2021-01-16 | 10:23 | 49.912
2021-01-16 | 10:23 | 49.913
2021-01-16 | 10:23 | 49.916
2021-01-16 | 10:23 | 49.918
2021-01-16 | 10:23 | 49.918
2021-01-16 | 10:23 | 49.917
2021-01-16 | 10:23 | 49.918
2021-01-16 | 10:23 | 49.918
2021-01-16 | 10:23 | 49.917
2021-01-16 | 10:23 | 49.914
2021-01-16 | 10:23 | 49.911
2021-01-16 | 10:23 | 49.907
2021-01-16 | 10:23 | 49.909
2021-01-16 | 10:23 | 49.909
2021-01-16 | 10:23 | 49.91
2021-01-16 | 10:23 | 49.909
2021-01-16 | 10:23 | 49.911
2021-01-16 | 10:23 | 49.908
2021-01-16 | 10:23 | 49.91
2021-01-16 | 10:23 | 49.911
2021-01-16 | 10:24 | 49.915
2021-01-16 | 10:24 | 49.915
2021-01-16 | 10:24 | 49.915
2021-01-16 | 10:24 | 49.916
2021-01-16 | 10:24 | 49.915
2021-01-16 | 10:24 | 49.913
2021-01-16 | 10:24 | 49.912
2021-01-16 | 10:24 | 49.911
2021-01-16 | 10:24 | 49.91
2021-01-16 | 10:24 | 49.909
2021-01-16 | 10:24 | 49.908
2021-01-16 | 10:24 | 49.912
2021-01-16 | 10:24 | 49.911
2021-01-16 | 10:24 | 49.911
2021-01-16 | 10:24 | 49.909
2021-01-16 | 10:24 | 49.908
2021-01-16 | 10:24 | 49.907
2021-01-16 | 10:24 | 49.905
2021-01-16 | 10:24 | 49.906
2021-01-16 | 10:24 | 49.904
2021-01-16 | 10:24 | 49.907
2021-01-16 | 10:24 | 49.907
2021-01-16 | 10:24 | 49.911
2021-01-16 | 10:24 | 49.913
2021-01-16 | 10:24 | 49.916
2021-01-16 | 10:24 | 49.919
2021-01-16 | 10:24 | 49.922
2021-01-16 | 10:24 | 49.922
2021-01-16 | 10:24 | 49.926
2021-01-16 | 10:24 | 49.926
2021-01-16 | 10:24 | 49.926
2021-01-16 | 10:24 | 49.921
2021-01-16 | 10:24 | 49.919
2021-01-16 | 10:24 | 49.915
2021-01-16 | 10:24 | 49.917
2021-01-16 | 10:24 | 49.917
2021-01-16 | 10:24 | 49.917
2021-01-16 | 10:24 | 49.915
2021-01-16 | 10:24 | 49.915
2021-01-16 | 10:24 | 49.915
2021-01-16 | 10:24 | 49.92
2021-01-16 | 10:24 | 49.921
2021-01-16 | 10:24 | 49.922
2021-01-16 | 10:24 | 49.918
2021-01-16 | 10:24 | 49.915
2021-01-16 | 10:24 | 49.911
2021-01-16 | 10:24 | 49.908
2021-01-16 | 10:24 | 49.905
2021-01-16 | 10:24 | 49.904
2021-01-16 | 10:24 | 49.905
2021-01-16 | 10:24 | 49.907
2021-01-16 | 10:24 | 49.907
2021-01-16 | 10:24 | 49.909
2021-01-16 | 10:24 | 49.908
2021-01-16 | 10:24 | 49.91
2021-01-16 | 10:24 | 49.91
2021-01-16 | 10:24 | 49.912
2021-01-16 | 10:24 | 49.911
2021-01-16 | 10:24 | 49.912
2021-01-16 | 10:24 | 49.911
2021-01-16 | 10:24 | 49.909
2021-01-16 | 10:25 | 49.908
2021-01-16 | 10:25 | 49.908
2021-01-16 | 10:25 | 49.908
2021-01-16 | 10:25 | 49.912
2021-01-16 | 10:25 | 49.914
2021-01-16 | 10:25 | 49.917
2021-01-16 | 10:25 | 49.918
2021-01-16 | 10:25 | 49.919
2021-01-16 | 10:25 | 49.917
2021-01-16 | 10:25 | 49.919
2021-01-16 | 10:25 | 49.919
2021-01-16 | 10:25 | 49.917
2021-01-16 | 10:25 | 49.914
2021-01-16 | 10:25 | 49.913
2021-01-16 | 10:25 | 49.91
2021-01-16 | 10:25 | 49.91
2021-01-16 | 10:25 | 49.912
2021-01-16 | 10:25 | 49.911
2021-01-16 | 10:25 | 49.914
2021-01-16 | 10:25 | 49.913
2021-01-16 | 10:25 | 49.914
2021-01-16 | 10:25 | 49.912
2021-01-16 | 10:25 | 49.913
2021-01-16 | 10:25 | 49.912
2021-01-16 | 10:25 | 49.914
2021-01-16 | 10:25 | 49.918
2021-01-16 | 10:25 | 49.922
2021-01-16 | 10:25 | 49.925
2021-01-16 | 10:25 | 49.927
2021-01-16 | 10:25 | 49.929
2021-01-16 | 10:25 | 49.927
2021-01-16 | 10:25 | 49.928
2021-01-16 | 10:25 | 49.927
2021-01-16 | 10:25 | 49.928
2021-01-16 | 10:25 | 49.926
2021-01-16 | 10:25 | 49.925
2021-01-16 | 10:25 | 49.923
2021-01-16 | 10:25 | 49.923
2021-01-16 | 10:25 | 49.925
2021-01-16 | 10:25 | 49.924
2021-01-16 | 10:25 | 49.927
2021-01-16 | 10:25 | 49.926
2021-01-16 | 10:25 | 49.929
2021-01-16 | 10:25 | 49.927
2021-01-16 | 10:25 | 49.928
2021-01-16 | 10:25 | 49.929
2021-01-16 | 10:25 | 49.93
2021-01-16 | 10:25 | 49.931
2021-01-16 | 10:25 | 49.93
2021-01-16 | 10:25 | 49.93
2021-01-16 | 10:25 | 49.926
2021-01-16 | 10:25 | 49.924
2021-01-16 | 10:25 | 49.923
2021-01-16 | 10:25 | 49.922
2021-01-16 | 10:25 | 49.923
2021-01-16 | 10:25 | 49.921
2021-01-16 | 10:25 | 49.921
2021-01-16 | 10:25 | 49.917
2021-01-16 | 10:25 | 49.917
2021-01-16 | 10:26 | 49.917
2021-01-16 | 10:26 | 49.917
2021-01-16 | 10:26 | 49.918
2021-01-16 | 10:26 | 49.919
2021-01-16 | 10:26 | 49.921
2021-01-16 | 10:26 | 49.923
2021-01-16 | 10:26 | 49.927
2021-01-16 | 10:26 | 49.926
2021-01-16 | 10:26 | 49.926
2021-01-16 | 10:26 | 49.926
2021-01-16 | 10:26 | 49.926
2021-01-16 | 10:26 | 49.926
2021-01-16 | 10:26 | 49.926
2021-01-16 | 10:26 | 49.926
2021-01-16 | 10:26 | 49.924
2021-01-16 | 10:26 | 49.925
2021-01-16 | 10:26 | 49.926
2021-01-16 | 10:26 | 49.927
2021-01-16 | 10:26 | 49.927
2021-01-16 | 10:26 | 49.927
2021-01-16 | 10:26 | 49.925
2021-01-16 | 10:26 | 49.923
2021-01-16 | 10:26 | 49.923
2021-01-16 | 10:26 | 49.923
2021-01-16 | 10:26 | 49.922
2021-01-16 | 10:26 | 49.924
2021-01-16 | 10:26 | 49.921
2021-01-16 | 10:26 | 49.923
2021-01-16 | 10:26 | 49.92
2021-01-16 | 10:26 | 49.916
2021-01-16 | 10:26 | 49.914
2021-01-16 | 10:26 | 49.91
2021-01-16 | 10:26 | 49.907
2021-01-16 | 10:26 | 49.902
2021-01-16 | 10:26 | 49.9
2021-01-16 | 10:26 | 49.902
2021-01-16 | 10:26 | 49.903
2021-01-16 | 10:26 | 49.908
2021-01-16 | 10:26 | 49.91
2021-01-16 | 10:26 | 49.913
2021-01-16 | 10:26 | 49.916
2021-01-16 | 10:26 | 49.917
2021-01-16 | 10:26 | 49.918
2021-01-16 | 10:26 | 49.919
2021-01-16 | 10:26 | 49.919
2021-01-16 | 10:26 | 49.922
2021-01-16 | 10:26 | 49.922
2021-01-16 | 10:26 | 49.923
2021-01-16 | 10:26 | 49.921
2021-01-16 | 10:26 | 49.918
2021-01-16 | 10:26 | 49.916
2021-01-16 | 10:26 | 49.916
2021-01-16 | 10:26 | 49.916
2021-01-16 | 10:26 | 49.92
2021-01-16 | 10:26 | 49.921
2021-01-16 | 10:26 | 49.921
2021-01-16 | 10:26 | 49.922
2021-01-16 | 10:26 | 49.923
2021-01-16 | 10:26 | 49.923
2021-01-16 | 10:26 | 49.922
2021-01-16 | 10:26 | 49.918
2021-01-16 | 10:27 | 49.915
2021-01-16 | 10:27 | 49.913
2021-01-16 | 10:27 | 49.91
2021-01-16 | 10:27 | 49.914
2021-01-16 | 10:27 | 49.915
2021-01-16 | 10:27 | 49.918
2021-01-16 | 10:27 | 49.921
2021-01-16 | 10:27 | 49.923
2021-01-16 | 10:27 | 49.924
2021-01-16 | 10:27 | 49.926
2021-01-16 | 10:27 | 49.926
2021-01-16 | 10:27 | 49.928
2021-01-16 | 10:27 | 49.928
2021-01-16 | 10:27 | 49.929
2021-01-16 | 10:27 | 49.929
2021-01-16 | 10:27 | 49.931
2021-01-16 | 10:27 | 49.93
2021-01-16 | 10:27 | 49.931
2021-01-16 | 10:27 | 49.933
2021-01-16 | 10:27 | 49.935
2021-01-16 | 10:27 | 49.937
2021-01-16 | 10:27 | 49.941
2021-01-16 | 10:27 | 49.943
2021-01-16 | 10:27 | 49.942
2021-01-16 | 10:27 | 49.94
2021-01-16 | 10:27 | 49.94
2021-01-16 | 10:27 | 49.941
2021-01-16 | 10:27 | 49.942
2021-01-16 | 10:27 | 49.941
2021-01-16 | 10:27 | 49.938
2021-01-16 | 10:27 | 49.936
2021-01-16 | 10:27 | 49.934
2021-01-16 | 10:27 | 49.931
2021-01-16 | 10:27 | 49.931
2021-01-16 | 10:27 | 49.933
2021-01-16 | 10:27 | 49.934
2021-01-16 | 10:27 | 49.933
2021-01-16 | 10:27 | 49.931
2021-01-16 | 10:27 | 49.928
2021-01-16 | 10:27 | 49.927
2021-01-16 | 10:27 | 49.928
2021-01-16 | 10:27 | 49.927
2021-01-16 | 10:27 | 49.929
2021-01-16 | 10:27 | 49.931
2021-01-16 | 10:27 | 49.931
2021-01-16 | 10:27 | 49.931
2021-01-16 | 10:27 | 49.932
2021-01-16 | 10:27 | 49.93
2021-01-16 | 10:27 | 49.928
2021-01-16 | 10:27 | 49.927
2021-01-16 | 10:27 | 49.93
2021-01-16 | 10:27 | 49.931
2021-01-16 | 10:27 | 49.933
2021-01-16 | 10:27 | 49.938
2021-01-16 | 10:27 | 49.94
2021-01-16 | 10:27 | 49.943
2021-01-16 | 10:27 | 49.941
2021-01-16 | 10:27 | 49.945
2021-01-16 | 10:27 | 49.946
2021-01-16 | 10:28 | 49.946
2021-01-16 | 10:28 | 49.949
2021-01-16 | 10:28 | 49.951
2021-01-16 | 10:28 | 49.952
2021-01-16 | 10:28 | 49.953
2021-01-16 | 10:28 | 49.951
2021-01-16 | 10:28 | 49.95
2021-01-16 | 10:28 | 49.949
2021-01-16 | 10:28 | 49.947
2021-01-16 | 10:28 | 49.947
2021-01-16 | 10:28 | 49.945
2021-01-16 | 10:28 | 49.944
2021-01-16 | 10:28 | 49.942
2021-01-16 | 10:28 | 49.941
2021-01-16 | 10:28 | 49.937
2021-01-16 | 10:28 | 49.937
2021-01-16 | 10:28 | 49.938
2021-01-16 | 10:28 | 49.935
2021-01-16 | 10:28 | 49.934
2021-01-16 | 10:28 | 49.935
2021-01-16 | 10:28 | 49.935
2021-01-16 | 10:28 | 49.934
2021-01-16 | 10:28 | 49.935
2021-01-16 | 10:28 | 49.938
2021-01-16 | 10:28 | 49.937
2021-01-16 | 10:28 | 49.937
2021-01-16 | 10:28 | 49.939
2021-01-16 | 10:28 | 49.938
2021-01-16 | 10:28 | 49.937
2021-01-16 | 10:28 | 49.937
2021-01-16 | 10:28 | 49.936
2021-01-16 | 10:28 | 49.934
2021-01-16 | 10:28 | 49.933
2021-01-16 | 10:28 | 49.93
2021-01-16 | 10:28 | 49.928
2021-01-16 | 10:28 | 49.927
2021-01-16 | 10:28 | 49.927
2021-01-16 | 10:28 | 49.928
2021-01-16 | 10:28 | 49.931
2021-01-16 | 10:28 | 49.931
2021-01-16 | 10:28 | 49.936
2021-01-16 | 10:28 | 49.935
2021-01-16 | 10:28 | 49.936
2021-01-16 | 10:28 | 49.935
2021-01-16 | 10:28 | 49.931
2021-01-16 | 10:28 | 49.931
2021-01-16 | 10:28 | 49.929
2021-01-16 | 10:28 | 49.928
2021-01-16 | 10:28 | 49.925
2021-01-16 | 10:28 | 49.923
2021-01-16 | 10:28 | 49.917
2021-01-16 | 10:28 | 49.916
2021-01-16 | 10:28 | 49.913
2021-01-16 | 10:28 | 49.914
2021-01-16 | 10:28 | 49.915
2021-01-16 | 10:28 | 49.915
2021-01-16 | 10:28 | 49.909
2021-01-16 | 10:28 | 49.907
2021-01-16 | 10:28 | 49.906
2021-01-16 | 10:28 | 49.906
2021-01-16 | 10:28 | 49.907
2021-01-16 | 10:29 | 49.908
2021-01-16 | 10:29 | 49.908
2021-01-16 | 10:29 | 49.909
2021-01-16 | 10:29 | 49.911
2021-01-16 | 10:29 | 49.91
2021-01-16 | 10:29 | 49.909
2021-01-16 | 10:29 | 49.907
2021-01-16 | 10:29 | 49.906
2021-01-16 | 10:29 | 49.907
2021-01-16 | 10:29 | 49.909
2021-01-16 | 10:29 | 49.91
2021-01-16 | 10:29 | 49.912
2021-01-16 | 10:29 | 49.914
2021-01-16 | 10:29 | 49.915
2021-01-16 | 10:29 | 49.915
2021-01-16 | 10:29 | 49.914
2021-01-16 | 10:29 | 49.914
2021-01-16 | 10:29 | 49.915
2021-01-16 | 10:29 | 49.914
2021-01-16 | 10:29 | 49.914
2021-01-16 | 10:29 | 49.913
2021-01-16 | 10:29 | 49.911
2021-01-16 | 10:29 | 49.909
2021-01-16 | 10:29 | 49.911
2021-01-16 | 10:29 | 49.912
2021-01-16 | 10:29 | 49.915
2021-01-16 | 10:29 | 49.916
2021-01-16 | 10:29 | 49.913
2021-01-16 | 10:29 | 49.913
2021-01-16 | 10:29 | 49.91
2021-01-16 | 10:29 | 49.909
2021-01-16 | 10:29 | 49.909
2021-01-16 | 10:29 | 49.912
2021-01-16 | 10:29 | 49.911
2021-01-16 | 10:29 | 49.909
2021-01-16 | 10:29 | 49.908
2021-01-16 | 10:29 | 49.909
2021-01-16 | 10:29 | 49.906
2021-01-16 | 10:29 | 49.906
2021-01-16 | 10:29 | 49.905
2021-01-16 | 10:29 | 49.904
2021-01-16 | 10:29 | 49.902
2021-01-16 | 10:29 | 49.898
2021-01-16 | 10:29 | 49.898
2021-01-16 | 10:29 | 49.899
2021-01-16 | 10:29 | 49.9
2021-01-16 | 10:29 | 49.9
2021-01-16 | 10:29 | 49.901
2021-01-16 | 10:29 | 49.901
2021-01-16 | 10:29 | 49.9
2021-01-16 | 10:29 | 49.899
2021-01-16 | 10:29 | 49.898
2021-01-16 | 10:29 | 49.896
2021-01-16 | 10:29 | 49.899
2021-01-16 | 10:29 | 49.898
2021-01-16 | 10:29 | 49.9
2021-01-16 | 10:29 | 49.903
2021-01-16 | 10:29 | 49.905
2021-01-16 | 10:29 | 49.907
2021-01-16 | 10:30 | 49.908
2021-01-16 | 10:30 | 49.908
2021-01-16 | 10:30 | 49.91
2021-01-16 | 10:30 | 49.913
2021-01-16 | 10:30 | 49.916
2021-01-16 | 10:30 | 49.919
2021-01-16 | 10:30 | 49.921
2021-01-16 | 10:30 | 49.923
2021-01-16 | 10:30 | 49.925
2021-01-16 | 10:30 | 49.928
2021-01-16 | 10:30 | 49.927
2021-01-16 | 10:30 | 49.925
2021-01-16 | 10:30 | 49.921
2021-01-16 | 10:30 | 49.915
2021-01-16 | 10:30 | 49.914
2021-01-16 | 10:30 | 49.912
2021-01-16 | 10:30 | 49.914
2021-01-16 | 10:30 | 49.912
2021-01-16 | 10:30 | 49.913
2021-01-16 | 10:30 | 49.913
2021-01-16 | 10:30 | 49.914
2021-01-16 | 10:30 | 49.913
2021-01-16 | 10:30 | 49.915
2021-01-16 | 10:30 | 49.915
2021-01-16 | 10:30 | 49.915
2021-01-16 | 10:30 | 49.913
2021-01-16 | 10:30 | 49.912
2021-01-16 | 10:30 | 49.91
2021-01-16 | 10:30 | 49.908
2021-01-16 | 10:30 | 49.906
2021-01-16 | 10:30 | 49.903
2021-01-16 | 10:30 | 49.898
2021-01-16 | 10:30 | 49.894
2021-01-16 | 10:30 | 49.893
2021-01-16 | 10:30 | 49.892
2021-01-16 | 10:30 | 49.892
2021-01-16 | 10:30 | 49.892
2021-01-16 | 10:30 | 49.893
2021-01-16 | 10:30 | 49.891
2021-01-16 | 10:30 | 49.89
2021-01-16 | 10:30 | 49.888
2021-01-16 | 10:30 | 49.889
2021-01-16 | 10:30 | 49.888
2021-01-16 | 10:30 | 49.889
2021-01-16 | 10:30 | 49.888
2021-01-16 | 10:30 | 49.887
2021-01-16 | 10:30 | 49.884
2021-01-16 | 10:30 | 49.882
2021-01-16 | 10:30 | 49.879
2021-01-16 | 10:30 | 49.877
2021-01-16 | 10:30 | 49.877
2021-01-16 | 10:30 | 49.876
2021-01-16 | 10:30 | 49.877
2021-01-16 | 10:30 | 49.878
2021-01-16 | 10:30 | 49.879
2021-01-16 | 10:30 | 49.881
2021-01-16 | 10:30 | 49.881
2021-01-16 | 10:30 | 49.881
2021-01-16 | 10:30 | 49.88
2021-01-16 | 10:30 | 49.879
2021-01-16 | 10:30 | 49.875
2021-01-16 | 10:31 | 49.874
2021-01-16 | 10:31 | 49.871
2021-01-16 | 10:31 | 49.872
2021-01-16 | 10:31 | 49.869
2021-01-16 | 10:31 | 49.867
2021-01-16 | 10:31 | 49.866
2021-01-16 | 10:31 | 49.865
2021-01-16 | 10:31 | 49.866
2021-01-16 | 10:31 | 49.866
2021-01-16 | 10:31 | 49.865
2021-01-16 | 10:31 | 49.865
2021-01-16 | 10:31 | 49.865
2021-01-16 | 10:31 | 49.867
2021-01-16 | 10:31 | 49.868
2021-01-16 | 10:31 | 49.87
2021-01-16 | 10:31 | 49.871
2021-01-16 | 10:31 | 49.87
2021-01-16 | 10:31 | 49.867
2021-01-16 | 10:31 | 49.866
2021-01-16 | 10:31 | 49.865
2021-01-16 | 10:31 | 49.863
2021-01-16 | 10:31 | 49.863
2021-01-16 | 10:31 | 49.864
2021-01-16 | 10:31 | 49.865
2021-01-16 | 10:31 | 49.867
2021-01-16 | 10:31 | 49.871
2021-01-16 | 10:31 | 49.873
2021-01-16 | 10:31 | 49.876
2021-01-16 | 10:31 | 49.878
2021-01-16 | 10:31 | 49.878
2021-01-16 | 10:31 | 49.877
2021-01-16 | 10:31 | 49.875
2021-01-16 | 10:31 | 49.877
2021-01-16 | 10:31 | 49.875
2021-01-16 | 10:31 | 49.872
2021-01-16 | 10:31 | 49.866
2021-01-16 | 10:31 | 49.865
2021-01-16 | 10:31 | 49.867
2021-01-16 | 10:31 | 49.871
2021-01-16 | 10:31 | 49.875
2021-01-16 | 10:31 | 49.881
2021-01-16 | 10:31 | 49.885
2021-01-16 | 10:31 | 49.887
2021-01-16 | 10:31 | 49.89
2021-01-16 | 10:31 | 49.893
2021-01-16 | 10:31 | 49.896
2021-01-16 | 10:31 | 49.894
2021-01-16 | 10:31 | 49.892
2021-01-16 | 10:31 | 49.888
2021-01-16 | 10:31 | 49.883
2021-01-16 | 10:31 | 49.881
2021-01-16 | 10:31 | 49.879
2021-01-16 | 10:31 | 49.88
2021-01-16 | 10:31 | 49.88
2021-01-16 | 10:31 | 49.881
2021-01-16 | 10:31 | 49.881
2021-01-16 | 10:31 | 49.878
2021-01-16 | 10:31 | 49.879
2021-01-16 | 10:31 | 49.879
2021-01-16 | 10:32 | 49.88
2021-01-16 | 10:32 | 49.881
2021-01-16 | 10:32 | 49.882
2021-01-16 | 10:32 | 49.883
2021-01-16 | 10:32 | 49.882
2021-01-16 | 10:32 | 49.886
2021-01-16 | 10:32 | 49.89
2021-01-16 | 10:32 | 49.891
2021-01-16 | 10:32 | 49.893
2021-01-16 | 10:32 | 49.894
2021-01-16 | 10:32 | 49.897
2021-01-16 | 10:32 | 49.899
2021-01-16 | 10:32 | 49.901
2021-01-16 | 10:32 | 49.902
2021-01-16 | 10:32 | 49.902
2021-01-16 | 10:32 | 49.903
2021-01-16 | 10:32 | 49.901
2021-01-16 | 10:32 | 49.9
2021-01-16 | 10:32 | 49.9
2021-01-16 | 10:32 | 49.899
2021-01-16 | 10:32 | 49.901
2021-01-16 | 10:32 | 49.9
2021-01-16 | 10:32 | 49.9
2021-01-16 | 10:32 | 49.902
2021-01-16 | 10:32 | 49.902
2021-01-16 | 10:32 | 49.904
2021-01-16 | 10:32 | 49.905
2021-01-16 | 10:32 | 49.905
2021-01-16 | 10:32 | 49.907
2021-01-16 | 10:32 | 49.905
2021-01-16 | 10:32 | 49.906
2021-01-16 | 10:32 | 49.904
2021-01-16 | 10:32 | 49.903
2021-01-16 | 10:32 | 49.904
2021-01-16 | 10:32 | 49.902
2021-01-16 | 10:32 | 49.903
2021-01-16 | 10:32 | 49.903
2021-01-16 | 10:32 | 49.905
2021-01-16 | 10:32 | 49.906
2021-01-16 | 10:32 | 49.909
2021-01-16 | 10:32 | 49.912
2021-01-16 | 10:32 | 49.913
2021-01-16 | 10:32 | 49.913
2021-01-16 | 10:32 | 49.912
2021-01-16 | 10:32 | 49.912
2021-01-16 | 10:32 | 49.912
2021-01-16 | 10:32 | 49.913
2021-01-16 | 10:32 | 49.912
2021-01-16 | 10:32 | 49.912
2021-01-16 | 10:32 | 49.91
2021-01-16 | 10:32 | 49.907
2021-01-16 | 10:32 | 49.906
2021-01-16 | 10:32 | 49.906
2021-01-16 | 10:32 | 49.907
2021-01-16 | 10:32 | 49.909
2021-01-16 | 10:32 | 49.91
2021-01-16 | 10:32 | 49.911
2021-01-16 | 10:32 | 49.911
2021-01-16 | 10:32 | 49.91
2021-01-16 | 10:32 | 49.909
2021-01-16 | 10:32 | 49.908
2021-01-16 | 10:33 | 49.907
2021-01-16 | 10:33 | 49.906
2021-01-16 | 10:33 | 49.904
2021-01-16 | 10:33 | 49.904
2021-01-16 | 10:33 | 49.905
2021-01-16 | 10:33 | 49.906
2021-01-16 | 10:33 | 49.909
2021-01-16 | 10:33 | 49.911
2021-01-16 | 10:33 | 49.912
2021-01-16 | 10:33 | 49.912
2021-01-16 | 10:33 | 49.909
2021-01-16 | 10:33 | 49.908
2021-01-16 | 10:33 | 49.906
2021-01-16 | 10:33 | 49.907
2021-01-16 | 10:33 | 49.909
2021-01-16 | 10:33 | 49.911
2021-01-16 | 10:33 | 49.914
2021-01-16 | 10:33 | 49.913
2021-01-16 | 10:33 | 49.913
2021-01-16 | 10:33 | 49.913
2021-01-16 | 10:33 | 49.914
2021-01-16 | 10:33 | 49.917
2021-01-16 | 10:33 | 49.919
2021-01-16 | 10:33 | 49.922
2021-01-16 | 10:33 | 49.922
2021-01-16 | 10:33 | 49.921
2021-01-16 | 10:33 | 49.92
2021-01-16 | 10:33 | 49.919
2021-01-16 | 10:33 | 49.919
2021-01-16 | 10:33 | 49.917
2021-01-16 | 10:33 | 49.912
2021-01-16 | 10:33 | 49.909
2021-01-16 | 10:33 | 49.908
2021-01-16 | 10:33 | 49.907
2021-01-16 | 10:33 | 49.907
2021-01-16 | 10:33 | 49.905
2021-01-16 | 10:33 | 49.906
2021-01-16 | 10:33 | 49.905
2021-01-16 | 10:33 | 49.902
2021-01-16 | 10:33 | 49.901
2021-01-16 | 10:33 | 49.902
2021-01-16 | 10:33 | 49.9
2021-01-16 | 10:33 | 49.901
2021-01-16 | 10:33 | 49.901
2021-01-16 | 10:33 | 49.902
2021-01-16 | 10:33 | 49.906
2021-01-16 | 10:33 | 49.906
2021-01-16 | 10:33 | 49.908
2021-01-16 | 10:33 | 49.907
2021-01-16 | 10:33 | 49.909
2021-01-16 | 10:33 | 49.91
2021-01-16 | 10:33 | 49.912
2021-01-16 | 10:33 | 49.914
2021-01-16 | 10:33 | 49.914
2021-01-16 | 10:33 | 49.913
2021-01-16 | 10:33 | 49.911
2021-01-16 | 10:33 | 49.909
2021-01-16 | 10:33 | 49.908
2021-01-16 | 10:33 | 49.908
2021-01-16 | 10:34 | 49.907
2021-01-16 | 10:34 | 49.909
2021-01-16 | 10:34 | 49.912
2021-01-16 | 10:34 | 49.915
2021-01-16 | 10:34 | 49.917
2021-01-16 | 10:34 | 49.917
2021-01-16 | 10:34 | 49.917
2021-01-16 | 10:34 | 49.916
2021-01-16 | 10:34 | 49.914
2021-01-16 | 10:34 | 49.914
2021-01-16 | 10:34 | 49.913
2021-01-16 | 10:34 | 49.914
2021-01-16 | 10:34 | 49.916
2021-01-16 | 10:34 | 49.919
2021-01-16 | 10:34 | 49.919
2021-01-16 | 10:34 | 49.92
2021-01-16 | 10:34 | 49.918
2021-01-16 | 10:34 | 49.914
2021-01-16 | 10:34 | 49.913
2021-01-16 | 10:34 | 49.914
2021-01-16 | 10:34 | 49.914
2021-01-16 | 10:34 | 49.915
2021-01-16 | 10:34 | 49.913
2021-01-16 | 10:34 | 49.914
2021-01-16 | 10:34 | 49.912
2021-01-16 | 10:34 | 49.912
2021-01-16 | 10:34 | 49.91
2021-01-16 | 10:34 | 49.909
2021-01-16 | 10:34 | 49.91
2021-01-16 | 10:34 | 49.91
2021-01-16 | 10:34 | 49.911
2021-01-16 | 10:34 | 49.911
2021-01-16 | 10:34 | 49.913
2021-01-16 | 10:34 | 49.913
2021-01-16 | 10:34 | 49.914
2021-01-16 | 10:34 | 49.915
2021-01-16 | 10:34 | 49.915
2021-01-16 | 10:34 | 49.916
2021-01-16 | 10:34 | 49.917
2021-01-16 | 10:34 | 49.918
2021-01-16 | 10:34 | 49.92
2021-01-16 | 10:34 | 49.921
2021-01-16 | 10:34 | 49.922
2021-01-16 | 10:34 | 49.923
2021-01-16 | 10:34 | 49.928
2021-01-16 | 10:34 | 49.931
2021-01-16 | 10:34 | 49.934
2021-01-16 | 10:34 | 49.937
2021-01-16 | 10:34 | 49.94
2021-01-16 | 10:34 | 49.942
2021-01-16 | 10:34 | 49.94
2021-01-16 | 10:34 | 49.938
2021-01-16 | 10:34 | 49.937
2021-01-16 | 10:34 | 49.936
2021-01-16 | 10:34 | 49.936
2021-01-16 | 10:34 | 49.936
2021-01-16 | 10:34 | 49.935
2021-01-16 | 10:34 | 49.937
2021-01-16 | 10:34 | 49.938
2021-01-16 | 10:34 | 49.941
2021-01-16 | 10:34 | 49.938
2021-01-16 | 10:35 | 49.936
2021-01-16 | 10:35 | 49.934
2021-01-16 | 10:35 | 49.937
2021-01-16 | 10:35 | 49.937
2021-01-16 | 10:35 | 49.936
2021-01-16 | 10:35 | 49.936
2021-01-16 | 10:35 | 49.932
2021-01-16 | 10:35 | 49.929
2021-01-16 | 10:35 | 49.929
2021-01-16 | 10:35 | 49.929
2021-01-16 | 10:35 | 49.932
2021-01-16 | 10:35 | 49.934
2021-01-16 | 10:35 | 49.935
2021-01-16 | 10:35 | 49.934
2021-01-16 | 10:35 | 49.933
2021-01-16 | 10:35 | 49.932
2021-01-16 | 10:35 | 49.932
2021-01-16 | 10:35 | 49.93
2021-01-16 | 10:35 | 49.929
2021-01-16 | 10:35 | 49.929
2021-01-16 | 10:35 | 49.93
2021-01-16 | 10:35 | 49.931
2021-01-16 | 10:35 | 49.93
2021-01-16 | 10:35 | 49.93
2021-01-16 | 10:35 | 49.93
2021-01-16 | 10:35 | 49.93
2021-01-16 | 10:35 | 49.93
2021-01-16 | 10:35 | 49.931
2021-01-16 | 10:35 | 49.929
2021-01-16 | 10:35 | 49.925
2021-01-16 | 10:35 | 49.924
2021-01-16 | 10:35 | 49.924
2021-01-16 | 10:35 | 49.926
2021-01-16 | 10:35 | 49.926
2021-01-16 | 10:35 | 49.93
2021-01-16 | 10:35 | 49.931
2021-01-16 | 10:35 | 49.934
2021-01-16 | 10:35 | 49.932
2021-01-16 | 10:35 | 49.932
2021-01-16 | 10:35 | 49.93
2021-01-16 | 10:35 | 49.931
2021-01-16 | 10:35 | 49.931
2021-01-16 | 10:35 | 49.933
2021-01-16 | 10:35 | 49.933
2021-01-16 | 10:35 | 49.934
2021-01-16 | 10:35 | 49.933
2021-01-16 | 10:35 | 49.933
2021-01-16 | 10:35 | 49.933
2021-01-16 | 10:35 | 49.935
2021-01-16 | 10:35 | 49.934
2021-01-16 | 10:35 | 49.936
2021-01-16 | 10:35 | 49.936
2021-01-16 | 10:35 | 49.936
2021-01-16 | 10:35 | 49.936
2021-01-16 | 10:35 | 49.935
2021-01-16 | 10:35 | 49.935
2021-01-16 | 10:35 | 49.934
2021-01-16 | 10:35 | 49.934
2021-01-16 | 10:35 | 49.934
2021-01-16 | 10:36 | 49.933
2021-01-16 | 10:36 | 49.934
2021-01-16 | 10:36 | 49.935
2021-01-16 | 10:36 | 49.933
2021-01-16 | 10:36 | 49.932
2021-01-16 | 10:36 | 49.93
2021-01-16 | 10:36 | 49.933
2021-01-16 | 10:36 | 49.931
2021-01-16 | 10:36 | 49.929
2021-01-16 | 10:36 | 49.932
2021-01-16 | 10:36 | 49.929
2021-01-16 | 10:36 | 49.931
2021-01-16 | 10:36 | 49.928
2021-01-16 | 10:36 | 49.929
2021-01-16 | 10:36 | 49.927
2021-01-16 | 10:36 | 49.927
2021-01-16 | 10:36 | 49.927
2021-01-16 | 10:36 | 49.927
2021-01-16 | 10:36 | 49.926
2021-01-16 | 10:36 | 49.927
2021-01-16 | 10:36 | 49.927
2021-01-16 | 10:36 | 49.932
2021-01-16 | 10:36 | 49.933
2021-01-16 | 10:36 | 49.936
2021-01-16 | 10:36 | 49.938
2021-01-16 | 10:36 | 49.942
2021-01-16 | 10:36 | 49.941
2021-01-16 | 10:36 | 49.941
2021-01-16 | 10:36 | 49.939
2021-01-16 | 10:36 | 49.94
2021-01-16 | 10:36 | 49.941
2021-01-16 | 10:36 | 49.943
2021-01-16 | 10:36 | 49.944
2021-01-16 | 10:36 | 49.945
2021-01-16 | 10:36 | 49.947
2021-01-16 | 10:36 | 49.947
2021-01-16 | 10:36 | 49.949
2021-01-16 | 10:36 | 49.948
2021-01-16 | 10:36 | 49.952
2021-01-16 | 10:36 | 49.953
2021-01-16 | 10:36 | 49.956
2021-01-16 | 10:36 | 49.96
2021-01-16 | 10:36 | 49.961
2021-01-16 | 10:36 | 49.959
2021-01-16 | 10:36 | 49.956
2021-01-16 | 10:36 | 49.955
2021-01-16 | 10:36 | 49.951
2021-01-16 | 10:36 | 49.951
2021-01-16 | 10:36 | 49.951
2021-01-16 | 10:36 | 49.952
2021-01-16 | 10:36 | 49.953
2021-01-16 | 10:36 | 49.951
2021-01-16 | 10:36 | 49.952
2021-01-16 | 10:36 | 49.95
2021-01-16 | 10:36 | 49.951
2021-01-16 | 10:36 | 49.952
2021-01-16 | 10:36 | 49.953
2021-01-16 | 10:36 | 49.954
2021-01-16 | 10:36 | 49.955
2021-01-16 | 10:36 | 49.957
2021-01-16 | 10:36 | 49.957
2021-01-16 | 10:37 | 49.96
2021-01-16 | 10:37 | 49.961
2021-01-16 | 10:37 | 49.963
2021-01-16 | 10:37 | 49.964
2021-01-16 | 10:37 | 49.962
2021-01-16 | 10:37 | 49.963
2021-01-16 | 10:37 | 49.963
2021-01-16 | 10:37 | 49.966
2021-01-16 | 10:37 | 49.965
2021-01-16 | 10:37 | 49.964
2021-01-16 | 10:37 | 49.964
2021-01-16 | 10:37 | 49.965
2021-01-16 | 10:37 | 49.966
2021-01-16 | 10:37 | 49.968
2021-01-16 | 10:37 | 49.97
2021-01-16 | 10:37 | 49.972
2021-01-16 | 10:37 | 49.972
2021-01-16 | 10:37 | 49.972
2021-01-16 | 10:37 | 49.971
2021-01-16 | 10:37 | 49.97
2021-01-16 | 10:37 | 49.968
2021-01-16 | 10:37 | 49.965
2021-01-16 | 10:37 | 49.967
2021-01-16 | 10:37 | 49.965
2021-01-16 | 10:37 | 49.965
2021-01-16 | 10:37 | 49.965
2021-01-16 | 10:37 | 49.966
2021-01-16 | 10:37 | 49.966
2021-01-16 | 10:37 | 49.97
2021-01-16 | 10:37 | 49.973
2021-01-16 | 10:37 | 49.974
2021-01-16 | 10:37 | 49.975
2021-01-16 | 10:37 | 49.976
2021-01-16 | 10:37 | 49.972
2021-01-16 | 10:37 | 49.968
2021-01-16 | 10:37 | 49.966
2021-01-16 | 10:37 | 49.962
2021-01-16 | 10:37 | 49.963
2021-01-16 | 10:37 | 49.962
2021-01-16 | 10:37 | 49.958
2021-01-16 | 10:37 | 49.957
2021-01-16 | 10:37 | 49.955
2021-01-16 | 10:37 | 49.955
2021-01-16 | 10:37 | 49.955
2021-01-16 | 10:37 | 49.96
2021-01-16 | 10:37 | 49.962
2021-01-16 | 10:37 | 49.962
2021-01-16 | 10:37 | 49.959
2021-01-16 | 10:37 | 49.958
2021-01-16 | 10:37 | 49.955
2021-01-16 | 10:37 | 49.955
2021-01-16 | 10:37 | 49.956
2021-01-16 | 10:37 | 49.957
2021-01-16 | 10:37 | 49.959
2021-01-16 | 10:37 | 49.96
2021-01-16 | 10:37 | 49.961
2021-01-16 | 10:37 | 49.961
2021-01-16 | 10:37 | 49.962
2021-01-16 | 10:37 | 49.962
2021-01-16 | 10:38 | 49.961
2021-01-16 | 10:38 | 49.959
2021-01-16 | 10:38 | 49.958
2021-01-16 | 10:38 | 49.959
2021-01-16 | 10:38 | 49.963
2021-01-16 | 10:38 | 49.964
2021-01-16 | 10:38 | 49.968
2021-01-16 | 10:38 | 49.972
2021-01-16 | 10:38 | 49.976
2021-01-16 | 10:38 | 49.979
2021-01-16 | 10:38 | 49.978
2021-01-16 | 10:38 | 49.978
2021-01-16 | 10:38 | 49.977
2021-01-16 | 10:38 | 49.975
2021-01-16 | 10:38 | 49.976
2021-01-16 | 10:38 | 49.977
2021-01-16 | 10:38 | 49.977
2021-01-16 | 10:38 | 49.977
2021-01-16 | 10:38 | 49.976
2021-01-16 | 10:38 | 49.977
2021-01-16 | 10:38 | 49.977
2021-01-16 | 10:38 | 49.976
2021-01-16 | 10:38 | 49.974
2021-01-16 | 10:38 | 49.977
2021-01-16 | 10:38 | 49.976
2021-01-16 | 10:38 | 49.974
2021-01-16 | 10:38 | 49.973
2021-01-16 | 10:38 | 49.974
2021-01-16 | 10:38 | 49.976
2021-01-16 | 10:38 | 49.976
2021-01-16 | 10:38 | 49.977
2021-01-16 | 10:38 | 49.972
2021-01-16 | 10:38 | 49.97
2021-01-16 | 10:38 | 49.968
2021-01-16 | 10:38 | 49.971
2021-01-16 | 10:38 | 49.971
2021-01-16 | 10:38 | 49.976
2021-01-16 | 10:38 | 49.978
2021-01-16 | 10:38 | 49.982
2021-01-16 | 10:38 | 49.987
2021-01-16 | 10:38 | 49.988
2021-01-16 | 10:38 | 49.987
2021-01-16 | 10:38 | 49.986
2021-01-16 | 10:38 | 49.984
2021-01-16 | 10:38 | 49.985
2021-01-16 | 10:38 | 49.987
2021-01-16 | 10:38 | 49.989
2021-01-16 | 10:38 | 49.989
2021-01-16 | 10:38 | 49.991
2021-01-16 | 10:38 | 49.992
2021-01-16 | 10:38 | 49.993
2021-01-16 | 10:38 | 49.993
2021-01-16 | 10:38 | 49.995
2021-01-16 | 10:38 | 49.996
2021-01-16 | 10:38 | 49.995
2021-01-16 | 10:38 | 49.997
2021-01-16 | 10:38 | 49.998
2021-01-16 | 10:38 | 49.997
2021-01-16 | 10:38 | 50
2021-01-16 | 10:38 | 49.997
2021-01-16 | 10:38 | 49.998
2021-01-16 | 10:39 | 49.996
2021-01-16 | 10:39 | 49.997
2021-01-16 | 10:39 | 49.994
2021-01-16 | 10:39 | 49.993
2021-01-16 | 10:39 | 49.993
2021-01-16 | 10:39 | 49.991
2021-01-16 | 10:39 | 49.99
2021-01-16 | 10:39 | 49.986
2021-01-16 | 10:39 | 49.985
2021-01-16 | 10:39 | 49.985
2021-01-16 | 10:39 | 49.984
2021-01-16 | 10:39 | 49.984
2021-01-16 | 10:39 | 49.979
2021-01-16 | 10:39 | 49.979
2021-01-16 | 10:39 | 49.98
2021-01-16 | 10:39 | 49.981
2021-01-16 | 10:39 | 49.982
2021-01-16 | 10:39 | 49.985
2021-01-16 | 10:39 | 49.985
2021-01-16 | 10:39 | 49.984
2021-01-16 | 10:39 | 49.985
2021-01-16 | 10:39 | 49.982
2021-01-16 | 10:39 | 49.982
2021-01-16 | 10:39 | 49.983
2021-01-16 | 10:39 | 49.983
2021-01-16 | 10:39 | 49.983
2021-01-16 | 10:39 | 49.983
2021-01-16 | 10:39 | 49.982
2021-01-16 | 10:39 | 49.983
2021-01-16 | 10:39 | 49.981
2021-01-16 | 10:39 | 49.983
2021-01-16 | 10:39 | 49.982
2021-01-16 | 10:39 | 49.983
2021-01-16 | 10:39 | 49.983
2021-01-16 | 10:39 | 49.986
2021-01-16 | 10:39 | 49.987
2021-01-16 | 10:39 | 49.987
2021-01-16 | 10:39 | 49.989
2021-01-16 | 10:39 | 49.984
2021-01-16 | 10:39 | 49.982
2021-01-16 | 10:39 | 49.978
2021-01-16 | 10:39 | 49.978
2021-01-16 | 10:39 | 49.977
2021-01-16 | 10:39 | 49.977
2021-01-16 | 10:39 | 49.98
2021-01-16 | 10:39 | 49.981
2021-01-16 | 10:39 | 49.984
2021-01-16 | 10:39 | 49.985
2021-01-16 | 10:39 | 49.984
2021-01-16 | 10:39 | 49.984
2021-01-16 | 10:39 | 49.981
2021-01-16 | 10:39 | 49.978
2021-01-16 | 10:39 | 49.976
2021-01-16 | 10:39 | 49.973
2021-01-16 | 10:39 | 49.971
2021-01-16 | 10:39 | 49.969
2021-01-16 | 10:39 | 49.968
2021-01-16 | 10:39 | 49.966
2021-01-16 | 10:39 | 49.968
2021-01-16 | 10:40 | 49.966
2021-01-16 | 10:40 | 49.965
2021-01-16 | 10:40 | 49.961
2021-01-16 | 10:40 | 49.963
2021-01-16 | 10:40 | 49.961
2021-01-16 | 10:40 | 49.963
2021-01-16 | 10:40 | 49.959
2021-01-16 | 10:40 | 49.959
2021-01-16 | 10:40 | 49.954
2021-01-16 | 10:40 | 49.95
2021-01-16 | 10:40 | 49.949
2021-01-16 | 10:40 | 49.949
2021-01-16 | 10:40 | 49.948
2021-01-16 | 10:40 | 49.951
2021-01-16 | 10:40 | 49.952
2021-01-16 | 10:40 | 49.955
2021-01-16 | 10:40 | 49.958
2021-01-16 | 10:40 | 49.959
2021-01-16 | 10:40 | 49.958
2021-01-16 | 10:40 | 49.958
2021-01-16 | 10:40 | 49.959
2021-01-16 | 10:40 | 49.957
2021-01-16 | 10:40 | 49.959
2021-01-16 | 10:40 | 49.958
2021-01-16 | 10:40 | 49.956
2021-01-16 | 10:40 | 49.954
2021-01-16 | 10:40 | 49.951
2021-01-16 | 10:40 | 49.948
2021-01-16 | 10:40 | 49.947
2021-01-16 | 10:40 | 49.946
2021-01-16 | 10:40 | 49.946
2021-01-16 | 10:40 | 49.943
2021-01-16 | 10:40 | 49.939
2021-01-16 | 10:40 | 49.942
2021-01-16 | 10:40 | 49.942
2021-01-16 | 10:40 | 49.941
2021-01-16 | 10:40 | 49.941
2021-01-16 | 10:40 | 49.94
2021-01-16 | 10:40 | 49.937
2021-01-16 | 10:40 | 49.939
2021-01-16 | 10:40 | 49.937
2021-01-16 | 10:40 | 49.936
2021-01-16 | 10:40 | 49.931
2021-01-16 | 10:40 | 49.926
2021-01-16 | 10:40 | 49.925
2021-01-16 | 10:40 | 49.925
2021-01-16 | 10:40 | 49.925
2021-01-16 | 10:40 | 49.923
2021-01-16 | 10:40 | 49.924
2021-01-16 | 10:40 | 49.921
2021-01-16 | 10:40 | 49.922
2021-01-16 | 10:40 | 49.921
2021-01-16 | 10:40 | 49.92
2021-01-16 | 10:40 | 49.921
2021-01-16 | 10:40 | 49.921
2021-01-16 | 10:40 | 49.923
2021-01-16 | 10:40 | 49.921
2021-01-16 | 10:40 | 49.921
2021-01-16 | 10:40 | 49.919
2021-01-16 | 10:40 | 49.922
2021-01-16 | 10:40 | 49.925
2021-01-16 | 10:41 | 49.927
2021-01-16 | 10:41 | 49.929
2021-01-16 | 10:41 | 49.933
2021-01-16 | 10:41 | 49.935
2021-01-16 | 10:41 | 49.938
2021-01-16 | 10:41 | 49.938
2021-01-16 | 10:41 | 49.938
2021-01-16 | 10:41 | 49.937
2021-01-16 | 10:41 | 49.935
2021-01-16 | 10:41 | 49.932
2021-01-16 | 10:41 | 49.932
2021-01-16 | 10:41 | 49.931
2021-01-16 | 10:41 | 49.933
2021-01-16 | 10:41 | 49.934
2021-01-16 | 10:41 | 49.936
2021-01-16 | 10:41 | 49.936
2021-01-16 | 10:41 | 49.936
2021-01-16 | 10:41 | 49.935
2021-01-16 | 10:41 | 49.936
2021-01-16 | 10:41 | 49.935
2021-01-16 | 10:41 | 49.936
2021-01-16 | 10:41 | 49.933
2021-01-16 | 10:41 | 49.935
2021-01-16 | 10:41 | 49.932
2021-01-16 | 10:41 | 49.932
2021-01-16 | 10:41 | 49.932
2021-01-16 | 10:41 | 49.936
2021-01-16 | 10:41 | 49.937
2021-01-16 | 10:41 | 49.939
2021-01-16 | 10:41 | 49.941
2021-01-16 | 10:41 | 49.94
2021-01-16 | 10:41 | 49.939
2021-01-16 | 10:41 | 49.938
2021-01-16 | 10:41 | 49.937
2021-01-16 | 10:41 | 49.938
2021-01-16 | 10:41 | 49.936
2021-01-16 | 10:41 | 49.938
2021-01-16 | 10:41 | 49.94
2021-01-16 | 10:41 | 49.941
2021-01-16 | 10:41 | 49.943
2021-01-16 | 10:41 | 49.943
2021-01-16 | 10:41 | 49.947
2021-01-16 | 10:41 | 49.949
2021-01-16 | 10:41 | 49.952
2021-01-16 | 10:41 | 49.954
2021-01-16 | 10:41 | 49.956
2021-01-16 | 10:41 | 49.955
2021-01-16 | 10:41 | 49.957
2021-01-16 | 10:41 | 49.955
2021-01-16 | 10:41 | 49.952
2021-01-16 | 10:41 | 49.95
2021-01-16 | 10:41 | 49.946
2021-01-16 | 10:41 | 49.944
2021-01-16 | 10:41 | 49.943
2021-01-16 | 10:41 | 49.943
2021-01-16 | 10:41 | 49.941
2021-01-16 | 10:41 | 49.942
2021-01-16 | 10:41 | 49.941
2021-01-16 | 10:41 | 49.941
2021-01-16 | 10:42 | 49.943
2021-01-16 | 10:42 | 49.943
2021-01-16 | 10:42 | 49.945
2021-01-16 | 10:42 | 49.946
2021-01-16 | 10:42 | 49.946
2021-01-16 | 10:42 | 49.944
2021-01-16 | 10:42 | 49.944
2021-01-16 | 10:42 | 49.945
2021-01-16 | 10:42 | 49.949
2021-01-16 | 10:42 | 49.949
2021-01-16 | 10:42 | 49.95
2021-01-16 | 10:42 | 49.95
2021-01-16 | 10:42 | 49.95
2021-01-16 | 10:42 | 49.948
2021-01-16 | 10:42 | 49.95
2021-01-16 | 10:42 | 49.951
2021-01-16 | 10:42 | 49.953
2021-01-16 | 10:42 | 49.954
2021-01-16 | 10:42 | 49.956
2021-01-16 | 10:42 | 49.963
2021-01-16 | 10:42 | 49.967
2021-01-16 | 10:42 | 49.969
2021-01-16 | 10:42 | 49.969
2021-01-16 | 10:42 | 49.969
2021-01-16 | 10:42 | 49.968
2021-01-16 | 10:42 | 49.967
2021-01-16 | 10:42 | 49.966
2021-01-16 | 10:42 | 49.967
2021-01-16 | 10:42 | 49.968
2021-01-16 | 10:42 | 49.967
2021-01-16 | 10:42 | 49.969
2021-01-16 | 10:42 | 49.965
2021-01-16 | 10:42 | 49.964
2021-01-16 | 10:42 | 49.961
2021-01-16 | 10:42 | 49.962
2021-01-16 | 10:42 | 49.961
2021-01-16 | 10:42 | 49.961
2021-01-16 | 10:42 | 49.962
2021-01-16 | 10:42 | 49.963
2021-01-16 | 10:42 | 49.963
2021-01-16 | 10:42 | 49.965
2021-01-16 | 10:42 | 49.967
2021-01-16 | 10:42 | 49.966
2021-01-16 | 10:42 | 49.968
2021-01-16 | 10:42 | 49.967
2021-01-16 | 10:42 | 49.969
2021-01-16 | 10:42 | 49.97
2021-01-16 | 10:42 | 49.969
2021-01-16 | 10:42 | 49.972
2021-01-16 | 10:42 | 49.971
2021-01-16 | 10:42 | 49.972
2021-01-16 | 10:42 | 49.972
2021-01-16 | 10:42 | 49.971
2021-01-16 | 10:42 | 49.971
2021-01-16 | 10:42 | 49.971
2021-01-16 | 10:42 | 49.971
2021-01-16 | 10:42 | 49.97
2021-01-16 | 10:42 | 49.968
2021-01-16 | 10:42 | 49.969
2021-01-16 | 10:42 | 49.971
2021-01-16 | 10:42 | 49.972
2021-01-16 | 10:43 | 49.971
2021-01-16 | 10:43 | 49.974
2021-01-16 | 10:43 | 49.976
2021-01-16 | 10:43 | 49.978
2021-01-16 | 10:43 | 49.979
2021-01-16 | 10:43 | 49.977
2021-01-16 | 10:43 | 49.976
2021-01-16 | 10:43 | 49.976
2021-01-16 | 10:43 | 49.975
2021-01-16 | 10:43 | 49.979
2021-01-16 | 10:43 | 49.983
2021-01-16 | 10:43 | 49.984
2021-01-16 | 10:43 | 49.985
2021-01-16 | 10:43 | 49.987
2021-01-16 | 10:43 | 49.986
2021-01-16 | 10:43 | 49.987
2021-01-16 | 10:43 | 49.985
2021-01-16 | 10:43 | 49.985
2021-01-16 | 10:43 | 49.985
2021-01-16 | 10:43 | 49.984
2021-01-16 | 10:43 | 49.985
2021-01-16 | 10:43 | 49.985
2021-01-16 | 10:43 | 49.984
2021-01-16 | 10:43 | 49.985
2021-01-16 | 10:43 | 49.986
2021-01-16 | 10:43 | 49.986
2021-01-16 | 10:43 | 49.984
2021-01-16 | 10:43 | 49.983
2021-01-16 | 10:43 | 49.98
2021-01-16 | 10:43 | 49.981
2021-01-16 | 10:43 | 49.98
2021-01-16 | 10:43 | 49.98
2021-01-16 | 10:43 | 49.98
2021-01-16 | 10:43 | 49.978
2021-01-16 | 10:43 | 49.978
2021-01-16 | 10:43 | 49.975
2021-01-16 | 10:43 | 49.976
2021-01-16 | 10:43 | 49.975
2021-01-16 | 10:43 | 49.974
2021-01-16 | 10:43 | 49.971
2021-01-16 | 10:43 | 49.968
2021-01-16 | 10:43 | 49.965
2021-01-16 | 10:43 | 49.961
2021-01-16 | 10:43 | 49.958
2021-01-16 | 10:43 | 49.952
2021-01-16 | 10:43 | 49.95
2021-01-16 | 10:43 | 49.95
2021-01-16 | 10:43 | 49.952
2021-01-16 | 10:43 | 49.951
2021-01-16 | 10:43 | 49.949
2021-01-16 | 10:43 | 49.948
2021-01-16 | 10:43 | 49.947
2021-01-16 | 10:43 | 49.947
2021-01-16 | 10:43 | 49.946
2021-01-16 | 10:43 | 49.949
2021-01-16 | 10:43 | 49.95
2021-01-16 | 10:43 | 49.95
2021-01-16 | 10:43 | 49.951
2021-01-16 | 10:43 | 49.952
2021-01-16 | 10:44 | 49.952
2021-01-16 | 10:44 | 49.952
2021-01-16 | 10:44 | 49.946
2021-01-16 | 10:44 | 49.941
2021-01-16 | 10:44 | 49.935
2021-01-16 | 10:44 | 49.932
2021-01-16 | 10:44 | 49.929
2021-01-16 | 10:44 | 49.93
2021-01-16 | 10:44 | 49.93
2021-01-16 | 10:44 | 49.93
2021-01-16 | 10:44 | 49.929
2021-01-16 | 10:44 | 49.928
2021-01-16 | 10:44 | 49.93
2021-01-16 | 10:44 | 49.931
2021-01-16 | 10:44 | 49.933
2021-01-16 | 10:44 | 49.934
2021-01-16 | 10:44 | 49.936
2021-01-16 | 10:44 | 49.936
2021-01-16 | 10:44 | 49.935
2021-01-16 | 10:44 | 49.936
2021-01-16 | 10:44 | 49.935
2021-01-16 | 10:44 | 49.938
2021-01-16 | 10:44 | 49.937
2021-01-16 | 10:44 | 49.938
2021-01-16 | 10:44 | 49.936
2021-01-16 | 10:44 | 49.936
2021-01-16 | 10:44 | 49.935
2021-01-16 | 10:44 | 49.935
2021-01-16 | 10:44 | 49.937
2021-01-16 | 10:44 | 49.938
2021-01-16 | 10:44 | 49.943
2021-01-16 | 10:44 | 49.944
2021-01-16 | 10:44 | 49.947
2021-01-16 | 10:44 | 49.946
2021-01-16 | 10:44 | 49.945
2021-01-16 | 10:44 | 49.943
2021-01-16 | 10:44 | 49.94
2021-01-16 | 10:44 | 49.939
2021-01-16 | 10:44 | 49.935
2021-01-16 | 10:44 | 49.933
2021-01-16 | 10:44 | 49.933
2021-01-16 | 10:44 | 49.934
2021-01-16 | 10:44 | 49.933
2021-01-16 | 10:44 | 49.931
2021-01-16 | 10:44 | 49.931
2021-01-16 | 10:44 | 49.93
2021-01-16 | 10:44 | 49.931
2021-01-16 | 10:44 | 49.934
2021-01-16 | 10:44 | 49.934
2021-01-16 | 10:44 | 49.937
2021-01-16 | 10:44 | 49.937
2021-01-16 | 10:44 | 49.939
2021-01-16 | 10:44 | 49.939
2021-01-16 | 10:44 | 49.939
2021-01-16 | 10:44 | 49.943
2021-01-16 | 10:44 | 49.946
2021-01-16 | 10:44 | 49.948
2021-01-16 | 10:44 | 49.953
2021-01-16 | 10:44 | 49.954
2021-01-16 | 10:44 | 49.955
2021-01-16 | 10:44 | 49.956
2021-01-16 | 10:45 | 49.955
2021-01-16 | 10:45 | 49.953
2021-01-16 | 10:45 | 49.952
2021-01-16 | 10:45 | 49.95
2021-01-16 | 10:45 | 49.95
2021-01-16 | 10:45 | 49.948
2021-01-16 | 10:45 | 49.948
2021-01-16 | 10:45 | 49.949
2021-01-16 | 10:45 | 49.948
2021-01-16 | 10:45 | 49.946
2021-01-16 | 10:45 | 49.947
2021-01-16 | 10:45 | 49.94
2021-01-16 | 10:45 | 49.933
2021-01-16 | 10:45 | 49.93
2021-01-16 | 10:45 | 49.928
2021-01-16 | 10:45 | 49.926
2021-01-16 | 10:45 | 49.926
2021-01-16 | 10:45 | 49.925
2021-01-16 | 10:45 | 49.926
2021-01-16 | 10:45 | 49.927
2021-01-16 | 10:45 | 49.927
2021-01-16 | 10:45 | 49.928
2021-01-16 | 10:45 | 49.923
2021-01-16 | 10:45 | 49.921
2021-01-16 | 10:45 | 49.921
2021-01-16 | 10:45 | 49.923
2021-01-16 | 10:45 | 49.922
2021-01-16 | 10:45 | 49.922
2021-01-16 | 10:45 | 49.923
2021-01-16 | 10:45 | 49.923
2021-01-16 | 10:45 | 49.924
2021-01-16 | 10:45 | 49.928
2021-01-16 | 10:45 | 49.929
2021-01-16 | 10:45 | 49.929
2021-01-16 | 10:45 | 49.928
2021-01-16 | 10:45 | 49.929
2021-01-16 | 10:45 | 49.927
2021-01-16 | 10:45 | 49.925
2021-01-16 | 10:45 | 49.925
2021-01-16 | 10:45 | 49.923
2021-01-16 | 10:45 | 49.924
2021-01-16 | 10:45 | 49.925
2021-01-16 | 10:45 | 49.923
2021-01-16 | 10:45 | 49.924
2021-01-16 | 10:45 | 49.923
2021-01-16 | 10:45 | 49.923
2021-01-16 | 10:45 | 49.922
2021-01-16 | 10:45 | 49.922
2021-01-16 | 10:45 | 49.922
2021-01-16 | 10:45 | 49.919
2021-01-16 | 10:45 | 49.918
2021-01-16 | 10:45 | 49.918
2021-01-16 | 10:45 | 49.916
2021-01-16 | 10:45 | 49.919
2021-01-16 | 10:45 | 49.92
2021-01-16 | 10:45 | 49.921
2021-01-16 | 10:45 | 49.92
2021-01-16 | 10:45 | 49.918
2021-01-16 | 10:45 | 49.916
2021-01-16 | 10:46 | 49.912
2021-01-16 | 10:46 | 49.912
2021-01-16 | 10:46 | 49.911
2021-01-16 | 10:46 | 49.913
2021-01-16 | 10:46 | 49.913
2021-01-16 | 10:46 | 49.914
2021-01-16 | 10:46 | 49.917
2021-01-16 | 10:46 | 49.918
2021-01-16 | 10:46 | 49.918
2021-01-16 | 10:46 | 49.917
2021-01-16 | 10:46 | 49.915
2021-01-16 | 10:46 | 49.911
2021-01-16 | 10:46 | 49.909
2021-01-16 | 10:46 | 49.908
2021-01-16 | 10:46 | 49.91
2021-01-16 | 10:46 | 49.914
2021-01-16 | 10:46 | 49.92
2021-01-16 | 10:46 | 49.924
2021-01-16 | 10:46 | 49.927
2021-01-16 | 10:46 | 49.93
2021-01-16 | 10:46 | 49.928
2021-01-16 | 10:46 | 49.929
2021-01-16 | 10:46 | 49.927
2021-01-16 | 10:46 | 49.927
2021-01-16 | 10:46 | 49.924
2021-01-16 | 10:46 | 49.921
2021-01-16 | 10:46 | 49.916
2021-01-16 | 10:46 | 49.912
2021-01-16 | 10:46 | 49.91
2021-01-16 | 10:46 | 49.905
2021-01-16 | 10:46 | 49.906
2021-01-16 | 10:46 | 49.906
2021-01-16 | 10:46 | 49.907
2021-01-16 | 10:46 | 49.909
2021-01-16 | 10:46 | 49.911
2021-01-16 | 10:46 | 49.912
2021-01-16 | 10:46 | 49.912
2021-01-16 | 10:46 | 49.914
2021-01-16 | 10:46 | 49.915
2021-01-16 | 10:46 | 49.914
2021-01-16 | 10:46 | 49.912
2021-01-16 | 10:46 | 49.913
2021-01-16 | 10:46 | 49.916
2021-01-16 | 10:46 | 49.921
2021-01-16 | 10:46 | 49.923
2021-01-16 | 10:46 | 49.927
2021-01-16 | 10:46 | 49.926
2021-01-16 | 10:46 | 49.929
2021-01-16 | 10:46 | 49.93
2021-01-16 | 10:46 | 49.93
2021-01-16 | 10:46 | 49.935
2021-01-16 | 10:46 | 49.936
2021-01-16 | 10:46 | 49.937
2021-01-16 | 10:46 | 49.942
2021-01-16 | 10:46 | 49.941
2021-01-16 | 10:46 | 49.943
2021-01-16 | 10:46 | 49.942
2021-01-16 | 10:46 | 49.945
2021-01-16 | 10:46 | 49.947
2021-01-16 | 10:46 | 49.948
2021-01-16 | 10:46 | 49.952
2021-01-16 | 10:47 | 49.953
2021-01-16 | 10:47 | 49.953
2021-01-16 | 10:47 | 49.95
2021-01-16 | 10:47 | 49.943
2021-01-16 | 10:47 | 49.941
2021-01-16 | 10:47 | 49.94
2021-01-16 | 10:47 | 49.941
2021-01-16 | 10:47 | 49.941
2021-01-16 | 10:47 | 49.94
2021-01-16 | 10:47 | 49.939
2021-01-16 | 10:47 | 49.939
2021-01-16 | 10:47 | 49.939
2021-01-16 | 10:47 | 49.942
2021-01-16 | 10:47 | 49.945
2021-01-16 | 10:47 | 49.945
2021-01-16 | 10:47 | 49.946
2021-01-16 | 10:47 | 49.945
2021-01-16 | 10:47 | 49.946
2021-01-16 | 10:47 | 49.947
2021-01-16 | 10:47 | 49.945
2021-01-16 | 10:47 | 49.945
2021-01-16 | 10:47 | 49.944
2021-01-16 | 10:47 | 49.941
2021-01-16 | 10:47 | 49.944
2021-01-16 | 10:47 | 49.943
2021-01-16 | 10:47 | 49.943
2021-01-16 | 10:47 | 49.942
2021-01-16 | 10:47 | 49.943
2021-01-16 | 10:47 | 49.944
2021-01-16 | 10:47 | 49.943
2021-01-16 | 10:47 | 49.945
2021-01-16 | 10:47 | 49.945
2021-01-16 | 10:47 | 49.946
2021-01-16 | 10:47 | 49.949
2021-01-16 | 10:47 | 49.948
2021-01-16 | 10:47 | 49.949
2021-01-16 | 10:47 | 49.946
2021-01-16 | 10:47 | 49.945
2021-01-16 | 10:47 | 49.942
2021-01-16 | 10:47 | 49.94
2021-01-16 | 10:47 | 49.938
2021-01-16 | 10:47 | 49.936
2021-01-16 | 10:47 | 49.937
2021-01-16 | 10:47 | 49.935
2021-01-16 | 10:47 | 49.933
2021-01-16 | 10:47 | 49.927
2021-01-16 | 10:47 | 49.926
2021-01-16 | 10:47 | 49.921
2021-01-16 | 10:47 | 49.92
2021-01-16 | 10:47 | 49.916
2021-01-16 | 10:47 | 49.919
2021-01-16 | 10:47 | 49.922
2021-01-16 | 10:47 | 49.926
2021-01-16 | 10:47 | 49.928
2021-01-16 | 10:47 | 49.931
2021-01-16 | 10:47 | 49.934
2021-01-16 | 10:47 | 49.933
2021-01-16 | 10:47 | 49.931
2021-01-16 | 10:47 | 49.93
2021-01-16 | 10:47 | 49.927
2021-01-16 | 10:48 | 49.924
2021-01-16 | 10:48 | 49.922
2021-01-16 | 10:48 | 49.919
2021-01-16 | 10:48 | 49.918
2021-01-16 | 10:48 | 49.92
2021-01-16 | 10:48 | 49.924
2021-01-16 | 10:48 | 49.921
2021-01-16 | 10:48 | 49.923
2021-01-16 | 10:48 | 49.924
2021-01-16 | 10:48 | 49.922
2021-01-16 | 10:48 | 49.925
2021-01-16 | 10:48 | 49.923
2021-01-16 | 10:48 | 49.918
2021-01-16 | 10:48 | 49.915
2021-01-16 | 10:48 | 49.915
2021-01-16 | 10:48 | 49.914
2021-01-16 | 10:48 | 49.919
2021-01-16 | 10:48 | 49.92
2021-01-16 | 10:48 | 49.925
2021-01-16 | 10:48 | 49.925
2021-01-16 | 10:48 | 49.927
2021-01-16 | 10:48 | 49.927
2021-01-16 | 10:48 | 49.927
2021-01-16 | 10:48 | 49.926
2021-01-16 | 10:48 | 49.924
2021-01-16 | 10:48 | 49.924
2021-01-16 | 10:48 | 49.918
2021-01-16 | 10:48 | 49.916
2021-01-16 | 10:48 | 49.913
2021-01-16 | 10:48 | 49.913
2021-01-16 | 10:48 | 49.912
2021-01-16 | 10:48 | 49.913
2021-01-16 | 10:48 | 49.914
2021-01-16 | 10:48 | 49.919
2021-01-16 | 10:48 | 49.923
2021-01-16 | 10:48 | 49.925
2021-01-16 | 10:48 | 49.926
2021-01-16 | 10:48 | 49.927
2021-01-16 | 10:48 | 49.931
2021-01-16 | 10:48 | 49.931
2021-01-16 | 10:48 | 49.932
2021-01-16 | 10:48 | 49.93
2021-01-16 | 10:48 | 49.932
2021-01-16 | 10:48 | 49.93
2021-01-16 | 10:48 | 49.932
2021-01-16 | 10:48 | 49.932
2021-01-16 | 10:48 | 49.929
2021-01-16 | 10:48 | 49.929
2021-01-16 | 10:48 | 49.928
2021-01-16 | 10:48 | 49.927
2021-01-16 | 10:48 | 49.93
2021-01-16 | 10:48 | 49.932
2021-01-16 | 10:48 | 49.934
2021-01-16 | 10:48 | 49.937
2021-01-16 | 10:48 | 49.937
2021-01-16 | 10:48 | 49.937
2021-01-16 | 10:48 | 49.937
2021-01-16 | 10:48 | 49.94
2021-01-16 | 10:48 | 49.942
2021-01-16 | 10:48 | 49.944
2021-01-16 | 10:49 | 49.94
2021-01-16 | 10:49 | 49.939
2021-01-16 | 10:49 | 49.936
2021-01-16 | 10:49 | 49.937
2021-01-16 | 10:49 | 49.937
2021-01-16 | 10:49 | 49.941
2021-01-16 | 10:49 | 49.942
2021-01-16 | 10:49 | 49.945
2021-01-16 | 10:49 | 49.947
2021-01-16 | 10:49 | 49.95
2021-01-16 | 10:49 | 49.953
2021-01-16 | 10:49 | 49.954
2021-01-16 | 10:49 | 49.953
2021-01-16 | 10:49 | 49.955
2021-01-16 | 10:49 | 49.957
2021-01-16 | 10:49 | 49.957
2021-01-16 | 10:49 | 49.959
2021-01-16 | 10:49 | 49.958
2021-01-16 | 10:49 | 49.958
2021-01-16 | 10:49 | 49.957
2021-01-16 | 10:49 | 49.955
2021-01-16 | 10:49 | 49.955
2021-01-16 | 10:49 | 49.955
2021-01-16 | 10:49 | 49.953
2021-01-16 | 10:49 | 49.953
2021-01-16 | 10:49 | 49.951
2021-01-16 | 10:49 | 49.951
2021-01-16 | 10:49 | 49.953
2021-01-16 | 10:49 | 49.951
2021-01-16 | 10:49 | 49.95
2021-01-16 | 10:49 | 49.947
2021-01-16 | 10:49 | 49.948
2021-01-16 | 10:49 | 49.945
2021-01-16 | 10:49 | 49.945
2021-01-16 | 10:49 | 49.943
2021-01-16 | 10:49 | 49.942
2021-01-16 | 10:49 | 49.94
2021-01-16 | 10:49 | 49.942
2021-01-16 | 10:49 | 49.943
2021-01-16 | 10:49 | 49.945
2021-01-16 | 10:49 | 49.946
2021-01-16 | 10:49 | 49.944
2021-01-16 | 10:49 | 49.946
2021-01-16 | 10:49 | 49.941
2021-01-16 | 10:49 | 49.942
2021-01-16 | 10:49 | 49.937
2021-01-16 | 10:49 | 49.933
2021-01-16 | 10:49 | 49.927
2021-01-16 | 10:49 | 49.927
2021-01-16 | 10:49 | 49.924
2021-01-16 | 10:49 | 49.923
2021-01-16 | 10:49 | 49.92
2021-01-16 | 10:49 | 49.921
2021-01-16 | 10:49 | 49.919
2021-01-16 | 10:49 | 49.92
2021-01-16 | 10:49 | 49.921
2021-01-16 | 10:49 | 49.925
2021-01-16 | 10:49 | 49.928
2021-01-16 | 10:49 | 49.927
2021-01-16 | 10:49 | 49.929
2021-01-16 | 10:50 | 49.929
2021-01-16 | 10:50 | 49.929
2021-01-16 | 10:50 | 49.928
2021-01-16 | 10:50 | 49.931
2021-01-16 | 10:50 | 49.933
2021-01-16 | 10:50 | 49.932
2021-01-16 | 10:50 | 49.935
2021-01-16 | 10:50 | 49.934
2021-01-16 | 10:50 | 49.933
2021-01-16 | 10:50 | 49.932
2021-01-16 | 10:50 | 49.936
2021-01-16 | 10:50 | 49.936
2021-01-16 | 10:50 | 49.938
2021-01-16 | 10:50 | 49.939
2021-01-16 | 10:50 | 49.941
2021-01-16 | 10:50 | 49.937
2021-01-16 | 10:50 | 49.937
2021-01-16 | 10:50 | 49.935
2021-01-16 | 10:50 | 49.934
2021-01-16 | 10:50 | 49.934
2021-01-16 | 10:50 | 49.936
2021-01-16 | 10:50 | 49.938
2021-01-16 | 10:50 | 49.94
2021-01-16 | 10:50 | 49.94
2021-01-16 | 10:50 | 49.937
2021-01-16 | 10:50 | 49.936
2021-01-16 | 10:50 | 49.933
2021-01-16 | 10:50 | 49.932
2021-01-16 | 10:50 | 49.929
2021-01-16 | 10:50 | 49.927
2021-01-16 | 10:50 | 49.923
2021-01-16 | 10:50 | 49.918
2021-01-16 | 10:50 | 49.915
2021-01-16 | 10:50 | 49.915
2021-01-16 | 10:50 | 49.914
2021-01-16 | 10:50 | 49.914
2021-01-16 | 10:50 | 49.917
2021-01-16 | 10:50 | 49.921
2021-01-16 | 10:50 | 49.926
2021-01-16 | 10:50 | 49.928
2021-01-16 | 10:50 | 49.93
2021-01-16 | 10:50 | 49.931
2021-01-16 | 10:50 | 49.937
2021-01-16 | 10:50 | 49.939
2021-01-16 | 10:50 | 49.939
2021-01-16 | 10:50 | 49.941
2021-01-16 | 10:50 | 49.94
2021-01-16 | 10:50 | 49.943
2021-01-16 | 10:50 | 49.943
2021-01-16 | 10:50 | 49.946
2021-01-16 | 10:50 | 49.945
2021-01-16 | 10:50 | 49.948
2021-01-16 | 10:50 | 49.949
2021-01-16 | 10:50 | 49.949
2021-01-16 | 10:50 | 49.948
2021-01-16 | 10:50 | 49.948
2021-01-16 | 10:50 | 49.95
2021-01-16 | 10:50 | 49.946
2021-01-16 | 10:50 | 49.946
2021-01-16 | 10:50 | 49.945
2021-01-16 | 10:51 | 49.945
2021-01-16 | 10:51 | 49.944
2021-01-16 | 10:51 | 49.946
2021-01-16 | 10:51 | 49.947
2021-01-16 | 10:51 | 49.948
2021-01-16 | 10:51 | 49.948
2021-01-16 | 10:51 | 49.947
2021-01-16 | 10:51 | 49.948
2021-01-16 | 10:51 | 49.947
2021-01-16 | 10:51 | 49.949
2021-01-16 | 10:51 | 49.948
2021-01-16 | 10:51 | 49.947
2021-01-16 | 10:51 | 49.946
2021-01-16 | 10:51 | 49.947
2021-01-16 | 10:51 | 49.944
2021-01-16 | 10:51 | 49.942
2021-01-16 | 10:51 | 49.941
2021-01-16 | 10:51 | 49.937
2021-01-16 | 10:51 | 49.935
2021-01-16 | 10:51 | 49.931
2021-01-16 | 10:51 | 49.928
2021-01-16 | 10:51 | 49.927
2021-01-16 | 10:51 | 49.926
2021-01-16 | 10:51 | 49.927
2021-01-16 | 10:51 | 49.927
2021-01-16 | 10:51 | 49.928
2021-01-16 | 10:51 | 49.928
2021-01-16 | 10:51 | 49.928
2021-01-16 | 10:51 | 49.932
2021-01-16 | 10:51 | 49.934
2021-01-16 | 10:51 | 49.938
2021-01-16 | 10:51 | 49.939
2021-01-16 | 10:51 | 49.941
2021-01-16 | 10:51 | 49.942
2021-01-16 | 10:51 | 49.944
2021-01-16 | 10:51 | 49.943
2021-01-16 | 10:51 | 49.945
2021-01-16 | 10:51 | 49.944
2021-01-16 | 10:51 | 49.942
2021-01-16 | 10:51 | 49.94
2021-01-16 | 10:51 | 49.935
2021-01-16 | 10:51 | 49.933
2021-01-16 | 10:51 | 49.932
2021-01-16 | 10:51 | 49.934
2021-01-16 | 10:51 | 49.933
2021-01-16 | 10:51 | 49.935
2021-01-16 | 10:51 | 49.935
2021-01-16 | 10:51 | 49.936
2021-01-16 | 10:51 | 49.934
2021-01-16 | 10:51 | 49.933
2021-01-16 | 10:51 | 49.934
2021-01-16 | 10:51 | 49.934
2021-01-16 | 10:51 | 49.934
2021-01-16 | 10:51 | 49.937
2021-01-16 | 10:51 | 49.935
2021-01-16 | 10:51 | 49.934
2021-01-16 | 10:51 | 49.935
2021-01-16 | 10:51 | 49.936
2021-01-16 | 10:51 | 49.935
2021-01-16 | 10:51 | 49.937
2021-01-16 | 10:52 | 49.938
2021-01-16 | 10:52 | 49.939
2021-01-16 | 10:52 | 49.937
2021-01-16 | 10:52 | 49.936
2021-01-16 | 10:52 | 49.937
2021-01-16 | 10:52 | 49.934
2021-01-16 | 10:52 | 49.933
2021-01-16 | 10:52 | 49.933
2021-01-16 | 10:52 | 49.934
2021-01-16 | 10:52 | 49.937
2021-01-16 | 10:52 | 49.941
2021-01-16 | 10:52 | 49.944
2021-01-16 | 10:52 | 49.947
2021-01-16 | 10:52 | 49.95
2021-01-16 | 10:52 | 49.952
2021-01-16 | 10:52 | 49.953
2021-01-16 | 10:52 | 49.952
2021-01-16 | 10:52 | 49.952
2021-01-16 | 10:52 | 49.948
2021-01-16 | 10:52 | 49.947
2021-01-16 | 10:52 | 49.942
2021-01-16 | 10:52 | 49.942
2021-01-16 | 10:52 | 49.94
2021-01-16 | 10:52 | 49.94
2021-01-16 | 10:52 | 49.942
2021-01-16 | 10:52 | 49.945
2021-01-16 | 10:52 | 49.945
2021-01-16 | 10:52 | 49.949
2021-01-16 | 10:52 | 49.949
2021-01-16 | 10:52 | 49.948
2021-01-16 | 10:52 | 49.947
2021-01-16 | 10:52 | 49.945
2021-01-16 | 10:52 | 49.943
2021-01-16 | 10:52 | 49.941
2021-01-16 | 10:52 | 49.94
2021-01-16 | 10:52 | 49.939
2021-01-16 | 10:52 | 49.938
2021-01-16 | 10:52 | 49.938
2021-01-16 | 10:52 | 49.94
2021-01-16 | 10:52 | 49.94
2021-01-16 | 10:52 | 49.941
2021-01-16 | 10:52 | 49.942
2021-01-16 | 10:52 | 49.947
2021-01-16 | 10:52 | 49.949
2021-01-16 | 10:52 | 49.949
2021-01-16 | 10:52 | 49.952
2021-01-16 | 10:52 | 49.95
2021-01-16 | 10:52 | 49.948
2021-01-16 | 10:52 | 49.946
2021-01-16 | 10:52 | 49.946
2021-01-16 | 10:52 | 49.942
2021-01-16 | 10:52 | 49.94
2021-01-16 | 10:52 | 49.94
2021-01-16 | 10:52 | 49.94
2021-01-16 | 10:52 | 49.94
2021-01-16 | 10:52 | 49.938
2021-01-16 | 10:52 | 49.936
2021-01-16 | 10:52 | 49.938
2021-01-16 | 10:52 | 49.941
2021-01-16 | 10:52 | 49.944
2021-01-16 | 10:53 | 49.944
2021-01-16 | 10:53 | 49.946
2021-01-16 | 10:53 | 49.946
2021-01-16 | 10:53 | 49.946
2021-01-16 | 10:53 | 49.944
2021-01-16 | 10:53 | 49.945
2021-01-16 | 10:53 | 49.944
2021-01-16 | 10:53 | 49.943
2021-01-16 | 10:53 | 49.939
2021-01-16 | 10:53 | 49.939
2021-01-16 | 10:53 | 49.938
2021-01-16 | 10:53 | 49.936
2021-01-16 | 10:53 | 49.936
2021-01-16 | 10:53 | 49.939
2021-01-16 | 10:53 | 49.939
2021-01-16 | 10:53 | 49.94
2021-01-16 | 10:53 | 49.942
2021-01-16 | 10:53 | 49.941
2021-01-16 | 10:53 | 49.941
2021-01-16 | 10:53 | 49.939
2021-01-16 | 10:53 | 49.939
2021-01-16 | 10:53 | 49.94
2021-01-16 | 10:53 | 49.941
2021-01-16 | 10:53 | 49.941
2021-01-16 | 10:53 | 49.947
2021-01-16 | 10:53 | 49.949
2021-01-16 | 10:53 | 49.953
2021-01-16 | 10:53 | 49.956
2021-01-16 | 10:53 | 49.958
2021-01-16 | 10:53 | 49.958
2021-01-16 | 10:53 | 49.955
2021-01-16 | 10:53 | 49.952
2021-01-16 | 10:53 | 49.95
2021-01-16 | 10:53 | 49.951
2021-01-16 | 10:53 | 49.951
2021-01-16 | 10:53 | 49.953
2021-01-16 | 10:53 | 49.954
2021-01-16 | 10:53 | 49.955
2021-01-16 | 10:53 | 49.956
2021-01-16 | 10:53 | 49.955
2021-01-16 | 10:53 | 49.957
2021-01-16 | 10:53 | 49.958
2021-01-16 | 10:53 | 49.959
2021-01-16 | 10:53 | 49.957
2021-01-16 | 10:53 | 49.956
2021-01-16 | 10:53 | 49.954
2021-01-16 | 10:53 | 49.951
2021-01-16 | 10:53 | 49.953
2021-01-16 | 10:53 | 49.952
2021-01-16 | 10:53 | 49.95
2021-01-16 | 10:53 | 49.951
2021-01-16 | 10:53 | 49.951
2021-01-16 | 10:53 | 49.952
2021-01-16 | 10:53 | 49.951
2021-01-16 | 10:53 | 49.953
2021-01-16 | 10:53 | 49.949
2021-01-16 | 10:53 | 49.947
2021-01-16 | 10:53 | 49.943
2021-01-16 | 10:53 | 49.942
2021-01-16 | 10:54 | 49.945
2021-01-16 | 10:54 | 49.943
2021-01-16 | 10:54 | 49.944
2021-01-16 | 10:54 | 49.944
2021-01-16 | 10:54 | 49.943
2021-01-16 | 10:54 | 49.942
2021-01-16 | 10:54 | 49.942
2021-01-16 | 10:54 | 49.941
2021-01-16 | 10:54 | 49.941
2021-01-16 | 10:54 | 49.942
2021-01-16 | 10:54 | 49.941
2021-01-16 | 10:54 | 49.942
2021-01-16 | 10:54 | 49.94
2021-01-16 | 10:54 | 49.941
2021-01-16 | 10:54 | 49.941
2021-01-16 | 10:54 | 49.942
2021-01-16 | 10:54 | 49.947
2021-01-16 | 10:54 | 49.95
2021-01-16 | 10:54 | 49.955
2021-01-16 | 10:54 | 49.958
2021-01-16 | 10:54 | 49.96
2021-01-16 | 10:54 | 49.961
2021-01-16 | 10:54 | 49.961
2021-01-16 | 10:54 | 49.961
2021-01-16 | 10:54 | 49.962
2021-01-16 | 10:54 | 49.961
2021-01-16 | 10:54 | 49.964
2021-01-16 | 10:54 | 49.965
2021-01-16 | 10:54 | 49.969
2021-01-16 | 10:54 | 49.972
2021-01-16 | 10:54 | 49.972
2021-01-16 | 10:54 | 49.973
2021-01-16 | 10:54 | 49.973
2021-01-16 | 10:54 | 49.97
2021-01-16 | 10:54 | 49.969
2021-01-16 | 10:54 | 49.97
2021-01-16 | 10:54 | 49.969
2021-01-16 | 10:54 | 49.967
2021-01-16 | 10:54 | 49.969
2021-01-16 | 10:54 | 49.972
2021-01-16 | 10:54 | 49.973
2021-01-16 | 10:54 | 49.977
2021-01-16 | 10:54 | 49.98
2021-01-16 | 10:54 | 49.981
2021-01-16 | 10:54 | 49.98
2021-01-16 | 10:54 | 49.98
2021-01-16 | 10:54 | 49.981
2021-01-16 | 10:54 | 49.982
2021-01-16 | 10:54 | 49.981
2021-01-16 | 10:54 | 49.981
2021-01-16 | 10:54 | 49.98
2021-01-16 | 10:54 | 49.977
2021-01-16 | 10:54 | 49.978
2021-01-16 | 10:54 | 49.979
2021-01-16 | 10:54 | 49.98
2021-01-16 | 10:54 | 49.979
2021-01-16 | 10:54 | 49.977
2021-01-16 | 10:54 | 49.975
2021-01-16 | 10:54 | 49.974
2021-01-16 | 10:54 | 49.972
2021-01-16 | 10:54 | 49.97
2021-01-16 | 10:55 | 49.967
2021-01-16 | 10:55 | 49.966
2021-01-16 | 10:55 | 49.965
2021-01-16 | 10:55 | 49.966
2021-01-16 | 10:55 | 49.97
2021-01-16 | 10:55 | 49.971
2021-01-16 | 10:55 | 49.972
2021-01-16 | 10:55 | 49.975
2021-01-16 | 10:55 | 49.978
2021-01-16 | 10:55 | 49.98
2021-01-16 | 10:55 | 49.984
2021-01-16 | 10:55 | 49.987
2021-01-16 | 10:55 | 49.987
2021-01-16 | 10:55 | 49.99
2021-01-16 | 10:55 | 49.993
2021-01-16 | 10:55 | 49.995
2021-01-16 | 10:55 | 49.997
2021-01-16 | 10:55 | 49.999
2021-01-16 | 10:55 | 50
2021-01-16 | 10:55 | 50
2021-01-16 | 10:55 | 49.998
2021-01-16 | 10:55 | 49.998
2021-01-16 | 10:55 | 50
2021-01-16 | 10:55 | 50
2021-01-16 | 10:55 | 50.003
2021-01-16 | 10:55 | 50.002
2021-01-16 | 10:55 | 50.003
2021-01-16 | 10:55 | 50.004
2021-01-16 | 10:55 | 50.004
2021-01-16 | 10:55 | 50.004
2021-01-16 | 10:55 | 50.002
2021-01-16 | 10:55 | 50.002
2021-01-16 | 10:55 | 50
2021-01-16 | 10:55 | 50
2021-01-16 | 10:55 | 49.998
2021-01-16 | 10:55 | 49.998
2021-01-16 | 10:55 | 49.997
2021-01-16 | 10:55 | 49.996
2021-01-16 | 10:55 | 49.992
2021-01-16 | 10:55 | 49.99
2021-01-16 | 10:55 | 49.987
2021-01-16 | 10:55 | 49.985
2021-01-16 | 10:55 | 49.984
2021-01-16 | 10:55 | 49.984
2021-01-16 | 10:55 | 49.982
2021-01-16 | 10:55 | 49.982
2021-01-16 | 10:55 | 49.982
2021-01-16 | 10:55 | 49.979
2021-01-16 | 10:55 | 49.979
2021-01-16 | 10:55 | 49.974
2021-01-16 | 10:55 | 49.974
2021-01-16 | 10:55 | 49.973
2021-01-16 | 10:55 | 49.974
2021-01-16 | 10:55 | 49.972
2021-01-16 | 10:55 | 49.972
2021-01-16 | 10:55 | 49.97
2021-01-16 | 10:55 | 49.972
2021-01-16 | 10:55 | 49.968
2021-01-16 | 10:55 | 49.967
2021-01-16 | 10:56 | 49.967
2021-01-16 | 10:56 | 49.967
2021-01-16 | 10:56 | 49.965
2021-01-16 | 10:56 | 49.962
2021-01-16 | 10:56 | 49.962
2021-01-16 | 10:56 | 49.963
2021-01-16 | 10:56 | 49.962
2021-01-16 | 10:56 | 49.963
2021-01-16 | 10:56 | 49.964
2021-01-16 | 10:56 | 49.962
2021-01-16 | 10:56 | 49.961
2021-01-16 | 10:56 | 49.96
2021-01-16 | 10:56 | 49.958
2021-01-16 | 10:56 | 49.957
2021-01-16 | 10:56 | 49.954
2021-01-16 | 10:56 | 49.952
2021-01-16 | 10:56 | 49.948
2021-01-16 | 10:56 | 49.945
2021-01-16 | 10:56 | 49.948
2021-01-16 | 10:56 | 49.948
2021-01-16 | 10:56 | 49.945
2021-01-16 | 10:56 | 49.944
2021-01-16 | 10:56 | 49.944
2021-01-16 | 10:56 | 49.943
2021-01-16 | 10:56 | 49.941
2021-01-16 | 10:56 | 49.938
2021-01-16 | 10:56 | 49.935
2021-01-16 | 10:56 | 49.936
2021-01-16 | 10:56 | 49.933
2021-01-16 | 10:56 | 49.93
2021-01-16 | 10:56 | 49.929
2021-01-16 | 10:56 | 49.929
2021-01-16 | 10:56 | 49.93
2021-01-16 | 10:56 | 49.935
2021-01-16 | 10:56 | 49.936
2021-01-16 | 10:56 | 49.936
2021-01-16 | 10:56 | 49.937
2021-01-16 | 10:56 | 49.937
2021-01-16 | 10:56 | 49.937
2021-01-16 | 10:56 | 49.938
2021-01-16 | 10:56 | 49.936
2021-01-16 | 10:56 | 49.938
2021-01-16 | 10:56 | 49.938
2021-01-16 | 10:56 | 49.939
2021-01-16 | 10:56 | 49.938
2021-01-16 | 10:56 | 49.936
2021-01-16 | 10:56 | 49.935
2021-01-16 | 10:56 | 49.932
2021-01-16 | 10:56 | 49.933
2021-01-16 | 10:56 | 49.934
2021-01-16 | 10:56 | 49.933
2021-01-16 | 10:56 | 49.937
2021-01-16 | 10:56 | 49.936
2021-01-16 | 10:56 | 49.935
2021-01-16 | 10:56 | 49.939
2021-01-16 | 10:56 | 49.942
2021-01-16 | 10:56 | 49.945
2021-01-16 | 10:56 | 49.949
2021-01-16 | 10:56 | 49.948
2021-01-16 | 10:56 | 49.949
2021-01-16 | 10:56 | 49.949
2021-01-16 | 10:57 | 49.951
2021-01-16 | 10:57 | 49.95
2021-01-16 | 10:57 | 49.948
2021-01-16 | 10:57 | 49.947
2021-01-16 | 10:57 | 49.944
2021-01-16 | 10:57 | 49.941
2021-01-16 | 10:57 | 49.941
2021-01-16 | 10:57 | 49.94
2021-01-16 | 10:57 | 49.936
2021-01-16 | 10:57 | 49.935
2021-01-16 | 10:57 | 49.932
2021-01-16 | 10:57 | 49.932
2021-01-16 | 10:57 | 49.931
2021-01-16 | 10:57 | 49.932
2021-01-16 | 10:57 | 49.934
2021-01-16 | 10:57 | 49.934
2021-01-16 | 10:57 | 49.934
2021-01-16 | 10:57 | 49.935
2021-01-16 | 10:57 | 49.932
2021-01-16 | 10:57 | 49.931
2021-01-16 | 10:57 | 49.931
2021-01-16 | 10:57 | 49.928
2021-01-16 | 10:57 | 49.928
2021-01-16 | 10:57 | 49.928
2021-01-16 | 10:57 | 49.928
2021-01-16 | 10:57 | 49.928
2021-01-16 | 10:57 | 49.928
2021-01-16 | 10:57 | 49.926
2021-01-16 | 10:57 | 49.92
2021-01-16 | 10:57 | 49.917
2021-01-16 | 10:57 | 49.915
2021-01-16 | 10:57 | 49.914
2021-01-16 | 10:57 | 49.915
2021-01-16 | 10:57 | 49.919
2021-01-16 | 10:57 | 49.918
2021-01-16 | 10:57 | 49.917
2021-01-16 | 10:57 | 49.916
2021-01-16 | 10:57 | 49.916
2021-01-16 | 10:57 | 49.918
2021-01-16 | 10:57 | 49.922
2021-01-16 | 10:57 | 49.923
2021-01-16 | 10:57 | 49.926
2021-01-16 | 10:57 | 49.927
2021-01-16 | 10:57 | 49.928
2021-01-16 | 10:57 | 49.929
2021-01-16 | 10:57 | 49.928
2021-01-16 | 10:57 | 49.928
2021-01-16 | 10:57 | 49.931
2021-01-16 | 10:57 | 49.93
2021-01-16 | 10:57 | 49.931
2021-01-16 | 10:57 | 49.932
2021-01-16 | 10:57 | 49.934
2021-01-16 | 10:57 | 49.937
2021-01-16 | 10:57 | 49.937
2021-01-16 | 10:57 | 49.937
2021-01-16 | 10:57 | 49.938
2021-01-16 | 10:57 | 49.935
2021-01-16 | 10:57 | 49.934
2021-01-16 | 10:57 | 49.931
2021-01-16 | 10:58 | 49.931
2021-01-16 | 10:58 | 49.929
2021-01-16 | 10:58 | 49.93
2021-01-16 | 10:58 | 49.93
2021-01-16 | 10:58 | 49.934
2021-01-16 | 10:58 | 49.937
2021-01-16 | 10:58 | 49.939
2021-01-16 | 10:58 | 49.94
2021-01-16 | 10:58 | 49.94
2021-01-16 | 10:58 | 49.94
2021-01-16 | 10:58 | 49.941
2021-01-16 | 10:58 | 49.942
2021-01-16 | 10:58 | 49.944
2021-01-16 | 10:58 | 49.946
2021-01-16 | 10:58 | 49.948
2021-01-16 | 10:58 | 49.947
2021-01-16 | 10:58 | 49.947
2021-01-16 | 10:58 | 49.944
2021-01-16 | 10:58 | 49.943
2021-01-16 | 10:58 | 49.943
2021-01-16 | 10:58 | 49.943
2021-01-16 | 10:58 | 49.941
2021-01-16 | 10:58 | 49.942
2021-01-16 | 10:58 | 49.941
2021-01-16 | 10:58 | 49.943
2021-01-16 | 10:58 | 49.945
2021-01-16 | 10:58 | 49.947
2021-01-16 | 10:58 | 49.946
2021-01-16 | 10:58 | 49.947
2021-01-16 | 10:58 | 49.949
2021-01-16 | 10:58 | 49.949
2021-01-16 | 10:58 | 49.95
2021-01-16 | 10:58 | 49.951
2021-01-16 | 10:58 | 49.952
2021-01-16 | 10:58 | 49.948
2021-01-16 | 10:58 | 49.948
2021-01-16 | 10:58 | 49.946
2021-01-16 | 10:58 | 49.947
2021-01-16 | 10:58 | 49.948
2021-01-16 | 10:58 | 49.949
2021-01-16 | 10:58 | 49.948
2021-01-16 | 10:58 | 49.945
2021-01-16 | 10:58 | 49.941
2021-01-16 | 10:58 | 49.938
2021-01-16 | 10:58 | 49.936
2021-01-16 | 10:58 | 49.933
2021-01-16 | 10:58 | 49.934
2021-01-16 | 10:58 | 49.935
2021-01-16 | 10:58 | 49.936
2021-01-16 | 10:58 | 49.937
2021-01-16 | 10:58 | 49.938
2021-01-16 | 10:58 | 49.938
2021-01-16 | 10:58 | 49.94
2021-01-16 | 10:58 | 49.939
2021-01-16 | 10:58 | 49.94
2021-01-16 | 10:58 | 49.935
2021-01-16 | 10:58 | 49.933
2021-01-16 | 10:58 | 49.93
2021-01-16 | 10:58 | 49.931
2021-01-16 | 10:58 | 49.93
2021-01-16 | 10:58 | 49.927
2021-01-16 | 10:59 | 49.926
2021-01-16 | 10:59 | 49.926
2021-01-16 | 10:59 | 49.926
2021-01-16 | 10:59 | 49.927
2021-01-16 | 10:59 | 49.928
2021-01-16 | 10:59 | 49.931
2021-01-16 | 10:59 | 49.935
2021-01-16 | 10:59 | 49.937
2021-01-16 | 10:59 | 49.939
2021-01-16 | 10:59 | 49.94
2021-01-16 | 10:59 | 49.942
2021-01-16 | 10:59 | 49.943
2021-01-16 | 10:59 | 49.939
2021-01-16 | 10:59 | 49.938
2021-01-16 | 10:59 | 49.937
2021-01-16 | 10:59 | 49.935
2021-01-16 | 10:59 | 49.933
2021-01-16 | 10:59 | 49.931
2021-01-16 | 10:59 | 49.928
2021-01-16 | 10:59 | 49.927
2021-01-16 | 10:59 | 49.927
2021-01-16 | 10:59 | 49.926
2021-01-16 | 10:59 | 49.927
2021-01-16 | 10:59 | 49.928
2021-01-16 | 10:59 | 49.927
2021-01-16 | 10:59 | 49.926
2021-01-16 | 10:59 | 49.927
2021-01-16 | 10:59 | 49.924
2021-01-16 | 10:59 | 49.92
2021-01-16 | 10:59 | 49.918
2021-01-16 | 10:59 | 49.913
2021-01-16 | 10:59 | 49.911
2021-01-16 | 10:59 | 49.909
2021-01-16 | 10:59 | 49.91
2021-01-16 | 10:59 | 49.908
2021-01-16 | 10:59 | 49.905
2021-01-16 | 10:59 | 49.902
2021-01-16 | 10:59 | 49.901
2021-01-16 | 10:59 | 49.898
2021-01-16 | 10:59 | 49.897
2021-01-16 | 10:59 | 49.895
2021-01-16 | 10:59 | 49.896
2021-01-16 | 10:59 | 49.895
2021-01-16 | 10:59 | 49.895
2021-01-16 | 10:59 | 49.894
2021-01-16 | 10:59 | 49.894
2021-01-16 | 10:59 | 49.895
2021-01-16 | 10:59 | 49.896
2021-01-16 | 10:59 | 49.899
2021-01-16 | 10:59 | 49.901
2021-01-16 | 10:59 | 49.906
2021-01-16 | 10:59 | 49.909
2021-01-16 | 10:59 | 49.912
2021-01-16 | 10:59 | 49.915
2021-01-16 | 10:59 | 49.916
2021-01-16 | 10:59 | 49.918
2021-01-16 | 10:59 | 49.923
2021-01-16 | 10:59 | 49.929
2021-01-16 | 10:59 | 49.933
2021-01-16 | 11:00 | 49.937
2021-01-16 | 11:00 | 49.938
2021-01-16 | 11:00 | 49.939
2021-01-16 | 11:00 | 49.94
2021-01-16 | 11:00 | 49.939
2021-01-16 | 11:00 | 49.939
2021-01-16 | 11:00 | 49.94
2021-01-16 | 11:00 | 49.938
2021-01-16 | 11:00 | 49.937
2021-01-16 | 11:00 | 49.937
2021-01-16 | 11:00 | 49.936
2021-01-16 | 11:00 | 49.937
2021-01-16 | 11:00 | 49.941
2021-01-16 | 11:00 | 49.943
2021-01-16 | 11:00 | 49.945
2021-01-16 | 11:00 | 49.946
2021-01-16 | 11:00 | 49.949
2021-01-16 | 11:00 | 49.95
2021-01-16 | 11:00 | 49.95
2021-01-16 | 11:00 | 49.951
2021-01-16 | 11:00 | 49.948
2021-01-16 | 11:00 | 49.948
2021-01-16 | 11:00 | 49.947
2021-01-16 | 11:00 | 49.947
2021-01-16 | 11:00 | 49.949
2021-01-16 | 11:00 | 49.95
2021-01-16 | 11:00 | 49.951
2021-01-16 | 11:00 | 49.954
2021-01-16 | 11:00 | 49.957
2021-01-16 | 11:00 | 49.956
2021-01-16 | 11:00 | 49.956
2021-01-16 | 11:00 | 49.953
2021-01-16 | 11:00 | 49.951
2021-01-16 | 11:00 | 49.95
2021-01-16 | 11:00 | 49.949
2021-01-16 | 11:00 | 49.947
2021-01-16 | 11:00 | 49.947
2021-01-16 | 11:00 | 49.95
2021-01-16 | 11:00 | 49.955
2021-01-16 | 11:00 | 49.961
2021-01-16 | 11:00 | 49.966
2021-01-16 | 11:00 | 49.967
2021-01-16 | 11:00 | 49.969
2021-01-16 | 11:00 | 49.968
2021-01-16 | 11:00 | 49.967
2021-01-16 | 11:00 | 49.964
2021-01-16 | 11:00 | 49.96
2021-01-16 | 11:00 | 49.952
2021-01-16 | 11:00 | 49.949
2021-01-16 | 11:00 | 49.95
2021-01-16 | 11:00 | 49.95
2021-01-16 | 11:00 | 49.95
2021-01-16 | 11:00 | 49.95
2021-01-16 | 11:00 | 49.95
2021-01-16 | 11:00 | 49.954
2021-01-16 | 11:00 | 49.955
2021-01-16 | 11:00 | 49.959
2021-01-16 | 11:00 | 49.956
2021-01-16 | 11:00 | 49.951
2021-01-16 | 11:00 | 49.945
2021-01-16 | 11:00 | 49.938
2021-01-16 | 11:01 | 49.934
2021-01-16 | 11:01 | 49.932
2021-01-16 | 11:01 | 49.928
2021-01-16 | 11:01 | 49.928
2021-01-16 | 11:01 | 49.927
2021-01-16 | 11:01 | 49.928
2021-01-16 | 11:01 | 49.933
2021-01-16 | 11:01 | 49.935
2021-01-16 | 11:01 | 49.939
2021-01-16 | 11:01 | 49.942
2021-01-16 | 11:01 | 49.943
2021-01-16 | 11:01 | 49.942
2021-01-16 | 11:01 | 49.94
2021-01-16 | 11:01 | 49.941
2021-01-16 | 11:01 | 49.941
2021-01-16 | 11:01 | 49.944
2021-01-16 | 11:01 | 49.944
2021-01-16 | 11:01 | 49.944
2021-01-16 | 11:01 | 49.944
2021-01-16 | 11:01 | 49.942
2021-01-16 | 11:01 | 49.943
2021-01-16 | 11:01 | 49.944
2021-01-16 | 11:01 | 49.946
2021-01-16 | 11:01 | 49.952
2021-01-16 | 11:01 | 49.953
2021-01-16 | 11:01 | 49.955
2021-01-16 | 11:01 | 49.956
2021-01-16 | 11:01 | 49.958
2021-01-16 | 11:01 | 49.959
2021-01-16 | 11:01 | 49.959
2021-01-16 | 11:01 | 49.957
2021-01-16 | 11:01 | 49.956
2021-01-16 | 11:01 | 49.954
2021-01-16 | 11:01 | 49.954
2021-01-16 | 11:01 | 49.951
2021-01-16 | 11:01 | 49.95
2021-01-16 | 11:01 | 49.955
2021-01-16 | 11:01 | 49.957
2021-01-16 | 11:01 | 49.96
2021-01-16 | 11:01 | 49.963
2021-01-16 | 11:01 | 49.964
2021-01-16 | 11:01 | 49.965
2021-01-16 | 11:01 | 49.963
2021-01-16 | 11:01 | 49.961
2021-01-16 | 11:01 | 49.961
2021-01-16 | 11:01 | 49.959
2021-01-16 | 11:01 | 49.959
2021-01-16 | 11:01 | 49.957
2021-01-16 | 11:01 | 49.957
2021-01-16 | 11:01 | 49.957
2021-01-16 | 11:01 | 49.96
2021-01-16 | 11:01 | 49.961
2021-01-16 | 11:01 | 49.963
2021-01-16 | 11:01 | 49.962
2021-01-16 | 11:01 | 49.96
2021-01-16 | 11:01 | 49.959
2021-01-16 | 11:01 | 49.958
2021-01-16 | 11:01 | 49.957
2021-01-16 | 11:01 | 49.957
2021-01-16 | 11:02 | 49.953
2021-01-16 | 11:02 | 49.952
2021-01-16 | 11:02 | 49.951
2021-01-16 | 11:02 | 49.95
2021-01-16 | 11:02 | 49.949
2021-01-16 | 11:02 | 49.951
2021-01-16 | 11:02 | 49.949
2021-01-16 | 11:02 | 49.948
2021-01-16 | 11:02 | 49.947
2021-01-16 | 11:02 | 49.946
2021-01-16 | 11:02 | 49.945
2021-01-16 | 11:02 | 49.945
2021-01-16 | 11:02 | 49.943
2021-01-16 | 11:02 | 49.944
2021-01-16 | 11:02 | 49.944
2021-01-16 | 11:02 | 49.945
2021-01-16 | 11:02 | 49.945
2021-01-16 | 11:02 | 49.944
2021-01-16 | 11:02 | 49.945
2021-01-16 | 11:02 | 49.947
2021-01-16 | 11:02 | 49.95
2021-01-16 | 11:02 | 49.952
2021-01-16 | 11:02 | 49.951
2021-01-16 | 11:02 | 49.949
2021-01-16 | 11:02 | 49.945
2021-01-16 | 11:02 | 49.943
2021-01-16 | 11:02 | 49.942
2021-01-16 | 11:02 | 49.946
2021-01-16 | 11:02 | 49.945
2021-01-16 | 11:02 | 49.944
2021-01-16 | 11:02 | 49.943
2021-01-16 | 11:02 | 49.943
2021-01-16 | 11:02 | 49.941
2021-01-16 | 11:02 | 49.941
2021-01-16 | 11:02 | 49.939
2021-01-16 | 11:02 | 49.938
2021-01-16 | 11:02 | 49.936
2021-01-16 | 11:02 | 49.935
2021-01-16 | 11:02 | 49.936
2021-01-16 | 11:02 | 49.936
2021-01-16 | 11:02 | 49.936
2021-01-16 | 11:02 | 49.934
2021-01-16 | 11:02 | 49.933
2021-01-16 | 11:02 | 49.933
2021-01-16 | 11:02 | 49.932
2021-01-16 | 11:02 | 49.936
2021-01-16 | 11:02 | 49.937
2021-01-16 | 11:02 | 49.935
2021-01-16 | 11:02 | 49.934
2021-01-16 | 11:02 | 49.934
2021-01-16 | 11:02 | 49.934
2021-01-16 | 11:02 | 49.935
2021-01-16 | 11:02 | 49.936
2021-01-16 | 11:02 | 49.937
2021-01-16 | 11:02 | 49.937
2021-01-16 | 11:02 | 49.94
2021-01-16 | 11:02 | 49.943
2021-01-16 | 11:02 | 49.945
2021-01-16 | 11:02 | 49.946
2021-01-16 | 11:02 | 49.947
2021-01-16 | 11:02 | 49.947
2021-01-16 | 11:03 | 49.947
2021-01-16 | 11:03 | 49.946
2021-01-16 | 11:03 | 49.945
2021-01-16 | 11:03 | 49.947
2021-01-16 | 11:03 | 49.949
2021-01-16 | 11:03 | 49.953
2021-01-16 | 11:03 | 49.956
2021-01-16 | 11:03 | 49.958
2021-01-16 | 11:03 | 49.959
2021-01-16 | 11:03 | 49.961
2021-01-16 | 11:03 | 49.962
2021-01-16 | 11:03 | 49.963
2021-01-16 | 11:03 | 49.965
2021-01-16 | 11:03 | 49.967
2021-01-16 | 11:03 | 49.969
2021-01-16 | 11:03 | 49.972
2021-01-16 | 11:03 | 49.977
2021-01-16 | 11:03 | 49.979
2021-01-16 | 11:03 | 49.982
2021-01-16 | 11:03 | 49.984
2021-01-16 | 11:03 | 49.986
2021-01-16 | 11:03 | 49.985
2021-01-16 | 11:03 | 49.983
2021-01-16 | 11:03 | 49.982
2021-01-16 | 11:03 | 49.985
2021-01-16 | 11:03 | 49.985
2021-01-16 | 11:03 | 49.985
2021-01-16 | 11:03 | 49.987
2021-01-16 | 11:03 | 49.987
2021-01-16 | 11:03 | 49.986
2021-01-16 | 11:03 | 49.987
2021-01-16 | 11:03 | 49.988
2021-01-16 | 11:03 | 49.989
2021-01-16 | 11:03 | 49.993
2021-01-16 | 11:03 | 49.995
2021-01-16 | 11:03 | 49.997
2021-01-16 | 11:03 | 49.998
2021-01-16 | 11:03 | 50.001
2021-01-16 | 11:03 | 50.003
2021-01-16 | 11:03 | 50.003
2021-01-16 | 11:03 | 50.002
2021-01-16 | 11:03 | 50.002
2021-01-16 | 11:03 | 50.002
2021-01-16 | 11:03 | 50.002
2021-01-16 | 11:03 | 49.998
2021-01-16 | 11:03 | 49.995
2021-01-16 | 11:03 | 49.996
2021-01-16 | 11:03 | 49.992
2021-01-16 | 11:03 | 49.987
2021-01-16 | 11:03 | 49.983
2021-01-16 | 11:03 | 49.979
2021-01-16 | 11:03 | 49.975
2021-01-16 | 11:03 | 49.971
2021-01-16 | 11:03 | 49.972
2021-01-16 | 11:03 | 49.972
2021-01-16 | 11:03 | 49.974
2021-01-16 | 11:03 | 49.975
2021-01-16 | 11:03 | 49.975
2021-01-16 | 11:03 | 49.974
2021-01-16 | 11:04 | 49.975
2021-01-16 | 11:04 | 49.977
2021-01-16 | 11:04 | 49.978
2021-01-16 | 11:04 | 49.979
2021-01-16 | 11:04 | 49.98
2021-01-16 | 11:04 | 49.979
2021-01-16 | 11:04 | 49.977
2021-01-16 | 11:04 | 49.975
2021-01-16 | 11:04 | 49.973
2021-01-16 | 11:04 | 49.973
2021-01-16 | 11:04 | 49.974
2021-01-16 | 11:04 | 49.974
2021-01-16 | 11:04 | 49.977
2021-01-16 | 11:04 | 49.978
2021-01-16 | 11:04 | 49.978
2021-01-16 | 11:04 | 49.976
2021-01-16 | 11:04 | 49.973
2021-01-16 | 11:04 | 49.969
2021-01-16 | 11:04 | 49.968
2021-01-16 | 11:04 | 49.965
2021-01-16 | 11:04 | 49.966
2021-01-16 | 11:04 | 49.966
2021-01-16 | 11:04 | 49.966
2021-01-16 | 11:04 | 49.969
2021-01-16 | 11:04 | 49.969
2021-01-16 | 11:04 | 49.972
2021-01-16 | 11:04 | 49.975
2021-01-16 | 11:04 | 49.975
2021-01-16 | 11:04 | 49.975
2021-01-16 | 11:04 | 49.975
2021-01-16 | 11:04 | 49.974
2021-01-16 | 11:04 | 49.972
2021-01-16 | 11:04 | 49.969
2021-01-16 | 11:04 | 49.968
2021-01-16 | 11:04 | 49.968
2021-01-16 | 11:04 | 49.97
2021-01-16 | 11:04 | 49.973
2021-01-16 | 11:04 | 49.973
2021-01-16 | 11:04 | 49.971
2021-01-16 | 11:04 | 49.969
2021-01-16 | 11:04 | 49.966
2021-01-16 | 11:04 | 49.962
2021-01-16 | 11:04 | 49.958
2021-01-16 | 11:04 | 49.956
2021-01-16 | 11:04 | 49.96
2021-01-16 | 11:04 | 49.963
2021-01-16 | 11:04 | 49.966
2021-01-16 | 11:04 | 49.97
2021-01-16 | 11:04 | 49.97
2021-01-16 | 11:04 | 49.97
2021-01-16 | 11:04 | 49.972
2021-01-16 | 11:04 | 49.971
2021-01-16 | 11:04 | 49.97
2021-01-16 | 11:04 | 49.969
2021-01-16 | 11:04 | 49.967
2021-01-16 | 11:04 | 49.968
2021-01-16 | 11:04 | 49.967
2021-01-16 | 11:04 | 49.968
2021-01-16 | 11:04 | 49.97
2021-01-16 | 11:04 | 49.97
2021-01-16 | 11:04 | 49.973
2021-01-16 | 11:05 | 49.976
2021-01-16 | 11:05 | 49.978
2021-01-16 | 11:05 | 49.984
2021-01-16 | 11:05 | 49.987
2021-01-16 | 11:05 | 49.988
2021-01-16 | 11:05 | 49.988
2021-01-16 | 11:05 | 49.984
2021-01-16 | 11:05 | 49.981
2021-01-16 | 11:05 | 49.979
2021-01-16 | 11:05 | 49.982
2021-01-16 | 11:05 | 49.986
2021-01-16 | 11:05 | 49.987
2021-01-16 | 11:05 | 49.988
2021-01-16 | 11:05 | 49.99
2021-01-16 | 11:05 | 49.992
2021-01-16 | 11:05 | 49.994
2021-01-16 | 11:05 | 49.998
2021-01-16 | 11:05 | 49.998
2021-01-16 | 11:05 | 50.001
2021-01-16 | 11:05 | 50.001
2021-01-16 | 11:05 | 50.004
2021-01-16 | 11:05 | 50.004
2021-01-16 | 11:05 | 50.006
2021-01-16 | 11:05 | 50.01
2021-01-16 | 11:05 | 50.015
2021-01-16 | 11:05 | 50.019
2021-01-16 | 11:05 | 50.021
2021-01-16 | 11:05 | 50.021
2021-01-16 | 11:05 | 50.024
2021-01-16 | 11:05 | 50.026
2021-01-16 | 11:05 | 50.03
2021-01-16 | 11:05 | 50.034
2021-01-16 | 11:05 | 50.035
2021-01-16 | 11:05 | 50.037
2021-01-16 | 11:05 | 50.041
2021-01-16 | 11:05 | 50.042
2021-01-16 | 11:05 | 50.045
2021-01-16 | 11:05 | 50.048
2021-01-16 | 11:05 | 50.048
2021-01-16 | 11:05 | 50.047
2021-01-16 | 11:05 | 50.046
2021-01-16 | 11:05 | 50.044
2021-01-16 | 11:05 | 50.042
2021-01-16 | 11:05 | 50.039
2021-01-16 | 11:05 | 50.04
2021-01-16 | 11:05 | 50.041
2021-01-16 | 11:05 | 50.046
2021-01-16 | 11:05 | 50.045
2021-01-16 | 11:05 | 50.044
2021-01-16 | 11:05 | 50.044
2021-01-16 | 11:05 | 50.047
2021-01-16 | 11:05 | 50.047
2021-01-16 | 11:05 | 50.049
2021-01-16 | 11:05 | 50.053
2021-01-16 | 11:05 | 50.054
2021-01-16 | 11:05 | 50.058
2021-01-16 | 11:05 | 50.056
2021-01-16 | 11:05 | 50.057
2021-01-16 | 11:05 | 50.054
2021-01-16 | 11:06 | 50.056
2021-01-16 | 11:06 | 50.056
2021-01-16 | 11:06 | 50.057
2021-01-16 | 11:06 | 50.057
2021-01-16 | 11:06 | 50.059
2021-01-16 | 11:06 | 50.058
2021-01-16 | 11:06 | 50.06
2021-01-16 | 11:06 | 50.06
2021-01-16 | 11:06 | 50.061
2021-01-16 | 11:06 | 50.064
2021-01-16 | 11:06 | 50.063
2021-01-16 | 11:06 | 50.062
2021-01-16 | 11:06 | 50.063
2021-01-16 | 11:06 | 50.062
2021-01-16 | 11:06 | 50.063
2021-01-16 | 11:06 | 50.061
2021-01-16 | 11:06 | 50.058
2021-01-16 | 11:06 | 50.055
2021-01-16 | 11:06 | 50.052
2021-01-16 | 11:06 | 50.049
2021-01-16 | 11:06 | 50.048
2021-01-16 | 11:06 | 50.045
2021-01-16 | 11:06 | 50.043
2021-01-16 | 11:06 | 50.043
2021-01-16 | 11:06 | 50.043
2021-01-16 | 11:06 | 50.043
2021-01-16 | 11:06 | 50.042
2021-01-16 | 11:06 | 50.042
2021-01-16 | 11:06 | 50.04
2021-01-16 | 11:06 | 50.036
2021-01-16 | 11:06 | 50.035
2021-01-16 | 11:06 | 50.033
2021-01-16 | 11:06 | 50.035
2021-01-16 | 11:06 | 50.035
2021-01-16 | 11:06 | 50.035
2021-01-16 | 11:06 | 50.034
2021-01-16 | 11:06 | 50.034
2021-01-16 | 11:06 | 50.034
2021-01-16 | 11:06 | 50.034
2021-01-16 | 11:06 | 50.034
2021-01-16 | 11:06 | 50.034
2021-01-16 | 11:06 | 50.035
2021-01-16 | 11:06 | 50.035
2021-01-16 | 11:06 | 50.036
2021-01-16 | 11:06 | 50.035
2021-01-16 | 11:06 | 50.037
2021-01-16 | 11:06 | 50.036
2021-01-16 | 11:06 | 50.035
2021-01-16 | 11:06 | 50.035
2021-01-16 | 11:06 | 50.037
2021-01-16 | 11:06 | 50.042
2021-01-16 | 11:06 | 50.044
2021-01-16 | 11:06 | 50.047
2021-01-16 | 11:06 | 50.052
2021-01-16 | 11:06 | 50.055
2021-01-16 | 11:06 | 50.058
2021-01-16 | 11:06 | 50.062
2021-01-16 | 11:06 | 50.065
2021-01-16 | 11:06 | 50.067
2021-01-16 | 11:06 | 50.067
2021-01-16 | 11:06 | 50.065
2021-01-16 | 11:07 | 50.061
2021-01-16 | 11:07 | 50.06
2021-01-16 | 11:07 | 50.059
2021-01-16 | 11:07 | 50.059
2021-01-16 | 11:07 | 50.06
2021-01-16 | 11:07 | 50.062
2021-01-16 | 11:07 | 50.061
2021-01-16 | 11:07 | 50.062
2021-01-16 | 11:07 | 50.064
2021-01-16 | 11:07 | 50.062
2021-01-16 | 11:07 | 50.064
2021-01-16 | 11:07 | 50.062
2021-01-16 | 11:07 | 50.059
2021-01-16 | 11:07 | 50.059
2021-01-16 | 11:07 | 50.059
2021-01-16 | 11:07 | 50.059
2021-01-16 | 11:07 | 50.059
2021-01-16 | 11:07 | 50.058
2021-01-16 | 11:07 | 50.059
2021-01-16 | 11:07 | 50.059
2021-01-16 | 11:07 | 50.061
2021-01-16 | 11:07 | 50.06
2021-01-16 | 11:07 | 50.059
2021-01-16 | 11:07 | 50.057
2021-01-16 | 11:07 | 50.058
2021-01-16 | 11:07 | 50.055
2021-01-16 | 11:07 | 50.053
2021-01-16 | 11:07 | 50.052
2021-01-16 | 11:07 | 50.054
2021-01-16 | 11:07 | 50.052
2021-01-16 | 11:07 | 50.053
2021-01-16 | 11:07 | 50.053
2021-01-16 | 11:07 | 50.052
2021-01-16 | 11:07 | 50.053
2021-01-16 | 11:07 | 50.052
2021-01-16 | 11:07 | 50.05
2021-01-16 | 11:07 | 50.051
2021-01-16 | 11:07 | 50.053
2021-01-16 | 11:07 | 50.056
2021-01-16 | 11:07 | 50.058
2021-01-16 | 11:07 | 50.06
2021-01-16 | 11:07 | 50.058
2021-01-16 | 11:07 | 50.058
2021-01-16 | 11:07 | 50.058
2021-01-16 | 11:07 | 50.059
2021-01-16 | 11:07 | 50.063
2021-01-16 | 11:07 | 50.064
2021-01-16 | 11:07 | 50.063
2021-01-16 | 11:07 | 50.062
2021-01-16 | 11:07 | 50.062
2021-01-16 | 11:07 | 50.061
2021-01-16 | 11:07 | 50.059
2021-01-16 | 11:07 | 50.057
2021-01-16 | 11:07 | 50.057
2021-01-16 | 11:07 | 50.055
2021-01-16 | 11:07 | 50.054
2021-01-16 | 11:07 | 50.056
2021-01-16 | 11:07 | 50.055
2021-01-16 | 11:07 | 50.053
2021-01-16 | 11:08 | 50.05
2021-01-16 | 11:08 | 50.053
2021-01-16 | 11:08 | 50.052
2021-01-16 | 11:08 | 50.051
2021-01-16 | 11:08 | 50.054
2021-01-16 | 11:08 | 50.056
2021-01-16 | 11:08 | 50.059
2021-01-16 | 11:08 | 50.06
2021-01-16 | 11:08 | 50.062
2021-01-16 | 11:08 | 50.065
2021-01-16 | 11:08 | 50.067
2021-01-16 | 11:08 | 50.068
2021-01-16 | 11:08 | 50.067
2021-01-16 | 11:08 | 50.066
2021-01-16 | 11:08 | 50.066
2021-01-16 | 11:08 | 50.067
2021-01-16 | 11:08 | 50.066
2021-01-16 | 11:08 | 50.063
2021-01-16 | 11:08 | 50.062
2021-01-16 | 11:08 | 50.059
2021-01-16 | 11:08 | 50.058
2021-01-16 | 11:08 | 50.057
2021-01-16 | 11:08 | 50.058
2021-01-16 | 11:08 | 50.057
2021-01-16 | 11:08 | 50.058
2021-01-16 | 11:08 | 50.057
2021-01-16 | 11:08 | 50.056
2021-01-16 | 11:08 | 50.056
2021-01-16 | 11:08 | 50.053
2021-01-16 | 11:08 | 50.053
2021-01-16 | 11:08 | 50.05
2021-01-16 | 11:08 | 50.049
2021-01-16 | 11:08 | 50.047
2021-01-16 | 11:08 | 50.046
2021-01-16 | 11:08 | 50.047
2021-01-16 | 11:08 | 50.046
2021-01-16 | 11:08 | 50.048
2021-01-16 | 11:08 | 50.046
2021-01-16 | 11:08 | 50.044
2021-01-16 | 11:08 | 50.043
2021-01-16 | 11:08 | 50.043
2021-01-16 | 11:08 | 50.042
2021-01-16 | 11:08 | 50.041
2021-01-16 | 11:08 | 50.041
2021-01-16 | 11:08 | 50.042
2021-01-16 | 11:08 | 50.041
2021-01-16 | 11:08 | 50.039
2021-01-16 | 11:08 | 50.037
2021-01-16 | 11:08 | 50.037
2021-01-16 | 11:08 | 50.039
2021-01-16 | 11:08 | 50.04
2021-01-16 | 11:08 | 50.042
2021-01-16 | 11:08 | 50.042
2021-01-16 | 11:08 | 50.044
2021-01-16 | 11:08 | 50.043
2021-01-16 | 11:08 | 50.045
2021-01-16 | 11:08 | 50.044
2021-01-16 | 11:08 | 50.043
2021-01-16 | 11:08 | 50.042
2021-01-16 | 11:08 | 50.04
2021-01-16 | 11:08 | 50.039
2021-01-16 | 11:09 | 50.037
2021-01-16 | 11:09 | 50.036
2021-01-16 | 11:09 | 50.036
2021-01-16 | 11:09 | 50.037
2021-01-16 | 11:09 | 50.039
2021-01-16 | 11:09 | 50.039
2021-01-16 | 11:09 | 50.04
2021-01-16 | 11:09 | 50.041
2021-01-16 | 11:09 | 50.044
2021-01-16 | 11:09 | 50.046
2021-01-16 | 11:09 | 50.049
2021-01-16 | 11:09 | 50.049
2021-01-16 | 11:09 | 50.051
2021-01-16 | 11:09 | 50.05
2021-01-16 | 11:09 | 50.046
2021-01-16 | 11:09 | 50.045
2021-01-16 | 11:09 | 50.041
2021-01-16 | 11:09 | 50.043
2021-01-16 | 11:09 | 50.045
2021-01-16 | 11:09 | 50.047
2021-01-16 | 11:09 | 50.048
2021-01-16 | 11:09 | 50.046
2021-01-16 | 11:09 | 50.049
2021-01-16 | 11:09 | 50.048
2021-01-16 | 11:09 | 50.048
2021-01-16 | 11:09 | 50.049
2021-01-16 | 11:09 | 50.051
2021-01-16 | 11:09 | 50.051
2021-01-16 | 11:09 | 50.051
2021-01-16 | 11:09 | 50.049
2021-01-16 | 11:09 | 50.048
2021-01-16 | 11:09 | 50.051
2021-01-16 | 11:09 | 50.052
2021-01-16 | 11:09 | 50.054
2021-01-16 | 11:09 | 50.052
2021-01-16 | 11:09 | 50.054
2021-01-16 | 11:09 | 50.053
2021-01-16 | 11:09 | 50.055
2021-01-16 | 11:09 | 50.054
2021-01-16 | 11:09 | 50.055
2021-01-16 | 11:09 | 50.053
2021-01-16 | 11:09 | 50.052
2021-01-16 | 11:09 | 50.051
2021-01-16 | 11:09 | 50.048
2021-01-16 | 11:09 | 50.048
2021-01-16 | 11:09 | 50.05
2021-01-16 | 11:09 | 50.051
2021-01-16 | 11:09 | 50.053
2021-01-16 | 11:09 | 50.057
2021-01-16 | 11:09 | 50.059
2021-01-16 | 11:09 | 50.059
2021-01-16 | 11:09 | 50.056
2021-01-16 | 11:09 | 50.056
2021-01-16 | 11:09 | 50.057
2021-01-16 | 11:09 | 50.06
2021-01-16 | 11:09 | 50.059
2021-01-16 | 11:09 | 50.06
2021-01-16 | 11:09 | 50.058
2021-01-16 | 11:09 | 50.059
2021-01-16 | 11:10 | 50.059
2021-01-16 | 11:10 | 50.058
2021-01-16 | 11:10 | 50.062
2021-01-16 | 11:10 | 50.061
2021-01-16 | 11:10 | 50.064
2021-01-16 | 11:10 | 50.064
2021-01-16 | 11:10 | 50.065
2021-01-16 | 11:10 | 50.066
2021-01-16 | 11:10 | 50.065
2021-01-16 | 11:10 | 50.066
2021-01-16 | 11:10 | 50.063
2021-01-16 | 11:10 | 50.063
2021-01-16 | 11:10 | 50.061
2021-01-16 | 11:10 | 50.062
2021-01-16 | 11:10 | 50.063
2021-01-16 | 11:10 | 50.063
2021-01-16 | 11:10 | 50.063
2021-01-16 | 11:10 | 50.064
2021-01-16 | 11:10 | 50.065
2021-01-16 | 11:10 | 50.066
2021-01-16 | 11:10 | 50.068
2021-01-16 | 11:10 | 50.069
2021-01-16 | 11:10 | 50.067
2021-01-16 | 11:10 | 50.067
2021-01-16 | 11:10 | 50.067
2021-01-16 | 11:10 | 50.07
2021-01-16 | 11:10 | 50.072
2021-01-16 | 11:10 | 50.074
2021-01-16 | 11:10 | 50.073
2021-01-16 | 11:10 | 50.073
2021-01-16 | 11:10 | 50.072
2021-01-16 | 11:10 | 50.069
2021-01-16 | 11:10 | 50.066
2021-01-16 | 11:10 | 50.062
2021-01-16 | 11:10 | 50.06
2021-01-16 | 11:10 | 50.058
2021-01-16 | 11:10 | 50.057
2021-01-16 | 11:10 | 50.054
2021-01-16 | 11:10 | 50.053
2021-01-16 | 11:10 | 50.052
2021-01-16 | 11:10 | 50.052
2021-01-16 | 11:10 | 50.054
2021-01-16 | 11:10 | 50.055
2021-01-16 | 11:10 | 50.055
2021-01-16 | 11:10 | 50.056
2021-01-16 | 11:10 | 50.056
2021-01-16 | 11:10 | 50.055
2021-01-16 | 11:10 | 50.056
2021-01-16 | 11:10 | 50.055
2021-01-16 | 11:10 | 50.056
2021-01-16 | 11:10 | 50.056
2021-01-16 | 11:10 | 50.057
2021-01-16 | 11:10 | 50.059
2021-01-16 | 11:10 | 50.062
2021-01-16 | 11:10 | 50.063
2021-01-16 | 11:10 | 50.064
2021-01-16 | 11:10 | 50.064
2021-01-16 | 11:10 | 50.061
2021-01-16 | 11:10 | 50.061
2021-01-16 | 11:10 | 50.061
2021-01-16 | 11:10 | 50.062
2021-01-16 | 11:11 | 50.061
2021-01-16 | 11:11 | 50.058
2021-01-16 | 11:11 | 50.057
2021-01-16 | 11:11 | 50.058
2021-01-16 | 11:11 | 50.057
2021-01-16 | 11:11 | 50.058
2021-01-16 | 11:11 | 50.059
2021-01-16 | 11:11 | 50.058
2021-01-16 | 11:11 | 50.059
2021-01-16 | 11:11 | 50.06
2021-01-16 | 11:11 | 50.06
2021-01-16 | 11:11 | 50.062
2021-01-16 | 11:11 | 50.062
2021-01-16 | 11:11 | 50.061
2021-01-16 | 11:11 | 50.061
2021-01-16 | 11:11 | 50.06
2021-01-16 | 11:11 | 50.062
2021-01-16 | 11:11 | 50.064
2021-01-16 | 11:11 | 50.068
2021-01-16 | 11:11 | 50.071
2021-01-16 | 11:11 | 50.071
2021-01-16 | 11:11 | 50.07
2021-01-16 | 11:11 | 50.069
2021-01-16 | 11:11 | 50.069
2021-01-16 | 11:11 | 50.072
2021-01-16 | 11:11 | 50.07
2021-01-16 | 11:11 | 50.07
2021-01-16 | 11:11 | 50.069
2021-01-16 | 11:11 | 50.069
2021-01-16 | 11:11 | 50.069
2021-01-16 | 11:11 | 50.067
2021-01-16 | 11:11 | 50.068
2021-01-16 | 11:11 | 50.068
2021-01-16 | 11:11 | 50.069
2021-01-16 | 11:11 | 50.068
2021-01-16 | 11:11 | 50.068
2021-01-16 | 11:11 | 50.067
2021-01-16 | 11:11 | 50.068
2021-01-16 | 11:11 | 50.068
2021-01-16 | 11:11 | 50.07
2021-01-16 | 11:11 | 50.072
2021-01-16 | 11:11 | 50.074
2021-01-16 | 11:11 | 50.075
2021-01-16 | 11:11 | 50.078
2021-01-16 | 11:11 | 50.08
2021-01-16 | 11:11 | 50.083
2021-01-16 | 11:11 | 50.086
2021-01-16 | 11:11 | 50.091
2021-01-16 | 11:11 | 50.092
2021-01-16 | 11:11 | 50.094
2021-01-16 | 11:11 | 50.093
2021-01-16 | 11:11 | 50.091
2021-01-16 | 11:11 | 50.085
2021-01-16 | 11:11 | 50.079
2021-01-16 | 11:11 | 50.074
2021-01-16 | 11:11 | 50.072
2021-01-16 | 11:11 | 50.068
2021-01-16 | 11:11 | 50.069
2021-01-16 | 11:11 | 50.069
2021-01-16 | 11:12 | 50.07
2021-01-16 | 11:12 | 50.07
2021-01-16 | 11:12 | 50.069
2021-01-16 | 11:12 | 50.071
2021-01-16 | 11:12 | 50.071
2021-01-16 | 11:12 | 50.072
2021-01-16 | 11:12 | 50.072
2021-01-16 | 11:12 | 50.074
2021-01-16 | 11:12 | 50.074
2021-01-16 | 11:12 | 50.077
2021-01-16 | 11:12 | 50.08
2021-01-16 | 11:12 | 50.083
2021-01-16 | 11:12 | 50.086
2021-01-16 | 11:12 | 50.088
2021-01-16 | 11:12 | 50.087
2021-01-16 | 11:12 | 50.087
2021-01-16 | 11:12 | 50.087
2021-01-16 | 11:12 | 50.083
2021-01-16 | 11:12 | 50.084
2021-01-16 | 11:12 | 50.082
2021-01-16 | 11:12 | 50.082
2021-01-16 | 11:12 | 50.079
2021-01-16 | 11:12 | 50.083
2021-01-16 | 11:12 | 50.084
2021-01-16 | 11:12 | 50.085
2021-01-16 | 11:12 | 50.084
2021-01-16 | 11:12 | 50.083
2021-01-16 | 11:12 | 50.079
2021-01-16 | 11:12 | 50.076
2021-01-16 | 11:12 | 50.074
2021-01-16 | 11:12 | 50.071
2021-01-16 | 11:12 | 50.071
2021-01-16 | 11:12 | 50.07
2021-01-16 | 11:12 | 50.069
2021-01-16 | 11:12 | 50.07
2021-01-16 | 11:12 | 50.068
2021-01-16 | 11:12 | 50.07
2021-01-16 | 11:12 | 50.07
2021-01-16 | 11:12 | 50.072
2021-01-16 | 11:12 | 50.07
2021-01-16 | 11:12 | 50.069
2021-01-16 | 11:12 | 50.071
2021-01-16 | 11:12 | 50.072
2021-01-16 | 11:12 | 50.074
2021-01-16 | 11:12 | 50.073
2021-01-16 | 11:12 | 50.073
2021-01-16 | 11:12 | 50.072
2021-01-16 | 11:12 | 50.07
2021-01-16 | 11:12 | 50.069
2021-01-16 | 11:12 | 50.071
2021-01-16 | 11:12 | 50.073
2021-01-16 | 11:12 | 50.074
2021-01-16 | 11:12 | 50.075
2021-01-16 | 11:12 | 50.074
2021-01-16 | 11:12 | 50.074
2021-01-16 | 11:12 | 50.073
2021-01-16 | 11:12 | 50.074
2021-01-16 | 11:12 | 50.072
2021-01-16 | 11:12 | 50.069
2021-01-16 | 11:12 | 50.067
2021-01-16 | 11:12 | 50.065
2021-01-16 | 11:13 | 50.062
2021-01-16 | 11:13 | 50.062
2021-01-16 | 11:13 | 50.062
2021-01-16 | 11:13 | 50.064
2021-01-16 | 11:13 | 50.066
2021-01-16 | 11:13 | 50.068
2021-01-16 | 11:13 | 50.073
2021-01-16 | 11:13 | 50.077
2021-01-16 | 11:13 | 50.08
2021-01-16 | 11:13 | 50.08
2021-01-16 | 11:13 | 50.084
2021-01-16 | 11:13 | 50.086
2021-01-16 | 11:13 | 50.088
2021-01-16 | 11:13 | 50.086
2021-01-16 | 11:13 | 50.083
2021-01-16 | 11:13 | 50.079
2021-01-16 | 11:13 | 50.078
2021-01-16 | 11:13 | 50.075
2021-01-16 | 11:13 | 50.073
2021-01-16 | 11:13 | 50.071
2021-01-16 | 11:13 | 50.073
2021-01-16 | 11:13 | 50.071
2021-01-16 | 11:13 | 50.07
2021-01-16 | 11:13 | 50.07
2021-01-16 | 11:13 | 50.071
2021-01-16 | 11:13 | 50.07
2021-01-16 | 11:13 | 50.071
2021-01-16 | 11:13 | 50.071
2021-01-16 | 11:13 | 50.075
2021-01-16 | 11:13 | 50.074
2021-01-16 | 11:13 | 50.075
2021-01-16 | 11:13 | 50.071
2021-01-16 | 11:13 | 50.068
2021-01-16 | 11:13 | 50.063
2021-01-16 | 11:13 | 50.061
2021-01-16 | 11:13 | 50.059
2021-01-16 | 11:13 | 50.054
2021-01-16 | 11:13 | 50.051
2021-01-16 | 11:13 | 50.049
2021-01-16 | 11:13 | 50.052
2021-01-16 | 11:13 | 50.05
2021-01-16 | 11:13 | 50.055
2021-01-16 | 11:13 | 50.057
2021-01-16 | 11:13 | 50.058
2021-01-16 | 11:13 | 50.06
2021-01-16 | 11:13 | 50.06
2021-01-16 | 11:13 | 50.061
2021-01-16 | 11:13 | 50.061
2021-01-16 | 11:13 | 50.063
2021-01-16 | 11:13 | 50.064
2021-01-16 | 11:13 | 50.066
2021-01-16 | 11:13 | 50.07
2021-01-16 | 11:13 | 50.068
2021-01-16 | 11:13 | 50.069
2021-01-16 | 11:13 | 50.068
2021-01-16 | 11:13 | 50.068
2021-01-16 | 11:13 | 50.067
2021-01-16 | 11:13 | 50.065
2021-01-16 | 11:13 | 50.068
2021-01-16 | 11:14 | 50.068
2021-01-16 | 11:14 | 50.069
2021-01-16 | 11:14 | 50.067
2021-01-16 | 11:14 | 50.065
2021-01-16 | 11:14 | 50.064
2021-01-16 | 11:14 | 50.062
2021-01-16 | 11:14 | 50.06
2021-01-16 | 11:14 | 50.057
2021-01-16 | 11:14 | 50.052
2021-01-16 | 11:14 | 50.051
2021-01-16 | 11:14 | 50.052
2021-01-16 | 11:14 | 50.052
2021-01-16 | 11:14 | 50.052
2021-01-16 | 11:14 | 50.052
2021-01-16 | 11:14 | 50.053
2021-01-16 | 11:14 | 50.054
2021-01-16 | 11:14 | 50.052
2021-01-16 | 11:14 | 50.051
2021-01-16 | 11:14 | 50.052
2021-01-16 | 11:14 | 50.048
2021-01-16 | 11:14 | 50.049
2021-01-16 | 11:14 | 50.047
2021-01-16 | 11:14 | 50.044
2021-01-16 | 11:14 | 50.043
2021-01-16 | 11:14 | 50.04
2021-01-16 | 11:14 | 50.042
2021-01-16 | 11:14 | 50.041
2021-01-16 | 11:14 | 50.038
2021-01-16 | 11:14 | 50.036
2021-01-16 | 11:14 | 50.035
2021-01-16 | 11:14 | 50.033
2021-01-16 | 11:14 | 50.033
2021-01-16 | 11:14 | 50.033
2021-01-16 | 11:14 | 50.031
2021-01-16 | 11:14 | 50.031
2021-01-16 | 11:14 | 50.034
2021-01-16 | 11:14 | 50.032
2021-01-16 | 11:14 | 50.031
2021-01-16 | 11:14 | 50.031
2021-01-16 | 11:14 | 50.028
2021-01-16 | 11:14 | 50.026
2021-01-16 | 11:14 | 50.023
2021-01-16 | 11:14 | 50.022
2021-01-16 | 11:14 | 50.023
2021-01-16 | 11:14 | 50.022
2021-01-16 | 11:14 | 50.021
2021-01-16 | 11:14 | 50.02
2021-01-16 | 11:14 | 50.021
2021-01-16 | 11:14 | 50.021
2021-01-16 | 11:14 | 50.023
2021-01-16 | 11:14 | 50.025
2021-01-16 | 11:14 | 50.027
2021-01-16 | 11:14 | 50.028
2021-01-16 | 11:14 | 50.027
2021-01-16 | 11:14 | 50.028
2021-01-16 | 11:14 | 50.029
2021-01-16 | 11:14 | 50.03
2021-01-16 | 11:14 | 50.03
2021-01-16 | 11:14 | 50.027
2021-01-16 | 11:14 | 50.026
2021-01-16 | 11:14 | 50.024
2021-01-16 | 11:15 | 50.021
2021-01-16 | 11:15 | 50.02
2021-01-16 | 11:15 | 50.02
2021-01-16 | 11:15 | 50.02
2021-01-16 | 11:15 | 50.024
2021-01-16 | 11:15 | 50.028
2021-01-16 | 11:15 | 50.031
2021-01-16 | 11:15 | 50.032
2021-01-16 | 11:15 | 50.029
2021-01-16 | 11:15 | 50.028
2021-01-16 | 11:15 | 50.023
2021-01-16 | 11:15 | 50.019
2021-01-16 | 11:15 | 50.016
2021-01-16 | 11:15 | 50.016
2021-01-16 | 11:15 | 50.015
2021-01-16 | 11:15 | 50.013
2021-01-16 | 11:15 | 50.012
2021-01-16 | 11:15 | 50.012
2021-01-16 | 11:15 | 50.01
2021-01-16 | 11:15 | 50.011
2021-01-16 | 11:15 | 50.012
2021-01-16 | 11:15 | 50.014
2021-01-16 | 11:15 | 50.015
2021-01-16 | 11:15 | 50.018
2021-01-16 | 11:15 | 50.019
2021-01-16 | 11:15 | 50.021
2021-01-16 | 11:15 | 50.022
2021-01-16 | 11:15 | 50.026
2021-01-16 | 11:15 | 50.028
2021-01-16 | 11:15 | 50.031
2021-01-16 | 11:15 | 50.031
2021-01-16 | 11:15 | 50.031
2021-01-16 | 11:15 | 50.031
2021-01-16 | 11:15 | 50.035
2021-01-16 | 11:15 | 50.037
2021-01-16 | 11:15 | 50.038
2021-01-16 | 11:15 | 50.043
2021-01-16 | 11:15 | 50.046
2021-01-16 | 11:15 | 50.05
2021-01-16 | 11:15 | 50.055
2021-01-16 | 11:15 | 50.054
2021-01-16 | 11:15 | 50.052
2021-01-16 | 11:15 | 50.05
2021-01-16 | 11:15 | 50.048
2021-01-16 | 11:15 | 50.049
2021-01-16 | 11:15 | 50.049
2021-01-16 | 11:15 | 50.049
2021-01-16 | 11:15 | 50.049
2021-01-16 | 11:15 | 50.049
2021-01-16 | 11:15 | 50.05
2021-01-16 | 11:15 | 50.052
2021-01-16 | 11:15 | 50.052
2021-01-16 | 11:15 | 50.05
2021-01-16 | 11:15 | 50.047
2021-01-16 | 11:15 | 50.045
2021-01-16 | 11:15 | 50.042
2021-01-16 | 11:15 | 50.04
2021-01-16 | 11:15 | 50.038
2021-01-16 | 11:15 | 50.037
2021-01-16 | 11:16 | 50.036
2021-01-16 | 11:16 | 50.036
2021-01-16 | 11:16 | 50.039
2021-01-16 | 11:16 | 50.042
2021-01-16 | 11:16 | 50.043
2021-01-16 | 11:16 | 50.046
2021-01-16 | 11:16 | 50.048
2021-01-16 | 11:16 | 50.051
2021-01-16 | 11:16 | 50.05
2021-01-16 | 11:16 | 50.052
2021-01-16 | 11:16 | 50.053
2021-01-16 | 11:16 | 50.051
2021-01-16 | 11:16 | 50.047
2021-01-16 | 11:16 | 50.042
2021-01-16 | 11:16 | 50.037
2021-01-16 | 11:16 | 50.034
2021-01-16 | 11:16 | 50.031
2021-01-16 | 11:16 | 50.031
2021-01-16 | 11:16 | 50.029
2021-01-16 | 11:16 | 50.027
2021-01-16 | 11:16 | 50.03
2021-01-16 | 11:16 | 50.032
2021-01-16 | 11:16 | 50.033
2021-01-16 | 11:16 | 50.033
2021-01-16 | 11:16 | 50.033
2021-01-16 | 11:16 | 50.034
2021-01-16 | 11:16 | 50.033
2021-01-16 | 11:16 | 50.033
2021-01-16 | 11:16 | 50.034
2021-01-16 | 11:16 | 50.036
2021-01-16 | 11:16 | 50.033
2021-01-16 | 11:16 | 50.032
2021-01-16 | 11:16 | 50.027
2021-01-16 | 11:16 | 50.022
2021-01-16 | 11:16 | 50.019
2021-01-16 | 11:16 | 50.017
2021-01-16 | 11:16 | 50.015
2021-01-16 | 11:16 | 50.013
2021-01-16 | 11:16 | 50.014
2021-01-16 | 11:16 | 50.016
2021-01-16 | 11:16 | 50.019
2021-01-16 | 11:16 | 50.024
2021-01-16 | 11:16 | 50.023
2021-01-16 | 11:16 | 50.023
2021-01-16 | 11:16 | 50.026
2021-01-16 | 11:16 | 50.024
2021-01-16 | 11:16 | 50.023
2021-01-16 | 11:16 | 50.023
2021-01-16 | 11:16 | 50.022
2021-01-16 | 11:16 | 50.02
2021-01-16 | 11:16 | 50.019
2021-01-16 | 11:16 | 50.02
2021-01-16 | 11:16 | 50.02
2021-01-16 | 11:16 | 50.02
2021-01-16 | 11:16 | 50.021
2021-01-16 | 11:16 | 50.022
2021-01-16 | 11:16 | 50.023
2021-01-16 | 11:16 | 50.019
2021-01-16 | 11:16 | 50.02
2021-01-16 | 11:16 | 50.02
2021-01-16 | 11:16 | 50.019
2021-01-16 | 11:17 | 50.017
2021-01-16 | 11:17 | 50.017
2021-01-16 | 11:17 | 50.016
2021-01-16 | 11:17 | 50.017
2021-01-16 | 11:17 | 50.018
2021-01-16 | 11:17 | 50.019
2021-01-16 | 11:17 | 50.02
2021-01-16 | 11:17 | 50.022
2021-01-16 | 11:17 | 50.022
2021-01-16 | 11:17 | 50.026
2021-01-16 | 11:17 | 50.026
2021-01-16 | 11:17 | 50.024
2021-01-16 | 11:17 | 50.023
2021-01-16 | 11:17 | 50.021
2021-01-16 | 11:17 | 50.017
2021-01-16 | 11:17 | 50.015
2021-01-16 | 11:17 | 50.017
2021-01-16 | 11:17 | 50.017
2021-01-16 | 11:17 | 50.015
2021-01-16 | 11:17 | 50.017
2021-01-16 | 11:17 | 50.016
2021-01-16 | 11:17 | 50.019
2021-01-16 | 11:17 | 50.021
2021-01-16 | 11:17 | 50.025
2021-01-16 | 11:17 | 50.026
2021-01-16 | 11:17 | 50.027
2021-01-16 | 11:17 | 50.026
2021-01-16 | 11:17 | 50.024
2021-01-16 | 11:17 | 50.022
2021-01-16 | 11:17 | 50.021
2021-01-16 | 11:17 | 50.02
2021-01-16 | 11:17 | 50.02
2021-01-16 | 11:17 | 50.02
2021-01-16 | 11:17 | 50.019
2021-01-16 | 11:17 | 50.018
2021-01-16 | 11:17 | 50.018
2021-01-16 | 11:17 | 50.016
2021-01-16 | 11:17 | 50.016
2021-01-16 | 11:17 | 50.016
2021-01-16 | 11:17 | 50.015
2021-01-16 | 11:17 | 50.016
2021-01-16 | 11:17 | 50.015
2021-01-16 | 11:17 | 50.013
2021-01-16 | 11:17 | 50.008
2021-01-16 | 11:17 | 50.005
2021-01-16 | 11:17 | 50.005
2021-01-16 | 11:17 | 50.004
2021-01-16 | 11:17 | 50.003
2021-01-16 | 11:17 | 50.002
2021-01-16 | 11:17 | 50.002
2021-01-16 | 11:17 | 50.002
2021-01-16 | 11:17 | 50.003
2021-01-16 | 11:17 | 50.005
2021-01-16 | 11:17 | 50.005
2021-01-16 | 11:17 | 50.004
2021-01-16 | 11:17 | 50.005
2021-01-16 | 11:17 | 50.005
2021-01-16 | 11:17 | 50.01
2021-01-16 | 11:17 | 50.013
2021-01-16 | 11:18 | 50.016
2021-01-16 | 11:18 | 50.017
2021-01-16 | 11:18 | 50.019
2021-01-16 | 11:18 | 50.019
2021-01-16 | 11:18 | 50.02
2021-01-16 | 11:18 | 50.021
2021-01-16 | 11:18 | 50.021
2021-01-16 | 11:18 | 50.02
2021-01-16 | 11:18 | 50.024
2021-01-16 | 11:18 | 50.026
2021-01-16 | 11:18 | 50.029
2021-01-16 | 11:18 | 50.031
2021-01-16 | 11:18 | 50.034
2021-01-16 | 11:18 | 50.034
2021-01-16 | 11:18 | 50.038
2021-01-16 | 11:18 | 50.037
2021-01-16 | 11:18 | 50.038
2021-01-16 | 11:18 | 50.037
2021-01-16 | 11:18 | 50.036
2021-01-16 | 11:18 | 50.038
2021-01-16 | 11:18 | 50.038
2021-01-16 | 11:18 | 50.036
2021-01-16 | 11:18 | 50.037
2021-01-16 | 11:18 | 50.035
2021-01-16 | 11:18 | 50.036
2021-01-16 | 11:18 | 50.034
2021-01-16 | 11:18 | 50.034
2021-01-16 | 11:18 | 50.031
2021-01-16 | 11:18 | 50.03
2021-01-16 | 11:18 | 50.026
2021-01-16 | 11:18 | 50.024
2021-01-16 | 11:18 | 50.019
2021-01-16 | 11:18 | 50.016
2021-01-16 | 11:18 | 50.013
2021-01-16 | 11:18 | 50.012
2021-01-16 | 11:18 | 50.016
2021-01-16 | 11:18 | 50.016
2021-01-16 | 11:18 | 50.019
2021-01-16 | 11:18 | 50.019
2021-01-16 | 11:18 | 50.017
2021-01-16 | 11:18 | 50.015
2021-01-16 | 11:18 | 50.015
2021-01-16 | 11:18 | 50.017
2021-01-16 | 11:18 | 50.015
2021-01-16 | 11:18 | 50.013
2021-01-16 | 11:18 | 50.013
2021-01-16 | 11:18 | 50.01
2021-01-16 | 11:18 | 50.009
2021-01-16 | 11:18 | 50.009
2021-01-16 | 11:18 | 50.007
2021-01-16 | 11:18 | 50.008
2021-01-16 | 11:18 | 50.004
2021-01-16 | 11:18 | 50.001
2021-01-16 | 11:18 | 49.995
2021-01-16 | 11:18 | 49.994
2021-01-16 | 11:18 | 49.988
2021-01-16 | 11:18 | 49.982
2021-01-16 | 11:18 | 49.978
2021-01-16 | 11:18 | 49.976
2021-01-16 | 11:18 | 49.976
2021-01-16 | 11:18 | 49.976
2021-01-16 | 11:19 | 49.979
2021-01-16 | 11:19 | 49.977
2021-01-16 | 11:19 | 49.979
2021-01-16 | 11:19 | 49.98
2021-01-16 | 11:19 | 49.982
2021-01-16 | 11:19 | 49.983
2021-01-16 | 11:19 | 49.984
2021-01-16 | 11:19 | 49.985
2021-01-16 | 11:19 | 49.987
2021-01-16 | 11:19 | 49.987
2021-01-16 | 11:19 | 49.986
2021-01-16 | 11:19 | 49.985
2021-01-16 | 11:19 | 49.984
2021-01-16 | 11:19 | 49.983
2021-01-16 | 11:19 | 49.982
2021-01-16 | 11:19 | 49.981
2021-01-16 | 11:19 | 49.979
2021-01-16 | 11:19 | 49.979
2021-01-16 | 11:19 | 49.979
2021-01-16 | 11:19 | 49.979
2021-01-16 | 11:19 | 49.981
2021-01-16 | 11:19 | 49.985
2021-01-16 | 11:19 | 49.988
2021-01-16 | 11:19 | 49.989
2021-01-16 | 11:19 | 49.989
2021-01-16 | 11:19 | 49.988
2021-01-16 | 11:19 | 49.988
2021-01-16 | 11:19 | 49.985
2021-01-16 | 11:19 | 49.985
2021-01-16 | 11:19 | 49.982
2021-01-16 | 11:19 | 49.981
2021-01-16 | 11:19 | 49.98
2021-01-16 | 11:19 | 49.979
2021-01-16 | 11:19 | 49.978
2021-01-16 | 11:19 | 49.98
2021-01-16 | 11:19 | 49.98
2021-01-16 | 11:19 | 49.983
2021-01-16 | 11:19 | 49.986
2021-01-16 | 11:19 | 49.988
2021-01-16 | 11:19 | 49.989
2021-01-16 | 11:19 | 49.99
2021-01-16 | 11:19 | 49.988
2021-01-16 | 11:19 | 49.988
2021-01-16 | 11:19 | 49.982
2021-01-16 | 11:19 | 49.978
2021-01-16 | 11:19 | 49.974
2021-01-16 | 11:19 | 49.973
2021-01-16 | 11:19 | 49.973
2021-01-16 | 11:19 | 49.975
2021-01-16 | 11:19 | 49.976
2021-01-16 | 11:19 | 49.977
2021-01-16 | 11:19 | 49.979
2021-01-16 | 11:19 | 49.983
2021-01-16 | 11:19 | 49.988
2021-01-16 | 11:19 | 49.989
2021-01-16 | 11:19 | 49.988
2021-01-16 | 11:19 | 49.985
2021-01-16 | 11:19 | 49.985
2021-01-16 | 11:19 | 49.982
2021-01-16 | 11:20 | 49.979
2021-01-16 | 11:20 | 49.977
2021-01-16 | 11:20 | 49.973
2021-01-16 | 11:20 | 49.969
2021-01-16 | 11:20 | 49.964
2021-01-16 | 11:20 | 49.963
2021-01-16 | 11:20 | 49.962
2021-01-16 | 11:20 | 49.963
2021-01-16 | 11:20 | 49.963
2021-01-16 | 11:20 | 49.963
2021-01-16 | 11:20 | 49.965
2021-01-16 | 11:20 | 49.967
2021-01-16 | 11:20 | 49.969
2021-01-16 | 11:20 | 49.965
2021-01-16 | 11:20 | 49.965
2021-01-16 | 11:20 | 49.964
2021-01-16 | 11:20 | 49.965
2021-01-16 | 11:20 | 49.967
2021-01-16 | 11:20 | 49.968
2021-01-16 | 11:20 | 49.97
2021-01-16 | 11:20 | 49.972
2021-01-16 | 11:20 | 49.975
2021-01-16 | 11:20 | 49.973
2021-01-16 | 11:20 | 49.972
2021-01-16 | 11:20 | 49.973
2021-01-16 | 11:20 | 49.973
2021-01-16 | 11:20 | 49.973
2021-01-16 | 11:20 | 49.974
2021-01-16 | 11:20 | 49.974
2021-01-16 | 11:20 | 49.975
2021-01-16 | 11:20 | 49.974
2021-01-16 | 11:20 | 49.973
2021-01-16 | 11:20 | 49.971
2021-01-16 | 11:20 | 49.97
2021-01-16 | 11:20 | 49.967
2021-01-16 | 11:20 | 49.965
2021-01-16 | 11:20 | 49.965
2021-01-16 | 11:20 | 49.964
2021-01-16 | 11:20 | 49.967
2021-01-16 | 11:20 | 49.967
2021-01-16 | 11:20 | 49.966
2021-01-16 | 11:20 | 49.963
2021-01-16 | 11:20 | 49.962
2021-01-16 | 11:20 | 49.96
2021-01-16 | 11:20 | 49.96
2021-01-16 | 11:20 | 49.959
2021-01-16 | 11:20 | 49.958
2021-01-16 | 11:20 | 49.956
2021-01-16 | 11:20 | 49.954
2021-01-16 | 11:20 | 49.955
2021-01-16 | 11:20 | 49.954
2021-01-16 | 11:20 | 49.954
2021-01-16 | 11:20 | 49.952
2021-01-16 | 11:20 | 49.955
2021-01-16 | 11:20 | 49.957
2021-01-16 | 11:20 | 49.961
2021-01-16 | 11:20 | 49.964
2021-01-16 | 11:20 | 49.968
2021-01-16 | 11:20 | 49.966
2021-01-16 | 11:20 | 49.968
2021-01-16 | 11:20 | 49.968
2021-01-16 | 11:21 | 49.97
2021-01-16 | 11:21 | 49.97
2021-01-16 | 11:21 | 49.973
2021-01-16 | 11:21 | 49.975
2021-01-16 | 11:21 | 49.977
2021-01-16 | 11:21 | 49.979
2021-01-16 | 11:21 | 49.98
2021-01-16 | 11:21 | 49.98
2021-01-16 | 11:21 | 49.978
2021-01-16 | 11:21 | 49.978
2021-01-16 | 11:21 | 49.976
2021-01-16 | 11:21 | 49.978
2021-01-16 | 11:21 | 49.979
2021-01-16 | 11:21 | 49.982
2021-01-16 | 11:21 | 49.983
2021-01-16 | 11:21 | 49.982
2021-01-16 | 11:21 | 49.981
2021-01-16 | 11:21 | 49.978
2021-01-16 | 11:21 | 49.976
2021-01-16 | 11:21 | 49.975
2021-01-16 | 11:21 | 49.974
2021-01-16 | 11:21 | 49.976
2021-01-16 | 11:21 | 49.976
2021-01-16 | 11:21 | 49.98
2021-01-16 | 11:21 | 49.982
2021-01-16 | 11:21 | 49.986
2021-01-16 | 11:21 | 49.985
2021-01-16 | 11:21 | 49.982
2021-01-16 | 11:21 | 49.981
2021-01-16 | 11:21 | 49.98
2021-01-16 | 11:21 | 49.979
2021-01-16 | 11:21 | 49.977
2021-01-16 | 11:21 | 49.977
2021-01-16 | 11:21 | 49.974
2021-01-16 | 11:21 | 49.972
2021-01-16 | 11:21 | 49.97
2021-01-16 | 11:21 | 49.969
2021-01-16 | 11:21 | 49.968
2021-01-16 | 11:21 | 49.968
2021-01-16 | 11:21 | 49.967
2021-01-16 | 11:21 | 49.967
2021-01-16 | 11:21 | 49.966
2021-01-16 | 11:21 | 49.967
2021-01-16 | 11:21 | 49.967
2021-01-16 | 11:21 | 49.964
2021-01-16 | 11:21 | 49.961
2021-01-16 | 11:21 | 49.958
2021-01-16 | 11:21 | 49.954
2021-01-16 | 11:21 | 49.952
2021-01-16 | 11:21 | 49.948
2021-01-16 | 11:21 | 49.948
2021-01-16 | 11:21 | 49.946
2021-01-16 | 11:21 | 49.946
2021-01-16 | 11:21 | 49.945
2021-01-16 | 11:21 | 49.944
2021-01-16 | 11:21 | 49.945
2021-01-16 | 11:21 | 49.945
2021-01-16 | 11:21 | 49.944
2021-01-16 | 11:21 | 49.946
2021-01-16 | 11:22 | 49.946
2021-01-16 | 11:22 | 49.946
2021-01-16 | 11:22 | 49.948
2021-01-16 | 11:22 | 49.951
2021-01-16 | 11:22 | 49.953
2021-01-16 | 11:22 | 49.954
2021-01-16 | 11:22 | 49.957
2021-01-16 | 11:22 | 49.956
2021-01-16 | 11:22 | 49.955
2021-01-16 | 11:22 | 49.957
2021-01-16 | 11:22 | 49.956
2021-01-16 | 11:22 | 49.955
2021-01-16 | 11:22 | 49.957
2021-01-16 | 11:22 | 49.958
2021-01-16 | 11:22 | 49.96
2021-01-16 | 11:22 | 49.96
2021-01-16 | 11:22 | 49.961
2021-01-16 | 11:22 | 49.961
2021-01-16 | 11:22 | 49.962
2021-01-16 | 11:22 | 49.961
2021-01-16 | 11:22 | 49.962
2021-01-16 | 11:22 | 49.963
2021-01-16 | 11:22 | 49.963
2021-01-16 | 11:22 | 49.962
2021-01-16 | 11:22 | 49.959
2021-01-16 | 11:22 | 49.959
2021-01-16 | 11:22 | 49.959
2021-01-16 | 11:22 | 49.962
2021-01-16 | 11:22 | 49.963
2021-01-16 | 11:22 | 49.966
2021-01-16 | 11:22 | 49.968
2021-01-16 | 11:22 | 49.971
2021-01-16 | 11:22 | 49.971
2021-01-16 | 11:22 | 49.973
2021-01-16 | 11:22 | 49.972
2021-01-16 | 11:22 | 49.97
2021-01-16 | 11:22 | 49.969
2021-01-16 | 11:22 | 49.97
2021-01-16 | 11:22 | 49.969
2021-01-16 | 11:22 | 49.969
2021-01-16 | 11:22 | 49.969
2021-01-16 | 11:22 | 49.97
2021-01-16 | 11:22 | 49.969
2021-01-16 | 11:22 | 49.97
2021-01-16 | 11:22 | 49.97
2021-01-16 | 11:22 | 49.971
2021-01-16 | 11:22 | 49.97
2021-01-16 | 11:22 | 49.968
2021-01-16 | 11:22 | 49.968
2021-01-16 | 11:22 | 49.969
2021-01-16 | 11:22 | 49.972
2021-01-16 | 11:22 | 49.972
2021-01-16 | 11:22 | 49.974
2021-01-16 | 11:22 | 49.97
2021-01-16 | 11:22 | 49.97
2021-01-16 | 11:22 | 49.968
2021-01-16 | 11:22 | 49.967
2021-01-16 | 11:22 | 49.965
2021-01-16 | 11:22 | 49.963
2021-01-16 | 11:22 | 49.96
2021-01-16 | 11:22 | 49.958
2021-01-16 | 11:23 | 49.958
2021-01-16 | 11:23 | 49.959
2021-01-16 | 11:23 | 49.962
2021-01-16 | 11:23 | 49.964
2021-01-16 | 11:23 | 49.965
2021-01-16 | 11:23 | 49.966
2021-01-16 | 11:23 | 49.969
2021-01-16 | 11:23 | 49.971
2021-01-16 | 11:23 | 49.973
2021-01-16 | 11:23 | 49.975
2021-01-16 | 11:23 | 49.977
2021-01-16 | 11:23 | 49.977
2021-01-16 | 11:23 | 49.979
2021-01-16 | 11:23 | 49.982
2021-01-16 | 11:23 | 49.983
2021-01-16 | 11:23 | 49.984
2021-01-16 | 11:23 | 49.984
2021-01-16 | 11:23 | 49.984
2021-01-16 | 11:23 | 49.984
2021-01-16 | 11:23 | 49.985
2021-01-16 | 11:23 | 49.986
2021-01-16 | 11:23 | 49.988
2021-01-16 | 11:23 | 49.985
2021-01-16 | 11:23 | 49.987
2021-01-16 | 11:23 | 49.986
2021-01-16 | 11:23 | 49.984
2021-01-16 | 11:23 | 49.981
2021-01-16 | 11:23 | 49.982
2021-01-16 | 11:23 | 49.98
2021-01-16 | 11:23 | 49.977
2021-01-16 | 11:23 | 49.975
2021-01-16 | 11:23 | 49.972
2021-01-16 | 11:23 | 49.971
2021-01-16 | 11:23 | 49.97
2021-01-16 | 11:23 | 49.968
2021-01-16 | 11:23 | 49.967
2021-01-16 | 11:23 | 49.969
2021-01-16 | 11:23 | 49.968
2021-01-16 | 11:23 | 49.97
2021-01-16 | 11:23 | 49.97
2021-01-16 | 11:23 | 49.97
2021-01-16 | 11:23 | 49.972
2021-01-16 | 11:23 | 49.972
2021-01-16 | 11:23 | 49.972
2021-01-16 | 11:23 | 49.973
2021-01-16 | 11:23 | 49.98
2021-01-16 | 11:23 | 49.986
2021-01-16 | 11:23 | 49.989
2021-01-16 | 11:23 | 49.992
2021-01-16 | 11:23 | 49.992
2021-01-16 | 11:23 | 49.992
2021-01-16 | 11:23 | 49.992
2021-01-16 | 11:23 | 49.988
2021-01-16 | 11:23 | 49.986
2021-01-16 | 11:23 | 49.984
2021-01-16 | 11:23 | 49.98
2021-01-16 | 11:23 | 49.98
2021-01-16 | 11:23 | 49.981
2021-01-16 | 11:23 | 49.982
2021-01-16 | 11:24 | 49.983
2021-01-16 | 11:24 | 49.982
2021-01-16 | 11:24 | 49.982
2021-01-16 | 11:24 | 49.979
2021-01-16 | 11:24 | 49.976
2021-01-16 | 11:24 | 49.974
2021-01-16 | 11:24 | 49.975
2021-01-16 | 11:24 | 49.97
2021-01-16 | 11:24 | 49.97
2021-01-16 | 11:24 | 49.968
2021-01-16 | 11:24 | 49.969
2021-01-16 | 11:24 | 49.968
2021-01-16 | 11:24 | 49.971
2021-01-16 | 11:24 | 49.975
2021-01-16 | 11:24 | 49.979
2021-01-16 | 11:24 | 49.985
2021-01-16 | 11:24 | 49.987
2021-01-16 | 11:24 | 49.99
2021-01-16 | 11:24 | 49.989
2021-01-16 | 11:24 | 49.989
2021-01-16 | 11:24 | 49.987
2021-01-16 | 11:24 | 49.985
2021-01-16 | 11:24 | 49.98
2021-01-16 | 11:24 | 49.977
2021-01-16 | 11:24 | 49.977
2021-01-16 | 11:24 | 49.976
2021-01-16 | 11:24 | 49.977
2021-01-16 | 11:24 | 49.976
2021-01-16 | 11:24 | 49.976
2021-01-16 | 11:24 | 49.974
2021-01-16 | 11:24 | 49.974
2021-01-16 | 11:24 | 49.972
2021-01-16 | 11:24 | 49.97
2021-01-16 | 11:24 | 49.972
2021-01-16 | 11:24 | 49.974
2021-01-16 | 11:24 | 49.978
2021-01-16 | 11:24 | 49.983
2021-01-16 | 11:24 | 49.986
2021-01-16 | 11:24 | 49.986
2021-01-16 | 11:24 | 49.983
2021-01-16 | 11:24 | 49.981
2021-01-16 | 11:24 | 49.98
2021-01-16 | 11:24 | 49.981
2021-01-16 | 11:24 | 49.982
2021-01-16 | 11:24 | 49.984
2021-01-16 | 11:24 | 49.986
2021-01-16 | 11:24 | 49.987
2021-01-16 | 11:24 | 49.987
2021-01-16 | 11:24 | 49.988
2021-01-16 | 11:24 | 49.991
2021-01-16 | 11:24 | 49.994
2021-01-16 | 11:24 | 49.997
2021-01-16 | 11:24 | 50.002
2021-01-16 | 11:24 | 50.003
2021-01-16 | 11:24 | 50.003
2021-01-16 | 11:24 | 50.006
2021-01-16 | 11:24 | 50.006
2021-01-16 | 11:24 | 50.009
2021-01-16 | 11:24 | 50.009
2021-01-16 | 11:24 | 50.01
2021-01-16 | 11:24 | 50.013
2021-01-16 | 11:25 | 50.013
2021-01-16 | 11:25 | 50.014
2021-01-16 | 11:25 | 50.013
2021-01-16 | 11:25 | 50.012
2021-01-16 | 11:25 | 50.012
2021-01-16 | 11:25 | 50.011
2021-01-16 | 11:25 | 50.013
2021-01-16 | 11:25 | 50.014
2021-01-16 | 11:25 | 50.013
2021-01-16 | 11:25 | 50.013
2021-01-16 | 11:25 | 50.015
2021-01-16 | 11:25 | 50.015
2021-01-16 | 11:25 | 50.019
2021-01-16 | 11:25 | 50.018
2021-01-16 | 11:25 | 50.02
2021-01-16 | 11:25 | 50.02
2021-01-16 | 11:25 | 50.02
2021-01-16 | 11:25 | 50.019
2021-01-16 | 11:25 | 50.017
2021-01-16 | 11:25 | 50.014
2021-01-16 | 11:25 | 50.011
2021-01-16 | 11:25 | 50.006
2021-01-16 | 11:25 | 50.004
2021-01-16 | 11:25 | 50.003
2021-01-16 | 11:25 | 50.002
2021-01-16 | 11:25 | 49.999
2021-01-16 | 11:25 | 49.998
2021-01-16 | 11:25 | 49.997
2021-01-16 | 11:25 | 49.995
2021-01-16 | 11:25 | 49.993
2021-01-16 | 11:25 | 49.991
2021-01-16 | 11:25 | 49.987
2021-01-16 | 11:25 | 49.982
2021-01-16 | 11:25 | 49.981
2021-01-16 | 11:25 | 49.978
2021-01-16 | 11:25 | 49.977
2021-01-16 | 11:25 | 49.979
2021-01-16 | 11:25 | 49.979
2021-01-16 | 11:25 | 49.978
2021-01-16 | 11:25 | 49.977
2021-01-16 | 11:25 | 49.975
2021-01-16 | 11:25 | 49.976
2021-01-16 | 11:25 | 49.974
2021-01-16 | 11:25 | 49.973
2021-01-16 | 11:25 | 49.973
2021-01-16 | 11:25 | 49.972
2021-01-16 | 11:25 | 49.97
2021-01-16 | 11:25 | 49.969
2021-01-16 | 11:25 | 49.97
2021-01-16 | 11:25 | 49.971
2021-01-16 | 11:25 | 49.972
2021-01-16 | 11:25 | 49.975
2021-01-16 | 11:25 | 49.975
2021-01-16 | 11:25 | 49.978
2021-01-16 | 11:25 | 49.977
2021-01-16 | 11:25 | 49.976
2021-01-16 | 11:25 | 49.978
2021-01-16 | 11:25 | 49.976
2021-01-16 | 11:25 | 49.979
2021-01-16 | 11:26 | 49.975
2021-01-16 | 11:26 | 49.976
2021-01-16 | 11:26 | 49.974
2021-01-16 | 11:26 | 49.973
2021-01-16 | 11:26 | 49.973
2021-01-16 | 11:26 | 49.973
2021-01-16 | 11:26 | 49.973
2021-01-16 | 11:26 | 49.975
2021-01-16 | 11:26 | 49.978
2021-01-16 | 11:26 | 49.978
2021-01-16 | 11:26 | 49.978
2021-01-16 | 11:26 | 49.976
2021-01-16 | 11:26 | 49.976
2021-01-16 | 11:26 | 49.977
2021-01-16 | 11:26 | 49.979
2021-01-16 | 11:26 | 49.977
2021-01-16 | 11:26 | 49.979
2021-01-16 | 11:26 | 49.98
2021-01-16 | 11:26 | 49.981
2021-01-16 | 11:26 | 49.981
2021-01-16 | 11:26 | 49.982
2021-01-16 | 11:26 | 49.984
2021-01-16 | 11:26 | 49.988
2021-01-16 | 11:26 | 49.989
2021-01-16 | 11:26 | 49.992
2021-01-16 | 11:26 | 49.996
2021-01-16 | 11:26 | 49.996
2021-01-16 | 11:26 | 49.998
2021-01-16 | 11:26 | 49.999
2021-01-16 | 11:26 | 50.002
2021-01-16 | 11:26 | 50.004
2021-01-16 | 11:26 | 50.005
2021-01-16 | 11:26 | 50.008
2021-01-16 | 11:26 | 50.011
2021-01-16 | 11:26 | 50.015
2021-01-16 | 11:26 | 50.018
2021-01-16 | 11:26 | 50.02
2021-01-16 | 11:26 | 50.02
2021-01-16 | 11:26 | 50.018
2021-01-16 | 11:26 | 50.02
2021-01-16 | 11:26 | 50.02
2021-01-16 | 11:26 | 50.019
2021-01-16 | 11:26 | 50.02
2021-01-16 | 11:26 | 50.019
2021-01-16 | 11:26 | 50.02
2021-01-16 | 11:26 | 50.022
2021-01-16 | 11:26 | 50.023
2021-01-16 | 11:26 | 50.026
2021-01-16 | 11:26 | 50.025
2021-01-16 | 11:26 | 50.028
2021-01-16 | 11:26 | 50.029
2021-01-16 | 11:26 | 50.03
2021-01-16 | 11:26 | 50.032
2021-01-16 | 11:26 | 50.032
2021-01-16 | 11:26 | 50.034
2021-01-16 | 11:26 | 50.034
2021-01-16 | 11:26 | 50.032
2021-01-16 | 11:26 | 50.031
2021-01-16 | 11:26 | 50.03
2021-01-16 | 11:26 | 50.03
2021-01-16 | 11:26 | 50.029
2021-01-16 | 11:27 | 50.026
2021-01-16 | 11:27 | 50.026
2021-01-16 | 11:27 | 50.024
2021-01-16 | 11:27 | 50.024
2021-01-16 | 11:27 | 50.022
2021-01-16 | 11:27 | 50.022
2021-01-16 | 11:27 | 50.023
2021-01-16 | 11:27 | 50.024
2021-01-16 | 11:27 | 50.026
2021-01-16 | 11:27 | 50.028
2021-01-16 | 11:27 | 50.028
2021-01-16 | 11:27 | 50.03
2021-01-16 | 11:27 | 50.031
2021-01-16 | 11:27 | 50.03
2021-01-16 | 11:27 | 50.03
2021-01-16 | 11:27 | 50.029
2021-01-16 | 11:27 | 50.026
2021-01-16 | 11:27 | 50.028
2021-01-16 | 11:27 | 50.029
2021-01-16 | 11:27 | 50.03
2021-01-16 | 11:27 | 50.03
2021-01-16 | 11:27 | 50.028
2021-01-16 | 11:27 | 50.025
2021-01-16 | 11:27 | 50.023
2021-01-16 | 11:27 | 50.017
2021-01-16 | 11:27 | 50.014
2021-01-16 | 11:27 | 50.01
2021-01-16 | 11:27 | 50.007
2021-01-16 | 11:27 | 50.007
2021-01-16 | 11:27 | 50.008
2021-01-16 | 11:27 | 50.006
2021-01-16 | 11:27 | 50.003
2021-01-16 | 11:27 | 50.002
2021-01-16 | 11:27 | 50.002
2021-01-16 | 11:27 | 50.005
2021-01-16 | 11:27 | 50.004
2021-01-16 | 11:27 | 50.003
2021-01-16 | 11:27 | 50.006
2021-01-16 | 11:27 | 50.006
2021-01-16 | 11:27 | 50.007
2021-01-16 | 11:27 | 50.005
2021-01-16 | 11:27 | 49.999
2021-01-16 | 11:27 | 49.993
2021-01-16 | 11:27 | 49.988
2021-01-16 | 11:27 | 49.986
2021-01-16 | 11:27 | 49.985
2021-01-16 | 11:27 | 49.984
2021-01-16 | 11:27 | 49.985
2021-01-16 | 11:27 | 49.985
2021-01-16 | 11:27 | 49.985
2021-01-16 | 11:27 | 49.983
2021-01-16 | 11:27 | 49.982
2021-01-16 | 11:27 | 49.983
2021-01-16 | 11:27 | 49.984
2021-01-16 | 11:27 | 49.986
2021-01-16 | 11:27 | 49.99
2021-01-16 | 11:27 | 49.994
2021-01-16 | 11:27 | 49.998
2021-01-16 | 11:27 | 50.002
2021-01-16 | 11:28 | 50.004
2021-01-16 | 11:28 | 50.009
2021-01-16 | 11:28 | 50.014
2021-01-16 | 11:28 | 50.02
2021-01-16 | 11:28 | 50.023
2021-01-16 | 11:28 | 50.025
2021-01-16 | 11:28 | 50.025
2021-01-16 | 11:28 | 50.025
2021-01-16 | 11:28 | 50.024
2021-01-16 | 11:28 | 50.021
2021-01-16 | 11:28 | 50.02
2021-01-16 | 11:28 | 50.019
2021-01-16 | 11:28 | 50.022
2021-01-16 | 11:28 | 50.025
2021-01-16 | 11:28 | 50.028
2021-01-16 | 11:28 | 50.028
2021-01-16 | 11:28 | 50.029
2021-01-16 | 11:28 | 50.029
2021-01-16 | 11:28 | 50.028
2021-01-16 | 11:28 | 50.029
2021-01-16 | 11:28 | 50.027
2021-01-16 | 11:28 | 50.028
2021-01-16 | 11:28 | 50.026
2021-01-16 | 11:28 | 50.027
2021-01-16 | 11:28 | 50.024
2021-01-16 | 11:28 | 50.022
2021-01-16 | 11:28 | 50.02
2021-01-16 | 11:28 | 50.017
2021-01-16 | 11:28 | 50.015
2021-01-16 | 11:28 | 50.014
2021-01-16 | 11:28 | 50.017
2021-01-16 | 11:28 | 50.014
2021-01-16 | 11:28 | 50.015
2021-01-16 | 11:28 | 50.015
2021-01-16 | 11:28 | 50.015
2021-01-16 | 11:28 | 50.016
2021-01-16 | 11:28 | 50.017
2021-01-16 | 11:28 | 50.017
2021-01-16 | 11:28 | 50.018
2021-01-16 | 11:28 | 50.019
2021-01-16 | 11:28 | 50.019
2021-01-16 | 11:28 | 50.02
2021-01-16 | 11:28 | 50.023
2021-01-16 | 11:28 | 50.023
2021-01-16 | 11:28 | 50.026
2021-01-16 | 11:28 | 50.025
2021-01-16 | 11:28 | 50.026
2021-01-16 | 11:28 | 50.022
2021-01-16 | 11:28 | 50.023
2021-01-16 | 11:28 | 50.02
2021-01-16 | 11:28 | 50.021
2021-01-16 | 11:28 | 50.019
2021-01-16 | 11:28 | 50.018
2021-01-16 | 11:28 | 50.014
2021-01-16 | 11:28 | 50.014
2021-01-16 | 11:28 | 50.013
2021-01-16 | 11:28 | 50.01
2021-01-16 | 11:28 | 50.011
2021-01-16 | 11:28 | 50.013
2021-01-16 | 11:28 | 50.016
2021-01-16 | 11:28 | 50.016
2021-01-16 | 11:29 | 50.017
2021-01-16 | 11:29 | 50.018
2021-01-16 | 11:29 | 50.02
2021-01-16 | 11:29 | 50.021
2021-01-16 | 11:29 | 50.021
2021-01-16 | 11:29 | 50.017
2021-01-16 | 11:29 | 50.017
2021-01-16 | 11:29 | 50.018
2021-01-16 | 11:29 | 50.018
2021-01-16 | 11:29 | 50.019
2021-01-16 | 11:29 | 50.019
2021-01-16 | 11:29 | 50.02
2021-01-16 | 11:29 | 50.021
2021-01-16 | 11:29 | 50.021
2021-01-16 | 11:29 | 50.022
2021-01-16 | 11:29 | 50.021
2021-01-16 | 11:29 | 50.023
2021-01-16 | 11:29 | 50.024
2021-01-16 | 11:29 | 50.025
2021-01-16 | 11:29 | 50.024
2021-01-16 | 11:29 | 50.02
2021-01-16 | 11:29 | 50.016
2021-01-16 | 11:29 | 50.012
2021-01-16 | 11:29 | 50.012
2021-01-16 | 11:29 | 50.013
2021-01-16 | 11:29 | 50.014
2021-01-16 | 11:29 | 50.016
2021-01-16 | 11:29 | 50.018
2021-01-16 | 11:29 | 50.022
2021-01-16 | 11:29 | 50.024
2021-01-16 | 11:29 | 50.023
2021-01-16 | 11:29 | 50.024
2021-01-16 | 11:29 | 50.025
2021-01-16 | 11:29 | 50.025
2021-01-16 | 11:29 | 50.023
2021-01-16 | 11:29 | 50.02
2021-01-16 | 11:29 | 50.019
2021-01-16 | 11:29 | 50.018
2021-01-16 | 11:29 | 50.016
2021-01-16 | 11:29 | 50.017
2021-01-16 | 11:29 | 50.019
2021-01-16 | 11:29 | 50.021
2021-01-16 | 11:29 | 50.022
2021-01-16 | 11:29 | 50.026
2021-01-16 | 11:29 | 50.027
2021-01-16 | 11:29 | 50.028
2021-01-16 | 11:29 | 50.029
2021-01-16 | 11:29 | 50.03
2021-01-16 | 11:29 | 50.03
2021-01-16 | 11:29 | 50.033
2021-01-16 | 11:29 | 50.035
2021-01-16 | 11:29 | 50.035
2021-01-16 | 11:29 | 50.036
2021-01-16 | 11:29 | 50.038
2021-01-16 | 11:29 | 50.04
2021-01-16 | 11:29 | 50.04
2021-01-16 | 11:29 | 50.041
2021-01-16 | 11:29 | 50.043
2021-01-16 | 11:29 | 50.044
2021-01-16 | 11:30 | 50.044
2021-01-16 | 11:30 | 50.046
2021-01-16 | 11:30 | 50.045
2021-01-16 | 11:30 | 50.044
2021-01-16 | 11:30 | 50.042
2021-01-16 | 11:30 | 50.037
2021-01-16 | 11:30 | 50.03
2021-01-16 | 11:30 | 50.024
2021-01-16 | 11:30 | 50.023
2021-01-16 | 11:30 | 50.022
2021-01-16 | 11:30 | 50.02
2021-01-16 | 11:30 | 50.02
2021-01-16 | 11:30 | 50.021
2021-01-16 | 11:30 | 50.021
2021-01-16 | 11:30 | 50.021
2021-01-16 | 11:30 | 50.02
2021-01-16 | 11:30 | 50.016
2021-01-16 | 11:30 | 50.015
2021-01-16 | 11:30 | 50.014
2021-01-16 | 11:30 | 50.012
2021-01-16 | 11:30 | 50.012
2021-01-16 | 11:30 | 50.011
2021-01-16 | 11:30 | 50.01
2021-01-16 | 11:30 | 50.011
2021-01-16 | 11:30 | 50.009
2021-01-16 | 11:30 | 50.008
2021-01-16 | 11:30 | 50.007
2021-01-16 | 11:30 | 50.003
2021-01-16 | 11:30 | 50.004
2021-01-16 | 11:30 | 50.005
2021-01-16 | 11:30 | 50.006
2021-01-16 | 11:30 | 50.005
2021-01-16 | 11:30 | 50
2021-01-16 | 11:30 | 49.999
2021-01-16 | 11:30 | 49.997
2021-01-16 | 11:30 | 49.996
2021-01-16 | 11:30 | 49.996
2021-01-16 | 11:30 | 49.997
2021-01-16 | 11:30 | 49.997
2021-01-16 | 11:30 | 49.997
2021-01-16 | 11:30 | 49.998
2021-01-16 | 11:30 | 49.997
2021-01-16 | 11:30 | 49.999
2021-01-16 | 11:30 | 49.995
2021-01-16 | 11:30 | 49.996
2021-01-16 | 11:30 | 49.994
2021-01-16 | 11:30 | 49.994
2021-01-16 | 11:30 | 49.992
2021-01-16 | 11:30 | 49.991
2021-01-16 | 11:30 | 49.989
2021-01-16 | 11:30 | 49.986
2021-01-16 | 11:30 | 49.985
2021-01-16 | 11:30 | 49.981
2021-01-16 | 11:30 | 49.979
2021-01-16 | 11:30 | 49.976
2021-01-16 | 11:30 | 49.977
2021-01-16 | 11:30 | 49.976
2021-01-16 | 11:30 | 49.975
2021-01-16 | 11:30 | 49.976
2021-01-16 | 11:30 | 49.977
2021-01-16 | 11:30 | 49.975
2021-01-16 | 11:31 | 49.977
2021-01-16 | 11:31 | 49.976
2021-01-16 | 11:31 | 49.979
2021-01-16 | 11:31 | 49.978
2021-01-16 | 11:31 | 49.978
2021-01-16 | 11:31 | 49.977
2021-01-16 | 11:31 | 49.977
2021-01-16 | 11:31 | 49.977
2021-01-16 | 11:31 | 49.978
2021-01-16 | 11:31 | 49.978
2021-01-16 | 11:31 | 49.978
2021-01-16 | 11:31 | 49.979
2021-01-16 | 11:31 | 49.98
2021-01-16 | 11:31 | 49.979
2021-01-16 | 11:31 | 49.979
2021-01-16 | 11:31 | 49.977
2021-01-16 | 11:31 | 49.978
2021-01-16 | 11:31 | 49.978
2021-01-16 | 11:31 | 49.977
2021-01-16 | 11:31 | 49.975
2021-01-16 | 11:31 | 49.974
2021-01-16 | 11:31 | 49.972
2021-01-16 | 11:31 | 49.97
2021-01-16 | 11:31 | 49.967
2021-01-16 | 11:31 | 49.965
2021-01-16 | 11:31 | 49.962
2021-01-16 | 11:31 | 49.96
2021-01-16 | 11:31 | 49.959
2021-01-16 | 11:31 | 49.956
2021-01-16 | 11:31 | 49.953
2021-01-16 | 11:31 | 49.951
2021-01-16 | 11:31 | 49.948
2021-01-16 | 11:31 | 49.949
2021-01-16 | 11:31 | 49.949
2021-01-16 | 11:31 | 49.95
2021-01-16 | 11:31 | 49.95
2021-01-16 | 11:31 | 49.949
2021-01-16 | 11:31 | 49.947
2021-01-16 | 11:31 | 49.944
2021-01-16 | 11:31 | 49.943
2021-01-16 | 11:31 | 49.943
2021-01-16 | 11:31 | 49.945
2021-01-16 | 11:31 | 49.947
2021-01-16 | 11:31 | 49.946
2021-01-16 | 11:31 | 49.945
2021-01-16 | 11:31 | 49.942
2021-01-16 | 11:31 | 49.942
2021-01-16 | 11:31 | 49.94
2021-01-16 | 11:31 | 49.937
2021-01-16 | 11:31 | 49.936
2021-01-16 | 11:31 | 49.933
2021-01-16 | 11:31 | 49.935
2021-01-16 | 11:31 | 49.94
2021-01-16 | 11:31 | 49.948
2021-01-16 | 11:31 | 49.95
2021-01-16 | 11:31 | 49.951
2021-01-16 | 11:31 | 49.949
2021-01-16 | 11:31 | 49.949
2021-01-16 | 11:31 | 49.948
2021-01-16 | 11:32 | 49.947
2021-01-16 | 11:32 | 49.944
2021-01-16 | 11:32 | 49.94
2021-01-16 | 11:32 | 49.941
2021-01-16 | 11:32 | 49.94
2021-01-16 | 11:32 | 49.942
2021-01-16 | 11:32 | 49.941
2021-01-16 | 11:32 | 49.944
2021-01-16 | 11:32 | 49.946
2021-01-16 | 11:32 | 49.948
2021-01-16 | 11:32 | 49.95
2021-01-16 | 11:32 | 49.949
2021-01-16 | 11:32 | 49.949
2021-01-16 | 11:32 | 49.946
2021-01-16 | 11:32 | 49.948
2021-01-16 | 11:32 | 49.946
2021-01-16 | 11:32 | 49.946
2021-01-16 | 11:32 | 49.945
2021-01-16 | 11:32 | 49.945
2021-01-16 | 11:32 | 49.942
2021-01-16 | 11:32 | 49.942
2021-01-16 | 11:32 | 49.945
2021-01-16 | 11:32 | 49.945
2021-01-16 | 11:32 | 49.946
2021-01-16 | 11:32 | 49.944
2021-01-16 | 11:32 | 49.943
2021-01-16 | 11:32 | 49.942
2021-01-16 | 11:32 | 49.942
2021-01-16 | 11:32 | 49.941
2021-01-16 | 11:32 | 49.938
2021-01-16 | 11:32 | 49.935
2021-01-16 | 11:32 | 49.932
2021-01-16 | 11:32 | 49.93
2021-01-16 | 11:32 | 49.929
2021-01-16 | 11:32 | 49.928
2021-01-16 | 11:32 | 49.928
2021-01-16 | 11:32 | 49.929
2021-01-16 | 11:32 | 49.93
2021-01-16 | 11:32 | 49.93
2021-01-16 | 11:32 | 49.931
2021-01-16 | 11:32 | 49.932
2021-01-16 | 11:32 | 49.935
2021-01-16 | 11:32 | 49.934
2021-01-16 | 11:32 | 49.935
2021-01-16 | 11:32 | 49.934
2021-01-16 | 11:32 | 49.933
2021-01-16 | 11:32 | 49.932
2021-01-16 | 11:32 | 49.934
2021-01-16 | 11:32 | 49.934
2021-01-16 | 11:32 | 49.935
2021-01-16 | 11:32 | 49.935
2021-01-16 | 11:32 | 49.933
2021-01-16 | 11:32 | 49.933
2021-01-16 | 11:32 | 49.932
2021-01-16 | 11:32 | 49.934
2021-01-16 | 11:32 | 49.933
2021-01-16 | 11:32 | 49.933
2021-01-16 | 11:32 | 49.933
2021-01-16 | 11:32 | 49.932
2021-01-16 | 11:32 | 49.932
2021-01-16 | 11:32 | 49.934
2021-01-16 | 11:33 | 49.935
2021-01-16 | 11:33 | 49.935
2021-01-16 | 11:33 | 49.935
2021-01-16 | 11:33 | 49.934
2021-01-16 | 11:33 | 49.934
2021-01-16 | 11:33 | 49.934
2021-01-16 | 11:33 | 49.934
2021-01-16 | 11:33 | 49.933
2021-01-16 | 11:33 | 49.935
2021-01-16 | 11:33 | 49.933
2021-01-16 | 11:33 | 49.932
2021-01-16 | 11:33 | 49.932
2021-01-16 | 11:33 | 49.929
2021-01-16 | 11:33 | 49.927
2021-01-16 | 11:33 | 49.925
2021-01-16 | 11:33 | 49.924
2021-01-16 | 11:33 | 49.924
2021-01-16 | 11:33 | 49.921
2021-01-16 | 11:33 | 49.919
2021-01-16 | 11:33 | 49.92
2021-01-16 | 11:33 | 49.917
2021-01-16 | 11:33 | 49.915
2021-01-16 | 11:33 | 49.918
2021-01-16 | 11:33 | 49.916
2021-01-16 | 11:33 | 49.916
2021-01-16 | 11:33 | 49.914
2021-01-16 | 11:33 | 49.914
2021-01-16 | 11:33 | 49.912
2021-01-16 | 11:33 | 49.911
2021-01-16 | 11:33 | 49.912
2021-01-16 | 11:33 | 49.909
2021-01-16 | 11:33 | 49.908
2021-01-16 | 11:33 | 49.906
2021-01-16 | 11:33 | 49.905
2021-01-16 | 11:33 | 49.905
2021-01-16 | 11:33 | 49.904
2021-01-16 | 11:33 | 49.903
2021-01-16 | 11:33 | 49.902
2021-01-16 | 11:33 | 49.901
2021-01-16 | 11:33 | 49.901
2021-01-16 | 11:33 | 49.9
2021-01-16 | 11:33 | 49.9
2021-01-16 | 11:33 | 49.899
2021-01-16 | 11:33 | 49.902
2021-01-16 | 11:33 | 49.899
2021-01-16 | 11:33 | 49.898
2021-01-16 | 11:33 | 49.896
2021-01-16 | 11:33 | 49.893
2021-01-16 | 11:33 | 49.895
2021-01-16 | 11:33 | 49.89
2021-01-16 | 11:33 | 49.887
2021-01-16 | 11:33 | 49.887
2021-01-16 | 11:33 | 49.886
2021-01-16 | 11:33 | 49.89
2021-01-16 | 11:33 | 49.891
2021-01-16 | 11:33 | 49.891
2021-01-16 | 11:33 | 49.892
2021-01-16 | 11:33 | 49.895
2021-01-16 | 11:33 | 49.897
2021-01-16 | 11:34 | 49.897
2021-01-16 | 11:34 | 49.898
2021-01-16 | 11:34 | 49.899
2021-01-16 | 11:34 | 49.898
2021-01-16 | 11:34 | 49.898
2021-01-16 | 11:34 | 49.897
2021-01-16 | 11:34 | 49.898
2021-01-16 | 11:34 | 49.898
2021-01-16 | 11:34 | 49.894
2021-01-16 | 11:34 | 49.894
2021-01-16 | 11:34 | 49.893
2021-01-16 | 11:34 | 49.894
2021-01-16 | 11:34 | 49.895
2021-01-16 | 11:34 | 49.897
2021-01-16 | 11:34 | 49.897
2021-01-16 | 11:34 | 49.897
2021-01-16 | 11:34 | 49.896
2021-01-16 | 11:34 | 49.895
2021-01-16 | 11:34 | 49.897
2021-01-16 | 11:34 | 49.899
2021-01-16 | 11:34 | 49.9
2021-01-16 | 11:34 | 49.9
2021-01-16 | 11:34 | 49.897
2021-01-16 | 11:34 | 49.9
2021-01-16 | 11:34 | 49.902
2021-01-16 | 11:34 | 49.904
2021-01-16 | 11:34 | 49.907
2021-01-16 | 11:34 | 49.907
2021-01-16 | 11:34 | 49.91
2021-01-16 | 11:34 | 49.91
2021-01-16 | 11:34 | 49.908
2021-01-16 | 11:34 | 49.908
2021-01-16 | 11:34 | 49.906
2021-01-16 | 11:34 | 49.904
2021-01-16 | 11:34 | 49.901
2021-01-16 | 11:34 | 49.9
2021-01-16 | 11:34 | 49.9
2021-01-16 | 11:34 | 49.897
2021-01-16 | 11:34 | 49.9
2021-01-16 | 11:34 | 49.903
2021-01-16 | 11:34 | 49.903
2021-01-16 | 11:34 | 49.906
2021-01-16 | 11:34 | 49.905
2021-01-16 | 11:34 | 49.904
2021-01-16 | 11:34 | 49.902
2021-01-16 | 11:34 | 49.903
2021-01-16 | 11:34 | 49.906
2021-01-16 | 11:34 | 49.904
2021-01-16 | 11:34 | 49.902
2021-01-16 | 11:34 | 49.903
2021-01-16 | 11:34 | 49.901
2021-01-16 | 11:34 | 49.901
2021-01-16 | 11:34 | 49.904
2021-01-16 | 11:34 | 49.906
2021-01-16 | 11:34 | 49.908
2021-01-16 | 11:34 | 49.908
2021-01-16 | 11:34 | 49.908
2021-01-16 | 11:34 | 49.911
2021-01-16 | 11:34 | 49.913
2021-01-16 | 11:34 | 49.913
2021-01-16 | 11:34 | 49.912
2021-01-16 | 11:35 | 49.909
2021-01-16 | 11:35 | 49.906
2021-01-16 | 11:35 | 49.904
2021-01-16 | 11:35 | 49.905
2021-01-16 | 11:35 | 49.908
2021-01-16 | 11:35 | 49.908
2021-01-16 | 11:35 | 49.911
2021-01-16 | 11:35 | 49.914
2021-01-16 | 11:35 | 49.916
2021-01-16 | 11:35 | 49.917
2021-01-16 | 11:35 | 49.917
2021-01-16 | 11:35 | 49.918
2021-01-16 | 11:35 | 49.916
2021-01-16 | 11:35 | 49.915
2021-01-16 | 11:35 | 49.915
2021-01-16 | 11:35 | 49.914
2021-01-16 | 11:35 | 49.913
2021-01-16 | 11:35 | 49.916
2021-01-16 | 11:35 | 49.916
2021-01-16 | 11:35 | 49.916
2021-01-16 | 11:35 | 49.914
2021-01-16 | 11:35 | 49.913
2021-01-16 | 11:35 | 49.914
2021-01-16 | 11:35 | 49.913
2021-01-16 | 11:35 | 49.909
2021-01-16 | 11:35 | 49.907
2021-01-16 | 11:35 | 49.903
2021-01-16 | 11:35 | 49.9
2021-01-16 | 11:35 | 49.9
2021-01-16 | 11:35 | 49.898
2021-01-16 | 11:35 | 49.897
2021-01-16 | 11:35 | 49.897
2021-01-16 | 11:35 | 49.896
2021-01-16 | 11:35 | 49.897
2021-01-16 | 11:35 | 49.897
2021-01-16 | 11:35 | 49.896
2021-01-16 | 11:35 | 49.893
2021-01-16 | 11:35 | 49.887
2021-01-16 | 11:35 | 49.883
2021-01-16 | 11:35 | 49.881
2021-01-16 | 11:35 | 49.878
2021-01-16 | 11:35 | 49.877
2021-01-16 | 11:35 | 49.877
2021-01-16 | 11:35 | 49.874
2021-01-16 | 11:35 | 49.875
2021-01-16 | 11:35 | 49.877
2021-01-16 | 11:35 | 49.881
2021-01-16 | 11:35 | 49.885
2021-01-16 | 11:35 | 49.888
2021-01-16 | 11:35 | 49.889
2021-01-16 | 11:35 | 49.89
2021-01-16 | 11:35 | 49.889
2021-01-16 | 11:35 | 49.888
2021-01-16 | 11:35 | 49.889
2021-01-16 | 11:35 | 49.886
2021-01-16 | 11:35 | 49.888
2021-01-16 | 11:35 | 49.887
2021-01-16 | 11:35 | 49.888
2021-01-16 | 11:35 | 49.891
2021-01-16 | 11:36 | 49.89
2021-01-16 | 11:36 | 49.89
2021-01-16 | 11:36 | 49.889
2021-01-16 | 11:36 | 49.888
2021-01-16 | 11:36 | 49.893
2021-01-16 | 11:36 | 49.897
2021-01-16 | 11:36 | 49.899
2021-01-16 | 11:36 | 49.902
2021-01-16 | 11:36 | 49.9
2021-01-16 | 11:36 | 49.9
2021-01-16 | 11:36 | 49.899
2021-01-16 | 11:36 | 49.898
2021-01-16 | 11:36 | 49.898
2021-01-16 | 11:36 | 49.898
2021-01-16 | 11:36 | 49.898
2021-01-16 | 11:36 | 49.897
2021-01-16 | 11:36 | 49.894
2021-01-16 | 11:36 | 49.895
2021-01-16 | 11:36 | 49.894
2021-01-16 | 11:36 | 49.895
2021-01-16 | 11:36 | 49.896
2021-01-16 | 11:36 | 49.897
2021-01-16 | 11:36 | 49.899
2021-01-16 | 11:36 | 49.901
2021-01-16 | 11:36 | 49.903
2021-01-16 | 11:36 | 49.903
2021-01-16 | 11:36 | 49.904
2021-01-16 | 11:36 | 49.904
2021-01-16 | 11:36 | 49.904
2021-01-16 | 11:36 | 49.901
2021-01-16 | 11:36 | 49.9
2021-01-16 | 11:36 | 49.901
2021-01-16 | 11:36 | 49.901
2021-01-16 | 11:36 | 49.902
2021-01-16 | 11:36 | 49.902
2021-01-16 | 11:36 | 49.902
2021-01-16 | 11:36 | 49.902
2021-01-16 | 11:36 | 49.904
2021-01-16 | 11:36 | 49.907
2021-01-16 | 11:36 | 49.907
2021-01-16 | 11:36 | 49.906
2021-01-16 | 11:36 | 49.908
2021-01-16 | 11:36 | 49.909
2021-01-16 | 11:36 | 49.912
2021-01-16 | 11:36 | 49.913
2021-01-16 | 11:36 | 49.913
2021-01-16 | 11:36 | 49.912
2021-01-16 | 11:36 | 49.914
2021-01-16 | 11:36 | 49.916
2021-01-16 | 11:36 | 49.92
2021-01-16 | 11:36 | 49.92
2021-01-16 | 11:36 | 49.916
2021-01-16 | 11:36 | 49.911
2021-01-16 | 11:36 | 49.906
2021-01-16 | 11:36 | 49.905
2021-01-16 | 11:36 | 49.905
2021-01-16 | 11:36 | 49.906
2021-01-16 | 11:36 | 49.904
2021-01-16 | 11:36 | 49.902
2021-01-16 | 11:36 | 49.9
2021-01-16 | 11:36 | 49.897
2021-01-16 | 11:37 | 49.896
2021-01-16 | 11:37 | 49.896
2021-01-16 | 11:37 | 49.898
2021-01-16 | 11:37 | 49.896
2021-01-16 | 11:37 | 49.894
2021-01-16 | 11:37 | 49.895
2021-01-16 | 11:37 | 49.896
2021-01-16 | 11:37 | 49.898
2021-01-16 | 11:37 | 49.9
2021-01-16 | 11:37 | 49.9
2021-01-16 | 11:37 | 49.904
2021-01-16 | 11:37 | 49.908
2021-01-16 | 11:37 | 49.909
2021-01-16 | 11:37 | 49.912
2021-01-16 | 11:37 | 49.911
2021-01-16 | 11:37 | 49.91
2021-01-16 | 11:37 | 49.908
2021-01-16 | 11:37 | 49.907
2021-01-16 | 11:37 | 49.908
2021-01-16 | 11:37 | 49.908
2021-01-16 | 11:37 | 49.912
2021-01-16 | 11:37 | 49.912
2021-01-16 | 11:37 | 49.917
2021-01-16 | 11:37 | 49.918
2021-01-16 | 11:37 | 49.918
2021-01-16 | 11:37 | 49.918
2021-01-16 | 11:37 | 49.916
2021-01-16 | 11:37 | 49.919
2021-01-16 | 11:37 | 49.918
2021-01-16 | 11:37 | 49.916
2021-01-16 | 11:37 | 49.91
2021-01-16 | 11:37 | 49.905
2021-01-16 | 11:37 | 49.902
2021-01-16 | 11:37 | 49.9
2021-01-16 | 11:37 | 49.896
2021-01-16 | 11:37 | 49.896
2021-01-16 | 11:37 | 49.894
2021-01-16 | 11:37 | 49.893
2021-01-16 | 11:37 | 49.891
2021-01-16 | 11:37 | 49.891
2021-01-16 | 11:37 | 49.893
2021-01-16 | 11:37 | 49.894
2021-01-16 | 11:37 | 49.896
2021-01-16 | 11:37 | 49.898
2021-01-16 | 11:37 | 49.895
2021-01-16 | 11:37 | 49.898
2021-01-16 | 11:37 | 49.899
2021-01-16 | 11:37 | 49.899
2021-01-16 | 11:37 | 49.904
2021-01-16 | 11:37 | 49.9
2021-01-16 | 11:37 | 49.9
2021-01-16 | 11:37 | 49.902
2021-01-16 | 11:37 | 49.903
2021-01-16 | 11:37 | 49.908
2021-01-16 | 11:37 | 49.912
2021-01-16 | 11:37 | 49.91
2021-01-16 | 11:37 | 49.909
2021-01-16 | 11:37 | 49.908
2021-01-16 | 11:37 | 49.906
2021-01-16 | 11:38 | 49.904
2021-01-16 | 11:38 | 49.904
2021-01-16 | 11:38 | 49.902
2021-01-16 | 11:38 | 49.902
2021-01-16 | 11:38 | 49.9
2021-01-16 | 11:38 | 49.902
2021-01-16 | 11:38 | 49.905
2021-01-16 | 11:38 | 49.907
2021-01-16 | 11:38 | 49.912
2021-01-16 | 11:38 | 49.917
2021-01-16 | 11:38 | 49.918
2021-01-16 | 11:38 | 49.918
2021-01-16 | 11:38 | 49.916
2021-01-16 | 11:38 | 49.914
2021-01-16 | 11:38 | 49.915
2021-01-16 | 11:38 | 49.915
2021-01-16 | 11:38 | 49.915
2021-01-16 | 11:38 | 49.918
2021-01-16 | 11:38 | 49.918
2021-01-16 | 11:38 | 49.917
2021-01-16 | 11:38 | 49.917
2021-01-16 | 11:38 | 49.915
2021-01-16 | 11:38 | 49.914
2021-01-16 | 11:38 | 49.911
2021-01-16 | 11:38 | 49.909
2021-01-16 | 11:38 | 49.908
2021-01-16 | 11:38 | 49.908
2021-01-16 | 11:38 | 49.907
2021-01-16 | 11:38 | 49.903
2021-01-16 | 11:38 | 49.905
2021-01-16 | 11:38 | 49.908
2021-01-16 | 11:38 | 49.907
2021-01-16 | 11:38 | 49.91
2021-01-16 | 11:38 | 49.912
2021-01-16 | 11:38 | 49.92
2021-01-16 | 11:38 | 49.929
2021-01-16 | 11:38 | 49.933
2021-01-16 | 11:38 | 49.934
2021-01-16 | 11:38 | 49.933
2021-01-16 | 11:38 | 49.929
2021-01-16 | 11:38 | 49.926
2021-01-16 | 11:38 | 49.924
2021-01-16 | 11:38 | 49.918
2021-01-16 | 11:38 | 49.917
2021-01-16 | 11:38 | 49.913
2021-01-16 | 11:38 | 49.911
2021-01-16 | 11:38 | 49.912
2021-01-16 | 11:38 | 49.91
2021-01-16 | 11:38 | 49.908
2021-01-16 | 11:38 | 49.909
2021-01-16 | 11:38 | 49.907
2021-01-16 | 11:38 | 49.907
2021-01-16 | 11:38 | 49.908
2021-01-16 | 11:38 | 49.905
2021-01-16 | 11:38 | 49.904
2021-01-16 | 11:38 | 49.904
2021-01-16 | 11:38 | 49.904
2021-01-16 | 11:38 | 49.905
2021-01-16 | 11:38 | 49.905
2021-01-16 | 11:38 | 49.905
2021-01-16 | 11:39 | 49.906
2021-01-16 | 11:39 | 49.906
2021-01-16 | 11:39 | 49.907
2021-01-16 | 11:39 | 49.908
2021-01-16 | 11:39 | 49.907
2021-01-16 | 11:39 | 49.905
2021-01-16 | 11:39 | 49.906
2021-01-16 | 11:39 | 49.906
2021-01-16 | 11:39 | 49.906
2021-01-16 | 11:39 | 49.906
2021-01-16 | 11:39 | 49.908
2021-01-16 | 11:39 | 49.909
2021-01-16 | 11:39 | 49.908
2021-01-16 | 11:39 | 49.91
2021-01-16 | 11:39 | 49.911
2021-01-16 | 11:39 | 49.911
2021-01-16 | 11:39 | 49.913
2021-01-16 | 11:39 | 49.913
2021-01-16 | 11:39 | 49.912
2021-01-16 | 11:39 | 49.913
2021-01-16 | 11:39 | 49.916
2021-01-16 | 11:39 | 49.916
2021-01-16 | 11:39 | 49.918
2021-01-16 | 11:39 | 49.918
2021-01-16 | 11:39 | 49.92
2021-01-16 | 11:39 | 49.92
2021-01-16 | 11:39 | 49.921
2021-01-16 | 11:39 | 49.921
2021-01-16 | 11:39 | 49.919
2021-01-16 | 11:39 | 49.919
2021-01-16 | 11:39 | 49.917
2021-01-16 | 11:39 | 49.912
2021-01-16 | 11:39 | 49.911
2021-01-16 | 11:39 | 49.908
2021-01-16 | 11:39 | 49.906
2021-01-16 | 11:39 | 49.906
2021-01-16 | 11:39 | 49.906
2021-01-16 | 11:39 | 49.906
2021-01-16 | 11:39 | 49.904
2021-01-16 | 11:39 | 49.904
2021-01-16 | 11:39 | 49.906
2021-01-16 | 11:39 | 49.906
2021-01-16 | 11:39 | 49.906
2021-01-16 | 11:39 | 49.905
2021-01-16 | 11:39 | 49.906
2021-01-16 | 11:39 | 49.903
2021-01-16 | 11:39 | 49.901
2021-01-16 | 11:39 | 49.901
2021-01-16 | 11:39 | 49.896
2021-01-16 | 11:39 | 49.897
2021-01-16 | 11:39 | 49.895
2021-01-16 | 11:39 | 49.896
2021-01-16 | 11:39 | 49.897
2021-01-16 | 11:39 | 49.897
2021-01-16 | 11:39 | 49.9
2021-01-16 | 11:39 | 49.9
2021-01-16 | 11:39 | 49.905
2021-01-16 | 11:39 | 49.906
2021-01-16 | 11:39 | 49.906
2021-01-16 | 11:39 | 49.908
2021-01-16 | 11:40 | 49.906
2021-01-16 | 11:40 | 49.907
2021-01-16 | 11:40 | 49.905
2021-01-16 | 11:40 | 49.905
2021-01-16 | 11:40 | 49.904
2021-01-16 | 11:40 | 49.904
2021-01-16 | 11:40 | 49.906
2021-01-16 | 11:40 | 49.908
2021-01-16 | 11:40 | 49.907
2021-01-16 | 11:40 | 49.905
2021-01-16 | 11:40 | 49.907
2021-01-16 | 11:40 | 49.907
2021-01-16 | 11:40 | 49.904
2021-01-16 | 11:40 | 49.903
2021-01-16 | 11:40 | 49.899
2021-01-16 | 11:40 | 49.897
2021-01-16 | 11:40 | 49.895
2021-01-16 | 11:40 | 49.894
2021-01-16 | 11:40 | 49.894
2021-01-16 | 11:40 | 49.893
2021-01-16 | 11:40 | 49.891
2021-01-16 | 11:40 | 49.892
2021-01-16 | 11:40 | 49.891
2021-01-16 | 11:40 | 49.888
2021-01-16 | 11:40 | 49.886
2021-01-16 | 11:40 | 49.887
2021-01-16 | 11:40 | 49.888
2021-01-16 | 11:40 | 49.889
2021-01-16 | 11:40 | 49.888
2021-01-16 | 11:40 | 49.888
2021-01-16 | 11:40 | 49.887
2021-01-16 | 11:40 | 49.887
2021-01-16 | 11:40 | 49.884
2021-01-16 | 11:40 | 49.883
2021-01-16 | 11:40 | 49.882
2021-01-16 | 11:40 | 49.884
2021-01-16 | 11:40 | 49.885
2021-01-16 | 11:40 | 49.888
2021-01-16 | 11:40 | 49.892
2021-01-16 | 11:40 | 49.894
2021-01-16 | 11:40 | 49.895
2021-01-16 | 11:40 | 49.894
2021-01-16 | 11:40 | 49.891
2021-01-16 | 11:40 | 49.885
2021-01-16 | 11:40 | 49.882
2021-01-16 | 11:40 | 49.878
2021-01-16 | 11:40 | 49.878
2021-01-16 | 11:40 | 49.874
2021-01-16 | 11:40 | 49.874
2021-01-16 | 11:40 | 49.871
2021-01-16 | 11:40 | 49.871
2021-01-16 | 11:40 | 49.866
2021-01-16 | 11:40 | 49.866
2021-01-16 | 11:40 | 49.863
2021-01-16 | 11:40 | 49.864
2021-01-16 | 11:40 | 49.864
2021-01-16 | 11:40 | 49.866
2021-01-16 | 11:40 | 49.868
2021-01-16 | 11:40 | 49.873
2021-01-16 | 11:40 | 49.876
2021-01-16 | 11:41 | 49.88
2021-01-16 | 11:41 | 49.879
2021-01-16 | 11:41 | 49.88
2021-01-16 | 11:41 | 49.879
2021-01-16 | 11:41 | 49.881
2021-01-16 | 11:41 | 49.88
2021-01-16 | 11:41 | 49.881
2021-01-16 | 11:41 | 49.88
2021-01-16 | 11:41 | 49.88
2021-01-16 | 11:41 | 49.878
2021-01-16 | 11:41 | 49.877
2021-01-16 | 11:41 | 49.872
2021-01-16 | 11:41 | 49.873
2021-01-16 | 11:41 | 49.872
2021-01-16 | 11:41 | 49.873
2021-01-16 | 11:41 | 49.873
2021-01-16 | 11:41 | 49.873
2021-01-16 | 11:41 | 49.87
2021-01-16 | 11:41 | 49.869
2021-01-16 | 11:41 | 49.868
2021-01-16 | 11:41 | 49.87
2021-01-16 | 11:41 | 49.87
2021-01-16 | 11:41 | 49.872
2021-01-16 | 11:41 | 49.874
2021-01-16 | 11:41 | 49.877
2021-01-16 | 11:41 | 49.878
2021-01-16 | 11:41 | 49.881
2021-01-16 | 11:41 | 49.881
2021-01-16 | 11:41 | 49.881
2021-01-16 | 11:41 | 49.879
2021-01-16 | 11:41 | 49.88
2021-01-16 | 11:41 | 49.877
2021-01-16 | 11:41 | 49.876
2021-01-16 | 11:41 | 49.875
2021-01-16 | 11:41 | 49.874
2021-01-16 | 11:41 | 49.875
2021-01-16 | 11:41 | 49.878
2021-01-16 | 11:41 | 49.878
2021-01-16 | 11:41 | 49.882
2021-01-16 | 11:41 | 49.882
2021-01-16 | 11:41 | 49.88
2021-01-16 | 11:41 | 49.878
2021-01-16 | 11:41 | 49.876
2021-01-16 | 11:41 | 49.872
2021-01-16 | 11:41 | 49.868
2021-01-16 | 11:41 | 49.868
2021-01-16 | 11:41 | 49.868
2021-01-16 | 11:41 | 49.87
2021-01-16 | 11:41 | 49.873
2021-01-16 | 11:41 | 49.874
2021-01-16 | 11:41 | 49.875
2021-01-16 | 11:41 | 49.875
2021-01-16 | 11:41 | 49.877
2021-01-16 | 11:41 | 49.88
2021-01-16 | 11:41 | 49.879
2021-01-16 | 11:41 | 49.879
2021-01-16 | 11:41 | 49.877
2021-01-16 | 11:41 | 49.874
2021-01-16 | 11:41 | 49.875
2021-01-16 | 11:41 | 49.876
2021-01-16 | 11:42 | 49.876
2021-01-16 | 11:42 | 49.873
2021-01-16 | 11:42 | 49.873
2021-01-16 | 11:42 | 49.874
2021-01-16 | 11:42 | 49.873
2021-01-16 | 11:42 | 49.875
2021-01-16 | 11:42 | 49.876
2021-01-16 | 11:42 | 49.877
2021-01-16 | 11:42 | 49.878
2021-01-16 | 11:42 | 49.881
2021-01-16 | 11:42 | 49.882
2021-01-16 | 11:42 | 49.881
2021-01-16 | 11:42 | 49.881
2021-01-16 | 11:42 | 49.878
2021-01-16 | 11:42 | 49.879
2021-01-16 | 11:42 | 49.877
2021-01-16 | 11:42 | 49.877
2021-01-16 | 11:42 | 49.877
2021-01-16 | 11:42 | 49.876
2021-01-16 | 11:42 | 49.878
2021-01-16 | 11:42 | 49.879
2021-01-16 | 11:42 | 49.88
2021-01-16 | 11:42 | 49.879
2021-01-16 | 11:42 | 49.878
2021-01-16 | 11:42 | 49.877
2021-01-16 | 11:42 | 49.876
2021-01-16 | 11:42 | 49.877
2021-01-16 | 11:42 | 49.879
2021-01-16 | 11:42 | 49.881
2021-01-16 | 11:42 | 49.881
2021-01-16 | 11:42 | 49.881
2021-01-16 | 11:42 | 49.88
2021-01-16 | 11:42 | 49.88
2021-01-16 | 11:42 | 49.881
2021-01-16 | 11:42 | 49.88
2021-01-16 | 11:42 | 49.883
2021-01-16 | 11:42 | 49.883
2021-01-16 | 11:42 | 49.881
2021-01-16 | 11:42 | 49.881
2021-01-16 | 11:42 | 49.878
2021-01-16 | 11:42 | 49.879
2021-01-16 | 11:42 | 49.88
2021-01-16 | 11:42 | 49.877
2021-01-16 | 11:42 | 49.878
2021-01-16 | 11:42 | 49.877
2021-01-16 | 11:42 | 49.879
2021-01-16 | 11:42 | 49.874
2021-01-16 | 11:42 | 49.875
2021-01-16 | 11:42 | 49.874
2021-01-16 | 11:42 | 49.875
2021-01-16 | 11:42 | 49.875
2021-01-16 | 11:42 | 49.873
2021-01-16 | 11:42 | 49.872
2021-01-16 | 11:42 | 49.873
2021-01-16 | 11:42 | 49.874
2021-01-16 | 11:42 | 49.875
2021-01-16 | 11:42 | 49.876
2021-01-16 | 11:42 | 49.877
2021-01-16 | 11:42 | 49.877
2021-01-16 | 11:42 | 49.876
2021-01-16 | 11:43 | 49.874
2021-01-16 | 11:43 | 49.877
2021-01-16 | 11:43 | 49.877
2021-01-16 | 11:43 | 49.878
2021-01-16 | 11:43 | 49.879
2021-01-16 | 11:43 | 49.876
2021-01-16 | 11:43 | 49.877
2021-01-16 | 11:43 | 49.88
2021-01-16 | 11:43 | 49.88
2021-01-16 | 11:43 | 49.886
2021-01-16 | 11:43 | 49.891
2021-01-16 | 11:43 | 49.891
2021-01-16 | 11:43 | 49.893
2021-01-16 | 11:43 | 49.892
2021-01-16 | 11:43 | 49.893
2021-01-16 | 11:43 | 49.894
2021-01-16 | 11:43 | 49.89
2021-01-16 | 11:43 | 49.889
2021-01-16 | 11:43 | 49.887
2021-01-16 | 11:43 | 49.884
2021-01-16 | 11:43 | 49.885
2021-01-16 | 11:43 | 49.885
2021-01-16 | 11:43 | 49.89
2021-01-16 | 11:43 | 49.893
2021-01-16 | 11:43 | 49.898
2021-01-16 | 11:43 | 49.899
2021-01-16 | 11:43 | 49.898
2021-01-16 | 11:43 | 49.898
2021-01-16 | 11:43 | 49.898
2021-01-16 | 11:43 | 49.894
2021-01-16 | 11:43 | 49.891
2021-01-16 | 11:43 | 49.889
2021-01-16 | 11:43 | 49.885
2021-01-16 | 11:43 | 49.883
2021-01-16 | 11:43 | 49.883
2021-01-16 | 11:43 | 49.881
2021-01-16 | 11:43 | 49.882
2021-01-16 | 11:43 | 49.88
2021-01-16 | 11:43 | 49.878
2021-01-16 | 11:43 | 49.88
2021-01-16 | 11:43 | 49.879
2021-01-16 | 11:43 | 49.875
2021-01-16 | 11:43 | 49.874
2021-01-16 | 11:43 | 49.87
2021-01-16 | 11:43 | 49.869
2021-01-16 | 11:43 | 49.866
2021-01-16 | 11:43 | 49.863
2021-01-16 | 11:43 | 49.866
2021-01-16 | 11:43 | 49.865
2021-01-16 | 11:43 | 49.867
2021-01-16 | 11:43 | 49.867
2021-01-16 | 11:43 | 49.865
2021-01-16 | 11:43 | 49.864
2021-01-16 | 11:43 | 49.859
2021-01-16 | 11:43 | 49.858
2021-01-16 | 11:43 | 49.856
2021-01-16 | 11:43 | 49.857
2021-01-16 | 11:43 | 49.861
2021-01-16 | 11:43 | 49.862
2021-01-16 | 11:43 | 49.864
2021-01-16 | 11:44 | 49.867
2021-01-16 | 11:44 | 49.867
2021-01-16 | 11:44 | 49.867
2021-01-16 | 11:44 | 49.866
2021-01-16 | 11:44 | 49.866
2021-01-16 | 11:44 | 49.867
2021-01-16 | 11:44 | 49.867
2021-01-16 | 11:44 | 49.867
2021-01-16 | 11:44 | 49.866
2021-01-16 | 11:44 | 49.865
2021-01-16 | 11:44 | 49.864
2021-01-16 | 11:44 | 49.862
2021-01-16 | 11:44 | 49.861
2021-01-16 | 11:44 | 49.857
2021-01-16 | 11:44 | 49.858
2021-01-16 | 11:44 | 49.857
2021-01-16 | 11:44 | 49.858
2021-01-16 | 11:44 | 49.857
2021-01-16 | 11:44 | 49.855
2021-01-16 | 11:44 | 49.855
2021-01-16 | 11:44 | 49.855
2021-01-16 | 11:44 | 49.852
2021-01-16 | 11:44 | 49.851
2021-01-16 | 11:44 | 49.849
2021-01-16 | 11:44 | 49.848
2021-01-16 | 11:44 | 49.845
2021-01-16 | 11:44 | 49.845
2021-01-16 | 11:44 | 49.847
2021-01-16 | 11:44 | 49.849
2021-01-16 | 11:44 | 49.853
2021-01-16 | 11:44 | 49.855
2021-01-16 | 11:44 | 49.856
2021-01-16 | 11:44 | 49.855
2021-01-16 | 11:44 | 49.854
2021-01-16 | 11:44 | 49.856
2021-01-16 | 11:44 | 49.854
2021-01-16 | 11:44 | 49.854
2021-01-16 | 11:44 | 49.855
2021-01-16 | 11:44 | 49.853
2021-01-16 | 11:44 | 49.853
2021-01-16 | 11:44 | 49.853
2021-01-16 | 11:44 | 49.852
2021-01-16 | 11:44 | 49.853
2021-01-16 | 11:44 | 49.853
2021-01-16 | 11:44 | 49.854
2021-01-16 | 11:44 | 49.855
2021-01-16 | 11:44 | 49.856
2021-01-16 | 11:44 | 49.858
2021-01-16 | 11:44 | 49.859
2021-01-16 | 11:44 | 49.862
2021-01-16 | 11:44 | 49.864
2021-01-16 | 11:44 | 49.869
2021-01-16 | 11:44 | 49.874
2021-01-16 | 11:44 | 49.882
2021-01-16 | 11:44 | 49.889
2021-01-16 | 11:44 | 49.898
2021-01-16 | 11:44 | 49.903
2021-01-16 | 11:44 | 49.907
2021-01-16 | 11:44 | 49.907
2021-01-16 | 11:44 | 49.907
2021-01-16 | 11:44 | 49.907
2021-01-16 | 11:45 | 49.905
2021-01-16 | 11:45 | 49.905
2021-01-16 | 11:45 | 49.9
2021-01-16 | 11:45 | 49.899
2021-01-16 | 11:45 | 49.899
2021-01-16 | 11:45 | 49.897
2021-01-16 | 11:45 | 49.896
2021-01-16 | 11:45 | 49.9
2021-01-16 | 11:45 | 49.902
2021-01-16 | 11:45 | 49.903
2021-01-16 | 11:45 | 49.9
2021-01-16 | 11:45 | 49.903
2021-01-16 | 11:45 | 49.906
2021-01-16 | 11:45 | 49.905
2021-01-16 | 11:45 | 49.909
2021-01-16 | 11:45 | 49.911
2021-01-16 | 11:45 | 49.912
2021-01-16 | 11:45 | 49.913
2021-01-16 | 11:45 | 49.913
2021-01-16 | 11:45 | 49.916
2021-01-16 | 11:45 | 49.916
2021-01-16 | 11:45 | 49.915
2021-01-16 | 11:45 | 49.916
2021-01-16 | 11:45 | 49.914
2021-01-16 | 11:45 | 49.913
2021-01-16 | 11:45 | 49.913
2021-01-16 | 11:45 | 49.91
2021-01-16 | 11:45 | 49.91
2021-01-16 | 11:45 | 49.907
2021-01-16 | 11:45 | 49.905
2021-01-16 | 11:45 | 49.906
2021-01-16 | 11:45 | 49.905
2021-01-16 | 11:45 | 49.909
2021-01-16 | 11:45 | 49.911
2021-01-16 | 11:45 | 49.913
2021-01-16 | 11:45 | 49.912
2021-01-16 | 11:45 | 49.913
2021-01-16 | 11:45 | 49.912
2021-01-16 | 11:45 | 49.912
2021-01-16 | 11:45 | 49.911
2021-01-16 | 11:45 | 49.909
2021-01-16 | 11:45 | 49.905
2021-01-16 | 11:45 | 49.902
2021-01-16 | 11:45 | 49.901
2021-01-16 | 11:45 | 49.897
2021-01-16 | 11:45 | 49.896
2021-01-16 | 11:45 | 49.893
2021-01-16 | 11:45 | 49.892
2021-01-16 | 11:45 | 49.896
2021-01-16 | 11:45 | 49.902
2021-01-16 | 11:45 | 49.907
2021-01-16 | 11:45 | 49.91
2021-01-16 | 11:45 | 49.911
2021-01-16 | 11:45 | 49.909
2021-01-16 | 11:45 | 49.911
2021-01-16 | 11:45 | 49.912
2021-01-16 | 11:45 | 49.913
2021-01-16 | 11:45 | 49.914
2021-01-16 | 11:45 | 49.915
2021-01-16 | 11:46 | 49.917
2021-01-16 | 11:46 | 49.916
2021-01-16 | 11:46 | 49.918
2021-01-16 | 11:46 | 49.918
2021-01-16 | 11:46 | 49.916
2021-01-16 | 11:46 | 49.915
2021-01-16 | 11:46 | 49.913
2021-01-16 | 11:46 | 49.913
2021-01-16 | 11:46 | 49.914
2021-01-16 | 11:46 | 49.918
2021-01-16 | 11:46 | 49.923
2021-01-16 | 11:46 | 49.923
2021-01-16 | 11:46 | 49.923
2021-01-16 | 11:46 | 49.922
2021-01-16 | 11:46 | 49.923
2021-01-16 | 11:46 | 49.923
2021-01-16 | 11:46 | 49.926
2021-01-16 | 11:46 | 49.923
2021-01-16 | 11:46 | 49.921
2021-01-16 | 11:46 | 49.917
2021-01-16 | 11:46 | 49.916
2021-01-16 | 11:46 | 49.915
2021-01-16 | 11:46 | 49.914
2021-01-16 | 11:46 | 49.915
2021-01-16 | 11:46 | 49.917
2021-01-16 | 11:46 | 49.917
2021-01-16 | 11:46 | 49.918
2021-01-16 | 11:46 | 49.918
2021-01-16 | 11:46 | 49.918
2021-01-16 | 11:46 | 49.913
2021-01-16 | 11:46 | 49.909
2021-01-16 | 11:46 | 49.907
2021-01-16 | 11:46 | 49.907
2021-01-16 | 11:46 | 49.907
2021-01-16 | 11:46 | 49.908
2021-01-16 | 11:46 | 49.912
2021-01-16 | 11:46 | 49.913
2021-01-16 | 11:46 | 49.916
2021-01-16 | 11:46 | 49.917
2021-01-16 | 11:46 | 49.919
2021-01-16 | 11:46 | 49.921
2021-01-16 | 11:46 | 49.919
2021-01-16 | 11:46 | 49.921
2021-01-16 | 11:46 | 49.919
2021-01-16 | 11:46 | 49.919
2021-01-16 | 11:46 | 49.917
2021-01-16 | 11:46 | 49.916
2021-01-16 | 11:46 | 49.915
2021-01-16 | 11:46 | 49.912
2021-01-16 | 11:46 | 49.912
2021-01-16 | 11:46 | 49.913
2021-01-16 | 11:46 | 49.916
2021-01-16 | 11:46 | 49.922
2021-01-16 | 11:46 | 49.928
2021-01-16 | 11:46 | 49.931
2021-01-16 | 11:46 | 49.934
2021-01-16 | 11:46 | 49.939
2021-01-16 | 11:46 | 49.941
2021-01-16 | 11:46 | 49.94
2021-01-16 | 11:46 | 49.937
2021-01-16 | 11:46 | 49.934
2021-01-16 | 11:47 | 49.929
2021-01-16 | 11:47 | 49.926
2021-01-16 | 11:47 | 49.923
2021-01-16 | 11:47 | 49.923
2021-01-16 | 11:47 | 49.922
2021-01-16 | 11:47 | 49.92
2021-01-16 | 11:47 | 49.919
2021-01-16 | 11:47 | 49.916
2021-01-16 | 11:47 | 49.916
2021-01-16 | 11:47 | 49.913
2021-01-16 | 11:47 | 49.912
2021-01-16 | 11:47 | 49.91
2021-01-16 | 11:47 | 49.908
2021-01-16 | 11:47 | 49.907
2021-01-16 | 11:47 | 49.908
2021-01-16 | 11:47 | 49.906
2021-01-16 | 11:47 | 49.904
2021-01-16 | 11:47 | 49.903
2021-01-16 | 11:47 | 49.902
2021-01-16 | 11:47 | 49.903
2021-01-16 | 11:47 | 49.904
2021-01-16 | 11:47 | 49.906
2021-01-16 | 11:47 | 49.906
2021-01-16 | 11:47 | 49.908
2021-01-16 | 11:47 | 49.91
2021-01-16 | 11:47 | 49.913
2021-01-16 | 11:47 | 49.915
2021-01-16 | 11:47 | 49.916
2021-01-16 | 11:47 | 49.914
2021-01-16 | 11:47 | 49.913
2021-01-16 | 11:47 | 49.913
2021-01-16 | 11:47 | 49.912
2021-01-16 | 11:47 | 49.912
2021-01-16 | 11:47 | 49.916
2021-01-16 | 11:47 | 49.918
2021-01-16 | 11:47 | 49.921
2021-01-16 | 11:47 | 49.923
2021-01-16 | 11:47 | 49.926
2021-01-16 | 11:47 | 49.927
2021-01-16 | 11:47 | 49.924
2021-01-16 | 11:47 | 49.922
2021-01-16 | 11:47 | 49.918
2021-01-16 | 11:47 | 49.918
2021-01-16 | 11:47 | 49.917
2021-01-16 | 11:47 | 49.921
2021-01-16 | 11:47 | 49.92
2021-01-16 | 11:47 | 49.92
2021-01-16 | 11:47 | 49.919
2021-01-16 | 11:47 | 49.92
2021-01-16 | 11:47 | 49.921
2021-01-16 | 11:47 | 49.923
2021-01-16 | 11:47 | 49.922
2021-01-16 | 11:47 | 49.923
2021-01-16 | 11:47 | 49.924
2021-01-16 | 11:47 | 49.923
2021-01-16 | 11:47 | 49.921
2021-01-16 | 11:47 | 49.92
2021-01-16 | 11:47 | 49.921
2021-01-16 | 11:47 | 49.922
2021-01-16 | 11:48 | 49.921
2021-01-16 | 11:48 | 49.922
2021-01-16 | 11:48 | 49.924
2021-01-16 | 11:48 | 49.925
2021-01-16 | 11:48 | 49.929
2021-01-16 | 11:48 | 49.93
2021-01-16 | 11:48 | 49.93
2021-01-16 | 11:48 | 49.926
2021-01-16 | 11:48 | 49.923
2021-01-16 | 11:48 | 49.92
2021-01-16 | 11:48 | 49.92
2021-01-16 | 11:48 | 49.919
2021-01-16 | 11:48 | 49.919
2021-01-16 | 11:48 | 49.918
2021-01-16 | 11:48 | 49.918
2021-01-16 | 11:48 | 49.916
2021-01-16 | 11:48 | 49.913
2021-01-16 | 11:48 | 49.912
2021-01-16 | 11:48 | 49.912
2021-01-16 | 11:48 | 49.912
2021-01-16 | 11:48 | 49.913
2021-01-16 | 11:48 | 49.917
2021-01-16 | 11:48 | 49.919
2021-01-16 | 11:48 | 49.921
2021-01-16 | 11:48 | 49.922
2021-01-16 | 11:48 | 49.922
2021-01-16 | 11:48 | 49.922
2021-01-16 | 11:48 | 49.923
2021-01-16 | 11:48 | 49.923
2021-01-16 | 11:48 | 49.925
2021-01-16 | 11:48 | 49.924
2021-01-16 | 11:48 | 49.92
2021-01-16 | 11:48 | 49.919
2021-01-16 | 11:48 | 49.918
2021-01-16 | 11:48 | 49.919
2021-01-16 | 11:48 | 49.919
2021-01-16 | 11:48 | 49.919
2021-01-16 | 11:48 | 49.919
2021-01-16 | 11:48 | 49.921
2021-01-16 | 11:48 | 49.921
2021-01-16 | 11:48 | 49.92
2021-01-16 | 11:48 | 49.921
2021-01-16 | 11:48 | 49.919
2021-01-16 | 11:48 | 49.918
2021-01-16 | 11:48 | 49.918
2021-01-16 | 11:48 | 49.919
2021-01-16 | 11:48 | 49.919
2021-01-16 | 11:48 | 49.919
2021-01-16 | 11:48 | 49.918
2021-01-16 | 11:48 | 49.92
2021-01-16 | 11:48 | 49.923
2021-01-16 | 11:48 | 49.92
2021-01-16 | 11:48 | 49.922
2021-01-16 | 11:48 | 49.918
2021-01-16 | 11:48 | 49.918
2021-01-16 | 11:48 | 49.92
2021-01-16 | 11:48 | 49.921
2021-01-16 | 11:48 | 49.922
2021-01-16 | 11:48 | 49.922
2021-01-16 | 11:48 | 49.924
2021-01-16 | 11:48 | 49.923
2021-01-16 | 11:49 | 49.924
2021-01-16 | 11:49 | 49.924
2021-01-16 | 11:49 | 49.924
2021-01-16 | 11:49 | 49.924
2021-01-16 | 11:49 | 49.926
2021-01-16 | 11:49 | 49.929
2021-01-16 | 11:49 | 49.931
2021-01-16 | 11:49 | 49.932
2021-01-16 | 11:49 | 49.931
2021-01-16 | 11:49 | 49.93
2021-01-16 | 11:49 | 49.933
2021-01-16 | 11:49 | 49.934
2021-01-16 | 11:49 | 49.936
2021-01-16 | 11:49 | 49.937
2021-01-16 | 11:49 | 49.939
2021-01-16 | 11:49 | 49.941
2021-01-16 | 11:49 | 49.943
2021-01-16 | 11:49 | 49.948
2021-01-16 | 11:49 | 49.949
2021-01-16 | 11:49 | 49.95
2021-01-16 | 11:49 | 49.949
2021-01-16 | 11:49 | 49.948
2021-01-16 | 11:49 | 49.947
2021-01-16 | 11:49 | 49.946
2021-01-16 | 11:49 | 49.944
2021-01-16 | 11:49 | 49.942
2021-01-16 | 11:49 | 49.941
2021-01-16 | 11:49 | 49.941
2021-01-16 | 11:49 | 49.943
2021-01-16 | 11:49 | 49.948
2021-01-16 | 11:49 | 49.951
2021-01-16 | 11:49 | 49.952
2021-01-16 | 11:49 | 49.952
2021-01-16 | 11:49 | 49.951
2021-01-16 | 11:49 | 49.951
2021-01-16 | 11:49 | 49.951
2021-01-16 | 11:49 | 49.953
2021-01-16 | 11:49 | 49.956
2021-01-16 | 11:49 | 49.958
2021-01-16 | 11:49 | 49.956
2021-01-16 | 11:49 | 49.953
2021-01-16 | 11:49 | 49.951
2021-01-16 | 11:49 | 49.946
2021-01-16 | 11:49 | 49.943
2021-01-16 | 11:49 | 49.942
2021-01-16 | 11:49 | 49.938
2021-01-16 | 11:49 | 49.936
2021-01-16 | 11:49 | 49.934
2021-01-16 | 11:49 | 49.932
2021-01-16 | 11:49 | 49.931
2021-01-16 | 11:49 | 49.93
2021-01-16 | 11:49 | 49.931
2021-01-16 | 11:49 | 49.933
2021-01-16 | 11:49 | 49.935
2021-01-16 | 11:49 | 49.938
2021-01-16 | 11:49 | 49.941
2021-01-16 | 11:49 | 49.938
2021-01-16 | 11:49 | 49.938
2021-01-16 | 11:49 | 49.939
2021-01-16 | 11:50 | 49.939
2021-01-16 | 11:50 | 49.941
2021-01-16 | 11:50 | 49.941
2021-01-16 | 11:50 | 49.94
2021-01-16 | 11:50 | 49.941
2021-01-16 | 11:50 | 49.942
2021-01-16 | 11:50 | 49.945
2021-01-16 | 11:50 | 49.948
2021-01-16 | 11:50 | 49.952
2021-01-16 | 11:50 | 49.953
2021-01-16 | 11:50 | 49.956
2021-01-16 | 11:50 | 49.956
2021-01-16 | 11:50 | 49.954
2021-01-16 | 11:50 | 49.953
2021-01-16 | 11:50 | 49.951
2021-01-16 | 11:50 | 49.95
2021-01-16 | 11:50 | 49.948
2021-01-16 | 11:50 | 49.948
2021-01-16 | 11:50 | 49.949
2021-01-16 | 11:50 | 49.95
2021-01-16 | 11:50 | 49.948
2021-01-16 | 11:50 | 49.948
2021-01-16 | 11:50 | 49.946
2021-01-16 | 11:50 | 49.947
2021-01-16 | 11:50 | 49.945
2021-01-16 | 11:50 | 49.946
2021-01-16 | 11:50 | 49.948
2021-01-16 | 11:50 | 49.946
2021-01-16 | 11:50 | 49.947
2021-01-16 | 11:50 | 49.947
2021-01-16 | 11:50 | 49.947
2021-01-16 | 11:50 | 49.949
2021-01-16 | 11:50 | 49.946
2021-01-16 | 11:50 | 49.946
2021-01-16 | 11:50 | 49.945
2021-01-16 | 11:50 | 49.944
2021-01-16 | 11:50 | 49.945
2021-01-16 | 11:50 | 49.947
2021-01-16 | 11:50 | 49.948
2021-01-16 | 11:50 | 49.951
2021-01-16 | 11:50 | 49.955
2021-01-16 | 11:50 | 49.958
2021-01-16 | 11:50 | 49.959
2021-01-16 | 11:50 | 49.96
2021-01-16 | 11:50 | 49.961
2021-01-16 | 11:50 | 49.962
2021-01-16 | 11:50 | 49.961
2021-01-16 | 11:50 | 49.962
2021-01-16 | 11:50 | 49.96
2021-01-16 | 11:50 | 49.96
2021-01-16 | 11:50 | 49.96
2021-01-16 | 11:50 | 49.958
2021-01-16 | 11:50 | 49.956
2021-01-16 | 11:50 | 49.957
2021-01-16 | 11:50 | 49.955
2021-01-16 | 11:50 | 49.956
2021-01-16 | 11:50 | 49.957
2021-01-16 | 11:50 | 49.956
2021-01-16 | 11:50 | 49.956
2021-01-16 | 11:50 | 49.954
2021-01-16 | 11:50 | 49.953
2021-01-16 | 11:51 | 49.953
2021-01-16 | 11:51 | 49.952
2021-01-16 | 11:51 | 49.953
2021-01-16 | 11:51 | 49.953
2021-01-16 | 11:51 | 49.952
2021-01-16 | 11:51 | 49.955
2021-01-16 | 11:51 | 49.957
2021-01-16 | 11:51 | 49.958
2021-01-16 | 11:51 | 49.957
2021-01-16 | 11:51 | 49.954
2021-01-16 | 11:51 | 49.951
2021-01-16 | 11:51 | 49.948
2021-01-16 | 11:51 | 49.945
2021-01-16 | 11:51 | 49.945
2021-01-16 | 11:51 | 49.945
2021-01-16 | 11:51 | 49.944
2021-01-16 | 11:51 | 49.947
2021-01-16 | 11:51 | 49.95
2021-01-16 | 11:51 | 49.95
2021-01-16 | 11:51 | 49.951
2021-01-16 | 11:51 | 49.953
2021-01-16 | 11:51 | 49.953
2021-01-16 | 11:51 | 49.951
2021-01-16 | 11:51 | 49.949
2021-01-16 | 11:51 | 49.949
2021-01-16 | 11:51 | 49.947
2021-01-16 | 11:51 | 49.944
2021-01-16 | 11:51 | 49.945
2021-01-16 | 11:51 | 49.943
2021-01-16 | 11:51 | 49.94
2021-01-16 | 11:51 | 49.936
2021-01-16 | 11:51 | 49.933
2021-01-16 | 11:51 | 49.93
2021-01-16 | 11:51 | 49.931
2021-01-16 | 11:51 | 49.932
2021-01-16 | 11:51 | 49.932
2021-01-16 | 11:51 | 49.93
2021-01-16 | 11:51 | 49.93
2021-01-16 | 11:51 | 49.931
2021-01-16 | 11:51 | 49.931
2021-01-16 | 11:51 | 49.926
2021-01-16 | 11:51 | 49.923
2021-01-16 | 11:51 | 49.922
2021-01-16 | 11:51 | 49.921
2021-01-16 | 11:51 | 49.919
2021-01-16 | 11:51 | 49.92
2021-01-16 | 11:51 | 49.921
2021-01-16 | 11:51 | 49.923
2021-01-16 | 11:51 | 49.925
2021-01-16 | 11:51 | 49.928
2021-01-16 | 11:51 | 49.932
2021-01-16 | 11:51 | 49.935
2021-01-16 | 11:51 | 49.938
2021-01-16 | 11:51 | 49.943
2021-01-16 | 11:51 | 49.945
2021-01-16 | 11:51 | 49.947
2021-01-16 | 11:51 | 49.947
2021-01-16 | 11:51 | 49.944
2021-01-16 | 11:51 | 49.942
2021-01-16 | 11:52 | 49.941
2021-01-16 | 11:52 | 49.938
2021-01-16 | 11:52 | 49.937
2021-01-16 | 11:52 | 49.934
2021-01-16 | 11:52 | 49.935
2021-01-16 | 11:52 | 49.937
2021-01-16 | 11:52 | 49.937
2021-01-16 | 11:52 | 49.937
2021-01-16 | 11:52 | 49.937
2021-01-16 | 11:52 | 49.938
2021-01-16 | 11:52 | 49.941
2021-01-16 | 11:52 | 49.944
2021-01-16 | 11:52 | 49.947
2021-01-16 | 11:52 | 49.948
2021-01-16 | 11:52 | 49.949
2021-01-16 | 11:52 | 49.951
2021-01-16 | 11:52 | 49.952
2021-01-16 | 11:52 | 49.953
2021-01-16 | 11:52 | 49.95
2021-01-16 | 11:52 | 49.947
2021-01-16 | 11:52 | 49.947
2021-01-16 | 11:52 | 49.946
2021-01-16 | 11:52 | 49.946
2021-01-16 | 11:52 | 49.943
2021-01-16 | 11:52 | 49.938
2021-01-16 | 11:52 | 49.931
2021-01-16 | 11:52 | 49.925
2021-01-16 | 11:52 | 49.918
2021-01-16 | 11:52 | 49.913
2021-01-16 | 11:52 | 49.908
2021-01-16 | 11:52 | 49.902
2021-01-16 | 11:52 | 49.895
2021-01-16 | 11:52 | 49.891
2021-01-16 | 11:52 | 49.891
2021-01-16 | 11:52 | 49.892
2021-01-16 | 11:52 | 49.892
2021-01-16 | 11:52 | 49.893
2021-01-16 | 11:52 | 49.893
2021-01-16 | 11:52 | 49.893
2021-01-16 | 11:52 | 49.896
2021-01-16 | 11:52 | 49.896
2021-01-16 | 11:52 | 49.895
2021-01-16 | 11:52 | 49.893
2021-01-16 | 11:52 | 49.893
2021-01-16 | 11:52 | 49.892
2021-01-16 | 11:52 | 49.894
2021-01-16 | 11:52 | 49.896
2021-01-16 | 11:52 | 49.896
2021-01-16 | 11:52 | 49.896
2021-01-16 | 11:52 | 49.894
2021-01-16 | 11:52 | 49.895
2021-01-16 | 11:52 | 49.897
2021-01-16 | 11:52 | 49.9
2021-01-16 | 11:52 | 49.9
2021-01-16 | 11:52 | 49.9
2021-01-16 | 11:52 | 49.9
2021-01-16 | 11:52 | 49.898
2021-01-16 | 11:52 | 49.9
2021-01-16 | 11:52 | 49.902
2021-01-16 | 11:52 | 49.904
2021-01-16 | 11:52 | 49.909
2021-01-16 | 11:53 | 49.909
2021-01-16 | 11:53 | 49.912
2021-01-16 | 11:53 | 49.912
2021-01-16 | 11:53 | 49.917
2021-01-16 | 11:53 | 49.917
2021-01-16 | 11:53 | 49.921
2021-01-16 | 11:53 | 49.922
2021-01-16 | 11:53 | 49.926
2021-01-16 | 11:53 | 49.928
2021-01-16 | 11:53 | 49.931
2021-01-16 | 11:53 | 49.934
2021-01-16 | 11:53 | 49.936
2021-01-16 | 11:53 | 49.938
2021-01-16 | 11:53 | 49.938
2021-01-16 | 11:53 | 49.937
2021-01-16 | 11:53 | 49.934
2021-01-16 | 11:53 | 49.933
2021-01-16 | 11:53 | 49.932
2021-01-16 | 11:53 | 49.934
2021-01-16 | 11:53 | 49.933
2021-01-16 | 11:53 | 49.932
2021-01-16 | 11:53 | 49.929
2021-01-16 | 11:53 | 49.928
2021-01-16 | 11:53 | 49.927
2021-01-16 | 11:53 | 49.924
2021-01-16 | 11:53 | 49.924
2021-01-16 | 11:53 | 49.921
2021-01-16 | 11:53 | 49.921
2021-01-16 | 11:53 | 49.918
2021-01-16 | 11:53 | 49.917
2021-01-16 | 11:53 | 49.915
2021-01-16 | 11:53 | 49.911
2021-01-16 | 11:53 | 49.911
2021-01-16 | 11:53 | 49.91
2021-01-16 | 11:53 | 49.913
2021-01-16 | 11:53 | 49.915
2021-01-16 | 11:53 | 49.918
2021-01-16 | 11:53 | 49.919
2021-01-16 | 11:53 | 49.921
2021-01-16 | 11:53 | 49.92
2021-01-16 | 11:53 | 49.921
2021-01-16 | 11:53 | 49.921
2021-01-16 | 11:53 | 49.922
2021-01-16 | 11:53 | 49.92
2021-01-16 | 11:53 | 49.919
2021-01-16 | 11:53 | 49.918
2021-01-16 | 11:53 | 49.916
2021-01-16 | 11:53 | 49.916
2021-01-16 | 11:53 | 49.916
2021-01-16 | 11:53 | 49.917
2021-01-16 | 11:53 | 49.914
2021-01-16 | 11:53 | 49.914
2021-01-16 | 11:53 | 49.914
2021-01-16 | 11:53 | 49.913
2021-01-16 | 11:53 | 49.914
2021-01-16 | 11:53 | 49.915
2021-01-16 | 11:53 | 49.917
2021-01-16 | 11:53 | 49.917
2021-01-16 | 11:53 | 49.919
2021-01-16 | 11:54 | 49.918
2021-01-16 | 11:54 | 49.92
2021-01-16 | 11:54 | 49.922
2021-01-16 | 11:54 | 49.925
2021-01-16 | 11:54 | 49.926
2021-01-16 | 11:54 | 49.927
2021-01-16 | 11:54 | 49.929
2021-01-16 | 11:54 | 49.93
2021-01-16 | 11:54 | 49.93
2021-01-16 | 11:54 | 49.93
2021-01-16 | 11:54 | 49.932
2021-01-16 | 11:54 | 49.93
2021-01-16 | 11:54 | 49.932
2021-01-16 | 11:54 | 49.935
2021-01-16 | 11:54 | 49.937
2021-01-16 | 11:54 | 49.938
2021-01-16 | 11:54 | 49.938
2021-01-16 | 11:54 | 49.938
2021-01-16 | 11:54 | 49.936
2021-01-16 | 11:54 | 49.936
2021-01-16 | 11:54 | 49.932
2021-01-16 | 11:54 | 49.931
2021-01-16 | 11:54 | 49.929
2021-01-16 | 11:54 | 49.928
2021-01-16 | 11:54 | 49.927
2021-01-16 | 11:54 | 49.927
2021-01-16 | 11:54 | 49.929
2021-01-16 | 11:54 | 49.929
2021-01-16 | 11:54 | 49.929
2021-01-16 | 11:54 | 49.927
2021-01-16 | 11:54 | 49.929
2021-01-16 | 11:54 | 49.928
2021-01-16 | 11:54 | 49.927
2021-01-16 | 11:54 | 49.928
2021-01-16 | 11:54 | 49.926
2021-01-16 | 11:54 | 49.927
2021-01-16 | 11:54 | 49.926
2021-01-16 | 11:54 | 49.929
2021-01-16 | 11:54 | 49.928
2021-01-16 | 11:54 | 49.93
2021-01-16 | 11:54 | 49.933
2021-01-16 | 11:54 | 49.934
2021-01-16 | 11:54 | 49.936
2021-01-16 | 11:54 | 49.937
2021-01-16 | 11:54 | 49.937
2021-01-16 | 11:54 | 49.939
2021-01-16 | 11:54 | 49.941
2021-01-16 | 11:54 | 49.943
2021-01-16 | 11:54 | 49.945
2021-01-16 | 11:54 | 49.947
2021-01-16 | 11:54 | 49.951
2021-01-16 | 11:54 | 49.952
2021-01-16 | 11:54 | 49.953
2021-01-16 | 11:54 | 49.95
2021-01-16 | 11:54 | 49.946
2021-01-16 | 11:54 | 49.944
2021-01-16 | 11:54 | 49.944
2021-01-16 | 11:54 | 49.946
2021-01-16 | 11:54 | 49.949
2021-01-16 | 11:54 | 49.946
2021-01-16 | 11:54 | 49.943
2021-01-16 | 11:55 | 49.941
2021-01-16 | 11:55 | 49.938
2021-01-16 | 11:55 | 49.936
2021-01-16 | 11:55 | 49.937
2021-01-16 | 11:55 | 49.939
2021-01-16 | 11:55 | 49.939
2021-01-16 | 11:55 | 49.939
2021-01-16 | 11:55 | 49.941
2021-01-16 | 11:55 | 49.944
2021-01-16 | 11:55 | 49.946
2021-01-16 | 11:55 | 49.95
2021-01-16 | 11:55 | 49.952
2021-01-16 | 11:55 | 49.953
2021-01-16 | 11:55 | 49.952
2021-01-16 | 11:55 | 49.952
2021-01-16 | 11:55 | 49.95
2021-01-16 | 11:55 | 49.95
2021-01-16 | 11:55 | 49.95
2021-01-16 | 11:55 | 49.951
2021-01-16 | 11:55 | 49.955
2021-01-16 | 11:55 | 49.956
2021-01-16 | 11:55 | 49.96
2021-01-16 | 11:55 | 49.961
2021-01-16 | 11:55 | 49.961
2021-01-16 | 11:55 | 49.962
2021-01-16 | 11:55 | 49.957
2021-01-16 | 11:55 | 49.956
2021-01-16 | 11:55 | 49.953
2021-01-16 | 11:55 | 49.951
2021-01-16 | 11:55 | 49.951
2021-01-16 | 11:55 | 49.95
2021-01-16 | 11:55 | 49.95
2021-01-16 | 11:55 | 49.95
2021-01-16 | 11:55 | 49.951
2021-01-16 | 11:55 | 49.952
2021-01-16 | 11:55 | 49.954
2021-01-16 | 11:55 | 49.957
2021-01-16 | 11:55 | 49.959
2021-01-16 | 11:55 | 49.961
2021-01-16 | 11:55 | 49.959
2021-01-16 | 11:55 | 49.957
2021-01-16 | 11:55 | 49.955
2021-01-16 | 11:55 | 49.957
2021-01-16 | 11:55 | 49.958
2021-01-16 | 11:55 | 49.959
2021-01-16 | 11:55 | 49.959
2021-01-16 | 11:55 | 49.957
2021-01-16 | 11:55 | 49.959
2021-01-16 | 11:55 | 49.957
2021-01-16 | 11:55 | 49.959
2021-01-16 | 11:55 | 49.96
2021-01-16 | 11:55 | 49.963
2021-01-16 | 11:55 | 49.967
2021-01-16 | 11:55 | 49.97
2021-01-16 | 11:55 | 49.972
2021-01-16 | 11:55 | 49.971
2021-01-16 | 11:55 | 49.972
2021-01-16 | 11:55 | 49.97
2021-01-16 | 11:55 | 49.969
2021-01-16 | 11:56 | 49.968
2021-01-16 | 11:56 | 49.966
2021-01-16 | 11:56 | 49.966
2021-01-16 | 11:56 | 49.966
2021-01-16 | 11:56 | 49.968
2021-01-16 | 11:56 | 49.97
2021-01-16 | 11:56 | 49.97
2021-01-16 | 11:56 | 49.967
2021-01-16 | 11:56 | 49.967
2021-01-16 | 11:56 | 49.965
2021-01-16 | 11:56 | 49.965
2021-01-16 | 11:56 | 49.962
2021-01-16 | 11:56 | 49.96
2021-01-16 | 11:56 | 49.953
2021-01-16 | 11:56 | 49.951
2021-01-16 | 11:56 | 49.951
2021-01-16 | 11:56 | 49.95
2021-01-16 | 11:56 | 49.952
2021-01-16 | 11:56 | 49.954
2021-01-16 | 11:56 | 49.956
2021-01-16 | 11:56 | 49.959
2021-01-16 | 11:56 | 49.961
2021-01-16 | 11:56 | 49.963
2021-01-16 | 11:56 | 49.967
2021-01-16 | 11:56 | 49.969
2021-01-16 | 11:56 | 49.971
2021-01-16 | 11:56 | 49.973
2021-01-16 | 11:56 | 49.973
2021-01-16 | 11:56 | 49.977
2021-01-16 | 11:56 | 49.975
2021-01-16 | 11:56 | 49.974
2021-01-16 | 11:56 | 49.97
2021-01-16 | 11:56 | 49.968
2021-01-16 | 11:56 | 49.966
2021-01-16 | 11:56 | 49.967
2021-01-16 | 11:56 | 49.964
2021-01-16 | 11:56 | 49.964
2021-01-16 | 11:56 | 49.961
2021-01-16 | 11:56 | 49.963
2021-01-16 | 11:56 | 49.961
2021-01-16 | 11:56 | 49.963
2021-01-16 | 11:56 | 49.962
2021-01-16 | 11:56 | 49.963
2021-01-16 | 11:56 | 49.963
2021-01-16 | 11:56 | 49.963
2021-01-16 | 11:56 | 49.965
2021-01-16 | 11:56 | 49.965
2021-01-16 | 11:56 | 49.966
2021-01-16 | 11:56 | 49.963
2021-01-16 | 11:56 | 49.961
2021-01-16 | 11:56 | 49.956
2021-01-16 | 11:56 | 49.957
2021-01-16 | 11:56 | 49.957
2021-01-16 | 11:56 | 49.962
2021-01-16 | 11:56 | 49.964
2021-01-16 | 11:56 | 49.967
2021-01-16 | 11:56 | 49.97
2021-01-16 | 11:56 | 49.971
2021-01-16 | 11:56 | 49.973
2021-01-16 | 11:56 | 49.972
2021-01-16 | 11:56 | 49.971
2021-01-16 | 11:57 | 49.97
2021-01-16 | 11:57 | 49.971
2021-01-16 | 11:57 | 49.971
2021-01-16 | 11:57 | 49.973
2021-01-16 | 11:57 | 49.972
2021-01-16 | 11:57 | 49.972
2021-01-16 | 11:57 | 49.97
2021-01-16 | 11:57 | 49.969
2021-01-16 | 11:57 | 49.969
2021-01-16 | 11:57 | 49.97
2021-01-16 | 11:57 | 49.972
2021-01-16 | 11:57 | 49.973
2021-01-16 | 11:57 | 49.974
2021-01-16 | 11:57 | 49.974
2021-01-16 | 11:57 | 49.973
2021-01-16 | 11:57 | 49.973
2021-01-16 | 11:57 | 49.972
2021-01-16 | 11:57 | 49.97
2021-01-16 | 11:57 | 49.967
2021-01-16 | 11:57 | 49.966
2021-01-16 | 11:57 | 49.964
2021-01-16 | 11:57 | 49.964
2021-01-16 | 11:57 | 49.964
2021-01-16 | 11:57 | 49.965
2021-01-16 | 11:57 | 49.969
2021-01-16 | 11:57 | 49.975
2021-01-16 | 11:57 | 49.98
2021-01-16 | 11:57 | 49.984
2021-01-16 | 11:57 | 49.987
2021-01-16 | 11:57 | 49.989
2021-01-16 | 11:57 | 49.992
2021-01-16 | 11:57 | 49.992
2021-01-16 | 11:57 | 49.992
2021-01-16 | 11:57 | 49.992
2021-01-16 | 11:57 | 49.994
2021-01-16 | 11:57 | 49.996
2021-01-16 | 11:57 | 49.997
2021-01-16 | 11:57 | 49.998
2021-01-16 | 11:57 | 49.998
2021-01-16 | 11:57 | 50.002
2021-01-16 | 11:57 | 50.003
2021-01-16 | 11:57 | 50.008
2021-01-16 | 11:57 | 50.009
2021-01-16 | 11:57 | 50.008
2021-01-16 | 11:57 | 50.007
2021-01-16 | 11:57 | 50.008
2021-01-16 | 11:57 | 50.01
2021-01-16 | 11:57 | 50.01
2021-01-16 | 11:57 | 50.013
2021-01-16 | 11:57 | 50.014
2021-01-16 | 11:57 | 50.015
2021-01-16 | 11:57 | 50.016
2021-01-16 | 11:57 | 50.016
2021-01-16 | 11:57 | 50.019
2021-01-16 | 11:57 | 50.02
2021-01-16 | 11:57 | 50.022
2021-01-16 | 11:57 | 50.023
2021-01-16 | 11:57 | 50.022
2021-01-16 | 11:57 | 50.02
2021-01-16 | 11:58 | 50.017
2021-01-16 | 11:58 | 50.016
2021-01-16 | 11:58 | 50.015
2021-01-16 | 11:58 | 50.015
2021-01-16 | 11:58 | 50.015
2021-01-16 | 11:58 | 50.016
2021-01-16 | 11:58 | 50.02
2021-01-16 | 11:58 | 50.02
2021-01-16 | 11:58 | 50.02
2021-01-16 | 11:58 | 50.017
2021-01-16 | 11:58 | 50.017
2021-01-16 | 11:58 | 50.015
2021-01-16 | 11:58 | 50.012
2021-01-16 | 11:58 | 50.01
2021-01-16 | 11:58 | 50.008
2021-01-16 | 11:58 | 50.007
2021-01-16 | 11:58 | 50.006
2021-01-16 | 11:58 | 50.005
2021-01-16 | 11:58 | 50.005
2021-01-16 | 11:58 | 50.006
2021-01-16 | 11:58 | 50.003
2021-01-16 | 11:58 | 50.004
2021-01-16 | 11:58 | 50.004
2021-01-16 | 11:58 | 50.008
2021-01-16 | 11:58 | 50.01
2021-01-16 | 11:58 | 50.016
2021-01-16 | 11:58 | 50.02
2021-01-16 | 11:58 | 50.022
2021-01-16 | 11:58 | 50.024
2021-01-16 | 11:58 | 50.026
2021-01-16 | 11:58 | 50.027
2021-01-16 | 11:58 | 50.029
2021-01-16 | 11:58 | 50.029
2021-01-16 | 11:58 | 50.026
2021-01-16 | 11:58 | 50.024
2021-01-16 | 11:58 | 50.023
2021-01-16 | 11:58 | 50.022
2021-01-16 | 11:58 | 50.023
2021-01-16 | 11:58 | 50.027
2021-01-16 | 11:58 | 50.03
2021-01-16 | 11:58 | 50.031
2021-01-16 | 11:58 | 50.031
2021-01-16 | 11:58 | 50.031
2021-01-16 | 11:58 | 50.029
2021-01-16 | 11:58 | 50.026
2021-01-16 | 11:58 | 50.023
2021-01-16 | 11:58 | 50.019
2021-01-16 | 11:58 | 50.017
2021-01-16 | 11:58 | 50.014
2021-01-16 | 11:58 | 50.014
2021-01-16 | 11:58 | 50.013
2021-01-16 | 11:58 | 50.016
2021-01-16 | 11:58 | 50.02
2021-01-16 | 11:58 | 50.023
2021-01-16 | 11:58 | 50.027
2021-01-16 | 11:58 | 50.026
2021-01-16 | 11:58 | 50.029
2021-01-16 | 11:58 | 50.029
2021-01-16 | 11:58 | 50.027
2021-01-16 | 11:58 | 50.027
2021-01-16 | 11:58 | 50.027
2021-01-16 | 11:59 | 50.026
2021-01-16 | 11:59 | 50.023
2021-01-16 | 11:59 | 50.023
2021-01-16 | 11:59 | 50.023
2021-01-16 | 11:59 | 50.022
2021-01-16 | 11:59 | 50.024
2021-01-16 | 11:59 | 50.024
2021-01-16 | 11:59 | 50.025
2021-01-16 | 11:59 | 50.026
2021-01-16 | 11:59 | 50.03
2021-01-16 | 11:59 | 50.03
2021-01-16 | 11:59 | 50.033
2021-01-16 | 11:59 | 50.029
2021-01-16 | 11:59 | 50.026
2021-01-16 | 11:59 | 50.023
2021-01-16 | 11:59 | 50.021
2021-01-16 | 11:59 | 50.018
2021-01-16 | 11:59 | 50.015
2021-01-16 | 11:59 | 50.013
2021-01-16 | 11:59 | 50.009
2021-01-16 | 11:59 | 50.007
2021-01-16 | 11:59 | 50.004
2021-01-16 | 11:59 | 50.002
2021-01-16 | 11:59 | 49.998
2021-01-16 | 11:59 | 49.996
2021-01-16 | 11:59 | 49.993
2021-01-16 | 11:59 | 49.988
2021-01-16 | 11:59 | 49.986
2021-01-16 | 11:59 | 49.981
2021-01-16 | 11:59 | 49.981
2021-01-16 | 11:59 | 49.98
2021-01-16 | 11:59 | 49.98
2021-01-16 | 11:59 | 49.978
2021-01-16 | 11:59 | 49.976
2021-01-16 | 11:59 | 49.975
2021-01-16 | 11:59 | 49.974
2021-01-16 | 11:59 | 49.974
2021-01-16 | 11:59 | 49.971
2021-01-16 | 11:59 | 49.971
2021-01-16 | 11:59 | 49.97
2021-01-16 | 11:59 | 49.969
2021-01-16 | 11:59 | 49.97
2021-01-16 | 11:59 | 49.971
2021-01-16 | 11:59 | 49.974
2021-01-16 | 11:59 | 49.974
2021-01-16 | 11:59 | 49.977
2021-01-16 | 11:59 | 49.976
2021-01-16 | 11:59 | 49.976
2021-01-16 | 11:59 | 49.975
2021-01-16 | 11:59 | 49.976
2021-01-16 | 11:59 | 49.973
2021-01-16 | 11:59 | 49.974
2021-01-16 | 11:59 | 49.976
2021-01-16 | 11:59 | 49.978
2021-01-16 | 11:59 | 49.98
2021-01-16 | 11:59 | 49.98
2021-01-16 | 11:59 | 49.983
2021-01-16 | 11:59 | 49.983
2021-01-16 | 11:59 | 49.987
2021-01-16 | 12:00 | 49.988
2021-01-16 | 12:00 | 49.99
2021-01-16 | 12:00 | 49.989
2021-01-16 | 12:00 | 49.986
2021-01-16 | 12:00 | 49.987
2021-01-16 | 12:00 | 49.984
2021-01-16 | 12:00 | 49.983
2021-01-16 | 12:00 | 49.984
2021-01-16 | 12:00 | 49.987
2021-01-16 | 12:00 | 49.987
2021-01-16 | 12:00 | 49.985
2021-01-16 | 12:00 | 49.985
2021-01-16 | 12:00 | 49.985
2021-01-16 | 12:00 | 49.987
2021-01-16 | 12:00 | 49.987
2021-01-16 | 12:00 | 49.989
2021-01-16 | 12:00 | 49.992
2021-01-16 | 12:00 | 49.993
2021-01-16 | 12:00 | 49.996
2021-01-16 | 12:00 | 49.996
2021-01-16 | 12:00 | 49.999
2021-01-16 | 12:00 | 49.998
2021-01-16 | 12:00 | 49.999
2021-01-16 | 12:00 | 49.998
2021-01-16 | 12:00 | 49.997
2021-01-16 | 12:00 | 49.995
2021-01-16 | 12:00 | 49.991
2021-01-16 | 12:00 | 49.988
2021-01-16 | 12:00 | 49.983
2021-01-16 | 12:00 | 49.979
2021-01-16 | 12:00 | 49.974
2021-01-16 | 12:00 | 49.971
2021-01-16 | 12:00 | 49.964
2021-01-16 | 12:00 | 49.961
2021-01-16 | 12:00 | 49.958
2021-01-16 | 12:00 | 49.957
2021-01-16 | 12:00 | 49.955
2021-01-16 | 12:00 | 49.954
2021-01-16 | 12:00 | 49.955
2021-01-16 | 12:00 | 49.957
2021-01-16 | 12:00 | 49.959
2021-01-16 | 12:00 | 49.96
2021-01-16 | 12:00 | 49.958
2021-01-16 | 12:00 | 49.959
2021-01-16 | 12:00 | 49.959
2021-01-16 | 12:00 | 49.959
2021-01-16 | 12:00 | 49.958
2021-01-16 | 12:00 | 49.954
2021-01-16 | 12:00 | 49.953
2021-01-16 | 12:00 | 49.949
2021-01-16 | 12:00 | 49.95
2021-01-16 | 12:00 | 49.948
2021-01-16 | 12:00 | 49.95
2021-01-16 | 12:00 | 49.948
2021-01-16 | 12:00 | 49.949
2021-01-16 | 12:00 | 49.949
2021-01-16 | 12:00 | 49.954
2021-01-16 | 12:00 | 49.955
2021-01-16 | 12:00 | 49.955
2021-01-16 | 12:00 | 49.953
2021-01-16 | 12:00 | 49.95
2021-01-16 | 12:01 | 49.949
2021-01-16 | 12:01 | 49.947
2021-01-16 | 12:01 | 49.948
2021-01-16 | 12:01 | 49.947
2021-01-16 | 12:01 | 49.946
2021-01-16 | 12:01 | 49.945
2021-01-16 | 12:01 | 49.943
2021-01-16 | 12:01 | 49.945
2021-01-16 | 12:01 | 49.945
2021-01-16 | 12:01 | 49.948
2021-01-16 | 12:01 | 49.948
2021-01-16 | 12:01 | 49.949
2021-01-16 | 12:01 | 49.948
2021-01-16 | 12:01 | 49.947
2021-01-16 | 12:01 | 49.947
2021-01-16 | 12:01 | 49.947
2021-01-16 | 12:01 | 49.951
2021-01-16 | 12:01 | 49.953
2021-01-16 | 12:01 | 49.953
2021-01-16 | 12:01 | 49.95
2021-01-16 | 12:01 | 49.946
2021-01-16 | 12:01 | 49.945
2021-01-16 | 12:01 | 49.943
2021-01-16 | 12:01 | 49.943
2021-01-16 | 12:01 | 49.941
2021-01-16 | 12:01 | 49.94
2021-01-16 | 12:01 | 49.94
2021-01-16 | 12:01 | 49.941
2021-01-16 | 12:01 | 49.944
2021-01-16 | 12:01 | 49.942
2021-01-16 | 12:01 | 49.941
2021-01-16 | 12:01 | 49.939
2021-01-16 | 12:01 | 49.939
2021-01-16 | 12:01 | 49.938
2021-01-16 | 12:01 | 49.937
2021-01-16 | 12:01 | 49.934
2021-01-16 | 12:01 | 49.931
2021-01-16 | 12:01 | 49.928
2021-01-16 | 12:01 | 49.922
2021-01-16 | 12:01 | 49.922
2021-01-16 | 12:01 | 49.92
2021-01-16 | 12:01 | 49.921
2021-01-16 | 12:01 | 49.922
2021-01-16 | 12:01 | 49.928
2021-01-16 | 12:01 | 49.928
2021-01-16 | 12:01 | 49.932
2021-01-16 | 12:01 | 49.934
2021-01-16 | 12:01 | 49.938
2021-01-16 | 12:01 | 49.939
2021-01-16 | 12:01 | 49.942
2021-01-16 | 12:01 | 49.944
2021-01-16 | 12:01 | 49.948
2021-01-16 | 12:01 | 49.948
2021-01-16 | 12:01 | 49.947
2021-01-16 | 12:01 | 49.946
2021-01-16 | 12:01 | 49.944
2021-01-16 | 12:01 | 49.943
2021-01-16 | 12:01 | 49.943
2021-01-16 | 12:01 | 49.941
2021-01-16 | 12:02 | 49.939
2021-01-16 | 12:02 | 49.94
2021-01-16 | 12:02 | 49.94
2021-01-16 | 12:02 | 49.94
2021-01-16 | 12:02 | 49.94
2021-01-16 | 12:02 | 49.944
2021-01-16 | 12:02 | 49.947
2021-01-16 | 12:02 | 49.951
2021-01-16 | 12:02 | 49.953
2021-01-16 | 12:02 | 49.954
2021-01-16 | 12:02 | 49.954
2021-01-16 | 12:02 | 49.955
2021-01-16 | 12:02 | 49.952
2021-01-16 | 12:02 | 49.952
2021-01-16 | 12:02 | 49.949
2021-01-16 | 12:02 | 49.948
2021-01-16 | 12:02 | 49.945
2021-01-16 | 12:02 | 49.945
2021-01-16 | 12:02 | 49.945
2021-01-16 | 12:02 | 49.947
2021-01-16 | 12:02 | 49.949
2021-01-16 | 12:02 | 49.951
2021-01-16 | 12:02 | 49.951
2021-01-16 | 12:02 | 49.951
2021-01-16 | 12:02 | 49.951
2021-01-16 | 12:02 | 49.949
2021-01-16 | 12:02 | 49.95
2021-01-16 | 12:02 | 49.948
2021-01-16 | 12:02 | 49.949
2021-01-16 | 12:02 | 49.948
2021-01-16 | 12:02 | 49.948
2021-01-16 | 12:02 | 49.945
2021-01-16 | 12:02 | 49.942
2021-01-16 | 12:02 | 49.939
2021-01-16 | 12:02 | 49.938
2021-01-16 | 12:02 | 49.938
2021-01-16 | 12:02 | 49.935
2021-01-16 | 12:02 | 49.936
2021-01-16 | 12:02 | 49.935
2021-01-16 | 12:02 | 49.937
2021-01-16 | 12:02 | 49.935
2021-01-16 | 12:02 | 49.934
2021-01-16 | 12:02 | 49.93
2021-01-16 | 12:02 | 49.929
2021-01-16 | 12:02 | 49.929
2021-01-16 | 12:02 | 49.93
2021-01-16 | 12:02 | 49.93
2021-01-16 | 12:02 | 49.931
2021-01-16 | 12:02 | 49.93
2021-01-16 | 12:02 | 49.928
2021-01-16 | 12:02 | 49.931
2021-01-16 | 12:02 | 49.933
2021-01-16 | 12:02 | 49.936
2021-01-16 | 12:02 | 49.935
2021-01-16 | 12:02 | 49.938
2021-01-16 | 12:02 | 49.94
2021-01-16 | 12:02 | 49.941
2021-01-16 | 12:02 | 49.94
2021-01-16 | 12:02 | 49.939
2021-01-16 | 12:02 | 49.937
2021-01-16 | 12:02 | 49.935
2021-01-16 | 12:03 | 49.936
2021-01-16 | 12:03 | 49.935
2021-01-16 | 12:03 | 49.937
2021-01-16 | 12:03 | 49.937
2021-01-16 | 12:03 | 49.94
2021-01-16 | 12:03 | 49.943
2021-01-16 | 12:03 | 49.947
2021-01-16 | 12:03 | 49.948
2021-01-16 | 12:03 | 49.951
2021-01-16 | 12:03 | 49.951
2021-01-16 | 12:03 | 49.952
2021-01-16 | 12:03 | 49.95
2021-01-16 | 12:03 | 49.953
2021-01-16 | 12:03 | 49.951
2021-01-16 | 12:03 | 49.95
2021-01-16 | 12:03 | 49.946
2021-01-16 | 12:03 | 49.946
2021-01-16 | 12:03 | 49.944
2021-01-16 | 12:03 | 49.941
2021-01-16 | 12:03 | 49.942
2021-01-16 | 12:03 | 49.942
2021-01-16 | 12:03 | 49.941
2021-01-16 | 12:03 | 49.941
2021-01-16 | 12:03 | 49.943
2021-01-16 | 12:03 | 49.945
2021-01-16 | 12:03 | 49.946
2021-01-16 | 12:03 | 49.945
2021-01-16 | 12:03 | 49.945
2021-01-16 | 12:03 | 49.941
2021-01-16 | 12:03 | 49.939
2021-01-16 | 12:03 | 49.934
2021-01-16 | 12:03 | 49.931
2021-01-16 | 12:03 | 49.926
2021-01-16 | 12:03 | 49.923
2021-01-16 | 12:03 | 49.919
2021-01-16 | 12:03 | 49.916
2021-01-16 | 12:03 | 49.917
2021-01-16 | 12:03 | 49.918
2021-01-16 | 12:03 | 49.919
2021-01-16 | 12:03 | 49.918
2021-01-16 | 12:03 | 49.919
2021-01-16 | 12:03 | 49.919
2021-01-16 | 12:03 | 49.917
2021-01-16 | 12:03 | 49.916
2021-01-16 | 12:03 | 49.913
2021-01-16 | 12:03 | 49.913
2021-01-16 | 12:03 | 49.908
2021-01-16 | 12:03 | 49.908
2021-01-16 | 12:03 | 49.907
2021-01-16 | 12:03 | 49.909
2021-01-16 | 12:03 | 49.907
2021-01-16 | 12:03 | 49.907
2021-01-16 | 12:03 | 49.907
2021-01-16 | 12:03 | 49.905
2021-01-16 | 12:03 | 49.905
2021-01-16 | 12:03 | 49.902
2021-01-16 | 12:03 | 49.901
2021-01-16 | 12:03 | 49.898
2021-01-16 | 12:03 | 49.897
2021-01-16 | 12:04 | 49.895
2021-01-16 | 12:04 | 49.896
2021-01-16 | 12:04 | 49.897
2021-01-16 | 12:04 | 49.903
2021-01-16 | 12:04 | 49.906
2021-01-16 | 12:04 | 49.911
2021-01-16 | 12:04 | 49.912
2021-01-16 | 12:04 | 49.914
2021-01-16 | 12:04 | 49.914
2021-01-16 | 12:04 | 49.913
2021-01-16 | 12:04 | 49.914
2021-01-16 | 12:04 | 49.913
2021-01-16 | 12:04 | 49.915
2021-01-16 | 12:04 | 49.915
2021-01-16 | 12:04 | 49.918
2021-01-16 | 12:04 | 49.918
2021-01-16 | 12:04 | 49.918
2021-01-16 | 12:04 | 49.915
2021-01-16 | 12:04 | 49.917
2021-01-16 | 12:04 | 49.918
2021-01-16 | 12:04 | 49.921
2021-01-16 | 12:04 | 49.924
2021-01-16 | 12:04 | 49.922
2021-01-16 | 12:04 | 49.925
2021-01-16 | 12:04 | 49.924
2021-01-16 | 12:04 | 49.922
2021-01-16 | 12:04 | 49.924
2021-01-16 | 12:04 | 49.923
2021-01-16 | 12:04 | 49.924
2021-01-16 | 12:04 | 49.925
2021-01-16 | 12:04 | 49.925
2021-01-16 | 12:04 | 49.926
2021-01-16 | 12:04 | 49.923
2021-01-16 | 12:04 | 49.922
2021-01-16 | 12:04 | 49.919
2021-01-16 | 12:04 | 49.922
2021-01-16 | 12:04 | 49.922
2021-01-16 | 12:04 | 49.926
2021-01-16 | 12:04 | 49.928
2021-01-16 | 12:04 | 49.931
2021-01-16 | 12:04 | 49.933
2021-01-16 | 12:04 | 49.934
2021-01-16 | 12:04 | 49.935
2021-01-16 | 12:04 | 49.937
2021-01-16 | 12:04 | 49.936
2021-01-16 | 12:04 | 49.937
2021-01-16 | 12:04 | 49.934
2021-01-16 | 12:04 | 49.933
2021-01-16 | 12:04 | 49.93
2021-01-16 | 12:04 | 49.925
2021-01-16 | 12:04 | 49.922
2021-01-16 | 12:04 | 49.921
2021-01-16 | 12:04 | 49.921
2021-01-16 | 12:04 | 49.922
2021-01-16 | 12:04 | 49.921
2021-01-16 | 12:04 | 49.922
2021-01-16 | 12:04 | 49.921
2021-01-16 | 12:04 | 49.921
2021-01-16 | 12:04 | 49.919
2021-01-16 | 12:04 | 49.919
2021-01-16 | 12:04 | 49.92
2021-01-16 | 12:05 | 49.92
2021-01-16 | 12:05 | 49.923
2021-01-16 | 12:05 | 49.924
2021-01-16 | 12:05 | 49.925
2021-01-16 | 12:05 | 49.926
2021-01-16 | 12:05 | 49.927
2021-01-16 | 12:05 | 49.927
2021-01-16 | 12:05 | 49.928
2021-01-16 | 12:05 | 49.927
2021-01-16 | 12:05 | 49.926
2021-01-16 | 12:05 | 49.926
2021-01-16 | 12:05 | 49.926
2021-01-16 | 12:05 | 49.925
2021-01-16 | 12:05 | 49.925
2021-01-16 | 12:05 | 49.923
2021-01-16 | 12:05 | 49.923
2021-01-16 | 12:05 | 49.92
2021-01-16 | 12:05 | 49.917
2021-01-16 | 12:05 | 49.914
2021-01-16 | 12:05 | 49.912
2021-01-16 | 12:05 | 49.912
2021-01-16 | 12:05 | 49.912
2021-01-16 | 12:05 | 49.91
2021-01-16 | 12:05 | 49.911
2021-01-16 | 12:05 | 49.913
2021-01-16 | 12:05 | 49.913
2021-01-16 | 12:05 | 49.914
2021-01-16 | 12:05 | 49.914
2021-01-16 | 12:05 | 49.912
2021-01-16 | 12:05 | 49.911
2021-01-16 | 12:05 | 49.907
2021-01-16 | 12:05 | 49.906
2021-01-16 | 12:05 | 49.903
2021-01-16 | 12:05 | 49.9
2021-01-16 | 12:05 | 49.899
2021-01-16 | 12:05 | 49.896
2021-01-16 | 12:05 | 49.893
2021-01-16 | 12:05 | 49.891
2021-01-16 | 12:05 | 49.892
2021-01-16 | 12:05 | 49.894
2021-01-16 | 12:05 | 49.894
2021-01-16 | 12:05 | 49.894
2021-01-16 | 12:05 | 49.893
2021-01-16 | 12:05 | 49.892
2021-01-16 | 12:05 | 49.89
2021-01-16 | 12:05 | 49.89
2021-01-16 | 12:05 | 49.89
2021-01-16 | 12:05 | 49.889
2021-01-16 | 12:05 | 49.887
2021-01-16 | 12:05 | 49.885
2021-01-16 | 12:05 | 49.885
2021-01-16 | 12:05 | 49.888
2021-01-16 | 12:05 | 49.89
2021-01-16 | 12:05 | 49.89
2021-01-16 | 12:05 | 49.891
2021-01-16 | 12:05 | 49.888
2021-01-16 | 12:05 | 49.891
2021-01-16 | 12:05 | 49.891
2021-01-16 | 12:05 | 49.893
2021-01-16 | 12:06 | 49.894
2021-01-16 | 12:06 | 49.895
2021-01-16 | 12:06 | 49.894
2021-01-16 | 12:06 | 49.894
2021-01-16 | 12:06 | 49.896
2021-01-16 | 12:06 | 49.899
2021-01-16 | 12:06 | 49.902
2021-01-16 | 12:06 | 49.903
2021-01-16 | 12:06 | 49.902
2021-01-16 | 12:06 | 49.9
2021-01-16 | 12:06 | 49.898
2021-01-16 | 12:06 | 49.897
2021-01-16 | 12:06 | 49.896
2021-01-16 | 12:06 | 49.897
2021-01-16 | 12:06 | 49.896
2021-01-16 | 12:06 | 49.898
2021-01-16 | 12:06 | 49.897
2021-01-16 | 12:06 | 49.898
2021-01-16 | 12:06 | 49.899
2021-01-16 | 12:06 | 49.9
2021-01-16 | 12:06 | 49.9
2021-01-16 | 12:06 | 49.901
2021-01-16 | 12:06 | 49.902
2021-01-16 | 12:06 | 49.9
2021-01-16 | 12:06 | 49.901
2021-01-16 | 12:06 | 49.903
2021-01-16 | 12:06 | 49.906
2021-01-16 | 12:06 | 49.908
2021-01-16 | 12:06 | 49.911
2021-01-16 | 12:06 | 49.911
2021-01-16 | 12:06 | 49.913
2021-01-16 | 12:06 | 49.911
2021-01-16 | 12:06 | 49.91
2021-01-16 | 12:06 | 49.91
2021-01-16 | 12:06 | 49.908
2021-01-16 | 12:06 | 49.908
2021-01-16 | 12:06 | 49.908
2021-01-16 | 12:06 | 49.906
2021-01-16 | 12:06 | 49.906
2021-01-16 | 12:06 | 49.902
2021-01-16 | 12:06 | 49.905
2021-01-16 | 12:06 | 49.903
2021-01-16 | 12:06 | 49.901
2021-01-16 | 12:06 | 49.904
2021-01-16 | 12:06 | 49.905
2021-01-16 | 12:06 | 49.906
2021-01-16 | 12:06 | 49.907
2021-01-16 | 12:06 | 49.906
2021-01-16 | 12:06 | 49.906
2021-01-16 | 12:06 | 49.905
2021-01-16 | 12:06 | 49.904
2021-01-16 | 12:06 | 49.906
2021-01-16 | 12:06 | 49.906
2021-01-16 | 12:06 | 49.905
2021-01-16 | 12:06 | 49.902
2021-01-16 | 12:06 | 49.901
2021-01-16 | 12:06 | 49.903
2021-01-16 | 12:06 | 49.907
2021-01-16 | 12:06 | 49.908
2021-01-16 | 12:06 | 49.912
2021-01-16 | 12:06 | 49.912
2021-01-16 | 12:07 | 49.91
2021-01-16 | 12:07 | 49.911
2021-01-16 | 12:07 | 49.91
2021-01-16 | 12:07 | 49.91
2021-01-16 | 12:07 | 49.907
2021-01-16 | 12:07 | 49.906
2021-01-16 | 12:07 | 49.906
2021-01-16 | 12:07 | 49.904
2021-01-16 | 12:07 | 49.902
2021-01-16 | 12:07 | 49.902
2021-01-16 | 12:07 | 49.899
2021-01-16 | 12:07 | 49.897
2021-01-16 | 12:07 | 49.896
2021-01-16 | 12:07 | 49.897
2021-01-16 | 12:07 | 49.898
2021-01-16 | 12:07 | 49.899
2021-01-16 | 12:07 | 49.899
2021-01-16 | 12:07 | 49.9
2021-01-16 | 12:07 | 49.901
2021-01-16 | 12:07 | 49.902
2021-01-16 | 12:07 | 49.902
2021-01-16 | 12:07 | 49.902
2021-01-16 | 12:07 | 49.903
2021-01-16 | 12:07 | 49.907
2021-01-16 | 12:07 | 49.908
2021-01-16 | 12:07 | 49.909
2021-01-16 | 12:07 | 49.906
2021-01-16 | 12:07 | 49.905
2021-01-16 | 12:07 | 49.904
2021-01-16 | 12:07 | 49.905
2021-01-16 | 12:07 | 49.906
2021-01-16 | 12:07 | 49.905
2021-01-16 | 12:07 | 49.905
2021-01-16 | 12:07 | 49.906
2021-01-16 | 12:07 | 49.905
2021-01-16 | 12:07 | 49.904
2021-01-16 | 12:07 | 49.904
2021-01-16 | 12:07 | 49.905
2021-01-16 | 12:07 | 49.904
2021-01-16 | 12:07 | 49.903
2021-01-16 | 12:07 | 49.903
2021-01-16 | 12:07 | 49.903
2021-01-16 | 12:07 | 49.903
2021-01-16 | 12:07 | 49.904
2021-01-16 | 12:07 | 49.905
2021-01-16 | 12:07 | 49.907
2021-01-16 | 12:07 | 49.909
2021-01-16 | 12:07 | 49.912
2021-01-16 | 12:07 | 49.914
2021-01-16 | 12:07 | 49.917
2021-01-16 | 12:07 | 49.917
2021-01-16 | 12:07 | 49.916
2021-01-16 | 12:07 | 49.914
2021-01-16 | 12:07 | 49.914
2021-01-16 | 12:07 | 49.911
2021-01-16 | 12:07 | 49.912
2021-01-16 | 12:07 | 49.912
2021-01-16 | 12:07 | 49.911
2021-01-16 | 12:07 | 49.912
2021-01-16 | 12:08 | 49.911
2021-01-16 | 12:08 | 49.911
2021-01-16 | 12:08 | 49.912
2021-01-16 | 12:08 | 49.911
2021-01-16 | 12:08 | 49.912
2021-01-16 | 12:08 | 49.914
2021-01-16 | 12:08 | 49.918
2021-01-16 | 12:08 | 49.919
2021-01-16 | 12:08 | 49.924
2021-01-16 | 12:08 | 49.925
2021-01-16 | 12:08 | 49.926
2021-01-16 | 12:08 | 49.925
2021-01-16 | 12:08 | 49.923
2021-01-16 | 12:08 | 49.919
2021-01-16 | 12:08 | 49.918
2021-01-16 | 12:08 | 49.915
2021-01-16 | 12:08 | 49.917
2021-01-16 | 12:08 | 49.918
2021-01-16 | 12:08 | 49.919
2021-01-16 | 12:08 | 49.92
2021-01-16 | 12:08 | 49.922
2021-01-16 | 12:08 | 49.922
2021-01-16 | 12:08 | 49.924
2021-01-16 | 12:08 | 49.923
2021-01-16 | 12:08 | 49.923
2021-01-16 | 12:08 | 49.923
2021-01-16 | 12:08 | 49.923
2021-01-16 | 12:08 | 49.922
2021-01-16 | 12:08 | 49.919
2021-01-16 | 12:08 | 49.916
2021-01-16 | 12:08 | 49.916
2021-01-16 | 12:08 | 49.918
2021-01-16 | 12:08 | 49.921
2021-01-16 | 12:08 | 49.923
2021-01-16 | 12:08 | 49.923
2021-01-16 | 12:08 | 49.921
2021-01-16 | 12:08 | 49.919
2021-01-16 | 12:08 | 49.915
2021-01-16 | 12:08 | 49.915
2021-01-16 | 12:08 | 49.914
2021-01-16 | 12:08 | 49.915
2021-01-16 | 12:08 | 49.914
2021-01-16 | 12:08 | 49.914
2021-01-16 | 12:08 | 49.913
2021-01-16 | 12:08 | 49.913
2021-01-16 | 12:08 | 49.913
2021-01-16 | 12:08 | 49.912
2021-01-16 | 12:08 | 49.911
2021-01-16 | 12:08 | 49.908
2021-01-16 | 12:08 | 49.908
2021-01-16 | 12:08 | 49.908
2021-01-16 | 12:08 | 49.909
2021-01-16 | 12:08 | 49.911
2021-01-16 | 12:08 | 49.913
2021-01-16 | 12:08 | 49.913
2021-01-16 | 12:08 | 49.913
2021-01-16 | 12:08 | 49.913
2021-01-16 | 12:08 | 49.912
2021-01-16 | 12:08 | 49.909
2021-01-16 | 12:08 | 49.908
2021-01-16 | 12:08 | 49.907
2021-01-16 | 12:09 | 49.906
2021-01-16 | 12:09 | 49.904
2021-01-16 | 12:09 | 49.903
2021-01-16 | 12:09 | 49.899
2021-01-16 | 12:09 | 49.896
2021-01-16 | 12:09 | 49.894
2021-01-16 | 12:09 | 49.891
2021-01-16 | 12:09 | 49.89
2021-01-16 | 12:09 | 49.891
2021-01-16 | 12:09 | 49.892
2021-01-16 | 12:09 | 49.892
2021-01-16 | 12:09 | 49.892
2021-01-16 | 12:09 | 49.892
2021-01-16 | 12:09 | 49.892
2021-01-16 | 12:09 | 49.891
2021-01-16 | 12:09 | 49.889
2021-01-16 | 12:09 | 49.888
2021-01-16 | 12:09 | 49.89
2021-01-16 | 12:09 | 49.89
2021-01-16 | 12:09 | 49.889
2021-01-16 | 12:09 | 49.892
2021-01-16 | 12:09 | 49.892
2021-01-16 | 12:09 | 49.891
2021-01-16 | 12:09 | 49.89
2021-01-16 | 12:09 | 49.889
2021-01-16 | 12:09 | 49.89
2021-01-16 | 12:09 | 49.891
2021-01-16 | 12:09 | 49.892
2021-01-16 | 12:09 | 49.892
2021-01-16 | 12:09 | 49.893
2021-01-16 | 12:09 | 49.892
2021-01-16 | 12:09 | 49.893
2021-01-16 | 12:09 | 49.893
2021-01-16 | 12:09 | 49.893
2021-01-16 | 12:09 | 49.892
2021-01-16 | 12:09 | 49.892
2021-01-16 | 12:09 | 49.891
2021-01-16 | 12:09 | 49.891
2021-01-16 | 12:09 | 49.891
2021-01-16 | 12:09 | 49.891
2021-01-16 | 12:09 | 49.891
2021-01-16 | 12:09 | 49.888
2021-01-16 | 12:09 | 49.892
2021-01-16 | 12:09 | 49.893
2021-01-16 | 12:09 | 49.895
2021-01-16 | 12:09 | 49.895
2021-01-16 | 12:09 | 49.895
2021-01-16 | 12:09 | 49.895
2021-01-16 | 12:09 | 49.896
2021-01-16 | 12:09 | 49.892
2021-01-16 | 12:09 | 49.891
2021-01-16 | 12:09 | 49.889
2021-01-16 | 12:09 | 49.887
2021-01-16 | 12:09 | 49.885
2021-01-16 | 12:09 | 49.885
2021-01-16 | 12:09 | 49.885
2021-01-16 | 12:09 | 49.885
2021-01-16 | 12:09 | 49.885
2021-01-16 | 12:09 | 49.886
2021-01-16 | 12:10 | 49.886
2021-01-16 | 12:10 | 49.887
2021-01-16 | 12:10 | 49.885
2021-01-16 | 12:10 | 49.888
2021-01-16 | 12:10 | 49.889
2021-01-16 | 12:10 | 49.888
2021-01-16 | 12:10 | 49.888
2021-01-16 | 12:10 | 49.888
2021-01-16 | 12:10 | 49.887
2021-01-16 | 12:10 | 49.886
2021-01-16 | 12:10 | 49.884
2021-01-16 | 12:10 | 49.885
2021-01-16 | 12:10 | 49.886
2021-01-16 | 12:10 | 49.89
2021-01-16 | 12:10 | 49.891
2021-01-16 | 12:10 | 49.893
2021-01-16 | 12:10 | 49.897
2021-01-16 | 12:10 | 49.898
2021-01-16 | 12:10 | 49.9
2021-01-16 | 12:10 | 49.899
2021-01-16 | 12:10 | 49.902
2021-01-16 | 12:10 | 49.905
2021-01-16 | 12:10 | 49.907
2021-01-16 | 12:10 | 49.909
2021-01-16 | 12:10 | 49.909
2021-01-16 | 12:10 | 49.91
2021-01-16 | 12:10 | 49.912
2021-01-16 | 12:10 | 49.912
2021-01-16 | 12:10 | 49.914
2021-01-16 | 12:10 | 49.913
2021-01-16 | 12:10 | 49.912
2021-01-16 | 12:10 | 49.911
2021-01-16 | 12:10 | 49.908
2021-01-16 | 12:10 | 49.908
2021-01-16 | 12:10 | 49.909
2021-01-16 | 12:10 | 49.912
2021-01-16 | 12:10 | 49.911
2021-01-16 | 12:10 | 49.909
2021-01-16 | 12:10 | 49.912
2021-01-16 | 12:10 | 49.91
2021-01-16 | 12:10 | 49.912
2021-01-16 | 12:10 | 49.911
2021-01-16 | 12:10 | 49.911
2021-01-16 | 12:10 | 49.912
2021-01-16 | 12:10 | 49.911
2021-01-16 | 12:10 | 49.912
2021-01-16 | 12:10 | 49.913
2021-01-16 | 12:10 | 49.916
2021-01-16 | 12:10 | 49.917
2021-01-16 | 12:10 | 49.917
2021-01-16 | 12:10 | 49.916
2021-01-16 | 12:10 | 49.914
2021-01-16 | 12:10 | 49.911
2021-01-16 | 12:10 | 49.909
2021-01-16 | 12:10 | 49.905
2021-01-16 | 12:10 | 49.902
2021-01-16 | 12:10 | 49.901
2021-01-16 | 12:10 | 49.901
2021-01-16 | 12:10 | 49.902
2021-01-16 | 12:10 | 49.906
2021-01-16 | 12:10 | 49.907
2021-01-16 | 12:11 | 49.909
2021-01-16 | 12:11 | 49.909
2021-01-16 | 12:11 | 49.908
2021-01-16 | 12:11 | 49.909
2021-01-16 | 12:11 | 49.909
2021-01-16 | 12:11 | 49.91
2021-01-16 | 12:11 | 49.912
2021-01-16 | 12:11 | 49.918
2021-01-16 | 12:11 | 49.921
2021-01-16 | 12:11 | 49.922
2021-01-16 | 12:11 | 49.921
2021-01-16 | 12:11 | 49.92
2021-01-16 | 12:11 | 49.918
2021-01-16 | 12:11 | 49.918
2021-01-16 | 12:11 | 49.917
2021-01-16 | 12:11 | 49.914
2021-01-16 | 12:11 | 49.913
2021-01-16 | 12:11 | 49.91
2021-01-16 | 12:11 | 49.91
2021-01-16 | 12:11 | 49.907
2021-01-16 | 12:11 | 49.907
2021-01-16 | 12:11 | 49.905
2021-01-16 | 12:11 | 49.906
2021-01-16 | 12:11 | 49.908
2021-01-16 | 12:11 | 49.912
2021-01-16 | 12:11 | 49.917
2021-01-16 | 12:11 | 49.919
2021-01-16 | 12:11 | 49.922
2021-01-16 | 12:11 | 49.924
2021-01-16 | 12:11 | 49.925
2021-01-16 | 12:11 | 49.924
2021-01-16 | 12:11 | 49.921
2021-01-16 | 12:11 | 49.919
2021-01-16 | 12:11 | 49.918
2021-01-16 | 12:11 | 49.919
2021-01-16 | 12:11 | 49.921
2021-01-16 | 12:11 | 49.923
2021-01-16 | 12:11 | 49.925
2021-01-16 | 12:11 | 49.927
2021-01-16 | 12:11 | 49.926
2021-01-16 | 12:11 | 49.926
2021-01-16 | 12:11 | 49.925
2021-01-16 | 12:11 | 49.925
2021-01-16 | 12:11 | 49.923
2021-01-16 | 12:11 | 49.925
2021-01-16 | 12:11 | 49.927
2021-01-16 | 12:11 | 49.928
2021-01-16 | 12:11 | 49.93
2021-01-16 | 12:11 | 49.93
2021-01-16 | 12:11 | 49.93
2021-01-16 | 12:11 | 49.929
2021-01-16 | 12:11 | 49.928
2021-01-16 | 12:11 | 49.93
2021-01-16 | 12:11 | 49.928
2021-01-16 | 12:11 | 49.928
2021-01-16 | 12:11 | 49.93
2021-01-16 | 12:11 | 49.933
2021-01-16 | 12:11 | 49.933
2021-01-16 | 12:11 | 49.935
2021-01-16 | 12:12 | 49.935
2021-01-16 | 12:12 | 49.934
2021-01-16 | 12:12 | 49.933
2021-01-16 | 12:12 | 49.934
2021-01-16 | 12:12 | 49.934
2021-01-16 | 12:12 | 49.933
2021-01-16 | 12:12 | 49.934
2021-01-16 | 12:12 | 49.933
2021-01-16 | 12:12 | 49.931
2021-01-16 | 12:12 | 49.93
2021-01-16 | 12:12 | 49.93
2021-01-16 | 12:12 | 49.929
2021-01-16 | 12:12 | 49.93
2021-01-16 | 12:12 | 49.93
2021-01-16 | 12:12 | 49.931
2021-01-16 | 12:12 | 49.931
2021-01-16 | 12:12 | 49.934
2021-01-16 | 12:12 | 49.936
2021-01-16 | 12:12 | 49.937
2021-01-16 | 12:12 | 49.938
2021-01-16 | 12:12 | 49.939
2021-01-16 | 12:12 | 49.938
2021-01-16 | 12:12 | 49.939
2021-01-16 | 12:12 | 49.938
2021-01-16 | 12:12 | 49.937
2021-01-16 | 12:12 | 49.937
2021-01-16 | 12:12 | 49.938
2021-01-16 | 12:12 | 49.94
2021-01-16 | 12:12 | 49.941
2021-01-16 | 12:12 | 49.941
2021-01-16 | 12:12 | 49.94
2021-01-16 | 12:12 | 49.94
2021-01-16 | 12:12 | 49.941
2021-01-16 | 12:12 | 49.939
2021-01-16 | 12:12 | 49.939
2021-01-16 | 12:12 | 49.939
2021-01-16 | 12:12 | 49.938
2021-01-16 | 12:12 | 49.936
2021-01-16 | 12:12 | 49.933
2021-01-16 | 12:12 | 49.929
2021-01-16 | 12:12 | 49.926
2021-01-16 | 12:12 | 49.923
2021-01-16 | 12:12 | 49.921
2021-01-16 | 12:12 | 49.92
2021-01-16 | 12:12 | 49.921
2021-01-16 | 12:12 | 49.921
2021-01-16 | 12:12 | 49.92
2021-01-16 | 12:12 | 49.918
2021-01-16 | 12:12 | 49.916
2021-01-16 | 12:12 | 49.913
2021-01-16 | 12:12 | 49.912
2021-01-16 | 12:12 | 49.912
2021-01-16 | 12:12 | 49.914
2021-01-16 | 12:12 | 49.915
2021-01-16 | 12:12 | 49.919
2021-01-16 | 12:12 | 49.919
2021-01-16 | 12:12 | 49.917
2021-01-16 | 12:12 | 49.914
2021-01-16 | 12:12 | 49.912
2021-01-16 | 12:12 | 49.91
2021-01-16 | 12:12 | 49.909
2021-01-16 | 12:13 | 49.907
2021-01-16 | 12:13 | 49.909
2021-01-16 | 12:13 | 49.911
2021-01-16 | 12:13 | 49.911
2021-01-16 | 12:13 | 49.913
2021-01-16 | 12:13 | 49.912
2021-01-16 | 12:13 | 49.912
2021-01-16 | 12:13 | 49.912
2021-01-16 | 12:13 | 49.914
2021-01-16 | 12:13 | 49.914
2021-01-16 | 12:13 | 49.913
2021-01-16 | 12:13 | 49.914
2021-01-16 | 12:13 | 49.912
2021-01-16 | 12:13 | 49.912
2021-01-16 | 12:13 | 49.911
2021-01-16 | 12:13 | 49.911
2021-01-16 | 12:13 | 49.909
2021-01-16 | 12:13 | 49.909
2021-01-16 | 12:13 | 49.91
2021-01-16 | 12:13 | 49.912
2021-01-16 | 12:13 | 49.913
2021-01-16 | 12:13 | 49.914
2021-01-16 | 12:13 | 49.917
2021-01-16 | 12:13 | 49.918
2021-01-16 | 12:13 | 49.916
2021-01-16 | 12:13 | 49.916
2021-01-16 | 12:13 | 49.915
2021-01-16 | 12:13 | 49.916
2021-01-16 | 12:13 | 49.915
2021-01-16 | 12:13 | 49.915
2021-01-16 | 12:13 | 49.913
2021-01-16 | 12:13 | 49.912
2021-01-16 | 12:13 | 49.914
2021-01-16 | 12:13 | 49.916
2021-01-16 | 12:13 | 49.918
2021-01-16 | 12:13 | 49.919
2021-01-16 | 12:13 | 49.921
2021-01-16 | 12:13 | 49.922
2021-01-16 | 12:13 | 49.921
2021-01-16 | 12:13 | 49.921
2021-01-16 | 12:13 | 49.919
2021-01-16 | 12:13 | 49.918
2021-01-16 | 12:13 | 49.915
2021-01-16 | 12:13 | 49.912
2021-01-16 | 12:13 | 49.911
2021-01-16 | 12:13 | 49.909
2021-01-16 | 12:13 | 49.907
2021-01-16 | 12:13 | 49.907
2021-01-16 | 12:13 | 49.906
2021-01-16 | 12:13 | 49.904
2021-01-16 | 12:13 | 49.903
2021-01-16 | 12:13 | 49.905
2021-01-16 | 12:13 | 49.902
2021-01-16 | 12:13 | 49.899
2021-01-16 | 12:13 | 49.896
2021-01-16 | 12:13 | 49.892
2021-01-16 | 12:13 | 49.892
2021-01-16 | 12:13 | 49.894
2021-01-16 | 12:13 | 49.894
2021-01-16 | 12:14 | 49.895
2021-01-16 | 12:14 | 49.897
2021-01-16 | 12:14 | 49.896
2021-01-16 | 12:14 | 49.901
2021-01-16 | 12:14 | 49.903
2021-01-16 | 12:14 | 49.907
2021-01-16 | 12:14 | 49.908
2021-01-16 | 12:14 | 49.91
2021-01-16 | 12:14 | 49.91
2021-01-16 | 12:14 | 49.912
2021-01-16 | 12:14 | 49.914
2021-01-16 | 12:14 | 49.918
2021-01-16 | 12:14 | 49.919
2021-01-16 | 12:14 | 49.92
2021-01-16 | 12:14 | 49.916
2021-01-16 | 12:14 | 49.916
2021-01-16 | 12:14 | 49.917
2021-01-16 | 12:14 | 49.916
2021-01-16 | 12:14 | 49.917
2021-01-16 | 12:14 | 49.915
2021-01-16 | 12:14 | 49.918
2021-01-16 | 12:14 | 49.919
2021-01-16 | 12:14 | 49.919
2021-01-16 | 12:14 | 49.92
2021-01-16 | 12:14 | 49.919
2021-01-16 | 12:14 | 49.919
2021-01-16 | 12:14 | 49.92
2021-01-16 | 12:14 | 49.921
2021-01-16 | 12:14 | 49.922
2021-01-16 | 12:14 | 49.921
2021-01-16 | 12:14 | 49.921
2021-01-16 | 12:14 | 49.918
2021-01-16 | 12:14 | 49.915
2021-01-16 | 12:14 | 49.911
2021-01-16 | 12:14 | 49.907
2021-01-16 | 12:14 | 49.902
2021-01-16 | 12:14 | 49.898
2021-01-16 | 12:14 | 49.897
2021-01-16 | 12:14 | 49.896
2021-01-16 | 12:14 | 49.901
2021-01-16 | 12:14 | 49.906
2021-01-16 | 12:14 | 49.909
2021-01-16 | 12:14 | 49.909
2021-01-16 | 12:14 | 49.911
2021-01-16 | 12:14 | 49.912
2021-01-16 | 12:14 | 49.91
2021-01-16 | 12:14 | 49.908
2021-01-16 | 12:14 | 49.909
2021-01-16 | 12:14 | 49.907
2021-01-16 | 12:14 | 49.905
2021-01-16 | 12:14 | 49.904
2021-01-16 | 12:14 | 49.906
2021-01-16 | 12:14 | 49.904
2021-01-16 | 12:14 | 49.906
2021-01-16 | 12:14 | 49.905
2021-01-16 | 12:14 | 49.906
2021-01-16 | 12:14 | 49.905
2021-01-16 | 12:14 | 49.906
2021-01-16 | 12:14 | 49.908
2021-01-16 | 12:14 | 49.909
2021-01-16 | 12:14 | 49.91
2021-01-16 | 12:15 | 49.911
2021-01-16 | 12:15 | 49.911
2021-01-16 | 12:15 | 49.909
2021-01-16 | 12:15 | 49.913
2021-01-16 | 12:15 | 49.912
2021-01-16 | 12:15 | 49.91
2021-01-16 | 12:15 | 49.908
2021-01-16 | 12:15 | 49.903
2021-01-16 | 12:15 | 49.901
2021-01-16 | 12:15 | 49.898
2021-01-16 | 12:15 | 49.897
2021-01-16 | 12:15 | 49.898
2021-01-16 | 12:15 | 49.9
2021-01-16 | 12:15 | 49.902
2021-01-16 | 12:15 | 49.905
2021-01-16 | 12:15 | 49.908
2021-01-16 | 12:15 | 49.91
2021-01-16 | 12:15 | 49.91
2021-01-16 | 12:15 | 49.91
2021-01-16 | 12:15 | 49.908
2021-01-16 | 12:15 | 49.907
2021-01-16 | 12:15 | 49.907
2021-01-16 | 12:15 | 49.907
2021-01-16 | 12:15 | 49.908
2021-01-16 | 12:15 | 49.905
2021-01-16 | 12:15 | 49.904
2021-01-16 | 12:15 | 49.901
2021-01-16 | 12:15 | 49.901
2021-01-16 | 12:15 | 49.9
2021-01-16 | 12:15 | 49.898
2021-01-16 | 12:15 | 49.895
2021-01-16 | 12:15 | 49.895
2021-01-16 | 12:15 | 49.895
2021-01-16 | 12:15 | 49.897
2021-01-16 | 12:15 | 49.894
2021-01-16 | 12:15 | 49.891
2021-01-16 | 12:15 | 49.889
2021-01-16 | 12:15 | 49.887
2021-01-16 | 12:15 | 49.885
2021-01-16 | 12:15 | 49.884
2021-01-16 | 12:15 | 49.883
2021-01-16 | 12:15 | 49.883
2021-01-16 | 12:15 | 49.883
2021-01-16 | 12:15 | 49.882
2021-01-16 | 12:15 | 49.884
2021-01-16 | 12:15 | 49.882
2021-01-16 | 12:15 | 49.88
2021-01-16 | 12:15 | 49.881
2021-01-16 | 12:15 | 49.881
2021-01-16 | 12:15 | 49.883
2021-01-16 | 12:15 | 49.883
2021-01-16 | 12:15 | 49.883
2021-01-16 | 12:15 | 49.881
2021-01-16 | 12:15 | 49.88
2021-01-16 | 12:15 | 49.879
2021-01-16 | 12:15 | 49.88
2021-01-16 | 12:15 | 49.88
2021-01-16 | 12:15 | 49.879
2021-01-16 | 12:15 | 49.881
2021-01-16 | 12:16 | 49.88
2021-01-16 | 12:16 | 49.88
2021-01-16 | 12:16 | 49.881
2021-01-16 | 12:16 | 49.882
2021-01-16 | 12:16 | 49.88
2021-01-16 | 12:16 | 49.879
2021-01-16 | 12:16 | 49.88
2021-01-16 | 12:16 | 49.883
2021-01-16 | 12:16 | 49.884
2021-01-16 | 12:16 | 49.885
2021-01-16 | 12:16 | 49.886
2021-01-16 | 12:16 | 49.886
2021-01-16 | 12:16 | 49.885
2021-01-16 | 12:16 | 49.884
2021-01-16 | 12:16 | 49.884
2021-01-16 | 12:16 | 49.885
2021-01-16 | 12:16 | 49.886
2021-01-16 | 12:16 | 49.889
2021-01-16 | 12:16 | 49.887
2021-01-16 | 12:16 | 49.885
2021-01-16 | 12:16 | 49.884
2021-01-16 | 12:16 | 49.884
2021-01-16 | 12:16 | 49.882
2021-01-16 | 12:16 | 49.882
2021-01-16 | 12:16 | 49.88
2021-01-16 | 12:16 | 49.879
2021-01-16 | 12:16 | 49.88
2021-01-16 | 12:16 | 49.878
2021-01-16 | 12:16 | 49.877
2021-01-16 | 12:16 | 49.876
2021-01-16 | 12:16 | 49.875
2021-01-16 | 12:16 | 49.872
2021-01-16 | 12:16 | 49.868
2021-01-16 | 12:16 | 49.867
2021-01-16 | 12:16 | 49.867
2021-01-16 | 12:16 | 49.869
2021-01-16 | 12:16 | 49.87
2021-01-16 | 12:16 | 49.871
2021-01-16 | 12:16 | 49.869
2021-01-16 | 12:16 | 49.868
2021-01-16 | 12:16 | 49.866
2021-01-16 | 12:16 | 49.865
2021-01-16 | 12:16 | 49.864
2021-01-16 | 12:16 | 49.862
2021-01-16 | 12:16 | 49.861
2021-01-16 | 12:16 | 49.861
2021-01-16 | 12:16 | 49.861
2021-01-16 | 12:16 | 49.861
2021-01-16 | 12:16 | 49.862
2021-01-16 | 12:16 | 49.863
2021-01-16 | 12:16 | 49.866
2021-01-16 | 12:16 | 49.866
2021-01-16 | 12:16 | 49.871
2021-01-16 | 12:16 | 49.871
2021-01-16 | 12:16 | 49.871
2021-01-16 | 12:16 | 49.87
2021-01-16 | 12:16 | 49.87
2021-01-16 | 12:16 | 49.869
2021-01-16 | 12:16 | 49.868
2021-01-16 | 12:16 | 49.867
2021-01-16 | 12:16 | 49.867
2021-01-16 | 12:17 | 49.867
2021-01-16 | 12:17 | 49.866
2021-01-16 | 12:17 | 49.866
2021-01-16 | 12:17 | 49.869
2021-01-16 | 12:17 | 49.87
2021-01-16 | 12:17 | 49.872
2021-01-16 | 12:17 | 49.871
2021-01-16 | 12:17 | 49.873
2021-01-16 | 12:17 | 49.874
2021-01-16 | 12:17 | 49.874
2021-01-16 | 12:17 | 49.872
2021-01-16 | 12:17 | 49.869
2021-01-16 | 12:17 | 49.868
2021-01-16 | 12:17 | 49.868
2021-01-16 | 12:17 | 49.871
2021-01-16 | 12:17 | 49.872
2021-01-16 | 12:17 | 49.87
2021-01-16 | 12:17 | 49.87
2021-01-16 | 12:17 | 49.868
2021-01-16 | 12:17 | 49.866
2021-01-16 | 12:17 | 49.863
2021-01-16 | 12:17 | 49.857
2021-01-16 | 12:17 | 49.853
2021-01-16 | 12:17 | 49.848
2021-01-16 | 12:17 | 49.846
2021-01-16 | 12:17 | 49.845
2021-01-16 | 12:17 | 49.844
2021-01-16 | 12:17 | 49.844
2021-01-16 | 12:17 | 49.845
2021-01-16 | 12:17 | 49.846
2021-01-16 | 12:17 | 49.845
2021-01-16 | 12:17 | 49.846
2021-01-16 | 12:17 | 49.847
2021-01-16 | 12:17 | 49.852
2021-01-16 | 12:17 | 49.859
2021-01-16 | 12:17 | 49.861
2021-01-16 | 12:17 | 49.865
2021-01-16 | 12:17 | 49.87
2021-01-16 | 12:17 | 49.875
2021-01-16 | 12:17 | 49.882
2021-01-16 | 12:17 | 49.887
2021-01-16 | 12:17 | 49.891
2021-01-16 | 12:17 | 49.892
2021-01-16 | 12:17 | 49.894
2021-01-16 | 12:17 | 49.895
2021-01-16 | 12:17 | 49.896
2021-01-16 | 12:17 | 49.896
2021-01-16 | 12:17 | 49.897
2021-01-16 | 12:17 | 49.897
2021-01-16 | 12:17 | 49.896
2021-01-16 | 12:17 | 49.898
2021-01-16 | 12:17 | 49.901
2021-01-16 | 12:17 | 49.903
2021-01-16 | 12:17 | 49.904
2021-01-16 | 12:17 | 49.905
2021-01-16 | 12:17 | 49.906
2021-01-16 | 12:17 | 49.906
2021-01-16 | 12:17 | 49.904
2021-01-16 | 12:17 | 49.906
2021-01-16 | 12:18 | 49.907
2021-01-16 | 12:18 | 49.909
2021-01-16 | 12:18 | 49.913
2021-01-16 | 12:18 | 49.915
2021-01-16 | 12:18 | 49.916
2021-01-16 | 12:18 | 49.916
2021-01-16 | 12:18 | 49.917
2021-01-16 | 12:18 | 49.916
2021-01-16 | 12:18 | 49.916
2021-01-16 | 12:18 | 49.917
2021-01-16 | 12:18 | 49.918
2021-01-16 | 12:18 | 49.918
2021-01-16 | 12:18 | 49.918
2021-01-16 | 12:18 | 49.918
2021-01-16 | 12:18 | 49.918
2021-01-16 | 12:18 | 49.916
2021-01-16 | 12:18 | 49.914
2021-01-16 | 12:18 | 49.912
2021-01-16 | 12:18 | 49.912
2021-01-16 | 12:18 | 49.913
2021-01-16 | 12:18 | 49.912
2021-01-16 | 12:18 | 49.909
2021-01-16 | 12:18 | 49.91
2021-01-16 | 12:18 | 49.909
2021-01-16 | 12:18 | 49.911
2021-01-16 | 12:18 | 49.912
2021-01-16 | 12:18 | 49.914
2021-01-16 | 12:18 | 49.915
2021-01-16 | 12:18 | 49.916
2021-01-16 | 12:18 | 49.917
2021-01-16 | 12:18 | 49.919
2021-01-16 | 12:18 | 49.919
2021-01-16 | 12:18 | 49.919
2021-01-16 | 12:18 | 49.92
2021-01-16 | 12:18 | 49.921
2021-01-16 | 12:18 | 49.921
2021-01-16 | 12:18 | 49.92
2021-01-16 | 12:18 | 49.919
2021-01-16 | 12:18 | 49.919
2021-01-16 | 12:18 | 49.916
2021-01-16 | 12:18 | 49.912
2021-01-16 | 12:18 | 49.911
2021-01-16 | 12:18 | 49.909
2021-01-16 | 12:18 | 49.909
2021-01-16 | 12:18 | 49.91
2021-01-16 | 12:18 | 49.911
2021-01-16 | 12:18 | 49.912
2021-01-16 | 12:18 | 49.914
2021-01-16 | 12:18 | 49.916
2021-01-16 | 12:18 | 49.919
2021-01-16 | 12:18 | 49.92
2021-01-16 | 12:18 | 49.922
2021-01-16 | 12:18 | 49.925
2021-01-16 | 12:18 | 49.928
2021-01-16 | 12:18 | 49.929
2021-01-16 | 12:18 | 49.932
2021-01-16 | 12:18 | 49.933
2021-01-16 | 12:18 | 49.933
2021-01-16 | 12:18 | 49.934
2021-01-16 | 12:18 | 49.937
2021-01-16 | 12:18 | 49.942
2021-01-16 | 12:19 | 49.948
2021-01-16 | 12:19 | 49.951
2021-01-16 | 12:19 | 49.954
2021-01-16 | 12:19 | 49.959
2021-01-16 | 12:19 | 49.964
2021-01-16 | 12:19 | 49.968
2021-01-16 | 12:19 | 49.97
2021-01-16 | 12:19 | 49.974
2021-01-16 | 12:19 | 49.977
2021-01-16 | 12:19 | 49.979
2021-01-16 | 12:19 | 49.981
2021-01-16 | 12:19 | 49.981
2021-01-16 | 12:19 | 49.982
2021-01-16 | 12:19 | 49.986
2021-01-16 | 12:19 | 49.988
2021-01-16 | 12:19 | 49.991
2021-01-16 | 12:19 | 49.992
2021-01-16 | 12:19 | 49.991
2021-01-16 | 12:19 | 49.989
2021-01-16 | 12:19 | 49.988
2021-01-16 | 12:19 | 49.986
2021-01-16 | 12:19 | 49.983
2021-01-16 | 12:19 | 49.981
2021-01-16 | 12:19 | 49.982
2021-01-16 | 12:19 | 49.984
2021-01-16 | 12:19 | 49.987
2021-01-16 | 12:19 | 49.988
2021-01-16 | 12:19 | 49.991
2021-01-16 | 12:19 | 49.994
2021-01-16 | 12:19 | 49.995
2021-01-16 | 12:19 | 49.995
2021-01-16 | 12:19 | 49.993
2021-01-16 | 12:19 | 49.992
2021-01-16 | 12:19 | 49.989
2021-01-16 | 12:19 | 49.986
2021-01-16 | 12:19 | 49.984
2021-01-16 | 12:19 | 49.982
2021-01-16 | 12:19 | 49.982
2021-01-16 | 12:19 | 49.982
2021-01-16 | 12:19 | 49.984
2021-01-16 | 12:19 | 49.983
2021-01-16 | 12:19 | 49.984
2021-01-16 | 12:19 | 49.984
2021-01-16 | 12:19 | 49.982
2021-01-16 | 12:19 | 49.982
2021-01-16 | 12:19 | 49.983
2021-01-16 | 12:19 | 49.981
2021-01-16 | 12:19 | 49.98
2021-01-16 | 12:19 | 49.977
2021-01-16 | 12:19 | 49.978
2021-01-16 | 12:19 | 49.978
2021-01-16 | 12:19 | 49.977
2021-01-16 | 12:19 | 49.979
2021-01-16 | 12:19 | 49.979
2021-01-16 | 12:19 | 49.979
2021-01-16 | 12:19 | 49.978
2021-01-16 | 12:19 | 49.975
2021-01-16 | 12:19 | 49.974
2021-01-16 | 12:19 | 49.971
2021-01-16 | 12:20 | 49.969
2021-01-16 | 12:20 | 49.97
2021-01-16 | 12:20 | 49.969
2021-01-16 | 12:20 | 49.967
2021-01-16 | 12:20 | 49.967
2021-01-16 | 12:20 | 49.964
2021-01-16 | 12:20 | 49.963
2021-01-16 | 12:20 | 49.962
2021-01-16 | 12:20 | 49.961
2021-01-16 | 12:20 | 49.96
2021-01-16 | 12:20 | 49.958
2021-01-16 | 12:20 | 49.957
2021-01-16 | 12:20 | 49.954
2021-01-16 | 12:20 | 49.952
2021-01-16 | 12:20 | 49.951
2021-01-16 | 12:20 | 49.95
2021-01-16 | 12:20 | 49.949
2021-01-16 | 12:20 | 49.95
2021-01-16 | 12:20 | 49.95
2021-01-16 | 12:20 | 49.95
2021-01-16 | 12:20 | 49.949
2021-01-16 | 12:20 | 49.949
2021-01-16 | 12:20 | 49.95
2021-01-16 | 12:20 | 49.951
2021-01-16 | 12:20 | 49.953
2021-01-16 | 12:20 | 49.954
2021-01-16 | 12:20 | 49.95
2021-01-16 | 12:20 | 49.946
2021-01-16 | 12:20 | 49.943
2021-01-16 | 12:20 | 49.94
2021-01-16 | 12:20 | 49.938
2021-01-16 | 12:20 | 49.936
2021-01-16 | 12:20 | 49.934
2021-01-16 | 12:20 | 49.935
2021-01-16 | 12:20 | 49.934
2021-01-16 | 12:20 | 49.934
2021-01-16 | 12:20 | 49.933
2021-01-16 | 12:20 | 49.933
2021-01-16 | 12:20 | 49.932
2021-01-16 | 12:20 | 49.931
2021-01-16 | 12:20 | 49.929
2021-01-16 | 12:20 | 49.927
2021-01-16 | 12:20 | 49.925
2021-01-16 | 12:20 | 49.923
2021-01-16 | 12:20 | 49.922
2021-01-16 | 12:20 | 49.921
2021-01-16 | 12:20 | 49.921
2021-01-16 | 12:20 | 49.918
2021-01-16 | 12:20 | 49.917
2021-01-16 | 12:20 | 49.918
2021-01-16 | 12:20 | 49.917
2021-01-16 | 12:20 | 49.917
2021-01-16 | 12:20 | 49.917
2021-01-16 | 12:20 | 49.916
2021-01-16 | 12:20 | 49.914
2021-01-16 | 12:20 | 49.914
2021-01-16 | 12:20 | 49.915
2021-01-16 | 12:20 | 49.916
2021-01-16 | 12:20 | 49.92
2021-01-16 | 12:20 | 49.924
2021-01-16 | 12:20 | 49.928
2021-01-16 | 12:21 | 49.926
2021-01-16 | 12:21 | 49.924
2021-01-16 | 12:21 | 49.925
2021-01-16 | 12:21 | 49.924
2021-01-16 | 12:21 | 49.926
2021-01-16 | 12:21 | 49.928
2021-01-16 | 12:21 | 49.929
2021-01-16 | 12:21 | 49.934
2021-01-16 | 12:21 | 49.936
2021-01-16 | 12:21 | 49.938
2021-01-16 | 12:21 | 49.938
2021-01-16 | 12:21 | 49.939
2021-01-16 | 12:21 | 49.941
2021-01-16 | 12:21 | 49.942
2021-01-16 | 12:21 | 49.942
2021-01-16 | 12:21 | 49.943
2021-01-16 | 12:21 | 49.943
2021-01-16 | 12:21 | 49.941
2021-01-16 | 12:21 | 49.939
2021-01-16 | 12:21 | 49.939
2021-01-16 | 12:21 | 49.941
2021-01-16 | 12:21 | 49.939
2021-01-16 | 12:21 | 49.939
2021-01-16 | 12:21 | 49.941
2021-01-16 | 12:21 | 49.946
2021-01-16 | 12:21 | 49.952
2021-01-16 | 12:21 | 49.959
2021-01-16 | 12:21 | 49.962
2021-01-16 | 12:21 | 49.964
2021-01-16 | 12:21 | 49.964
2021-01-16 | 12:21 | 49.962
2021-01-16 | 12:21 | 49.96
2021-01-16 | 12:21 | 49.96
2021-01-16 | 12:21 | 49.958
2021-01-16 | 12:21 | 49.955
2021-01-16 | 12:21 | 49.954
2021-01-16 | 12:21 | 49.954
2021-01-16 | 12:21 | 49.952
2021-01-16 | 12:21 | 49.949
2021-01-16 | 12:21 | 49.946
2021-01-16 | 12:21 | 49.94
2021-01-16 | 12:21 | 49.937
2021-01-16 | 12:21 | 49.936
2021-01-16 | 12:21 | 49.937
2021-01-16 | 12:21 | 49.937
2021-01-16 | 12:21 | 49.937
2021-01-16 | 12:21 | 49.937
2021-01-16 | 12:21 | 49.937
2021-01-16 | 12:21 | 49.939
2021-01-16 | 12:21 | 49.941
2021-01-16 | 12:21 | 49.946
2021-01-16 | 12:21 | 49.95
2021-01-16 | 12:21 | 49.955
2021-01-16 | 12:21 | 49.957
2021-01-16 | 12:21 | 49.96
2021-01-16 | 12:21 | 49.96
2021-01-16 | 12:21 | 49.961
2021-01-16 | 12:21 | 49.962
2021-01-16 | 12:21 | 49.961
2021-01-16 | 12:22 | 49.962
2021-01-16 | 12:22 | 49.963
2021-01-16 | 12:22 | 49.965
2021-01-16 | 12:22 | 49.968
2021-01-16 | 12:22 | 49.97
2021-01-16 | 12:22 | 49.972
2021-01-16 | 12:22 | 49.972
2021-01-16 | 12:22 | 49.975
2021-01-16 | 12:22 | 49.976
2021-01-16 | 12:22 | 49.975
2021-01-16 | 12:22 | 49.973
2021-01-16 | 12:22 | 49.973
2021-01-16 | 12:22 | 49.971
2021-01-16 | 12:22 | 49.97
2021-01-16 | 12:22 | 49.97
2021-01-16 | 12:22 | 49.971
2021-01-16 | 12:22 | 49.971
2021-01-16 | 12:22 | 49.971
2021-01-16 | 12:22 | 49.971
2021-01-16 | 12:22 | 49.969
2021-01-16 | 12:22 | 49.97
2021-01-16 | 12:22 | 49.97
2021-01-16 | 12:22 | 49.971
2021-01-16 | 12:22 | 49.972
2021-01-16 | 12:22 | 49.972
2021-01-16 | 12:22 | 49.971
2021-01-16 | 12:22 | 49.966
2021-01-16 | 12:22 | 49.965
2021-01-16 | 12:22 | 49.964
2021-01-16 | 12:22 | 49.962
2021-01-16 | 12:22 | 49.96
2021-01-16 | 12:22 | 49.959
2021-01-16 | 12:22 | 49.957
2021-01-16 | 12:22 | 49.956
2021-01-16 | 12:22 | 49.955
2021-01-16 | 12:22 | 49.956
2021-01-16 | 12:22 | 49.957
2021-01-16 | 12:22 | 49.955
2021-01-16 | 12:22 | 49.955
2021-01-16 | 12:22 | 49.956
2021-01-16 | 12:22 | 49.956
2021-01-16 | 12:22 | 49.956
2021-01-16 | 12:22 | 49.957
2021-01-16 | 12:22 | 49.959
2021-01-16 | 12:22 | 49.961
2021-01-16 | 12:22 | 49.962
2021-01-16 | 12:22 | 49.963
2021-01-16 | 12:22 | 49.964
2021-01-16 | 12:22 | 49.965
2021-01-16 | 12:22 | 49.966
2021-01-16 | 12:22 | 49.969
2021-01-16 | 12:22 | 49.972
2021-01-16 | 12:22 | 49.972
2021-01-16 | 12:22 | 49.972
2021-01-16 | 12:22 | 49.97
2021-01-16 | 12:22 | 49.966
2021-01-16 | 12:22 | 49.961
2021-01-16 | 12:22 | 49.958
2021-01-16 | 12:22 | 49.957
2021-01-16 | 12:22 | 49.955
2021-01-16 | 12:22 | 49.954
2021-01-16 | 12:23 | 49.953
2021-01-16 | 12:23 | 49.952
2021-01-16 | 12:23 | 49.952
2021-01-16 | 12:23 | 49.949
2021-01-16 | 12:23 | 49.947
2021-01-16 | 12:23 | 49.945
2021-01-16 | 12:23 | 49.944
2021-01-16 | 12:23 | 49.944
2021-01-16 | 12:23 | 49.945
2021-01-16 | 12:23 | 49.948
2021-01-16 | 12:23 | 49.951
2021-01-16 | 12:23 | 49.954
2021-01-16 | 12:23 | 49.959
2021-01-16 | 12:23 | 49.962
2021-01-16 | 12:23 | 49.963
2021-01-16 | 12:23 | 49.964
2021-01-16 | 12:23 | 49.963
2021-01-16 | 12:23 | 49.965
2021-01-16 | 12:23 | 49.966
2021-01-16 | 12:23 | 49.966
2021-01-16 | 12:23 | 49.969
2021-01-16 | 12:23 | 49.973
2021-01-16 | 12:23 | 49.977
2021-01-16 | 12:23 | 49.98
2021-01-16 | 12:23 | 49.982
2021-01-16 | 12:23 | 49.984
2021-01-16 | 12:23 | 49.984
2021-01-16 | 12:23 | 49.982
2021-01-16 | 12:23 | 49.98
2021-01-16 | 12:23 | 49.977
2021-01-16 | 12:23 | 49.972
2021-01-16 | 12:23 | 49.968
2021-01-16 | 12:23 | 49.965
2021-01-16 | 12:23 | 49.961
2021-01-16 | 12:23 | 49.958
2021-01-16 | 12:23 | 49.957
2021-01-16 | 12:23 | 49.958
2021-01-16 | 12:23 | 49.96
2021-01-16 | 12:23 | 49.962
2021-01-16 | 12:23 | 49.963
2021-01-16 | 12:23 | 49.963
2021-01-16 | 12:23 | 49.963
2021-01-16 | 12:23 | 49.958
2021-01-16 | 12:23 | 49.955
2021-01-16 | 12:23 | 49.952
2021-01-16 | 12:23 | 49.947
2021-01-16 | 12:23 | 49.944
2021-01-16 | 12:23 | 49.945
2021-01-16 | 12:23 | 49.945
2021-01-16 | 12:23 | 49.945
2021-01-16 | 12:23 | 49.945
2021-01-16 | 12:23 | 49.946
2021-01-16 | 12:23 | 49.948
2021-01-16 | 12:23 | 49.949
2021-01-16 | 12:23 | 49.947
2021-01-16 | 12:23 | 49.946
2021-01-16 | 12:23 | 49.947
2021-01-16 | 12:23 | 49.949
2021-01-16 | 12:23 | 49.949
2021-01-16 | 12:24 | 49.949
2021-01-16 | 12:24 | 49.948
2021-01-16 | 12:24 | 49.948
2021-01-16 | 12:24 | 49.947
2021-01-16 | 12:24 | 49.945
2021-01-16 | 12:24 | 49.944
2021-01-16 | 12:24 | 49.945
2021-01-16 | 12:24 | 49.944
2021-01-16 | 12:24 | 49.943
2021-01-16 | 12:24 | 49.944
2021-01-16 | 12:24 | 49.949
2021-01-16 | 12:24 | 49.952
2021-01-16 | 12:24 | 49.953
2021-01-16 | 12:24 | 49.956
2021-01-16 | 12:24 | 49.958
2021-01-16 | 12:24 | 49.96
2021-01-16 | 12:24 | 49.96
2021-01-16 | 12:24 | 49.958
2021-01-16 | 12:24 | 49.954
2021-01-16 | 12:24 | 49.952
2021-01-16 | 12:24 | 49.953
2021-01-16 | 12:24 | 49.954
2021-01-16 | 12:24 | 49.952
2021-01-16 | 12:24 | 49.949
2021-01-16 | 12:24 | 49.945
2021-01-16 | 12:24 | 49.944
2021-01-16 | 12:24 | 49.943
2021-01-16 | 12:24 | 49.943
2021-01-16 | 12:24 | 49.941
2021-01-16 | 12:24 | 49.943
2021-01-16 | 12:24 | 49.943
2021-01-16 | 12:24 | 49.943
2021-01-16 | 12:24 | 49.945
2021-01-16 | 12:24 | 49.947
2021-01-16 | 12:24 | 49.947
2021-01-16 | 12:24 | 49.946
2021-01-16 | 12:24 | 49.944
2021-01-16 | 12:24 | 49.945
2021-01-16 | 12:24 | 49.944
2021-01-16 | 12:24 | 49.943
2021-01-16 | 12:24 | 49.942
2021-01-16 | 12:24 | 49.94
2021-01-16 | 12:24 | 49.938
2021-01-16 | 12:24 | 49.939
2021-01-16 | 12:24 | 49.939
2021-01-16 | 12:24 | 49.939
2021-01-16 | 12:24 | 49.939
2021-01-16 | 12:24 | 49.938
2021-01-16 | 12:24 | 49.939
2021-01-16 | 12:24 | 49.94
2021-01-16 | 12:24 | 49.941
2021-01-16 | 12:24 | 49.942
2021-01-16 | 12:24 | 49.941
2021-01-16 | 12:24 | 49.942
2021-01-16 | 12:24 | 49.942
2021-01-16 | 12:24 | 49.945
2021-01-16 | 12:24 | 49.949
2021-01-16 | 12:24 | 49.962
2021-01-16 | 12:24 | 49.956
2021-01-16 | 12:24 | 49.958
2021-01-16 | 12:24 | 49.959
2021-01-16 | 12:25 | 49.958
2021-01-16 | 12:25 | 49.959
2021-01-16 | 12:25 | 49.958
2021-01-16 | 12:25 | 49.96
2021-01-16 | 12:25 | 49.961
2021-01-16 | 12:25 | 49.962
2021-01-16 | 12:25 | 49.96
2021-01-16 | 12:25 | 49.96
2021-01-16 | 12:25 | 49.96
2021-01-16 | 12:25 | 49.961
2021-01-16 | 12:25 | 49.962
2021-01-16 | 12:25 | 49.96
2021-01-16 | 12:25 | 49.962
2021-01-16 | 12:25 | 49.964
2021-01-16 | 12:25 | 49.965
2021-01-16 | 12:25 | 49.964
2021-01-16 | 12:25 | 49.963
2021-01-16 | 12:25 | 49.962
2021-01-16 | 12:25 | 49.96
2021-01-16 | 12:25 | 49.958
2021-01-16 | 12:25 | 49.958
2021-01-16 | 12:25 | 49.96
2021-01-16 | 12:25 | 49.96
2021-01-16 | 12:25 | 49.962
2021-01-16 | 12:25 | 49.961
2021-01-16 | 12:25 | 49.961
2021-01-16 | 12:25 | 49.958
2021-01-16 | 12:25 | 49.959
2021-01-16 | 12:25 | 49.956
2021-01-16 | 12:25 | 49.957
2021-01-16 | 12:25 | 49.955
2021-01-16 | 12:25 | 49.954
2021-01-16 | 12:25 | 49.952
2021-01-16 | 12:25 | 49.95
2021-01-16 | 12:25 | 49.948
2021-01-16 | 12:25 | 49.946
2021-01-16 | 12:25 | 49.944
2021-01-16 | 12:25 | 49.942
2021-01-16 | 12:25 | 49.94
2021-01-16 | 12:25 | 49.937
2021-01-16 | 12:25 | 49.937
2021-01-16 | 12:25 | 49.939
2021-01-16 | 12:25 | 49.942
2021-01-16 | 12:25 | 49.942
2021-01-16 | 12:25 | 49.94
2021-01-16 | 12:25 | 49.939
2021-01-16 | 12:25 | 49.94
2021-01-16 | 12:25 | 49.939
2021-01-16 | 12:25 | 49.939
2021-01-16 | 12:25 | 49.937
2021-01-16 | 12:25 | 49.933
2021-01-16 | 12:25 | 49.93
2021-01-16 | 12:25 | 49.931
2021-01-16 | 12:25 | 49.934
2021-01-16 | 12:25 | 49.938
2021-01-16 | 12:25 | 49.942
2021-01-16 | 12:25 | 49.946
2021-01-16 | 12:25 | 49.947
2021-01-16 | 12:25 | 49.947
2021-01-16 | 12:26 | 49.946
2021-01-16 | 12:26 | 49.942
2021-01-16 | 12:26 | 49.94
2021-01-16 | 12:26 | 49.933
2021-01-16 | 12:26 | 49.928
2021-01-16 | 12:26 | 49.918
2021-01-16 | 12:26 | 49.911
2021-01-16 | 12:26 | 49.905
2021-01-16 | 12:26 | 49.902
2021-01-16 | 12:26 | 49.899
2021-01-16 | 12:26 | 49.896
2021-01-16 | 12:26 | 49.896
2021-01-16 | 12:26 | 49.901
2021-01-16 | 12:26 | 49.906
2021-01-16 | 12:26 | 49.907
2021-01-16 | 12:26 | 49.911
2021-01-16 | 12:26 | 49.913
2021-01-16 | 12:26 | 49.912
2021-01-16 | 12:26 | 49.911
2021-01-16 | 12:26 | 49.911
2021-01-16 | 12:26 | 49.91
2021-01-16 | 12:26 | 49.909
2021-01-16 | 12:26 | 49.905
2021-01-16 | 12:26 | 49.9
2021-01-16 | 12:26 | 49.896
2021-01-16 | 12:26 | 49.895
2021-01-16 | 12:26 | 49.892
2021-01-16 | 12:26 | 49.889
2021-01-16 | 12:26 | 49.889
2021-01-16 | 12:26 | 49.894
2021-01-16 | 12:26 | 49.897
2021-01-16 | 12:26 | 49.898
2021-01-16 | 12:26 | 49.898
2021-01-16 | 12:26 | 49.9
2021-01-16 | 12:26 | 49.899
2021-01-16 | 12:26 | 49.899
2021-01-16 | 12:26 | 49.899
2021-01-16 | 12:26 | 49.9
2021-01-16 | 12:26 | 49.901
2021-01-16 | 12:26 | 49.902
2021-01-16 | 12:26 | 49.903
2021-01-16 | 12:26 | 49.904
2021-01-16 | 12:26 | 49.903
2021-01-16 | 12:26 | 49.901
2021-01-16 | 12:26 | 49.9
2021-01-16 | 12:26 | 49.9
2021-01-16 | 12:26 | 49.9
2021-01-16 | 12:26 | 49.902
2021-01-16 | 12:26 | 49.903
2021-01-16 | 12:26 | 49.904
2021-01-16 | 12:26 | 49.907
2021-01-16 | 12:26 | 49.906
2021-01-16 | 12:26 | 49.906
2021-01-16 | 12:26 | 49.904
2021-01-16 | 12:26 | 49.907
2021-01-16 | 12:26 | 49.907
2021-01-16 | 12:26 | 49.908
2021-01-16 | 12:26 | 49.91
2021-01-16 | 12:26 | 49.913
2021-01-16 | 12:26 | 49.915
2021-01-16 | 12:26 | 49.917
2021-01-16 | 12:27 | 49.92
2021-01-16 | 12:27 | 49.922
2021-01-16 | 12:27 | 49.926
2021-01-16 | 12:27 | 49.928
2021-01-16 | 12:27 | 49.926
2021-01-16 | 12:27 | 49.924
2021-01-16 | 12:27 | 49.924
2021-01-16 | 12:27 | 49.923
2021-01-16 | 12:27 | 49.919
2021-01-16 | 12:27 | 49.915
2021-01-16 | 12:27 | 49.914
2021-01-16 | 12:27 | 49.912
2021-01-16 | 12:27 | 49.911
2021-01-16 | 12:27 | 49.91
2021-01-16 | 12:27 | 49.909
2021-01-16 | 12:27 | 49.908
2021-01-16 | 12:27 | 49.908
2021-01-16 | 12:27 | 49.908
2021-01-16 | 12:27 | 49.908
2021-01-16 | 12:27 | 49.908
2021-01-16 | 12:27 | 49.908
2021-01-16 | 12:27 | 49.908
2021-01-16 | 12:27 | 49.91
2021-01-16 | 12:27 | 49.912
2021-01-16 | 12:27 | 49.913
2021-01-16 | 12:27 | 49.913
2021-01-16 | 12:27 | 49.915
2021-01-16 | 12:27 | 49.916
2021-01-16 | 12:27 | 49.917
2021-01-16 | 12:27 | 49.915
2021-01-16 | 12:27 | 49.917
2021-01-16 | 12:27 | 49.916
2021-01-16 | 12:27 | 49.917
2021-01-16 | 12:27 | 49.916
2021-01-16 | 12:27 | 49.918
2021-01-16 | 12:27 | 49.918
2021-01-16 | 12:27 | 49.92
2021-01-16 | 12:27 | 49.923
2021-01-16 | 12:27 | 49.926
2021-01-16 | 12:27 | 49.927
2021-01-16 | 12:27 | 49.927
2021-01-16 | 12:27 | 49.928
2021-01-16 | 12:27 | 49.929
2021-01-16 | 12:27 | 49.927
2021-01-16 | 12:27 | 49.927
2021-01-16 | 12:27 | 49.927
2021-01-16 | 12:27 | 49.929
2021-01-16 | 12:27 | 49.932
2021-01-16 | 12:27 | 49.93
2021-01-16 | 12:27 | 49.929
2021-01-16 | 12:27 | 49.927
2021-01-16 | 12:27 | 49.926
2021-01-16 | 12:27 | 49.925
2021-01-16 | 12:27 | 49.925
2021-01-16 | 12:27 | 49.923
2021-01-16 | 12:27 | 49.922
2021-01-16 | 12:27 | 49.922
2021-01-16 | 12:27 | 49.924
2021-01-16 | 12:27 | 49.926
2021-01-16 | 12:28 | 49.929
2021-01-16 | 12:28 | 49.931
2021-01-16 | 12:28 | 49.934
2021-01-16 | 12:28 | 49.933
2021-01-16 | 12:28 | 49.936
2021-01-16 | 12:28 | 49.938
2021-01-16 | 12:28 | 49.941
2021-01-16 | 12:28 | 49.941
2021-01-16 | 12:28 | 49.941
2021-01-16 | 12:28 | 49.941
2021-01-16 | 12:28 | 49.943
2021-01-16 | 12:28 | 49.943
2021-01-16 | 12:28 | 49.944
2021-01-16 | 12:28 | 49.943
2021-01-16 | 12:28 | 49.943
2021-01-16 | 12:28 | 49.942
2021-01-16 | 12:28 | 49.941
2021-01-16 | 12:28 | 49.94
2021-01-16 | 12:28 | 49.943
2021-01-16 | 12:28 | 49.942
2021-01-16 | 12:28 | 49.941
2021-01-16 | 12:28 | 49.942
2021-01-16 | 12:28 | 49.94
2021-01-16 | 12:28 | 49.941
2021-01-16 | 12:28 | 49.942
2021-01-16 | 12:28 | 49.938
2021-01-16 | 12:28 | 49.937
2021-01-16 | 12:28 | 49.934
2021-01-16 | 12:28 | 49.934
2021-01-16 | 12:28 | 49.934
2021-01-16 | 12:28 | 49.935
2021-01-16 | 12:28 | 49.933
2021-01-16 | 12:28 | 49.932
2021-01-16 | 12:28 | 49.932
2021-01-16 | 12:28 | 49.933
2021-01-16 | 12:28 | 49.935
2021-01-16 | 12:28 | 49.937
2021-01-16 | 12:28 | 49.936
2021-01-16 | 12:28 | 49.935
2021-01-16 | 12:28 | 49.935
2021-01-16 | 12:28 | 49.935
2021-01-16 | 12:28 | 49.934
2021-01-16 | 12:28 | 49.93
2021-01-16 | 12:28 | 49.929
2021-01-16 | 12:28 | 49.927
2021-01-16 | 12:28 | 49.925
2021-01-16 | 12:28 | 49.925
2021-01-16 | 12:28 | 49.926
2021-01-16 | 12:28 | 49.927
2021-01-16 | 12:28 | 49.926
2021-01-16 | 12:28 | 49.926
2021-01-16 | 12:28 | 49.93
2021-01-16 | 12:28 | 49.935
2021-01-16 | 12:28 | 49.936
2021-01-16 | 12:28 | 49.94
2021-01-16 | 12:28 | 49.943
2021-01-16 | 12:28 | 49.943
2021-01-16 | 12:28 | 49.941
2021-01-16 | 12:28 | 49.942
2021-01-16 | 12:28 | 49.942
2021-01-16 | 12:28 | 49.941
2021-01-16 | 12:29 | 49.944
2021-01-16 | 12:29 | 49.944
2021-01-16 | 12:29 | 49.943
2021-01-16 | 12:29 | 49.941
2021-01-16 | 12:29 | 49.941
2021-01-16 | 12:29 | 49.939
2021-01-16 | 12:29 | 49.937
2021-01-16 | 12:29 | 49.935
2021-01-16 | 12:29 | 49.933
2021-01-16 | 12:29 | 49.932
2021-01-16 | 12:29 | 49.933
2021-01-16 | 12:29 | 49.935
2021-01-16 | 12:29 | 49.937
2021-01-16 | 12:29 | 49.938
2021-01-16 | 12:29 | 49.939
2021-01-16 | 12:29 | 49.942
2021-01-16 | 12:29 | 49.943
2021-01-16 | 12:29 | 49.948
2021-01-16 | 12:29 | 49.951
2021-01-16 | 12:29 | 49.952
2021-01-16 | 12:29 | 49.954
2021-01-16 | 12:29 | 49.955
2021-01-16 | 12:29 | 49.954
2021-01-16 | 12:29 | 49.955
2021-01-16 | 12:29 | 49.958
2021-01-16 | 12:29 | 49.959
2021-01-16 | 12:29 | 49.96
2021-01-16 | 12:29 | 49.957
2021-01-16 | 12:29 | 49.958
2021-01-16 | 12:29 | 49.957
2021-01-16 | 12:29 | 49.96
2021-01-16 | 12:29 | 49.959
2021-01-16 | 12:29 | 49.962
2021-01-16 | 12:29 | 49.958
2021-01-16 | 12:29 | 49.956
2021-01-16 | 12:29 | 49.952
2021-01-16 | 12:29 | 49.949
2021-01-16 | 12:29 | 49.949
2021-01-16 | 12:29 | 49.946
2021-01-16 | 12:29 | 49.945
2021-01-16 | 12:29 | 49.946
2021-01-16 | 12:29 | 49.948
2021-01-16 | 12:29 | 49.949
2021-01-16 | 12:29 | 49.951
2021-01-16 | 12:29 | 49.951
2021-01-16 | 12:29 | 49.951
2021-01-16 | 12:29 | 49.949
2021-01-16 | 12:29 | 49.949
2021-01-16 | 12:29 | 49.948
2021-01-16 | 12:29 | 49.948
2021-01-16 | 12:29 | 49.949
2021-01-16 | 12:29 | 49.949
2021-01-16 | 12:29 | 49.947
2021-01-16 | 12:29 | 49.945
2021-01-16 | 12:29 | 49.941
2021-01-16 | 12:29 | 49.942
2021-01-16 | 12:29 | 49.943
2021-01-16 | 12:29 | 49.943
2021-01-16 | 12:29 | 49.947
2021-01-16 | 12:30 | 49.949
2021-01-16 | 12:30 | 49.952
2021-01-16 | 12:30 | 49.95
2021-01-16 | 12:30 | 49.95
2021-01-16 | 12:30 | 49.946
2021-01-16 | 12:30 | 49.945
2021-01-16 | 12:30 | 49.945
2021-01-16 | 12:30 | 49.944
2021-01-16 | 12:30 | 49.946
2021-01-16 | 12:30 | 49.947
2021-01-16 | 12:30 | 49.948
2021-01-16 | 12:30 | 49.948
2021-01-16 | 12:30 | 49.947
2021-01-16 | 12:30 | 49.949
2021-01-16 | 12:30 | 49.949
2021-01-16 | 12:30 | 49.948
2021-01-16 | 12:30 | 49.948
2021-01-16 | 12:30 | 49.946
2021-01-16 | 12:30 | 49.948
2021-01-16 | 12:30 | 49.949
2021-01-16 | 12:30 | 49.947
2021-01-16 | 12:30 | 49.948
2021-01-16 | 12:30 | 49.945
2021-01-16 | 12:30 | 49.94
2021-01-16 | 12:30 | 49.94
2021-01-16 | 12:30 | 49.938
2021-01-16 | 12:30 | 49.938
2021-01-16 | 12:30 | 49.938
2021-01-16 | 12:30 | 49.937
2021-01-16 | 12:30 | 49.938
2021-01-16 | 12:30 | 49.935
2021-01-16 | 12:30 | 49.935
2021-01-16 | 12:30 | 49.935
2021-01-16 | 12:30 | 49.936
2021-01-16 | 12:30 | 49.939
2021-01-16 | 12:30 | 49.94
2021-01-16 | 12:30 | 49.943
2021-01-16 | 12:30 | 49.944
2021-01-16 | 12:30 | 49.945
2021-01-16 | 12:30 | 49.944
2021-01-16 | 12:30 | 49.945
2021-01-16 | 12:30 | 49.947
2021-01-16 | 12:30 | 49.948
2021-01-16 | 12:30 | 49.947
2021-01-16 | 12:30 | 49.949
2021-01-16 | 12:30 | 49.949
2021-01-16 | 12:30 | 49.949
2021-01-16 | 12:30 | 49.947
2021-01-16 | 12:30 | 49.946
2021-01-16 | 12:30 | 49.947
2021-01-16 | 12:30 | 49.949
2021-01-16 | 12:30 | 49.949
2021-01-16 | 12:30 | 49.949
2021-01-16 | 12:30 | 49.95
2021-01-16 | 12:30 | 49.948
2021-01-16 | 12:30 | 49.95
2021-01-16 | 12:30 | 49.949
2021-01-16 | 12:30 | 49.947
2021-01-16 | 12:30 | 49.948
2021-01-16 | 12:30 | 49.948
2021-01-16 | 12:30 | 49.95
2021-01-16 | 12:31 | 49.949
2021-01-16 | 12:31 | 49.952
2021-01-16 | 12:31 | 49.95
2021-01-16 | 12:31 | 49.951
2021-01-16 | 12:31 | 49.951
2021-01-16 | 12:31 | 49.953
2021-01-16 | 12:31 | 49.954
2021-01-16 | 12:31 | 49.955
2021-01-16 | 12:31 | 49.957
2021-01-16 | 12:31 | 49.957
2021-01-16 | 12:31 | 49.96
2021-01-16 | 12:31 | 49.963
2021-01-16 | 12:31 | 49.968
2021-01-16 | 12:31 | 49.972
2021-01-16 | 12:31 | 49.973
2021-01-16 | 12:31 | 49.971
2021-01-16 | 12:31 | 49.97
2021-01-16 | 12:31 | 49.969
2021-01-16 | 12:31 | 49.964
2021-01-16 | 12:31 | 49.962
2021-01-16 | 12:31 | 49.961
2021-01-16 | 12:31 | 49.96
2021-01-16 | 12:31 | 49.961
2021-01-16 | 12:31 | 49.961
2021-01-16 | 12:31 | 49.962
2021-01-16 | 12:31 | 49.963
2021-01-16 | 12:31 | 49.966
2021-01-16 | 12:31 | 49.969
2021-01-16 | 12:31 | 49.969
2021-01-16 | 12:31 | 49.969
2021-01-16 | 12:31 | 49.966
2021-01-16 | 12:31 | 49.965
2021-01-16 | 12:31 | 49.961
2021-01-16 | 12:31 | 49.959
2021-01-16 | 12:31 | 49.956
2021-01-16 | 12:31 | 49.95
2021-01-16 | 12:31 | 49.947
2021-01-16 | 12:31 | 49.945
2021-01-16 | 12:31 | 49.944
2021-01-16 | 12:31 | 49.945
2021-01-16 | 12:31 | 49.944
2021-01-16 | 12:31 | 49.944
2021-01-16 | 12:31 | 49.943
2021-01-16 | 12:31 | 49.943
2021-01-16 | 12:31 | 49.943
2021-01-16 | 12:31 | 49.942
2021-01-16 | 12:31 | 49.941
2021-01-16 | 12:31 | 49.938
2021-01-16 | 12:31 | 49.936
2021-01-16 | 12:31 | 49.933
2021-01-16 | 12:31 | 49.93
2021-01-16 | 12:31 | 49.929
2021-01-16 | 12:31 | 49.93
2021-01-16 | 12:31 | 49.931
2021-01-16 | 12:31 | 49.932
2021-01-16 | 12:31 | 49.931
2021-01-16 | 12:31 | 49.932
2021-01-16 | 12:31 | 49.932
2021-01-16 | 12:31 | 49.931
2021-01-16 | 12:32 | 49.933
2021-01-16 | 12:32 | 49.935
2021-01-16 | 12:32 | 49.938
2021-01-16 | 12:32 | 49.939
2021-01-16 | 12:32 | 49.942
2021-01-16 | 12:32 | 49.947
2021-01-16 | 12:32 | 49.953
2021-01-16 | 12:32 | 49.957
2021-01-16 | 12:32 | 49.96
2021-01-16 | 12:32 | 49.962
2021-01-16 | 12:32 | 49.961
2021-01-16 | 12:32 | 49.961
2021-01-16 | 12:32 | 49.962
2021-01-16 | 12:32 | 49.96
2021-01-16 | 12:32 | 49.96
2021-01-16 | 12:32 | 49.955
2021-01-16 | 12:32 | 49.952
2021-01-16 | 12:32 | 49.952
2021-01-16 | 12:32 | 49.952
2021-01-16 | 12:32 | 49.951
2021-01-16 | 12:32 | 49.95
2021-01-16 | 12:32 | 49.951
2021-01-16 | 12:32 | 49.951
2021-01-16 | 12:32 | 49.952
2021-01-16 | 12:32 | 49.952
2021-01-16 | 12:32 | 49.954
2021-01-16 | 12:32 | 49.953
2021-01-16 | 12:32 | 49.955
2021-01-16 | 12:32 | 49.956
2021-01-16 | 12:32 | 49.958
2021-01-16 | 12:32 | 49.959
2021-01-16 | 12:32 | 49.958
2021-01-16 | 12:32 | 49.957
2021-01-16 | 12:32 | 49.957
2021-01-16 | 12:32 | 49.956
2021-01-16 | 12:32 | 49.956
2021-01-16 | 12:32 | 49.959
2021-01-16 | 12:32 | 49.96
2021-01-16 | 12:32 | 49.961
2021-01-16 | 12:32 | 49.961
2021-01-16 | 12:32 | 49.963
2021-01-16 | 12:32 | 49.964
2021-01-16 | 12:32 | 49.966
2021-01-16 | 12:32 | 49.965
2021-01-16 | 12:32 | 49.966
2021-01-16 | 12:32 | 49.963
2021-01-16 | 12:32 | 49.964
2021-01-16 | 12:32 | 49.966
2021-01-16 | 12:32 | 49.967
2021-01-16 | 12:32 | 49.968
2021-01-16 | 12:32 | 49.967
2021-01-16 | 12:32 | 49.966
2021-01-16 | 12:32 | 49.965
2021-01-16 | 12:32 | 49.965
2021-01-16 | 12:32 | 49.965
2021-01-16 | 12:32 | 49.967
2021-01-16 | 12:32 | 49.969
2021-01-16 | 12:32 | 49.97
2021-01-16 | 12:32 | 49.97
2021-01-16 | 12:32 | 49.968
2021-01-16 | 12:32 | 49.966
2021-01-16 | 12:33 | 49.964
2021-01-16 | 12:33 | 49.963
2021-01-16 | 12:33 | 49.963
2021-01-16 | 12:33 | 49.962
2021-01-16 | 12:33 | 49.962
2021-01-16 | 12:33 | 49.962
2021-01-16 | 12:33 | 49.964
2021-01-16 | 12:33 | 49.965
2021-01-16 | 12:33 | 49.965
2021-01-16 | 12:33 | 49.967
2021-01-16 | 12:33 | 49.965
2021-01-16 | 12:33 | 49.966
2021-01-16 | 12:33 | 49.965
2021-01-16 | 12:33 | 49.966
2021-01-16 | 12:33 | 49.968
2021-01-16 | 12:33 | 49.97
2021-01-16 | 12:33 | 49.973
2021-01-16 | 12:33 | 49.975
2021-01-16 | 12:33 | 49.977
2021-01-16 | 12:33 | 49.978
2021-01-16 | 12:33 | 49.976
2021-01-16 | 12:33 | 49.974
2021-01-16 | 12:33 | 49.97
2021-01-16 | 12:33 | 49.964
2021-01-16 | 12:33 | 49.958
2021-01-16 | 12:33 | 49.95
2021-01-16 | 12:33 | 49.942
2021-01-16 | 12:33 | 49.933
2021-01-16 | 12:33 | 49.926
2021-01-16 | 12:33 | 49.918
2021-01-16 | 12:33 | 49.911
2021-01-16 | 12:33 | 49.906
2021-01-16 | 12:33 | 49.904
2021-01-16 | 12:33 | 49.903
2021-01-16 | 12:33 | 49.904
2021-01-16 | 12:33 | 49.906
2021-01-16 | 12:33 | 49.909
2021-01-16 | 12:33 | 49.909
2021-01-16 | 12:33 | 49.909
2021-01-16 | 12:33 | 49.909
2021-01-16 | 12:33 | 49.907
2021-01-16 | 12:33 | 49.908
2021-01-16 | 12:33 | 49.909
2021-01-16 | 12:33 | 49.91
2021-01-16 | 12:33 | 49.911
2021-01-16 | 12:33 | 49.908
2021-01-16 | 12:33 | 49.906
2021-01-16 | 12:33 | 49.905
2021-01-16 | 12:33 | 49.9
2021-01-16 | 12:33 | 49.9
2021-01-16 | 12:33 | 49.898
2021-01-16 | 12:33 | 49.899
2021-01-16 | 12:33 | 49.899
2021-01-16 | 12:33 | 49.898
2021-01-16 | 12:33 | 49.898
2021-01-16 | 12:33 | 49.9
2021-01-16 | 12:33 | 49.902
2021-01-16 | 12:33 | 49.903
2021-01-16 | 12:33 | 49.905
2021-01-16 | 12:34 | 49.906
2021-01-16 | 12:34 | 49.908
2021-01-16 | 12:34 | 49.909
2021-01-16 | 12:34 | 49.911
2021-01-16 | 12:34 | 49.91
2021-01-16 | 12:34 | 49.912
2021-01-16 | 12:34 | 49.911
2021-01-16 | 12:34 | 49.911
2021-01-16 | 12:34 | 49.912
2021-01-16 | 12:34 | 49.91
2021-01-16 | 12:34 | 49.911
2021-01-16 | 12:34 | 49.911
2021-01-16 | 12:34 | 49.911
2021-01-16 | 12:34 | 49.912
2021-01-16 | 12:34 | 49.913
2021-01-16 | 12:34 | 49.914
2021-01-16 | 12:34 | 49.914
2021-01-16 | 12:34 | 49.912
2021-01-16 | 12:34 | 49.914
2021-01-16 | 12:34 | 49.916
2021-01-16 | 12:34 | 49.918
2021-01-16 | 12:34 | 49.918
2021-01-16 | 12:34 | 49.92
2021-01-16 | 12:34 | 49.918
2021-01-16 | 12:34 | 49.917
2021-01-16 | 12:34 | 49.916
2021-01-16 | 12:34 | 49.915
2021-01-16 | 12:34 | 49.914
2021-01-16 | 12:34 | 49.915
2021-01-16 | 12:34 | 49.915
2021-01-16 | 12:34 | 49.916
2021-01-16 | 12:34 | 49.916
2021-01-16 | 12:34 | 49.915
2021-01-16 | 12:34 | 49.914
2021-01-16 | 12:34 | 49.914
2021-01-16 | 12:34 | 49.915
2021-01-16 | 12:34 | 49.918
2021-01-16 | 12:34 | 49.919
2021-01-16 | 12:34 | 49.92
2021-01-16 | 12:34 | 49.921
2021-01-16 | 12:34 | 49.923
2021-01-16 | 12:34 | 49.925
2021-01-16 | 12:34 | 49.928
2021-01-16 | 12:34 | 49.93
2021-01-16 | 12:34 | 49.931
2021-01-16 | 12:34 | 49.932
2021-01-16 | 12:34 | 49.932
2021-01-16 | 12:34 | 49.934
2021-01-16 | 12:34 | 49.934
2021-01-16 | 12:34 | 49.935
2021-01-16 | 12:34 | 49.937
2021-01-16 | 12:34 | 49.937
2021-01-16 | 12:34 | 49.938
2021-01-16 | 12:34 | 49.935
2021-01-16 | 12:34 | 49.935
2021-01-16 | 12:34 | 49.935
2021-01-16 | 12:34 | 49.936
2021-01-16 | 12:34 | 49.937
2021-01-16 | 12:34 | 49.936
2021-01-16 | 12:34 | 49.937
2021-01-16 | 12:34 | 49.937
2021-01-16 | 12:35 | 49.937
2021-01-16 | 12:35 | 49.938
2021-01-16 | 12:35 | 49.941
2021-01-16 | 12:35 | 49.943
2021-01-16 | 12:35 | 49.945
2021-01-16 | 12:35 | 49.949
2021-01-16 | 12:35 | 49.95
2021-01-16 | 12:35 | 49.953
2021-01-16 | 12:35 | 49.954
2021-01-16 | 12:35 | 49.954
2021-01-16 | 12:35 | 49.954
2021-01-16 | 12:35 | 49.954
2021-01-16 | 12:35 | 49.953
2021-01-16 | 12:35 | 49.952
2021-01-16 | 12:35 | 49.951
2021-01-16 | 12:35 | 49.951
2021-01-16 | 12:35 | 49.951
2021-01-16 | 12:35 | 49.952
2021-01-16 | 12:35 | 49.954
2021-01-16 | 12:35 | 49.954
2021-01-16 | 12:35 | 49.954
2021-01-16 | 12:35 | 49.954
2021-01-16 | 12:35 | 49.951
2021-01-16 | 12:35 | 49.953
2021-01-16 | 12:35 | 49.951
2021-01-16 | 12:35 | 49.952
2021-01-16 | 12:35 | 49.951
2021-01-16 | 12:35 | 49.95
2021-01-16 | 12:35 | 49.95
2021-01-16 | 12:35 | 49.948
2021-01-16 | 12:35 | 49.946
2021-01-16 | 12:35 | 49.945
2021-01-16 | 12:35 | 49.944
2021-01-16 | 12:35 | 49.941
2021-01-16 | 12:35 | 49.94
2021-01-16 | 12:35 | 49.939
2021-01-16 | 12:35 | 49.939
2021-01-16 | 12:35 | 49.937
2021-01-16 | 12:35 | 49.937
2021-01-16 | 12:35 | 49.94
2021-01-16 | 12:35 | 49.943
2021-01-16 | 12:35 | 49.945
2021-01-16 | 12:35 | 49.949
2021-01-16 | 12:35 | 49.95
2021-01-16 | 12:35 | 49.952
2021-01-16 | 12:35 | 49.953
2021-01-16 | 12:35 | 49.956
2021-01-16 | 12:35 | 49.959
2021-01-16 | 12:35 | 49.962
2021-01-16 | 12:35 | 49.965
2021-01-16 | 12:35 | 49.969
2021-01-16 | 12:35 | 49.971
2021-01-16 | 12:35 | 49.976
2021-01-16 | 12:35 | 49.975
2021-01-16 | 12:35 | 49.975
2021-01-16 | 12:35 | 49.976
2021-01-16 | 12:35 | 49.977
2021-01-16 | 12:35 | 49.975
2021-01-16 | 12:35 | 49.974
2021-01-16 | 12:36 | 49.973
2021-01-16 | 12:36 | 49.972
2021-01-16 | 12:36 | 49.975
2021-01-16 | 12:36 | 49.974
2021-01-16 | 12:36 | 49.973
2021-01-16 | 12:36 | 49.971
2021-01-16 | 12:36 | 49.968
2021-01-16 | 12:36 | 49.966
2021-01-16 | 12:36 | 49.964
2021-01-16 | 12:36 | 49.964
2021-01-16 | 12:36 | 49.964
2021-01-16 | 12:36 | 49.963
2021-01-16 | 12:36 | 49.964
2021-01-16 | 12:36 | 49.964
2021-01-16 | 12:36 | 49.964
2021-01-16 | 12:36 | 49.964
2021-01-16 | 12:36 | 49.964
2021-01-16 | 12:36 | 49.963
2021-01-16 | 12:36 | 49.964
2021-01-16 | 12:36 | 49.964
2021-01-16 | 12:36 | 49.964
2021-01-16 | 12:36 | 49.963
2021-01-16 | 12:36 | 49.962
2021-01-16 | 12:36 | 49.96
2021-01-16 | 12:36 | 49.958
2021-01-16 | 12:36 | 49.958
2021-01-16 | 12:36 | 49.955
2021-01-16 | 12:36 | 49.952
2021-01-16 | 12:36 | 49.949
2021-01-16 | 12:36 | 49.944
2021-01-16 | 12:36 | 49.943
2021-01-16 | 12:36 | 49.94
2021-01-16 | 12:36 | 49.941
2021-01-16 | 12:36 | 49.941
2021-01-16 | 12:36 | 49.941
2021-01-16 | 12:36 | 49.944
2021-01-16 | 12:36 | 49.947
2021-01-16 | 12:36 | 49.949
2021-01-16 | 12:36 | 49.949
2021-01-16 | 12:36 | 49.948
2021-01-16 | 12:36 | 49.948
2021-01-16 | 12:36 | 49.946
2021-01-16 | 12:36 | 49.944
2021-01-16 | 12:36 | 49.942
2021-01-16 | 12:36 | 49.944
2021-01-16 | 12:36 | 49.946
2021-01-16 | 12:36 | 49.948
2021-01-16 | 12:36 | 49.95
2021-01-16 | 12:36 | 49.95
2021-01-16 | 12:36 | 49.95
2021-01-16 | 12:36 | 49.95
2021-01-16 | 12:36 | 49.95
2021-01-16 | 12:36 | 49.952
2021-01-16 | 12:36 | 49.953
2021-01-16 | 12:36 | 49.953
2021-01-16 | 12:36 | 49.956
2021-01-16 | 12:36 | 49.959
2021-01-16 | 12:36 | 49.962
2021-01-16 | 12:36 | 49.963
2021-01-16 | 12:36 | 49.962
2021-01-16 | 12:36 | 49.965
2021-01-16 | 12:37 | 49.965
2021-01-16 | 12:37 | 49.966
2021-01-16 | 12:37 | 49.965
2021-01-16 | 12:37 | 49.966
2021-01-16 | 12:37 | 49.968
2021-01-16 | 12:37 | 49.969
2021-01-16 | 12:37 | 49.97
2021-01-16 | 12:37 | 49.971
2021-01-16 | 12:37 | 49.974
2021-01-16 | 12:37 | 49.977
2021-01-16 | 12:37 | 49.983
2021-01-16 | 12:37 | 49.985
2021-01-16 | 12:37 | 49.987
2021-01-16 | 12:37 | 49.986
2021-01-16 | 12:37 | 49.984
2021-01-16 | 12:37 | 49.982
2021-01-16 | 12:37 | 49.981
2021-01-16 | 12:37 | 49.983
2021-01-16 | 12:37 | 49.984
2021-01-16 | 12:37 | 49.985
2021-01-16 | 12:37 | 49.988
2021-01-16 | 12:37 | 49.989
2021-01-16 | 12:37 | 49.99
2021-01-16 | 12:37 | 49.99
2021-01-16 | 12:37 | 49.99
2021-01-16 | 12:37 | 49.988
2021-01-16 | 12:37 | 49.987
2021-01-16 | 12:37 | 49.986
2021-01-16 | 12:37 | 49.988
2021-01-16 | 12:37 | 49.989
2021-01-16 | 12:37 | 49.987
2021-01-16 | 12:37 | 49.986
2021-01-16 | 12:37 | 49.983
2021-01-16 | 12:37 | 49.982
2021-01-16 | 12:37 | 49.98
2021-01-16 | 12:37 | 49.981
2021-01-16 | 12:37 | 49.983
2021-01-16 | 12:37 | 49.984
2021-01-16 | 12:37 | 49.987
2021-01-16 | 12:37 | 49.99
2021-01-16 | 12:37 | 49.992
2021-01-16 | 12:37 | 49.993
2021-01-16 | 12:37 | 49.996
2021-01-16 | 12:37 | 49.999
2021-01-16 | 12:37 | 50
2021-01-16 | 12:37 | 50
2021-01-16 | 12:37 | 50
2021-01-16 | 12:37 | 50.002
2021-01-16 | 12:37 | 50.003
2021-01-16 | 12:37 | 50.005
2021-01-16 | 12:37 | 50.003
2021-01-16 | 12:37 | 50.001
2021-01-16 | 12:37 | 50
2021-01-16 | 12:37 | 49.999
2021-01-16 | 12:37 | 50.001
2021-01-16 | 12:37 | 50.002
2021-01-16 | 12:37 | 50.002
2021-01-16 | 12:37 | 50
2021-01-16 | 12:37 | 50
2021-01-16 | 12:38 | 49.997
2021-01-16 | 12:38 | 49.995
2021-01-16 | 12:38 | 49.989
2021-01-16 | 12:38 | 49.986
2021-01-16 | 12:38 | 49.983
2021-01-16 | 12:38 | 49.981
2021-01-16 | 12:38 | 49.981
2021-01-16 | 12:38 | 49.978
2021-01-16 | 12:38 | 49.98
2021-01-16 | 12:38 | 49.98
2021-01-16 | 12:38 | 49.981
2021-01-16 | 12:38 | 49.982
2021-01-16 | 12:38 | 49.982
2021-01-16 | 12:38 | 49.981
2021-01-16 | 12:38 | 49.983
2021-01-16 | 12:38 | 49.986
2021-01-16 | 12:38 | 49.99
2021-01-16 | 12:38 | 49.991
2021-01-16 | 12:38 | 49.991
2021-01-16 | 12:38 | 49.991
2021-01-16 | 12:38 | 49.99
2021-01-16 | 12:38 | 49.987
2021-01-16 | 12:38 | 49.984
2021-01-16 | 12:38 | 49.981
2021-01-16 | 12:38 | 49.979
2021-01-16 | 12:38 | 49.98
2021-01-16 | 12:38 | 49.982
2021-01-16 | 12:38 | 49.985
2021-01-16 | 12:38 | 49.985
2021-01-16 | 12:38 | 49.985
2021-01-16 | 12:38 | 49.985
2021-01-16 | 12:38 | 49.987
2021-01-16 | 12:38 | 49.986
2021-01-16 | 12:38 | 49.985
2021-01-16 | 12:38 | 49.983
2021-01-16 | 12:38 | 49.979
2021-01-16 | 12:38 | 49.976
2021-01-16 | 12:38 | 49.976
2021-01-16 | 12:38 | 49.974
2021-01-16 | 12:38 | 49.974
2021-01-16 | 12:38 | 49.974
2021-01-16 | 12:38 | 49.972
2021-01-16 | 12:38 | 49.965
2021-01-16 | 12:38 | 49.958
2021-01-16 | 12:38 | 49.964
2021-01-16 | 12:38 | 49.974
2021-01-16 | 12:38 | 49.98
2021-01-16 | 12:38 | 49.983
2021-01-16 | 12:38 | 49.987
2021-01-16 | 12:38 | 49.989
2021-01-16 | 12:38 | 49.992
2021-01-16 | 12:38 | 49.994
2021-01-16 | 12:38 | 49.994
2021-01-16 | 12:38 | 49.992
2021-01-16 | 12:38 | 49.989
2021-01-16 | 12:38 | 49.983
2021-01-16 | 12:38 | 49.98
2021-01-16 | 12:38 | 49.976
2021-01-16 | 12:38 | 49.976
2021-01-16 | 12:38 | 49.974
2021-01-16 | 12:39 | 49.971
2021-01-16 | 12:39 | 49.971
2021-01-16 | 12:39 | 49.972
2021-01-16 | 12:39 | 49.974
2021-01-16 | 12:39 | 49.976
2021-01-16 | 12:39 | 49.979
2021-01-16 | 12:39 | 49.983
2021-01-16 | 12:39 | 49.986
2021-01-16 | 12:39 | 49.987
2021-01-16 | 12:39 | 49.988
2021-01-16 | 12:39 | 49.988
2021-01-16 | 12:39 | 49.988
2021-01-16 | 12:39 | 49.988
2021-01-16 | 12:39 | 49.986
2021-01-16 | 12:39 | 49.985
2021-01-16 | 12:39 | 49.983
2021-01-16 | 12:39 | 49.981
2021-01-16 | 12:39 | 49.981
2021-01-16 | 12:39 | 49.982
2021-01-16 | 12:39 | 49.983
2021-01-16 | 12:39 | 49.985
2021-01-16 | 12:39 | 49.984
2021-01-16 | 12:39 | 49.984
2021-01-16 | 12:39 | 49.982
2021-01-16 | 12:39 | 49.98
2021-01-16 | 12:39 | 49.978
2021-01-16 | 12:39 | 49.979
2021-01-16 | 12:39 | 49.979
2021-01-16 | 12:39 | 49.978
2021-01-16 | 12:39 | 49.978
2021-01-16 | 12:39 | 49.977
2021-01-16 | 12:39 | 49.974
2021-01-16 | 12:39 | 49.973
2021-01-16 | 12:39 | 49.972
2021-01-16 | 12:39 | 49.971
2021-01-16 | 12:39 | 49.971
2021-01-16 | 12:39 | 49.972
2021-01-16 | 12:39 | 49.973
2021-01-16 | 12:39 | 49.973
2021-01-16 | 12:39 | 49.973
2021-01-16 | 12:39 | 49.972
2021-01-16 | 12:39 | 49.972
2021-01-16 | 12:39 | 49.972
2021-01-16 | 12:39 | 49.973
2021-01-16 | 12:39 | 49.972
2021-01-16 | 12:39 | 49.97
2021-01-16 | 12:39 | 49.968
2021-01-16 | 12:39 | 49.966
2021-01-16 | 12:39 | 49.965
2021-01-16 | 12:39 | 49.963
2021-01-16 | 12:39 | 49.961
2021-01-16 | 12:39 | 49.961
2021-01-16 | 12:39 | 49.962
2021-01-16 | 12:39 | 49.964
2021-01-16 | 12:39 | 49.966
2021-01-16 | 12:39 | 49.968
2021-01-16 | 12:39 | 49.97
2021-01-16 | 12:39 | 49.968
2021-01-16 | 12:39 | 49.967
2021-01-16 | 12:39 | 49.965
2021-01-16 | 12:39 | 49.962
2021-01-16 | 12:40 | 49.961
2021-01-16 | 12:40 | 49.961
2021-01-16 | 12:40 | 49.961
2021-01-16 | 12:40 | 49.963
2021-01-16 | 12:40 | 49.966
2021-01-16 | 12:40 | 49.969
2021-01-16 | 12:40 | 49.971
2021-01-16 | 12:40 | 49.974
2021-01-16 | 12:40 | 49.974
2021-01-16 | 12:40 | 49.975
2021-01-16 | 12:40 | 49.974
2021-01-16 | 12:40 | 49.972
2021-01-16 | 12:40 | 49.97
2021-01-16 | 12:40 | 49.971
2021-01-16 | 12:40 | 49.97
2021-01-16 | 12:40 | 49.967
2021-01-16 | 12:40 | 49.966
2021-01-16 | 12:40 | 49.965
2021-01-16 | 12:40 | 49.968
2021-01-16 | 12:40 | 49.969
2021-01-16 | 12:40 | 49.974
2021-01-16 | 12:40 | 49.977
2021-01-16 | 12:40 | 49.979
2021-01-16 | 12:40 | 49.981
2021-01-16 | 12:40 | 49.98
2021-01-16 | 12:40 | 49.979
2021-01-16 | 12:40 | 49.98
2021-01-16 | 12:40 | 49.98
2021-01-16 | 12:40 | 49.977
2021-01-16 | 12:40 | 49.976
2021-01-16 | 12:40 | 49.974
2021-01-16 | 12:40 | 49.972
2021-01-16 | 12:40 | 49.971
2021-01-16 | 12:40 | 49.969
2021-01-16 | 12:40 | 49.97
2021-01-16 | 12:40 | 49.971
2021-01-16 | 12:40 | 49.974
2021-01-16 | 12:40 | 49.975
2021-01-16 | 12:40 | 49.977
2021-01-16 | 12:40 | 49.977
2021-01-16 | 12:40 | 49.976
2021-01-16 | 12:40 | 49.976
2021-01-16 | 12:40 | 49.973
2021-01-16 | 12:40 | 49.97
2021-01-16 | 12:40 | 49.967
2021-01-16 | 12:40 | 49.965
2021-01-16 | 12:40 | 49.967
2021-01-16 | 12:40 | 49.967
2021-01-16 | 12:40 | 49.968
2021-01-16 | 12:40 | 49.97
2021-01-16 | 12:40 | 49.973
2021-01-16 | 12:40 | 49.977
2021-01-16 | 12:40 | 49.978
2021-01-16 | 12:40 | 49.981
2021-01-16 | 12:40 | 49.984
2021-01-16 | 12:40 | 49.985
2021-01-16 | 12:40 | 49.988
2021-01-16 | 12:40 | 49.991
2021-01-16 | 12:40 | 49.995
2021-01-16 | 12:41 | 49.995
2021-01-16 | 12:41 | 49.995
2021-01-16 | 12:41 | 49.995
2021-01-16 | 12:41 | 49.995
2021-01-16 | 12:41 | 49.994
2021-01-16 | 12:41 | 49.994
2021-01-16 | 12:41 | 49.996
2021-01-16 | 12:41 | 49.998
2021-01-16 | 12:41 | 50
2021-01-16 | 12:41 | 50.001
2021-01-16 | 12:41 | 50.001
2021-01-16 | 12:41 | 50
2021-01-16 | 12:41 | 49.997
2021-01-16 | 12:41 | 49.989
2021-01-16 | 12:41 | 49.981
2021-01-16 | 12:41 | 49.984
2021-01-16 | 12:41 | 49.987
2021-01-16 | 12:41 | 49.993
2021-01-16 | 12:41 | 49.996
2021-01-16 | 12:41 | 50.001
2021-01-16 | 12:41 | 50.005
2021-01-16 | 12:41 | 50.009
2021-01-16 | 12:41 | 50.011
2021-01-16 | 12:41 | 50.015
2021-01-16 | 12:41 | 50.018
2021-01-16 | 12:41 | 50.021
2021-01-16 | 12:41 | 50.022
2021-01-16 | 12:41 | 50.023
2021-01-16 | 12:41 | 50.023
2021-01-16 | 12:41 | 50.021
2021-01-16 | 12:41 | 50.02
2021-01-16 | 12:41 | 50.019
2021-01-16 | 12:41 | 50.016
2021-01-16 | 12:41 | 50.014
2021-01-16 | 12:41 | 50.013
2021-01-16 | 12:41 | 50.012
2021-01-16 | 12:41 | 50.011
2021-01-16 | 12:41 | 50.01
2021-01-16 | 12:41 | 50.008
2021-01-16 | 12:41 | 50.005
2021-01-16 | 12:41 | 50.002
2021-01-16 | 12:41 | 49.998
2021-01-16 | 12:41 | 49.995
2021-01-16 | 12:41 | 49.992
2021-01-16 | 12:41 | 49.989
2021-01-16 | 12:41 | 49.986
2021-01-16 | 12:41 | 49.984
2021-01-16 | 12:41 | 49.983
2021-01-16 | 12:41 | 49.983
2021-01-16 | 12:41 | 49.984
2021-01-16 | 12:41 | 49.987
2021-01-16 | 12:41 | 49.991
2021-01-16 | 12:41 | 49.995
2021-01-16 | 12:41 | 49.997
2021-01-16 | 12:41 | 49.997
2021-01-16 | 12:41 | 49.997
2021-01-16 | 12:41 | 49.998
2021-01-16 | 12:41 | 49.999
2021-01-16 | 12:41 | 50.002
2021-01-16 | 12:41 | 50.004
2021-01-16 | 12:41 | 50.007
2021-01-16 | 12:42 | 50.012
2021-01-16 | 12:42 | 50.015
2021-01-16 | 12:42 | 50.016
2021-01-16 | 12:42 | 50.018
2021-01-16 | 12:42 | 50.018
2021-01-16 | 12:42 | 50.016
2021-01-16 | 12:42 | 50.014
2021-01-16 | 12:42 | 50.013
2021-01-16 | 12:42 | 50.01
2021-01-16 | 12:42 | 50.009
2021-01-16 | 12:42 | 50.008
2021-01-16 | 12:42 | 50.009
2021-01-16 | 12:42 | 50.01
2021-01-16 | 12:42 | 50.01
2021-01-16 | 12:42 | 50.009
2021-01-16 | 12:42 | 50.009
2021-01-16 | 12:42 | 50.009
2021-01-16 | 12:42 | 50.009
2021-01-16 | 12:42 | 50.01
2021-01-16 | 12:42 | 50.009
2021-01-16 | 12:42 | 50.008
2021-01-16 | 12:42 | 50.007
2021-01-16 | 12:42 | 50.007
2021-01-16 | 12:42 | 50.006
2021-01-16 | 12:42 | 50.004
2021-01-16 | 12:42 | 50.004
2021-01-16 | 12:42 | 50.005
2021-01-16 | 12:42 | 50.007
2021-01-16 | 12:42 | 50.012
2021-01-16 | 12:42 | 50.017
2021-01-16 | 12:42 | 50.021
2021-01-16 | 12:42 | 50.021
2021-01-16 | 12:42 | 50.022
2021-01-16 | 12:42 | 50.021
2021-01-16 | 12:42 | 50.019
2021-01-16 | 12:42 | 50.018
2021-01-16 | 12:42 | 50.017
2021-01-16 | 12:42 | 50.014
2021-01-16 | 12:42 | 50.01
2021-01-16 | 12:42 | 50.009
2021-01-16 | 12:42 | 50.007
2021-01-16 | 12:42 | 50.005
2021-01-16 | 12:42 | 50.002
2021-01-16 | 12:42 | 50
2021-01-16 | 12:42 | 49.999
2021-01-16 | 12:42 | 49.999
2021-01-16 | 12:42 | 49.999
2021-01-16 | 12:42 | 49.998
2021-01-16 | 12:42 | 49.997
2021-01-16 | 12:42 | 49.996
2021-01-16 | 12:42 | 49.994
2021-01-16 | 12:42 | 49.994
2021-01-16 | 12:42 | 49.991
2021-01-16 | 12:42 | 49.988
2021-01-16 | 12:42 | 49.985
2021-01-16 | 12:42 | 49.982
2021-01-16 | 12:42 | 49.981
2021-01-16 | 12:42 | 49.982
2021-01-16 | 12:42 | 49.984
2021-01-16 | 12:43 | 49.986
2021-01-16 | 12:43 | 49.989
2021-01-16 | 12:43 | 49.991
2021-01-16 | 12:43 | 49.992
2021-01-16 | 12:43 | 49.995
2021-01-16 | 12:43 | 50
2021-01-16 | 12:43 | 50.004
2021-01-16 | 12:43 | 50.004
2021-01-16 | 12:43 | 50.005
2021-01-16 | 12:43 | 50.008
2021-01-16 | 12:43 | 50.01
2021-01-16 | 12:43 | 50.013
2021-01-16 | 12:43 | 50.016
2021-01-16 | 12:43 | 50.019
2021-01-16 | 12:43 | 50.021
2021-01-16 | 12:43 | 50.023
2021-01-16 | 12:43 | 50.022
2021-01-16 | 12:43 | 50.023
2021-01-16 | 12:43 | 50.025
2021-01-16 | 12:43 | 50.024
2021-01-16 | 12:43 | 50.026
2021-01-16 | 12:43 | 50.025
2021-01-16 | 12:43 | 50.026
2021-01-16 | 12:43 | 50.027
2021-01-16 | 12:43 | 50.028
2021-01-16 | 12:43 | 50.027
2021-01-16 | 12:43 | 50.029
2021-01-16 | 12:43 | 50.028
2021-01-16 | 12:43 | 50.028
2021-01-16 | 12:43 | 50.028
2021-01-16 | 12:43 | 50.027
2021-01-16 | 12:43 | 50.027
2021-01-16 | 12:43 | 50.025
2021-01-16 | 12:43 | 50.025
2021-01-16 | 12:43 | 50.025
2021-01-16 | 12:43 | 50.025
2021-01-16 | 12:43 | 50.024
2021-01-16 | 12:43 | 50.024
2021-01-16 | 12:43 | 50.024
2021-01-16 | 12:43 | 50.024
2021-01-16 | 12:43 | 50.022
2021-01-16 | 12:43 | 50.019
2021-01-16 | 12:43 | 50.017
2021-01-16 | 12:43 | 50.015
2021-01-16 | 12:43 | 50.015
2021-01-16 | 12:43 | 50.014
2021-01-16 | 12:43 | 50.013
2021-01-16 | 12:43 | 50.011
2021-01-16 | 12:43 | 50.012
2021-01-16 | 12:43 | 50.01
2021-01-16 | 12:43 | 50.009
2021-01-16 | 12:43 | 50.007
2021-01-16 | 12:43 | 50.004
2021-01-16 | 12:43 | 50.003
2021-01-16 | 12:43 | 50.003
2021-01-16 | 12:43 | 50.003
2021-01-16 | 12:43 | 50.002
2021-01-16 | 12:43 | 50.001
2021-01-16 | 12:43 | 50
2021-01-16 | 12:43 | 50
2021-01-16 | 12:43 | 50.001
2021-01-16 | 12:44 | 50.004
2021-01-16 | 12:44 | 50.004
2021-01-16 | 12:44 | 50.005
2021-01-16 | 12:44 | 50.007
2021-01-16 | 12:44 | 50.008
2021-01-16 | 12:44 | 50.012
2021-01-16 | 12:44 | 50.011
2021-01-16 | 12:44 | 50.012
2021-01-16 | 12:44 | 50.012
2021-01-16 | 12:44 | 50.011
2021-01-16 | 12:44 | 50.009
2021-01-16 | 12:44 | 50.008
2021-01-16 | 12:44 | 50.011
2021-01-16 | 12:44 | 50.016
2021-01-16 | 12:44 | 50.02
2021-01-16 | 12:44 | 50.023
2021-01-16 | 12:44 | 50.027
2021-01-16 | 12:44 | 50.029
2021-01-16 | 12:44 | 50.029
2021-01-16 | 12:44 | 50.028
2021-01-16 | 12:44 | 50.026
2021-01-16 | 12:44 | 50.025
2021-01-16 | 12:44 | 50.021
2021-01-16 | 12:44 | 50.02
2021-01-16 | 12:44 | 50.017
2021-01-16 | 12:44 | 50.016
2021-01-16 | 12:44 | 50.015
2021-01-16 | 12:44 | 50.015
2021-01-16 | 12:44 | 50.017
2021-01-16 | 12:44 | 50.018
2021-01-16 | 12:44 | 50.018
2021-01-16 | 12:44 | 50.014
2021-01-16 | 12:44 | 50.008
2021-01-16 | 12:44 | 50.01
2021-01-16 | 12:44 | 50.011
2021-01-16 | 12:44 | 50.014
2021-01-16 | 12:44 | 50.016
2021-01-16 | 12:44 | 50.018
2021-01-16 | 12:44 | 50.019
2021-01-16 | 12:44 | 50.021
2021-01-16 | 12:44 | 50.022
2021-01-16 | 12:44 | 50.023
2021-01-16 | 12:44 | 50.022
2021-01-16 | 12:44 | 50.021
2021-01-16 | 12:44 | 50.02
2021-01-16 | 12:44 | 50.02
2021-01-16 | 12:44 | 50.02
2021-01-16 | 12:44 | 50.02
2021-01-16 | 12:44 | 50.016
2021-01-16 | 12:44 | 50.014
2021-01-16 | 12:44 | 50.01
2021-01-16 | 12:44 | 50.006
2021-01-16 | 12:44 | 50.001
2021-01-16 | 12:44 | 49.996
2021-01-16 | 12:44 | 49.993
2021-01-16 | 12:44 | 49.994
2021-01-16 | 12:44 | 49.993
2021-01-16 | 12:44 | 49.993
2021-01-16 | 12:44 | 49.993
2021-01-16 | 12:45 | 49.992
2021-01-16 | 12:45 | 49.991
2021-01-16 | 12:45 | 49.99
2021-01-16 | 12:45 | 49.99
2021-01-16 | 12:45 | 49.99
2021-01-16 | 12:45 | 49.99
2021-01-16 | 12:45 | 49.989
2021-01-16 | 12:45 | 49.988
2021-01-16 | 12:45 | 49.988
2021-01-16 | 12:45 | 49.986
2021-01-16 | 12:45 | 49.985
2021-01-16 | 12:45 | 49.984
2021-01-16 | 12:45 | 49.984
2021-01-16 | 12:45 | 49.985
2021-01-16 | 12:45 | 49.986
2021-01-16 | 12:45 | 49.984
2021-01-16 | 12:45 | 49.982
2021-01-16 | 12:45 | 49.98
2021-01-16 | 12:45 | 49.978
2021-01-16 | 12:45 | 49.976
2021-01-16 | 12:45 | 49.975
2021-01-16 | 12:45 | 49.976
2021-01-16 | 12:45 | 49.978
2021-01-16 | 12:45 | 49.979
2021-01-16 | 12:45 | 49.979
2021-01-16 | 12:45 | 49.983
2021-01-16 | 12:45 | 49.984
2021-01-16 | 12:45 | 49.985
2021-01-16 | 12:45 | 49.986
2021-01-16 | 12:45 | 49.987
2021-01-16 | 12:45 | 49.988
2021-01-16 | 12:45 | 49.988
2021-01-16 | 12:45 | 49.988
2021-01-16 | 12:45 | 49.99
2021-01-16 | 12:45 | 49.991
2021-01-16 | 12:45 | 49.992
2021-01-16 | 12:45 | 49.994
2021-01-16 | 12:45 | 49.996
2021-01-16 | 12:45 | 49.998
2021-01-16 | 12:45 | 49.998
2021-01-16 | 12:45 | 49.996
2021-01-16 | 12:45 | 49.994
2021-01-16 | 12:45 | 49.992
2021-01-16 | 12:45 | 49.995
2021-01-16 | 12:45 | 49.996
2021-01-16 | 12:45 | 50
2021-01-16 | 12:45 | 50.002
2021-01-16 | 12:45 | 50.002
2021-01-16 | 12:45 | 50.002
2021-01-16 | 12:45 | 50
2021-01-16 | 12:45 | 49.999
2021-01-16 | 12:45 | 49.995
2021-01-16 | 12:45 | 49.991
2021-01-16 | 12:45 | 49.986
2021-01-16 | 12:45 | 49.983
2021-01-16 | 12:45 | 49.981
2021-01-16 | 12:45 | 49.982
2021-01-16 | 12:45 | 49.983
2021-01-16 | 12:45 | 49.986
2021-01-16 | 12:45 | 49.985
2021-01-16 | 12:45 | 49.986
2021-01-16 | 12:46 | 49.986
2021-01-16 | 12:46 | 49.984
2021-01-16 | 12:46 | 49.984
2021-01-16 | 12:46 | 49.984
2021-01-16 | 12:46 | 49.982
2021-01-16 | 12:46 | 49.981
2021-01-16 | 12:46 | 49.979
2021-01-16 | 12:46 | 49.979
2021-01-16 | 12:46 | 49.979
2021-01-16 | 12:46 | 49.981
2021-01-16 | 12:46 | 49.984
2021-01-16 | 12:46 | 49.987
2021-01-16 | 12:46 | 49.987
2021-01-16 | 12:46 | 49.986
2021-01-16 | 12:46 | 49.984
2021-01-16 | 12:46 | 49.984
2021-01-16 | 12:46 | 49.984
2021-01-16 | 12:46 | 49.983
2021-01-16 | 12:46 | 49.984
2021-01-16 | 12:46 | 49.984
2021-01-16 | 12:46 | 49.989
2021-01-16 | 12:46 | 49.99
2021-01-16 | 12:46 | 49.991
2021-01-16 | 12:46 | 49.992
2021-01-16 | 12:46 | 49.992
2021-01-16 | 12:46 | 49.993
2021-01-16 | 12:46 | 49.993
2021-01-16 | 12:46 | 49.995
2021-01-16 | 12:46 | 49.995
2021-01-16 | 12:46 | 49.995
2021-01-16 | 12:46 | 49.995
2021-01-16 | 12:46 | 49.994
2021-01-16 | 12:46 | 49.992
2021-01-16 | 12:46 | 49.994
2021-01-16 | 12:46 | 49.993
2021-01-16 | 12:46 | 49.993
2021-01-16 | 12:46 | 49.994
2021-01-16 | 12:46 | 49.994
2021-01-16 | 12:46 | 49.996
2021-01-16 | 12:46 | 49.998
2021-01-16 | 12:46 | 49.997
2021-01-16 | 12:46 | 49.995
2021-01-16 | 12:46 | 49.993
2021-01-16 | 12:46 | 49.994
2021-01-16 | 12:46 | 49.995
2021-01-16 | 12:46 | 49.998
2021-01-16 | 12:46 | 49.997
2021-01-16 | 12:46 | 49.998
2021-01-16 | 12:46 | 49.996
2021-01-16 | 12:46 | 49.995
2021-01-16 | 12:46 | 49.992
2021-01-16 | 12:46 | 49.991
2021-01-16 | 12:46 | 49.99
2021-01-16 | 12:46 | 49.988
2021-01-16 | 12:46 | 49.99
2021-01-16 | 12:46 | 49.991
2021-01-16 | 12:46 | 49.992
2021-01-16 | 12:46 | 49.995
2021-01-16 | 12:46 | 49.999
2021-01-16 | 12:47 | 49.999
2021-01-16 | 12:47 | 50.002
2021-01-16 | 12:47 | 50.003
2021-01-16 | 12:47 | 50.005
2021-01-16 | 12:47 | 50.007
2021-01-16 | 12:47 | 50.009
2021-01-16 | 12:47 | 50.011
2021-01-16 | 12:47 | 50.013
2021-01-16 | 12:47 | 50.017
2021-01-16 | 12:47 | 50.019
2021-01-16 | 12:47 | 50.025
2021-01-16 | 12:47 | 50.026
2021-01-16 | 12:47 | 50.025
2021-01-16 | 12:47 | 50.027
2021-01-16 | 12:47 | 50.028
2021-01-16 | 12:47 | 50.029
2021-01-16 | 12:47 | 50.028
2021-01-16 | 12:47 | 50.028
2021-01-16 | 12:47 | 50.029
2021-01-16 | 12:47 | 50.03
2021-01-16 | 12:47 | 50.028
2021-01-16 | 12:47 | 50.024
2021-01-16 | 12:47 | 50.022
2021-01-16 | 12:47 | 50.02
2021-01-16 | 12:47 | 50.018
2021-01-16 | 12:47 | 50.019
2021-01-16 | 12:47 | 50.019
2021-01-16 | 12:47 | 50.02
2021-01-16 | 12:47 | 50.02
2021-01-16 | 12:47 | 50.021
2021-01-16 | 12:47 | 50.023
2021-01-16 | 12:47 | 50.023
2021-01-16 | 12:47 | 50.022
2021-01-16 | 12:47 | 50.018
2021-01-16 | 12:47 | 50.014
2021-01-16 | 12:47 | 50.011
2021-01-16 | 12:47 | 50.01
2021-01-16 | 12:47 | 50.007
2021-01-16 | 12:47 | 50.005
2021-01-16 | 12:47 | 50.004
2021-01-16 | 12:47 | 50.004
2021-01-16 | 12:47 | 50.005
2021-01-16 | 12:47 | 50.01
2021-01-16 | 12:47 | 50.015
2021-01-16 | 12:47 | 50.018
2021-01-16 | 12:47 | 50.021
2021-01-16 | 12:47 | 50.025
2021-01-16 | 12:47 | 50.026
2021-01-16 | 12:47 | 50.024
2021-01-16 | 12:47 | 50.02
2021-01-16 | 12:47 | 50.02
2021-01-16 | 12:47 | 50.017
2021-01-16 | 12:47 | 50.017
2021-01-16 | 12:47 | 50.018
2021-01-16 | 12:47 | 50.017
2021-01-16 | 12:47 | 50.019
2021-01-16 | 12:47 | 50.019
2021-01-16 | 12:47 | 50.018
2021-01-16 | 12:47 | 50.018
2021-01-16 | 12:47 | 50.02
2021-01-16 | 12:47 | 50.022
2021-01-16 | 12:48 | 50.027
2021-01-16 | 12:48 | 50.03
2021-01-16 | 12:48 | 50.031
2021-01-16 | 12:48 | 50.033
2021-01-16 | 12:48 | 50.034
2021-01-16 | 12:48 | 50.036
2021-01-16 | 12:48 | 50.037
2021-01-16 | 12:48 | 50.037
2021-01-16 | 12:48 | 50.037
2021-01-16 | 12:48 | 50.036
2021-01-16 | 12:48 | 50.036
2021-01-16 | 12:48 | 50.037
2021-01-16 | 12:48 | 50.037
2021-01-16 | 12:48 | 50.037
2021-01-16 | 12:48 | 50.036
2021-01-16 | 12:48 | 50.039
2021-01-16 | 12:48 | 50.041
2021-01-16 | 12:48 | 50.043
2021-01-16 | 12:48 | 50.044
2021-01-16 | 12:48 | 50.044
2021-01-16 | 12:48 | 50.044
2021-01-16 | 12:48 | 50.046
2021-01-16 | 12:48 | 50.045
2021-01-16 | 12:48 | 50.046
2021-01-16 | 12:48 | 50.05
2021-01-16 | 12:48 | 50.051
2021-01-16 | 12:48 | 50.051
2021-01-16 | 12:48 | 50.051
2021-01-16 | 12:48 | 50.053
2021-01-16 | 12:48 | 50.055
2021-01-16 | 12:48 | 50.054
2021-01-16 | 12:48 | 50.052
2021-01-16 | 12:48 | 50.048
2021-01-16 | 12:48 | 50.047
2021-01-16 | 12:48 | 50.045
2021-01-16 | 12:48 | 50.044
2021-01-16 | 12:48 | 50.044
2021-01-16 | 12:48 | 50.043
2021-01-16 | 12:48 | 50.04
2021-01-16 | 12:48 | 50.04
2021-01-16 | 12:48 | 50.04
2021-01-16 | 12:48 | 50.04
2021-01-16 | 12:48 | 50.042
2021-01-16 | 12:48 | 50.043
2021-01-16 | 12:48 | 50.049
2021-01-16 | 12:48 | 50.05
2021-01-16 | 12:48 | 50.052
2021-01-16 | 12:48 | 50.053
2021-01-16 | 12:48 | 50.053
2021-01-16 | 12:48 | 50.053
2021-01-16 | 12:48 | 50.055
2021-01-16 | 12:48 | 50.056
2021-01-16 | 12:48 | 50.055
2021-01-16 | 12:48 | 50.055
2021-01-16 | 12:48 | 50.056
2021-01-16 | 12:48 | 50.053
2021-01-16 | 12:48 | 50.053
2021-01-16 | 12:48 | 50.053
2021-01-16 | 12:48 | 50.05
2021-01-16 | 12:49 | 50.049
2021-01-16 | 12:49 | 50.05
2021-01-16 | 12:49 | 50.046
2021-01-16 | 12:49 | 50.046
2021-01-16 | 12:49 | 50.046
2021-01-16 | 12:49 | 50.047
2021-01-16 | 12:49 | 50.049
2021-01-16 | 12:49 | 50.048
2021-01-16 | 12:49 | 50.049
2021-01-16 | 12:49 | 50.053
2021-01-16 | 12:49 | 50.055
2021-01-16 | 12:49 | 50.059
2021-01-16 | 12:49 | 50.06
2021-01-16 | 12:49 | 50.063
2021-01-16 | 12:49 | 50.065
2021-01-16 | 12:49 | 50.065
2021-01-16 | 12:49 | 50.066
2021-01-16 | 12:49 | 50.062
2021-01-16 | 12:49 | 50.06
2021-01-16 | 12:49 | 50.058
2021-01-16 | 12:49 | 50.055
2021-01-16 | 12:49 | 50.055
2021-01-16 | 12:49 | 50.055
2021-01-16 | 12:49 | 50.056
2021-01-16 | 12:49 | 50.058
2021-01-16 | 12:49 | 50.061
2021-01-16 | 12:49 | 50.061
2021-01-16 | 12:49 | 50.061
2021-01-16 | 12:49 | 50.062
2021-01-16 | 12:49 | 50.06
2021-01-16 | 12:49 | 50.06
2021-01-16 | 12:49 | 50.058
2021-01-16 | 12:49 | 50.058
2021-01-16 | 12:49 | 50.059
2021-01-16 | 12:49 | 50.059
2021-01-16 | 12:49 | 50.06
2021-01-16 | 12:49 | 50.059
2021-01-16 | 12:49 | 50.059
2021-01-16 | 12:49 | 50.056
2021-01-16 | 12:49 | 50.055
2021-01-16 | 12:49 | 50.055
2021-01-16 | 12:49 | 50.055
2021-01-16 | 12:49 | 50.052
2021-01-16 | 12:49 | 50.05
2021-01-16 | 12:49 | 50.048
2021-01-16 | 12:49 | 50.048
2021-01-16 | 12:49 | 50.051
2021-01-16 | 12:49 | 50.049
2021-01-16 | 12:49 | 50.048
2021-01-16 | 12:49 | 50.047
2021-01-16 | 12:49 | 50.046
2021-01-16 | 12:49 | 50.044
2021-01-16 | 12:49 | 50.042
2021-01-16 | 12:49 | 50.041
2021-01-16 | 12:49 | 50.039
2021-01-16 | 12:49 | 50.04
2021-01-16 | 12:49 | 50.043
2021-01-16 | 12:49 | 50.046
2021-01-16 | 12:49 | 50.047
2021-01-16 | 12:49 | 50.05
2021-01-16 | 12:49 | 50.051
2021-01-16 | 12:50 | 50.051
2021-01-16 | 12:50 | 50.053
2021-01-16 | 12:50 | 50.053
2021-01-16 | 12:50 | 50.053
2021-01-16 | 12:50 | 50.053
2021-01-16 | 12:50 | 50.052
2021-01-16 | 12:50 | 50.054
2021-01-16 | 12:50 | 50.053
2021-01-16 | 12:50 | 50.055
2021-01-16 | 12:50 | 50.054
2021-01-16 | 12:50 | 50.054
2021-01-16 | 12:50 | 50.055
2021-01-16 | 12:50 | 50.056
2021-01-16 | 12:50 | 50.059
2021-01-16 | 12:50 | 50.06
2021-01-16 | 12:50 | 50.062
2021-01-16 | 12:50 | 50.063
2021-01-16 | 12:50 | 50.062
2021-01-16 | 12:50 | 50.064
2021-01-16 | 12:50 | 50.064
2021-01-16 | 12:50 | 50.064
2021-01-16 | 12:50 | 50.062
2021-01-16 | 12:50 | 50.059
2021-01-16 | 12:50 | 50.059
2021-01-16 | 12:50 | 50.055
2021-01-16 | 12:50 | 50.053
2021-01-16 | 12:50 | 50.052
2021-01-16 | 12:50 | 50.049
2021-01-16 | 12:50 | 50.047
2021-01-16 | 12:50 | 50.045
2021-01-16 | 12:50 | 50.045
2021-01-16 | 12:50 | 50.046
2021-01-16 | 12:50 | 50.045
2021-01-16 | 12:50 | 50.045
2021-01-16 | 12:50 | 50.042
2021-01-16 | 12:50 | 50.042
2021-01-16 | 12:50 | 50.044
2021-01-16 | 12:50 | 50.044
2021-01-16 | 12:50 | 50.046
2021-01-16 | 12:50 | 50.045
2021-01-16 | 12:50 | 50.049
2021-01-16 | 12:50 | 50.053
2021-01-16 | 12:50 | 50.055
2021-01-16 | 12:50 | 50.059
2021-01-16 | 12:50 | 50.061
2021-01-16 | 12:50 | 50.066
2021-01-16 | 12:50 | 50.067
2021-01-16 | 12:50 | 50.066
2021-01-16 | 12:50 | 50.064
2021-01-16 | 12:50 | 50.062
2021-01-16 | 12:50 | 50.062
2021-01-16 | 12:50 | 50.057
2021-01-16 | 12:50 | 50.053
2021-01-16 | 12:50 | 50.048
2021-01-16 | 12:50 | 50.048
2021-01-16 | 12:50 | 50.047
2021-01-16 | 12:50 | 50.051
2021-01-16 | 12:50 | 50.053
2021-01-16 | 12:50 | 50.056
2021-01-16 | 12:51 | 50.059
2021-01-16 | 12:51 | 50.06
2021-01-16 | 12:51 | 50.062
2021-01-16 | 12:51 | 50.063
2021-01-16 | 12:51 | 50.064
2021-01-16 | 12:51 | 50.06
2021-01-16 | 12:51 | 50.057
2021-01-16 | 12:51 | 50.053
2021-01-16 | 12:51 | 50.053
2021-01-16 | 12:51 | 50.052
2021-01-16 | 12:51 | 50.052
2021-01-16 | 12:51 | 50.052
2021-01-16 | 12:51 | 50.053
2021-01-16 | 12:51 | 50.051
2021-01-16 | 12:51 | 50.049
2021-01-16 | 12:51 | 50.05
2021-01-16 | 12:51 | 50.049
2021-01-16 | 12:51 | 50.048
2021-01-16 | 12:51 | 50.047
2021-01-16 | 12:51 | 50.046
2021-01-16 | 12:51 | 50.043
2021-01-16 | 12:51 | 50.042
2021-01-16 | 12:51 | 50.044
2021-01-16 | 12:51 | 50.047
2021-01-16 | 12:51 | 50.053
2021-01-16 | 12:51 | 50.053
2021-01-16 | 12:51 | 50.055
2021-01-16 | 12:51 | 50.055
2021-01-16 | 12:51 | 50.054
2021-01-16 | 12:51 | 50.055
2021-01-16 | 12:51 | 50.053
2021-01-16 | 12:51 | 50.052
2021-01-16 | 12:51 | 50.052
2021-01-16 | 12:51 | 50.051
2021-01-16 | 12:51 | 50.05
2021-01-16 | 12:51 | 50.051
2021-01-16 | 12:51 | 50.049
2021-01-16 | 12:51 | 50.045
2021-01-16 | 12:51 | 50.043
2021-01-16 | 12:51 | 50.04
2021-01-16 | 12:51 | 50.04
2021-01-16 | 12:51 | 50.038
2021-01-16 | 12:51 | 50.032
2021-01-16 | 12:51 | 50.027
2021-01-16 | 12:51 | 50.024
2021-01-16 | 12:51 | 50.021
2021-01-16 | 12:51 | 50.02
2021-01-16 | 12:51 | 50.019
2021-01-16 | 12:51 | 50.019
2021-01-16 | 12:51 | 50.023
2021-01-16 | 12:51 | 50.022
2021-01-16 | 12:51 | 50.025
2021-01-16 | 12:51 | 50.026
2021-01-16 | 12:51 | 50.028
2021-01-16 | 12:51 | 50.029
2021-01-16 | 12:51 | 50.032
2021-01-16 | 12:51 | 50.033
2021-01-16 | 12:51 | 50.033
2021-01-16 | 12:51 | 50.034
2021-01-16 | 12:51 | 50.034
2021-01-16 | 12:51 | 50.033
2021-01-16 | 12:52 | 50.037
2021-01-16 | 12:52 | 50.038
2021-01-16 | 12:52 | 50.043
2021-01-16 | 12:52 | 50.043
2021-01-16 | 12:52 | 50.045
2021-01-16 | 12:52 | 50.046
2021-01-16 | 12:52 | 50.047
2021-01-16 | 12:52 | 50.048
2021-01-16 | 12:52 | 50.051
2021-01-16 | 12:52 | 50.053
2021-01-16 | 12:52 | 50.055
2021-01-16 | 12:52 | 50.056
2021-01-16 | 12:52 | 50.056
2021-01-16 | 12:52 | 50.06
2021-01-16 | 12:52 | 50.067
2021-01-16 | 12:52 | 50.077
2021-01-16 | 12:52 | 50.082
2021-01-16 | 12:52 | 50.086
2021-01-16 | 12:52 | 50.088
2021-01-16 | 12:52 | 50.089
2021-01-16 | 12:52 | 50.091
2021-01-16 | 12:52 | 50.091
2021-01-16 | 12:52 | 50.092
2021-01-16 | 12:52 | 50.091
2021-01-16 | 12:52 | 50.092
2021-01-16 | 12:52 | 50.092
2021-01-16 | 12:52 | 50.091
2021-01-16 | 12:52 | 50.092
2021-01-16 | 12:52 | 50.089
2021-01-16 | 12:52 | 50.088
2021-01-16 | 12:52 | 50.083
2021-01-16 | 12:52 | 50.083
2021-01-16 | 12:52 | 50.079
2021-01-16 | 12:52 | 50.076
2021-01-16 | 12:52 | 50.073
2021-01-16 | 12:52 | 50.071
2021-01-16 | 12:52 | 50.067
2021-01-16 | 12:52 | 50.066
2021-01-16 | 12:52 | 50.068
2021-01-16 | 12:52 | 50.07
2021-01-16 | 12:52 | 50.073
2021-01-16 | 12:52 | 50.076
2021-01-16 | 12:52 | 50.08
2021-01-16 | 12:52 | 50.081
2021-01-16 | 12:52 | 50.081
2021-01-16 | 12:52 | 50.08
2021-01-16 | 12:52 | 50.078
2021-01-16 | 12:52 | 50.075
2021-01-16 | 12:52 | 50.073
2021-01-16 | 12:52 | 50.071
2021-01-16 | 12:52 | 50.067
2021-01-16 | 12:52 | 50.063
2021-01-16 | 12:52 | 50.06
2021-01-16 | 12:52 | 50.06
2021-01-16 | 12:52 | 50.059
2021-01-16 | 12:52 | 50.061
2021-01-16 | 12:52 | 50.064
2021-01-16 | 12:52 | 50.067
2021-01-16 | 12:52 | 50.068
2021-01-16 | 12:52 | 50.069
2021-01-16 | 12:53 | 50.068
2021-01-16 | 12:53 | 50.07
2021-01-16 | 12:53 | 50.07
2021-01-16 | 12:53 | 50.07
2021-01-16 | 12:53 | 50.068
2021-01-16 | 12:53 | 50.065
2021-01-16 | 12:53 | 50.062
2021-01-16 | 12:53 | 50.062
2021-01-16 | 12:53 | 50.061
2021-01-16 | 12:53 | 50.063
2021-01-16 | 12:53 | 50.063
2021-01-16 | 12:53 | 50.064
2021-01-16 | 12:53 | 50.064
2021-01-16 | 12:53 | 50.065
2021-01-16 | 12:53 | 50.066
2021-01-16 | 12:53 | 50.071
2021-01-16 | 12:53 | 50.073
2021-01-16 | 12:53 | 50.077
2021-01-16 | 12:53 | 50.077
2021-01-16 | 12:53 | 50.08
2021-01-16 | 12:53 | 50.078
2021-01-16 | 12:53 | 50.078
2021-01-16 | 12:53 | 50.076
2021-01-16 | 12:53 | 50.073
2021-01-16 | 12:53 | 50.072
2021-01-16 | 12:53 | 50.07
2021-01-16 | 12:53 | 50.066
2021-01-16 | 12:53 | 50.061
2021-01-16 | 12:53 | 50.055
2021-01-16 | 12:53 | 50.055
2021-01-16 | 12:53 | 50.054
2021-01-16 | 12:53 | 50.056
2021-01-16 | 12:53 | 50.056
2021-01-16 | 12:53 | 50.059
2021-01-16 | 12:53 | 50.057
2021-01-16 | 12:53 | 50.056
2021-01-16 | 12:53 | 50.054
2021-01-16 | 12:53 | 50.053
2021-01-16 | 12:53 | 50.052
2021-01-16 | 12:53 | 50.054
2021-01-16 | 12:53 | 50.053
2021-01-16 | 12:53 | 50.055
2021-01-16 | 12:53 | 50.055
2021-01-16 | 12:53 | 50.058
2021-01-16 | 12:53 | 50.058
2021-01-16 | 12:53 | 50.06
2021-01-16 | 12:53 | 50.061
2021-01-16 | 12:53 | 50.065
2021-01-16 | 12:53 | 50.066
2021-01-16 | 12:53 | 50.065
2021-01-16 | 12:53 | 50.064
2021-01-16 | 12:53 | 50.063
2021-01-16 | 12:53 | 50.063
2021-01-16 | 12:53 | 50.064
2021-01-16 | 12:53 | 50.064
2021-01-16 | 12:53 | 50.065
2021-01-16 | 12:53 | 50.064
2021-01-16 | 12:53 | 50.065
2021-01-16 | 12:53 | 50.066
2021-01-16 | 12:54 | 50.068
2021-01-16 | 12:54 | 50.066
2021-01-16 | 12:54 | 50.064
2021-01-16 | 12:54 | 50.064
2021-01-16 | 12:54 | 50.062
2021-01-16 | 12:54 | 50.061
2021-01-16 | 12:54 | 50.062
2021-01-16 | 12:54 | 50.062
2021-01-16 | 12:54 | 50.061
2021-01-16 | 12:54 | 50.064
2021-01-16 | 12:54 | 50.063
2021-01-16 | 12:54 | 50.065
2021-01-16 | 12:54 | 50.068
2021-01-16 | 12:54 | 50.065
2021-01-16 | 12:54 | 50.06
2021-01-16 | 12:54 | 50.058
2021-01-16 | 12:54 | 50.057
2021-01-16 | 12:54 | 50.055
2021-01-16 | 12:54 | 50.056
2021-01-16 | 12:54 | 50.057
2021-01-16 | 12:54 | 50.054
2021-01-16 | 12:54 | 50.054
2021-01-16 | 12:54 | 50.052
2021-01-16 | 12:54 | 50.052
2021-01-16 | 12:54 | 50.053
2021-01-16 | 12:54 | 50.054
2021-01-16 | 12:54 | 50.053
2021-01-16 | 12:54 | 50.053
2021-01-16 | 12:54 | 50.054
2021-01-16 | 12:54 | 50.057
2021-01-16 | 12:54 | 50.057
2021-01-16 | 12:54 | 50.059
2021-01-16 | 12:54 | 50.059
2021-01-16 | 12:54 | 50.06
2021-01-16 | 12:54 | 50.061
2021-01-16 | 12:54 | 50.063
2021-01-16 | 12:54 | 50.063
2021-01-16 | 12:54 | 50.064
2021-01-16 | 12:54 | 50.063
2021-01-16 | 12:54 | 50.063
2021-01-16 | 12:54 | 50.059
2021-01-16 | 12:54 | 50.059
2021-01-16 | 12:54 | 50.059
2021-01-16 | 12:54 | 50.057
2021-01-16 | 12:54 | 50.057
2021-01-16 | 12:54 | 50.057
2021-01-16 | 12:54 | 50.058
2021-01-16 | 12:54 | 50.058
2021-01-16 | 12:54 | 50.06
2021-01-16 | 12:54 | 50.06
2021-01-16 | 12:54 | 50.058
2021-01-16 | 12:54 | 50.058
2021-01-16 | 12:54 | 50.054
2021-01-16 | 12:54 | 50.051
2021-01-16 | 12:54 | 50.049
2021-01-16 | 12:54 | 50.048
2021-01-16 | 12:54 | 50.047
2021-01-16 | 12:54 | 50.048
2021-01-16 | 12:54 | 50.05
2021-01-16 | 12:54 | 50.056
2021-01-16 | 12:54 | 50.058
2021-01-16 | 12:55 | 50.062
2021-01-16 | 12:55 | 50.062
2021-01-16 | 12:55 | 50.064
2021-01-16 | 12:55 | 50.062
2021-01-16 | 12:55 | 50.064
2021-01-16 | 12:55 | 50.06
2021-01-16 | 12:55 | 50.061
2021-01-16 | 12:55 | 50.058
2021-01-16 | 12:55 | 50.059
2021-01-16 | 12:55 | 50.056
2021-01-16 | 12:55 | 50.055
2021-01-16 | 12:55 | 50.051
2021-01-16 | 12:55 | 50.049
2021-01-16 | 12:55 | 50.049
2021-01-16 | 12:55 | 50.049
2021-01-16 | 12:55 | 50.054
2021-01-16 | 12:55 | 50.055
2021-01-16 | 12:55 | 50.054
2021-01-16 | 12:55 | 50.053
2021-01-16 | 12:55 | 50.055
2021-01-16 | 12:55 | 50.058
2021-01-16 | 12:55 | 50.059
2021-01-16 | 12:55 | 50.063
2021-01-16 | 12:55 | 50.066
2021-01-16 | 12:55 | 50.068
2021-01-16 | 12:55 | 50.067
2021-01-16 | 12:55 | 50.067
2021-01-16 | 12:55 | 50.066
2021-01-16 | 12:55 | 50.065
2021-01-16 | 12:55 | 50.065
2021-01-16 | 12:55 | 50.062
2021-01-16 | 12:55 | 50.059
2021-01-16 | 12:55 | 50.058
2021-01-16 | 12:55 | 50.057
2021-01-16 | 12:55 | 50.06
2021-01-16 | 12:55 | 50.062
2021-01-16 | 12:55 | 50.062
2021-01-16 | 12:55 | 50.068
2021-01-16 | 12:55 | 50.07
2021-01-16 | 12:55 | 50.073
2021-01-16 | 12:55 | 50.074
2021-01-16 | 12:55 | 50.075
2021-01-16 | 12:55 | 50.074
2021-01-16 | 12:55 | 50.075
2021-01-16 | 12:55 | 50.073
2021-01-16 | 12:55 | 50.075
2021-01-16 | 12:55 | 50.073
2021-01-16 | 12:55 | 50.074
2021-01-16 | 12:55 | 50.074
2021-01-16 | 12:55 | 50.075
2021-01-16 | 12:55 | 50.075
2021-01-16 | 12:55 | 50.076
2021-01-16 | 12:55 | 50.077
2021-01-16 | 12:55 | 50.077
2021-01-16 | 12:55 | 50.075
2021-01-16 | 12:55 | 50.075
2021-01-16 | 12:55 | 50.075
2021-01-16 | 12:55 | 50.076
2021-01-16 | 12:55 | 50.073
2021-01-16 | 12:56 | 50.072
2021-01-16 | 12:56 | 50.07
2021-01-16 | 12:56 | 50.067
2021-01-16 | 12:56 | 50.067
2021-01-16 | 12:56 | 50.066
2021-01-16 | 12:56 | 50.068
2021-01-16 | 12:56 | 50.068
2021-01-16 | 12:56 | 50.069
2021-01-16 | 12:56 | 50.068
2021-01-16 | 12:56 | 50.069
2021-01-16 | 12:56 | 50.069
2021-01-16 | 12:56 | 50.07
2021-01-16 | 12:56 | 50.068
2021-01-16 | 12:56 | 50.067
2021-01-16 | 12:56 | 50.064
2021-01-16 | 12:56 | 50.061
2021-01-16 | 12:56 | 50.058
2021-01-16 | 12:56 | 50.051
2021-01-16 | 12:56 | 50.045
2021-01-16 | 12:56 | 50.041
2021-01-16 | 12:56 | 50.041
2021-01-16 | 12:56 | 50.036
2021-01-16 | 12:56 | 50.036
2021-01-16 | 12:56 | 50.034
2021-01-16 | 12:56 | 50.039
2021-01-16 | 12:56 | 50.033
2021-01-16 | 12:56 | 50.031
2021-01-16 | 12:56 | 50.028
2021-01-16 | 12:56 | 50.026
2021-01-16 | 12:56 | 50.028
2021-01-16 | 12:56 | 50.024
2021-01-16 | 12:56 | 50.022
2021-01-16 | 12:56 | 50.019
2021-01-16 | 12:56 | 50.017
2021-01-16 | 12:56 | 50.017
2021-01-16 | 12:56 | 50.017
2021-01-16 | 12:56 | 50.02
2021-01-16 | 12:56 | 50.023
2021-01-16 | 12:56 | 50.027
2021-01-16 | 12:56 | 50.031
2021-01-16 | 12:56 | 50.032
2021-01-16 | 12:56 | 50.035
2021-01-16 | 12:56 | 50.035
2021-01-16 | 12:56 | 50.035
2021-01-16 | 12:56 | 50.035
2021-01-16 | 12:56 | 50.035
2021-01-16 | 12:56 | 50.034
2021-01-16 | 12:56 | 50.034
2021-01-16 | 12:56 | 50.032
2021-01-16 | 12:56 | 50.031
2021-01-16 | 12:56 | 50.029
2021-01-16 | 12:56 | 50.027
2021-01-16 | 12:56 | 50.025
2021-01-16 | 12:56 | 50.024
2021-01-16 | 12:56 | 50.024
2021-01-16 | 12:56 | 50.022
2021-01-16 | 12:56 | 50.019
2021-01-16 | 12:56 | 50.016
2021-01-16 | 12:56 | 50.014
2021-01-16 | 12:56 | 50.014
2021-01-16 | 12:56 | 50.015
2021-01-16 | 12:57 | 50.017
2021-01-16 | 12:57 | 50.02
2021-01-16 | 12:57 | 50.021
2021-01-16 | 12:57 | 50.025
2021-01-16 | 12:57 | 50.031
2021-01-16 | 12:57 | 50.035
2021-01-16 | 12:57 | 50.036
2021-01-16 | 12:57 | 50.039
2021-01-16 | 12:57 | 50.041
2021-01-16 | 12:57 | 50.042
2021-01-16 | 12:57 | 50.044
2021-01-16 | 12:57 | 50.044
2021-01-16 | 12:57 | 50.046
2021-01-16 | 12:57 | 50.045
2021-01-16 | 12:57 | 50.046
2021-01-16 | 12:57 | 50.045
2021-01-16 | 12:57 | 50.045
2021-01-16 | 12:57 | 50.043
2021-01-16 | 12:57 | 50.041
2021-01-16 | 12:57 | 50.041
2021-01-16 | 12:57 | 50.042
2021-01-16 | 12:57 | 50.041
2021-01-16 | 12:57 | 50.037
2021-01-16 | 12:57 | 50.034
2021-01-16 | 12:57 | 50.031
2021-01-16 | 12:57 | 50.028
2021-01-16 | 12:57 | 50.026
2021-01-16 | 12:57 | 50.024
2021-01-16 | 12:57 | 50.019
2021-01-16 | 12:57 | 50.018
2021-01-16 | 12:57 | 50.016
2021-01-16 | 12:57 | 50.014
2021-01-16 | 12:57 | 50.012
2021-01-16 | 12:57 | 50.013
2021-01-16 | 12:57 | 50.013
2021-01-16 | 12:57 | 50.011
2021-01-16 | 12:57 | 50.011
2021-01-16 | 12:57 | 50.011
2021-01-16 | 12:57 | 50.008
2021-01-16 | 12:57 | 50.007
2021-01-16 | 12:57 | 50.006
2021-01-16 | 12:57 | 50.005
2021-01-16 | 12:57 | 50.003
2021-01-16 | 12:57 | 49.999
2021-01-16 | 12:57 | 49.999
2021-01-16 | 12:57 | 49.999
2021-01-16 | 12:57 | 49.998
2021-01-16 | 12:57 | 50
2021-01-16 | 12:57 | 50
2021-01-16 | 12:57 | 50.001
2021-01-16 | 12:57 | 50.004
2021-01-16 | 12:57 | 50.005
2021-01-16 | 12:57 | 50.007
2021-01-16 | 12:57 | 50.008
2021-01-16 | 12:57 | 50.012
2021-01-16 | 12:57 | 50.013
2021-01-16 | 12:57 | 50.016
2021-01-16 | 12:57 | 50.018
2021-01-16 | 12:57 | 50.02
2021-01-16 | 12:58 | 50.023
2021-01-16 | 12:58 | 50.023
2021-01-16 | 12:58 | 50.023
2021-01-16 | 12:58 | 50.021
2021-01-16 | 12:58 | 50.019
2021-01-16 | 12:58 | 50.018
2021-01-16 | 12:58 | 50.015
2021-01-16 | 12:58 | 50.013
2021-01-16 | 12:58 | 50.01
2021-01-16 | 12:58 | 50.009
2021-01-16 | 12:58 | 50.006
2021-01-16 | 12:58 | 50.002
2021-01-16 | 12:58 | 49.998
2021-01-16 | 12:58 | 49.994
2021-01-16 | 12:58 | 49.989
2021-01-16 | 12:58 | 49.986
2021-01-16 | 12:58 | 49.983
2021-01-16 | 12:58 | 49.978
2021-01-16 | 12:58 | 49.979
2021-01-16 | 12:58 | 49.975
2021-01-16 | 12:58 | 49.973
2021-01-16 | 12:58 | 49.972
2021-01-16 | 12:58 | 49.974
2021-01-16 | 12:58 | 49.973
2021-01-16 | 12:58 | 49.976
2021-01-16 | 12:58 | 49.98
2021-01-16 | 12:58 | 49.983
2021-01-16 | 12:58 | 49.982
2021-01-16 | 12:58 | 49.981
2021-01-16 | 12:58 | 49.982
2021-01-16 | 12:58 | 49.98
2021-01-16 | 12:58 | 49.975
2021-01-16 | 12:58 | 49.974
2021-01-16 | 12:58 | 49.972
2021-01-16 | 12:58 | 49.971
2021-01-16 | 12:58 | 49.971
2021-01-16 | 12:58 | 49.972
2021-01-16 | 12:58 | 49.973
2021-01-16 | 12:58 | 49.971
2021-01-16 | 12:58 | 49.967
2021-01-16 | 12:58 | 49.965
2021-01-16 | 12:58 | 49.964
2021-01-16 | 12:58 | 49.963
2021-01-16 | 12:58 | 49.962
2021-01-16 | 12:58 | 49.958
2021-01-16 | 12:58 | 49.955
2021-01-16 | 12:58 | 49.954
2021-01-16 | 12:58 | 49.954
2021-01-16 | 12:58 | 49.956
2021-01-16 | 12:58 | 49.954
2021-01-16 | 12:58 | 49.955
2021-01-16 | 12:58 | 49.954
2021-01-16 | 12:58 | 49.954
2021-01-16 | 12:58 | 49.953
2021-01-16 | 12:58 | 49.954
2021-01-16 | 12:58 | 49.954
2021-01-16 | 12:58 | 49.953
2021-01-16 | 12:58 | 49.953
2021-01-16 | 12:58 | 49.955
2021-01-16 | 12:58 | 49.956
2021-01-16 | 12:58 | 49.958
2021-01-16 | 12:59 | 49.958
2021-01-16 | 12:59 | 49.957
2021-01-16 | 12:59 | 49.956
2021-01-16 | 12:59 | 49.956
2021-01-16 | 12:59 | 49.956
2021-01-16 | 12:59 | 49.957
2021-01-16 | 12:59 | 49.958
2021-01-16 | 12:59 | 49.958
2021-01-16 | 12:59 | 49.956
2021-01-16 | 12:59 | 49.954
2021-01-16 | 12:59 | 49.952
2021-01-16 | 12:59 | 49.95
2021-01-16 | 12:59 | 49.948
2021-01-16 | 12:59 | 49.948
2021-01-16 | 12:59 | 49.947
2021-01-16 | 12:59 | 49.947
2021-01-16 | 12:59 | 49.949
2021-01-16 | 12:59 | 49.951
2021-01-16 | 12:59 | 49.953
2021-01-16 | 12:59 | 49.956
2021-01-16 | 12:59 | 49.957
2021-01-16 | 12:59 | 49.959
2021-01-16 | 12:59 | 49.961
2021-01-16 | 12:59 | 49.961
2021-01-16 | 12:59 | 49.961
2021-01-16 | 12:59 | 49.959
2021-01-16 | 12:59 | 49.957
2021-01-16 | 12:59 | 49.957
2021-01-16 | 12:59 | 49.955
2021-01-16 | 12:59 | 49.954
2021-01-16 | 12:59 | 49.952
2021-01-16 | 12:59 | 49.949
2021-01-16 | 12:59 | 49.949
2021-01-16 | 12:59 | 49.949
2021-01-16 | 12:59 | 49.95
2021-01-16 | 12:59 | 49.952
2021-01-16 | 12:59 | 49.952
2021-01-16 | 12:59 | 49.953
2021-01-16 | 12:59 | 49.952
2021-01-16 | 12:59 | 49.95
2021-01-16 | 12:59 | 49.948
2021-01-16 | 12:59 | 49.945
2021-01-16 | 12:59 | 49.941
2021-01-16 | 12:59 | 49.939
2021-01-16 | 12:59 | 49.937
2021-01-16 | 12:59 | 49.933
2021-01-16 | 12:59 | 49.933
2021-01-16 | 12:59 | 49.933
2021-01-16 | 12:59 | 49.935
2021-01-16 | 12:59 | 49.938
2021-01-16 | 12:59 | 49.939
2021-01-16 | 12:59 | 49.94
2021-01-16 | 12:59 | 49.94
2021-01-16 | 12:59 | 49.939
2021-01-16 | 12:59 | 49.936
2021-01-16 | 12:59 | 49.934
2021-01-16 | 12:59 | 49.933
2021-01-16 | 12:59 | 49.933
2021-01-16 | 12:59 | 49.935
2021-01-16 | 13:00 | 49.936
2021-01-16 | 13:00 | 49.937
2021-01-16 | 13:00 | 49.937
2021-01-16 | 13:00 | 49.936
2021-01-16 | 13:00 | 49.935
2021-01-16 | 13:00 | 49.935
2021-01-16 | 13:00 | 49.935
2021-01-16 | 13:00 | 49.936
2021-01-16 | 13:00 | 49.932
2021-01-16 | 13:00 | 49.93
2021-01-16 | 13:00 | 49.926
2021-01-16 | 13:00 | 49.925
2021-01-16 | 13:00 | 49.922
2021-01-16 | 13:00 | 49.921
2021-01-16 | 13:00 | 49.921
2021-01-16 | 13:00 | 49.922
2021-01-16 | 13:00 | 49.927
2021-01-16 | 13:00 | 49.932
2021-01-16 | 13:00 | 49.935
2021-01-16 | 13:00 | 49.939
2021-01-16 | 13:00 | 49.939
2021-01-16 | 13:00 | 49.939
2021-01-16 | 13:00 | 49.934
2021-01-16 | 13:00 | 49.932
2021-01-16 | 13:00 | 49.926
2021-01-16 | 13:00 | 49.922
2021-01-16 | 13:00 | 49.917
2021-01-16 | 13:00 | 49.915
2021-01-16 | 13:00 | 49.912
2021-01-16 | 13:00 | 49.909
2021-01-16 | 13:00 | 49.908
2021-01-16 | 13:00 | 49.903
2021-01-16 | 13:00 | 49.901
2021-01-16 | 13:00 | 49.897
2021-01-16 | 13:00 | 49.896
2021-01-16 | 13:00 | 49.897
2021-01-16 | 13:00 | 49.897
2021-01-16 | 13:00 | 49.9
2021-01-16 | 13:00 | 49.901
2021-01-16 | 13:00 | 49.901
2021-01-16 | 13:00 | 49.901
2021-01-16 | 13:00 | 49.9
2021-01-16 | 13:00 | 49.896
2021-01-16 | 13:00 | 49.893
2021-01-16 | 13:00 | 49.891
2021-01-16 | 13:00 | 49.891
2021-01-16 | 13:00 | 49.892
2021-01-16 | 13:00 | 49.895
2021-01-16 | 13:00 | 49.897
2021-01-16 | 13:00 | 49.9
2021-01-16 | 13:00 | 49.9
2021-01-16 | 13:00 | 49.898
2021-01-16 | 13:00 | 49.896
2021-01-16 | 13:00 | 49.895
2021-01-16 | 13:00 | 49.893
2021-01-16 | 13:00 | 49.894
2021-01-16 | 13:00 | 49.893
2021-01-16 | 13:00 | 49.89
2021-01-16 | 13:00 | 49.889
2021-01-16 | 13:00 | 49.888
2021-01-16 | 13:00 | 49.888
2021-01-16 | 13:01 | 49.888
2021-01-16 | 13:01 | 49.892
2021-01-16 | 13:01 | 49.896
2021-01-16 | 13:01 | 49.901
2021-01-16 | 13:01 | 49.902
2021-01-16 | 13:01 | 49.902
2021-01-16 | 13:01 | 49.901
2021-01-16 | 13:01 | 49.9
2021-01-16 | 13:01 | 49.894
2021-01-16 | 13:01 | 49.889
2021-01-16 | 13:01 | 49.889
2021-01-16 | 13:01 | 49.891
2021-01-16 | 13:01 | 49.893
2021-01-16 | 13:01 | 49.894
2021-01-16 | 13:01 | 49.894
2021-01-16 | 13:01 | 49.893
2021-01-16 | 13:01 | 49.893
2021-01-16 | 13:01 | 49.891
2021-01-16 | 13:01 | 49.89
2021-01-16 | 13:01 | 49.889
2021-01-16 | 13:01 | 49.886
2021-01-16 | 13:01 | 49.886
2021-01-16 | 13:01 | 49.889
2021-01-16 | 13:01 | 49.889
2021-01-16 | 13:01 | 49.89
2021-01-16 | 13:01 | 49.888
2021-01-16 | 13:01 | 49.885
2021-01-16 | 13:01 | 49.882
2021-01-16 | 13:01 | 49.882
2021-01-16 | 13:01 | 49.882
2021-01-16 | 13:01 | 49.88
2021-01-16 | 13:01 | 49.878
2021-01-16 | 13:01 | 49.876
2021-01-16 | 13:01 | 49.873
2021-01-16 | 13:01 | 49.871
2021-01-16 | 13:01 | 49.87
2021-01-16 | 13:01 | 49.868
2021-01-16 | 13:01 | 49.868
2021-01-16 | 13:01 | 49.869
2021-01-16 | 13:01 | 49.868
2021-01-16 | 13:01 | 49.869
2021-01-16 | 13:01 | 49.867
2021-01-16 | 13:01 | 49.867
2021-01-16 | 13:01 | 49.868
2021-01-16 | 13:01 | 49.871
2021-01-16 | 13:01 | 49.873
2021-01-16 | 13:01 | 49.874
2021-01-16 | 13:01 | 49.875
2021-01-16 | 13:01 | 49.877
2021-01-16 | 13:01 | 49.878
2021-01-16 | 13:01 | 49.88
2021-01-16 | 13:01 | 49.88
2021-01-16 | 13:01 | 49.878
2021-01-16 | 13:01 | 49.879
2021-01-16 | 13:01 | 49.877
2021-01-16 | 13:01 | 49.876
2021-01-16 | 13:01 | 49.876
2021-01-16 | 13:01 | 49.876
2021-01-16 | 13:01 | 49.876
2021-01-16 | 13:02 | 49.875
2021-01-16 | 13:02 | 49.873
2021-01-16 | 13:02 | 49.873
2021-01-16 | 13:02 | 49.872
2021-01-16 | 13:02 | 49.875
2021-01-16 | 13:02 | 49.876
2021-01-16 | 13:02 | 49.876
2021-01-16 | 13:02 | 49.878
2021-01-16 | 13:02 | 49.879
2021-01-16 | 13:02 | 49.879
2021-01-16 | 13:02 | 49.879
2021-01-16 | 13:02 | 49.879
2021-01-16 | 13:02 | 49.884
2021-01-16 | 13:02 | 49.886
2021-01-16 | 13:02 | 49.89
2021-01-16 | 13:02 | 49.889
2021-01-16 | 13:02 | 49.889
2021-01-16 | 13:02 | 49.886
2021-01-16 | 13:02 | 49.884
2021-01-16 | 13:02 | 49.881
2021-01-16 | 13:02 | 49.877
2021-01-16 | 13:02 | 49.874
2021-01-16 | 13:02 | 49.87
2021-01-16 | 13:02 | 49.866
2021-01-16 | 13:02 | 49.863
2021-01-16 | 13:02 | 49.862
2021-01-16 | 13:02 | 49.861
2021-01-16 | 13:02 | 49.861
2021-01-16 | 13:02 | 49.862
2021-01-16 | 13:02 | 49.864
2021-01-16 | 13:02 | 49.864
2021-01-16 | 13:02 | 49.866
2021-01-16 | 13:02 | 49.869
2021-01-16 | 13:02 | 49.871
2021-01-16 | 13:02 | 49.874
2021-01-16 | 13:02 | 49.879
2021-01-16 | 13:02 | 49.882
2021-01-16 | 13:02 | 49.885
2021-01-16 | 13:02 | 49.887
2021-01-16 | 13:02 | 49.889
2021-01-16 | 13:02 | 49.893
2021-01-16 | 13:02 | 49.898
2021-01-16 | 13:02 | 49.902
2021-01-16 | 13:02 | 49.904
2021-01-16 | 13:02 | 49.905
2021-01-16 | 13:02 | 49.903
2021-01-16 | 13:02 | 49.902
2021-01-16 | 13:02 | 49.9
2021-01-16 | 13:02 | 49.898
2021-01-16 | 13:02 | 49.896
2021-01-16 | 13:02 | 49.892
2021-01-16 | 13:02 | 49.89
2021-01-16 | 13:02 | 49.888
2021-01-16 | 13:02 | 49.888
2021-01-16 | 13:02 | 49.888
2021-01-16 | 13:02 | 49.889
2021-01-16 | 13:02 | 49.891
2021-01-16 | 13:02 | 49.894
2021-01-16 | 13:02 | 49.893
2021-01-16 | 13:02 | 49.894
2021-01-16 | 13:02 | 49.896
2021-01-16 | 13:03 | 49.894
2021-01-16 | 13:03 | 49.896
2021-01-16 | 13:03 | 49.895
2021-01-16 | 13:03 | 49.89
2021-01-16 | 13:03 | 49.883
2021-01-16 | 13:03 | 49.879
2021-01-16 | 13:03 | 49.879
2021-01-16 | 13:03 | 49.879
2021-01-16 | 13:03 | 49.88
2021-01-16 | 13:03 | 49.883
2021-01-16 | 13:03 | 49.886
2021-01-16 | 13:03 | 49.89
2021-01-16 | 13:03 | 49.894
2021-01-16 | 13:03 | 49.909
2021-01-16 | 13:03 | 49.901
2021-01-16 | 13:03 | 49.903
2021-01-16 | 13:03 | 49.904
2021-01-16 | 13:03 | 49.906
2021-01-16 | 13:03 | 49.907
2021-01-16 | 13:03 | 49.908
2021-01-16 | 13:03 | 49.907
2021-01-16 | 13:03 | 49.907
2021-01-16 | 13:03 | 49.909
2021-01-16 | 13:03 | 49.912
2021-01-16 | 13:03 | 49.915
2021-01-16 | 13:03 | 49.918
2021-01-16 | 13:03 | 49.922
2021-01-16 | 13:03 | 49.922
2021-01-16 | 13:03 | 49.926
2021-01-16 | 13:03 | 49.928
2021-01-16 | 13:03 | 49.929
2021-01-16 | 13:03 | 49.928
2021-01-16 | 13:03 | 49.928
2021-01-16 | 13:03 | 49.925
2021-01-16 | 13:03 | 49.924
2021-01-16 | 13:03 | 49.922
2021-01-16 | 13:03 | 49.919
2021-01-16 | 13:03 | 49.916
2021-01-16 | 13:03 | 49.915
2021-01-16 | 13:03 | 49.913
2021-01-16 | 13:03 | 49.911
2021-01-16 | 13:03 | 49.908
2021-01-16 | 13:03 | 49.907
2021-01-16 | 13:03 | 49.905
2021-01-16 | 13:03 | 49.904
2021-01-16 | 13:03 | 49.905
2021-01-16 | 13:03 | 49.904
2021-01-16 | 13:03 | 49.902
2021-01-16 | 13:03 | 49.901
2021-01-16 | 13:03 | 49.901
2021-01-16 | 13:03 | 49.901
2021-01-16 | 13:03 | 49.901
2021-01-16 | 13:03 | 49.903
2021-01-16 | 13:03 | 49.908
2021-01-16 | 13:03 | 49.914
2021-01-16 | 13:03 | 49.919
2021-01-16 | 13:03 | 49.922
2021-01-16 | 13:03 | 49.924
2021-01-16 | 13:03 | 49.923
2021-01-16 | 13:04 | 49.923
2021-01-16 | 13:04 | 49.924
2021-01-16 | 13:04 | 49.924
2021-01-16 | 13:04 | 49.924
2021-01-16 | 13:04 | 49.921
2021-01-16 | 13:04 | 49.921
2021-01-16 | 13:04 | 49.92
2021-01-16 | 13:04 | 49.921
2021-01-16 | 13:04 | 49.925
2021-01-16 | 13:04 | 49.928
2021-01-16 | 13:04 | 49.929
2021-01-16 | 13:04 | 49.929
2021-01-16 | 13:04 | 49.93
2021-01-16 | 13:04 | 49.929
2021-01-16 | 13:04 | 49.927
2021-01-16 | 13:04 | 49.925
2021-01-16 | 13:04 | 49.923
2021-01-16 | 13:04 | 49.922
2021-01-16 | 13:04 | 49.922
2021-01-16 | 13:04 | 49.922
2021-01-16 | 13:04 | 49.923
2021-01-16 | 13:04 | 49.923
2021-01-16 | 13:04 | 49.922
2021-01-16 | 13:04 | 49.922
2021-01-16 | 13:04 | 49.923
2021-01-16 | 13:04 | 49.925
2021-01-16 | 13:04 | 49.929
2021-01-16 | 13:04 | 49.935
2021-01-16 | 13:04 | 49.94
2021-01-16 | 13:04 | 49.942
2021-01-16 | 13:04 | 49.942
2021-01-16 | 13:04 | 49.94
2021-01-16 | 13:04 | 49.938
2021-01-16 | 13:04 | 49.938
2021-01-16 | 13:04 | 49.934
2021-01-16 | 13:04 | 49.933
2021-01-16 | 13:04 | 49.932
2021-01-16 | 13:04 | 49.933
2021-01-16 | 13:04 | 49.932
2021-01-16 | 13:04 | 49.934
2021-01-16 | 13:04 | 49.936
2021-01-16 | 13:04 | 49.941
2021-01-16 | 13:04 | 49.944
2021-01-16 | 13:04 | 49.946
2021-01-16 | 13:04 | 49.948
2021-01-16 | 13:04 | 49.948
2021-01-16 | 13:04 | 49.948
2021-01-16 | 13:04 | 49.949
2021-01-16 | 13:04 | 49.948
2021-01-16 | 13:04 | 49.944
2021-01-16 | 13:04 | 49.941
2021-01-16 | 13:04 | 49.94
2021-01-16 | 13:04 | 49.94
2021-01-16 | 13:04 | 49.943
2021-01-16 | 13:04 | 49.946
2021-01-16 | 13:04 | 49.951
2021-01-16 | 13:04 | 49.954
2021-01-16 | 13:04 | 49.955
2021-01-16 | 13:04 | 49.956
2021-01-16 | 13:04 | 49.956
2021-01-16 | 13:04 | 49.957
2021-01-16 | 13:05 | 49.955
2021-01-16 | 13:05 | 49.954
2021-01-16 | 13:05 | 49.952
2021-01-16 | 13:05 | 49.951
2021-01-16 | 13:05 | 49.952
2021-01-16 | 13:05 | 49.951
2021-01-16 | 13:05 | 49.952
2021-01-16 | 13:05 | 49.951
2021-01-16 | 13:05 | 49.954
2021-01-16 | 13:05 | 49.954
2021-01-16 | 13:05 | 49.954
2021-01-16 | 13:05 | 49.952
2021-01-16 | 13:05 | 49.949
2021-01-16 | 13:05 | 49.951
2021-01-16 | 13:05 | 49.954
2021-01-16 | 13:05 | 49.955
2021-01-16 | 13:05 | 49.954
2021-01-16 | 13:05 | 49.951
2021-01-16 | 13:05 | 49.95
2021-01-16 | 13:05 | 49.946
2021-01-16 | 13:05 | 49.944
2021-01-16 | 13:05 | 49.942
2021-01-16 | 13:05 | 49.943
2021-01-16 | 13:05 | 49.946
2021-01-16 | 13:05 | 49.949
2021-01-16 | 13:05 | 49.95
2021-01-16 | 13:05 | 49.954
2021-01-16 | 13:05 | 49.956
2021-01-16 | 13:05 | 49.956
2021-01-16 | 13:05 | 49.957
2021-01-16 | 13:05 | 49.953
2021-01-16 | 13:05 | 49.948
2021-01-16 | 13:05 | 49.946
2021-01-16 | 13:05 | 49.945
2021-01-16 | 13:05 | 49.942
2021-01-16 | 13:05 | 49.942
2021-01-16 | 13:05 | 49.942
2021-01-16 | 13:05 | 49.941
2021-01-16 | 13:05 | 49.941
2021-01-16 | 13:05 | 49.94
2021-01-16 | 13:05 | 49.941
2021-01-16 | 13:05 | 49.943
2021-01-16 | 13:05 | 49.943
2021-01-16 | 13:05 | 49.946
2021-01-16 | 13:05 | 49.946
2021-01-16 | 13:05 | 49.948
2021-01-16 | 13:05 | 49.949
2021-01-16 | 13:05 | 49.952
2021-01-16 | 13:05 | 49.954
2021-01-16 | 13:05 | 49.954
2021-01-16 | 13:05 | 49.954
2021-01-16 | 13:05 | 49.954
2021-01-16 | 13:05 | 49.952
2021-01-16 | 13:05 | 49.949
2021-01-16 | 13:05 | 49.949
2021-01-16 | 13:05 | 49.947
2021-01-16 | 13:05 | 49.946
2021-01-16 | 13:05 | 49.946
2021-01-16 | 13:05 | 49.947
2021-01-16 | 13:06 | 49.945
2021-01-16 | 13:06 | 49.945
2021-01-16 | 13:06 | 49.944
2021-01-16 | 13:06 | 49.943
2021-01-16 | 13:06 | 49.943
2021-01-16 | 13:06 | 49.944
2021-01-16 | 13:06 | 49.945
2021-01-16 | 13:06 | 49.945
2021-01-16 | 13:06 | 49.944
2021-01-16 | 13:06 | 49.945
2021-01-16 | 13:06 | 49.947
2021-01-16 | 13:06 | 49.947
2021-01-16 | 13:06 | 49.948
2021-01-16 | 13:06 | 49.949
2021-01-16 | 13:06 | 49.949
2021-01-16 | 13:06 | 49.95
2021-01-16 | 13:06 | 49.955
2021-01-16 | 13:06 | 49.957
2021-01-16 | 13:06 | 49.958
2021-01-16 | 13:06 | 49.958
2021-01-16 | 13:06 | 49.959
2021-01-16 | 13:06 | 49.958
2021-01-16 | 13:06 | 49.956
2021-01-16 | 13:06 | 49.954
2021-01-16 | 13:06 | 49.952
2021-01-16 | 13:06 | 49.95
2021-01-16 | 13:06 | 49.948
2021-01-16 | 13:06 | 49.946
2021-01-16 | 13:06 | 49.946
2021-01-16 | 13:06 | 49.945
2021-01-16 | 13:06 | 49.944
2021-01-16 | 13:06 | 49.94
2021-01-16 | 13:06 | 49.937
2021-01-16 | 13:06 | 49.938
2021-01-16 | 13:06 | 49.937
2021-01-16 | 13:06 | 49.937
2021-01-16 | 13:06 | 49.938
2021-01-16 | 13:06 | 49.938
2021-01-16 | 13:06 | 49.939
2021-01-16 | 13:06 | 49.94
2021-01-16 | 13:06 | 49.94
2021-01-16 | 13:06 | 49.938
2021-01-16 | 13:06 | 49.939
2021-01-16 | 13:06 | 49.939
2021-01-16 | 13:06 | 49.938
2021-01-16 | 13:06 | 49.933
2021-01-16 | 13:06 | 49.93
2021-01-16 | 13:06 | 49.93
2021-01-16 | 13:06 | 49.93
2021-01-16 | 13:06 | 49.929
2021-01-16 | 13:06 | 49.928
2021-01-16 | 13:06 | 49.93
2021-01-16 | 13:06 | 49.933
2021-01-16 | 13:06 | 49.934
2021-01-16 | 13:06 | 49.932
2021-01-16 | 13:06 | 49.931
2021-01-16 | 13:06 | 49.932
2021-01-16 | 13:06 | 49.931
2021-01-16 | 13:06 | 49.933
2021-01-16 | 13:06 | 49.934
2021-01-16 | 13:06 | 49.934
2021-01-16 | 13:07 | 49.933
2021-01-16 | 13:07 | 49.933
2021-01-16 | 13:07 | 49.931
2021-01-16 | 13:07 | 49.93
2021-01-16 | 13:07 | 49.931
2021-01-16 | 13:07 | 49.931
2021-01-16 | 13:07 | 49.931
2021-01-16 | 13:07 | 49.933
2021-01-16 | 13:07 | 49.932
2021-01-16 | 13:07 | 49.934
2021-01-16 | 13:07 | 49.938
2021-01-16 | 13:07 | 49.938
2021-01-16 | 13:07 | 49.94
2021-01-16 | 13:07 | 49.944
2021-01-16 | 13:07 | 49.945
2021-01-16 | 13:07 | 49.947
2021-01-16 | 13:07 | 49.949
2021-01-16 | 13:07 | 49.949
2021-01-16 | 13:07 | 49.95
2021-01-16 | 13:07 | 49.953
2021-01-16 | 13:07 | 49.952
2021-01-16 | 13:07 | 49.954
2021-01-16 | 13:07 | 49.956
2021-01-16 | 13:07 | 49.958
2021-01-16 | 13:07 | 49.961
2021-01-16 | 13:07 | 49.962
2021-01-16 | 13:07 | 49.963
2021-01-16 | 13:07 | 49.963
2021-01-16 | 13:07 | 49.962
2021-01-16 | 13:07 | 49.959
2021-01-16 | 13:07 | 49.958
2021-01-16 | 13:07 | 49.955
2021-01-16 | 13:07 | 49.955
2021-01-16 | 13:07 | 49.955
2021-01-16 | 13:07 | 49.954
2021-01-16 | 13:07 | 49.956
2021-01-16 | 13:07 | 49.956
2021-01-16 | 13:07 | 49.957
2021-01-16 | 13:07 | 49.956
2021-01-16 | 13:07 | 49.956
2021-01-16 | 13:07 | 49.957
2021-01-16 | 13:07 | 49.96
2021-01-16 | 13:07 | 49.962
2021-01-16 | 13:07 | 49.964
2021-01-16 | 13:07 | 49.964
2021-01-16 | 13:07 | 49.968
2021-01-16 | 13:07 | 49.967
2021-01-16 | 13:07 | 49.966
2021-01-16 | 13:07 | 49.968
2021-01-16 | 13:07 | 49.969
2021-01-16 | 13:07 | 49.971
2021-01-16 | 13:07 | 49.974
2021-01-16 | 13:07 | 49.973
2021-01-16 | 13:07 | 49.979
2021-01-16 | 13:07 | 49.978
2021-01-16 | 13:07 | 49.978
2021-01-16 | 13:07 | 49.977
2021-01-16 | 13:07 | 49.975
2021-01-16 | 13:07 | 49.976
2021-01-16 | 13:08 | 49.976
2021-01-16 | 13:08 | 49.978
2021-01-16 | 13:08 | 49.979
2021-01-16 | 13:08 | 49.979
2021-01-16 | 13:08 | 49.98
2021-01-16 | 13:08 | 49.978
2021-01-16 | 13:08 | 49.979
2021-01-16 | 13:08 | 49.976
2021-01-16 | 13:08 | 49.975
2021-01-16 | 13:08 | 49.973
2021-01-16 | 13:08 | 49.972
2021-01-16 | 13:08 | 49.973
2021-01-16 | 13:08 | 49.972
2021-01-16 | 13:08 | 49.972
2021-01-16 | 13:08 | 49.968
2021-01-16 | 13:08 | 49.971
2021-01-16 | 13:08 | 49.969
2021-01-16 | 13:08 | 49.968
2021-01-16 | 13:08 | 49.971
2021-01-16 | 13:08 | 49.971
2021-01-16 | 13:08 | 49.972
2021-01-16 | 13:08 | 49.971
2021-01-16 | 13:08 | 49.973
2021-01-16 | 13:08 | 49.974
2021-01-16 | 13:08 | 49.977
2021-01-16 | 13:08 | 49.974
2021-01-16 | 13:08 | 49.973
2021-01-16 | 13:08 | 49.973
2021-01-16 | 13:08 | 49.974
2021-01-16 | 13:08 | 49.976
2021-01-16 | 13:08 | 49.977
2021-01-16 | 13:08 | 49.978
2021-01-16 | 13:08 | 49.976
2021-01-16 | 13:08 | 49.975
2021-01-16 | 13:08 | 49.973
2021-01-16 | 13:08 | 49.971
2021-01-16 | 13:08 | 49.969
2021-01-16 | 13:08 | 49.967
2021-01-16 | 13:08 | 49.965
2021-01-16 | 13:08 | 49.963
2021-01-16 | 13:08 | 49.963
2021-01-16 | 13:08 | 49.966
2021-01-16 | 13:08 | 49.965
2021-01-16 | 13:08 | 49.968
2021-01-16 | 13:08 | 49.968
2021-01-16 | 13:08 | 49.97
2021-01-16 | 13:08 | 49.971
2021-01-16 | 13:08 | 49.972
2021-01-16 | 13:08 | 49.97
2021-01-16 | 13:08 | 49.97
2021-01-16 | 13:08 | 49.968
2021-01-16 | 13:08 | 49.966
2021-01-16 | 13:08 | 49.966
2021-01-16 | 13:08 | 49.966
2021-01-16 | 13:08 | 49.967
2021-01-16 | 13:08 | 49.966
2021-01-16 | 13:08 | 49.967
2021-01-16 | 13:08 | 49.967
2021-01-16 | 13:08 | 49.971
2021-01-16 | 13:08 | 49.972
2021-01-16 | 13:08 | 49.975
2021-01-16 | 13:09 | 49.977
2021-01-16 | 13:09 | 49.98
2021-01-16 | 13:09 | 49.985
2021-01-16 | 13:09 | 49.986
2021-01-16 | 13:09 | 49.988
2021-01-16 | 13:09 | 49.989
2021-01-16 | 13:09 | 49.99
2021-01-16 | 13:09 | 49.988
2021-01-16 | 13:09 | 49.987
2021-01-16 | 13:09 | 49.986
2021-01-16 | 13:09 | 49.987
2021-01-16 | 13:09 | 49.985
2021-01-16 | 13:09 | 49.984
2021-01-16 | 13:09 | 49.983
2021-01-16 | 13:09 | 49.981
2021-01-16 | 13:09 | 49.979
2021-01-16 | 13:09 | 49.978
2021-01-16 | 13:09 | 49.979
2021-01-16 | 13:09 | 49.98
2021-01-16 | 13:09 | 49.984
2021-01-16 | 13:09 | 49.986
2021-01-16 | 13:09 | 49.986
2021-01-16 | 13:09 | 49.986
2021-01-16 | 13:09 | 49.987
2021-01-16 | 13:09 | 49.986
2021-01-16 | 13:09 | 49.984
2021-01-16 | 13:09 | 49.98
2021-01-16 | 13:09 | 49.979
2021-01-16 | 13:09 | 49.975
2021-01-16 | 13:09 | 49.978
2021-01-16 | 13:09 | 49.977
2021-01-16 | 13:09 | 49.978
2021-01-16 | 13:09 | 49.976
2021-01-16 | 13:09 | 49.975
2021-01-16 | 13:09 | 49.973
2021-01-16 | 13:09 | 49.972
2021-01-16 | 13:09 | 49.969
2021-01-16 | 13:09 | 49.968
2021-01-16 | 13:09 | 49.967
2021-01-16 | 13:09 | 49.965
2021-01-16 | 13:09 | 49.964
2021-01-16 | 13:09 | 49.964
2021-01-16 | 13:09 | 49.964
2021-01-16 | 13:09 | 49.966
2021-01-16 | 13:09 | 49.965
2021-01-16 | 13:09 | 49.962
2021-01-16 | 13:09 | 49.958
2021-01-16 | 13:09 | 49.958
2021-01-16 | 13:09 | 49.955
2021-01-16 | 13:09 | 49.953
2021-01-16 | 13:09 | 49.951
2021-01-16 | 13:09 | 49.95
2021-01-16 | 13:09 | 49.948
2021-01-16 | 13:09 | 49.947
2021-01-16 | 13:09 | 49.944
2021-01-16 | 13:09 | 49.941
2021-01-16 | 13:09 | 49.937
2021-01-16 | 13:09 | 49.935
2021-01-16 | 13:09 | 49.934
2021-01-16 | 13:10 | 49.935
2021-01-16 | 13:10 | 49.933
2021-01-16 | 13:10 | 49.933
2021-01-16 | 13:10 | 49.93
2021-01-16 | 13:10 | 49.93
2021-01-16 | 13:10 | 49.932
2021-01-16 | 13:10 | 49.931
2021-01-16 | 13:10 | 49.928
2021-01-16 | 13:10 | 49.927
2021-01-16 | 13:10 | 49.922
2021-01-16 | 13:10 | 49.921
2021-01-16 | 13:10 | 49.917
2021-01-16 | 13:10 | 49.917
2021-01-16 | 13:10 | 49.915
2021-01-16 | 13:10 | 49.916
2021-01-16 | 13:10 | 49.914
2021-01-16 | 13:10 | 49.914
2021-01-16 | 13:10 | 49.917
2021-01-16 | 13:10 | 49.923
2021-01-16 | 13:10 | 49.928
2021-01-16 | 13:10 | 49.935
2021-01-16 | 13:10 | 49.937
2021-01-16 | 13:10 | 49.943
2021-01-16 | 13:10 | 49.943
2021-01-16 | 13:10 | 49.943
2021-01-16 | 13:10 | 49.941
2021-01-16 | 13:10 | 49.938
2021-01-16 | 13:10 | 49.935
2021-01-16 | 13:10 | 49.934
2021-01-16 | 13:10 | 49.932
2021-01-16 | 13:10 | 49.932
2021-01-16 | 13:10 | 49.933
2021-01-16 | 13:10 | 49.931
2021-01-16 | 13:10 | 49.931
2021-01-16 | 13:10 | 49.933
2021-01-16 | 13:10 | 49.937
2021-01-16 | 13:10 | 49.938
2021-01-16 | 13:10 | 49.94
2021-01-16 | 13:10 | 49.937
2021-01-16 | 13:10 | 49.936
2021-01-16 | 13:10 | 49.936
2021-01-16 | 13:10 | 49.937
2021-01-16 | 13:10 | 49.939
2021-01-16 | 13:10 | 49.942
2021-01-16 | 13:10 | 49.944
2021-01-16 | 13:10 | 49.946
2021-01-16 | 13:10 | 49.947
2021-01-16 | 13:10 | 49.947
2021-01-16 | 13:10 | 49.949
2021-01-16 | 13:10 | 49.951
2021-01-16 | 13:10 | 49.952
2021-01-16 | 13:10 | 49.951
2021-01-16 | 13:10 | 49.95
2021-01-16 | 13:10 | 49.949
2021-01-16 | 13:10 | 49.95
2021-01-16 | 13:10 | 49.949
2021-01-16 | 13:10 | 49.95
2021-01-16 | 13:10 | 49.952
2021-01-16 | 13:10 | 49.951
2021-01-16 | 13:10 | 49.953
2021-01-16 | 13:10 | 49.955
2021-01-16 | 13:11 | 49.957
2021-01-16 | 13:11 | 49.962
2021-01-16 | 13:11 | 49.963
2021-01-16 | 13:11 | 49.966
2021-01-16 | 13:11 | 49.967
2021-01-16 | 13:11 | 49.97
2021-01-16 | 13:11 | 49.971
2021-01-16 | 13:11 | 49.974
2021-01-16 | 13:11 | 49.975
2021-01-16 | 13:11 | 49.976
2021-01-16 | 13:11 | 49.976
2021-01-16 | 13:11 | 49.974
2021-01-16 | 13:11 | 49.974
2021-01-16 | 13:11 | 49.973
2021-01-16 | 13:11 | 49.972
2021-01-16 | 13:11 | 49.972
2021-01-16 | 13:11 | 49.973
2021-01-16 | 13:11 | 49.973
2021-01-16 | 13:11 | 49.973
2021-01-16 | 13:11 | 49.973
2021-01-16 | 13:11 | 49.973
2021-01-16 | 13:11 | 49.971
2021-01-16 | 13:11 | 49.969
2021-01-16 | 13:11 | 49.969
2021-01-16 | 13:11 | 49.967
2021-01-16 | 13:11 | 49.965
2021-01-16 | 13:11 | 49.965
2021-01-16 | 13:11 | 49.965
2021-01-16 | 13:11 | 49.967
2021-01-16 | 13:11 | 49.964
2021-01-16 | 13:11 | 49.962
2021-01-16 | 13:11 | 49.957
2021-01-16 | 13:11 | 49.957
2021-01-16 | 13:11 | 49.954
2021-01-16 | 13:11 | 49.955
2021-01-16 | 13:11 | 49.955
2021-01-16 | 13:11 | 49.956
2021-01-16 | 13:11 | 49.955
2021-01-16 | 13:11 | 49.956
2021-01-16 | 13:11 | 49.958
2021-01-16 | 13:11 | 49.959
2021-01-16 | 13:11 | 49.962
2021-01-16 | 13:11 | 49.964
2021-01-16 | 13:11 | 49.964
2021-01-16 | 13:11 | 49.963
2021-01-16 | 13:11 | 49.963
2021-01-16 | 13:11 | 49.962
2021-01-16 | 13:11 | 49.963
2021-01-16 | 13:11 | 49.962
2021-01-16 | 13:11 | 49.965
2021-01-16 | 13:11 | 49.964
2021-01-16 | 13:11 | 49.961
2021-01-16 | 13:11 | 49.958
2021-01-16 | 13:11 | 49.954
2021-01-16 | 13:11 | 49.951
2021-01-16 | 13:11 | 49.949
2021-01-16 | 13:11 | 49.953
2021-01-16 | 13:11 | 49.958
2021-01-16 | 13:11 | 49.962
2021-01-16 | 13:12 | 49.965
2021-01-16 | 13:12 | 49.969
2021-01-16 | 13:12 | 49.969
2021-01-16 | 13:12 | 49.971
2021-01-16 | 13:12 | 49.972
2021-01-16 | 13:12 | 49.973
2021-01-16 | 13:12 | 49.976
2021-01-16 | 13:12 | 49.977
2021-01-16 | 13:12 | 49.978
2021-01-16 | 13:12 | 49.98
2021-01-16 | 13:12 | 49.985
2021-01-16 | 13:12 | 49.988
2021-01-16 | 13:12 | 49.992
2021-01-16 | 13:12 | 49.993
2021-01-16 | 13:12 | 49.996
2021-01-16 | 13:12 | 49.999
2021-01-16 | 13:12 | 50.003
2021-01-16 | 13:12 | 50.001
2021-01-16 | 13:12 | 50.002
2021-01-16 | 13:12 | 50.001
2021-01-16 | 13:12 | 50.002
2021-01-16 | 13:12 | 50
2021-01-16 | 13:12 | 50
2021-01-16 | 13:12 | 49.999
2021-01-16 | 13:12 | 49.997
2021-01-16 | 13:12 | 49.998
2021-01-16 | 13:12 | 49.998
2021-01-16 | 13:12 | 50
2021-01-16 | 13:12 | 50
2021-01-16 | 13:12 | 50.002
2021-01-16 | 13:12 | 50.002
2021-01-16 | 13:12 | 50.004
2021-01-16 | 13:12 | 50.004
2021-01-16 | 13:12 | 50.009
2021-01-16 | 13:12 | 50.01
2021-01-16 | 13:12 | 50.015
2021-01-16 | 13:12 | 50.018
2021-01-16 | 13:12 | 50.022
2021-01-16 | 13:12 | 50.024
2021-01-16 | 13:12 | 50.026
2021-01-16 | 13:12 | 50.025
2021-01-16 | 13:12 | 50.026
2021-01-16 | 13:12 | 50.027
2021-01-16 | 13:12 | 50.029
2021-01-16 | 13:12 | 50.03
2021-01-16 | 13:12 | 50.032
2021-01-16 | 13:12 | 50.033
2021-01-16 | 13:12 | 50.032
2021-01-16 | 13:12 | 50.033
2021-01-16 | 13:12 | 50.033
2021-01-16 | 13:12 | 50.035
2021-01-16 | 13:12 | 50.035
2021-01-16 | 13:12 | 50.033
2021-01-16 | 13:12 | 50.033
2021-01-16 | 13:12 | 50.033
2021-01-16 | 13:12 | 50.037
2021-01-16 | 13:12 | 50.036
2021-01-16 | 13:12 | 50.035
2021-01-16 | 13:12 | 50.036
2021-01-16 | 13:12 | 50.036
2021-01-16 | 13:12 | 50.04
2021-01-16 | 13:13 | 50.042
2021-01-16 | 13:13 | 50.044
2021-01-16 | 13:13 | 50.046
2021-01-16 | 13:13 | 50.046
2021-01-16 | 13:13 | 50.047
2021-01-16 | 13:13 | 50.047
2021-01-16 | 13:13 | 50.047
2021-01-16 | 13:13 | 50.048
2021-01-16 | 13:13 | 50.047
2021-01-16 | 13:13 | 50.047
2021-01-16 | 13:13 | 50.047
2021-01-16 | 13:13 | 50.045
2021-01-16 | 13:13 | 50.047
2021-01-16 | 13:13 | 50.046
2021-01-16 | 13:13 | 50.046
2021-01-16 | 13:13 | 50.046
2021-01-16 | 13:13 | 50.047
2021-01-16 | 13:13 | 50.05
2021-01-16 | 13:13 | 50.052
2021-01-16 | 13:13 | 50.056
2021-01-16 | 13:13 | 50.058
2021-01-16 | 13:13 | 50.058
2021-01-16 | 13:13 | 50.058
2021-01-16 | 13:13 | 50.057
2021-01-16 | 13:13 | 50.057
2021-01-16 | 13:13 | 50.056
2021-01-16 | 13:13 | 50.057
2021-01-16 | 13:13 | 50.056
2021-01-16 | 13:13 | 50.059
2021-01-16 | 13:13 | 50.057
2021-01-16 | 13:13 | 50.056
2021-01-16 | 13:13 | 50.05
2021-01-16 | 13:13 | 50.046
2021-01-16 | 13:13 | 50.041
2021-01-16 | 13:13 | 50.036
2021-01-16 | 13:13 | 50.03
2021-01-16 | 13:13 | 50.028
2021-01-16 | 13:13 | 50.024
2021-01-16 | 13:13 | 50.023
2021-01-16 | 13:13 | 50.02
2021-01-16 | 13:13 | 50.018
2021-01-16 | 13:13 | 50.017
2021-01-16 | 13:13 | 50.019
2021-01-16 | 13:13 | 50.021
2021-01-16 | 13:13 | 50.022
2021-01-16 | 13:13 | 50.022
2021-01-16 | 13:13 | 50.022
2021-01-16 | 13:13 | 50.019
2021-01-16 | 13:13 | 50.018
2021-01-16 | 13:13 | 50.014
2021-01-16 | 13:13 | 50.012
2021-01-16 | 13:13 | 50.013
2021-01-16 | 13:13 | 50.01
2021-01-16 | 13:13 | 50.01
2021-01-16 | 13:13 | 50.01
2021-01-16 | 13:13 | 50.012
2021-01-16 | 13:13 | 50.013
2021-01-16 | 13:13 | 50.017
2021-01-16 | 13:13 | 50.02
2021-01-16 | 13:14 | 50.024
2021-01-16 | 13:14 | 50.024
2021-01-16 | 13:14 | 50.024
2021-01-16 | 13:14 | 50.025
2021-01-16 | 13:14 | 50.025
2021-01-16 | 13:14 | 50.025
2021-01-16 | 13:14 | 50.025
2021-01-16 | 13:14 | 50.025
2021-01-16 | 13:14 | 50.024
2021-01-16 | 13:14 | 50.024
2021-01-16 | 13:14 | 50.021
2021-01-16 | 13:14 | 50.023
2021-01-16 | 13:14 | 50.022
2021-01-16 | 13:14 | 50.027
2021-01-16 | 13:14 | 50.029
2021-01-16 | 13:14 | 50.031
2021-01-16 | 13:14 | 50.032
2021-01-16 | 13:14 | 50.031
2021-01-16 | 13:14 | 50.032
2021-01-16 | 13:14 | 50.029
2021-01-16 | 13:14 | 50.024
2021-01-16 | 13:14 | 50.02
2021-01-16 | 13:14 | 50.022
2021-01-16 | 13:14 | 50.023
2021-01-16 | 13:14 | 50.023
2021-01-16 | 13:14 | 50.02
2021-01-16 | 13:14 | 50.015
2021-01-16 | 13:14 | 50.009
2021-01-16 | 13:14 | 50
2021-01-16 | 13:14 | 49.995
2021-01-16 | 13:14 | 49.987
2021-01-16 | 13:14 | 49.978
2021-01-16 | 13:14 | 49.969
2021-01-16 | 13:14 | 49.966
2021-01-16 | 13:14 | 49.964
2021-01-16 | 13:14 | 49.965
2021-01-16 | 13:14 | 49.965
2021-01-16 | 13:14 | 49.968
2021-01-16 | 13:14 | 49.972
2021-01-16 | 13:14 | 49.974
2021-01-16 | 13:14 | 49.975
2021-01-16 | 13:14 | 49.976
2021-01-16 | 13:14 | 49.975
2021-01-16 | 13:14 | 49.974
2021-01-16 | 13:14 | 49.973
2021-01-16 | 13:14 | 49.974
2021-01-16 | 13:14 | 49.97
2021-01-16 | 13:14 | 49.969
2021-01-16 | 13:14 | 49.967
2021-01-16 | 13:14 | 49.968
2021-01-16 | 13:14 | 49.968
2021-01-16 | 13:14 | 49.97
2021-01-16 | 13:14 | 49.969
2021-01-16 | 13:14 | 49.969
2021-01-16 | 13:14 | 49.972
2021-01-16 | 13:14 | 49.972
2021-01-16 | 13:14 | 49.973
2021-01-16 | 13:14 | 49.973
2021-01-16 | 13:14 | 49.976
2021-01-16 | 13:14 | 49.976
2021-01-16 | 13:14 | 49.978
2021-01-16 | 13:15 | 49.977
2021-01-16 | 13:15 | 49.978
2021-01-16 | 13:15 | 49.979
2021-01-16 | 13:15 | 49.98
2021-01-16 | 13:15 | 49.981
2021-01-16 | 13:15 | 49.977
2021-01-16 | 13:15 | 49.974
2021-01-16 | 13:15 | 49.975
2021-01-16 | 13:15 | 49.973
2021-01-16 | 13:15 | 49.971
2021-01-16 | 13:15 | 49.97
2021-01-16 | 13:15 | 49.968
2021-01-16 | 13:15 | 49.967
2021-01-16 | 13:15 | 49.965
2021-01-16 | 13:15 | 49.966
2021-01-16 | 13:15 | 49.967
2021-01-16 | 13:15 | 49.971
2021-01-16 | 13:15 | 49.973
2021-01-16 | 13:15 | 49.976
2021-01-16 | 13:15 | 49.977
2021-01-16 | 13:15 | 49.977
2021-01-16 | 13:15 | 49.977
2021-01-16 | 13:15 | 49.976
2021-01-16 | 13:15 | 49.977
2021-01-16 | 13:15 | 49.977
2021-01-16 | 13:15 | 49.979
2021-01-16 | 13:15 | 49.982
2021-01-16 | 13:15 | 49.982
2021-01-16 | 13:15 | 49.984
2021-01-16 | 13:15 | 49.983
2021-01-16 | 13:15 | 49.983
2021-01-16 | 13:15 | 49.98
2021-01-16 | 13:15 | 49.979
2021-01-16 | 13:15 | 49.979
2021-01-16 | 13:15 | 49.98
2021-01-16 | 13:15 | 49.981
2021-01-16 | 13:15 | 49.981
2021-01-16 | 13:15 | 49.983
2021-01-16 | 13:15 | 49.985
2021-01-16 | 13:15 | 49.988
2021-01-16 | 13:15 | 49.989
2021-01-16 | 13:15 | 49.988
2021-01-16 | 13:15 | 49.986
2021-01-16 | 13:15 | 49.985
2021-01-16 | 13:15 | 49.981
2021-01-16 | 13:15 | 49.981
2021-01-16 | 13:15 | 49.98
2021-01-16 | 13:15 | 49.981
2021-01-16 | 13:15 | 49.98
2021-01-16 | 13:15 | 49.982
2021-01-16 | 13:15 | 49.986
2021-01-16 | 13:15 | 49.988
2021-01-16 | 13:15 | 49.991
2021-01-16 | 13:15 | 49.992
2021-01-16 | 13:15 | 49.993
2021-01-16 | 13:15 | 49.993
2021-01-16 | 13:15 | 49.992
2021-01-16 | 13:15 | 49.99
2021-01-16 | 13:15 | 49.991
2021-01-16 | 13:16 | 49.987
2021-01-16 | 13:16 | 49.986
2021-01-16 | 13:16 | 49.984
2021-01-16 | 13:16 | 49.985
2021-01-16 | 13:16 | 49.983
2021-01-16 | 13:16 | 49.984
2021-01-16 | 13:16 | 49.983
2021-01-16 | 13:16 | 49.984
2021-01-16 | 13:16 | 49.984
2021-01-16 | 13:16 | 49.984
2021-01-16 | 13:16 | 49.984
2021-01-16 | 13:16 | 49.982
2021-01-16 | 13:16 | 49.982
2021-01-16 | 13:16 | 49.98
2021-01-16 | 13:16 | 49.979
2021-01-16 | 13:16 | 49.977
2021-01-16 | 13:16 | 49.979
2021-01-16 | 13:16 | 49.977
2021-01-16 | 13:16 | 49.98
2021-01-16 | 13:16 | 49.981
2021-01-16 | 13:16 | 49.984
2021-01-16 | 13:16 | 49.986
2021-01-16 | 13:16 | 49.988
2021-01-16 | 13:16 | 49.985
2021-01-16 | 13:16 | 49.984
2021-01-16 | 13:16 | 49.981
2021-01-16 | 13:16 | 49.977
2021-01-16 | 13:16 | 49.977
2021-01-16 | 13:16 | 49.974
2021-01-16 | 13:16 | 49.974
2021-01-16 | 13:16 | 49.974
2021-01-16 | 13:16 | 49.975
2021-01-16 | 13:16 | 49.98
2021-01-16 | 13:16 | 49.982
2021-01-16 | 13:16 | 49.987
2021-01-16 | 13:16 | 49.99
2021-01-16 | 13:16 | 49.992
2021-01-16 | 13:16 | 49.991
2021-01-16 | 13:16 | 49.989
2021-01-16 | 13:16 | 49.986
2021-01-16 | 13:16 | 49.982
2021-01-16 | 13:16 | 49.979
2021-01-16 | 13:16 | 49.976
2021-01-16 | 13:16 | 49.973
2021-01-16 | 13:16 | 49.97
2021-01-16 | 13:16 | 49.969
2021-01-16 | 13:16 | 49.968
2021-01-16 | 13:16 | 49.964
2021-01-16 | 13:16 | 49.958
2021-01-16 | 13:16 | 49.951
2021-01-16 | 13:16 | 49.952
2021-01-16 | 13:16 | 49.954
2021-01-16 | 13:16 | 49.958
2021-01-16 | 13:16 | 49.961
2021-01-16 | 13:16 | 49.963
2021-01-16 | 13:16 | 49.963
2021-01-16 | 13:16 | 49.965
2021-01-16 | 13:16 | 49.966
2021-01-16 | 13:16 | 49.966
2021-01-16 | 13:16 | 49.969
2021-01-16 | 13:16 | 49.969
2021-01-16 | 13:17 | 49.968
2021-01-16 | 13:17 | 49.968
2021-01-16 | 13:17 | 49.967
2021-01-16 | 13:17 | 49.967
2021-01-16 | 13:17 | 49.968
2021-01-16 | 13:17 | 49.967
2021-01-16 | 13:17 | 49.968
2021-01-16 | 13:17 | 49.969
2021-01-16 | 13:17 | 49.97
2021-01-16 | 13:17 | 49.971
2021-01-16 | 13:17 | 49.973
2021-01-16 | 13:17 | 49.976
2021-01-16 | 13:17 | 49.979
2021-01-16 | 13:17 | 49.981
2021-01-16 | 13:17 | 49.983
2021-01-16 | 13:17 | 49.983
2021-01-16 | 13:17 | 49.981
2021-01-16 | 13:17 | 49.979
2021-01-16 | 13:17 | 49.978
2021-01-16 | 13:17 | 49.976
2021-01-16 | 13:17 | 49.974
2021-01-16 | 13:17 | 49.971
2021-01-16 | 13:17 | 49.967
2021-01-16 | 13:17 | 49.966
2021-01-16 | 13:17 | 49.965
2021-01-16 | 13:17 | 49.964
2021-01-16 | 13:17 | 49.964
2021-01-16 | 13:17 | 49.964
2021-01-16 | 13:17 | 49.964
2021-01-16 | 13:17 | 49.963
2021-01-16 | 13:17 | 49.965
2021-01-16 | 13:17 | 49.964
2021-01-16 | 13:17 | 49.964
2021-01-16 | 13:17 | 49.964
2021-01-16 | 13:17 | 49.964
2021-01-16 | 13:17 | 49.963
2021-01-16 | 13:17 | 49.963
2021-01-16 | 13:17 | 49.963
2021-01-16 | 13:17 | 49.965
2021-01-16 | 13:17 | 49.967
2021-01-16 | 13:17 | 49.968
2021-01-16 | 13:17 | 49.969
2021-01-16 | 13:17 | 49.969
2021-01-16 | 13:17 | 49.97
2021-01-16 | 13:17 | 49.969
2021-01-16 | 13:17 | 49.968
2021-01-16 | 13:17 | 49.969
2021-01-16 | 13:17 | 49.969
2021-01-16 | 13:17 | 49.97
2021-01-16 | 13:17 | 49.972
2021-01-16 | 13:17 | 49.972
2021-01-16 | 13:17 | 49.972
2021-01-16 | 13:17 | 49.972
2021-01-16 | 13:17 | 49.973
2021-01-16 | 13:17 | 49.975
2021-01-16 | 13:17 | 49.976
2021-01-16 | 13:17 | 49.979
2021-01-16 | 13:17 | 49.979
2021-01-16 | 13:17 | 49.98
2021-01-16 | 13:18 | 49.98
2021-01-16 | 13:18 | 49.982
2021-01-16 | 13:18 | 49.983
2021-01-16 | 13:18 | 49.984
2021-01-16 | 13:18 | 49.985
2021-01-16 | 13:18 | 49.984
2021-01-16 | 13:18 | 49.983
2021-01-16 | 13:18 | 49.983
2021-01-16 | 13:18 | 49.984
2021-01-16 | 13:18 | 49.985
2021-01-16 | 13:18 | 49.986
2021-01-16 | 13:18 | 49.985
2021-01-16 | 13:18 | 49.985
2021-01-16 | 13:18 | 49.986
2021-01-16 | 13:18 | 49.985
2021-01-16 | 13:18 | 49.983
2021-01-16 | 13:18 | 49.98
2021-01-16 | 13:18 | 49.978
2021-01-16 | 13:18 | 49.978
2021-01-16 | 13:18 | 49.976
2021-01-16 | 13:18 | 49.975
2021-01-16 | 13:18 | 49.972
2021-01-16 | 13:18 | 49.971
2021-01-16 | 13:18 | 49.971
2021-01-16 | 13:18 | 49.97
2021-01-16 | 13:18 | 49.967
2021-01-16 | 13:18 | 49.964
2021-01-16 | 13:18 | 49.96
2021-01-16 | 13:18 | 49.955
2021-01-16 | 13:18 | 49.954
2021-01-16 | 13:18 | 49.951
2021-01-16 | 13:18 | 49.949
2021-01-16 | 13:18 | 49.948
2021-01-16 | 13:18 | 49.947
2021-01-16 | 13:18 | 49.947
2021-01-16 | 13:18 | 49.948
2021-01-16 | 13:18 | 49.95
2021-01-16 | 13:18 | 49.949
2021-01-16 | 13:18 | 49.951
2021-01-16 | 13:18 | 49.949
2021-01-16 | 13:18 | 49.949
2021-01-16 | 13:18 | 49.946
2021-01-16 | 13:18 | 49.942
2021-01-16 | 13:18 | 49.944
2021-01-16 | 13:18 | 49.942
2021-01-16 | 13:18 | 49.942
2021-01-16 | 13:18 | 49.943
2021-01-16 | 13:18 | 49.943
2021-01-16 | 13:18 | 49.937
2021-01-16 | 13:18 | 49.933
2021-01-16 | 13:18 | 49.928
2021-01-16 | 13:18 | 49.926
2021-01-16 | 13:18 | 49.924
2021-01-16 | 13:18 | 49.925
2021-01-16 | 13:18 | 49.929
2021-01-16 | 13:18 | 49.933
2021-01-16 | 13:18 | 49.933
2021-01-16 | 13:18 | 49.934
2021-01-16 | 13:18 | 49.935
2021-01-16 | 13:18 | 49.937
2021-01-16 | 13:18 | 49.938
2021-01-16 | 13:19 | 49.938
2021-01-16 | 13:19 | 49.934
2021-01-16 | 13:19 | 49.93
2021-01-16 | 13:19 | 49.931
2021-01-16 | 13:19 | 49.932
2021-01-16 | 13:19 | 49.932
2021-01-16 | 13:19 | 49.928
2021-01-16 | 13:19 | 49.926
2021-01-16 | 13:19 | 49.924
2021-01-16 | 13:19 | 49.925
2021-01-16 | 13:19 | 49.924
2021-01-16 | 13:19 | 49.926
2021-01-16 | 13:19 | 49.927
2021-01-16 | 13:19 | 49.93
2021-01-16 | 13:19 | 49.932
2021-01-16 | 13:19 | 49.935
2021-01-16 | 13:19 | 49.935
2021-01-16 | 13:19 | 49.935
2021-01-16 | 13:19 | 49.936
2021-01-16 | 13:19 | 49.935
2021-01-16 | 13:19 | 49.935
2021-01-16 | 13:19 | 49.935
2021-01-16 | 13:19 | 49.932
2021-01-16 | 13:19 | 49.929
2021-01-16 | 13:19 | 49.927
2021-01-16 | 13:19 | 49.928
2021-01-16 | 13:19 | 49.926
2021-01-16 | 13:19 | 49.927
2021-01-16 | 13:19 | 49.93
2021-01-16 | 13:19 | 49.932
2021-01-16 | 13:19 | 49.935
2021-01-16 | 13:19 | 49.938
2021-01-16 | 13:19 | 49.938
2021-01-16 | 13:19 | 49.938
2021-01-16 | 13:19 | 49.936
2021-01-16 | 13:19 | 49.936
2021-01-16 | 13:19 | 49.938
2021-01-16 | 13:19 | 49.937
2021-01-16 | 13:19 | 49.937
2021-01-16 | 13:19 | 49.94
2021-01-16 | 13:19 | 49.94
2021-01-16 | 13:19 | 49.938
2021-01-16 | 13:19 | 49.94
2021-01-16 | 13:19 | 49.938
2021-01-16 | 13:19 | 49.936
2021-01-16 | 13:19 | 49.934
2021-01-16 | 13:19 | 49.936
2021-01-16 | 13:19 | 49.937
2021-01-16 | 13:19 | 49.935
2021-01-16 | 13:19 | 49.935
2021-01-16 | 13:19 | 49.934
2021-01-16 | 13:19 | 49.934
2021-01-16 | 13:19 | 49.935
2021-01-16 | 13:19 | 49.938
2021-01-16 | 13:19 | 49.94
2021-01-16 | 13:19 | 49.943
2021-01-16 | 13:19 | 49.943
2021-01-16 | 13:19 | 49.945
2021-01-16 | 13:19 | 49.948
2021-01-16 | 13:20 | 49.951
2021-01-16 | 13:20 | 49.953
2021-01-16 | 13:20 | 49.956
2021-01-16 | 13:20 | 49.961
2021-01-16 | 13:20 | 49.965
2021-01-16 | 13:20 | 49.969
2021-01-16 | 13:20 | 49.97
2021-01-16 | 13:20 | 49.971
2021-01-16 | 13:20 | 49.968
2021-01-16 | 13:20 | 49.967
2021-01-16 | 13:20 | 49.965
2021-01-16 | 13:20 | 49.965
2021-01-16 | 13:20 | 49.965
2021-01-16 | 13:20 | 49.964
2021-01-16 | 13:20 | 49.962
2021-01-16 | 13:20 | 49.961
2021-01-16 | 13:20 | 49.96
2021-01-16 | 13:20 | 49.957
2021-01-16 | 13:20 | 49.954
2021-01-16 | 13:20 | 49.953
2021-01-16 | 13:20 | 49.952
2021-01-16 | 13:20 | 49.949
2021-01-16 | 13:20 | 49.949
2021-01-16 | 13:20 | 49.947
2021-01-16 | 13:20 | 49.944
2021-01-16 | 13:20 | 49.942
2021-01-16 | 13:20 | 49.939
2021-01-16 | 13:20 | 49.939
2021-01-16 | 13:20 | 49.943
2021-01-16 | 13:20 | 49.948
2021-01-16 | 13:20 | 49.954
2021-01-16 | 13:20 | 49.955
2021-01-16 | 13:20 | 49.953
2021-01-16 | 13:20 | 49.952
2021-01-16 | 13:20 | 49.953
2021-01-16 | 13:20 | 49.951
2021-01-16 | 13:20 | 49.949
2021-01-16 | 13:20 | 49.949
2021-01-16 | 13:20 | 49.948
2021-01-16 | 13:20 | 49.945
2021-01-16 | 13:20 | 49.942
2021-01-16 | 13:20 | 49.941
2021-01-16 | 13:20 | 49.939
2021-01-16 | 13:20 | 49.938
2021-01-16 | 13:20 | 49.936
2021-01-16 | 13:20 | 49.934
2021-01-16 | 13:20 | 49.933
2021-01-16 | 13:20 | 49.935
2021-01-16 | 13:20 | 49.935
2021-01-16 | 13:20 | 49.936
2021-01-16 | 13:20 | 49.938
2021-01-16 | 13:20 | 49.934
2021-01-16 | 13:20 | 49.932
2021-01-16 | 13:20 | 49.932
2021-01-16 | 13:20 | 49.932
2021-01-16 | 13:20 | 49.931
2021-01-16 | 13:20 | 49.932
2021-01-16 | 13:20 | 49.932
2021-01-16 | 13:20 | 49.929
2021-01-16 | 13:20 | 49.925
2021-01-16 | 13:20 | 49.926
2021-01-16 | 13:21 | 49.924
2021-01-16 | 13:21 | 49.922
2021-01-16 | 13:21 | 49.922
2021-01-16 | 13:21 | 49.925
2021-01-16 | 13:21 | 49.927
2021-01-16 | 13:21 | 49.929
2021-01-16 | 13:21 | 49.93
2021-01-16 | 13:21 | 49.932
2021-01-16 | 13:21 | 49.93
2021-01-16 | 13:21 | 49.931
2021-01-16 | 13:21 | 49.929
2021-01-16 | 13:21 | 49.928
2021-01-16 | 13:21 | 49.924
2021-01-16 | 13:21 | 49.921
2021-01-16 | 13:21 | 49.919
2021-01-16 | 13:21 | 49.918
2021-01-16 | 13:21 | 49.919
2021-01-16 | 13:21 | 49.92
2021-01-16 | 13:21 | 49.923
2021-01-16 | 13:21 | 49.925
2021-01-16 | 13:21 | 49.926
2021-01-16 | 13:21 | 49.926
2021-01-16 | 13:21 | 49.928
2021-01-16 | 13:21 | 49.93
2021-01-16 | 13:21 | 49.928
2021-01-16 | 13:21 | 49.929
2021-01-16 | 13:21 | 49.927
2021-01-16 | 13:21 | 49.926
2021-01-16 | 13:21 | 49.924
2021-01-16 | 13:21 | 49.921
2021-01-16 | 13:21 | 49.919
2021-01-16 | 13:21 | 49.921
2021-01-16 | 13:21 | 49.925
2021-01-16 | 13:21 | 49.925
2021-01-16 | 13:21 | 49.927
2021-01-16 | 13:21 | 49.928
2021-01-16 | 13:21 | 49.927
2021-01-16 | 13:21 | 49.927
2021-01-16 | 13:21 | 49.925
2021-01-16 | 13:21 | 49.922
2021-01-16 | 13:21 | 49.92
2021-01-16 | 13:21 | 49.919
2021-01-16 | 13:21 | 49.92
2021-01-16 | 13:21 | 49.919
2021-01-16 | 13:21 | 49.915
2021-01-16 | 13:21 | 49.909
2021-01-16 | 13:21 | 49.905
2021-01-16 | 13:21 | 49.902
2021-01-16 | 13:21 | 49.9
2021-01-16 | 13:21 | 49.899
2021-01-16 | 13:21 | 49.898
2021-01-16 | 13:21 | 49.9
2021-01-16 | 13:21 | 49.9
2021-01-16 | 13:21 | 49.903
2021-01-16 | 13:21 | 49.905
2021-01-16 | 13:21 | 49.907
2021-01-16 | 13:21 | 49.911
2021-01-16 | 13:21 | 49.913
2021-01-16 | 13:21 | 49.915
2021-01-16 | 13:22 | 49.919
2021-01-16 | 13:22 | 49.918
2021-01-16 | 13:22 | 49.92
2021-01-16 | 13:22 | 49.922
2021-01-16 | 13:22 | 49.924
2021-01-16 | 13:22 | 49.923
2021-01-16 | 13:22 | 49.923
2021-01-16 | 13:22 | 49.92
2021-01-16 | 13:22 | 49.921
2021-01-16 | 13:22 | 49.92
2021-01-16 | 13:22 | 49.922
2021-01-16 | 13:22 | 49.92
2021-01-16 | 13:22 | 49.919
2021-01-16 | 13:22 | 49.917
2021-01-16 | 13:22 | 49.917
2021-01-16 | 13:22 | 49.917
2021-01-16 | 13:22 | 49.917
2021-01-16 | 13:22 | 49.922
2021-01-16 | 13:22 | 49.925
2021-01-16 | 13:22 | 49.927
2021-01-16 | 13:22 | 49.929
2021-01-16 | 13:22 | 49.931
2021-01-16 | 13:22 | 49.931
2021-01-16 | 13:22 | 49.932
2021-01-16 | 13:22 | 49.934
2021-01-16 | 13:22 | 49.933
2021-01-16 | 13:22 | 49.934
2021-01-16 | 13:22 | 49.933
2021-01-16 | 13:22 | 49.934
2021-01-16 | 13:22 | 49.934
2021-01-16 | 13:22 | 49.936
2021-01-16 | 13:22 | 49.933
2021-01-16 | 13:22 | 49.931
2021-01-16 | 13:22 | 49.931
2021-01-16 | 13:22 | 49.929
2021-01-16 | 13:22 | 49.929
2021-01-16 | 13:22 | 49.929
2021-01-16 | 13:22 | 49.928
2021-01-16 | 13:22 | 49.928
2021-01-16 | 13:22 | 49.932
2021-01-16 | 13:22 | 49.934
2021-01-16 | 13:22 | 49.936
2021-01-16 | 13:22 | 49.941
2021-01-16 | 13:22 | 49.944
2021-01-16 | 13:22 | 49.948
2021-01-16 | 13:22 | 49.951
2021-01-16 | 13:22 | 49.953
2021-01-16 | 13:22 | 49.958
2021-01-16 | 13:22 | 49.962
2021-01-16 | 13:22 | 49.963
2021-01-16 | 13:22 | 49.965
2021-01-16 | 13:22 | 49.966
2021-01-16 | 13:22 | 49.966
2021-01-16 | 13:22 | 49.967
2021-01-16 | 13:22 | 49.968
2021-01-16 | 13:22 | 49.966
2021-01-16 | 13:22 | 49.967
2021-01-16 | 13:22 | 49.966
2021-01-16 | 13:22 | 49.964
2021-01-16 | 13:22 | 49.962
2021-01-16 | 13:22 | 49.961
2021-01-16 | 13:23 | 49.96
2021-01-16 | 13:23 | 49.96
2021-01-16 | 13:23 | 49.96
2021-01-16 | 13:23 | 49.959
2021-01-16 | 13:23 | 49.958
2021-01-16 | 13:23 | 49.956
2021-01-16 | 13:23 | 49.957
2021-01-16 | 13:23 | 49.957
2021-01-16 | 13:23 | 49.957
2021-01-16 | 13:23 | 49.958
2021-01-16 | 13:23 | 49.956
2021-01-16 | 13:23 | 49.952
2021-01-16 | 13:23 | 49.948
2021-01-16 | 13:23 | 49.945
2021-01-16 | 13:23 | 49.942
2021-01-16 | 13:23 | 49.942
2021-01-16 | 13:23 | 49.937
2021-01-16 | 13:23 | 49.938
2021-01-16 | 13:23 | 49.938
2021-01-16 | 13:23 | 49.936
2021-01-16 | 13:23 | 49.936
2021-01-16 | 13:23 | 49.937
2021-01-16 | 13:23 | 49.937
2021-01-16 | 13:23 | 49.936
2021-01-16 | 13:23 | 49.936
2021-01-16 | 13:23 | 49.937
2021-01-16 | 13:23 | 49.938
2021-01-16 | 13:23 | 49.938
2021-01-16 | 13:23 | 49.939
2021-01-16 | 13:23 | 49.942
2021-01-16 | 13:23 | 49.94
2021-01-16 | 13:23 | 49.938
2021-01-16 | 13:23 | 49.937
2021-01-16 | 13:23 | 49.934
2021-01-16 | 13:23 | 49.934
2021-01-16 | 13:23 | 49.932
2021-01-16 | 13:23 | 49.931
2021-01-16 | 13:23 | 49.929
2021-01-16 | 13:23 | 49.928
2021-01-16 | 13:23 | 49.929
2021-01-16 | 13:23 | 49.929
2021-01-16 | 13:23 | 49.932
2021-01-16 | 13:23 | 49.937
2021-01-16 | 13:23 | 49.938
2021-01-16 | 13:23 | 49.939
2021-01-16 | 13:23 | 49.939
2021-01-16 | 13:23 | 49.938
2021-01-16 | 13:23 | 49.938
2021-01-16 | 13:23 | 49.939
2021-01-16 | 13:23 | 49.938
2021-01-16 | 13:23 | 49.938
2021-01-16 | 13:23 | 49.938
2021-01-16 | 13:23 | 49.938
2021-01-16 | 13:23 | 49.939
2021-01-16 | 13:23 | 49.94
2021-01-16 | 13:23 | 49.942
2021-01-16 | 13:23 | 49.939
2021-01-16 | 13:23 | 49.941
2021-01-16 | 13:23 | 49.942
2021-01-16 | 13:24 | 49.943
2021-01-16 | 13:24 | 49.942
2021-01-16 | 13:24 | 49.943
2021-01-16 | 13:24 | 49.943
2021-01-16 | 13:24 | 49.945
2021-01-16 | 13:24 | 49.947
2021-01-16 | 13:24 | 49.946
2021-01-16 | 13:24 | 49.949
2021-01-16 | 13:24 | 49.95
2021-01-16 | 13:24 | 49.952
2021-01-16 | 13:24 | 49.952
2021-01-16 | 13:24 | 49.952
2021-01-16 | 13:24 | 49.95
2021-01-16 | 13:24 | 49.953
2021-01-16 | 13:24 | 49.954
2021-01-16 | 13:24 | 49.955
2021-01-16 | 13:24 | 49.956
2021-01-16 | 13:24 | 49.957
2021-01-16 | 13:24 | 49.958
2021-01-16 | 13:24 | 49.961
2021-01-16 | 13:24 | 49.962
2021-01-16 | 13:24 | 49.966
2021-01-16 | 13:24 | 49.969
2021-01-16 | 13:24 | 49.974
2021-01-16 | 13:24 | 49.978
2021-01-16 | 13:24 | 49.98
2021-01-16 | 13:24 | 49.983
2021-01-16 | 13:24 | 49.983
2021-01-16 | 13:24 | 49.981
2021-01-16 | 13:24 | 49.98
2021-01-16 | 13:24 | 49.978
2021-01-16 | 13:24 | 49.977
2021-01-16 | 13:24 | 49.977
2021-01-16 | 13:24 | 49.974
2021-01-16 | 13:24 | 49.973
2021-01-16 | 13:24 | 49.972
2021-01-16 | 13:24 | 49.972
2021-01-16 | 13:24 | 49.973
2021-01-16 | 13:24 | 49.975
2021-01-16 | 13:24 | 49.975
2021-01-16 | 13:24 | 49.976
2021-01-16 | 13:24 | 49.976
2021-01-16 | 13:24 | 49.976
2021-01-16 | 13:24 | 49.975
2021-01-16 | 13:24 | 49.972
2021-01-16 | 13:24 | 49.975
2021-01-16 | 13:24 | 49.976
2021-01-16 | 13:24 | 49.978
2021-01-16 | 13:24 | 49.98
2021-01-16 | 13:24 | 49.979
2021-01-16 | 13:24 | 49.979
2021-01-16 | 13:24 | 49.981
2021-01-16 | 13:24 | 49.984
2021-01-16 | 13:24 | 49.986
2021-01-16 | 13:24 | 49.987
2021-01-16 | 13:24 | 49.987
2021-01-16 | 13:24 | 49.989
2021-01-16 | 13:24 | 49.988
2021-01-16 | 13:24 | 49.992
2021-01-16 | 13:24 | 49.993
2021-01-16 | 13:24 | 49.993
2021-01-16 | 13:25 | 49.994
2021-01-16 | 13:25 | 49.996
2021-01-16 | 13:25 | 49.998
2021-01-16 | 13:25 | 49.997
2021-01-16 | 13:25 | 49.998
2021-01-16 | 13:25 | 50.001
2021-01-16 | 13:25 | 50.001
2021-01-16 | 13:25 | 50.002
2021-01-16 | 13:25 | 50.003
2021-01-16 | 13:25 | 50.003
2021-01-16 | 13:25 | 50.003
2021-01-16 | 13:25 | 50.003
2021-01-16 | 13:25 | 50.004
2021-01-16 | 13:25 | 50.006
2021-01-16 | 13:25 | 50.007
2021-01-16 | 13:25 | 50.006
2021-01-16 | 13:25 | 50.005
2021-01-16 | 13:25 | 50.003
2021-01-16 | 13:25 | 50.001
2021-01-16 | 13:25 | 49.999
2021-01-16 | 13:25 | 49.998
2021-01-16 | 13:25 | 49.999
2021-01-16 | 13:25 | 50
2021-01-16 | 13:25 | 50.002
2021-01-16 | 13:25 | 50.004
2021-01-16 | 13:25 | 50.004
2021-01-16 | 13:25 | 50.003
2021-01-16 | 13:25 | 50.003
2021-01-16 | 13:25 | 50.003
2021-01-16 | 13:25 | 50.004
2021-01-16 | 13:25 | 50.005
2021-01-16 | 13:25 | 50.004
2021-01-16 | 13:25 | 50.006
2021-01-16 | 13:25 | 50.007
2021-01-16 | 13:25 | 50.008
2021-01-16 | 13:25 | 50.008
2021-01-16 | 13:25 | 50.011
2021-01-16 | 13:25 | 50.013
2021-01-16 | 13:25 | 50.011
2021-01-16 | 13:25 | 50.011
2021-01-16 | 13:25 | 50.008
2021-01-16 | 13:25 | 50.009
2021-01-16 | 13:25 | 50.007
2021-01-16 | 13:25 | 50.006
2021-01-16 | 13:25 | 50.006
2021-01-16 | 13:25 | 50.007
2021-01-16 | 13:25 | 50.007
2021-01-16 | 13:25 | 50.008
2021-01-16 | 13:25 | 50.008
2021-01-16 | 13:25 | 50.008
2021-01-16 | 13:25 | 50.01
2021-01-16 | 13:25 | 50.008
2021-01-16 | 13:25 | 50.01
2021-01-16 | 13:25 | 50.011
2021-01-16 | 13:25 | 50.013
2021-01-16 | 13:25 | 50.013
2021-01-16 | 13:25 | 50.012
2021-01-16 | 13:25 | 50.012
2021-01-16 | 13:25 | 50.01
2021-01-16 | 13:26 | 50.007
2021-01-16 | 13:26 | 50.008
2021-01-16 | 13:26 | 50.009
2021-01-16 | 13:26 | 50.008
2021-01-16 | 13:26 | 50.006
2021-01-16 | 13:26 | 50.005
2021-01-16 | 13:26 | 50.003
2021-01-16 | 13:26 | 50.002
2021-01-16 | 13:26 | 50.004
2021-01-16 | 13:26 | 50.008
2021-01-16 | 13:26 | 50.01
2021-01-16 | 13:26 | 50.012
2021-01-16 | 13:26 | 50.012
2021-01-16 | 13:26 | 50.015
2021-01-16 | 13:26 | 50.018
2021-01-16 | 13:26 | 50.019
2021-01-16 | 13:26 | 50.022
2021-01-16 | 13:26 | 50.024
2021-01-16 | 13:26 | 50.025
2021-01-16 | 13:26 | 50.025
2021-01-16 | 13:26 | 50.026
2021-01-16 | 13:26 | 50.019
2021-01-16 | 13:26 | 50.016
2021-01-16 | 13:26 | 50.012
2021-01-16 | 13:26 | 50.011
2021-01-16 | 13:26 | 50.009
2021-01-16 | 13:26 | 50.011
2021-01-16 | 13:26 | 50.014
2021-01-16 | 13:26 | 50.017
2021-01-16 | 13:26 | 50.019
2021-01-16 | 13:26 | 50.021
2021-01-16 | 13:26 | 50.021
2021-01-16 | 13:26 | 50.02
2021-01-16 | 13:26 | 50.021
2021-01-16 | 13:26 | 50.02
2021-01-16 | 13:26 | 50.016
2021-01-16 | 13:26 | 50.015
2021-01-16 | 13:26 | 50.014
2021-01-16 | 13:26 | 50.012
2021-01-16 | 13:26 | 50.013
2021-01-16 | 13:26 | 50.014
2021-01-16 | 13:26 | 50.017
2021-01-16 | 13:26 | 50.016
2021-01-16 | 13:26 | 50.016
2021-01-16 | 13:26 | 50.018
2021-01-16 | 13:26 | 50.022
2021-01-16 | 13:26 | 50.022
2021-01-16 | 13:26 | 50.023
2021-01-16 | 13:26 | 50.026
2021-01-16 | 13:26 | 50.027
2021-01-16 | 13:26 | 50.024
2021-01-16 | 13:26 | 50.025
2021-01-16 | 13:26 | 50.022
2021-01-16 | 13:26 | 50.02
2021-01-16 | 13:26 | 50.014
2021-01-16 | 13:26 | 50.009
2021-01-16 | 13:26 | 50.002
2021-01-16 | 13:26 | 50.006
2021-01-16 | 13:26 | 50.005
2021-01-16 | 13:26 | 50.005
2021-01-16 | 13:26 | 50.008
2021-01-16 | 13:27 | 50.011
2021-01-16 | 13:27 | 50.018
2021-01-16 | 13:27 | 50.027
2021-01-16 | 13:27 | 50.032
2021-01-16 | 13:27 | 50.034
2021-01-16 | 13:27 | 50.039
2021-01-16 | 13:27 | 50.043
2021-01-16 | 13:27 | 50.048
2021-01-16 | 13:27 | 50.048
2021-01-16 | 13:27 | 50.047
2021-01-16 | 13:27 | 50.044
2021-01-16 | 13:27 | 50.046
2021-01-16 | 13:27 | 50.045
2021-01-16 | 13:27 | 50.045
2021-01-16 | 13:27 | 50.044
2021-01-16 | 13:27 | 50.043
2021-01-16 | 13:27 | 50.044
2021-01-16 | 13:27 | 50.043
2021-01-16 | 13:27 | 50.044
2021-01-16 | 13:27 | 50.048
2021-01-16 | 13:27 | 50.052
2021-01-16 | 13:27 | 50.053
2021-01-16 | 13:27 | 50.056
2021-01-16 | 13:27 | 50.058
2021-01-16 | 13:27 | 50.059
2021-01-16 | 13:27 | 50.062
2021-01-16 | 13:27 | 50.069
2021-01-16 | 13:27 | 50.072
2021-01-16 | 13:27 | 50.07
2021-01-16 | 13:27 | 50.068
2021-01-16 | 13:27 | 50.07
2021-01-16 | 13:27 | 50.069
2021-01-16 | 13:27 | 50.069
2021-01-16 | 13:27 | 50.067
2021-01-16 | 13:27 | 50.067
2021-01-16 | 13:27 | 50.065
2021-01-16 | 13:27 | 50.063
2021-01-16 | 13:27 | 50.062
2021-01-16 | 13:27 | 50.062
2021-01-16 | 13:27 | 50.061
2021-01-16 | 13:27 | 50.061
2021-01-16 | 13:27 | 50.06
2021-01-16 | 13:27 | 50.058
2021-01-16 | 13:27 | 50.058
2021-01-16 | 13:27 | 50.059
2021-01-16 | 13:27 | 50.06
2021-01-16 | 13:27 | 50.061
2021-01-16 | 13:27 | 50.062
2021-01-16 | 13:27 | 50.064
2021-01-16 | 13:27 | 50.064
2021-01-16 | 13:27 | 50.065
2021-01-16 | 13:27 | 50.067
2021-01-16 | 13:27 | 50.07
2021-01-16 | 13:27 | 50.07
2021-01-16 | 13:27 | 50.069
2021-01-16 | 13:27 | 50.071
2021-01-16 | 13:27 | 50.07
2021-01-16 | 13:27 | 50.068
2021-01-16 | 13:27 | 50.066
2021-01-16 | 13:28 | 50.068
2021-01-16 | 13:28 | 50.068
2021-01-16 | 13:28 | 50.068
2021-01-16 | 13:28 | 50.07
2021-01-16 | 13:28 | 50.073
2021-01-16 | 13:28 | 50.072
2021-01-16 | 13:28 | 50.07
2021-01-16 | 13:28 | 50.068
2021-01-16 | 13:28 | 50.067
2021-01-16 | 13:28 | 50.07
2021-01-16 | 13:28 | 50.067
2021-01-16 | 13:28 | 50.069
2021-01-16 | 13:28 | 50.068
2021-01-16 | 13:28 | 50.068
2021-01-16 | 13:28 | 50.066
2021-01-16 | 13:28 | 50.064
2021-01-16 | 13:28 | 50.06
2021-01-16 | 13:28 | 50.059
2021-01-16 | 13:28 | 50.057
2021-01-16 | 13:28 | 50.055
2021-01-16 | 13:28 | 50.058
2021-01-16 | 13:28 | 50.057
2021-01-16 | 13:28 | 50.056
2021-01-16 | 13:28 | 50.057
2021-01-16 | 13:28 | 50.058
2021-01-16 | 13:28 | 50.06
2021-01-16 | 13:28 | 50.06
2021-01-16 | 13:28 | 50.06
2021-01-16 | 13:28 | 50.06
2021-01-16 | 13:28 | 50.059
2021-01-16 | 13:28 | 50.059
2021-01-16 | 13:28 | 50.06
2021-01-16 | 13:28 | 50.061
2021-01-16 | 13:28 | 50.062
2021-01-16 | 13:28 | 50.064
2021-01-16 | 13:28 | 50.066
2021-01-16 | 13:28 | 50.068
2021-01-16 | 13:28 | 50.07
2021-01-16 | 13:28 | 50.069
2021-01-16 | 13:28 | 50.07
2021-01-16 | 13:28 | 50.069
2021-01-16 | 13:28 | 50.069
2021-01-16 | 13:28 | 50.069
2021-01-16 | 13:28 | 50.07
2021-01-16 | 13:28 | 50.07
2021-01-16 | 13:28 | 50.068
2021-01-16 | 13:28 | 50.066
2021-01-16 | 13:28 | 50.067
2021-01-16 | 13:28 | 50.069
2021-01-16 | 13:28 | 50.07
2021-01-16 | 13:28 | 50.071
2021-01-16 | 13:28 | 50.071
2021-01-16 | 13:28 | 50.072
2021-01-16 | 13:28 | 50.073
2021-01-16 | 13:28 | 50.074
2021-01-16 | 13:28 | 50.075
2021-01-16 | 13:28 | 50.075
2021-01-16 | 13:28 | 50.076
2021-01-16 | 13:28 | 50.08
2021-01-16 | 13:28 | 50.08
2021-01-16 | 13:28 | 50.08
2021-01-16 | 13:29 | 50.083
2021-01-16 | 13:29 | 50.083
2021-01-16 | 13:29 | 50.085
2021-01-16 | 13:29 | 50.089
2021-01-16 | 13:29 | 50.091
2021-01-16 | 13:29 | 50.095
2021-01-16 | 13:29 | 50.099
2021-01-16 | 13:29 | 50.102
2021-01-16 | 13:29 | 50.11
2021-01-16 | 13:29 | 50.115
2021-01-16 | 13:29 | 50.119
2021-01-16 | 13:29 | 50.124
2021-01-16 | 13:29 | 50.126
2021-01-16 | 13:29 | 50.127
2021-01-16 | 13:29 | 50.131
2021-01-16 | 13:29 | 50.13
2021-01-16 | 13:29 | 50.126
2021-01-16 | 13:29 | 50.122
2021-01-16 | 13:29 | 50.118
2021-01-16 | 13:29 | 50.113
2021-01-16 | 13:29 | 50.104
2021-01-16 | 13:29 | 50.095
2021-01-16 | 13:29 | 50.096
2021-01-16 | 13:29 | 50.095
2021-01-16 | 13:29 | 50.097
2021-01-16 | 13:29 | 50.098
2021-01-16 | 13:29 | 50.1
2021-01-16 | 13:29 | 50.104
2021-01-16 | 13:29 | 50.105
2021-01-16 | 13:29 | 50.106
2021-01-16 | 13:29 | 50.108
2021-01-16 | 13:29 | 50.108
2021-01-16 | 13:29 | 50.109
2021-01-16 | 13:29 | 50.108
2021-01-16 | 13:29 | 50.107
2021-01-16 | 13:29 | 50.104
2021-01-16 | 13:29 | 50.106
2021-01-16 | 13:29 | 50.103
2021-01-16 | 13:29 | 50.104
2021-01-16 | 13:29 | 50.102
2021-01-16 | 13:29 | 50.1
2021-01-16 | 13:29 | 50.098
2021-01-16 | 13:29 | 50.097
2021-01-16 | 13:29 | 50.099
2021-01-16 | 13:29 | 50.102
2021-01-16 | 13:29 | 50.102
2021-01-16 | 13:29 | 50.106
2021-01-16 | 13:29 | 50.107
2021-01-16 | 13:29 | 50.11
2021-01-16 | 13:29 | 50.111
2021-01-16 | 13:29 | 50.111
2021-01-16 | 13:29 | 50.116
2021-01-16 | 13:29 | 50.118
2021-01-16 | 13:29 | 50.121
2021-01-16 | 13:29 | 50.121
2021-01-16 | 13:29 | 50.121
2021-01-16 | 13:29 | 50.122
2021-01-16 | 13:29 | 50.121
2021-01-16 | 13:29 | 50.121
2021-01-16 | 13:30 | 50.119
2021-01-16 | 13:30 | 50.12
2021-01-16 | 13:30 | 50.117
2021-01-16 | 13:30 | 50.117
2021-01-16 | 13:30 | 50.115
2021-01-16 | 13:30 | 50.111
2021-01-16 | 13:30 | 50.106
2021-01-16 | 13:30 | 50.106
2021-01-16 | 13:30 | 50.103
2021-01-16 | 13:30 | 50.103
2021-01-16 | 13:30 | 50.103
2021-01-16 | 13:30 | 50.102
2021-01-16 | 13:30 | 50.101
2021-01-16 | 13:30 | 50.103
2021-01-16 | 13:30 | 50.101
2021-01-16 | 13:30 | 50.101
2021-01-16 | 13:30 | 50.101
2021-01-16 | 13:30 | 50.102
2021-01-16 | 13:30 | 50.104
2021-01-16 | 13:30 | 50.1
2021-01-16 | 13:30 | 50.099
2021-01-16 | 13:30 | 50.1
2021-01-16 | 13:30 | 50.099
2021-01-16 | 13:30 | 50.098
2021-01-16 | 13:30 | 50.1
2021-01-16 | 13:30 | 50.1
2021-01-16 | 13:30 | 50.103
2021-01-16 | 13:30 | 50.105
2021-01-16 | 13:30 | 50.106
2021-01-16 | 13:30 | 50.109
2021-01-16 | 13:30 | 50.11
2021-01-16 | 13:30 | 50.108
2021-01-16 | 13:30 | 50.101
2021-01-16 | 13:30 | 50.098
2021-01-16 | 13:30 | 50.094
2021-01-16 | 13:30 | 50.089
2021-01-16 | 13:30 | 50.086
2021-01-16 | 13:30 | 50.083
2021-01-16 | 13:30 | 50.081
2021-01-16 | 13:30 | 50.079
2021-01-16 | 13:30 | 50.08
2021-01-16 | 13:30 | 50.079
2021-01-16 | 13:30 | 50.08
2021-01-16 | 13:30 | 50.082
2021-01-16 | 13:30 | 50.083
2021-01-16 | 13:30 | 50.085
2021-01-16 | 13:30 | 50.082
2021-01-16 | 13:30 | 50.08
2021-01-16 | 13:30 | 50.079
2021-01-16 | 13:30 | 50.077
2021-01-16 | 13:30 | 50.075
2021-01-16 | 13:30 | 50.072
2021-01-16 | 13:30 | 50.069
2021-01-16 | 13:30 | 50.066
2021-01-16 | 13:30 | 50.067
2021-01-16 | 13:30 | 50.067
2021-01-16 | 13:30 | 50.068
2021-01-16 | 13:30 | 50.067
2021-01-16 | 13:30 | 50.068
2021-01-16 | 13:30 | 50.069
2021-01-16 | 13:30 | 50.07
2021-01-16 | 13:31 | 50.069
2021-01-16 | 13:31 | 50.069
2021-01-16 | 13:31 | 50.07
2021-01-16 | 13:31 | 50.069
2021-01-16 | 13:31 | 50.07
2021-01-16 | 13:31 | 50.072
2021-01-16 | 13:31 | 50.075
2021-01-16 | 13:31 | 50.072
2021-01-16 | 13:31 | 50.075
2021-01-16 | 13:31 | 50.074
2021-01-16 | 13:31 | 50.075
2021-01-16 | 13:31 | 50.075
2021-01-16 | 13:31 | 50.077
2021-01-16 | 13:31 | 50.079
2021-01-16 | 13:31 | 50.081
2021-01-16 | 13:31 | 50.08
2021-01-16 | 13:31 | 50.08
2021-01-16 | 13:31 | 50.079
2021-01-16 | 13:31 | 50.08
2021-01-16 | 13:31 | 50.08
2021-01-16 | 13:31 | 50.079
2021-01-16 | 13:31 | 50.078
2021-01-16 | 13:31 | 50.076
2021-01-16 | 13:31 | 50.075
2021-01-16 | 13:31 | 50.075
2021-01-16 | 13:31 | 50.073
2021-01-16 | 13:31 | 50.071
2021-01-16 | 13:31 | 50.066
2021-01-16 | 13:31 | 50.063
2021-01-16 | 13:31 | 50.06
2021-01-16 | 13:31 | 50.056
2021-01-16 | 13:31 | 50.054
2021-01-16 | 13:31 | 50.05
2021-01-16 | 13:31 | 50.048
2021-01-16 | 13:31 | 50.046
2021-01-16 | 13:31 | 50.045
2021-01-16 | 13:31 | 50.044
2021-01-16 | 13:31 | 50.044
2021-01-16 | 13:31 | 50.042
2021-01-16 | 13:31 | 50.042
2021-01-16 | 13:31 | 50.04
2021-01-16 | 13:31 | 50.041
2021-01-16 | 13:31 | 50.04
2021-01-16 | 13:31 | 50.039
2021-01-16 | 13:31 | 50.039
2021-01-16 | 13:31 | 50.038
2021-01-16 | 13:31 | 50.037
2021-01-16 | 13:31 | 50.034
2021-01-16 | 13:31 | 50.035
2021-01-16 | 13:31 | 50.037
2021-01-16 | 13:31 | 50.034
2021-01-16 | 13:31 | 50.032
2021-01-16 | 13:31 | 50.03
2021-01-16 | 13:31 | 50.029
2021-01-16 | 13:31 | 50.029
2021-01-16 | 13:31 | 50.028
2021-01-16 | 13:31 | 50.028
2021-01-16 | 13:31 | 50.029
2021-01-16 | 13:31 | 50.031
2021-01-16 | 13:32 | 50.033
2021-01-16 | 13:32 | 50.034
2021-01-16 | 13:32 | 50.036
2021-01-16 | 13:32 | 50.035
2021-01-16 | 13:32 | 50.036
2021-01-16 | 13:32 | 50.038
2021-01-16 | 13:32 | 50.039
2021-01-16 | 13:32 | 50.04
2021-01-16 | 13:32 | 50.041
2021-01-16 | 13:32 | 50.04
2021-01-16 | 13:32 | 50.038
2021-01-16 | 13:32 | 50.035
2021-01-16 | 13:32 | 50.034
2021-01-16 | 13:32 | 50.034
2021-01-16 | 13:32 | 50.038
2021-01-16 | 13:32 | 50.037
2021-01-16 | 13:32 | 50.039
2021-01-16 | 13:32 | 50.042
2021-01-16 | 13:32 | 50.044
2021-01-16 | 13:32 | 50.048
2021-01-16 | 13:32 | 50.05
2021-01-16 | 13:32 | 50.051
2021-01-16 | 13:32 | 50.05
2021-01-16 | 13:32 | 50.049
2021-01-16 | 13:32 | 50.051
2021-01-16 | 13:32 | 50.05
2021-01-16 | 13:32 | 50.051
2021-01-16 | 13:32 | 50.049
2021-01-16 | 13:32 | 50.043
2021-01-16 | 13:32 | 50.039
2021-01-16 | 13:32 | 50.035
2021-01-16 | 13:32 | 50.032
2021-01-16 | 13:32 | 50.031
2021-01-16 | 13:32 | 50.03
2021-01-16 | 13:32 | 50.029
2021-01-16 | 13:32 | 50.029
2021-01-16 | 13:32 | 50.03
2021-01-16 | 13:32 | 50.031
2021-01-16 | 13:32 | 50.031
2021-01-16 | 13:32 | 50.029
2021-01-16 | 13:32 | 50.025
2021-01-16 | 13:32 | 50.022
2021-01-16 | 13:32 | 50.022
2021-01-16 | 13:32 | 50.024
2021-01-16 | 13:32 | 50.028
2021-01-16 | 13:32 | 50.03
2021-01-16 | 13:32 | 50.033
2021-01-16 | 13:32 | 50.033
2021-01-16 | 13:32 | 50.033
2021-01-16 | 13:32 | 50.034
2021-01-16 | 13:32 | 50.035
2021-01-16 | 13:32 | 50.032
2021-01-16 | 13:32 | 50.029
2021-01-16 | 13:32 | 50.026
2021-01-16 | 13:32 | 50.022
2021-01-16 | 13:32 | 50.019
2021-01-16 | 13:32 | 50.016
2021-01-16 | 13:32 | 50.013
2021-01-16 | 13:32 | 50.012
2021-01-16 | 13:32 | 50.012
2021-01-16 | 13:32 | 50.011
2021-01-16 | 13:33 | 50.01
2021-01-16 | 13:33 | 50.011
2021-01-16 | 13:33 | 50.01
2021-01-16 | 13:33 | 50.009
2021-01-16 | 13:33 | 50.006
2021-01-16 | 13:33 | 50.005
2021-01-16 | 13:33 | 50.001
2021-01-16 | 13:33 | 49.999
2021-01-16 | 13:33 | 49.996
2021-01-16 | 13:33 | 49.993
2021-01-16 | 13:33 | 49.99
2021-01-16 | 13:33 | 49.987
2021-01-16 | 13:33 | 49.987
2021-01-16 | 13:33 | 49.989
2021-01-16 | 13:33 | 49.989
2021-01-16 | 13:33 | 49.992
2021-01-16 | 13:33 | 49.994
2021-01-16 | 13:33 | 49.994
2021-01-16 | 13:33 | 49.995
2021-01-16 | 13:33 | 49.996
2021-01-16 | 13:33 | 49.998
2021-01-16 | 13:33 | 50.001
2021-01-16 | 13:33 | 50.003
2021-01-16 | 13:33 | 50.004
2021-01-16 | 13:33 | 50.007
2021-01-16 | 13:33 | 50.008
2021-01-16 | 13:33 | 50.011
2021-01-16 | 13:33 | 50.014
2021-01-16 | 13:33 | 50.016
2021-01-16 | 13:33 | 50.016
2021-01-16 | 13:33 | 50.016
2021-01-16 | 13:33 | 50.015
2021-01-16 | 13:33 | 50.013
2021-01-16 | 13:33 | 50.01
2021-01-16 | 13:33 | 50.007
2021-01-16 | 13:33 | 50.005
2021-01-16 | 13:33 | 50.003
2021-01-16 | 13:33 | 50.002
2021-01-16 | 13:33 | 50.003
2021-01-16 | 13:33 | 50.003
2021-01-16 | 13:33 | 50.002
2021-01-16 | 13:33 | 50
2021-01-16 | 13:33 | 49.997
2021-01-16 | 13:33 | 49.993
2021-01-16 | 13:33 | 49.987
2021-01-16 | 13:33 | 49.985
2021-01-16 | 13:33 | 49.981
2021-01-16 | 13:33 | 49.979
2021-01-16 | 13:33 | 49.978
2021-01-16 | 13:33 | 49.976
2021-01-16 | 13:33 | 49.975
2021-01-16 | 13:33 | 49.975
2021-01-16 | 13:33 | 49.978
2021-01-16 | 13:33 | 49.977
2021-01-16 | 13:33 | 49.977
2021-01-16 | 13:33 | 49.977
2021-01-16 | 13:33 | 49.978
2021-01-16 | 13:33 | 49.98
2021-01-16 | 13:33 | 49.987
2021-01-16 | 13:34 | 49.99
2021-01-16 | 13:34 | 49.993
2021-01-16 | 13:34 | 49.994
2021-01-16 | 13:34 | 49.994
2021-01-16 | 13:34 | 49.994
2021-01-16 | 13:34 | 49.996
2021-01-16 | 13:34 | 49.982
2021-01-16 | 13:34 | 49.996
2021-01-16 | 13:34 | 49.997
2021-01-16 | 13:34 | 50.003
2021-01-16 | 13:34 | 50.003
2021-01-16 | 13:34 | 50.031
2021-01-16 | 13:34 | 50.009
2021-01-16 | 13:34 | 50.014
2021-01-16 | 13:34 | 50.018
2021-01-16 | 13:34 | 50.022
2021-01-16 | 13:34 | 50.023
2021-01-16 | 13:34 | 50.026
2021-01-16 | 13:34 | 50.029
2021-01-16 | 13:34 | 50.035
2021-01-16 | 13:34 | 50.037
2021-01-16 | 13:34 | 50.039
2021-01-16 | 13:34 | 50.039
2021-01-16 | 13:34 | 50.041
2021-01-16 | 13:34 | 50.043
2021-01-16 | 13:34 | 50.043
2021-01-16 | 13:34 | 50.044
2021-01-16 | 13:34 | 50.045
2021-01-16 | 13:34 | 50.045
2021-01-16 | 13:34 | 50.046
2021-01-16 | 13:34 | 50.049
2021-01-16 | 13:34 | 50.048
2021-01-16 | 13:34 | 50.047
2021-01-16 | 13:34 | 50.047
2021-01-16 | 13:34 | 50.048
2021-01-16 | 13:34 | 50.047
2021-01-16 | 13:34 | 50.047
2021-01-16 | 13:34 | 50.048
2021-01-16 | 13:34 | 50.046
2021-01-16 | 13:34 | 50.047
2021-01-16 | 13:34 | 50.046
2021-01-16 | 13:34 | 50.045
2021-01-16 | 13:34 | 50.046
2021-01-16 | 13:34 | 50.045
2021-01-16 | 13:34 | 50.045
2021-01-16 | 13:34 | 50.044
2021-01-16 | 13:34 | 50.044
2021-01-16 | 13:34 | 50.041
2021-01-16 | 13:34 | 50.04
2021-01-16 | 13:34 | 50.038
2021-01-16 | 13:34 | 50.037
2021-01-16 | 13:34 | 50.037
2021-01-16 | 13:34 | 50.036
2021-01-16 | 13:34 | 50.036
2021-01-16 | 13:34 | 50.034
2021-01-16 | 13:34 | 50.032
2021-01-16 | 13:34 | 50.033
2021-01-16 | 13:34 | 50.034
2021-01-16 | 13:34 | 50.035
2021-01-16 | 13:34 | 50.037
2021-01-16 | 13:34 | 50.037
2021-01-16 | 13:35 | 50.038
2021-01-16 | 13:35 | 50.04
2021-01-16 | 13:35 | 50.04
2021-01-16 | 13:35 | 50.043
2021-01-16 | 13:35 | 50.045
2021-01-16 | 13:35 | 50.048
2021-01-16 | 13:35 | 50.051
2021-01-16 | 13:35 | 50.049
2021-01-16 | 13:35 | 50.048
2021-01-16 | 13:35 | 50.047
2021-01-16 | 13:35 | 50.046
2021-01-16 | 13:35 | 50.046
2021-01-16 | 13:35 | 50.048
2021-01-16 | 13:35 | 50.048
2021-01-16 | 13:35 | 50.048
2021-01-16 | 13:35 | 50.046
2021-01-16 | 13:35 | 50.044
2021-01-16 | 13:35 | 50.039
2021-01-16 | 13:35 | 50.039
2021-01-16 | 13:35 | 50.036
2021-01-16 | 13:35 | 50.037
2021-01-16 | 13:35 | 50.036
2021-01-16 | 13:35 | 50.036
2021-01-16 | 13:35 | 50.035
2021-01-16 | 13:35 | 50.034
2021-01-16 | 13:35 | 50.031
2021-01-16 | 13:35 | 50.031
2021-01-16 | 13:35 | 50.03
2021-01-16 | 13:35 | 50.031
2021-01-16 | 13:35 | 50.031
2021-01-16 | 13:35 | 50.03
2021-01-16 | 13:35 | 50.03
2021-01-16 | 13:35 | 50.031
2021-01-16 | 13:35 | 50.031
2021-01-16 | 13:35 | 50.032
2021-01-16 | 13:35 | 50.03
2021-01-16 | 13:35 | 50.031
2021-01-16 | 13:35 | 50.031
2021-01-16 | 13:35 | 50.03
2021-01-16 | 13:35 | 50.03
2021-01-16 | 13:35 | 50.029
2021-01-16 | 13:35 | 50.028
2021-01-16 | 13:35 | 50.03
2021-01-16 | 13:35 | 50.032
2021-01-16 | 13:35 | 50.032
2021-01-16 | 13:35 | 50.033
2021-01-16 | 13:35 | 50.034
2021-01-16 | 13:35 | 50.036
2021-01-16 | 13:35 | 50.035
2021-01-16 | 13:35 | 50.034
2021-01-16 | 13:35 | 50.03
2021-01-16 | 13:35 | 50.029
2021-01-16 | 13:35 | 50.029
2021-01-16 | 13:35 | 50.027
2021-01-16 | 13:35 | 50.027
2021-01-16 | 13:35 | 50.028
2021-01-16 | 13:35 | 50.025
2021-01-16 | 13:35 | 50.023
2021-01-16 | 13:35 | 50.022
2021-01-16 | 13:36 | 50.02
2021-01-16 | 13:36 | 50.024
2021-01-16 | 13:36 | 50.028
2021-01-16 | 13:36 | 50.031
2021-01-16 | 13:36 | 50.032
2021-01-16 | 13:36 | 50.033
2021-01-16 | 13:36 | 50.03
2021-01-16 | 13:36 | 50.027
2021-01-16 | 13:36 | 50.025
2021-01-16 | 13:36 | 50.022
2021-01-16 | 13:36 | 50.023
2021-01-16 | 13:36 | 50.022
2021-01-16 | 13:36 | 50.022
2021-01-16 | 13:36 | 50.023
2021-01-16 | 13:36 | 50.026
2021-01-16 | 13:36 | 50.028
2021-01-16 | 13:36 | 50.03
2021-01-16 | 13:36 | 50.033
2021-01-16 | 13:36 | 50.033
2021-01-16 | 13:36 | 50.032
2021-01-16 | 13:36 | 50.033
2021-01-16 | 13:36 | 50.035
2021-01-16 | 13:36 | 50.035
2021-01-16 | 13:36 | 50.035
2021-01-16 | 13:36 | 50.036
2021-01-16 | 13:36 | 50.036
2021-01-16 | 13:36 | 50.035
2021-01-16 | 13:36 | 50.034
2021-01-16 | 13:36 | 50.032
2021-01-16 | 13:36 | 50.031
2021-01-16 | 13:36 | 50.028
2021-01-16 | 13:36 | 50.027
2021-01-16 | 13:36 | 50.027
2021-01-16 | 13:36 | 50.025
2021-01-16 | 13:36 | 50.024
2021-01-16 | 13:36 | 50.023
2021-01-16 | 13:36 | 50.02
2021-01-16 | 13:36 | 50.021
2021-01-16 | 13:36 | 50.021
2021-01-16 | 13:36 | 50.02
2021-01-16 | 13:36 | 50.019
2021-01-16 | 13:36 | 50.02
2021-01-16 | 13:36 | 50.02
2021-01-16 | 13:36 | 50.022
2021-01-16 | 13:36 | 50.023
2021-01-16 | 13:36 | 50.021
2021-01-16 | 13:36 | 50.022
2021-01-16 | 13:36 | 50.022
2021-01-16 | 13:36 | 50.021
2021-01-16 | 13:36 | 50.02
2021-01-16 | 13:36 | 50.017
2021-01-16 | 13:36 | 50.013
2021-01-16 | 13:36 | 50.01
2021-01-16 | 13:36 | 50.01
2021-01-16 | 13:36 | 50.008
2021-01-16 | 13:36 | 50.008
2021-01-16 | 13:36 | 50.007
2021-01-16 | 13:36 | 50.008
2021-01-16 | 13:36 | 50.011
2021-01-16 | 13:36 | 50.013
2021-01-16 | 13:36 | 50.011
2021-01-16 | 13:37 | 50.013
2021-01-16 | 13:37 | 50.016
2021-01-16 | 13:37 | 50.015
2021-01-16 | 13:37 | 50.016
2021-01-16 | 13:37 | 50.013
2021-01-16 | 13:37 | 50.011
2021-01-16 | 13:37 | 50.011
2021-01-16 | 13:37 | 50.008
2021-01-16 | 13:37 | 50.007
2021-01-16 | 13:37 | 50.006
2021-01-16 | 13:37 | 50.004
2021-01-16 | 13:37 | 50.005
2021-01-16 | 13:37 | 50.004
2021-01-16 | 13:37 | 50.004
2021-01-16 | 13:37 | 50.004
2021-01-16 | 13:37 | 50.004
2021-01-16 | 13:37 | 50.006
2021-01-16 | 13:37 | 50.008
2021-01-16 | 13:37 | 50.009
2021-01-16 | 13:37 | 50.011
2021-01-16 | 13:37 | 50.012
2021-01-16 | 13:37 | 50.011
2021-01-16 | 13:37 | 50.012
2021-01-16 | 13:37 | 50.011
2021-01-16 | 13:37 | 50.014
2021-01-16 | 13:37 | 50.015
2021-01-16 | 13:37 | 50.015
2021-01-16 | 13:37 | 50.017
2021-01-16 | 13:37 | 50.016
2021-01-16 | 13:37 | 50.018
2021-01-16 | 13:37 | 50.018
2021-01-16 | 13:37 | 50.019
2021-01-16 | 13:37 | 50.02
2021-01-16 | 13:37 | 50.021
2021-01-16 | 13:37 | 50.023
2021-01-16 | 13:37 | 50.023
2021-01-16 | 13:37 | 50.027
2021-01-16 | 13:37 | 50.033
2021-01-16 | 13:37 | 50.036
2021-01-16 | 13:37 | 50.04
2021-01-16 | 13:37 | 50.042
2021-01-16 | 13:37 | 50.045
2021-01-16 | 13:37 | 50.044
2021-01-16 | 13:37 | 50.047
2021-01-16 | 13:37 | 50.047
2021-01-16 | 13:37 | 50.048
2021-01-16 | 13:37 | 50.049
2021-01-16 | 13:37 | 50.053
2021-01-16 | 13:37 | 50.054
2021-01-16 | 13:37 | 50.058
2021-01-16 | 13:37 | 50.058
2021-01-16 | 13:37 | 50.06
2021-01-16 | 13:37 | 50.057
2021-01-16 | 13:37 | 50.058
2021-01-16 | 13:37 | 50.057
2021-01-16 | 13:37 | 50.058
2021-01-16 | 13:37 | 50.056
2021-01-16 | 13:37 | 50.057
2021-01-16 | 13:37 | 50.054
2021-01-16 | 13:38 | 50.056
2021-01-16 | 13:38 | 50.056
2021-01-16 | 13:38 | 50.059
2021-01-16 | 13:38 | 50.06
2021-01-16 | 13:38 | 50.062
2021-01-16 | 13:38 | 50.063
2021-01-16 | 13:38 | 50.061
2021-01-16 | 13:38 | 50.061
2021-01-16 | 13:38 | 50.058
2021-01-16 | 13:38 | 50.057
2021-01-16 | 13:38 | 50.053
2021-01-16 | 13:38 | 50.049
2021-01-16 | 13:38 | 50.05
2021-01-16 | 13:38 | 50.051
2021-01-16 | 13:38 | 50.053
2021-01-16 | 13:38 | 50.055
2021-01-16 | 13:38 | 50.057
2021-01-16 | 13:38 | 50.06
2021-01-16 | 13:38 | 50.059
2021-01-16 | 13:38 | 50.058
2021-01-16 | 13:38 | 50.058
2021-01-16 | 13:38 | 50.056
2021-01-16 | 13:38 | 50.058
2021-01-16 | 13:38 | 50.061
2021-01-16 | 13:38 | 50.061
2021-01-16 | 13:38 | 50.063
2021-01-16 | 13:38 | 50.062
2021-01-16 | 13:38 | 50.063
2021-01-16 | 13:38 | 50.061
2021-01-16 | 13:38 | 50.06
2021-01-16 | 13:38 | 50.057
2021-01-16 | 13:38 | 50.056
2021-01-16 | 13:38 | 50.054
2021-01-16 | 13:38 | 50.053
2021-01-16 | 13:38 | 50.052
2021-01-16 | 13:38 | 50.051
2021-01-16 | 13:38 | 50.048
2021-01-16 | 13:38 | 50.046
2021-01-16 | 13:38 | 50.048
2021-01-16 | 13:38 | 50.048
2021-01-16 | 13:38 | 50.049
2021-01-16 | 13:38 | 50.05
2021-01-16 | 13:38 | 50.052
2021-01-16 | 13:38 | 50.052
2021-01-16 | 13:38 | 50.053
2021-01-16 | 13:38 | 50.054
2021-01-16 | 13:38 | 50.052
2021-01-16 | 13:38 | 50.051
2021-01-16 | 13:38 | 50.05
2021-01-16 | 13:38 | 50.049
2021-01-16 | 13:38 | 50.05
2021-01-16 | 13:38 | 50.053
2021-01-16 | 13:38 | 50.051
2021-01-16 | 13:38 | 50.049
2021-01-16 | 13:38 | 50.048
2021-01-16 | 13:38 | 50.049
2021-01-16 | 13:38 | 50.046
2021-01-16 | 13:38 | 50.041
2021-01-16 | 13:38 | 50.042
2021-01-16 | 13:38 | 50.04
2021-01-16 | 13:38 | 50.038
2021-01-16 | 13:39 | 50.042
2021-01-16 | 13:39 | 50.043
2021-01-16 | 13:39 | 50.048
2021-01-16 | 13:39 | 50.048
2021-01-16 | 13:39 | 50.049
2021-01-16 | 13:39 | 50.052
2021-01-16 | 13:39 | 50.053
2021-01-16 | 13:39 | 50.053
2021-01-16 | 13:39 | 50.055
2021-01-16 | 13:39 | 50.054
2021-01-16 | 13:39 | 50.054
2021-01-16 | 13:39 | 50.054
2021-01-16 | 13:39 | 50.054
2021-01-16 | 13:39 | 50.057
2021-01-16 | 13:39 | 50.061
2021-01-16 | 13:39 | 50.062
2021-01-16 | 13:39 | 50.067
2021-01-16 | 13:39 | 50.069
2021-01-16 | 13:39 | 50.07
2021-01-16 | 13:39 | 50.071
2021-01-16 | 13:39 | 50.073
2021-01-16 | 13:39 | 50.073
2021-01-16 | 13:39 | 50.071
2021-01-16 | 13:39 | 50.069
2021-01-16 | 13:39 | 50.068
2021-01-16 | 13:39 | 50.067
2021-01-16 | 13:39 | 50.065
2021-01-16 | 13:39 | 50.062
2021-01-16 | 13:39 | 50.061
2021-01-16 | 13:39 | 50.06
2021-01-16 | 13:39 | 50.057
2021-01-16 | 13:39 | 50.055
2021-01-16 | 13:39 | 50.057
2021-01-16 | 13:39 | 50.06
2021-01-16 | 13:39 | 50.062
2021-01-16 | 13:39 | 50.061
2021-01-16 | 13:39 | 50.061
2021-01-16 | 13:39 | 50.063
2021-01-16 | 13:39 | 50.063
2021-01-16 | 13:39 | 50.06
2021-01-16 | 13:39 | 50.06
2021-01-16 | 13:39 | 50.057
2021-01-16 | 13:39 | 50.053
2021-01-16 | 13:39 | 50.051
2021-01-16 | 13:39 | 50.046
2021-01-16 | 13:39 | 50.046
2021-01-16 | 13:39 | 50.042
2021-01-16 | 13:39 | 50.041
2021-01-16 | 13:39 | 50.039
2021-01-16 | 13:39 | 50.038
2021-01-16 | 13:39 | 50.038
2021-01-16 | 13:39 | 50.038
2021-01-16 | 13:39 | 50.036
2021-01-16 | 13:39 | 50.035
2021-01-16 | 13:39 | 50.036
2021-01-16 | 13:39 | 50.039
2021-01-16 | 13:39 | 50.04
2021-01-16 | 13:39 | 50.042
2021-01-16 | 13:39 | 50.045
2021-01-16 | 13:40 | 50.05
2021-01-16 | 13:40 | 50.05
2021-01-16 | 13:40 | 50.052
2021-01-16 | 13:40 | 50.051
2021-01-16 | 13:40 | 50.053
2021-01-16 | 13:40 | 50.053
2021-01-16 | 13:40 | 50.051
2021-01-16 | 13:40 | 50.049
2021-01-16 | 13:40 | 50.047
2021-01-16 | 13:40 | 50.049
2021-01-16 | 13:40 | 50.051
2021-01-16 | 13:40 | 50.052
2021-01-16 | 13:40 | 50.052
2021-01-16 | 13:40 | 50.055
2021-01-16 | 13:40 | 50.057
2021-01-16 | 13:40 | 50.055
2021-01-16 | 13:40 | 50.053
2021-01-16 | 13:40 | 50.051
2021-01-16 | 13:40 | 50.052
2021-01-16 | 13:40 | 50.051
2021-01-16 | 13:40 | 50.052
2021-01-16 | 13:40 | 50.051
2021-01-16 | 13:40 | 50.054
2021-01-16 | 13:40 | 50.056
2021-01-16 | 13:40 | 50.06
2021-01-16 | 13:40 | 50.064
2021-01-16 | 13:40 | 50.067
2021-01-16 | 13:40 | 50.068
2021-01-16 | 13:40 | 50.068
2021-01-16 | 13:40 | 50.068
2021-01-16 | 13:40 | 50.072
2021-01-16 | 13:40 | 50.071
2021-01-16 | 13:40 | 50.072
2021-01-16 | 13:40 | 50.072
2021-01-16 | 13:40 | 50.074
2021-01-16 | 13:40 | 50.074
2021-01-16 | 13:40 | 50.075
2021-01-16 | 13:40 | 50.075
2021-01-16 | 13:40 | 50.076
2021-01-16 | 13:40 | 50.072
2021-01-16 | 13:40 | 50.071
2021-01-16 | 13:40 | 50.068
2021-01-16 | 13:40 | 50.066
2021-01-16 | 13:40 | 50.068
2021-01-16 | 13:40 | 50.069
2021-01-16 | 13:40 | 50.071
2021-01-16 | 13:40 | 50.072
2021-01-16 | 13:40 | 50.074
2021-01-16 | 13:40 | 50.073
2021-01-16 | 13:40 | 50.074
2021-01-16 | 13:40 | 50.078
2021-01-16 | 13:40 | 50.08
2021-01-16 | 13:40 | 50.081
2021-01-16 | 13:40 | 50.082
2021-01-16 | 13:40 | 50.084
2021-01-16 | 13:40 | 50.085
2021-01-16 | 13:40 | 50.084
2021-01-16 | 13:40 | 50.084
2021-01-16 | 13:40 | 50.084
2021-01-16 | 13:40 | 50.083
2021-01-16 | 13:40 | 50.085
2021-01-16 | 13:41 | 50.085
2021-01-16 | 13:41 | 50.086
2021-01-16 | 13:41 | 50.086
2021-01-16 | 13:41 | 50.088
2021-01-16 | 13:41 | 50.085
2021-01-16 | 13:41 | 50.084
2021-01-16 | 13:41 | 50.084
2021-01-16 | 13:41 | 50.082
2021-01-16 | 13:41 | 50.083
2021-01-16 | 13:41 | 50.079
2021-01-16 | 13:41 | 50.082
2021-01-16 | 13:41 | 50.08
2021-01-16 | 13:41 | 50.08
2021-01-16 | 13:41 | 50.084
2021-01-16 | 13:41 | 50.083
2021-01-16 | 13:41 | 50.084
2021-01-16 | 13:41 | 50.087
2021-01-16 | 13:41 | 50.086
2021-01-16 | 13:41 | 50.085
2021-01-16 | 13:41 | 50.085
2021-01-16 | 13:41 | 50.087
2021-01-16 | 13:41 | 50.087
2021-01-16 | 13:41 | 50.088
2021-01-16 | 13:41 | 50.088
2021-01-16 | 13:41 | 50.093
2021-01-16 | 13:41 | 50.096
2021-01-16 | 13:41 | 50.099
2021-01-16 | 13:41 | 50.101
2021-01-16 | 13:41 | 50.098
2021-01-16 | 13:41 | 50.098
2021-01-16 | 13:41 | 50.093
2021-01-16 | 13:41 | 50.092
2021-01-16 | 13:41 | 50.096
2021-01-16 | 13:41 | 50.099
2021-01-16 | 13:41 | 50.101
2021-01-16 | 13:41 | 50.102
2021-01-16 | 13:41 | 50.105
2021-01-16 | 13:41 | 50.107
2021-01-16 | 13:41 | 50.107
2021-01-16 | 13:41 | 50.108
2021-01-16 | 13:41 | 50.106
2021-01-16 | 13:41 | 50.108
2021-01-16 | 13:41 | 50.108
2021-01-16 | 13:41 | 50.107
2021-01-16 | 13:41 | 50.107
2021-01-16 | 13:41 | 50.107
2021-01-16 | 13:41 | 50.109
2021-01-16 | 13:41 | 50.108
2021-01-16 | 13:41 | 50.109
2021-01-16 | 13:41 | 50.109
2021-01-16 | 13:41 | 50.108
2021-01-16 | 13:41 | 50.107
2021-01-16 | 13:41 | 50.105
2021-01-16 | 13:41 | 50.103
2021-01-16 | 13:41 | 50.101
2021-01-16 | 13:41 | 50.099
2021-01-16 | 13:41 | 50.1
2021-01-16 | 13:41 | 50.101
2021-01-16 | 13:41 | 50.101
2021-01-16 | 13:42 | 50.103
2021-01-16 | 13:42 | 50.103
2021-01-16 | 13:42 | 50.101
2021-01-16 | 13:42 | 50.1
2021-01-16 | 13:42 | 50.1
2021-01-16 | 13:42 | 50.102
2021-01-16 | 13:42 | 50.103
2021-01-16 | 13:42 | 50.104
2021-01-16 | 13:42 | 50.104
2021-01-16 | 13:42 | 50.102
2021-01-16 | 13:42 | 50.102
2021-01-16 | 13:42 | 50.101
2021-01-16 | 13:42 | 50.104
2021-01-16 | 13:42 | 50.105
2021-01-16 | 13:42 | 50.108
2021-01-16 | 13:42 | 50.108
2021-01-16 | 13:42 | 50.112
2021-01-16 | 13:42 | 50.113
2021-01-16 | 13:42 | 50.114
2021-01-16 | 13:42 | 50.114
2021-01-16 | 13:42 | 50.118
2021-01-16 | 13:42 | 50.117
2021-01-16 | 13:42 | 50.115
2021-01-16 | 13:42 | 50.112
2021-01-16 | 13:42 | 50.107
2021-01-16 | 13:42 | 50.104
2021-01-16 | 13:42 | 50.101
2021-01-16 | 13:42 | 50.101
2021-01-16 | 13:42 | 50.102
2021-01-16 | 13:42 | 50.105
2021-01-16 | 13:42 | 50.105
2021-01-16 | 13:42 | 50.103
2021-01-16 | 13:42 | 50.105
2021-01-16 | 13:42 | 50.105
2021-01-16 | 13:42 | 50.105
2021-01-16 | 13:42 | 50.105
2021-01-16 | 13:42 | 50.105
2021-01-16 | 13:42 | 50.103
2021-01-16 | 13:42 | 50.105
2021-01-16 | 13:42 | 50.105
2021-01-16 | 13:42 | 50.105
2021-01-16 | 13:42 | 50.104
2021-01-16 | 13:42 | 50.104
2021-01-16 | 13:42 | 50.102
2021-01-16 | 13:42 | 50.103
2021-01-16 | 13:42 | 50.104
2021-01-16 | 13:42 | 50.102
2021-01-16 | 13:42 | 50.101
2021-01-16 | 13:42 | 50.105
2021-01-16 | 13:42 | 50.104
2021-01-16 | 13:42 | 50.103
2021-01-16 | 13:42 | 50.102
2021-01-16 | 13:42 | 50.101
2021-01-16 | 13:42 | 50.101
2021-01-16 | 13:42 | 50.101
2021-01-16 | 13:42 | 50.1
2021-01-16 | 13:42 | 50.098
2021-01-16 | 13:42 | 50.099
2021-01-16 | 13:42 | 50.101
2021-01-16 | 13:42 | 50.099
2021-01-16 | 13:42 | 50.1
2021-01-16 | 13:43 | 50.099
2021-01-16 | 13:43 | 50.098
2021-01-16 | 13:43 | 50.098
2021-01-16 | 13:43 | 50.097
2021-01-16 | 13:43 | 50.099
2021-01-16 | 13:43 | 50.1
2021-01-16 | 13:43 | 50.102
2021-01-16 | 13:43 | 50.1
2021-01-16 | 13:43 | 50.099
2021-01-16 | 13:43 | 50.1
2021-01-16 | 13:43 | 50.101
2021-01-16 | 13:43 | 50.102
2021-01-16 | 13:43 | 50.102
2021-01-16 | 13:43 | 50.101
2021-01-16 | 13:43 | 50.101
2021-01-16 | 13:43 | 50.102
2021-01-16 | 13:43 | 50.101
2021-01-16 | 13:43 | 50.099
2021-01-16 | 13:43 | 50.098
2021-01-16 | 13:43 | 50.096
2021-01-16 | 13:43 | 50.094
2021-01-16 | 13:43 | 50.093
2021-01-16 | 13:43 | 50.091
2021-01-16 | 13:43 | 50.092
2021-01-16 | 13:43 | 50.09
2021-01-16 | 13:43 | 50.088
2021-01-16 | 13:43 | 50.088
2021-01-16 | 13:43 | 50.087
2021-01-16 | 13:43 | 50.085
2021-01-16 | 13:43 | 50.083
2021-01-16 | 13:43 | 50.079
2021-01-16 | 13:43 | 50.076
2021-01-16 | 13:43 | 50.072
2021-01-16 | 13:43 | 50.068
2021-01-16 | 13:43 | 50.066
2021-01-16 | 13:43 | 50.065
2021-01-16 | 13:43 | 50.064
2021-01-16 | 13:43 | 50.06
2021-01-16 | 13:43 | 50.058
2021-01-16 | 13:43 | 50.055
2021-01-16 | 13:43 | 50.052
2021-01-16 | 13:43 | 50.051
2021-01-16 | 13:43 | 50.049
2021-01-16 | 13:43 | 50.047
2021-01-16 | 13:43 | 50.045
2021-01-16 | 13:43 | 50.041
2021-01-16 | 13:43 | 50.038
2021-01-16 | 13:43 | 50.034
2021-01-16 | 13:43 | 50.031
2021-01-16 | 13:43 | 50.028
2021-01-16 | 13:43 | 50.025
2021-01-16 | 13:43 | 50.023
2021-01-16 | 13:43 | 50.024
2021-01-16 | 13:43 | 50.024
2021-01-16 | 13:43 | 50.027
2021-01-16 | 13:43 | 50.028
2021-01-16 | 13:43 | 50.029
2021-01-16 | 13:43 | 50.027
2021-01-16 | 13:43 | 50.026
2021-01-16 | 13:44 | 50.023
2021-01-16 | 13:44 | 50.022
2021-01-16 | 13:44 | 50.022
2021-01-16 | 13:44 | 50.021
2021-01-16 | 13:44 | 50.022
2021-01-16 | 13:44 | 50.02
2021-01-16 | 13:44 | 50.018
2021-01-16 | 13:44 | 50.017
2021-01-16 | 13:44 | 50.014
2021-01-16 | 13:44 | 50.01
2021-01-16 | 13:44 | 50.004
2021-01-16 | 13:44 | 50
2021-01-16 | 13:44 | 49.992
2021-01-16 | 13:44 | 49.987
2021-01-16 | 13:44 | 49.983
2021-01-16 | 13:44 | 49.979
2021-01-16 | 13:44 | 49.977
2021-01-16 | 13:44 | 49.976
2021-01-16 | 13:44 | 49.977
2021-01-16 | 13:44 | 49.976
2021-01-16 | 13:44 | 49.974
2021-01-16 | 13:44 | 49.974
2021-01-16 | 13:44 | 49.974
2021-01-16 | 13:44 | 49.973
2021-01-16 | 13:44 | 49.974
2021-01-16 | 13:44 | 49.973
2021-01-16 | 13:44 | 49.973
2021-01-16 | 13:44 | 49.975
2021-01-16 | 13:44 | 49.976
2021-01-16 | 13:44 | 49.979
2021-01-16 | 13:44 | 49.977
2021-01-16 | 13:44 | 49.976
2021-01-16 | 13:44 | 49.978
2021-01-16 | 13:44 | 49.979
2021-01-16 | 13:44 | 49.979
2021-01-16 | 13:44 | 49.979
2021-01-16 | 13:44 | 49.979
2021-01-16 | 13:44 | 49.98
2021-01-16 | 13:44 | 49.978
2021-01-16 | 13:44 | 49.977
2021-01-16 | 13:44 | 49.976
2021-01-16 | 13:44 | 49.974
2021-01-16 | 13:44 | 49.972
2021-01-16 | 13:44 | 49.973
2021-01-16 | 13:44 | 49.973
2021-01-16 | 13:44 | 49.973
2021-01-16 | 13:44 | 49.975
2021-01-16 | 13:44 | 49.976
2021-01-16 | 13:44 | 49.977
2021-01-16 | 13:44 | 49.975
2021-01-16 | 13:44 | 49.975
2021-01-16 | 13:44 | 49.976
2021-01-16 | 13:44 | 49.976
2021-01-16 | 13:44 | 49.978
2021-01-16 | 13:44 | 49.979
2021-01-16 | 13:44 | 49.977
2021-01-16 | 13:44 | 49.976
2021-01-16 | 13:44 | 49.972
2021-01-16 | 13:44 | 49.971
2021-01-16 | 13:44 | 49.967
2021-01-16 | 13:44 | 49.966
2021-01-16 | 13:45 | 49.963
2021-01-16 | 13:45 | 49.962
2021-01-16 | 13:45 | 49.962
2021-01-16 | 13:45 | 49.963
2021-01-16 | 13:45 | 49.964
2021-01-16 | 13:45 | 49.965
2021-01-16 | 13:45 | 49.969
2021-01-16 | 13:45 | 49.974
2021-01-16 | 13:45 | 49.979
2021-01-16 | 13:45 | 49.981
2021-01-16 | 13:45 | 49.982
2021-01-16 | 13:45 | 49.982
2021-01-16 | 13:45 | 49.985
2021-01-16 | 13:45 | 49.986
2021-01-16 | 13:45 | 49.988
2021-01-16 | 13:45 | 49.987
2021-01-16 | 13:45 | 49.988
2021-01-16 | 13:45 | 49.988
2021-01-16 | 13:45 | 49.991
2021-01-16 | 13:45 | 49.994
2021-01-16 | 13:45 | 50
2021-01-16 | 13:45 | 50
2021-01-16 | 13:45 | 50.001
2021-01-16 | 13:45 | 50.003
2021-01-16 | 13:45 | 50.005
2021-01-16 | 13:45 | 50.008
2021-01-16 | 13:45 | 50.01
2021-01-16 | 13:45 | 50.011
2021-01-16 | 13:45 | 50.011
2021-01-16 | 13:45 | 50.009
2021-01-16 | 13:45 | 50.007
2021-01-16 | 13:45 | 50.003
2021-01-16 | 13:45 | 50.003
2021-01-16 | 13:45 | 50.002
2021-01-16 | 13:45 | 50.001
2021-01-16 | 13:45 | 49.999
2021-01-16 | 13:45 | 49.997
2021-01-16 | 13:45 | 49.994
2021-01-16 | 13:45 | 49.989
2021-01-16 | 13:45 | 49.986
2021-01-16 | 13:45 | 49.985
2021-01-16 | 13:45 | 49.982
2021-01-16 | 13:45 | 49.979
2021-01-16 | 13:45 | 49.978
2021-01-16 | 13:45 | 49.977
2021-01-16 | 13:45 | 49.976
2021-01-16 | 13:45 | 49.977
2021-01-16 | 13:45 | 49.978
2021-01-16 | 13:45 | 49.976
2021-01-16 | 13:45 | 49.976
2021-01-16 | 13:45 | 49.975
2021-01-16 | 13:45 | 49.976
2021-01-16 | 13:45 | 49.973
2021-01-16 | 13:45 | 49.973
2021-01-16 | 13:45 | 49.972
2021-01-16 | 13:45 | 49.972
2021-01-16 | 13:45 | 49.972
2021-01-16 | 13:45 | 49.971
2021-01-16 | 13:45 | 49.971
2021-01-16 | 13:46 | 49.97
2021-01-16 | 13:46 | 49.97
2021-01-16 | 13:46 | 49.97
2021-01-16 | 13:46 | 49.97
2021-01-16 | 13:46 | 49.976
2021-01-16 | 13:46 | 49.979
2021-01-16 | 13:46 | 49.98
2021-01-16 | 13:46 | 49.979
2021-01-16 | 13:46 | 49.979
2021-01-16 | 13:46 | 49.981
2021-01-16 | 13:46 | 49.982
2021-01-16 | 13:46 | 49.983
2021-01-16 | 13:46 | 49.981
2021-01-16 | 13:46 | 49.981
2021-01-16 | 13:46 | 49.978
2021-01-16 | 13:46 | 49.977
2021-01-16 | 13:46 | 49.974
2021-01-16 | 13:46 | 49.972
2021-01-16 | 13:46 | 49.968
2021-01-16 | 13:46 | 49.966
2021-01-16 | 13:46 | 49.965
2021-01-16 | 13:46 | 49.964
2021-01-16 | 13:46 | 49.964
2021-01-16 | 13:46 | 49.964
2021-01-16 | 13:46 | 49.964
2021-01-16 | 13:46 | 49.965
2021-01-16 | 13:46 | 49.966
2021-01-16 | 13:46 | 49.967
2021-01-16 | 13:46 | 49.97
2021-01-16 | 13:46 | 49.971
2021-01-16 | 13:46 | 49.972
2021-01-16 | 13:46 | 49.973
2021-01-16 | 13:46 | 49.972
2021-01-16 | 13:46 | 49.97
2021-01-16 | 13:46 | 49.969
2021-01-16 | 13:46 | 49.968
2021-01-16 | 13:46 | 49.967
2021-01-16 | 13:46 | 49.967
2021-01-16 | 13:46 | 49.964
2021-01-16 | 13:46 | 49.964
2021-01-16 | 13:46 | 49.962
2021-01-16 | 13:46 | 49.96
2021-01-16 | 13:46 | 49.957
2021-01-16 | 13:46 | 49.953
2021-01-16 | 13:46 | 49.951
2021-01-16 | 13:46 | 49.95
2021-01-16 | 13:46 | 49.951
2021-01-16 | 13:46 | 49.95
2021-01-16 | 13:46 | 49.952
2021-01-16 | 13:46 | 49.954
2021-01-16 | 13:46 | 49.955
2021-01-16 | 13:46 | 49.954
2021-01-16 | 13:46 | 49.953
2021-01-16 | 13:46 | 49.954
2021-01-16 | 13:46 | 49.955
2021-01-16 | 13:46 | 49.955
2021-01-16 | 13:46 | 49.958
2021-01-16 | 13:46 | 49.961
2021-01-16 | 13:46 | 49.964
2021-01-16 | 13:46 | 49.966
2021-01-16 | 13:46 | 49.967
2021-01-16 | 13:47 | 49.966
2021-01-16 | 13:47 | 49.967
2021-01-16 | 13:47 | 49.968
2021-01-16 | 13:47 | 49.969
2021-01-16 | 13:47 | 49.969
2021-01-16 | 13:47 | 49.971
2021-01-16 | 13:47 | 49.97
2021-01-16 | 13:47 | 49.967
2021-01-16 | 13:47 | 49.964
2021-01-16 | 13:47 | 49.961
2021-01-16 | 13:47 | 49.959
2021-01-16 | 13:47 | 49.956
2021-01-16 | 13:47 | 49.955
2021-01-16 | 13:47 | 49.953
2021-01-16 | 13:47 | 49.952
2021-01-16 | 13:47 | 49.952
2021-01-16 | 13:47 | 49.95
2021-01-16 | 13:47 | 49.948
2021-01-16 | 13:47 | 49.947
2021-01-16 | 13:47 | 49.945
2021-01-16 | 13:47 | 49.945
2021-01-16 | 13:47 | 49.944
2021-01-16 | 13:47 | 49.943
2021-01-16 | 13:47 | 49.942
2021-01-16 | 13:47 | 49.939
2021-01-16 | 13:47 | 49.937
2021-01-16 | 13:47 | 49.933
2021-01-16 | 13:47 | 49.932
2021-01-16 | 13:47 | 49.935
2021-01-16 | 13:47 | 49.937
2021-01-16 | 13:47 | 49.934
2021-01-16 | 13:47 | 49.932
2021-01-16 | 13:47 | 49.931
2021-01-16 | 13:47 | 49.93
2021-01-16 | 13:47 | 49.932
2021-01-16 | 13:47 | 49.931
2021-01-16 | 13:47 | 49.932
2021-01-16 | 13:47 | 49.931
2021-01-16 | 13:47 | 49.93
2021-01-16 | 13:47 | 49.929
2021-01-16 | 13:47 | 49.929
2021-01-16 | 13:47 | 49.929
2021-01-16 | 13:47 | 49.929
2021-01-16 | 13:47 | 49.928
2021-01-16 | 13:47 | 49.926
2021-01-16 | 13:47 | 49.922
2021-01-16 | 13:47 | 49.917
2021-01-16 | 13:47 | 49.916
2021-01-16 | 13:47 | 49.916
2021-01-16 | 13:47 | 49.915
2021-01-16 | 13:47 | 49.915
2021-01-16 | 13:47 | 49.918
2021-01-16 | 13:47 | 49.918
2021-01-16 | 13:47 | 49.915
2021-01-16 | 13:47 | 49.915
2021-01-16 | 13:47 | 49.916
2021-01-16 | 13:47 | 49.916
2021-01-16 | 13:47 | 49.917
2021-01-16 | 13:47 | 49.918
2021-01-16 | 13:48 | 49.916
2021-01-16 | 13:48 | 49.915
2021-01-16 | 13:48 | 49.914
2021-01-16 | 13:48 | 49.916
2021-01-16 | 13:48 | 49.917
2021-01-16 | 13:48 | 49.919
2021-01-16 | 13:48 | 49.921
2021-01-16 | 13:48 | 49.921
2021-01-16 | 13:48 | 49.923
2021-01-16 | 13:48 | 49.925
2021-01-16 | 13:48 | 49.927
2021-01-16 | 13:48 | 49.928
2021-01-16 | 13:48 | 49.929
2021-01-16 | 13:48 | 49.929
2021-01-16 | 13:48 | 49.929
2021-01-16 | 13:48 | 49.93
2021-01-16 | 13:48 | 49.93
2021-01-16 | 13:48 | 49.93
2021-01-16 | 13:48 | 49.928
2021-01-16 | 13:48 | 49.928
2021-01-16 | 13:48 | 49.926
2021-01-16 | 13:48 | 49.924
2021-01-16 | 13:48 | 49.923
2021-01-16 | 13:48 | 49.922
2021-01-16 | 13:48 | 49.922
2021-01-16 | 13:48 | 49.921
2021-01-16 | 13:48 | 49.921
2021-01-16 | 13:48 | 49.919
2021-01-16 | 13:48 | 49.919
2021-01-16 | 13:48 | 49.919
2021-01-16 | 13:48 | 49.919
2021-01-16 | 13:48 | 49.919
2021-01-16 | 13:48 | 49.918
2021-01-16 | 13:48 | 49.918
2021-01-16 | 13:48 | 49.917
2021-01-16 | 13:48 | 49.915
2021-01-16 | 13:48 | 49.912
2021-01-16 | 13:48 | 49.91
2021-01-16 | 13:48 | 49.908
2021-01-16 | 13:48 | 49.905
2021-01-16 | 13:48 | 49.902
2021-01-16 | 13:48 | 49.9
2021-01-16 | 13:48 | 49.899
2021-01-16 | 13:48 | 49.896
2021-01-16 | 13:48 | 49.896
2021-01-16 | 13:48 | 49.895
2021-01-16 | 13:48 | 49.893
2021-01-16 | 13:48 | 49.893
2021-01-16 | 13:48 | 49.89
2021-01-16 | 13:48 | 49.889
2021-01-16 | 13:48 | 49.889
2021-01-16 | 13:48 | 49.891
2021-01-16 | 13:48 | 49.89
2021-01-16 | 13:48 | 49.892
2021-01-16 | 13:48 | 49.892
2021-01-16 | 13:48 | 49.892
2021-01-16 | 13:48 | 49.892
2021-01-16 | 13:48 | 49.894
2021-01-16 | 13:48 | 49.894
2021-01-16 | 13:48 | 49.896
2021-01-16 | 13:48 | 49.899
2021-01-16 | 13:49 | 49.898
2021-01-16 | 13:49 | 49.896
2021-01-16 | 13:49 | 49.896
2021-01-16 | 13:49 | 49.895
2021-01-16 | 13:49 | 49.896
2021-01-16 | 13:49 | 49.899
2021-01-16 | 13:49 | 49.897
2021-01-16 | 13:49 | 49.897
2021-01-16 | 13:49 | 49.898
2021-01-16 | 13:49 | 49.897
2021-01-16 | 13:49 | 49.898
2021-01-16 | 13:49 | 49.897
2021-01-16 | 13:49 | 49.898
2021-01-16 | 13:49 | 49.9
2021-01-16 | 13:49 | 49.903
2021-01-16 | 13:49 | 49.906
2021-01-16 | 13:49 | 49.909
2021-01-16 | 13:49 | 49.908
2021-01-16 | 13:49 | 49.906
2021-01-16 | 13:49 | 49.907
2021-01-16 | 13:49 | 49.907
2021-01-16 | 13:49 | 49.906
2021-01-16 | 13:49 | 49.907
2021-01-16 | 13:49 | 49.905
2021-01-16 | 13:49 | 49.902
2021-01-16 | 13:49 | 49.903
2021-01-16 | 13:49 | 49.903
2021-01-16 | 13:49 | 49.903
2021-01-16 | 13:49 | 49.904
2021-01-16 | 13:49 | 49.905
2021-01-16 | 13:49 | 49.906
2021-01-16 | 13:49 | 49.906
2021-01-16 | 13:49 | 49.906
2021-01-16 | 13:49 | 49.906
2021-01-16 | 13:49 | 49.905
2021-01-16 | 13:49 | 49.904
2021-01-16 | 13:49 | 49.901
2021-01-16 | 13:49 | 49.898
2021-01-16 | 13:49 | 49.895
2021-01-16 | 13:49 | 49.892
2021-01-16 | 13:49 | 49.89
2021-01-16 | 13:49 | 49.887
2021-01-16 | 13:49 | 49.887
2021-01-16 | 13:49 | 49.886
2021-01-16 | 13:49 | 49.886
2021-01-16 | 13:49 | 49.888
2021-01-16 | 13:49 | 49.888
2021-01-16 | 13:49 | 49.889
2021-01-16 | 13:49 | 49.888
2021-01-16 | 13:49 | 49.89
2021-01-16 | 13:49 | 49.892
2021-01-16 | 13:49 | 49.892
2021-01-16 | 13:49 | 49.893
2021-01-16 | 13:49 | 49.894
2021-01-16 | 13:49 | 49.898
2021-01-16 | 13:49 | 49.903
2021-01-16 | 13:49 | 49.905
2021-01-16 | 13:49 | 49.907
2021-01-16 | 13:49 | 49.911
2021-01-16 | 13:50 | 49.915
2021-01-16 | 13:50 | 49.918
2021-01-16 | 13:50 | 49.919
2021-01-16 | 13:50 | 49.918
2021-01-16 | 13:50 | 49.92
2021-01-16 | 13:50 | 49.921
2021-01-16 | 13:50 | 49.922
2021-01-16 | 13:50 | 49.92
2021-01-16 | 13:50 | 49.922
2021-01-16 | 13:50 | 49.923
2021-01-16 | 13:50 | 49.923
2021-01-16 | 13:50 | 49.924
2021-01-16 | 13:50 | 49.924
2021-01-16 | 13:50 | 49.924
2021-01-16 | 13:50 | 49.922
2021-01-16 | 13:50 | 49.922
2021-01-16 | 13:50 | 49.921
2021-01-16 | 13:50 | 49.92
2021-01-16 | 13:50 | 49.921
2021-01-16 | 13:50 | 49.919
2021-01-16 | 13:50 | 49.917
2021-01-16 | 13:50 | 49.915
2021-01-16 | 13:50 | 49.914
2021-01-16 | 13:50 | 49.912
2021-01-16 | 13:50 | 49.91
2021-01-16 | 13:50 | 49.907
2021-01-16 | 13:50 | 49.906
2021-01-16 | 13:50 | 49.91
2021-01-16 | 13:50 | 49.914
2021-01-16 | 13:50 | 49.917
2021-01-16 | 13:50 | 49.919
2021-01-16 | 13:50 | 49.921
2021-01-16 | 13:50 | 49.92
2021-01-16 | 13:50 | 49.915
2021-01-16 | 13:50 | 49.912
2021-01-16 | 13:50 | 49.911
2021-01-16 | 13:50 | 49.912
2021-01-16 | 13:50 | 49.911
2021-01-16 | 13:50 | 49.91
2021-01-16 | 13:50 | 49.909
2021-01-16 | 13:50 | 49.908
2021-01-16 | 13:50 | 49.904
2021-01-16 | 13:50 | 49.901
2021-01-16 | 13:50 | 49.895
2021-01-16 | 13:50 | 49.893
2021-01-16 | 13:50 | 49.888
2021-01-16 | 13:50 | 49.885
2021-01-16 | 13:50 | 49.886
2021-01-16 | 13:50 | 49.885
2021-01-16 | 13:50 | 49.884
2021-01-16 | 13:50 | 49.885
2021-01-16 | 13:50 | 49.882
2021-01-16 | 13:50 | 49.882
2021-01-16 | 13:50 | 49.878
2021-01-16 | 13:50 | 49.877
2021-01-16 | 13:50 | 49.875
2021-01-16 | 13:50 | 49.876
2021-01-16 | 13:50 | 49.874
2021-01-16 | 13:50 | 49.872
2021-01-16 | 13:50 | 49.87
2021-01-16 | 13:50 | 49.868
2021-01-16 | 13:51 | 49.868
2021-01-16 | 13:51 | 49.864
2021-01-16 | 13:51 | 49.862
2021-01-16 | 13:51 | 49.858
2021-01-16 | 13:51 | 49.853
2021-01-16 | 13:51 | 49.853
2021-01-16 | 13:51 | 49.85
2021-01-16 | 13:51 | 49.853
2021-01-16 | 13:51 | 49.853
2021-01-16 | 13:51 | 49.855
2021-01-16 | 13:51 | 49.855
2021-01-16 | 13:51 | 49.853
2021-01-16 | 13:51 | 49.85
2021-01-16 | 13:51 | 49.851
2021-01-16 | 13:51 | 49.851
2021-01-16 | 13:51 | 49.852
2021-01-16 | 13:51 | 49.851
2021-01-16 | 13:51 | 49.851
2021-01-16 | 13:51 | 49.852
2021-01-16 | 13:51 | 49.853
2021-01-16 | 13:51 | 49.853
2021-01-16 | 13:51 | 49.852
2021-01-16 | 13:51 | 49.85
2021-01-16 | 13:51 | 49.847
2021-01-16 | 13:51 | 49.845
2021-01-16 | 13:51 | 49.845
2021-01-16 | 13:51 | 49.843
2021-01-16 | 13:51 | 49.843
2021-01-16 | 13:51 | 49.838
2021-01-16 | 13:51 | 49.84
2021-01-16 | 13:51 | 49.842
2021-01-16 | 13:51 | 49.844
2021-01-16 | 13:51 | 49.85
2021-01-16 | 13:51 | 49.855
2021-01-16 | 13:51 | 49.86
2021-01-16 | 13:51 | 49.866
2021-01-16 | 13:51 | 49.87
2021-01-16 | 13:51 | 49.874
2021-01-16 | 13:51 | 49.876
2021-01-16 | 13:51 | 49.88
2021-01-16 | 13:51 | 49.881
2021-01-16 | 13:51 | 49.884
2021-01-16 | 13:51 | 49.886
2021-01-16 | 13:51 | 49.886
2021-01-16 | 13:51 | 49.888
2021-01-16 | 13:51 | 49.891
2021-01-16 | 13:51 | 49.892
2021-01-16 | 13:51 | 49.893
2021-01-16 | 13:51 | 49.893
2021-01-16 | 13:51 | 49.897
2021-01-16 | 13:51 | 49.896
2021-01-16 | 13:51 | 49.896
2021-01-16 | 13:51 | 49.896
2021-01-16 | 13:51 | 49.896
2021-01-16 | 13:51 | 49.893
2021-01-16 | 13:51 | 49.894
2021-01-16 | 13:51 | 49.891
2021-01-16 | 13:51 | 49.892
2021-01-16 | 13:51 | 49.895
2021-01-16 | 13:52 | 49.895
2021-01-16 | 13:52 | 49.895
2021-01-16 | 13:52 | 49.897
2021-01-16 | 13:52 | 49.898
2021-01-16 | 13:52 | 49.897
2021-01-16 | 13:52 | 49.897
2021-01-16 | 13:52 | 49.897
2021-01-16 | 13:52 | 49.895
2021-01-16 | 13:52 | 49.894
2021-01-16 | 13:52 | 49.894
2021-01-16 | 13:52 | 49.895
2021-01-16 | 13:52 | 49.893
2021-01-16 | 13:52 | 49.893
2021-01-16 | 13:52 | 49.892
2021-01-16 | 13:52 | 49.892
2021-01-16 | 13:52 | 49.891
2021-01-16 | 13:52 | 49.89
2021-01-16 | 13:52 | 49.891
2021-01-16 | 13:52 | 49.893
2021-01-16 | 13:52 | 49.896
2021-01-16 | 13:52 | 49.9
2021-01-16 | 13:52 | 49.904
2021-01-16 | 13:52 | 49.907
2021-01-16 | 13:52 | 49.912
2021-01-16 | 13:52 | 49.915
2021-01-16 | 13:52 | 49.917
2021-01-16 | 13:52 | 49.917
2021-01-16 | 13:52 | 49.92
2021-01-16 | 13:52 | 49.923
2021-01-16 | 13:52 | 49.926
2021-01-16 | 13:52 | 49.928
2021-01-16 | 13:52 | 49.928
2021-01-16 | 13:52 | 49.926
2021-01-16 | 13:52 | 49.923
2021-01-16 | 13:52 | 49.923
2021-01-16 | 13:52 | 49.921
2021-01-16 | 13:52 | 49.922
2021-01-16 | 13:52 | 49.92
2021-01-16 | 13:52 | 49.919
2021-01-16 | 13:52 | 49.92
2021-01-16 | 13:52 | 49.917
2021-01-16 | 13:52 | 49.918
2021-01-16 | 13:52 | 49.916
2021-01-16 | 13:52 | 49.914
2021-01-16 | 13:52 | 49.913
2021-01-16 | 13:52 | 49.913
2021-01-16 | 13:52 | 49.914
2021-01-16 | 13:52 | 49.914
2021-01-16 | 13:52 | 49.915
2021-01-16 | 13:52 | 49.917
2021-01-16 | 13:52 | 49.92
2021-01-16 | 13:52 | 49.924
2021-01-16 | 13:52 | 49.925
2021-01-16 | 13:52 | 49.929
2021-01-16 | 13:52 | 49.933
2021-01-16 | 13:52 | 49.937
2021-01-16 | 13:52 | 49.942
2021-01-16 | 13:52 | 49.946
2021-01-16 | 13:52 | 49.947
2021-01-16 | 13:52 | 49.947
2021-01-16 | 13:52 | 49.948
2021-01-16 | 13:53 | 49.948
2021-01-16 | 13:53 | 49.951
2021-01-16 | 13:53 | 49.953
2021-01-16 | 13:53 | 49.954
2021-01-16 | 13:53 | 49.955
2021-01-16 | 13:53 | 49.955
2021-01-16 | 13:53 | 49.954
2021-01-16 | 13:53 | 49.954
2021-01-16 | 13:53 | 49.952
2021-01-16 | 13:53 | 49.951
2021-01-16 | 13:53 | 49.952
2021-01-16 | 13:53 | 49.95
2021-01-16 | 13:53 | 49.95
2021-01-16 | 13:53 | 49.949
2021-01-16 | 13:53 | 49.947
2021-01-16 | 13:53 | 49.946
2021-01-16 | 13:53 | 49.944
2021-01-16 | 13:53 | 49.944
2021-01-16 | 13:53 | 49.944
2021-01-16 | 13:53 | 49.944
2021-01-16 | 13:53 | 49.941
2021-01-16 | 13:53 | 49.94
2021-01-16 | 13:53 | 49.94
2021-01-16 | 13:53 | 49.94
2021-01-16 | 13:53 | 49.94
2021-01-16 | 13:53 | 49.939
2021-01-16 | 13:53 | 49.938
2021-01-16 | 13:53 | 49.937
2021-01-16 | 13:53 | 49.938
2021-01-16 | 13:53 | 49.937
2021-01-16 | 13:53 | 49.935
2021-01-16 | 13:53 | 49.933
2021-01-16 | 13:53 | 49.934
2021-01-16 | 13:53 | 49.937
2021-01-16 | 13:53 | 49.938
2021-01-16 | 13:53 | 49.939
2021-01-16 | 13:53 | 49.938
2021-01-16 | 13:53 | 49.938
2021-01-16 | 13:53 | 49.938
2021-01-16 | 13:53 | 49.94
2021-01-16 | 13:53 | 49.941
2021-01-16 | 13:53 | 49.939
2021-01-16 | 13:53 | 49.939
2021-01-16 | 13:53 | 49.94
2021-01-16 | 13:53 | 49.94
2021-01-16 | 13:53 | 49.942
2021-01-16 | 13:53 | 49.941
2021-01-16 | 13:53 | 49.941
2021-01-16 | 13:53 | 49.94
2021-01-16 | 13:53 | 49.94
2021-01-16 | 13:53 | 49.94
2021-01-16 | 13:53 | 49.939
2021-01-16 | 13:53 | 49.938
2021-01-16 | 13:53 | 49.938
2021-01-16 | 13:53 | 49.936
2021-01-16 | 13:53 | 49.937
2021-01-16 | 13:53 | 49.938
2021-01-16 | 13:53 | 49.939
2021-01-16 | 13:53 | 49.94
2021-01-16 | 13:54 | 49.94
2021-01-16 | 13:54 | 49.938
2021-01-16 | 13:54 | 49.938
2021-01-16 | 13:54 | 49.935
2021-01-16 | 13:54 | 49.933
2021-01-16 | 13:54 | 49.931
2021-01-16 | 13:54 | 49.93
2021-01-16 | 13:54 | 49.928
2021-01-16 | 13:54 | 49.928
2021-01-16 | 13:54 | 49.929
2021-01-16 | 13:54 | 49.929
2021-01-16 | 13:54 | 49.931
2021-01-16 | 13:54 | 49.93
2021-01-16 | 13:54 | 49.929
2021-01-16 | 13:54 | 49.929
2021-01-16 | 13:54 | 49.93
2021-01-16 | 13:54 | 49.93
2021-01-16 | 13:54 | 49.929
2021-01-16 | 13:54 | 49.929
2021-01-16 | 13:54 | 49.929
2021-01-16 | 13:54 | 49.929
2021-01-16 | 13:54 | 49.928
2021-01-16 | 13:54 | 49.929
2021-01-16 | 13:54 | 49.927
2021-01-16 | 13:54 | 49.927
2021-01-16 | 13:54 | 49.926
2021-01-16 | 13:54 | 49.929
2021-01-16 | 13:54 | 49.931
2021-01-16 | 13:54 | 49.933
2021-01-16 | 13:54 | 49.933
2021-01-16 | 13:54 | 49.932
2021-01-16 | 13:54 | 49.934
2021-01-16 | 13:54 | 49.937
2021-01-16 | 13:54 | 49.939
2021-01-16 | 13:54 | 49.938
2021-01-16 | 13:54 | 49.937
2021-01-16 | 13:54 | 49.936
2021-01-16 | 13:54 | 49.938
2021-01-16 | 13:54 | 49.938
2021-01-16 | 13:54 | 49.936
2021-01-16 | 13:54 | 49.936
2021-01-16 | 13:54 | 49.936
2021-01-16 | 13:54 | 49.937
2021-01-16 | 13:54 | 49.94
2021-01-16 | 13:54 | 49.942
2021-01-16 | 13:54 | 49.943
2021-01-16 | 13:54 | 49.944
2021-01-16 | 13:54 | 49.945
2021-01-16 | 13:54 | 49.944
2021-01-16 | 13:54 | 49.942
2021-01-16 | 13:54 | 49.941
2021-01-16 | 13:54 | 49.941
2021-01-16 | 13:54 | 49.941
2021-01-16 | 13:54 | 49.941
2021-01-16 | 13:54 | 49.941
2021-01-16 | 13:54 | 49.943
2021-01-16 | 13:54 | 49.944
2021-01-16 | 13:54 | 49.944
2021-01-16 | 13:54 | 49.944
2021-01-16 | 13:54 | 49.943
2021-01-16 | 13:54 | 49.944
2021-01-16 | 13:55 | 49.949
2021-01-16 | 13:55 | 49.953
2021-01-16 | 13:55 | 49.955
2021-01-16 | 13:55 | 49.955
2021-01-16 | 13:55 | 49.954
2021-01-16 | 13:55 | 49.953
2021-01-16 | 13:55 | 49.954
2021-01-16 | 13:55 | 49.955
2021-01-16 | 13:55 | 49.956
2021-01-16 | 13:55 | 49.957
2021-01-16 | 13:55 | 49.956
2021-01-16 | 13:55 | 49.955
2021-01-16 | 13:55 | 49.953
2021-01-16 | 13:55 | 49.953
2021-01-16 | 13:55 | 49.951
2021-01-16 | 13:55 | 49.95
2021-01-16 | 13:55 | 49.95
2021-01-16 | 13:55 | 49.95
2021-01-16 | 13:55 | 49.947
2021-01-16 | 13:55 | 49.946
2021-01-16 | 13:55 | 49.946
2021-01-16 | 13:55 | 49.947
2021-01-16 | 13:55 | 49.949
2021-01-16 | 13:55 | 49.95
2021-01-16 | 13:55 | 49.949
2021-01-16 | 13:55 | 49.947
2021-01-16 | 13:55 | 49.948
2021-01-16 | 13:55 | 49.949
2021-01-16 | 13:55 | 49.951
2021-01-16 | 13:55 | 49.953
2021-01-16 | 13:55 | 49.952
2021-01-16 | 13:55 | 49.948
2021-01-16 | 13:55 | 49.946
2021-01-16 | 13:55 | 49.944
2021-01-16 | 13:55 | 49.943
2021-01-16 | 13:55 | 49.941
2021-01-16 | 13:55 | 49.942
2021-01-16 | 13:55 | 49.941
2021-01-16 | 13:55 | 49.941
2021-01-16 | 13:55 | 49.942
2021-01-16 | 13:55 | 49.941
2021-01-16 | 13:55 | 49.94
2021-01-16 | 13:55 | 49.939
2021-01-16 | 13:55 | 49.939
2021-01-16 | 13:55 | 49.938
2021-01-16 | 13:55 | 49.938
2021-01-16 | 13:55 | 49.94
2021-01-16 | 13:55 | 49.941
2021-01-16 | 13:55 | 49.943
2021-01-16 | 13:55 | 49.945
2021-01-16 | 13:55 | 49.944
2021-01-16 | 13:55 | 49.943
2021-01-16 | 13:55 | 49.942
2021-01-16 | 13:55 | 49.943
2021-01-16 | 13:55 | 49.945
2021-01-16 | 13:55 | 49.945
2021-01-16 | 13:55 | 49.943
2021-01-16 | 13:55 | 49.94
2021-01-16 | 13:55 | 49.939
2021-01-16 | 13:56 | 49.936
2021-01-16 | 13:56 | 49.934
2021-01-16 | 13:56 | 49.933
2021-01-16 | 13:56 | 49.934
2021-01-16 | 13:56 | 49.935
2021-01-16 | 13:56 | 49.935
2021-01-16 | 13:56 | 49.937
2021-01-16 | 13:56 | 49.938
2021-01-16 | 13:56 | 49.94
2021-01-16 | 13:56 | 49.943
2021-01-16 | 13:56 | 49.944
2021-01-16 | 13:56 | 49.944
2021-01-16 | 13:56 | 49.944
2021-01-16 | 13:56 | 49.943
2021-01-16 | 13:56 | 49.941
2021-01-16 | 13:56 | 49.94
2021-01-16 | 13:56 | 49.939
2021-01-16 | 13:56 | 49.939
2021-01-16 | 13:56 | 49.942
2021-01-16 | 13:56 | 49.944
2021-01-16 | 13:56 | 49.943
2021-01-16 | 13:56 | 49.944
2021-01-16 | 13:56 | 49.944
2021-01-16 | 13:56 | 49.946
2021-01-16 | 13:56 | 49.946
2021-01-16 | 13:56 | 49.943
2021-01-16 | 13:56 | 49.941
2021-01-16 | 13:56 | 49.941
2021-01-16 | 13:56 | 49.942
2021-01-16 | 13:56 | 49.945
2021-01-16 | 13:56 | 49.945
2021-01-16 | 13:56 | 49.945
2021-01-16 | 13:56 | 49.946
2021-01-16 | 13:56 | 49.947
2021-01-16 | 13:56 | 49.949
2021-01-16 | 13:56 | 49.949
2021-01-16 | 13:56 | 49.95
2021-01-16 | 13:56 | 49.954
2021-01-16 | 13:56 | 49.957
2021-01-16 | 13:56 | 49.957
2021-01-16 | 13:56 | 49.957
2021-01-16 | 13:56 | 49.958
2021-01-16 | 13:56 | 49.959
2021-01-16 | 13:56 | 49.958
2021-01-16 | 13:56 | 49.956
2021-01-16 | 13:56 | 49.955
2021-01-16 | 13:56 | 49.955
2021-01-16 | 13:56 | 49.955
2021-01-16 | 13:56 | 49.957
2021-01-16 | 13:56 | 49.956
2021-01-16 | 13:56 | 49.959
2021-01-16 | 13:56 | 49.96
2021-01-16 | 13:56 | 49.958
2021-01-16 | 13:56 | 49.957
2021-01-16 | 13:56 | 49.952
2021-01-16 | 13:56 | 49.951
2021-01-16 | 13:56 | 49.949
2021-01-16 | 13:56 | 49.948
2021-01-16 | 13:56 | 49.946
2021-01-16 | 13:56 | 49.945
2021-01-16 | 13:56 | 49.946
2021-01-16 | 13:57 | 49.946
2021-01-16 | 13:57 | 49.947
2021-01-16 | 13:57 | 49.946
2021-01-16 | 13:57 | 49.947
2021-01-16 | 13:57 | 49.95
2021-01-16 | 13:57 | 49.952
2021-01-16 | 13:57 | 49.953
2021-01-16 | 13:57 | 49.951
2021-01-16 | 13:57 | 49.954
2021-01-16 | 13:57 | 49.957
2021-01-16 | 13:57 | 49.959
2021-01-16 | 13:57 | 49.959
2021-01-16 | 13:57 | 49.96
2021-01-16 | 13:57 | 49.962
2021-01-16 | 13:57 | 49.96
2021-01-16 | 13:57 | 49.961
2021-01-16 | 13:57 | 49.958
2021-01-16 | 13:57 | 49.955
2021-01-16 | 13:57 | 49.953
2021-01-16 | 13:57 | 49.952
2021-01-16 | 13:57 | 49.949
2021-01-16 | 13:57 | 49.947
2021-01-16 | 13:57 | 49.944
2021-01-16 | 13:57 | 49.941
2021-01-16 | 13:57 | 49.94
2021-01-16 | 13:57 | 49.94
2021-01-16 | 13:57 | 49.941
2021-01-16 | 13:57 | 49.939
2021-01-16 | 13:57 | 49.939
2021-01-16 | 13:57 | 49.939
2021-01-16 | 13:57 | 49.937
2021-01-16 | 13:57 | 49.937
2021-01-16 | 13:57 | 49.937
2021-01-16 | 13:57 | 49.937
2021-01-16 | 13:57 | 49.935
2021-01-16 | 13:57 | 49.933
2021-01-16 | 13:57 | 49.932
2021-01-16 | 13:57 | 49.933
2021-01-16 | 13:57 | 49.934
2021-01-16 | 13:57 | 49.939
2021-01-16 | 13:57 | 49.942
2021-01-16 | 13:57 | 49.942
2021-01-16 | 13:57 | 49.942
2021-01-16 | 13:57 | 49.942
2021-01-16 | 13:57 | 49.941
2021-01-16 | 13:57 | 49.943
2021-01-16 | 13:57 | 49.942
2021-01-16 | 13:57 | 49.94
2021-01-16 | 13:57 | 49.94
2021-01-16 | 13:57 | 49.94
2021-01-16 | 13:57 | 49.94
2021-01-16 | 13:57 | 49.941
2021-01-16 | 13:57 | 49.942
2021-01-16 | 13:57 | 49.942
2021-01-16 | 13:57 | 49.942
2021-01-16 | 13:57 | 49.937
2021-01-16 | 13:57 | 49.935
2021-01-16 | 13:57 | 49.935
2021-01-16 | 13:57 | 49.935
2021-01-16 | 13:58 | 49.937
2021-01-16 | 13:58 | 49.939
2021-01-16 | 13:58 | 49.941
2021-01-16 | 13:58 | 49.941
2021-01-16 | 13:58 | 49.944
2021-01-16 | 13:58 | 49.944
2021-01-16 | 13:58 | 49.944
2021-01-16 | 13:58 | 49.945
2021-01-16 | 13:58 | 49.944
2021-01-16 | 13:58 | 49.942
2021-01-16 | 13:58 | 49.941
2021-01-16 | 13:58 | 49.941
2021-01-16 | 13:58 | 49.941
2021-01-16 | 13:58 | 49.942
2021-01-16 | 13:58 | 49.943
2021-01-16 | 13:58 | 49.944
2021-01-16 | 13:58 | 49.946
2021-01-16 | 13:58 | 49.946
2021-01-16 | 13:58 | 49.946
2021-01-16 | 13:58 | 49.945
2021-01-16 | 13:58 | 49.945
2021-01-16 | 13:58 | 49.948
2021-01-16 | 13:58 | 49.951
2021-01-16 | 13:58 | 49.952
2021-01-16 | 13:58 | 49.952
2021-01-16 | 13:58 | 49.953
2021-01-16 | 13:58 | 49.951
2021-01-16 | 13:58 | 49.952
2021-01-16 | 13:58 | 49.95
2021-01-16 | 13:58 | 49.951
2021-01-16 | 13:58 | 49.951
2021-01-16 | 13:58 | 49.95
2021-01-16 | 13:58 | 49.952
2021-01-16 | 13:58 | 49.953
2021-01-16 | 13:58 | 49.953
2021-01-16 | 13:58 | 49.951
2021-01-16 | 13:58 | 49.952
2021-01-16 | 13:58 | 49.952
2021-01-16 | 13:58 | 49.951
2021-01-16 | 13:58 | 49.948
2021-01-16 | 13:58 | 49.949
2021-01-16 | 13:58 | 49.951
2021-01-16 | 13:58 | 49.951
2021-01-16 | 13:58 | 49.952
2021-01-16 | 13:58 | 49.951
2021-01-16 | 13:58 | 49.95
2021-01-16 | 13:58 | 49.951
2021-01-16 | 13:58 | 49.949
2021-01-16 | 13:58 | 49.947
2021-01-16 | 13:58 | 49.946
2021-01-16 | 13:58 | 49.947
2021-01-16 | 13:58 | 49.949
2021-01-16 | 13:58 | 49.95
2021-01-16 | 13:58 | 49.953
2021-01-16 | 13:58 | 49.954
2021-01-16 | 13:58 | 49.954
2021-01-16 | 13:58 | 49.953
2021-01-16 | 13:58 | 49.951
2021-01-16 | 13:58 | 49.95
2021-01-16 | 13:58 | 49.95
2021-01-16 | 13:58 | 49.953
2021-01-16 | 13:59 | 49.953
2021-01-16 | 13:59 | 49.953
2021-01-16 | 13:59 | 49.951
2021-01-16 | 13:59 | 49.948
2021-01-16 | 13:59 | 49.945
2021-01-16 | 13:59 | 49.945
2021-01-16 | 13:59 | 49.943
2021-01-16 | 13:59 | 49.94
2021-01-16 | 13:59 | 49.939
2021-01-16 | 13:59 | 49.94
2021-01-16 | 13:59 | 49.942
2021-01-16 | 13:59 | 49.941
2021-01-16 | 13:59 | 49.942
2021-01-16 | 13:59 | 49.942
2021-01-16 | 13:59 | 49.944
2021-01-16 | 13:59 | 49.946
2021-01-16 | 13:59 | 49.948
2021-01-16 | 13:59 | 49.948
2021-01-16 | 13:59 | 49.949
2021-01-16 | 13:59 | 49.948
2021-01-16 | 13:59 | 49.949
2021-01-16 | 13:59 | 49.95
2021-01-16 | 13:59 | 49.951
2021-01-16 | 13:59 | 49.952
2021-01-16 | 13:59 | 49.952
2021-01-16 | 13:59 | 49.954
2021-01-16 | 13:59 | 49.956
2021-01-16 | 13:59 | 49.956
2021-01-16 | 13:59 | 49.955
2021-01-16 | 13:59 | 49.955
2021-01-16 | 13:59 | 49.956
2021-01-16 | 13:59 | 49.955
2021-01-16 | 13:59 | 49.955
2021-01-16 | 13:59 | 49.955
2021-01-16 | 13:59 | 49.957
2021-01-16 | 13:59 | 49.958
2021-01-16 | 13:59 | 49.96
2021-01-16 | 13:59 | 49.959
2021-01-16 | 13:59 | 49.962
2021-01-16 | 13:59 | 49.963
2021-01-16 | 13:59 | 49.964
2021-01-16 | 13:59 | 49.962
2021-01-16 | 13:59 | 49.964
2021-01-16 | 13:59 | 49.965
2021-01-16 | 13:59 | 49.967
2021-01-16 | 13:59 | 49.966
2021-01-16 | 13:59 | 49.964
2021-01-16 | 13:59 | 49.961
2021-01-16 | 13:59 | 49.959
2021-01-16 | 13:59 | 49.955
2021-01-16 | 13:59 | 49.95
2021-01-16 | 13:59 | 49.948
2021-01-16 | 13:59 | 49.945
2021-01-16 | 13:59 | 49.941
2021-01-16 | 13:59 | 49.938
2021-01-16 | 13:59 | 49.936
2021-01-16 | 13:59 | 49.936
2021-01-16 | 13:59 | 49.936
2021-01-16 | 13:59 | 49.934
2021-01-16 | 14:00 | 49.932
2021-01-16 | 14:00 | 49.93
2021-01-16 | 14:00 | 49.928
2021-01-16 | 14:00 | 49.925
2021-01-16 | 14:00 | 49.922
2021-01-16 | 14:00 | 49.92
2021-01-16 | 14:00 | 49.92
2021-01-16 | 14:00 | 49.919
2021-01-16 | 14:00 | 49.918
2021-01-16 | 14:00 | 49.918
2021-01-16 | 14:00 | 49.919
2021-01-16 | 14:00 | 49.916
2021-01-16 | 14:00 | 49.917
2021-01-16 | 14:00 | 49.917
2021-01-16 | 14:00 | 49.919
2021-01-16 | 14:00 | 49.919
2021-01-16 | 14:00 | 49.92
2021-01-16 | 14:00 | 49.923
2021-01-16 | 14:00 | 49.92
2021-01-16 | 14:00 | 49.917
2021-01-16 | 14:00 | 49.915
2021-01-16 | 14:00 | 49.91
2021-01-16 | 14:00 | 49.908
2021-01-16 | 14:00 | 49.904
2021-01-16 | 14:00 | 49.903
2021-01-16 | 14:00 | 49.899
2021-01-16 | 14:00 | 49.897
2021-01-16 | 14:00 | 49.893
2021-01-16 | 14:00 | 49.89
2021-01-16 | 14:00 | 49.89
2021-01-16 | 14:00 | 49.889
2021-01-16 | 14:00 | 49.884
2021-01-16 | 14:00 | 49.881
2021-01-16 | 14:00 | 49.876
2021-01-16 | 14:00 | 49.875
2021-01-16 | 14:00 | 49.876
2021-01-16 | 14:00 | 49.874
2021-01-16 | 14:00 | 49.873
2021-01-16 | 14:00 | 49.873
2021-01-16 | 14:00 | 49.873
2021-01-16 | 14:00 | 49.872
2021-01-16 | 14:00 | 49.87
2021-01-16 | 14:00 | 49.867
2021-01-16 | 14:00 | 49.864
2021-01-16 | 14:00 | 49.86
2021-01-16 | 14:00 | 49.859
2021-01-16 | 14:00 | 49.859
2021-01-16 | 14:00 | 49.857
2021-01-16 | 14:00 | 49.856
2021-01-16 | 14:00 | 49.856
2021-01-16 | 14:00 | 49.853
2021-01-16 | 14:00 | 49.85
2021-01-16 | 14:00 | 49.848
2021-01-16 | 14:00 | 49.844
2021-01-16 | 14:00 | 49.845
2021-01-16 | 14:00 | 49.843
2021-01-16 | 14:00 | 49.843
2021-01-16 | 14:00 | 49.844
2021-01-16 | 14:00 | 49.843
2021-01-16 | 14:00 | 49.842
2021-01-16 | 14:00 | 49.843
2021-01-16 | 14:01 | 49.841
2021-01-16 | 14:01 | 49.84
2021-01-16 | 14:01 | 49.84
2021-01-16 | 14:01 | 49.839
2021-01-16 | 14:01 | 49.84
2021-01-16 | 14:01 | 49.839
2021-01-16 | 14:01 | 49.838
2021-01-16 | 14:01 | 49.838
2021-01-16 | 14:01 | 49.839
2021-01-16 | 14:01 | 49.84
2021-01-16 | 14:01 | 49.838
2021-01-16 | 14:01 | 49.836
2021-01-16 | 14:01 | 49.836
2021-01-16 | 14:01 | 49.835
2021-01-16 | 14:01 | 49.838
2021-01-16 | 14:01 | 49.838
2021-01-16 | 14:01 | 49.836
2021-01-16 | 14:01 | 49.838
2021-01-16 | 14:01 | 49.839
2021-01-16 | 14:01 | 49.842
2021-01-16 | 14:01 | 49.842
2021-01-16 | 14:01 | 49.842
2021-01-16 | 14:01 | 49.844
2021-01-16 | 14:01 | 49.844
2021-01-16 | 14:01 | 49.847
2021-01-16 | 14:01 | 49.845
2021-01-16 | 14:01 | 49.843
2021-01-16 | 14:01 | 49.847
2021-01-16 | 14:01 | 49.848
2021-01-16 | 14:01 | 49.85
2021-01-16 | 14:01 | 49.85
2021-01-16 | 14:01 | 49.849
2021-01-16 | 14:01 | 49.846
2021-01-16 | 14:01 | 49.845
2021-01-16 | 14:01 | 49.841
2021-01-16 | 14:01 | 49.838
2021-01-16 | 14:01 | 49.835
2021-01-16 | 14:01 | 49.833
2021-01-16 | 14:01 | 49.832
2021-01-16 | 14:01 | 49.832
2021-01-16 | 14:01 | 49.83
2021-01-16 | 14:01 | 49.829
2021-01-16 | 14:01 | 49.829
2021-01-16 | 14:01 | 49.83
2021-01-16 | 14:01 | 49.83
2021-01-16 | 14:01 | 49.828
2021-01-16 | 14:01 | 49.831
2021-01-16 | 14:01 | 49.83
2021-01-16 | 14:01 | 49.831
2021-01-16 | 14:01 | 49.833
2021-01-16 | 14:01 | 49.832
2021-01-16 | 14:01 | 49.832
2021-01-16 | 14:01 | 49.832
2021-01-16 | 14:01 | 49.83
2021-01-16 | 14:01 | 49.826
2021-01-16 | 14:01 | 49.826
2021-01-16 | 14:01 | 49.822
2021-01-16 | 14:01 | 49.822
2021-01-16 | 14:01 | 49.825
2021-01-16 | 14:02 | 49.828
2021-01-16 | 14:02 | 49.832
2021-01-16 | 14:02 | 49.839
2021-01-16 | 14:02 | 49.843
2021-01-16 | 14:02 | 49.851
2021-01-16 | 14:02 | 49.857
2021-01-16 | 14:02 | 49.858
2021-01-16 | 14:02 | 49.864
2021-01-16 | 14:02 | 49.87
2021-01-16 | 14:02 | 49.872
2021-01-16 | 14:02 | 49.875
2021-01-16 | 14:02 | 49.875
2021-01-16 | 14:02 | 49.875
2021-01-16 | 14:02 | 49.874
2021-01-16 | 14:02 | 49.875
2021-01-16 | 14:02 | 49.876
2021-01-16 | 14:02 | 49.877
2021-01-16 | 14:02 | 49.878
2021-01-16 | 14:02 | 49.879
2021-01-16 | 14:02 | 49.882
2021-01-16 | 14:02 | 49.883
2021-01-16 | 14:02 | 49.886
2021-01-16 | 14:02 | 49.887
2021-01-16 | 14:02 | 49.891
2021-01-16 | 14:02 | 49.895
2021-01-16 | 14:02 | 49.895
2021-01-16 | 14:02 | 49.897
2021-01-16 | 14:02 | 49.9
2021-01-16 | 14:02 | 49.904
2021-01-16 | 14:02 | 49.906
2021-01-16 | 14:02 | 49.909
2021-01-16 | 14:02 | 49.91
2021-01-16 | 14:02 | 49.908
2021-01-16 | 14:02 | 49.906
2021-01-16 | 14:02 | 49.906
2021-01-16 | 14:02 | 49.907
2021-01-16 | 14:02 | 49.907
2021-01-16 | 14:02 | 49.908
2021-01-16 | 14:02 | 49.906
2021-01-16 | 14:02 | 49.905
2021-01-16 | 14:02 | 49.907
2021-01-16 | 14:02 | 49.912
2021-01-16 | 14:02 | 49.915
2021-01-16 | 14:02 | 49.921
2021-01-16 | 14:02 | 49.923
2021-01-16 | 14:02 | 49.925
2021-01-16 | 14:02 | 49.926
2021-01-16 | 14:02 | 49.928
2021-01-16 | 14:02 | 49.931
2021-01-16 | 14:02 | 49.933
2021-01-16 | 14:02 | 49.933
2021-01-16 | 14:02 | 49.932
2021-01-16 | 14:02 | 49.933
2021-01-16 | 14:02 | 49.933
2021-01-16 | 14:02 | 49.936
2021-01-16 | 14:02 | 49.939
2021-01-16 | 14:02 | 49.942
2021-01-16 | 14:02 | 49.945
2021-01-16 | 14:02 | 49.944
2021-01-16 | 14:02 | 49.948
2021-01-16 | 14:02 | 49.949
2021-01-16 | 14:03 | 49.948
2021-01-16 | 14:03 | 49.948
2021-01-16 | 14:03 | 49.948
2021-01-16 | 14:03 | 49.947
2021-01-16 | 14:03 | 49.946
2021-01-16 | 14:03 | 49.945
2021-01-16 | 14:03 | 49.943
2021-01-16 | 14:03 | 49.942
2021-01-16 | 14:03 | 49.942
2021-01-16 | 14:03 | 49.943
2021-01-16 | 14:03 | 49.944
2021-01-16 | 14:03 | 49.949
2021-01-16 | 14:03 | 49.952
2021-01-16 | 14:03 | 49.955
2021-01-16 | 14:03 | 49.96
2021-01-16 | 14:03 | 49.962
2021-01-16 | 14:03 | 49.965
2021-01-16 | 14:03 | 49.965
2021-01-16 | 14:03 | 49.969
2021-01-16 | 14:03 | 49.97
2021-01-16 | 14:03 | 49.969
2021-01-16 | 14:03 | 49.97
2021-01-16 | 14:03 | 49.971
2021-01-16 | 14:03 | 49.972
2021-01-16 | 14:03 | 49.973
2021-01-16 | 14:03 | 49.975
2021-01-16 | 14:03 | 49.976
2021-01-16 | 14:03 | 49.976
2021-01-16 | 14:03 | 49.977
2021-01-16 | 14:03 | 49.979
2021-01-16 | 14:03 | 49.979
2021-01-16 | 14:03 | 49.979
2021-01-16 | 14:03 | 49.98
2021-01-16 | 14:03 | 49.979
2021-01-16 | 14:03 | 49.981
2021-01-16 | 14:03 | 49.982
2021-01-16 | 14:03 | 49.982
2021-01-16 | 14:03 | 49.982
2021-01-16 | 14:03 | 49.983
2021-01-16 | 14:03 | 49.982
2021-01-16 | 14:03 | 49.983
2021-01-16 | 14:03 | 49.985
2021-01-16 | 14:03 | 49.986
2021-01-16 | 14:03 | 49.989
2021-01-16 | 14:03 | 49.989
2021-01-16 | 14:03 | 49.989
2021-01-16 | 14:03 | 49.991
2021-01-16 | 14:03 | 49.989
2021-01-16 | 14:03 | 49.991
2021-01-16 | 14:03 | 49.991
2021-01-16 | 14:03 | 49.99
2021-01-16 | 14:03 | 49.991
2021-01-16 | 14:03 | 49.992
2021-01-16 | 14:03 | 49.991
2021-01-16 | 14:03 | 49.992
2021-01-16 | 14:03 | 49.99
2021-01-16 | 14:03 | 49.988
2021-01-16 | 14:03 | 49.986
2021-01-16 | 14:03 | 49.983
2021-01-16 | 14:04 | 49.982
2021-01-16 | 14:04 | 49.979
2021-01-16 | 14:04 | 49.979
2021-01-16 | 14:04 | 49.981
2021-01-16 | 14:04 | 49.981
2021-01-16 | 14:04 | 49.983
2021-01-16 | 14:04 | 49.987
2021-01-16 | 14:04 | 49.987
2021-01-16 | 14:04 | 49.991
2021-01-16 | 14:04 | 49.998
2021-01-16 | 14:04 | 50.003
2021-01-16 | 14:04 | 50.009
2021-01-16 | 14:04 | 50.014
2021-01-16 | 14:04 | 50.018
2021-01-16 | 14:04 | 50.019
2021-01-16 | 14:04 | 50.021
2021-01-16 | 14:04 | 50.021
2021-01-16 | 14:04 | 50.024
2021-01-16 | 14:04 | 50.021
2021-01-16 | 14:04 | 50.022
2021-01-16 | 14:04 | 50.021
2021-01-16 | 14:04 | 50.02
2021-01-16 | 14:04 | 50.019
2021-01-16 | 14:04 | 50.019
2021-01-16 | 14:04 | 50.02
2021-01-16 | 14:04 | 50.021
2021-01-16 | 14:04 | 50.024
2021-01-16 | 14:04 | 50.026
2021-01-16 | 14:04 | 50.032
2021-01-16 | 14:04 | 50.036
2021-01-16 | 14:04 | 50.04
2021-01-16 | 14:04 | 50.042
2021-01-16 | 14:04 | 50.041
2021-01-16 | 14:04 | 50.041
2021-01-16 | 14:04 | 50.039
2021-01-16 | 14:04 | 50.038
2021-01-16 | 14:04 | 50.038
2021-01-16 | 14:04 | 50.036
2021-01-16 | 14:04 | 50.035
2021-01-16 | 14:04 | 50.033
2021-01-16 | 14:04 | 50.03
2021-01-16 | 14:04 | 50.028
2021-01-16 | 14:04 | 50.027
2021-01-16 | 14:04 | 50.026
2021-01-16 | 14:04 | 50.025
2021-01-16 | 14:04 | 50.028
2021-01-16 | 14:04 | 50.026
2021-01-16 | 14:04 | 50.028
2021-01-16 | 14:04 | 50.029
2021-01-16 | 14:04 | 50.028
2021-01-16 | 14:04 | 50.029
2021-01-16 | 14:04 | 50.029
2021-01-16 | 14:04 | 50.028
2021-01-16 | 14:04 | 50.029
2021-01-16 | 14:04 | 50.031
2021-01-16 | 14:04 | 50.03
2021-01-16 | 14:04 | 50.031
2021-01-16 | 14:04 | 50.031
2021-01-16 | 14:04 | 50.031
2021-01-16 | 14:04 | 50.032
2021-01-16 | 14:04 | 50.032
2021-01-16 | 14:05 | 50.03
2021-01-16 | 14:05 | 50.029
2021-01-16 | 14:05 | 50.028
2021-01-16 | 14:05 | 50.029
2021-01-16 | 14:05 | 50.03
2021-01-16 | 14:05 | 50.027
2021-01-16 | 14:05 | 50.027
2021-01-16 | 14:05 | 50.028
2021-01-16 | 14:05 | 50.028
2021-01-16 | 14:05 | 50.028
2021-01-16 | 14:05 | 50.027
2021-01-16 | 14:05 | 50.029
2021-01-16 | 14:05 | 50.027
2021-01-16 | 14:05 | 50.026
2021-01-16 | 14:05 | 50.027
2021-01-16 | 14:05 | 50.026
2021-01-16 | 14:05 | 50.025
2021-01-16 | 14:05 | 50.023
2021-01-16 | 14:05 | 50.023
2021-01-16 | 14:05 | 50.021
2021-01-16 | 14:05 | 50.018
2021-01-16 | 14:05 | 50.017
2021-01-16 | 14:05 | 50.019
2021-01-16 | 14:05 | 50.022
2021-01-16 | 14:05 | 50.023
2021-01-16 | 14:05 | 50.025
2021-01-16 | 14:05 | 50.025
2021-01-16 | 14:05 | 50.025
2021-01-16 | 14:05 | 50.025
2021-01-16 | 14:05 | 50.025
2021-01-16 | 14:05 | 50.023
2021-01-16 | 14:05 | 50.017
2021-01-16 | 14:05 | 50.013
2021-01-16 | 14:05 | 50.009
2021-01-16 | 14:05 | 50.01
2021-01-16 | 14:05 | 50.01
2021-01-16 | 14:05 | 50.01
2021-01-16 | 14:05 | 50.008
2021-01-16 | 14:05 | 50.009
2021-01-16 | 14:05 | 50.008
2021-01-16 | 14:05 | 50.007
2021-01-16 | 14:05 | 50.009
2021-01-16 | 14:05 | 50.01
2021-01-16 | 14:05 | 50.009
2021-01-16 | 14:05 | 50.009
2021-01-16 | 14:05 | 50.008
2021-01-16 | 14:05 | 50.008
2021-01-16 | 14:05 | 50.011
2021-01-16 | 14:05 | 50.011
2021-01-16 | 14:05 | 50.011
2021-01-16 | 14:05 | 50.01
2021-01-16 | 14:05 | 50.008
2021-01-16 | 14:05 | 50.006
2021-01-16 | 14:05 | 50.004
2021-01-16 | 14:05 | 50.001
2021-01-16 | 14:05 | 49.998
2021-01-16 | 14:05 | 49.999
2021-01-16 | 14:05 | 49.998
2021-01-16 | 14:05 | 49.996
2021-01-16 | 14:06 | 49.997
2021-01-16 | 14:06 | 49.998
2021-01-16 | 14:06 | 49.998
2021-01-16 | 14:06 | 50
2021-01-16 | 14:06 | 50.001
2021-01-16 | 14:06 | 50.004
2021-01-16 | 14:06 | 50.008
2021-01-16 | 14:06 | 50.009
2021-01-16 | 14:06 | 50.012
2021-01-16 | 14:06 | 50.016
2021-01-16 | 14:06 | 50.018
2021-01-16 | 14:06 | 50.022
2021-01-16 | 14:06 | 50.023
2021-01-16 | 14:06 | 50.025
2021-01-16 | 14:06 | 50.025
2021-01-16 | 14:06 | 50.024
2021-01-16 | 14:06 | 50.024
2021-01-16 | 14:06 | 50.021
2021-01-16 | 14:06 | 50.02
2021-01-16 | 14:06 | 50.02
2021-01-16 | 14:06 | 50.019
2021-01-16 | 14:06 | 50.021
2021-01-16 | 14:06 | 50.021
2021-01-16 | 14:06 | 50.02
2021-01-16 | 14:06 | 50.019
2021-01-16 | 14:06 | 50.018
2021-01-16 | 14:06 | 50.017
2021-01-16 | 14:06 | 50.018
2021-01-16 | 14:06 | 50.016
2021-01-16 | 14:06 | 50.014
2021-01-16 | 14:06 | 50.013
2021-01-16 | 14:06 | 50.009
2021-01-16 | 14:06 | 50.008
2021-01-16 | 14:06 | 50.005
2021-01-16 | 14:06 | 50.003
2021-01-16 | 14:06 | 50.003
2021-01-16 | 14:06 | 50
2021-01-16 | 14:06 | 49.998
2021-01-16 | 14:06 | 49.997
2021-01-16 | 14:06 | 49.997
2021-01-16 | 14:06 | 49.998
2021-01-16 | 14:06 | 49.999
2021-01-16 | 14:06 | 50
2021-01-16 | 14:06 | 50.004
2021-01-16 | 14:06 | 50.008
2021-01-16 | 14:06 | 50.009
2021-01-16 | 14:06 | 50.011
2021-01-16 | 14:06 | 50.013
2021-01-16 | 14:06 | 50.014
2021-01-16 | 14:06 | 50.015
2021-01-16 | 14:06 | 50.017
2021-01-16 | 14:06 | 50.017
2021-01-16 | 14:06 | 50.015
2021-01-16 | 14:06 | 50.016
2021-01-16 | 14:06 | 50.013
2021-01-16 | 14:06 | 50.011
2021-01-16 | 14:06 | 50.01
2021-01-16 | 14:06 | 50.008
2021-01-16 | 14:06 | 50.003
2021-01-16 | 14:06 | 49.998
2021-01-16 | 14:06 | 49.991
2021-01-16 | 14:07 | 49.984
2021-01-16 | 14:07 | 49.975
2021-01-16 | 14:07 | 49.969
2021-01-16 | 14:07 | 49.961
2021-01-16 | 14:07 | 49.955
2021-01-16 | 14:07 | 49.947
2021-01-16 | 14:07 | 49.943
2021-01-16 | 14:07 | 49.939
2021-01-16 | 14:07 | 49.934
2021-01-16 | 14:07 | 49.932
2021-01-16 | 14:07 | 49.931
2021-01-16 | 14:07 | 49.932
2021-01-16 | 14:07 | 49.934
2021-01-16 | 14:07 | 49.936
2021-01-16 | 14:07 | 49.939
2021-01-16 | 14:07 | 49.941
2021-01-16 | 14:07 | 49.941
2021-01-16 | 14:07 | 49.943
2021-01-16 | 14:07 | 49.946
2021-01-16 | 14:07 | 49.949
2021-01-16 | 14:07 | 49.95
2021-01-16 | 14:07 | 49.951
2021-01-16 | 14:07 | 49.95
2021-01-16 | 14:07 | 49.948
2021-01-16 | 14:07 | 49.947
2021-01-16 | 14:07 | 49.946
2021-01-16 | 14:07 | 49.941
2021-01-16 | 14:07 | 49.94
2021-01-16 | 14:07 | 49.94
2021-01-16 | 14:07 | 49.94
2021-01-16 | 14:07 | 49.939
2021-01-16 | 14:07 | 49.938
2021-01-16 | 14:07 | 49.936
2021-01-16 | 14:07 | 49.936
2021-01-16 | 14:07 | 49.936
2021-01-16 | 14:07 | 49.935
2021-01-16 | 14:07 | 49.936
2021-01-16 | 14:07 | 49.935
2021-01-16 | 14:07 | 49.936
2021-01-16 | 14:07 | 49.938
2021-01-16 | 14:07 | 49.939
2021-01-16 | 14:07 | 49.94
2021-01-16 | 14:07 | 49.94
2021-01-16 | 14:07 | 49.945
2021-01-16 | 14:07 | 49.945
2021-01-16 | 14:07 | 49.945
2021-01-16 | 14:07 | 49.947
2021-01-16 | 14:07 | 49.949
2021-01-16 | 14:07 | 49.953
2021-01-16 | 14:07 | 49.957
2021-01-16 | 14:07 | 49.957
2021-01-16 | 14:07 | 49.958
2021-01-16 | 14:07 | 49.958
2021-01-16 | 14:07 | 49.957
2021-01-16 | 14:07 | 49.957
2021-01-16 | 14:07 | 49.958
2021-01-16 | 14:07 | 49.956
2021-01-16 | 14:07 | 49.955
2021-01-16 | 14:07 | 49.955
2021-01-16 | 14:08 | 49.956
2021-01-16 | 14:08 | 49.958
2021-01-16 | 14:08 | 49.959
2021-01-16 | 14:08 | 49.962
2021-01-16 | 14:08 | 49.963
2021-01-16 | 14:08 | 49.962
2021-01-16 | 14:08 | 49.962
2021-01-16 | 14:08 | 49.962
2021-01-16 | 14:08 | 49.962
2021-01-16 | 14:08 | 49.963
2021-01-16 | 14:08 | 49.965
2021-01-16 | 14:08 | 49.966
2021-01-16 | 14:08 | 49.964
2021-01-16 | 14:08 | 49.963
2021-01-16 | 14:08 | 49.964
2021-01-16 | 14:08 | 49.965
2021-01-16 | 14:08 | 49.967
2021-01-16 | 14:08 | 49.97
2021-01-16 | 14:08 | 49.975
2021-01-16 | 14:08 | 49.977
2021-01-16 | 14:08 | 49.976
2021-01-16 | 14:08 | 49.977
2021-01-16 | 14:08 | 49.978
2021-01-16 | 14:08 | 49.98
2021-01-16 | 14:08 | 49.981
2021-01-16 | 14:08 | 49.982
2021-01-16 | 14:08 | 49.984
2021-01-16 | 14:08 | 49.984
2021-01-16 | 14:08 | 49.984
2021-01-16 | 14:08 | 49.982
2021-01-16 | 14:08 | 49.983
2021-01-16 | 14:08 | 49.985
2021-01-16 | 14:08 | 49.986
2021-01-16 | 14:08 | 49.985
2021-01-16 | 14:08 | 49.983
2021-01-16 | 14:08 | 49.983
2021-01-16 | 14:08 | 49.984
2021-01-16 | 14:08 | 49.983
2021-01-16 | 14:08 | 49.981
2021-01-16 | 14:08 | 49.98
2021-01-16 | 14:08 | 49.98
2021-01-16 | 14:08 | 49.978
2021-01-16 | 14:08 | 49.976
2021-01-16 | 14:08 | 49.977
2021-01-16 | 14:08 | 49.977
2021-01-16 | 14:08 | 49.974
2021-01-16 | 14:08 | 49.973
2021-01-16 | 14:08 | 49.972
2021-01-16 | 14:08 | 49.974
2021-01-16 | 14:08 | 49.974
2021-01-16 | 14:08 | 49.974
2021-01-16 | 14:08 | 49.971
2021-01-16 | 14:08 | 49.969
2021-01-16 | 14:08 | 49.97
2021-01-16 | 14:08 | 49.971
2021-01-16 | 14:08 | 49.971
2021-01-16 | 14:08 | 49.972
2021-01-16 | 14:08 | 49.973
2021-01-16 | 14:08 | 49.976
2021-01-16 | 14:08 | 49.977
2021-01-16 | 14:09 | 49.975
2021-01-16 | 14:09 | 49.974
2021-01-16 | 14:09 | 49.973
2021-01-16 | 14:09 | 49.972
2021-01-16 | 14:09 | 49.974
2021-01-16 | 14:09 | 49.975
2021-01-16 | 14:09 | 49.976
2021-01-16 | 14:09 | 49.976
2021-01-16 | 14:09 | 49.978
2021-01-16 | 14:09 | 49.979
2021-01-16 | 14:09 | 49.979
2021-01-16 | 14:09 | 49.981
2021-01-16 | 14:09 | 49.983
2021-01-16 | 14:09 | 49.984
2021-01-16 | 14:09 | 49.985
2021-01-16 | 14:09 | 49.984
2021-01-16 | 14:09 | 49.982
2021-01-16 | 14:09 | 49.98
2021-01-16 | 14:09 | 49.979
2021-01-16 | 14:09 | 49.979
2021-01-16 | 14:09 | 49.979
2021-01-16 | 14:09 | 49.979
2021-01-16 | 14:09 | 49.98
2021-01-16 | 14:09 | 49.983
2021-01-16 | 14:09 | 49.983
2021-01-16 | 14:09 | 49.983
2021-01-16 | 14:09 | 49.983
2021-01-16 | 14:09 | 49.983
2021-01-16 | 14:09 | 49.983
2021-01-16 | 14:09 | 49.983
2021-01-16 | 14:09 | 49.983
2021-01-16 | 14:09 | 49.982
2021-01-16 | 14:09 | 49.982
2021-01-16 | 14:09 | 49.982
2021-01-16 | 14:09 | 49.981
2021-01-16 | 14:09 | 49.98
2021-01-16 | 14:09 | 49.984
2021-01-16 | 14:09 | 49.986
2021-01-16 | 14:09 | 49.988
2021-01-16 | 14:09 | 49.987
2021-01-16 | 14:09 | 49.988
2021-01-16 | 14:09 | 49.99
2021-01-16 | 14:09 | 49.992
2021-01-16 | 14:09 | 49.994
2021-01-16 | 14:09 | 49.995
2021-01-16 | 14:09 | 49.999
2021-01-16 | 14:09 | 49.999
2021-01-16 | 14:09 | 49.998
2021-01-16 | 14:09 | 49.996
2021-01-16 | 14:09 | 49.997
2021-01-16 | 14:09 | 49.994
2021-01-16 | 14:09 | 49.99
2021-01-16 | 14:09 | 49.982
2021-01-16 | 14:09 | 49.978
2021-01-16 | 14:09 | 49.976
2021-01-16 | 14:09 | 49.972
2021-01-16 | 14:09 | 49.971
2021-01-16 | 14:09 | 49.97
2021-01-16 | 14:09 | 49.968
2021-01-16 | 14:09 | 49.966
2021-01-16 | 14:09 | 49.969
2021-01-16 | 14:10 | 49.968
2021-01-16 | 14:10 | 49.969
2021-01-16 | 14:10 | 49.967
2021-01-16 | 14:10 | 49.97
2021-01-16 | 14:10 | 49.97
2021-01-16 | 14:10 | 49.968
2021-01-16 | 14:10 | 49.968
2021-01-16 | 14:10 | 49.968
2021-01-16 | 14:10 | 49.969
2021-01-16 | 14:10 | 49.966
2021-01-16 | 14:10 | 49.966
2021-01-16 | 14:10 | 49.969
2021-01-16 | 14:10 | 49.973
2021-01-16 | 14:10 | 49.977
2021-01-16 | 14:10 | 49.982
2021-01-16 | 14:10 | 49.986
2021-01-16 | 14:10 | 49.988
2021-01-16 | 14:10 | 49.988
2021-01-16 | 14:10 | 49.989
2021-01-16 | 14:10 | 49.991
2021-01-16 | 14:10 | 49.994
2021-01-16 | 14:10 | 49.995
2021-01-16 | 14:10 | 49.992
2021-01-16 | 14:10 | 49.986
2021-01-16 | 14:10 | 49.979
2021-01-16 | 14:10 | 49.968
2021-01-16 | 14:10 | 49.957
2021-01-16 | 14:10 | 49.949
2021-01-16 | 14:10 | 49.942
2021-01-16 | 14:10 | 49.938
2021-01-16 | 14:10 | 49.933
2021-01-16 | 14:10 | 49.929
2021-01-16 | 14:10 | 49.932
2021-01-16 | 14:10 | 49.936
2021-01-16 | 14:10 | 49.938
2021-01-16 | 14:10 | 49.94
2021-01-16 | 14:10 | 49.943
2021-01-16 | 14:10 | 49.945
2021-01-16 | 14:10 | 49.946
2021-01-16 | 14:10 | 49.945
2021-01-16 | 14:10 | 49.943
2021-01-16 | 14:10 | 49.942
2021-01-16 | 14:10 | 49.939
2021-01-16 | 14:10 | 49.939
2021-01-16 | 14:10 | 49.938
2021-01-16 | 14:10 | 49.939
2021-01-16 | 14:10 | 49.939
2021-01-16 | 14:10 | 49.943
2021-01-16 | 14:10 | 49.944
2021-01-16 | 14:10 | 49.945
2021-01-16 | 14:10 | 49.947
2021-01-16 | 14:10 | 49.949
2021-01-16 | 14:10 | 49.951
2021-01-16 | 14:10 | 49.95
2021-01-16 | 14:10 | 49.949
2021-01-16 | 14:10 | 49.949
2021-01-16 | 14:10 | 49.949
2021-01-16 | 14:10 | 49.949
2021-01-16 | 14:10 | 49.948
2021-01-16 | 14:11 | 49.949
2021-01-16 | 14:11 | 49.949
2021-01-16 | 14:11 | 49.95
2021-01-16 | 14:11 | 49.949
2021-01-16 | 14:11 | 49.949
2021-01-16 | 14:11 | 49.95
2021-01-16 | 14:11 | 49.951
2021-01-16 | 14:11 | 49.953
2021-01-16 | 14:11 | 49.953
2021-01-16 | 14:11 | 49.956
2021-01-16 | 14:11 | 49.956
2021-01-16 | 14:11 | 49.957
2021-01-16 | 14:11 | 49.957
2021-01-16 | 14:11 | 49.955
2021-01-16 | 14:11 | 49.956
2021-01-16 | 14:11 | 49.956
2021-01-16 | 14:11 | 49.956
2021-01-16 | 14:11 | 49.955
2021-01-16 | 14:11 | 49.952
2021-01-16 | 14:11 | 49.953
2021-01-16 | 14:11 | 49.952
2021-01-16 | 14:11 | 49.948
2021-01-16 | 14:11 | 49.949
2021-01-16 | 14:11 | 49.952
2021-01-16 | 14:11 | 49.955
2021-01-16 | 14:11 | 49.957
2021-01-16 | 14:11 | 49.958
2021-01-16 | 14:11 | 49.961
2021-01-16 | 14:11 | 49.963
2021-01-16 | 14:11 | 49.963
2021-01-16 | 14:11 | 49.962
2021-01-16 | 14:11 | 49.959
2021-01-16 | 14:11 | 49.957
2021-01-16 | 14:11 | 49.954
2021-01-16 | 14:11 | 49.951
2021-01-16 | 14:11 | 49.948
2021-01-16 | 14:11 | 49.949
2021-01-16 | 14:11 | 49.95
2021-01-16 | 14:11 | 49.95
2021-01-16 | 14:11 | 49.951
2021-01-16 | 14:11 | 49.952
2021-01-16 | 14:11 | 49.952
2021-01-16 | 14:11 | 49.953
2021-01-16 | 14:11 | 49.954
2021-01-16 | 14:11 | 49.955
2021-01-16 | 14:11 | 49.955
2021-01-16 | 14:11 | 49.955
2021-01-16 | 14:11 | 49.953
2021-01-16 | 14:11 | 49.955
2021-01-16 | 14:11 | 49.957
2021-01-16 | 14:11 | 49.956
2021-01-16 | 14:11 | 49.959
2021-01-16 | 14:11 | 49.962
2021-01-16 | 14:11 | 49.964
2021-01-16 | 14:11 | 49.967
2021-01-16 | 14:11 | 49.969
2021-01-16 | 14:11 | 49.967
2021-01-16 | 14:11 | 49.967
2021-01-16 | 14:11 | 49.966
2021-01-16 | 14:11 | 49.966
2021-01-16 | 14:11 | 49.965
2021-01-16 | 14:12 | 49.964
2021-01-16 | 14:12 | 49.962
2021-01-16 | 14:12 | 49.961
2021-01-16 | 14:12 | 49.961
2021-01-16 | 14:12 | 49.959
2021-01-16 | 14:12 | 49.96
2021-01-16 | 14:12 | 49.96
2021-01-16 | 14:12 | 49.962
2021-01-16 | 14:12 | 49.963
2021-01-16 | 14:12 | 49.963
2021-01-16 | 14:12 | 49.96
2021-01-16 | 14:12 | 49.957
2021-01-16 | 14:12 | 49.956
2021-01-16 | 14:12 | 49.955
2021-01-16 | 14:12 | 49.956
2021-01-16 | 14:12 | 49.955
2021-01-16 | 14:12 | 49.955
2021-01-16 | 14:12 | 49.955
2021-01-16 | 14:12 | 49.955
2021-01-16 | 14:12 | 49.955
2021-01-16 | 14:12 | 49.954
2021-01-16 | 14:12 | 49.954
2021-01-16 | 14:12 | 49.954
2021-01-16 | 14:12 | 49.954
2021-01-16 | 14:12 | 49.955
2021-01-16 | 14:12 | 49.956
2021-01-16 | 14:12 | 49.957
2021-01-16 | 14:12 | 49.956
2021-01-16 | 14:12 | 49.958
2021-01-16 | 14:12 | 49.96
2021-01-16 | 14:12 | 49.96
2021-01-16 | 14:12 | 49.956
2021-01-16 | 14:12 | 49.953
2021-01-16 | 14:12 | 49.951
2021-01-16 | 14:12 | 49.95
2021-01-16 | 14:12 | 49.949
2021-01-16 | 14:12 | 49.948
2021-01-16 | 14:12 | 49.947
2021-01-16 | 14:12 | 49.946
2021-01-16 | 14:12 | 49.944
2021-01-16 | 14:12 | 49.943
2021-01-16 | 14:12 | 49.941
2021-01-16 | 14:12 | 49.942
2021-01-16 | 14:12 | 49.941
2021-01-16 | 14:12 | 49.939
2021-01-16 | 14:12 | 49.938
2021-01-16 | 14:12 | 49.937
2021-01-16 | 14:12 | 49.934
2021-01-16 | 14:12 | 49.934
2021-01-16 | 14:12 | 49.936
2021-01-16 | 14:12 | 49.938
2021-01-16 | 14:12 | 49.937
2021-01-16 | 14:12 | 49.934
2021-01-16 | 14:12 | 49.932
2021-01-16 | 14:12 | 49.932
2021-01-16 | 14:12 | 49.933
2021-01-16 | 14:12 | 49.936
2021-01-16 | 14:12 | 49.938
2021-01-16 | 14:12 | 49.939
2021-01-16 | 14:13 | 49.94
2021-01-16 | 14:13 | 49.941
2021-01-16 | 14:13 | 49.942
2021-01-16 | 14:13 | 49.943
2021-01-16 | 14:13 | 49.942
2021-01-16 | 14:13 | 49.943
2021-01-16 | 14:13 | 49.944
2021-01-16 | 14:13 | 49.945
2021-01-16 | 14:13 | 49.945
2021-01-16 | 14:13 | 49.945
2021-01-16 | 14:13 | 49.947
2021-01-16 | 14:13 | 49.948
2021-01-16 | 14:13 | 49.948
2021-01-16 | 14:13 | 49.95
2021-01-16 | 14:13 | 49.949
2021-01-16 | 14:13 | 49.946
2021-01-16 | 14:13 | 49.944
2021-01-16 | 14:13 | 49.943
2021-01-16 | 14:13 | 49.943
2021-01-16 | 14:13 | 49.944
2021-01-16 | 14:13 | 49.944
2021-01-16 | 14:13 | 49.943
2021-01-16 | 14:13 | 49.945
2021-01-16 | 14:13 | 49.944
2021-01-16 | 14:13 | 49.944
2021-01-16 | 14:13 | 49.944
2021-01-16 | 14:13 | 49.943
2021-01-16 | 14:13 | 49.946
2021-01-16 | 14:13 | 49.946
2021-01-16 | 14:13 | 49.945
2021-01-16 | 14:13 | 49.943
2021-01-16 | 14:13 | 49.942
2021-01-16 | 14:13 | 49.941
2021-01-16 | 14:13 | 49.936
2021-01-16 | 14:13 | 49.934
2021-01-16 | 14:13 | 49.931
2021-01-16 | 14:13 | 49.932
2021-01-16 | 14:13 | 49.932
2021-01-16 | 14:13 | 49.931
2021-01-16 | 14:13 | 49.931
2021-01-16 | 14:13 | 49.928
2021-01-16 | 14:13 | 49.928
2021-01-16 | 14:13 | 49.926
2021-01-16 | 14:13 | 49.926
2021-01-16 | 14:13 | 49.924
2021-01-16 | 14:13 | 49.926
2021-01-16 | 14:13 | 49.926
2021-01-16 | 14:13 | 49.927
2021-01-16 | 14:13 | 49.927
2021-01-16 | 14:13 | 49.927
2021-01-16 | 14:13 | 49.925
2021-01-16 | 14:13 | 49.926
2021-01-16 | 14:13 | 49.926
2021-01-16 | 14:13 | 49.927
2021-01-16 | 14:13 | 49.927
2021-01-16 | 14:13 | 49.927
2021-01-16 | 14:13 | 49.926
2021-01-16 | 14:13 | 49.927
2021-01-16 | 14:13 | 49.928
2021-01-16 | 14:13 | 49.93
2021-01-16 | 14:13 | 49.931
2021-01-16 | 14:14 | 49.931
2021-01-16 | 14:14 | 49.929
2021-01-16 | 14:14 | 49.929
2021-01-16 | 14:14 | 49.931
2021-01-16 | 14:14 | 49.931
2021-01-16 | 14:14 | 49.935
2021-01-16 | 14:14 | 49.937
2021-01-16 | 14:14 | 49.938
2021-01-16 | 14:14 | 49.939
2021-01-16 | 14:14 | 49.939
2021-01-16 | 14:14 | 49.94
2021-01-16 | 14:14 | 49.941
2021-01-16 | 14:14 | 49.942
2021-01-16 | 14:14 | 49.939
2021-01-16 | 14:14 | 49.939
2021-01-16 | 14:14 | 49.938
2021-01-16 | 14:14 | 49.939
2021-01-16 | 14:14 | 49.94
2021-01-16 | 14:14 | 49.938
2021-01-16 | 14:14 | 49.936
2021-01-16 | 14:14 | 49.935
2021-01-16 | 14:14 | 49.935
2021-01-16 | 14:14 | 49.934
2021-01-16 | 14:14 | 49.933
2021-01-16 | 14:14 | 49.933
2021-01-16 | 14:14 | 49.931
2021-01-16 | 14:14 | 49.93
2021-01-16 | 14:14 | 49.93
2021-01-16 | 14:14 | 49.93
2021-01-16 | 14:14 | 49.929
2021-01-16 | 14:14 | 49.931
2021-01-16 | 14:14 | 49.927
2021-01-16 | 14:14 | 49.925
2021-01-16 | 14:14 | 49.923
2021-01-16 | 14:14 | 49.923
2021-01-16 | 14:14 | 49.921
2021-01-16 | 14:14 | 49.921
2021-01-16 | 14:14 | 49.925
2021-01-16 | 14:14 | 49.924
2021-01-16 | 14:14 | 49.923
2021-01-16 | 14:14 | 49.925
2021-01-16 | 14:14 | 49.927
2021-01-16 | 14:14 | 49.929
2021-01-16 | 14:14 | 49.932
2021-01-16 | 14:14 | 49.932
2021-01-16 | 14:14 | 49.933
2021-01-16 | 14:14 | 49.932
2021-01-16 | 14:14 | 49.934
2021-01-16 | 14:14 | 49.932
2021-01-16 | 14:14 | 49.931
2021-01-16 | 14:14 | 49.93
2021-01-16 | 14:14 | 49.931
2021-01-16 | 14:14 | 49.932
2021-01-16 | 14:14 | 49.934
2021-01-16 | 14:14 | 49.935
2021-01-16 | 14:14 | 49.938
2021-01-16 | 14:14 | 49.938
2021-01-16 | 14:14 | 49.941
2021-01-16 | 14:14 | 49.94
2021-01-16 | 14:15 | 49.94
2021-01-16 | 14:15 | 49.939
2021-01-16 | 14:15 | 49.938
2021-01-16 | 14:15 | 49.937
2021-01-16 | 14:15 | 49.938
2021-01-16 | 14:15 | 49.938
2021-01-16 | 14:15 | 49.936
2021-01-16 | 14:15 | 49.938
2021-01-16 | 14:15 | 49.939
2021-01-16 | 14:15 | 49.936
2021-01-16 | 14:15 | 49.938
2021-01-16 | 14:15 | 49.94
2021-01-16 | 14:15 | 49.943
2021-01-16 | 14:15 | 49.945
2021-01-16 | 14:15 | 49.948
2021-01-16 | 14:15 | 49.951
2021-01-16 | 14:15 | 49.952
2021-01-16 | 14:15 | 49.955
2021-01-16 | 14:15 | 49.958
2021-01-16 | 14:15 | 49.96
2021-01-16 | 14:15 | 49.959
2021-01-16 | 14:15 | 49.959
2021-01-16 | 14:15 | 49.96
2021-01-16 | 14:15 | 49.958
2021-01-16 | 14:15 | 49.955
2021-01-16 | 14:15 | 49.953
2021-01-16 | 14:15 | 49.951
2021-01-16 | 14:15 | 49.948
2021-01-16 | 14:15 | 49.948
2021-01-16 | 14:15 | 49.95
2021-01-16 | 14:15 | 49.952
2021-01-16 | 14:15 | 49.952
2021-01-16 | 14:15 | 49.953
2021-01-16 | 14:15 | 49.955
2021-01-16 | 14:15 | 49.955
2021-01-16 | 14:15 | 49.956
2021-01-16 | 14:15 | 49.958
2021-01-16 | 14:15 | 49.959
2021-01-16 | 14:15 | 49.957
2021-01-16 | 14:15 | 49.955
2021-01-16 | 14:15 | 49.956
2021-01-16 | 14:15 | 49.955
2021-01-16 | 14:15 | 49.954
2021-01-16 | 14:15 | 49.953
2021-01-16 | 14:15 | 49.951
2021-01-16 | 14:15 | 49.948
2021-01-16 | 14:15 | 49.948
2021-01-16 | 14:15 | 49.948
2021-01-16 | 14:15 | 49.952
2021-01-16 | 14:15 | 49.952
2021-01-16 | 14:15 | 49.955
2021-01-16 | 14:15 | 49.957
2021-01-16 | 14:15 | 49.956
2021-01-16 | 14:15 | 49.956
2021-01-16 | 14:15 | 49.955
2021-01-16 | 14:15 | 49.952
2021-01-16 | 14:15 | 49.95
2021-01-16 | 14:15 | 49.946
2021-01-16 | 14:15 | 49.945
2021-01-16 | 14:15 | 49.946
2021-01-16 | 14:15 | 49.947
2021-01-16 | 14:16 | 49.949
2021-01-16 | 14:16 | 49.951
2021-01-16 | 14:16 | 49.95
2021-01-16 | 14:16 | 49.947
2021-01-16 | 14:16 | 49.945
2021-01-16 | 14:16 | 49.947
2021-01-16 | 14:16 | 49.945
2021-01-16 | 14:16 | 49.944
2021-01-16 | 14:16 | 49.944
2021-01-16 | 14:16 | 49.947
2021-01-16 | 14:16 | 49.949
2021-01-16 | 14:16 | 49.952
2021-01-16 | 14:16 | 49.954
2021-01-16 | 14:16 | 49.953
2021-01-16 | 14:16 | 49.952
2021-01-16 | 14:16 | 49.949
2021-01-16 | 14:16 | 49.948
2021-01-16 | 14:16 | 49.945
2021-01-16 | 14:16 | 49.94
2021-01-16 | 14:16 | 49.934
2021-01-16 | 14:16 | 49.93
2021-01-16 | 14:16 | 49.929
2021-01-16 | 14:16 | 49.931
2021-01-16 | 14:16 | 49.934
2021-01-16 | 14:16 | 49.935
2021-01-16 | 14:16 | 49.936
2021-01-16 | 14:16 | 49.934
2021-01-16 | 14:16 | 49.933
2021-01-16 | 14:16 | 49.929
2021-01-16 | 14:16 | 49.924
2021-01-16 | 14:16 | 49.922
2021-01-16 | 14:16 | 49.92
2021-01-16 | 14:16 | 49.917
2021-01-16 | 14:16 | 49.914
2021-01-16 | 14:16 | 49.912
2021-01-16 | 14:16 | 49.912
2021-01-16 | 14:16 | 49.912
2021-01-16 | 14:16 | 49.912
2021-01-16 | 14:16 | 49.911
2021-01-16 | 14:16 | 49.911
2021-01-16 | 14:16 | 49.91
2021-01-16 | 14:16 | 49.91
2021-01-16 | 14:16 | 49.912
2021-01-16 | 14:16 | 49.915
2021-01-16 | 14:16 | 49.92
2021-01-16 | 14:16 | 49.923
2021-01-16 | 14:16 | 49.926
2021-01-16 | 14:16 | 49.929
2021-01-16 | 14:16 | 49.932
2021-01-16 | 14:16 | 49.933
2021-01-16 | 14:16 | 49.933
2021-01-16 | 14:16 | 49.933
2021-01-16 | 14:16 | 49.933
2021-01-16 | 14:16 | 49.935
2021-01-16 | 14:16 | 49.934
2021-01-16 | 14:16 | 49.932
2021-01-16 | 14:16 | 49.93
2021-01-16 | 14:16 | 49.928
2021-01-16 | 14:16 | 49.927
2021-01-16 | 14:17 | 49.925
2021-01-16 | 14:17 | 49.926
2021-01-16 | 14:17 | 49.925
2021-01-16 | 14:17 | 49.924
2021-01-16 | 14:17 | 49.922
2021-01-16 | 14:17 | 49.923
2021-01-16 | 14:17 | 49.925
2021-01-16 | 14:17 | 49.928
2021-01-16 | 14:17 | 49.927
2021-01-16 | 14:17 | 49.927
2021-01-16 | 14:17 | 49.93
2021-01-16 | 14:17 | 49.932
2021-01-16 | 14:17 | 49.935
2021-01-16 | 14:17 | 49.935
2021-01-16 | 14:17 | 49.936
2021-01-16 | 14:17 | 49.938
2021-01-16 | 14:17 | 49.939
2021-01-16 | 14:17 | 49.939
2021-01-16 | 14:17 | 49.94
2021-01-16 | 14:17 | 49.941
2021-01-16 | 14:17 | 49.941
2021-01-16 | 14:17 | 49.943
2021-01-16 | 14:17 | 49.943
2021-01-16 | 14:17 | 49.943
2021-01-16 | 14:17 | 49.941
2021-01-16 | 14:17 | 49.939
2021-01-16 | 14:17 | 49.938
2021-01-16 | 14:17 | 49.938
2021-01-16 | 14:17 | 49.937
2021-01-16 | 14:17 | 49.936
2021-01-16 | 14:17 | 49.938
2021-01-16 | 14:17 | 49.937
2021-01-16 | 14:17 | 49.936
2021-01-16 | 14:17 | 49.934
2021-01-16 | 14:17 | 49.934
2021-01-16 | 14:17 | 49.934
2021-01-16 | 14:17 | 49.936
2021-01-16 | 14:17 | 49.938
2021-01-16 | 14:17 | 49.94
2021-01-16 | 14:17 | 49.941
2021-01-16 | 14:17 | 49.941
2021-01-16 | 14:17 | 49.939
2021-01-16 | 14:17 | 49.937
2021-01-16 | 14:17 | 49.937
2021-01-16 | 14:17 | 49.939
2021-01-16 | 14:17 | 49.942
2021-01-16 | 14:17 | 49.945
2021-01-16 | 14:17 | 49.946
2021-01-16 | 14:17 | 49.944
2021-01-16 | 14:17 | 49.946
2021-01-16 | 14:17 | 49.948
2021-01-16 | 14:17 | 49.946
2021-01-16 | 14:17 | 49.943
2021-01-16 | 14:17 | 49.939
2021-01-16 | 14:17 | 49.937
2021-01-16 | 14:17 | 49.936
2021-01-16 | 14:17 | 49.933
2021-01-16 | 14:17 | 49.934
2021-01-16 | 14:17 | 49.934
2021-01-16 | 14:17 | 49.932
2021-01-16 | 14:17 | 49.932
2021-01-16 | 14:18 | 49.932
2021-01-16 | 14:18 | 49.931
2021-01-16 | 14:18 | 49.93
2021-01-16 | 14:18 | 49.93
2021-01-16 | 14:18 | 49.93
2021-01-16 | 14:18 | 49.928
2021-01-16 | 14:18 | 49.926
2021-01-16 | 14:18 | 49.925
2021-01-16 | 14:18 | 49.927
2021-01-16 | 14:18 | 49.927
2021-01-16 | 14:18 | 49.928
2021-01-16 | 14:18 | 49.929
2021-01-16 | 14:18 | 49.933
2021-01-16 | 14:18 | 49.935
2021-01-16 | 14:18 | 49.939
2021-01-16 | 14:18 | 49.942
2021-01-16 | 14:18 | 49.944
2021-01-16 | 14:18 | 49.947
2021-01-16 | 14:18 | 49.948
2021-01-16 | 14:18 | 49.947
2021-01-16 | 14:18 | 49.945
2021-01-16 | 14:18 | 49.943
2021-01-16 | 14:18 | 49.94
2021-01-16 | 14:18 | 49.935
2021-01-16 | 14:18 | 49.933
2021-01-16 | 14:18 | 49.931
2021-01-16 | 14:18 | 49.93
2021-01-16 | 14:18 | 49.928
2021-01-16 | 14:18 | 49.927
2021-01-16 | 14:18 | 49.927
2021-01-16 | 14:18 | 49.925
2021-01-16 | 14:18 | 49.924
2021-01-16 | 14:18 | 49.925
2021-01-16 | 14:18 | 49.927
2021-01-16 | 14:18 | 49.926
2021-01-16 | 14:18 | 49.924
2021-01-16 | 14:18 | 49.923
2021-01-16 | 14:18 | 49.923
2021-01-16 | 14:18 | 49.925
2021-01-16 | 14:18 | 49.928
2021-01-16 | 14:18 | 49.927
2021-01-16 | 14:18 | 49.927
2021-01-16 | 14:18 | 49.929
2021-01-16 | 14:18 | 49.929
2021-01-16 | 14:18 | 49.93
2021-01-16 | 14:18 | 49.932
2021-01-16 | 14:18 | 49.935
2021-01-16 | 14:18 | 49.936
2021-01-16 | 14:18 | 49.938
2021-01-16 | 14:18 | 49.939
2021-01-16 | 14:18 | 49.941
2021-01-16 | 14:18 | 49.941
2021-01-16 | 14:18 | 49.943
2021-01-16 | 14:18 | 49.944
2021-01-16 | 14:18 | 49.944
2021-01-16 | 14:18 | 49.945
2021-01-16 | 14:18 | 49.946
2021-01-16 | 14:18 | 49.947
2021-01-16 | 14:18 | 49.95
2021-01-16 | 14:19 | 49.952
2021-01-16 | 14:19 | 49.957
2021-01-16 | 14:19 | 49.958
2021-01-16 | 14:19 | 49.96
2021-01-16 | 14:19 | 49.96
2021-01-16 | 14:19 | 49.959
2021-01-16 | 14:19 | 49.955
2021-01-16 | 14:19 | 49.953
2021-01-16 | 14:19 | 49.948
2021-01-16 | 14:19 | 49.946
2021-01-16 | 14:19 | 49.944
2021-01-16 | 14:19 | 49.941
2021-01-16 | 14:19 | 49.94
2021-01-16 | 14:19 | 49.941
2021-01-16 | 14:19 | 49.944
2021-01-16 | 14:19 | 49.95
2021-01-16 | 14:19 | 49.955
2021-01-16 | 14:19 | 49.958
2021-01-16 | 14:19 | 49.962
2021-01-16 | 14:19 | 49.966
2021-01-16 | 14:19 | 49.97
2021-01-16 | 14:19 | 49.971
2021-01-16 | 14:19 | 49.969
2021-01-16 | 14:19 | 49.969
2021-01-16 | 14:19 | 49.967
2021-01-16 | 14:19 | 49.965
2021-01-16 | 14:19 | 49.965
2021-01-16 | 14:19 | 49.965
2021-01-16 | 14:19 | 49.965
2021-01-16 | 14:19 | 49.965
2021-01-16 | 14:19 | 49.965
2021-01-16 | 14:19 | 49.965
2021-01-16 | 14:19 | 49.965
2021-01-16 | 14:19 | 49.964
2021-01-16 | 14:19 | 49.966
2021-01-16 | 14:19 | 49.966
2021-01-16 | 14:19 | 49.965
2021-01-16 | 14:19 | 49.966
2021-01-16 | 14:19 | 49.963
2021-01-16 | 14:19 | 49.964
2021-01-16 | 14:19 | 49.963
2021-01-16 | 14:19 | 49.961
2021-01-16 | 14:19 | 49.961
2021-01-16 | 14:19 | 49.961
2021-01-16 | 14:19 | 49.959
2021-01-16 | 14:19 | 49.959
2021-01-16 | 14:19 | 49.957
2021-01-16 | 14:19 | 49.956
2021-01-16 | 14:19 | 49.954
2021-01-16 | 14:19 | 49.953
2021-01-16 | 14:19 | 49.954
2021-01-16 | 14:19 | 49.955
2021-01-16 | 14:19 | 49.955
2021-01-16 | 14:19 | 49.955
2021-01-16 | 14:19 | 49.953
2021-01-16 | 14:19 | 49.95
2021-01-16 | 14:19 | 49.95
2021-01-16 | 14:19 | 49.951
2021-01-16 | 14:19 | 49.948
2021-01-16 | 14:19 | 49.946
2021-01-16 | 14:19 | 49.942
2021-01-16 | 14:20 | 49.939
2021-01-16 | 14:20 | 49.937
2021-01-16 | 14:20 | 49.934
2021-01-16 | 14:20 | 49.936
2021-01-16 | 14:20 | 49.935
2021-01-16 | 14:20 | 49.934
2021-01-16 | 14:20 | 49.934
2021-01-16 | 14:20 | 49.936
2021-01-16 | 14:20 | 49.939
2021-01-16 | 14:20 | 49.944
2021-01-16 | 14:20 | 49.946
2021-01-16 | 14:20 | 49.949
2021-01-16 | 14:20 | 49.952
2021-01-16 | 14:20 | 49.956
2021-01-16 | 14:20 | 49.958
2021-01-16 | 14:20 | 49.962
2021-01-16 | 14:20 | 49.965
2021-01-16 | 14:20 | 49.967
2021-01-16 | 14:20 | 49.968
2021-01-16 | 14:20 | 49.969
2021-01-16 | 14:20 | 49.968
2021-01-16 | 14:20 | 49.969
2021-01-16 | 14:20 | 49.967
2021-01-16 | 14:20 | 49.968
2021-01-16 | 14:20 | 49.969
2021-01-16 | 14:20 | 49.97
2021-01-16 | 14:20 | 49.97
2021-01-16 | 14:20 | 49.971
2021-01-16 | 14:20 | 49.972
2021-01-16 | 14:20 | 49.973
2021-01-16 | 14:20 | 49.974
2021-01-16 | 14:20 | 49.974
2021-01-16 | 14:20 | 49.974
2021-01-16 | 14:20 | 49.975
2021-01-16 | 14:20 | 49.978
2021-01-16 | 14:20 | 49.981
2021-01-16 | 14:20 | 49.981
2021-01-16 | 14:20 | 49.979
2021-01-16 | 14:20 | 49.977
2021-01-16 | 14:20 | 49.978
2021-01-16 | 14:20 | 49.974
2021-01-16 | 14:20 | 49.972
2021-01-16 | 14:20 | 49.967
2021-01-16 | 14:20 | 49.962
2021-01-16 | 14:20 | 49.96
2021-01-16 | 14:20 | 49.96
2021-01-16 | 14:20 | 49.963
2021-01-16 | 14:20 | 49.968
2021-01-16 | 14:20 | 49.971
2021-01-16 | 14:20 | 49.973
2021-01-16 | 14:20 | 49.975
2021-01-16 | 14:20 | 49.976
2021-01-16 | 14:20 | 49.975
2021-01-16 | 14:20 | 49.977
2021-01-16 | 14:20 | 49.975
2021-01-16 | 14:20 | 49.976
2021-01-16 | 14:20 | 49.978
2021-01-16 | 14:20 | 49.979
2021-01-16 | 14:20 | 49.98
2021-01-16 | 14:21 | 49.984
2021-01-16 | 14:21 | 49.986
2021-01-16 | 14:21 | 49.987
2021-01-16 | 14:21 | 49.988
2021-01-16 | 14:21 | 49.987
2021-01-16 | 14:21 | 49.987
2021-01-16 | 14:21 | 49.989
2021-01-16 | 14:21 | 49.986
2021-01-16 | 14:21 | 49.985
2021-01-16 | 14:21 | 49.984
2021-01-16 | 14:21 | 49.982
2021-01-16 | 14:21 | 49.98
2021-01-16 | 14:21 | 49.978
2021-01-16 | 14:21 | 49.974
2021-01-16 | 14:21 | 49.97
2021-01-16 | 14:21 | 49.967
2021-01-16 | 14:21 | 49.966
2021-01-16 | 14:21 | 49.965
2021-01-16 | 14:21 | 49.968
2021-01-16 | 14:21 | 49.97
2021-01-16 | 14:21 | 49.972
2021-01-16 | 14:21 | 49.975
2021-01-16 | 14:21 | 49.977
2021-01-16 | 14:21 | 49.975
2021-01-16 | 14:21 | 49.976
2021-01-16 | 14:21 | 49.977
2021-01-16 | 14:21 | 49.976
2021-01-16 | 14:21 | 49.975
2021-01-16 | 14:21 | 49.975
2021-01-16 | 14:21 | 49.974
2021-01-16 | 14:21 | 49.972
2021-01-16 | 14:21 | 49.97
2021-01-16 | 14:21 | 49.97
2021-01-16 | 14:21 | 49.968
2021-01-16 | 14:21 | 49.966
2021-01-16 | 14:21 | 49.964
2021-01-16 | 14:21 | 49.965
2021-01-16 | 14:21 | 49.962
2021-01-16 | 14:21 | 49.96
2021-01-16 | 14:21 | 49.958
2021-01-16 | 14:21 | 49.958
2021-01-16 | 14:21 | 49.959
2021-01-16 | 14:21 | 49.961
2021-01-16 | 14:21 | 49.962
2021-01-16 | 14:21 | 49.963
2021-01-16 | 14:21 | 49.961
2021-01-16 | 14:21 | 49.961
2021-01-16 | 14:21 | 49.963
2021-01-16 | 14:21 | 49.964
2021-01-16 | 14:21 | 49.964
2021-01-16 | 14:21 | 49.967
2021-01-16 | 14:21 | 49.968
2021-01-16 | 14:21 | 49.971
2021-01-16 | 14:21 | 49.972
2021-01-16 | 14:21 | 49.973
2021-01-16 | 14:21 | 49.975
2021-01-16 | 14:21 | 49.975
2021-01-16 | 14:21 | 49.976
2021-01-16 | 14:21 | 49.977
2021-01-16 | 14:21 | 49.98
2021-01-16 | 14:21 | 49.984
2021-01-16 | 14:22 | 49.986
2021-01-16 | 14:22 | 49.991
2021-01-16 | 14:22 | 49.994
2021-01-16 | 14:22 | 49.998
2021-01-16 | 14:22 | 50.001
2021-01-16 | 14:22 | 50
2021-01-16 | 14:22 | 50.001
2021-01-16 | 14:22 | 50.005
2021-01-16 | 14:22 | 50.007
2021-01-16 | 14:22 | 50.009
2021-01-16 | 14:22 | 50.011
2021-01-16 | 14:22 | 50.015
2021-01-16 | 14:22 | 50.016
2021-01-16 | 14:22 | 50.015
2021-01-16 | 14:22 | 50.016
2021-01-16 | 14:22 | 50.018
2021-01-16 | 14:22 | 50.02
2021-01-16 | 14:22 | 50.02
2021-01-16 | 14:22 | 50.017
2021-01-16 | 14:22 | 50.016
2021-01-16 | 14:22 | 50.014
2021-01-16 | 14:22 | 50.011
2021-01-16 | 14:22 | 50.011
2021-01-16 | 14:22 | 50.014
2021-01-16 | 14:22 | 50.017
2021-01-16 | 14:22 | 50.018
2021-01-16 | 14:22 | 50.017
2021-01-16 | 14:22 | 50.017
2021-01-16 | 14:22 | 50.017
2021-01-16 | 14:22 | 50.017
2021-01-16 | 14:22 | 50.015
2021-01-16 | 14:22 | 50.011
2021-01-16 | 14:22 | 50.007
2021-01-16 | 14:22 | 50.001
2021-01-16 | 14:22 | 49.994
2021-01-16 | 14:22 | 49.99
2021-01-16 | 14:22 | 49.985
2021-01-16 | 14:22 | 49.979
2021-01-16 | 14:22 | 49.975
2021-01-16 | 14:22 | 49.972
2021-01-16 | 14:22 | 49.969
2021-01-16 | 14:22 | 49.968
2021-01-16 | 14:22 | 49.968
2021-01-16 | 14:22 | 49.968
2021-01-16 | 14:22 | 49.967
2021-01-16 | 14:22 | 49.964
2021-01-16 | 14:22 | 49.962
2021-01-16 | 14:22 | 49.962
2021-01-16 | 14:22 | 49.961
2021-01-16 | 14:22 | 49.96
2021-01-16 | 14:22 | 49.962
2021-01-16 | 14:22 | 49.963
2021-01-16 | 14:22 | 49.965
2021-01-16 | 14:22 | 49.967
2021-01-16 | 14:22 | 49.972
2021-01-16 | 14:22 | 49.973
2021-01-16 | 14:22 | 49.978
2021-01-16 | 14:22 | 49.982
2021-01-16 | 14:22 | 49.984
2021-01-16 | 14:22 | 49.984
2021-01-16 | 14:23 | 49.983
2021-01-16 | 14:23 | 49.983
2021-01-16 | 14:23 | 49.981
2021-01-16 | 14:23 | 49.977
2021-01-16 | 14:23 | 49.976
2021-01-16 | 14:23 | 49.973
2021-01-16 | 14:23 | 49.972
2021-01-16 | 14:23 | 49.971
2021-01-16 | 14:23 | 49.97
2021-01-16 | 14:23 | 49.968
2021-01-16 | 14:23 | 49.968
2021-01-16 | 14:23 | 49.969
2021-01-16 | 14:23 | 49.972
2021-01-16 | 14:23 | 49.972
2021-01-16 | 14:23 | 49.975
2021-01-16 | 14:23 | 49.976
2021-01-16 | 14:23 | 49.977
2021-01-16 | 14:23 | 49.977
2021-01-16 | 14:23 | 49.975
2021-01-16 | 14:23 | 49.972
2021-01-16 | 14:23 | 49.971
2021-01-16 | 14:23 | 49.97
2021-01-16 | 14:23 | 49.969
2021-01-16 | 14:23 | 49.968
2021-01-16 | 14:23 | 49.969
2021-01-16 | 14:23 | 49.971
2021-01-16 | 14:23 | 49.974
2021-01-16 | 14:23 | 49.978
2021-01-16 | 14:23 | 49.981
2021-01-16 | 14:23 | 49.984
2021-01-16 | 14:23 | 49.988
2021-01-16 | 14:23 | 49.99
2021-01-16 | 14:23 | 49.993
2021-01-16 | 14:23 | 49.997
2021-01-16 | 14:23 | 50.003
2021-01-16 | 14:23 | 50.006
2021-01-16 | 14:23 | 50.009
2021-01-16 | 14:23 | 50.012
2021-01-16 | 14:23 | 50.014
2021-01-16 | 14:23 | 50.015
2021-01-16 | 14:23 | 50.019
2021-01-16 | 14:23 | 50.019
2021-01-16 | 14:23 | 50.017
2021-01-16 | 14:23 | 50.014
2021-01-16 | 14:23 | 50.011
2021-01-16 | 14:23 | 50.007
2021-01-16 | 14:23 | 50.006
2021-01-16 | 14:23 | 50.004
2021-01-16 | 14:23 | 50.001
2021-01-16 | 14:23 | 49.998
2021-01-16 | 14:23 | 49.997
2021-01-16 | 14:23 | 49.995
2021-01-16 | 14:23 | 49.996
2021-01-16 | 14:23 | 49.998
2021-01-16 | 14:23 | 49.999
2021-01-16 | 14:23 | 50.002
2021-01-16 | 14:23 | 50.003
2021-01-16 | 14:23 | 50.003
2021-01-16 | 14:23 | 50.002
2021-01-16 | 14:24 | 50
2021-01-16 | 14:24 | 49.998
2021-01-16 | 14:24 | 49.996
2021-01-16 | 14:24 | 49.994
2021-01-16 | 14:24 | 49.99
2021-01-16 | 14:24 | 49.987
2021-01-16 | 14:24 | 49.987
2021-01-16 | 14:24 | 49.988
2021-01-16 | 14:24 | 49.987
2021-01-16 | 14:24 | 49.988
2021-01-16 | 14:24 | 49.99
2021-01-16 | 14:24 | 49.988
2021-01-16 | 14:24 | 49.988
2021-01-16 | 14:24 | 49.989
2021-01-16 | 14:24 | 49.988
2021-01-16 | 14:24 | 49.988
2021-01-16 | 14:24 | 49.989
2021-01-16 | 14:24 | 49.991
2021-01-16 | 14:24 | 49.992
2021-01-16 | 14:24 | 49.994
2021-01-16 | 14:24 | 49.997
2021-01-16 | 14:24 | 49.997
2021-01-16 | 14:24 | 49.996
2021-01-16 | 14:24 | 49.996
2021-01-16 | 14:24 | 49.995
2021-01-16 | 14:24 | 49.997
2021-01-16 | 14:24 | 49.999
2021-01-16 | 14:24 | 50.002
2021-01-16 | 14:24 | 50.001
2021-01-16 | 14:24 | 50.002
2021-01-16 | 14:24 | 50.005
2021-01-16 | 14:24 | 50.004
2021-01-16 | 14:24 | 50.004
2021-01-16 | 14:24 | 50.004
2021-01-16 | 14:24 | 50.006
2021-01-16 | 14:24 | 50.006
2021-01-16 | 14:24 | 50.008
2021-01-16 | 14:24 | 50.009
2021-01-16 | 14:24 | 50.01
2021-01-16 | 14:24 | 50.013
2021-01-16 | 14:24 | 50.015
2021-01-16 | 14:24 | 50.017
2021-01-16 | 14:24 | 50.017
2021-01-16 | 14:24 | 50.018
2021-01-16 | 14:24 | 50.018
2021-01-16 | 14:24 | 50.015
2021-01-16 | 14:24 | 50.012
2021-01-16 | 14:24 | 50.01
2021-01-16 | 14:24 | 50.007
2021-01-16 | 14:24 | 50.007
2021-01-16 | 14:24 | 50.007
2021-01-16 | 14:24 | 50.008
2021-01-16 | 14:24 | 50.007
2021-01-16 | 14:24 | 50.005
2021-01-16 | 14:24 | 50.006
2021-01-16 | 14:24 | 50.007
2021-01-16 | 14:24 | 50.005
2021-01-16 | 14:24 | 50.007
2021-01-16 | 14:24 | 50.008
2021-01-16 | 14:24 | 50.007
2021-01-16 | 14:24 | 50.007
2021-01-16 | 14:25 | 50.008
2021-01-16 | 14:25 | 50.011
2021-01-16 | 14:25 | 50.015
2021-01-16 | 14:25 | 50.018
2021-01-16 | 14:25 | 50.022
2021-01-16 | 14:25 | 50.024
2021-01-16 | 14:25 | 50.026
2021-01-16 | 14:25 | 50.027
2021-01-16 | 14:25 | 50.029
2021-01-16 | 14:25 | 50.028
2021-01-16 | 14:25 | 50.031
2021-01-16 | 14:25 | 50.031
2021-01-16 | 14:25 | 50.032
2021-01-16 | 14:25 | 50.034
2021-01-16 | 14:25 | 50.035
2021-01-16 | 14:25 | 50.035
2021-01-16 | 14:25 | 50.035
2021-01-16 | 14:25 | 50.035
2021-01-16 | 14:25 | 50.034
2021-01-16 | 14:25 | 50.035
2021-01-16 | 14:25 | 50.036
2021-01-16 | 14:25 | 50.038
2021-01-16 | 14:25 | 50.036
2021-01-16 | 14:25 | 50.035
2021-01-16 | 14:25 | 50.034
2021-01-16 | 14:25 | 50.033
2021-01-16 | 14:25 | 50.029
2021-01-16 | 14:25 | 50.028
2021-01-16 | 14:25 | 50.028
2021-01-16 | 14:25 | 50.03
2021-01-16 | 14:25 | 50.029
2021-01-16 | 14:25 | 50.028
2021-01-16 | 14:25 | 50.026
2021-01-16 | 14:25 | 50.025
2021-01-16 | 14:25 | 50.024
2021-01-16 | 14:25 | 50.02
2021-01-16 | 14:25 | 50.018
2021-01-16 | 14:25 | 50.018
2021-01-16 | 14:25 | 50.018
2021-01-16 | 14:25 | 50.017
2021-01-16 | 14:25 | 50.018
2021-01-16 | 14:25 | 50.021
2021-01-16 | 14:25 | 50.019
2021-01-16 | 14:25 | 50.017
2021-01-16 | 14:25 | 50.014
2021-01-16 | 14:25 | 50.012
2021-01-16 | 14:25 | 50.012
2021-01-16 | 14:25 | 50.01
2021-01-16 | 14:25 | 50.009
2021-01-16 | 14:25 | 50.008
2021-01-16 | 14:25 | 50.007
2021-01-16 | 14:25 | 50.005
2021-01-16 | 14:25 | 50.003
2021-01-16 | 14:25 | 50.004
2021-01-16 | 14:25 | 50.002
2021-01-16 | 14:25 | 50
2021-01-16 | 14:25 | 50
2021-01-16 | 14:25 | 49.998
2021-01-16 | 14:25 | 49.998
2021-01-16 | 14:26 | 49.995
2021-01-16 | 14:26 | 49.992
2021-01-16 | 14:26 | 49.989
2021-01-16 | 14:26 | 49.986
2021-01-16 | 14:26 | 49.988
2021-01-16 | 14:26 | 49.991
2021-01-16 | 14:26 | 49.995
2021-01-16 | 14:26 | 50
2021-01-16 | 14:26 | 50.001
2021-01-16 | 14:26 | 50.004
2021-01-16 | 14:26 | 50.009
2021-01-16 | 14:26 | 50.011
2021-01-16 | 14:26 | 50.009
2021-01-16 | 14:26 | 50.009
2021-01-16 | 14:26 | 50.007
2021-01-16 | 14:26 | 50.005
2021-01-16 | 14:26 | 50.007
2021-01-16 | 14:26 | 50.003
2021-01-16 | 14:26 | 50.002
2021-01-16 | 14:26 | 50.001
2021-01-16 | 14:26 | 49.998
2021-01-16 | 14:26 | 49.995
2021-01-16 | 14:26 | 49.992
2021-01-16 | 14:26 | 49.989
2021-01-16 | 14:26 | 49.987
2021-01-16 | 14:26 | 49.985
2021-01-16 | 14:26 | 49.983
2021-01-16 | 14:26 | 49.984
2021-01-16 | 14:26 | 49.983
2021-01-16 | 14:26 | 49.985
2021-01-16 | 14:26 | 49.985
2021-01-16 | 14:26 | 49.985
2021-01-16 | 14:26 | 49.987
2021-01-16 | 14:26 | 49.988
2021-01-16 | 14:26 | 49.99
2021-01-16 | 14:26 | 49.99
2021-01-16 | 14:26 | 49.99
2021-01-16 | 14:26 | 49.994
2021-01-16 | 14:26 | 49.995
2021-01-16 | 14:26 | 49.998
2021-01-16 | 14:26 | 50.002
2021-01-16 | 14:26 | 50.004
2021-01-16 | 14:26 | 50.007
2021-01-16 | 14:26 | 50.008
2021-01-16 | 14:26 | 50.007
2021-01-16 | 14:26 | 50.007
2021-01-16 | 14:26 | 50.009
2021-01-16 | 14:26 | 50.012
2021-01-16 | 14:26 | 50.013
2021-01-16 | 14:26 | 50.015
2021-01-16 | 14:26 | 50.017
2021-01-16 | 14:26 | 50.016
2021-01-16 | 14:26 | 50.016
2021-01-16 | 14:26 | 50.014
2021-01-16 | 14:26 | 50.015
2021-01-16 | 14:26 | 50.013
2021-01-16 | 14:26 | 50.013
2021-01-16 | 14:26 | 50.014
2021-01-16 | 14:26 | 50.015
2021-01-16 | 14:26 | 50.014
2021-01-16 | 14:26 | 50.013
2021-01-16 | 14:27 | 50.012
2021-01-16 | 14:27 | 50.01
2021-01-16 | 14:27 | 50.008
2021-01-16 | 14:27 | 50.008
2021-01-16 | 14:27 | 50.005
2021-01-16 | 14:27 | 50.005
2021-01-16 | 14:27 | 50.004
2021-01-16 | 14:27 | 50.003
2021-01-16 | 14:27 | 50.005
2021-01-16 | 14:27 | 50.005
2021-01-16 | 14:27 | 50.005
2021-01-16 | 14:27 | 50.005
2021-01-16 | 14:27 | 50.009
2021-01-16 | 14:27 | 50.009
2021-01-16 | 14:27 | 50.009
2021-01-16 | 14:27 | 50.008
2021-01-16 | 14:27 | 50.006
2021-01-16 | 14:27 | 50.006
2021-01-16 | 14:27 | 50.005
2021-01-16 | 14:27 | 50.006
2021-01-16 | 14:27 | 50.005
2021-01-16 | 14:27 | 50.006
2021-01-16 | 14:27 | 50.007
2021-01-16 | 14:27 | 50.006
2021-01-16 | 14:27 | 50.007
2021-01-16 | 14:27 | 50.004
2021-01-16 | 14:27 | 50.004
2021-01-16 | 14:27 | 50.002
2021-01-16 | 14:27 | 50.002
2021-01-16 | 14:27 | 50
2021-01-16 | 14:27 | 49.998
2021-01-16 | 14:27 | 49.995
2021-01-16 | 14:27 | 49.989
2021-01-16 | 14:27 | 49.985
2021-01-16 | 14:27 | 49.982
2021-01-16 | 14:27 | 49.981
2021-01-16 | 14:27 | 49.98
2021-01-16 | 14:27 | 49.981
2021-01-16 | 14:27 | 49.979
2021-01-16 | 14:27 | 49.979
2021-01-16 | 14:27 | 49.977
2021-01-16 | 14:27 | 49.976
2021-01-16 | 14:27 | 49.973
2021-01-16 | 14:27 | 49.973
2021-01-16 | 14:27 | 49.971
2021-01-16 | 14:27 | 49.97
2021-01-16 | 14:27 | 49.969
2021-01-16 | 14:27 | 49.968
2021-01-16 | 14:27 | 49.968
2021-01-16 | 14:27 | 49.968
2021-01-16 | 14:27 | 49.97
2021-01-16 | 14:27 | 49.97
2021-01-16 | 14:27 | 49.97
2021-01-16 | 14:27 | 49.969
2021-01-16 | 14:27 | 49.969
2021-01-16 | 14:27 | 49.968
2021-01-16 | 14:27 | 49.966
2021-01-16 | 14:27 | 49.967
2021-01-16 | 14:27 | 49.968
2021-01-16 | 14:28 | 49.969
2021-01-16 | 14:28 | 49.97
2021-01-16 | 14:28 | 49.972
2021-01-16 | 14:28 | 49.973
2021-01-16 | 14:28 | 49.975
2021-01-16 | 14:28 | 49.978
2021-01-16 | 14:28 | 49.981
2021-01-16 | 14:28 | 49.984
2021-01-16 | 14:28 | 49.985
2021-01-16 | 14:28 | 49.991
2021-01-16 | 14:28 | 49.992
2021-01-16 | 14:28 | 49.996
2021-01-16 | 14:28 | 49.995
2021-01-16 | 14:28 | 49.996
2021-01-16 | 14:28 | 49.997
2021-01-16 | 14:28 | 49.998
2021-01-16 | 14:28 | 50
2021-01-16 | 14:28 | 50.002
2021-01-16 | 14:28 | 50.002
2021-01-16 | 14:28 | 50.005
2021-01-16 | 14:28 | 50.007
2021-01-16 | 14:28 | 50.009
2021-01-16 | 14:28 | 50.01
2021-01-16 | 14:28 | 50.01
2021-01-16 | 14:28 | 50.01
2021-01-16 | 14:28 | 50.011
2021-01-16 | 14:28 | 50.013
2021-01-16 | 14:28 | 50.013
2021-01-16 | 14:28 | 50.015
2021-01-16 | 14:28 | 50.016
2021-01-16 | 14:28 | 50.016
2021-01-16 | 14:28 | 50.013
2021-01-16 | 14:28 | 50.013
2021-01-16 | 14:28 | 50.009
2021-01-16 | 14:28 | 50.004
2021-01-16 | 14:28 | 50
2021-01-16 | 14:28 | 49.995
2021-01-16 | 14:28 | 49.992
2021-01-16 | 14:28 | 49.983
2021-01-16 | 14:28 | 49.979
2021-01-16 | 14:28 | 49.976
2021-01-16 | 14:28 | 49.974
2021-01-16 | 14:28 | 49.97
2021-01-16 | 14:28 | 49.967
2021-01-16 | 14:28 | 49.965
2021-01-16 | 14:28 | 49.963
2021-01-16 | 14:28 | 49.962
2021-01-16 | 14:28 | 49.962
2021-01-16 | 14:28 | 49.961
2021-01-16 | 14:28 | 49.958
2021-01-16 | 14:28 | 49.96
2021-01-16 | 14:28 | 49.96
2021-01-16 | 14:28 | 49.962
2021-01-16 | 14:28 | 49.966
2021-01-16 | 14:28 | 49.967
2021-01-16 | 14:28 | 49.968
2021-01-16 | 14:28 | 49.969
2021-01-16 | 14:28 | 49.968
2021-01-16 | 14:28 | 49.969
2021-01-16 | 14:28 | 49.971
2021-01-16 | 14:28 | 49.968
2021-01-16 | 14:29 | 49.966
2021-01-16 | 14:29 | 49.964
2021-01-16 | 14:29 | 49.961
2021-01-16 | 14:29 | 49.961
2021-01-16 | 14:29 | 49.96
2021-01-16 | 14:29 | 49.96
2021-01-16 | 14:29 | 49.96
2021-01-16 | 14:29 | 49.957
2021-01-16 | 14:29 | 49.96
2021-01-16 | 14:29 | 49.96
2021-01-16 | 14:29 | 49.959
2021-01-16 | 14:29 | 49.957
2021-01-16 | 14:29 | 49.954
2021-01-16 | 14:29 | 49.953
2021-01-16 | 14:29 | 49.953
2021-01-16 | 14:29 | 49.954
2021-01-16 | 14:29 | 49.956
2021-01-16 | 14:29 | 49.956
2021-01-16 | 14:29 | 49.956
2021-01-16 | 14:29 | 49.957
2021-01-16 | 14:29 | 49.956
2021-01-16 | 14:29 | 49.956
2021-01-16 | 14:29 | 49.955
2021-01-16 | 14:29 | 49.953
2021-01-16 | 14:29 | 49.95
2021-01-16 | 14:29 | 49.945
2021-01-16 | 14:29 | 49.941
2021-01-16 | 14:29 | 49.939
2021-01-16 | 14:29 | 49.938
2021-01-16 | 14:29 | 49.936
2021-01-16 | 14:29 | 49.936
2021-01-16 | 14:29 | 49.935
2021-01-16 | 14:29 | 49.934
2021-01-16 | 14:29 | 49.938
2021-01-16 | 14:29 | 49.939
2021-01-16 | 14:29 | 49.94
2021-01-16 | 14:29 | 49.94
2021-01-16 | 14:29 | 49.939
2021-01-16 | 14:29 | 49.938
2021-01-16 | 14:29 | 49.939
2021-01-16 | 14:29 | 49.938
2021-01-16 | 14:29 | 49.94
2021-01-16 | 14:29 | 49.94
2021-01-16 | 14:29 | 49.941
2021-01-16 | 14:29 | 49.942
2021-01-16 | 14:29 | 49.944
2021-01-16 | 14:29 | 49.945
2021-01-16 | 14:29 | 49.947
2021-01-16 | 14:29 | 49.949
2021-01-16 | 14:29 | 49.952
2021-01-16 | 14:29 | 49.954
2021-01-16 | 14:29 | 49.953
2021-01-16 | 14:29 | 49.954
2021-01-16 | 14:29 | 49.957
2021-01-16 | 14:29 | 49.958
2021-01-16 | 14:29 | 49.958
2021-01-16 | 14:29 | 49.961
2021-01-16 | 14:29 | 49.964
2021-01-16 | 14:29 | 49.965
2021-01-16 | 14:30 | 49.966
2021-01-16 | 14:30 | 49.964
2021-01-16 | 14:30 | 49.962
2021-01-16 | 14:30 | 49.962
2021-01-16 | 14:30 | 49.962
2021-01-16 | 14:30 | 49.959
2021-01-16 | 14:30 | 49.958
2021-01-16 | 14:30 | 49.958
2021-01-16 | 14:30 | 49.954
2021-01-16 | 14:30 | 49.951
2021-01-16 | 14:30 | 49.949
2021-01-16 | 14:30 | 49.945
2021-01-16 | 14:30 | 49.943
2021-01-16 | 14:30 | 49.941
2021-01-16 | 14:30 | 49.938
2021-01-16 | 14:30 | 49.936
2021-01-16 | 14:30 | 49.937
2021-01-16 | 14:30 | 49.938
2021-01-16 | 14:30 | 49.94
2021-01-16 | 14:30 | 49.941
2021-01-16 | 14:30 | 49.942
2021-01-16 | 14:30 | 49.94
2021-01-16 | 14:30 | 49.94
2021-01-16 | 14:30 | 49.94
2021-01-16 | 14:30 | 49.939
2021-01-16 | 14:30 | 49.939
2021-01-16 | 14:30 | 49.94
2021-01-16 | 14:30 | 49.938
2021-01-16 | 14:30 | 49.94
2021-01-16 | 14:30 | 49.941
2021-01-16 | 14:30 | 49.943
2021-01-16 | 14:30 | 49.943
2021-01-16 | 14:30 | 49.94
2021-01-16 | 14:30 | 49.939
2021-01-16 | 14:30 | 49.936
2021-01-16 | 14:30 | 49.934
2021-01-16 | 14:30 | 49.936
2021-01-16 | 14:30 | 49.938
2021-01-16 | 14:30 | 49.937
2021-01-16 | 14:30 | 49.938
2021-01-16 | 14:30 | 49.94
2021-01-16 | 14:30 | 49.938
2021-01-16 | 14:30 | 49.936
2021-01-16 | 14:30 | 49.935
2021-01-16 | 14:30 | 49.931
2021-01-16 | 14:30 | 49.928
2021-01-16 | 14:30 | 49.925
2021-01-16 | 14:30 | 49.923
2021-01-16 | 14:30 | 49.919
2021-01-16 | 14:30 | 49.917
2021-01-16 | 14:30 | 49.915
2021-01-16 | 14:30 | 49.915
2021-01-16 | 14:30 | 49.914
2021-01-16 | 14:30 | 49.918
2021-01-16 | 14:30 | 49.919
2021-01-16 | 14:30 | 49.916
2021-01-16 | 14:30 | 49.916
2021-01-16 | 14:30 | 49.915
2021-01-16 | 14:30 | 49.913
2021-01-16 | 14:30 | 49.914
2021-01-16 | 14:30 | 49.915
2021-01-16 | 14:31 | 49.911
2021-01-16 | 14:31 | 49.91
2021-01-16 | 14:31 | 49.911
2021-01-16 | 14:31 | 49.91
2021-01-16 | 14:31 | 49.91
2021-01-16 | 14:31 | 49.91
2021-01-16 | 14:31 | 49.91
2021-01-16 | 14:31 | 49.911
2021-01-16 | 14:31 | 49.912
2021-01-16 | 14:31 | 49.912
2021-01-16 | 14:31 | 49.911
2021-01-16 | 14:31 | 49.911
2021-01-16 | 14:31 | 49.908
2021-01-16 | 14:31 | 49.908
2021-01-16 | 14:31 | 49.906
2021-01-16 | 14:31 | 49.905
2021-01-16 | 14:31 | 49.905
2021-01-16 | 14:31 | 49.905
2021-01-16 | 14:31 | 49.905
2021-01-16 | 14:31 | 49.909
2021-01-16 | 14:31 | 49.91
2021-01-16 | 14:31 | 49.911
2021-01-16 | 14:31 | 49.914
2021-01-16 | 14:31 | 49.916
2021-01-16 | 14:31 | 49.917
2021-01-16 | 14:31 | 49.917
2021-01-16 | 14:31 | 49.913
2021-01-16 | 14:31 | 49.91
2021-01-16 | 14:31 | 49.907
2021-01-16 | 14:31 | 49.905
2021-01-16 | 14:31 | 49.902
2021-01-16 | 14:31 | 49.9
2021-01-16 | 14:31 | 49.895
2021-01-16 | 14:31 | 49.893
2021-01-16 | 14:31 | 49.889
2021-01-16 | 14:31 | 49.885
2021-01-16 | 14:31 | 49.882
2021-01-16 | 14:31 | 49.879
2021-01-16 | 14:31 | 49.877
2021-01-16 | 14:31 | 49.876
2021-01-16 | 14:31 | 49.877
2021-01-16 | 14:31 | 49.879
2021-01-16 | 14:31 | 49.882
2021-01-16 | 14:31 | 49.88
2021-01-16 | 14:31 | 49.879
2021-01-16 | 14:31 | 49.88
2021-01-16 | 14:31 | 49.878
2021-01-16 | 14:31 | 49.881
2021-01-16 | 14:31 | 49.88
2021-01-16 | 14:31 | 49.88
2021-01-16 | 14:31 | 49.878
2021-01-16 | 14:31 | 49.878
2021-01-16 | 14:31 | 49.88
2021-01-16 | 14:31 | 49.885
2021-01-16 | 14:31 | 49.888
2021-01-16 | 14:31 | 49.891
2021-01-16 | 14:31 | 49.895
2021-01-16 | 14:31 | 49.898
2021-01-16 | 14:31 | 49.901
2021-01-16 | 14:32 | 49.904
2021-01-16 | 14:32 | 49.905
2021-01-16 | 14:32 | 49.906
2021-01-16 | 14:32 | 49.906
2021-01-16 | 14:32 | 49.902
2021-01-16 | 14:32 | 49.902
2021-01-16 | 14:32 | 49.9
2021-01-16 | 14:32 | 49.898
2021-01-16 | 14:32 | 49.898
2021-01-16 | 14:32 | 49.894
2021-01-16 | 14:32 | 49.891
2021-01-16 | 14:32 | 49.891
2021-01-16 | 14:32 | 49.892
2021-01-16 | 14:32 | 49.893
2021-01-16 | 14:32 | 49.893
2021-01-16 | 14:32 | 49.892
2021-01-16 | 14:32 | 49.894
2021-01-16 | 14:32 | 49.893
2021-01-16 | 14:32 | 49.89
2021-01-16 | 14:32 | 49.89
2021-01-16 | 14:32 | 49.888
2021-01-16 | 14:32 | 49.887
2021-01-16 | 14:32 | 49.884
2021-01-16 | 14:32 | 49.882
2021-01-16 | 14:32 | 49.881
2021-01-16 | 14:32 | 49.88
2021-01-16 | 14:32 | 49.879
2021-01-16 | 14:32 | 49.88
2021-01-16 | 14:32 | 49.879
2021-01-16 | 14:32 | 49.878
2021-01-16 | 14:32 | 49.879
2021-01-16 | 14:32 | 49.875
2021-01-16 | 14:32 | 49.872
2021-01-16 | 14:32 | 49.87
2021-01-16 | 14:32 | 49.868
2021-01-16 | 14:32 | 49.867
2021-01-16 | 14:32 | 49.868
2021-01-16 | 14:32 | 49.867
2021-01-16 | 14:32 | 49.869
2021-01-16 | 14:32 | 49.867
2021-01-16 | 14:32 | 49.865
2021-01-16 | 14:32 | 49.864
2021-01-16 | 14:32 | 49.864
2021-01-16 | 14:32 | 49.866
2021-01-16 | 14:32 | 49.867
2021-01-16 | 14:32 | 49.867
2021-01-16 | 14:32 | 49.869
2021-01-16 | 14:32 | 49.872
2021-01-16 | 14:32 | 49.876
2021-01-16 | 14:32 | 49.879
2021-01-16 | 14:32 | 49.881
2021-01-16 | 14:32 | 49.883
2021-01-16 | 14:32 | 49.883
2021-01-16 | 14:32 | 49.881
2021-01-16 | 14:32 | 49.883
2021-01-16 | 14:32 | 49.883
2021-01-16 | 14:32 | 49.885
2021-01-16 | 14:32 | 49.887
2021-01-16 | 14:32 | 49.888
2021-01-16 | 14:32 | 49.889
2021-01-16 | 14:32 | 49.888
2021-01-16 | 14:33 | 49.886
2021-01-16 | 14:33 | 49.885
2021-01-16 | 14:33 | 49.884
2021-01-16 | 14:33 | 49.884
2021-01-16 | 14:33 | 49.882
2021-01-16 | 14:33 | 49.881
2021-01-16 | 14:33 | 49.881
2021-01-16 | 14:33 | 49.882
2021-01-16 | 14:33 | 49.882
2021-01-16 | 14:33 | 49.885
2021-01-16 | 14:33 | 49.887
2021-01-16 | 14:33 | 49.886
2021-01-16 | 14:33 | 49.885
2021-01-16 | 14:33 | 49.885
2021-01-16 | 14:33 | 49.883
2021-01-16 | 14:33 | 49.883
2021-01-16 | 14:33 | 49.882
2021-01-16 | 14:33 | 49.881
2021-01-16 | 14:33 | 49.883
2021-01-16 | 14:33 | 49.883
2021-01-16 | 14:33 | 49.882
2021-01-16 | 14:33 | 49.883
2021-01-16 | 14:33 | 49.883
2021-01-16 | 14:33 | 49.883
2021-01-16 | 14:33 | 49.883
2021-01-16 | 14:33 | 49.88
2021-01-16 | 14:33 | 49.877
2021-01-16 | 14:33 | 49.876
2021-01-16 | 14:33 | 49.876
2021-01-16 | 14:33 | 49.876
2021-01-16 | 14:33 | 49.876
2021-01-16 | 14:33 | 49.875
2021-01-16 | 14:33 | 49.876
2021-01-16 | 14:33 | 49.874
2021-01-16 | 14:33 | 49.874
2021-01-16 | 14:33 | 49.874
2021-01-16 | 14:33 | 49.873
2021-01-16 | 14:33 | 49.872
2021-01-16 | 14:33 | 49.872
2021-01-16 | 14:33 | 49.872
2021-01-16 | 14:33 | 49.872
2021-01-16 | 14:33 | 49.874
2021-01-16 | 14:33 | 49.876
2021-01-16 | 14:33 | 49.878
2021-01-16 | 14:33 | 49.879
2021-01-16 | 14:33 | 49.882
2021-01-16 | 14:33 | 49.884
2021-01-16 | 14:33 | 49.886
2021-01-16 | 14:33 | 49.89
2021-01-16 | 14:33 | 49.892
2021-01-16 | 14:33 | 49.894
2021-01-16 | 14:33 | 49.895
2021-01-16 | 14:33 | 49.897
2021-01-16 | 14:33 | 49.898
2021-01-16 | 14:33 | 49.899
2021-01-16 | 14:33 | 49.902
2021-01-16 | 14:33 | 49.903
2021-01-16 | 14:33 | 49.904
2021-01-16 | 14:33 | 49.902
2021-01-16 | 14:34 | 49.902
2021-01-16 | 14:34 | 49.901
2021-01-16 | 14:34 | 49.898
2021-01-16 | 14:34 | 49.898
2021-01-16 | 14:34 | 49.898
2021-01-16 | 14:34 | 49.896
2021-01-16 | 14:34 | 49.895
2021-01-16 | 14:34 | 49.897
2021-01-16 | 14:34 | 49.899
2021-01-16 | 14:34 | 49.9
2021-01-16 | 14:34 | 49.9
2021-01-16 | 14:34 | 49.901
2021-01-16 | 14:34 | 49.899
2021-01-16 | 14:34 | 49.898
2021-01-16 | 14:34 | 49.895
2021-01-16 | 14:34 | 49.888
2021-01-16 | 14:34 | 49.884
2021-01-16 | 14:34 | 49.881
2021-01-16 | 14:34 | 49.877
2021-01-16 | 14:34 | 49.877
2021-01-16 | 14:34 | 49.876
2021-01-16 | 14:34 | 49.874
2021-01-16 | 14:34 | 49.871
2021-01-16 | 14:34 | 49.873
2021-01-16 | 14:34 | 49.875
2021-01-16 | 14:34 | 49.879
2021-01-16 | 14:34 | 49.879
2021-01-16 | 14:34 | 49.88
2021-01-16 | 14:34 | 49.882
2021-01-16 | 14:34 | 49.885
2021-01-16 | 14:34 | 49.887
2021-01-16 | 14:34 | 49.889
2021-01-16 | 14:34 | 49.889
2021-01-16 | 14:34 | 49.891
2021-01-16 | 14:34 | 49.888
2021-01-16 | 14:34 | 49.887
2021-01-16 | 14:34 | 49.885
2021-01-16 | 14:34 | 49.884
2021-01-16 | 14:34 | 49.881
2021-01-16 | 14:34 | 49.878
2021-01-16 | 14:34 | 49.876
2021-01-16 | 14:34 | 49.873
2021-01-16 | 14:34 | 49.869
2021-01-16 | 14:34 | 49.865
2021-01-16 | 14:34 | 49.865
2021-01-16 | 14:34 | 49.86
2021-01-16 | 14:34 | 49.855
2021-01-16 | 14:34 | 49.854
2021-01-16 | 14:34 | 49.854
2021-01-16 | 14:34 | 49.852
2021-01-16 | 14:34 | 49.85
2021-01-16 | 14:34 | 49.85
2021-01-16 | 14:34 | 49.852
2021-01-16 | 14:34 | 49.851
2021-01-16 | 14:34 | 49.851
2021-01-16 | 14:34 | 49.853
2021-01-16 | 14:34 | 49.853
2021-01-16 | 14:34 | 49.853
2021-01-16 | 14:34 | 49.851
2021-01-16 | 14:34 | 49.85
2021-01-16 | 14:34 | 49.848
2021-01-16 | 14:35 | 49.846
2021-01-16 | 14:35 | 49.843
2021-01-16 | 14:35 | 49.841
2021-01-16 | 14:35 | 49.839
2021-01-16 | 14:35 | 49.839
2021-01-16 | 14:35 | 49.84
2021-01-16 | 14:35 | 49.842
2021-01-16 | 14:35 | 49.842
2021-01-16 | 14:35 | 49.845
2021-01-16 | 14:35 | 49.846
2021-01-16 | 14:35 | 49.847
2021-01-16 | 14:35 | 49.85
2021-01-16 | 14:35 | 49.849
2021-01-16 | 14:35 | 49.851
2021-01-16 | 14:35 | 49.848
2021-01-16 | 14:35 | 49.846
2021-01-16 | 14:35 | 49.843
2021-01-16 | 14:35 | 49.839
2021-01-16 | 14:35 | 49.837
2021-01-16 | 14:35 | 49.835
2021-01-16 | 14:35 | 49.832
2021-01-16 | 14:35 | 49.827
2021-01-16 | 14:35 | 49.822
2021-01-16 | 14:35 | 49.821
2021-01-16 | 14:35 | 49.817
2021-01-16 | 14:35 | 49.816
2021-01-16 | 14:35 | 49.815
2021-01-16 | 14:35 | 49.815
2021-01-16 | 14:35 | 49.817
2021-01-16 | 14:35 | 49.816
2021-01-16 | 14:35 | 49.818
2021-01-16 | 14:35 | 49.822
2021-01-16 | 14:35 | 49.824
2021-01-16 | 14:35 | 49.828
2021-01-16 | 14:35 | 49.831
2021-01-16 | 14:35 | 49.835
2021-01-16 | 14:35 | 49.84
2021-01-16 | 14:35 | 49.845
2021-01-16 | 14:35 | 49.855
2021-01-16 | 14:35 | 49.863
2021-01-16 | 14:35 | 49.869
2021-01-16 | 14:35 | 49.874
2021-01-16 | 14:35 | 49.874
2021-01-16 | 14:35 | 49.875
2021-01-16 | 14:35 | 49.874
2021-01-16 | 14:35 | 49.874
2021-01-16 | 14:35 | 49.874
2021-01-16 | 14:35 | 49.875
2021-01-16 | 14:35 | 49.876
2021-01-16 | 14:35 | 49.877
2021-01-16 | 14:35 | 49.881
2021-01-16 | 14:35 | 49.884
2021-01-16 | 14:35 | 49.888
2021-01-16 | 14:35 | 49.888
2021-01-16 | 14:35 | 49.886
2021-01-16 | 14:35 | 49.887
2021-01-16 | 14:35 | 49.889
2021-01-16 | 14:35 | 49.888
2021-01-16 | 14:35 | 49.886
2021-01-16 | 14:36 | 49.887
2021-01-16 | 14:36 | 49.886
2021-01-16 | 14:36 | 49.885
2021-01-16 | 14:36 | 49.888
2021-01-16 | 14:36 | 49.887
2021-01-16 | 14:36 | 49.888
2021-01-16 | 14:36 | 49.89
2021-01-16 | 14:36 | 49.89
2021-01-16 | 14:36 | 49.891
2021-01-16 | 14:36 | 49.889
2021-01-16 | 14:36 | 49.888
2021-01-16 | 14:36 | 49.886
2021-01-16 | 14:36 | 49.886
2021-01-16 | 14:36 | 49.885
2021-01-16 | 14:36 | 49.884
2021-01-16 | 14:36 | 49.884
2021-01-16 | 14:36 | 49.884
2021-01-16 | 14:36 | 49.886
2021-01-16 | 14:36 | 49.887
2021-01-16 | 14:36 | 49.887
2021-01-16 | 14:36 | 49.889
2021-01-16 | 14:36 | 49.89
2021-01-16 | 14:36 | 49.89
2021-01-16 | 14:36 | 49.893
2021-01-16 | 14:36 | 49.894
2021-01-16 | 14:36 | 49.897
2021-01-16 | 14:36 | 49.901
2021-01-16 | 14:36 | 49.904
2021-01-16 | 14:36 | 49.905
2021-01-16 | 14:36 | 49.905
2021-01-16 | 14:36 | 49.903
2021-01-16 | 14:36 | 49.901
2021-01-16 | 14:36 | 49.9
2021-01-16 | 14:36 | 49.898
2021-01-16 | 14:36 | 49.897
2021-01-16 | 14:36 | 49.893
2021-01-16 | 14:36 | 49.89
2021-01-16 | 14:36 | 49.886
2021-01-16 | 14:36 | 49.886
2021-01-16 | 14:36 | 49.887
2021-01-16 | 14:36 | 49.89
2021-01-16 | 14:36 | 49.892
2021-01-16 | 14:36 | 49.893
2021-01-16 | 14:36 | 49.897
2021-01-16 | 14:36 | 49.9
2021-01-16 | 14:36 | 49.903
2021-01-16 | 14:36 | 49.903
2021-01-16 | 14:36 | 49.903
2021-01-16 | 14:36 | 49.901
2021-01-16 | 14:36 | 49.9
2021-01-16 | 14:36 | 49.9
2021-01-16 | 14:36 | 49.902
2021-01-16 | 14:36 | 49.905
2021-01-16 | 14:36 | 49.913
2021-01-16 | 14:36 | 49.915
2021-01-16 | 14:36 | 49.917
2021-01-16 | 14:36 | 49.915
2021-01-16 | 14:36 | 49.917
2021-01-16 | 14:36 | 49.917
2021-01-16 | 14:36 | 49.919
2021-01-16 | 14:36 | 49.925
2021-01-16 | 14:37 | 49.927
2021-01-16 | 14:37 | 49.931
2021-01-16 | 14:37 | 49.936
2021-01-16 | 14:37 | 49.945
2021-01-16 | 14:37 | 49.954
2021-01-16 | 14:37 | 49.962
2021-01-16 | 14:37 | 49.969
2021-01-16 | 14:37 | 49.978
2021-01-16 | 14:37 | 49.984
2021-01-16 | 14:37 | 49.986
2021-01-16 | 14:37 | 49.986
2021-01-16 | 14:37 | 49.983
2021-01-16 | 14:37 | 49.981
2021-01-16 | 14:37 | 49.978
2021-01-16 | 14:37 | 49.976
2021-01-16 | 14:37 | 49.972
2021-01-16 | 14:37 | 49.968
2021-01-16 | 14:37 | 49.963
2021-01-16 | 14:37 | 49.96
2021-01-16 | 14:37 | 49.957
2021-01-16 | 14:37 | 49.958
2021-01-16 | 14:37 | 49.958
2021-01-16 | 14:37 | 49.958
2021-01-16 | 14:37 | 49.958
2021-01-16 | 14:37 | 49.959
2021-01-16 | 14:37 | 49.962
2021-01-16 | 14:37 | 49.962
2021-01-16 | 14:37 | 49.963
2021-01-16 | 14:37 | 49.964
2021-01-16 | 14:37 | 49.966
2021-01-16 | 14:37 | 49.969
2021-01-16 | 14:37 | 49.972
2021-01-16 | 14:37 | 49.974
2021-01-16 | 14:37 | 49.977
2021-01-16 | 14:37 | 49.977
2021-01-16 | 14:37 | 49.976
2021-01-16 | 14:37 | 49.977
2021-01-16 | 14:37 | 49.976
2021-01-16 | 14:37 | 49.974
2021-01-16 | 14:37 | 49.976
2021-01-16 | 14:37 | 49.976
2021-01-16 | 14:37 | 49.976
2021-01-16 | 14:37 | 49.974
2021-01-16 | 14:37 | 49.972
2021-01-16 | 14:37 | 49.97
2021-01-16 | 14:37 | 49.97
2021-01-16 | 14:37 | 49.971
2021-01-16 | 14:37 | 49.973
2021-01-16 | 14:37 | 49.974
2021-01-16 | 14:37 | 49.978
2021-01-16 | 14:37 | 49.979
2021-01-16 | 14:37 | 49.98
2021-01-16 | 14:37 | 49.981
2021-01-16 | 14:37 | 49.982
2021-01-16 | 14:37 | 49.982
2021-01-16 | 14:37 | 49.983
2021-01-16 | 14:37 | 49.985
2021-01-16 | 14:37 | 49.987
2021-01-16 | 14:37 | 49.988
2021-01-16 | 14:38 | 49.991
2021-01-16 | 14:38 | 49.993
2021-01-16 | 14:38 | 49.997
2021-01-16 | 14:38 | 49.999
2021-01-16 | 14:38 | 50.001
2021-01-16 | 14:38 | 50
2021-01-16 | 14:38 | 49.999
2021-01-16 | 14:38 | 50
2021-01-16 | 14:38 | 50.001
2021-01-16 | 14:38 | 50.002
2021-01-16 | 14:38 | 50.002
2021-01-16 | 14:38 | 50.001
2021-01-16 | 14:38 | 50.001
2021-01-16 | 14:38 | 50
2021-01-16 | 14:38 | 49.998
2021-01-16 | 14:38 | 49.997
2021-01-16 | 14:38 | 49.995
2021-01-16 | 14:38 | 49.992
2021-01-16 | 14:38 | 49.987
2021-01-16 | 14:38 | 49.982
2021-01-16 | 14:38 | 49.976
2021-01-16 | 14:38 | 49.976
2021-01-16 | 14:38 | 49.976
2021-01-16 | 14:38 | 49.975
2021-01-16 | 14:38 | 49.976
2021-01-16 | 14:38 | 49.975
2021-01-16 | 14:38 | 49.976
2021-01-16 | 14:38 | 49.978
2021-01-16 | 14:38 | 49.978
2021-01-16 | 14:38 | 49.977
2021-01-16 | 14:38 | 49.976
2021-01-16 | 14:38 | 49.974
2021-01-16 | 14:38 | 49.97
2021-01-16 | 14:38 | 49.969
2021-01-16 | 14:38 | 49.965
2021-01-16 | 14:38 | 49.965
2021-01-16 | 14:38 | 49.965
2021-01-16 | 14:38 | 49.965
2021-01-16 | 14:38 | 49.965
2021-01-16 | 14:38 | 49.966
2021-01-16 | 14:38 | 49.966
2021-01-16 | 14:38 | 49.967
2021-01-16 | 14:38 | 49.969
2021-01-16 | 14:38 | 49.971
2021-01-16 | 14:38 | 49.973
2021-01-16 | 14:38 | 49.974
2021-01-16 | 14:38 | 49.979
2021-01-16 | 14:38 | 49.983
2021-01-16 | 14:38 | 49.988
2021-01-16 | 14:38 | 49.99
2021-01-16 | 14:38 | 49.989
2021-01-16 | 14:38 | 49.99
2021-01-16 | 14:38 | 49.987
2021-01-16 | 14:38 | 49.986
2021-01-16 | 14:38 | 49.98
2021-01-16 | 14:38 | 49.981
2021-01-16 | 14:38 | 49.979
2021-01-16 | 14:38 | 49.976
2021-01-16 | 14:38 | 49.973
2021-01-16 | 14:38 | 49.971
2021-01-16 | 14:38 | 49.97
2021-01-16 | 14:39 | 49.966
2021-01-16 | 14:39 | 49.968
2021-01-16 | 14:39 | 49.967
2021-01-16 | 14:39 | 49.966
2021-01-16 | 14:39 | 49.969
2021-01-16 | 14:39 | 49.968
2021-01-16 | 14:39 | 49.966
2021-01-16 | 14:39 | 49.965
2021-01-16 | 14:39 | 49.968
2021-01-16 | 14:39 | 49.965
2021-01-16 | 14:39 | 49.966
2021-01-16 | 14:39 | 49.966
2021-01-16 | 14:39 | 49.964
2021-01-16 | 14:39 | 49.965
2021-01-16 | 14:39 | 49.964
2021-01-16 | 14:39 | 49.966
2021-01-16 | 14:39 | 49.967
2021-01-16 | 14:39 | 49.966
2021-01-16 | 14:39 | 49.965
2021-01-16 | 14:39 | 49.962
2021-01-16 | 14:39 | 49.962
2021-01-16 | 14:39 | 49.96
2021-01-16 | 14:39 | 49.961
2021-01-16 | 14:39 | 49.962
2021-01-16 | 14:39 | 49.963
2021-01-16 | 14:39 | 49.962
2021-01-16 | 14:39 | 49.962
2021-01-16 | 14:39 | 49.965
2021-01-16 | 14:39 | 49.969
2021-01-16 | 14:39 | 49.975
2021-01-16 | 14:39 | 49.976
2021-01-16 | 14:39 | 49.978
2021-01-16 | 14:39 | 49.976
2021-01-16 | 14:39 | 49.975
2021-01-16 | 14:39 | 49.971
2021-01-16 | 14:39 | 49.969
2021-01-16 | 14:39 | 49.965
2021-01-16 | 14:39 | 49.965
2021-01-16 | 14:39 | 49.965
2021-01-16 | 14:39 | 49.963
2021-01-16 | 14:39 | 49.963
2021-01-16 | 14:39 | 49.965
2021-01-16 | 14:39 | 49.966
2021-01-16 | 14:39 | 49.965
2021-01-16 | 14:39 | 49.964
2021-01-16 | 14:39 | 49.965
2021-01-16 | 14:39 | 49.966
2021-01-16 | 14:39 | 49.966
2021-01-16 | 14:39 | 49.964
2021-01-16 | 14:39 | 49.961
2021-01-16 | 14:39 | 49.96
2021-01-16 | 14:39 | 49.961
2021-01-16 | 14:39 | 49.962
2021-01-16 | 14:39 | 49.963
2021-01-16 | 14:39 | 49.962
2021-01-16 | 14:39 | 49.963
2021-01-16 | 14:39 | 49.964
2021-01-16 | 14:39 | 49.964
2021-01-16 | 14:39 | 49.964
2021-01-16 | 14:40 | 49.964
2021-01-16 | 14:40 | 49.961
2021-01-16 | 14:40 | 49.961
2021-01-16 | 14:40 | 49.961
2021-01-16 | 14:40 | 49.962
2021-01-16 | 14:40 | 49.965
2021-01-16 | 14:40 | 49.965
2021-01-16 | 14:40 | 49.965
2021-01-16 | 14:40 | 49.965
2021-01-16 | 14:40 | 49.964
2021-01-16 | 14:40 | 49.961
2021-01-16 | 14:40 | 49.958
2021-01-16 | 14:40 | 49.955
2021-01-16 | 14:40 | 49.953
2021-01-16 | 14:40 | 49.949
2021-01-16 | 14:40 | 49.947
2021-01-16 | 14:40 | 49.949
2021-01-16 | 14:40 | 49.95
2021-01-16 | 14:40 | 49.95
2021-01-16 | 14:40 | 49.949
2021-01-16 | 14:40 | 49.946
2021-01-16 | 14:40 | 49.946
2021-01-16 | 14:40 | 49.945
2021-01-16 | 14:40 | 49.945
2021-01-16 | 14:40 | 49.944
2021-01-16 | 14:40 | 49.941
2021-01-16 | 14:40 | 49.937
2021-01-16 | 14:40 | 49.936
2021-01-16 | 14:40 | 49.933
2021-01-16 | 14:40 | 49.931
2021-01-16 | 14:40 | 49.931
2021-01-16 | 14:40 | 49.932
2021-01-16 | 14:40 | 49.931
2021-01-16 | 14:40 | 49.932
2021-01-16 | 14:40 | 49.93
2021-01-16 | 14:40 | 49.932
2021-01-16 | 14:40 | 49.932
2021-01-16 | 14:40 | 49.932
2021-01-16 | 14:40 | 49.928
2021-01-16 | 14:40 | 49.922
2021-01-16 | 14:40 | 49.924
2021-01-16 | 14:40 | 49.92
2021-01-16 | 14:40 | 49.919
2021-01-16 | 14:40 | 49.917
2021-01-16 | 14:40 | 49.916
2021-01-16 | 14:40 | 49.915
2021-01-16 | 14:40 | 49.914
2021-01-16 | 14:40 | 49.913
2021-01-16 | 14:40 | 49.913
2021-01-16 | 14:40 | 49.916
2021-01-16 | 14:40 | 49.918
2021-01-16 | 14:40 | 49.919
2021-01-16 | 14:40 | 49.918
2021-01-16 | 14:40 | 49.916
2021-01-16 | 14:40 | 49.916
2021-01-16 | 14:40 | 49.916
2021-01-16 | 14:40 | 49.917
2021-01-16 | 14:40 | 49.917
2021-01-16 | 14:40 | 49.917
2021-01-16 | 14:40 | 49.914
2021-01-16 | 14:40 | 49.913
2021-01-16 | 14:41 | 49.915
2021-01-16 | 14:41 | 49.918
2021-01-16 | 14:41 | 49.919
2021-01-16 | 14:41 | 49.919
2021-01-16 | 14:41 | 49.918
2021-01-16 | 14:41 | 49.916
2021-01-16 | 14:41 | 49.916
2021-01-16 | 14:41 | 49.917
2021-01-16 | 14:41 | 49.916
2021-01-16 | 14:41 | 49.914
2021-01-16 | 14:41 | 49.914
2021-01-16 | 14:41 | 49.916
2021-01-16 | 14:41 | 49.916
2021-01-16 | 14:41 | 49.916
2021-01-16 | 14:41 | 49.915
2021-01-16 | 14:41 | 49.913
2021-01-16 | 14:41 | 49.913
2021-01-16 | 14:41 | 49.913
2021-01-16 | 14:41 | 49.914
2021-01-16 | 14:41 | 49.915
2021-01-16 | 14:41 | 49.916
2021-01-16 | 14:41 | 49.914
2021-01-16 | 14:41 | 49.914
2021-01-16 | 14:41 | 49.912
2021-01-16 | 14:41 | 49.914
2021-01-16 | 14:41 | 49.917
2021-01-16 | 14:41 | 49.921
2021-01-16 | 14:41 | 49.924
2021-01-16 | 14:41 | 49.926
2021-01-16 | 14:41 | 49.927
2021-01-16 | 14:41 | 49.929
2021-01-16 | 14:41 | 49.931
2021-01-16 | 14:41 | 49.931
2021-01-16 | 14:41 | 49.931
2021-01-16 | 14:41 | 49.932
2021-01-16 | 14:41 | 49.933
2021-01-16 | 14:41 | 49.933
2021-01-16 | 14:41 | 49.936
2021-01-16 | 14:41 | 49.938
2021-01-16 | 14:41 | 49.94
2021-01-16 | 14:41 | 49.939
2021-01-16 | 14:41 | 49.941
2021-01-16 | 14:41 | 49.938
2021-01-16 | 14:41 | 49.936
2021-01-16 | 14:41 | 49.938
2021-01-16 | 14:41 | 49.94
2021-01-16 | 14:41 | 49.94
2021-01-16 | 14:41 | 49.938
2021-01-16 | 14:41 | 49.94
2021-01-16 | 14:41 | 49.94
2021-01-16 | 14:41 | 49.94
2021-01-16 | 14:41 | 49.941
2021-01-16 | 14:41 | 49.942
2021-01-16 | 14:41 | 49.942
2021-01-16 | 14:41 | 49.944
2021-01-16 | 14:41 | 49.948
2021-01-16 | 14:41 | 49.95
2021-01-16 | 14:41 | 49.952
2021-01-16 | 14:41 | 49.955
2021-01-16 | 14:42 | 49.957
2021-01-16 | 14:42 | 49.959
2021-01-16 | 14:42 | 49.962
2021-01-16 | 14:42 | 49.963
2021-01-16 | 14:42 | 49.961
2021-01-16 | 14:42 | 49.96
2021-01-16 | 14:42 | 49.957
2021-01-16 | 14:42 | 49.953
2021-01-16 | 14:42 | 49.953
2021-01-16 | 14:42 | 49.95
2021-01-16 | 14:42 | 49.949
2021-01-16 | 14:42 | 49.945
2021-01-16 | 14:42 | 49.944
2021-01-16 | 14:42 | 49.94
2021-01-16 | 14:42 | 49.939
2021-01-16 | 14:42 | 49.939
2021-01-16 | 14:42 | 49.938
2021-01-16 | 14:42 | 49.941
2021-01-16 | 14:42 | 49.943
2021-01-16 | 14:42 | 49.946
2021-01-16 | 14:42 | 49.947
2021-01-16 | 14:42 | 49.944
2021-01-16 | 14:42 | 49.943
2021-01-16 | 14:42 | 49.942
2021-01-16 | 14:42 | 49.941
2021-01-16 | 14:42 | 49.941
2021-01-16 | 14:42 | 49.938
2021-01-16 | 14:42 | 49.936
2021-01-16 | 14:42 | 49.934
2021-01-16 | 14:42 | 49.934
2021-01-16 | 14:42 | 49.933
2021-01-16 | 14:42 | 49.93
2021-01-16 | 14:42 | 49.929
2021-01-16 | 14:42 | 49.928
2021-01-16 | 14:42 | 49.926
2021-01-16 | 14:42 | 49.924
2021-01-16 | 14:42 | 49.922
2021-01-16 | 14:42 | 49.919
2021-01-16 | 14:42 | 49.921
2021-01-16 | 14:42 | 49.92
2021-01-16 | 14:42 | 49.918
2021-01-16 | 14:42 | 49.916
2021-01-16 | 14:42 | 49.916
2021-01-16 | 14:42 | 49.915
2021-01-16 | 14:42 | 49.916
2021-01-16 | 14:42 | 49.917
2021-01-16 | 14:42 | 49.918
2021-01-16 | 14:42 | 49.919
2021-01-16 | 14:42 | 49.919
2021-01-16 | 14:42 | 49.918
2021-01-16 | 14:42 | 49.917
2021-01-16 | 14:42 | 49.917
2021-01-16 | 14:42 | 49.916
2021-01-16 | 14:42 | 49.916
2021-01-16 | 14:42 | 49.912
2021-01-16 | 14:42 | 49.909
2021-01-16 | 14:42 | 49.909
2021-01-16 | 14:42 | 49.909
2021-01-16 | 14:42 | 49.91
2021-01-16 | 14:42 | 49.912
2021-01-16 | 14:42 | 49.912
2021-01-16 | 14:43 | 49.914
2021-01-16 | 14:43 | 49.916
2021-01-16 | 14:43 | 49.921
2021-01-16 | 14:43 | 49.922
2021-01-16 | 14:43 | 49.923
2021-01-16 | 14:43 | 49.923
2021-01-16 | 14:43 | 49.924
2021-01-16 | 14:43 | 49.925
2021-01-16 | 14:43 | 49.926
2021-01-16 | 14:43 | 49.924
2021-01-16 | 14:43 | 49.924
2021-01-16 | 14:43 | 49.927
2021-01-16 | 14:43 | 49.925
2021-01-16 | 14:43 | 49.924
2021-01-16 | 14:43 | 49.924
2021-01-16 | 14:43 | 49.926
2021-01-16 | 14:43 | 49.928
2021-01-16 | 14:43 | 49.932
2021-01-16 | 14:43 | 49.932
2021-01-16 | 14:43 | 49.936
2021-01-16 | 14:43 | 49.937
2021-01-16 | 14:43 | 49.938
2021-01-16 | 14:43 | 49.939
2021-01-16 | 14:43 | 49.941
2021-01-16 | 14:43 | 49.944
2021-01-16 | 14:43 | 49.946
2021-01-16 | 14:43 | 49.95
2021-01-16 | 14:43 | 49.954
2021-01-16 | 14:43 | 49.954
2021-01-16 | 14:43 | 49.954
2021-01-16 | 14:43 | 49.953
2021-01-16 | 14:43 | 49.951
2021-01-16 | 14:43 | 49.953
2021-01-16 | 14:43 | 49.951
2021-01-16 | 14:43 | 49.951
2021-01-16 | 14:43 | 49.95
2021-01-16 | 14:43 | 49.95
2021-01-16 | 14:43 | 49.948
2021-01-16 | 14:43 | 49.949
2021-01-16 | 14:43 | 49.948
2021-01-16 | 14:43 | 49.945
2021-01-16 | 14:43 | 49.947
2021-01-16 | 14:43 | 49.946
2021-01-16 | 14:43 | 49.948
2021-01-16 | 14:43 | 49.95
2021-01-16 | 14:43 | 49.95
2021-01-16 | 14:43 | 49.948
2021-01-16 | 14:43 | 49.949
2021-01-16 | 14:43 | 49.948
2021-01-16 | 14:43 | 49.948
2021-01-16 | 14:43 | 49.948
2021-01-16 | 14:43 | 49.948
2021-01-16 | 14:43 | 49.953
2021-01-16 | 14:43 | 49.955
2021-01-16 | 14:43 | 49.956
2021-01-16 | 14:43 | 49.955
2021-01-16 | 14:43 | 49.957
2021-01-16 | 14:43 | 49.956
2021-01-16 | 14:43 | 49.957
2021-01-16 | 14:44 | 49.955
2021-01-16 | 14:44 | 49.955
2021-01-16 | 14:44 | 49.954
2021-01-16 | 14:44 | 49.953
2021-01-16 | 14:44 | 49.95
2021-01-16 | 14:44 | 49.951
2021-01-16 | 14:44 | 49.95
2021-01-16 | 14:44 | 49.945
2021-01-16 | 14:44 | 49.946
2021-01-16 | 14:44 | 49.943
2021-01-16 | 14:44 | 49.942
2021-01-16 | 14:44 | 49.943
2021-01-16 | 14:44 | 49.945
2021-01-16 | 14:44 | 49.947
2021-01-16 | 14:44 | 49.947
2021-01-16 | 14:44 | 49.947
2021-01-16 | 14:44 | 49.949
2021-01-16 | 14:44 | 49.951
2021-01-16 | 14:44 | 49.951
2021-01-16 | 14:44 | 49.952
2021-01-16 | 14:44 | 49.949
2021-01-16 | 14:44 | 49.949
2021-01-16 | 14:44 | 49.948
2021-01-16 | 14:44 | 49.948
2021-01-16 | 14:44 | 49.948
2021-01-16 | 14:44 | 49.945
2021-01-16 | 14:44 | 49.944
2021-01-16 | 14:44 | 49.94
2021-01-16 | 14:44 | 49.937
2021-01-16 | 14:44 | 49.935
2021-01-16 | 14:44 | 49.934
2021-01-16 | 14:44 | 49.933
2021-01-16 | 14:44 | 49.931
2021-01-16 | 14:44 | 49.933
2021-01-16 | 14:44 | 49.933
2021-01-16 | 14:44 | 49.935
2021-01-16 | 14:44 | 49.938
2021-01-16 | 14:44 | 49.941
2021-01-16 | 14:44 | 49.945
2021-01-16 | 14:44 | 49.948
2021-01-16 | 14:44 | 49.95
2021-01-16 | 14:44 | 49.954
2021-01-16 | 14:44 | 49.954
2021-01-16 | 14:44 | 49.954
2021-01-16 | 14:44 | 49.954
2021-01-16 | 14:44 | 49.953
2021-01-16 | 14:44 | 49.95
2021-01-16 | 14:44 | 49.948
2021-01-16 | 14:44 | 49.949
2021-01-16 | 14:44 | 49.947
2021-01-16 | 14:44 | 49.946
2021-01-16 | 14:44 | 49.944
2021-01-16 | 14:44 | 49.942
2021-01-16 | 14:44 | 49.942
2021-01-16 | 14:44 | 49.943
2021-01-16 | 14:44 | 49.945
2021-01-16 | 14:44 | 49.946
2021-01-16 | 14:44 | 49.945
2021-01-16 | 14:44 | 49.947
2021-01-16 | 14:44 | 49.945
2021-01-16 | 14:44 | 49.945
2021-01-16 | 14:45 | 49.944
2021-01-16 | 14:45 | 49.943
2021-01-16 | 14:45 | 49.943
2021-01-16 | 14:45 | 49.94
2021-01-16 | 14:45 | 49.938
2021-01-16 | 14:45 | 49.937
2021-01-16 | 14:45 | 49.934
2021-01-16 | 14:45 | 49.931
2021-01-16 | 14:45 | 49.928
2021-01-16 | 14:45 | 49.926
2021-01-16 | 14:45 | 49.924
2021-01-16 | 14:45 | 49.923
2021-01-16 | 14:45 | 49.92
2021-01-16 | 14:45 | 49.92
2021-01-16 | 14:45 | 49.92
2021-01-16 | 14:45 | 49.92
2021-01-16 | 14:45 | 49.918
2021-01-16 | 14:45 | 49.919
2021-01-16 | 14:45 | 49.919
2021-01-16 | 14:45 | 49.919
2021-01-16 | 14:45 | 49.919
2021-01-16 | 14:45 | 49.917
2021-01-16 | 14:45 | 49.917
2021-01-16 | 14:45 | 49.918
2021-01-16 | 14:45 | 49.917
2021-01-16 | 14:45 | 49.917
2021-01-16 | 14:45 | 49.918
2021-01-16 | 14:45 | 49.916
2021-01-16 | 14:45 | 49.915
2021-01-16 | 14:45 | 49.913
2021-01-16 | 14:45 | 49.912
2021-01-16 | 14:45 | 49.909
2021-01-16 | 14:45 | 49.908
2021-01-16 | 14:45 | 49.909
2021-01-16 | 14:45 | 49.91
2021-01-16 | 14:45 | 49.911
2021-01-16 | 14:45 | 49.913
2021-01-16 | 14:45 | 49.912
2021-01-16 | 14:45 | 49.913
2021-01-16 | 14:45 | 49.914
2021-01-16 | 14:45 | 49.917
2021-01-16 | 14:45 | 49.919
2021-01-16 | 14:45 | 49.921
2021-01-16 | 14:45 | 49.92
2021-01-16 | 14:45 | 49.922
2021-01-16 | 14:45 | 49.925
2021-01-16 | 14:45 | 49.924
2021-01-16 | 14:45 | 49.924
2021-01-16 | 14:45 | 49.924
2021-01-16 | 14:45 | 49.92
2021-01-16 | 14:45 | 49.919
2021-01-16 | 14:45 | 49.92
2021-01-16 | 14:45 | 49.919
2021-01-16 | 14:45 | 49.92
2021-01-16 | 14:45 | 49.92
2021-01-16 | 14:45 | 49.92
2021-01-16 | 14:45 | 49.919
2021-01-16 | 14:45 | 49.918
2021-01-16 | 14:45 | 49.918
2021-01-16 | 14:46 | 49.92
2021-01-16 | 14:46 | 49.923
2021-01-16 | 14:46 | 49.925
2021-01-16 | 14:46 | 49.928
2021-01-16 | 14:46 | 49.931
2021-01-16 | 14:46 | 49.934
2021-01-16 | 14:46 | 49.936
2021-01-16 | 14:46 | 49.937
2021-01-16 | 14:46 | 49.94
2021-01-16 | 14:46 | 49.943
2021-01-16 | 14:46 | 49.943
2021-01-16 | 14:46 | 49.943
2021-01-16 | 14:46 | 49.943
2021-01-16 | 14:46 | 49.944
2021-01-16 | 14:46 | 49.945
2021-01-16 | 14:46 | 49.946
2021-01-16 | 14:46 | 49.946
2021-01-16 | 14:46 | 49.944
2021-01-16 | 14:46 | 49.941
2021-01-16 | 14:46 | 49.939
2021-01-16 | 14:46 | 49.942
2021-01-16 | 14:46 | 49.943
2021-01-16 | 14:46 | 49.943
2021-01-16 | 14:46 | 49.944
2021-01-16 | 14:46 | 49.947
2021-01-16 | 14:46 | 49.948
2021-01-16 | 14:46 | 49.95
2021-01-16 | 14:46 | 49.95
2021-01-16 | 14:46 | 49.952
2021-01-16 | 14:46 | 49.955
2021-01-16 | 14:46 | 49.954
2021-01-16 | 14:46 | 49.954
2021-01-16 | 14:46 | 49.955
2021-01-16 | 14:46 | 49.957
2021-01-16 | 14:46 | 49.957
2021-01-16 | 14:46 | 49.961
2021-01-16 | 14:46 | 49.961
2021-01-16 | 14:46 | 49.961
2021-01-16 | 14:46 | 49.958
2021-01-16 | 14:46 | 49.958
2021-01-16 | 14:46 | 49.954
2021-01-16 | 14:46 | 49.952
2021-01-16 | 14:46 | 49.95
2021-01-16 | 14:46 | 49.947
2021-01-16 | 14:46 | 49.948
2021-01-16 | 14:46 | 49.948
2021-01-16 | 14:46 | 49.945
2021-01-16 | 14:46 | 49.944
2021-01-16 | 14:46 | 49.942
2021-01-16 | 14:46 | 49.944
2021-01-16 | 14:46 | 49.942
2021-01-16 | 14:46 | 49.942
2021-01-16 | 14:46 | 49.941
2021-01-16 | 14:46 | 49.941
2021-01-16 | 14:46 | 49.939
2021-01-16 | 14:46 | 49.94
2021-01-16 | 14:46 | 49.945
2021-01-16 | 14:46 | 49.948
2021-01-16 | 14:46 | 49.95
2021-01-16 | 14:46 | 49.949
2021-01-16 | 14:46 | 49.951
2021-01-16 | 14:47 | 49.952
2021-01-16 | 14:47 | 49.951
2021-01-16 | 14:47 | 49.951
2021-01-16 | 14:47 | 49.952
2021-01-16 | 14:47 | 49.953
2021-01-16 | 14:47 | 49.953
2021-01-16 | 14:47 | 49.951
2021-01-16 | 14:47 | 49.949
2021-01-16 | 14:47 | 49.95
2021-01-16 | 14:47 | 49.952
2021-01-16 | 14:47 | 49.951
2021-01-16 | 14:47 | 49.952
2021-01-16 | 14:47 | 49.955
2021-01-16 | 14:47 | 49.956
2021-01-16 | 14:47 | 49.956
2021-01-16 | 14:47 | 49.955
2021-01-16 | 14:47 | 49.955
2021-01-16 | 14:47 | 49.956
2021-01-16 | 14:47 | 49.955
2021-01-16 | 14:47 | 49.958
2021-01-16 | 14:47 | 49.958
2021-01-16 | 14:47 | 49.956
2021-01-16 | 14:47 | 49.955
2021-01-16 | 14:47 | 49.954
2021-01-16 | 14:47 | 49.954
2021-01-16 | 14:47 | 49.955
2021-01-16 | 14:47 | 49.954
2021-01-16 | 14:47 | 49.956
2021-01-16 | 14:47 | 49.958
2021-01-16 | 14:47 | 49.957
2021-01-16 | 14:47 | 49.961
2021-01-16 | 14:47 | 49.962
2021-01-16 | 14:47 | 49.963
2021-01-16 | 14:47 | 49.962
2021-01-16 | 14:47 | 49.961
2021-01-16 | 14:47 | 49.96
2021-01-16 | 14:47 | 49.961
2021-01-16 | 14:47 | 49.963
2021-01-16 | 14:47 | 49.965
2021-01-16 | 14:47 | 49.966
2021-01-16 | 14:47 | 49.968
2021-01-16 | 14:47 | 49.973
2021-01-16 | 14:47 | 49.977
2021-01-16 | 14:47 | 49.979
2021-01-16 | 14:47 | 49.981
2021-01-16 | 14:47 | 49.981
2021-01-16 | 14:47 | 49.986
2021-01-16 | 14:47 | 49.987
2021-01-16 | 14:47 | 49.988
2021-01-16 | 14:47 | 49.992
2021-01-16 | 14:47 | 49.994
2021-01-16 | 14:47 | 49.994
2021-01-16 | 14:47 | 49.998
2021-01-16 | 14:47 | 50.002
2021-01-16 | 14:47 | 50.006
2021-01-16 | 14:47 | 50.01
2021-01-16 | 14:47 | 50.013
2021-01-16 | 14:47 | 50.017
2021-01-16 | 14:47 | 50.018
2021-01-16 | 14:48 | 50.022
2021-01-16 | 14:48 | 50.022
2021-01-16 | 14:48 | 50.024
2021-01-16 | 14:48 | 50.023
2021-01-16 | 14:48 | 50.024
2021-01-16 | 14:48 | 50.022
2021-01-16 | 14:48 | 50.022
2021-01-16 | 14:48 | 50.02
2021-01-16 | 14:48 | 50.019
2021-01-16 | 14:48 | 50.019
2021-01-16 | 14:48 | 50.017
2021-01-16 | 14:48 | 50.017
2021-01-16 | 14:48 | 50.016
2021-01-16 | 14:48 | 50.015
2021-01-16 | 14:48 | 50.016
2021-01-16 | 14:48 | 50.017
2021-01-16 | 14:48 | 50.015
2021-01-16 | 14:48 | 50.016
2021-01-16 | 14:48 | 50.017
2021-01-16 | 14:48 | 50.017
2021-01-16 | 14:48 | 50.017
2021-01-16 | 14:48 | 50.02
2021-01-16 | 14:48 | 50.021
2021-01-16 | 14:48 | 50.022
2021-01-16 | 14:48 | 50.022
2021-01-16 | 14:48 | 50.024
2021-01-16 | 14:48 | 50.024
2021-01-16 | 14:48 | 50.025
2021-01-16 | 14:48 | 50.026
2021-01-16 | 14:48 | 50.03
2021-01-16 | 14:48 | 50.033
2021-01-16 | 14:48 | 50.035
2021-01-16 | 14:48 | 50.039
2021-01-16 | 14:48 | 50.045
2021-01-16 | 14:48 | 50.049
2021-01-16 | 14:48 | 50.052
2021-01-16 | 14:48 | 50.056
2021-01-16 | 14:48 | 50.057
2021-01-16 | 14:48 | 50.057
2021-01-16 | 14:48 | 50.058
2021-01-16 | 14:48 | 50.058
2021-01-16 | 14:48 | 50.057
2021-01-16 | 14:48 | 50.056
2021-01-16 | 14:48 | 50.057
2021-01-16 | 14:48 | 50.061
2021-01-16 | 14:48 | 50.064
2021-01-16 | 14:48 | 50.063
2021-01-16 | 14:48 | 50.065
2021-01-16 | 14:48 | 50.07
2021-01-16 | 14:48 | 50.07
2021-01-16 | 14:48 | 50.069
2021-01-16 | 14:48 | 50.068
2021-01-16 | 14:48 | 50.066
2021-01-16 | 14:48 | 50.064
2021-01-16 | 14:48 | 50.063
2021-01-16 | 14:48 | 50.063
2021-01-16 | 14:48 | 50.064
2021-01-16 | 14:48 | 50.064
2021-01-16 | 14:48 | 50.063
2021-01-16 | 14:48 | 50.065
2021-01-16 | 14:48 | 50.067
2021-01-16 | 14:49 | 50.065
2021-01-16 | 14:49 | 50.063
2021-01-16 | 14:49 | 50.061
2021-01-16 | 14:49 | 50.061
2021-01-16 | 14:49 | 50.061
2021-01-16 | 14:49 | 50.062
2021-01-16 | 14:49 | 50.063
2021-01-16 | 14:49 | 50.063
2021-01-16 | 14:49 | 50.064
2021-01-16 | 14:49 | 50.066
2021-01-16 | 14:49 | 50.067
2021-01-16 | 14:49 | 50.071
2021-01-16 | 14:49 | 50.071
2021-01-16 | 14:49 | 50.07
2021-01-16 | 14:49 | 50.07
2021-01-16 | 14:49 | 50.071
2021-01-16 | 14:49 | 50.07
2021-01-16 | 14:49 | 50.071
2021-01-16 | 14:49 | 50.072
2021-01-16 | 14:49 | 50.075
2021-01-16 | 14:49 | 50.077
2021-01-16 | 14:49 | 50.08
2021-01-16 | 14:49 | 50.08
2021-01-16 | 14:49 | 50.084
2021-01-16 | 14:49 | 50.084
2021-01-16 | 14:49 | 50.085
2021-01-16 | 14:49 | 50.086
2021-01-16 | 14:49 | 50.089
2021-01-16 | 14:49 | 50.092
2021-01-16 | 14:49 | 50.094
2021-01-16 | 14:49 | 50.096
2021-01-16 | 14:49 | 50.098
2021-01-16 | 14:49 | 50.097
2021-01-16 | 14:49 | 50.097
2021-01-16 | 14:49 | 50.097
2021-01-16 | 14:49 | 50.097
2021-01-16 | 14:49 | 50.098
2021-01-16 | 14:49 | 50.098
2021-01-16 | 14:49 | 50.098
2021-01-16 | 14:49 | 50.099
2021-01-16 | 14:49 | 50.099
2021-01-16 | 14:49 | 50.097
2021-01-16 | 14:49 | 50.092
2021-01-16 | 14:49 | 50.092
2021-01-16 | 14:49 | 50.091
2021-01-16 | 14:49 | 50.085
2021-01-16 | 14:49 | 50.083
2021-01-16 | 14:49 | 50.082
2021-01-16 | 14:49 | 50.082
2021-01-16 | 14:49 | 50.081
2021-01-16 | 14:49 | 50.081
2021-01-16 | 14:49 | 50.082
2021-01-16 | 14:49 | 50.08
2021-01-16 | 14:49 | 50.079
2021-01-16 | 14:49 | 50.079
2021-01-16 | 14:49 | 50.077
2021-01-16 | 14:49 | 50.075
2021-01-16 | 14:49 | 50.074
2021-01-16 | 14:49 | 50.071
2021-01-16 | 14:50 | 50.068
2021-01-16 | 14:50 | 50.067
2021-01-16 | 14:50 | 50.066
2021-01-16 | 14:50 | 50.064
2021-01-16 | 14:50 | 50.063
2021-01-16 | 14:50 | 50.062
2021-01-16 | 14:50 | 50.064
2021-01-16 | 14:50 | 50.065
2021-01-16 | 14:50 | 50.069
2021-01-16 | 14:50 | 50.074
2021-01-16 | 14:50 | 50.076
2021-01-16 | 14:50 | 50.077
2021-01-16 | 14:50 | 50.079
2021-01-16 | 14:50 | 50.083
2021-01-16 | 14:50 | 50.082
2021-01-16 | 14:50 | 50.082
2021-01-16 | 14:50 | 50.083
2021-01-16 | 14:50 | 50.083
2021-01-16 | 14:50 | 50.082
2021-01-16 | 14:50 | 50.083
2021-01-16 | 14:50 | 50.082
2021-01-16 | 14:50 | 50.081
2021-01-16 | 14:50 | 50.079
2021-01-16 | 14:50 | 50.078
2021-01-16 | 14:50 | 50.079
2021-01-16 | 14:50 | 50.078
2021-01-16 | 14:50 | 50.078
2021-01-16 | 14:50 | 50.079
2021-01-16 | 14:50 | 50.08
2021-01-16 | 14:50 | 50.08
2021-01-16 | 14:50 | 50.08
2021-01-16 | 14:50 | 50.077
2021-01-16 | 14:50 | 50.075
2021-01-16 | 14:50 | 50.076
2021-01-16 | 14:50 | 50.074
2021-01-16 | 14:50 | 50.076
2021-01-16 | 14:50 | 50.078
2021-01-16 | 14:50 | 50.08
2021-01-16 | 14:50 | 50.08
2021-01-16 | 14:50 | 50.081
2021-01-16 | 14:50 | 50.079
2021-01-16 | 14:50 | 50.081
2021-01-16 | 14:50 | 50.081
2021-01-16 | 14:50 | 50.082
2021-01-16 | 14:50 | 50.084
2021-01-16 | 14:50 | 50.085
2021-01-16 | 14:50 | 50.085
2021-01-16 | 14:50 | 50.086
2021-01-16 | 14:50 | 50.084
2021-01-16 | 14:50 | 50.085
2021-01-16 | 14:50 | 50.085
2021-01-16 | 14:50 | 50.086
2021-01-16 | 14:50 | 50.087
2021-01-16 | 14:50 | 50.092
2021-01-16 | 14:50 | 50.096
2021-01-16 | 14:50 | 50.098
2021-01-16 | 14:50 | 50.102
2021-01-16 | 14:50 | 50.103
2021-01-16 | 14:50 | 50.104
2021-01-16 | 14:50 | 50.103
2021-01-16 | 14:50 | 50.1
2021-01-16 | 14:51 | 50.095
2021-01-16 | 14:51 | 50.092
2021-01-16 | 14:51 | 50.09
2021-01-16 | 14:51 | 50.088
2021-01-16 | 14:51 | 50.087
2021-01-16 | 14:51 | 50.084
2021-01-16 | 14:51 | 50.081
2021-01-16 | 14:51 | 50.078
2021-01-16 | 14:51 | 50.075
2021-01-16 | 14:51 | 50.073
2021-01-16 | 14:51 | 50.071
2021-01-16 | 14:51 | 50.067
2021-01-16 | 14:51 | 50.062
2021-01-16 | 14:51 | 50.058
2021-01-16 | 14:51 | 50.056
2021-01-16 | 14:51 | 50.055
2021-01-16 | 14:51 | 50.053
2021-01-16 | 14:51 | 50.052
2021-01-16 | 14:51 | 50.052
2021-01-16 | 14:51 | 50.051
2021-01-16 | 14:51 | 50.049
2021-01-16 | 14:51 | 50.049
2021-01-16 | 14:51 | 50.047
2021-01-16 | 14:51 | 50.047
2021-01-16 | 14:51 | 50.047
2021-01-16 | 14:51 | 50.045
2021-01-16 | 14:51 | 50.045
2021-01-16 | 14:51 | 50.044
2021-01-16 | 14:51 | 50.041
2021-01-16 | 14:51 | 50.04
2021-01-16 | 14:51 | 50.035
2021-01-16 | 14:51 | 50.032
2021-01-16 | 14:51 | 50.028
2021-01-16 | 14:51 | 50.024
2021-01-16 | 14:51 | 50.022
2021-01-16 | 14:51 | 50.017
2021-01-16 | 14:51 | 50.012
2021-01-16 | 14:51 | 50.006
2021-01-16 | 14:51 | 49.998
2021-01-16 | 14:51 | 49.991
2021-01-16 | 14:51 | 49.982
2021-01-16 | 14:51 | 49.973
2021-01-16 | 14:51 | 49.963
2021-01-16 | 14:51 | 49.957
2021-01-16 | 14:51 | 49.949
2021-01-16 | 14:51 | 49.946
2021-01-16 | 14:51 | 49.944
2021-01-16 | 14:51 | 49.942
2021-01-16 | 14:51 | 49.943
2021-01-16 | 14:51 | 49.943
2021-01-16 | 14:51 | 49.943
2021-01-16 | 14:51 | 49.945
2021-01-16 | 14:51 | 49.945
2021-01-16 | 14:51 | 49.945
2021-01-16 | 14:51 | 49.945
2021-01-16 | 14:51 | 49.942
2021-01-16 | 14:51 | 49.939
2021-01-16 | 14:51 | 49.938
2021-01-16 | 14:51 | 49.936
2021-01-16 | 14:52 | 49.936
2021-01-16 | 14:52 | 49.936
2021-01-16 | 14:52 | 49.936
2021-01-16 | 14:52 | 49.937
2021-01-16 | 14:52 | 49.942
2021-01-16 | 14:52 | 49.943
2021-01-16 | 14:52 | 49.946
2021-01-16 | 14:52 | 49.951
2021-01-16 | 14:52 | 49.954
2021-01-16 | 14:52 | 49.957
2021-01-16 | 14:52 | 49.962
2021-01-16 | 14:52 | 49.962
2021-01-16 | 14:52 | 49.96
2021-01-16 | 14:52 | 49.959
2021-01-16 | 14:52 | 49.96
2021-01-16 | 14:52 | 49.96
2021-01-16 | 14:52 | 49.962
2021-01-16 | 14:52 | 49.963
2021-01-16 | 14:52 | 49.965
2021-01-16 | 14:52 | 49.965
2021-01-16 | 14:52 | 49.966
2021-01-16 | 14:52 | 49.965
2021-01-16 | 14:52 | 49.965
2021-01-16 | 14:52 | 49.966
2021-01-16 | 14:52 | 49.968
2021-01-16 | 14:52 | 49.97
2021-01-16 | 14:52 | 49.971
2021-01-16 | 14:52 | 49.97
2021-01-16 | 14:52 | 49.971
2021-01-16 | 14:52 | 49.973
2021-01-16 | 14:52 | 49.973
2021-01-16 | 14:52 | 49.972
2021-01-16 | 14:52 | 49.971
2021-01-16 | 14:52 | 49.972
2021-01-16 | 14:52 | 49.972
2021-01-16 | 14:52 | 49.971
2021-01-16 | 14:52 | 49.974
2021-01-16 | 14:52 | 49.981
2021-01-16 | 14:52 | 49.981
2021-01-16 | 14:52 | 49.982
2021-01-16 | 14:52 | 49.981
2021-01-16 | 14:52 | 49.981
2021-01-16 | 14:52 | 49.982
2021-01-16 | 14:52 | 49.98
2021-01-16 | 14:52 | 49.978
2021-01-16 | 14:52 | 49.978
2021-01-16 | 14:52 | 49.978
2021-01-16 | 14:52 | 49.979
2021-01-16 | 14:52 | 49.979
2021-01-16 | 14:52 | 49.979
2021-01-16 | 14:52 | 49.977
2021-01-16 | 14:52 | 49.978
2021-01-16 | 14:52 | 49.981
2021-01-16 | 14:52 | 49.983
2021-01-16 | 14:52 | 49.982
2021-01-16 | 14:52 | 49.983
2021-01-16 | 14:52 | 49.979
2021-01-16 | 14:52 | 49.978
2021-01-16 | 14:52 | 49.977
2021-01-16 | 14:52 | 49.973
2021-01-16 | 14:52 | 49.973
2021-01-16 | 14:53 | 49.97
2021-01-16 | 14:53 | 49.965
2021-01-16 | 14:53 | 49.962
2021-01-16 | 14:53 | 49.958
2021-01-16 | 14:53 | 49.956
2021-01-16 | 14:53 | 49.953
2021-01-16 | 14:53 | 49.952
2021-01-16 | 14:53 | 49.953
2021-01-16 | 14:53 | 49.957
2021-01-16 | 14:53 | 49.955
2021-01-16 | 14:53 | 49.957
2021-01-16 | 14:53 | 49.958
2021-01-16 | 14:53 | 49.958
2021-01-16 | 14:53 | 49.957
2021-01-16 | 14:53 | 49.955
2021-01-16 | 14:53 | 49.952
2021-01-16 | 14:53 | 49.951
2021-01-16 | 14:53 | 49.955
2021-01-16 | 14:53 | 49.957
2021-01-16 | 14:53 | 49.96
2021-01-16 | 14:53 | 49.964
2021-01-16 | 14:53 | 49.968
2021-01-16 | 14:53 | 49.971
2021-01-16 | 14:53 | 49.974
2021-01-16 | 14:53 | 49.979
2021-01-16 | 14:53 | 49.982
2021-01-16 | 14:53 | 49.989
2021-01-16 | 14:53 | 49.992
2021-01-16 | 14:53 | 49.994
2021-01-16 | 14:53 | 49.996
2021-01-16 | 14:53 | 49.998
2021-01-16 | 14:53 | 50
2021-01-16 | 14:53 | 50.001
2021-01-16 | 14:53 | 50.001
2021-01-16 | 14:53 | 50.001
2021-01-16 | 14:53 | 50.002
2021-01-16 | 14:53 | 50
2021-01-16 | 14:53 | 49.998
2021-01-16 | 14:53 | 49.996
2021-01-16 | 14:53 | 49.994
2021-01-16 | 14:53 | 49.994
2021-01-16 | 14:53 | 49.994
2021-01-16 | 14:53 | 49.993
2021-01-16 | 14:53 | 49.994
2021-01-16 | 14:53 | 49.992
2021-01-16 | 14:53 | 49.991
2021-01-16 | 14:53 | 49.99
2021-01-16 | 14:53 | 49.988
2021-01-16 | 14:53 | 49.988
2021-01-16 | 14:53 | 49.99
2021-01-16 | 14:53 | 49.99
2021-01-16 | 14:53 | 49.99
2021-01-16 | 14:53 | 49.99
2021-01-16 | 14:53 | 49.992
2021-01-16 | 14:53 | 49.991
2021-01-16 | 14:53 | 49.99
2021-01-16 | 14:53 | 49.992
2021-01-16 | 14:53 | 49.991
2021-01-16 | 14:53 | 49.99
2021-01-16 | 14:54 | 49.991
2021-01-16 | 14:54 | 49.988
2021-01-16 | 14:54 | 49.987
2021-01-16 | 14:54 | 49.987
2021-01-16 | 14:54 | 49.986
2021-01-16 | 14:54 | 49.988
2021-01-16 | 14:54 | 49.988
2021-01-16 | 14:54 | 49.987
2021-01-16 | 14:54 | 49.989
2021-01-16 | 14:54 | 49.988
2021-01-16 | 14:54 | 49.988
2021-01-16 | 14:54 | 49.987
2021-01-16 | 14:54 | 49.991
2021-01-16 | 14:54 | 49.993
2021-01-16 | 14:54 | 49.994
2021-01-16 | 14:54 | 49.995
2021-01-16 | 14:54 | 49.994
2021-01-16 | 14:54 | 49.994
2021-01-16 | 14:54 | 49.995
2021-01-16 | 14:54 | 49.995
2021-01-16 | 14:54 | 49.997
2021-01-16 | 14:54 | 49.994
2021-01-16 | 14:54 | 49.996
2021-01-16 | 14:54 | 49.996
2021-01-16 | 14:54 | 49.997
2021-01-16 | 14:54 | 50.001
2021-01-16 | 14:54 | 50.004
2021-01-16 | 14:54 | 50.009
2021-01-16 | 14:54 | 50.014
2021-01-16 | 14:54 | 50.021
2021-01-16 | 14:54 | 50.028
2021-01-16 | 14:54 | 50.034
2021-01-16 | 14:54 | 50.037
2021-01-16 | 14:54 | 50.041
2021-01-16 | 14:54 | 50.045
2021-01-16 | 14:54 | 50.045
2021-01-16 | 14:54 | 50.044
2021-01-16 | 14:54 | 50.043
2021-01-16 | 14:54 | 50.039
2021-01-16 | 14:54 | 50.037
2021-01-16 | 14:54 | 50.034
2021-01-16 | 14:54 | 50.032
2021-01-16 | 14:54 | 50.031
2021-01-16 | 14:54 | 50.028
2021-01-16 | 14:54 | 50.028
2021-01-16 | 14:54 | 50.027
2021-01-16 | 14:54 | 50.029
2021-01-16 | 14:54 | 50.031
2021-01-16 | 14:54 | 50.03
2021-01-16 | 14:54 | 50.032
2021-01-16 | 14:54 | 50.033
2021-01-16 | 14:54 | 50.033
2021-01-16 | 14:54 | 50.032
2021-01-16 | 14:54 | 50.032
2021-01-16 | 14:54 | 50.034
2021-01-16 | 14:54 | 50.036
2021-01-16 | 14:54 | 50.036
2021-01-16 | 14:54 | 50.038
2021-01-16 | 14:54 | 50.04
2021-01-16 | 14:54 | 50.041
2021-01-16 | 14:54 | 50.045
2021-01-16 | 14:55 | 50.047
2021-01-16 | 14:55 | 50.049
2021-01-16 | 14:55 | 50.053
2021-01-16 | 14:55 | 50.056
2021-01-16 | 14:55 | 50.057
2021-01-16 | 14:55 | 50.057
2021-01-16 | 14:55 | 50.057
2021-01-16 | 14:55 | 50.056
2021-01-16 | 14:55 | 50.057
2021-01-16 | 14:55 | 50.056
2021-01-16 | 14:55 | 50.055
2021-01-16 | 14:55 | 50.058
2021-01-16 | 14:55 | 50.06
2021-01-16 | 14:55 | 50.06
2021-01-16 | 14:55 | 50.061
2021-01-16 | 14:55 | 50.061
2021-01-16 | 14:55 | 50.062
2021-01-16 | 14:55 | 50.062
2021-01-16 | 14:55 | 50.063
2021-01-16 | 14:55 | 50.061
2021-01-16 | 14:55 | 50.059
2021-01-16 | 14:55 | 50.057
2021-01-16 | 14:55 | 50.053
2021-01-16 | 14:55 | 50.049
2021-01-16 | 14:55 | 50.045
2021-01-16 | 14:55 | 50.041
2021-01-16 | 14:55 | 50.037
2021-01-16 | 14:55 | 50.038
2021-01-16 | 14:55 | 50.04
2021-01-16 | 14:55 | 50.037
2021-01-16 | 14:55 | 50.037
2021-01-16 | 14:55 | 50.039
2021-01-16 | 14:55 | 50.039
2021-01-16 | 14:55 | 50.041
2021-01-16 | 14:55 | 50.044
2021-01-16 | 14:55 | 50.043
2021-01-16 | 14:55 | 50.043
2021-01-16 | 14:55 | 50.046
2021-01-16 | 14:55 | 50.048
2021-01-16 | 14:55 | 50.049
2021-01-16 | 14:55 | 50.049
2021-01-16 | 14:55 | 50.049
2021-01-16 | 14:55 | 50.047
2021-01-16 | 14:55 | 50.046
2021-01-16 | 14:55 | 50.048
2021-01-16 | 14:55 | 50.047
2021-01-16 | 14:55 | 50.048
2021-01-16 | 14:55 | 50.049
2021-01-16 | 14:55 | 50.047
2021-01-16 | 14:55 | 50.048
2021-01-16 | 14:55 | 50.049
2021-01-16 | 14:55 | 50.051
2021-01-16 | 14:55 | 50.052
2021-01-16 | 14:55 | 50.049
2021-01-16 | 14:55 | 50.051
2021-01-16 | 14:55 | 50.053
2021-01-16 | 14:55 | 50.054
2021-01-16 | 14:55 | 50.053
2021-01-16 | 14:55 | 50.055
2021-01-16 | 14:56 | 50.055
2021-01-16 | 14:56 | 50.055
2021-01-16 | 14:56 | 50.054
2021-01-16 | 14:56 | 50.056
2021-01-16 | 14:56 | 50.054
2021-01-16 | 14:56 | 50.051
2021-01-16 | 14:56 | 50.051
2021-01-16 | 14:56 | 50.048
2021-01-16 | 14:56 | 50.045
2021-01-16 | 14:56 | 50.04
2021-01-16 | 14:56 | 50.038
2021-01-16 | 14:56 | 50.038
2021-01-16 | 14:56 | 50.038
2021-01-16 | 14:56 | 50.038
2021-01-16 | 14:56 | 50.039
2021-01-16 | 14:56 | 50.038
2021-01-16 | 14:56 | 50.042
2021-01-16 | 14:56 | 50.048
2021-01-16 | 14:56 | 50.053
2021-01-16 | 14:56 | 50.057
2021-01-16 | 14:56 | 50.063
2021-01-16 | 14:56 | 50.065
2021-01-16 | 14:56 | 50.064
2021-01-16 | 14:56 | 50.067
2021-01-16 | 14:56 | 50.065
2021-01-16 | 14:56 | 50.063
2021-01-16 | 14:56 | 50.061
2021-01-16 | 14:56 | 50.062
2021-01-16 | 14:56 | 50.061
2021-01-16 | 14:56 | 50.062
2021-01-16 | 14:56 | 50.064
2021-01-16 | 14:56 | 50.064
2021-01-16 | 14:56 | 50.063
2021-01-16 | 14:56 | 50.062
2021-01-16 | 14:56 | 50.06
2021-01-16 | 14:56 | 50.06
2021-01-16 | 14:56 | 50.057
2021-01-16 | 14:56 | 50.056
2021-01-16 | 14:56 | 50.056
2021-01-16 | 14:56 | 50.056
2021-01-16 | 14:56 | 50.055
2021-01-16 | 14:56 | 50.057
2021-01-16 | 14:56 | 50.062
2021-01-16 | 14:56 | 50.066
2021-01-16 | 14:56 | 50.068
2021-01-16 | 14:56 | 50.071
2021-01-16 | 14:56 | 50.074
2021-01-16 | 14:56 | 50.077
2021-01-16 | 14:56 | 50.079
2021-01-16 | 14:56 | 50.078
2021-01-16 | 14:56 | 50.077
2021-01-16 | 14:56 | 50.073
2021-01-16 | 14:56 | 50.072
2021-01-16 | 14:56 | 50.069
2021-01-16 | 14:56 | 50.069
2021-01-16 | 14:56 | 50.071
2021-01-16 | 14:56 | 50.072
2021-01-16 | 14:56 | 50.075
2021-01-16 | 14:56 | 50.075
2021-01-16 | 14:56 | 50.078
2021-01-16 | 14:56 | 50.078
2021-01-16 | 14:57 | 50.079
2021-01-16 | 14:57 | 50.08
2021-01-16 | 14:57 | 50.083
2021-01-16 | 14:57 | 50.083
2021-01-16 | 14:57 | 50.082
2021-01-16 | 14:57 | 50.08
2021-01-16 | 14:57 | 50.08
2021-01-16 | 14:57 | 50.077
2021-01-16 | 14:57 | 50.079
2021-01-16 | 14:57 | 50.078
2021-01-16 | 14:57 | 50.08
2021-01-16 | 14:57 | 50.079
2021-01-16 | 14:57 | 50.079
2021-01-16 | 14:57 | 50.078
2021-01-16 | 14:57 | 50.078
2021-01-16 | 14:57 | 50.08
2021-01-16 | 14:57 | 50.084
2021-01-16 | 14:57 | 50.084
2021-01-16 | 14:57 | 50.087
2021-01-16 | 14:57 | 50.088
2021-01-16 | 14:57 | 50.088
2021-01-16 | 14:57 | 50.089
2021-01-16 | 14:57 | 50.089
2021-01-16 | 14:57 | 50.091
2021-01-16 | 14:57 | 50.09
2021-01-16 | 14:57 | 50.089
2021-01-16 | 14:57 | 50.087
2021-01-16 | 14:57 | 50.088
2021-01-16 | 14:57 | 50.086
2021-01-16 | 14:57 | 50.083
2021-01-16 | 14:57 | 50.083
2021-01-16 | 14:57 | 50.08
2021-01-16 | 14:57 | 50.08
2021-01-16 | 14:57 | 50.079
2021-01-16 | 14:57 | 50.08
2021-01-16 | 14:57 | 50.079
2021-01-16 | 14:57 | 50.076
2021-01-16 | 14:57 | 50.073
2021-01-16 | 14:57 | 50.07
2021-01-16 | 14:57 | 50.067
2021-01-16 | 14:57 | 50.063
2021-01-16 | 14:57 | 50.06
2021-01-16 | 14:57 | 50.053
2021-01-16 | 14:57 | 50.051
2021-01-16 | 14:57 | 50.049
2021-01-16 | 14:57 | 50.05
2021-01-16 | 14:57 | 50.049
2021-01-16 | 14:57 | 50.049
2021-01-16 | 14:57 | 50.05
2021-01-16 | 14:57 | 50.051
2021-01-16 | 14:57 | 50.051
2021-01-16 | 14:57 | 50.051
2021-01-16 | 14:57 | 50.05
2021-01-16 | 14:57 | 50.052
2021-01-16 | 14:57 | 50.054
2021-01-16 | 14:57 | 50.056
2021-01-16 | 14:57 | 50.056
2021-01-16 | 14:57 | 50.054
2021-01-16 | 14:57 | 50.053
2021-01-16 | 14:58 | 50.049
2021-01-16 | 14:58 | 50.049
2021-01-16 | 14:58 | 50.048
2021-01-16 | 14:58 | 50.05
2021-01-16 | 14:58 | 50.049
2021-01-16 | 14:58 | 50.047
2021-01-16 | 14:58 | 50.048
2021-01-16 | 14:58 | 50.05
2021-01-16 | 14:58 | 50.049
2021-01-16 | 14:58 | 50.047
2021-01-16 | 14:58 | 50.047
2021-01-16 | 14:58 | 50.047
2021-01-16 | 14:58 | 50.048
2021-01-16 | 14:58 | 50.048
2021-01-16 | 14:58 | 50.049
2021-01-16 | 14:58 | 50.051
2021-01-16 | 14:58 | 50.052
2021-01-16 | 14:58 | 50.055
2021-01-16 | 14:58 | 50.055
2021-01-16 | 14:58 | 50.056
2021-01-16 | 14:58 | 50.056
2021-01-16 | 14:58 | 50.055
2021-01-16 | 14:58 | 50.053
2021-01-16 | 14:58 | 50.054
2021-01-16 | 14:58 | 50.052
2021-01-16 | 14:58 | 50.046
2021-01-16 | 14:58 | 50.042
2021-01-16 | 14:58 | 50.039
2021-01-16 | 14:58 | 50.037
2021-01-16 | 14:58 | 50.039
2021-01-16 | 14:58 | 50.038
2021-01-16 | 14:58 | 50.036
2021-01-16 | 14:58 | 50.036
2021-01-16 | 14:58 | 50.036
2021-01-16 | 14:58 | 50.035
2021-01-16 | 14:58 | 50.036
2021-01-16 | 14:58 | 50.037
2021-01-16 | 14:58 | 50.038
2021-01-16 | 14:58 | 50.036
2021-01-16 | 14:58 | 50.036
2021-01-16 | 14:58 | 50.033
2021-01-16 | 14:58 | 50.03
2021-01-16 | 14:58 | 50.027
2021-01-16 | 14:58 | 50.025
2021-01-16 | 14:58 | 50.022
2021-01-16 | 14:58 | 50.023
2021-01-16 | 14:58 | 50.022
2021-01-16 | 14:58 | 50.022
2021-01-16 | 14:58 | 50.022
2021-01-16 | 14:58 | 50.022
2021-01-16 | 14:58 | 50.022
2021-01-16 | 14:58 | 50.02
2021-01-16 | 14:58 | 50.019
2021-01-16 | 14:58 | 50.019
2021-01-16 | 14:58 | 50.019
2021-01-16 | 14:58 | 50.021
2021-01-16 | 14:58 | 50.025
2021-01-16 | 14:58 | 50.027
2021-01-16 | 14:58 | 50.027
2021-01-16 | 14:58 | 50.028
2021-01-16 | 14:58 | 50.028
2021-01-16 | 14:59 | 50.029
2021-01-16 | 14:59 | 50.027
2021-01-16 | 14:59 | 50.024
2021-01-16 | 14:59 | 50.023
2021-01-16 | 14:59 | 50.024
2021-01-16 | 14:59 | 50.024
2021-01-16 | 14:59 | 50.025
2021-01-16 | 14:59 | 50.026
2021-01-16 | 14:59 | 50.027
2021-01-16 | 14:59 | 50.029
2021-01-16 | 14:59 | 50.028
2021-01-16 | 14:59 | 50.028
2021-01-16 | 14:59 | 50.027
2021-01-16 | 14:59 | 50.029
2021-01-16 | 14:59 | 50.033
2021-01-16 | 14:59 | 50.037
2021-01-16 | 14:59 | 50.04
2021-01-16 | 14:59 | 50.041
2021-01-16 | 14:59 | 50.043
2021-01-16 | 14:59 | 50.043
2021-01-16 | 14:59 | 50.044
2021-01-16 | 14:59 | 50.042
2021-01-16 | 14:59 | 50.043
2021-01-16 | 14:59 | 50.039
2021-01-16 | 14:59 | 50.036
2021-01-16 | 14:59 | 50.032
2021-01-16 | 14:59 | 50.03
2021-01-16 | 14:59 | 50.027
2021-01-16 | 14:59 | 50.027
2021-01-16 | 14:59 | 50.026
2021-01-16 | 14:59 | 50.028
2021-01-16 | 14:59 | 50.029
2021-01-16 | 14:59 | 50.033
2021-01-16 | 14:59 | 50.036
2021-01-16 | 14:59 | 50.039
2021-01-16 | 14:59 | 50.043
2021-01-16 | 14:59 | 50.044
2021-01-16 | 14:59 | 50.046
2021-01-16 | 14:59 | 50.047
2021-01-16 | 14:59 | 50.046
2021-01-16 | 14:59 | 50.048
2021-01-16 | 14:59 | 50.051
2021-01-16 | 14:59 | 50.054
2021-01-16 | 14:59 | 50.056
2021-01-16 | 14:59 | 50.058
2021-01-16 | 14:59 | 50.06
2021-01-16 | 14:59 | 50.059
2021-01-16 | 14:59 | 50.061
2021-01-16 | 14:59 | 50.059
2021-01-16 | 14:59 | 50.06
2021-01-16 | 14:59 | 50.059
2021-01-16 | 14:59 | 50.058
2021-01-16 | 14:59 | 50.054
2021-01-16 | 14:59 | 50.054
2021-01-16 | 14:59 | 50.053
2021-01-16 | 14:59 | 50.051
2021-01-16 | 14:59 | 50.047
2021-01-16 | 14:59 | 50.044
2021-01-16 | 14:59 | 50.04
2021-01-16 | 15:00 | 50.038
2021-01-16 | 15:00 | 50.036
2021-01-16 | 15:00 | 50.033
2021-01-16 | 15:00 | 50.029
2021-01-16 | 15:00 | 50.029
2021-01-16 | 15:00 | 50.025
2021-01-16 | 15:00 | 50.024
2021-01-16 | 15:00 | 50.025
2021-01-16 | 15:00 | 50.027
2021-01-16 | 15:00 | 50.03
2021-01-16 | 15:00 | 50.031
2021-01-16 | 15:00 | 50.033
2021-01-16 | 15:00 | 50.03
2021-01-16 | 15:00 | 50.028
2021-01-16 | 15:00 | 50.024
2021-01-16 | 15:00 | 50.021
2021-01-16 | 15:00 | 50.017
2021-01-16 | 15:00 | 50.013
2021-01-16 | 15:00 | 50.011
2021-01-16 | 15:00 | 50.011
2021-01-16 | 15:00 | 50.011
2021-01-16 | 15:00 | 50.014
2021-01-16 | 15:00 | 50.015
2021-01-16 | 15:00 | 50.013
2021-01-16 | 15:00 | 50.013
2021-01-16 | 15:00 | 50.011
2021-01-16 | 15:00 | 50.008
2021-01-16 | 15:00 | 50.002
2021-01-16 | 15:00 | 49.996
2021-01-16 | 15:00 | 49.99
2021-01-16 | 15:00 | 49.984
2021-01-16 | 15:00 | 49.979
2021-01-16 | 15:00 | 49.976
2021-01-16 | 15:00 | 49.975
2021-01-16 | 15:00 | 49.973
2021-01-16 | 15:00 | 49.973
2021-01-16 | 15:00 | 49.974
2021-01-16 | 15:00 | 49.973
2021-01-16 | 15:00 | 49.974
2021-01-16 | 15:00 | 49.973
2021-01-16 | 15:00 | 49.974
2021-01-16 | 15:00 | 49.971
2021-01-16 | 15:00 | 49.973
2021-01-16 | 15:00 | 49.969
2021-01-16 | 15:00 | 49.97
2021-01-16 | 15:00 | 49.97
2021-01-16 | 15:00 | 49.968
2021-01-16 | 15:00 | 49.967
2021-01-16 | 15:00 | 49.964
2021-01-16 | 15:00 | 49.963
2021-01-16 | 15:00 | 49.964
2021-01-16 | 15:00 | 49.963
2021-01-16 | 15:00 | 49.962
2021-01-16 | 15:00 | 49.962
2021-01-16 | 15:00 | 49.961
2021-01-16 | 15:00 | 49.96
2021-01-16 | 15:00 | 49.959
2021-01-16 | 15:00 | 49.96
2021-01-16 | 15:00 | 49.958
2021-01-16 | 15:00 | 49.953
2021-01-16 | 15:00 | 49.951
2021-01-16 | 15:01 | 49.951
2021-01-16 | 15:01 | 49.95
2021-01-16 | 15:01 | 49.952
2021-01-16 | 15:01 | 49.953
2021-01-16 | 15:01 | 49.953
2021-01-16 | 15:01 | 49.953
2021-01-16 | 15:01 | 49.954
2021-01-16 | 15:01 | 49.955
2021-01-16 | 15:01 | 49.955
2021-01-16 | 15:01 | 49.956
2021-01-16 | 15:01 | 49.957
2021-01-16 | 15:01 | 49.96
2021-01-16 | 15:01 | 49.964
2021-01-16 | 15:01 | 49.967
2021-01-16 | 15:01 | 49.97
2021-01-16 | 15:01 | 49.972
2021-01-16 | 15:01 | 49.973
2021-01-16 | 15:01 | 49.973
2021-01-16 | 15:01 | 49.972
2021-01-16 | 15:01 | 49.972
2021-01-16 | 15:01 | 49.973
2021-01-16 | 15:01 | 49.974
2021-01-16 | 15:01 | 49.972
2021-01-16 | 15:01 | 49.97
2021-01-16 | 15:01 | 49.968
2021-01-16 | 15:01 | 49.968
2021-01-16 | 15:01 | 49.969
2021-01-16 | 15:01 | 49.971
2021-01-16 | 15:01 | 49.975
2021-01-16 | 15:01 | 49.976
2021-01-16 | 15:01 | 49.98
2021-01-16 | 15:01 | 49.978
2021-01-16 | 15:01 | 49.979
2021-01-16 | 15:01 | 49.978
2021-01-16 | 15:01 | 49.976
2021-01-16 | 15:01 | 49.976
2021-01-16 | 15:01 | 49.973
2021-01-16 | 15:01 | 49.974
2021-01-16 | 15:01 | 49.974
2021-01-16 | 15:01 | 49.974
2021-01-16 | 15:01 | 49.974
2021-01-16 | 15:01 | 49.973
2021-01-16 | 15:01 | 49.975
2021-01-16 | 15:01 | 49.976
2021-01-16 | 15:01 | 49.973
2021-01-16 | 15:01 | 49.974
2021-01-16 | 15:01 | 49.972
2021-01-16 | 15:01 | 49.971
2021-01-16 | 15:01 | 49.969
2021-01-16 | 15:01 | 49.967
2021-01-16 | 15:01 | 49.967
2021-01-16 | 15:01 | 49.965
2021-01-16 | 15:01 | 49.963
2021-01-16 | 15:01 | 49.96
2021-01-16 | 15:01 | 49.957
2021-01-16 | 15:01 | 49.956
2021-01-16 | 15:01 | 49.956
2021-01-16 | 15:01 | 49.957
2021-01-16 | 15:01 | 49.959
2021-01-16 | 15:02 | 49.96
2021-01-16 | 15:02 | 49.959
2021-01-16 | 15:02 | 49.959
2021-01-16 | 15:02 | 49.96
2021-01-16 | 15:02 | 49.958
2021-01-16 | 15:02 | 49.959
2021-01-16 | 15:02 | 49.959
2021-01-16 | 15:02 | 49.959
2021-01-16 | 15:02 | 49.958
2021-01-16 | 15:02 | 49.956
2021-01-16 | 15:02 | 49.954
2021-01-16 | 15:02 | 49.95
2021-01-16 | 15:02 | 49.949
2021-01-16 | 15:02 | 49.948
2021-01-16 | 15:02 | 49.946
2021-01-16 | 15:02 | 49.946
2021-01-16 | 15:02 | 49.943
2021-01-16 | 15:02 | 49.944
2021-01-16 | 15:02 | 49.943
2021-01-16 | 15:02 | 49.941
2021-01-16 | 15:02 | 49.941
2021-01-16 | 15:02 | 49.941
2021-01-16 | 15:02 | 49.94
2021-01-16 | 15:02 | 49.938
2021-01-16 | 15:02 | 49.936
2021-01-16 | 15:02 | 49.934
2021-01-16 | 15:02 | 49.933
2021-01-16 | 15:02 | 49.933
2021-01-16 | 15:02 | 49.932
2021-01-16 | 15:02 | 49.929
2021-01-16 | 15:02 | 49.926
2021-01-16 | 15:02 | 49.92
2021-01-16 | 15:02 | 49.915
2021-01-16 | 15:02 | 49.912
2021-01-16 | 15:02 | 49.91
2021-01-16 | 15:02 | 49.908
2021-01-16 | 15:02 | 49.911
2021-01-16 | 15:02 | 49.912
2021-01-16 | 15:02 | 49.913
2021-01-16 | 15:02 | 49.914
2021-01-16 | 15:02 | 49.913
2021-01-16 | 15:02 | 49.916
2021-01-16 | 15:02 | 49.917
2021-01-16 | 15:02 | 49.915
2021-01-16 | 15:02 | 49.915
2021-01-16 | 15:02 | 49.913
2021-01-16 | 15:02 | 49.911
2021-01-16 | 15:02 | 49.912
2021-01-16 | 15:02 | 49.909
2021-01-16 | 15:02 | 49.91
2021-01-16 | 15:02 | 49.911
2021-01-16 | 15:02 | 49.907
2021-01-16 | 15:02 | 49.906
2021-01-16 | 15:02 | 49.906
2021-01-16 | 15:02 | 49.903
2021-01-16 | 15:02 | 49.906
2021-01-16 | 15:02 | 49.903
2021-01-16 | 15:02 | 49.902
2021-01-16 | 15:02 | 49.903
2021-01-16 | 15:02 | 49.901
2021-01-16 | 15:02 | 49.901
2021-01-16 | 15:03 | 49.901
2021-01-16 | 15:03 | 49.9
2021-01-16 | 15:03 | 49.899
2021-01-16 | 15:03 | 49.9
2021-01-16 | 15:03 | 49.897
2021-01-16 | 15:03 | 49.9
2021-01-16 | 15:03 | 49.905
2021-01-16 | 15:03 | 49.908
2021-01-16 | 15:03 | 49.91
2021-01-16 | 15:03 | 49.914
2021-01-16 | 15:03 | 49.915
2021-01-16 | 15:03 | 49.916
2021-01-16 | 15:03 | 49.915
2021-01-16 | 15:03 | 49.911
2021-01-16 | 15:03 | 49.907
2021-01-16 | 15:03 | 49.905
2021-01-16 | 15:03 | 49.901
2021-01-16 | 15:03 | 49.898
2021-01-16 | 15:03 | 49.896
2021-01-16 | 15:03 | 49.893
2021-01-16 | 15:03 | 49.891
2021-01-16 | 15:03 | 49.889
2021-01-16 | 15:03 | 49.893
2021-01-16 | 15:03 | 49.893
2021-01-16 | 15:03 | 49.895
2021-01-16 | 15:03 | 49.895
2021-01-16 | 15:03 | 49.893
2021-01-16 | 15:03 | 49.893
2021-01-16 | 15:03 | 49.893
2021-01-16 | 15:03 | 49.895
2021-01-16 | 15:03 | 49.898
2021-01-16 | 15:03 | 49.902
2021-01-16 | 15:03 | 49.909
2021-01-16 | 15:03 | 49.916
2021-01-16 | 15:03 | 49.923
2021-01-16 | 15:03 | 49.931
2021-01-16 | 15:03 | 49.939
2021-01-16 | 15:03 | 49.947
2021-01-16 | 15:03 | 49.956
2021-01-16 | 15:03 | 49.964
2021-01-16 | 15:03 | 49.972
2021-01-16 | 15:03 | 49.979
2021-01-16 | 15:03 | 49.983
2021-01-16 | 15:03 | 49.988
2021-01-16 | 15:03 | 49.99
2021-01-16 | 15:03 | 49.993
2021-01-16 | 15:03 | 49.994
2021-01-16 | 15:03 | 49.994
2021-01-16 | 15:03 | 49.992
2021-01-16 | 15:03 | 49.991
2021-01-16 | 15:03 | 49.992
2021-01-16 | 15:03 | 49.992
2021-01-16 | 15:03 | 49.992
2021-01-16 | 15:03 | 49.993
2021-01-16 | 15:03 | 49.992
2021-01-16 | 15:03 | 49.992
2021-01-16 | 15:03 | 49.992
2021-01-16 | 15:03 | 49.993
2021-01-16 | 15:03 | 49.992
2021-01-16 | 15:04 | 49.99
2021-01-16 | 15:04 | 49.989
2021-01-16 | 15:04 | 49.985
2021-01-16 | 15:04 | 49.981
2021-01-16 | 15:04 | 49.979
2021-01-16 | 15:04 | 49.976
2021-01-16 | 15:04 | 49.974
2021-01-16 | 15:04 | 49.974
2021-01-16 | 15:04 | 49.975
2021-01-16 | 15:04 | 49.974
2021-01-16 | 15:04 | 49.971
2021-01-16 | 15:04 | 49.97
2021-01-16 | 15:04 | 49.969
2021-01-16 | 15:04 | 49.968
2021-01-16 | 15:04 | 49.969
2021-01-16 | 15:04 | 49.973
2021-01-16 | 15:04 | 49.975
2021-01-16 | 15:04 | 49.976
2021-01-16 | 15:04 | 49.975
2021-01-16 | 15:04 | 49.977
2021-01-16 | 15:04 | 49.978
2021-01-16 | 15:04 | 49.976
2021-01-16 | 15:04 | 49.973
2021-01-16 | 15:04 | 49.971
2021-01-16 | 15:04 | 49.972
2021-01-16 | 15:04 | 49.967
2021-01-16 | 15:04 | 49.963
2021-01-16 | 15:04 | 49.961
2021-01-16 | 15:04 | 49.96
2021-01-16 | 15:04 | 49.958
2021-01-16 | 15:04 | 49.955
2021-01-16 | 15:04 | 49.954
2021-01-16 | 15:04 | 49.955
2021-01-16 | 15:04 | 49.956
2021-01-16 | 15:04 | 49.955
2021-01-16 | 15:04 | 49.956
2021-01-16 | 15:04 | 49.958
2021-01-16 | 15:04 | 49.959
2021-01-16 | 15:04 | 49.958
2021-01-16 | 15:04 | 49.957
2021-01-16 | 15:04 | 49.958
2021-01-16 | 15:04 | 49.958
2021-01-16 | 15:04 | 49.96
2021-01-16 | 15:04 | 49.961
2021-01-16 | 15:04 | 49.963
2021-01-16 | 15:04 | 49.967
2021-01-16 | 15:04 | 49.969
2021-01-16 | 15:04 | 49.971
2021-01-16 | 15:04 | 49.972
2021-01-16 | 15:04 | 49.974
2021-01-16 | 15:04 | 49.976
2021-01-16 | 15:04 | 49.976
2021-01-16 | 15:04 | 49.975
2021-01-16 | 15:04 | 49.97
2021-01-16 | 15:04 | 49.965
2021-01-16 | 15:04 | 49.963
2021-01-16 | 15:04 | 49.962
2021-01-16 | 15:04 | 49.961
2021-01-16 | 15:04 | 49.957
2021-01-16 | 15:04 | 49.96
2021-01-16 | 15:04 | 49.958
2021-01-16 | 15:05 | 49.952
2021-01-16 | 15:05 | 49.95
2021-01-16 | 15:05 | 49.949
2021-01-16 | 15:05 | 49.949
2021-01-16 | 15:05 | 49.951
2021-01-16 | 15:05 | 49.95
2021-01-16 | 15:05 | 49.95
2021-01-16 | 15:05 | 49.95
2021-01-16 | 15:05 | 49.95
2021-01-16 | 15:05 | 49.952
2021-01-16 | 15:05 | 49.953
2021-01-16 | 15:05 | 49.952
2021-01-16 | 15:05 | 49.953
2021-01-16 | 15:05 | 49.956
2021-01-16 | 15:05 | 49.959
2021-01-16 | 15:05 | 49.958
2021-01-16 | 15:05 | 49.959
2021-01-16 | 15:05 | 49.961
2021-01-16 | 15:05 | 49.96
2021-01-16 | 15:05 | 49.962
2021-01-16 | 15:05 | 49.963
2021-01-16 | 15:05 | 49.962
2021-01-16 | 15:05 | 49.963
2021-01-16 | 15:05 | 49.965
2021-01-16 | 15:05 | 49.968
2021-01-16 | 15:05 | 49.968
2021-01-16 | 15:05 | 49.971
2021-01-16 | 15:05 | 49.971
2021-01-16 | 15:05 | 49.971
2021-01-16 | 15:05 | 49.97
2021-01-16 | 15:05 | 49.968
2021-01-16 | 15:05 | 49.965
2021-01-16 | 15:05 | 49.963
2021-01-16 | 15:05 | 49.961
2021-01-16 | 15:05 | 49.958
2021-01-16 | 15:05 | 49.96
2021-01-16 | 15:05 | 49.956
2021-01-16 | 15:05 | 49.956
2021-01-16 | 15:05 | 49.956
2021-01-16 | 15:05 | 49.957
2021-01-16 | 15:05 | 49.962
2021-01-16 | 15:05 | 49.966
2021-01-16 | 15:05 | 49.968
2021-01-16 | 15:05 | 49.97
2021-01-16 | 15:05 | 49.971
2021-01-16 | 15:05 | 49.973
2021-01-16 | 15:05 | 49.972
2021-01-16 | 15:05 | 49.967
2021-01-16 | 15:05 | 49.965
2021-01-16 | 15:05 | 49.96
2021-01-16 | 15:05 | 49.955
2021-01-16 | 15:05 | 49.947
2021-01-16 | 15:05 | 49.94
2021-01-16 | 15:05 | 49.933
2021-01-16 | 15:05 | 49.93
2021-01-16 | 15:05 | 49.927
2021-01-16 | 15:05 | 49.926
2021-01-16 | 15:05 | 49.928
2021-01-16 | 15:05 | 49.933
2021-01-16 | 15:06 | 49.938
2021-01-16 | 15:06 | 49.941
2021-01-16 | 15:06 | 49.942
2021-01-16 | 15:06 | 49.945
2021-01-16 | 15:06 | 49.944
2021-01-16 | 15:06 | 49.941
2021-01-16 | 15:06 | 49.937
2021-01-16 | 15:06 | 49.932
2021-01-16 | 15:06 | 49.929
2021-01-16 | 15:06 | 49.927
2021-01-16 | 15:06 | 49.925
2021-01-16 | 15:06 | 49.924
2021-01-16 | 15:06 | 49.923
2021-01-16 | 15:06 | 49.922
2021-01-16 | 15:06 | 49.92
2021-01-16 | 15:06 | 49.92
2021-01-16 | 15:06 | 49.92
2021-01-16 | 15:06 | 49.922
2021-01-16 | 15:06 | 49.921
2021-01-16 | 15:06 | 49.923
2021-01-16 | 15:06 | 49.922
2021-01-16 | 15:06 | 49.925
2021-01-16 | 15:06 | 49.924
2021-01-16 | 15:06 | 49.924
2021-01-16 | 15:06 | 49.924
2021-01-16 | 15:06 | 49.924
2021-01-16 | 15:06 | 49.925
2021-01-16 | 15:06 | 49.926
2021-01-16 | 15:06 | 49.927
2021-01-16 | 15:06 | 49.927
2021-01-16 | 15:06 | 49.929
2021-01-16 | 15:06 | 49.93
2021-01-16 | 15:06 | 49.928
2021-01-16 | 15:06 | 49.927
2021-01-16 | 15:06 | 49.923
2021-01-16 | 15:06 | 49.924
2021-01-16 | 15:06 | 49.923
2021-01-16 | 15:06 | 49.921
2021-01-16 | 15:06 | 49.924
2021-01-16 | 15:06 | 49.924
2021-01-16 | 15:06 | 49.923
2021-01-16 | 15:06 | 49.923
2021-01-16 | 15:06 | 49.924
2021-01-16 | 15:06 | 49.925
2021-01-16 | 15:06 | 49.926
2021-01-16 | 15:06 | 49.927
2021-01-16 | 15:06 | 49.928
2021-01-16 | 15:06 | 49.93
2021-01-16 | 15:06 | 49.931
2021-01-16 | 15:06 | 49.929
2021-01-16 | 15:06 | 49.93
2021-01-16 | 15:06 | 49.933
2021-01-16 | 15:06 | 49.933
2021-01-16 | 15:06 | 49.935
2021-01-16 | 15:06 | 49.934
2021-01-16 | 15:06 | 49.934
2021-01-16 | 15:06 | 49.933
2021-01-16 | 15:06 | 49.932
2021-01-16 | 15:06 | 49.933
2021-01-16 | 15:06 | 49.935
2021-01-16 | 15:06 | 49.935
2021-01-16 | 15:07 | 49.933
2021-01-16 | 15:07 | 49.933
2021-01-16 | 15:07 | 49.932
2021-01-16 | 15:07 | 49.933
2021-01-16 | 15:07 | 49.933
2021-01-16 | 15:07 | 49.936
2021-01-16 | 15:07 | 49.939
2021-01-16 | 15:07 | 49.943
2021-01-16 | 15:07 | 49.947
2021-01-16 | 15:07 | 49.948
2021-01-16 | 15:07 | 49.95
2021-01-16 | 15:07 | 49.953
2021-01-16 | 15:07 | 49.953
2021-01-16 | 15:07 | 49.953
2021-01-16 | 15:07 | 49.955
2021-01-16 | 15:07 | 49.957
2021-01-16 | 15:07 | 49.958
2021-01-16 | 15:07 | 49.958
2021-01-16 | 15:07 | 49.959
2021-01-16 | 15:07 | 49.962
2021-01-16 | 15:07 | 49.963
2021-01-16 | 15:07 | 49.964
2021-01-16 | 15:07 | 49.964
2021-01-16 | 15:07 | 49.967
2021-01-16 | 15:07 | 49.966
2021-01-16 | 15:07 | 49.967
2021-01-16 | 15:07 | 49.967
2021-01-16 | 15:07 | 49.965
2021-01-16 | 15:07 | 49.963
2021-01-16 | 15:07 | 49.962
2021-01-16 | 15:07 | 49.959
2021-01-16 | 15:07 | 49.963
2021-01-16 | 15:07 | 49.964
2021-01-16 | 15:07 | 49.967
2021-01-16 | 15:07 | 49.971
2021-01-16 | 15:07 | 49.974
2021-01-16 | 15:07 | 49.977
2021-01-16 | 15:07 | 49.981
2021-01-16 | 15:07 | 49.982
2021-01-16 | 15:07 | 49.984
2021-01-16 | 15:07 | 49.987
2021-01-16 | 15:07 | 49.986
2021-01-16 | 15:07 | 49.983
2021-01-16 | 15:07 | 49.98
2021-01-16 | 15:07 | 49.981
2021-01-16 | 15:07 | 49.979
2021-01-16 | 15:07 | 49.979
2021-01-16 | 15:07 | 49.979
2021-01-16 | 15:07 | 49.98
2021-01-16 | 15:07 | 49.983
2021-01-16 | 15:07 | 49.985
2021-01-16 | 15:07 | 49.985
2021-01-16 | 15:07 | 49.984
2021-01-16 | 15:07 | 49.983
2021-01-16 | 15:07 | 49.983
2021-01-16 | 15:07 | 49.983
2021-01-16 | 15:07 | 49.981
2021-01-16 | 15:07 | 49.979
2021-01-16 | 15:07 | 49.975
2021-01-16 | 15:08 | 49.972
2021-01-16 | 15:08 | 49.969
2021-01-16 | 15:08 | 49.969
2021-01-16 | 15:08 | 49.966
2021-01-16 | 15:08 | 49.966
2021-01-16 | 15:08 | 49.964
2021-01-16 | 15:08 | 49.964
2021-01-16 | 15:08 | 49.964
2021-01-16 | 15:08 | 49.964
2021-01-16 | 15:08 | 49.966
2021-01-16 | 15:08 | 49.967
2021-01-16 | 15:08 | 49.968
2021-01-16 | 15:08 | 49.967
2021-01-16 | 15:08 | 49.97
2021-01-16 | 15:08 | 49.971
2021-01-16 | 15:08 | 49.97
2021-01-16 | 15:08 | 49.972
2021-01-16 | 15:08 | 49.971
2021-01-16 | 15:08 | 49.971
2021-01-16 | 15:08 | 49.972
2021-01-16 | 15:08 | 49.971
2021-01-16 | 15:08 | 49.973
2021-01-16 | 15:08 | 49.973
2021-01-16 | 15:08 | 49.972
2021-01-16 | 15:08 | 49.972
2021-01-16 | 15:08 | 49.971
2021-01-16 | 15:08 | 49.97
2021-01-16 | 15:08 | 49.97
2021-01-16 | 15:08 | 49.969
2021-01-16 | 15:08 | 49.968
2021-01-16 | 15:08 | 49.969
2021-01-16 | 15:08 | 49.97
2021-01-16 | 15:08 | 49.971
2021-01-16 | 15:08 | 49.972
2021-01-16 | 15:08 | 49.969
2021-01-16 | 15:08 | 49.968
2021-01-16 | 15:08 | 49.967
2021-01-16 | 15:08 | 49.964
2021-01-16 | 15:08 | 49.963
2021-01-16 | 15:08 | 49.961
2021-01-16 | 15:08 | 49.958
2021-01-16 | 15:08 | 49.958
2021-01-16 | 15:08 | 49.959
2021-01-16 | 15:08 | 49.958
2021-01-16 | 15:08 | 49.958
2021-01-16 | 15:08 | 49.959
2021-01-16 | 15:08 | 49.957
2021-01-16 | 15:08 | 49.958
2021-01-16 | 15:08 | 49.96
2021-01-16 | 15:08 | 49.961
2021-01-16 | 15:08 | 49.961
2021-01-16 | 15:08 | 49.96
2021-01-16 | 15:08 | 49.958
2021-01-16 | 15:08 | 49.958
2021-01-16 | 15:08 | 49.957
2021-01-16 | 15:08 | 49.957
2021-01-16 | 15:08 | 49.956
2021-01-16 | 15:08 | 49.956
2021-01-16 | 15:08 | 49.956
2021-01-16 | 15:08 | 49.954
2021-01-16 | 15:08 | 49.954
2021-01-16 | 15:09 | 49.955
2021-01-16 | 15:09 | 49.956
2021-01-16 | 15:09 | 49.959
2021-01-16 | 15:09 | 49.96
2021-01-16 | 15:09 | 49.963
2021-01-16 | 15:09 | 49.967
2021-01-16 | 15:09 | 49.968
2021-01-16 | 15:09 | 49.971
2021-01-16 | 15:09 | 49.97
2021-01-16 | 15:09 | 49.969
2021-01-16 | 15:09 | 49.968
2021-01-16 | 15:09 | 49.969
2021-01-16 | 15:09 | 49.972
2021-01-16 | 15:09 | 49.974
2021-01-16 | 15:09 | 49.976
2021-01-16 | 15:09 | 49.98
2021-01-16 | 15:09 | 49.979
2021-01-16 | 15:09 | 49.98
2021-01-16 | 15:09 | 49.98
2021-01-16 | 15:09 | 49.977
2021-01-16 | 15:09 | 49.975
2021-01-16 | 15:09 | 49.971
2021-01-16 | 15:09 | 49.968
2021-01-16 | 15:09 | 49.966
2021-01-16 | 15:09 | 49.965
2021-01-16 | 15:09 | 49.962
2021-01-16 | 15:09 | 49.961
2021-01-16 | 15:09 | 49.957
2021-01-16 | 15:09 | 49.954
2021-01-16 | 15:09 | 49.954
2021-01-16 | 15:09 | 49.956
2021-01-16 | 15:09 | 49.957
2021-01-16 | 15:09 | 49.956
2021-01-16 | 15:09 | 49.957
2021-01-16 | 15:09 | 49.956
2021-01-16 | 15:09 | 49.957
2021-01-16 | 15:09 | 49.958
2021-01-16 | 15:09 | 49.958
2021-01-16 | 15:09 | 49.957
2021-01-16 | 15:09 | 49.957
2021-01-16 | 15:09 | 49.958
2021-01-16 | 15:09 | 49.958
2021-01-16 | 15:09 | 49.96
2021-01-16 | 15:09 | 49.964
2021-01-16 | 15:09 | 49.971
2021-01-16 | 15:09 | 49.976
2021-01-16 | 15:09 | 49.977
2021-01-16 | 15:09 | 49.978
2021-01-16 | 15:09 | 49.977
2021-01-16 | 15:09 | 49.975
2021-01-16 | 15:09 | 49.976
2021-01-16 | 15:09 | 49.976
2021-01-16 | 15:09 | 49.976
2021-01-16 | 15:09 | 49.974
2021-01-16 | 15:09 | 49.973
2021-01-16 | 15:09 | 49.975
2021-01-16 | 15:09 | 49.974
2021-01-16 | 15:09 | 49.972
2021-01-16 | 15:09 | 49.971
2021-01-16 | 15:10 | 49.97
2021-01-16 | 15:10 | 49.971
2021-01-16 | 15:10 | 49.974
2021-01-16 | 15:10 | 49.976
2021-01-16 | 15:10 | 49.977
2021-01-16 | 15:10 | 49.976
2021-01-16 | 15:10 | 49.977
2021-01-16 | 15:10 | 49.979
2021-01-16 | 15:10 | 49.977
2021-01-16 | 15:10 | 49.978
2021-01-16 | 15:10 | 49.976
2021-01-16 | 15:10 | 49.974
2021-01-16 | 15:10 | 49.975
2021-01-16 | 15:10 | 49.974
2021-01-16 | 15:10 | 49.975
2021-01-16 | 15:10 | 49.976
2021-01-16 | 15:10 | 49.975
2021-01-16 | 15:10 | 49.973
2021-01-16 | 15:10 | 49.972
2021-01-16 | 15:10 | 49.97
2021-01-16 | 15:10 | 49.97
2021-01-16 | 15:10 | 49.972
2021-01-16 | 15:10 | 49.974
2021-01-16 | 15:10 | 49.976
2021-01-16 | 15:10 | 49.976
2021-01-16 | 15:10 | 49.978
2021-01-16 | 15:10 | 49.978
2021-01-16 | 15:10 | 49.98
2021-01-16 | 15:10 | 49.981
2021-01-16 | 15:10 | 49.979
2021-01-16 | 15:10 | 49.978
2021-01-16 | 15:10 | 49.978
2021-01-16 | 15:10 | 49.975
2021-01-16 | 15:10 | 49.973
2021-01-16 | 15:10 | 49.971
2021-01-16 | 15:10 | 49.97
2021-01-16 | 15:10 | 49.969
2021-01-16 | 15:10 | 49.966
2021-01-16 | 15:10 | 49.964
2021-01-16 | 15:10 | 49.965
2021-01-16 | 15:10 | 49.963
2021-01-16 | 15:10 | 49.964
2021-01-16 | 15:10 | 49.963
2021-01-16 | 15:10 | 49.963
2021-01-16 | 15:10 | 49.963
2021-01-16 | 15:10 | 49.966
2021-01-16 | 15:10 | 49.968
2021-01-16 | 15:10 | 49.97
2021-01-16 | 15:10 | 49.97
2021-01-16 | 15:10 | 49.972
2021-01-16 | 15:10 | 49.976
2021-01-16 | 15:10 | 49.974
2021-01-16 | 15:10 | 49.975
2021-01-16 | 15:10 | 49.976
2021-01-16 | 15:10 | 49.975
2021-01-16 | 15:10 | 49.978
2021-01-16 | 15:10 | 49.98
2021-01-16 | 15:10 | 49.984
2021-01-16 | 15:10 | 49.987
2021-01-16 | 15:10 | 49.988
2021-01-16 | 15:10 | 49.989
2021-01-16 | 15:11 | 49.988
2021-01-16 | 15:11 | 49.99
2021-01-16 | 15:11 | 49.993
2021-01-16 | 15:11 | 49.992
2021-01-16 | 15:11 | 49.992
2021-01-16 | 15:11 | 49.988
2021-01-16 | 15:11 | 49.984
2021-01-16 | 15:11 | 49.98
2021-01-16 | 15:11 | 49.978
2021-01-16 | 15:11 | 49.976
2021-01-16 | 15:11 | 49.974
2021-01-16 | 15:11 | 49.971
2021-01-16 | 15:11 | 49.971
2021-01-16 | 15:11 | 49.968
2021-01-16 | 15:11 | 49.965
2021-01-16 | 15:11 | 49.964
2021-01-16 | 15:11 | 49.961
2021-01-16 | 15:11 | 49.958
2021-01-16 | 15:11 | 49.959
2021-01-16 | 15:11 | 49.959
2021-01-16 | 15:11 | 49.962
2021-01-16 | 15:11 | 49.965
2021-01-16 | 15:11 | 49.964
2021-01-16 | 15:11 | 49.965
2021-01-16 | 15:11 | 49.968
2021-01-16 | 15:11 | 49.97
2021-01-16 | 15:11 | 49.971
2021-01-16 | 15:11 | 49.971
2021-01-16 | 15:11 | 49.969
2021-01-16 | 15:11 | 49.969
2021-01-16 | 15:11 | 49.966
2021-01-16 | 15:11 | 49.968
2021-01-16 | 15:11 | 49.967
2021-01-16 | 15:11 | 49.968
2021-01-16 | 15:11 | 49.969
2021-01-16 | 15:11 | 49.969
2021-01-16 | 15:11 | 49.97
2021-01-16 | 15:11 | 49.97
2021-01-16 | 15:11 | 49.971
2021-01-16 | 15:11 | 49.972
2021-01-16 | 15:11 | 49.974
2021-01-16 | 15:11 | 49.974
2021-01-16 | 15:11 | 49.975
2021-01-16 | 15:11 | 49.973
2021-01-16 | 15:11 | 49.974
2021-01-16 | 15:11 | 49.973
2021-01-16 | 15:11 | 49.972
2021-01-16 | 15:11 | 49.971
2021-01-16 | 15:11 | 49.968
2021-01-16 | 15:11 | 49.965
2021-01-16 | 15:11 | 49.963
2021-01-16 | 15:11 | 49.965
2021-01-16 | 15:11 | 49.964
2021-01-16 | 15:11 | 49.965
2021-01-16 | 15:11 | 49.966
2021-01-16 | 15:11 | 49.966
2021-01-16 | 15:11 | 49.968
2021-01-16 | 15:11 | 49.968
2021-01-16 | 15:11 | 49.969
2021-01-16 | 15:12 | 49.971
2021-01-16 | 15:12 | 49.975
2021-01-16 | 15:12 | 49.977
2021-01-16 | 15:12 | 49.981
2021-01-16 | 15:12 | 49.984
2021-01-16 | 15:12 | 49.984
2021-01-16 | 15:12 | 49.985
2021-01-16 | 15:12 | 49.984
2021-01-16 | 15:12 | 49.987
2021-01-16 | 15:12 | 49.986
2021-01-16 | 15:12 | 49.99
2021-01-16 | 15:12 | 49.99
2021-01-16 | 15:12 | 49.991
2021-01-16 | 15:12 | 49.991
2021-01-16 | 15:12 | 49.991
2021-01-16 | 15:12 | 49.99
2021-01-16 | 15:12 | 49.992
2021-01-16 | 15:12 | 49.992
2021-01-16 | 15:12 | 49.99
2021-01-16 | 15:12 | 49.987
2021-01-16 | 15:12 | 49.986
2021-01-16 | 15:12 | 49.982
2021-01-16 | 15:12 | 49.98
2021-01-16 | 15:12 | 49.977
2021-01-16 | 15:12 | 49.975
2021-01-16 | 15:12 | 49.976
2021-01-16 | 15:12 | 49.975
2021-01-16 | 15:12 | 49.976
2021-01-16 | 15:12 | 49.976
2021-01-16 | 15:12 | 49.977
2021-01-16 | 15:12 | 49.975
2021-01-16 | 15:12 | 49.974
2021-01-16 | 15:12 | 49.971
2021-01-16 | 15:12 | 49.971
2021-01-16 | 15:12 | 49.972
2021-01-16 | 15:12 | 49.971
2021-01-16 | 15:12 | 49.97
2021-01-16 | 15:12 | 49.968
2021-01-16 | 15:12 | 49.968
2021-01-16 | 15:12 | 49.966
2021-01-16 | 15:12 | 49.967
2021-01-16 | 15:12 | 49.966
2021-01-16 | 15:12 | 49.966
2021-01-16 | 15:12 | 49.966
2021-01-16 | 15:12 | 49.965
2021-01-16 | 15:12 | 49.964
2021-01-16 | 15:12 | 49.964
2021-01-16 | 15:12 | 49.964
2021-01-16 | 15:12 | 49.961
2021-01-16 | 15:12 | 49.961
2021-01-16 | 15:12 | 49.956
2021-01-16 | 15:12 | 49.955
2021-01-16 | 15:12 | 49.955
2021-01-16 | 15:12 | 49.954
2021-01-16 | 15:12 | 49.956
2021-01-16 | 15:12 | 49.957
2021-01-16 | 15:12 | 49.955
2021-01-16 | 15:12 | 49.955
2021-01-16 | 15:12 | 49.955
2021-01-16 | 15:12 | 49.954
2021-01-16 | 15:12 | 49.954
2021-01-16 | 15:13 | 49.951
2021-01-16 | 15:13 | 49.947
2021-01-16 | 15:13 | 49.946
2021-01-16 | 15:13 | 49.948
2021-01-16 | 15:13 | 49.952
2021-01-16 | 15:13 | 49.958
2021-01-16 | 15:13 | 49.961
2021-01-16 | 15:13 | 49.966
2021-01-16 | 15:13 | 49.972
2021-01-16 | 15:13 | 49.975
2021-01-16 | 15:13 | 49.978
2021-01-16 | 15:13 | 49.982
2021-01-16 | 15:13 | 49.984
2021-01-16 | 15:13 | 49.985
2021-01-16 | 15:13 | 49.984
2021-01-16 | 15:13 | 49.983
2021-01-16 | 15:13 | 49.983
2021-01-16 | 15:13 | 49.981
2021-01-16 | 15:13 | 49.979
2021-01-16 | 15:13 | 49.975
2021-01-16 | 15:13 | 49.974
2021-01-16 | 15:13 | 49.974
2021-01-16 | 15:13 | 49.971
2021-01-16 | 15:13 | 49.972
2021-01-16 | 15:13 | 49.971
2021-01-16 | 15:13 | 49.971
2021-01-16 | 15:13 | 49.972
2021-01-16 | 15:13 | 49.972
2021-01-16 | 15:13 | 49.972
2021-01-16 | 15:13 | 49.973
2021-01-16 | 15:13 | 49.97
2021-01-16 | 15:13 | 49.972
2021-01-16 | 15:13 | 49.971
2021-01-16 | 15:13 | 49.968
2021-01-16 | 15:13 | 49.97
2021-01-16 | 15:13 | 49.969
2021-01-16 | 15:13 | 49.968
2021-01-16 | 15:13 | 49.97
2021-01-16 | 15:13 | 49.969
2021-01-16 | 15:13 | 49.97
2021-01-16 | 15:13 | 49.971
2021-01-16 | 15:13 | 49.971
2021-01-16 | 15:13 | 49.972
2021-01-16 | 15:13 | 49.975
2021-01-16 | 15:13 | 49.974
2021-01-16 | 15:13 | 49.976
2021-01-16 | 15:13 | 49.975
2021-01-16 | 15:13 | 49.974
2021-01-16 | 15:13 | 49.977
2021-01-16 | 15:13 | 49.979
2021-01-16 | 15:13 | 49.98
2021-01-16 | 15:13 | 49.983
2021-01-16 | 15:13 | 49.982
2021-01-16 | 15:13 | 49.979
2021-01-16 | 15:13 | 49.979
2021-01-16 | 15:13 | 49.977
2021-01-16 | 15:13 | 49.978
2021-01-16 | 15:13 | 49.977
2021-01-16 | 15:13 | 49.979
2021-01-16 | 15:14 | 49.977
2021-01-16 | 15:14 | 49.975
2021-01-16 | 15:14 | 49.975
2021-01-16 | 15:14 | 49.973
2021-01-16 | 15:14 | 49.974
2021-01-16 | 15:14 | 49.974
2021-01-16 | 15:14 | 49.973
2021-01-16 | 15:14 | 49.974
2021-01-16 | 15:14 | 49.975
2021-01-16 | 15:14 | 49.975
2021-01-16 | 15:14 | 49.978
2021-01-16 | 15:14 | 49.98
2021-01-16 | 15:14 | 49.983
2021-01-16 | 15:14 | 49.988
2021-01-16 | 15:14 | 49.99
2021-01-16 | 15:14 | 49.993
2021-01-16 | 15:14 | 49.995
2021-01-16 | 15:14 | 49.998
2021-01-16 | 15:14 | 49.999
2021-01-16 | 15:14 | 49.999
2021-01-16 | 15:14 | 50
2021-01-16 | 15:14 | 49.999
2021-01-16 | 15:14 | 50.001
2021-01-16 | 15:14 | 50.003
2021-01-16 | 15:14 | 50.002
2021-01-16 | 15:14 | 50.002
2021-01-16 | 15:14 | 50.001
2021-01-16 | 15:14 | 49.997
2021-01-16 | 15:14 | 49.996
2021-01-16 | 15:14 | 49.991
2021-01-16 | 15:14 | 49.987
2021-01-16 | 15:14 | 49.981
2021-01-16 | 15:14 | 49.977
2021-01-16 | 15:14 | 49.974
2021-01-16 | 15:14 | 49.972
2021-01-16 | 15:14 | 49.973
2021-01-16 | 15:14 | 49.97
2021-01-16 | 15:14 | 49.967
2021-01-16 | 15:14 | 49.968
2021-01-16 | 15:14 | 49.963
2021-01-16 | 15:14 | 49.96
2021-01-16 | 15:14 | 49.957
2021-01-16 | 15:14 | 49.957
2021-01-16 | 15:14 | 49.957
2021-01-16 | 15:14 | 49.96
2021-01-16 | 15:14 | 49.96
2021-01-16 | 15:14 | 49.961
2021-01-16 | 15:14 | 49.965
2021-01-16 | 15:14 | 49.966
2021-01-16 | 15:14 | 49.967
2021-01-16 | 15:14 | 49.971
2021-01-16 | 15:14 | 49.973
2021-01-16 | 15:14 | 49.974
2021-01-16 | 15:14 | 49.977
2021-01-16 | 15:14 | 49.978
2021-01-16 | 15:14 | 49.978
2021-01-16 | 15:14 | 49.977
2021-01-16 | 15:14 | 49.978
2021-01-16 | 15:14 | 49.978
2021-01-16 | 15:14 | 49.979
2021-01-16 | 15:14 | 49.978
2021-01-16 | 15:15 | 49.979
2021-01-16 | 15:15 | 49.979
2021-01-16 | 15:15 | 49.979
2021-01-16 | 15:15 | 49.977
2021-01-16 | 15:15 | 49.979
2021-01-16 | 15:15 | 49.982
2021-01-16 | 15:15 | 49.983
2021-01-16 | 15:15 | 49.986
2021-01-16 | 15:15 | 49.987
2021-01-16 | 15:15 | 49.985
2021-01-16 | 15:15 | 49.987
2021-01-16 | 15:15 | 49.985
2021-01-16 | 15:15 | 49.983
2021-01-16 | 15:15 | 49.98
2021-01-16 | 15:15 | 49.978
2021-01-16 | 15:15 | 49.974
2021-01-16 | 15:15 | 49.972
2021-01-16 | 15:15 | 49.973
2021-01-16 | 15:15 | 49.973
2021-01-16 | 15:15 | 49.973
2021-01-16 | 15:15 | 49.974
2021-01-16 | 15:15 | 49.975
2021-01-16 | 15:15 | 49.976
2021-01-16 | 15:15 | 49.978
2021-01-16 | 15:15 | 49.978
2021-01-16 | 15:15 | 49.979
2021-01-16 | 15:15 | 49.98
2021-01-16 | 15:15 | 49.983
2021-01-16 | 15:15 | 49.986
2021-01-16 | 15:15 | 49.987
2021-01-16 | 15:15 | 49.988
2021-01-16 | 15:15 | 49.988
2021-01-16 | 15:15 | 49.987
2021-01-16 | 15:15 | 49.988
2021-01-16 | 15:15 | 49.987
2021-01-16 | 15:15 | 49.985
2021-01-16 | 15:15 | 49.986
2021-01-16 | 15:15 | 49.987
2021-01-16 | 15:15 | 49.986
2021-01-16 | 15:15 | 49.982
2021-01-16 | 15:15 | 49.981
2021-01-16 | 15:15 | 49.98
2021-01-16 | 15:15 | 49.981
2021-01-16 | 15:15 | 49.979
2021-01-16 | 15:15 | 49.978
2021-01-16 | 15:15 | 49.978
2021-01-16 | 15:15 | 49.979
2021-01-16 | 15:15 | 49.979
2021-01-16 | 15:15 | 49.982
2021-01-16 | 15:15 | 49.983
2021-01-16 | 15:15 | 49.986
2021-01-16 | 15:15 | 49.989
2021-01-16 | 15:15 | 49.991
2021-01-16 | 15:15 | 49.994
2021-01-16 | 15:15 | 49.995
2021-01-16 | 15:15 | 49.997
2021-01-16 | 15:15 | 49.999
2021-01-16 | 15:15 | 50.005
2021-01-16 | 15:15 | 50.009
2021-01-16 | 15:16 | 50.015
2021-01-16 | 15:16 | 50.019
2021-01-16 | 15:16 | 50.022
2021-01-16 | 15:16 | 50.025
2021-01-16 | 15:16 | 50.028
2021-01-16 | 15:16 | 50.028
2021-01-16 | 15:16 | 50.031
2021-01-16 | 15:16 | 50.033
2021-01-16 | 15:16 | 50.032
2021-01-16 | 15:16 | 50.031
2021-01-16 | 15:16 | 50.031
2021-01-16 | 15:16 | 50.031
2021-01-16 | 15:16 | 50.031
2021-01-16 | 15:16 | 50.034
2021-01-16 | 15:16 | 50.034
2021-01-16 | 15:16 | 50.033
2021-01-16 | 15:16 | 50.032
2021-01-16 | 15:16 | 50.031
2021-01-16 | 15:16 | 50.031
2021-01-16 | 15:16 | 50.029
2021-01-16 | 15:16 | 50.028
2021-01-16 | 15:16 | 50.025
2021-01-16 | 15:16 | 50.023
2021-01-16 | 15:16 | 50.022
2021-01-16 | 15:16 | 50.021
2021-01-16 | 15:16 | 50.02
2021-01-16 | 15:16 | 50.02
2021-01-16 | 15:16 | 50.019
2021-01-16 | 15:16 | 50.02
2021-01-16 | 15:16 | 50.019
2021-01-16 | 15:16 | 50.02
2021-01-16 | 15:16 | 50.02
2021-01-16 | 15:16 | 50.021
2021-01-16 | 15:16 | 50.023
2021-01-16 | 15:16 | 50.023
2021-01-16 | 15:16 | 50.023
2021-01-16 | 15:16 | 50.024
2021-01-16 | 15:16 | 50.025
2021-01-16 | 15:16 | 50.022
2021-01-16 | 15:16 | 50.022
2021-01-16 | 15:16 | 50.025
2021-01-16 | 15:16 | 50.026
2021-01-16 | 15:16 | 50.027
2021-01-16 | 15:16 | 50.027
2021-01-16 | 15:16 | 50.025
2021-01-16 | 15:16 | 50.027
2021-01-16 | 15:16 | 50.028
2021-01-16 | 15:16 | 50.026
2021-01-16 | 15:16 | 50.025
2021-01-16 | 15:16 | 50.025
2021-01-16 | 15:16 | 50.024
2021-01-16 | 15:16 | 50.025
2021-01-16 | 15:16 | 50.024
2021-01-16 | 15:16 | 50.024
2021-01-16 | 15:16 | 50.024
2021-01-16 | 15:16 | 50.025
2021-01-16 | 15:16 | 50.023
2021-01-16 | 15:16 | 50.022
2021-01-16 | 15:16 | 50.02
2021-01-16 | 15:16 | 50.02
2021-01-16 | 15:16 | 50.019
2021-01-16 | 15:17 | 50.019
2021-01-16 | 15:17 | 50.019
2021-01-16 | 15:17 | 50.022
2021-01-16 | 15:17 | 50.024
2021-01-16 | 15:17 | 50.025
2021-01-16 | 15:17 | 50.027
2021-01-16 | 15:17 | 50.029
2021-01-16 | 15:17 | 50.03
2021-01-16 | 15:17 | 50.029
2021-01-16 | 15:17 | 50.03
2021-01-16 | 15:17 | 50.028
2021-01-16 | 15:17 | 50.029
2021-01-16 | 15:17 | 50.031
2021-01-16 | 15:17 | 50.032
2021-01-16 | 15:17 | 50.036
2021-01-16 | 15:17 | 50.039
2021-01-16 | 15:17 | 50.041
2021-01-16 | 15:17 | 50.044
2021-01-16 | 15:17 | 50.043
2021-01-16 | 15:17 | 50.041
2021-01-16 | 15:17 | 50.04
2021-01-16 | 15:17 | 50.039
2021-01-16 | 15:17 | 50.033
2021-01-16 | 15:17 | 50.029
2021-01-16 | 15:17 | 50.025
2021-01-16 | 15:17 | 50.024
2021-01-16 | 15:17 | 50.025
2021-01-16 | 15:17 | 50.024
2021-01-16 | 15:17 | 50.024
2021-01-16 | 15:17 | 50.024
2021-01-16 | 15:17 | 50.024
2021-01-16 | 15:17 | 50.025
2021-01-16 | 15:17 | 50.026
2021-01-16 | 15:17 | 50.03
2021-01-16 | 15:17 | 50.033
2021-01-16 | 15:17 | 50.036
2021-01-16 | 15:17 | 50.037
2021-01-16 | 15:17 | 50.037
2021-01-16 | 15:17 | 50.038
2021-01-16 | 15:17 | 50.04
2021-01-16 | 15:17 | 50.04
2021-01-16 | 15:17 | 50.042
2021-01-16 | 15:17 | 50.044
2021-01-16 | 15:17 | 50.044
2021-01-16 | 15:17 | 50.045
2021-01-16 | 15:17 | 50.046
2021-01-16 | 15:17 | 50.043
2021-01-16 | 15:17 | 50.039
2021-01-16 | 15:17 | 50.035
2021-01-16 | 15:17 | 50.03
2021-01-16 | 15:17 | 50.028
2021-01-16 | 15:17 | 50.028
2021-01-16 | 15:17 | 50.028
2021-01-16 | 15:17 | 50.029
2021-01-16 | 15:17 | 50.029
2021-01-16 | 15:17 | 50.028
2021-01-16 | 15:17 | 50.026
2021-01-16 | 15:17 | 50.028
2021-01-16 | 15:17 | 50.028
2021-01-16 | 15:18 | 50.028
2021-01-16 | 15:18 | 50.029
2021-01-16 | 15:18 | 50.029
2021-01-16 | 15:18 | 50.031
2021-01-16 | 15:18 | 50.03
2021-01-16 | 15:18 | 50.031
2021-01-16 | 15:18 | 50.033
2021-01-16 | 15:18 | 50.036
2021-01-16 | 15:18 | 50.039
2021-01-16 | 15:18 | 50.044
2021-01-16 | 15:18 | 50.047
2021-01-16 | 15:18 | 50.049
2021-01-16 | 15:18 | 50.05
2021-01-16 | 15:18 | 50.053
2021-01-16 | 15:18 | 50.053
2021-01-16 | 15:18 | 50.054
2021-01-16 | 15:18 | 50.052
2021-01-16 | 15:18 | 50.049
2021-01-16 | 15:18 | 50.048
2021-01-16 | 15:18 | 50.048
2021-01-16 | 15:18 | 50.047
2021-01-16 | 15:18 | 50.044
2021-01-16 | 15:18 | 50.042
2021-01-16 | 15:18 | 50.038
2021-01-16 | 15:18 | 50.035
2021-01-16 | 15:18 | 50.034
2021-01-16 | 15:18 | 50.034
2021-01-16 | 15:18 | 50.034
2021-01-16 | 15:18 | 50.035
2021-01-16 | 15:18 | 50.032
2021-01-16 | 15:18 | 50.029
2021-01-16 | 15:18 | 50.028
2021-01-16 | 15:18 | 50.028
2021-01-16 | 15:18 | 50.028
2021-01-16 | 15:18 | 50.027
2021-01-16 | 15:18 | 50.026
2021-01-16 | 15:18 | 50.024
2021-01-16 | 15:18 | 50.025
2021-01-16 | 15:18 | 50.026
2021-01-16 | 15:18 | 50.025
2021-01-16 | 15:18 | 50.026
2021-01-16 | 15:18 | 50.024
2021-01-16 | 15:18 | 50.027
2021-01-16 | 15:18 | 50.027
2021-01-16 | 15:18 | 50.027
2021-01-16 | 15:18 | 50.029
2021-01-16 | 15:18 | 50.029
2021-01-16 | 15:18 | 50.03
2021-01-16 | 15:18 | 50.033
2021-01-16 | 15:18 | 50.036
2021-01-16 | 15:18 | 50.038
2021-01-16 | 15:18 | 50.039
2021-01-16 | 15:18 | 50.04
2021-01-16 | 15:18 | 50.044
2021-01-16 | 15:18 | 50.045
2021-01-16 | 15:18 | 50.046
2021-01-16 | 15:18 | 50.047
2021-01-16 | 15:18 | 50.049
2021-01-16 | 15:18 | 50.048
2021-01-16 | 15:18 | 50.046
2021-01-16 | 15:18 | 50.045
2021-01-16 | 15:19 | 50.045
2021-01-16 | 15:19 | 50.045
2021-01-16 | 15:19 | 50.044
2021-01-16 | 15:19 | 50.044
2021-01-16 | 15:19 | 50.046
2021-01-16 | 15:19 | 50.047
2021-01-16 | 15:19 | 50.048
2021-01-16 | 15:19 | 50.047
2021-01-16 | 15:19 | 50.048
2021-01-16 | 15:19 | 50.05
2021-01-16 | 15:19 | 50.051
2021-01-16 | 15:19 | 50.054
2021-01-16 | 15:19 | 50.056
2021-01-16 | 15:19 | 50.055
2021-01-16 | 15:19 | 50.056
2021-01-16 | 15:19 | 50.059
2021-01-16 | 15:19 | 50.059
2021-01-16 | 15:19 | 50.059
2021-01-16 | 15:19 | 50.06
2021-01-16 | 15:19 | 50.06
2021-01-16 | 15:19 | 50.062
2021-01-16 | 15:19 | 50.061
2021-01-16 | 15:19 | 50.06
2021-01-16 | 15:19 | 50.059
2021-01-16 | 15:19 | 50.053
2021-01-16 | 15:19 | 50.047
2021-01-16 | 15:19 | 50.041
2021-01-16 | 15:19 | 50.033
2021-01-16 | 15:19 | 50.025
2021-01-16 | 15:19 | 50.017
2021-01-16 | 15:19 | 50.009
2021-01-16 | 15:19 | 50.005
2021-01-16 | 15:19 | 50.004
2021-01-16 | 15:19 | 50.002
2021-01-16 | 15:19 | 50.001
2021-01-16 | 15:19 | 50.001
2021-01-16 | 15:19 | 49.999
2021-01-16 | 15:19 | 50.001
2021-01-16 | 15:19 | 50.003
2021-01-16 | 15:19 | 50.002
2021-01-16 | 15:19 | 50.003
2021-01-16 | 15:19 | 50.005
2021-01-16 | 15:19 | 50.006
2021-01-16 | 15:19 | 50.006
2021-01-16 | 15:19 | 50.006
2021-01-16 | 15:19 | 50.007
2021-01-16 | 15:19 | 50.007
2021-01-16 | 15:19 | 50.006
2021-01-16 | 15:19 | 50.006
2021-01-16 | 15:19 | 50.007
2021-01-16 | 15:19 | 50.008
2021-01-16 | 15:19 | 50.005
2021-01-16 | 15:19 | 50.003
2021-01-16 | 15:19 | 50.002
2021-01-16 | 15:19 | 50.001
2021-01-16 | 15:19 | 50
2021-01-16 | 15:19 | 49.998
2021-01-16 | 15:19 | 49.996
2021-01-16 | 15:19 | 49.992
2021-01-16 | 15:20 | 49.987
2021-01-16 | 15:20 | 49.983
2021-01-16 | 15:20 | 49.977
2021-01-16 | 15:20 | 49.971
2021-01-16 | 15:20 | 49.968
2021-01-16 | 15:20 | 49.969
2021-01-16 | 15:20 | 49.967
2021-01-16 | 15:20 | 49.966
2021-01-16 | 15:20 | 49.963
2021-01-16 | 15:20 | 49.962
2021-01-16 | 15:20 | 49.96
2021-01-16 | 15:20 | 49.959
2021-01-16 | 15:20 | 49.959
2021-01-16 | 15:20 | 49.959
2021-01-16 | 15:20 | 49.963
2021-01-16 | 15:20 | 49.964
2021-01-16 | 15:20 | 49.965
2021-01-16 | 15:20 | 49.966
2021-01-16 | 15:20 | 49.97
2021-01-16 | 15:20 | 49.971
2021-01-16 | 15:20 | 49.972
2021-01-16 | 15:20 | 49.973
2021-01-16 | 15:20 | 49.973
2021-01-16 | 15:20 | 49.974
2021-01-16 | 15:20 | 49.975
2021-01-16 | 15:20 | 49.978
2021-01-16 | 15:20 | 49.978
2021-01-16 | 15:20 | 49.978
2021-01-16 | 15:20 | 49.974
2021-01-16 | 15:20 | 49.972
2021-01-16 | 15:20 | 49.971
2021-01-16 | 15:20 | 49.967
2021-01-16 | 15:20 | 49.966
2021-01-16 | 15:20 | 49.965
2021-01-16 | 15:20 | 49.966
2021-01-16 | 15:20 | 49.968
2021-01-16 | 15:20 | 49.968
2021-01-16 | 15:20 | 49.97
2021-01-16 | 15:20 | 49.971
2021-01-16 | 15:20 | 49.968
2021-01-16 | 15:20 | 49.965
2021-01-16 | 15:20 | 49.962
2021-01-16 | 15:20 | 49.961
2021-01-16 | 15:20 | 49.96
2021-01-16 | 15:20 | 49.959
2021-01-16 | 15:20 | 49.96
2021-01-16 | 15:20 | 49.962
2021-01-16 | 15:20 | 49.961
2021-01-16 | 15:20 | 49.963
2021-01-16 | 15:20 | 49.966
2021-01-16 | 15:20 | 49.968
2021-01-16 | 15:20 | 49.971
2021-01-16 | 15:20 | 49.974
2021-01-16 | 15:20 | 49.977
2021-01-16 | 15:20 | 49.98
2021-01-16 | 15:20 | 49.982
2021-01-16 | 15:20 | 49.986
2021-01-16 | 15:20 | 49.99
2021-01-16 | 15:20 | 49.991
2021-01-16 | 15:20 | 49.994
2021-01-16 | 15:20 | 49.995
2021-01-16 | 15:21 | 49.995
2021-01-16 | 15:21 | 49.994
2021-01-16 | 15:21 | 49.993
2021-01-16 | 15:21 | 49.993
2021-01-16 | 15:21 | 49.994
2021-01-16 | 15:21 | 49.994
2021-01-16 | 15:21 | 49.994
2021-01-16 | 15:21 | 49.995
2021-01-16 | 15:21 | 49.992
2021-01-16 | 15:21 | 49.991
2021-01-16 | 15:21 | 49.991
2021-01-16 | 15:21 | 49.989
2021-01-16 | 15:21 | 49.991
2021-01-16 | 15:21 | 49.993
2021-01-16 | 15:21 | 49.994
2021-01-16 | 15:21 | 49.997
2021-01-16 | 15:21 | 49.998
2021-01-16 | 15:21 | 49.999
2021-01-16 | 15:21 | 49.998
2021-01-16 | 15:21 | 49.998
2021-01-16 | 15:21 | 49.997
2021-01-16 | 15:21 | 49.997
2021-01-16 | 15:21 | 49.993
2021-01-16 | 15:21 | 49.99
2021-01-16 | 15:21 | 49.986
2021-01-16 | 15:21 | 49.98
2021-01-16 | 15:21 | 49.976
2021-01-16 | 15:21 | 49.975
2021-01-16 | 15:21 | 49.973
2021-01-16 | 15:21 | 49.973
2021-01-16 | 15:21 | 49.972
2021-01-16 | 15:21 | 49.971
2021-01-16 | 15:21 | 49.969
2021-01-16 | 15:21 | 49.969
2021-01-16 | 15:21 | 49.967
2021-01-16 | 15:21 | 49.967
2021-01-16 | 15:21 | 49.968
2021-01-16 | 15:21 | 49.968
2021-01-16 | 15:21 | 49.968
2021-01-16 | 15:21 | 49.967
2021-01-16 | 15:21 | 49.964
2021-01-16 | 15:21 | 49.962
2021-01-16 | 15:21 | 49.96
2021-01-16 | 15:21 | 49.96
2021-01-16 | 15:21 | 49.961
2021-01-16 | 15:21 | 49.96
2021-01-16 | 15:21 | 49.961
2021-01-16 | 15:21 | 49.963
2021-01-16 | 15:21 | 49.967
2021-01-16 | 15:21 | 49.972
2021-01-16 | 15:21 | 49.974
2021-01-16 | 15:21 | 49.976
2021-01-16 | 15:21 | 49.976
2021-01-16 | 15:21 | 49.98
2021-01-16 | 15:21 | 49.978
2021-01-16 | 15:21 | 49.983
2021-01-16 | 15:21 | 49.985
2021-01-16 | 15:21 | 49.987
2021-01-16 | 15:21 | 49.985
2021-01-16 | 15:22 | 49.986
2021-01-16 | 15:22 | 49.985
2021-01-16 | 15:22 | 49.985
2021-01-16 | 15:22 | 49.985
2021-01-16 | 15:22 | 49.983
2021-01-16 | 15:22 | 49.983
2021-01-16 | 15:22 | 49.984
2021-01-16 | 15:22 | 49.985
2021-01-16 | 15:22 | 49.986
2021-01-16 | 15:22 | 49.988
2021-01-16 | 15:22 | 49.989
2021-01-16 | 15:22 | 49.99
2021-01-16 | 15:22 | 49.992
2021-01-16 | 15:22 | 49.993
2021-01-16 | 15:22 | 49.996
2021-01-16 | 15:22 | 49.997
2021-01-16 | 15:22 | 49.998
2021-01-16 | 15:22 | 50
2021-01-16 | 15:22 | 49.999
2021-01-16 | 15:22 | 50.001
2021-01-16 | 15:22 | 50.004
2021-01-16 | 15:22 | 50.005
2021-01-16 | 15:22 | 50.006
2021-01-16 | 15:22 | 50.007
2021-01-16 | 15:22 | 50.007
2021-01-16 | 15:22 | 50.008
2021-01-16 | 15:22 | 50.012
2021-01-16 | 15:22 | 50.012
2021-01-16 | 15:22 | 50.018
2021-01-16 | 15:22 | 50.021
2021-01-16 | 15:22 | 50.021
2021-01-16 | 15:22 | 50.023
2021-01-16 | 15:22 | 50.022
2021-01-16 | 15:22 | 50.022
2021-01-16 | 15:22 | 50.023
2021-01-16 | 15:22 | 50.018
2021-01-16 | 15:22 | 50.018
2021-01-16 | 15:22 | 50.018
2021-01-16 | 15:22 | 50.017
2021-01-16 | 15:22 | 50.015
2021-01-16 | 15:22 | 50.018
2021-01-16 | 15:22 | 50.02
2021-01-16 | 15:22 | 50.021
2021-01-16 | 15:22 | 50.022
2021-01-16 | 15:22 | 50.022
2021-01-16 | 15:22 | 50.023
2021-01-16 | 15:22 | 50.023
2021-01-16 | 15:22 | 50.025
2021-01-16 | 15:22 | 50.027
2021-01-16 | 15:22 | 50.03
2021-01-16 | 15:22 | 50.035
2021-01-16 | 15:22 | 50.038
2021-01-16 | 15:22 | 50.04
2021-01-16 | 15:22 | 50.043
2021-01-16 | 15:22 | 50.044
2021-01-16 | 15:22 | 50.044
2021-01-16 | 15:22 | 50.042
2021-01-16 | 15:22 | 50.039
2021-01-16 | 15:22 | 50.038
2021-01-16 | 15:22 | 50.033
2021-01-16 | 15:22 | 50.03
2021-01-16 | 15:23 | 50.028
2021-01-16 | 15:23 | 50.027
2021-01-16 | 15:23 | 50.026
2021-01-16 | 15:23 | 50.026
2021-01-16 | 15:23 | 50.027
2021-01-16 | 15:23 | 50.027
2021-01-16 | 15:23 | 50.028
2021-01-16 | 15:23 | 50.027
2021-01-16 | 15:23 | 50.026
2021-01-16 | 15:23 | 50.028
2021-01-16 | 15:23 | 50.027
2021-01-16 | 15:23 | 50.028
2021-01-16 | 15:23 | 50.029
2021-01-16 | 15:23 | 50.03
2021-01-16 | 15:23 | 50.033
2021-01-16 | 15:23 | 50.034
2021-01-16 | 15:23 | 50.038
2021-01-16 | 15:23 | 50.04
2021-01-16 | 15:23 | 50.042
2021-01-16 | 15:23 | 50.043
2021-01-16 | 15:23 | 50.043
2021-01-16 | 15:23 | 50.044
2021-01-16 | 15:23 | 50.045
2021-01-16 | 15:23 | 50.045
2021-01-16 | 15:23 | 50.044
2021-01-16 | 15:23 | 50.041
2021-01-16 | 15:23 | 50.043
2021-01-16 | 15:23 | 50.042
2021-01-16 | 15:23 | 50.04
2021-01-16 | 15:23 | 50.04
2021-01-16 | 15:23 | 50.037
2021-01-16 | 15:23 | 50.035
2021-01-16 | 15:23 | 50.031
2021-01-16 | 15:23 | 50.028
2021-01-16 | 15:23 | 50.023
2021-01-16 | 15:23 | 50.018
2021-01-16 | 15:23 | 50.015
2021-01-16 | 15:23 | 50.014
2021-01-16 | 15:23 | 50.01
2021-01-16 | 15:23 | 50.01
2021-01-16 | 15:23 | 50.008
2021-01-16 | 15:23 | 50.01
2021-01-16 | 15:23 | 50.01
2021-01-16 | 15:23 | 50.012
2021-01-16 | 15:23 | 50.015
2021-01-16 | 15:23 | 50.017
2021-01-16 | 15:23 | 50.018
2021-01-16 | 15:23 | 50.019
2021-01-16 | 15:23 | 50.022
2021-01-16 | 15:23 | 50.025
2021-01-16 | 15:23 | 50.026
2021-01-16 | 15:23 | 50.028
2021-01-16 | 15:23 | 50.025
2021-01-16 | 15:23 | 50.025
2021-01-16 | 15:23 | 50.025
2021-01-16 | 15:23 | 50.023
2021-01-16 | 15:23 | 50.024
2021-01-16 | 15:23 | 50.023
2021-01-16 | 15:23 | 50.026
2021-01-16 | 15:24 | 50.029
2021-01-16 | 15:24 | 50.029
2021-01-16 | 15:24 | 50.032
2021-01-16 | 15:24 | 50.032
2021-01-16 | 15:24 | 50.034
2021-01-16 | 15:24 | 50.035
2021-01-16 | 15:24 | 50.035
2021-01-16 | 15:24 | 50.035
2021-01-16 | 15:24 | 50.032
2021-01-16 | 15:24 | 50.035
2021-01-16 | 15:24 | 50.042
2021-01-16 | 15:24 | 50.047
2021-01-16 | 15:24 | 50.052
2021-01-16 | 15:24 | 50.055
2021-01-16 | 15:24 | 50.058
2021-01-16 | 15:24 | 50.061
2021-01-16 | 15:24 | 50.061
2021-01-16 | 15:24 | 50.06
2021-01-16 | 15:24 | 50.061
2021-01-16 | 15:24 | 50.059
2021-01-16 | 15:24 | 50.063
2021-01-16 | 15:24 | 50.065
2021-01-16 | 15:24 | 50.068
2021-01-16 | 15:24 | 50.069
2021-01-16 | 15:24 | 50.074
2021-01-16 | 15:24 | 50.076
2021-01-16 | 15:24 | 50.078
2021-01-16 | 15:24 | 50.081
2021-01-16 | 15:24 | 50.082
2021-01-16 | 15:24 | 50.085
2021-01-16 | 15:24 | 50.085
2021-01-16 | 15:24 | 50.086
2021-01-16 | 15:24 | 50.084
2021-01-16 | 15:24 | 50.086
2021-01-16 | 15:24 | 50.084
2021-01-16 | 15:24 | 50.085
2021-01-16 | 15:24 | 50.084
2021-01-16 | 15:24 | 50.083
2021-01-16 | 15:24 | 50.081
2021-01-16 | 15:24 | 50.081
2021-01-16 | 15:24 | 50.08
2021-01-16 | 15:24 | 50.08
2021-01-16 | 15:24 | 50.082
2021-01-16 | 15:24 | 50.083
2021-01-16 | 15:24 | 50.085
2021-01-16 | 15:24 | 50.083
2021-01-16 | 15:24 | 50.086
2021-01-16 | 15:24 | 50.086
2021-01-16 | 15:24 | 50.087
2021-01-16 | 15:24 | 50.087
2021-01-16 | 15:24 | 50.087
2021-01-16 | 15:24 | 50.087
2021-01-16 | 15:24 | 50.086
2021-01-16 | 15:24 | 50.088
2021-01-16 | 15:24 | 50.085
2021-01-16 | 15:24 | 50.086
2021-01-16 | 15:24 | 50.085
2021-01-16 | 15:24 | 50.087
2021-01-16 | 15:24 | 50.089
2021-01-16 | 15:24 | 50.093
2021-01-16 | 15:24 | 50.094
2021-01-16 | 15:25 | 50.095
2021-01-16 | 15:25 | 50.095
2021-01-16 | 15:25 | 50.099
2021-01-16 | 15:25 | 50.1
2021-01-16 | 15:25 | 50.101
2021-01-16 | 15:25 | 50.101
2021-01-16 | 15:25 | 50.103
2021-01-16 | 15:25 | 50.101
2021-01-16 | 15:25 | 50.1
2021-01-16 | 15:25 | 50.101
2021-01-16 | 15:25 | 50.101
2021-01-16 | 15:25 | 50.101
2021-01-16 | 15:25 | 50.1
2021-01-16 | 15:25 | 50.1
2021-01-16 | 15:25 | 50.099
2021-01-16 | 15:25 | 50.099
2021-01-16 | 15:25 | 50.098
2021-01-16 | 15:25 | 50.098
2021-01-16 | 15:25 | 50.095
2021-01-16 | 15:25 | 50.096
2021-01-16 | 15:25 | 50.093
2021-01-16 | 15:25 | 50.094
2021-01-16 | 15:25 | 50.093
2021-01-16 | 15:25 | 50.094
2021-01-16 | 15:25 | 50.094
2021-01-16 | 15:25 | 50.092
2021-01-16 | 15:25 | 50.092
2021-01-16 | 15:25 | 50.091
2021-01-16 | 15:25 | 50.092
2021-01-16 | 15:25 | 50.091
2021-01-16 | 15:25 | 50.089
2021-01-16 | 15:25 | 50.086
2021-01-16 | 15:25 | 50.086
2021-01-16 | 15:25 | 50.085
2021-01-16 | 15:25 | 50.085
2021-01-16 | 15:25 | 50.083
2021-01-16 | 15:25 | 50.083
2021-01-16 | 15:25 | 50.083
2021-01-16 | 15:25 | 50.082
2021-01-16 | 15:25 | 50.081
2021-01-16 | 15:25 | 50.08
2021-01-16 | 15:25 | 50.078
2021-01-16 | 15:25 | 50.081
2021-01-16 | 15:25 | 50.082
2021-01-16 | 15:25 | 50.083
2021-01-16 | 15:25 | 50.082
2021-01-16 | 15:25 | 50.082
2021-01-16 | 15:25 | 50.079
2021-01-16 | 15:25 | 50.076
2021-01-16 | 15:25 | 50.076
2021-01-16 | 15:25 | 50.073
2021-01-16 | 15:25 | 50.073
2021-01-16 | 15:25 | 50.07
2021-01-16 | 15:25 | 50.071
2021-01-16 | 15:25 | 50.073
2021-01-16 | 15:25 | 50.073
2021-01-16 | 15:25 | 50.075
2021-01-16 | 15:25 | 50.077
2021-01-16 | 15:25 | 50.081
2021-01-16 | 15:26 | 50.083
2021-01-16 | 15:26 | 50.087
2021-01-16 | 15:26 | 50.089
2021-01-16 | 15:26 | 50.094
2021-01-16 | 15:26 | 50.095
2021-01-16 | 15:26 | 50.095
2021-01-16 | 15:26 | 50.096
2021-01-16 | 15:26 | 50.096
2021-01-16 | 15:26 | 50.098
2021-01-16 | 15:26 | 50.099
2021-01-16 | 15:26 | 50.097
2021-01-16 | 15:26 | 50.098
2021-01-16 | 15:26 | 50.098
2021-01-16 | 15:26 | 50.098
2021-01-16 | 15:26 | 50.096
2021-01-16 | 15:26 | 50.096
2021-01-16 | 15:26 | 50.095
2021-01-16 | 15:26 | 50.098
2021-01-16 | 15:26 | 50.097
2021-01-16 | 15:26 | 50.095
2021-01-16 | 15:26 | 50.095
2021-01-16 | 15:26 | 50.093
2021-01-16 | 15:26 | 50.093
2021-01-16 | 15:26 | 50.092
2021-01-16 | 15:26 | 50.092
2021-01-16 | 15:26 | 50.094
2021-01-16 | 15:26 | 50.092
2021-01-16 | 15:26 | 50.091
2021-01-16 | 15:26 | 50.091
2021-01-16 | 15:26 | 50.09
2021-01-16 | 15:26 | 50.092
2021-01-16 | 15:26 | 50.093
2021-01-16 | 15:26 | 50.091
2021-01-16 | 15:26 | 50.092
2021-01-16 | 15:26 | 50.092
2021-01-16 | 15:26 | 50.092
2021-01-16 | 15:26 | 50.091
2021-01-16 | 15:26 | 50.088
2021-01-16 | 15:26 | 50.084
2021-01-16 | 15:26 | 50.081
2021-01-16 | 15:26 | 50.077
2021-01-16 | 15:26 | 50.075
2021-01-16 | 15:26 | 50.075
2021-01-16 | 15:26 | 50.075
2021-01-16 | 15:26 | 50.075
2021-01-16 | 15:26 | 50.074
2021-01-16 | 15:26 | 50.076
2021-01-16 | 15:26 | 50.077
2021-01-16 | 15:26 | 50.078
2021-01-16 | 15:26 | 50.08
2021-01-16 | 15:26 | 50.078
2021-01-16 | 15:26 | 50.078
2021-01-16 | 15:26 | 50.079
2021-01-16 | 15:26 | 50.079
2021-01-16 | 15:26 | 50.081
2021-01-16 | 15:26 | 50.08
2021-01-16 | 15:26 | 50.08
2021-01-16 | 15:26 | 50.079
2021-01-16 | 15:26 | 50.077
2021-01-16 | 15:26 | 50.076
2021-01-16 | 15:26 | 50.076
2021-01-16 | 15:27 | 50.075
2021-01-16 | 15:27 | 50.078
2021-01-16 | 15:27 | 50.079
2021-01-16 | 15:27 | 50.079
2021-01-16 | 15:27 | 50.079
2021-01-16 | 15:27 | 50.081
2021-01-16 | 15:27 | 50.083
2021-01-16 | 15:27 | 50.085
2021-01-16 | 15:27 | 50.087
2021-01-16 | 15:27 | 50.088
2021-01-16 | 15:27 | 50.087
2021-01-16 | 15:27 | 50.086
2021-01-16 | 15:27 | 50.087
2021-01-16 | 15:27 | 50.087
2021-01-16 | 15:27 | 50.087
2021-01-16 | 15:27 | 50.089
2021-01-16 | 15:27 | 50.09
2021-01-16 | 15:27 | 50.093
2021-01-16 | 15:27 | 50.097
2021-01-16 | 15:27 | 50.097
2021-01-16 | 15:27 | 50.1
2021-01-16 | 15:27 | 50.099
2021-01-16 | 15:27 | 50.1
2021-01-16 | 15:27 | 50.101
2021-01-16 | 15:27 | 50.104
2021-01-16 | 15:27 | 50.106
2021-01-16 | 15:27 | 50.105
2021-01-16 | 15:27 | 50.107
2021-01-16 | 15:27 | 50.108
2021-01-16 | 15:27 | 50.108
2021-01-16 | 15:27 | 50.108
2021-01-16 | 15:27 | 50.109
2021-01-16 | 15:27 | 50.108
2021-01-16 | 15:27 | 50.108
2021-01-16 | 15:27 | 50.107
2021-01-16 | 15:27 | 50.106
2021-01-16 | 15:27 | 50.107
2021-01-16 | 15:27 | 50.111
2021-01-16 | 15:27 | 50.11
2021-01-16 | 15:27 | 50.11
2021-01-16 | 15:27 | 50.112
2021-01-16 | 15:27 | 50.112
2021-01-16 | 15:27 | 50.11
2021-01-16 | 15:27 | 50.114
2021-01-16 | 15:27 | 50.115
2021-01-16 | 15:27 | 50.116
2021-01-16 | 15:27 | 50.118
2021-01-16 | 15:27 | 50.119
2021-01-16 | 15:27 | 50.122
2021-01-16 | 15:27 | 50.124
2021-01-16 | 15:27 | 50.124
2021-01-16 | 15:27 | 50.125
2021-01-16 | 15:27 | 50.125
2021-01-16 | 15:27 | 50.126
2021-01-16 | 15:27 | 50.128
2021-01-16 | 15:27 | 50.129
2021-01-16 | 15:27 | 50.13
2021-01-16 | 15:27 | 50.129
2021-01-16 | 15:27 | 50.131
2021-01-16 | 15:28 | 50.133
2021-01-16 | 15:28 | 50.134
2021-01-16 | 15:28 | 50.136
2021-01-16 | 15:28 | 50.135
2021-01-16 | 15:28 | 50.132
2021-01-16 | 15:28 | 50.131
2021-01-16 | 15:28 | 50.127
2021-01-16 | 15:28 | 50.123
2021-01-16 | 15:28 | 50.121
2021-01-16 | 15:28 | 50.119
2021-01-16 | 15:28 | 50.118
2021-01-16 | 15:28 | 50.122
2021-01-16 | 15:28 | 50.121
2021-01-16 | 15:28 | 50.123
2021-01-16 | 15:28 | 50.127
2021-01-16 | 15:28 | 50.127
2021-01-16 | 15:28 | 50.126
2021-01-16 | 15:28 | 50.128
2021-01-16 | 15:28 | 50.129
2021-01-16 | 15:28 | 50.13
2021-01-16 | 15:28 | 50.132
2021-01-16 | 15:28 | 50.13
2021-01-16 | 15:28 | 50.129
2021-01-16 | 15:28 | 50.125
2021-01-16 | 15:28 | 50.12
2021-01-16 | 15:28 | 50.117
2021-01-16 | 15:28 | 50.119
2021-01-16 | 15:28 | 50.12
2021-01-16 | 15:28 | 50.123
2021-01-16 | 15:28 | 50.123
2021-01-16 | 15:28 | 50.122
2021-01-16 | 15:28 | 50.121
2021-01-16 | 15:28 | 50.119
2021-01-16 | 15:28 | 50.121
2021-01-16 | 15:28 | 50.121
2021-01-16 | 15:28 | 50.119
2021-01-16 | 15:28 | 50.118
2021-01-16 | 15:28 | 50.119
2021-01-16 | 15:28 | 50.116
2021-01-16 | 15:28 | 50.119
2021-01-16 | 15:28 | 50.118
2021-01-16 | 15:28 | 50.119
2021-01-16 | 15:28 | 50.122
2021-01-16 | 15:28 | 50.122
2021-01-16 | 15:28 | 50.123
2021-01-16 | 15:28 | 50.125
2021-01-16 | 15:28 | 50.125
2021-01-16 | 15:28 | 50.124
2021-01-16 | 15:28 | 50.125
2021-01-16 | 15:28 | 50.127
2021-01-16 | 15:28 | 50.128
2021-01-16 | 15:28 | 50.126
2021-01-16 | 15:28 | 50.125
2021-01-16 | 15:28 | 50.123
2021-01-16 | 15:28 | 50.123
2021-01-16 | 15:28 | 50.119
2021-01-16 | 15:28 | 50.118
2021-01-16 | 15:28 | 50.118
2021-01-16 | 15:28 | 50.118
2021-01-16 | 15:28 | 50.118
2021-01-16 | 15:28 | 50.118
2021-01-16 | 15:29 | 50.119
2021-01-16 | 15:29 | 50.12
2021-01-16 | 15:29 | 50.119
2021-01-16 | 15:29 | 50.117
2021-01-16 | 15:29 | 50.115
2021-01-16 | 15:29 | 50.113
2021-01-16 | 15:29 | 50.112
2021-01-16 | 15:29 | 50.114
2021-01-16 | 15:29 | 50.114
2021-01-16 | 15:29 | 50.117
2021-01-16 | 15:29 | 50.118
2021-01-16 | 15:29 | 50.119
2021-01-16 | 15:29 | 50.118
2021-01-16 | 15:29 | 50.115
2021-01-16 | 15:29 | 50.115
2021-01-16 | 15:29 | 50.113
2021-01-16 | 15:29 | 50.112
2021-01-16 | 15:29 | 50.11
2021-01-16 | 15:29 | 50.109
2021-01-16 | 15:29 | 50.11
2021-01-16 | 15:29 | 50.107
2021-01-16 | 15:29 | 50.108
2021-01-16 | 15:29 | 50.109
2021-01-16 | 15:29 | 50.109
2021-01-16 | 15:29 | 50.111
2021-01-16 | 15:29 | 50.113
2021-01-16 | 15:29 | 50.115
2021-01-16 | 15:29 | 50.118
2021-01-16 | 15:29 | 50.121
2021-01-16 | 15:29 | 50.124
2021-01-16 | 15:29 | 50.126
2021-01-16 | 15:29 | 50.125
2021-01-16 | 15:29 | 50.124
2021-01-16 | 15:29 | 50.124
2021-01-16 | 15:29 | 50.122
2021-01-16 | 15:29 | 50.118
2021-01-16 | 15:29 | 50.116
2021-01-16 | 15:29 | 50.113
2021-01-16 | 15:29 | 50.109
2021-01-16 | 15:29 | 50.108
2021-01-16 | 15:29 | 50.11
2021-01-16 | 15:29 | 50.11
2021-01-16 | 15:29 | 50.113
2021-01-16 | 15:29 | 50.115
2021-01-16 | 15:29 | 50.115
2021-01-16 | 15:29 | 50.115
2021-01-16 | 15:29 | 50.115
2021-01-16 | 15:29 | 50.112
2021-01-16 | 15:29 | 50.11
2021-01-16 | 15:29 | 50.106
2021-01-16 | 15:29 | 50.102
2021-01-16 | 15:29 | 50.1
2021-01-16 | 15:29 | 50.099
2021-01-16 | 15:29 | 50.1
2021-01-16 | 15:29 | 50.1
2021-01-16 | 15:29 | 50.103
2021-01-16 | 15:29 | 50.104
2021-01-16 | 15:29 | 50.106
2021-01-16 | 15:29 | 50.109
2021-01-16 | 15:30 | 50.11
2021-01-16 | 15:30 | 50.111
2021-01-16 | 15:30 | 50.112
2021-01-16 | 15:30 | 50.11
2021-01-16 | 15:30 | 50.109
2021-01-16 | 15:30 | 50.107
2021-01-16 | 15:30 | 50.105
2021-01-16 | 15:30 | 50.101
2021-01-16 | 15:30 | 50.101
2021-01-16 | 15:30 | 50.103
2021-01-16 | 15:30 | 50.105
2021-01-16 | 15:30 | 50.106
2021-01-16 | 15:30 | 50.109
2021-01-16 | 15:30 | 50.111
2021-01-16 | 15:30 | 50.109
2021-01-16 | 15:30 | 50.112
2021-01-16 | 15:30 | 50.112
2021-01-16 | 15:30 | 50.115
2021-01-16 | 15:30 | 50.116
2021-01-16 | 15:30 | 50.115
2021-01-16 | 15:30 | 50.116
2021-01-16 | 15:30 | 50.116
2021-01-16 | 15:30 | 50.116
2021-01-16 | 15:30 | 50.115
2021-01-16 | 15:30 | 50.114
2021-01-16 | 15:30 | 50.114
2021-01-16 | 15:30 | 50.11
2021-01-16 | 15:30 | 50.105
2021-01-16 | 15:30 | 50.103
2021-01-16 | 15:30 | 50.103
2021-01-16 | 15:30 | 50.102
2021-01-16 | 15:30 | 50.101
2021-01-16 | 15:30 | 50.1
2021-01-16 | 15:30 | 50.099
2021-01-16 | 15:30 | 50.098
2021-01-16 | 15:30 | 50.096
2021-01-16 | 15:30 | 50.096
2021-01-16 | 15:30 | 50.096
2021-01-16 | 15:30 | 50.095
2021-01-16 | 15:30 | 50.094
2021-01-16 | 15:30 | 50.096
2021-01-16 | 15:30 | 50.097
2021-01-16 | 15:30 | 50.098
2021-01-16 | 15:30 | 50.097
2021-01-16 | 15:30 | 50.098
2021-01-16 | 15:30 | 50.101
2021-01-16 | 15:30 | 50.1
2021-01-16 | 15:30 | 50.1
2021-01-16 | 15:30 | 50.099
2021-01-16 | 15:30 | 50.098
2021-01-16 | 15:30 | 50.095
2021-01-16 | 15:30 | 50.095
2021-01-16 | 15:30 | 50.095
2021-01-16 | 15:30 | 50.095
2021-01-16 | 15:30 | 50.094
2021-01-16 | 15:30 | 50.093
2021-01-16 | 15:30 | 50.091
2021-01-16 | 15:30 | 50.089
2021-01-16 | 15:30 | 50.088
2021-01-16 | 15:30 | 50.088
2021-01-16 | 15:30 | 50.086
2021-01-16 | 15:31 | 50.086
2021-01-16 | 15:31 | 50.085
2021-01-16 | 15:31 | 50.083
2021-01-16 | 15:31 | 50.082
2021-01-16 | 15:31 | 50.084
2021-01-16 | 15:31 | 50.082
2021-01-16 | 15:31 | 50.082
2021-01-16 | 15:31 | 50.081
2021-01-16 | 15:31 | 50.082
2021-01-16 | 15:31 | 50.083
2021-01-16 | 15:31 | 50.083
2021-01-16 | 15:31 | 50.083
2021-01-16 | 15:31 | 50.08
2021-01-16 | 15:31 | 50.078
2021-01-16 | 15:31 | 50.077
2021-01-16 | 15:31 | 50.077
2021-01-16 | 15:31 | 50.079
2021-01-16 | 15:31 | 50.082
2021-01-16 | 15:31 | 50.085
2021-01-16 | 15:31 | 50.086
2021-01-16 | 15:31 | 50.09
2021-01-16 | 15:31 | 50.091
2021-01-16 | 15:31 | 50.094
2021-01-16 | 15:31 | 50.098
2021-01-16 | 15:31 | 50.099
2021-01-16 | 15:31 | 50.102
2021-01-16 | 15:31 | 50.103
2021-01-16 | 15:31 | 50.104
2021-01-16 | 15:31 | 50.106
2021-01-16 | 15:31 | 50.103
2021-01-16 | 15:31 | 50.103
2021-01-16 | 15:31 | 50.102
2021-01-16 | 15:31 | 50.1
2021-01-16 | 15:31 | 50.104
2021-01-16 | 15:31 | 50.106
2021-01-16 | 15:31 | 50.108
2021-01-16 | 15:31 | 50.11
2021-01-16 | 15:31 | 50.111
2021-01-16 | 15:31 | 50.107
2021-01-16 | 15:31 | 50.108
2021-01-16 | 15:31 | 50.106
2021-01-16 | 15:31 | 50.103
2021-01-16 | 15:31 | 50.101
2021-01-16 | 15:31 | 50.1
2021-01-16 | 15:31 | 50.098
2021-01-16 | 15:31 | 50.099
2021-01-16 | 15:31 | 50.097
2021-01-16 | 15:31 | 50.097
2021-01-16 | 15:31 | 50.098
2021-01-16 | 15:31 | 50.099
2021-01-16 | 15:31 | 50.099
2021-01-16 | 15:31 | 50.098
2021-01-16 | 15:31 | 50.095
2021-01-16 | 15:31 | 50.095
2021-01-16 | 15:31 | 50.094
2021-01-16 | 15:31 | 50.09
2021-01-16 | 15:31 | 50.09
2021-01-16 | 15:31 | 50.089
2021-01-16 | 15:31 | 50.09
2021-01-16 | 15:32 | 50.09
2021-01-16 | 15:32 | 50.09
2021-01-16 | 15:32 | 50.091
2021-01-16 | 15:32 | 50.094
2021-01-16 | 15:32 | 50.094
2021-01-16 | 15:32 | 50.093
2021-01-16 | 15:32 | 50.093
2021-01-16 | 15:32 | 50.092
2021-01-16 | 15:32 | 50.095
2021-01-16 | 15:32 | 50.096
2021-01-16 | 15:32 | 50.098
2021-01-16 | 15:32 | 50.099
2021-01-16 | 15:32 | 50.099
2021-01-16 | 15:32 | 50.099
2021-01-16 | 15:32 | 50.098
2021-01-16 | 15:32 | 50.098
2021-01-16 | 15:32 | 50.097
2021-01-16 | 15:32 | 50.098
2021-01-16 | 15:32 | 50.098
2021-01-16 | 15:32 | 50.097
2021-01-16 | 15:32 | 50.099
2021-01-16 | 15:32 | 50.097
2021-01-16 | 15:32 | 50.096
2021-01-16 | 15:32 | 50.096
2021-01-16 | 15:32 | 50.093
2021-01-16 | 15:32 | 50.094
2021-01-16 | 15:32 | 50.094
2021-01-16 | 15:32 | 50.096
2021-01-16 | 15:32 | 50.097
2021-01-16 | 15:32 | 50.097
2021-01-16 | 15:32 | 50.095
2021-01-16 | 15:32 | 50.093
2021-01-16 | 15:32 | 50.091
2021-01-16 | 15:32 | 50.089
2021-01-16 | 15:32 | 50.088
2021-01-16 | 15:32 | 50.084
2021-01-16 | 15:32 | 50.083
2021-01-16 | 15:32 | 50.082
2021-01-16 | 15:32 | 50.079
2021-01-16 | 15:32 | 50.078
2021-01-16 | 15:32 | 50.077
2021-01-16 | 15:32 | 50.076
2021-01-16 | 15:32 | 50.074
2021-01-16 | 15:32 | 50.074
2021-01-16 | 15:32 | 50.074
2021-01-16 | 15:32 | 50.074
2021-01-16 | 15:32 | 50.075
2021-01-16 | 15:32 | 50.076
2021-01-16 | 15:32 | 50.079
2021-01-16 | 15:32 | 50.082
2021-01-16 | 15:32 | 50.081
2021-01-16 | 15:32 | 50.083
2021-01-16 | 15:32 | 50.083
2021-01-16 | 15:32 | 50.082
2021-01-16 | 15:32 | 50.08
2021-01-16 | 15:32 | 50.075
2021-01-16 | 15:32 | 50.071
2021-01-16 | 15:32 | 50.069
2021-01-16 | 15:32 | 50.068
2021-01-16 | 15:32 | 50.069
2021-01-16 | 15:32 | 50.07
2021-01-16 | 15:33 | 50.068
2021-01-16 | 15:33 | 50.066
2021-01-16 | 15:33 | 50.067
2021-01-16 | 15:33 | 50.066
2021-01-16 | 15:33 | 50.067
2021-01-16 | 15:33 | 50.066
2021-01-16 | 15:33 | 50.067
2021-01-16 | 15:33 | 50.069
2021-01-16 | 15:33 | 50.068
2021-01-16 | 15:33 | 50.069
2021-01-16 | 15:33 | 50.069
2021-01-16 | 15:33 | 50.069
2021-01-16 | 15:33 | 50.072
2021-01-16 | 15:33 | 50.073
2021-01-16 | 15:33 | 50.078
2021-01-16 | 15:33 | 50.082
2021-01-16 | 15:33 | 50.083
2021-01-16 | 15:33 | 50.086
2021-01-16 | 15:33 | 50.087
2021-01-16 | 15:33 | 50.09
2021-01-16 | 15:33 | 50.092
2021-01-16 | 15:33 | 50.092
2021-01-16 | 15:33 | 50.091
2021-01-16 | 15:33 | 50.091
2021-01-16 | 15:33 | 50.09
2021-01-16 | 15:33 | 50.089
2021-01-16 | 15:33 | 50.086
2021-01-16 | 15:33 | 50.085
2021-01-16 | 15:33 | 50.084
2021-01-16 | 15:33 | 50.081
2021-01-16 | 15:33 | 50.08
2021-01-16 | 15:33 | 50.08
2021-01-16 | 15:33 | 50.078
2021-01-16 | 15:33 | 50.077
2021-01-16 | 15:33 | 50.074
2021-01-16 | 15:33 | 50.07
2021-01-16 | 15:33 | 50.069
2021-01-16 | 15:33 | 50.068
2021-01-16 | 15:33 | 50.067
2021-01-16 | 15:33 | 50.066
2021-01-16 | 15:33 | 50.067
2021-01-16 | 15:33 | 50.062
2021-01-16 | 15:33 | 50.061
2021-01-16 | 15:33 | 50.06
2021-01-16 | 15:33 | 50.058
2021-01-16 | 15:33 | 50.055
2021-01-16 | 15:33 | 50.052
2021-01-16 | 15:33 | 50.051
2021-01-16 | 15:33 | 50.051
2021-01-16 | 15:33 | 50.049
2021-01-16 | 15:33 | 50.05
2021-01-16 | 15:33 | 50.05
2021-01-16 | 15:33 | 50.05
2021-01-16 | 15:33 | 50.051
2021-01-16 | 15:33 | 50.053
2021-01-16 | 15:33 | 50.053
2021-01-16 | 15:33 | 50.052
2021-01-16 | 15:33 | 50.053
2021-01-16 | 15:33 | 50.05
2021-01-16 | 15:34 | 50.049
2021-01-16 | 15:34 | 50.049
2021-01-16 | 15:34 | 50.052
2021-01-16 | 15:34 | 50.053
2021-01-16 | 15:34 | 50.054
2021-01-16 | 15:34 | 50.055
2021-01-16 | 15:34 | 50.055
2021-01-16 | 15:34 | 50.057
2021-01-16 | 15:34 | 50.059
2021-01-16 | 15:34 | 50.06
2021-01-16 | 15:34 | 50.061
2021-01-16 | 15:34 | 50.059
2021-01-16 | 15:34 | 50.061
2021-01-16 | 15:34 | 50.061
2021-01-16 | 15:34 | 50.062
2021-01-16 | 15:34 | 50.064
2021-01-16 | 15:34 | 50.064
2021-01-16 | 15:34 | 50.064
2021-01-16 | 15:34 | 50.062
2021-01-16 | 15:34 | 50.062
2021-01-16 | 15:34 | 50.063
2021-01-16 | 15:34 | 50.064
2021-01-16 | 15:34 | 50.065
2021-01-16 | 15:34 | 50.063
2021-01-16 | 15:34 | 50.063
2021-01-16 | 15:34 | 50.063
2021-01-16 | 15:34 | 50.063
2021-01-16 | 15:34 | 50.061
2021-01-16 | 15:34 | 50.06
2021-01-16 | 15:34 | 50.06
2021-01-16 | 15:34 | 50.059
2021-01-16 | 15:34 | 50.056
2021-01-16 | 15:34 | 50.054
2021-01-16 | 15:34 | 50.052
2021-01-16 | 15:34 | 50.051
2021-01-16 | 15:34 | 50.053
2021-01-16 | 15:34 | 50.053
2021-01-16 | 15:34 | 50.056
2021-01-16 | 15:34 | 50.06
2021-01-16 | 15:34 | 50.062
2021-01-16 | 15:34 | 50.062
2021-01-16 | 15:34 | 50.064
2021-01-16 | 15:34 | 50.065
2021-01-16 | 15:34 | 50.067
2021-01-16 | 15:34 | 50.069
2021-01-16 | 15:34 | 50.071
2021-01-16 | 15:34 | 50.073
2021-01-16 | 15:34 | 50.073
2021-01-16 | 15:34 | 50.074
2021-01-16 | 15:34 | 50.074
2021-01-16 | 15:34 | 50.073
2021-01-16 | 15:34 | 50.071
2021-01-16 | 15:34 | 50.07
2021-01-16 | 15:34 | 50.068
2021-01-16 | 15:34 | 50.071
2021-01-16 | 15:34 | 50.071
2021-01-16 | 15:34 | 50.071
2021-01-16 | 15:34 | 50.069
2021-01-16 | 15:34 | 50.07
2021-01-16 | 15:34 | 50.067
2021-01-16 | 15:34 | 50.063
2021-01-16 | 15:35 | 50.058
2021-01-16 | 15:35 | 50.056
2021-01-16 | 15:35 | 50.054
2021-01-16 | 15:35 | 50.05
2021-01-16 | 15:35 | 50.05
2021-01-16 | 15:35 | 50.047
2021-01-16 | 15:35 | 50.048
2021-01-16 | 15:35 | 50.046
2021-01-16 | 15:35 | 50.045
2021-01-16 | 15:35 | 50.043
2021-01-16 | 15:35 | 50.043
2021-01-16 | 15:35 | 50.038
2021-01-16 | 15:35 | 50.04
2021-01-16 | 15:35 | 50.039
2021-01-16 | 15:35 | 50.039
2021-01-16 | 15:35 | 50.038
2021-01-16 | 15:35 | 50.037
2021-01-16 | 15:35 | 50.035
2021-01-16 | 15:35 | 50.034
2021-01-16 | 15:35 | 50.033
2021-01-16 | 15:35 | 50.034
2021-01-16 | 15:35 | 50.033
2021-01-16 | 15:35 | 50.034
2021-01-16 | 15:35 | 50.034
2021-01-16 | 15:35 | 50.035
2021-01-16 | 15:35 | 50.034
2021-01-16 | 15:35 | 50.037
2021-01-16 | 15:35 | 50.038
2021-01-16 | 15:35 | 50.04
2021-01-16 | 15:35 | 50.043
2021-01-16 | 15:35 | 50.043
2021-01-16 | 15:35 | 50.043
2021-01-16 | 15:35 | 50.042
2021-01-16 | 15:35 | 50.04
2021-01-16 | 15:35 | 50.037
2021-01-16 | 15:35 | 50.036
2021-01-16 | 15:35 | 50.035
2021-01-16 | 15:35 | 50.036
2021-01-16 | 15:35 | 50.037
2021-01-16 | 15:35 | 50.042
2021-01-16 | 15:35 | 50.042
2021-01-16 | 15:35 | 50.045
2021-01-16 | 15:35 | 50.047
2021-01-16 | 15:35 | 50.048
2021-01-16 | 15:35 | 50.05
2021-01-16 | 15:35 | 50.053
2021-01-16 | 15:35 | 50.054
2021-01-16 | 15:35 | 50.054
2021-01-16 | 15:35 | 50.053
2021-01-16 | 15:35 | 50.056
2021-01-16 | 15:35 | 50.056
2021-01-16 | 15:35 | 50.056
2021-01-16 | 15:35 | 50.058
2021-01-16 | 15:35 | 50.061
2021-01-16 | 15:35 | 50.055
2021-01-16 | 15:35 | 50.053
2021-01-16 | 15:35 | 50.051
2021-01-16 | 15:35 | 50.049
2021-01-16 | 15:35 | 50.044
2021-01-16 | 15:36 | 50.042
2021-01-16 | 15:36 | 50.039
2021-01-16 | 15:36 | 50.04
2021-01-16 | 15:36 | 50.038
2021-01-16 | 15:36 | 50.036
2021-01-16 | 15:36 | 50.035
2021-01-16 | 15:36 | 50.033
2021-01-16 | 15:36 | 50.033
2021-01-16 | 15:36 | 50.031
2021-01-16 | 15:36 | 50.028
2021-01-16 | 15:36 | 50.029
2021-01-16 | 15:36 | 50.03
2021-01-16 | 15:36 | 50.033
2021-01-16 | 15:36 | 50.036
2021-01-16 | 15:36 | 50.037
2021-01-16 | 15:36 | 50.04
2021-01-16 | 15:36 | 50.043
2021-01-16 | 15:36 | 50.046
2021-01-16 | 15:36 | 50.048
2021-01-16 | 15:36 | 50.052
2021-01-16 | 15:36 | 50.055
2021-01-16 | 15:36 | 50.056
2021-01-16 | 15:36 | 50.059
2021-01-16 | 15:36 | 50.06
2021-01-16 | 15:36 | 50.059
2021-01-16 | 15:36 | 50.058
2021-01-16 | 15:36 | 50.061
2021-01-16 | 15:36 | 50.059
2021-01-16 | 15:36 | 50.058
2021-01-16 | 15:36 | 50.054
2021-01-16 | 15:36 | 50.054
2021-01-16 | 15:36 | 50.053
2021-01-16 | 15:36 | 50.054
2021-01-16 | 15:36 | 50.054
2021-01-16 | 15:36 | 50.055
2021-01-16 | 15:36 | 50.055
2021-01-16 | 15:36 | 50.055
2021-01-16 | 15:36 | 50.056
2021-01-16 | 15:36 | 50.056
2021-01-16 | 15:36 | 50.054
2021-01-16 | 15:36 | 50.05
2021-01-16 | 15:36 | 50.048
2021-01-16 | 15:36 | 50.045
2021-01-16 | 15:36 | 50.046
2021-01-16 | 15:36 | 50.043
2021-01-16 | 15:36 | 50.042
2021-01-16 | 15:36 | 50.041
2021-01-16 | 15:36 | 50.039
2021-01-16 | 15:36 | 50.041
2021-01-16 | 15:36 | 50.045
2021-01-16 | 15:36 | 50.048
2021-01-16 | 15:36 | 50.049
2021-01-16 | 15:36 | 50.048
2021-01-16 | 15:36 | 50.048
2021-01-16 | 15:36 | 50.047
2021-01-16 | 15:36 | 50.047
2021-01-16 | 15:36 | 50.046
2021-01-16 | 15:36 | 50.045
2021-01-16 | 15:36 | 50.044
2021-01-16 | 15:36 | 50.043
2021-01-16 | 15:36 | 50.043
2021-01-16 | 15:37 | 50.04
2021-01-16 | 15:37 | 50.039
2021-01-16 | 15:37 | 50.038
2021-01-16 | 15:37 | 50.035
2021-01-16 | 15:37 | 50.033
2021-01-16 | 15:37 | 50.034
2021-01-16 | 15:37 | 50.034
2021-01-16 | 15:37 | 50.033
2021-01-16 | 15:37 | 50.031
2021-01-16 | 15:37 | 50.031
2021-01-16 | 15:37 | 50.031
2021-01-16 | 15:37 | 50.032
2021-01-16 | 15:37 | 50.033
2021-01-16 | 15:37 | 50.034
2021-01-16 | 15:37 | 50.036
2021-01-16 | 15:37 | 50.037
2021-01-16 | 15:37 | 50.035
2021-01-16 | 15:37 | 50.035
2021-01-16 | 15:37 | 50.034
2021-01-16 | 15:37 | 50.033
2021-01-16 | 15:37 | 50.032
2021-01-16 | 15:37 | 50.033
2021-01-16 | 15:37 | 50.035
2021-01-16 | 15:37 | 50.037
2021-01-16 | 15:37 | 50.042
2021-01-16 | 15:37 | 50.044
2021-01-16 | 15:37 | 50.047
2021-01-16 | 15:37 | 50.053
2021-01-16 | 15:37 | 50.058
2021-01-16 | 15:37 | 50.062
2021-01-16 | 15:37 | 50.063
2021-01-16 | 15:37 | 50.063
2021-01-16 | 15:37 | 50.061
2021-01-16 | 15:37 | 50.056
2021-01-16 | 15:37 | 50.054
2021-01-16 | 15:37 | 50.049
2021-01-16 | 15:37 | 50.042
2021-01-16 | 15:37 | 50.039
2021-01-16 | 15:37 | 50.036
2021-01-16 | 15:37 | 50.038
2021-01-16 | 15:37 | 50.036
2021-01-16 | 15:37 | 50.035
2021-01-16 | 15:37 | 50.033
2021-01-16 | 15:37 | 50.032
2021-01-16 | 15:37 | 50.033
2021-01-16 | 15:37 | 50.033
2021-01-16 | 15:37 | 50.031
2021-01-16 | 15:37 | 50.03
2021-01-16 | 15:37 | 50.03
2021-01-16 | 15:37 | 50.029
2021-01-16 | 15:37 | 50.029
2021-01-16 | 15:37 | 50.03
2021-01-16 | 15:37 | 50.032
2021-01-16 | 15:37 | 50.033
2021-01-16 | 15:37 | 50.033
2021-01-16 | 15:37 | 50.036
2021-01-16 | 15:37 | 50.038
2021-01-16 | 15:37 | 50.042
2021-01-16 | 15:37 | 50.041
2021-01-16 | 15:38 | 50.043
2021-01-16 | 15:38 | 50.042
2021-01-16 | 15:38 | 50.041
2021-01-16 | 15:38 | 50.038
2021-01-16 | 15:38 | 50.037
2021-01-16 | 15:38 | 50.037
2021-01-16 | 15:38 | 50.037
2021-01-16 | 15:38 | 50.036
2021-01-16 | 15:38 | 50.035
2021-01-16 | 15:38 | 50.034
2021-01-16 | 15:38 | 50.033
2021-01-16 | 15:38 | 50.033
2021-01-16 | 15:38 | 50.033
2021-01-16 | 15:38 | 50.033
2021-01-16 | 15:38 | 50.031
2021-01-16 | 15:38 | 50.03
2021-01-16 | 15:38 | 50.031
2021-01-16 | 15:38 | 50.032
2021-01-16 | 15:38 | 50.032
2021-01-16 | 15:38 | 50.034
2021-01-16 | 15:38 | 50.034
2021-01-16 | 15:38 | 50.034
2021-01-16 | 15:38 | 50.035
2021-01-16 | 15:38 | 50.034
2021-01-16 | 15:38 | 50.034
2021-01-16 | 15:38 | 50.035
2021-01-16 | 15:38 | 50.036
2021-01-16 | 15:38 | 50.035
2021-01-16 | 15:38 | 50.035
2021-01-16 | 15:38 | 50.034
2021-01-16 | 15:38 | 50.031
2021-01-16 | 15:38 | 50.029
2021-01-16 | 15:38 | 50.029
2021-01-16 | 15:38 | 50.029
2021-01-16 | 15:38 | 50.031
2021-01-16 | 15:38 | 50.033
2021-01-16 | 15:38 | 50.035
2021-01-16 | 15:38 | 50.036
2021-01-16 | 15:38 | 50.036
2021-01-16 | 15:38 | 50.037
2021-01-16 | 15:38 | 50.037
2021-01-16 | 15:38 | 50.036
2021-01-16 | 15:38 | 50.036
2021-01-16 | 15:38 | 50.033
2021-01-16 | 15:38 | 50.03
2021-01-16 | 15:38 | 50.027
2021-01-16 | 15:38 | 50.027
2021-01-16 | 15:38 | 50.027
2021-01-16 | 15:38 | 50.027
2021-01-16 | 15:38 | 50.026
2021-01-16 | 15:38 | 50.025
2021-01-16 | 15:38 | 50.024
2021-01-16 | 15:38 | 50.022
2021-01-16 | 15:38 | 50.02
2021-01-16 | 15:38 | 50.021
2021-01-16 | 15:38 | 50.021
2021-01-16 | 15:38 | 50.021
2021-01-16 | 15:38 | 50.02
2021-01-16 | 15:38 | 50.017
2021-01-16 | 15:38 | 50.014
2021-01-16 | 15:39 | 50.013
2021-01-16 | 15:39 | 50.014
2021-01-16 | 15:39 | 50.013
2021-01-16 | 15:39 | 50.012
2021-01-16 | 15:39 | 50.012
2021-01-16 | 15:39 | 50.011
2021-01-16 | 15:39 | 50.01
2021-01-16 | 15:39 | 50.01
2021-01-16 | 15:39 | 50.009
2021-01-16 | 15:39 | 50.009
2021-01-16 | 15:39 | 50.01
2021-01-16 | 15:39 | 50.011
2021-01-16 | 15:39 | 50.01
2021-01-16 | 15:39 | 50.013
2021-01-16 | 15:39 | 50.012
2021-01-16 | 15:39 | 50.013
2021-01-16 | 15:39 | 50.013
2021-01-16 | 15:39 | 50.013
2021-01-16 | 15:39 | 50.013
2021-01-16 | 15:39 | 50.015
2021-01-16 | 15:39 | 50.017
2021-01-16 | 15:39 | 50.019
2021-01-16 | 15:39 | 50.019
2021-01-16 | 15:39 | 50.021
2021-01-16 | 15:39 | 50.02
2021-01-16 | 15:39 | 50.02
2021-01-16 | 15:39 | 50.018
2021-01-16 | 15:39 | 50.017
2021-01-16 | 15:39 | 50.017
2021-01-16 | 15:39 | 50.019
2021-01-16 | 15:39 | 50.018
2021-01-16 | 15:39 | 50.018
2021-01-16 | 15:39 | 50.017
2021-01-16 | 15:39 | 50.016
2021-01-16 | 15:39 | 50.014
2021-01-16 | 15:39 | 50.014
2021-01-16 | 15:39 | 50.016
2021-01-16 | 15:39 | 50.013
2021-01-16 | 15:39 | 50.011
2021-01-16 | 15:39 | 50.007
2021-01-16 | 15:39 | 50.003
2021-01-16 | 15:39 | 49.999
2021-01-16 | 15:39 | 49.995
2021-01-16 | 15:39 | 49.993
2021-01-16 | 15:39 | 49.991
2021-01-16 | 15:39 | 49.99
2021-01-16 | 15:39 | 49.988
2021-01-16 | 15:39 | 49.987
2021-01-16 | 15:39 | 49.983
2021-01-16 | 15:39 | 49.979
2021-01-16 | 15:39 | 49.974
2021-01-16 | 15:39 | 49.97
2021-01-16 | 15:39 | 49.968
2021-01-16 | 15:39 | 49.965
2021-01-16 | 15:39 | 49.964
2021-01-16 | 15:39 | 49.962
2021-01-16 | 15:39 | 49.96
2021-01-16 | 15:39 | 49.961
2021-01-16 | 15:39 | 49.962
2021-01-16 | 15:39 | 49.963
2021-01-16 | 15:39 | 49.962
2021-01-16 | 15:40 | 49.961
2021-01-16 | 15:40 | 49.962
2021-01-16 | 15:40 | 49.963
2021-01-16 | 15:40 | 49.965
2021-01-16 | 15:40 | 49.967
2021-01-16 | 15:40 | 49.967
2021-01-16 | 15:40 | 49.969
2021-01-16 | 15:40 | 49.97
2021-01-16 | 15:40 | 49.971
2021-01-16 | 15:40 | 49.974
2021-01-16 | 15:40 | 49.978
2021-01-16 | 15:40 | 49.978
2021-01-16 | 15:40 | 49.979
2021-01-16 | 15:40 | 49.978
2021-01-16 | 15:40 | 49.976
2021-01-16 | 15:40 | 49.975
2021-01-16 | 15:40 | 49.973
2021-01-16 | 15:40 | 49.971
2021-01-16 | 15:40 | 49.971
2021-01-16 | 15:40 | 49.97
2021-01-16 | 15:40 | 49.968
2021-01-16 | 15:40 | 49.966
2021-01-16 | 15:40 | 49.963
2021-01-16 | 15:40 | 49.963
2021-01-16 | 15:40 | 49.964
2021-01-16 | 15:40 | 49.964
2021-01-16 | 15:40 | 49.965
2021-01-16 | 15:40 | 49.964
2021-01-16 | 15:40 | 49.963
2021-01-16 | 15:40 | 49.963
2021-01-16 | 15:40 | 49.961
2021-01-16 | 15:40 | 49.957
2021-01-16 | 15:40 | 49.955
2021-01-16 | 15:40 | 49.953
2021-01-16 | 15:40 | 49.952
2021-01-16 | 15:40 | 49.95
2021-01-16 | 15:40 | 49.949
2021-01-16 | 15:40 | 49.946
2021-01-16 | 15:40 | 49.944
2021-01-16 | 15:40 | 49.943
2021-01-16 | 15:40 | 49.939
2021-01-16 | 15:40 | 49.936
2021-01-16 | 15:40 | 49.934
2021-01-16 | 15:40 | 49.93
2021-01-16 | 15:40 | 49.929
2021-01-16 | 15:40 | 49.927
2021-01-16 | 15:40 | 49.926
2021-01-16 | 15:40 | 49.925
2021-01-16 | 15:40 | 49.925
2021-01-16 | 15:40 | 49.923
2021-01-16 | 15:40 | 49.923
2021-01-16 | 15:40 | 49.921
2021-01-16 | 15:40 | 49.922
2021-01-16 | 15:40 | 49.921
2021-01-16 | 15:40 | 49.919
2021-01-16 | 15:40 | 49.918
2021-01-16 | 15:40 | 49.917
2021-01-16 | 15:40 | 49.914
2021-01-16 | 15:40 | 49.912
2021-01-16 | 15:41 | 49.911
2021-01-16 | 15:41 | 49.91
2021-01-16 | 15:41 | 49.908
2021-01-16 | 15:41 | 49.907
2021-01-16 | 15:41 | 49.908
2021-01-16 | 15:41 | 49.908
2021-01-16 | 15:41 | 49.908
2021-01-16 | 15:41 | 49.91
2021-01-16 | 15:41 | 49.91
2021-01-16 | 15:41 | 49.91
2021-01-16 | 15:41 | 49.913
2021-01-16 | 15:41 | 49.911
2021-01-16 | 15:41 | 49.911
2021-01-16 | 15:41 | 49.912
2021-01-16 | 15:41 | 49.915
2021-01-16 | 15:41 | 49.914
2021-01-16 | 15:41 | 49.914
2021-01-16 | 15:41 | 49.912
2021-01-16 | 15:41 | 49.916
2021-01-16 | 15:41 | 49.917
2021-01-16 | 15:41 | 49.919
2021-01-16 | 15:41 | 49.917
2021-01-16 | 15:41 | 49.918
2021-01-16 | 15:41 | 49.919
2021-01-16 | 15:41 | 49.919
2021-01-16 | 15:41 | 49.918
2021-01-16 | 15:41 | 49.916
2021-01-16 | 15:41 | 49.915
2021-01-16 | 15:41 | 49.914
2021-01-16 | 15:41 | 49.913
2021-01-16 | 15:41 | 49.914
2021-01-16 | 15:41 | 49.913
2021-01-16 | 15:41 | 49.913
2021-01-16 | 15:41 | 49.915
2021-01-16 | 15:41 | 49.916
2021-01-16 | 15:41 | 49.918
2021-01-16 | 15:41 | 49.919
2021-01-16 | 15:41 | 49.921
2021-01-16 | 15:41 | 49.92
2021-01-16 | 15:41 | 49.918
2021-01-16 | 15:41 | 49.916
2021-01-16 | 15:41 | 49.915
2021-01-16 | 15:41 | 49.913
2021-01-16 | 15:41 | 49.914
2021-01-16 | 15:41 | 49.916
2021-01-16 | 15:41 | 49.917
2021-01-16 | 15:41 | 49.919
2021-01-16 | 15:41 | 49.92
2021-01-16 | 15:41 | 49.923
2021-01-16 | 15:41 | 49.926
2021-01-16 | 15:41 | 49.928
2021-01-16 | 15:41 | 49.928
2021-01-16 | 15:41 | 49.928
2021-01-16 | 15:41 | 49.926
2021-01-16 | 15:41 | 49.924
2021-01-16 | 15:41 | 49.92
2021-01-16 | 15:41 | 49.919
2021-01-16 | 15:41 | 49.92
2021-01-16 | 15:41 | 49.92
2021-01-16 | 15:41 | 49.92
2021-01-16 | 15:41 | 49.92
2021-01-16 | 15:42 | 49.917
2021-01-16 | 15:42 | 49.917
2021-01-16 | 15:42 | 49.916
2021-01-16 | 15:42 | 49.914
2021-01-16 | 15:42 | 49.91
2021-01-16 | 15:42 | 49.908
2021-01-16 | 15:42 | 49.907
2021-01-16 | 15:42 | 49.907
2021-01-16 | 15:42 | 49.906
2021-01-16 | 15:42 | 49.905
2021-01-16 | 15:42 | 49.902
2021-01-16 | 15:42 | 49.903
2021-01-16 | 15:42 | 49.901
2021-01-16 | 15:42 | 49.902
2021-01-16 | 15:42 | 49.903
2021-01-16 | 15:42 | 49.904
2021-01-16 | 15:42 | 49.904
2021-01-16 | 15:42 | 49.904
2021-01-16 | 15:42 | 49.907
2021-01-16 | 15:42 | 49.908
2021-01-16 | 15:42 | 49.908
2021-01-16 | 15:42 | 49.909
2021-01-16 | 15:42 | 49.906
2021-01-16 | 15:42 | 49.905
2021-01-16 | 15:42 | 49.905
2021-01-16 | 15:42 | 49.906
2021-01-16 | 15:42 | 49.905
2021-01-16 | 15:42 | 49.904
2021-01-16 | 15:42 | 49.901
2021-01-16 | 15:42 | 49.901
2021-01-16 | 15:42 | 49.899
2021-01-16 | 15:42 | 49.898
2021-01-16 | 15:42 | 49.9
2021-01-16 | 15:42 | 49.9
2021-01-16 | 15:42 | 49.903
2021-01-16 | 15:42 | 49.903
2021-01-16 | 15:42 | 49.903
2021-01-16 | 15:42 | 49.905
2021-01-16 | 15:42 | 49.908
2021-01-16 | 15:42 | 49.909
2021-01-16 | 15:42 | 49.91
2021-01-16 | 15:42 | 49.913
2021-01-16 | 15:42 | 49.913
2021-01-16 | 15:42 | 49.916
2021-01-16 | 15:42 | 49.915
2021-01-16 | 15:42 | 49.914
2021-01-16 | 15:42 | 49.914
2021-01-16 | 15:42 | 49.914
2021-01-16 | 15:42 | 49.914
2021-01-16 | 15:42 | 49.914
2021-01-16 | 15:42 | 49.914
2021-01-16 | 15:42 | 49.914
2021-01-16 | 15:42 | 49.915
2021-01-16 | 15:42 | 49.914
2021-01-16 | 15:42 | 49.913
2021-01-16 | 15:42 | 49.914
2021-01-16 | 15:42 | 49.914
2021-01-16 | 15:42 | 49.913
2021-01-16 | 15:42 | 49.911
2021-01-16 | 15:43 | 49.912
2021-01-16 | 15:43 | 49.912
2021-01-16 | 15:43 | 49.912
2021-01-16 | 15:43 | 49.911
2021-01-16 | 15:43 | 49.911
2021-01-16 | 15:43 | 49.913
2021-01-16 | 15:43 | 49.915
2021-01-16 | 15:43 | 49.916
2021-01-16 | 15:43 | 49.917
2021-01-16 | 15:43 | 49.917
2021-01-16 | 15:43 | 49.918
2021-01-16 | 15:43 | 49.92
2021-01-16 | 15:43 | 49.923
2021-01-16 | 15:43 | 49.924
2021-01-16 | 15:43 | 49.926
2021-01-16 | 15:43 | 49.927
2021-01-16 | 15:43 | 49.929
2021-01-16 | 15:43 | 49.93
2021-01-16 | 15:43 | 49.933
2021-01-16 | 15:43 | 49.934
2021-01-16 | 15:43 | 49.936
2021-01-16 | 15:43 | 49.938
2021-01-16 | 15:43 | 49.936
2021-01-16 | 15:43 | 49.934
2021-01-16 | 15:43 | 49.934
2021-01-16 | 15:43 | 49.934
2021-01-16 | 15:43 | 49.934
2021-01-16 | 15:43 | 49.935
2021-01-16 | 15:43 | 49.938
2021-01-16 | 15:43 | 49.941
2021-01-16 | 15:43 | 49.941
2021-01-16 | 15:43 | 49.94
2021-01-16 | 15:43 | 49.937
2021-01-16 | 15:43 | 49.935
2021-01-16 | 15:43 | 49.93
2021-01-16 | 15:43 | 49.924
2021-01-16 | 15:43 | 49.918
2021-01-16 | 15:43 | 49.913
2021-01-16 | 15:43 | 49.91
2021-01-16 | 15:43 | 49.911
2021-01-16 | 15:43 | 49.913
2021-01-16 | 15:43 | 49.913
2021-01-16 | 15:43 | 49.91
2021-01-16 | 15:43 | 49.909
2021-01-16 | 15:43 | 49.906
2021-01-16 | 15:43 | 49.905
2021-01-16 | 15:43 | 49.905
2021-01-16 | 15:43 | 49.904
2021-01-16 | 15:43 | 49.903
2021-01-16 | 15:43 | 49.902
2021-01-16 | 15:43 | 49.902
2021-01-16 | 15:43 | 49.905
2021-01-16 | 15:43 | 49.906
2021-01-16 | 15:43 | 49.909
2021-01-16 | 15:43 | 49.908
2021-01-16 | 15:43 | 49.907
2021-01-16 | 15:43 | 49.905
2021-01-16 | 15:43 | 49.905
2021-01-16 | 15:43 | 49.906
2021-01-16 | 15:43 | 49.907
2021-01-16 | 15:43 | 49.909
2021-01-16 | 15:44 | 49.909
2021-01-16 | 15:44 | 49.91
2021-01-16 | 15:44 | 49.913
2021-01-16 | 15:44 | 49.911
2021-01-16 | 15:44 | 49.911
2021-01-16 | 15:44 | 49.911
2021-01-16 | 15:44 | 49.909
2021-01-16 | 15:44 | 49.911
2021-01-16 | 15:44 | 49.911
2021-01-16 | 15:44 | 49.914
2021-01-16 | 15:44 | 49.914
2021-01-16 | 15:44 | 49.915
2021-01-16 | 15:44 | 49.913
2021-01-16 | 15:44 | 49.912
2021-01-16 | 15:44 | 49.914
2021-01-16 | 15:44 | 49.915
2021-01-16 | 15:44 | 49.916
2021-01-16 | 15:44 | 49.917
2021-01-16 | 15:44 | 49.916
2021-01-16 | 15:44 | 49.917
2021-01-16 | 15:44 | 49.917
2021-01-16 | 15:44 | 49.918
2021-01-16 | 15:44 | 49.919
2021-01-16 | 15:44 | 49.92
2021-01-16 | 15:44 | 49.921
2021-01-16 | 15:44 | 49.922
2021-01-16 | 15:44 | 49.924
2021-01-16 | 15:44 | 49.926
2021-01-16 | 15:44 | 49.927
2021-01-16 | 15:44 | 49.929
2021-01-16 | 15:44 | 49.929
2021-01-16 | 15:44 | 49.927
2021-01-16 | 15:44 | 49.927
2021-01-16 | 15:44 | 49.927
2021-01-16 | 15:44 | 49.926
2021-01-16 | 15:44 | 49.923
2021-01-16 | 15:44 | 49.922
2021-01-16 | 15:44 | 49.921
2021-01-16 | 15:44 | 49.919
2021-01-16 | 15:44 | 49.919
2021-01-16 | 15:44 | 49.918
2021-01-16 | 15:44 | 49.919
2021-01-16 | 15:44 | 49.919
2021-01-16 | 15:44 | 49.921
2021-01-16 | 15:44 | 49.923
2021-01-16 | 15:44 | 49.925
2021-01-16 | 15:44 | 49.928
2021-01-16 | 15:44 | 49.928
2021-01-16 | 15:44 | 49.929
2021-01-16 | 15:44 | 49.931
2021-01-16 | 15:44 | 49.934
2021-01-16 | 15:44 | 49.935
2021-01-16 | 15:44 | 49.937
2021-01-16 | 15:44 | 49.939
2021-01-16 | 15:44 | 49.941
2021-01-16 | 15:44 | 49.943
2021-01-16 | 15:44 | 49.943
2021-01-16 | 15:44 | 49.944
2021-01-16 | 15:44 | 49.944
2021-01-16 | 15:45 | 49.943
2021-01-16 | 15:45 | 49.941
2021-01-16 | 15:45 | 49.94
2021-01-16 | 15:45 | 49.939
2021-01-16 | 15:45 | 49.939
2021-01-16 | 15:45 | 49.939
2021-01-16 | 15:45 | 49.937
2021-01-16 | 15:45 | 49.937
2021-01-16 | 15:45 | 49.936
2021-01-16 | 15:45 | 49.936
2021-01-16 | 15:45 | 49.935
2021-01-16 | 15:45 | 49.934
2021-01-16 | 15:45 | 49.93
2021-01-16 | 15:45 | 49.928
2021-01-16 | 15:45 | 49.929
2021-01-16 | 15:45 | 49.932
2021-01-16 | 15:45 | 49.935
2021-01-16 | 15:45 | 49.938
2021-01-16 | 15:45 | 49.939
2021-01-16 | 15:45 | 49.938
2021-01-16 | 15:45 | 49.937
2021-01-16 | 15:45 | 49.938
2021-01-16 | 15:45 | 49.937
2021-01-16 | 15:45 | 49.936
2021-01-16 | 15:45 | 49.934
2021-01-16 | 15:45 | 49.931
2021-01-16 | 15:45 | 49.929
2021-01-16 | 15:45 | 49.927
2021-01-16 | 15:45 | 49.926
2021-01-16 | 15:45 | 49.925
2021-01-16 | 15:45 | 49.925
2021-01-16 | 15:45 | 49.924
2021-01-16 | 15:45 | 49.924
2021-01-16 | 15:45 | 49.923
2021-01-16 | 15:45 | 49.922
2021-01-16 | 15:45 | 49.921
2021-01-16 | 15:45 | 49.922
2021-01-16 | 15:45 | 49.922
2021-01-16 | 15:45 | 49.922
2021-01-16 | 15:45 | 49.922
2021-01-16 | 15:45 | 49.92
2021-01-16 | 15:45 | 49.922
2021-01-16 | 15:45 | 49.921
2021-01-16 | 15:45 | 49.923
2021-01-16 | 15:45 | 49.923
2021-01-16 | 15:45 | 49.924
2021-01-16 | 15:45 | 49.925
2021-01-16 | 15:45 | 49.926
2021-01-16 | 15:45 | 49.927
2021-01-16 | 15:45 | 49.927
2021-01-16 | 15:45 | 49.926
2021-01-16 | 15:45 | 49.925
2021-01-16 | 15:45 | 49.925
2021-01-16 | 15:45 | 49.926
2021-01-16 | 15:45 | 49.926
2021-01-16 | 15:45 | 49.926
2021-01-16 | 15:45 | 49.926
2021-01-16 | 15:45 | 49.924
2021-01-16 | 15:45 | 49.925
2021-01-16 | 15:45 | 49.924
2021-01-16 | 15:45 | 49.922
2021-01-16 | 15:46 | 49.921
2021-01-16 | 15:46 | 49.923
2021-01-16 | 15:46 | 49.922
2021-01-16 | 15:46 | 49.921
2021-01-16 | 15:46 | 49.919
2021-01-16 | 15:46 | 49.918
2021-01-16 | 15:46 | 49.918
2021-01-16 | 15:46 | 49.916
2021-01-16 | 15:46 | 49.916
2021-01-16 | 15:46 | 49.916
2021-01-16 | 15:46 | 49.914
2021-01-16 | 15:46 | 49.913
2021-01-16 | 15:46 | 49.912
2021-01-16 | 15:46 | 49.913
2021-01-16 | 15:46 | 49.913
2021-01-16 | 15:46 | 49.913
2021-01-16 | 15:46 | 49.911
2021-01-16 | 15:46 | 49.909
2021-01-16 | 15:46 | 49.908
2021-01-16 | 15:46 | 49.909
2021-01-16 | 15:46 | 49.911
2021-01-16 | 15:46 | 49.912
2021-01-16 | 15:46 | 49.912
2021-01-16 | 15:46 | 49.916
2021-01-16 | 15:46 | 49.917
2021-01-16 | 15:46 | 49.917
2021-01-16 | 15:46 | 49.916
2021-01-16 | 15:46 | 49.918
2021-01-16 | 15:46 | 49.918
2021-01-16 | 15:46 | 49.92
2021-01-16 | 15:46 | 49.919
2021-01-16 | 15:46 | 49.92
2021-01-16 | 15:46 | 49.92
2021-01-16 | 15:46 | 49.92
2021-01-16 | 15:46 | 49.918
2021-01-16 | 15:46 | 49.916
2021-01-16 | 15:46 | 49.914
2021-01-16 | 15:46 | 49.913
2021-01-16 | 15:46 | 49.911
2021-01-16 | 15:46 | 49.911
2021-01-16 | 15:46 | 49.911
2021-01-16 | 15:46 | 49.91
2021-01-16 | 15:46 | 49.911
2021-01-16 | 15:46 | 49.911
2021-01-16 | 15:46 | 49.909
2021-01-16 | 15:46 | 49.907
2021-01-16 | 15:46 | 49.908
2021-01-16 | 15:46 | 49.908
2021-01-16 | 15:46 | 49.908
2021-01-16 | 15:46 | 49.91
2021-01-16 | 15:46 | 49.911
2021-01-16 | 15:46 | 49.915
2021-01-16 | 15:46 | 49.916
2021-01-16 | 15:46 | 49.919
2021-01-16 | 15:46 | 49.921
2021-01-16 | 15:46 | 49.922
2021-01-16 | 15:46 | 49.926
2021-01-16 | 15:46 | 49.93
2021-01-16 | 15:46 | 49.931
2021-01-16 | 15:47 | 49.934
2021-01-16 | 15:47 | 49.936
2021-01-16 | 15:47 | 49.939
2021-01-16 | 15:47 | 49.939
2021-01-16 | 15:47 | 49.941
2021-01-16 | 15:47 | 49.942
2021-01-16 | 15:47 | 49.94
2021-01-16 | 15:47 | 49.937
2021-01-16 | 15:47 | 49.937
2021-01-16 | 15:47 | 49.936
2021-01-16 | 15:47 | 49.936
2021-01-16 | 15:47 | 49.934
2021-01-16 | 15:47 | 49.933
2021-01-16 | 15:47 | 49.933
2021-01-16 | 15:47 | 49.932
2021-01-16 | 15:47 | 49.931
2021-01-16 | 15:47 | 49.931
2021-01-16 | 15:47 | 49.93
2021-01-16 | 15:47 | 49.927
2021-01-16 | 15:47 | 49.925
2021-01-16 | 15:47 | 49.924
2021-01-16 | 15:47 | 49.921
2021-01-16 | 15:47 | 49.919
2021-01-16 | 15:47 | 49.921
2021-01-16 | 15:47 | 49.92
2021-01-16 | 15:47 | 49.918
2021-01-16 | 15:47 | 49.919
2021-01-16 | 15:47 | 49.919
2021-01-16 | 15:47 | 49.916
2021-01-16 | 15:47 | 49.915
2021-01-16 | 15:47 | 49.914
2021-01-16 | 15:47 | 49.912
2021-01-16 | 15:47 | 49.909
2021-01-16 | 15:47 | 49.912
2021-01-16 | 15:47 | 49.914
2021-01-16 | 15:47 | 49.914
2021-01-16 | 15:47 | 49.915
2021-01-16 | 15:47 | 49.913
2021-01-16 | 15:47 | 49.912
2021-01-16 | 15:47 | 49.912
2021-01-16 | 15:47 | 49.913
2021-01-16 | 15:47 | 49.914
2021-01-16 | 15:47 | 49.916
2021-01-16 | 15:47 | 49.918
2021-01-16 | 15:47 | 49.918
2021-01-16 | 15:47 | 49.922
2021-01-16 | 15:47 | 49.923
2021-01-16 | 15:47 | 49.925
2021-01-16 | 15:47 | 49.926
2021-01-16 | 15:47 | 49.923
2021-01-16 | 15:47 | 49.925
2021-01-16 | 15:47 | 49.923
2021-01-16 | 15:47 | 49.922
2021-01-16 | 15:47 | 49.922
2021-01-16 | 15:47 | 49.921
2021-01-16 | 15:47 | 49.921
2021-01-16 | 15:47 | 49.92
2021-01-16 | 15:47 | 49.922
2021-01-16 | 15:47 | 49.921
2021-01-16 | 15:47 | 49.921
2021-01-16 | 15:47 | 49.922
2021-01-16 | 15:48 | 49.921
2021-01-16 | 15:48 | 49.924
2021-01-16 | 15:48 | 49.927
2021-01-16 | 15:48 | 49.929
2021-01-16 | 15:48 | 49.932
2021-01-16 | 15:48 | 49.934
2021-01-16 | 15:48 | 49.935
2021-01-16 | 15:48 | 49.936
2021-01-16 | 15:48 | 49.934
2021-01-16 | 15:48 | 49.936
2021-01-16 | 15:48 | 49.935
2021-01-16 | 15:48 | 49.935
2021-01-16 | 15:48 | 49.933
2021-01-16 | 15:48 | 49.932
2021-01-16 | 15:48 | 49.931
2021-01-16 | 15:48 | 49.93
2021-01-16 | 15:48 | 49.928
2021-01-16 | 15:48 | 49.928
2021-01-16 | 15:48 | 49.928
2021-01-16 | 15:48 | 49.929
2021-01-16 | 15:48 | 49.931
2021-01-16 | 15:48 | 49.932
2021-01-16 | 15:48 | 49.933
2021-01-16 | 15:48 | 49.934
2021-01-16 | 15:48 | 49.938
2021-01-16 | 15:48 | 49.939
2021-01-16 | 15:48 | 49.94
2021-01-16 | 15:48 | 49.94
2021-01-16 | 15:48 | 49.939
2021-01-16 | 15:48 | 49.938
2021-01-16 | 15:48 | 49.936
2021-01-16 | 15:48 | 49.935
2021-01-16 | 15:48 | 49.936
2021-01-16 | 15:48 | 49.94
2021-01-16 | 15:48 | 49.944
2021-01-16 | 15:48 | 49.945
2021-01-16 | 15:48 | 49.947
2021-01-16 | 15:48 | 49.948
2021-01-16 | 15:48 | 49.95
2021-01-16 | 15:48 | 49.95
2021-01-16 | 15:48 | 49.952
2021-01-16 | 15:48 | 49.95
2021-01-16 | 15:48 | 49.948
2021-01-16 | 15:48 | 49.949
2021-01-16 | 15:48 | 49.948
2021-01-16 | 15:48 | 49.947
2021-01-16 | 15:48 | 49.946
2021-01-16 | 15:48 | 49.946
2021-01-16 | 15:48 | 49.946
2021-01-16 | 15:48 | 49.945
2021-01-16 | 15:48 | 49.945
2021-01-16 | 15:48 | 49.945
2021-01-16 | 15:48 | 49.944
2021-01-16 | 15:48 | 49.941
2021-01-16 | 15:48 | 49.937
2021-01-16 | 15:48 | 49.934
2021-01-16 | 15:48 | 49.931
2021-01-16 | 15:48 | 49.926
2021-01-16 | 15:48 | 49.923
2021-01-16 | 15:49 | 49.922
2021-01-16 | 15:49 | 49.921
2021-01-16 | 15:49 | 49.921
2021-01-16 | 15:49 | 49.918
2021-01-16 | 15:49 | 49.916
2021-01-16 | 15:49 | 49.916
2021-01-16 | 15:49 | 49.917
2021-01-16 | 15:49 | 49.919
2021-01-16 | 15:49 | 49.92
2021-01-16 | 15:49 | 49.924
2021-01-16 | 15:49 | 49.923
2021-01-16 | 15:49 | 49.924
2021-01-16 | 15:49 | 49.923
2021-01-16 | 15:49 | 49.923
2021-01-16 | 15:49 | 49.92
2021-01-16 | 15:49 | 49.916
2021-01-16 | 15:49 | 49.916
2021-01-16 | 15:49 | 49.915
2021-01-16 | 15:49 | 49.912
2021-01-16 | 15:49 | 49.91
2021-01-16 | 15:49 | 49.908
2021-01-16 | 15:49 | 49.906
2021-01-16 | 15:49 | 49.905
2021-01-16 | 15:49 | 49.904
2021-01-16 | 15:49 | 49.904
2021-01-16 | 15:49 | 49.903
2021-01-16 | 15:49 | 49.903
2021-01-16 | 15:49 | 49.902
2021-01-16 | 15:49 | 49.904
2021-01-16 | 15:49 | 49.906
2021-01-16 | 15:49 | 49.906
2021-01-16 | 15:49 | 49.909
2021-01-16 | 15:49 | 49.908
2021-01-16 | 15:49 | 49.909
2021-01-16 | 15:49 | 49.911
2021-01-16 | 15:49 | 49.912
2021-01-16 | 15:49 | 49.915
2021-01-16 | 15:49 | 49.915
2021-01-16 | 15:49 | 49.916
2021-01-16 | 15:49 | 49.916
2021-01-16 | 15:49 | 49.917
2021-01-16 | 15:49 | 49.917
2021-01-16 | 15:49 | 49.917
2021-01-16 | 15:49 | 49.919
2021-01-16 | 15:49 | 49.92
2021-01-16 | 15:49 | 49.922
2021-01-16 | 15:49 | 49.924
2021-01-16 | 15:49 | 49.926
2021-01-16 | 15:49 | 49.928
2021-01-16 | 15:49 | 49.929
2021-01-16 | 15:49 | 49.926
2021-01-16 | 15:49 | 49.922
2021-01-16 | 15:49 | 49.921
2021-01-16 | 15:49 | 49.919
2021-01-16 | 15:49 | 49.918
2021-01-16 | 15:49 | 49.917
2021-01-16 | 15:49 | 49.915
2021-01-16 | 15:49 | 49.911
2021-01-16 | 15:49 | 49.909
2021-01-16 | 15:49 | 49.909
2021-01-16 | 15:49 | 49.905
2021-01-16 | 15:50 | 49.901
2021-01-16 | 15:50 | 49.899
2021-01-16 | 15:50 | 49.898
2021-01-16 | 15:50 | 49.897
2021-01-16 | 15:50 | 49.9
2021-01-16 | 15:50 | 49.899
2021-01-16 | 15:50 | 49.9
2021-01-16 | 15:50 | 49.902
2021-01-16 | 15:50 | 49.903
2021-01-16 | 15:50 | 49.905
2021-01-16 | 15:50 | 49.908
2021-01-16 | 15:50 | 49.907
2021-01-16 | 15:50 | 49.909
2021-01-16 | 15:50 | 49.911
2021-01-16 | 15:50 | 49.911
2021-01-16 | 15:50 | 49.914
2021-01-16 | 15:50 | 49.915
2021-01-16 | 15:50 | 49.917
2021-01-16 | 15:50 | 49.917
2021-01-16 | 15:50 | 49.919
2021-01-16 | 15:50 | 49.919
2021-01-16 | 15:50 | 49.921
2021-01-16 | 15:50 | 49.921
2021-01-16 | 15:50 | 49.92
2021-01-16 | 15:50 | 49.918
2021-01-16 | 15:50 | 49.916
2021-01-16 | 15:50 | 49.911
2021-01-16 | 15:50 | 49.91
2021-01-16 | 15:50 | 49.911
2021-01-16 | 15:50 | 49.909
2021-01-16 | 15:50 | 49.905
2021-01-16 | 15:50 | 49.901
2021-01-16 | 15:50 | 49.899
2021-01-16 | 15:50 | 49.897
2021-01-16 | 15:50 | 49.896
2021-01-16 | 15:50 | 49.897
2021-01-16 | 15:50 | 49.9
2021-01-16 | 15:50 | 49.902
2021-01-16 | 15:50 | 49.902
2021-01-16 | 15:50 | 49.903
2021-01-16 | 15:50 | 49.902
2021-01-16 | 15:50 | 49.904
2021-01-16 | 15:50 | 49.904
2021-01-16 | 15:50 | 49.902
2021-01-16 | 15:50 | 49.902
2021-01-16 | 15:50 | 49.903
2021-01-16 | 15:50 | 49.906
2021-01-16 | 15:50 | 49.908
2021-01-16 | 15:50 | 49.91
2021-01-16 | 15:50 | 49.913
2021-01-16 | 15:50 | 49.916
2021-01-16 | 15:50 | 49.917
2021-01-16 | 15:50 | 49.918
2021-01-16 | 15:50 | 49.92
2021-01-16 | 15:50 | 49.92
2021-01-16 | 15:50 | 49.92
2021-01-16 | 15:50 | 49.919
2021-01-16 | 15:50 | 49.917
2021-01-16 | 15:50 | 49.916
2021-01-16 | 15:51 | 49.917
2021-01-16 | 15:51 | 49.917
2021-01-16 | 15:51 | 49.915
2021-01-16 | 15:51 | 49.913
2021-01-16 | 15:51 | 49.913
2021-01-16 | 15:51 | 49.915
2021-01-16 | 15:51 | 49.92
2021-01-16 | 15:51 | 49.922
2021-01-16 | 15:51 | 49.926
2021-01-16 | 15:51 | 49.927
2021-01-16 | 15:51 | 49.93
2021-01-16 | 15:51 | 49.93
2021-01-16 | 15:51 | 49.932
2021-01-16 | 15:51 | 49.934
2021-01-16 | 15:51 | 49.933
2021-01-16 | 15:51 | 49.931
2021-01-16 | 15:51 | 49.929
2021-01-16 | 15:51 | 49.926
2021-01-16 | 15:51 | 49.924
2021-01-16 | 15:51 | 49.924
2021-01-16 | 15:51 | 49.925
2021-01-16 | 15:51 | 49.927
2021-01-16 | 15:51 | 49.93
2021-01-16 | 15:51 | 49.932
2021-01-16 | 15:51 | 49.932
2021-01-16 | 15:51 | 49.934
2021-01-16 | 15:51 | 49.933
2021-01-16 | 15:51 | 49.935
2021-01-16 | 15:51 | 49.934
2021-01-16 | 15:51 | 49.932
2021-01-16 | 15:51 | 49.932
2021-01-16 | 15:51 | 49.932
2021-01-16 | 15:51 | 49.93
2021-01-16 | 15:51 | 49.928
2021-01-16 | 15:51 | 49.927
2021-01-16 | 15:51 | 49.927
2021-01-16 | 15:51 | 49.926
2021-01-16 | 15:51 | 49.925
2021-01-16 | 15:51 | 49.925
2021-01-16 | 15:51 | 49.923
2021-01-16 | 15:51 | 49.921
2021-01-16 | 15:51 | 49.918
2021-01-16 | 15:51 | 49.917
2021-01-16 | 15:51 | 49.916
2021-01-16 | 15:51 | 49.915
2021-01-16 | 15:51 | 49.915
2021-01-16 | 15:51 | 49.915
2021-01-16 | 15:51 | 49.914
2021-01-16 | 15:51 | 49.915
2021-01-16 | 15:51 | 49.916
2021-01-16 | 15:51 | 49.915
2021-01-16 | 15:51 | 49.915
2021-01-16 | 15:51 | 49.915
2021-01-16 | 15:51 | 49.917
2021-01-16 | 15:51 | 49.919
2021-01-16 | 15:51 | 49.919
2021-01-16 | 15:51 | 49.918
2021-01-16 | 15:51 | 49.917
2021-01-16 | 15:51 | 49.914
2021-01-16 | 15:51 | 49.912
2021-01-16 | 15:51 | 49.906
2021-01-16 | 15:52 | 49.902
2021-01-16 | 15:52 | 49.899
2021-01-16 | 15:52 | 49.899
2021-01-16 | 15:52 | 49.901
2021-01-16 | 15:52 | 49.905
2021-01-16 | 15:52 | 49.909
2021-01-16 | 15:52 | 49.914
2021-01-16 | 15:52 | 49.917
2021-01-16 | 15:52 | 49.916
2021-01-16 | 15:52 | 49.914
2021-01-16 | 15:52 | 49.914
2021-01-16 | 15:52 | 49.916
2021-01-16 | 15:52 | 49.92
2021-01-16 | 15:52 | 49.921
2021-01-16 | 15:52 | 49.923
2021-01-16 | 15:52 | 49.923
2021-01-16 | 15:52 | 49.923
2021-01-16 | 15:52 | 49.922
2021-01-16 | 15:52 | 49.922
2021-01-16 | 15:52 | 49.924
2021-01-16 | 15:52 | 49.923
2021-01-16 | 15:52 | 49.922
2021-01-16 | 15:52 | 49.92
2021-01-16 | 15:52 | 49.92
2021-01-16 | 15:52 | 49.92
2021-01-16 | 15:52 | 49.918
2021-01-16 | 15:52 | 49.917
2021-01-16 | 15:52 | 49.917
2021-01-16 | 15:52 | 49.916
2021-01-16 | 15:52 | 49.913
2021-01-16 | 15:52 | 49.911
2021-01-16 | 15:52 | 49.91
2021-01-16 | 15:52 | 49.911
2021-01-16 | 15:52 | 49.91
2021-01-16 | 15:52 | 49.91
2021-01-16 | 15:52 | 49.909
2021-01-16 | 15:52 | 49.91
2021-01-16 | 15:52 | 49.91
2021-01-16 | 15:52 | 49.909
2021-01-16 | 15:52 | 49.909
2021-01-16 | 15:52 | 49.91
2021-01-16 | 15:52 | 49.91
2021-01-16 | 15:52 | 49.909
2021-01-16 | 15:52 | 49.909
2021-01-16 | 15:52 | 49.908
2021-01-16 | 15:52 | 49.902
2021-01-16 | 15:52 | 49.9
2021-01-16 | 15:52 | 49.896
2021-01-16 | 15:52 | 49.892
2021-01-16 | 15:52 | 49.887
2021-01-16 | 15:52 | 49.884
2021-01-16 | 15:52 | 49.883
2021-01-16 | 15:52 | 49.883
2021-01-16 | 15:52 | 49.883
2021-01-16 | 15:52 | 49.882
2021-01-16 | 15:52 | 49.883
2021-01-16 | 15:52 | 49.884
2021-01-16 | 15:52 | 49.883
2021-01-16 | 15:52 | 49.883
2021-01-16 | 15:52 | 49.881
2021-01-16 | 15:53 | 49.881
2021-01-16 | 15:53 | 49.881
2021-01-16 | 15:53 | 49.881
2021-01-16 | 15:53 | 49.884
2021-01-16 | 15:53 | 49.883
2021-01-16 | 15:53 | 49.884
2021-01-16 | 15:53 | 49.882
2021-01-16 | 15:53 | 49.884
2021-01-16 | 15:53 | 49.884
2021-01-16 | 15:53 | 49.886
2021-01-16 | 15:53 | 49.888
2021-01-16 | 15:53 | 49.889
2021-01-16 | 15:53 | 49.889
2021-01-16 | 15:53 | 49.887
2021-01-16 | 15:53 | 49.887
2021-01-16 | 15:53 | 49.888
2021-01-16 | 15:53 | 49.889
2021-01-16 | 15:53 | 49.889
2021-01-16 | 15:53 | 49.891
2021-01-16 | 15:53 | 49.892
2021-01-16 | 15:53 | 49.892
2021-01-16 | 15:53 | 49.891
2021-01-16 | 15:53 | 49.89
2021-01-16 | 15:53 | 49.889
2021-01-16 | 15:53 | 49.89
2021-01-16 | 15:53 | 49.888
2021-01-16 | 15:53 | 49.887
2021-01-16 | 15:53 | 49.888
2021-01-16 | 15:53 | 49.887
2021-01-16 | 15:53 | 49.886
2021-01-16 | 15:53 | 49.884
2021-01-16 | 15:53 | 49.884
2021-01-16 | 15:53 | 49.883
2021-01-16 | 15:53 | 49.883
2021-01-16 | 15:53 | 49.884
2021-01-16 | 15:53 | 49.885
2021-01-16 | 15:53 | 49.882
2021-01-16 | 15:53 | 49.881
2021-01-16 | 15:53 | 49.881
2021-01-16 | 15:53 | 49.882
2021-01-16 | 15:53 | 49.883
2021-01-16 | 15:53 | 49.883
2021-01-16 | 15:53 | 49.883
2021-01-16 | 15:53 | 49.883
2021-01-16 | 15:53 | 49.883
2021-01-16 | 15:53 | 49.883
2021-01-16 | 15:53 | 49.886
2021-01-16 | 15:53 | 49.883
2021-01-16 | 15:53 | 49.883
2021-01-16 | 15:53 | 49.882
2021-01-16 | 15:53 | 49.882
2021-01-16 | 15:53 | 49.882
2021-01-16 | 15:53 | 49.879
2021-01-16 | 15:53 | 49.877
2021-01-16 | 15:53 | 49.877
2021-01-16 | 15:53 | 49.878
2021-01-16 | 15:53 | 49.878
2021-01-16 | 15:53 | 49.879
2021-01-16 | 15:53 | 49.882
2021-01-16 | 15:54 | 49.885
2021-01-16 | 15:54 | 49.884
2021-01-16 | 15:54 | 49.883
2021-01-16 | 15:54 | 49.882
2021-01-16 | 15:54 | 49.883
2021-01-16 | 15:54 | 49.881
2021-01-16 | 15:54 | 49.88
2021-01-16 | 15:54 | 49.876
2021-01-16 | 15:54 | 49.875
2021-01-16 | 15:54 | 49.873
2021-01-16 | 15:54 | 49.873
2021-01-16 | 15:54 | 49.871
2021-01-16 | 15:54 | 49.871
2021-01-16 | 15:54 | 49.873
2021-01-16 | 15:54 | 49.874
2021-01-16 | 15:54 | 49.875
2021-01-16 | 15:54 | 49.877
2021-01-16 | 15:54 | 49.875
2021-01-16 | 15:54 | 49.878
2021-01-16 | 15:54 | 49.878
2021-01-16 | 15:54 | 49.879
2021-01-16 | 15:54 | 49.879
2021-01-16 | 15:54 | 49.878
2021-01-16 | 15:54 | 49.877
2021-01-16 | 15:54 | 49.875
2021-01-16 | 15:54 | 49.875
2021-01-16 | 15:54 | 49.873
2021-01-16 | 15:54 | 49.873
2021-01-16 | 15:54 | 49.872
2021-01-16 | 15:54 | 49.871
2021-01-16 | 15:54 | 49.871
2021-01-16 | 15:54 | 49.87
2021-01-16 | 15:54 | 49.869
2021-01-16 | 15:54 | 49.866
2021-01-16 | 15:54 | 49.861
2021-01-16 | 15:54 | 49.859
2021-01-16 | 15:54 | 49.859
2021-01-16 | 15:54 | 49.858
2021-01-16 | 15:54 | 49.858
2021-01-16 | 15:54 | 49.855
2021-01-16 | 15:54 | 49.853
2021-01-16 | 15:54 | 49.853
2021-01-16 | 15:54 | 49.852
2021-01-16 | 15:54 | 49.855
2021-01-16 | 15:54 | 49.856
2021-01-16 | 15:54 | 49.857
2021-01-16 | 15:54 | 49.86
2021-01-16 | 15:54 | 49.862
2021-01-16 | 15:54 | 49.862
2021-01-16 | 15:54 | 49.862
2021-01-16 | 15:54 | 49.862
2021-01-16 | 15:54 | 49.862
2021-01-16 | 15:54 | 49.862
2021-01-16 | 15:54 | 49.861
2021-01-16 | 15:54 | 49.862
2021-01-16 | 15:54 | 49.86
2021-01-16 | 15:54 | 49.856
2021-01-16 | 15:54 | 49.853
2021-01-16 | 15:54 | 49.85
2021-01-16 | 15:54 | 49.849
2021-01-16 | 15:54 | 49.845
2021-01-16 | 15:55 | 49.846
2021-01-16 | 15:55 | 49.843
2021-01-16 | 15:55 | 49.844
2021-01-16 | 15:55 | 49.843
2021-01-16 | 15:55 | 49.842
2021-01-16 | 15:55 | 49.842
2021-01-16 | 15:55 | 49.843
2021-01-16 | 15:55 | 49.845
2021-01-16 | 15:55 | 49.843
2021-01-16 | 15:55 | 49.842
2021-01-16 | 15:55 | 49.841
2021-01-16 | 15:55 | 49.84
2021-01-16 | 15:55 | 49.84
2021-01-16 | 15:55 | 49.838
2021-01-16 | 15:55 | 49.837
2021-01-16 | 15:55 | 49.838
2021-01-16 | 15:55 | 49.841
2021-01-16 | 15:55 | 49.843
2021-01-16 | 15:55 | 49.843
2021-01-16 | 15:55 | 49.847
2021-01-16 | 15:55 | 49.85
2021-01-16 | 15:55 | 49.851
2021-01-16 | 15:55 | 49.852
2021-01-16 | 15:55 | 49.855
2021-01-16 | 15:55 | 49.856
2021-01-16 | 15:55 | 49.856
2021-01-16 | 15:55 | 49.856
2021-01-16 | 15:55 | 49.855
2021-01-16 | 15:55 | 49.853
2021-01-16 | 15:55 | 49.851
2021-01-16 | 15:55 | 49.847
2021-01-16 | 15:55 | 49.846
2021-01-16 | 15:55 | 49.847
2021-01-16 | 15:55 | 49.849
2021-01-16 | 15:55 | 49.852
2021-01-16 | 15:55 | 49.855
2021-01-16 | 15:55 | 49.86
2021-01-16 | 15:55 | 49.859
2021-01-16 | 15:55 | 49.863
2021-01-16 | 15:55 | 49.868
2021-01-16 | 15:55 | 49.872
2021-01-16 | 15:55 | 49.873
2021-01-16 | 15:55 | 49.874
2021-01-16 | 15:55 | 49.876
2021-01-16 | 15:55 | 49.875
2021-01-16 | 15:55 | 49.874
2021-01-16 | 15:55 | 49.877
2021-01-16 | 15:55 | 49.877
2021-01-16 | 15:55 | 49.878
2021-01-16 | 15:55 | 49.877
2021-01-16 | 15:55 | 49.878
2021-01-16 | 15:55 | 49.881
2021-01-16 | 15:55 | 49.88
2021-01-16 | 15:55 | 49.882
2021-01-16 | 15:55 | 49.882
2021-01-16 | 15:55 | 49.88
2021-01-16 | 15:55 | 49.879
2021-01-16 | 15:55 | 49.878
2021-01-16 | 15:55 | 49.883
2021-01-16 | 15:56 | 49.885
2021-01-16 | 15:56 | 49.884
2021-01-16 | 15:56 | 49.883
2021-01-16 | 15:56 | 49.88
2021-01-16 | 15:56 | 49.878
2021-01-16 | 15:56 | 49.879
2021-01-16 | 15:56 | 49.88
2021-01-16 | 15:56 | 49.878
2021-01-16 | 15:56 | 49.877
2021-01-16 | 15:56 | 49.877
2021-01-16 | 15:56 | 49.876
2021-01-16 | 15:56 | 49.874
2021-01-16 | 15:56 | 49.873
2021-01-16 | 15:56 | 49.871
2021-01-16 | 15:56 | 49.87
2021-01-16 | 15:56 | 49.871
2021-01-16 | 15:56 | 49.872
2021-01-16 | 15:56 | 49.872
2021-01-16 | 15:56 | 49.873
2021-01-16 | 15:56 | 49.876
2021-01-16 | 15:56 | 49.876
2021-01-16 | 15:56 | 49.876
2021-01-16 | 15:56 | 49.877
2021-01-16 | 15:56 | 49.877
2021-01-16 | 15:56 | 49.878
2021-01-16 | 15:56 | 49.879
2021-01-16 | 15:56 | 49.881
2021-01-16 | 15:56 | 49.884
2021-01-16 | 15:56 | 49.885
2021-01-16 | 15:56 | 49.885
2021-01-16 | 15:56 | 49.885
2021-01-16 | 15:56 | 49.883
2021-01-16 | 15:56 | 49.881
2021-01-16 | 15:56 | 49.88
2021-01-16 | 15:56 | 49.878
2021-01-16 | 15:56 | 49.877
2021-01-16 | 15:56 | 49.874
2021-01-16 | 15:56 | 49.872
2021-01-16 | 15:56 | 49.87
2021-01-16 | 15:56 | 49.867
2021-01-16 | 15:56 | 49.868
2021-01-16 | 15:56 | 49.869
2021-01-16 | 15:56 | 49.87
2021-01-16 | 15:56 | 49.871
2021-01-16 | 15:56 | 49.872
2021-01-16 | 15:56 | 49.873
2021-01-16 | 15:56 | 49.876
2021-01-16 | 15:56 | 49.876
2021-01-16 | 15:56 | 49.879
2021-01-16 | 15:56 | 49.877
2021-01-16 | 15:56 | 49.877
2021-01-16 | 15:56 | 49.877
2021-01-16 | 15:56 | 49.878
2021-01-16 | 15:56 | 49.882
2021-01-16 | 15:56 | 49.883
2021-01-16 | 15:56 | 49.886
2021-01-16 | 15:56 | 49.888
2021-01-16 | 15:56 | 49.893
2021-01-16 | 15:56 | 49.895
2021-01-16 | 15:56 | 49.898
2021-01-16 | 15:56 | 49.903
2021-01-16 | 15:57 | 49.908
2021-01-16 | 15:57 | 49.914
2021-01-16 | 15:57 | 49.921
2021-01-16 | 15:57 | 49.926
2021-01-16 | 15:57 | 49.925
2021-01-16 | 15:57 | 49.924
2021-01-16 | 15:57 | 49.925
2021-01-16 | 15:57 | 49.925
2021-01-16 | 15:57 | 49.926
2021-01-16 | 15:57 | 49.93
2021-01-16 | 15:57 | 49.932
2021-01-16 | 15:57 | 49.932
2021-01-16 | 15:57 | 49.935
2021-01-16 | 15:57 | 49.938
2021-01-16 | 15:57 | 49.942
2021-01-16 | 15:57 | 49.944
2021-01-16 | 15:57 | 49.946
2021-01-16 | 15:57 | 49.946
2021-01-16 | 15:57 | 49.945
2021-01-16 | 15:57 | 49.944
2021-01-16 | 15:57 | 49.943
2021-01-16 | 15:57 | 49.944
2021-01-16 | 15:57 | 49.942
2021-01-16 | 15:57 | 49.942
2021-01-16 | 15:57 | 49.938
2021-01-16 | 15:57 | 49.937
2021-01-16 | 15:57 | 49.933
2021-01-16 | 15:57 | 49.935
2021-01-16 | 15:57 | 49.935
2021-01-16 | 15:57 | 49.936
2021-01-16 | 15:57 | 49.934
2021-01-16 | 15:57 | 49.931
2021-01-16 | 15:57 | 49.927
2021-01-16 | 15:57 | 49.927
2021-01-16 | 15:57 | 49.925
2021-01-16 | 15:57 | 49.926
2021-01-16 | 15:57 | 49.924
2021-01-16 | 15:57 | 49.922
2021-01-16 | 15:57 | 49.918
2021-01-16 | 15:57 | 49.916
2021-01-16 | 15:57 | 49.917
2021-01-16 | 15:57 | 49.915
2021-01-16 | 15:57 | 49.915
2021-01-16 | 15:57 | 49.914
2021-01-16 | 15:57 | 49.914
2021-01-16 | 15:57 | 49.913
2021-01-16 | 15:57 | 49.914
2021-01-16 | 15:57 | 49.915
2021-01-16 | 15:57 | 49.916
2021-01-16 | 15:57 | 49.915
2021-01-16 | 15:57 | 49.915
2021-01-16 | 15:57 | 49.914
2021-01-16 | 15:57 | 49.917
2021-01-16 | 15:57 | 49.915
2021-01-16 | 15:57 | 49.915
2021-01-16 | 15:57 | 49.913
2021-01-16 | 15:57 | 49.911
2021-01-16 | 15:57 | 49.91
2021-01-16 | 15:57 | 49.912
2021-01-16 | 15:58 | 49.911
2021-01-16 | 15:58 | 49.908
2021-01-16 | 15:58 | 49.91
2021-01-16 | 15:58 | 49.909
2021-01-16 | 15:58 | 49.906
2021-01-16 | 15:58 | 49.906
2021-01-16 | 15:58 | 49.903
2021-01-16 | 15:58 | 49.904
2021-01-16 | 15:58 | 49.906
2021-01-16 | 15:58 | 49.907
2021-01-16 | 15:58 | 49.909
2021-01-16 | 15:58 | 49.906
2021-01-16 | 15:58 | 49.906
2021-01-16 | 15:58 | 49.908
2021-01-16 | 15:58 | 49.91
2021-01-16 | 15:58 | 49.915
2021-01-16 | 15:58 | 49.919
2021-01-16 | 15:58 | 49.922
2021-01-16 | 15:58 | 49.93
2021-01-16 | 15:58 | 49.929
2021-01-16 | 15:58 | 49.931
2021-01-16 | 15:58 | 49.934
2021-01-16 | 15:58 | 49.934
2021-01-16 | 15:58 | 49.932
2021-01-16 | 15:58 | 49.927
2021-01-16 | 15:58 | 49.927
2021-01-16 | 15:58 | 49.926
2021-01-16 | 15:58 | 49.923
2021-01-16 | 15:58 | 49.925
2021-01-16 | 15:58 | 49.923
2021-01-16 | 15:58 | 49.922
2021-01-16 | 15:58 | 49.92
2021-01-16 | 15:58 | 49.92
2021-01-16 | 15:58 | 49.922
2021-01-16 | 15:58 | 49.923
2021-01-16 | 15:58 | 49.926
2021-01-16 | 15:58 | 49.931
2021-01-16 | 15:58 | 49.937
2021-01-16 | 15:58 | 49.941
2021-01-16 | 15:58 | 49.945
2021-01-16 | 15:58 | 49.945
2021-01-16 | 15:58 | 49.947
2021-01-16 | 15:58 | 49.948
2021-01-16 | 15:58 | 49.947
2021-01-16 | 15:58 | 49.948
2021-01-16 | 15:58 | 49.948
2021-01-16 | 15:58 | 49.949
2021-01-16 | 15:58 | 49.948
2021-01-16 | 15:58 | 49.948
2021-01-16 | 15:58 | 49.949
2021-01-16 | 15:58 | 49.952
2021-01-16 | 15:58 | 49.953
2021-01-16 | 15:58 | 49.956
2021-01-16 | 15:58 | 49.959
2021-01-16 | 15:58 | 49.961
2021-01-16 | 15:58 | 49.962
2021-01-16 | 15:58 | 49.965
2021-01-16 | 15:58 | 49.965
2021-01-16 | 15:58 | 49.963
2021-01-16 | 15:58 | 49.961
2021-01-16 | 15:58 | 49.962
2021-01-16 | 15:59 | 49.962
2021-01-16 | 15:59 | 49.96
2021-01-16 | 15:59 | 49.961
2021-01-16 | 15:59 | 49.964
2021-01-16 | 15:59 | 49.966
2021-01-16 | 15:59 | 49.967
2021-01-16 | 15:59 | 49.968
2021-01-16 | 15:59 | 49.97
2021-01-16 | 15:59 | 49.972
2021-01-16 | 15:59 | 49.974
2021-01-16 | 15:59 | 49.974
2021-01-16 | 15:59 | 49.974
2021-01-16 | 15:59 | 49.972
2021-01-16 | 15:59 | 49.975
2021-01-16 | 15:59 | 49.973
2021-01-16 | 15:59 | 49.973
2021-01-16 | 15:59 | 49.971
2021-01-16 | 15:59 | 49.968
2021-01-16 | 15:59 | 49.967
2021-01-16 | 15:59 | 49.967
2021-01-16 | 15:59 | 49.967
2021-01-16 | 15:59 | 49.968
2021-01-16 | 15:59 | 49.97
2021-01-16 | 15:59 | 49.971
2021-01-16 | 15:59 | 49.97
2021-01-16 | 15:59 | 49.971
2021-01-16 | 15:59 | 49.969
2021-01-16 | 15:59 | 49.969
2021-01-16 | 15:59 | 49.969
2021-01-16 | 15:59 | 49.969
2021-01-16 | 15:59 | 49.968
2021-01-16 | 15:59 | 49.969
2021-01-16 | 15:59 | 49.966
2021-01-16 | 15:59 | 49.965
2021-01-16 | 15:59 | 49.967
2021-01-16 | 15:59 | 49.967
2021-01-16 | 15:59 | 49.969
2021-01-16 | 15:59 | 49.971
2021-01-16 | 15:59 | 49.973
2021-01-16 | 15:59 | 49.975
2021-01-16 | 15:59 | 49.976
2021-01-16 | 15:59 | 49.978
2021-01-16 | 15:59 | 49.978
2021-01-16 | 15:59 | 49.979
2021-01-16 | 15:59 | 49.979
2021-01-16 | 15:59 | 49.981
2021-01-16 | 15:59 | 49.981
2021-01-16 | 15:59 | 49.981
2021-01-16 | 15:59 | 49.98
2021-01-16 | 15:59 | 49.982
2021-01-16 | 15:59 | 49.981
2021-01-16 | 15:59 | 49.981
2021-01-16 | 15:59 | 49.979
2021-01-16 | 15:59 | 49.976
2021-01-16 | 15:59 | 49.975
2021-01-16 | 15:59 | 49.972
2021-01-16 | 15:59 | 49.971
2021-01-16 | 15:59 | 49.971
2021-01-16 | 15:59 | 49.969
2021-01-16 | 16:00 | 49.968
2021-01-16 | 16:00 | 49.964
2021-01-16 | 16:00 | 49.962
2021-01-16 | 16:00 | 49.958
2021-01-16 | 16:00 | 49.956
2021-01-16 | 16:00 | 49.954
2021-01-16 | 16:00 | 49.953
2021-01-16 | 16:00 | 49.952
2021-01-16 | 16:00 | 49.951
2021-01-16 | 16:00 | 49.948
2021-01-16 | 16:00 | 49.946
2021-01-16 | 16:00 | 49.947
2021-01-16 | 16:00 | 49.946
2021-01-16 | 16:00 | 49.949
2021-01-16 | 16:00 | 49.952
2021-01-16 | 16:00 | 49.954
2021-01-16 | 16:00 | 49.958
2021-01-16 | 16:00 | 49.96
2021-01-16 | 16:00 | 49.963
2021-01-16 | 16:00 | 49.963
2021-01-16 | 16:00 | 49.966
2021-01-16 | 16:00 | 49.97
2021-01-16 | 16:00 | 49.972
2021-01-16 | 16:00 | 49.976
2021-01-16 | 16:00 | 49.976
2021-01-16 | 16:00 | 49.979
2021-01-16 | 16:00 | 49.982
2021-01-16 | 16:00 | 49.982
2021-01-16 | 16:00 | 49.983
2021-01-16 | 16:00 | 49.986
2021-01-16 | 16:00 | 49.986
2021-01-16 | 16:00 | 49.988
2021-01-16 | 16:00 | 49.99
2021-01-16 | 16:00 | 49.99
2021-01-16 | 16:00 | 49.99
2021-01-16 | 16:00 | 49.99
2021-01-16 | 16:00 | 49.988
2021-01-16 | 16:00 | 49.987
2021-01-16 | 16:00 | 49.985
2021-01-16 | 16:00 | 49.983
2021-01-16 | 16:00 | 49.981
2021-01-16 | 16:00 | 49.982
2021-01-16 | 16:00 | 49.981
2021-01-16 | 16:00 | 49.98
2021-01-16 | 16:00 | 49.979
2021-01-16 | 16:00 | 49.977
2021-01-16 | 16:00 | 49.979
2021-01-16 | 16:00 | 49.982
2021-01-16 | 16:00 | 49.983
2021-01-16 | 16:00 | 49.984
2021-01-16 | 16:00 | 49.985
2021-01-16 | 16:00 | 49.986
2021-01-16 | 16:00 | 49.988
2021-01-16 | 16:00 | 49.989
2021-01-16 | 16:00 | 49.99
2021-01-16 | 16:00 | 49.991
2021-01-16 | 16:00 | 49.991
2021-01-16 | 16:00 | 49.989
2021-01-16 | 16:00 | 49.991
2021-01-16 | 16:00 | 49.992
2021-01-16 | 16:00 | 49.991
2021-01-16 | 16:01 | 49.99
2021-01-16 | 16:01 | 49.99
2021-01-16 | 16:01 | 49.991
2021-01-16 | 16:01 | 49.992
2021-01-16 | 16:01 | 49.993
2021-01-16 | 16:01 | 49.994
2021-01-16 | 16:01 | 49.995
2021-01-16 | 16:01 | 49.997
2021-01-16 | 16:01 | 50.001
2021-01-16 | 16:01 | 50.004
2021-01-16 | 16:01 | 50.009
2021-01-16 | 16:01 | 50.014
2021-01-16 | 16:01 | 50.019
2021-01-16 | 16:01 | 50.023
2021-01-16 | 16:01 | 50.028
2021-01-16 | 16:01 | 50.032
2021-01-16 | 16:01 | 50.036
2021-01-16 | 16:01 | 50.041
2021-01-16 | 16:01 | 50.043
2021-01-16 | 16:01 | 50.045
2021-01-16 | 16:01 | 50.047
2021-01-16 | 16:01 | 50.048
2021-01-16 | 16:01 | 50.05
2021-01-16 | 16:01 | 50.052
2021-01-16 | 16:01 | 50.056
2021-01-16 | 16:01 | 50.061
2021-01-16 | 16:01 | 50.066
2021-01-16 | 16:01 | 50.07
2021-01-16 | 16:01 | 50.073
2021-01-16 | 16:01 | 50.077
2021-01-16 | 16:01 | 50.077
2021-01-16 | 16:01 | 50.076
2021-01-16 | 16:01 | 50.078
2021-01-16 | 16:01 | 50.079
2021-01-16 | 16:01 | 50.08
2021-01-16 | 16:01 | 50.081
2021-01-16 | 16:01 | 50.081
2021-01-16 | 16:01 | 50.081
2021-01-16 | 16:01 | 50.081
2021-01-16 | 16:01 | 50.081
2021-01-16 | 16:01 | 50.081
2021-01-16 | 16:01 | 50.081
2021-01-16 | 16:01 | 50.083
2021-01-16 | 16:01 | 50.084
2021-01-16 | 16:01 | 50.088
2021-01-16 | 16:01 | 50.09
2021-01-16 | 16:01 | 50.093
2021-01-16 | 16:01 | 50.096
2021-01-16 | 16:01 | 50.099
2021-01-16 | 16:01 | 50.102
2021-01-16 | 16:01 | 50.101
2021-01-16 | 16:01 | 50.101
2021-01-16 | 16:01 | 50.101
2021-01-16 | 16:01 | 50.103
2021-01-16 | 16:01 | 50.106
2021-01-16 | 16:01 | 50.108
2021-01-16 | 16:01 | 50.11
2021-01-16 | 16:01 | 50.111
2021-01-16 | 16:01 | 50.114
2021-01-16 | 16:01 | 50.115
2021-01-16 | 16:02 | 50.116
2021-01-16 | 16:02 | 50.116
2021-01-16 | 16:02 | 50.116
2021-01-16 | 16:02 | 50.116
2021-01-16 | 16:02 | 50.116
2021-01-16 | 16:02 | 50.117
2021-01-16 | 16:02 | 50.119
2021-01-16 | 16:02 | 50.119
2021-01-16 | 16:02 | 50.12
2021-01-16 | 16:02 | 50.121
2021-01-16 | 16:02 | 50.121
2021-01-16 | 16:02 | 50.122
2021-01-16 | 16:02 | 50.126
2021-01-16 | 16:02 | 50.13
2021-01-16 | 16:02 | 50.133
2021-01-16 | 16:02 | 50.134
2021-01-16 | 16:02 | 50.135
2021-01-16 | 16:02 | 50.134
2021-01-16 | 16:02 | 50.132
2021-01-16 | 16:02 | 50.131
2021-01-16 | 16:02 | 50.128
2021-01-16 | 16:02 | 50.126
2021-01-16 | 16:02 | 50.127
2021-01-16 | 16:02 | 50.126
2021-01-16 | 16:02 | 50.126
2021-01-16 | 16:02 | 50.127
2021-01-16 | 16:02 | 50.126
2021-01-16 | 16:02 | 50.126
2021-01-16 | 16:02 | 50.125
2021-01-16 | 16:02 | 50.126
2021-01-16 | 16:02 | 50.129
2021-01-16 | 16:02 | 50.129
2021-01-16 | 16:02 | 50.129
2021-01-16 | 16:02 | 50.13
2021-01-16 | 16:02 | 50.129
2021-01-16 | 16:02 | 50.129
2021-01-16 | 16:02 | 50.126
2021-01-16 | 16:02 | 50.126
2021-01-16 | 16:02 | 50.126
2021-01-16 | 16:02 | 50.128
2021-01-16 | 16:02 | 50.129
2021-01-16 | 16:02 | 50.132
2021-01-16 | 16:02 | 50.136
2021-01-16 | 16:02 | 50.138
2021-01-16 | 16:02 | 50.141
2021-01-16 | 16:02 | 50.146
2021-01-16 | 16:02 | 50.149
2021-01-16 | 16:02 | 50.149
2021-01-16 | 16:02 | 50.15
2021-01-16 | 16:02 | 50.15
2021-01-16 | 16:02 | 50.149
2021-01-16 | 16:02 | 50.148
2021-01-16 | 16:02 | 50.146
2021-01-16 | 16:02 | 50.144
2021-01-16 | 16:02 | 50.144
2021-01-16 | 16:02 | 50.143
2021-01-16 | 16:02 | 50.141
2021-01-16 | 16:02 | 50.14
2021-01-16 | 16:02 | 50.141
2021-01-16 | 16:02 | 50.138
2021-01-16 | 16:03 | 50.139
2021-01-16 | 16:03 | 50.139
2021-01-16 | 16:03 | 50.139
2021-01-16 | 16:03 | 50.139
2021-01-16 | 16:03 | 50.137
2021-01-16 | 16:03 | 50.136
2021-01-16 | 16:03 | 50.133
2021-01-16 | 16:03 | 50.134
2021-01-16 | 16:03 | 50.133
2021-01-16 | 16:03 | 50.134
2021-01-16 | 16:03 | 50.135
2021-01-16 | 16:03 | 50.136
2021-01-16 | 16:03 | 50.138
2021-01-16 | 16:03 | 50.139
2021-01-16 | 16:03 | 50.142
2021-01-16 | 16:03 | 50.143
2021-01-16 | 16:03 | 50.144
2021-01-16 | 16:03 | 50.146
2021-01-16 | 16:03 | 50.15
2021-01-16 | 16:03 | 50.153
2021-01-16 | 16:03 | 50.155
2021-01-16 | 16:03 | 50.155
2021-01-16 | 16:03 | 50.152
2021-01-16 | 16:03 | 50.149
2021-01-16 | 16:03 | 50.146
2021-01-16 | 16:03 | 50.14
2021-01-16 | 16:03 | 50.132
2021-01-16 | 16:03 | 50.123
2021-01-16 | 16:03 | 50.114
2021-01-16 | 16:03 | 50.108
2021-01-16 | 16:03 | 50.102
2021-01-16 | 16:03 | 50.098
2021-01-16 | 16:03 | 50.098
2021-01-16 | 16:03 | 50.099
2021-01-16 | 16:03 | 50.098
2021-01-16 | 16:03 | 50.1
2021-01-16 | 16:03 | 50.102
2021-01-16 | 16:03 | 50.106
2021-01-16 | 16:03 | 50.11
2021-01-16 | 16:03 | 50.113
2021-01-16 | 16:03 | 50.115
2021-01-16 | 16:03 | 50.118
2021-01-16 | 16:03 | 50.12
2021-01-16 | 16:03 | 50.122
2021-01-16 | 16:03 | 50.125
2021-01-16 | 16:03 | 50.128
2021-01-16 | 16:03 | 50.128
2021-01-16 | 16:03 | 50.126
2021-01-16 | 16:03 | 50.126
2021-01-16 | 16:03 | 50.126
2021-01-16 | 16:03 | 50.122
2021-01-16 | 16:03 | 50.116
2021-01-16 | 16:03 | 50.112
2021-01-16 | 16:03 | 50.109
2021-01-16 | 16:03 | 50.107
2021-01-16 | 16:03 | 50.104
2021-01-16 | 16:03 | 50.103
2021-01-16 | 16:03 | 50.101
2021-01-16 | 16:03 | 50.099
2021-01-16 | 16:04 | 50.097
2021-01-16 | 16:04 | 50.096
2021-01-16 | 16:04 | 50.094
2021-01-16 | 16:04 | 50.091
2021-01-16 | 16:04 | 50.093
2021-01-16 | 16:04 | 50.093
2021-01-16 | 16:04 | 50.091
2021-01-16 | 16:04 | 50.091
2021-01-16 | 16:04 | 50.092
2021-01-16 | 16:04 | 50.093
2021-01-16 | 16:04 | 50.094
2021-01-16 | 16:04 | 50.096
2021-01-16 | 16:04 | 50.096
2021-01-16 | 16:04 | 50.096
2021-01-16 | 16:04 | 50.096
2021-01-16 | 16:04 | 50.096
2021-01-16 | 16:04 | 50.095
2021-01-16 | 16:04 | 50.094
2021-01-16 | 16:04 | 50.09
2021-01-16 | 16:04 | 50.09
2021-01-16 | 16:04 | 50.089
2021-01-16 | 16:04 | 50.089
2021-01-16 | 16:04 | 50.087
2021-01-16 | 16:04 | 50.084
2021-01-16 | 16:04 | 50.081
2021-01-16 | 16:04 | 50.079
2021-01-16 | 16:04 | 50.077
2021-01-16 | 16:04 | 50.077
2021-01-16 | 16:04 | 50.078
2021-01-16 | 16:04 | 50.078
2021-01-16 | 16:04 | 50.078
2021-01-16 | 16:04 | 50.079
2021-01-16 | 16:04 | 50.078
2021-01-16 | 16:04 | 50.078
2021-01-16 | 16:04 | 50.079
2021-01-16 | 16:04 | 50.08
2021-01-16 | 16:04 | 50.081
2021-01-16 | 16:04 | 50.083
2021-01-16 | 16:04 | 50.082
2021-01-16 | 16:04 | 50.086
2021-01-16 | 16:04 | 50.087
2021-01-16 | 16:04 | 50.087
2021-01-16 | 16:04 | 50.086
2021-01-16 | 16:04 | 50.088
2021-01-16 | 16:04 | 50.09
2021-01-16 | 16:04 | 50.092
2021-01-16 | 16:04 | 50.094
2021-01-16 | 16:04 | 50.094
2021-01-16 | 16:04 | 50.095
2021-01-16 | 16:04 | 50.095
2021-01-16 | 16:04 | 50.098
2021-01-16 | 16:04 | 50.1
2021-01-16 | 16:04 | 50.104
2021-01-16 | 16:04 | 50.107
2021-01-16 | 16:04 | 50.108
2021-01-16 | 16:04 | 50.108
2021-01-16 | 16:04 | 50.107
2021-01-16 | 16:04 | 50.107
2021-01-16 | 16:04 | 50.11
2021-01-16 | 16:04 | 50.112
2021-01-16 | 16:04 | 50.112
2021-01-16 | 16:05 | 50.112
2021-01-16 | 16:05 | 50.114
2021-01-16 | 16:05 | 50.117
2021-01-16 | 16:05 | 50.116
2021-01-16 | 16:05 | 50.12
2021-01-16 | 16:05 | 50.121
2021-01-16 | 16:05 | 50.121
2021-01-16 | 16:05 | 50.121
2021-01-16 | 16:05 | 50.123
2021-01-16 | 16:05 | 50.125
2021-01-16 | 16:05 | 50.129
2021-01-16 | 16:05 | 50.131
2021-01-16 | 16:05 | 50.134
2021-01-16 | 16:05 | 50.133
2021-01-16 | 16:05 | 50.131
2021-01-16 | 16:05 | 50.131
2021-01-16 | 16:05 | 50.131
2021-01-16 | 16:05 | 50.131
2021-01-16 | 16:05 | 50.127
2021-01-16 | 16:05 | 50.127
2021-01-16 | 16:05 | 50.126
2021-01-16 | 16:05 | 50.127
2021-01-16 | 16:05 | 50.125
2021-01-16 | 16:05 | 50.126
2021-01-16 | 16:05 | 50.127
2021-01-16 | 16:05 | 50.127
2021-01-16 | 16:05 | 50.13
2021-01-16 | 16:05 | 50.131
2021-01-16 | 16:05 | 50.131
2021-01-16 | 16:05 | 50.129
2021-01-16 | 16:05 | 50.127
2021-01-16 | 16:05 | 50.125
2021-01-16 | 16:05 | 50.126
2021-01-16 | 16:05 | 50.124
2021-01-16 | 16:05 | 50.122
2021-01-16 | 16:05 | 50.121
2021-01-16 | 16:05 | 50.122
2021-01-16 | 16:05 | 50.122
2021-01-16 | 16:05 | 50.124
2021-01-16 | 16:05 | 50.123
2021-01-16 | 16:05 | 50.123
2021-01-16 | 16:05 | 50.124
2021-01-16 | 16:05 | 50.125
2021-01-16 | 16:05 | 50.125
2021-01-16 | 16:05 | 50.124
2021-01-16 | 16:05 | 50.124
2021-01-16 | 16:05 | 50.126
2021-01-16 | 16:05 | 50.125
2021-01-16 | 16:05 | 50.125
2021-01-16 | 16:05 | 50.126
2021-01-16 | 16:05 | 50.126
2021-01-16 | 16:05 | 50.127
2021-01-16 | 16:05 | 50.129
2021-01-16 | 16:05 | 50.128
2021-01-16 | 16:05 | 50.129
2021-01-16 | 16:05 | 50.132
2021-01-16 | 16:05 | 50.133
2021-01-16 | 16:05 | 50.14
2021-01-16 | 16:05 | 50.145
2021-01-16 | 16:05 | 50.144
2021-01-16 | 16:06 | 50.14
2021-01-16 | 16:06 | 50.138
2021-01-16 | 16:06 | 50.137
2021-01-16 | 16:06 | 50.134
2021-01-16 | 16:06 | 50.133
2021-01-16 | 16:06 | 50.132
2021-01-16 | 16:06 | 50.13
2021-01-16 | 16:06 | 50.129
2021-01-16 | 16:06 | 50.129
2021-01-16 | 16:06 | 50.129
2021-01-16 | 16:06 | 50.129
2021-01-16 | 16:06 | 50.131
2021-01-16 | 16:06 | 50.133
2021-01-16 | 16:06 | 50.133
2021-01-16 | 16:06 | 50.131
2021-01-16 | 16:06 | 50.129
2021-01-16 | 16:06 | 50.127
2021-01-16 | 16:06 | 50.125
2021-01-16 | 16:06 | 50.123
2021-01-16 | 16:06 | 50.121
2021-01-16 | 16:06 | 50.119
2021-01-16 | 16:06 | 50.117
2021-01-16 | 16:06 | 50.117
2021-01-16 | 16:06 | 50.116
2021-01-16 | 16:06 | 50.115
2021-01-16 | 16:06 | 50.115
2021-01-16 | 16:06 | 50.117
2021-01-16 | 16:06 | 50.116
2021-01-16 | 16:06 | 50.117
2021-01-16 | 16:06 | 50.114
2021-01-16 | 16:06 | 50.112
2021-01-16 | 16:06 | 50.11
2021-01-16 | 16:06 | 50.109
2021-01-16 | 16:06 | 50.106
2021-01-16 | 16:06 | 50.107
2021-01-16 | 16:06 | 50.11
2021-01-16 | 16:06 | 50.108
2021-01-16 | 16:06 | 50.108
2021-01-16 | 16:06 | 50.109
2021-01-16 | 16:06 | 50.11
2021-01-16 | 16:06 | 50.109
2021-01-16 | 16:06 | 50.107
2021-01-16 | 16:06 | 50.103
2021-01-16 | 16:06 | 50.102
2021-01-16 | 16:06 | 50.101
2021-01-16 | 16:06 | 50.101
2021-01-16 | 16:06 | 50.098
2021-01-16 | 16:06 | 50.1
2021-01-16 | 16:06 | 50.099
2021-01-16 | 16:06 | 50.1
2021-01-16 | 16:06 | 50.098
2021-01-16 | 16:06 | 50.098
2021-01-16 | 16:06 | 50.101
2021-01-16 | 16:06 | 50.1
2021-01-16 | 16:06 | 50.1
2021-01-16 | 16:06 | 50.099
2021-01-16 | 16:06 | 50.098
2021-01-16 | 16:06 | 50.095
2021-01-16 | 16:06 | 50.096
2021-01-16 | 16:06 | 50.099
2021-01-16 | 16:07 | 50.102
2021-01-16 | 16:07 | 50.102
2021-01-16 | 16:07 | 50.102
2021-01-16 | 16:07 | 50.102
2021-01-16 | 16:07 | 50.102
2021-01-16 | 16:07 | 50.102
2021-01-16 | 16:07 | 50.101
2021-01-16 | 16:07 | 50.101
2021-01-16 | 16:07 | 50.098
2021-01-16 | 16:07 | 50.098
2021-01-16 | 16:07 | 50.095
2021-01-16 | 16:07 | 50.094
2021-01-16 | 16:07 | 50.093
2021-01-16 | 16:07 | 50.09
2021-01-16 | 16:07 | 50.088
2021-01-16 | 16:07 | 50.087
2021-01-16 | 16:07 | 50.084
2021-01-16 | 16:07 | 50.084
2021-01-16 | 16:07 | 50.085
2021-01-16 | 16:07 | 50.082
2021-01-16 | 16:07 | 50.082
2021-01-16 | 16:07 | 50.079
2021-01-16 | 16:07 | 50.079
2021-01-16 | 16:07 | 50.077
2021-01-16 | 16:07 | 50.076
2021-01-16 | 16:07 | 50.074
2021-01-16 | 16:07 | 50.072
2021-01-16 | 16:07 | 50.072
2021-01-16 | 16:07 | 50.071
2021-01-16 | 16:07 | 50.072
2021-01-16 | 16:07 | 50.067
2021-01-16 | 16:07 | 50.065
2021-01-16 | 16:07 | 50.063
2021-01-16 | 16:07 | 50.062
2021-01-16 | 16:07 | 50.065
2021-01-16 | 16:07 | 50.066
2021-01-16 | 16:07 | 50.068
2021-01-16 | 16:07 | 50.067
2021-01-16 | 16:07 | 50.068
2021-01-16 | 16:07 | 50.069
2021-01-16 | 16:07 | 50.066
2021-01-16 | 16:07 | 50.066
2021-01-16 | 16:07 | 50.068
2021-01-16 | 16:07 | 50.067
2021-01-16 | 16:07 | 50.064
2021-01-16 | 16:07 | 50.063
2021-01-16 | 16:07 | 50.062
2021-01-16 | 16:07 | 50.062
2021-01-16 | 16:07 | 50.063
2021-01-16 | 16:07 | 50.063
2021-01-16 | 16:07 | 50.063
2021-01-16 | 16:07 | 50.066
2021-01-16 | 16:07 | 50.066
2021-01-16 | 16:07 | 50.067
2021-01-16 | 16:07 | 50.067
2021-01-16 | 16:07 | 50.065
2021-01-16 | 16:07 | 50.067
2021-01-16 | 16:07 | 50.068
2021-01-16 | 16:07 | 50.068
2021-01-16 | 16:08 | 50.069
2021-01-16 | 16:08 | 50.069
2021-01-16 | 16:08 | 50.071
2021-01-16 | 16:08 | 50.07
2021-01-16 | 16:08 | 50.068
2021-01-16 | 16:08 | 50.067
2021-01-16 | 16:08 | 50.067
2021-01-16 | 16:08 | 50.068
2021-01-16 | 16:08 | 50.066
2021-01-16 | 16:08 | 50.067
2021-01-16 | 16:08 | 50.068
2021-01-16 | 16:08 | 50.066
2021-01-16 | 16:08 | 50.066
2021-01-16 | 16:08 | 50.062
2021-01-16 | 16:08 | 50.06
2021-01-16 | 16:08 | 50.06
2021-01-16 | 16:08 | 50.058
2021-01-16 | 16:08 | 50.06
2021-01-16 | 16:08 | 50.06
2021-01-16 | 16:08 | 50.058
2021-01-16 | 16:08 | 50.056
2021-01-16 | 16:08 | 50.057
2021-01-16 | 16:08 | 50.058
2021-01-16 | 16:08 | 50.056
2021-01-16 | 16:08 | 50.057
2021-01-16 | 16:08 | 50.056
2021-01-16 | 16:08 | 50.056
2021-01-16 | 16:08 | 50.057
2021-01-16 | 16:08 | 50.058
2021-01-16 | 16:08 | 50.06
2021-01-16 | 16:08 | 50.061
2021-01-16 | 16:08 | 50.058
2021-01-16 | 16:08 | 50.057
2021-01-16 | 16:08 | 50.056
2021-01-16 | 16:08 | 50.056
2021-01-16 | 16:08 | 50.056
2021-01-16 | 16:08 | 50.054
2021-01-16 | 16:08 | 50.053
2021-01-16 | 16:08 | 50.052
2021-01-16 | 16:08 | 50.051
2021-01-16 | 16:08 | 50.051
2021-01-16 | 16:08 | 50.049
2021-01-16 | 16:08 | 50.05
2021-01-16 | 16:08 | 50.051
2021-01-16 | 16:08 | 50.05
2021-01-16 | 16:08 | 50.049
2021-01-16 | 16:08 | 50.047
2021-01-16 | 16:08 | 50.046
2021-01-16 | 16:08 | 50.046
2021-01-16 | 16:08 | 50.044
2021-01-16 | 16:08 | 50.043
2021-01-16 | 16:08 | 50.042
2021-01-16 | 16:08 | 50.041
2021-01-16 | 16:08 | 50.039
2021-01-16 | 16:08 | 50.041
2021-01-16 | 16:08 | 50.041
2021-01-16 | 16:08 | 50.037
2021-01-16 | 16:08 | 50.036
2021-01-16 | 16:08 | 50.036
2021-01-16 | 16:08 | 50.035
2021-01-16 | 16:08 | 50.034
2021-01-16 | 16:09 | 50.033
2021-01-16 | 16:09 | 50.034
2021-01-16 | 16:09 | 50.03
2021-01-16 | 16:09 | 50.029
2021-01-16 | 16:09 | 50.028
2021-01-16 | 16:09 | 50.025
2021-01-16 | 16:09 | 50.021
2021-01-16 | 16:09 | 50.02
2021-01-16 | 16:09 | 50.018
2021-01-16 | 16:09 | 50.015
2021-01-16 | 16:09 | 50.012
2021-01-16 | 16:09 | 50.009
2021-01-16 | 16:09 | 50.006
2021-01-16 | 16:09 | 50.005
2021-01-16 | 16:09 | 50.004
2021-01-16 | 16:09 | 50.003
2021-01-16 | 16:09 | 50.002
2021-01-16 | 16:09 | 50.002
2021-01-16 | 16:09 | 50.002
2021-01-16 | 16:09 | 50.004
2021-01-16 | 16:09 | 50.004
2021-01-16 | 16:09 | 50.002
2021-01-16 | 16:09 | 50.002
2021-01-16 | 16:09 | 50.001
2021-01-16 | 16:09 | 49.999
2021-01-16 | 16:09 | 49.998
2021-01-16 | 16:09 | 49.995
2021-01-16 | 16:09 | 49.993
2021-01-16 | 16:09 | 49.99
2021-01-16 | 16:09 | 49.988
2021-01-16 | 16:09 | 49.983
2021-01-16 | 16:09 | 49.982
2021-01-16 | 16:09 | 49.981
2021-01-16 | 16:09 | 49.982
2021-01-16 | 16:09 | 49.981
2021-01-16 | 16:09 | 49.979
2021-01-16 | 16:09 | 49.976
2021-01-16 | 16:09 | 49.975
2021-01-16 | 16:09 | 49.974
2021-01-16 | 16:09 | 49.973
2021-01-16 | 16:09 | 49.972
2021-01-16 | 16:09 | 49.97
2021-01-16 | 16:09 | 49.97
2021-01-16 | 16:09 | 49.968
2021-01-16 | 16:09 | 49.965
2021-01-16 | 16:09 | 49.963
2021-01-16 | 16:09 | 49.961
2021-01-16 | 16:09 | 49.961
2021-01-16 | 16:09 | 49.96
2021-01-16 | 16:09 | 49.959
2021-01-16 | 16:09 | 49.954
2021-01-16 | 16:09 | 49.951
2021-01-16 | 16:09 | 49.946
2021-01-16 | 16:09 | 49.942
2021-01-16 | 16:09 | 49.94
2021-01-16 | 16:09 | 49.938
2021-01-16 | 16:09 | 49.938
2021-01-16 | 16:09 | 49.938
2021-01-16 | 16:09 | 49.94
2021-01-16 | 16:10 | 49.941
2021-01-16 | 16:10 | 49.942
2021-01-16 | 16:10 | 49.945
2021-01-16 | 16:10 | 49.946
2021-01-16 | 16:10 | 49.948
2021-01-16 | 16:10 | 49.946
2021-01-16 | 16:10 | 49.944
2021-01-16 | 16:10 | 49.943
2021-01-16 | 16:10 | 49.943
2021-01-16 | 16:10 | 49.943
2021-01-16 | 16:10 | 49.944
2021-01-16 | 16:10 | 49.944
2021-01-16 | 16:10 | 49.943
2021-01-16 | 16:10 | 49.943
2021-01-16 | 16:10 | 49.944
2021-01-16 | 16:10 | 49.944
2021-01-16 | 16:10 | 49.946
2021-01-16 | 16:10 | 49.949
2021-01-16 | 16:10 | 49.952
2021-01-16 | 16:10 | 49.953
2021-01-16 | 16:10 | 49.951
2021-01-16 | 16:10 | 49.95
2021-01-16 | 16:10 | 49.949
2021-01-16 | 16:10 | 49.949
2021-01-16 | 16:10 | 49.947
2021-01-16 | 16:10 | 49.945
2021-01-16 | 16:10 | 49.944
2021-01-16 | 16:10 | 49.942
2021-01-16 | 16:10 | 49.94
2021-01-16 | 16:10 | 49.939
2021-01-16 | 16:10 | 49.94
2021-01-16 | 16:10 | 49.94
2021-01-16 | 16:10 | 49.94
2021-01-16 | 16:10 | 49.939
2021-01-16 | 16:10 | 49.938
2021-01-16 | 16:10 | 49.937
2021-01-16 | 16:10 | 49.936
2021-01-16 | 16:10 | 49.935
2021-01-16 | 16:10 | 49.932
2021-01-16 | 16:10 | 49.929
2021-01-16 | 16:10 | 49.927
2021-01-16 | 16:10 | 49.926
2021-01-16 | 16:10 | 49.925
2021-01-16 | 16:10 | 49.925
2021-01-16 | 16:10 | 49.926
2021-01-16 | 16:10 | 49.926
2021-01-16 | 16:10 | 49.927
2021-01-16 | 16:10 | 49.928
2021-01-16 | 16:10 | 49.929
2021-01-16 | 16:10 | 49.929
2021-01-16 | 16:10 | 49.928
2021-01-16 | 16:10 | 49.926
2021-01-16 | 16:10 | 49.923
2021-01-16 | 16:10 | 49.921
2021-01-16 | 16:10 | 49.92
2021-01-16 | 16:10 | 49.918
2021-01-16 | 16:10 | 49.918
2021-01-16 | 16:10 | 49.917
2021-01-16 | 16:10 | 49.918
2021-01-16 | 16:10 | 49.918
2021-01-16 | 16:10 | 49.92
2021-01-16 | 16:11 | 49.921
2021-01-16 | 16:11 | 49.921
2021-01-16 | 16:11 | 49.921
2021-01-16 | 16:11 | 49.92
2021-01-16 | 16:11 | 49.92
2021-01-16 | 16:11 | 49.917
2021-01-16 | 16:11 | 49.917
2021-01-16 | 16:11 | 49.915
2021-01-16 | 16:11 | 49.914
2021-01-16 | 16:11 | 49.911
2021-01-16 | 16:11 | 49.91
2021-01-16 | 16:11 | 49.909
2021-01-16 | 16:11 | 49.907
2021-01-16 | 16:11 | 49.905
2021-01-16 | 16:11 | 49.905
2021-01-16 | 16:11 | 49.907
2021-01-16 | 16:11 | 49.909
2021-01-16 | 16:11 | 49.909
2021-01-16 | 16:11 | 49.91
2021-01-16 | 16:11 | 49.91
2021-01-16 | 16:11 | 49.911
2021-01-16 | 16:11 | 49.911
2021-01-16 | 16:11 | 49.911
2021-01-16 | 16:11 | 49.911
2021-01-16 | 16:11 | 49.909
2021-01-16 | 16:11 | 49.906
2021-01-16 | 16:11 | 49.902
2021-01-16 | 16:11 | 49.898
2021-01-16 | 16:11 | 49.894
2021-01-16 | 16:11 | 49.891
2021-01-16 | 16:11 | 49.888
2021-01-16 | 16:11 | 49.887
2021-01-16 | 16:11 | 49.887
2021-01-16 | 16:11 | 49.885
2021-01-16 | 16:11 | 49.883
2021-01-16 | 16:11 | 49.881
2021-01-16 | 16:11 | 49.88
2021-01-16 | 16:11 | 49.88
2021-01-16 | 16:11 | 49.881
2021-01-16 | 16:11 | 49.881
2021-01-16 | 16:11 | 49.881
2021-01-16 | 16:11 | 49.879
2021-01-16 | 16:11 | 49.879
2021-01-16 | 16:11 | 49.879
2021-01-16 | 16:11 | 49.879
2021-01-16 | 16:11 | 49.879
2021-01-16 | 16:11 | 49.878
2021-01-16 | 16:11 | 49.876
2021-01-16 | 16:11 | 49.877
2021-01-16 | 16:11 | 49.879
2021-01-16 | 16:11 | 49.881
2021-01-16 | 16:11 | 49.882
2021-01-16 | 16:11 | 49.886
2021-01-16 | 16:11 | 49.887
2021-01-16 | 16:11 | 49.887
2021-01-16 | 16:11 | 49.886
2021-01-16 | 16:11 | 49.885
2021-01-16 | 16:11 | 49.884
2021-01-16 | 16:11 | 49.884
2021-01-16 | 16:12 | 49.885
2021-01-16 | 16:12 | 49.883
2021-01-16 | 16:12 | 49.883
2021-01-16 | 16:12 | 49.881
2021-01-16 | 16:12 | 49.881
2021-01-16 | 16:12 | 49.878
2021-01-16 | 16:12 | 49.875
2021-01-16 | 16:12 | 49.873
2021-01-16 | 16:12 | 49.872
2021-01-16 | 16:12 | 49.872
2021-01-16 | 16:12 | 49.873
2021-01-16 | 16:12 | 49.873
2021-01-16 | 16:12 | 49.876
2021-01-16 | 16:12 | 49.878
2021-01-16 | 16:12 | 49.88
2021-01-16 | 16:12 | 49.882
2021-01-16 | 16:12 | 49.884
2021-01-16 | 16:12 | 49.884
2021-01-16 | 16:12 | 49.883
2021-01-16 | 16:12 | 49.882
2021-01-16 | 16:12 | 49.879
2021-01-16 | 16:12 | 49.876
2021-01-16 | 16:12 | 49.874
2021-01-16 | 16:12 | 49.873
2021-01-16 | 16:12 | 49.871
2021-01-16 | 16:12 | 49.871
2021-01-16 | 16:12 | 49.869
2021-01-16 | 16:12 | 49.868
2021-01-16 | 16:12 | 49.869
2021-01-16 | 16:12 | 49.87
2021-01-16 | 16:12 | 49.872
2021-01-16 | 16:12 | 49.873
2021-01-16 | 16:12 | 49.873
2021-01-16 | 16:12 | 49.874
2021-01-16 | 16:12 | 49.874
2021-01-16 | 16:12 | 49.874
2021-01-16 | 16:12 | 49.875
2021-01-16 | 16:12 | 49.873
2021-01-16 | 16:12 | 49.869
2021-01-16 | 16:12 | 49.867
2021-01-16 | 16:12 | 49.864
2021-01-16 | 16:12 | 49.859
2021-01-16 | 16:12 | 49.855
2021-01-16 | 16:12 | 49.854
2021-01-16 | 16:12 | 49.852
2021-01-16 | 16:12 | 49.851
2021-01-16 | 16:12 | 49.852
2021-01-16 | 16:12 | 49.851
2021-01-16 | 16:12 | 49.85
2021-01-16 | 16:12 | 49.848
2021-01-16 | 16:12 | 49.847
2021-01-16 | 16:12 | 49.845
2021-01-16 | 16:12 | 49.845
2021-01-16 | 16:12 | 49.844
2021-01-16 | 16:12 | 49.843
2021-01-16 | 16:12 | 49.842
2021-01-16 | 16:12 | 49.841
2021-01-16 | 16:12 | 49.84
2021-01-16 | 16:12 | 49.842
2021-01-16 | 16:12 | 49.842
2021-01-16 | 16:12 | 49.844
2021-01-16 | 16:13 | 49.843
2021-01-16 | 16:13 | 49.841
2021-01-16 | 16:13 | 49.839
2021-01-16 | 16:13 | 49.84
2021-01-16 | 16:13 | 49.841
2021-01-16 | 16:13 | 49.841
2021-01-16 | 16:13 | 49.838
2021-01-16 | 16:13 | 49.837
2021-01-16 | 16:13 | 49.833
2021-01-16 | 16:13 | 49.83
2021-01-16 | 16:13 | 49.827
2021-01-16 | 16:13 | 49.827
2021-01-16 | 16:13 | 49.826
2021-01-16 | 16:13 | 49.826
2021-01-16 | 16:13 | 49.829
2021-01-16 | 16:13 | 49.83
2021-01-16 | 16:13 | 49.832
2021-01-16 | 16:13 | 49.836
2021-01-16 | 16:13 | 49.837
2021-01-16 | 16:13 | 49.838
2021-01-16 | 16:13 | 49.836
2021-01-16 | 16:13 | 49.836
2021-01-16 | 16:13 | 49.836
2021-01-16 | 16:13 | 49.837
2021-01-16 | 16:13 | 49.837
2021-01-16 | 16:13 | 49.838
2021-01-16 | 16:13 | 49.839
2021-01-16 | 16:13 | 49.841
2021-01-16 | 16:13 | 49.844
2021-01-16 | 16:13 | 49.843
2021-01-16 | 16:13 | 49.842
2021-01-16 | 16:13 | 49.843
2021-01-16 | 16:13 | 49.844
2021-01-16 | 16:13 | 49.844
2021-01-16 | 16:13 | 49.844
2021-01-16 | 16:13 | 49.847
2021-01-16 | 16:13 | 49.85
2021-01-16 | 16:13 | 49.854
2021-01-16 | 16:13 | 49.86
2021-01-16 | 16:13 | 49.863
2021-01-16 | 16:13 | 49.868
2021-01-16 | 16:13 | 49.872
2021-01-16 | 16:13 | 49.874
2021-01-16 | 16:13 | 49.878
2021-01-16 | 16:13 | 49.877
2021-01-16 | 16:13 | 49.877
2021-01-16 | 16:13 | 49.877
2021-01-16 | 16:13 | 49.877
2021-01-16 | 16:13 | 49.876
2021-01-16 | 16:13 | 49.874
2021-01-16 | 16:13 | 49.869
2021-01-16 | 16:13 | 49.866
2021-01-16 | 16:13 | 49.863
2021-01-16 | 16:13 | 49.861
2021-01-16 | 16:13 | 49.861
2021-01-16 | 16:13 | 49.861
2021-01-16 | 16:13 | 49.859
2021-01-16 | 16:13 | 49.856
2021-01-16 | 16:13 | 49.853
2021-01-16 | 16:14 | 49.85
2021-01-16 | 16:14 | 49.849
2021-01-16 | 16:14 | 49.849
2021-01-16 | 16:14 | 49.85
2021-01-16 | 16:14 | 49.847
2021-01-16 | 16:14 | 49.847
2021-01-16 | 16:14 | 49.846
2021-01-16 | 16:14 | 49.846
2021-01-16 | 16:14 | 49.848
2021-01-16 | 16:14 | 49.85
2021-01-16 | 16:14 | 49.851
2021-01-16 | 16:14 | 49.852
2021-01-16 | 16:14 | 49.855
2021-01-16 | 16:14 | 49.858
2021-01-16 | 16:14 | 49.861
2021-01-16 | 16:14 | 49.863
2021-01-16 | 16:14 | 49.865
2021-01-16 | 16:14 | 49.866
2021-01-16 | 16:14 | 49.87
2021-01-16 | 16:14 | 49.872
2021-01-16 | 16:14 | 49.877
2021-01-16 | 16:14 | 49.88
2021-01-16 | 16:14 | 49.884
2021-01-16 | 16:14 | 49.889
2021-01-16 | 16:14 | 49.893
2021-01-16 | 16:14 | 49.896
2021-01-16 | 16:14 | 49.9
2021-01-16 | 16:14 | 49.901
2021-01-16 | 16:14 | 49.901
2021-01-16 | 16:14 | 49.9
2021-01-16 | 16:14 | 49.9
2021-01-16 | 16:14 | 49.9
2021-01-16 | 16:14 | 49.898
2021-01-16 | 16:14 | 49.894
2021-01-16 | 16:14 | 49.889
2021-01-16 | 16:14 | 49.885
2021-01-16 | 16:14 | 49.883
2021-01-16 | 16:14 | 49.882
2021-01-16 | 16:14 | 49.88
2021-01-16 | 16:14 | 49.878
2021-01-16 | 16:14 | 49.876
2021-01-16 | 16:14 | 49.872
2021-01-16 | 16:14 | 49.871
2021-01-16 | 16:14 | 49.871
2021-01-16 | 16:14 | 49.874
2021-01-16 | 16:14 | 49.876
2021-01-16 | 16:14 | 49.877
2021-01-16 | 16:14 | 49.881
2021-01-16 | 16:14 | 49.883
2021-01-16 | 16:14 | 49.886
2021-01-16 | 16:14 | 49.89
2021-01-16 | 16:14 | 49.893
2021-01-16 | 16:14 | 49.897
2021-01-16 | 16:14 | 49.9
2021-01-16 | 16:14 | 49.903
2021-01-16 | 16:14 | 49.904
2021-01-16 | 16:14 | 49.904
2021-01-16 | 16:14 | 49.903
2021-01-16 | 16:14 | 49.903
2021-01-16 | 16:14 | 49.902
2021-01-16 | 16:14 | 49.9
2021-01-16 | 16:15 | 49.898
2021-01-16 | 16:15 | 49.897
2021-01-16 | 16:15 | 49.897
2021-01-16 | 16:15 | 49.898
2021-01-16 | 16:15 | 49.898
2021-01-16 | 16:15 | 49.899
2021-01-16 | 16:15 | 49.901
2021-01-16 | 16:15 | 49.903
2021-01-16 | 16:15 | 49.907
2021-01-16 | 16:15 | 49.909
2021-01-16 | 16:15 | 49.912
2021-01-16 | 16:15 | 49.914
2021-01-16 | 16:15 | 49.915
2021-01-16 | 16:15 | 49.916
2021-01-16 | 16:15 | 49.917
2021-01-16 | 16:15 | 49.918
2021-01-16 | 16:15 | 49.919
2021-01-16 | 16:15 | 49.92
2021-01-16 | 16:15 | 49.922
2021-01-16 | 16:15 | 49.923
2021-01-16 | 16:15 | 49.924
2021-01-16 | 16:15 | 49.926
2021-01-16 | 16:15 | 49.927
2021-01-16 | 16:15 | 49.929
2021-01-16 | 16:15 | 49.933
2021-01-16 | 16:15 | 49.936
2021-01-16 | 16:15 | 49.937
2021-01-16 | 16:15 | 49.938
2021-01-16 | 16:15 | 49.94
2021-01-16 | 16:15 | 49.941
2021-01-16 | 16:15 | 49.942
2021-01-16 | 16:15 | 49.943
2021-01-16 | 16:15 | 49.944
2021-01-16 | 16:15 | 49.947
2021-01-16 | 16:15 | 49.947
2021-01-16 | 16:15 | 49.949
2021-01-16 | 16:15 | 49.95
2021-01-16 | 16:15 | 49.95
2021-01-16 | 16:15 | 49.953
2021-01-16 | 16:15 | 49.949
2021-01-16 | 16:15 | 49.948
2021-01-16 | 16:15 | 49.946
2021-01-16 | 16:15 | 49.943
2021-01-16 | 16:15 | 49.943
2021-01-16 | 16:15 | 49.943
2021-01-16 | 16:15 | 49.944
2021-01-16 | 16:15 | 49.948
2021-01-16 | 16:15 | 49.951
2021-01-16 | 16:15 | 49.956
2021-01-16 | 16:15 | 49.96
2021-01-16 | 16:15 | 49.962
2021-01-16 | 16:15 | 49.962
2021-01-16 | 16:15 | 49.964
2021-01-16 | 16:15 | 49.965
2021-01-16 | 16:15 | 49.965
2021-01-16 | 16:15 | 49.964
2021-01-16 | 16:15 | 49.962
2021-01-16 | 16:15 | 49.962
2021-01-16 | 16:15 | 49.962
2021-01-16 | 16:16 | 49.964
2021-01-16 | 16:16 | 49.966
2021-01-16 | 16:16 | 49.969
2021-01-16 | 16:16 | 49.968
2021-01-16 | 16:16 | 49.968
2021-01-16 | 16:16 | 49.969
2021-01-16 | 16:16 | 49.968
2021-01-16 | 16:16 | 49.967
2021-01-16 | 16:16 | 49.97
2021-01-16 | 16:16 | 49.97
2021-01-16 | 16:16 | 49.969
2021-01-16 | 16:16 | 49.972
2021-01-16 | 16:16 | 49.971
2021-01-16 | 16:16 | 49.972
2021-01-16 | 16:16 | 49.971
2021-01-16 | 16:16 | 49.973
2021-01-16 | 16:16 | 49.972
2021-01-16 | 16:16 | 49.974
2021-01-16 | 16:16 | 49.974
2021-01-16 | 16:16 | 49.977
2021-01-16 | 16:16 | 49.978
2021-01-16 | 16:16 | 49.978
2021-01-16 | 16:16 | 49.98
2021-01-16 | 16:16 | 49.981
2021-01-16 | 16:16 | 49.982
2021-01-16 | 16:16 | 49.983
2021-01-16 | 16:16 | 49.982
2021-01-16 | 16:16 | 49.981
2021-01-16 | 16:16 | 49.98
2021-01-16 | 16:16 | 49.98
2021-01-16 | 16:16 | 49.978
2021-01-16 | 16:16 | 49.977
2021-01-16 | 16:16 | 49.975
2021-01-16 | 16:16 | 49.975
2021-01-16 | 16:16 | 49.973
2021-01-16 | 16:16 | 49.972
2021-01-16 | 16:16 | 49.974
2021-01-16 | 16:16 | 49.973
2021-01-16 | 16:16 | 49.973
2021-01-16 | 16:16 | 49.974
2021-01-16 | 16:16 | 49.975
2021-01-16 | 16:16 | 49.976
2021-01-16 | 16:16 | 49.976
2021-01-16 | 16:16 | 49.975
2021-01-16 | 16:16 | 49.976
2021-01-16 | 16:16 | 49.975
2021-01-16 | 16:16 | 49.974
2021-01-16 | 16:16 | 49.974
2021-01-16 | 16:16 | 49.973
2021-01-16 | 16:16 | 49.973
2021-01-16 | 16:16 | 49.972
2021-01-16 | 16:16 | 49.973
2021-01-16 | 16:16 | 49.972
2021-01-16 | 16:16 | 49.972
2021-01-16 | 16:16 | 49.97
2021-01-16 | 16:16 | 49.971
2021-01-16 | 16:16 | 49.973
2021-01-16 | 16:16 | 49.975
2021-01-16 | 16:16 | 49.976
2021-01-16 | 16:16 | 49.977
2021-01-16 | 16:16 | 49.981
2021-01-16 | 16:17 | 49.984
2021-01-16 | 16:17 | 49.988
2021-01-16 | 16:17 | 49.992
2021-01-16 | 16:17 | 49.998
2021-01-16 | 16:17 | 50.003
2021-01-16 | 16:17 | 50.008
2021-01-16 | 16:17 | 50.013
2021-01-16 | 16:17 | 50.016
2021-01-16 | 16:17 | 50.018
2021-01-16 | 16:17 | 50.02
2021-01-16 | 16:17 | 50.022
2021-01-16 | 16:17 | 50.023
2021-01-16 | 16:17 | 50.026
2021-01-16 | 16:17 | 50.027
2021-01-16 | 16:17 | 50.028
2021-01-16 | 16:17 | 50.028
2021-01-16 | 16:17 | 50.03
2021-01-16 | 16:17 | 50.031
2021-01-16 | 16:17 | 50.032
2021-01-16 | 16:17 | 50.035
2021-01-16 | 16:17 | 50.036
2021-01-16 | 16:17 | 50.038
2021-01-16 | 16:17 | 50.036
2021-01-16 | 16:17 | 50.037
2021-01-16 | 16:17 | 50.036
2021-01-16 | 16:17 | 50.036
2021-01-16 | 16:17 | 50.037
2021-01-16 | 16:17 | 50.04
2021-01-16 | 16:17 | 50.04
2021-01-16 | 16:17 | 50.043
2021-01-16 | 16:17 | 50.042
2021-01-16 | 16:17 | 50.042
2021-01-16 | 16:17 | 50.04
2021-01-16 | 16:17 | 50.039
2021-01-16 | 16:17 | 50.036
2021-01-16 | 16:17 | 50.034
2021-01-16 | 16:17 | 50.029
2021-01-16 | 16:17 | 50.025
2021-01-16 | 16:17 | 50.021
2021-01-16 | 16:17 | 50.019
2021-01-16 | 16:17 | 50.018
2021-01-16 | 16:17 | 50.017
2021-01-16 | 16:17 | 50.02
2021-01-16 | 16:17 | 50.023
2021-01-16 | 16:17 | 50.025
2021-01-16 | 16:17 | 50.027
2021-01-16 | 16:17 | 50.029
2021-01-16 | 16:17 | 50.031
2021-01-16 | 16:17 | 50.033
2021-01-16 | 16:17 | 50.035
2021-01-16 | 16:17 | 50.034
2021-01-16 | 16:17 | 50.036
2021-01-16 | 16:17 | 50.035
2021-01-16 | 16:17 | 50.034
2021-01-16 | 16:17 | 50.032
2021-01-16 | 16:17 | 50.031
2021-01-16 | 16:17 | 50.031
2021-01-16 | 16:17 | 50.032
2021-01-16 | 16:17 | 50.032
2021-01-16 | 16:18 | 50.031
2021-01-16 | 16:18 | 50.03
2021-01-16 | 16:18 | 50.029
2021-01-16 | 16:18 | 50.03
2021-01-16 | 16:18 | 50.032
2021-01-16 | 16:18 | 50.031
2021-01-16 | 16:18 | 50.033
2021-01-16 | 16:18 | 50.033
2021-01-16 | 16:18 | 50.034
2021-01-16 | 16:18 | 50.036
2021-01-16 | 16:18 | 50.039
2021-01-16 | 16:18 | 50.038
2021-01-16 | 16:18 | 50.039
2021-01-16 | 16:18 | 50.04
2021-01-16 | 16:18 | 50.042
2021-01-16 | 16:18 | 50.043
2021-01-16 | 16:18 | 50.045
2021-01-16 | 16:18 | 50.046
2021-01-16 | 16:18 | 50.045
2021-01-16 | 16:18 | 50.044
2021-01-16 | 16:18 | 50.043
2021-01-16 | 16:18 | 50.044
2021-01-16 | 16:18 | 50.046
2021-01-16 | 16:18 | 50.044
2021-01-16 | 16:18 | 50.042
2021-01-16 | 16:18 | 50.043
2021-01-16 | 16:18 | 50.045
2021-01-16 | 16:18 | 50.046
2021-01-16 | 16:18 | 50.048
2021-01-16 | 16:18 | 50.051
2021-01-16 | 16:18 | 50.054
2021-01-16 | 16:18 | 50.059
2021-01-16 | 16:18 | 50.06
2021-01-16 | 16:18 | 50.062
2021-01-16 | 16:18 | 50.063
2021-01-16 | 16:18 | 50.062
2021-01-16 | 16:18 | 50.062
2021-01-16 | 16:18 | 50.06
2021-01-16 | 16:18 | 50.061
2021-01-16 | 16:18 | 50.061
2021-01-16 | 16:18 | 50.06
2021-01-16 | 16:18 | 50.058
2021-01-16 | 16:18 | 50.057
2021-01-16 | 16:18 | 50.055
2021-01-16 | 16:18 | 50.055
2021-01-16 | 16:18 | 50.053
2021-01-16 | 16:18 | 50.051
2021-01-16 | 16:18 | 50.05
2021-01-16 | 16:18 | 50.051
2021-01-16 | 16:18 | 50.048
2021-01-16 | 16:18 | 50.049
2021-01-16 | 16:18 | 50.051
2021-01-16 | 16:18 | 50.052
2021-01-16 | 16:18 | 50.056
2021-01-16 | 16:18 | 50.059
2021-01-16 | 16:18 | 50.061
2021-01-16 | 16:18 | 50.065
2021-01-16 | 16:18 | 50.067
2021-01-16 | 16:18 | 50.07
2021-01-16 | 16:18 | 50.071
2021-01-16 | 16:18 | 50.072
2021-01-16 | 16:19 | 50.073
2021-01-16 | 16:19 | 50.072
2021-01-16 | 16:19 | 50.069
2021-01-16 | 16:19 | 50.067
2021-01-16 | 16:19 | 50.065
2021-01-16 | 16:19 | 50.064
2021-01-16 | 16:19 | 50.064
2021-01-16 | 16:19 | 50.063
2021-01-16 | 16:19 | 50.063
2021-01-16 | 16:19 | 50.062
2021-01-16 | 16:19 | 50.06
2021-01-16 | 16:19 | 50.059
2021-01-16 | 16:19 | 50.06
2021-01-16 | 16:19 | 50.058
2021-01-16 | 16:19 | 50.056
2021-01-16 | 16:19 | 50.057
2021-01-16 | 16:19 | 50.055
2021-01-16 | 16:19 | 50.052
2021-01-16 | 16:19 | 50.05
2021-01-16 | 16:19 | 50.049
2021-01-16 | 16:19 | 50.05
2021-01-16 | 16:19 | 50.049
2021-01-16 | 16:19 | 50.048
2021-01-16 | 16:19 | 50.045
2021-01-16 | 16:19 | 50.04
2021-01-16 | 16:19 | 50.036
2021-01-16 | 16:19 | 50.031
2021-01-16 | 16:19 | 50.023
2021-01-16 | 16:19 | 50.016
2021-01-16 | 16:19 | 50.009
2021-01-16 | 16:19 | 50.001
2021-01-16 | 16:19 | 49.994
2021-01-16 | 16:19 | 49.991
2021-01-16 | 16:19 | 49.99
2021-01-16 | 16:19 | 49.988
2021-01-16 | 16:19 | 49.986
2021-01-16 | 16:19 | 49.985
2021-01-16 | 16:19 | 49.985
2021-01-16 | 16:19 | 49.983
2021-01-16 | 16:19 | 49.984
2021-01-16 | 16:19 | 49.984
2021-01-16 | 16:19 | 49.985
2021-01-16 | 16:19 | 49.986
2021-01-16 | 16:19 | 49.989
2021-01-16 | 16:19 | 49.991
2021-01-16 | 16:19 | 49.994
2021-01-16 | 16:19 | 49.995
2021-01-16 | 16:19 | 49.996
2021-01-16 | 16:19 | 49.995
2021-01-16 | 16:19 | 49.993
2021-01-16 | 16:19 | 49.991
2021-01-16 | 16:19 | 49.987
2021-01-16 | 16:19 | 49.984
2021-01-16 | 16:19 | 49.982
2021-01-16 | 16:19 | 49.98
2021-01-16 | 16:19 | 49.979
2021-01-16 | 16:19 | 49.977
2021-01-16 | 16:19 | 49.978
2021-01-16 | 16:19 | 49.978
2021-01-16 | 16:20 | 49.976
2021-01-16 | 16:20 | 49.973
2021-01-16 | 16:20 | 49.972
2021-01-16 | 16:20 | 49.971
2021-01-16 | 16:20 | 49.972
2021-01-16 | 16:20 | 49.975
2021-01-16 | 16:20 | 49.977
2021-01-16 | 16:20 | 49.979
2021-01-16 | 16:20 | 49.98
2021-01-16 | 16:20 | 49.983
2021-01-16 | 16:20 | 49.985
2021-01-16 | 16:20 | 49.986
2021-01-16 | 16:20 | 49.987
2021-01-16 | 16:20 | 49.989
2021-01-16 | 16:20 | 49.991
2021-01-16 | 16:20 | 49.992
2021-01-16 | 16:20 | 49.992
2021-01-16 | 16:20 | 49.994
2021-01-16 | 16:20 | 49.993
2021-01-16 | 16:20 | 49.992
2021-01-16 | 16:20 | 49.991
2021-01-16 | 16:20 | 49.991
2021-01-16 | 16:20 | 49.992
2021-01-16 | 16:20 | 49.993
2021-01-16 | 16:20 | 49.994
2021-01-16 | 16:20 | 49.996
2021-01-16 | 16:20 | 49.999
2021-01-16 | 16:20 | 50.003
2021-01-16 | 16:20 | 50.007
2021-01-16 | 16:20 | 50.008
2021-01-16 | 16:20 | 50.011
2021-01-16 | 16:20 | 50.014
2021-01-16 | 16:20 | 50.017
2021-01-16 | 16:20 | 50.02
2021-01-16 | 16:20 | 50.023
2021-01-16 | 16:20 | 50.027
2021-01-16 | 16:20 | 50.027
2021-01-16 | 16:20 | 50.027
2021-01-16 | 16:20 | 50.027
2021-01-16 | 16:20 | 50.026
2021-01-16 | 16:20 | 50.026
2021-01-16 | 16:20 | 50.026
2021-01-16 | 16:20 | 50.025
2021-01-16 | 16:20 | 50.024
2021-01-16 | 16:20 | 50.022
2021-01-16 | 16:20 | 50.021
2021-01-16 | 16:20 | 50.021
2021-01-16 | 16:20 | 50.018
2021-01-16 | 16:20 | 50.018
2021-01-16 | 16:20 | 50.017
2021-01-16 | 16:20 | 50.017
2021-01-16 | 16:20 | 50.02
2021-01-16 | 16:20 | 50.024
2021-01-16 | 16:20 | 50.03
2021-01-16 | 16:20 | 50.034
2021-01-16 | 16:20 | 50.035
2021-01-16 | 16:20 | 50.036
2021-01-16 | 16:20 | 50.037
2021-01-16 | 16:20 | 50.036
2021-01-16 | 16:20 | 50.035
2021-01-16 | 16:20 | 50.033
2021-01-16 | 16:21 | 50.03
2021-01-16 | 16:21 | 50.03
2021-01-16 | 16:21 | 50.031
2021-01-16 | 16:21 | 50.032
2021-01-16 | 16:21 | 50.032
2021-01-16 | 16:21 | 50.035
2021-01-16 | 16:21 | 50.036
2021-01-16 | 16:21 | 50.037
2021-01-16 | 16:21 | 50.039
2021-01-16 | 16:21 | 50.038
2021-01-16 | 16:21 | 50.038
2021-01-16 | 16:21 | 50.038
2021-01-16 | 16:21 | 50.037
2021-01-16 | 16:21 | 50.037
2021-01-16 | 16:21 | 50.036
2021-01-16 | 16:21 | 50.035
2021-01-16 | 16:21 | 50.032
2021-01-16 | 16:21 | 50.03
2021-01-16 | 16:21 | 50.029
2021-01-16 | 16:21 | 50.027
2021-01-16 | 16:21 | 50.023
2021-01-16 | 16:21 | 50.023
2021-01-16 | 16:21 | 50.022
2021-01-16 | 16:21 | 50.02
2021-01-16 | 16:21 | 50.018
2021-01-16 | 16:21 | 50.017
2021-01-16 | 16:21 | 50.018
2021-01-16 | 16:21 | 50.02
2021-01-16 | 16:21 | 50.023
2021-01-16 | 16:21 | 50.024
2021-01-16 | 16:21 | 50.024
2021-01-16 | 16:21 | 50.024
2021-01-16 | 16:21 | 50.023
2021-01-16 | 16:21 | 50.023
2021-01-16 | 16:21 | 50.025
2021-01-16 | 16:21 | 50.025
2021-01-16 | 16:21 | 50.027
2021-01-16 | 16:21 | 50.028
2021-01-16 | 16:21 | 50.028
2021-01-16 | 16:21 | 50.028
2021-01-16 | 16:21 | 50.025
2021-01-16 | 16:21 | 50.022
2021-01-16 | 16:21 | 50.017
2021-01-16 | 16:21 | 50.015
2021-01-16 | 16:21 | 50.01
2021-01-16 | 16:21 | 50.008
2021-01-16 | 16:21 | 50.007
2021-01-16 | 16:21 | 50.006
2021-01-16 | 16:21 | 50.004
2021-01-16 | 16:21 | 50.003
2021-01-16 | 16:21 | 50.001
2021-01-16 | 16:21 | 50.001
2021-01-16 | 16:21 | 50.002
2021-01-16 | 16:21 | 50.004
2021-01-16 | 16:21 | 50.007
2021-01-16 | 16:21 | 50.01
2021-01-16 | 16:21 | 50.015
2021-01-16 | 16:21 | 50.018
2021-01-16 | 16:21 | 50.023
2021-01-16 | 16:22 | 50.027
2021-01-16 | 16:22 | 50.029
2021-01-16 | 16:22 | 50.03
2021-01-16 | 16:22 | 50.032
2021-01-16 | 16:22 | 50.033
2021-01-16 | 16:22 | 50.036
2021-01-16 | 16:22 | 50.035
2021-01-16 | 16:22 | 50.038
2021-01-16 | 16:22 | 50.038
2021-01-16 | 16:22 | 50.039
2021-01-16 | 16:22 | 50.04
2021-01-16 | 16:22 | 50.039
2021-01-16 | 16:22 | 50.04
2021-01-16 | 16:22 | 50.04
2021-01-16 | 16:22 | 50.039
2021-01-16 | 16:22 | 50.039
2021-01-16 | 16:22 | 50.039
2021-01-16 | 16:22 | 50.036
2021-01-16 | 16:22 | 50.037
2021-01-16 | 16:22 | 50.038
2021-01-16 | 16:22 | 50.04
2021-01-16 | 16:22 | 50.042
2021-01-16 | 16:22 | 50.043
2021-01-16 | 16:22 | 50.046
2021-01-16 | 16:22 | 50.048
2021-01-16 | 16:22 | 50.05
2021-01-16 | 16:22 | 50.052
2021-01-16 | 16:22 | 50.054
2021-01-16 | 16:22 | 50.053
2021-01-16 | 16:22 | 50.053
2021-01-16 | 16:22 | 50.051
2021-01-16 | 16:22 | 50.053
2021-01-16 | 16:22 | 50.054
2021-01-16 | 16:22 | 50.053
2021-01-16 | 16:22 | 50.052
2021-01-16 | 16:22 | 50.052
2021-01-16 | 16:22 | 50.049
2021-01-16 | 16:22 | 50.047
2021-01-16 | 16:22 | 50.044
2021-01-16 | 16:22 | 50.04
2021-01-16 | 16:22 | 50.036
2021-01-16 | 16:22 | 50.034
2021-01-16 | 16:22 | 50.032
2021-01-16 | 16:22 | 50.029
2021-01-16 | 16:22 | 50.029
2021-01-16 | 16:22 | 50.03
2021-01-16 | 16:22 | 50.031
2021-01-16 | 16:22 | 50.033
2021-01-16 | 16:22 | 50.035
2021-01-16 | 16:22 | 50.035
2021-01-16 | 16:22 | 50.035
2021-01-16 | 16:22 | 50.035
2021-01-16 | 16:22 | 50.036
2021-01-16 | 16:22 | 50.035
2021-01-16 | 16:22 | 50.035
2021-01-16 | 16:22 | 50.033
2021-01-16 | 16:22 | 50.031
2021-01-16 | 16:22 | 50.03
2021-01-16 | 16:22 | 50.03
2021-01-16 | 16:22 | 50.029
2021-01-16 | 16:22 | 50.03
2021-01-16 | 16:23 | 50.029
2021-01-16 | 16:23 | 50.03
2021-01-16 | 16:23 | 50.028
2021-01-16 | 16:23 | 50.027
2021-01-16 | 16:23 | 50.027
2021-01-16 | 16:23 | 50.028
2021-01-16 | 16:23 | 50.026
2021-01-16 | 16:23 | 50.023
2021-01-16 | 16:23 | 50.023
2021-01-16 | 16:23 | 50.02
2021-01-16 | 16:23 | 50.019
2021-01-16 | 16:23 | 50.019
2021-01-16 | 16:23 | 50.019
2021-01-16 | 16:23 | 50.018
2021-01-16 | 16:23 | 50.017
2021-01-16 | 16:23 | 50.017
2021-01-16 | 16:23 | 50.018
2021-01-16 | 16:23 | 50.02
2021-01-16 | 16:23 | 50.021
2021-01-16 | 16:23 | 50.023
2021-01-16 | 16:23 | 50.024
2021-01-16 | 16:23 | 50.024
2021-01-16 | 16:23 | 50.026
2021-01-16 | 16:23 | 50.027
2021-01-16 | 16:23 | 50.029
2021-01-16 | 16:23 | 50.029
2021-01-16 | 16:23 | 50.03
2021-01-16 | 16:23 | 50.034
2021-01-16 | 16:23 | 50.038
2021-01-16 | 16:23 | 50.041
2021-01-16 | 16:23 | 50.042
2021-01-16 | 16:23 | 50.043
2021-01-16 | 16:23 | 50.044
2021-01-16 | 16:23 | 50.043
2021-01-16 | 16:23 | 50.042
2021-01-16 | 16:23 | 50.044
2021-01-16 | 16:23 | 50.043
2021-01-16 | 16:23 | 50.044
2021-01-16 | 16:23 | 50.044
2021-01-16 | 16:23 | 50.042
2021-01-16 | 16:23 | 50.042
2021-01-16 | 16:23 | 50.041
2021-01-16 | 16:23 | 50.043
2021-01-16 | 16:23 | 50.04
2021-01-16 | 16:23 | 50.04
2021-01-16 | 16:23 | 50.041
2021-01-16 | 16:23 | 50.042
2021-01-16 | 16:23 | 50.041
2021-01-16 | 16:23 | 50.042
2021-01-16 | 16:23 | 50.041
2021-01-16 | 16:23 | 50.041
2021-01-16 | 16:23 | 50.039
2021-01-16 | 16:23 | 50.039
2021-01-16 | 16:23 | 50.039
2021-01-16 | 16:23 | 50.036
2021-01-16 | 16:23 | 50.038
2021-01-16 | 16:23 | 50.037
2021-01-16 | 16:23 | 50.039
2021-01-16 | 16:23 | 50.042
2021-01-16 | 16:24 | 50.046
2021-01-16 | 16:24 | 50.048
2021-01-16 | 16:24 | 50.049
2021-01-16 | 16:24 | 50.05
2021-01-16 | 16:24 | 50.051
2021-01-16 | 16:24 | 50.05
2021-01-16 | 16:24 | 50.049
2021-01-16 | 16:24 | 50.05
2021-01-16 | 16:24 | 50.05
2021-01-16 | 16:24 | 50.048
2021-01-16 | 16:24 | 50.045
2021-01-16 | 16:24 | 50.043
2021-01-16 | 16:24 | 50.044
2021-01-16 | 16:24 | 50.046
2021-01-16 | 16:24 | 50.047
2021-01-16 | 16:24 | 50.049
2021-01-16 | 16:24 | 50.051
2021-01-16 | 16:24 | 50.054
2021-01-16 | 16:24 | 50.056
2021-01-16 | 16:24 | 50.061
2021-01-16 | 16:24 | 50.063
2021-01-16 | 16:24 | 50.063
2021-01-16 | 16:24 | 50.065
2021-01-16 | 16:24 | 50.066
2021-01-16 | 16:24 | 50.068
2021-01-16 | 16:24 | 50.068
2021-01-16 | 16:24 | 50.067
2021-01-16 | 16:24 | 50.066
2021-01-16 | 16:24 | 50.064
2021-01-16 | 16:24 | 50.065
2021-01-16 | 16:24 | 50.064
2021-01-16 | 16:24 | 50.064
2021-01-16 | 16:24 | 50.063
2021-01-16 | 16:24 | 50.062
2021-01-16 | 16:24 | 50.06
2021-01-16 | 16:24 | 50.059
2021-01-16 | 16:24 | 50.056
2021-01-16 | 16:24 | 50.055
2021-01-16 | 16:24 | 50.053
2021-01-16 | 16:24 | 50.05
2021-01-16 | 16:24 | 50.047
2021-01-16 | 16:24 | 50.045
2021-01-16 | 16:24 | 50.042
2021-01-16 | 16:24 | 50.043
2021-01-16 | 16:24 | 50.044
2021-01-16 | 16:24 | 50.047
2021-01-16 | 16:24 | 50.049
2021-01-16 | 16:24 | 50.052
2021-01-16 | 16:24 | 50.052
2021-01-16 | 16:24 | 50.054
2021-01-16 | 16:24 | 50.055
2021-01-16 | 16:24 | 50.056
2021-01-16 | 16:24 | 50.056
2021-01-16 | 16:24 | 50.055
2021-01-16 | 16:24 | 50.055
2021-01-16 | 16:24 | 50.054
2021-01-16 | 16:24 | 50.053
2021-01-16 | 16:24 | 50.053
2021-01-16 | 16:24 | 50.053
2021-01-16 | 16:24 | 50.053
2021-01-16 | 16:25 | 50.054
2021-01-16 | 16:25 | 50.053
2021-01-16 | 16:25 | 50.053
2021-01-16 | 16:25 | 50.054
2021-01-16 | 16:25 | 50.053
2021-01-16 | 16:25 | 50.052
2021-01-16 | 16:25 | 50.051
2021-01-16 | 16:25 | 50.05
2021-01-16 | 16:25 | 50.047
2021-01-16 | 16:25 | 50.045
2021-01-16 | 16:25 | 50.043
2021-01-16 | 16:25 | 50.041
2021-01-16 | 16:25 | 50.041
2021-01-16 | 16:25 | 50.04
2021-01-16 | 16:25 | 50.038
2021-01-16 | 16:25 | 50.037
2021-01-16 | 16:25 | 50.038
2021-01-16 | 16:25 | 50.039
2021-01-16 | 16:25 | 50.041
2021-01-16 | 16:25 | 50.043
2021-01-16 | 16:25 | 50.045
2021-01-16 | 16:25 | 50.046
2021-01-16 | 16:25 | 50.047
2021-01-16 | 16:25 | 50.051
2021-01-16 | 16:25 | 50.054
2021-01-16 | 16:25 | 50.056
2021-01-16 | 16:25 | 50.058
2021-01-16 | 16:25 | 50.062
2021-01-16 | 16:25 | 50.064
2021-01-16 | 16:25 | 50.065
2021-01-16 | 16:25 | 50.065
2021-01-16 | 16:25 | 50.063
2021-01-16 | 16:25 | 50.061
2021-01-16 | 16:25 | 50.061
2021-01-16 | 16:25 | 50.058
2021-01-16 | 16:25 | 50.06
2021-01-16 | 16:25 | 50.059
2021-01-16 | 16:25 | 50.058
2021-01-16 | 16:25 | 50.058
2021-01-16 | 16:25 | 50.056
2021-01-16 | 16:25 | 50.056
2021-01-16 | 16:25 | 50.055
2021-01-16 | 16:25 | 50.054
2021-01-16 | 16:25 | 50.052
2021-01-16 | 16:25 | 50.052
2021-01-16 | 16:25 | 50.053
2021-01-16 | 16:25 | 50.053
2021-01-16 | 16:25 | 50.051
2021-01-16 | 16:25 | 50.052
2021-01-16 | 16:25 | 50.052
2021-01-16 | 16:25 | 50.05
2021-01-16 | 16:25 | 50.05
2021-01-16 | 16:25 | 50.049
2021-01-16 | 16:25 | 50.048
2021-01-16 | 16:25 | 50.047
2021-01-16 | 16:25 | 50.044
2021-01-16 | 16:25 | 50.044
2021-01-16 | 16:25 | 50.044
2021-01-16 | 16:25 | 50.042
2021-01-16 | 16:25 | 50.041
2021-01-16 | 16:26 | 50.04
2021-01-16 | 16:26 | 50.037
2021-01-16 | 16:26 | 50.036
2021-01-16 | 16:26 | 50.034
2021-01-16 | 16:26 | 50.034
2021-01-16 | 16:26 | 50.031
2021-01-16 | 16:26 | 50.029
2021-01-16 | 16:26 | 50.026
2021-01-16 | 16:26 | 50.025
2021-01-16 | 16:26 | 50.026
2021-01-16 | 16:26 | 50.028
2021-01-16 | 16:26 | 50.03
2021-01-16 | 16:26 | 50.031
2021-01-16 | 16:26 | 50.033
2021-01-16 | 16:26 | 50.035
2021-01-16 | 16:26 | 50.036
2021-01-16 | 16:26 | 50.037
2021-01-16 | 16:26 | 50.037
2021-01-16 | 16:26 | 50.038
2021-01-16 | 16:26 | 50.039
2021-01-16 | 16:26 | 50.039
2021-01-16 | 16:26 | 50.039
2021-01-16 | 16:26 | 50.039
2021-01-16 | 16:26 | 50.039
2021-01-16 | 16:26 | 50.041
2021-01-16 | 16:26 | 50.042
2021-01-16 | 16:26 | 50.044
2021-01-16 | 16:26 | 50.044
2021-01-16 | 16:26 | 50.047
2021-01-16 | 16:26 | 50.05
2021-01-16 | 16:26 | 50.053
2021-01-16 | 16:26 | 50.055
2021-01-16 | 16:26 | 50.055
2021-01-16 | 16:26 | 50.055
2021-01-16 | 16:26 | 50.055
2021-01-16 | 16:26 | 50.054
2021-01-16 | 16:26 | 50.054
2021-01-16 | 16:26 | 50.052
2021-01-16 | 16:26 | 50.051
2021-01-16 | 16:26 | 50.049
2021-01-16 | 16:26 | 50.049
2021-01-16 | 16:26 | 50.048
2021-01-16 | 16:26 | 50.048
2021-01-16 | 16:26 | 50.046
2021-01-16 | 16:26 | 50.045
2021-01-16 | 16:26 | 50.046
2021-01-16 | 16:26 | 50.047
2021-01-16 | 16:26 | 50.048
2021-01-16 | 16:26 | 50.049
2021-01-16 | 16:26 | 50.05
2021-01-16 | 16:26 | 50.051
2021-01-16 | 16:26 | 50.052
2021-01-16 | 16:26 | 50.052
2021-01-16 | 16:26 | 50.052
2021-01-16 | 16:26 | 50.052
2021-01-16 | 16:26 | 50.05
2021-01-16 | 16:26 | 50.051
2021-01-16 | 16:26 | 50.051
2021-01-16 | 16:26 | 50.052
2021-01-16 | 16:26 | 50.051
2021-01-16 | 16:26 | 50.05
2021-01-16 | 16:27 | 50.05
2021-01-16 | 16:27 | 50.049
2021-01-16 | 16:27 | 50.048
2021-01-16 | 16:27 | 50.049
2021-01-16 | 16:27 | 50.052
2021-01-16 | 16:27 | 50.053
2021-01-16 | 16:27 | 50.052
2021-01-16 | 16:27 | 50.051
2021-01-16 | 16:27 | 50.053
2021-01-16 | 16:27 | 50.055
2021-01-16 | 16:27 | 50.055
2021-01-16 | 16:27 | 50.057
2021-01-16 | 16:27 | 50.054
2021-01-16 | 16:27 | 50.05
2021-01-16 | 16:27 | 50.045
2021-01-16 | 16:27 | 50.039
2021-01-16 | 16:27 | 50.034
2021-01-16 | 16:27 | 50.028
2021-01-16 | 16:27 | 50.024
2021-01-16 | 16:27 | 50.021
2021-01-16 | 16:27 | 50.018
2021-01-16 | 16:27 | 50.018
2021-01-16 | 16:27 | 50.017
2021-01-16 | 16:27 | 50.016
2021-01-16 | 16:27 | 50.016
2021-01-16 | 16:27 | 50.015
2021-01-16 | 16:27 | 50.014
2021-01-16 | 16:27 | 50.013
2021-01-16 | 16:27 | 50.015
2021-01-16 | 16:27 | 50.017
2021-01-16 | 16:27 | 50.018
2021-01-16 | 16:27 | 50.021
2021-01-16 | 16:27 | 50.023
2021-01-16 | 16:27 | 50.025
2021-01-16 | 16:27 | 50.025
2021-01-16 | 16:27 | 50.025
2021-01-16 | 16:27 | 50.025
2021-01-16 | 16:27 | 50.025
2021-01-16 | 16:27 | 50.025
2021-01-16 | 16:27 | 50.027
2021-01-16 | 16:27 | 50.029
2021-01-16 | 16:27 | 50.031
2021-01-16 | 16:27 | 50.033
2021-01-16 | 16:27 | 50.035
2021-01-16 | 16:27 | 50.037
2021-01-16 | 16:27 | 50.035
2021-01-16 | 16:27 | 50.035
2021-01-16 | 16:27 | 50.033
2021-01-16 | 16:27 | 50.029
2021-01-16 | 16:27 | 50.025
2021-01-16 | 16:27 | 50.02
2021-01-16 | 16:27 | 50.014
2021-01-16 | 16:27 | 50.01
2021-01-16 | 16:27 | 50.006
2021-01-16 | 16:27 | 50.001
2021-01-16 | 16:27 | 49.999
2021-01-16 | 16:27 | 49.995
2021-01-16 | 16:27 | 49.992
2021-01-16 | 16:27 | 49.988
2021-01-16 | 16:27 | 49.985
2021-01-16 | 16:28 | 49.983
2021-01-16 | 16:28 | 49.982
2021-01-16 | 16:28 | 49.983
2021-01-16 | 16:28 | 49.985
2021-01-16 | 16:28 | 49.987
2021-01-16 | 16:28 | 49.989
2021-01-16 | 16:28 | 49.992
2021-01-16 | 16:28 | 49.995
2021-01-16 | 16:28 | 50
2021-01-16 | 16:28 | 50.003
2021-01-16 | 16:28 | 50.006
2021-01-16 | 16:28 | 50.008
2021-01-16 | 16:28 | 50.009
2021-01-16 | 16:28 | 50.009
2021-01-16 | 16:28 | 50.011
2021-01-16 | 16:28 | 50.014
2021-01-16 | 16:28 | 50.017
2021-01-16 | 16:28 | 50.018
2021-01-16 | 16:28 | 50.019
2021-01-16 | 16:28 | 50.022
2021-01-16 | 16:28 | 50.025
2021-01-16 | 16:28 | 50.028
2021-01-16 | 16:28 | 50.029
2021-01-16 | 16:28 | 50.028
2021-01-16 | 16:28 | 50.028
2021-01-16 | 16:28 | 50.025
2021-01-16 | 16:28 | 50.022
2021-01-16 | 16:28 | 50.015
2021-01-16 | 16:28 | 50.012
2021-01-16 | 16:28 | 50.007
2021-01-16 | 16:28 | 50.003
2021-01-16 | 16:28 | 49.995
2021-01-16 | 16:28 | 49.989
2021-01-16 | 16:28 | 49.984
2021-01-16 | 16:28 | 49.981
2021-01-16 | 16:28 | 49.98
2021-01-16 | 16:28 | 49.978
2021-01-16 | 16:28 | 49.977
2021-01-16 | 16:28 | 49.978
2021-01-16 | 16:28 | 49.979
2021-01-16 | 16:28 | 49.981
2021-01-16 | 16:28 | 49.98
2021-01-16 | 16:28 | 49.981
2021-01-16 | 16:28 | 49.981
2021-01-16 | 16:28 | 49.979
2021-01-16 | 16:28 | 49.977
2021-01-16 | 16:28 | 49.975
2021-01-16 | 16:28 | 49.974
2021-01-16 | 16:28 | 49.973
2021-01-16 | 16:28 | 49.974
2021-01-16 | 16:28 | 49.975
2021-01-16 | 16:28 | 49.978
2021-01-16 | 16:28 | 49.98
2021-01-16 | 16:28 | 49.977
2021-01-16 | 16:28 | 49.974
2021-01-16 | 16:28 | 49.973
2021-01-16 | 16:28 | 49.97
2021-01-16 | 16:28 | 49.971
2021-01-16 | 16:28 | 49.972
2021-01-16 | 16:29 | 49.974
2021-01-16 | 16:29 | 49.973
2021-01-16 | 16:29 | 49.972
2021-01-16 | 16:29 | 49.971
2021-01-16 | 16:29 | 49.972
2021-01-16 | 16:29 | 49.974
2021-01-16 | 16:29 | 49.977
2021-01-16 | 16:29 | 49.979
2021-01-16 | 16:29 | 49.979
2021-01-16 | 16:29 | 49.979
2021-01-16 | 16:29 | 49.978
2021-01-16 | 16:29 | 49.976
2021-01-16 | 16:29 | 49.977
2021-01-16 | 16:29 | 49.978
2021-01-16 | 16:29 | 49.98
2021-01-16 | 16:29 | 49.979
2021-01-16 | 16:29 | 49.981
2021-01-16 | 16:29 | 49.981
2021-01-16 | 16:29 | 49.981
2021-01-16 | 16:29 | 49.981
2021-01-16 | 16:29 | 49.979
2021-01-16 | 16:29 | 49.977
2021-01-16 | 16:29 | 49.976
2021-01-16 | 16:29 | 49.975
2021-01-16 | 16:29 | 49.972
2021-01-16 | 16:29 | 49.971
2021-01-16 | 16:29 | 49.969
2021-01-16 | 16:29 | 49.969
2021-01-16 | 16:29 | 49.97
2021-01-16 | 16:29 | 49.97
2021-01-16 | 16:29 | 49.967
2021-01-16 | 16:29 | 49.964
2021-01-16 | 16:29 | 49.961
2021-01-16 | 16:29 | 49.958
2021-01-16 | 16:29 | 49.956
2021-01-16 | 16:29 | 49.952
2021-01-16 | 16:29 | 49.948
2021-01-16 | 16:29 | 49.945
2021-01-16 | 16:29 | 49.944
2021-01-16 | 16:29 | 49.94
2021-01-16 | 16:29 | 49.941
2021-01-16 | 16:29 | 49.943
2021-01-16 | 16:29 | 49.95
2021-01-16 | 16:29 | 49.957
2021-01-16 | 16:29 | 49.966
2021-01-16 | 16:29 | 49.975
2021-01-16 | 16:29 | 49.984
2021-01-16 | 16:29 | 49.993
2021-01-16 | 16:29 | 50.001
2021-01-16 | 16:29 | 50.012
2021-01-16 | 16:29 | 50.02
2021-01-16 | 16:29 | 50.027
2021-01-16 | 16:29 | 50.033
2021-01-16 | 16:29 | 50.04
2021-01-16 | 16:29 | 50.045
2021-01-16 | 16:29 | 50.048
2021-01-16 | 16:29 | 50.051
2021-01-16 | 16:29 | 50.053
2021-01-16 | 16:29 | 50.053
2021-01-16 | 16:29 | 50.055
2021-01-16 | 16:30 | 50.056
2021-01-16 | 16:30 | 50.059
2021-01-16 | 16:30 | 50.059
2021-01-16 | 16:30 | 50.061
2021-01-16 | 16:30 | 50.061
2021-01-16 | 16:30 | 50.061
2021-01-16 | 16:30 | 50.061
2021-01-16 | 16:30 | 50.061
2021-01-16 | 16:30 | 50.063
2021-01-16 | 16:30 | 50.062
2021-01-16 | 16:30 | 50.061
2021-01-16 | 16:30 | 50.061
2021-01-16 | 16:30 | 50.059
2021-01-16 | 16:30 | 50.06
2021-01-16 | 16:30 | 50.061
2021-01-16 | 16:30 | 50.06
2021-01-16 | 16:30 | 50.06
2021-01-16 | 16:30 | 50.058
2021-01-16 | 16:30 | 50.057
2021-01-16 | 16:30 | 50.057
2021-01-16 | 16:30 | 50.054
2021-01-16 | 16:30 | 50.053
2021-01-16 | 16:30 | 50.052
2021-01-16 | 16:30 | 50.052
2021-01-16 | 16:30 | 50.053
2021-01-16 | 16:30 | 50.05
2021-01-16 | 16:30 | 50.049
2021-01-16 | 16:30 | 50.047
2021-01-16 | 16:30 | 50.046
2021-01-16 | 16:30 | 50.045

## Event 20210123-1
In UTC
Date | Time | Freq
2021-01-23 | 11:57 | 50.054
2021-01-23 | 11:57 | 50.053
2021-01-23 | 11:57 | 50.053
2021-01-23 | 11:57 | 50.052
2021-01-23 | 11:57 | 50.053
2021-01-23 | 11:57 | 50.053
2021-01-23 | 11:57 | 50.056
2021-01-23 | 11:57 | 50.057
2021-01-23 | 11:57 | 50.059
2021-01-23 | 11:57 | 50.059
2021-01-23 | 11:57 | 50.057
2021-01-23 | 11:57 | 50.055
2021-01-23 | 11:57 | 50.054
2021-01-23 | 11:57 | 50.052
2021-01-23 | 11:57 | 50.051
2021-01-23 | 11:57 | 50.048
2021-01-23 | 11:57 | 50.049
2021-01-23 | 11:57 | 50.05
2021-01-23 | 11:57 | 50.052
2021-01-23 | 11:57 | 50.054
2021-01-23 | 11:57 | 50.055
2021-01-23 | 11:57 | 50.055
2021-01-23 | 11:57 | 50.056
2021-01-23 | 11:57 | 50.055
2021-01-23 | 11:57 | 50.059
2021-01-23 | 11:57 | 50.057
2021-01-23 | 11:57 | 50.057
2021-01-23 | 11:57 | 50.059
2021-01-23 | 11:57 | 50.059
2021-01-23 | 11:57 | 50.06
2021-01-23 | 11:58 | 50.059
2021-01-23 | 11:58 | 50.057
2021-01-23 | 11:58 | 50.057
2021-01-23 | 11:58 | 50.056
2021-01-23 | 11:58 | 50.056
2021-01-23 | 11:58 | 50.055
2021-01-23 | 11:58 | 50.053
2021-01-23 | 11:58 | 50.052
2021-01-23 | 11:58 | 50.053
2021-01-23 | 11:58 | 50.054
2021-01-23 | 11:58 | 50.055
2021-01-23 | 11:58 | 50.055
2021-01-23 | 11:58 | 50.056
2021-01-23 | 11:58 | 50.055
2021-01-23 | 11:58 | 50.058
2021-01-23 | 11:58 | 50.059
2021-01-23 | 11:58 | 50.059
2021-01-23 | 11:58 | 50.057
2021-01-23 | 11:58 | 50.058
2021-01-23 | 11:58 | 50.058
2021-01-23 | 11:58 | 50.057
2021-01-23 | 11:58 | 50.058
2021-01-23 | 11:58 | 50.06
2021-01-23 | 11:58 | 50.06
2021-01-23 | 11:58 | 50.062
2021-01-23 | 11:58 | 50.063
2021-01-23 | 11:58 | 50.065
2021-01-23 | 11:58 | 50.064
2021-01-23 | 11:58 | 50.066
2021-01-23 | 11:58 | 50.065
2021-01-23 | 11:58 | 50.065
2021-01-23 | 11:58 | 50.064
2021-01-23 | 11:58 | 50.064
2021-01-23 | 11:58 | 50.066
2021-01-23 | 11:58 | 50.064
2021-01-23 | 11:58 | 50.065
2021-01-23 | 11:58 | 50.064
2021-01-23 | 11:58 | 50.064
2021-01-23 | 11:58 | 50.065
2021-01-23 | 11:58 | 50.066
2021-01-23 | 11:58 | 50.064
2021-01-23 | 11:58 | 50.064
2021-01-23 | 11:58 | 50.063
2021-01-23 | 11:58 | 50.062
2021-01-23 | 11:58 | 50.061
2021-01-23 | 11:58 | 50.061
2021-01-23 | 11:58 | 50.06
2021-01-23 | 11:58 | 50.058
2021-01-23 | 11:58 | 50.056
2021-01-23 | 11:58 | 50.053
2021-01-23 | 11:58 | 50.052
2021-01-23 | 11:58 | 50.05
2021-01-23 | 11:58 | 50.048
2021-01-23 | 11:58 | 50.047
2021-01-23 | 11:58 | 50.045
2021-01-23 | 11:58 | 50.042
2021-01-23 | 11:58 | 50.039
2021-01-23 | 11:58 | 50.038
2021-01-23 | 11:58 | 50.036
2021-01-23 | 11:58 | 50.033
2021-01-23 | 11:58 | 50.033
2021-01-23 | 11:59 | 50.032
2021-01-23 | 11:59 | 50.033
2021-01-23 | 11:59 | 50.03
2021-01-23 | 11:59 | 50.029
2021-01-23 | 11:59 | 50.027
2021-01-23 | 11:59 | 50.025
2021-01-23 | 11:59 | 50.025
2021-01-23 | 11:59 | 50.023
2021-01-23 | 11:59 | 50.021
2021-01-23 | 11:59 | 50.02
2021-01-23 | 11:59 | 50.017
2021-01-23 | 11:59 | 50.015
2021-01-23 | 11:59 | 50.015
2021-01-23 | 11:59 | 50.015
2021-01-23 | 11:59 | 50.016
2021-01-23 | 11:59 | 50.016
2021-01-23 | 11:59 | 50.017
2021-01-23 | 11:59 | 50.018
2021-01-23 | 11:59 | 50.019
2021-01-23 | 11:59 | 50.022
2021-01-23 | 11:59 | 50.023
2021-01-23 | 11:59 | 50.035
2021-01-23 | 11:59 | 50.012
2021-01-23 | 11:59 | 50.007
2021-01-23 | 11:59 | 50
2021-01-23 | 11:59 | 49.993
2021-01-23 | 11:59 | 49.987
2021-01-23 | 11:59 | 49.979
2021-01-23 | 11:59 | 49.974
2021-01-23 | 11:59 | 49.97
2021-01-23 | 11:59 | 49.966
2021-01-23 | 11:59 | 49.965
2021-01-23 | 11:59 | 49.965
2021-01-23 | 11:59 | 49.962
2021-01-23 | 11:59 | 49.964
2021-01-23 | 11:59 | 49.964
2021-01-23 | 11:59 | 49.963
2021-01-23 | 11:59 | 49.961
2021-01-23 | 11:59 | 49.958
2021-01-23 | 11:59 | 49.958
2021-01-23 | 11:59 | 49.958
2021-01-23 | 11:59 | 49.957
2021-01-23 | 11:59 | 49.956
2021-01-23 | 11:59 | 49.958
2021-01-23 | 11:59 | 49.957
2021-01-23 | 11:59 | 49.958
2021-01-23 | 11:59 | 49.96
2021-01-23 | 11:59 | 49.96
2021-01-23 | 11:59 | 49.96
2021-01-23 | 11:59 | 49.96
2021-01-23 | 11:59 | 49.959
2021-01-23 | 11:59 | 49.958
2021-01-23 | 11:59 | 49.957
2021-01-23 | 11:59 | 49.955
2021-01-23 | 11:59 | 49.954
2021-01-23 | 11:59 | 49.953
2021-01-23 | 11:59 | 49.952
2021-01-23 | 11:59 | 49.952
2021-01-23 | 11:59 | 49.95
2021-01-23 | 12:00 | 49.949
2021-01-23 | 12:00 | 49.946
2021-01-23 | 12:00 | 49.942
2021-01-23 | 12:00 | 49.94
2021-01-23 | 12:00 | 49.938
2021-01-23 | 12:00 | 49.937
2021-01-23 | 12:00 | 49.934
2021-01-23 | 12:00 | 49.934
2021-01-23 | 12:00 | 49.933
2021-01-23 | 12:00 | 49.934
2021-01-23 | 12:00 | 49.935
2021-01-23 | 12:00 | 49.937
2021-01-23 | 12:00 | 49.94
2021-01-23 | 12:00 | 49.942
2021-01-23 | 12:00 | 49.945
2021-01-23 | 12:00 | 49.947
2021-01-23 | 12:00 | 49.946
2021-01-23 | 12:00 | 49.946
2021-01-23 | 12:00 | 49.948
2021-01-23 | 12:00 | 49.948
2021-01-23 | 12:00 | 49.948
2021-01-23 | 12:00 | 49.947
2021-01-23 | 12:00 | 49.948
2021-01-23 | 12:00 | 49.947
2021-01-23 | 12:00 | 49.948
2021-01-23 | 12:00 | 49.947
2021-01-23 | 12:00 | 49.947
2021-01-23 | 12:00 | 49.945
2021-01-23 | 12:00 | 49.942
2021-01-23 | 12:00 | 49.94
2021-01-23 | 12:00 | 49.938
2021-01-23 | 12:00 | 49.933
2021-01-23 | 12:00 | 49.929
2021-01-23 | 12:00 | 49.924
2021-01-23 | 12:00 | 49.92
2021-01-23 | 12:00 | 49.918
2021-01-23 | 12:00 | 49.918
2021-01-23 | 12:00 | 49.917
2021-01-23 | 12:00 | 49.918
2021-01-23 | 12:00 | 49.918
2021-01-23 | 12:00 | 49.921
2021-01-23 | 12:00 | 49.923
2021-01-23 | 12:00 | 49.921
2021-01-23 | 12:00 | 49.923
2021-01-23 | 12:00 | 49.92
2021-01-23 | 12:00 | 49.92
2021-01-23 | 12:00 | 49.923
2021-01-23 | 12:00 | 49.926
2021-01-23 | 12:00 | 49.929
2021-01-23 | 12:00 | 49.931
2021-01-23 | 12:00 | 49.933
2021-01-23 | 12:00 | 49.938
2021-01-23 | 12:00 | 49.94
2021-01-23 | 12:00 | 49.943
2021-01-23 | 12:00 | 49.945
2021-01-23 | 12:00 | 49.947
2021-01-23 | 12:00 | 49.949
2021-01-23 | 12:00 | 49.948
2021-01-23 | 12:00 | 49.948
2021-01-23 | 12:00 | 49.949
2021-01-23 | 12:00 | 49.949
2021-01-23 | 12:01 | 49.947
2021-01-23 | 12:01 | 49.949
2021-01-23 | 12:01 | 49.95
2021-01-23 | 12:01 | 49.951
2021-01-23 | 12:01 | 49.95
2021-01-23 | 12:01 | 49.951
2021-01-23 | 12:01 | 49.951
2021-01-23 | 12:01 | 49.953
2021-01-23 | 12:01 | 49.953
2021-01-23 | 12:01 | 49.955
2021-01-23 | 12:01 | 49.954
2021-01-23 | 12:01 | 49.954
2021-01-23 | 12:01 | 49.955
2021-01-23 | 12:01 | 49.955
2021-01-23 | 12:01 | 49.953
2021-01-23 | 12:01 | 49.954
2021-01-23 | 12:01 | 49.954
2021-01-23 | 12:01 | 49.954
2021-01-23 | 12:01 | 49.954
2021-01-23 | 12:01 | 49.954
2021-01-23 | 12:01 | 49.953
2021-01-23 | 12:01 | 49.953
2021-01-23 | 12:01 | 49.952
2021-01-23 | 12:01 | 49.951
2021-01-23 | 12:01 | 49.949
2021-01-23 | 12:01 | 49.948
2021-01-23 | 12:01 | 49.945
2021-01-23 | 12:01 | 49.944
2021-01-23 | 12:01 | 49.943
2021-01-23 | 12:01 | 49.942
2021-01-23 | 12:01 | 49.94
2021-01-23 | 12:01 | 49.942
2021-01-23 | 12:01 | 49.942
2021-01-23 | 12:01 | 49.944
2021-01-23 | 12:01 | 49.944
2021-01-23 | 12:01 | 49.944
2021-01-23 | 12:01 | 49.945
2021-01-23 | 12:01 | 49.943
2021-01-23 | 12:01 | 49.939
2021-01-23 | 12:01 | 49.938
2021-01-23 | 12:01 | 49.935
2021-01-23 | 12:01 | 49.935
2021-01-23 | 12:01 | 49.919
2021-01-23 | 12:01 | 49.902
2021-01-23 | 12:01 | 49.883
2021-01-23 | 12:01 | 49.87
2021-01-23 | 12:01 | 49.857
2021-01-23 | 12:01 | 49.85
2021-01-23 | 12:01 | 49.844
2021-01-23 | 12:01 | 49.839
2021-01-23 | 12:01 | 49.834
2021-01-23 | 12:01 | 49.831
2021-01-23 | 12:01 | 49.829
2021-01-23 | 12:01 | 49.826
2021-01-23 | 12:01 | 49.826
2021-01-23 | 12:01 | 49.828
2021-01-23 | 12:01 | 49.827
2021-01-23 | 12:01 | 49.828
2021-01-23 | 12:01 | 49.829
2021-01-23 | 12:02 | 49.829
2021-01-23 | 12:02 | 49.829
2021-01-23 | 12:02 | 49.83
2021-01-23 | 12:02 | 49.831
2021-01-23 | 12:02 | 49.832
2021-01-23 | 12:02 | 49.831
2021-01-23 | 12:02 | 49.83
2021-01-23 | 12:02 | 49.828
2021-01-23 | 12:02 | 49.827
2021-01-23 | 12:02 | 49.826
2021-01-23 | 12:02 | 49.826
2021-01-23 | 12:02 | 49.826
2021-01-23 | 12:02 | 49.829
2021-01-23 | 12:02 | 49.829
2021-01-23 | 12:02 | 49.829
2021-01-23 | 12:02 | 49.827
2021-01-23 | 12:02 | 49.825
2021-01-23 | 12:02 | 49.82
2021-01-23 | 12:02 | 49.818
2021-01-23 | 12:02 | 49.815
2021-01-23 | 12:02 | 49.813
2021-01-23 | 12:02 | 49.811
2021-01-23 | 12:02 | 49.809
2021-01-23 | 12:02 | 49.808
2021-01-23 | 12:02 | 49.808
2021-01-23 | 12:02 | 49.807
2021-01-23 | 12:02 | 49.806
2021-01-23 | 12:02 | 49.806
2021-01-23 | 12:02 | 49.807
2021-01-23 | 12:02 | 49.808
2021-01-23 | 12:02 | 49.811
2021-01-23 | 12:02 | 49.815
2021-01-23 | 12:02 | 49.818
2021-01-23 | 12:02 | 49.823
2021-01-23 | 12:02 | 49.827
2021-01-23 | 12:02 | 49.832
2021-01-23 | 12:02 | 49.838
2021-01-23 | 12:02 | 49.842
2021-01-23 | 12:02 | 49.848
2021-01-23 | 12:02 | 49.855
2021-01-23 | 12:02 | 49.859
2021-01-23 | 12:02 | 49.863
2021-01-23 | 12:02 | 49.867
2021-01-23 | 12:02 | 49.872
2021-01-23 | 12:02 | 49.875
2021-01-23 | 12:02 | 49.875
2021-01-23 | 12:02 | 49.878
2021-01-23 | 12:02 | 49.88
2021-01-23 | 12:02 | 49.883
2021-01-23 | 12:02 | 49.886
2021-01-23 | 12:02 | 49.888
2021-01-23 | 12:02 | 49.891
2021-01-23 | 12:02 | 49.894
2021-01-23 | 12:02 | 49.897
2021-01-23 | 12:02 | 49.899
2021-01-23 | 12:02 | 49.903
2021-01-23 | 12:02 | 49.904
2021-01-23 | 12:02 | 49.909
2021-01-23 | 12:02 | 49.91
2021-01-23 | 12:02 | 49.913
2021-01-23 | 12:02 | 49.914
2021-01-23 | 12:03 | 49.916
2021-01-23 | 12:03 | 49.916
2021-01-23 | 12:03 | 49.918
2021-01-23 | 12:03 | 49.92
2021-01-23 | 12:03 | 49.922
2021-01-23 | 12:03 | 49.923
2021-01-23 | 12:03 | 49.925
2021-01-23 | 12:03 | 49.926
2021-01-23 | 12:03 | 49.927
2021-01-23 | 12:03 | 49.929
2021-01-23 | 12:03 | 49.929
2021-01-23 | 12:03 | 49.929
2021-01-23 | 12:03 | 49.929
2021-01-23 | 12:03 | 49.928
2021-01-23 | 12:03 | 49.93
2021-01-23 | 12:03 | 49.929
2021-01-23 | 12:03 | 49.929
2021-01-23 | 12:03 | 49.928
2021-01-23 | 12:03 | 49.929
2021-01-23 | 12:03 | 49.929
2021-01-23 | 12:03 | 49.929
2021-01-23 | 12:03 | 49.929
2021-01-23 | 12:03 | 49.932
2021-01-23 | 12:03 | 49.932
2021-01-23 | 12:03 | 49.933
2021-01-23 | 12:03 | 49.934
2021-01-23 | 12:03 | 49.935
2021-01-23 | 12:03 | 49.936
2021-01-23 | 12:03 | 49.937
2021-01-23 | 12:03 | 49.939
2021-01-23 | 12:03 | 49.941
2021-01-23 | 12:03 | 49.942
2021-01-23 | 12:03 | 49.943
2021-01-23 | 12:03 | 49.944
2021-01-23 | 12:03 | 49.944
2021-01-23 | 12:03 | 49.941
2021-01-23 | 12:03 | 49.941
2021-01-23 | 12:03 | 49.942
2021-01-23 | 12:03 | 49.942
2021-01-23 | 12:03 | 49.941
2021-01-23 | 12:03 | 49.941
2021-01-23 | 12:03 | 49.942
2021-01-23 | 12:03 | 49.94
2021-01-23 | 12:03 | 49.938
2021-01-23 | 12:03 | 49.938
2021-01-23 | 12:03 | 49.936
2021-01-23 | 12:03 | 49.938
2021-01-23 | 12:03 | 49.938
2021-01-23 | 12:03 | 49.941
2021-01-23 | 12:03 | 49.941
2021-01-23 | 12:03 | 49.942
2021-01-23 | 12:03 | 49.944
2021-01-23 | 12:03 | 49.946
2021-01-23 | 12:03 | 49.948
2021-01-23 | 12:03 | 49.949
2021-01-23 | 12:03 | 49.952
2021-01-23 | 12:03 | 49.955
2021-01-23 | 12:03 | 49.957
2021-01-23 | 12:03 | 49.959
2021-01-23 | 12:04 | 49.963
2021-01-23 | 12:04 | 49.965
2021-01-23 | 12:04 | 49.967
2021-01-23 | 12:04 | 49.971
2021-01-23 | 12:04 | 49.975
2021-01-23 | 12:04 | 49.978
2021-01-23 | 12:04 | 49.981
2021-01-23 | 12:04 | 49.985
2021-01-23 | 12:04 | 49.986
2021-01-23 | 12:04 | 49.985
2021-01-23 | 12:04 | 49.985
2021-01-23 | 12:04 | 49.985
2021-01-23 | 12:04 | 49.983
2021-01-23 | 12:04 | 49.982
2021-01-23 | 12:04 | 49.982
2021-01-23 | 12:04 | 49.981
2021-01-23 | 12:04 | 49.98
2021-01-23 | 12:04 | 49.98
2021-01-23 | 12:04 | 49.98
2021-01-23 | 12:04 | 49.98
2021-01-23 | 12:04 | 49.981
2021-01-23 | 12:04 | 49.983
2021-01-23 | 12:04 | 49.985
2021-01-23 | 12:04 | 49.986
2021-01-23 | 12:04 | 49.986
2021-01-23 | 12:04 | 49.987
2021-01-23 | 12:04 | 49.986
2021-01-23 | 12:04 | 49.984
2021-01-23 | 12:04 | 49.982
2021-01-23 | 12:04 | 49.983
2021-01-23 | 12:04 | 49.983
2021-01-23 | 12:04 | 49.981
2021-01-23 | 12:04 | 49.979
2021-01-23 | 12:04 | 49.978
2021-01-23 | 12:04 | 49.977
2021-01-23 | 12:04 | 49.977
2021-01-23 | 12:04 | 49.976
2021-01-23 | 12:04 | 49.977
2021-01-23 | 12:04 | 49.979
2021-01-23 | 12:04 | 49.982
2021-01-23 | 12:04 | 49.981
2021-01-23 | 12:04 | 49.983
2021-01-23 | 12:04 | 49.983
2021-01-23 | 12:04 | 49.983
2021-01-23 | 12:04 | 49.983
2021-01-23 | 12:04 | 49.982
2021-01-23 | 12:04 | 49.981
2021-01-23 | 12:04 | 49.978
2021-01-23 | 12:04 | 49.976
2021-01-23 | 12:04 | 49.975
2021-01-23 | 12:04 | 49.972
2021-01-23 | 12:04 | 49.97
2021-01-23 | 12:04 | 49.969
2021-01-23 | 12:04 | 49.967
2021-01-23 | 12:04 | 49.967
2021-01-23 | 12:04 | 49.969
2021-01-23 | 12:04 | 49.97
2021-01-23 | 12:04 | 49.971
2021-01-23 | 12:04 | 49.97
2021-01-23 | 12:04 | 49.97
2021-01-23 | 12:04 | 49.969
2021-01-23 | 12:05 | 49.97
2021-01-23 | 12:05 | 49.969
2021-01-23 | 12:05 | 49.97
2021-01-23 | 12:05 | 49.97
2021-01-23 | 12:05 | 49.97
2021-01-23 | 12:05 | 49.968
2021-01-23 | 12:05 | 49.969
2021-01-23 | 12:05 | 49.967
2021-01-23 | 12:05 | 49.966
2021-01-23 | 12:05 | 49.965
2021-01-23 | 12:05 | 49.965
2021-01-23 | 12:05 | 49.963
2021-01-23 | 12:05 | 49.961
2021-01-23 | 12:05 | 49.96
2021-01-23 | 12:05 | 49.96
2021-01-23 | 12:05 | 49.96
2021-01-23 | 12:05 | 49.961
2021-01-23 | 12:05 | 49.963
2021-01-23 | 12:05 | 49.964
2021-01-23 | 12:05 | 49.966
2021-01-23 | 12:05 | 49.965
2021-01-23 | 12:05 | 49.965
2021-01-23 | 12:05 | 49.965
2021-01-23 | 12:05 | 49.964
2021-01-23 | 12:05 | 49.962
2021-01-23 | 12:05 | 49.957
2021-01-23 | 12:05 | 49.957
2021-01-23 | 12:05 | 49.954
2021-01-23 | 12:05 | 49.952
2021-01-23 | 12:05 | 49.952
2021-01-23 | 12:05 | 49.951
2021-01-23 | 12:05 | 49.951
2021-01-23 | 12:05 | 49.95
2021-01-23 | 12:05 | 49.948
2021-01-23 | 12:05 | 49.947
2021-01-23 | 12:05 | 49.946
2021-01-23 | 12:05 | 49.946
2021-01-23 | 12:05 | 49.946
2021-01-23 | 12:05 | 49.946
2021-01-23 | 12:05 | 49.945
2021-01-23 | 12:05 | 49.945
2021-01-23 | 12:05 | 49.944
2021-01-23 | 12:05 | 49.943
2021-01-23 | 12:05 | 49.941
2021-01-23 | 12:05 | 49.941
2021-01-23 | 12:05 | 49.942
2021-01-23 | 12:05 | 49.943
2021-01-23 | 12:05 | 49.943
2021-01-23 | 12:05 | 49.943
2021-01-23 | 12:05 | 49.941
2021-01-23 | 12:05 | 49.943
2021-01-23 | 12:05 | 49.943
2021-01-23 | 12:05 | 49.942
2021-01-23 | 12:05 | 49.943
2021-01-23 | 12:05 | 49.943
2021-01-23 | 12:05 | 49.941
2021-01-23 | 12:05 | 49.94
2021-01-23 | 12:05 | 49.94
2021-01-23 | 12:05 | 49.943
2021-01-23 | 12:06 | 49.946
2021-01-23 | 12:06 | 49.947
2021-01-23 | 12:06 | 49.95
2021-01-23 | 12:06 | 49.953
2021-01-23 | 12:06 | 49.956
2021-01-23 | 12:06 | 49.959
2021-01-23 | 12:06 | 49.961
2021-01-23 | 12:06 | 49.961
2021-01-23 | 12:06 | 49.962
2021-01-23 | 12:06 | 49.964
2021-01-23 | 12:06 | 49.964
2021-01-23 | 12:06 | 49.965
2021-01-23 | 12:06 | 49.966
2021-01-23 | 12:06 | 49.968
2021-01-23 | 12:06 | 49.969
2021-01-23 | 12:06 | 49.97
2021-01-23 | 12:06 | 49.972
2021-01-23 | 12:06 | 49.973
2021-01-23 | 12:06 | 49.973
2021-01-23 | 12:06 | 49.973
2021-01-23 | 12:06 | 49.972
2021-01-23 | 12:06 | 49.972
2021-01-23 | 12:06 | 49.971
2021-01-23 | 12:06 | 49.971
2021-01-23 | 12:06 | 49.968
2021-01-23 | 12:06 | 49.966
2021-01-23 | 12:06 | 49.966
2021-01-23 | 12:06 | 49.963
2021-01-23 | 12:06 | 49.96
2021-01-23 | 12:06 | 49.957
2021-01-23 | 12:06 | 49.955
2021-01-23 | 12:06 | 49.951
2021-01-23 | 12:06 | 49.95
2021-01-23 | 12:06 | 49.949
2021-01-23 | 12:06 | 49.948
2021-01-23 | 12:06 | 49.947
2021-01-23 | 12:06 | 49.947
2021-01-23 | 12:06 | 49.944
2021-01-23 | 12:06 | 49.943
2021-01-23 | 12:06 | 49.943
2021-01-23 | 12:06 | 49.943
2021-01-23 | 12:06 | 49.94
2021-01-23 | 12:06 | 49.943
2021-01-23 | 12:06 | 49.943
2021-01-23 | 12:06 | 49.944
2021-01-23 | 12:06 | 49.946
2021-01-23 | 12:06 | 49.948
2021-01-23 | 12:06 | 49.949
2021-01-23 | 12:06 | 49.952
2021-01-23 | 12:06 | 49.955
2021-01-23 | 12:06 | 49.96
2021-01-23 | 12:06 | 49.965
2021-01-23 | 12:06 | 49.97
2021-01-23 | 12:06 | 49.972
2021-01-23 | 12:06 | 49.975
2021-01-23 | 12:06 | 49.975
2021-01-23 | 12:06 | 49.974
2021-01-23 | 12:06 | 49.974
2021-01-23 | 12:06 | 49.975
2021-01-23 | 12:06 | 49.973
2021-01-23 | 12:06 | 49.973
2021-01-23 | 12:07 | 49.974
2021-01-23 | 12:07 | 49.973
2021-01-23 | 12:07 | 49.973
2021-01-23 | 12:07 | 49.973
2021-01-23 | 12:07 | 49.975
2021-01-23 | 12:07 | 49.977
2021-01-23 | 12:07 | 49.978
2021-01-23 | 12:07 | 49.979
2021-01-23 | 12:07 | 49.98
2021-01-23 | 12:07 | 49.982
2021-01-23 | 12:07 | 49.981
2021-01-23 | 12:07 | 49.981
2021-01-23 | 12:07 | 49.981
2021-01-23 | 12:07 | 49.979
2021-01-23 | 12:07 | 49.978
2021-01-23 | 12:07 | 49.98
2021-01-23 | 12:07 | 49.98
2021-01-23 | 12:07 | 49.981
2021-01-23 | 12:07 | 49.981
2021-01-23 | 12:07 | 49.982
2021-01-23 | 12:07 | 49.984
2021-01-23 | 12:07 | 49.987
2021-01-23 | 12:07 | 49.99
2021-01-23 | 12:07 | 49.992
2021-01-23 | 12:07 | 49.996
2021-01-23 | 12:07 | 49.999
2021-01-23 | 12:07 | 50.002
2021-01-23 | 12:07 | 50.003
2021-01-23 | 12:07 | 50.004

## Event 20210129-1
In UTC
Date | Time | Freq
2021-01-29 | 6:07 | 49.921
2021-01-29 | 6:07 | 49.922
2021-01-29 | 6:07 | 49.919
2021-01-29 | 6:07 | 49.916
2021-01-29 | 6:07 | 49.912
2021-01-29 | 6:07 | 49.911
2021-01-29 | 6:07 | 49.91
2021-01-29 | 6:07 | 49.909
2021-01-29 | 6:07 | 49.91
2021-01-29 | 6:07 | 49.909
2021-01-29 | 6:07 | 49.908
2021-01-29 | 6:07 | 49.908
2021-01-29 | 6:07 | 49.908
2021-01-29 | 6:07 | 49.909
2021-01-29 | 6:07 | 49.905
2021-01-29 | 6:07 | 49.904
2021-01-29 | 6:07 | 49.903
2021-01-29 | 6:07 | 49.903
2021-01-29 | 6:07 | 49.903
2021-01-29 | 6:07 | 49.904
2021-01-29 | 6:07 | 49.905
2021-01-29 | 6:07 | 49.904
2021-01-29 | 6:07 | 49.905
2021-01-29 | 6:07 | 49.906
2021-01-29 | 6:07 | 49.908
2021-01-29 | 6:07 | 49.906
2021-01-29 | 6:07 | 49.905
2021-01-29 | 6:07 | 49.905
2021-01-29 | 6:07 | 49.903
2021-01-29 | 6:07 | 49.901
2021-01-29 | 6:08 | 49.9
2021-01-29 | 6:08 | 49.901
2021-01-29 | 6:08 | 49.902
2021-01-29 | 6:08 | 49.903
2021-01-29 | 6:08 | 49.901
2021-01-29 | 6:08 | 49.898
2021-01-29 | 6:08 | 49.898
2021-01-29 | 6:08 | 49.896
2021-01-29 | 6:08 | 49.893
2021-01-29 | 6:08 | 49.892
2021-01-29 | 6:08 | 49.895
2021-01-29 | 6:08 | 49.896
2021-01-29 | 6:08 | 49.899
2021-01-29 | 6:08 | 49.898
2021-01-29 | 6:08 | 49.902
2021-01-29 | 6:08 | 49.905
2021-01-29 | 6:08 | 49.906
2021-01-29 | 6:08 | 49.908
2021-01-29 | 6:08 | 49.906
2021-01-29 | 6:08 | 49.905
2021-01-29 | 6:08 | 49.905
2021-01-29 | 6:08 | 49.905
2021-01-29 | 6:08 | 49.901
2021-01-29 | 6:08 | 49.899
2021-01-29 | 6:08 | 49.898
2021-01-29 | 6:08 | 49.899
2021-01-29 | 6:08 | 49.896
2021-01-29 | 6:08 | 49.895
2021-01-29 | 6:08 | 49.892
2021-01-29 | 6:08 | 49.89
2021-01-29 | 6:08 | 49.888
2021-01-29 | 6:08 | 49.886
2021-01-29 | 6:08 | 49.884
2021-01-29 | 6:08 | 49.886
2021-01-29 | 6:08 | 49.888
2021-01-29 | 6:08 | 49.891
2021-01-29 | 6:08 | 49.893
2021-01-29 | 6:08 | 49.891
2021-01-29 | 6:08 | 49.808
2021-01-29 | 6:08 | 49.723
2021-01-29 | 6:08 | 49.68
2021-01-29 | 6:08 | 49.663
2021-01-29 | 6:08 | 49.658
2021-01-29 | 6:08 | 49.656
2021-01-29 | 6:08 | 49.654
2021-01-29 | 6:08 | 49.656
2021-01-29 | 6:08 | 49.658
2021-01-29 | 6:08 | 49.661
2021-01-29 | 6:08 | 49.662
2021-01-29 | 6:08 | 49.664
2021-01-29 | 6:08 | 49.668
2021-01-29 | 6:08 | 49.67
2021-01-29 | 6:08 | 49.669
2021-01-29 | 6:08 | 49.671
2021-01-29 | 6:08 | 49.67
2021-01-29 | 6:08 | 49.67
2021-01-29 | 6:08 | 49.672
2021-01-29 | 6:08 | 49.674
2021-01-29 | 6:08 | 49.675
2021-01-29 | 6:08 | 49.674
2021-01-29 | 6:08 | 49.675
2021-01-29 | 6:09 | 49.676
2021-01-29 | 6:09 | 49.676
2021-01-29 | 6:09 | 49.677
2021-01-29 | 6:09 | 49.675
2021-01-29 | 6:09 | 49.673
2021-01-29 | 6:09 | 49.671
2021-01-29 | 6:09 | 49.669
2021-01-29 | 6:09 | 49.667
2021-01-29 | 6:09 | 49.668
2021-01-29 | 6:09 | 49.669
2021-01-29 | 6:09 | 49.669
2021-01-29 | 6:09 | 49.667
2021-01-29 | 6:09 | 49.665
2021-01-29 | 6:09 | 49.663
2021-01-29 | 6:09 | 49.662
2021-01-29 | 6:09 | 49.657
2021-01-29 | 6:09 | 49.658
2021-01-29 | 6:09 | 49.659
2021-01-29 | 6:09 | 49.66
2021-01-29 | 6:09 | 49.661
2021-01-29 | 6:09 | 49.66
2021-01-29 | 6:09 | 49.661
2021-01-29 | 6:09 | 49.661
2021-01-29 | 6:09 | 49.66
2021-01-29 | 6:09 | 49.661
2021-01-29 | 6:09 | 49.661
2021-01-29 | 6:09 | 49.663
2021-01-29 | 6:09 | 49.663
2021-01-29 | 6:09 | 49.664
2021-01-29 | 6:09 | 49.662
2021-01-29 | 6:09 | 49.659
2021-01-29 | 6:09 | 49.657
2021-01-29 | 6:09 | 49.653
2021-01-29 | 6:09 | 49.649
2021-01-29 | 6:09 | 49.647
2021-01-29 | 6:09 | 49.645
2021-01-29 | 6:09 | 49.643
2021-01-29 | 6:09 | 49.644
2021-01-29 | 6:09 | 49.642
2021-01-29 | 6:09 | 49.644
2021-01-29 | 6:09 | 49.644
2021-01-29 | 6:09 | 49.644
2021-01-29 | 6:09 | 49.643
2021-01-29 | 6:09 | 49.645
2021-01-29 | 6:09 | 49.645
2021-01-29 | 6:09 | 49.644
2021-01-29 | 6:09 | 49.643
2021-01-29 | 6:09 | 49.641
2021-01-29 | 6:09 | 49.639
2021-01-29 | 6:09 | 49.638
2021-01-29 | 6:09 | 49.638
2021-01-29 | 6:09 | 49.637
2021-01-29 | 6:09 | 49.64
2021-01-29 | 6:09 | 49.644
2021-01-29 | 6:09 | 49.646
2021-01-29 | 6:09 | 49.648
2021-01-29 | 6:09 | 49.65
2021-01-29 | 6:09 | 49.652
2021-01-29 | 6:09 | 49.653
2021-01-29 | 6:09 | 49.654
2021-01-29 | 6:10 | 49.66
2021-01-29 | 6:10 | 49.665
2021-01-29 | 6:10 | 49.666
2021-01-29 | 6:10 | 49.667
2021-01-29 | 6:10 | 49.667
2021-01-29 | 6:10 | 49.669
2021-01-29 | 6:10 | 49.67
2021-01-29 | 6:10 | 49.673
2021-01-29 | 6:10 | 49.676
2021-01-29 | 6:10 | 49.68
2021-01-29 | 6:10 | 49.684
2021-01-29 | 6:10 | 49.686
2021-01-29 | 6:10 | 49.689
2021-01-29 | 6:10 | 49.694
2021-01-29 | 6:10 | 49.695
2021-01-29 | 6:10 | 49.696
2021-01-29 | 6:10 | 49.696
2021-01-29 | 6:10 | 49.696
2021-01-29 | 6:10 | 49.697
2021-01-29 | 6:10 | 49.698
2021-01-29 | 6:10 | 49.697
2021-01-29 | 6:10 | 49.697
2021-01-29 | 6:10 | 49.698
2021-01-29 | 6:10 | 49.696
2021-01-29 | 6:10 | 49.696
2021-01-29 | 6:10 | 49.696
2021-01-29 | 6:10 | 49.695
2021-01-29 | 6:10 | 49.696
2021-01-29 | 6:10 | 49.696
2021-01-29 | 6:10 | 49.698
2021-01-29 | 6:10 | 49.698
2021-01-29 | 6:10 | 49.697
2021-01-29 | 6:10 | 49.699
2021-01-29 | 6:10 | 49.701
2021-01-29 | 6:10 | 49.704
2021-01-29 | 6:10 | 49.705
2021-01-29 | 6:10 | 49.705
2021-01-29 | 6:10 | 49.705
2021-01-29 | 6:10 | 49.701
2021-01-29 | 6:10 | 49.7
2021-01-29 | 6:10 | 49.699
2021-01-29 | 6:10 | 49.701
2021-01-29 | 6:10 | 49.703
2021-01-29 | 6:10 | 49.703
2021-01-29 | 6:10 | 49.701
2021-01-29 | 6:10 | 49.703
2021-01-29 | 6:10 | 49.701
2021-01-29 | 6:10 | 49.701
2021-01-29 | 6:10 | 49.703
2021-01-29 | 6:10 | 49.704
2021-01-29 | 6:10 | 49.706
2021-01-29 | 6:10 | 49.707
2021-01-29 | 6:10 | 49.709
2021-01-29 | 6:10 | 49.71
2021-01-29 | 6:10 | 49.711
2021-01-29 | 6:10 | 49.712
2021-01-29 | 6:10 | 49.711
2021-01-29 | 6:10 | 49.713
2021-01-29 | 6:10 | 49.714
2021-01-29 | 6:10 | 49.712
2021-01-29 | 6:11 | 49.709
2021-01-29 | 6:11 | 49.707
2021-01-29 | 6:11 | 49.705
2021-01-29 | 6:11 | 49.704
2021-01-29 | 6:11 | 49.703
2021-01-29 | 6:11 | 49.701
2021-01-29 | 6:11 | 49.701
2021-01-29 | 6:11 | 49.701
2021-01-29 | 6:11 | 49.699
2021-01-29 | 6:11 | 49.7
2021-01-29 | 6:11 | 49.702
2021-01-29 | 6:11 | 49.703
2021-01-29 | 6:11 | 49.703
2021-01-29 | 6:11 | 49.705
2021-01-29 | 6:11 | 49.705
2021-01-29 | 6:11 | 49.705
2021-01-29 | 6:11 | 49.703
2021-01-29 | 6:11 | 49.703
2021-01-29 | 6:11 | 49.701
2021-01-29 | 6:11 | 49.7
2021-01-29 | 6:11 | 49.697
2021-01-29 | 6:11 | 49.695
2021-01-29 | 6:11 | 49.694
2021-01-29 | 6:11 | 49.693
2021-01-29 | 6:11 | 49.691
2021-01-29 | 6:11 | 49.692
2021-01-29 | 6:11 | 49.693
2021-01-29 | 6:11 | 49.693
2021-01-29 | 6:11 | 49.692
2021-01-29 | 6:11 | 49.693
2021-01-29 | 6:11 | 49.692
2021-01-29 | 6:11 | 49.69
2021-01-29 | 6:11 | 49.688
2021-01-29 | 6:11 | 49.686
2021-01-29 | 6:11 | 49.683
2021-01-29 | 6:11 | 49.683
2021-01-29 | 6:11 | 49.682
2021-01-29 | 6:11 | 49.682
2021-01-29 | 6:11 | 49.682
2021-01-29 | 6:11 | 49.684
2021-01-29 | 6:11 | 49.687
2021-01-29 | 6:11 | 49.69
2021-01-29 | 6:11 | 49.693
2021-01-29 | 6:11 | 49.692
2021-01-29 | 6:11 | 49.693
2021-01-29 | 6:11 | 49.692
2021-01-29 | 6:11 | 49.689
2021-01-29 | 6:11 | 49.688
2021-01-29 | 6:11 | 49.691
2021-01-29 | 6:11 | 49.693
2021-01-29 | 6:11 | 49.696
2021-01-29 | 6:11 | 49.696
2021-01-29 | 6:11 | 49.697
2021-01-29 | 6:11 | 49.698
2021-01-29 | 6:11 | 49.696
2021-01-29 | 6:11 | 49.697
2021-01-29 | 6:11 | 49.698
2021-01-29 | 6:11 | 49.696
2021-01-29 | 6:11 | 49.695
2021-01-29 | 6:11 | 49.694
2021-01-29 | 6:12 | 49.695
2021-01-29 | 6:12 | 49.695
2021-01-29 | 6:12 | 49.698
2021-01-29 | 6:12 | 49.7
2021-01-29 | 6:12 | 49.703
2021-01-29 | 6:12 | 49.704
2021-01-29 | 6:12 | 49.706
2021-01-29 | 6:12 | 49.708
2021-01-29 | 6:12 | 49.71
2021-01-29 | 6:12 | 49.712
2021-01-29 | 6:12 | 49.728
2021-01-29 | 6:12 | 49.739
2021-01-29 | 6:12 | 49.748
2021-01-29 | 6:12 | 49.753
2021-01-29 | 6:12 | 49.757
2021-01-29 | 6:12 | 49.761
2021-01-29 | 6:12 | 49.764
2021-01-29 | 6:12 | 49.768
2021-01-29 | 6:12 | 49.77
2021-01-29 | 6:12 | 49.772
2021-01-29 | 6:12 | 49.775
2021-01-29 | 6:12 | 49.776
2021-01-29 | 6:12 | 49.775
2021-01-29 | 6:12 | 49.775
2021-01-29 | 6:12 | 49.776
2021-01-29 | 6:12 | 49.777
2021-01-29 | 6:12 | 49.78
2021-01-29 | 6:12 | 49.786
2021-01-29 | 6:12 | 49.79
2021-01-29 | 6:12 | 49.793
2021-01-29 | 6:12 | 49.793
2021-01-29 | 6:12 | 49.795
2021-01-29 | 6:12 | 49.794
2021-01-29 | 6:12 | 49.796
2021-01-29 | 6:12 | 49.798
2021-01-29 | 6:12 | 49.797
2021-01-29 | 6:12 | 49.797
2021-01-29 | 6:12 | 49.797
2021-01-29 | 6:12 | 49.799
2021-01-29 | 6:12 | 49.803
2021-01-29 | 6:12 | 49.805
2021-01-29 | 6:12 | 49.806
2021-01-29 | 6:12 | 49.807
2021-01-29 | 6:12 | 49.806
2021-01-29 | 6:12 | 49.807
2021-01-29 | 6:12 | 49.808
2021-01-29 | 6:12 | 49.807
2021-01-29 | 6:12 | 49.806
2021-01-29 | 6:12 | 49.806
2021-01-29 | 6:12 | 49.808
2021-01-29 | 6:12 | 49.808
2021-01-29 | 6:12 | 49.809
2021-01-29 | 6:12 | 49.813
2021-01-29 | 6:12 | 49.814
2021-01-29 | 6:12 | 49.816
2021-01-29 | 6:12 | 49.816
2021-01-29 | 6:12 | 49.818
2021-01-29 | 6:12 | 49.82
2021-01-29 | 6:12 | 49.82
2021-01-29 | 6:12 | 49.82
2021-01-29 | 6:13 | 49.82
2021-01-29 | 6:13 | 49.822
2021-01-29 | 6:13 | 49.824
2021-01-29 | 6:13 | 49.824
2021-01-29 | 6:13 | 49.826
2021-01-29 | 6:13 | 49.827
2021-01-29 | 6:13 | 49.831
2021-01-29 | 6:13 | 49.835
2021-01-29 | 6:13 | 49.839
2021-01-29 | 6:13 | 49.843
2021-01-29 | 6:13 | 49.845
2021-01-29 | 6:13 | 49.846
2021-01-29 | 6:13 | 49.845
2021-01-29 | 6:13 | 49.844
2021-01-29 | 6:13 | 49.844
2021-01-29 | 6:13 | 49.841
2021-01-29 | 6:13 | 49.841
2021-01-29 | 6:13 | 49.84
2021-01-29 | 6:13 | 49.843
2021-01-29 | 6:13 | 49.844
2021-01-29 | 6:13 | 49.844
2021-01-29 | 6:13 | 49.844
2021-01-29 | 6:13 | 49.845
2021-01-29 | 6:13 | 49.838
2021-01-29 | 6:13 | 49.835
2021-01-29 | 6:13 | 49.833
2021-01-29 | 6:13 | 49.83
2021-01-29 | 6:13 | 49.83
2021-01-29 | 6:13 | 49.831
2021-01-29 | 6:13 | 49.832
2021-01-29 | 6:13 | 49.833
2021-01-29 | 6:13 | 49.833
2021-01-29 | 6:13 | 49.834
2021-01-29 | 6:13 | 49.833
2021-01-29 | 6:13 | 49.831
2021-01-29 | 6:13 | 49.832
2021-01-29 | 6:13 | 49.832
2021-01-29 | 6:13 | 49.834
2021-01-29 | 6:13 | 49.837
2021-01-29 | 6:13 | 49.836
2021-01-29 | 6:13 | 49.84
2021-01-29 | 6:13 | 49.842
2021-01-29 | 6:13 | 49.841
2021-01-29 | 6:13 | 49.84
2021-01-29 | 6:13 | 49.836
2021-01-29 | 6:13 | 49.835
2021-01-29 | 6:13 | 49.834
2021-01-29 | 6:13 | 49.837
2021-01-29 | 6:13 | 49.839
2021-01-29 | 6:13 | 49.843
2021-01-29 | 6:13 | 49.847
2021-01-29 | 6:13 | 49.847
2021-01-29 | 6:13 | 49.848
2021-01-29 | 6:13 | 49.849
2021-01-29 | 6:13 | 49.85
2021-01-29 | 6:13 | 49.852
2021-01-29 | 6:13 | 49.854
2021-01-29 | 6:13 | 49.858
2021-01-29 | 6:13 | 49.862
2021-01-29 | 6:13 | 49.866
2021-01-29 | 6:14 | 49.867
2021-01-29 | 6:14 | 49.866
2021-01-29 | 6:14 | 49.866
2021-01-29 | 6:14 | 49.863
2021-01-29 | 6:14 | 49.86
2021-01-29 | 6:14 | 49.859
2021-01-29 | 6:14 | 49.861
2021-01-29 | 6:14 | 49.863
2021-01-29 | 6:14 | 49.866
2021-01-29 | 6:14 | 49.868
2021-01-29 | 6:14 | 49.87
2021-01-29 | 6:14 | 49.872
2021-01-29 | 6:14 | 49.872
2021-01-29 | 6:14 | 49.872
2021-01-29 | 6:14 | 49.873
2021-01-29 | 6:14 | 49.873
2021-01-29 | 6:14 | 49.875
2021-01-29 | 6:14 | 49.881
2021-01-29 | 6:14 | 49.885
2021-01-29 | 6:14 | 49.89
2021-01-29 | 6:14 | 49.894
2021-01-29 | 6:14 | 49.895
2021-01-29 | 6:14 | 49.895
2021-01-29 | 6:14 | 49.895
2021-01-29 | 6:14 | 49.895
2021-01-29 | 6:14 | 49.894
2021-01-29 | 6:14 | 49.894
2021-01-29 | 6:14 | 49.895
2021-01-29 | 6:14 | 49.895
2021-01-29 | 6:14 | 49.898
2021-01-29 | 6:14 | 49.896
2021-01-29 | 6:14 | 49.898
2021-01-29 | 6:14 | 49.899
2021-01-29 | 6:14 | 49.9
2021-01-29 | 6:14 | 49.904
2021-01-29 | 6:14 | 49.909
2021-01-29 | 6:14 | 49.912
2021-01-29 | 6:14 | 49.914
2021-01-29 | 6:14 | 49.916
2021-01-29 | 6:14 | 49.918
2021-01-29 | 6:14 | 49.914
2021-01-29 | 6:14 | 49.911
2021-01-29 | 6:14 | 49.904
2021-01-29 | 6:14 | 49.903
2021-01-29 | 6:14 | 49.9
2021-01-29 | 6:14 | 49.897
2021-01-29 | 6:14 | 49.901
2021-01-29 | 6:14 | 49.906
2021-01-29 | 6:14 | 49.91
2021-01-29 | 6:14 | 49.911
2021-01-29 | 6:14 | 49.91
2021-01-29 | 6:14 | 49.909
2021-01-29 | 6:14 | 49.909
2021-01-29 | 6:14 | 49.907
2021-01-29 | 6:14 | 49.905
2021-01-29 | 6:14 | 49.904
2021-01-29 | 6:14 | 49.904
2021-01-29 | 6:14 | 49.904
2021-01-29 | 6:14 | 49.904
2021-01-29 | 6:14 | 49.906
2021-01-29 | 6:15 | 49.906
2021-01-29 | 6:15 | 49.908
2021-01-29 | 6:15 | 49.909
2021-01-29 | 6:15 | 49.911
2021-01-29 | 6:15 | 49.914
2021-01-29 | 6:15 | 49.915
2021-01-29 | 6:15 | 49.913
2021-01-29 | 6:15 | 49.913
2021-01-29 | 6:15 | 49.91
2021-01-29 | 6:15 | 49.911
2021-01-29 | 6:15 | 49.908
2021-01-29 | 6:15 | 49.908
2021-01-29 | 6:15 | 49.907
2021-01-29 | 6:15 | 49.907
2021-01-29 | 6:15 | 49.903
2021-01-29 | 6:15 | 49.904
2021-01-29 | 6:15 | 49.902
2021-01-29 | 6:15 | 49.904
2021-01-29 | 6:15 | 49.903
2021-01-29 | 6:15 | 49.908
2021-01-29 | 6:15 | 49.91
2021-01-29 | 6:15 | 49.912
2021-01-29 | 6:15 | 49.912
2021-01-29 | 6:15 | 49.914
2021-01-29 | 6:15 | 49.914
2021-01-29 | 6:15 | 49.912
2021-01-29 | 6:15 | 49.912
2021-01-29 | 6:15 | 49.913
2021-01-29 | 6:15 | 49.917
2021-01-29 | 6:15 | 49.919
2021-01-29 | 6:15 | 49.921
2021-01-29 | 6:15 | 49.921
2021-01-29 | 6:15 | 49.92
2021-01-29 | 6:15 | 49.92
2021-01-29 | 6:15 | 49.922
2021-01-29 | 6:15 | 49.924
2021-01-29 | 6:15 | 49.924
2021-01-29 | 6:15 | 49.924
2021-01-29 | 6:15 | 49.922
2021-01-29 | 6:15 | 49.924
2021-01-29 | 6:15 | 49.924
2021-01-29 | 6:15 | 49.924
2021-01-29 | 6:15 | 49.923
2021-01-29 | 6:15 | 49.924
2021-01-29 | 6:15 | 49.925
2021-01-29 | 6:15 | 49.926
2021-01-29 | 6:15 | 49.927
2021-01-29 | 6:15 | 49.928
2021-01-29 | 6:15 | 49.928
2021-01-29 | 6:15 | 49.928
2021-01-29 | 6:15 | 49.926
2021-01-29 | 6:15 | 49.925
2021-01-29 | 6:15 | 49.924
2021-01-29 | 6:15 | 49.925
2021-01-29 | 6:15 | 49.928
2021-01-29 | 6:15 | 49.931
2021-01-29 | 6:15 | 49.931
2021-01-29 | 6:15 | 49.933
2021-01-29 | 6:15 | 49.932
2021-01-29 | 6:16 | 49.932
2021-01-29 | 6:16 | 49.932
2021-01-29 | 6:16 | 49.928
2021-01-29 | 6:16 | 49.928
2021-01-29 | 6:16 | 49.927
2021-01-29 | 6:16 | 49.928
2021-01-29 | 6:16 | 49.929
2021-01-29 | 6:16 | 49.931
2021-01-29 | 6:16 | 49.933
2021-01-29 | 6:16 | 49.935
2021-01-29 | 6:16 | 49.939
2021-01-29 | 6:16 | 49.943
2021-01-29 | 6:16 | 49.943
2021-01-29 | 6:16 | 49.946
2021-01-29 | 6:16 | 49.948
2021-01-29 | 6:16 | 49.95
2021-01-29 | 6:16 | 49.951
2021-01-29 | 6:16 | 49.951
2021-01-29 | 6:16 | 49.949
2021-01-29 | 6:16 | 49.946
2021-01-29 | 6:16 | 49.943
2021-01-29 | 6:16 | 49.943
2021-01-29 | 6:16 | 49.94
2021-01-29 | 6:16 | 49.939
2021-01-29 | 6:16 | 49.936
2021-01-29 | 6:16 | 49.93
2021-01-29 | 6:16 | 49.926
2021-01-29 | 6:16 | 49.924
2021-01-29 | 6:16 | 49.922
2021-01-29 | 6:16 | 49.922
2021-01-29 | 6:16 | 49.921
2021-01-29 | 6:16 | 49.92
2021-01-29 | 6:16 | 49.918
2021-01-29 | 6:16 | 49.918
2021-01-29 | 6:16 | 49.918
2021-01-29 | 6:16 | 49.918
2021-01-29 | 6:16 | 49.92
2021-01-29 | 6:16 | 49.922
2021-01-29 | 6:16 | 49.921
2021-01-29 | 6:16 | 49.92
2021-01-29 | 6:16 | 49.922
2021-01-29 | 6:16 | 49.921
2021-01-29 | 6:16 | 49.921
2021-01-29 | 6:16 | 49.917
2021-01-29 | 6:16 | 49.914
2021-01-29 | 6:16 | 49.912
2021-01-29 | 6:16 | 49.911
2021-01-29 | 6:16 | 49.91
2021-01-29 | 6:16 | 49.909
2021-01-29 | 6:16 | 49.907
2021-01-29 | 6:16 | 49.908
2021-01-29 | 6:16 | 49.908
2021-01-29 | 6:16 | 49.911
2021-01-29 | 6:16 | 49.913
2021-01-29 | 6:16 | 49.915
2021-01-29 | 6:16 | 49.918
2021-01-29 | 6:16 | 49.919
2021-01-29 | 6:16 | 49.919
2021-01-29 | 6:16 | 49.917
2021-01-29 | 6:16 | 49.912
2021-01-29 | 6:16 | 49.909
2021-01-29 | 6:17 | 49.908
2021-01-29 | 6:17 | 49.907
2021-01-29 | 6:17 | 49.908
2021-01-29 | 6:17 | 49.911
2021-01-29 | 6:17 | 49.912
2021-01-29 | 6:17 | 49.916
2021-01-29 | 6:17 | 49.918
2021-01-29 | 6:17 | 49.918
2021-01-29 | 6:17 | 49.916
2021-01-29 | 6:17 | 49.918
2021-01-29 | 6:17 | 49.92
2021-01-29 | 6:17 | 49.918
2021-01-29 | 6:17 | 49.914
2021-01-29 | 6:17 | 49.911
2021-01-29 | 6:17 | 49.91
2021-01-29 | 6:17 | 49.909
2021-01-29 | 6:17 | 49.908
2021-01-29 | 6:17 | 49.907
2021-01-29 | 6:17 | 49.907
2021-01-29 | 6:17 | 49.904
2021-01-29 | 6:17 | 49.904
2021-01-29 | 6:17 | 49.904
2021-01-29 | 6:17 | 49.906
2021-01-29 | 6:17 | 49.907
2021-01-29 | 6:17 | 49.909
2021-01-29 | 6:17 | 49.909
2021-01-29 | 6:17 | 49.909
2021-01-29 | 6:17 | 49.909
2021-01-29 | 6:17 | 49.906
2021-01-29 | 6:17 | 49.905
2021-01-29 | 6:17 | 49.903
2021-01-29 | 6:17 | 49.905
2021-01-29 | 6:17 | 49.905
2021-01-29 | 6:17 | 49.906
2021-01-29 | 6:17 | 49.907
2021-01-29 | 6:17 | 49.91
2021-01-29 | 6:17 | 49.915
2021-01-29 | 6:17 | 49.918
2021-01-29 | 6:17 | 49.922
2021-01-29 | 6:17 | 49.922
2021-01-29 | 6:17 | 49.922
2021-01-29 | 6:17 | 49.922
2021-01-29 | 6:17 | 49.922
2021-01-29 | 6:17 | 49.921
2021-01-29 | 6:17 | 49.92
2021-01-29 | 6:17 | 49.923
2021-01-29 | 6:17 | 49.923
2021-01-29 | 6:17 | 49.921
2021-01-29 | 6:17 | 49.921
2021-01-29 | 6:17 | 49.924
2021-01-29 | 6:17 | 49.924
2021-01-29 | 6:17 | 49.924
2021-01-29 | 6:17 | 49.924
2021-01-29 | 6:17 | 49.924
2021-01-29 | 6:17 | 49.924
2021-01-29 | 6:17 | 49.925
2021-01-29 | 6:17 | 49.926
2021-01-29 | 6:17 | 49.927
2021-01-29 | 6:17 | 49.926
2021-01-29 | 6:18 | 49.924
2021-01-29 | 6:18 | 49.922
2021-01-29 | 6:18 | 49.922
2021-01-29 | 6:18 | 49.923
2021-01-29 | 6:18 | 49.924
2021-01-29 | 6:18 | 49.924
2021-01-29 | 6:18 | 49.925
2021-01-29 | 6:18 | 49.925
2021-01-29 | 6:18 | 49.923
2021-01-29 | 6:18 | 49.923
2021-01-29 | 6:18 | 49.922
2021-01-29 | 6:18 | 49.923
2021-01-29 | 6:18 | 49.921
2021-01-29 | 6:18 | 49.922
2021-01-29 | 6:18 | 49.922
2021-01-29 | 6:18 | 49.92
2021-01-29 | 6:18 | 49.92
2021-01-29 | 6:18 | 49.918
2021-01-29 | 6:18 | 49.919
2021-01-29 | 6:18 | 49.917
2021-01-29 | 6:18 | 49.915
2021-01-29 | 6:18 | 49.914
2021-01-29 | 6:18 | 49.912
2021-01-29 | 6:18 | 49.912
2021-01-29 | 6:18 | 49.91
2021-01-29 | 6:18 | 49.908
2021-01-29 | 6:18 | 49.905
2021-01-29 | 6:18 | 49.904
2021-01-29 | 6:18 | 49.905
2021-01-29 | 6:18 | 49.908
2021-01-29 | 6:18 | 49.911
2021-01-29 | 6:18 | 49.914
2021-01-29 | 6:18 | 49.916
2021-01-29 | 6:18 | 49.916
2021-01-29 | 6:18 | 49.916
2021-01-29 | 6:18 | 49.916
2021-01-29 | 6:18 | 49.916
2021-01-29 | 6:18 | 49.917
2021-01-29 | 6:18 | 49.914
2021-01-29 | 6:18 | 49.915
2021-01-29 | 6:18 | 49.912
2021-01-29 | 6:18 | 49.908
2021-01-29 | 6:18 | 49.906
2021-01-29 | 6:18 | 49.905
2021-01-29 | 6:18 | 49.905
2021-01-29 | 6:18 | 49.905
2021-01-29 | 6:18 | 49.906
2021-01-29 | 6:18 | 49.908
2021-01-29 | 6:18 | 49.913
2021-01-29 | 6:18 | 49.915
2021-01-29 | 6:18 | 49.917
2021-01-29 | 6:18 | 49.916
2021-01-29 | 6:18 | 49.917
2021-01-29 | 6:18 | 49.914
2021-01-29 | 6:18 | 49.912
2021-01-29 | 6:18 | 49.912
2021-01-29 | 6:18 | 49.916
2021-01-29 | 6:18 | 49.916
2021-01-29 | 6:18 | 49.92
2021-01-29 | 6:18 | 49.923
2021-01-29 | 6:18 | 49.919
2021-01-29 | 6:19 | 49.913
2021-01-29 | 6:19 | 49.906
2021-01-29 | 6:19 | 49.9
2021-01-29 | 6:19 | 49.898
2021-01-29 | 6:19 | 49.897
2021-01-29 | 6:19 | 49.899
2021-01-29 | 6:19 | 49.901
2021-01-29 | 6:19 | 49.901
2021-01-29 | 6:19 | 49.904
2021-01-29 | 6:19 | 49.903
2021-01-29 | 6:19 | 49.902
2021-01-29 | 6:19 | 49.901
2021-01-29 | 6:19 | 49.901
2021-01-29 | 6:19 | 49.899
2021-01-29 | 6:19 | 49.897
2021-01-29 | 6:19 | 49.896
2021-01-29 | 6:19 | 49.894
2021-01-29 | 6:19 | 49.892
2021-01-29 | 6:19 | 49.893
2021-01-29 | 6:19 | 49.896
2021-01-29 | 6:19 | 49.898
2021-01-29 | 6:19 | 49.9
2021-01-29 | 6:19 | 49.902
2021-01-29 | 6:19 | 49.905
2021-01-29 | 6:19 | 49.909
2021-01-29 | 6:19 | 49.912
2021-01-29 | 6:19 | 49.914
2021-01-29 | 6:19 | 49.913
2021-01-29 | 6:19 | 49.911
2021-01-29 | 6:19 | 49.909
2021-01-29 | 6:19 | 49.907
2021-01-29 | 6:19 | 49.904
2021-01-29 | 6:19 | 49.905
2021-01-29 | 6:19 | 49.907
2021-01-29 | 6:19 | 49.908
2021-01-29 | 6:19 | 49.91
2021-01-29 | 6:19 | 49.912
2021-01-29 | 6:19 | 49.916
2021-01-29 | 6:19 | 49.917
2021-01-29 | 6:19 | 49.919
2021-01-29 | 6:19 | 49.924
2021-01-29 | 6:19 | 49.927
2021-01-29 | 6:19 | 49.928
2021-01-29 | 6:19 | 49.929
2021-01-29 | 6:19 | 49.931
2021-01-29 | 6:19 | 49.93
2021-01-29 | 6:19 | 49.931
2021-01-29 | 6:19 | 49.932
2021-01-29 | 6:19 | 49.932
2021-01-29 | 6:19 | 49.93
2021-01-29 | 6:19 | 49.927
2021-01-29 | 6:19 | 49.925
2021-01-29 | 6:19 | 49.923
2021-01-29 | 6:19 | 49.919
2021-01-29 | 6:19 | 49.914
2021-01-29 | 6:19 | 49.912
2021-01-29 | 6:19 | 49.912
2021-01-29 | 6:19 | 49.913
2021-01-29 | 6:19 | 49.915
2021-01-29 | 6:20 | 49.919
2021-01-29 | 6:20 | 49.921
2021-01-29 | 6:20 | 49.922
2021-01-29 | 6:20 | 49.92
2021-01-29 | 6:20 | 49.92
2021-01-29 | 6:20 | 49.925
2021-01-29 | 6:20 | 49.928
2021-01-29 | 6:20 | 49.934
2021-01-29 | 6:20 | 49.937
2021-01-29 | 6:20 | 49.938
2021-01-29 | 6:20 | 49.939
2021-01-29 | 6:20 | 49.941
2021-01-29 | 6:20 | 49.944
2021-01-29 | 6:20 | 49.944
2021-01-29 | 6:20 | 49.946
2021-01-29 | 6:20 | 49.947
2021-01-29 | 6:20 | 49.948
2021-01-29 | 6:20 | 49.946
2021-01-29 | 6:20 | 49.943
2021-01-29 | 6:20 | 49.941
2021-01-29 | 6:20 | 49.942
2021-01-29 | 6:20 | 49.943
2021-01-29 | 6:20 | 49.941
2021-01-29 | 6:20 | 49.941
2021-01-29 | 6:20 | 49.941
2021-01-29 | 6:20 | 49.942
2021-01-29 | 6:20 | 49.943
2021-01-29 | 6:20 | 49.944
2021-01-29 | 6:20 | 49.945
2021-01-29 | 6:20 | 49.945
2021-01-29 | 6:20 | 49.942
2021-01-29 | 6:20 | 49.941
2021-01-29 | 6:20 | 49.939
2021-01-29 | 6:20 | 49.936
2021-01-29 | 6:20 | 49.937
2021-01-29 | 6:20 | 49.937
2021-01-29 | 6:20 | 49.937
2021-01-29 | 6:20 | 49.938
2021-01-29 | 6:20 | 49.937
2021-01-29 | 6:20 | 49.937
2021-01-29 | 6:20 | 49.938
2021-01-29 | 6:20 | 49.939
2021-01-29 | 6:20 | 49.943
2021-01-29 | 6:20 | 49.945
2021-01-29 | 6:20 | 49.947
2021-01-29 | 6:20 | 49.95
2021-01-29 | 6:20 | 49.952
2021-01-29 | 6:20 | 49.954
2021-01-29 | 6:20 | 49.954
2021-01-29 | 6:20 | 49.954
2021-01-29 | 6:20 | 49.953
2021-01-29 | 6:20 | 49.951
2021-01-29 | 6:20 | 49.95
2021-01-29 | 6:20 | 49.946
2021-01-29 | 6:20 | 49.942
2021-01-29 | 6:20 | 49.94
2021-01-29 | 6:20 | 49.937
2021-01-29 | 6:20 | 49.938
2021-01-29 | 6:20 | 49.939
2021-01-29 | 6:20 | 49.94
2021-01-29 | 6:20 | 49.942
2021-01-29 | 6:21 | 49.944
2021-01-29 | 6:21 | 49.947
2021-01-29 | 6:21 | 49.95
2021-01-29 | 6:21 | 49.95
2021-01-29 | 6:21 | 49.951
2021-01-29 | 6:21 | 49.951
2021-01-29 | 6:21 | 49.949
2021-01-29 | 6:21 | 49.947
2021-01-29 | 6:21 | 49.942
2021-01-29 | 6:21 | 49.939
2021-01-29 | 6:21 | 49.937
2021-01-29 | 6:21 | 49.934
2021-01-29 | 6:21 | 49.932
2021-01-29 | 6:21 | 49.929
2021-01-29 | 6:21 | 49.93
2021-01-29 | 6:21 | 49.933
2021-01-29 | 6:21 | 49.936
2021-01-29 | 6:21 | 49.939
2021-01-29 | 6:21 | 49.941
2021-01-29 | 6:21 | 49.942
2021-01-29 | 6:21 | 49.944
2021-01-29 | 6:21 | 49.946
2021-01-29 | 6:21 | 49.947
2021-01-29 | 6:21 | 49.947
2021-01-29 | 6:21 | 49.946
2021-01-29 | 6:21 | 49.944
2021-01-29 | 6:21 | 49.94
2021-01-29 | 6:21 | 49.94
2021-01-29 | 6:21 | 49.939
2021-01-29 | 6:21 | 49.939
2021-01-29 | 6:21 | 49.937
2021-01-29 | 6:21 | 49.937
2021-01-29 | 6:21 | 49.936
2021-01-29 | 6:21 | 49.937
2021-01-29 | 6:21 | 49.94
2021-01-29 | 6:21 | 49.94
2021-01-29 | 6:21 | 49.939
2021-01-29 | 6:21 | 49.936
2021-01-29 | 6:21 | 49.936
2021-01-29 | 6:21 | 49.936
2021-01-29 | 6:21 | 49.933
2021-01-29 | 6:21 | 49.931
2021-01-29 | 6:21 | 49.929
2021-01-29 | 6:21 | 49.926
2021-01-29 | 6:21 | 49.926
2021-01-29 | 6:21 | 49.924
2021-01-29 | 6:21 | 49.923
2021-01-29 | 6:21 | 49.925
2021-01-29 | 6:21 | 49.925
2021-01-29 | 6:21 | 49.929
2021-01-29 | 6:21 | 49.93
2021-01-29 | 6:21 | 49.934
2021-01-29 | 6:21 | 49.94
2021-01-29 | 6:21 | 49.945
2021-01-29 | 6:21 | 49.947
2021-01-29 | 6:21 | 49.949
2021-01-29 | 6:21 | 49.952
2021-01-29 | 6:21 | 49.955
2021-01-29 | 6:21 | 49.957
2021-01-29 | 6:22 | 49.96
2021-01-29 | 6:22 | 49.959
2021-01-29 | 6:22 | 49.96
2021-01-29 | 6:22 | 49.96
2021-01-29 | 6:22 | 49.96
2021-01-29 | 6:22 | 49.959
2021-01-29 | 6:22 | 49.955
2021-01-29 | 6:22 | 49.948
2021-01-29 | 6:22 | 49.944
2021-01-29 | 6:22 | 49.941
2021-01-29 | 6:22 | 49.94
2021-01-29 | 6:22 | 49.94
2021-01-29 | 6:22 | 49.94
2021-01-29 | 6:22 | 49.942
2021-01-29 | 6:22 | 49.943
2021-01-29 | 6:22 | 49.943
2021-01-29 | 6:22 | 49.943
2021-01-29 | 6:22 | 49.945
2021-01-29 | 6:22 | 49.945
2021-01-29 | 6:22 | 49.948
2021-01-29 | 6:22 | 49.949
2021-01-29 | 6:22 | 49.948
2021-01-29 | 6:22 | 49.95
2021-01-29 | 6:22 | 49.951
2021-01-29 | 6:22 | 49.949
2021-01-29 | 6:22 | 49.95
2021-01-29 | 6:22 | 49.955
2021-01-29 | 6:22 | 49.954
2021-01-29 | 6:22 | 49.955
2021-01-29 | 6:22 | 49.955
2021-01-29 | 6:22 | 49.959
2021-01-29 | 6:22 | 49.961
2021-01-29 | 6:22 | 49.967
2021-01-29 | 6:22 | 49.973
2021-01-29 | 6:22 | 49.975
2021-01-29 | 6:22 | 49.976
2021-01-29 | 6:22 | 49.977
2021-01-29 | 6:22 | 49.977
2021-01-29 | 6:22 | 49.977
2021-01-29 | 6:22 | 49.976
2021-01-29 | 6:22 | 49.976
2021-01-29 | 6:22 | 49.973
2021-01-29 | 6:22 | 49.974
2021-01-29 | 6:22 | 49.975
2021-01-29 | 6:22 | 49.977
2021-01-29 | 6:22 | 49.978
2021-01-29 | 6:22 | 49.98
2021-01-29 | 6:22 | 49.981
2021-01-29 | 6:22 | 49.981
2021-01-29 | 6:22 | 49.98
2021-01-29 | 6:22 | 49.978
2021-01-29 | 6:22 | 49.974
2021-01-29 | 6:22 | 49.972
2021-01-29 | 6:22 | 49.971
2021-01-29 | 6:22 | 49.97
2021-01-29 | 6:22 | 49.972
2021-01-29 | 6:22 | 49.974
2021-01-29 | 6:22 | 49.973
2021-01-29 | 6:22 | 49.974
2021-01-29 | 6:22 | 49.974
2021-01-29 | 6:22 | 49.977
2021-01-29 | 6:23 | 49.978
2021-01-29 | 6:23 | 49.978
2021-01-29 | 6:23 | 49.977
2021-01-29 | 6:23 | 49.976
2021-01-29 | 6:23 | 49.977
2021-01-29 | 6:23 | 49.976
2021-01-29 | 6:23 | 49.975
2021-01-29 | 6:23 | 49.973
2021-01-29 | 6:23 | 49.973
2021-01-29 | 6:23 | 49.971
2021-01-29 | 6:23 | 49.97
2021-01-29 | 6:23 | 49.972
2021-01-29 | 6:23 | 49.973
2021-01-29 | 6:23 | 49.971
2021-01-29 | 6:23 | 49.97
2021-01-29 | 6:23 | 49.97
2021-01-29 | 6:23 | 49.969
2021-01-29 | 6:23 | 49.968
2021-01-29 | 6:23 | 49.968
2021-01-29 | 6:23 | 49.968
2021-01-29 | 6:23 | 49.968
2021-01-29 | 6:23 | 49.964
2021-01-29 | 6:23 | 49.962
2021-01-29 | 6:23 | 49.961
2021-01-29 | 6:23 | 49.958
2021-01-29 | 6:23 | 49.958
2021-01-29 | 6:23 | 49.957
2021-01-29 | 6:23 | 49.954
2021-01-29 | 6:23 | 49.952
2021-01-29 | 6:23 | 49.952
2021-01-29 | 6:23 | 49.951
2021-01-29 | 6:23 | 49.952
2021-01-29 | 6:23 | 49.955
2021-01-29 | 6:23 | 49.955
2021-01-29 | 6:23 | 49.954
2021-01-29 | 6:23 | 49.952
2021-01-29 | 6:23 | 49.952
2021-01-29 | 6:23 | 49.95
2021-01-29 | 6:23 | 49.95
2021-01-29 | 6:23 | 49.949
2021-01-29 | 6:23 | 49.946
2021-01-29 | 6:23 | 49.944
2021-01-29 | 6:23 | 49.943
2021-01-29 | 6:23 | 49.942
2021-01-29 | 6:23 | 49.946
2021-01-29 | 6:23 | 49.949
2021-01-29 | 6:23 | 49.951
2021-01-29 | 6:23 | 49.954
2021-01-29 | 6:23 | 49.956
2021-01-29 | 6:23 | 49.957
2021-01-29 | 6:23 | 49.952
2021-01-29 | 6:23 | 49.948
2021-01-29 | 6:23 | 49.943
2021-01-29 | 6:23 | 49.941
2021-01-29 | 6:23 | 49.938
2021-01-29 | 6:23 | 49.936
2021-01-29 | 6:23 | 49.937
2021-01-29 | 6:23 | 49.935
2021-01-29 | 6:23 | 49.934
2021-01-29 | 6:24 | 49.935
2021-01-29 | 6:24 | 49.935
2021-01-29 | 6:24 | 49.934
2021-01-29 | 6:24 | 49.934
2021-01-29 | 6:24 | 49.935
2021-01-29 | 6:24 | 49.939
2021-01-29 | 6:24 | 49.94
2021-01-29 | 6:24 | 49.942
2021-01-29 | 6:24 | 49.943
2021-01-29 | 6:24 | 49.945
2021-01-29 | 6:24 | 49.944
2021-01-29 | 6:24 | 49.944
2021-01-29 | 6:24 | 49.945
2021-01-29 | 6:24 | 49.948
2021-01-29 | 6:24 | 49.948
2021-01-29 | 6:24 | 49.947
2021-01-29 | 6:24 | 49.944
2021-01-29 | 6:24 | 49.94
2021-01-29 | 6:24 | 49.939
2021-01-29 | 6:24 | 49.939
2021-01-29 | 6:24 | 49.939
2021-01-29 | 6:24 | 49.94
2021-01-29 | 6:24 | 49.938
2021-01-29 | 6:24 | 49.941
2021-01-29 | 6:24 | 49.94
2021-01-29 | 6:24 | 49.938
2021-01-29 | 6:24 | 49.939
2021-01-29 | 6:24 | 49.938
2021-01-29 | 6:24 | 49.94
2021-01-29 | 6:24 | 49.941
2021-01-29 | 6:24 | 49.942
2021-01-29 | 6:24 | 49.941
2021-01-29 | 6:24 | 49.943
2021-01-29 | 6:24 | 49.94
2021-01-29 | 6:24 | 49.943
2021-01-29 | 6:24 | 49.944
2021-01-29 | 6:24 | 49.948
2021-01-29 | 6:24 | 49.948
2021-01-29 | 6:24 | 49.951
2021-01-29 | 6:24 | 49.954
2021-01-29 | 6:24 | 49.955
2021-01-29 | 6:24 | 49.958
2021-01-29 | 6:24 | 49.957
2021-01-29 | 6:24 | 49.957
2021-01-29 | 6:24 | 49.957
2021-01-29 | 6:24 | 49.958
2021-01-29 | 6:24 | 49.957
2021-01-29 | 6:24 | 49.954
2021-01-29 | 6:24 | 49.954
2021-01-29 | 6:24 | 49.954
2021-01-29 | 6:24 | 49.956
2021-01-29 | 6:24 | 49.957
2021-01-29 | 6:24 | 49.956
2021-01-29 | 6:24 | 49.954
2021-01-29 | 6:24 | 49.95
2021-01-29 | 6:24 | 49.946
2021-01-29 | 6:24 | 49.945
2021-01-29 | 6:24 | 49.946
2021-01-29 | 6:24 | 49.948
2021-01-29 | 6:24 | 49.951
2021-01-29 | 6:24 | 49.952
2021-01-29 | 6:25 | 49.956
2021-01-29 | 6:25 | 49.959
2021-01-29 | 6:25 | 49.963
2021-01-29 | 6:25 | 49.962
2021-01-29 | 6:25 | 49.962
2021-01-29 | 6:25 | 49.96
2021-01-29 | 6:25 | 49.958
2021-01-29 | 6:25 | 49.955
2021-01-29 | 6:25 | 49.953
2021-01-29 | 6:25 | 49.953
2021-01-29 | 6:25 | 49.95
2021-01-29 | 6:25 | 49.949
2021-01-29 | 6:25 | 49.95
2021-01-29 | 6:25 | 49.95
2021-01-29 | 6:25 | 49.952
2021-01-29 | 6:25 | 49.952
2021-01-29 | 6:25 | 49.951
2021-01-29 | 6:25 | 49.951
2021-01-29 | 6:25 | 49.953
2021-01-29 | 6:25 | 49.953
2021-01-29 | 6:25 | 49.956
2021-01-29 | 6:25 | 49.955
2021-01-29 | 6:25 | 49.954
2021-01-29 | 6:25 | 49.954
2021-01-29 | 6:25 | 49.951
2021-01-29 | 6:25 | 49.948
2021-01-29 | 6:25 | 49.95
2021-01-29 | 6:25 | 49.946
2021-01-29 | 6:25 | 49.947
2021-01-29 | 6:25 | 49.952
2021-01-29 | 6:25 | 49.953
2021-01-29 | 6:25 | 49.956
2021-01-29 | 6:25 | 49.959
2021-01-29 | 6:25 | 49.961
2021-01-29 | 6:25 | 49.961
2021-01-29 | 6:25 | 49.958
2021-01-29 | 6:25 | 49.956
2021-01-29 | 6:25 | 49.953
2021-01-29 | 6:25 | 49.949
2021-01-29 | 6:25 | 49.945
2021-01-29 | 6:25 | 49.942
2021-01-29 | 6:25 | 49.94
2021-01-29 | 6:25 | 49.938
2021-01-29 | 6:25 | 49.935
2021-01-29 | 6:25 | 49.935
2021-01-29 | 6:25 | 49.938
2021-01-29 | 6:25 | 49.938
2021-01-29 | 6:25 | 49.94
2021-01-29 | 6:25 | 49.939
2021-01-29 | 6:25 | 49.942
2021-01-29 | 6:25 | 49.942
2021-01-29 | 6:25 | 49.942
2021-01-29 | 6:25 | 49.942
2021-01-29 | 6:25 | 49.941
2021-01-29 | 6:25 | 49.938
2021-01-29 | 6:25 | 49.938
2021-01-29 | 6:25 | 49.935
2021-01-29 | 6:25 | 49.934
2021-01-29 | 6:25 | 49.932
2021-01-29 | 6:26 | 49.932
2021-01-29 | 6:26 | 49.933
2021-01-29 | 6:26 | 49.932
2021-01-29 | 6:26 | 49.931
2021-01-29 | 6:26 | 49.929
2021-01-29 | 6:26 | 49.929
2021-01-29 | 6:26 | 49.927
2021-01-29 | 6:26 | 49.926
2021-01-29 | 6:26 | 49.928
2021-01-29 | 6:26 | 49.929
2021-01-29 | 6:26 | 49.93
2021-01-29 | 6:26 | 49.933
2021-01-29 | 6:26 | 49.935
2021-01-29 | 6:26 | 49.935
2021-01-29 | 6:26 | 49.937
2021-01-29 | 6:26 | 49.935
2021-01-29 | 6:26 | 49.936
2021-01-29 | 6:26 | 49.937
2021-01-29 | 6:26 | 49.939
2021-01-29 | 6:26 | 49.94
2021-01-29 | 6:26 | 49.943
2021-01-29 | 6:26 | 49.944
2021-01-29 | 6:26 | 49.947
2021-01-29 | 6:26 | 49.948
2021-01-29 | 6:26 | 49.952
2021-01-29 | 6:26 | 49.951
2021-01-29 | 6:26 | 49.954
2021-01-29 | 6:26 | 49.957
2021-01-29 | 6:26 | 49.957
2021-01-29 | 6:26 | 49.958
2021-01-29 | 6:26 | 49.96
2021-01-29 | 6:26 | 49.96
2021-01-29 | 6:26 | 49.96
2021-01-29 | 6:26 | 49.962
2021-01-29 | 6:26 | 49.963
2021-01-29 | 6:26 | 49.965
2021-01-29 | 6:26 | 49.964
2021-01-29 | 6:26 | 49.963
2021-01-29 | 6:26 | 49.963
2021-01-29 | 6:26 | 49.962
2021-01-29 | 6:26 | 49.961
2021-01-29 | 6:26 | 49.957
2021-01-29 | 6:26 | 49.956
2021-01-29 | 6:26 | 49.955
2021-01-29 | 6:26 | 49.953
2021-01-29 | 6:26 | 49.951
2021-01-29 | 6:26 | 49.95
2021-01-29 | 6:26 | 49.95
2021-01-29 | 6:26 | 49.95
2021-01-29 | 6:26 | 49.952
2021-01-29 | 6:26 | 49.953
2021-01-29 | 6:26 | 49.957
2021-01-29 | 6:26 | 49.957
2021-01-29 | 6:26 | 49.96
2021-01-29 | 6:26 | 49.959
2021-01-29 | 6:26 | 49.962
2021-01-29 | 6:26 | 49.958
2021-01-29 | 6:26 | 49.958
2021-01-29 | 6:26 | 49.959
2021-01-29 | 6:26 | 49.96
2021-01-29 | 6:26 | 49.961
2021-01-29 | 6:27 | 49.963
2021-01-29 | 6:27 | 49.967
2021-01-29 | 6:27 | 49.969
2021-01-29 | 6:27 | 49.972
2021-01-29 | 6:27 | 49.971
2021-01-29 | 6:27 | 49.974
2021-01-29 | 6:27 | 49.973
2021-01-29 | 6:27 | 49.975
2021-01-29 | 6:27 | 49.975
2021-01-29 | 6:27 | 49.976
2021-01-29 | 6:27 | 49.976
2021-01-29 | 6:27 | 49.976
2021-01-29 | 6:27 | 49.972
2021-01-29 | 6:27 | 49.968
2021-01-29 | 6:27 | 49.966
2021-01-29 | 6:27 | 49.96
2021-01-29 | 6:27 | 49.952
2021-01-29 | 6:27 | 49.948
2021-01-29 | 6:27 | 49.944
2021-01-29 | 6:27 | 49.944
2021-01-29 | 6:27 | 49.941
2021-01-29 | 6:27 | 49.943
2021-01-29 | 6:27 | 49.945
2021-01-29 | 6:27 | 49.947
2021-01-29 | 6:27 | 49.947
2021-01-29 | 6:27 | 49.947
2021-01-29 | 6:27 | 49.95
2021-01-29 | 6:27 | 49.951
2021-01-29 | 6:27 | 49.952
2021-01-29 | 6:27 | 49.953
2021-01-29 | 6:27 | 49.953
2021-01-29 | 6:27 | 49.948
2021-01-29 | 6:27 | 49.942
2021-01-29 | 6:27 | 49.937
2021-01-29 | 6:27 | 49.933
2021-01-29 | 6:27 | 49.929
2021-01-29 | 6:27 | 49.928
2021-01-29 | 6:27 | 49.926
2021-01-29 | 6:27 | 49.925
2021-01-29 | 6:27 | 49.923
2021-01-29 | 6:27 | 49.922
2021-01-29 | 6:27 | 49.923
2021-01-29 | 6:27 | 49.922
2021-01-29 | 6:27 | 49.92
2021-01-29 | 6:27 | 49.921
2021-01-29 | 6:27 | 49.924
2021-01-29 | 6:27 | 49.928
2021-01-29 | 6:27 | 49.928
2021-01-29 | 6:27 | 49.927
2021-01-29 | 6:27 | 49.929
2021-01-29 | 6:27 | 49.93
2021-01-29 | 6:27 | 49.93
2021-01-29 | 6:27 | 49.931
2021-01-29 | 6:27 | 49.935
2021-01-29 | 6:27 | 49.934
2021-01-29 | 6:27 | 49.93
2021-01-29 | 6:27 | 49.93
2021-01-29 | 6:27 | 49.927
2021-01-29 | 6:27 | 49.927
2021-01-29 | 6:28 | 49.926
2021-01-29 | 6:28 | 49.924
2021-01-29 | 6:28 | 49.926
2021-01-29 | 6:28 | 49.927
2021-01-29 | 6:28 | 49.926
2021-01-29 | 6:28 | 49.924
2021-01-29 | 6:28 | 49.922
2021-01-29 | 6:28 | 49.921
2021-01-29 | 6:28 | 49.923
2021-01-29 | 6:28 | 49.925
2021-01-29 | 6:28 | 49.926
2021-01-29 | 6:28 | 49.93
2021-01-29 | 6:28 | 49.931
2021-01-29 | 6:28 | 49.931
2021-01-29 | 6:28 | 49.929
2021-01-29 | 6:28 | 49.927
2021-01-29 | 6:28 | 49.928
2021-01-29 | 6:28 | 49.927
2021-01-29 | 6:28 | 49.926
2021-01-29 | 6:28 | 49.926
2021-01-29 | 6:28 | 49.926
2021-01-29 | 6:28 | 49.93
2021-01-29 | 6:28 | 49.93
2021-01-29 | 6:28 | 49.931
2021-01-29 | 6:28 | 49.932
2021-01-29 | 6:28 | 49.931
2021-01-29 | 6:28 | 49.932
2021-01-29 | 6:28 | 49.932
2021-01-29 | 6:28 | 49.932
2021-01-29 | 6:28 | 49.927
2021-01-29 | 6:28 | 49.923
2021-01-29 | 6:28 | 49.921
2021-01-29 | 6:28 | 49.92
2021-01-29 | 6:28 | 49.92
2021-01-29 | 6:28 | 49.919
2021-01-29 | 6:28 | 49.915
2021-01-29 | 6:28 | 49.913
2021-01-29 | 6:28 | 49.909
2021-01-29 | 6:28 | 49.912
2021-01-29 | 6:28 | 49.916
2021-01-29 | 6:28 | 49.916
2021-01-29 | 6:28 | 49.922
2021-01-29 | 6:28 | 49.924
2021-01-29 | 6:28 | 49.927
2021-01-29 | 6:28 | 49.934
2021-01-29 | 6:28 | 49.934
2021-01-29 | 6:28 | 49.936
2021-01-29 | 6:28 | 49.933
2021-01-29 | 6:28 | 49.933
2021-01-29 | 6:28 | 49.934
2021-01-29 | 6:28 | 49.937
2021-01-29 | 6:28 | 49.933
2021-01-29 | 6:28 | 49.93
2021-01-29 | 6:28 | 49.93
2021-01-29 | 6:28 | 49.93
2021-01-29 | 6:28 | 49.932
2021-01-29 | 6:28 | 49.932
2021-01-29 | 6:28 | 49.934
2021-01-29 | 6:28 | 49.935
2021-01-29 | 6:28 | 49.935
2021-01-29 | 6:28 | 49.935
2021-01-29 | 6:29 | 49.937
2021-01-29 | 6:29 | 49.937
2021-01-29 | 6:29 | 49.939
2021-01-29 | 6:29 | 49.94
2021-01-29 | 6:29 | 49.94
2021-01-29 | 6:29 | 49.94
2021-01-29 | 6:29 | 49.937
2021-01-29 | 6:29 | 49.937
2021-01-29 | 6:29 | 49.935
2021-01-29 | 6:29 | 49.933
2021-01-29 | 6:29 | 49.933
2021-01-29 | 6:29 | 49.934
2021-01-29 | 6:29 | 49.934
2021-01-29 | 6:29 | 49.936
2021-01-29 | 6:29 | 49.936
2021-01-29 | 6:29 | 49.938
2021-01-29 | 6:29 | 49.937
2021-01-29 | 6:29 | 49.935
2021-01-29 | 6:29 | 49.936
2021-01-29 | 6:29 | 49.94
2021-01-29 | 6:29 | 49.945
2021-01-29 | 6:29 | 49.947
2021-01-29 | 6:29 | 49.949
2021-01-29 | 6:29 | 49.958
2021-01-29 | 6:29 | 49.962
2021-01-29 | 6:29 | 49.964
2021-01-29 | 6:29 | 49.967
2021-01-29 | 6:29 | 49.968
2021-01-29 | 6:29 | 49.968
2021-01-29 | 6:29 | 49.965
2021-01-29 | 6:29 | 49.964
2021-01-29 | 6:29 | 49.962
2021-01-29 | 6:29 | 49.96
2021-01-29 | 6:29 | 49.959
2021-01-29 | 6:29 | 49.959
2021-01-29 | 6:29 | 49.958
2021-01-29 | 6:29 | 49.959
2021-01-29 | 6:29 | 49.959
2021-01-29 | 6:29 | 49.96
2021-01-29 | 6:29 | 49.961
2021-01-29 | 6:29 | 49.967
2021-01-29 | 6:29 | 49.971
2021-01-29 | 6:29 | 49.976
2021-01-29 | 6:29 | 49.979
2021-01-29 | 6:29 | 49.98
2021-01-29 | 6:29 | 49.98
2021-01-29 | 6:29 | 49.977
2021-01-29 | 6:29 | 49.978
2021-01-29 | 6:29 | 49.976
2021-01-29 | 6:29 | 49.978
2021-01-29 | 6:29 | 49.98
2021-01-29 | 6:29 | 49.984
2021-01-29 | 6:29 | 49.988
2021-01-29 | 6:29 | 49.991
2021-01-29 | 6:29 | 49.995
2021-01-29 | 6:29 | 49.999
2021-01-29 | 6:29 | 50
2021-01-29 | 6:29 | 50.003
2021-01-29 | 6:29 | 50.004
2021-01-29 | 6:30 | 50.005
2021-01-29 | 6:30 | 50.006
2021-01-29 | 6:30 | 50.007
2021-01-29 | 6:30 | 50.007
2021-01-29 | 6:30 | 50.008
2021-01-29 | 6:30 | 50.009
2021-01-29 | 6:30 | 50.011
2021-01-29 | 6:30 | 50.015
2021-01-29 | 6:30 | 50.014
2021-01-29 | 6:30 | 50.016
2021-01-29 | 6:30 | 50.021
2021-01-29 | 6:30 | 50.021
2021-01-29 | 6:30 | 50.02
2021-01-29 | 6:30 | 50.019
2021-01-29 | 6:30 | 50.018
2021-01-29 | 6:30 | 50.015
2021-01-29 | 6:30 | 50.011
2021-01-29 | 6:30 | 50.009
2021-01-29 | 6:30 | 50.008
2021-01-29 | 6:30 | 50.003
2021-01-29 | 6:30 | 50.001
2021-01-29 | 6:30 | 50.001
2021-01-29 | 6:30 | 50.001
2021-01-29 | 6:30 | 50.002
2021-01-29 | 6:30 | 50.003
2021-01-29 | 6:30 | 50.005
2021-01-29 | 6:30 | 50.005
2021-01-29 | 6:30 | 50.005
2021-01-29 | 6:30 | 50.009
2021-01-29 | 6:30 | 50.011