## Slide 1: CMP326: Introducing a ‘Turbine Availability Factor’ for use in Frequency Response Capacity Calculation for Power Park Modules (PPMs)
11th December 2020
James Stone, NGESO

## Slide 2: Contents
1 | Background | 
2 | Introduction to the Defect | 
3 | Why is change required | 
4 | The Proposed Solution | 
5 | Terms of Reference | 

## Slide 3
Background
The Mandatory Services Agreement (MSA) between the ESO and a Power Station governs the provision of and payment for the service of Frequency Response referred to as ‘Mode A Frequency Response’
Under the CUSC, Power Stations can be instructed to provide Mode A Frequency Response as part of the MSA for which they are paid a ‘Holding Payment’ – this payment is made for the capability of the unit to provide response and reflects the fact that the site may be operating outside of normal conditions to provide balancing support
For each of the types of response capability a site can provide when instructed (Primary, Secondary and High Frequency Response), a Holding Payment is calculated using the Power Stations known response capability i.e. the change in power output the site is expected to achieve based on the ‘response capability tables’ (from compliance testing) at various levels of de-load
The key part of the Holding Payment calculation where this capability is reflected is the MW variable

## Slide 4: Introduction to the Defect - full turbine availability at site
The Current Situation
20 Turbines at 5MW each
De-Load | Primary | Secondary | High
0 | 0 | 0 | 15
10 | 10 | 10 | 15
20 | 15 | 20 | 15
30 | 15 | 25 | 15
… |  |  | 
90 | 15 | 25 | 0
De-loading by 10MW requires each turbine to reduce power output by 0.5MW*.
To provide 10MW of primary response all 20 turbines ramp up 0.5MW back to full load within 10 seconds.
Sites produce data for the response capability tables during NGESO compliance testing
*assuming the de-load volume is spread equally across all turbines

## Slide 5: Introduction to the Defect - reduced turbine availability
The Current Situation
De-Load | Primary | Secondary | High
20 | 15 | 20 | 20
When some turbines on site are unavailable the ramp rate of the remaining must be higher
All 20 turbines are available
10 turbines are unavailable
To achieve 20MW de-load all turbines reduce power output by 2MW.
To provide 15MW of primary response each turbine must ramp up 1.5MW in 10 seconds.
To achieve 20MW de-load all turbines reduce power output by 1MW.
To provide 15MW of primary response each turbine must ramp up 0.75MW in 10 seconds.

## Slide 6: Frequency Response capability test results
Windfarm compliance testing provides Frequency Response capability information for MSAs
The below real world test involved 2 PPMs at the same site:
PP1 41/45 turbines available (dark blue line) vs PP2 40/45 turbines available (light blue line)
Frequency Deviation -0.48Hz
Frequency Deviation +0.52Hz

## Slide 7: Frequency Response capability test results continued
The below real world test involved a PPM response test using 45 turbines vs 41
The test results for both sites demonstrate the theory that a site cannot achieve the expected change in power output when there are a number of turbines unavailable

## Slide 8: How common is turbine unavailability?
“For wind farms not in construction, the large majority have at least 90% of turbines operational 90% of the time”. ~ Recommendation for the Evaluation of Wind Farm Power Available Signal Accuracy, University of Strathclyde

## Slide 9
Why is change needed?
Without increasing the individual /second ramp rate of an individual turbine the example site cannot achieve the expected change in power output (based on the response capability tables) at 20MW de-load when 10 of the turbines are unavailable for response.
Real world compliance tests confirm levels of turbine availability do impact Frequency Response capabilities.
Currently sites with turbines unavailable for response mean the CUSC Section 4 Holding Payment calculation is overestimating their true response capability and therefore overpaying in these situations.
As the NGESO control room implements more projects which will enable a greater volume of wind to be instructed for Frequency Response the need to address the issue around accurate reflection of response capability in the holding payments will become greater.

## Slide 10: Proposed Solution
De-Load | Primary | Secondary | High
0 | 0 | 0 | 15
10 | 10 | 10 | 15
20 | 15 | 20 | 15
30 | 15 | 25 | 15
… |  |  | 
90 | 15 | 25 | 0
Pmw should never exceed the Pcap in the Holding Payment calculation.
Example using Primary Response
Worked Example*
All turbines are available
4 turbines are unavailable
10 turbines are unavailable
Introduce a cap on the MW element in the Holding Payment calculation to reflect reduced capability to ramp from de-loaded positions – this will be dependent on proportion of turbines available
* Uses example site with 20 Turbines at 5MW each

## Slide 11: Terms of Reference
In addition the Workgroup shall consider and report on the following specific issues:
Consider effect in terms of Frequency Containment Reserve (FCR) and Frequency Restoration Reserve (FRR); This change will ensure payments for MFR are reflective of site response capability which should generally open up the MFR market and support the ESO by increasing competition for procurement of balancing services
Consider evidence of Ramp Rate capability testing if available or desktop analysis if possible – as per slide 6-7
Does the proposal better facilitate achievement of the CUSC Objectives:
(a) The efficient discharge by the Licensee of the obligations imposed on it by the Act and the Transmission Licence; - Positive: Introducing a cap on the maximum response capability for PPMs based on the turbine availability will support the efficient discharge of the C16 license conditions as it will provide more accurate response capability data and allow the NGESO control room to make more efficient decisions in terms of which sites to instruct for MFR when balancing the system
(b) Facilitating effective competition in the generation and supply of electricity, and (so far as consistent therewith) facilitating such competition in the sale, distribution and purchase of electricity; - None
(c) Compliance with the Electricity Regulation and any relevant legally binding decision of the European Commission and/or the Agency; - None
(d) Promoting efficiency in the implementation and administration of the CUSC arrangements - Positive: updates the CUSC to reflect an accurate and true response capability meaning BSUoS payers will only be paying for actual holding capability