## Slide 1: Emergency and Restoration Code – Phase II Workgroup 4 – GC0148 5 October 2021

## Slide 2: Agenda
Review of Actions from the previous Meeting and general update
Status of E&R Phase I Proposals
Updated System Defence, System Restoration and Test Plans
Control Telephony Standard
Distributed Re-Start
Notification letter
Treatment of Non-CUSC Parties falling under E&R
Next steps Updates
AOB

## Slide 3: Actions
See Actions and Minutes following last meeting held on 18th August
  Check on approved Terms and Conditions with OFGEM and feedback to Work Group
  Circulate document on System Defence Plan and System Restoration Plan and Test Plan to Work Group – Completed – see later slides and documents circulated in advance of meeting
  Control Telephony Standard – Comments from Workgroup sought. Some internal ESO Comments received highlighted in Slide Pack
  Circulate the following Distributed Re-Start documents (Completed)
(a) Functional specification for operational telecoms including resilience requirements
(b) Information on the Distributed ReStart Controller
  Article 40(E&R) Paragraphs 2d,2e (1,2,3). How are these discharged in terms of the Distributed Restart Work and GC0148? (Ongoing)
  E&R Notification: What is ESO doing to notify SGU’s on E&R currently? – Updated draft letter prepared and circulated in advance of the meeting.
  See also ongoing actions (Ref Copy of Action Tracker - GC0148_AJ051021)

## Slide 4: Status of E&R Phase I Proposals
Article No. | NCER documents | Status | Date submitted (Issue number)
Article 4.2a) | T&Cs for Defence providers | Approved 13th July 2021 | 20/12/2019 (Issue 3)
Article 4.2b) | T&Cs for Restoration providers |  | 
Article 4.2c) | List of SGUs (submitted as appendix to SDP and SRP) | Approved 13th July 2021 | 20/12/2019 (Issue 3)
Article 4.2d) | High priority SGUs ((submitted as appendix to SDP and SRP) | Approved 13th July 2021 | 20/12/2019 (Issue 3)
Article 4.2e) | Market Suspension and Restoration rules with intermediate methodology | Approved 11th June 2021 | 21/01/2020 (Issue 3)
Article 4.2f) | Imbalance settlement rules for suspension of activities |  | 
Article 4.2g) | Test plan | Approved 13th July 2021 | 20/12/2019 (Issue 1)
Article 4.5) | System Defence plan | Approval not required by Ofgem, but NGESO should notify Ofgem of any changes | 20/12/2019 (Issue 3 – Issue 4 will reflect recent updates)
Article 4.5) | System Restoration plan | Approval not required by Ofgem, but NGESO should notify Ofgem of any changes | 
Link to publications on NGESO website (decision letters also published):
https://www.nationalgrideso.com/industry-information/codes/european-network-codes/other-enc-documents

## Slide 5: Key Updates to System Defence Plan (Issue 4)
Added version control to reflect updates made
Clarified that Ofgem does not need to approve the System Defence Plan, however, NGESO will notify them of any changes made.
EU Exit reference - Most of the EU NCER code has been retained via the SIs, so the requirements will largely apply unchanged.
Refresh of document to reflect Grid Code updates (GC0096, GC0125, GC0127, GC0128 and GC0147) and approval of SGU list, T&Cs and Test Plan. Refences to the GC modifications have been removed and new references added the Grid Code clauses as they are now approved and part of the Grid Code
Added a section on ‘Manual Generation Disconnection’ to reflect GC0147 outcome (ODFM and Emergency Disconnection of Embedded Generation implemented) and other disconnection services.
Obligations on non-CUSC parties added to Appendix A: GB Parties within the scope of the System Defence Plan?
Updates to System Defence Plan providing linkage to the Test Plan including Assurance and Compliance Testing
NB - The System Defence Plan will need to be updated again to reflect E&R Phase 2 changes (GC0148). This has been outlined in the plan as a future change.

## Slide 6: Key Updates to System Restoration Plan (Issue 4)
Added version control to reflect updates made
Ofgem does not need to approve the System Restoration Plan, however, NGESO will notify them of any changes made.
EU Exit reference - Most of the EU NCER code has been retained via the SIs, so the requirements will largely apply unchanged.
Refresh of document to reflect Grid Code updates (GC0096, GC0125, GC0127, GC0128 and GC0144) and approval of SGU list, T&Cs and Test Plan. Refences to the GC modifications have been removed as they are now approved and part of the Grid Code
Following the SGU approval, NGESO will notify affected parties of their obligations (via a notification letter, attached for comments/review). These updates are reflected in section 6 of the System Restoration Plan.
Corrected Appendix A: GB Parties within the scope of the System Restoration Plan
NB - The System Restoration Plan will need to be updated again to reflect E&R Phase 2 changes (GC0148).

## Slide 7: Key Updates to Test Plan (Issue 2)
Added version control to reflect updates made
EU Exit reference - Most of the EU NCER code has been retained via the SIs, so the requirements will largely apply unchanged.
Test Plan now referenced in the System Defence Plan relating to Compliance and Assurance
NB - The Test Plan will need to be updated again to reflect E&R Phase 2 changes (GC0148).

## Slide 8: Control Telephony Standard
Additional comments from within the ESO received include:-
  Priority Call – Control Call, initiated by the ENCC or TNCC using the priority feature of their telephony terminals. On encountering congestion a priority control call will disconnect calls of a lower priority
A Routine Control Call will not override of an Admin Call but will ring the bell (plus beep in the ear) to alert of another call
A Priority Control Call will override an Admin Call on Network Congestion and if the Control Point Phone is busy.
A Priority Call will not override a Routine control Call but will ring the bell (plus beep in the ear) to alert of another call
An Emergency Call to a Control Point will override Admin, Routine and Priority Calls on congestion and will disconnect the existing call and start to ring once handset is replaced. This will also disconnect the call if the Control Point Phone is busy.
An Emergency Call to the Control Room will override Admin, Routine and Priority Calls on congestion.
In Section 5&6 Should there be a comment on the Orange phone in the event of there being and ESO and ETO handset?
In Section 6, The Bell will ring continuously and the phone will ring normal cadence at the same time
An emergency Call to a Blackstart Phone (LJRP) will Ring the Phone and Bell with a Burst ring to differentiate it from Admin (Normal), or Control Call (Continuous).
An Emergency Call from a Control Phone to the Control Room is a special alert on the Turrets.
No Emergency Call take place to a (non-blackstart) Control Phone at a substation
Comments requested from other Workgroup members before a new version is issued for comment

## Slide 9: Distributed Re-Start
Good progress being made on drafting
Grid Code and Distribution Code drafting well advanced with only minor updates and consistency checks being made ahead of sharing with the workgroup
Copies of the following documents can be accessed from the links below
  Organisational Systems and Telecommunications Design Stage II Report, section 4 contains the functional specification for operational telecommunications including resilience requirements.
  Organisational Systems and Telecommunications Design Stage I Report, section 9 contains information on the Distributed ReStart Zone Controller – but this is not the functional specification. The functional specification for the controller will not be published until February next year.
Initial high level work started on the STC Drafting noting that this falls outside the governance of GC0148 and is STC Panel issue
A detailed report on Distributed Re-Start is due to be issued later in the year which will be issued by the Distributed Re-Start Project team

## Slide 10: Notification Letter
A draft notification letter was prepared in August 2019 and shared with Workgroup Members
Following approval of the SGU list and Terms and Conditions, the ESO is now in a position to formally notify parties (ie those who are listed in Appendix A of the System Defence and System Restoration Plan) who will fall under the requirements of the Emergency and Restoration Code
An updated draft notification letter (dated September 2021) has been prepared and circulated to Workgroup members ahead of this meeting.
Views sought from the Workgroup on the draft notification letter before formal issue.

## Slide 11: Treatment of Non-CUSC Parties falling under E&R
The System Defence and System Restoration Plan (Appendix A) detail the SGU’s (Significant Grid User’s) who will fall under the auspices of the EU Emergency and Restoration Code
As part of the GC0148 Workgroup a requirement under the “Terms of Reference” would be to establish how smaller Non-CUSC Parties could be caught under the EU Emergency and Restoration Code
  Contractual arrangements with the provider – Distributed Re-Start would be an example where a party providing an Anchor Plant (Black Start) Capability or indeed a “Top Up Service” would be caught under the Emergency and Restoration Code.
  This would equally apply to other contracts where there is a need to provide a defence of restoration measure
  The Table in Appendix A of the System Defence Plan and System Restoration Plan has been updated to reflect this.

## Slide 12: Next Steps
Progress outstanding actions in particular
  Treatment of netted demand under LFDD, legal interpretation and interaction with DNO’s – E-Mail sent to Carl Henshaw to understand DNO thinking.
  Legal interpretation of way forward still under consideration
  Develop legal drafting for Storage based on GC0127 Alternative, European Expert Storage Group and Distribution Code Storage consultation – Ongoing – will be circulated to Workgroup when available.
  Mapping table
    Placed on hold temporarily until further certainty has been gained in respect of specific areas.