## Version History
Version | Details
1 | This file only contains the reporting associated with CG151 for November 2021. Going forward this will be included in the combined system incident reporting for both GC105 and GC151
2 | This file contains both the reporting associated with GC105 and GC151 for November 2021.

## Notes
Subject | Notes
RoCoF | RoCoF=(frequency_500ms - frequency_0ms)/500ms RoCoF is calculated using 500ms sliding window. Note that smaller losses will have less accurate ROCOF calculations The RoCoF figure in this report is from external service
System Inertia | Monitoring which transmission-connected generators are running and adding an estimate of inertia from embedded generation and demand
Data 'N/A' | N/A: data not applicable or potentially unreliable. For example, there maybe events when the loss of infeed or exfeed is not instantaneous (over long time period), the calculated RoCoF may not be indicative. For some events, during a disturbance the data may potentially be unreliable. NGESO will apply engineering judgement to determine whether the derived/calculated data is suitable for sharing.

## Transmission Faults (GC0151)
Location | Network Operator | Date Time | Voltage Trace (Refer to sheet) | Notes
Peterhead 275kV S/S Mesh Corner 1 | SHETL | 2021-11-02 04:15
Cowley - Culham Jet - Didcot | NGET | 2021-11-02 18:32
Redmoss GT2 275kV | SHETL | 2021-11-03 19:59
Blackhillock 275/132KV SGT4 | SHETL | 2021-11-04 12:53
Feckenham SVC6 | NGET | 2021-11-04 18:12
East Claydon 132kV Bus Coupler 1 | NGET | 2021-11-05 06:23 |  | Forced trip (CB was already in open position)
Tealing 275KV SVC | SHETL | 2021-11-10 12:03
Bramford - Norwich Main 2 | NGET | 2021-11-10 19:53
Peterhead 275kV CB L45 | SHETL | 2021-11-11 19:18
Richborough DRC5 | NGET | 2021-11-12 07:12
Chesterfield - High Marnham 2 | NGET | 2021-11-12 17:47 |  | Tripped during return to service
Errochty - Tummel no.1 132kV (ME1) Circuit | SHETL | 2021-11-12 20:17
Fort Augustus 400/132kV SGT5 | SHETL | 2021-11-13 22:24 | V20211113-1
Bolney DRC6 | NGET | 2021-11-15 14:26
Kirkby 132kV MSC3B | NGET | 2021-11-16 12:07
Mannington SVC1 | NGET | 2021-11-16 13:57
Pelham - Waltham Cross 2 | NGET | 2021-11-17 18:20 |  | Tripped during return to service
Spittal 275kV H14 G1 | SHETL | 2021-11-18 03:04
Nursling 132/33kV T1 | NGET | 2021-11-25 15:42
Kingsnorth SGT1 and SR1 | NGET | 2021-11-26 03:39
Blackhillock - Kintore 275KV cct XH1 | SHETL | 2021-11-26 15:59 |  | Storm Arwen related
Blackhillock - Kintore 275KV cct XH1 | SHETL | 2021-11-26 16:05 |  | Storm Arwen related
Kintore - Dyce 132KV cct XPS | SHETL | 2021-11-26 16:17 |  | Storm Arwen related
Kintore - Craigiebuckler 132KV cct XCN | SHETL | 2021-11-26 16:43 |  | Storm Arwen related
Blackhillock - Macduff 132KV cct HMN | SHETL | 2021-11-26 16:44 |  | Storm Arwen related
Blackhillock - Macduff 132KV cct HMN | SHETL | 2021-11-26 16:44 |  | Storm Arwen related
Kincardine (old) - Fetteresso 275kV | SPT | 2021-11-26 16:51 |  | Storm Arwen related
Fettereso - Kincardine 275Kv cct SY2/YZ2 | SHETL | 2021-11-26 16:51 |  | Storm Arwen related
Kintore - Craigiebuckler 132KV cct XCN | SHETL | 2021-11-26 16:58 |  | Storm Arwen related
Craigiebuckler - Fiddes - Tarland 132KV cct CF / CLS | SHETL | 2021-11-26 16:59 |  | Storm Arwen related
Kintore - Craigiebuckler - tarland 132KV cct XCW / CLN | SHETL | 2021-11-26 17:13 |  | Storm Arwen related
New Deer - Rothienorman 275KV cct NDR1 | SHETL | 2021-11-26 17:33 |  | Storm Arwen related
Craigiebuckler - Fiddes - Tarland 132KV cct CF / CLS | SHETL | 2021-11-26 17:46 |  | Storm Arwen related
Errochty - Griffin - Burghmuir 132KV cct EG1 GP1 | SHETL | 2021-11-26 19:39 |  | Storm Arwen related
Harker - Hutton 1 | NGET | 2021-11-26 19:43 |  | Storm Arwen related
Torness - Crystal Rig 400kV | SPT | 2021-11-26 20:30 |  | Storm Arwen related
Killin Inverarnan NL1 132kV | SHETL | 2021-11-26 21:04 |  | Storm Arwen related
Errochty Griffin Burghmuir 132kV EG1/GP1 | SHETL | 2021-11-26 21:20 |  | Storm Arwen related
Smeaton - Fallago 400kV | SPT | 2021-11-26 21:23 |  | Storm Arwen related
Errochty Griffin Burghmuir 132kV EG1/GP1 | SHETL | 2021-11-26 21:23 |  | Storm Arwen related
Harker - Hutton 1 | NGET | 2021-11-26 22:06 |  | Storm Arwen related
Smeaton - Fallago 400kV | SPT | 2021-11-26 22:17 |  | Storm Arwen related
Harker - Hutton 1 | NGET | 2021-11-26 22:30 |  | Storm Arwen related
Connahs Quay - Capenhurst 1 | NGET | 2021-11-26 22:55 |  | Storm Arwen related
Connahs Quay - Bodelwyddan - Pentir 2 | NGET | 2021-11-26 22:58 |  | Storm Arwen related
Connahs Quay - Bodelwyddan - Pentir 2 | NGET | 2021-11-26 22:59 |  | Storm Arwen related
Smeaton - Fallago 400kV | SPT | 2021-11-26 23:12 |  | Storm Arwen related
Connahs Quay - Capenhurst 1 | NGET | 2021-11-26 23:13 |  | Storm Arwen related
Connahs Quay - Capenhurst 1 | NGET | 2021-11-26 23:15 |  | Storm Arwen related
Connahs Quay - Bodelwyddan - Pentir 2 | NGET | 2021-11-27 00:29 |  | Storm Arwen related
Errochty Griffin EG1 CIRCUIT | SHETL | 2021-11-27 02:04 |  | Storm Arwen related
Eggborough - Rochdale, Rochdale SGT3 | NGET | 2021-11-27 02:18 |  | Storm Arwen related
Blyth SGT2A | NGET | 2021-11-27 02:29 |  | Storm Arwen related
Eggborough - Rochdale, Rochdale SGT3 | NGET | 2021-11-27 02:32 |  | Storm Arwen related
Eggborough - Rochdale, Rochdale SGT3 | NGET | 2021-11-27 02:49 |  | Storm Arwen related
Eggborough - Rochdale, Rochdale SGT3 | NGET | 2021-11-27 02:54 |  | Storm Arwen related
Rochdale - Stalybridge, Rochdale SGT2 | NGET | 2021-11-27 02:54 |  | Storm Arwen related
Eggborough - Rochdale, Rochdale SGT3 | NGET | 2021-11-27 02:58 |  | Storm Arwen related
Rochdale - Stalybridge, Rochdale SGT2 | NGET | 2021-11-27 03:00 |  | Storm Arwen related
Elland - Stalybridge, Elland SGT4 | NGET | 2021-11-27 03:00 |  | Storm Arwen related
Eggborough - Rochdale, Rochdale SGT3 | NGET | 2021-11-27 03:11 |  | Storm Arwen related
Rochdale - Stalybridge, Rochdale SGT2 | NGET | 2021-11-27 03:11 |  | Storm Arwen related
Eggborough - Rochdale, Rochdale SGT3 | NGET | 2021-11-27 03:14 |  | Storm Arwen related
Rochdale - Stalybridge, Rochdale SGT2 | NGET | 2021-11-27 03:14 |  | Storm Arwen related
Rochdale - Stalybridge, Rochdale SGT2 | NGET | 2021-11-27 03:36 |  | Storm Arwen related
Elland - Stalybridge, Elland SGT4 | NGET | 2021-11-27 03:37 |  | Storm Arwen related
Elland - Stalybridge, Elland SGT4 | NGET | 2021-11-27 04:11 |  | Storm Arwen related
Eggborough - Rochdale, Rochdale SGT3 | NGET | 2021-11-27 04:16 |  | Storm Arwen related
Rochdale - Stalybridge, Rochdale SGT2 | NGET | 2021-11-27 04:16 |  | Storm Arwen related
Eggborough - Rochdale, Rochdale SGT3 | NGET | 2021-11-27 04:17 |  | Storm Arwen related
Rochdale - Stalybridge, Rochdale SGT2 | NGET | 2021-11-27 04:17 |  | Storm Arwen related
Eggborough - Rochdale, Rochdale SGT3 | NGET | 2021-11-27 04:40 |  | Storm Arwen related
Rochdale - Stalybridge, Rochdale SGT2 | NGET | 2021-11-27 04:40 |  | Storm Arwen related
Eggborough - Rochdale, Rochdale SGT3 | NGET | 2021-11-27 04:45 |  | Storm Arwen related
Rochdale - Stalybridge, Rochdale SGT2 | NGET | 2021-11-27 04:45 |  | Storm Arwen related
Wylfa SGT3 | NGET | 2021-11-28 04:56
Connahs Quay - Bodelwyddan - Pentir 2 | NGET | 2021-11-28 12:13
Connahs Quay - Bodelwyddan - Pentir 2 | NGET | 2021-11-28 12:23
Cockenzie - Eccles 400kV | SPT | 2021-11-29 19:02
Richborough DRC5 | NGET | 2021-11-30 01:56

## System Incidents (GC0105)
|  |  | Date and time of the incident | System frequency trace (1-second interval) for the incident | System frequency immediately before the incident | System frequency immediately after the incident | Maximum/Minimum rate of change of frequency (RoCoF) of the incident | System inertia at the time of the incident | Where known, MW trip/loss of all generation/ interconnection related to the incident |  | Where known, MW trip/loss of all Embedded Generation(EG) related to the incident | Where known, MW trip/loss of all DNO demand related to the incident; | Transmission fault associated with the incident; | Any transient voltage dip (loss % and duration) at the local substation associated with the incident | Any other data to gain a clearer understanding of the incident and its potential implications
Reference | Name | Notes | Date Time | System Frequency (Refer to sheet) | Pre-Event Frequency (Hz) | Post-Event Frequency (Hz) | RoCoF (Hz/s) | System Inertia (GVAs) | Generation/Interconnection (MW) |  | EG (MW) | Demand (MW) | Transmission fault | Voltage Dip | Additional data
20211103-1 | Frequency excursion to 50.31Hz |  | 2021-11-03 07:00 | F20211103-1 | 50.228 | 50.308 | 0.0084857 | 309
20211103-2 | Deload of WBURB-1 |  | 2021-11-03 07:03 | F20211103-2 | 49.97 | 49.815 | -0.026557 | 309 | WBURB-1 | -400
20211105-2 | Trip of WBURB-1 |  | 2021-11-05 05:49 | F20211105-2 | 50.092 | 50.007 | -0.014282 | 217 | WBURB-1 | -262
20211109-1 | Trip of NSL |  | 2021-11-09 17:28 | F20211109-1 | 50.028 | 49.744 | -0.065484 | 317 | NSL | -700
20211119-1 | Trip of Triton Knoll |  | 2021-11-19 10:10 | F20211119-1 | 50.079 | 49.986 | -0.028538 | 268 |  | -300
20211119-2 | Trip of IFA |  | 2021-11-19 10:19 | F20211119-2 | 50.021 | 50.268 | 0.090547 | 268 | IFA | 1000
20211119-3 | Trip of SCCL-1 |  | 2021-11-19 15:36 | F20211119-3 | 50.059 | 49.941 | -0.031433 | 285 | SCCL-1 | -335
20211125-1 | Trip of WBURB-1 |  | 2021-11-25 18:40 | F20211125-1 | 49.943 | 49.83 | -0.02527 | 334 | WBURB-1 | 343
20211127-1 | Trip of CARR-2 |  | 2021-11-27 07:15 | F20211127-1 | 50.061 | 49.908 | -0.066843 | 211 | CARR-2 | -400
20211127-2 | Trip of CNQPS-3 |  | 2021-11-27 09:40 | F20211127-2 | 49.964 | 49.881 | -0.037896 | 229 | CNQPS-3 | -330
20211129-1 | Trip of WBURB-3 |  | 2021-11-29 17:32 | F20211129-1 | 49.966 | 49.826 | -0.027213 | 335 | WBURB-3 | -430

## V20211113-1
| Date | Time | Time in S | V1(V) | V2(V) | V3(V)
8695 | 2021-11-13 | 22:24 | 11.5 | 75693 | 75803 | 75875
8696 | 2021-11-13 | 22:24 | 11.5 | 75692 | 75803 | 75876
8697 | 2021-11-13 | 22:24 | 11.5001 | 75691 | 75803 | 75877
8698 | 2021-11-13 | 22:24 | 11.5001 | 75690 | 75803 | 75878
8699 | 2021-11-13 | 22:24 | 11.5001 | 75690 | 75802 | 75879
8700 | 2021-11-13 | 22:24 | 11.5001 | 75689 | 75802 | 75880
8701 | 2021-11-13 | 22:24 | 11.5002 | 75688 | 75802 | 75881
8702 | 2021-11-13 | 22:24 | 11.5002 | 75687 | 75802 | 75882
8703 | 2021-11-13 | 22:24 | 11.5002 | 75686 | 75802 | 75883
8704 | 2021-11-13 | 22:24 | 11.5003 | 75685 | 75802 | 75884
8705 | 2021-11-13 | 22:24 | 11.5003 | 75684 | 75802 | 75885
8706 | 2021-11-13 | 22:24 | 11.5003 | 75683 | 75802 | 75886
8707 | 2021-11-13 | 22:24 | 11.5003 | 75682 | 75802 | 75887
8708 | 2021-11-13 | 22:24 | 11.5004 | 75681 | 75802 | 75888
8709 | 2021-11-13 | 22:24 | 11.5004 | 75680 | 75802 | 75890
8710 | 2021-11-13 | 22:24 | 11.5004 | 75679 | 75803 | 75891
8711 | 2021-11-13 | 22:24 | 11.5005 | 75678 | 75803 | 75892
8712 | 2021-11-13 | 22:24 | 11.5005 | 75677 | 75803 | 75892
8713 | 2021-11-13 | 22:24 | 11.5005 | 75676 | 75803 | 75893
8714 | 2021-11-13 | 22:24 | 11.5005 | 75675 | 75803 | 75894
8715 | 2021-11-13 | 22:24 | 11.5006 | 75674 | 75804 | 75895
8716 | 2021-11-13 | 22:24 | 11.5006 | 75673 | 75804 | 75896
8717 | 2021-11-13 | 22:24 | 11.5006 | 75672 | 75804 | 75896
8718 | 2021-11-13 | 22:24 | 11.5007 | 75671 | 75805 | 75897
8719 | 2021-11-13 | 22:24 | 11.5007 | 75670 | 75805 | 75898
8720 | 2021-11-13 | 22:24 | 11.5007 | 75669 | 75806 | 75899
8721 | 2021-11-13 | 22:24 | 11.5008 | 75667 | 75806 | 75900
8722 | 2021-11-13 | 22:24 | 11.5008 | 75666 | 75806 | 75900
8723 | 2021-11-13 | 22:24 | 11.5008 | 75665 | 75807 | 75901
8724 | 2021-11-13 | 22:24 | 11.5008 | 75664 | 75807 | 75902
8725 | 2021-11-13 | 22:24 | 11.5009 | 75663 | 75808 | 75902
8726 | 2021-11-13 | 22:24 | 11.5009 | 75662 | 75808 | 75902
8727 | 2021-11-13 | 22:24 | 11.5009 | 75661 | 75809 | 75903
8728 | 2021-11-13 | 22:24 | 11.501 | 75660 | 75810 | 75904
8729 | 2021-11-13 | 22:24 | 11.501 | 75659 | 75810 | 75905
8730 | 2021-11-13 | 22:24 | 11.501 | 75658 | 75811 | 75905
8731 | 2021-11-13 | 22:24 | 11.501 | 75657 | 75811 | 75906
8732 | 2021-11-13 | 22:24 | 11.5011 | 75656 | 75812 | 75906
8733 | 2021-11-13 | 22:24 | 11.5011 | 75655 | 75813 | 75907
8734 | 2021-11-13 | 22:24 | 11.5011 | 75654 | 75813 | 75907
8735 | 2021-11-13 | 22:24 | 11.5012 | 75652 | 75814 | 75908
8736 | 2021-11-13 | 22:24 | 11.5012 | 75651 | 75814 | 75908
8737 | 2021-11-13 | 22:24 | 11.5012 | 75650 | 75815 | 75908
8738 | 2021-11-13 | 22:24 | 11.5012 | 75649 | 75816 | 75909
8739 | 2021-11-13 | 22:24 | 11.5013 | 75648 | 75816 | 75909
8740 | 2021-11-13 | 22:24 | 11.5013 | 75647 | 75817 | 75909
8741 | 2021-11-13 | 22:24 | 11.5013 | 75646 | 75818 | 75909
8742 | 2021-11-13 | 22:24 | 11.5014 | 75645 | 75819 | 75909
8743 | 2021-11-13 | 22:24 | 11.5014 | 75644 | 75819 | 75910
8744 | 2021-11-13 | 22:24 | 11.5014 | 75643 | 75820 | 75910
8745 | 2021-11-13 | 22:24 | 11.5014 | 75642 | 75821 | 75910
8746 | 2021-11-13 | 22:24 | 11.5015 | 75641 | 75822 | 75910
8747 | 2021-11-13 | 22:24 | 11.5015 | 75640 | 75823 | 75910
8748 | 2021-11-13 | 22:24 | 11.5015 | 75639 | 75824 | 75910
8749 | 2021-11-13 | 22:24 | 11.5016 | 75638 | 75825 | 75910
8750 | 2021-11-13 | 22:24 | 11.5016 | 75637 | 75826 | 75910
8751 | 2021-11-13 | 22:24 | 11.5016 | 75636 | 75827 | 75910
8752 | 2021-11-13 | 22:24 | 11.5016 | 75635 | 75828 | 75909
8753 | 2021-11-13 | 22:24 | 11.5017 | 75634 | 75829 | 75909
8754 | 2021-11-13 | 22:24 | 11.5017 | 75633 | 75830 | 75909
8755 | 2021-11-13 | 22:24 | 11.5017 | 75632 | 75831 | 75909
8756 | 2021-11-13 | 22:24 | 11.5018 | 75631 | 75832 | 75908
8757 | 2021-11-13 | 22:24 | 11.5018 | 75630 | 75833 | 75908
8758 | 2021-11-13 | 22:24 | 11.5018 | 75629 | 75834 | 75907
8759 | 2021-11-13 | 22:24 | 11.5018 | 75628 | 75835 | 75907
8760 | 2021-11-13 | 22:24 | 11.5019 | 75627 | 75836 | 75906
8761 | 2021-11-13 | 22:24 | 11.5019 | 75627 | 75838 | 75906
8762 | 2021-11-13 | 22:24 | 11.5019 | 75626 | 75839 | 75905
8763 | 2021-11-13 | 22:24 | 11.502 | 75625 | 75840 | 75905
8764 | 2021-11-13 | 22:24 | 11.502 | 75624 | 75841 | 75904
8765 | 2021-11-13 | 22:24 | 11.502 | 75624 | 75843 | 75904
8766 | 2021-11-13 | 22:24 | 11.502 | 75623 | 75844 | 75903
8767 | 2021-11-13 | 22:24 | 11.5021 | 75622 | 75845 | 75902
8768 | 2021-11-13 | 22:24 | 11.5021 | 75622 | 75847 | 75901
8769 | 2021-11-13 | 22:24 | 11.5021 | 75621 | 75848 | 75901
8770 | 2021-11-13 | 22:24 | 11.5022 | 75620 | 75849 | 75900
8771 | 2021-11-13 | 22:24 | 11.5022 | 75620 | 75851 | 75899
8772 | 2021-11-13 | 22:24 | 11.5022 | 75619 | 75852 | 75899
8773 | 2021-11-13 | 22:24 | 11.5022 | 75619 | 75853 | 75898
8774 | 2021-11-13 | 22:24 | 11.5023 | 75618 | 75854 | 75898
8775 | 2021-11-13 | 22:24 | 11.5023 | 75618 | 75855 | 75897
8776 | 2021-11-13 | 22:24 | 11.5023 | 75617 | 75857 | 75896
8777 | 2021-11-13 | 22:24 | 11.5024 | 75617 | 75858 | 75896
8778 | 2021-11-13 | 22:24 | 11.5024 | 75617 | 75859 | 75895
8779 | 2021-11-13 | 22:24 | 11.5024 | 75616 | 75860 | 75894
8780 | 2021-11-13 | 22:24 | 11.5024 | 75616 | 75861 | 75893
8781 | 2021-11-13 | 22:24 | 11.5025 | 75616 | 75862 | 75893
8782 | 2021-11-13 | 22:24 | 11.5025 | 75615 | 75863 | 75892
8783 | 2021-11-13 | 22:24 | 11.5025 | 75615 | 75864 | 75891
8784 | 2021-11-13 | 22:24 | 11.5026 | 75615 | 75865 | 75890
8785 | 2021-11-13 | 22:24 | 11.5026 | 75615 | 75866 | 75889
8786 | 2021-11-13 | 22:24 | 11.5026 | 75615 | 75867 | 75888
8787 | 2021-11-13 | 22:24 | 11.5026 | 75615 | 75868 | 75888
8788 | 2021-11-13 | 22:24 | 11.5027 | 75615 | 75869 | 75887
8789 | 2021-11-13 | 22:24 | 11.5027 | 75615 | 75870 | 75886
8790 | 2021-11-13 | 22:24 | 11.5027 | 75615 | 75871 | 75885
8791 | 2021-11-13 | 22:24 | 11.5028 | 75615 | 75872 | 75884
8792 | 2021-11-13 | 22:24 | 11.5028 | 75615 | 75873 | 75884
8793 | 2021-11-13 | 22:24 | 11.5028 | 75615 | 75875 | 75883
8794 | 2021-11-13 | 22:24 | 11.5028 | 75615 | 75876 | 75882
8795 | 2021-11-13 | 22:24 | 11.5029 | 75615 | 75877 | 75881
8796 | 2021-11-13 | 22:24 | 11.5029 | 75615 | 75878 | 75880
8797 | 2021-11-13 | 22:24 | 11.5029 | 75615 | 75879 | 75880
8798 | 2021-11-13 | 22:24 | 11.503 | 75615 | 75880 | 75879
8799 | 2021-11-13 | 22:24 | 11.503 | 75616 | 75881 | 75878
8800 | 2021-11-13 | 22:24 | 11.503 | 75616 | 75882 | 75877
8801 | 2021-11-13 | 22:24 | 11.503 | 75616 | 75883 | 75876
8802 | 2021-11-13 | 22:24 | 11.5031 | 75616 | 75884 | 75875
8803 | 2021-11-13 | 22:24 | 11.5031 | 75617 | 75885 | 75874
8804 | 2021-11-13 | 22:24 | 11.5031 | 75617 | 75886 | 75873
8805 | 2021-11-13 | 22:24 | 11.5032 | 75618 | 75887 | 75872
8806 | 2021-11-13 | 22:24 | 11.5032 | 75618 | 75888 | 75871
8807 | 2021-11-13 | 22:24 | 11.5032 | 75618 | 75889 | 75870
8808 | 2021-11-13 | 22:24 | 11.5032 | 75619 | 75890 | 75869
8809 | 2021-11-13 | 22:24 | 11.5033 | 75619 | 75891 | 75868
8810 | 2021-11-13 | 22:24 | 11.5033 | 75620 | 75891 | 75867
8811 | 2021-11-13 | 22:24 | 11.5033 | 75620 | 75892 | 75866
8812 | 2021-11-13 | 22:24 | 11.5034 | 75621 | 75893 | 75865
8813 | 2021-11-13 | 22:24 | 11.5034 | 75621 | 75894 | 75864
8814 | 2021-11-13 | 22:24 | 11.5034 | 75622 | 75895 | 75863
8815 | 2021-11-13 | 22:24 | 11.5035 | 75623 | 75895 | 75862
8816 | 2021-11-13 | 22:24 | 11.5035 | 75623 | 75896 | 75861
8817 | 2021-11-13 | 22:24 | 11.5035 | 75624 | 75896 | 75860
8818 | 2021-11-13 | 22:24 | 11.5035 | 75625 | 75897 | 75859
8819 | 2021-11-13 | 22:24 | 11.5036 | 75625 | 75897 | 75858
8820 | 2021-11-13 | 22:24 | 11.5036 | 75626 | 75897 | 75856
8821 | 2021-11-13 | 22:24 | 11.5036 | 75627 | 75897 | 75855
8822 | 2021-11-13 | 22:24 | 11.5037 | 75628 | 75897 | 75854
8823 | 2021-11-13 | 22:24 | 11.5037 | 75628 | 75898 | 75853
8824 | 2021-11-13 | 22:24 | 11.5037 | 75629 | 75898 | 75852
8825 | 2021-11-13 | 22:24 | 11.5037 | 75630 | 75898 | 75851
8826 | 2021-11-13 | 22:24 | 11.5038 | 75631 | 75898 | 75849
8827 | 2021-11-13 | 22:24 | 11.5038 | 75632 | 75899 | 75848
8828 | 2021-11-13 | 22:24 | 11.5038 | 75633 | 75899 | 75847
8829 | 2021-11-13 | 22:24 | 11.5039 | 75633 | 75899 | 75846
8830 | 2021-11-13 | 22:24 | 11.5039 | 75634 | 75899 | 75845
8831 | 2021-11-13 | 22:24 | 11.5039 | 75635 | 75898 | 75844
8832 | 2021-11-13 | 22:24 | 11.5039 | 75636 | 75898 | 75843
8833 | 2021-11-13 | 22:24 | 11.504 | 75637 | 75898 | 75841
8834 | 2021-11-13 | 22:24 | 11.504 | 75638 | 75898 | 75840
8835 | 2021-11-13 | 22:24 | 11.504 | 75639 | 75898 | 75839
8836 | 2021-11-13 | 22:24 | 11.5041 | 75640 | 75898 | 75838
8837 | 2021-11-13 | 22:24 | 11.5041 | 75641 | 75898 | 75837
8838 | 2021-11-13 | 22:24 | 11.5041 | 75642 | 75897 | 75836
8839 | 2021-11-13 | 22:24 | 11.5041 | 75644 | 75897 | 75835
8840 | 2021-11-13 | 22:24 | 11.5042 | 75645 | 75897 | 75834
8841 | 2021-11-13 | 22:24 | 11.5042 | 75646 | 75897 | 75833
8842 | 2021-11-13 | 22:24 | 11.5042 | 75647 | 75896 | 75832
8843 | 2021-11-13 | 22:24 | 11.5043 | 75648 | 75896 | 75831
8844 | 2021-11-13 | 22:24 | 11.5043 | 75649 | 75896 | 75830
8845 | 2021-11-13 | 22:24 | 11.5043 | 75650 | 75895 | 75829
8846 | 2021-11-13 | 22:24 | 11.5043 | 75651 | 75895 | 75829
8847 | 2021-11-13 | 22:24 | 11.5044 | 75652 | 75895 | 75828
8848 | 2021-11-13 | 22:24 | 11.5044 | 75653 | 75894 | 75827
8849 | 2021-11-13 | 22:24 | 11.5044 | 75654 | 75894 | 75826
8850 | 2021-11-13 | 22:24 | 11.5045 | 75655 | 75893 | 75826
8851 | 2021-11-13 | 22:24 | 11.5045 | 75656 | 75893 | 75825
8852 | 2021-11-13 | 22:24 | 11.5045 | 75657 | 75892 | 75824
8853 | 2021-11-13 | 22:24 | 11.5045 | 75658 | 75892 | 75824
8854 | 2021-11-13 | 22:24 | 11.5046 | 75660 | 75891 | 75823
8855 | 2021-11-13 | 22:24 | 11.5046 | 75661 | 75891 | 75822
8856 | 2021-11-13 | 22:24 | 11.5046 | 75662 | 75891 | 75822
8857 | 2021-11-13 | 22:24 | 11.5047 | 75664 | 75890 | 75821
8858 | 2021-11-13 | 22:24 | 11.5047 | 75665 | 75889 | 75821
8859 | 2021-11-13 | 22:24 | 11.5047 | 75666 | 75888 | 75820
8860 | 2021-11-13 | 22:24 | 11.5047 | 75667 | 75887 | 75820
8861 | 2021-11-13 | 22:24 | 11.5048 | 75668 | 75886 | 75819
8862 | 2021-11-13 | 22:24 | 11.5048 | 75669 | 75885 | 75819
8863 | 2021-11-13 | 22:24 | 11.5048 | 75670 | 75884 | 75819
8864 | 2021-11-13 | 22:24 | 11.5049 | 75671 | 75883 | 75818
8865 | 2021-11-13 | 22:24 | 11.5049 | 75672 | 75882 | 75818
8866 | 2021-11-13 | 22:24 | 11.5049 | 75673 | 75881 | 75818
8867 | 2021-11-13 | 22:24 | 11.5049 | 75674 | 75879 | 75818
8868 | 2021-11-13 | 22:24 | 11.505 | 75675 | 75878 | 75817
8869 | 2021-11-13 | 22:24 | 11.505 | 75676 | 75877 | 75817
8870 | 2021-11-13 | 22:24 | 11.505 | 75677 | 75876 | 75817
8871 | 2021-11-13 | 22:24 | 11.5051 | 75678 | 75875 | 75817
8872 | 2021-11-13 | 22:24 | 11.5051 | 75679 | 75873 | 75817
8873 | 2021-11-13 | 22:24 | 11.5051 | 75680 | 75872 | 75817
8874 | 2021-11-13 | 22:24 | 11.5051 | 75680 | 75871 | 75817
8875 | 2021-11-13 | 22:24 | 11.5052 | 75681 | 75870 | 75817
8876 | 2021-11-13 | 22:24 | 11.5052 | 75682 | 75868 | 75817
8877 | 2021-11-13 | 22:24 | 11.5052 | 75683 | 75867 | 75817
8878 | 2021-11-13 | 22:24 | 11.5053 | 75684 | 75866 | 75817
8879 | 2021-11-13 | 22:24 | 11.5053 | 75684 | 75865 | 75817
8880 | 2021-11-13 | 22:24 | 11.5053 | 75685 | 75864 | 75817
8881 | 2021-11-13 | 22:24 | 11.5053 | 75686 | 75863 | 75817
8882 | 2021-11-13 | 22:24 | 11.5054 | 75687 | 75861 | 75817
8883 | 2021-11-13 | 22:24 | 11.5054 | 75687 | 75860 | 75818
8884 | 2021-11-13 | 22:24 | 11.5054 | 75688 | 75859 | 75818
8885 | 2021-11-13 | 22:24 | 11.5055 | 75689 | 75858 | 75818
8886 | 2021-11-13 | 22:24 | 11.5055 | 75689 | 75857 | 75818
8887 | 2021-11-13 | 22:24 | 11.5055 | 75690 | 75856 | 75819
8888 | 2021-11-13 | 22:24 | 11.5055 | 75691 | 75855 | 75819
8889 | 2021-11-13 | 22:24 | 11.5056 | 75691 | 75854 | 75819
8890 | 2021-11-13 | 22:24 | 11.5056 | 75692 | 75853 | 75820
8891 | 2021-11-13 | 22:24 | 11.5056 | 75692 | 75852 | 75820
8892 | 2021-11-13 | 22:24 | 11.5057 | 75692 | 75851 | 75820
8893 | 2021-11-13 | 22:24 | 11.5057 | 75693 | 75850 | 75821
8894 | 2021-11-13 | 22:24 | 11.5057 | 75693 | 75849 | 75821
8895 | 2021-11-13 | 22:24 | 11.5057 | 75694 | 75848 | 75822
8896 | 2021-11-13 | 22:24 | 11.5058 | 75695 | 75847 | 75822
8897 | 2021-11-13 | 22:24 | 11.5058 | 75696 | 75846 | 75823
8898 | 2021-11-13 | 22:24 | 11.5058 | 75697 | 75845 | 75823
8899 | 2021-11-13 | 22:24 | 11.5059 | 75697 | 75844 | 75824
8900 | 2021-11-13 | 22:24 | 11.5059 | 75698 | 75843 | 75825
8901 | 2021-11-13 | 22:24 | 11.5059 | 75699 | 75842 | 75825
8902 | 2021-11-13 | 22:24 | 11.5059 | 75699 | 75841 | 75826
8903 | 2021-11-13 | 22:24 | 11.506 | 75700 | 75840 | 75826
8904 | 2021-11-13 | 22:24 | 11.506 | 75700 | 75839 | 75827
8905 | 2021-11-13 | 22:24 | 11.506 | 75701 | 75838 | 75828
8906 | 2021-11-13 | 22:24 | 11.5061 | 75701 | 75837 | 75828
8907 | 2021-11-13 | 22:24 | 11.5061 | 75701 | 75836 | 75829
8908 | 2021-11-13 | 22:24 | 11.5061 | 75702 | 75835 | 75830
8909 | 2021-11-13 | 22:24 | 11.5062 | 75702 | 75834 | 75831
8910 | 2021-11-13 | 22:24 | 11.5062 | 75703 | 75833 | 75831
8911 | 2021-11-13 | 22:24 | 11.5062 | 75703 | 75832 | 75832
8912 | 2021-11-13 | 22:24 | 11.5062 | 75704 | 75831 | 75833
8913 | 2021-11-13 | 22:24 | 11.5063 | 75704 | 75830 | 75834
8914 | 2021-11-13 | 22:24 | 11.5063 | 75704 | 75829 | 75835
8915 | 2021-11-13 | 22:24 | 11.5063 | 75704 | 75828 | 75836
8916 | 2021-11-13 | 22:24 | 11.5064 | 75705 | 75827 | 75837
8917 | 2021-11-13 | 22:24 | 11.5064 | 75705 | 75826 | 75838
8918 | 2021-11-13 | 22:24 | 11.5064 | 75705 | 75825 | 75839
8919 | 2021-11-13 | 22:24 | 11.5064 | 75705 | 75824 | 75840
8920 | 2021-11-13 | 22:24 | 11.5065 | 75706 | 75823 | 75841
8921 | 2021-11-13 | 22:24 | 11.5065 | 75706 | 75822 | 75842
8922 | 2021-11-13 | 22:24 | 11.5065 | 75706 | 75821 | 75843
8923 | 2021-11-13 | 22:24 | 11.5066 | 75706 | 75820 | 75844
8924 | 2021-11-13 | 22:24 | 11.5066 | 75706 | 75819 | 75845
8925 | 2021-11-13 | 22:24 | 11.5066 | 75706 | 75818 | 75846
8926 | 2021-11-13 | 22:24 | 11.5066 | 75706 | 75817 | 75848
8927 | 2021-11-13 | 22:24 | 11.5067 | 75706 | 75816 | 75849
8928 | 2021-11-13 | 22:24 | 11.5067 | 75706 | 75815 | 75850
8929 | 2021-11-13 | 22:24 | 11.5067 | 75706 | 75814 | 75852
8930 | 2021-11-13 | 22:24 | 11.5068 | 75706 | 75813 | 75853
8931 | 2021-11-13 | 22:24 | 11.5068 | 75706 | 75813 | 75854
8932 | 2021-11-13 | 22:24 | 11.5068 | 75705 | 75812 | 75855
8933 | 2021-11-13 | 22:24 | 11.5068 | 75705 | 75811 | 75857
8934 | 2021-11-13 | 22:24 | 11.5069 | 75704 | 75810 | 75858
8935 | 2021-11-13 | 22:24 | 11.5069 | 75703 | 75809 | 75859
8936 | 2021-11-13 | 22:24 | 11.5069 | 75703 | 75809 | 75860
8937 | 2021-11-13 | 22:24 | 11.507 | 75702 | 75808 | 75861
8938 | 2021-11-13 | 22:24 | 11.507 | 75702 | 75807 | 75862
8939 | 2021-11-13 | 22:24 | 11.507 | 75701 | 75807 | 75864
8940 | 2021-11-13 | 22:24 | 11.507 | 75701 | 75806 | 75865
8941 | 2021-11-13 | 22:24 | 11.5071 | 75700 | 75805 | 75867
8942 | 2021-11-13 | 22:24 | 11.5071 | 75700 | 75805 | 75868
8943 | 2021-11-13 | 22:24 | 11.5071 | 75699 | 75804 | 75869
8944 | 2021-11-13 | 22:24 | 11.5072 | 75698 | 75804 | 75870
8945 | 2021-11-13 | 22:24 | 11.5072 | 75698 | 75803 | 75872
8946 | 2021-11-13 | 22:24 | 11.5072 | 75697 | 75803 | 75873
8947 | 2021-11-13 | 22:24 | 11.5072 | 75696 | 75803 | 75874
8948 | 2021-11-13 | 22:24 | 11.5073 | 75695 | 75802 | 75875
8949 | 2021-11-13 | 22:24 | 11.5073 | 75694 | 75802 | 75876
8950 | 2021-11-13 | 22:24 | 11.5073 | 75693 | 75802 | 75877
8951 | 2021-11-13 | 22:24 | 11.5074 | 75692 | 75801 | 75878
8952 | 2021-11-13 | 22:24 | 11.5074 | 75691 | 75801 | 75879
8953 | 2021-11-13 | 22:24 | 11.5074 | 75690 | 75801 | 75880
8954 | 2021-11-13 | 22:24 | 11.5074 | 75689 | 75801 | 75881
8955 | 2021-11-13 | 22:24 | 11.5075 | 75688 | 75801 | 75882
8956 | 2021-11-13 | 22:24 | 11.5075 | 75687 | 75801 | 75883
8957 | 2021-11-13 | 22:24 | 11.5075 | 75686 | 75801 | 75884
8958 | 2021-11-13 | 22:24 | 11.5076 | 75685 | 75800 | 75885
8959 | 2021-11-13 | 22:24 | 11.5076 | 75685 | 75800 | 75886
8960 | 2021-11-13 | 22:24 | 11.5076 | 75684 | 75800 | 75887
8961 | 2021-11-13 | 22:24 | 11.5076 | 75683 | 75800 | 75888
8962 | 2021-11-13 | 22:24 | 11.5077 | 75682 | 75800 | 75889
8963 | 2021-11-13 | 22:24 | 11.5077 | 75681 | 75801 | 75890
8964 | 2021-11-13 | 22:24 | 11.5077 | 75680 | 75801 | 75891
8965 | 2021-11-13 | 22:24 | 11.5078 | 75679 | 75801 | 75892
8966 | 2021-11-13 | 22:24 | 11.5078 | 75678 | 75801 | 75892
8967 | 2021-11-13 | 22:24 | 11.5078 | 75677 | 75801 | 75893
8968 | 2021-11-13 | 22:24 | 11.5078 | 75676 | 75801 | 75894
8969 | 2021-11-13 | 22:24 | 11.5079 | 75675 | 75802 | 75895
8970 | 2021-11-13 | 22:24 | 11.5079 | 75674 | 75802 | 75896
8971 | 2021-11-13 | 22:24 | 11.5079 | 75673 | 75802 | 75897
8972 | 2021-11-13 | 22:24 | 11.508 | 75672 | 75802 | 75898
8973 | 2021-11-13 | 22:24 | 11.508 | 75671 | 75803 | 75899
8974 | 2021-11-13 | 22:24 | 11.508 | 75670 | 75803 | 75900
8975 | 2021-11-13 | 22:24 | 11.508 | 75669 | 75803 | 75901
8976 | 2021-11-13 | 22:24 | 11.5081 | 75668 | 75804 | 75901
8977 | 2021-11-13 | 22:24 | 11.5081 | 75667 | 75804 | 75902
8978 | 2021-11-13 | 22:24 | 11.5081 | 75666 | 75805 | 75903
8979 | 2021-11-13 | 22:24 | 11.5082 | 75665 | 75805 | 75903
8980 | 2021-11-13 | 22:24 | 11.5082 | 75664 | 75806 | 75904
8981 | 2021-11-13 | 22:24 | 11.5082 | 75663 | 75806 | 75905
8982 | 2021-11-13 | 22:24 | 11.5082 | 75662 | 75807 | 75905
8983 | 2021-11-13 | 22:24 | 11.5083 | 75661 | 75807 | 75906
8984 | 2021-11-13 | 22:24 | 11.5083 | 75660 | 75808 | 75907
8985 | 2021-11-13 | 22:24 | 11.5083 | 75659 | 75808 | 75908
8986 | 2021-11-13 | 22:24 | 11.5084 | 75658 | 75809 | 75908
8987 | 2021-11-13 | 22:24 | 11.5084 | 75657 | 75809 | 75909
8988 | 2021-11-13 | 22:24 | 11.5084 | 75656 | 75810 | 75910
8989 | 2021-11-13 | 22:24 | 11.5084 | 75655 | 75811 | 75910
8990 | 2021-11-13 | 22:24 | 11.5085 | 75654 | 75811 | 75911
8991 | 2021-11-13 | 22:24 | 11.5085 | 75653 | 75812 | 75912
8992 | 2021-11-13 | 22:24 | 11.5085 | 75651 | 75813 | 75912
8993 | 2021-11-13 | 22:24 | 11.5086 | 75650 | 75814 | 75913
8994 | 2021-11-13 | 22:24 | 11.5086 | 75649 | 75814 | 75913
8995 | 2021-11-13 | 22:24 | 11.5086 | 75648 | 75815 | 75913
8996 | 2021-11-13 | 22:24 | 11.5086 | 75647 | 75816 | 75913
8997 | 2021-11-13 | 22:24 | 11.5087 | 75646 | 75817 | 75913
8998 | 2021-11-13 | 22:24 | 11.5087 | 75645 | 75817 | 75913
8999 | 2021-11-13 | 22:24 | 11.5087 | 75644 | 75818 | 75913
9000 | 2021-11-13 | 22:24 | 11.5088 | 75643 | 75819 | 75913
9001 | 2021-11-13 | 22:24 | 11.5088 | 75642 | 75820 | 75914
9002 | 2021-11-13 | 22:24 | 11.5088 | 75640 | 75821 | 75914
9003 | 2021-11-13 | 22:24 | 11.5089 | 75639 | 75822 | 75914
9004 | 2021-11-13 | 22:24 | 11.5089 | 75638 | 75823 | 75914
9005 | 2021-11-13 | 22:24 | 11.5089 | 75637 | 75825 | 75915
9006 | 2021-11-13 | 22:24 | 11.5089 | 75636 | 75826 | 75915
9007 | 2021-11-13 | 22:24 | 11.509 | 75635 | 75827 | 75915
9008 | 2021-11-13 | 22:24 | 11.509 | 75634 | 75828 | 75914
9009 | 2021-11-13 | 22:24 | 11.509 | 75633 | 75829 | 75914
9010 | 2021-11-13 | 22:24 | 11.5091 | 75632 | 75830 | 75914
9011 | 2021-11-13 | 22:24 | 11.5091 | 75631 | 75831 | 75914
9012 | 2021-11-13 | 22:24 | 11.5091 | 75630 | 75833 | 75913
9013 | 2021-11-13 | 22:24 | 11.5091 | 75629 | 75834 | 75913
9014 | 2021-11-13 | 22:24 | 11.5092 | 75628 | 75835 | 75913
9015 | 2021-11-13 | 22:24 | 11.5092 | 75627 | 75836 | 75912
9016 | 2021-11-13 | 22:24 | 11.5092 | 75626 | 75837 | 75912
9017 | 2021-11-13 | 22:24 | 11.5093 | 75625 | 75839 | 75911
9018 | 2021-11-13 | 22:24 | 11.5093 | 75624 | 75840 | 75910
9019 | 2021-11-13 | 22:24 | 11.5093 | 75623 | 75841 | 75910
9020 | 2021-11-13 | 22:24 | 11.5093 | 75623 | 75842 | 75909
9021 | 2021-11-13 | 22:24 | 11.5094 | 75622 | 75844 | 75909
9022 | 2021-11-13 | 22:24 | 11.5094 | 75621 | 75845 | 75908
9023 | 2021-11-13 | 22:24 | 11.5094 | 75620 | 75846 | 75907
9024 | 2021-11-13 | 22:24 | 11.5095 | 75620 | 75848 | 75907
9025 | 2021-11-13 | 22:24 | 11.5095 | 75619 | 75849 | 75906
9026 | 2021-11-13 | 22:24 | 11.5095 | 75619 | 75850 | 75905
9027 | 2021-11-13 | 22:24 | 11.5095 | 75618 | 75851 | 75904
9028 | 2021-11-13 | 22:24 | 11.5096 | 75617 | 75852 | 75903
9029 | 2021-11-13 | 22:24 | 11.5096 | 75617 | 75853 | 75903
9030 | 2021-11-13 | 22:24 | 11.5096 | 75617 | 75854 | 75902
9031 | 2021-11-13 | 22:24 | 11.5097 | 75616 | 75855 | 75901
9032 | 2021-11-13 | 22:24 | 11.5097 | 75616 | 75856 | 75900
9033 | 2021-11-13 | 22:24 | 11.5097 | 75615 | 75857 | 75899
9034 | 2021-11-13 | 22:24 | 11.5097 | 75615 | 75858 | 75898
9035 | 2021-11-13 | 22:24 | 11.5098 | 75615 | 75859 | 75897
9036 | 2021-11-13 | 22:24 | 11.5098 | 75614 | 75860 | 75897
9037 | 2021-11-13 | 22:24 | 11.5098 | 75614 | 75861 | 75896
9038 | 2021-11-13 | 22:24 | 11.5099 | 75614 | 75862 | 75894
9039 | 2021-11-13 | 22:24 | 11.5099 | 75614 | 75863 | 75893
9040 | 2021-11-13 | 22:24 | 11.5099 | 75614 | 75864 | 75892
9041 | 2021-11-13 | 22:24 | 11.5099 | 75613 | 75865 | 75891
9042 | 2021-11-13 | 22:24 | 11.51 | 75613 | 75866 | 75890
9043 | 2021-11-13 | 22:24 | 11.51 | 75613 | 75866 | 75889
9044 | 2021-11-13 | 22:24 | 11.51 | 75613 | 75867 | 75888
9045 | 2021-11-13 | 22:24 | 11.5101 | 75613 | 75868 | 75887
9046 | 2021-11-13 | 22:24 | 11.5101 | 75613 | 75869 | 75886
9047 | 2021-11-13 | 22:24 | 11.5101 | 75613 | 75870 | 75885
9048 | 2021-11-13 | 22:24 | 11.5101 | 75613 | 75871 | 75884
9049 | 2021-11-13 | 22:24 | 11.5102 | 75613 | 75872 | 75884
9050 | 2021-11-13 | 22:24 | 11.5102 | 75613 | 75872 | 75883
9051 | 2021-11-13 | 22:24 | 11.5102 | 75614 | 75873 | 75882
9052 | 2021-11-13 | 22:24 | 11.5103 | 75614 | 75874 | 75881
9053 | 2021-11-13 | 22:24 | 11.5103 | 75614 | 75875 | 75880
9054 | 2021-11-13 | 22:24 | 11.5103 | 75614 | 75876 | 75879
9055 | 2021-11-13 | 22:24 | 11.5103 | 75614 | 75877 | 75878
9056 | 2021-11-13 | 22:24 | 11.5104 | 75615 | 75878 | 75877
9057 | 2021-11-13 | 22:24 | 11.5104 | 75615 | 75879 | 75876
9058 | 2021-11-13 | 22:24 | 11.5104 | 75615 | 75879 | 75875
9059 | 2021-11-13 | 22:24 | 11.5105 | 75616 | 75880 | 75874
9060 | 2021-11-13 | 22:24 | 11.5105 | 75616 | 75881 | 75873
9061 | 2021-11-13 | 22:24 | 11.5105 | 75616 | 75882 | 75872
9062 | 2021-11-13 | 22:24 | 11.5105 | 75617 | 75883 | 75871
9063 | 2021-11-13 | 22:24 | 11.5106 | 75617 | 75884 | 75870
9064 | 2021-11-13 | 22:24 | 11.5106 | 75617 | 75885 | 75869
9065 | 2021-11-13 | 22:24 | 11.5106 | 75618 | 75886 | 75868
9066 | 2021-11-13 | 22:24 | 11.5107 | 75618 | 75887 | 75867
9067 | 2021-11-13 | 22:24 | 11.5107 | 75619 | 75888 | 75866
9068 | 2021-11-13 | 22:24 | 11.5107 | 75620 | 75889 | 75865
9069 | 2021-11-13 | 22:24 | 11.5107 | 75620 | 75890 | 75864
9070 | 2021-11-13 | 22:24 | 11.5108 | 75621 | 75890 | 75863
9071 | 2021-11-13 | 22:24 | 11.5108 | 75621 | 75891 | 75862
9072 | 2021-11-13 | 22:24 | 11.5108 | 75622 | 75892 | 75861
9073 | 2021-11-13 | 22:24 | 11.5109 | 75623 | 75892 | 75860
9074 | 2021-11-13 | 22:24 | 11.5109 | 75623 | 75893 | 75859
9075 | 2021-11-13 | 22:24 | 11.5109 | 75624 | 75894 | 75857
9076 | 2021-11-13 | 22:24 | 11.5109 | 75625 | 75894 | 75856
9077 | 2021-11-13 | 22:24 | 11.511 | 75626 | 75894 | 75855
9078 | 2021-11-13 | 22:24 | 11.511 | 75626 | 75894 | 75854
9079 | 2021-11-13 | 22:24 | 11.511 | 75627 | 75895 | 75853
9080 | 2021-11-13 | 22:24 | 11.5111 | 75628 | 75895 | 75852
9081 | 2021-11-13 | 22:24 | 11.5111 | 75629 | 75895 | 75850
9082 | 2021-11-13 | 22:24 | 11.5111 | 75630 | 75896 | 75849
9083 | 2021-11-13 | 22:24 | 11.5111 | 75630 | 75896 | 75848
9084 | 2021-11-13 | 22:24 | 11.5112 | 75631 | 75896 | 75847
9085 | 2021-11-13 | 22:24 | 11.5112 | 75632 | 75896 | 75846
9086 | 2021-11-13 | 22:24 | 11.5112 | 75633 | 75896 | 75845
9087 | 2021-11-13 | 22:24 | 11.5113 | 75634 | 75895 | 75843
9088 | 2021-11-13 | 22:24 | 11.5113 | 75635 | 75895 | 75842
9089 | 2021-11-13 | 22:24 | 11.5113 | 75636 | 75895 | 75841
9090 | 2021-11-13 | 22:24 | 11.5113 | 75637 | 75895 | 75840
9091 | 2021-11-13 | 22:24 | 11.5114 | 75638 | 75895 | 75839
9092 | 2021-11-13 | 22:24 | 11.5114 | 75639 | 75894 | 75838
9093 | 2021-11-13 | 22:24 | 11.5114 | 75641 | 75894 | 75837
9094 | 2021-11-13 | 22:24 | 11.5115 | 75642 | 75894 | 75836
9095 | 2021-11-13 | 22:24 | 11.5115 | 75643 | 75894 | 75835
9096 | 2021-11-13 | 22:24 | 11.5115 | 75644 | 75894 | 75834
9097 | 2021-11-13 | 22:24 | 11.5116 | 75645 | 75893 | 75833
9098 | 2021-11-13 | 22:24 | 11.5116 | 75646 | 75893 | 75832
9099 | 2021-11-13 | 22:24 | 11.5116 | 75648 | 75893 | 75831
9100 | 2021-11-13 | 22:24 | 11.5116 | 75649 | 75892 | 75830
9101 | 2021-11-13 | 22:24 | 11.5117 | 75650 | 75892 | 75829
9102 | 2021-11-13 | 22:24 | 11.5117 | 75651 | 75891 | 75828
9103 | 2021-11-13 | 22:24 | 11.5117 | 75652 | 75891 | 75827
9104 | 2021-11-13 | 22:24 | 11.5118 | 75653 | 75890 | 75827
9105 | 2021-11-13 | 22:24 | 11.5118 | 75654 | 75890 | 75826
9106 | 2021-11-13 | 22:24 | 11.5118 | 75655 | 75890 | 75825
9107 | 2021-11-13 | 22:24 | 11.5118 | 75656 | 75889 | 75824
9108 | 2021-11-13 | 22:24 | 11.5119 | 75658 | 75889 | 75824
9109 | 2021-11-13 | 22:24 | 11.5119 | 75659 | 75889 | 75823
9110 | 2021-11-13 | 22:24 | 11.5119 | 75660 | 75888 | 75822
9111 | 2021-11-13 | 22:24 | 11.512 | 75661 | 75888 | 75822
9112 | 2021-11-13 | 22:24 | 11.512 | 75662 | 75887 | 75821
9113 | 2021-11-13 | 22:24 | 11.512 | 75664 | 75887 | 75821
9114 | 2021-11-13 | 22:24 | 11.512 | 75665 | 75886 | 75820
9115 | 2021-11-13 | 22:24 | 11.5121 | 75666 | 75885 | 75820
9116 | 2021-11-13 | 22:24 | 11.5121 | 75667 | 75884 | 75819
9117 | 2021-11-13 | 22:24 | 11.5121 | 75668 | 75884 | 75819
9118 | 2021-11-13 | 22:24 | 11.5122 | 75669 | 75883 | 75819
9119 | 2021-11-13 | 22:24 | 11.5122 | 75670 | 75882 | 75818
9120 | 2021-11-13 | 22:24 | 11.5122 | 75671 | 75881 | 75818
9121 | 2021-11-13 | 22:24 | 11.5122 | 75672 | 75880 | 75818
9122 | 2021-11-13 | 22:24 | 11.5123 | 75673 | 75879 | 75817
9123 | 2021-11-13 | 22:24 | 11.5123 | 75674 | 75878 | 75817
9124 | 2021-11-13 | 22:24 | 11.5123 | 75675 | 75877 | 75817
9125 | 2021-11-13 | 22:24 | 11.5124 | 75676 | 75876 | 75817
9126 | 2021-11-13 | 22:24 | 11.5124 | 75677 | 75875 | 75817
9127 | 2021-11-13 | 22:24 | 11.5124 | 75678 | 75874 | 75817
9128 | 2021-11-13 | 22:24 | 11.5124 | 75679 | 75873 | 75817
9129 | 2021-11-13 | 22:24 | 11.5125 | 75680 | 75871 | 75816
9130 | 2021-11-13 | 22:24 | 11.5125 | 75681 | 75870 | 75816
9131 | 2021-11-13 | 22:24 | 11.5125 | 75682 | 75869 | 75816
9132 | 2021-11-13 | 22:24 | 11.5126 | 75683 | 75868 | 75816
9133 | 2021-11-13 | 22:24 | 11.5126 | 75684 | 75867 | 75816
9134 | 2021-11-13 | 22:24 | 11.5126 | 75685 | 75866 | 75817
9135 | 2021-11-13 | 22:24 | 11.5126 | 75686 | 75865 | 75817
9136 | 2021-11-13 | 22:24 | 11.5127 | 75687 | 75864 | 75817
9137 | 2021-11-13 | 22:24 | 11.5127 | 75688 | 75862 | 75817
9138 | 2021-11-13 | 22:24 | 11.5127 | 75689 | 75861 | 75817
9139 | 2021-11-13 | 22:24 | 11.5128 | 75690 | 75860 | 75817
9140 | 2021-11-13 | 22:24 | 11.5128 | 75691 | 75859 | 75818
9141 | 2021-11-13 | 22:24 | 11.5128 | 75692 | 75858 | 75818
9142 | 2021-11-13 | 22:24 | 11.5128 | 75693 | 75857 | 75818
9143 | 2021-11-13 | 22:24 | 11.5129 | 75694 | 75856 | 75818
9144 | 2021-11-13 | 22:24 | 11.5129 | 75695 | 75855 | 75819
9145 | 2021-11-13 | 22:24 | 11.5129 | 75695 | 75854 | 75819
9146 | 2021-11-13 | 22:24 | 11.513 | 75696 | 75853 | 75820
9147 | 2021-11-13 | 22:24 | 11.513 | 75697 | 75851 | 75820
9148 | 2021-11-13 | 22:24 | 11.513 | 75698 | 75850 | 75820
9149 | 2021-11-13 | 22:24 | 11.513 | 75698 | 75849 | 75821
9150 | 2021-11-13 | 22:24 | 11.5131 | 75699 | 75848 | 75821
9151 | 2021-11-13 | 22:24 | 11.5131 | 75700 | 75847 | 75822
9152 | 2021-11-13 | 22:24 | 11.5131 | 75701 | 75846 | 75823
9153 | 2021-11-13 | 22:24 | 11.5132 | 75702 | 75845 | 75823
9154 | 2021-11-13 | 22:24 | 11.5132 | 75702 | 75844 | 75824
9155 | 2021-11-13 | 22:24 | 11.5132 | 75703 | 75843 | 75824
9156 | 2021-11-13 | 22:24 | 11.5132 | 75704 | 75842 | 75825
9157 | 2021-11-13 | 22:24 | 11.5133 | 75704 | 75841 | 75826
9158 | 2021-11-13 | 22:24 | 11.5133 | 75705 | 75840 | 75826
9159 | 2021-11-13 | 22:24 | 11.5133 | 75706 | 75839 | 75827
9160 | 2021-11-13 | 22:24 | 11.5134 | 75706 | 75838 | 75828
9161 | 2021-11-13 | 22:24 | 11.5134 | 75707 | 75837 | 75829
9162 | 2021-11-13 | 22:24 | 11.5134 | 75707 | 75836 | 75829
9163 | 2021-11-13 | 22:24 | 11.5134 | 75708 | 75835 | 75830
9164 | 2021-11-13 | 22:24 | 11.5135 | 75708 | 75834 | 75831
9165 | 2021-11-13 | 22:24 | 11.5135 | 75708 | 75833 | 75832
9166 | 2021-11-13 | 22:24 | 11.5135 | 75708 | 75831 | 75832
9167 | 2021-11-13 | 22:24 | 11.5136 | 75708 | 75831 | 75833
9168 | 2021-11-13 | 22:24 | 11.5136 | 75708 | 75830 | 75834
9169 | 2021-11-13 | 22:24 | 11.5136 | 75708 | 75829 | 75835
9170 | 2021-11-13 | 22:24 | 11.5136 | 75708 | 75827 | 75836
9171 | 2021-11-13 | 22:24 | 11.5137 | 75709 | 75826 | 75837
9172 | 2021-11-13 | 22:24 | 11.5137 | 75709 | 75825 | 75838
9173 | 2021-11-13 | 22:24 | 11.5137 | 75709 | 75824 | 75839
9174 | 2021-11-13 | 22:24 | 11.5138 | 75709 | 75823 | 75840
9175 | 2021-11-13 | 22:24 | 11.5138 | 75708 | 75822 | 75841
9176 | 2021-11-13 | 22:24 | 11.5138 | 75708 | 75821 | 75842
9177 | 2021-11-13 | 22:24 | 11.5138 | 75708 | 75820 | 75843
9178 | 2021-11-13 | 22:24 | 11.5139 | 75708 | 75819 | 75844
9179 | 2021-11-13 | 22:24 | 11.5139 | 75707 | 75818 | 75845
9180 | 2021-11-13 | 22:24 | 11.5139 | 75707 | 75817 | 75846
9181 | 2021-11-13 | 22:24 | 11.514 | 75707 | 75816 | 75847
9182 | 2021-11-13 | 22:24 | 11.514 | 75706 | 75815 | 75848
9183 | 2021-11-13 | 22:24 | 11.514 | 75706 | 75814 | 75849
9184 | 2021-11-13 | 22:24 | 11.514 | 75706 | 75813 | 75850
9185 | 2021-11-13 | 22:24 | 11.5141 | 75705 | 75812 | 75851
9186 | 2021-11-13 | 22:24 | 11.5141 | 75704 | 75811 | 75852
9187 | 2021-11-13 | 22:24 | 11.5141 | 75703 | 75810 | 75853
9188 | 2021-11-13 | 22:24 | 11.5142 | 75703 | 75809 | 75854
9189 | 2021-11-13 | 22:24 | 11.5142 | 75702 | 75808 | 75856
9190 | 2021-11-13 | 22:24 | 11.5142 | 75701 | 75807 | 75857
9191 | 2021-11-13 | 22:24 | 11.5143 | 75701 | 75807 | 75858
9192 | 2021-11-13 | 22:24 | 11.5143 | 75700 | 75806 | 75859
9193 | 2021-11-13 | 22:24 | 11.5143 | 75699 | 75805 | 75860
9194 | 2021-11-13 | 22:24 | 11.5143 | 75699 | 75805 | 75861
9195 | 2021-11-13 | 22:24 | 11.5144 | 75698 | 75804 | 75863
9196 | 2021-11-13 | 22:24 | 11.5144 | 75697 | 75803 | 75864
9197 | 2021-11-13 | 22:24 | 11.5144 | 75696 | 75803 | 75865
9198 | 2021-11-13 | 22:24 | 11.5145 | 75696 | 75802 | 75866
9199 | 2021-11-13 | 22:24 | 11.5145 | 75695 | 75802 | 75867
9200 | 2021-11-13 | 22:24 | 11.5145 | 75694 | 75801 | 75868
9201 | 2021-11-13 | 22:24 | 11.5145 | 75693 | 75801 | 75869
9202 | 2021-11-13 | 22:24 | 11.5146 | 75693 | 75800 | 75871
9203 | 2021-11-13 | 22:24 | 11.5146 | 75692 | 75800 | 75872
9204 | 2021-11-13 | 22:24 | 11.5146 | 75691 | 75800 | 75873
9205 | 2021-11-13 | 22:24 | 11.5147 | 75690 | 75799 | 75874
9206 | 2021-11-13 | 22:24 | 11.5147 | 75689 | 75799 | 75875
9207 | 2021-11-13 | 22:24 | 11.5147 | 75688 | 75799 | 75876
9208 | 2021-11-13 | 22:24 | 11.5147 | 75687 | 75798 | 75876
9209 | 2021-11-13 | 22:24 | 11.5148 | 75686 | 75798 | 75877
9210 | 2021-11-13 | 22:24 | 11.5148 | 75685 | 75798 | 75878
9211 | 2021-11-13 | 22:24 | 11.5148 | 75684 | 75798 | 75879
9212 | 2021-11-13 | 22:24 | 11.5149 | 75683 | 75798 | 75880
9213 | 2021-11-13 | 22:24 | 11.5149 | 75682 | 75798 | 75881
9214 | 2021-11-13 | 22:24 | 11.5149 | 75681 | 75798 | 75882
9215 | 2021-11-13 | 22:24 | 11.5149 | 75680 | 75798 | 75883
9216 | 2021-11-13 | 22:24 | 11.515 | 75679 | 75798 | 75883
9217 | 2021-11-13 | 22:24 | 11.515 | 75678 | 75798 | 75884
9218 | 2021-11-13 | 22:24 | 11.515 | 75677 | 75798 | 75885
9219 | 2021-11-13 | 22:24 | 11.5151 | 75676 | 75798 | 75886
9220 | 2021-11-13 | 22:24 | 11.5151 | 75675 | 75798 | 75887
9221 | 2021-11-13 | 22:24 | 11.5151 | 75674 | 75798 | 75888
9222 | 2021-11-13 | 22:24 | 11.5151 | 75673 | 75798 | 75889
9223 | 2021-11-13 | 22:24 | 11.5152 | 75672 | 75798 | 75889
9224 | 2021-11-13 | 22:24 | 11.5152 | 75671 | 75799 | 75890
9225 | 2021-11-13 | 22:24 | 11.5152 | 75670 | 75799 | 75891
9226 | 2021-11-13 | 22:24 | 11.5153 | 75669 | 75799 | 75892
9227 | 2021-11-13 | 22:24 | 11.5153 | 75668 | 75799 | 75893
9228 | 2021-11-13 | 22:24 | 11.5153 | 75667 | 75800 | 75894
9229 | 2021-11-13 | 22:24 | 11.5153 | 75666 | 75800 | 75894
9230 | 2021-11-13 | 22:24 | 11.5154 | 75665 | 75800 | 75895
9231 | 2021-11-13 | 22:24 | 11.5154 | 75664 | 75801 | 75896
9232 | 2021-11-13 | 22:24 | 11.5154 | 75663 | 75801 | 75897
9233 | 2021-11-13 | 22:24 | 11.5155 | 75662 | 75801 | 75898
9234 | 2021-11-13 | 22:24 | 11.5155 | 75661 | 75802 | 75899
9235 | 2021-11-13 | 22:24 | 11.5155 | 75660 | 75802 | 75900
9236 | 2021-11-13 | 22:24 | 11.5155 | 75659 | 75803 | 75900
9237 | 2021-11-13 | 22:24 | 11.5156 | 75658 | 75803 | 75901
9238 | 2021-11-13 | 22:24 | 11.5156 | 75657 | 75804 | 75902
9239 | 2021-11-13 | 22:24 | 11.5156 | 75656 | 75804 | 75903
9240 | 2021-11-13 | 22:24 | 11.5157 | 75655 | 75805 | 75903
9241 | 2021-11-13 | 22:24 | 11.5157 | 75654 | 75806 | 75904
9242 | 2021-11-13 | 22:24 | 11.5157 | 75653 | 75806 | 75905
9243 | 2021-11-13 | 22:24 | 11.5157 | 75652 | 75807 | 75906
9244 | 2021-11-13 | 22:24 | 11.5158 | 75651 | 75807 | 75907
9245 | 2021-11-13 | 22:24 | 11.5158 | 75650 | 75808 | 75907
9246 | 2021-11-13 | 22:24 | 11.5158 | 75649 | 75809 | 75908
9247 | 2021-11-13 | 22:24 | 11.5159 | 75648 | 75810 | 75909
9248 | 2021-11-13 | 22:24 | 11.5159 | 75647 | 75810 | 75909
9249 | 2021-11-13 | 22:24 | 11.5159 | 75646 | 75811 | 75910
9250 | 2021-11-13 | 22:24 | 11.5159 | 75645 | 75812 | 75910
9251 | 2021-11-13 | 22:24 | 11.516 | 75644 | 75813 | 75910
9252 | 2021-11-13 | 22:24 | 11.516 | 75643 | 75813 | 75910
9253 | 2021-11-13 | 22:24 | 11.516 | 75642 | 75814 | 75911
9254 | 2021-11-13 | 22:24 | 11.5161 | 75641 | 75815 | 75911
9255 | 2021-11-13 | 22:24 | 11.5161 | 75640 | 75816 | 75911
9256 | 2021-11-13 | 22:24 | 11.5161 | 75639 | 75817 | 75911
9257 | 2021-11-13 | 22:24 | 11.5161 | 75638 | 75818 | 75911
9258 | 2021-11-13 | 22:24 | 11.5162 | 75637 | 75819 | 75911
9259 | 2021-11-13 | 22:24 | 11.5162 | 75636 | 75820 | 75911
9260 | 2021-11-13 | 22:24 | 11.5162 | 75635 | 75821 | 75911
9261 | 2021-11-13 | 22:24 | 11.5163 | 75634 | 75822 | 75912
9262 | 2021-11-13 | 22:24 | 11.5163 | 75633 | 75823 | 75912
9263 | 2021-11-13 | 22:24 | 11.5163 | 75632 | 75824 | 75912
9264 | 2021-11-13 | 22:24 | 11.5163 | 75631 | 75825 | 75912
9265 | 2021-11-13 | 22:24 | 11.5164 | 75630 | 75826 | 75912
9266 | 2021-11-13 | 22:24 | 11.5164 | 75629 | 75827 | 75912
9267 | 2021-11-13 | 22:24 | 11.5164 | 75628 | 75828 | 75911
9268 | 2021-11-13 | 22:24 | 11.5165 | 75627 | 75829 | 75911
9269 | 2021-11-13 | 22:24 | 11.5165 | 75626 | 75830 | 75911
9270 | 2021-11-13 | 22:24 | 11.5165 | 75625 | 75831 | 75910
9271 | 2021-11-13 | 22:24 | 11.5165 | 75624 | 75832 | 75910
9272 | 2021-11-13 | 22:24 | 11.5166 | 75623 | 75833 | 75909
9273 | 2021-11-13 | 22:24 | 11.5166 | 75623 | 75835 | 75909
9274 | 2021-11-13 | 22:24 | 11.5166 | 75622 | 75836 | 75908
9275 | 2021-11-13 | 22:24 | 11.5167 | 75621 | 75837 | 75908
9276 | 2021-11-13 | 22:24 | 11.5167 | 75620 | 75838 | 75907
9277 | 2021-11-13 | 22:24 | 11.5167 | 75619 | 75840 | 75906
9278 | 2021-11-13 | 22:24 | 11.5167 | 75619 | 75841 | 75906
9279 | 2021-11-13 | 22:24 | 11.5168 | 75618 | 75842 | 75905
9280 | 2021-11-13 | 22:24 | 11.5168 | 75617 | 75843 | 75904
9281 | 2021-11-13 | 22:24 | 11.5168 | 75617 | 75845 | 75904
9282 | 2021-11-13 | 22:24 | 11.5169 | 75616 | 75846 | 75903
9283 | 2021-11-13 | 22:24 | 11.5169 | 75615 | 75847 | 75902
9284 | 2021-11-13 | 22:24 | 11.5169 | 75615 | 75849 | 75901
9285 | 2021-11-13 | 22:24 | 11.517 | 75614 | 75850 | 75900
9286 | 2021-11-13 | 22:24 | 11.517 | 75614 | 75851 | 75900
9287 | 2021-11-13 | 22:24 | 11.517 | 75613 | 75852 | 75899
9288 | 2021-11-13 | 22:24 | 11.517 | 75613 | 75854 | 75898
9289 | 2021-11-13 | 22:24 | 11.5171 | 75613 | 75855 | 75897
9290 | 2021-11-13 | 22:24 | 11.5171 | 75612 | 75856 | 75896
9291 | 2021-11-13 | 22:24 | 11.5171 | 75612 | 75857 | 75895
9292 | 2021-11-13 | 22:24 | 11.5172 | 75612 | 75858 | 75894
9293 | 2021-11-13 | 22:24 | 11.5172 | 75612 | 75859 | 75893
9294 | 2021-11-13 | 22:24 | 11.5172 | 75611 | 75860 | 75892
9295 | 2021-11-13 | 22:24 | 11.5172 | 75611 | 75861 | 75891
9296 | 2021-11-13 | 22:24 | 11.5173 | 75611 | 75862 | 75890
9297 | 2021-11-13 | 22:24 | 11.5173 | 75611 | 75863 | 75889
9298 | 2021-11-13 | 22:24 | 11.5173 | 75611 | 75864 | 75888
9299 | 2021-11-13 | 22:24 | 11.5174 | 75611 | 75865 | 75887
9300 | 2021-11-13 | 22:24 | 11.5174 | 75611 | 75866 | 75886
9301 | 2021-11-13 | 22:24 | 11.5174 | 75611 | 75867 | 75885
9302 | 2021-11-13 | 22:24 | 11.5174 | 75611 | 75867 | 75884
9303 | 2021-11-13 | 22:24 | 11.5175 | 75611 | 75868 | 75884
9304 | 2021-11-13 | 22:24 | 11.5175 | 75611 | 75869 | 75883
9305 | 2021-11-13 | 22:24 | 11.5175 | 75611 | 75870 | 75882
9306 | 2021-11-13 | 22:24 | 11.5176 | 75611 | 75871 | 75881
9307 | 2021-11-13 | 22:24 | 11.5176 | 75611 | 75872 | 75880
9308 | 2021-11-13 | 22:24 | 11.5176 | 75611 | 75873 | 75879
9309 | 2021-11-13 | 22:24 | 11.5176 | 75611 | 75874 | 75878
9310 | 2021-11-13 | 22:24 | 11.5177 | 75612 | 75874 | 75877
9311 | 2021-11-13 | 22:24 | 11.5177 | 75612 | 75875 | 75876
9312 | 2021-11-13 | 22:24 | 11.5177 | 75612 | 75876 | 75875
9313 | 2021-11-13 | 22:24 | 11.5178 | 75612 | 75876 | 75874
9314 | 2021-11-13 | 22:24 | 11.5178 | 75613 | 75877 | 75873
9315 | 2021-11-13 | 22:24 | 11.5178 | 75613 | 75877 | 75872
9316 | 2021-11-13 | 22:24 | 11.5178 | 75613 | 75878 | 75871
9317 | 2021-11-13 | 22:24 | 11.5179 | 75614 | 75879 | 75869
9318 | 2021-11-13 | 22:24 | 11.5179 | 75614 | 75879 | 75868
9319 | 2021-11-13 | 22:24 | 11.5179 | 75614 | 75880 | 75867
9320 | 2021-11-13 | 22:24 | 11.518 | 75615 | 75881 | 75866
9321 | 2021-11-13 | 22:24 | 11.518 | 75615 | 75882 | 75865
9322 | 2021-11-13 | 22:24 | 11.518 | 75616 | 75883 | 75864
9323 | 2021-11-13 | 22:24 | 11.518 | 75616 | 75884 | 75863
9324 | 2021-11-13 | 22:24 | 11.5181 | 75617 | 75884 | 75862
9325 | 2021-11-13 | 22:24 | 11.5181 | 75618 | 75885 | 75861
9326 | 2021-11-13 | 22:24 | 11.5181 | 75618 | 75886 | 75860
9327 | 2021-11-13 | 22:24 | 11.5182 | 75619 | 75886 | 75859
9328 | 2021-11-13 | 22:24 | 11.5182 | 75619 | 75887 | 75858
9329 | 2021-11-13 | 22:24 | 11.5182 | 75620 | 75887 | 75857
9330 | 2021-11-13 | 22:24 | 11.5182 | 75621 | 75888 | 75855
9331 | 2021-11-13 | 22:24 | 11.5183 | 75622 | 75888 | 75854
9332 | 2021-11-13 | 22:24 | 11.5183 | 75622 | 75888 | 75853
9333 | 2021-11-13 | 22:24 | 11.5183 | 75623 | 75888 | 75852
9334 | 2021-11-13 | 22:24 | 11.5184 | 75624 | 75888 | 75851
9335 | 2021-11-13 | 22:24 | 11.5184 | 75624 | 75888 | 75850
9336 | 2021-11-13 | 22:24 | 11.5184 | 75625 | 75889 | 75848
9337 | 2021-11-13 | 22:24 | 11.5184 | 75626 | 75889 | 75847
9338 | 2021-11-13 | 22:24 | 11.5185 | 75627 | 75889 | 75846
9339 | 2021-11-13 | 22:24 | 11.5185 | 75628 | 75889 | 75845
9340 | 2021-11-13 | 22:24 | 11.5185 | 75629 | 75889 | 75844
9341 | 2021-11-13 | 22:24 | 11.5186 | 75630 | 75889 | 75842
9342 | 2021-11-13 | 22:24 | 11.5186 | 75630 | 75889 | 75841
9343 | 2021-11-13 | 22:24 | 11.5186 | 75631 | 75889 | 75840
9344 | 2021-11-13 | 22:24 | 11.5186 | 75632 | 75888 | 75839
9345 | 2021-11-13 | 22:24 | 11.5187 | 75633 | 75888 | 75838
9346 | 2021-11-13 | 22:24 | 11.5187 | 75634 | 75888 | 75837
9347 | 2021-11-13 | 22:24 | 11.5187 | 75635 | 75888 | 75836
9348 | 2021-11-13 | 22:24 | 11.5188 | 75636 | 75888 | 75834
9349 | 2021-11-13 | 22:24 | 11.5188 | 75637 | 75888 | 75833
9350 | 2021-11-13 | 22:24 | 11.5188 | 75638 | 75887 | 75832
9351 | 2021-11-13 | 22:24 | 11.5188 | 75639 | 75887 | 75831
9352 | 2021-11-13 | 22:24 | 11.5189 | 75641 | 75887 | 75830
9353 | 2021-11-13 | 22:24 | 11.5189 | 75642 | 75886 | 75829
9354 | 2021-11-13 | 22:24 | 11.5189 | 75643 | 75886 | 75828
9355 | 2021-11-13 | 22:24 | 11.519 | 75644 | 75886 | 75828
9356 | 2021-11-13 | 22:24 | 11.519 | 75645 | 75885 | 75827
9357 | 2021-11-13 | 22:24 | 11.519 | 75646 | 75885 | 75826
9358 | 2021-11-13 | 22:24 | 11.519 | 75647 | 75885 | 75825
9359 | 2021-11-13 | 22:24 | 11.5191 | 75648 | 75884 | 75824
9360 | 2021-11-13 | 22:24 | 11.5191 | 75649 | 75884 | 75823
9361 | 2021-11-13 | 22:24 | 11.5191 | 75650 | 75883 | 75823
9362 | 2021-11-13 | 22:24 | 11.5192 | 75651 | 75883 | 75822
9363 | 2021-11-13 | 22:24 | 11.5192 | 75653 | 75882 | 75821
9364 | 2021-11-13 | 22:24 | 11.5192 | 75654 | 75882 | 75821
9365 | 2021-11-13 | 22:24 | 11.5192 | 75655 | 75882 | 75820
9366 | 2021-11-13 | 22:24 | 11.5193 | 75656 | 75881 | 75820
9367 | 2021-11-13 | 22:24 | 11.5193 | 75658 | 75881 | 75819
9368 | 2021-11-13 | 22:24 | 11.5193 | 75659 | 75880 | 75819
9369 | 2021-11-13 | 22:24 | 11.5194 | 75660 | 75880 | 75818
9370 | 2021-11-13 | 22:24 | 11.5194 | 75662 | 75880 | 75818
9371 | 2021-11-13 | 22:24 | 11.5194 | 75663 | 75879 | 75817
9372 | 2021-11-13 | 22:24 | 11.5194 | 75664 | 75878 | 75817
9373 | 2021-11-13 | 22:24 | 11.5195 | 75665 | 75878 | 75816
9374 | 2021-11-13 | 22:24 | 11.5195 | 75666 | 75877 | 75816
9375 | 2021-11-13 | 22:24 | 11.5195 | 75667 | 75876 | 75816
9376 | 2021-11-13 | 22:24 | 11.5196 | 75668 | 75875 | 75816
9377 | 2021-11-13 | 22:24 | 11.5196 | 75669 | 75874 | 75815
9378 | 2021-11-13 | 22:24 | 11.5196 | 75670 | 75874 | 75815
9379 | 2021-11-13 | 22:24 | 11.5196 | 75672 | 75873 | 75815
9380 | 2021-11-13 | 22:24 | 11.5197 | 75673 | 75872 | 75815
9381 | 2021-11-13 | 22:24 | 11.5197 | 75674 | 75871 | 75814
9382 | 2021-11-13 | 22:24 | 11.5197 | 75675 | 75871 | 75814
9383 | 2021-11-13 | 22:24 | 11.5198 | 75677 | 75870 | 75814
9384 | 2021-11-13 | 22:24 | 11.5198 | 75678 | 75869 | 75814
9385 | 2021-11-13 | 22:24 | 11.5198 | 75679 | 75868 | 75814
9386 | 2021-11-13 | 22:24 | 11.5199 | 75680 | 75867 | 75814
9387 | 2021-11-13 | 22:24 | 11.5199 | 75681 | 75867 | 75814
9388 | 2021-11-13 | 22:24 | 11.5199 | 75682 | 75866 | 75814
9389 | 2021-11-13 | 22:24 | 11.5199 | 75683 | 75865 | 75814
9390 | 2021-11-13 | 22:24 | 11.52 | 75685 | 75864 | 75814
9391 | 2021-11-13 | 22:24 | 11.52 | 75686 | 75863 | 75814
9392 | 2021-11-13 | 22:24 | 11.52 | 75687 | 75863 | 75815
9393 | 2021-11-13 | 22:24 | 11.5201 | 75688 | 75862 | 75815
9394 | 2021-11-13 | 22:24 | 11.5201 | 75690 | 75861 | 75815
9395 | 2021-11-13 | 22:24 | 11.5201 | 75690 | 75860 | 75815
9396 | 2021-11-13 | 22:24 | 11.5201 | 75691 | 75859 | 75815
9397 | 2021-11-13 | 22:24 | 11.5202 | 75692 | 75858 | 75816
9398 | 2021-11-13 | 22:24 | 11.5202 | 75693 | 75858 | 75816
9399 | 2021-11-13 | 22:24 | 11.5202 | 75694 | 75857 | 75816
9400 | 2021-11-13 | 22:24 | 11.5203 | 75695 | 75856 | 75816
9401 | 2021-11-13 | 22:24 | 11.5203 | 75696 | 75855 | 75817
9402 | 2021-11-13 | 22:24 | 11.5203 | 75697 | 75854 | 75817
9403 | 2021-11-13 | 22:24 | 11.5203 | 75698 | 75853 | 75818
9404 | 2021-11-13 | 22:24 | 11.5204 | 75699 | 75852 | 75818
9405 | 2021-11-13 | 22:24 | 11.5204 | 75700 | 75851 | 75819
9406 | 2021-11-13 | 22:24 | 11.5204 | 75701 | 75850 | 75819
9407 | 2021-11-13 | 22:24 | 11.5205 | 75701 | 75850 | 75820
9408 | 2021-11-13 | 22:24 | 11.5205 | 75702 | 75849 | 75820
9409 | 2021-11-13 | 22:24 | 11.5205 | 75703 | 75848 | 75821
9410 | 2021-11-13 | 22:24 | 11.5205 | 75704 | 75847 | 75821
9411 | 2021-11-13 | 22:24 | 11.5206 | 75705 | 75846 | 75822
9412 | 2021-11-13 | 22:24 | 11.5206 | 75706 | 75845 | 75823
9413 | 2021-11-13 | 22:24 | 11.5206 | 75707 | 75844 | 75824
9414 | 2021-11-13 | 22:24 | 11.5207 | 75708 | 75843 | 75824
9415 | 2021-11-13 | 22:24 | 11.5207 | 75708 | 75842 | 75825
9416 | 2021-11-13 | 22:24 | 11.5207 | 75709 | 75841 | 75826
9417 | 2021-11-13 | 22:24 | 11.5207 | 75709 | 75839 | 75826
9418 | 2021-11-13 | 22:24 | 11.5208 | 75710 | 75838 | 75827
9419 | 2021-11-13 | 22:24 | 11.5208 | 75710 | 75837 | 75828
9420 | 2021-11-13 | 22:24 | 11.5208 | 75710 | 75836 | 75829
9421 | 2021-11-13 | 22:24 | 11.5209 | 75711 | 75835 | 75829
9422 | 2021-11-13 | 22:24 | 11.5209 | 75711 | 75834 | 75830
9423 | 2021-11-13 | 22:24 | 11.5209 | 75712 | 75833 | 75831
9424 | 2021-11-13 | 22:24 | 11.5209 | 75712 | 75832 | 75832
9425 | 2021-11-13 | 22:24 | 11.521 | 75712 | 75831 | 75833
9426 | 2021-11-13 | 22:24 | 11.521 | 75712 | 75830 | 75834
9427 | 2021-11-13 | 22:24 | 11.521 | 75712 | 75829 | 75835
9428 | 2021-11-13 | 22:24 | 11.5211 | 75712 | 75828 | 75836
9429 | 2021-11-13 | 22:24 | 11.5211 | 75712 | 75827 | 75837
9430 | 2021-11-13 | 22:24 | 11.5211 | 75712 | 75826 | 75838
9431 | 2021-11-13 | 22:24 | 11.5211 | 75712 | 75825 | 75839
9432 | 2021-11-13 | 22:24 | 11.5212 | 75711 | 75823 | 75840
9433 | 2021-11-13 | 22:24 | 11.5212 | 75711 | 75822 | 75841
9434 | 2021-11-13 | 22:24 | 11.5212 | 75711 | 75821 | 75842
9435 | 2021-11-13 | 22:24 | 11.5213 | 75710 | 75820 | 75843
9436 | 2021-11-13 | 22:24 | 11.5213 | 75710 | 75819 | 75844
9437 | 2021-11-13 | 22:24 | 11.5213 | 75710 | 75818 | 75845
9438 | 2021-11-13 | 22:24 | 11.5213 | 75709 | 75817 | 75847
9439 | 2021-11-13 | 22:24 | 11.5214 | 75709 | 75816 | 75848
9440 | 2021-11-13 | 22:24 | 11.5214 | 75708 | 75815 | 75849
9441 | 2021-11-13 | 22:24 | 11.5214 | 75708 | 75814 | 75850
9442 | 2021-11-13 | 22:24 | 11.5215 | 75707 | 75813 | 75851
9443 | 2021-11-13 | 22:24 | 11.5215 | 75706 | 75812 | 75852
9444 | 2021-11-13 | 22:24 | 11.5215 | 75706 | 75812 | 75853
9445 | 2021-11-13 | 22:24 | 11.5215 | 75705 | 75811 | 75854
9446 | 2021-11-13 | 22:24 | 11.5216 | 75704 | 75810 | 75856
9447 | 2021-11-13 | 22:24 | 11.5216 | 75704 | 75809 | 75857
9448 | 2021-11-13 | 22:24 | 11.5216 | 75703 | 75808 | 75858
9449 | 2021-11-13 | 22:24 | 11.5217 | 75702 | 75808 | 75859
9450 | 2021-11-13 | 22:24 | 11.5217 | 75701 | 75807 | 75860
9451 | 2021-11-13 | 22:24 | 11.5217 | 75700 | 75806 | 75861
9452 | 2021-11-13 | 22:24 | 11.5217 | 75699 | 75806 | 75862
9453 | 2021-11-13 | 22:24 | 11.5218 | 75699 | 75805 | 75863
9454 | 2021-11-13 | 22:24 | 11.5218 | 75698 | 75804 | 75865
9455 | 2021-11-13 | 22:24 | 11.5218 | 75697 | 75804 | 75866
9456 | 2021-11-13 | 22:24 | 11.5219 | 75696 | 75803 | 75867
9457 | 2021-11-13 | 22:24 | 11.5219 | 75695 | 75803 | 75868
9458 | 2021-11-13 | 22:24 | 11.5219 | 75694 | 75803 | 75869
9459 | 2021-11-13 | 22:24 | 11.5219 | 75693 | 75802 | 75870
9460 | 2021-11-13 | 22:24 | 11.522 | 75692 | 75802 | 75871
9461 | 2021-11-13 | 22:24 | 11.522 | 75691 | 75802 | 75872
9462 | 2021-11-13 | 22:24 | 11.522 | 75690 | 75801 | 75873
9463 | 2021-11-13 | 22:24 | 11.5221 | 75689 | 75801 | 75874
9464 | 2021-11-13 | 22:24 | 11.5221 | 75688 | 75801 | 75875
9465 | 2021-11-13 | 22:24 | 11.5221 | 75688 | 75801 | 75876
9466 | 2021-11-13 | 22:24 | 11.5221 | 75687 | 75801 | 75877
9467 | 2021-11-13 | 22:24 | 11.5222 | 75686 | 75800 | 75878
9468 | 2021-11-13 | 22:24 | 11.5222 | 75685 | 75800 | 75879
9469 | 2021-11-13 | 22:24 | 11.5222 | 75684 | 75800 | 75879
9470 | 2021-11-13 | 22:24 | 11.5223 | 75683 | 75800 | 75880
9471 | 2021-11-13 | 22:24 | 11.5223 | 75682 | 75800 | 75881
9472 | 2021-11-13 | 22:24 | 11.5223 | 75681 | 75800 | 75882
9473 | 2021-11-13 | 22:24 | 11.5223 | 75680 | 75800 | 75883
9474 | 2021-11-13 | 22:24 | 11.5224 | 75680 | 75800 | 75884
9475 | 2021-11-13 | 22:24 | 11.5224 | 75679 | 75800 | 75885
9476 | 2021-11-13 | 22:24 | 11.5224 | 75678 | 75801 | 75886
9477 | 2021-11-13 | 22:24 | 11.5225 | 75677 | 75801 | 75887
9478 | 2021-11-13 | 22:24 | 11.5225 | 75676 | 75801 | 75887
9479 | 2021-11-13 | 22:24 | 11.5225 | 75675 | 75801 | 75888
9480 | 2021-11-13 | 22:24 | 11.5226 | 75674 | 75801 | 75889
9481 | 2021-11-13 | 22:24 | 11.5226 | 75672 | 75801 | 75890
9482 | 2021-11-13 | 22:24 | 11.5226 | 75672 | 75802 | 75890
9483 | 2021-11-13 | 22:24 | 11.5226 | 75671 | 75802 | 75891
9484 | 2021-11-13 | 22:24 | 11.5227 | 75670 | 75802 | 75892
9485 | 2021-11-13 | 22:24 | 11.5227 | 75669 | 75803 | 75893
9486 | 2021-11-13 | 22:24 | 11.5227 | 75668 | 75803 | 75894
9487 | 2021-11-13 | 22:24 | 11.5228 | 75667 | 75804 | 75895
9488 | 2021-11-13 | 22:24 | 11.5228 | 75665 | 75804 | 75896
9489 | 2021-11-13 | 22:24 | 11.5228 | 75664 | 75804 | 75897
9490 | 2021-11-13 | 22:24 | 11.5228 | 75663 | 75805 | 75897
9491 | 2021-11-13 | 22:24 | 11.5229 | 75662 | 75805 | 75898
9492 | 2021-11-13 | 22:24 | 11.5229 | 75661 | 75806 | 75898
9493 | 2021-11-13 | 22:24 | 11.5229 | 75660 | 75806 | 75899
9494 | 2021-11-13 | 22:24 | 11.523 | 75658 | 75807 | 75900
9495 | 2021-11-13 | 22:24 | 11.523 | 75657 | 75808 | 75901
9496 | 2021-11-13 | 22:24 | 11.523 | 75656 | 75808 | 75901
9497 | 2021-11-13 | 22:24 | 11.523 | 75655 | 75809 | 75902
9498 | 2021-11-13 | 22:24 | 11.5231 | 75654 | 75809 | 75903
9499 | 2021-11-13 | 22:24 | 11.5231 | 75653 | 75810 | 75904
9500 | 2021-11-13 | 22:24 | 11.5231 | 75652 | 75811 | 75904
9501 | 2021-11-13 | 22:24 | 11.5232 | 75651 | 75811 | 75905
9502 | 2021-11-13 | 22:24 | 11.5232 | 75650 | 75812 | 75905
9503 | 2021-11-13 | 22:24 | 11.5232 | 75649 | 75813 | 75905
9504 | 2021-11-13 | 22:24 | 11.5232 | 75647 | 75814 | 75906
9505 | 2021-11-13 | 22:24 | 11.5233 | 75646 | 75814 | 75906
9506 | 2021-11-13 | 22:24 | 11.5233 | 75645 | 75815 | 75906
9507 | 2021-11-13 | 22:24 | 11.5233 | 75644 | 75816 | 75907
9508 | 2021-11-13 | 22:24 | 11.5234 | 75643 | 75817 | 75907
9509 | 2021-11-13 | 22:24 | 11.5234 | 75642 | 75818 | 75907
9510 | 2021-11-13 | 22:24 | 11.5234 | 75641 | 75819 | 75907
9511 | 2021-11-13 | 22:24 | 11.5234 | 75640 | 75819 | 75907
9512 | 2021-11-13 | 22:24 | 11.5235 | 75639 | 75820 | 75907
9513 | 2021-11-13 | 22:24 | 11.5235 | 75638 | 75821 | 75907
9514 | 2021-11-13 | 22:24 | 11.5235 | 75637 | 75822 | 75907
9515 | 2021-11-13 | 22:24 | 11.5236 | 75636 | 75823 | 75907
9516 | 2021-11-13 | 22:24 | 11.5236 | 75635 | 75824 | 75907
9517 | 2021-11-13 | 22:24 | 11.5236 | 75634 | 75825 | 75907
9518 | 2021-11-13 | 22:24 | 11.5236 | 75633 | 75826 | 75907
9519 | 2021-11-13 | 22:24 | 11.5237 | 75632 | 75827 | 75907
9520 | 2021-11-13 | 22:24 | 11.5237 | 75631 | 75828 | 75907
9521 | 2021-11-13 | 22:24 | 11.5237 | 75629 | 75829 | 75906
9522 | 2021-11-13 | 22:24 | 11.5238 | 75629 | 75830 | 75906
9523 | 2021-11-13 | 22:24 | 11.5238 | 75628 | 75831 | 75906
9524 | 2021-11-13 | 22:24 | 11.5238 | 75627 | 75832 | 75905
9525 | 2021-11-13 | 22:24 | 11.5238 | 75626 | 75833 | 75905
9526 | 2021-11-13 | 22:24 | 11.5239 | 75625 | 75834 | 75905
9527 | 2021-11-13 | 22:24 | 11.5239 | 75624 | 75835 | 75904
9528 | 2021-11-13 | 22:24 | 11.5239 | 75623 | 75837 | 75904
9529 | 2021-11-13 | 22:24 | 11.524 | 75622 | 75838 | 75904
9530 | 2021-11-13 | 22:24 | 11.524 | 75622 | 75839 | 75903
9531 | 2021-11-13 | 22:24 | 11.524 | 75621 | 75840 | 75903
9532 | 2021-11-13 | 22:24 | 11.524 | 75620 | 75841 | 75902
9533 | 2021-11-13 | 22:24 | 11.5241 | 75619 | 75843 | 75902
9534 | 2021-11-13 | 22:24 | 11.5241 | 75619 | 75844 | 75901
9535 | 2021-11-13 | 22:24 | 11.5241 | 75618 | 75845 | 75900
9536 | 2021-11-13 | 22:24 | 11.5242 | 75618 | 75847 | 75900
9537 | 2021-11-13 | 22:24 | 11.5242 | 75617 | 75848 | 75899
9538 | 2021-11-13 | 22:24 | 11.5242 | 75616 | 75849 | 75899
9539 | 2021-11-13 | 22:24 | 11.5242 | 75616 | 75851 | 75898
9540 | 2021-11-13 | 22:24 | 11.5243 | 75615 | 75852 | 75897
9541 | 2021-11-13 | 22:24 | 11.5243 | 75615 | 75854 | 75896
9542 | 2021-11-13 | 22:24 | 11.5243 | 75614 | 75855 | 75896
9543 | 2021-11-13 | 22:24 | 11.5244 | 75614 | 75856 | 75895
9544 | 2021-11-13 | 22:24 | 11.5244 | 75613 | 75857 | 75894
9545 | 2021-11-13 | 22:24 | 11.5244 | 75613 | 75858 | 75894
9546 | 2021-11-13 | 22:24 | 11.5244 | 75613 | 75860 | 75893
9547 | 2021-11-13 | 22:24 | 11.5245 | 75612 | 75861 | 75892
9548 | 2021-11-13 | 22:24 | 11.5245 | 75612 | 75862 | 75891
9549 | 2021-11-13 | 22:24 | 11.5245 | 75612 | 75863 | 75890
9550 | 2021-11-13 | 22:24 | 11.5246 | 75612 | 75864 | 75890
9551 | 2021-11-13 | 22:24 | 11.5246 | 75612 | 75866 | 75889
9552 | 2021-11-13 | 22:24 | 11.5246 | 75611 | 75867 | 75888
9553 | 2021-11-13 | 22:24 | 11.5246 | 75611 | 75868 | 75887
9554 | 2021-11-13 | 22:24 | 11.5247 | 75611 | 75869 | 75886
9555 | 2021-11-13 | 22:24 | 11.5247 | 75611 | 75870 | 75885
9556 | 2021-11-13 | 22:24 | 11.5247 | 75611 | 75871 | 75884
9557 | 2021-11-13 | 22:24 | 11.5248 | 75611 | 75872 | 75884
9558 | 2021-11-13 | 22:24 | 11.5248 | 75611 | 75873 | 75883
9559 | 2021-11-13 | 22:24 | 11.5248 | 75611 | 75874 | 75882
9560 | 2021-11-13 | 22:24 | 11.5248 | 75611 | 75875 | 75881
9561 | 2021-11-13 | 22:24 | 11.5249 | 75611 | 75877 | 75880
9562 | 2021-11-13 | 22:24 | 11.5249 | 75611 | 75878 | 75879
9563 | 2021-11-13 | 22:24 | 11.5249 | 75612 | 75879 | 75878
9564 | 2021-11-13 | 22:24 | 11.525 | 75612 | 75880 | 75877
9565 | 2021-11-13 | 22:24 | 11.525 | 75612 | 75880 | 75876
9566 | 2021-11-13 | 22:24 | 11.525 | 75612 | 75881 | 75875
9567 | 2021-11-13 | 22:24 | 11.525 | 75612 | 75882 | 75874
9568 | 2021-11-13 | 22:24 | 11.5251 | 75613 | 75883 | 75873
9569 | 2021-11-13 | 22:24 | 11.5251 | 75613 | 75883 | 75872
9570 | 2021-11-13 | 22:24 | 11.5251 | 75613 | 75884 | 75871
9571 | 2021-11-13 | 22:24 | 11.5252 | 75614 | 75885 | 75870
9572 | 2021-11-13 | 22:24 | 11.5252 | 75614 | 75886 | 75869
9573 | 2021-11-13 | 22:24 | 11.5252 | 75614 | 75887 | 75868
9574 | 2021-11-13 | 22:24 | 11.5253 | 75615 | 75888 | 75867
9575 | 2021-11-13 | 22:24 | 11.5253 | 75615 | 75889 | 75865
9576 | 2021-11-13 | 22:24 | 11.5253 | 75616 | 75889 | 75864
9577 | 2021-11-13 | 22:24 | 11.5253 | 75616 | 75890 | 75863
9578 | 2021-11-13 | 22:24 | 11.5254 | 75617 | 75891 | 75862
9579 | 2021-11-13 | 22:24 | 11.5254 | 75617 | 75892 | 75861
9580 | 2021-11-13 | 22:24 | 11.5254 | 75618 | 75893 | 75860
9581 | 2021-11-13 | 22:24 | 11.5255 | 75619 | 75894 | 75859
9582 | 2021-11-13 | 22:24 | 11.5255 | 75619 | 75894 | 75858
9583 | 2021-11-13 | 22:24 | 11.5255 | 75620 | 75895 | 75857
9584 | 2021-11-13 | 22:24 | 11.5255 | 75621 | 75895 | 75856
9585 | 2021-11-13 | 22:24 | 11.5256 | 75621 | 75896 | 75855
9586 | 2021-11-13 | 22:24 | 11.5256 | 75622 | 75896 | 75854
9587 | 2021-11-13 | 22:24 | 11.5256 | 75623 | 75896 | 75853
9588 | 2021-11-13 | 22:24 | 11.5257 | 75623 | 75897 | 75851
9589 | 2021-11-13 | 22:24 | 11.5257 | 75624 | 75897 | 75850
9590 | 2021-11-13 | 22:24 | 11.5257 | 75625 | 75897 | 75849
9591 | 2021-11-13 | 22:24 | 11.5257 | 75626 | 75898 | 75848
9592 | 2021-11-13 | 22:24 | 11.5258 | 75626 | 75898 | 75847
9593 | 2021-11-13 | 22:24 | 11.5258 | 75627 | 75898 | 75846
9594 | 2021-11-13 | 22:24 | 11.5258 | 75628 | 75898 | 75845
9595 | 2021-11-13 | 22:24 | 11.5259 | 75629 | 75898 | 75844
9596 | 2021-11-13 | 22:24 | 11.5259 | 75630 | 75898 | 75843
9597 | 2021-11-13 | 22:24 | 11.5259 | 75630 | 75898 | 75842
9598 | 2021-11-13 | 22:24 | 11.5259 | 75631 | 75898 | 75840
9599 | 2021-11-13 | 22:24 | 11.526 | 75632 | 75898 | 75839
9600 | 2021-11-13 | 22:24 | 11.526 | 75633 | 75898 | 75838
9601 | 2021-11-13 | 22:24 | 11.526 | 75634 | 75898 | 75837
9602 | 2021-11-13 | 22:24 | 11.5261 | 75635 | 75898 | 75836
9603 | 2021-11-13 | 22:24 | 11.5261 | 75636 | 75898 | 75835
9604 | 2021-11-13 | 22:24 | 11.5261 | 75638 | 75898 | 75834
9605 | 2021-11-13 | 22:24 | 11.5261 | 75639 | 75898 | 75833
9606 | 2021-11-13 | 22:24 | 11.5262 | 75640 | 75897 | 75832
9607 | 2021-11-13 | 22:24 | 11.5262 | 75641 | 75897 | 75831
9608 | 2021-11-13 | 22:24 | 11.5262 | 75642 | 75897 | 75830
9609 | 2021-11-13 | 22:24 | 11.5263 | 75643 | 75897 | 75829
9610 | 2021-11-13 | 22:24 | 11.5263 | 75644 | 75897 | 75828
9611 | 2021-11-13 | 22:24 | 11.5263 | 75645 | 75896 | 75827
9612 | 2021-11-13 | 22:24 | 11.5263 | 75646 | 75896 | 75826
9613 | 2021-11-13 | 22:24 | 11.5264 | 75647 | 75896 | 75825
9614 | 2021-11-13 | 22:24 | 11.5264 | 75648 | 75895 | 75824
9615 | 2021-11-13 | 22:24 | 11.5264 | 75650 | 75895 | 75824
9616 | 2021-11-13 | 22:24 | 11.5265 | 75651 | 75894 | 75823
9617 | 2021-11-13 | 22:24 | 11.5265 | 75652 | 75893 | 75822
9618 | 2021-11-13 | 22:24 | 11.5265 | 75653 | 75893 | 75821
9619 | 2021-11-13 | 22:24 | 11.5265 | 75654 | 75892 | 75821
9620 | 2021-11-13 | 22:24 | 11.5266 | 75655 | 75891 | 75820
9621 | 2021-11-13 | 22:24 | 11.5266 | 75656 | 75891 | 75819
9622 | 2021-11-13 | 22:24 | 11.5266 | 75658 | 75890 | 75819
9623 | 2021-11-13 | 22:24 | 11.5267 | 75659 | 75890 | 75818
9624 | 2021-11-13 | 22:24 | 11.5267 | 75660 | 75889 | 75818
9625 | 2021-11-13 | 22:24 | 11.5267 | 75662 | 75889 | 75817
9626 | 2021-11-13 | 22:24 | 11.5267 | 75663 | 75888 | 75817
9627 | 2021-11-13 | 22:24 | 11.5268 | 75664 | 75887 | 75816
9628 | 2021-11-13 | 22:24 | 11.5268 | 75665 | 75886 | 75816
9629 | 2021-11-13 | 22:24 | 11.5268 | 75666 | 75884 | 75815
9630 | 2021-11-13 | 22:24 | 11.5269 | 75667 | 75883 | 75815
9631 | 2021-11-13 | 22:24 | 11.5269 | 75668 | 75882 | 75815
9632 | 2021-11-13 | 22:24 | 11.5269 | 75670 | 75881 | 75814
9633 | 2021-11-13 | 22:24 | 11.5269 | 75671 | 75880 | 75814
9634 | 2021-11-13 | 22:24 | 11.527 | 75672 | 75879 | 75814
9635 | 2021-11-13 | 22:24 | 11.527 | 75673 | 75878 | 75814
9636 | 2021-11-13 | 22:24 | 11.527 | 75674 | 75876 | 75813
9637 | 2021-11-13 | 22:24 | 11.5271 | 75675 | 75875 | 75813
9638 | 2021-11-13 | 22:24 | 11.5271 | 75676 | 75874 | 75813
9639 | 2021-11-13 | 22:24 | 11.5271 | 75677 | 75873 | 75813
9640 | 2021-11-13 | 22:24 | 11.5271 | 75678 | 75872 | 75813
9641 | 2021-11-13 | 22:24 | 11.5272 | 75679 | 75871 | 75813
9642 | 2021-11-13 | 22:24 | 11.5272 | 75680 | 75870 | 75813
9643 | 2021-11-13 | 22:24 | 11.5272 | 75681 | 75869 | 75813
9644 | 2021-11-13 | 22:24 | 11.5273 | 75682 | 75868 | 75813
9645 | 2021-11-13 | 22:24 | 11.5273 | 75683 | 75867 | 75813
9646 | 2021-11-13 | 22:24 | 11.5273 | 75684 | 75866 | 75813
9647 | 2021-11-13 | 22:24 | 11.5273 | 75685 | 75865 | 75813
9648 | 2021-11-13 | 22:24 | 11.5274 | 75686 | 75864 | 75813
9649 | 2021-11-13 | 22:24 | 11.5274 | 75687 | 75863 | 75813
9650 | 2021-11-13 | 22:24 | 11.5274 | 75688 | 75862 | 75814
9651 | 2021-11-13 | 22:24 | 11.5275 | 75688 | 75861 | 75814
9652 | 2021-11-13 | 22:24 | 11.5275 | 75689 | 75860 | 75814
9653 | 2021-11-13 | 22:24 | 11.5275 | 75690 | 75859 | 75814
9654 | 2021-11-13 | 22:24 | 11.5275 | 75691 | 75858 | 75815
9655 | 2021-11-13 | 22:24 | 11.5276 | 75692 | 75857 | 75815
9656 | 2021-11-13 | 22:24 | 11.5276 | 75692 | 75856 | 75815
9657 | 2021-11-13 | 22:24 | 11.5276 | 75693 | 75855 | 75816
9658 | 2021-11-13 | 22:24 | 11.5277 | 75693 | 75854 | 75816
9659 | 2021-11-13 | 22:24 | 11.5277 | 75694 | 75853 | 75816
9660 | 2021-11-13 | 22:24 | 11.5277 | 75694 | 75852 | 75817
9661 | 2021-11-13 | 22:24 | 11.5277 | 75695 | 75851 | 75817
9662 | 2021-11-13 | 22:24 | 11.5278 | 75695 | 75850 | 75818
9663 | 2021-11-13 | 22:24 | 11.5278 | 75696 | 75849 | 75818
9664 | 2021-11-13 | 22:24 | 11.5278 | 75697 | 75848 | 75819
9665 | 2021-11-13 | 22:24 | 11.5279 | 75698 | 75847 | 75819
9666 | 2021-11-13 | 22:24 | 11.5279 | 75698 | 75846 | 75820
9667 | 2021-11-13 | 22:24 | 11.5279 | 75699 | 75845 | 75820
9668 | 2021-11-13 | 22:24 | 11.528 | 75699 | 75844 | 75821
9669 | 2021-11-13 | 22:24 | 11.528 | 75699 | 75843 | 75822
9670 | 2021-11-13 | 22:24 | 11.528 | 75700 | 75842 | 75822
9671 | 2021-11-13 | 22:24 | 11.528 | 75700 | 75841 | 75823
9672 | 2021-11-13 | 22:24 | 11.5281 | 75700 | 75839 | 75823
9673 | 2021-11-13 | 22:24 | 11.5281 | 75701 | 75838 | 75824
9674 | 2021-11-13 | 22:24 | 11.5281 | 75701 | 75837 | 75825
9675 | 2021-11-13 | 22:24 | 11.5282 | 75701 | 75836 | 75826
9676 | 2021-11-13 | 22:24 | 11.5282 | 75701 | 75835 | 75826
9677 | 2021-11-13 | 22:24 | 11.5282 | 75702 | 75834 | 75827
9678 | 2021-11-13 | 22:24 | 11.5282 | 75702 | 75833 | 75828
9679 | 2021-11-13 | 22:24 | 11.5283 | 75702 | 75832 | 75829
9680 | 2021-11-13 | 22:24 | 11.5283 | 75702 | 75830 | 75830
9681 | 2021-11-13 | 22:24 | 11.5283 | 75702 | 75829 | 75831
9682 | 2021-11-13 | 22:24 | 11.5284 | 75703 | 75828 | 75831
9683 | 2021-11-13 | 22:24 | 11.5284 | 75703 | 75827 | 75832
9684 | 2021-11-13 | 22:24 | 11.5284 | 75703 | 75826 | 75833
9685 | 2021-11-13 | 22:24 | 11.5284 | 75703 | 75825 | 75834
9686 | 2021-11-13 | 22:24 | 11.5285 | 75703 | 75824 | 75835
9687 | 2021-11-13 | 22:24 | 11.5285 | 75703 | 75823 | 75836
9688 | 2021-11-13 | 22:24 | 11.5285 | 75703 | 75822 | 75837
9689 | 2021-11-13 | 22:24 | 11.5286 | 75703 | 75821 | 75839
9690 | 2021-11-13 | 22:24 | 11.5286 | 75703 | 75820 | 75840
9691 | 2021-11-13 | 22:24 | 11.5286 | 75703 | 75819 | 75841
9692 | 2021-11-13 | 22:24 | 11.5286 | 75703 | 75818 | 75842
9693 | 2021-11-13 | 22:24 | 11.5287 | 75703 | 75817 | 75843
9694 | 2021-11-13 | 22:24 | 11.5287 | 75702 | 75817 | 75844
9695 | 2021-11-13 | 22:24 | 11.5287 | 75702 | 75816 | 75845
9696 | 2021-11-13 | 22:24 | 11.5288 | 75702 | 75815 | 75846
9697 | 2021-11-13 | 22:24 | 11.5288 | 75702 | 75814 | 75847
9698 | 2021-11-13 | 22:24 | 11.5288 | 75701 | 75813 | 75848
9699 | 2021-11-13 | 22:24 | 11.5288 | 75701 | 75812 | 75849
9700 | 2021-11-13 | 22:24 | 11.5289 | 75700 | 75812 | 75851
9701 | 2021-11-13 | 22:24 | 11.5289 | 75700 | 75811 | 75851
9702 | 2021-11-13 | 22:24 | 11.5289 | 75699 | 75810 | 75853
9703 | 2021-11-13 | 22:24 | 11.529 | 75698 | 75810 | 75854
9704 | 2021-11-13 | 22:24 | 11.529 | 75698 | 75809 | 75855
9705 | 2021-11-13 | 22:24 | 11.529 | 75697 | 75808 | 75856
9706 | 2021-11-13 | 22:24 | 11.529 | 75697 | 75808 | 75857
9707 | 2021-11-13 | 22:24 | 11.5291 | 75696 | 75807 | 75859
9708 | 2021-11-13 | 22:24 | 11.5291 | 75696 | 75807 | 75860
9709 | 2021-11-13 | 22:24 | 11.5291 | 75695 | 75806 | 75861
9710 | 2021-11-13 | 22:24 | 11.5292 | 75694 | 75805 | 75862
9711 | 2021-11-13 | 22:24 | 11.5292 | 75693 | 75805 | 75863
9712 | 2021-11-13 | 22:24 | 11.5292 | 75693 | 75805 | 75864
9713 | 2021-11-13 | 22:24 | 11.5292 | 75692 | 75804 | 75866
9714 | 2021-11-13 | 22:24 | 11.5293 | 75691 | 75804 | 75867
9715 | 2021-11-13 | 22:24 | 11.5293 | 75690 | 75803 | 75868
9716 | 2021-11-13 | 22:24 | 11.5293 | 75689 | 75803 | 75869
9717 | 2021-11-13 | 22:24 | 11.5294 | 75689 | 75803 | 75870
9718 | 2021-11-13 | 22:24 | 11.5294 | 75688 | 75802 | 75871
9719 | 2021-11-13 | 22:24 | 11.5294 | 75687 | 75802 | 75872
9720 | 2021-11-13 | 22:24 | 11.5294 | 75686 | 75802 | 75873
9721 | 2021-11-13 | 22:24 | 11.5295 | 75685 | 75802 | 75874
9722 | 2021-11-13 | 22:24 | 11.5295 | 75684 | 75802 | 75875
9723 | 2021-11-13 | 22:24 | 11.5295 | 75683 | 75802 | 75876
9724 | 2021-11-13 | 22:24 | 11.5296 | 75682 | 75801 | 75878
9725 | 2021-11-13 | 22:24 | 11.5296 | 75681 | 75801 | 75879
9726 | 2021-11-13 | 22:24 | 11.5296 | 75681 | 75801 | 75880
9727 | 2021-11-13 | 22:24 | 11.5296 | 75680 | 75801 | 75881
9728 | 2021-11-13 | 22:24 | 11.5297 | 75679 | 75801 | 75882
9729 | 2021-11-13 | 22:24 | 11.5297 | 75678 | 75801 | 75883
9730 | 2021-11-13 | 22:24 | 11.5297 | 75677 | 75801 | 75884
9731 | 2021-11-13 | 22:24 | 11.5298 | 75676 | 75802 | 75885
9732 | 2021-11-13 | 22:24 | 11.5298 | 75675 | 75802 | 75886
9733 | 2021-11-13 | 22:24 | 11.5298 | 75674 | 75802 | 75887
9734 | 2021-11-13 | 22:24 | 11.5298 | 75673 | 75802 | 75887
9735 | 2021-11-13 | 22:24 | 11.5299 | 75672 | 75802 | 75888
9736 | 2021-11-13 | 22:24 | 11.5299 | 75671 | 75802 | 75889
9737 | 2021-11-13 | 22:24 | 11.5299 | 75670 | 75803 | 75890
9738 | 2021-11-13 | 22:24 | 11.53 | 75669 | 75803 | 75891
9739 | 2021-11-13 | 22:24 | 11.53 | 75668 | 75803 | 75892
9740 | 2021-11-13 | 22:24 | 11.53 | 75667 | 75804 | 75893
9741 | 2021-11-13 | 22:24 | 11.53 | 75666 | 75804 | 75894
9742 | 2021-11-13 | 22:24 | 11.5301 | 75665 | 75804 | 75895
9743 | 2021-11-13 | 22:24 | 11.5301 | 75665 | 75805 | 75896
9744 | 2021-11-13 | 22:24 | 11.5301 | 75664 | 75805 | 75897
9745 | 2021-11-13 | 22:24 | 11.5302 | 75663 | 75805 | 75898
9746 | 2021-11-13 | 22:24 | 11.5302 | 75662 | 75806 | 75898
9747 | 2021-11-13 | 22:24 | 11.5302 | 75661 | 75806 | 75899
9748 | 2021-11-13 | 22:24 | 11.5302 | 75660 | 75807 | 75900
9749 | 2021-11-13 | 22:24 | 11.5303 | 75659 | 75807 | 75901
9750 | 2021-11-13 | 22:24 | 11.5303 | 75658 | 75808 | 75902
9751 | 2021-11-13 | 22:24 | 11.5303 | 75657 | 75808 | 75903
9752 | 2021-11-13 | 22:24 | 11.5304 | 75656 | 75809 | 75903
9753 | 2021-11-13 | 22:24 | 11.5304 | 75655 | 75809 | 75904
9754 | 2021-11-13 | 22:24 | 11.5304 | 75654 | 75810 | 75905
9755 | 2021-11-13 | 22:24 | 11.5304 | 75653 | 75810 | 75906
9756 | 2021-11-13 | 22:24 | 11.5305 | 75652 | 75811 | 75906
9757 | 2021-11-13 | 22:24 | 11.5305 | 75651 | 75812 | 75907
9758 | 2021-11-13 | 22:24 | 11.5305 | 75650 | 75813 | 75907
9759 | 2021-11-13 | 22:24 | 11.5306 | 75649 | 75813 | 75908
9760 | 2021-11-13 | 22:24 | 11.5306 | 75648 | 75814 | 75908
9761 | 2021-11-13 | 22:24 | 11.5306 | 75647 | 75815 | 75909
9762 | 2021-11-13 | 22:24 | 11.5307 | 75646 | 75816 | 75909
9763 | 2021-11-13 | 22:24 | 11.5307 | 75645 | 75816 | 75909
9764 | 2021-11-13 | 22:24 | 11.5307 | 75644 | 75817 | 75909
9765 | 2021-11-13 | 22:24 | 11.5307 | 75643 | 75818 | 75909
9766 | 2021-11-13 | 22:24 | 11.5308 | 75642 | 75819 | 75909
9767 | 2021-11-13 | 22:24 | 11.5308 | 75640 | 75820 | 75909
9768 | 2021-11-13 | 22:24 | 11.5308 | 75639 | 75821 | 75910
9769 | 2021-11-13 | 22:24 | 11.5309 | 75638 | 75822 | 75910
9770 | 2021-11-13 | 22:24 | 11.5309 | 75637 | 75823 | 75910
9771 | 2021-11-13 | 22:24 | 11.5309 | 75636 | 75824 | 75910
9772 | 2021-11-13 | 22:24 | 11.5309 | 75635 | 75825 | 75910
9773 | 2021-11-13 | 22:24 | 11.531 | 75634 | 75826 | 75910
9774 | 2021-11-13 | 22:24 | 11.531 | 75633 | 75828 | 75910
9775 | 2021-11-13 | 22:24 | 11.531 | 75632 | 75829 | 75909
9776 | 2021-11-13 | 22:24 | 11.5311 | 75631 | 75830 | 75909
9777 | 2021-11-13 | 22:24 | 11.5311 | 75630 | 75831 | 75909
9778 | 2021-11-13 | 22:24 | 11.5311 | 75629 | 75832 | 75909
9779 | 2021-11-13 | 22:24 | 11.5311 | 75628 | 75833 | 75908
9780 | 2021-11-13 | 22:24 | 11.5312 | 75627 | 75835 | 75908
9781 | 2021-11-13 | 22:24 | 11.5312 | 75626 | 75836 | 75908
9782 | 2021-11-13 | 22:24 | 11.5312 | 75625 | 75837 | 75907
9783 | 2021-11-13 | 22:24 | 11.5313 | 75624 | 75838 | 75907
9784 | 2021-11-13 | 22:24 | 11.5313 | 75623 | 75839 | 75906
9785 | 2021-11-13 | 22:24 | 11.5313 | 75622 | 75840 | 75906
9786 | 2021-11-13 | 22:24 | 11.5313 | 75622 | 75841 | 75905
9787 | 2021-11-13 | 22:24 | 11.5314 | 75621 | 75842 | 75904
9788 | 2021-11-13 | 22:24 | 11.5314 | 75620 | 75843 | 75904
9789 | 2021-11-13 | 22:24 | 11.5314 | 75619 | 75845 | 75903
9790 | 2021-11-13 | 22:24 | 11.5315 | 75619 | 75846 | 75903
9791 | 2021-11-13 | 22:24 | 11.5315 | 75618 | 75847 | 75902
9792 | 2021-11-13 | 22:24 | 11.5315 | 75617 | 75848 | 75902
9793 | 2021-11-13 | 22:24 | 11.5315 | 75617 | 75850 | 75901
9794 | 2021-11-13 | 22:24 | 11.5316 | 75616 | 75851 | 75900
9795 | 2021-11-13 | 22:24 | 11.5316 | 75616 | 75852 | 75899
9796 | 2021-11-13 | 22:24 | 11.5316 | 75615 | 75852 | 75899
9797 | 2021-11-13 | 22:24 | 11.5317 | 75615 | 75853 | 75898
9798 | 2021-11-13 | 22:24 | 11.5317 | 75614 | 75854 | 75897
9799 | 2021-11-13 | 22:24 | 11.5317 | 75614 | 75856 | 75896
9800 | 2021-11-13 | 22:24 | 11.5317 | 75614 | 75857 | 75895
9801 | 2021-11-13 | 22:24 | 11.5318 | 75613 | 75858 | 75895
9802 | 2021-11-13 | 22:24 | 11.5318 | 75613 | 75859 | 75894
9803 | 2021-11-13 | 22:24 | 11.5318 | 75613 | 75860 | 75893
9804 | 2021-11-13 | 22:24 | 11.5319 | 75612 | 75861 | 75892
9805 | 2021-11-13 | 22:24 | 11.5319 | 75612 | 75862 | 75891
9806 | 2021-11-13 | 22:24 | 11.5319 | 75612 | 75863 | 75890
9807 | 2021-11-13 | 22:24 | 11.5319 | 75612 | 75864 | 75889
9808 | 2021-11-13 | 22:24 | 11.532 | 75612 | 75865 | 75888
9809 | 2021-11-13 | 22:24 | 11.532 | 75612 | 75866 | 75887
9810 | 2021-11-13 | 22:24 | 11.532 | 75612 | 75866 | 75886
9811 | 2021-11-13 | 22:24 | 11.5321 | 75612 | 75867 | 75885
9812 | 2021-11-13 | 22:24 | 11.5321 | 75612 | 75869 | 75884
9813 | 2021-11-13 | 22:24 | 11.5321 | 75612 | 75870 | 75883
9814 | 2021-11-13 | 22:24 | 11.5321 | 75612 | 75871 | 75882
9815 | 2021-11-13 | 22:24 | 11.5322 | 75612 | 75871 | 75881
9816 | 2021-11-13 | 22:24 | 11.5322 | 75612 | 75872 | 75880
9817 | 2021-11-13 | 22:24 | 11.5322 | 75612 | 75873 | 75878
9818 | 2021-11-13 | 22:24 | 11.5323 | 75612 | 75874 | 75877
9819 | 2021-11-13 | 22:24 | 11.5323 | 75612 | 75875 | 75876
9820 | 2021-11-13 | 22:24 | 11.5323 | 75612 | 75876 | 75875
9821 | 2021-11-13 | 22:24 | 11.5323 | 75613 | 75877 | 75874
9822 | 2021-11-13 | 22:24 | 11.5324 | 75613 | 75878 | 75873
9823 | 2021-11-13 | 22:24 | 11.5324 | 75613 | 75879 | 75872
9824 | 2021-11-13 | 22:24 | 11.5324 | 75613 | 75880 | 75871
9825 | 2021-11-13 | 22:24 | 11.5325 | 75614 | 75881 | 75870
9826 | 2021-11-13 | 22:24 | 11.5325 | 75614 | 75881 | 75869
9827 | 2021-11-13 | 22:24 | 11.5325 | 75614 | 75882 | 75868
9828 | 2021-11-13 | 22:24 | 11.5325 | 75615 | 75883 | 75867
9829 | 2021-11-13 | 22:24 | 11.5326 | 75615 | 75884 | 75866
9830 | 2021-11-13 | 22:24 | 11.5326 | 75615 | 75884 | 75865
9831 | 2021-11-13 | 22:24 | 11.5326 | 75616 | 75885 | 75864
9832 | 2021-11-13 | 22:24 | 11.5327 | 75616 | 75886 | 75863
9833 | 2021-11-13 | 22:24 | 11.5327 | 75617 | 75887 | 75862
9834 | 2021-11-13 | 22:24 | 11.5327 | 75617 | 75888 | 75861
9835 | 2021-11-13 | 22:24 | 11.5327 | 75618 | 75889 | 75860
9836 | 2021-11-13 | 22:24 | 11.5328 | 75619 | 75890 | 75859
9837 | 2021-11-13 | 22:24 | 11.5328 | 75619 | 75891 | 75859
9838 | 2021-11-13 | 22:24 | 11.5328 | 75620 | 75892 | 75858
9839 | 2021-11-13 | 22:24 | 11.5329 | 75620 | 75892 | 75857
9840 | 2021-11-13 | 22:24 | 11.5329 | 75621 | 75893 | 75856
9841 | 2021-11-13 | 22:24 | 11.5329 | 75622 | 75894 | 75855
9842 | 2021-11-13 | 22:24 | 11.5329 | 75623 | 75894 | 75854
9843 | 2021-11-13 | 22:24 | 11.533 | 75623 | 75895 | 75852
9844 | 2021-11-13 | 22:24 | 11.533 | 75624 | 75895 | 75851
9845 | 2021-11-13 | 22:24 | 11.533 | 75625 | 75895 | 75850
9846 | 2021-11-13 | 22:24 | 11.5331 | 75625 | 75896 | 75849
9847 | 2021-11-13 | 22:24 | 11.5331 | 75626 | 75896 | 75848
9848 | 2021-11-13 | 22:24 | 11.5331 | 75627 | 75896 | 75846
9849 | 2021-11-13 | 22:24 | 11.5331 | 75628 | 75896 | 75845
9850 | 2021-11-13 | 22:24 | 11.5332 | 75629 | 75897 | 75844
9851 | 2021-11-13 | 22:24 | 11.5332 | 75630 | 75897 | 75843
9852 | 2021-11-13 | 22:24 | 11.5332 | 75631 | 75897 | 75842
9853 | 2021-11-13 | 22:24 | 11.5333 | 75632 | 75897 | 75841
9854 | 2021-11-13 | 22:24 | 11.5333 | 75633 | 75897 | 75840
9855 | 2021-11-13 | 22:24 | 11.5333 | 75634 | 75897 | 75839
9856 | 2021-11-13 | 22:24 | 11.5334 | 75635 | 75896 | 75838
9857 | 2021-11-13 | 22:24 | 11.5334 | 75636 | 75896 | 75837
9858 | 2021-11-13 | 22:24 | 11.5334 | 75637 | 75896 | 75835
9859 | 2021-11-13 | 22:24 | 11.5334 | 75638 | 75896 | 75834
9860 | 2021-11-13 | 22:24 | 11.5335 | 75639 | 75896 | 75833
9861 | 2021-11-13 | 22:24 | 11.5335 | 75640 | 75895 | 75832
9862 | 2021-11-13 | 22:24 | 11.5335 | 75641 | 75895 | 75831
9863 | 2021-11-13 | 22:24 | 11.5336 | 75642 | 75895 | 75830
9864 | 2021-11-13 | 22:24 | 11.5336 | 75644 | 75895 | 75829
9865 | 2021-11-13 | 22:24 | 11.5336 | 75645 | 75894 | 75828
9866 | 2021-11-13 | 22:24 | 11.5336 | 75646 | 75894 | 75827
9867 | 2021-11-13 | 22:24 | 11.5337 | 75647 | 75893 | 75826
9868 | 2021-11-13 | 22:24 | 11.5337 | 75648 | 75893 | 75826
9869 | 2021-11-13 | 22:24 | 11.5337 | 75649 | 75892 | 75825
9870 | 2021-11-13 | 22:24 | 11.5338 | 75650 | 75892 | 75824
9871 | 2021-11-13 | 22:24 | 11.5338 | 75651 | 75892 | 75823
9872 | 2021-11-13 | 22:24 | 11.5338 | 75652 | 75891 | 75822
9873 | 2021-11-13 | 22:24 | 11.5338 | 75654 | 75891 | 75822
9874 | 2021-11-13 | 22:24 | 11.5339 | 75655 | 75891 | 75821
9875 | 2021-11-13 | 22:24 | 11.5339 | 75656 | 75890 | 75820
9876 | 2021-11-13 | 22:24 | 11.5339 | 75658 | 75890 | 75819
9877 | 2021-11-13 | 22:24 | 11.534 | 75659 | 75890 | 75819
9878 | 2021-11-13 | 22:24 | 11.534 | 75660 | 75889 | 75818
9879 | 2021-11-13 | 22:24 | 11.534 | 75662 | 75889 | 75818
9880 | 2021-11-13 | 22:24 | 11.534 | 75663 | 75888 | 75817
9881 | 2021-11-13 | 22:24 | 11.5341 | 75664 | 75888 | 75817
9882 | 2021-11-13 | 22:24 | 11.5341 | 75666 | 75887 | 75816
9883 | 2021-11-13 | 22:24 | 11.5341 | 75667 | 75886 | 75816
9884 | 2021-11-13 | 22:24 | 11.5342 | 75668 | 75885 | 75815
9885 | 2021-11-13 | 22:24 | 11.5342 | 75669 | 75885 | 75815
9886 | 2021-11-13 | 22:24 | 11.5342 | 75671 | 75884 | 75815
9887 | 2021-11-13 | 22:24 | 11.5342 | 75672 | 75883 | 75814
9888 | 2021-11-13 | 22:24 | 11.5343 | 75673 | 75882 | 75814
9889 | 2021-11-13 | 22:24 | 11.5343 | 75674 | 75881 | 75814
9890 | 2021-11-13 | 22:24 | 11.5343 | 75675 | 75880 | 75813
9891 | 2021-11-13 | 22:24 | 11.5344 | 75677 | 75879 | 75813
9892 | 2021-11-13 | 22:24 | 11.5344 | 75678 | 75878 | 75813
9893 | 2021-11-13 | 22:24 | 11.5344 | 75679 | 75877 | 75813
9894 | 2021-11-13 | 22:24 | 11.5344 | 75680 | 75876 | 75813
9895 | 2021-11-13 | 22:24 | 11.5345 | 75681 | 75875 | 75813
9896 | 2021-11-13 | 22:24 | 11.5345 | 75682 | 75874 | 75813
9897 | 2021-11-13 | 22:24 | 11.5345 | 75683 | 75873 | 75813
9898 | 2021-11-13 | 22:24 | 11.5346 | 75684 | 75873 | 75813
9899 | 2021-11-13 | 22:24 | 11.5346 | 75685 | 75872 | 75813
9900 | 2021-11-13 | 22:24 | 11.5346 | 75686 | 75871 | 75813
9901 | 2021-11-13 | 22:24 | 11.5346 | 75687 | 75870 | 75813
9902 | 2021-11-13 | 22:24 | 11.5347 | 75688 | 75869 | 75813
9903 | 2021-11-13 | 22:24 | 11.5347 | 75689 | 75868 | 75813
9904 | 2021-11-13 | 22:24 | 11.5347 | 75690 | 75867 | 75813
9905 | 2021-11-13 | 22:24 | 11.5348 | 75691 | 75866 | 75813
9906 | 2021-11-13 | 22:24 | 11.5348 | 75692 | 75865 | 75814
9907 | 2021-11-13 | 22:24 | 11.5348 | 75693 | 75864 | 75814
9908 | 2021-11-13 | 22:24 | 11.5348 | 75694 | 75863 | 75814
9909 | 2021-11-13 | 22:24 | 11.5349 | 75695 | 75862 | 75814
9910 | 2021-11-13 | 22:24 | 11.5349 | 75696 | 75861 | 75815
9911 | 2021-11-13 | 22:24 | 11.5349 | 75697 | 75860 | 75815
9912 | 2021-11-13 | 22:24 | 11.535 | 75698 | 75859 | 75815
9913 | 2021-11-13 | 22:24 | 11.535 | 75698 | 75858 | 75816
9914 | 2021-11-13 | 22:24 | 11.535 | 75699 | 75857 | 75816
9915 | 2021-11-13 | 22:24 | 11.535 | 75699 | 75856 | 75816
9916 | 2021-11-13 | 22:24 | 11.5351 | 75700 | 75854 | 75817
9917 | 2021-11-13 | 22:24 | 11.5351 | 75701 | 75853 | 75817
9918 | 2021-11-13 | 22:24 | 11.5351 | 75701 | 75852 | 75818
9919 | 2021-11-13 | 22:24 | 11.5352 | 75702 | 75851 | 75818
9920 | 2021-11-13 | 22:24 | 11.5352 | 75703 | 75850 | 75819
9921 | 2021-11-13 | 22:24 | 11.5352 | 75703 | 75849 | 75819
9922 | 2021-11-13 | 22:24 | 11.5352 | 75704 | 75848 | 75820
9923 | 2021-11-13 | 22:24 | 11.5353 | 75704 | 75847 | 75821
9924 | 2021-11-13 | 22:24 | 11.5353 | 75705 | 75846 | 75821
9925 | 2021-11-13 | 22:24 | 11.5353 | 75705 | 75845 | 75822
9926 | 2021-11-13 | 22:24 | 11.5354 | 75706 | 75844 | 75823
9927 | 2021-11-13 | 22:24 | 11.5354 | 75706 | 75843 | 75823
9928 | 2021-11-13 | 22:24 | 11.5354 | 75706 | 75842 | 75824
9929 | 2021-11-13 | 22:24 | 11.5354 | 75707 | 75841 | 75825
9930 | 2021-11-13 | 22:24 | 11.5355 | 75707 | 75840 | 75826
9931 | 2021-11-13 | 22:24 | 11.5355 | 75707 | 75839 | 75826
9932 | 2021-11-13 | 22:24 | 11.5355 | 75707 | 75837 | 75827
9933 | 2021-11-13 | 22:24 | 11.5356 | 75707 | 75836 | 75828
9934 | 2021-11-13 | 22:24 | 11.5356 | 75708 | 75835 | 75829
9935 | 2021-11-13 | 22:24 | 11.5356 | 75708 | 75834 | 75830
9936 | 2021-11-13 | 22:24 | 11.5356 | 75708 | 75833 | 75831
9937 | 2021-11-13 | 22:24 | 11.5357 | 75708 | 75832 | 75832
9938 | 2021-11-13 | 22:24 | 11.5357 | 75708 | 75831 | 75833
9939 | 2021-11-13 | 22:24 | 11.5357 | 75708 | 75829 | 75834
9940 | 2021-11-13 | 22:24 | 11.5358 | 75708 | 75828 | 75835
9941 | 2021-11-13 | 22:24 | 11.5358 | 75708 | 75827 | 75836
9942 | 2021-11-13 | 22:24 | 11.5358 | 75708 | 75826 | 75837
9943 | 2021-11-13 | 22:24 | 11.5358 | 75708 | 75825 | 75838
9944 | 2021-11-13 | 22:24 | 11.5359 | 75708 | 75824 | 75839
9945 | 2021-11-13 | 22:24 | 11.5359 | 75708 | 75823 | 75840
9946 | 2021-11-13 | 22:24 | 11.5359 | 75708 | 75822 | 75841
9947 | 2021-11-13 | 22:24 | 11.536 | 75708 | 75821 | 75842
9948 | 2021-11-13 | 22:24 | 11.536 | 75708 | 75820 | 75843
9949 | 2021-11-13 | 22:24 | 11.536 | 75707 | 75819 | 75845
9950 | 2021-11-13 | 22:24 | 11.5361 | 75707 | 75818 | 75846
9951 | 2021-11-13 | 22:24 | 11.5361 | 75707 | 75817 | 75847
9952 | 2021-11-13 | 22:24 | 11.5361 | 75707 | 75816 | 75848
9953 | 2021-11-13 | 22:24 | 11.5361 | 75706 | 75815 | 75849
9954 | 2021-11-13 | 22:24 | 11.5362 | 75706 | 75814 | 75851
9955 | 2021-11-13 | 22:24 | 11.5362 | 75705 | 75813 | 75852
9956 | 2021-11-13 | 22:24 | 11.5362 | 75704 | 75813 | 75853
9957 | 2021-11-13 | 22:24 | 11.5363 | 75704 | 75812 | 75854
9958 | 2021-11-13 | 22:24 | 11.5363 | 75703 | 75811 | 75855
9959 | 2021-11-13 | 22:24 | 11.5363 | 75702 | 75810 | 75857
9960 | 2021-11-13 | 22:24 | 11.5363 | 75702 | 75810 | 75858
9961 | 2021-11-13 | 22:24 | 11.5364 | 75701 | 75809 | 75859
9962 | 2021-11-13 | 22:24 | 11.5364 | 75701 | 75808 | 75860
9963 | 2021-11-13 | 22:24 | 11.5364 | 75700 | 75808 | 75861
9964 | 2021-11-13 | 22:24 | 11.5365 | 75699 | 75807 | 75863
9965 | 2021-11-13 | 22:24 | 11.5365 | 75698 | 75807 | 75864
9966 | 2021-11-13 | 22:24 | 11.5365 | 75698 | 75806 | 75865
9967 | 2021-11-13 | 22:24 | 11.5365 | 75697 | 75806 | 75866
9968 | 2021-11-13 | 22:24 | 11.5366 | 75697 | 75805 | 75867
9969 | 2021-11-13 | 22:24 | 11.5366 | 75696 | 75805 | 75869
9970 | 2021-11-13 | 22:24 | 11.5366 | 75695 | 75805 | 75870
9971 | 2021-11-13 | 22:24 | 11.5367 | 75694 | 75804 | 75871
9972 | 2021-11-13 | 22:24 | 11.5367 | 75693 | 75804 | 75872
9973 | 2021-11-13 | 22:24 | 11.5367 | 75692 | 75804 | 75873
9974 | 2021-11-13 | 22:24 | 11.5367 | 75691 | 75803 | 75874
9975 | 2021-11-13 | 22:24 | 11.5368 | 75690 | 75803 | 75874
9976 | 2021-11-13 | 22:24 | 11.5368 | 75689 | 75803 | 75875
9977 | 2021-11-13 | 22:24 | 11.5368 | 75688 | 75803 | 75876
9978 | 2021-11-13 | 22:24 | 11.5369 | 75687 | 75803 | 75877
9979 | 2021-11-13 | 22:24 | 11.5369 | 75686 | 75803 | 75879
9980 | 2021-11-13 | 22:24 | 11.5369 | 75686 | 75802 | 75880
9981 | 2021-11-13 | 22:24 | 11.5369 | 75685 | 75802 | 75881
9982 | 2021-11-13 | 22:24 | 11.537 | 75684 | 75802 | 75882
9983 | 2021-11-13 | 22:24 | 11.537 | 75683 | 75802 | 75883
9984 | 2021-11-13 | 22:24 | 11.537 | 75682 | 75802 | 75884
9985 | 2021-11-13 | 22:24 | 11.5371 | 75681 | 75802 | 75885
9986 | 2021-11-13 | 22:24 | 11.5371 | 75680 | 75803 | 75885
9987 | 2021-11-13 | 22:24 | 11.5371 | 75679 | 75803 | 75886
9988 | 2021-11-13 | 22:24 | 11.5371 | 75678 | 75803 | 75887
9989 | 2021-11-13 | 22:24 | 11.5372 | 75676 | 75803 | 75888
9990 | 2021-11-13 | 22:24 | 11.5372 | 75675 | 75803 | 75889
9991 | 2021-11-13 | 22:24 | 11.5372 | 75674 | 75803 | 75890
9992 | 2021-11-13 | 22:24 | 11.5373 | 75673 | 75804 | 75891
9993 | 2021-11-13 | 22:24 | 11.5373 | 75672 | 75804 | 75892
9994 | 2021-11-13 | 22:24 | 11.5373 | 75671 | 75804 | 75893
9995 | 2021-11-13 | 22:24 | 11.5373 | 75670 | 75804 | 75894
9996 | 2021-11-13 | 22:24 | 11.5374 | 75669 | 75805 | 75894
9997 | 2021-11-13 | 22:24 | 11.5374 | 75668 | 75805 | 75895
9998 | 2021-11-13 | 22:24 | 11.5374 | 75667 | 75805 | 75896
9999 | 2021-11-13 | 22:24 | 11.5375 | 75666 | 75806 | 75897
10000 | 2021-11-13 | 22:24 | 11.5375 | 75665 | 75806 | 75897
10001 | 2021-11-13 | 22:24 | 11.5375 | 75664 | 75807 | 75898
10002 | 2021-11-13 | 22:24 | 11.5375 | 75663 | 75807 | 75899
10003 | 2021-11-13 | 22:24 | 11.5376 | 75662 | 75808 | 75899
10004 | 2021-11-13 | 22:24 | 11.5376 | 75661 | 75808 | 75900
10005 | 2021-11-13 | 22:24 | 11.5376 | 75659 | 75809 | 75900
10006 | 2021-11-13 | 22:24 | 11.5377 | 75658 | 75809 | 75901
10007 | 2021-11-13 | 22:24 | 11.5377 | 75657 | 75810 | 75901
10008 | 2021-11-13 | 22:24 | 11.5377 | 75656 | 75810 | 75902
10009 | 2021-11-13 | 22:24 | 11.5377 | 75655 | 75811 | 75903
10010 | 2021-11-13 | 22:24 | 11.5378 | 75654 | 75811 | 75903
10011 | 2021-11-13 | 22:24 | 11.5378 | 75653 | 75812 | 75904
10012 | 2021-11-13 | 22:24 | 11.5378 | 75652 | 75813 | 75905
10013 | 2021-11-13 | 22:24 | 11.5379 | 75651 | 75813 | 75905
10014 | 2021-11-13 | 22:24 | 11.5379 | 75650 | 75814 | 75906
10015 | 2021-11-13 | 22:24 | 11.5379 | 75649 | 75815 | 75906
10016 | 2021-11-13 | 22:24 | 11.5379 | 75648 | 75815 | 75906
10017 | 2021-11-13 | 22:24 | 11.538 | 75647 | 75816 | 75907
10018 | 2021-11-13 | 22:24 | 11.538 | 75646 | 75817 | 75907
10019 | 2021-11-13 | 22:24 | 11.538 | 75645 | 75817 | 75907
10020 | 2021-11-13 | 22:24 | 11.5381 | 75644 | 75818 | 75907
10021 | 2021-11-13 | 22:24 | 11.5381 | 75642 | 75819 | 75907
10022 | 2021-11-13 | 22:24 | 11.5381 | 75641 | 75820 | 75907
10023 | 2021-11-13 | 22:24 | 11.5381 | 75640 | 75821 | 75908
10024 | 2021-11-13 | 22:24 | 11.5382 | 75639 | 75822 | 75908
10025 | 2021-11-13 | 22:24 | 11.5382 | 75638 | 75823 | 75908
10026 | 2021-11-13 | 22:24 | 11.5382 | 75637 | 75824 | 75908
10027 | 2021-11-13 | 22:24 | 11.5383 | 75636 | 75825 | 75908
10028 | 2021-11-13 | 22:24 | 11.5383 | 75635 | 75826 | 75908
10029 | 2021-11-13 | 22:24 | 11.5383 | 75634 | 75827 | 75908
10030 | 2021-11-13 | 22:24 | 11.5383 | 75633 | 75828 | 75908
10031 | 2021-11-13 | 22:24 | 11.5384 | 75632 | 75829 | 75908
10032 | 2021-11-13 | 22:24 | 11.5384 | 75631 | 75830 | 75908
10033 | 2021-11-13 | 22:24 | 11.5384 | 75630 | 75831 | 75908
10034 | 2021-11-13 | 22:24 | 11.5385 | 75629 | 75833 | 75907
10035 | 2021-11-13 | 22:24 | 11.5385 | 75628 | 75834 | 75907
10036 | 2021-11-13 | 22:24 | 11.5385 | 75627 | 75835 | 75906
10037 | 2021-11-13 | 22:24 | 11.5385 | 75626 | 75836 | 75906
10038 | 2021-11-13 | 22:24 | 11.5386 | 75626 | 75837 | 75905
10039 | 2021-11-13 | 22:24 | 11.5386 | 75625 | 75838 | 75905
10040 | 2021-11-13 | 22:24 | 11.5386 | 75624 | 75839 | 75904
10041 | 2021-11-13 | 22:24 | 11.5387 | 75623 | 75840 | 75904
10042 | 2021-11-13 | 22:24 | 11.5387 | 75622 | 75842 | 75903
10043 | 2021-11-13 | 22:24 | 11.5387 | 75622 | 75843 | 75903
10044 | 2021-11-13 | 22:24 | 11.5388 | 75621 | 75844 | 75903
10045 | 2021-11-13 | 22:24 | 11.5388 | 75620 | 75845 | 75902
10046 | 2021-11-13 | 22:24 | 11.5388 | 75619 | 75846 | 75901
10047 | 2021-11-13 | 22:24 | 11.5388 | 75619 | 75848 | 75901
10048 | 2021-11-13 | 22:24 | 11.5389 | 75618 | 75849 | 75900
10049 | 2021-11-13 | 22:24 | 11.5389 | 75618 | 75850 | 75899
10050 | 2021-11-13 | 22:24 | 11.5389 | 75617 | 75851 | 75899
10051 | 2021-11-13 | 22:24 | 11.539 | 75617 | 75852 | 75898
10052 | 2021-11-13 | 22:24 | 11.539 | 75616 | 75854 | 75898
10053 | 2021-11-13 | 22:24 | 11.539 | 75616 | 75855 | 75897
10054 | 2021-11-13 | 22:24 | 11.539 | 75615 | 75856 | 75896
10055 | 2021-11-13 | 22:24 | 11.5391 | 75615 | 75857 | 75896
10056 | 2021-11-13 | 22:24 | 11.5391 | 75615 | 75858 | 75895
10057 | 2021-11-13 | 22:24 | 11.5391 | 75614 | 75859 | 75894
10058 | 2021-11-13 | 22:24 | 11.5392 | 75614 | 75861 | 75893
10059 | 2021-11-13 | 22:24 | 11.5392 | 75614 | 75862 | 75893
10060 | 2021-11-13 | 22:24 | 11.5392 | 75614 | 75863 | 75892
10061 | 2021-11-13 | 22:24 | 11.5392 | 75613 | 75864 | 75891
10062 | 2021-11-13 | 22:24 | 11.5393 | 75613 | 75865 | 75890
10063 | 2021-11-13 | 22:24 | 11.5393 | 75613 | 75866 | 75889
10064 | 2021-11-13 | 22:24 | 11.5393 | 75613 | 75867 | 75888
10065 | 2021-11-13 | 22:24 | 11.5394 | 75613 | 75868 | 75887
10066 | 2021-11-13 | 22:24 | 11.5394 | 75613 | 75869 | 75886
10067 | 2021-11-13 | 22:24 | 11.5394 | 75613 | 75870 | 75885
10068 | 2021-11-13 | 22:24 | 11.5394 | 75613 | 75871 | 75884
10069 | 2021-11-13 | 22:24 | 11.5395 | 75613 | 75872 | 75883
10070 | 2021-11-13 | 22:24 | 11.5395 | 75613 | 75873 | 75882
10071 | 2021-11-13 | 22:24 | 11.5395 | 75613 | 75874 | 75882
10072 | 2021-11-13 | 22:24 | 11.5396 | 75613 | 75875 | 75881
10073 | 2021-11-13 | 22:24 | 11.5396 | 75613 | 75876 | 75880
10074 | 2021-11-13 | 22:24 | 11.5396 | 75613 | 75877 | 75879
10075 | 2021-11-13 | 22:24 | 11.5396 | 75613 | 75878 | 75878
10076 | 2021-11-13 | 22:24 | 11.5397 | 75613 | 75879 | 75877
10077 | 2021-11-13 | 22:24 | 11.5397 | 75614 | 75880 | 75876
10078 | 2021-11-13 | 22:24 | 11.5397 | 75614 | 75880 | 75875
10079 | 2021-11-13 | 22:24 | 11.5398 | 75614 | 75881 | 75874
10080 | 2021-11-13 | 22:24 | 11.5398 | 75614 | 75882 | 75873
10081 | 2021-11-13 | 22:24 | 11.5398 | 75615 | 75882 | 75872
10082 | 2021-11-13 | 22:24 | 11.5398 | 75615 | 75883 | 75870
10083 | 2021-11-13 | 22:24 | 11.5399 | 75615 | 75884 | 75869
10084 | 2021-11-13 | 22:24 | 11.5399 | 75616 | 75884 | 75868
10085 | 2021-11-13 | 22:24 | 11.5399 | 75616 | 75885 | 75867
10086 | 2021-11-13 | 22:24 | 11.54 | 75617 | 75886 | 75866
10087 | 2021-11-13 | 22:24 | 11.54 | 75617 | 75887 | 75865
10088 | 2021-11-13 | 22:24 | 11.54 | 75618 | 75887 | 75864
10089 | 2021-11-13 | 22:24 | 11.54 | 75618 | 75888 | 75863
10090 | 2021-11-13 | 22:24 | 11.5401 | 75618 | 75889 | 75862
10091 | 2021-11-13 | 22:24 | 11.5401 | 75619 | 75890 | 75861
10092 | 2021-11-13 | 22:24 | 11.5401 | 75620 | 75890 | 75860
10093 | 2021-11-13 | 22:24 | 11.5402 | 75620 | 75891 | 75859
10094 | 2021-11-13 | 22:24 | 11.5402 | 75621 | 75892 | 75858
10095 | 2021-11-13 | 22:24 | 11.5402 | 75622 | 75893 | 75857
10096 | 2021-11-13 | 22:24 | 11.5402 | 75622 | 75893 | 75856
10097 | 2021-11-13 | 22:24 | 11.5403 | 75623 | 75894 | 75854
10098 | 2021-11-13 | 22:24 | 11.5403 | 75624 | 75894 | 75853
10099 | 2021-11-13 | 22:24 | 11.5403 | 75624 | 75894 | 75852
10100 | 2021-11-13 | 22:24 | 11.5404 | 75625 | 75895 | 75851
10101 | 2021-11-13 | 22:24 | 11.5404 | 75626 | 75895 | 75850
10102 | 2021-11-13 | 22:24 | 11.5404 | 75627 | 75895 | 75849
10103 | 2021-11-13 | 22:24 | 11.5404 | 75628 | 75896 | 75848
10104 | 2021-11-13 | 22:24 | 11.5405 | 75628 | 75896 | 75847
10105 | 2021-11-13 | 22:24 | 11.5405 | 75629 | 75896 | 75846
10106 | 2021-11-13 | 22:24 | 11.5405 | 75630 | 75896 | 75845
10107 | 2021-11-13 | 22:24 | 11.5406 | 75631 | 75897 | 75843
10108 | 2021-11-13 | 22:24 | 11.5406 | 75632 | 75897 | 75842
10109 | 2021-11-13 | 22:24 | 11.5406 | 75633 | 75897 | 75841
10110 | 2021-11-13 | 22:24 | 11.5406 | 75634 | 75897 | 75840
10111 | 2021-11-13 | 22:24 | 11.5407 | 75635 | 75897 | 75839
10112 | 2021-11-13 | 22:24 | 11.5407 | 75636 | 75897 | 75838
10113 | 2021-11-13 | 22:24 | 11.5407 | 75637 | 75897 | 75837
10114 | 2021-11-13 | 22:24 | 11.5408 | 75638 | 75897 | 75836
10115 | 2021-11-13 | 22:24 | 11.5408 | 75639 | 75897 | 75835
10116 | 2021-11-13 | 22:24 | 11.5408 | 75640 | 75897 | 75834
10117 | 2021-11-13 | 22:24 | 11.5408 | 75641 | 75897 | 75833
10118 | 2021-11-13 | 22:24 | 11.5409 | 75642 | 75897 | 75832
10119 | 2021-11-13 | 22:24 | 11.5409 | 75644 | 75896 | 75831
10120 | 2021-11-13 | 22:24 | 11.5409 | 75645 | 75896 | 75830
10121 | 2021-11-13 | 22:24 | 11.541 | 75646 | 75896 | 75829
10122 | 2021-11-13 | 22:24 | 11.541 | 75647 | 75895 | 75828
10123 | 2021-11-13 | 22:24 | 11.541 | 75648 | 75895 | 75827
10124 | 2021-11-13 | 22:24 | 11.541 | 75649 | 75895 | 75826
10125 | 2021-11-13 | 22:24 | 11.5411 | 75650 | 75895 | 75826
10126 | 2021-11-13 | 22:24 | 11.5411 | 75651 | 75894 | 75825
10127 | 2021-11-13 | 22:24 | 11.5411 | 75652 | 75894 | 75824
10128 | 2021-11-13 | 22:24 | 11.5412 | 75654 | 75894 | 75823
10129 | 2021-11-13 | 22:24 | 11.5412 | 75655 | 75893 | 75822
10130 | 2021-11-13 | 22:24 | 11.5412 | 75656 | 75893 | 75822
10131 | 2021-11-13 | 22:24 | 11.5412 | 75657 | 75892 | 75821
10132 | 2021-11-13 | 22:24 | 11.5413 | 75658 | 75892 | 75821
10133 | 2021-11-13 | 22:24 | 11.5413 | 75659 | 75891 | 75820
10134 | 2021-11-13 | 22:24 | 11.5413 | 75660 | 75891 | 75820
10135 | 2021-11-13 | 22:24 | 11.5414 | 75662 | 75890 | 75819
10136 | 2021-11-13 | 22:24 | 11.5414 | 75663 | 75890 | 75819
10137 | 2021-11-13 | 22:24 | 11.5414 | 75664 | 75889 | 75818
10138 | 2021-11-13 | 22:24 | 11.5415 | 75666 | 75888 | 75818
10139 | 2021-11-13 | 22:24 | 11.5415 | 75667 | 75888 | 75817
10140 | 2021-11-13 | 22:24 | 11.5415 | 75668 | 75887 | 75817
10141 | 2021-11-13 | 22:24 | 11.5415 | 75669 | 75886 | 75817
10142 | 2021-11-13 | 22:24 | 11.5416 | 75670 | 75885 | 75816
10143 | 2021-11-13 | 22:24 | 11.5416 | 75671 | 75884 | 75816
10144 | 2021-11-13 | 22:24 | 11.5416 | 75672 | 75883 | 75816
10145 | 2021-11-13 | 22:24 | 11.5417 | 75673 | 75882 | 75815
10146 | 2021-11-13 | 22:24 | 11.5417 | 75674 | 75881 | 75815
10147 | 2021-11-13 | 22:24 | 11.5417 | 75675 | 75880 | 75815
10148 | 2021-11-13 | 22:24 | 11.5417 | 75676 | 75879 | 75815
10149 | 2021-11-13 | 22:24 | 11.5418 | 75678 | 75878 | 75815
10150 | 2021-11-13 | 22:24 | 11.5418 | 75679 | 75877 | 75815
10151 | 2021-11-13 | 22:24 | 11.5418 | 75680 | 75876 | 75814
10152 | 2021-11-13 | 22:24 | 11.5419 | 75681 | 75875 | 75814
10153 | 2021-11-13 | 22:24 | 11.5419 | 75682 | 75874 | 75814
10154 | 2021-11-13 | 22:24 | 11.5419 | 75683 | 75873 | 75814
10155 | 2021-11-13 | 22:24 | 11.5419 | 75684 | 75872 | 75814
10156 | 2021-11-13 | 22:24 | 11.542 | 75685 | 75871 | 75814
10157 | 2021-11-13 | 22:24 | 11.542 | 75686 | 75870 | 75815
10158 | 2021-11-13 | 22:24 | 11.542 | 75687 | 75869 | 75815
10159 | 2021-11-13 | 22:24 | 11.5421 | 75688 | 75868 | 75815
10160 | 2021-11-13 | 22:24 | 11.5421 | 75689 | 75867 | 75815
10161 | 2021-11-13 | 22:24 | 11.5421 | 75690 | 75866 | 75815
10162 | 2021-11-13 | 22:24 | 11.5421 | 75691 | 75865 | 75815
10163 | 2021-11-13 | 22:24 | 11.5422 | 75692 | 75864 | 75816
10164 | 2021-11-13 | 22:24 | 11.5422 | 75693 | 75863 | 75816
10165 | 2021-11-13 | 22:24 | 11.5422 | 75694 | 75862 | 75816
10166 | 2021-11-13 | 22:24 | 11.5423 | 75695 | 75861 | 75817
10167 | 2021-11-13 | 22:24 | 11.5423 | 75696 | 75860 | 75817
10168 | 2021-11-13 | 22:24 | 11.5423 | 75697 | 75859 | 75817
10169 | 2021-11-13 | 22:24 | 11.5423 | 75697 | 75858 | 75818
10170 | 2021-11-13 | 22:24 | 11.5424 | 75698 | 75857 | 75818
10171 | 2021-11-13 | 22:24 | 11.5424 | 75699 | 75856 | 75819
10172 | 2021-11-13 | 22:24 | 11.5424 | 75700 | 75855 | 75819
10173 | 2021-11-13 | 22:24 | 11.5425 | 75700 | 75854 | 75820
10174 | 2021-11-13 | 22:24 | 11.5425 | 75701 | 75853 | 75820
10175 | 2021-11-13 | 22:24 | 11.5425 | 75701 | 75852 | 75821
10176 | 2021-11-13 | 22:24 | 11.5425 | 75702 | 75851 | 75821
10177 | 2021-11-13 | 22:24 | 11.5426 | 75703 | 75850 | 75822
10178 | 2021-11-13 | 22:24 | 11.5426 | 75704 | 75849 | 75822
10179 | 2021-11-13 | 22:24 | 11.5426 | 75705 | 75847 | 75823
10180 | 2021-11-13 | 22:24 | 11.5427 | 75706 | 75846 | 75824
10181 | 2021-11-13 | 22:24 | 11.5427 | 75706 | 75845 | 75824
10182 | 2021-11-13 | 22:24 | 11.5427 | 75707 | 75844 | 75825
10183 | 2021-11-13 | 22:24 | 11.5427 | 75707 | 75843 | 75826
10184 | 2021-11-13 | 22:24 | 11.5428 | 75707 | 75842 | 75826
10185 | 2021-11-13 | 22:24 | 11.5428 | 75708 | 75841 | 75827
10186 | 2021-11-13 | 22:24 | 11.5428 | 75708 | 75840 | 75828
10187 | 2021-11-13 | 22:24 | 11.5429 | 75708 | 75838 | 75829
10188 | 2021-11-13 | 22:24 | 11.5429 | 75708 | 75837 | 75829
10189 | 2021-11-13 | 22:24 | 11.5429 | 75709 | 75836 | 75830
10190 | 2021-11-13 | 22:24 | 11.5429 | 75709 | 75835 | 75831
10191 | 2021-11-13 | 22:24 | 11.543 | 75709 | 75834 | 75832
10192 | 2021-11-13 | 22:24 | 11.543 | 75709 | 75833 | 75833
10193 | 2021-11-13 | 22:24 | 11.543 | 75709 | 75832 | 75834
10194 | 2021-11-13 | 22:24 | 11.5431 | 75709 | 75831 | 75835
10195 | 2021-11-13 | 22:24 | 11.5431 | 75709 | 75830 | 75836
10196 | 2021-11-13 | 22:24 | 11.5431 | 75709 | 75829 | 75837
10197 | 2021-11-13 | 22:24 | 11.5431 | 75709 | 75828 | 75838
10198 | 2021-11-13 | 22:24 | 11.5432 | 75709 | 75827 | 75839
10199 | 2021-11-13 | 22:24 | 11.5432 | 75709 | 75825 | 75840
10200 | 2021-11-13 | 22:24 | 11.5432 | 75709 | 75824 | 75841
10201 | 2021-11-13 | 22:24 | 11.5433 | 75709 | 75823 | 75842
10202 | 2021-11-13 | 22:24 | 11.5433 | 75708 | 75822 | 75843
10203 | 2021-11-13 | 22:24 | 11.5433 | 75708 | 75821 | 75845
10204 | 2021-11-13 | 22:24 | 11.5433 | 75708 | 75820 | 75846
10205 | 2021-11-13 | 22:24 | 11.5434 | 75707 | 75819 | 75847
10206 | 2021-11-13 | 22:24 | 11.5434 | 75707 | 75818 | 75848
10207 | 2021-11-13 | 22:24 | 11.5434 | 75707 | 75817 | 75849
10208 | 2021-11-13 | 22:24 | 11.5435 | 75706 | 75816 | 75851
10209 | 2021-11-13 | 22:24 | 11.5435 | 75706 | 75816 | 75852
10210 | 2021-11-13 | 22:24 | 11.5435 | 75705 | 75815 | 75853
10211 | 2021-11-13 | 22:24 | 11.5435 | 75705 | 75814 | 75854
10212 | 2021-11-13 | 22:24 | 11.5436 | 75704 | 75813 | 75855
10213 | 2021-11-13 | 22:24 | 11.5436 | 75703 | 75812 | 75856
10214 | 2021-11-13 | 22:24 | 11.5436 | 75703 | 75811 | 75858
10215 | 2021-11-13 | 22:24 | 11.5437 | 75702 | 75811 | 75859
10216 | 2021-11-13 | 22:24 | 11.5437 | 75702 | 75810 | 75860
10217 | 2021-11-13 | 22:24 | 11.5437 | 75701 | 75809 | 75861
10218 | 2021-11-13 | 22:24 | 11.5437 | 75700 | 75809 | 75862
10219 | 2021-11-13 | 22:24 | 11.5438 | 75700 | 75808 | 75863
10220 | 2021-11-13 | 22:24 | 11.5438 | 75699 | 75808 | 75865
10221 | 2021-11-13 | 22:24 | 11.5438 | 75699 | 75807 | 75866
10222 | 2021-11-13 | 22:24 | 11.5439 | 75698 | 75807 | 75867
10223 | 2021-11-13 | 22:24 | 11.5439 | 75697 | 75806 | 75868
10224 | 2021-11-13 | 22:24 | 11.5439 | 75696 | 75806 | 75869
10225 | 2021-11-13 | 22:24 | 11.5439 | 75696 | 75805 | 75870
10226 | 2021-11-13 | 22:24 | 11.544 | 75695 | 75805 | 75871
10227 | 2021-11-13 | 22:24 | 11.544 | 75694 | 75805 | 75872
10228 | 2021-11-13 | 22:24 | 11.544 | 75693 | 75804 | 75873
10229 | 2021-11-13 | 22:24 | 11.5441 | 75692 | 75804 | 75874
10230 | 2021-11-13 | 22:24 | 11.5441 | 75691 | 75804 | 75875
10231 | 2021-11-13 | 22:24 | 11.5441 | 75690 | 75804 | 75876
10232 | 2021-11-13 | 22:24 | 11.5442 | 75689 | 75803 | 75877
10233 | 2021-11-13 | 22:24 | 11.5442 | 75688 | 75803 | 75878
10234 | 2021-11-13 | 22:24 | 11.5442 | 75687 | 75803 | 75878
10235 | 2021-11-13 | 22:24 | 11.5442 | 75686 | 75803 | 75879
10236 | 2021-11-13 | 22:24 | 11.5443 | 75686 | 75803 | 75880
10237 | 2021-11-13 | 22:24 | 11.5443 | 75685 | 75803 | 75881
10238 | 2021-11-13 | 22:24 | 11.5443 | 75684 | 75803 | 75882
10239 | 2021-11-13 | 22:24 | 11.5444 | 75683 | 75803 | 75883
10240 | 2021-11-13 | 22:24 | 11.5444 | 75682 | 75803 | 75884
10241 | 2021-11-13 | 22:24 | 11.5444 | 75681 | 75803 | 75885
10242 | 2021-11-13 | 22:24 | 11.5444 | 75680 | 75803 | 75886
10243 | 2021-11-13 | 22:24 | 11.5445 | 75679 | 75803 | 75887
10244 | 2021-11-13 | 22:24 | 11.5445 | 75678 | 75803 | 75888
10245 | 2021-11-13 | 22:24 | 11.5445 | 75676 | 75804 | 75889
10246 | 2021-11-13 | 22:24 | 11.5446 | 75675 | 75804 | 75890
10247 | 2021-11-13 | 22:24 | 11.5446 | 75674 | 75804 | 75891
10248 | 2021-11-13 | 22:24 | 11.5446 | 75673 | 75804 | 75891
10249 | 2021-11-13 | 22:24 | 11.5446 | 75672 | 75804 | 75892
10250 | 2021-11-13 | 22:24 | 11.5447 | 75671 | 75805 | 75893
10251 | 2021-11-13 | 22:24 | 11.5447 | 75670 | 75805 | 75894
10252 | 2021-11-13 | 22:24 | 11.5447 | 75669 | 75805 | 75895
10253 | 2021-11-13 | 22:24 | 11.5448 | 75668 | 75806 | 75896
10254 | 2021-11-13 | 22:24 | 11.5448 | 75667 | 75806 | 75896
10255 | 2021-11-13 | 22:24 | 11.5448 | 75666 | 75807 | 75897
10256 | 2021-11-13 | 22:24 | 11.5448 | 75665 | 75807 | 75898
10257 | 2021-11-13 | 22:24 | 11.5449 | 75664 | 75808 | 75898
10258 | 2021-11-13 | 22:24 | 11.5449 | 75663 | 75808 | 75899
10259 | 2021-11-13 | 22:24 | 11.5449 | 75662 | 75809 | 75900
10260 | 2021-11-13 | 22:24 | 11.545 | 75661 | 75809 | 75900
10261 | 2021-11-13 | 22:24 | 11.545 | 75660 | 75810 | 75901
10262 | 2021-11-13 | 22:24 | 11.545 | 75658 | 75810 | 75902
10263 | 2021-11-13 | 22:24 | 11.545 | 75658 | 75811 | 75902
10264 | 2021-11-13 | 22:24 | 11.5451 | 75656 | 75811 | 75903
10265 | 2021-11-13 | 22:24 | 11.5451 | 75656 | 75812 | 75904
10266 | 2021-11-13 | 22:24 | 11.5451 | 75654 | 75813 | 75904
10267 | 2021-11-13 | 22:24 | 11.5452 | 75653 | 75813 | 75905
10268 | 2021-11-13 | 22:24 | 11.5452 | 75652 | 75814 | 75906
10269 | 2021-11-13 | 22:24 | 11.5452 | 75651 | 75815 | 75906
10270 | 2021-11-13 | 22:24 | 11.5452 | 75650 | 75815 | 75907
10271 | 2021-11-13 | 22:24 | 11.5453 | 75649 | 75816 | 75907
10272 | 2021-11-13 | 22:24 | 11.5453 | 75648 | 75817 | 75908
10273 | 2021-11-13 | 22:24 | 11.5453 | 75647 | 75818 | 75908
10274 | 2021-11-13 | 22:24 | 11.5454 | 75646 | 75818 | 75908
10275 | 2021-11-13 | 22:24 | 11.5454 | 75645 | 75819 | 75909
10276 | 2021-11-13 | 22:24 | 11.5454 | 75644 | 75820 | 75909
10277 | 2021-11-13 | 22:24 | 11.5454 | 75643 | 75821 | 75909
10278 | 2021-11-13 | 22:24 | 11.5455 | 75642 | 75822 | 75909
10279 | 2021-11-13 | 22:24 | 11.5455 | 75641 | 75822 | 75909
10280 | 2021-11-13 | 22:24 | 11.5455 | 75639 | 75823 | 75909
10281 | 2021-11-13 | 22:24 | 11.5456 | 75638 | 75824 | 75909
10282 | 2021-11-13 | 22:24 | 11.5456 | 75637 | 75825 | 75910
10283 | 2021-11-13 | 22:24 | 11.5456 | 75636 | 75826 | 75910
10284 | 2021-11-13 | 22:24 | 11.5456 | 75635 | 75827 | 75910
10285 | 2021-11-13 | 22:24 | 11.5457 | 75634 | 75828 | 75910
10286 | 2021-11-13 | 22:24 | 11.5457 | 75633 | 75830 | 75909
10287 | 2021-11-13 | 22:24 | 11.5457 | 75632 | 75831 | 75909
10288 | 2021-11-13 | 22:24 | 11.5458 | 75631 | 75832 | 75909
10289 | 2021-11-13 | 22:24 | 11.5458 | 75630 | 75833 | 75909
10290 | 2021-11-13 | 22:24 | 11.5458 | 75629 | 75834 | 75908
10291 | 2021-11-13 | 22:24 | 11.5458 | 75628 | 75835 | 75908
10292 | 2021-11-13 | 22:24 | 11.5459 | 75628 | 75836 | 75908
10293 | 2021-11-13 | 22:24 | 11.5459 | 75627 | 75837 | 75907
10294 | 2021-11-13 | 22:24 | 11.5459 | 75626 | 75838 | 75907
10295 | 2021-11-13 | 22:24 | 11.546 | 75625 | 75839 | 75906
10296 | 2021-11-13 | 22:24 | 11.546 | 75624 | 75841 | 75906
10297 | 2021-11-13 | 22:24 | 11.546 | 75623 | 75842 | 75905
10298 | 2021-11-13 | 22:24 | 11.546 | 75623 | 75843 | 75904
10299 | 2021-11-13 | 22:24 | 11.5461 | 75622 | 75844 | 75903
10300 | 2021-11-13 | 22:24 | 11.5461 | 75621 | 75846 | 75903
10301 | 2021-11-13 | 22:24 | 11.5461 | 75620 | 75847 | 75902
10302 | 2021-11-13 | 22:24 | 11.5462 | 75620 | 75848 | 75901
10303 | 2021-11-13 | 22:24 | 11.5462 | 75619 | 75849 | 75901
10304 | 2021-11-13 | 22:24 | 11.5462 | 75618 | 75850 | 75900
10305 | 2021-11-13 | 22:24 | 11.5462 | 75618 | 75852 | 75899
10306 | 2021-11-13 | 22:24 | 11.5463 | 75617 | 75853 | 75899
10307 | 2021-11-13 | 22:24 | 11.5463 | 75617 | 75854 | 75898
10308 | 2021-11-13 | 22:24 | 11.5463 | 75616 | 75856 | 75897
10309 | 2021-11-13 | 22:24 | 11.5464 | 75616 | 75857 | 75896
10310 | 2021-11-13 | 22:24 | 11.5464 | 75615 | 75858 | 75896
10311 | 2021-11-13 | 22:24 | 11.5464 | 75615 | 75859 | 75895
10312 | 2021-11-13 | 22:24 | 11.5464 | 75614 | 75860 | 75894
10313 | 2021-11-13 | 22:24 | 11.5465 | 75614 | 75861 | 75893
10314 | 2021-11-13 | 22:24 | 11.5465 | 75614 | 75862 | 75892
10315 | 2021-11-13 | 22:24 | 11.5465 | 75613 | 75864 | 75892
10316 | 2021-11-13 | 22:24 | 11.5466 | 75613 | 75865 | 75891
10317 | 2021-11-13 | 22:24 | 11.5466 | 75613 | 75866 | 75890
10318 | 2021-11-13 | 22:24 | 11.5466 | 75613 | 75867 | 75889
10319 | 2021-11-13 | 22:24 | 11.5466 | 75613 | 75868 | 75888
10320 | 2021-11-13 | 22:24 | 11.5467 | 75613 | 75869 | 75887
10321 | 2021-11-13 | 22:24 | 11.5467 | 75612 | 75870 | 75886
10322 | 2021-11-13 | 22:24 | 11.5467 | 75612 | 75871 | 75885
10323 | 2021-11-13 | 22:24 | 11.5468 | 75612 | 75872 | 75884
10324 | 2021-11-13 | 22:24 | 11.5468 | 75612 | 75873 | 75883
10325 | 2021-11-13 | 22:24 | 11.5468 | 75612 | 75874 | 75883
10326 | 2021-11-13 | 22:24 | 11.5469 | 75612 | 75876 | 75882
10327 | 2021-11-13 | 22:24 | 11.5469 | 75612 | 75877 | 75881
10328 | 2021-11-13 | 22:24 | 11.5469 | 75613 | 75878 | 75880
10329 | 2021-11-13 | 22:24 | 11.5469 | 75613 | 75879 | 75879
10330 | 2021-11-13 | 22:24 | 11.547 | 75613 | 75880 | 75878
10331 | 2021-11-13 | 22:24 | 11.547 | 75613 | 75881 | 75877
10332 | 2021-11-13 | 22:24 | 11.547 | 75613 | 75882 | 75876
10333 | 2021-11-13 | 22:24 | 11.5471 | 75613 | 75883 | 75875
10334 | 2021-11-13 | 22:24 | 11.5471 | 75614 | 75884 | 75874
10335 | 2021-11-13 | 22:24 | 11.5471 | 75614 | 75884 | 75873
10336 | 2021-11-13 | 22:24 | 11.5471 | 75614 | 75885 | 75872
10337 | 2021-11-13 | 22:24 | 11.5472 | 75615 | 75886 | 75871
10338 | 2021-11-13 | 22:24 | 11.5472 | 75615 | 75887 | 75870
10339 | 2021-11-13 | 22:24 | 11.5472 | 75615 | 75888 | 75869
10340 | 2021-11-13 | 22:24 | 11.5473 | 75616 | 75889 | 75868
10341 | 2021-11-13 | 22:24 | 11.5473 | 75616 | 75889 | 75867
10342 | 2021-11-13 | 22:24 | 11.5473 | 75617 | 75890 | 75866
10343 | 2021-11-13 | 22:24 | 11.5473 | 75617 | 75891 | 75865
10344 | 2021-11-13 | 22:24 | 11.5474 | 75618 | 75892 | 75864
10345 | 2021-11-13 | 22:24 | 11.5474 | 75618 | 75893 | 75863
10346 | 2021-11-13 | 22:24 | 11.5474 | 75619 | 75894 | 75862
10347 | 2021-11-13 | 22:24 | 11.5475 | 75619 | 75894 | 75861
10348 | 2021-11-13 | 22:24 | 11.5475 | 75620 | 75895 | 75860
10349 | 2021-11-13 | 22:24 | 11.5475 | 75621 | 75896 | 75859
10350 | 2021-11-13 | 22:24 | 11.5475 | 75621 | 75897 | 75858
10351 | 2021-11-13 | 22:24 | 11.5476 | 75622 | 75897 | 75857
10352 | 2021-11-13 | 22:24 | 11.5476 | 75623 | 75898 | 75856
10353 | 2021-11-13 | 22:24 | 11.5476 | 75623 | 75898 | 75855
10354 | 2021-11-13 | 22:24 | 11.5477 | 75624 | 75898 | 75854
10355 | 2021-11-13 | 22:24 | 11.5477 | 75625 | 75899 | 75853
10356 | 2021-11-13 | 22:24 | 11.5477 | 75626 | 75899 | 75852
10357 | 2021-11-13 | 22:24 | 11.5477 | 75626 | 75900 | 75850
10358 | 2021-11-13 | 22:24 | 11.5478 | 75627 | 75900 | 75849
10359 | 2021-11-13 | 22:24 | 11.5478 | 75628 | 75901 | 75848
10360 | 2021-11-13 | 22:24 | 11.5478 | 75629 | 75901 | 75847
10361 | 2021-11-13 | 22:24 | 11.5479 | 75630 | 75902 | 75846
10362 | 2021-11-13 | 22:24 | 11.5479 | 75631 | 75902 | 75845
10363 | 2021-11-13 | 22:24 | 11.5479 | 75631 | 75902 | 75844
10364 | 2021-11-13 | 22:24 | 11.5479 | 75632 | 75902 | 75842
10365 | 2021-11-13 | 22:24 | 11.548 | 75633 | 75902 | 75841
10366 | 2021-11-13 | 22:24 | 11.548 | 75634 | 75902 | 75840
10367 | 2021-11-13 | 22:24 | 11.548 | 75635 | 75902 | 75839
10368 | 2021-11-13 | 22:24 | 11.5481 | 75636 | 75902 | 75838
10369 | 2021-11-13 | 22:24 | 11.5481 | 75637 | 75902 | 75837
10370 | 2021-11-13 | 22:24 | 11.5481 | 75638 | 75902 | 75835
10371 | 2021-11-13 | 22:24 | 11.5481 | 75639 | 75902 | 75834
10372 | 2021-11-13 | 22:24 | 11.5482 | 75640 | 75901 | 75833
10373 | 2021-11-13 | 22:24 | 11.5482 | 75641 | 75901 | 75832
10374 | 2021-11-13 | 22:24 | 11.5482 | 75642 | 75900 | 75831
10375 | 2021-11-13 | 22:24 | 11.5483 | 75643 | 75900 | 75831
10376 | 2021-11-13 | 22:24 | 11.5483 | 75644 | 75900 | 75830
10377 | 2021-11-13 | 22:24 | 11.5483 | 75645 | 75899 | 75829
10378 | 2021-11-13 | 22:24 | 11.5483 | 75646 | 75899 | 75828
10379 | 2021-11-13 | 22:24 | 11.5484 | 75647 | 75898 | 75827
10380 | 2021-11-13 | 22:24 | 11.5484 | 75648 | 75898 | 75826
10381 | 2021-11-13 | 22:24 | 11.5484 | 75649 | 75897 | 75825
10382 | 2021-11-13 | 22:24 | 11.5485 | 75650 | 75896 | 75824
10383 | 2021-11-13 | 22:24 | 11.5485 | 75651 | 75895 | 75824
10384 | 2021-11-13 | 22:24 | 11.5485 | 75652 | 75895 | 75823
10385 | 2021-11-13 | 22:24 | 11.5485 | 75653 | 75894 | 75822
10386 | 2021-11-13 | 22:24 | 11.5486 | 75654 | 75893 | 75822
10387 | 2021-11-13 | 22:24 | 11.5486 | 75655 | 75893 | 75821
10388 | 2021-11-13 | 22:24 | 11.5486 | 75656 | 75892 | 75820
10389 | 2021-11-13 | 22:24 | 11.5487 | 75658 | 75891 | 75820
10390 | 2021-11-13 | 22:24 | 11.5487 | 75659 | 75891 | 75819
10391 | 2021-11-13 | 22:24 | 11.5487 | 75660 | 75890 | 75818
10392 | 2021-11-13 | 22:24 | 11.5487 | 75661 | 75889 | 75818
10393 | 2021-11-13 | 22:24 | 11.5488 | 75662 | 75888 | 75817
10394 | 2021-11-13 | 22:24 | 11.5488 | 75663 | 75887 | 75817
10395 | 2021-11-13 | 22:24 | 11.5488 | 75664 | 75886 | 75817
10396 | 2021-11-13 | 22:24 | 11.5489 | 75665 | 75885 | 75816
10397 | 2021-11-13 | 22:24 | 11.5489 | 75666 | 75884 | 75816
10398 | 2021-11-13 | 22:24 | 11.5489 | 75667 | 75883 | 75815
10399 | 2021-11-13 | 22:24 | 11.5489 | 75668 | 75881 | 75815
10400 | 2021-11-13 | 22:24 | 11.549 | 75669 | 75880 | 75815
10401 | 2021-11-13 | 22:24 | 11.549 | 75670 | 75879 | 75815
10402 | 2021-11-13 | 22:24 | 11.549 | 75671 | 75878 | 75814
10403 | 2021-11-13 | 22:24 | 11.5491 | 75672 | 75877 | 75814
10404 | 2021-11-13 | 22:24 | 11.5491 | 75673 | 75875 | 75814
10405 | 2021-11-13 | 22:24 | 11.5491 | 75674 | 75874 | 75814
10406 | 2021-11-13 | 22:24 | 11.5491 | 75675 | 75873 | 75814
10407 | 2021-11-13 | 22:24 | 11.5492 | 75676 | 75872 | 75814
10408 | 2021-11-13 | 22:24 | 11.5492 | 75677 | 75871 | 75814
10409 | 2021-11-13 | 22:24 | 11.5492 | 75678 | 75870 | 75814
10410 | 2021-11-13 | 22:24 | 11.5493 | 75679 | 75868 | 75814
10411 | 2021-11-13 | 22:24 | 11.5493 | 75680 | 75867 | 75814
10412 | 2021-11-13 | 22:24 | 11.5493 | 75681 | 75866 | 75814
10413 | 2021-11-13 | 22:24 | 11.5493 | 75682 | 75865 | 75814
10414 | 2021-11-13 | 22:24 | 11.5494 | 75683 | 75864 | 75814
10415 | 2021-11-13 | 22:24 | 11.5494 | 75684 | 75863 | 75814
10416 | 2021-11-13 | 22:24 | 11.5494 | 75684 | 75862 | 75814
10417 | 2021-11-13 | 22:24 | 11.5495 | 75685 | 75861 | 75814
10418 | 2021-11-13 | 22:24 | 11.5495 | 75686 | 75860 | 75815
10419 | 2021-11-13 | 22:24 | 11.5495 | 75687 | 75859 | 75815
10420 | 2021-11-13 | 22:24 | 11.5495 | 75688 | 75858 | 75815
10421 | 2021-11-13 | 22:24 | 11.5496 | 75689 | 75857 | 75815
10422 | 2021-11-13 | 22:24 | 11.5496 | 75690 | 75856 | 75816
10423 | 2021-11-13 | 22:24 | 11.5496 | 75690 | 75855 | 75816
10424 | 2021-11-13 | 22:24 | 11.5497 | 75691 | 75854 | 75817
10425 | 2021-11-13 | 22:24 | 11.5497 | 75691 | 75853 | 75817
10426 | 2021-11-13 | 22:24 | 11.5497 | 75692 | 75852 | 75817
10427 | 2021-11-13 | 22:24 | 11.5498 | 75693 | 75851 | 75818
10428 | 2021-11-13 | 22:24 | 11.5498 | 75693 | 75850 | 75818
10429 | 2021-11-13 | 22:24 | 11.5498 | 75694 | 75849 | 75819
10430 | 2021-11-13 | 22:24 | 11.5498 | 75695 | 75848 | 75819
10431 | 2021-11-13 | 22:24 | 11.5499 | 75696 | 75847 | 75820
10432 | 2021-11-13 | 22:24 | 11.5499 | 75697 | 75846 | 75821
10433 | 2021-11-13 | 22:24 | 11.5499 | 75698 | 75845 | 75821
10434 | 2021-11-13 | 22:24 | 11.55 | 75699 | 75844 | 75822
10435 | 2021-11-13 | 22:24 | 11.55 | 75699 | 75843 | 75822
10436 | 2021-11-13 | 22:24 | 11.55 | 75700 | 75842 | 75823
10437 | 2021-11-13 | 22:24 | 11.55 | 75701 | 75841 | 75824
10438 | 2021-11-13 | 22:24 | 11.5501 | 75701 | 75839 | 75824
10439 | 2021-11-13 | 22:24 | 11.5501 | 75702 | 75838 | 75825
10440 | 2021-11-13 | 22:24 | 11.5501 | 75702 | 75837 | 75826
10441 | 2021-11-13 | 22:24 | 11.5502 | 75702 | 75836 | 75826
10442 | 2021-11-13 | 22:24 | 11.5502 | 75703 | 75835 | 75827
10443 | 2021-11-13 | 22:24 | 11.5502 | 75703 | 75834 | 75828
10444 | 2021-11-13 | 22:24 | 11.5502 | 75703 | 75833 | 75829
10445 | 2021-11-13 | 22:24 | 11.5503 | 75704 | 75832 | 75829
10446 | 2021-11-13 | 22:24 | 11.5503 | 75704 | 75831 | 75830
10447 | 2021-11-13 | 22:24 | 11.5503 | 75704 | 75830 | 75831
10448 | 2021-11-13 | 22:24 | 11.5504 | 75705 | 75829 | 75832
10449 | 2021-11-13 | 22:24 | 11.5504 | 75705 | 75828 | 75833
10450 | 2021-11-13 | 22:24 | 11.5504 | 75705 | 75827 | 75834
10451 | 2021-11-13 | 22:24 | 11.5504 | 75705 | 75826 | 75835
10452 | 2021-11-13 | 22:24 | 11.5505 | 75705 | 75825 | 75836
10453 | 2021-11-13 | 22:24 | 11.5505 | 75705 | 75824 | 75837
10454 | 2021-11-13 | 22:24 | 11.5505 | 75705 | 75823 | 75838
10455 | 2021-11-13 | 22:24 | 11.5506 | 75705 | 75822 | 75839
10456 | 2021-11-13 | 22:24 | 11.5506 | 75705 | 75822 | 75840
10457 | 2021-11-13 | 22:24 | 11.5506 | 75704 | 75821 | 75841
10458 | 2021-11-13 | 22:24 | 11.5506 | 75704 | 75820 | 75842
10459 | 2021-11-13 | 22:24 | 11.5507 | 75704 | 75819 | 75843
10460 | 2021-11-13 | 22:24 | 11.5507 | 75704 | 75818 | 75844
10461 | 2021-11-13 | 22:24 | 11.5507 | 75704 | 75817 | 75845
10462 | 2021-11-13 | 22:24 | 11.5508 | 75703 | 75816 | 75847
10463 | 2021-11-13 | 22:24 | 11.5508 | 75703 | 75815 | 75848
10464 | 2021-11-13 | 22:24 | 11.5508 | 75703 | 75814 | 75849
10465 | 2021-11-13 | 22:24 | 11.5508 | 75702 | 75813 | 75850
10466 | 2021-11-13 | 22:24 | 11.5509 | 75702 | 75813 | 75851
10467 | 2021-11-13 | 22:24 | 11.5509 | 75701 | 75812 | 75852
10468 | 2021-11-13 | 22:24 | 11.5509 | 75700 | 75811 | 75853
10469 | 2021-11-13 | 22:24 | 11.551 | 75700 | 75810 | 75854
10470 | 2021-11-13 | 22:24 | 11.551 | 75699 | 75809 | 75855
10471 | 2021-11-13 | 22:24 | 11.551 | 75698 | 75809 | 75856
10472 | 2021-11-13 | 22:24 | 11.551 | 75697 | 75808 | 75858
10473 | 2021-11-13 | 22:24 | 11.5511 | 75697 | 75807 | 75859
10474 | 2021-11-13 | 22:24 | 11.5511 | 75696 | 75807 | 75860
10475 | 2021-11-13 | 22:24 | 11.5511 | 75696 | 75806 | 75861
10476 | 2021-11-13 | 22:24 | 11.5512 | 75695 | 75805 | 75863
10477 | 2021-11-13 | 22:24 | 11.5512 | 75694 | 75805 | 75864
10478 | 2021-11-13 | 22:24 | 11.5512 | 75693 | 75804 | 75865
10479 | 2021-11-13 | 22:24 | 11.5512 | 75692 | 75804 | 75866
10480 | 2021-11-13 | 22:24 | 11.5513 | 75691 | 75803 | 75867
10481 | 2021-11-13 | 22:24 | 11.5513 | 75690 | 75803 | 75868
10482 | 2021-11-13 | 22:24 | 11.5513 | 75690 | 75803 | 75869
10483 | 2021-11-13 | 22:24 | 11.5514 | 75689 | 75802 | 75870
10484 | 2021-11-13 | 22:24 | 11.5514 | 75688 | 75802 | 75871
10485 | 2021-11-13 | 22:24 | 11.5514 | 75687 | 75802 | 75872
10486 | 2021-11-13 | 22:24 | 11.5514 | 75686 | 75801 | 75873
10487 | 2021-11-13 | 22:24 | 11.5515 | 75685 | 75801 | 75874
10488 | 2021-11-13 | 22:24 | 11.5515 | 75684 | 75801 | 75875
10489 | 2021-11-13 | 22:24 | 11.5515 | 75683 | 75801 | 75876
10490 | 2021-11-13 | 22:24 | 11.5516 | 75682 | 75801 | 75877
10491 | 2021-11-13 | 22:24 | 11.5516 | 75681 | 75801 | 75878
10492 | 2021-11-13 | 22:24 | 11.5516 | 75680 | 75801 | 75879
10493 | 2021-11-13 | 22:24 | 11.5516 | 75679 | 75801 | 75880
10494 | 2021-11-13 | 22:24 | 11.5517 | 75679 | 75801 | 75881
10495 | 2021-11-13 | 22:24 | 11.5517 | 75678 | 75801 | 75882
10496 | 2021-11-13 | 22:24 | 11.5517 | 75677 | 75801 | 75883
10497 | 2021-11-13 | 22:24 | 11.5518 | 75676 | 75801 | 75884
10498 | 2021-11-13 | 22:24 | 11.5518 | 75675 | 75801 | 75885
10499 | 2021-11-13 | 22:24 | 11.5518 | 75674 | 75801 | 75886
10500 | 2021-11-13 | 22:24 | 11.5518 | 75673 | 75801 | 75886
10501 | 2021-11-13 | 22:24 | 11.5519 | 75672 | 75801 | 75887
10502 | 2021-11-13 | 22:24 | 11.5519 | 75671 | 75801 | 75888
10503 | 2021-11-13 | 22:24 | 11.5519 | 75670 | 75802 | 75889
10504 | 2021-11-13 | 22:24 | 11.552 | 75669 | 75802 | 75890
10505 | 2021-11-13 | 22:24 | 11.552 | 75668 | 75802 | 75891
10506 | 2021-11-13 | 22:24 | 11.552 | 75667 | 75802 | 75892
10507 | 2021-11-13 | 22:24 | 11.552 | 75666 | 75803 | 75893
10508 | 2021-11-13 | 22:24 | 11.5521 | 75666 | 75803 | 75894
10509 | 2021-11-13 | 22:24 | 11.5521 | 75665 | 75803 | 75894
10510 | 2021-11-13 | 22:24 | 11.5521 | 75664 | 75804 | 75895
10511 | 2021-11-13 | 22:24 | 11.5522 | 75663 | 75804 | 75896
10512 | 2021-11-13 | 22:24 | 11.5522 | 75662 | 75805 | 75897
10513 | 2021-11-13 | 22:24 | 11.5522 | 75661 | 75805 | 75897
10514 | 2021-11-13 | 22:24 | 11.5522 | 75660 | 75805 | 75898
10515 | 2021-11-13 | 22:24 | 11.5523 | 75659 | 75806 | 75899
10516 | 2021-11-13 | 22:24 | 11.5523 | 75658 | 75806 | 75900
10517 | 2021-11-13 | 22:24 | 11.5523 | 75657 | 75807 | 75900
10518 | 2021-11-13 | 22:24 | 11.5524 | 75656 | 75807 | 75901
10519 | 2021-11-13 | 22:24 | 11.5524 | 75655 | 75808 | 75901
10520 | 2021-11-13 | 22:24 | 11.5524 | 75654 | 75809 | 75902
10521 | 2021-11-13 | 22:24 | 11.5525 | 75653 | 75809 | 75903
10522 | 2021-11-13 | 22:24 | 11.5525 | 75652 | 75810 | 75903
10523 | 2021-11-13 | 22:24 | 11.5525 | 75651 | 75810 | 75904
10524 | 2021-11-13 | 22:24 | 11.5525 | 75650 | 75811 | 75905
10525 | 2021-11-13 | 22:24 | 11.5526 | 75649 | 75812 | 75905
10526 | 2021-11-13 | 22:24 | 11.5526 | 75648 | 75812 | 75906
10527 | 2021-11-13 | 22:24 | 11.5526 | 75647 | 75813 | 75906
10528 | 2021-11-13 | 22:24 | 11.5527 | 75646 | 75814 | 75906
10529 | 2021-11-13 | 22:24 | 11.5527 | 75645 | 75814 | 75906
10530 | 2021-11-13 | 22:24 | 11.5527 | 75644 | 75815 | 75906
10531 | 2021-11-13 | 22:24 | 11.5527 | 75643 | 75816 | 75906
10532 | 2021-11-13 | 22:24 | 11.5528 | 75642 | 75817 | 75907
10533 | 2021-11-13 | 22:24 | 11.5528 | 75641 | 75818 | 75907
10534 | 2021-11-13 | 22:24 | 11.5528 | 75640 | 75818 | 75907
10535 | 2021-11-13 | 22:24 | 11.5529 | 75638 | 75819 | 75908
10536 | 2021-11-13 | 22:24 | 11.5529 | 75637 | 75820 | 75908
10537 | 2021-11-13 | 22:24 | 11.5529 | 75636 | 75821 | 75908
10538 | 2021-11-13 | 22:24 | 11.5529 | 75635 | 75822 | 75908
10539 | 2021-11-13 | 22:24 | 11.553 | 75634 | 75823 | 75908
10540 | 2021-11-13 | 22:24 | 11.553 | 75633 | 75825 | 75908
10541 | 2021-11-13 | 22:24 | 11.553 | 75632 | 75826 | 75908
10542 | 2021-11-13 | 22:24 | 11.5531 | 75631 | 75827 | 75907
10543 | 2021-11-13 | 22:24 | 11.5531 | 75630 | 75828 | 75907
10544 | 2021-11-13 | 22:24 | 11.5531 | 75629 | 75829 | 75907
10545 | 2021-11-13 | 22:24 | 11.5531 | 75628 | 75830 | 75906
10546 | 2021-11-13 | 22:24 | 11.5532 | 75627 | 75831 | 75906
10547 | 2021-11-13 | 22:24 | 11.5532 | 75626 | 75832 | 75905
10548 | 2021-11-13 | 22:24 | 11.5532 | 75625 | 75833 | 75905
10549 | 2021-11-13 | 22:24 | 11.5533 | 75624 | 75834 | 75904
10550 | 2021-11-13 | 22:24 | 11.5533 | 75623 | 75836 | 75904
10551 | 2021-11-13 | 22:24 | 11.5533 | 75622 | 75837 | 75903
10552 | 2021-11-13 | 22:24 | 11.5533 | 75621 | 75838 | 75902
10553 | 2021-11-13 | 22:24 | 11.5534 | 75620 | 75839 | 75902
10554 | 2021-11-13 | 22:24 | 11.5534 | 75620 | 75841 | 75901
10555 | 2021-11-13 | 22:24 | 11.5534 | 75619 | 75842 | 75900
10556 | 2021-11-13 | 22:24 | 11.5535 | 75618 | 75843 | 75900
10557 | 2021-11-13 | 22:24 | 11.5535 | 75617 | 75845 | 75899
10558 | 2021-11-13 | 22:24 | 11.5535 | 75617 | 75846 | 75898
10559 | 2021-11-13 | 22:24 | 11.5535 | 75616 | 75847 | 75898
10560 | 2021-11-13 | 22:24 | 11.5536 | 75615 | 75848 | 75897
10561 | 2021-11-13 | 22:24 | 11.5536 | 75615 | 75849 | 75896
10562 | 2021-11-13 | 22:24 | 11.5536 | 75614 | 75850 | 75895
10563 | 2021-11-13 | 22:24 | 11.5537 | 75614 | 75851 | 75895
10564 | 2021-11-13 | 22:24 | 11.5537 | 75613 | 75852 | 75894
10565 | 2021-11-13 | 22:24 | 11.5537 | 75613 | 75853 | 75893
10566 | 2021-11-13 | 22:24 | 11.5537 | 75612 | 75855 | 75892
10567 | 2021-11-13 | 22:24 | 11.5538 | 75612 | 75856 | 75892
10568 | 2021-11-13 | 22:24 | 11.5538 | 75612 | 75857 | 75891
10569 | 2021-11-13 | 22:24 | 11.5538 | 75611 | 75858 | 75890
10570 | 2021-11-13 | 22:24 | 11.5539 | 75611 | 75859 | 75889
10571 | 2021-11-13 | 22:24 | 11.5539 | 75611 | 75860 | 75889
10572 | 2021-11-13 | 22:24 | 11.5539 | 75610 | 75861 | 75888
10573 | 2021-11-13 | 22:24 | 11.5539 | 75610 | 75862 | 75887
10574 | 2021-11-13 | 22:24 | 11.554 | 75610 | 75863 | 75886
10575 | 2021-11-13 | 22:24 | 11.554 | 75610 | 75865 | 75885
10576 | 2021-11-13 | 22:24 | 11.554 | 75610 | 75866 | 75884
10577 | 2021-11-13 | 22:24 | 11.5541 | 75610 | 75867 | 75884
10578 | 2021-11-13 | 22:24 | 11.5541 | 75610 | 75868 | 75883
10579 | 2021-11-13 | 22:24 | 11.5541 | 75610 | 75869 | 75882
10580 | 2021-11-13 | 22:24 | 11.5541 | 75610 | 75870 | 75881
10581 | 2021-11-13 | 22:24 | 11.5542 | 75610 | 75871 | 75880
10582 | 2021-11-13 | 22:24 | 11.5542 | 75610 | 75872 | 75879
10583 | 2021-11-13 | 22:24 | 11.5542 | 75610 | 75874 | 75879
10584 | 2021-11-13 | 22:24 | 11.5543 | 75610 | 75875 | 75878
10585 | 2021-11-13 | 22:24 | 11.5543 | 75610 | 75876 | 75877
10586 | 2021-11-13 | 22:24 | 11.5543 | 75610 | 75877 | 75876
10587 | 2021-11-13 | 22:24 | 11.5543 | 75610 | 75878 | 75875
10588 | 2021-11-13 | 22:24 | 11.5544 | 75611 | 75880 | 75874
10589 | 2021-11-13 | 22:24 | 11.5544 | 75611 | 75881 | 75873
10590 | 2021-11-13 | 22:24 | 11.5544 | 75611 | 75882 | 75872
10591 | 2021-11-13 | 22:24 | 11.5545 | 75611 | 75883 | 75871
10592 | 2021-11-13 | 22:24 | 11.5545 | 75612 | 75884 | 75870
10593 | 2021-11-13 | 22:24 | 11.5545 | 75612 | 75885 | 75869
10594 | 2021-11-13 | 22:24 | 11.5545 | 75612 | 75886 | 75868
10595 | 2021-11-13 | 22:24 | 11.5546 | 75613 | 75887 | 75867
10596 | 2021-11-13 | 22:24 | 11.5546 | 75613 | 75888 | 75866
10597 | 2021-11-13 | 22:24 | 11.5546 | 75614 | 75889 | 75866
10598 | 2021-11-13 | 22:24 | 11.5547 | 75614 | 75890 | 75865
10599 | 2021-11-13 | 22:24 | 11.5547 | 75614 | 75891 | 75864
10600 | 2021-11-13 | 22:24 | 11.5547 | 75615 | 75892 | 75863
10601 | 2021-11-13 | 22:24 | 11.5547 | 75616 | 75893 | 75862
10602 | 2021-11-13 | 22:24 | 11.5548 | 75616 | 75893 | 75861
10603 | 2021-11-13 | 22:24 | 11.5548 | 75617 | 75894 | 75860
10604 | 2021-11-13 | 22:24 | 11.5548 | 75617 | 75895 | 75859
10605 | 2021-11-13 | 22:24 | 11.5549 | 75618 | 75896 | 75858
10606 | 2021-11-13 | 22:24 | 11.5549 | 75619 | 75896 | 75857
10607 | 2021-11-13 | 22:24 | 11.5549 | 75619 | 75896 | 75856
10608 | 2021-11-13 | 22:24 | 11.5549 | 75620 | 75897 | 75855
10609 | 2021-11-13 | 22:24 | 11.555 | 75621 | 75897 | 75854
10610 | 2021-11-13 | 22:24 | 11.555 | 75621 | 75897 | 75852
10611 | 2021-11-13 | 22:24 | 11.555 | 75622 | 75898 | 75851
10612 | 2021-11-13 | 22:24 | 11.5551 | 75623 | 75898 | 75850
10613 | 2021-11-13 | 22:24 | 11.5551 | 75624 | 75898 | 75849
10614 | 2021-11-13 | 22:24 | 11.5551 | 75624 | 75898 | 75848
10615 | 2021-11-13 | 22:24 | 11.5552 | 75625 | 75898 | 75846
10616 | 2021-11-13 | 22:24 | 11.5552 | 75626 | 75898 | 75845
10617 | 2021-11-13 | 22:24 | 11.5552 | 75627 | 75898 | 75844
10618 | 2021-11-13 | 22:24 | 11.5552 | 75628 | 75898 | 75843
10619 | 2021-11-13 | 22:24 | 11.5553 | 75629 | 75898 | 75842
10620 | 2021-11-13 | 22:24 | 11.5553 | 75630 | 75898 | 75840
10621 | 2021-11-13 | 22:24 | 11.5553 | 75631 | 75898 | 75839
10622 | 2021-11-13 | 22:24 | 11.5554 | 75632 | 75898 | 75838
10623 | 2021-11-13 | 22:24 | 11.5554 | 75633 | 75898 | 75837
10624 | 2021-11-13 | 22:24 | 11.5554 | 75634 | 75897 | 75836
10625 | 2021-11-13 | 22:24 | 11.5554 | 75635 | 75897 | 75834
10626 | 2021-11-13 | 22:24 | 11.5555 | 75636 | 75897 | 75833
10627 | 2021-11-13 | 22:24 | 11.5555 | 75637 | 75897 | 75832
10628 | 2021-11-13 | 22:24 | 11.5555 | 75638 | 75896 | 75831
10629 | 2021-11-13 | 22:24 | 11.5556 | 75639 | 75896 | 75830
10630 | 2021-11-13 | 22:24 | 11.5556 | 75640 | 75896 | 75829
10631 | 2021-11-13 | 22:24 | 11.5556 | 75641 | 75895 | 75828
10632 | 2021-11-13 | 22:24 | 11.5556 | 75642 | 75895 | 75827
10633 | 2021-11-13 | 22:24 | 11.5557 | 75644 | 75895 | 75826
10634 | 2021-11-13 | 22:24 | 11.5557 | 75645 | 75894 | 75825
10635 | 2021-11-13 | 22:24 | 11.5557 | 75646 | 75894 | 75824
10636 | 2021-11-13 | 22:24 | 11.5558 | 75647 | 75893 | 75824
10637 | 2021-11-13 | 22:24 | 11.5558 | 75648 | 75893 | 75823
10638 | 2021-11-13 | 22:24 | 11.5558 | 75649 | 75893 | 75822
10639 | 2021-11-13 | 22:24 | 11.5558 | 75650 | 75892 | 75821
10640 | 2021-11-13 | 22:24 | 11.5559 | 75651 | 75892 | 75820
10641 | 2021-11-13 | 22:24 | 11.5559 | 75652 | 75891 | 75820
10642 | 2021-11-13 | 22:24 | 11.5559 | 75654 | 75891 | 75819
10643 | 2021-11-13 | 22:24 | 11.556 | 75655 | 75891 | 75818
10644 | 2021-11-13 | 22:24 | 11.556 | 75656 | 75890 | 75818
10645 | 2021-11-13 | 22:24 | 11.556 | 75657 | 75890 | 75817
10646 | 2021-11-13 | 22:24 | 11.556 | 75659 | 75889 | 75817
10647 | 2021-11-13 | 22:24 | 11.5561 | 75660 | 75889 | 75816
10648 | 2021-11-13 | 22:24 | 11.5561 | 75661 | 75888 | 75816
10649 | 2021-11-13 | 22:24 | 11.5561 | 75662 | 75887 | 75815
10650 | 2021-11-13 | 22:24 | 11.5562 | 75663 | 75887 | 75815
10651 | 2021-11-13 | 22:24 | 11.5562 | 75664 | 75886 | 75814
10652 | 2021-11-13 | 22:24 | 11.5562 | 75666 | 75885 | 75814
10653 | 2021-11-13 | 22:24 | 11.5562 | 75667 | 75884 | 75814
10654 | 2021-11-13 | 22:24 | 11.5563 | 75668 | 75883 | 75813
10655 | 2021-11-13 | 22:24 | 11.5563 | 75669 | 75882 | 75813
10656 | 2021-11-13 | 22:24 | 11.5563 | 75670 | 75880 | 75813
10657 | 2021-11-13 | 22:24 | 11.5564 | 75671 | 75879 | 75813
10658 | 2021-11-13 | 22:24 | 11.5564 | 75672 | 75878 | 75812
10659 | 2021-11-13 | 22:24 | 11.5564 | 75673 | 75877 | 75812
10660 | 2021-11-13 | 22:24 | 11.5564 | 75674 | 75876 | 75812
10661 | 2021-11-13 | 22:24 | 11.5565 | 75675 | 75875 | 75812
10662 | 2021-11-13 | 22:24 | 11.5565 | 75676 | 75874 | 75812
10663 | 2021-11-13 | 22:24 | 11.5565 | 75677 | 75873 | 75812
10664 | 2021-11-13 | 22:24 | 11.5566 | 75678 | 75872 | 75812
10665 | 2021-11-13 | 22:24 | 11.5566 | 75679 | 75871 | 75812
10666 | 2021-11-13 | 22:24 | 11.5566 | 75680 | 75870 | 75812
10667 | 2021-11-13 | 22:24 | 11.5566 | 75681 | 75868 | 75812
10668 | 2021-11-13 | 22:24 | 11.5567 | 75682 | 75867 | 75812
10669 | 2021-11-13 | 22:24 | 11.5567 | 75683 | 75866 | 75812
10670 | 2021-11-13 | 22:24 | 11.5567 | 75684 | 75865 | 75812
10671 | 2021-11-13 | 22:24 | 11.5568 | 75685 | 75864 | 75812
10672 | 2021-11-13 | 22:24 | 11.5568 | 75686 | 75863 | 75812
10673 | 2021-11-13 | 22:24 | 11.5568 | 75687 | 75862 | 75813
10674 | 2021-11-13 | 22:24 | 11.5568 | 75688 | 75861 | 75813
10675 | 2021-11-13 | 22:24 | 11.5569 | 75689 | 75860 | 75813
10676 | 2021-11-13 | 22:24 | 11.5569 | 75690 | 75858 | 75813
10677 | 2021-11-13 | 22:24 | 11.5569 | 75691 | 75857 | 75814
10678 | 2021-11-13 | 22:24 | 11.557 | 75691 | 75856 | 75814
10679 | 2021-11-13 | 22:24 | 11.557 | 75692 | 75855 | 75814
10680 | 2021-11-13 | 22:24 | 11.557 | 75693 | 75855 | 75815
10681 | 2021-11-13 | 22:24 | 11.557 | 75693 | 75854 | 75815
10682 | 2021-11-13 | 22:24 | 11.5571 | 75694 | 75853 | 75816
10683 | 2021-11-13 | 22:24 | 11.5571 | 75695 | 75852 | 75816
10684 | 2021-11-13 | 22:24 | 11.5571 | 75696 | 75851 | 75817
10685 | 2021-11-13 | 22:24 | 11.5572 | 75697 | 75850 | 75817
10686 | 2021-11-13 | 22:24 | 11.5572 | 75697 | 75849 | 75818
10687 | 2021-11-13 | 22:24 | 11.5572 | 75698 | 75848 | 75818
10688 | 2021-11-13 | 22:24 | 11.5572 | 75699 | 75847 | 75819
10689 | 2021-11-13 | 22:24 | 11.5573 | 75699 | 75846 | 75820
10690 | 2021-11-13 | 22:24 | 11.5573 | 75700 | 75845 | 75820
10691 | 2021-11-13 | 22:24 | 11.5573 | 75701 | 75844 | 75821
10692 | 2021-11-13 | 22:24 | 11.5574 | 75702 | 75843 | 75821
10693 | 2021-11-13 | 22:24 | 11.5574 | 75703 | 75842 | 75822
10694 | 2021-11-13 | 22:24 | 11.5574 | 75703 | 75841 | 75823
10695 | 2021-11-13 | 22:24 | 11.5574 | 75704 | 75840 | 75824
10696 | 2021-11-13 | 22:24 | 11.5575 | 75704 | 75839 | 75824
10697 | 2021-11-13 | 22:24 | 11.5575 | 75704 | 75838 | 75825
10698 | 2021-11-13 | 22:24 | 11.5575 | 75705 | 75837 | 75826
10699 | 2021-11-13 | 22:24 | 11.5576 | 75705 | 75836 | 75826
10700 | 2021-11-13 | 22:24 | 11.5576 | 75705 | 75835 | 75827
10701 | 2021-11-13 | 22:24 | 11.5576 | 75705 | 75834 | 75828
10702 | 2021-11-13 | 22:24 | 11.5576 | 75705 | 75833 | 75829
10703 | 2021-11-13 | 22:24 | 11.5577 | 75706 | 75832 | 75830
10704 | 2021-11-13 | 22:24 | 11.5577 | 75706 | 75831 | 75831
10705 | 2021-11-13 | 22:24 | 11.5577 | 75706 | 75830 | 75832
10706 | 2021-11-13 | 22:24 | 11.5578 | 75706 | 75829 | 75833
10707 | 2021-11-13 | 22:24 | 11.5578 | 75706 | 75828 | 75833
10708 | 2021-11-13 | 22:24 | 11.5578 | 75706 | 75827 | 75834
10709 | 2021-11-13 | 22:24 | 11.5579 | 75706 | 75826 | 75835
10710 | 2021-11-13 | 22:24 | 11.5579 | 75706 | 75825 | 75836
10711 | 2021-11-13 | 22:24 | 11.5579 | 75706 | 75824 | 75837
10712 | 2021-11-13 | 22:24 | 11.5579 | 75706 | 75823 | 75838
10713 | 2021-11-13 | 22:24 | 11.558 | 75706 | 75822 | 75840
10714 | 2021-11-13 | 22:24 | 11.558 | 75706 | 75821 | 75841
10715 | 2021-11-13 | 22:24 | 11.558 | 75706 | 75820 | 75842
10716 | 2021-11-13 | 22:24 | 11.5581 | 75706 | 75819 | 75843
10717 | 2021-11-13 | 22:24 | 11.5581 | 75705 | 75818 | 75844
10718 | 2021-11-13 | 22:24 | 11.5581 | 75705 | 75817 | 75845
10719 | 2021-11-13 | 22:24 | 11.5581 | 75704 | 75816 | 75847
10720 | 2021-11-13 | 22:24 | 11.5582 | 75704 | 75815 | 75848
10721 | 2021-11-13 | 22:24 | 11.5582 | 75703 | 75814 | 75849
10722 | 2021-11-13 | 22:24 | 11.5582 | 75703 | 75813 | 75850
10723 | 2021-11-13 | 22:24 | 11.5583 | 75702 | 75812 | 75851
10724 | 2021-11-13 | 22:24 | 11.5583 | 75702 | 75812 | 75853
10725 | 2021-11-13 | 22:24 | 11.5583 | 75701 | 75811 | 75854
10726 | 2021-11-13 | 22:24 | 11.5583 | 75700 | 75810 | 75855
10727 | 2021-11-13 | 22:24 | 11.5584 | 75700 | 75809 | 75856
10728 | 2021-11-13 | 22:24 | 11.5584 | 75699 | 75809 | 75858
10729 | 2021-11-13 | 22:24 | 11.5584 | 75698 | 75808 | 75859
10730 | 2021-11-13 | 22:24 | 11.5585 | 75698 | 75807 | 75860
10731 | 2021-11-13 | 22:24 | 11.5585 | 75697 | 75807 | 75861
10732 | 2021-11-13 | 22:24 | 11.5585 | 75696 | 75806 | 75863
10733 | 2021-11-13 | 22:24 | 11.5585 | 75695 | 75806 | 75864
10734 | 2021-11-13 | 22:24 | 11.5586 | 75695 | 75805 | 75865
10735 | 2021-11-13 | 22:24 | 11.5586 | 75694 | 75805 | 75866
10736 | 2021-11-13 | 22:24 | 11.5586 | 75693 | 75804 | 75867
10737 | 2021-11-13 | 22:24 | 11.5587 | 75693 | 75804 | 75869
10738 | 2021-11-13 | 22:24 | 11.5587 | 75692 | 75804 | 75870
10739 | 2021-11-13 | 22:24 | 11.5587 | 75691 | 75803 | 75871
10740 | 2021-11-13 | 22:24 | 11.5587 | 75689 | 75803 | 75872
10741 | 2021-11-13 | 22:24 | 11.5588 | 75688 | 75803 | 75873
10742 | 2021-11-13 | 22:24 | 11.5588 | 75687 | 75802 | 75873
10743 | 2021-11-13 | 22:24 | 11.5588 | 75686 | 75802 | 75874
10744 | 2021-11-13 | 22:24 | 11.5589 | 75685 | 75802 | 75875
10745 | 2021-11-13 | 22:24 | 11.5589 | 75684 | 75802 | 75876
10746 | 2021-11-13 | 22:24 | 11.5589 | 75684 | 75802 | 75877
10747 | 2021-11-13 | 22:24 | 11.5589 | 75683 | 75802 | 75878
10748 | 2021-11-13 | 22:24 | 11.559 | 75682 | 75802 | 75879
10749 | 2021-11-13 | 22:24 | 11.559 | 75681 | 75802 | 75880
10750 | 2021-11-13 | 22:24 | 11.559 | 75680 | 75802 | 75881
10751 | 2021-11-13 | 22:24 | 11.5591 | 75679 | 75802 | 75882
10752 | 2021-11-13 | 22:24 | 11.5591 | 75678 | 75802 | 75883
10753 | 2021-11-13 | 22:24 | 11.5591 | 75677 | 75802 | 75884
10754 | 2021-11-13 | 22:24 | 11.5591 | 75676 | 75802 | 75885
10755 | 2021-11-13 | 22:24 | 11.5592 | 75675 | 75802 | 75886
10756 | 2021-11-13 | 22:24 | 11.5592 | 75674 | 75802 | 75887
10757 | 2021-11-13 | 22:24 | 11.5592 | 75673 | 75802 | 75888
10758 | 2021-11-13 | 22:24 | 11.5593 | 75672 | 75803 | 75889
10759 | 2021-11-13 | 22:24 | 11.5593 | 75671 | 75803 | 75890
10760 | 2021-11-13 | 22:24 | 11.5593 | 75669 | 75803 | 75891
10761 | 2021-11-13 | 22:24 | 11.5593 | 75668 | 75803 | 75891
10762 | 2021-11-13 | 22:24 | 11.5594 | 75667 | 75804 | 75892
10763 | 2021-11-13 | 22:24 | 11.5594 | 75666 | 75804 | 75893
10764 | 2021-11-13 | 22:24 | 11.5594 | 75665 | 75804 | 75894
10765 | 2021-11-13 | 22:24 | 11.5595 | 75664 | 75805 | 75895
10766 | 2021-11-13 | 22:24 | 11.5595 | 75663 | 75805 | 75895
10767 | 2021-11-13 | 22:24 | 11.5595 | 75662 | 75806 | 75896
10768 | 2021-11-13 | 22:24 | 11.5595 | 75661 | 75806 | 75897
10769 | 2021-11-13 | 22:24 | 11.5596 | 75660 | 75807 | 75898
10770 | 2021-11-13 | 22:24 | 11.5596 | 75659 | 75807 | 75898
10771 | 2021-11-13 | 22:24 | 11.5596 | 75658 | 75807 | 75899
10772 | 2021-11-13 | 22:24 | 11.5597 | 75657 | 75808 | 75899
10773 | 2021-11-13 | 22:24 | 11.5597 | 75656 | 75808 | 75900
10774 | 2021-11-13 | 22:24 | 11.5597 | 75655 | 75809 | 75901
10775 | 2021-11-13 | 22:24 | 11.5597 | 75654 | 75810 | 75901
10776 | 2021-11-13 | 22:24 | 11.5598 | 75653 | 75810 | 75902
10777 | 2021-11-13 | 22:24 | 11.5598 | 75652 | 75811 | 75903
10778 | 2021-11-13 | 22:24 | 11.5598 | 75651 | 75811 | 75903
10779 | 2021-11-13 | 22:24 | 11.5599 | 75650 | 75812 | 75904
10780 | 2021-11-13 | 22:24 | 11.5599 | 75649 | 75813 | 75904
10781 | 2021-11-13 | 22:24 | 11.5599 | 75648 | 75813 | 75905
10782 | 2021-11-13 | 22:24 | 11.5599 | 75647 | 75814 | 75905
10783 | 2021-11-13 | 22:24 | 11.56 | 75646 | 75815 | 75906
10784 | 2021-11-13 | 22:24 | 11.56 | 75645 | 75815 | 75906
10785 | 2021-11-13 | 22:24 | 11.56 | 75644 | 75816 | 75906
10786 | 2021-11-13 | 22:24 | 11.5601 | 75643 | 75817 | 75906
10787 | 2021-11-13 | 22:24 | 11.5601 | 75642 | 75818 | 75906
10788 | 2021-11-13 | 22:24 | 11.5601 | 75641 | 75818 | 75907
10789 | 2021-11-13 | 22:24 | 11.5601 | 75640 | 75819 | 75907
10790 | 2021-11-13 | 22:24 | 11.5602 | 75639 | 75820 | 75907
10791 | 2021-11-13 | 22:24 | 11.5602 | 75638 | 75821 | 75907
10792 | 2021-11-13 | 22:24 | 11.5602 | 75637 | 75822 | 75907
10793 | 2021-11-13 | 22:24 | 11.5603 | 75636 | 75823 | 75907
10794 | 2021-11-13 | 22:24 | 11.5603 | 75635 | 75824 | 75907
10795 | 2021-11-13 | 22:24 | 11.5603 | 75634 | 75825 | 75907
10796 | 2021-11-13 | 22:24 | 11.5603 | 75633 | 75826 | 75907
10797 | 2021-11-13 | 22:24 | 11.5604 | 75632 | 75827 | 75907
10798 | 2021-11-13 | 22:24 | 11.5604 | 75631 | 75828 | 75907
10799 | 2021-11-13 | 22:24 | 11.5604 | 75630 | 75829 | 75907
10800 | 2021-11-13 | 22:24 | 11.5605 | 75629 | 75830 | 75906
10801 | 2021-11-13 | 22:24 | 11.5605 | 75628 | 75831 | 75906
10802 | 2021-11-13 | 22:24 | 11.5605 | 75627 | 75832 | 75906
10803 | 2021-11-13 | 22:24 | 11.5606 | 75626 | 75834 | 75905
10804 | 2021-11-13 | 22:24 | 11.5606 | 75625 | 75835 | 75905
10805 | 2021-11-13 | 22:24 | 11.5606 | 75624 | 75836 | 75904
10806 | 2021-11-13 | 22:24 | 11.5606 | 75623 | 75837 | 75904
10807 | 2021-11-13 | 22:24 | 11.5607 | 75622 | 75838 | 75903
10808 | 2021-11-13 | 22:24 | 11.5607 | 75621 | 75840 | 75903
10809 | 2021-11-13 | 22:24 | 11.5607 | 75620 | 75841 | 75902
10810 | 2021-11-13 | 22:24 | 11.5608 | 75620 | 75842 | 75902
10811 | 2021-11-13 | 22:24 | 11.5608 | 75619 | 75844 | 75901
10812 | 2021-11-13 | 22:24 | 11.5608 | 75618 | 75845 | 75901
10813 | 2021-11-13 | 22:24 | 11.5608 | 75617 | 75846 | 75900
10814 | 2021-11-13 | 22:24 | 11.5609 | 75617 | 75848 | 75900
10815 | 2021-11-13 | 22:24 | 11.5609 | 75616 | 75849 | 75899
10816 | 2021-11-13 | 22:24 | 11.5609 | 75616 | 75850 | 75898
10817 | 2021-11-13 | 22:24 | 11.561 | 75615 | 75852 | 75898
10818 | 2021-11-13 | 22:24 | 11.561 | 75614 | 75853 | 75897
10819 | 2021-11-13 | 22:24 | 11.561 | 75614 | 75854 | 75896
10820 | 2021-11-13 | 22:24 | 11.561 | 75614 | 75855 | 75896
10821 | 2021-11-13 | 22:24 | 11.5611 | 75613 | 75857 | 75895
10822 | 2021-11-13 | 22:24 | 11.5611 | 75613 | 75858 | 75894
10823 | 2021-11-13 | 22:24 | 11.5611 | 75612 | 75859 | 75894
10824 | 2021-11-13 | 22:24 | 11.5612 | 75612 | 75860 | 75893
10825 | 2021-11-13 | 22:24 | 11.5612 | 75612 | 75861 | 75892
10826 | 2021-11-13 | 22:24 | 11.5612 | 75612 | 75862 | 75892
10827 | 2021-11-13 | 22:24 | 11.5612 | 75611 | 75863 | 75891
10828 | 2021-11-13 | 22:24 | 11.5613 | 75611 | 75865 | 75890
10829 | 2021-11-13 | 22:24 | 11.5613 | 75611 | 75866 | 75889
10830 | 2021-11-13 | 22:24 | 11.5613 | 75611 | 75867 | 75889
10831 | 2021-11-13 | 22:24 | 11.5614 | 75611 | 75868 | 75888
10832 | 2021-11-13 | 22:24 | 11.5614 | 75611 | 75869 | 75887
10833 | 2021-11-13 | 22:24 | 11.5614 | 75610 | 75870 | 75886
10834 | 2021-11-13 | 22:24 | 11.5614 | 75610 | 75871 | 75886
10835 | 2021-11-13 | 22:24 | 11.5615 | 75610 | 75872 | 75885
10836 | 2021-11-13 | 22:24 | 11.5615 | 75610 | 75873 | 75884
10837 | 2021-11-13 | 22:24 | 11.5615 | 75610 | 75874 | 75883
10838 | 2021-11-13 | 22:24 | 11.5616 | 75611 | 75875 | 75883
10839 | 2021-11-13 | 22:24 | 11.5616 | 75611 | 75876 | 75882
10840 | 2021-11-13 | 22:24 | 11.5616 | 75611 | 75877 | 75881
10841 | 2021-11-13 | 22:24 | 11.5616 | 75611 | 75878 | 75881
10842 | 2021-11-13 | 22:24 | 11.5617 | 75611 | 75880 | 75880
10843 | 2021-11-13 | 22:24 | 11.5617 | 75611 | 75881 | 75879
10844 | 2021-11-13 | 22:24 | 11.5617 | 75611 | 75882 | 75878
10845 | 2021-11-13 | 22:24 | 11.5618 | 75612 | 75883 | 75877
10846 | 2021-11-13 | 22:24 | 11.5618 | 75612 | 75884 | 75876
10847 | 2021-11-13 | 22:24 | 11.5618 | 75612 | 75885 | 75876
10848 | 2021-11-13 | 22:24 | 11.5618 | 75613 | 75886 | 75875
10849 | 2021-11-13 | 22:24 | 11.5619 | 75613 | 75887 | 75874
10850 | 2021-11-13 | 22:24 | 11.5619 | 75613 | 75888 | 75873
10851 | 2021-11-13 | 22:24 | 11.5619 | 75614 | 75889 | 75872
10852 | 2021-11-13 | 22:24 | 11.562 | 75614 | 75890 | 75871
10853 | 2021-11-13 | 22:24 | 11.562 | 75614 | 75891 | 75870
10854 | 2021-11-13 | 22:24 | 11.562 | 75615 | 75892 | 75869
10855 | 2021-11-13 | 22:24 | 11.562 | 75615 | 75893 | 75868
10856 | 2021-11-13 | 22:24 | 11.5621 | 75616 | 75894 | 75867
10857 | 2021-11-13 | 22:24 | 11.5621 | 75616 | 75895 | 75866
10858 | 2021-11-13 | 22:24 | 11.5621 | 75617 | 75896 | 75865
10859 | 2021-11-13 | 22:24 | 11.5622 | 75618 | 75897 | 75864
10860 | 2021-11-13 | 22:24 | 11.5622 | 75618 | 75898 | 75863
10861 | 2021-11-13 | 22:24 | 11.5622 | 75619 | 75899 | 75862
10862 | 2021-11-13 | 22:24 | 11.5622 | 75620 | 75900 | 75861
10863 | 2021-11-13 | 22:24 | 11.5623 | 75620 | 75900 | 75860
10864 | 2021-11-13 | 22:24 | 11.5623 | 75621 | 75901 | 75858
10865 | 2021-11-13 | 22:24 | 11.5623 | 75622 | 75901 | 75857
10866 | 2021-11-13 | 22:24 | 11.5624 | 75623 | 75901 | 75856
10867 | 2021-11-13 | 22:24 | 11.5624 | 75623 | 75901 | 75855
10868 | 2021-11-13 | 22:24 | 11.5624 | 75624 | 75901 | 75854
10869 | 2021-11-13 | 22:24 | 11.5624 | 75625 | 75902 | 75853
10870 | 2021-11-13 | 22:24 | 11.5625 | 75626 | 75902 | 75852
10871 | 2021-11-13 | 22:24 | 11.5625 | 75627 | 75902 | 75850
10872 | 2021-11-13 | 22:24 | 11.5625 | 75628 | 75902 | 75849
10873 | 2021-11-13 | 22:24 | 11.5626 | 75628 | 75902 | 75848
10874 | 2021-11-13 | 22:24 | 11.5626 | 75629 | 75902 | 75847
10875 | 2021-11-13 | 22:24 | 11.5626 | 75630 | 75902 | 75846
10876 | 2021-11-13 | 22:24 | 11.5626 | 75631 | 75902 | 75845
10877 | 2021-11-13 | 22:24 | 11.5627 | 75632 | 75902 | 75843
10878 | 2021-11-13 | 22:24 | 11.5627 | 75633 | 75902 | 75842
10879 | 2021-11-13 | 22:24 | 11.5627 | 75634 | 75901 | 75841
10880 | 2021-11-13 | 22:24 | 11.5628 | 75635 | 75901 | 75840
10881 | 2021-11-13 | 22:24 | 11.5628 | 75636 | 75901 | 75839
10882 | 2021-11-13 | 22:24 | 11.5628 | 75637 | 75901 | 75838
10883 | 2021-11-13 | 22:24 | 11.5628 | 75639 | 75900 | 75836
10884 | 2021-11-13 | 22:24 | 11.5629 | 75640 | 75900 | 75835
10885 | 2021-11-13 | 22:24 | 11.5629 | 75641 | 75900 | 75834
10886 | 2021-11-13 | 22:24 | 11.5629 | 75642 | 75900 | 75833
10887 | 2021-11-13 | 22:24 | 11.563 | 75643 | 75900 | 75832
10888 | 2021-11-13 | 22:24 | 11.563 | 75644 | 75899 | 75831
10889 | 2021-11-13 | 22:24 | 11.563 | 75646 | 75899 | 75830
10890 | 2021-11-13 | 22:24 | 11.563 | 75647 | 75899 | 75829
10891 | 2021-11-13 | 22:24 | 11.5631 | 75648 | 75899 | 75828
10892 | 2021-11-13 | 22:24 | 11.5631 | 75649 | 75898 | 75828
10893 | 2021-11-13 | 22:24 | 11.5631 | 75650 | 75898 | 75827
10894 | 2021-11-13 | 22:24 | 11.5632 | 75652 | 75898 | 75826
10895 | 2021-11-13 | 22:24 | 11.5632 | 75653 | 75897 | 75825
10896 | 2021-11-13 | 22:24 | 11.5632 | 75654 | 75897 | 75824
10897 | 2021-11-13 | 22:24 | 11.5633 | 75655 | 75896 | 75823
10898 | 2021-11-13 | 22:24 | 11.5633 | 75656 | 75896 | 75823
10899 | 2021-11-13 | 22:24 | 11.5633 | 75657 | 75895 | 75822
10900 | 2021-11-13 | 22:24 | 11.5633 | 75659 | 75895 | 75822
10901 | 2021-11-13 | 22:24 | 11.5634 | 75660 | 75894 | 75821
10902 | 2021-11-13 | 22:24 | 11.5634 | 75661 | 75894 | 75820
10903 | 2021-11-13 | 22:24 | 11.5634 | 75663 | 75893 | 75820
10904 | 2021-11-13 | 22:24 | 11.5635 | 75664 | 75892 | 75819
10905 | 2021-11-13 | 22:24 | 11.5635 | 75665 | 75891 | 75819
10906 | 2021-11-13 | 22:24 | 11.5635 | 75666 | 75890 | 75818
10907 | 2021-11-13 | 22:24 | 11.5635 | 75668 | 75889 | 75818
10908 | 2021-11-13 | 22:24 | 11.5636 | 75669 | 75888 | 75818
10909 | 2021-11-13 | 22:24 | 11.5636 | 75670 | 75887 | 75817
10910 | 2021-11-13 | 22:24 | 11.5636 | 75671 | 75886 | 75817
10911 | 2021-11-13 | 22:24 | 11.5637 | 75672 | 75885 | 75817
10912 | 2021-11-13 | 22:24 | 11.5637 | 75673 | 75884 | 75817
10913 | 2021-11-13 | 22:24 | 11.5637 | 75674 | 75882 | 75816
10914 | 2021-11-13 | 22:24 | 11.5637 | 75675 | 75881 | 75816
10915 | 2021-11-13 | 22:24 | 11.5638 | 75676 | 75880 | 75816
10916 | 2021-11-13 | 22:24 | 11.5638 | 75677 | 75879 | 75816
10917 | 2021-11-13 | 22:24 | 11.5638 | 75678 | 75878 | 75816
10918 | 2021-11-13 | 22:24 | 11.5639 | 75679 | 75877 | 75816
10919 | 2021-11-13 | 22:24 | 11.5639 | 75680 | 75875 | 75816
10920 | 2021-11-13 | 22:24 | 11.5639 | 75681 | 75874 | 75815
10921 | 2021-11-13 | 22:24 | 11.5639 | 75682 | 75873 | 75815
10922 | 2021-11-13 | 22:24 | 11.564 | 75683 | 75872 | 75816
10923 | 2021-11-13 | 22:24 | 11.564 | 75684 | 75871 | 75816
10924 | 2021-11-13 | 22:24 | 11.564 | 75685 | 75870 | 75816
10925 | 2021-11-13 | 22:24 | 11.5641 | 75686 | 75868 | 75816
10926 | 2021-11-13 | 22:24 | 11.5641 | 75687 | 75867 | 75816
10927 | 2021-11-13 | 22:24 | 11.5641 | 75688 | 75866 | 75816
10928 | 2021-11-13 | 22:24 | 11.5641 | 75689 | 75865 | 75816
10929 | 2021-11-13 | 22:24 | 11.5642 | 75690 | 75864 | 75817
10930 | 2021-11-13 | 22:24 | 11.5642 | 75690 | 75863 | 75817
10931 | 2021-11-13 | 22:24 | 11.5642 | 75691 | 75862 | 75817
10932 | 2021-11-13 | 22:24 | 11.5643 | 75692 | 75861 | 75817
10933 | 2021-11-13 | 22:24 | 11.5643 | 75693 | 75860 | 75818
10934 | 2021-11-13 | 22:24 | 11.5643 | 75694 | 75859 | 75818
10935 | 2021-11-13 | 22:24 | 11.5643 | 75694 | 75858 | 75818
10936 | 2021-11-13 | 22:24 | 11.5644 | 75695 | 75857 | 75819
10937 | 2021-11-13 | 22:24 | 11.5644 | 75696 | 75856 | 75819
10938 | 2021-11-13 | 22:24 | 11.5644 | 75696 | 75855 | 75820
10939 | 2021-11-13 | 22:24 | 11.5645 | 75697 | 75854 | 75820
10940 | 2021-11-13 | 22:24 | 11.5645 | 75697 | 75853 | 75820
10941 | 2021-11-13 | 22:24 | 11.5645 | 75698 | 75852 | 75821
10942 | 2021-11-13 | 22:24 | 11.5645 | 75698 | 75851 | 75821
10943 | 2021-11-13 | 22:24 | 11.5646 | 75699 | 75851 | 75822
10944 | 2021-11-13 | 22:24 | 11.5646 | 75700 | 75850 | 75823
10945 | 2021-11-13 | 22:24 | 11.5646 | 75701 | 75849 | 75823
10946 | 2021-11-13 | 22:24 | 11.5647 | 75702 | 75848 | 75824
10947 | 2021-11-13 | 22:24 | 11.5647 | 75702 | 75847 | 75825
10948 | 2021-11-13 | 22:24 | 11.5647 | 75703 | 75845 | 75825
10949 | 2021-11-13 | 22:24 | 11.5647 | 75703 | 75844 | 75826
10950 | 2021-11-13 | 22:24 | 11.5648 | 75704 | 75843 | 75827
10951 | 2021-11-13 | 22:24 | 11.5648 | 75704 | 75842 | 75827
10952 | 2021-11-13 | 22:24 | 11.5648 | 75705 | 75841 | 75828
10953 | 2021-11-13 | 22:24 | 11.5649 | 75705 | 75840 | 75829
10954 | 2021-11-13 | 22:24 | 11.5649 | 75705 | 75839 | 75830
10955 | 2021-11-13 | 22:24 | 11.5649 | 75706 | 75837 | 75830
10956 | 2021-11-13 | 22:24 | 11.5649 | 75706 | 75836 | 75831
10957 | 2021-11-13 | 22:24 | 11.565 | 75707 | 75835 | 75832
10958 | 2021-11-13 | 22:24 | 11.565 | 75707 | 75834 | 75833
10959 | 2021-11-13 | 22:24 | 11.565 | 75707 | 75833 | 75834
10960 | 2021-11-13 | 22:24 | 11.5651 | 75707 | 75832 | 75835
10961 | 2021-11-13 | 22:24 | 11.5651 | 75707 | 75831 | 75836
10962 | 2021-11-13 | 22:24 | 11.5651 | 75707 | 75829 | 75837
10963 | 2021-11-13 | 22:24 | 11.5651 | 75707 | 75828 | 75838
10964 | 2021-11-13 | 22:24 | 11.5652 | 75707 | 75827 | 75839
10965 | 2021-11-13 | 22:24 | 11.5652 | 75707 | 75826 | 75840
10966 | 2021-11-13 | 22:24 | 11.5652 | 75707 | 75825 | 75841
10967 | 2021-11-13 | 22:24 | 11.5653 | 75707 | 75824 | 75842
10968 | 2021-11-13 | 22:24 | 11.5653 | 75707 | 75823 | 75843
10969 | 2021-11-13 | 22:24 | 11.5653 | 75707 | 75822 | 75844
10970 | 2021-11-13 | 22:24 | 11.5653 | 75706 | 75821 | 75846
10971 | 2021-11-13 | 22:24 | 11.5654 | 75706 | 75820 | 75847
10972 | 2021-11-13 | 22:24 | 11.5654 | 75706 | 75819 | 75848
10973 | 2021-11-13 | 22:24 | 11.5654 | 75705 | 75818 | 75849
10974 | 2021-11-13 | 22:24 | 11.5655 | 75705 | 75817 | 75850
10975 | 2021-11-13 | 22:24 | 11.5655 | 75704 | 75816 | 75851
10976 | 2021-11-13 | 22:24 | 11.5655 | 75704 | 75815 | 75853
10977 | 2021-11-13 | 22:24 | 11.5655 | 75703 | 75814 | 75854
10978 | 2021-11-13 | 22:24 | 11.5656 | 75703 | 75813 | 75855
10979 | 2021-11-13 | 22:24 | 11.5656 | 75702 | 75813 | 75856
10980 | 2021-11-13 | 22:24 | 11.5656 | 75702 | 75812 | 75857
10981 | 2021-11-13 | 22:24 | 11.5657 | 75701 | 75811 | 75858
10982 | 2021-11-13 | 22:24 | 11.5657 | 75700 | 75810 | 75859
10983 | 2021-11-13 | 22:24 | 11.5657 | 75699 | 75810 | 75860
10984 | 2021-11-13 | 22:24 | 11.5657 | 75699 | 75809 | 75862
10985 | 2021-11-13 | 22:24 | 11.5658 | 75698 | 75808 | 75863
10986 | 2021-11-13 | 22:24 | 11.5658 | 75698 | 75808 | 75864
10987 | 2021-11-13 | 22:24 | 11.5658 | 75697 | 75807 | 75865
10988 | 2021-11-13 | 22:24 | 11.5659 | 75697 | 75807 | 75867
10989 | 2021-11-13 | 22:24 | 11.5659 | 75696 | 75806 | 75868
10990 | 2021-11-13 | 22:24 | 11.5659 | 75695 | 75806 | 75870
10991 | 2021-11-13 | 22:24 | 11.566 | 75695 | 75805 | 75871
10992 | 2021-11-13 | 22:24 | 11.566 | 75694 | 75805 | 75872
10993 | 2021-11-13 | 22:24 | 11.566 | 75693 | 75805 | 75873
10994 | 2021-11-13 | 22:24 | 11.566 | 75692 | 75804 | 75874
10995 | 2021-11-13 | 22:24 | 11.5661 | 75691 | 75804 | 75875
10996 | 2021-11-13 | 22:24 | 11.5661 | 75690 | 75804 | 75876
10997 | 2021-11-13 | 22:24 | 11.5661 | 75689 | 75803 | 75877
10998 | 2021-11-13 | 22:24 | 11.5662 | 75688 | 75803 | 75878
10999 | 2021-11-13 | 22:24 | 11.5662 | 75687 | 75803 | 75879
11000 | 2021-11-13 | 22:24 | 11.5662 | 75687 | 75803 | 75880
11001 | 2021-11-13 | 22:24 | 11.5662 | 75686 | 75803 | 75881
11002 | 2021-11-13 | 22:24 | 11.5663 | 75685 | 75803 | 75882
11003 | 2021-11-13 | 22:24 | 11.5663 | 75684 | 75803 | 75883
11004 | 2021-11-13 | 22:24 | 11.5663 | 75683 | 75803 | 75884
11005 | 2021-11-13 | 22:24 | 11.5664 | 75682 | 75803 | 75885
11006 | 2021-11-13 | 22:24 | 11.5664 | 75681 | 75803 | 75886
11007 | 2021-11-13 | 22:24 | 11.5664 | 75680 | 75803 | 75887
11008 | 2021-11-13 | 22:24 | 11.5664 | 75679 | 75803 | 75888
11009 | 2021-11-13 | 22:24 | 11.5665 | 75678 | 75803 | 75889
11010 | 2021-11-13 | 22:24 | 11.5665 | 75677 | 75803 | 75890
11011 | 2021-11-13 | 22:24 | 11.5665 | 75676 | 75803 | 75891
11012 | 2021-11-13 | 22:24 | 11.5666 | 75675 | 75803 | 75892
11013 | 2021-11-13 | 22:24 | 11.5666 | 75674 | 75803 | 75893
11014 | 2021-11-13 | 22:24 | 11.5666 | 75673 | 75804 | 75893
11015 | 2021-11-13 | 22:24 | 11.5666 | 75672 | 75804 | 75894
11016 | 2021-11-13 | 22:24 | 11.5667 | 75671 | 75804 | 75895
11017 | 2021-11-13 | 22:24 | 11.5667 | 75670 | 75804 | 75896
11018 | 2021-11-13 | 22:24 | 11.5667 | 75669 | 75805 | 75897
11019 | 2021-11-13 | 22:24 | 11.5668 | 75668 | 75805 | 75898
11020 | 2021-11-13 | 22:24 | 11.5668 | 75667 | 75806 | 75899
11021 | 2021-11-13 | 22:24 | 11.5668 | 75666 | 75806 | 75900
11022 | 2021-11-13 | 22:24 | 11.5668 | 75665 | 75806 | 75901
11023 | 2021-11-13 | 22:24 | 11.5669 | 75664 | 75807 | 75902
11024 | 2021-11-13 | 22:24 | 11.5669 | 75663 | 75807 | 75903
11025 | 2021-11-13 | 22:24 | 11.5669 | 75662 | 75808 | 75903
11026 | 2021-11-13 | 22:24 | 11.567 | 75661 | 75808 | 75904
11027 | 2021-11-13 | 22:24 | 11.567 | 75660 | 75809 | 75905
11028 | 2021-11-13 | 22:24 | 11.567 | 75659 | 75809 | 75906
11029 | 2021-11-13 | 22:24 | 11.567 | 75658 | 75810 | 75907
11030 | 2021-11-13 | 22:24 | 11.5671 | 75657 | 75810 | 75907
11031 | 2021-11-13 | 22:24 | 11.5671 | 75656 | 75811 | 75908
11032 | 2021-11-13 | 22:24 | 11.5671 | 75655 | 75812 | 75909
11033 | 2021-11-13 | 22:24 | 11.5672 | 75654 | 75812 | 75910
11034 | 2021-11-13 | 22:24 | 11.5672 | 75653 | 75813 | 75910
11035 | 2021-11-13 | 22:24 | 11.5672 | 75651 | 75813 | 75911
11036 | 2021-11-13 | 22:24 | 11.5672 | 75650 | 75814 | 75911
11037 | 2021-11-13 | 22:24 | 11.5673 | 75649 | 75815 | 75912
11038 | 2021-11-13 | 22:24 | 11.5673 | 75648 | 75815 | 75912
11039 | 2021-11-13 | 22:24 | 11.5673 | 75647 | 75816 | 75912
11040 | 2021-11-13 | 22:24 | 11.5674 | 75646 | 75817 | 75912
11041 | 2021-11-13 | 22:24 | 11.5674 | 75645 | 75818 | 75913
11042 | 2021-11-13 | 22:24 | 11.5674 | 75644 | 75818 | 75913
11043 | 2021-11-13 | 22:24 | 11.5674 | 75643 | 75819 | 75912
11044 | 2021-11-13 | 22:24 | 11.5675 | 75641 | 75820 | 75912
11045 | 2021-11-13 | 22:24 | 11.5675 | 75640 | 75821 | 75912
11046 | 2021-11-13 | 22:24 | 11.5675 | 75639 | 75822 | 75912
11047 | 2021-11-13 | 22:24 | 11.5676 | 75638 | 75822 | 75912
11048 | 2021-11-13 | 22:24 | 11.5676 | 75637 | 75823 | 75912
11049 | 2021-11-13 | 22:24 | 11.5676 | 75636 | 75824 | 75912
11050 | 2021-11-13 | 22:24 | 11.5676 | 75635 | 75825 | 75912
11051 | 2021-11-13 | 22:24 | 11.5677 | 75634 | 75826 | 75912
11052 | 2021-11-13 | 22:24 | 11.5677 | 75633 | 75827 | 75912
11053 | 2021-11-13 | 22:24 | 11.5677 | 75632 | 75829 | 75912
11054 | 2021-11-13 | 22:24 | 11.5678 | 75631 | 75830 | 75911
11055 | 2021-11-13 | 22:24 | 11.5678 | 75630 | 75831 | 75911
11056 | 2021-11-13 | 22:24 | 11.5678 | 75629 | 75832 | 75911
11057 | 2021-11-13 | 22:24 | 11.5678 | 75628 | 75833 | 75910
11058 | 2021-11-13 | 22:24 | 11.5679 | 75627 | 75834 | 75910
11059 | 2021-11-13 | 22:24 | 11.5679 | 75626 | 75835 | 75910
11060 | 2021-11-13 | 22:24 | 11.5679 | 75625 | 75836 | 75909
11061 | 2021-11-13 | 22:24 | 11.568 | 75624 | 75837 | 75909
11062 | 2021-11-13 | 22:24 | 11.568 | 75623 | 75839 | 75909
11063 | 2021-11-13 | 22:24 | 11.568 | 75622 | 75840 | 75908
11064 | 2021-11-13 | 22:24 | 11.568 | 75622 | 75841 | 75908
11065 | 2021-11-13 | 22:24 | 11.5681 | 75621 | 75842 | 75907
11066 | 2021-11-13 | 22:24 | 11.5681 | 75620 | 75844 | 75907
11067 | 2021-11-13 | 22:24 | 11.5681 | 75619 | 75845 | 75906
11068 | 2021-11-13 | 22:24 | 11.5682 | 75619 | 75846 | 75906
11069 | 2021-11-13 | 22:24 | 11.5682 | 75618 | 75848 | 75905
11070 | 2021-11-13 | 22:24 | 11.5682 | 75617 | 75849 | 75904
11071 | 2021-11-13 | 22:24 | 11.5682 | 75617 | 75851 | 75904
11072 | 2021-11-13 | 22:24 | 11.5683 | 75616 | 75852 | 75903
11073 | 2021-11-13 | 22:24 | 11.5683 | 75615 | 75853 | 75902
11074 | 2021-11-13 | 22:24 | 11.5683 | 75615 | 75855 | 75902
11075 | 2021-11-13 | 22:24 | 11.5684 | 75614 | 75856 | 75901
11076 | 2021-11-13 | 22:24 | 11.5684 | 75614 | 75857 | 75900
11077 | 2021-11-13 | 22:24 | 11.5684 | 75614 | 75858 | 75899
11078 | 2021-11-13 | 22:24 | 11.5684 | 75613 | 75859 | 75898
11079 | 2021-11-13 | 22:24 | 11.5685 | 75613 | 75860 | 75897
11080 | 2021-11-13 | 22:24 | 11.5685 | 75612 | 75862 | 75897
11081 | 2021-11-13 | 22:24 | 11.5685 | 75612 | 75863 | 75896
11082 | 2021-11-13 | 22:24 | 11.5686 | 75612 | 75864 | 75895
11083 | 2021-11-13 | 22:24 | 11.5686 | 75612 | 75865 | 75894
11084 | 2021-11-13 | 22:24 | 11.5686 | 75611 | 75866 | 75893
11085 | 2021-11-13 | 22:24 | 11.5687 | 75611 | 75867 | 75892
11086 | 2021-11-13 | 22:24 | 11.5687 | 75611 | 75868 | 75891
11087 | 2021-11-13 | 22:24 | 11.5687 | 75611 | 75869 | 75890
11088 | 2021-11-13 | 22:24 | 11.5687 | 75611 | 75870 | 75889
11089 | 2021-11-13 | 22:24 | 11.5688 | 75611 | 75871 | 75888
11090 | 2021-11-13 | 22:24 | 11.5688 | 75611 | 75872 | 75887
11091 | 2021-11-13 | 22:24 | 11.5688 | 75611 | 75873 | 75886
11092 | 2021-11-13 | 22:24 | 11.5689 | 75611 | 75874 | 75885
11093 | 2021-11-13 | 22:24 | 11.5689 | 75611 | 75874 | 75884
11094 | 2021-11-13 | 22:24 | 11.5689 | 75611 | 75875 | 75884
11095 | 2021-11-13 | 22:24 | 11.5689 | 75611 | 75876 | 75883
11096 | 2021-11-13 | 22:24 | 11.569 | 75611 | 75877 | 75882
11097 | 2021-11-13 | 22:24 | 11.569 | 75611 | 75878 | 75881
11098 | 2021-11-13 | 22:24 | 11.569 | 75611 | 75879 | 75880
11099 | 2021-11-13 | 22:24 | 11.5691 | 75611 | 75879 | 75879
11100 | 2021-11-13 | 22:24 | 11.5691 | 75612 | 75880 | 75878
11101 | 2021-11-13 | 22:24 | 11.5691 | 75612 | 75881 | 75877
11102 | 2021-11-13 | 22:24 | 11.5691 | 75612 | 75881 | 75876
11103 | 2021-11-13 | 22:24 | 11.5692 | 75612 | 75882 | 75875
11104 | 2021-11-13 | 22:24 | 11.5692 | 75613 | 75883 | 75873
11105 | 2021-11-13 | 22:24 | 11.5692 | 75613 | 75884 | 75872
11106 | 2021-11-13 | 22:24 | 11.5693 | 75613 | 75884 | 75871
11107 | 2021-11-13 | 22:24 | 11.5693 | 75614 | 75885 | 75870
11108 | 2021-11-13 | 22:24 | 11.5693 | 75614 | 75885 | 75869
11109 | 2021-11-13 | 22:24 | 11.5693 | 75615 | 75886 | 75868
11110 | 2021-11-13 | 22:24 | 11.5694 | 75615 | 75887 | 75867
11111 | 2021-11-13 | 22:24 | 11.5694 | 75615 | 75888 | 75866
11112 | 2021-11-13 | 22:24 | 11.5694 | 75616 | 75889 | 75865
11113 | 2021-11-13 | 22:24 | 11.5695 | 75617 | 75889 | 75864
11114 | 2021-11-13 | 22:24 | 11.5695 | 75617 | 75890 | 75863
11115 | 2021-11-13 | 22:24 | 11.5695 | 75618 | 75891 | 75862
11116 | 2021-11-13 | 22:24 | 11.5695 | 75618 | 75892 | 75861
11117 | 2021-11-13 | 22:24 | 11.5696 | 75619 | 75893 | 75860
11118 | 2021-11-13 | 22:24 | 11.5696 | 75620 | 75893 | 75859
11119 | 2021-11-13 | 22:24 | 11.5696 | 75620 | 75894 | 75858
11120 | 2021-11-13 | 22:24 | 11.5697 | 75621 | 75894 | 75857
11121 | 2021-11-13 | 22:24 | 11.5697 | 75622 | 75895 | 75856
11122 | 2021-11-13 | 22:24 | 11.5697 | 75622 | 75895 | 75855
11123 | 2021-11-13 | 22:24 | 11.5697 | 75623 | 75896 | 75854
11124 | 2021-11-13 | 22:24 | 11.5698 | 75624 | 75896 | 75853
11125 | 2021-11-13 | 22:24 | 11.5698 | 75625 | 75897 | 75852
11126 | 2021-11-13 | 22:24 | 11.5698 | 75626 | 75897 | 75850
11127 | 2021-11-13 | 22:24 | 11.5699 | 75627 | 75898 | 75849
11128 | 2021-11-13 | 22:24 | 11.5699 | 75627 | 75898 | 75848
11129 | 2021-11-13 | 22:24 | 11.5699 | 75628 | 75898 | 75847
11130 | 2021-11-13 | 22:24 | 11.5699 | 75629 | 75898 | 75846
11131 | 2021-11-13 | 22:24 | 11.57 | 75630 | 75899 | 75845
11132 | 2021-11-13 | 22:24 | 11.57 | 75631 | 75899 | 75844
11133 | 2021-11-13 | 22:24 | 11.57 | 75632 | 75899 | 75843
11134 | 2021-11-13 | 22:24 | 11.5701 | 75633 | 75899 | 75842
11135 | 2021-11-13 | 22:24 | 11.5701 | 75634 | 75899 | 75841
11136 | 2021-11-13 | 22:24 | 11.5701 | 75635 | 75899 | 75840
11137 | 2021-11-13 | 22:24 | 11.5701 | 75636 | 75899 | 75839
11138 | 2021-11-13 | 22:24 | 11.5702 | 75638 | 75899 | 75838
11139 | 2021-11-13 | 22:24 | 11.5702 | 75639 | 75899 | 75837
11140 | 2021-11-13 | 22:24 | 11.5702 | 75640 | 75899 | 75836
11141 | 2021-11-13 | 22:24 | 11.5703 | 75641 | 75899 | 75835
11142 | 2021-11-13 | 22:24 | 11.5703 | 75642 | 75899 | 75834
11143 | 2021-11-13 | 22:24 | 11.5703 | 75643 | 75899 | 75833
11144 | 2021-11-13 | 22:24 | 11.5703 | 75644 | 75898 | 75832
11145 | 2021-11-13 | 22:24 | 11.5704 | 75646 | 75898 | 75831
11146 | 2021-11-13 | 22:24 | 11.5704 | 75647 | 75898 | 75830
11147 | 2021-11-13 | 22:24 | 11.5704 | 75648 | 75898 | 75829
11148 | 2021-11-13 | 22:24 | 11.5705 | 75649 | 75897 | 75828
11149 | 2021-11-13 | 22:24 | 11.5705 | 75650 | 75897 | 75828
11150 | 2021-11-13 | 22:24 | 11.5705 | 75651 | 75896 | 75827
11151 | 2021-11-13 | 22:24 | 11.5705 | 75653 | 75896 | 75826
11152 | 2021-11-13 | 22:24 | 11.5706 | 75654 | 75895 | 75826
11153 | 2021-11-13 | 22:24 | 11.5706 | 75655 | 75895 | 75825
11154 | 2021-11-13 | 22:24 | 11.5706 | 75656 | 75894 | 75824
11155 | 2021-11-13 | 22:24 | 11.5707 | 75657 | 75894 | 75823
11156 | 2021-11-13 | 22:24 | 11.5707 | 75659 | 75893 | 75823
11157 | 2021-11-13 | 22:24 | 11.5707 | 75660 | 75893 | 75822
11158 | 2021-11-13 | 22:24 | 11.5707 | 75661 | 75892 | 75822
11159 | 2021-11-13 | 22:24 | 11.5708 | 75663 | 75891 | 75821
11160 | 2021-11-13 | 22:24 | 11.5708 | 75664 | 75891 | 75821
11161 | 2021-11-13 | 22:24 | 11.5708 | 75665 | 75890 | 75820
11162 | 2021-11-13 | 22:24 | 11.5709 | 75666 | 75889 | 75820
11163 | 2021-11-13 | 22:24 | 11.5709 | 75667 | 75887 | 75820
11164 | 2021-11-13 | 22:24 | 11.5709 | 75668 | 75886 | 75819
11165 | 2021-11-13 | 22:24 | 11.5709 | 75669 | 75885 | 75819
11166 | 2021-11-13 | 22:24 | 11.571 | 75670 | 75884 | 75819
11167 | 2021-11-13 | 22:24 | 11.571 | 75671 | 75883 | 75818
11168 | 2021-11-13 | 22:24 | 11.571 | 75673 | 75882 | 75818
11169 | 2021-11-13 | 22:24 | 11.5711 | 75674 | 75881 | 75818
11170 | 2021-11-13 | 22:24 | 11.5711 | 75675 | 75880 | 75817
11171 | 2021-11-13 | 22:24 | 11.5711 | 75676 | 75879 | 75817
11172 | 2021-11-13 | 22:24 | 11.5711 | 75677 | 75877 | 75817
11173 | 2021-11-13 | 22:24 | 11.5712 | 75678 | 75876 | 75817
11174 | 2021-11-13 | 22:24 | 11.5712 | 75678 | 75875 | 75817
11175 | 2021-11-13 | 22:24 | 11.5712 | 75679 | 75874 | 75817
11176 | 2021-11-13 | 22:24 | 11.5713 | 75680 | 75873 | 75817
11177 | 2021-11-13 | 22:24 | 11.5713 | 75681 | 75872 | 75817
11178 | 2021-11-13 | 22:24 | 11.5713 | 75682 | 75871 | 75817
11179 | 2021-11-13 | 22:24 | 11.5714 | 75683 | 75869 | 75817
11180 | 2021-11-13 | 22:24 | 11.5714 | 75684 | 75868 | 75817
11181 | 2021-11-13 | 22:24 | 11.5714 | 75685 | 75867 | 75817
11182 | 2021-11-13 | 22:24 | 11.5714 | 75686 | 75866 | 75817
11183 | 2021-11-13 | 22:24 | 11.5715 | 75687 | 75865 | 75818
11184 | 2021-11-13 | 22:24 | 11.5715 | 75687 | 75864 | 75818
11185 | 2021-11-13 | 22:24 | 11.5715 | 75688 | 75863 | 75818
11186 | 2021-11-13 | 22:24 | 11.5716 | 75689 | 75862 | 75818
11187 | 2021-11-13 | 22:24 | 11.5716 | 75690 | 75861 | 75819
11188 | 2021-11-13 | 22:24 | 11.5716 | 75691 | 75860 | 75819
11189 | 2021-11-13 | 22:24 | 11.5716 | 75692 | 75859 | 75819
11190 | 2021-11-13 | 22:24 | 11.5717 | 75692 | 75858 | 75820
11191 | 2021-11-13 | 22:24 | 11.5717 | 75693 | 75857 | 75820
11192 | 2021-11-13 | 22:24 | 11.5717 | 75693 | 75856 | 75820
11193 | 2021-11-13 | 22:24 | 11.5718 | 75694 | 75855 | 75821
11194 | 2021-11-13 | 22:24 | 11.5718 | 75694 | 75853 | 75821
11195 | 2021-11-13 | 22:24 | 11.5718 | 75695 | 75852 | 75821
11196 | 2021-11-13 | 22:24 | 11.5718 | 75696 | 75851 | 75822
11197 | 2021-11-13 | 22:24 | 11.5719 | 75697 | 75850 | 75822
11198 | 2021-11-13 | 22:24 | 11.5719 | 75697 | 75849 | 75823
11199 | 2021-11-13 | 22:24 | 11.5719 | 75698 | 75848 | 75824
11200 | 2021-11-13 | 22:24 | 11.572 | 75699 | 75847 | 75824
11201 | 2021-11-13 | 22:24 | 11.572 | 75699 | 75846 | 75825
11202 | 2021-11-13 | 22:24 | 11.572 | 75700 | 75845 | 75825
11203 | 2021-11-13 | 22:24 | 11.572 | 75700 | 75843 | 75826
11204 | 2021-11-13 | 22:24 | 11.5721 | 75700 | 75842 | 75826
11205 | 2021-11-13 | 22:24 | 11.5721 | 75701 | 75841 | 75827
11206 | 2021-11-13 | 22:24 | 11.5721 | 75701 | 75840 | 75828
11207 | 2021-11-13 | 22:24 | 11.5722 | 75701 | 75839 | 75829
11208 | 2021-11-13 | 22:24 | 11.5722 | 75702 | 75838 | 75829
11209 | 2021-11-13 | 22:24 | 11.5722 | 75702 | 75837 | 75830
11210 | 2021-11-13 | 22:24 | 11.5722 | 75702 | 75836 | 75831
11211 | 2021-11-13 | 22:24 | 11.5723 | 75702 | 75834 | 75832
11212 | 2021-11-13 | 22:24 | 11.5723 | 75702 | 75833 | 75832
11213 | 2021-11-13 | 22:24 | 11.5723 | 75702 | 75832 | 75833
11214 | 2021-11-13 | 22:24 | 11.5724 | 75702 | 75831 | 75834
11215 | 2021-11-13 | 22:24 | 11.5724 | 75702 | 75830 | 75835
11216 | 2021-11-13 | 22:24 | 11.5724 | 75703 | 75829 | 75836
11217 | 2021-11-13 | 22:24 | 11.5724 | 75703 | 75828 | 75837
11218 | 2021-11-13 | 22:24 | 11.5725 | 75703 | 75827 | 75838
11219 | 2021-11-13 | 22:24 | 11.5725 | 75703 | 75826 | 75839
11220 | 2021-11-13 | 22:24 | 11.5725 | 75703 | 75825 | 75840
11221 | 2021-11-13 | 22:24 | 11.5726 | 75703 | 75824 | 75841
11222 | 2021-11-13 | 22:24 | 11.5726 | 75703 | 75823 | 75842
11223 | 2021-11-13 | 22:24 | 11.5726 | 75703 | 75822 | 75843
11224 | 2021-11-13 | 22:24 | 11.5726 | 75703 | 75821 | 75844
11225 | 2021-11-13 | 22:24 | 11.5727 | 75702 | 75820 | 75845
11226 | 2021-11-13 | 22:24 | 11.5727 | 75702 | 75819 | 75846
11227 | 2021-11-13 | 22:24 | 11.5727 | 75702 | 75818 | 75847
11228 | 2021-11-13 | 22:24 | 11.5728 | 75701 | 75817 | 75849
11229 | 2021-11-13 | 22:24 | 11.5728 | 75701 | 75816 | 75850
11230 | 2021-11-13 | 22:24 | 11.5728 | 75701 | 75815 | 75851
11231 | 2021-11-13 | 22:24 | 11.5728 | 75700 | 75814 | 75852
11232 | 2021-11-13 | 22:24 | 11.5729 | 75700 | 75813 | 75853
11233 | 2021-11-13 | 22:24 | 11.5729 | 75699 | 75812 | 75854
11234 | 2021-11-13 | 22:24 | 11.5729 | 75698 | 75811 | 75855
11235 | 2021-11-13 | 22:24 | 11.573 | 75697 | 75810 | 75856
11236 | 2021-11-13 | 22:24 | 11.573 | 75697 | 75810 | 75857
11237 | 2021-11-13 | 22:24 | 11.573 | 75696 | 75809 | 75858
11238 | 2021-11-13 | 22:24 | 11.573 | 75695 | 75808 | 75859
11239 | 2021-11-13 | 22:24 | 11.5731 | 75694 | 75808 | 75861
11240 | 2021-11-13 | 22:24 | 11.5731 | 75694 | 75807 | 75862
11241 | 2021-11-13 | 22:24 | 11.5731 | 75693 | 75806 | 75863
11242 | 2021-11-13 | 22:24 | 11.5732 | 75692 | 75806 | 75864
11243 | 2021-11-13 | 22:24 | 11.5732 | 75692 | 75805 | 75866
11244 | 2021-11-13 | 22:24 | 11.5732 | 75691 | 75804 | 75867
11245 | 2021-11-13 | 22:24 | 11.5732 | 75690 | 75804 | 75868
11246 | 2021-11-13 | 22:24 | 11.5733 | 75689 | 75803 | 75869
11247 | 2021-11-13 | 22:24 | 11.5733 | 75688 | 75803 | 75870
11248 | 2021-11-13 | 22:24 | 11.5733 | 75687 | 75803 | 75871
11249 | 2021-11-13 | 22:24 | 11.5734 | 75687 | 75802 | 75872
11250 | 2021-11-13 | 22:24 | 11.5734 | 75686 | 75802 | 75874
11251 | 2021-11-13 | 22:24 | 11.5734 | 75685 | 75802 | 75875
11252 | 2021-11-13 | 22:24 | 11.5734 | 75684 | 75801 | 75876
11253 | 2021-11-13 | 22:24 | 11.5735 | 75683 | 75801 | 75877
11254 | 2021-11-13 | 22:24 | 11.5735 | 75682 | 75801 | 75878
11255 | 2021-11-13 | 22:24 | 11.5735 | 75681 | 75801 | 75879
11256 | 2021-11-13 | 22:24 | 11.5736 | 75680 | 75801 | 75879
11257 | 2021-11-13 | 22:24 | 11.5736 | 75679 | 75800 | 75880
11258 | 2021-11-13 | 22:24 | 11.5736 | 75679 | 75800 | 75881
11259 | 2021-11-13 | 22:24 | 11.5736 | 75678 | 75800 | 75883
11260 | 2021-11-13 | 22:24 | 11.5737 | 75677 | 75800 | 75884
11261 | 2021-11-13 | 22:24 | 11.5737 | 75676 | 75800 | 75885
11262 | 2021-11-13 | 22:24 | 11.5737 | 75676 | 75800 | 75886
11263 | 2021-11-13 | 22:24 | 11.5738 | 75675 | 75800 | 75887
11264 | 2021-11-13 | 22:24 | 11.5738 | 75674 | 75800 | 75887
11265 | 2021-11-13 | 22:24 | 11.5738 | 75673 | 75800 | 75888
11266 | 2021-11-13 | 22:24 | 11.5738 | 75672 | 75801 | 75889
11267 | 2021-11-13 | 22:24 | 11.5739 | 75671 | 75801 | 75890
11268 | 2021-11-13 | 22:24 | 11.5739 | 75670 | 75801 | 75891
11269 | 2021-11-13 | 22:24 | 11.5739 | 75669 | 75801 | 75891
11270 | 2021-11-13 | 22:24 | 11.574 | 75668 | 75801 | 75892
11271 | 2021-11-13 | 22:24 | 11.574 | 75667 | 75801 | 75893
11272 | 2021-11-13 | 22:24 | 11.574 | 75666 | 75802 | 75894
11273 | 2021-11-13 | 22:24 | 11.5741 | 75665 | 75802 | 75895
11274 | 2021-11-13 | 22:24 | 11.5741 | 75665 | 75802 | 75895
11275 | 2021-11-13 | 22:24 | 11.5741 | 75663 | 75803 | 75896
11276 | 2021-11-13 | 22:24 | 11.5741 | 75663 | 75803 | 75897
11277 | 2021-11-13 | 22:24 | 11.5742 | 75662 | 75803 | 75898
11278 | 2021-11-13 | 22:24 | 11.5742 | 75661 | 75804 | 75898
11279 | 2021-11-13 | 22:24 | 11.5742 | 75660 | 75804 | 75899
11280 | 2021-11-13 | 22:24 | 11.5743 | 75659 | 75804 | 75900
11281 | 2021-11-13 | 22:24 | 11.5743 | 75658 | 75805 | 75901
11282 | 2021-11-13 | 22:24 | 11.5743 | 75657 | 75805 | 75902
11283 | 2021-11-13 | 22:24 | 11.5743 | 75656 | 75806 | 75902
11284 | 2021-11-13 | 22:24 | 11.5744 | 75655 | 75806 | 75903
11285 | 2021-11-13 | 22:24 | 11.5744 | 75654 | 75807 | 75904
11286 | 2021-11-13 | 22:24 | 11.5744 | 75653 | 75807 | 75904
11287 | 2021-11-13 | 22:24 | 11.5745 | 75652 | 75808 | 75905
11288 | 2021-11-13 | 22:24 | 11.5745 | 75651 | 75809 | 75906
11289 | 2021-11-13 | 22:24 | 11.5745 | 75650 | 75809 | 75907
11290 | 2021-11-13 | 22:24 | 11.5745 | 75649 | 75810 | 75908
11291 | 2021-11-13 | 22:24 | 11.5746 | 75648 | 75811 | 75908
11292 | 2021-11-13 | 22:24 | 11.5746 | 75647 | 75811 | 75909
11293 | 2021-11-13 | 22:24 | 11.5746 | 75646 | 75812 | 75909
11294 | 2021-11-13 | 22:24 | 11.5747 | 75645 | 75813 | 75910
11295 | 2021-11-13 | 22:24 | 11.5747 | 75644 | 75814 | 75910
11296 | 2021-11-13 | 22:24 | 11.5747 | 75643 | 75814 | 75910
11297 | 2021-11-13 | 22:24 | 11.5747 | 75642 | 75815 | 75910
11298 | 2021-11-13 | 22:24 | 11.5748 | 75641 | 75816 | 75910
11299 | 2021-11-13 | 22:24 | 11.5748 | 75639 | 75817 | 75910
11300 | 2021-11-13 | 22:24 | 11.5748 | 75638 | 75817 | 75910
11301 | 2021-11-13 | 22:24 | 11.5749 | 75637 | 75818 | 75910
11302 | 2021-11-13 | 22:24 | 11.5749 | 75636 | 75819 | 75911
11303 | 2021-11-13 | 22:24 | 11.5749 | 75635 | 75820 | 75911
11304 | 2021-11-13 | 22:24 | 11.5749 | 75634 | 75821 | 75911
11305 | 2021-11-13 | 22:24 | 11.575 | 75633 | 75822 | 75911
11306 | 2021-11-13 | 22:24 | 11.575 | 75632 | 75823 | 75911
11307 | 2021-11-13 | 22:24 | 11.575 | 75631 | 75824 | 75911
11308 | 2021-11-13 | 22:24 | 11.5751 | 75630 | 75825 | 75911
11309 | 2021-11-13 | 22:24 | 11.5751 | 75629 | 75827 | 75911
11310 | 2021-11-13 | 22:24 | 11.5751 | 75628 | 75828 | 75911
11311 | 2021-11-13 | 22:24 | 11.5751 | 75627 | 75829 | 75911
11312 | 2021-11-13 | 22:24 | 11.5752 | 75626 | 75830 | 75910
11313 | 2021-11-13 | 22:24 | 11.5752 | 75625 | 75831 | 75910
11314 | 2021-11-13 | 22:24 | 11.5752 | 75624 | 75832 | 75910
11315 | 2021-11-13 | 22:24 | 11.5753 | 75623 | 75833 | 75909
11316 | 2021-11-13 | 22:24 | 11.5753 | 75623 | 75834 | 75909
11317 | 2021-11-13 | 22:24 | 11.5753 | 75622 | 75835 | 75909
11318 | 2021-11-13 | 22:24 | 11.5753 | 75621 | 75836 | 75908
11319 | 2021-11-13 | 22:24 | 11.5754 | 75620 | 75837 | 75908
11320 | 2021-11-13 | 22:24 | 11.5754 | 75619 | 75839 | 75907
11321 | 2021-11-13 | 22:24 | 11.5754 | 75619 | 75840 | 75907
11322 | 2021-11-13 | 22:24 | 11.5755 | 75618 | 75841 | 75906
11323 | 2021-11-13 | 22:24 | 11.5755 | 75617 | 75842 | 75905
11324 | 2021-11-13 | 22:24 | 11.5755 | 75617 | 75844 | 75905
11325 | 2021-11-13 | 22:24 | 11.5755 | 75616 | 75845 | 75904
11326 | 2021-11-13 | 22:24 | 11.5756 | 75615 | 75846 | 75904
11327 | 2021-11-13 | 22:24 | 11.5756 | 75615 | 75847 | 75903
11328 | 2021-11-13 | 22:24 | 11.5756 | 75614 | 75849 | 75902
11329 | 2021-11-13 | 22:24 | 11.5757 | 75613 | 75850 | 75901
11330 | 2021-11-13 | 22:24 | 11.5757 | 75613 | 75851 | 75901
11331 | 2021-11-13 | 22:24 | 11.5757 | 75612 | 75852 | 75900
11332 | 2021-11-13 | 22:24 | 11.5757 | 75612 | 75853 | 75899
11333 | 2021-11-13 | 22:24 | 11.5758 | 75612 | 75854 | 75898
11334 | 2021-11-13 | 22:24 | 11.5758 | 75611 | 75855 | 75898
11335 | 2021-11-13 | 22:24 | 11.5758 | 75611 | 75857 | 75897
11336 | 2021-11-13 | 22:24 | 11.5759 | 75611 | 75858 | 75896
11337 | 2021-11-13 | 22:24 | 11.5759 | 75610 | 75859 | 75895
11338 | 2021-11-13 | 22:24 | 11.5759 | 75610 | 75860 | 75894
11339 | 2021-11-13 | 22:24 | 11.5759 | 75610 | 75861 | 75893
11340 | 2021-11-13 | 22:24 | 11.576 | 75610 | 75862 | 75891
11341 | 2021-11-13 | 22:24 | 11.576 | 75609 | 75863 | 75890
11342 | 2021-11-13 | 22:24 | 11.576 | 75609 | 75864 | 75889
11343 | 2021-11-13 | 22:24 | 11.5761 | 75609 | 75865 | 75888
11344 | 2021-11-13 | 22:24 | 11.5761 | 75609 | 75866 | 75887
11345 | 2021-11-13 | 22:24 | 11.5761 | 75609 | 75866 | 75886
11346 | 2021-11-13 | 22:24 | 11.5761 | 75609 | 75867 | 75885
11347 | 2021-11-13 | 22:24 | 11.5762 | 75609 | 75868 | 75884
11348 | 2021-11-13 | 22:24 | 11.5762 | 75609 | 75869 | 75883
11349 | 2021-11-13 | 22:24 | 11.5762 | 75609 | 75870 | 75882
11350 | 2021-11-13 | 22:24 | 11.5763 | 75609 | 75871 | 75881
11351 | 2021-11-13 | 22:24 | 11.5763 | 75609 | 75872 | 75879
11352 | 2021-11-13 | 22:24 | 11.5763 | 75609 | 75873 | 75878
11353 | 2021-11-13 | 22:24 | 11.5763 | 75609 | 75874 | 75877
11354 | 2021-11-13 | 22:24 | 11.5764 | 75610 | 75875 | 75876
11355 | 2021-11-13 | 22:24 | 11.5764 | 75610 | 75876 | 75875
11356 | 2021-11-13 | 22:24 | 11.5764 | 75610 | 75877 | 75874
11357 | 2021-11-13 | 22:24 | 11.5765 | 75610 | 75877 | 75873
11358 | 2021-11-13 | 22:24 | 11.5765 | 75611 | 75878 | 75872
11359 | 2021-11-13 | 22:24 | 11.5765 | 75611 | 75879 | 75871
11360 | 2021-11-13 | 22:24 | 11.5765 | 75611 | 75879 | 75870
11361 | 2021-11-13 | 22:24 | 11.5766 | 75612 | 75880 | 75869
11362 | 2021-11-13 | 22:24 | 11.5766 | 75612 | 75881 | 75868
11363 | 2021-11-13 | 22:24 | 11.5766 | 75612 | 75881 | 75867
11364 | 2021-11-13 | 22:24 | 11.5767 | 75613 | 75882 | 75866
11365 | 2021-11-13 | 22:24 | 11.5767 | 75613 | 75883 | 75865
11366 | 2021-11-13 | 22:24 | 11.5767 | 75614 | 75884 | 75864
11367 | 2021-11-13 | 22:24 | 11.5768 | 75614 | 75885 | 75862
11368 | 2021-11-13 | 22:24 | 11.5768 | 75615 | 75886 | 75862
11369 | 2021-11-13 | 22:24 | 11.5768 | 75615 | 75886 | 75861
11370 | 2021-11-13 | 22:24 | 11.5768 | 75616 | 75887 | 75860
11371 | 2021-11-13 | 22:24 | 11.5769 | 75616 | 75888 | 75859
11372 | 2021-11-13 | 22:24 | 11.5769 | 75617 | 75889 | 75858
11373 | 2021-11-13 | 22:24 | 11.5769 | 75617 | 75889 | 75857
11374 | 2021-11-13 | 22:24 | 11.577 | 75618 | 75890 | 75856
11375 | 2021-11-13 | 22:24 | 11.577 | 75619 | 75890 | 75855
11376 | 2021-11-13 | 22:24 | 11.577 | 75619 | 75891 | 75854
11377 | 2021-11-13 | 22:24 | 11.577 | 75620 | 75891 | 75852
11378 | 2021-11-13 | 22:24 | 11.5771 | 75621 | 75891 | 75851
11379 | 2021-11-13 | 22:24 | 11.5771 | 75621 | 75891 | 75850
11380 | 2021-11-13 | 22:24 | 11.5771 | 75622 | 75891 | 75849
11381 | 2021-11-13 | 22:24 | 11.5772 | 75623 | 75892 | 75848
11382 | 2021-11-13 | 22:24 | 11.5772 | 75624 | 75892 | 75847
11383 | 2021-11-13 | 22:24 | 11.5772 | 75624 | 75892 | 75845
11384 | 2021-11-13 | 22:24 | 11.5772 | 75625 | 75892 | 75844
11385 | 2021-11-13 | 22:24 | 11.5773 | 75626 | 75893 | 75843
11386 | 2021-11-13 | 22:24 | 11.5773 | 75627 | 75893 | 75842
11387 | 2021-11-13 | 22:24 | 11.5773 | 75628 | 75893 | 75841
11388 | 2021-11-13 | 22:24 | 11.5774 | 75629 | 75893 | 75840
11389 | 2021-11-13 | 22:24 | 11.5774 | 75630 | 75892 | 75839
11390 | 2021-11-13 | 22:24 | 11.5774 | 75631 | 75892 | 75838
11391 | 2021-11-13 | 22:24 | 11.5774 | 75632 | 75892 | 75837
11392 | 2021-11-13 | 22:24 | 11.5775 | 75633 | 75892 | 75836
11393 | 2021-11-13 | 22:24 | 11.5775 | 75634 | 75892 | 75835
11394 | 2021-11-13 | 22:24 | 11.5775 | 75635 | 75892 | 75834
11395 | 2021-11-13 | 22:24 | 11.5776 | 75636 | 75892 | 75833
11396 | 2021-11-13 | 22:24 | 11.5776 | 75637 | 75892 | 75832
11397 | 2021-11-13 | 22:24 | 11.5776 | 75638 | 75892 | 75831
11398 | 2021-11-13 | 22:24 | 11.5776 | 75640 | 75892 | 75830
11399 | 2021-11-13 | 22:24 | 11.5777 | 75641 | 75891 | 75829
11400 | 2021-11-13 | 22:24 | 11.5777 | 75642 | 75891 | 75828
11401 | 2021-11-13 | 22:24 | 11.5777 | 75643 | 75891 | 75827
11402 | 2021-11-13 | 22:24 | 11.5778 | 75644 | 75890 | 75826
11403 | 2021-11-13 | 22:24 | 11.5778 | 75645 | 75890 | 75826
11404 | 2021-11-13 | 22:24 | 11.5778 | 75646 | 75890 | 75825
11405 | 2021-11-13 | 22:24 | 11.5778 | 75647 | 75890 | 75824
11406 | 2021-11-13 | 22:24 | 11.5779 | 75648 | 75889 | 75823
11407 | 2021-11-13 | 22:24 | 11.5779 | 75649 | 75889 | 75823
11408 | 2021-11-13 | 22:24 | 11.5779 | 75650 | 75889 | 75822
11409 | 2021-11-13 | 22:24 | 11.578 | 75652 | 75889 | 75821
11410 | 2021-11-13 | 22:24 | 11.578 | 75653 | 75888 | 75821
11411 | 2021-11-13 | 22:24 | 11.578 | 75654 | 75888 | 75820
11412 | 2021-11-13 | 22:24 | 11.578 | 75655 | 75887 | 75820
11413 | 2021-11-13 | 22:24 | 11.5781 | 75657 | 75887 | 75819
11414 | 2021-11-13 | 22:24 | 11.5781 | 75658 | 75886 | 75819
11415 | 2021-11-13 | 22:24 | 11.5781 | 75659 | 75886 | 75818
11416 | 2021-11-13 | 22:24 | 11.5782 | 75660 | 75885 | 75818
11417 | 2021-11-13 | 22:24 | 11.5782 | 75661 | 75884 | 75817
11418 | 2021-11-13 | 22:24 | 11.5782 | 75662 | 75883 | 75817
11419 | 2021-11-13 | 22:24 | 11.5782 | 75664 | 75882 | 75817
11420 | 2021-11-13 | 22:24 | 11.5783 | 75665 | 75881 | 75816
11421 | 2021-11-13 | 22:24 | 11.5783 | 75666 | 75881 | 75816
11422 | 2021-11-13 | 22:24 | 11.5783 | 75667 | 75879 | 75816
11423 | 2021-11-13 | 22:24 | 11.5784 | 75668 | 75878 | 75815
11424 | 2021-11-13 | 22:24 | 11.5784 | 75669 | 75877 | 75815
11425 | 2021-11-13 | 22:24 | 11.5784 | 75670 | 75876 | 75815
11426 | 2021-11-13 | 22:24 | 11.5784 | 75671 | 75875 | 75815
11427 | 2021-11-13 | 22:24 | 11.5785 | 75672 | 75874 | 75815
11428 | 2021-11-13 | 22:24 | 11.5785 | 75673 | 75873 | 75814
11429 | 2021-11-13 | 22:24 | 11.5785 | 75675 | 75872 | 75814
11430 | 2021-11-13 | 22:24 | 11.5786 | 75676 | 75871 | 75814
11431 | 2021-11-13 | 22:24 | 11.5786 | 75677 | 75870 | 75814
11432 | 2021-11-13 | 22:24 | 11.5786 | 75678 | 75869 | 75814
11433 | 2021-11-13 | 22:24 | 11.5786 | 75678 | 75868 | 75814
11434 | 2021-11-13 | 22:24 | 11.5787 | 75679 | 75867 | 75814
11435 | 2021-11-13 | 22:24 | 11.5787 | 75680 | 75866 | 75814
11436 | 2021-11-13 | 22:24 | 11.5787 | 75681 | 75865 | 75814
11437 | 2021-11-13 | 22:24 | 11.5788 | 75682 | 75864 | 75815
11438 | 2021-11-13 | 22:24 | 11.5788 | 75683 | 75862 | 75815
11439 | 2021-11-13 | 22:24 | 11.5788 | 75684 | 75861 | 75815
11440 | 2021-11-13 | 22:24 | 11.5788 | 75685 | 75860 | 75815
11441 | 2021-11-13 | 22:24 | 11.5789 | 75687 | 75859 | 75815
11442 | 2021-11-13 | 22:24 | 11.5789 | 75687 | 75858 | 75816
11443 | 2021-11-13 | 22:24 | 11.5789 | 75688 | 75857 | 75816
11444 | 2021-11-13 | 22:24 | 11.579 | 75689 | 75856 | 75816
11445 | 2021-11-13 | 22:24 | 11.579 | 75690 | 75855 | 75817
11446 | 2021-11-13 | 22:24 | 11.579 | 75690 | 75854 | 75817
11447 | 2021-11-13 | 22:24 | 11.579 | 75691 | 75853 | 75817
11448 | 2021-11-13 | 22:24 | 11.5791 | 75692 | 75852 | 75818
11449 | 2021-11-13 | 22:24 | 11.5791 | 75692 | 75851 | 75818
11450 | 2021-11-13 | 22:24 | 11.5791 | 75693 | 75850 | 75818
11451 | 2021-11-13 | 22:24 | 11.5792 | 75694 | 75849 | 75819
11452 | 2021-11-13 | 22:24 | 11.5792 | 75695 | 75848 | 75819
11453 | 2021-11-13 | 22:24 | 11.5792 | 75695 | 75847 | 75820
11454 | 2021-11-13 | 22:24 | 11.5792 | 75696 | 75846 | 75820
11455 | 2021-11-13 | 22:24 | 11.5793 | 75697 | 75845 | 75821
11456 | 2021-11-13 | 22:24 | 11.5793 | 75697 | 75845 | 75822
11457 | 2021-11-13 | 22:24 | 11.5793 | 75698 | 75844 | 75822
11458 | 2021-11-13 | 22:24 | 11.5794 | 75699 | 75843 | 75823
11459 | 2021-11-13 | 22:24 | 11.5794 | 75700 | 75842 | 75823
11460 | 2021-11-13 | 22:24 | 11.5794 | 75700 | 75841 | 75824
11461 | 2021-11-13 | 22:24 | 11.5795 | 75701 | 75840 | 75825
11462 | 2021-11-13 | 22:24 | 11.5795 | 75701 | 75839 | 75825
11463 | 2021-11-13 | 22:24 | 11.5795 | 75701 | 75838 | 75826
11464 | 2021-11-13 | 22:24 | 11.5795 | 75701 | 75837 | 75827
11465 | 2021-11-13 | 22:24 | 11.5796 | 75702 | 75836 | 75828
11466 | 2021-11-13 | 22:24 | 11.5796 | 75702 | 75835 | 75828
11467 | 2021-11-13 | 22:24 | 11.5796 | 75702 | 75834 | 75829
11468 | 2021-11-13 | 22:24 | 11.5797 | 75702 | 75833 | 75830
11469 | 2021-11-13 | 22:24 | 11.5797 | 75703 | 75832 | 75831
11470 | 2021-11-13 | 22:24 | 11.5797 | 75703 | 75831 | 75832
11471 | 2021-11-13 | 22:24 | 11.5797 | 75703 | 75830 | 75833
11472 | 2021-11-13 | 22:24 | 11.5798 | 75703 | 75829 | 75833
11473 | 2021-11-13 | 22:24 | 11.5798 | 75704 | 75828 | 75834
11474 | 2021-11-13 | 22:24 | 11.5798 | 75704 | 75827 | 75835
11475 | 2021-11-13 | 22:24 | 11.5799 | 75704 | 75826 | 75836
11476 | 2021-11-13 | 22:24 | 11.5799 | 75704 | 75825 | 75837
11477 | 2021-11-13 | 22:24 | 11.5799 | 75704 | 75824 | 75838
11478 | 2021-11-13 | 22:24 | 11.5799 | 75704 | 75824 | 75839
11479 | 2021-11-13 | 22:24 | 11.58 | 75704 | 75823 | 75840
11480 | 2021-11-13 | 22:24 | 11.58 | 75704 | 75822 | 75841
11481 | 2021-11-13 | 22:24 | 11.58 | 75704 | 75821 | 75842
11482 | 2021-11-13 | 22:24 | 11.5801 | 75704 | 75820 | 75843
11483 | 2021-11-13 | 22:24 | 11.5801 | 75703 | 75819 | 75844
11484 | 2021-11-13 | 22:24 | 11.5801 | 75703 | 75818 | 75845
11485 | 2021-11-13 | 22:24 | 11.5801 | 75703 | 75817 | 75847
11486 | 2021-11-13 | 22:24 | 11.5802 | 75702 | 75816 | 75848
11487 | 2021-11-13 | 22:24 | 11.5802 | 75702 | 75815 | 75849
11488 | 2021-11-13 | 22:24 | 11.5802 | 75702 | 75814 | 75850
11489 | 2021-11-13 | 22:24 | 11.5803 | 75701 | 75813 | 75851
11490 | 2021-11-13 | 22:24 | 11.5803 | 75701 | 75813 | 75853
11491 | 2021-11-13 | 22:24 | 11.5803 | 75700 | 75812 | 75854
11492 | 2021-11-13 | 22:24 | 11.5803 | 75700 | 75811 | 75855
11493 | 2021-11-13 | 22:24 | 11.5804 | 75699 | 75810 | 75856
11494 | 2021-11-13 | 22:24 | 11.5804 | 75699 | 75810 | 75858
11495 | 2021-11-13 | 22:24 | 11.5804 | 75698 | 75809 | 75859
11496 | 2021-11-13 | 22:24 | 11.5805 | 75697 | 75808 | 75860
11497 | 2021-11-13 | 22:24 | 11.5805 | 75697 | 75808 | 75862
11498 | 2021-11-13 | 22:24 | 11.5805 | 75697 | 75807 | 75863
11499 | 2021-11-13 | 22:24 | 11.5805 | 75696 | 75806 | 75864
11500 | 2021-11-13 | 22:24 | 11.5806 | 75696 | 75806 | 75866
11501 | 2021-11-13 | 22:24 | 11.5806 | 75695 | 75805 | 75867
11502 | 2021-11-13 | 22:24 | 11.5806 | 75695 | 75805 | 75869
11503 | 2021-11-13 | 22:24 | 11.5807 | 75694 | 75804 | 75870
11504 | 2021-11-13 | 22:24 | 11.5807 | 75693 | 75804 | 75871
11505 | 2021-11-13 | 22:24 | 11.5807 | 75693 | 75804 | 75872
11506 | 2021-11-13 | 22:24 | 11.5807 | 75692 | 75803 | 75873
11507 | 2021-11-13 | 22:24 | 11.5808 | 75691 | 75803 | 75874
11508 | 2021-11-13 | 22:24 | 11.5808 | 75690 | 75803 | 75875
11509 | 2021-11-13 | 22:24 | 11.5808 | 75689 | 75803 | 75876
11510 | 2021-11-13 | 22:24 | 11.5809 | 75688 | 75802 | 75877
11511 | 2021-11-13 | 22:24 | 11.5809 | 75687 | 75802 | 75878
11512 | 2021-11-13 | 22:24 | 11.5809 | 75686 | 75802 | 75880
11513 | 2021-11-13 | 22:24 | 11.5809 | 75686 | 75802 | 75881
11514 | 2021-11-13 | 22:24 | 11.581 | 75685 | 75802 | 75882
11515 | 2021-11-13 | 22:24 | 11.581 | 75684 | 75802 | 75883
11516 | 2021-11-13 | 22:24 | 11.581 | 75683 | 75802 | 75884
11517 | 2021-11-13 | 22:24 | 11.5811 | 75682 | 75802 | 75885
11518 | 2021-11-13 | 22:24 | 11.5811 | 75681 | 75802 | 75886
11519 | 2021-11-13 | 22:24 | 11.5811 | 75680 | 75802 | 75887
11520 | 2021-11-13 | 22:24 | 11.5811 | 75679 | 75802 | 75888
11521 | 2021-11-13 | 22:24 | 11.5812 | 75678 | 75802 | 75889
11522 | 2021-11-13 | 22:24 | 11.5812 | 75677 | 75802 | 75889
11523 | 2021-11-13 | 22:24 | 11.5812 | 75676 | 75802 | 75890
11524 | 2021-11-13 | 22:24 | 11.5813 | 75674 | 75803 | 75891
11525 | 2021-11-13 | 22:24 | 11.5813 | 75673 | 75803 | 75892
11526 | 2021-11-13 | 22:24 | 11.5813 | 75672 | 75803 | 75893
11527 | 2021-11-13 | 22:24 | 11.5813 | 75671 | 75803 | 75894
11528 | 2021-11-13 | 22:24 | 11.5814 | 75670 | 75803 | 75894
11529 | 2021-11-13 | 22:24 | 11.5814 | 75669 | 75804 | 75895
11530 | 2021-11-13 | 22:24 | 11.5814 | 75668 | 75804 | 75896
11531 | 2021-11-13 | 22:24 | 11.5815 | 75667 | 75804 | 75897
11532 | 2021-11-13 | 22:24 | 11.5815 | 75666 | 75805 | 75897
11533 | 2021-11-13 | 22:24 | 11.5815 | 75665 | 75805 | 75898
11534 | 2021-11-13 | 22:24 | 11.5815 | 75664 | 75806 | 75899
11535 | 2021-11-13 | 22:24 | 11.5816 | 75663 | 75806 | 75900
11536 | 2021-11-13 | 22:24 | 11.5816 | 75662 | 75807 | 75900
11537 | 2021-11-13 | 22:24 | 11.5816 | 75661 | 75807 | 75901
11538 | 2021-11-13 | 22:24 | 11.5817 | 75660 | 75807 | 75901
11539 | 2021-11-13 | 22:24 | 11.5817 | 75659 | 75808 | 75902
11540 | 2021-11-13 | 22:24 | 11.5817 | 75658 | 75809 | 75902
11541 | 2021-11-13 | 22:24 | 11.5817 | 75657 | 75809 | 75903
11542 | 2021-11-13 | 22:24 | 11.5818 | 75656 | 75810 | 75903
11543 | 2021-11-13 | 22:24 | 11.5818 | 75655 | 75810 | 75904
11544 | 2021-11-13 | 22:24 | 11.5818 | 75654 | 75811 | 75905
11545 | 2021-11-13 | 22:24 | 11.5819 | 75653 | 75811 | 75905
11546 | 2021-11-13 | 22:24 | 11.5819 | 75652 | 75812 | 75906
11547 | 2021-11-13 | 22:24 | 11.5819 | 75651 | 75813 | 75906
11548 | 2021-11-13 | 22:24 | 11.5819 | 75649 | 75813 | 75907
11549 | 2021-11-13 | 22:24 | 11.582 | 75648 | 75814 | 75907
11550 | 2021-11-13 | 22:24 | 11.582 | 75647 | 75815 | 75907
11551 | 2021-11-13 | 22:24 | 11.582 | 75646 | 75816 | 75907
11552 | 2021-11-13 | 22:24 | 11.5821 | 75645 | 75816 | 75907
11553 | 2021-11-13 | 22:24 | 11.5821 | 75644 | 75817 | 75907
11554 | 2021-11-13 | 22:24 | 11.5821 | 75643 | 75818 | 75907
11555 | 2021-11-13 | 22:24 | 11.5821 | 75642 | 75819 | 75907
11556 | 2021-11-13 | 22:24 | 11.5822 | 75641 | 75819 | 75908
11557 | 2021-11-13 | 22:24 | 11.5822 | 75640 | 75820 | 75908
11558 | 2021-11-13 | 22:24 | 11.5822 | 75639 | 75821 | 75908
11559 | 2021-11-13 | 22:24 | 11.5823 | 75638 | 75822 | 75908
11560 | 2021-11-13 | 22:24 | 11.5823 | 75637 | 75823 | 75908
11561 | 2021-11-13 | 22:24 | 11.5823 | 75636 | 75824 | 75908
11562 | 2021-11-13 | 22:24 | 11.5824 | 75635 | 75825 | 75908
11563 | 2021-11-13 | 22:24 | 11.5824 | 75634 | 75826 | 75908
11564 | 2021-11-13 | 22:24 | 11.5824 | 75633 | 75827 | 75908
11565 | 2021-11-13 | 22:24 | 11.5824 | 75632 | 75828 | 75908
11566 | 2021-11-13 | 22:24 | 11.5825 | 75631 | 75829 | 75907
11567 | 2021-11-13 | 22:24 | 11.5825 | 75630 | 75830 | 75907
11568 | 2021-11-13 | 22:24 | 11.5825 | 75629 | 75831 | 75907
11569 | 2021-11-13 | 22:24 | 11.5826 | 75628 | 75832 | 75906
11570 | 2021-11-13 | 22:24 | 11.5826 | 75627 | 75833 | 75906
11571 | 2021-11-13 | 22:24 | 11.5826 | 75626 | 75834 | 75905
11572 | 2021-11-13 | 22:24 | 11.5826 | 75625 | 75835 | 75905
11573 | 2021-11-13 | 22:24 | 11.5827 | 75625 | 75836 | 75904
11574 | 2021-11-13 | 22:24 | 11.5827 | 75624 | 75837 | 75904
11575 | 2021-11-13 | 22:24 | 11.5827 | 75623 | 75839 | 75903
11576 | 2021-11-13 | 22:24 | 11.5828 | 75622 | 75840 | 75903
11577 | 2021-11-13 | 22:24 | 11.5828 | 75621 | 75841 | 75902
11578 | 2021-11-13 | 22:24 | 11.5828 | 75621 | 75842 | 75902
11579 | 2021-11-13 | 22:24 | 11.5828 | 75620 | 75843 | 75901
11580 | 2021-11-13 | 22:24 | 11.5829 | 75619 | 75845 | 75900
11581 | 2021-11-13 | 22:24 | 11.5829 | 75618 | 75846 | 75900
11582 | 2021-11-13 | 22:24 | 11.5829 | 75618 | 75847 | 75899
11583 | 2021-11-13 | 22:24 | 11.583 | 75617 | 75848 | 75898
11584 | 2021-11-13 | 22:24 | 11.583 | 75617 | 75850 | 75897
11585 | 2021-11-13 | 22:24 | 11.583 | 75616 | 75851 | 75897
11586 | 2021-11-13 | 22:24 | 11.583 | 75616 | 75852 | 75896
11587 | 2021-11-13 | 22:24 | 11.5831 | 75615 | 75853 | 75896
11588 | 2021-11-13 | 22:24 | 11.5831 | 75615 | 75855 | 75895
11589 | 2021-11-13 | 22:24 | 11.5831 | 75614 | 75856 | 75894
11590 | 2021-11-13 | 22:24 | 11.5832 | 75614 | 75857 | 75893
11591 | 2021-11-13 | 22:24 | 11.5832 | 75614 | 75858 | 75892
11592 | 2021-11-13 | 22:24 | 11.5832 | 75613 | 75859 | 75891
11593 | 2021-11-13 | 22:24 | 11.5832 | 75613 | 75860 | 75891
11594 | 2021-11-13 | 22:24 | 11.5833 | 75613 | 75862 | 75890
11595 | 2021-11-13 | 22:24 | 11.5833 | 75613 | 75863 | 75889
11596 | 2021-11-13 | 22:24 | 11.5833 | 75612 | 75864 | 75888
11597 | 2021-11-13 | 22:24 | 11.5834 | 75612 | 75865 | 75887
11598 | 2021-11-13 | 22:24 | 11.5834 | 75612 | 75866 | 75886
11599 | 2021-11-13 | 22:24 | 11.5834 | 75612 | 75867 | 75885
11600 | 2021-11-13 | 22:24 | 11.5834 | 75612 | 75868 | 75884
11601 | 2021-11-13 | 22:24 | 11.5835 | 75612 | 75869 | 75883
11602 | 2021-11-13 | 22:24 | 11.5835 | 75612 | 75870 | 75882
11603 | 2021-11-13 | 22:24 | 11.5835 | 75612 | 75870 | 75881
11604 | 2021-11-13 | 22:24 | 11.5836 | 75612 | 75871 | 75881
11605 | 2021-11-13 | 22:24 | 11.5836 | 75612 | 75872 | 75880
11606 | 2021-11-13 | 22:24 | 11.5836 | 75612 | 75873 | 75879
11607 | 2021-11-13 | 22:24 | 11.5836 | 75612 | 75874 | 75878
11608 | 2021-11-13 | 22:24 | 11.5837 | 75612 | 75875 | 75877
11609 | 2021-11-13 | 22:24 | 11.5837 | 75613 | 75876 | 75876
11610 | 2021-11-13 | 22:24 | 11.5837 | 75613 | 75877 | 75875
11611 | 2021-11-13 | 22:24 | 11.5838 | 75613 | 75878 | 75874
11612 | 2021-11-13 | 22:24 | 11.5838 | 75613 | 75878 | 75873
11613 | 2021-11-13 | 22:24 | 11.5838 | 75613 | 75879 | 75872
11614 | 2021-11-13 | 22:24 | 11.5838 | 75614 | 75880 | 75871
11615 | 2021-11-13 | 22:24 | 11.5839 | 75614 | 75880 | 75870
11616 | 2021-11-13 | 22:24 | 11.5839 | 75614 | 75881 | 75869
11617 | 2021-11-13 | 22:24 | 11.5839 | 75615 | 75882 | 75868
11618 | 2021-11-13 | 22:24 | 11.584 | 75615 | 75883 | 75867
11619 | 2021-11-13 | 22:24 | 11.584 | 75615 | 75884 | 75866
11620 | 2021-11-13 | 22:24 | 11.584 | 75616 | 75885 | 75865
11621 | 2021-11-13 | 22:24 | 11.584 | 75616 | 75886 | 75864
11622 | 2021-11-13 | 22:24 | 11.5841 | 75617 | 75887 | 75864
11623 | 2021-11-13 | 22:24 | 11.5841 | 75617 | 75888 | 75863
11624 | 2021-11-13 | 22:24 | 11.5841 | 75618 | 75888 | 75862
11625 | 2021-11-13 | 22:24 | 11.5842 | 75618 | 75889 | 75861
11626 | 2021-11-13 | 22:24 | 11.5842 | 75619 | 75890 | 75860
11627 | 2021-11-13 | 22:24 | 11.5842 | 75619 | 75891 | 75859
11628 | 2021-11-13 | 22:24 | 11.5842 | 75620 | 75892 | 75858
11629 | 2021-11-13 | 22:24 | 11.5843 | 75621 | 75893 | 75857
11630 | 2021-11-13 | 22:24 | 11.5843 | 75621 | 75893 | 75856
11631 | 2021-11-13 | 22:24 | 11.5843 | 75622 | 75894 | 75855
11632 | 2021-11-13 | 22:24 | 11.5844 | 75623 | 75894 | 75854
11633 | 2021-11-13 | 22:24 | 11.5844 | 75623 | 75895 | 75853
11634 | 2021-11-13 | 22:24 | 11.5844 | 75624 | 75895 | 75852
11635 | 2021-11-13 | 22:24 | 11.5844 | 75625 | 75895 | 75851
11636 | 2021-11-13 | 22:24 | 11.5845 | 75626 | 75896 | 75850
11637 | 2021-11-13 | 22:24 | 11.5845 | 75626 | 75896 | 75849
11638 | 2021-11-13 | 22:24 | 11.5845 | 75627 | 75897 | 75848
11639 | 2021-11-13 | 22:24 | 11.5846 | 75628 | 75897 | 75846
11640 | 2021-11-13 | 22:24 | 11.5846 | 75629 | 75897 | 75845
11641 | 2021-11-13 | 22:24 | 11.5846 | 75630 | 75898 | 75844
11642 | 2021-11-13 | 22:24 | 11.5846 | 75631 | 75898 | 75843
11643 | 2021-11-13 | 22:24 | 11.5847 | 75632 | 75898 | 75842
11644 | 2021-11-13 | 22:24 | 11.5847 | 75633 | 75898 | 75841
11645 | 2021-11-13 | 22:24 | 11.5847 | 75633 | 75898 | 75840
11646 | 2021-11-13 | 22:24 | 11.5848 | 75635 | 75897 | 75839
11647 | 2021-11-13 | 22:24 | 11.5848 | 75636 | 75897 | 75838
11648 | 2021-11-13 | 22:24 | 11.5848 | 75637 | 75897 | 75837
11649 | 2021-11-13 | 22:24 | 11.5848 | 75638 | 75897 | 75836
11650 | 2021-11-13 | 22:24 | 11.5849 | 75639 | 75897 | 75835
11651 | 2021-11-13 | 22:24 | 11.5849 | 75640 | 75897 | 75834
11652 | 2021-11-13 | 22:24 | 11.5849 | 75641 | 75897 | 75833
11653 | 2021-11-13 | 22:24 | 11.585 | 75642 | 75897 | 75832
11654 | 2021-11-13 | 22:24 | 11.585 | 75644 | 75896 | 75831
11655 | 2021-11-13 | 22:24 | 11.585 | 75645 | 75896 | 75830
11656 | 2021-11-13 | 22:24 | 11.5851 | 75646 | 75896 | 75829
11657 | 2021-11-13 | 22:24 | 11.5851 | 75647 | 75895 | 75828
11658 | 2021-11-13 | 22:24 | 11.5851 | 75648 | 75895 | 75827
11659 | 2021-11-13 | 22:24 | 11.5851 | 75649 | 75895 | 75826
11660 | 2021-11-13 | 22:24 | 11.5852 | 75650 | 75894 | 75826
11661 | 2021-11-13 | 22:24 | 11.5852 | 75652 | 75894 | 75825
11662 | 2021-11-13 | 22:24 | 11.5852 | 75653 | 75894 | 75824
11663 | 2021-11-13 | 22:24 | 11.5853 | 75654 | 75893 | 75823
11664 | 2021-11-13 | 22:24 | 11.5853 | 75655 | 75892 | 75823
11665 | 2021-11-13 | 22:24 | 11.5853 | 75656 | 75892 | 75822
11666 | 2021-11-13 | 22:24 | 11.5853 | 75657 | 75891 | 75821
11667 | 2021-11-13 | 22:24 | 11.5854 | 75658 | 75891 | 75821
11668 | 2021-11-13 | 22:24 | 11.5854 | 75659 | 75890 | 75820
11669 | 2021-11-13 | 22:24 | 11.5854 | 75661 | 75890 | 75820
11670 | 2021-11-13 | 22:24 | 11.5855 | 75662 | 75889 | 75819
11671 | 2021-11-13 | 22:24 | 11.5855 | 75663 | 75888 | 75819
11672 | 2021-11-13 | 22:24 | 11.5855 | 75664 | 75887 | 75818
11673 | 2021-11-13 | 22:24 | 11.5855 | 75666 | 75886 | 75818
11674 | 2021-11-13 | 22:24 | 11.5856 | 75667 | 75885 | 75817
11675 | 2021-11-13 | 22:24 | 11.5856 | 75668 | 75884 | 75817
11676 | 2021-11-13 | 22:24 | 11.5856 | 75669 | 75883 | 75816
11677 | 2021-11-13 | 22:24 | 11.5857 | 75670 | 75882 | 75816
11678 | 2021-11-13 | 22:24 | 11.5857 | 75671 | 75881 | 75816
11679 | 2021-11-13 | 22:24 | 11.5857 | 75672 | 75880 | 75816
11680 | 2021-11-13 | 22:24 | 11.5857 | 75673 | 75879 | 75815
11681 | 2021-11-13 | 22:24 | 11.5858 | 75674 | 75878 | 75815
11682 | 2021-11-13 | 22:24 | 11.5858 | 75675 | 75877 | 75815
11683 | 2021-11-13 | 22:24 | 11.5858 | 75676 | 75875 | 75815
11684 | 2021-11-13 | 22:24 | 11.5859 | 75677 | 75874 | 75815
11685 | 2021-11-13 | 22:24 | 11.5859 | 75678 | 75873 | 75815
11686 | 2021-11-13 | 22:24 | 11.5859 | 75679 | 75872 | 75815
11687 | 2021-11-13 | 22:24 | 11.5859 | 75680 | 75871 | 75815
11688 | 2021-11-13 | 22:24 | 11.586 | 75681 | 75870 | 75815
11689 | 2021-11-13 | 22:24 | 11.586 | 75682 | 75869 | 75815
11690 | 2021-11-13 | 22:24 | 11.586 | 75683 | 75868 | 75815
11691 | 2021-11-13 | 22:24 | 11.5861 | 75684 | 75867 | 75815
11692 | 2021-11-13 | 22:24 | 11.5861 | 75685 | 75866 | 75815
11693 | 2021-11-13 | 22:24 | 11.5861 | 75686 | 75865 | 75815
11694 | 2021-11-13 | 22:24 | 11.5861 | 75687 | 75864 | 75815
11695 | 2021-11-13 | 22:24 | 11.5862 | 75687 | 75863 | 75815
11696 | 2021-11-13 | 22:24 | 11.5862 | 75688 | 75862 | 75816
11697 | 2021-11-13 | 22:24 | 11.5862 | 75689 | 75861 | 75816
11698 | 2021-11-13 | 22:24 | 11.5863 | 75689 | 75860 | 75816
11699 | 2021-11-13 | 22:24 | 11.5863 | 75690 | 75859 | 75816
11700 | 2021-11-13 | 22:24 | 11.5863 | 75691 | 75858 | 75817
11701 | 2021-11-13 | 22:24 | 11.5863 | 75692 | 75857 | 75817
11702 | 2021-11-13 | 22:24 | 11.5864 | 75693 | 75856 | 75817
11703 | 2021-11-13 | 22:24 | 11.5864 | 75693 | 75855 | 75818
11704 | 2021-11-13 | 22:24 | 11.5864 | 75694 | 75853 | 75818
11705 | 2021-11-13 | 22:24 | 11.5865 | 75694 | 75853 | 75819
11706 | 2021-11-13 | 22:24 | 11.5865 | 75695 | 75851 | 75819
11707 | 2021-11-13 | 22:24 | 11.5865 | 75695 | 75850 | 75820
11708 | 2021-11-13 | 22:24 | 11.5865 | 75696 | 75849 | 75820
11709 | 2021-11-13 | 22:24 | 11.5866 | 75697 | 75848 | 75820
11710 | 2021-11-13 | 22:24 | 11.5866 | 75697 | 75848 | 75821
11711 | 2021-11-13 | 22:24 | 11.5866 | 75698 | 75847 | 75822
11712 | 2021-11-13 | 22:24 | 11.5867 | 75699 | 75846 | 75822
11713 | 2021-11-13 | 22:24 | 11.5867 | 75700 | 75844 | 75823
11714 | 2021-11-13 | 22:24 | 11.5867 | 75701 | 75843 | 75823
11715 | 2021-11-13 | 22:24 | 11.5867 | 75702 | 75842 | 75824
11716 | 2021-11-13 | 22:24 | 11.5868 | 75702 | 75841 | 75825
11717 | 2021-11-13 | 22:24 | 11.5868 | 75702 | 75840 | 75825
11718 | 2021-11-13 | 22:24 | 11.5868 | 75703 | 75839 | 75826
11719 | 2021-11-13 | 22:24 | 11.5869 | 75703 | 75838 | 75827
11720 | 2021-11-13 | 22:24 | 11.5869 | 75703 | 75837 | 75827
11721 | 2021-11-13 | 22:24 | 11.5869 | 75704 | 75836 | 75828
11722 | 2021-11-13 | 22:24 | 11.5869 | 75704 | 75835 | 75829
11723 | 2021-11-13 | 22:24 | 11.587 | 75704 | 75834 | 75830
11724 | 2021-11-13 | 22:24 | 11.587 | 75705 | 75832 | 75831
11725 | 2021-11-13 | 22:24 | 11.587 | 75705 | 75831 | 75832
11726 | 2021-11-13 | 22:24 | 11.5871 | 75705 | 75830 | 75833
11727 | 2021-11-13 | 22:24 | 11.5871 | 75705 | 75829 | 75833
11728 | 2021-11-13 | 22:24 | 11.5871 | 75706 | 75828 | 75834
11729 | 2021-11-13 | 22:24 | 11.5871 | 75706 | 75827 | 75835
11730 | 2021-11-13 | 22:24 | 11.5872 | 75706 | 75826 | 75836
11731 | 2021-11-13 | 22:24 | 11.5872 | 75706 | 75825 | 75837
11732 | 2021-11-13 | 22:24 | 11.5872 | 75706 | 75824 | 75838
11733 | 2021-11-13 | 22:24 | 11.5873 | 75706 | 75823 | 75839
11734 | 2021-11-13 | 22:24 | 11.5873 | 75706 | 75822 | 75841
11735 | 2021-11-13 | 22:24 | 11.5873 | 75706 | 75821 | 75842
11736 | 2021-11-13 | 22:24 | 11.5873 | 75705 | 75820 | 75843
11737 | 2021-11-13 | 22:24 | 11.5874 | 75705 | 75819 | 75844
11738 | 2021-11-13 | 22:24 | 11.5874 | 75705 | 75818 | 75845
11739 | 2021-11-13 | 22:24 | 11.5874 | 75704 | 75818 | 75846
11740 | 2021-11-13 | 22:24 | 11.5875 | 75704 | 75817 | 75847
11741 | 2021-11-13 | 22:24 | 11.5875 | 75704 | 75816 | 75848
11742 | 2021-11-13 | 22:24 | 11.5875 | 75703 | 75815 | 75849
11743 | 2021-11-13 | 22:24 | 11.5875 | 75703 | 75814 | 75851
11744 | 2021-11-13 | 22:24 | 11.5876 | 75703 | 75813 | 75852
11745 | 2021-11-13 | 22:24 | 11.5876 | 75702 | 75812 | 75853
11746 | 2021-11-13 | 22:24 | 11.5876 | 75702 | 75812 | 75854
11747 | 2021-11-13 | 22:24 | 11.5877 | 75701 | 75811 | 75855
11748 | 2021-11-13 | 22:24 | 11.5877 | 75701 | 75810 | 75857
11749 | 2021-11-13 | 22:24 | 11.5877 | 75700 | 75809 | 75858
11750 | 2021-11-13 | 22:24 | 11.5878 | 75699 | 75809 | 75859
11751 | 2021-11-13 | 22:24 | 11.5878 | 75699 | 75808 | 75860
11752 | 2021-11-13 | 22:24 | 11.5878 | 75698 | 75807 | 75861
11753 | 2021-11-13 | 22:24 | 11.5878 | 75698 | 75807 | 75862
11754 | 2021-11-13 | 22:24 | 11.5879 | 75697 | 75806 | 75864
11755 | 2021-11-13 | 22:24 | 11.5879 | 75697 | 75806 | 75865
11756 | 2021-11-13 | 22:24 | 11.5879 | 75696 | 75805 | 75866
11757 | 2021-11-13 | 22:24 | 11.588 | 75696 | 75805 | 75867
11758 | 2021-11-13 | 22:24 | 11.588 | 75695 | 75804 | 75868
11759 | 2021-11-13 | 22:24 | 11.588 | 75694 | 75804 | 75869
11760 | 2021-11-13 | 22:24 | 11.588 | 75693 | 75804 | 75870
11761 | 2021-11-13 | 22:24 | 11.5881 | 75693 | 75803 | 75871
11762 | 2021-11-13 | 22:24 | 11.5881 | 75692 | 75803 | 75872
11763 | 2021-11-13 | 22:24 | 11.5881 | 75691 | 75803 | 75874
11764 | 2021-11-13 | 22:24 | 11.5882 | 75690 | 75803 | 75875
11765 | 2021-11-13 | 22:24 | 11.5882 | 75689 | 75802 | 75876
11766 | 2021-11-13 | 22:24 | 11.5882 | 75689 | 75802 | 75877
11767 | 2021-11-13 | 22:24 | 11.5882 | 75688 | 75802 | 75878
11768 | 2021-11-13 | 22:24 | 11.5883 | 75687 | 75802 | 75879
11769 | 2021-11-13 | 22:24 | 11.5883 | 75686 | 75802 | 75880
11770 | 2021-11-13 | 22:24 | 11.5883 | 75685 | 75802 | 75881
11771 | 2021-11-13 | 22:24 | 11.5884 | 75685 | 75802 | 75882
11772 | 2021-11-13 | 22:24 | 11.5884 | 75684 | 75802 | 75883
11773 | 2021-11-13 | 22:24 | 11.5884 | 75683 | 75802 | 75884
11774 | 2021-11-13 | 22:24 | 11.5884 | 75682 | 75802 | 75885
11775 | 2021-11-13 | 22:24 | 11.5885 | 75682 | 75802 | 75887
11776 | 2021-11-13 | 22:24 | 11.5885 | 75681 | 75802 | 75888
11777 | 2021-11-13 | 22:24 | 11.5885 | 75680 | 75802 | 75889
11778 | 2021-11-13 | 22:24 | 11.5886 | 75679 | 75802 | 75889
11779 | 2021-11-13 | 22:24 | 11.5886 | 75678 | 75802 | 75890
11780 | 2021-11-13 | 22:24 | 11.5886 | 75677 | 75802 | 75891
11781 | 2021-11-13 | 22:24 | 11.5886 | 75676 | 75803 | 75892
11782 | 2021-11-13 | 22:24 | 11.5887 | 75675 | 75803 | 75893
11783 | 2021-11-13 | 22:24 | 11.5887 | 75674 | 75803 | 75894
11784 | 2021-11-13 | 22:24 | 11.5887 | 75673 | 75803 | 75895
11785 | 2021-11-13 | 22:24 | 11.5888 | 75672 | 75804 | 75896
11786 | 2021-11-13 | 22:24 | 11.5888 | 75671 | 75804 | 75897
11787 | 2021-11-13 | 22:24 | 11.5888 | 75670 | 75805 | 75898
11788 | 2021-11-13 | 22:24 | 11.5888 | 75669 | 75805 | 75899
11789 | 2021-11-13 | 22:24 | 11.5889 | 75667 | 75805 | 75900
11790 | 2021-11-13 | 22:24 | 11.5889 | 75666 | 75806 | 75901
11791 | 2021-11-13 | 22:24 | 11.5889 | 75665 | 75806 | 75902
11792 | 2021-11-13 | 22:24 | 11.589 | 75664 | 75807 | 75903
11793 | 2021-11-13 | 22:24 | 11.589 | 75663 | 75807 | 75903
11794 | 2021-11-13 | 22:24 | 11.589 | 75662 | 75808 | 75904
11795 | 2021-11-13 | 22:24 | 11.589 | 75661 | 75808 | 75905
11796 | 2021-11-13 | 22:24 | 11.5891 | 75660 | 75809 | 75906
11797 | 2021-11-13 | 22:24 | 11.5891 | 75659 | 75810 | 75907
11798 | 2021-11-13 | 22:24 | 11.5891 | 75657 | 75810 | 75907
11799 | 2021-11-13 | 22:24 | 11.5892 | 75656 | 75811 | 75908
11800 | 2021-11-13 | 22:24 | 11.5892 | 75655 | 75812 | 75909
11801 | 2021-11-13 | 22:24 | 11.5892 | 75654 | 75812 | 75909
11802 | 2021-11-13 | 22:24 | 11.5892 | 75653 | 75813 | 75910
11803 | 2021-11-13 | 22:24 | 11.5893 | 75652 | 75814 | 75910
11804 | 2021-11-13 | 22:24 | 11.5893 | 75651 | 75814 | 75911
11805 | 2021-11-13 | 22:24 | 11.5893 | 75650 | 75815 | 75911
11806 | 2021-11-13 | 22:24 | 11.5894 | 75649 | 75816 | 75912
11807 | 2021-11-13 | 22:24 | 11.5894 | 75648 | 75817 | 75912
11808 | 2021-11-13 | 22:24 | 11.5894 | 75646 | 75818 | 75912
11809 | 2021-11-13 | 22:24 | 11.5894 | 75645 | 75818 | 75912
11810 | 2021-11-13 | 22:24 | 11.5895 | 75644 | 75819 | 75912
11811 | 2021-11-13 | 22:24 | 11.5895 | 75643 | 75820 | 75912
11812 | 2021-11-13 | 22:24 | 11.5895 | 75642 | 75821 | 75912
11813 | 2021-11-13 | 22:24 | 11.5896 | 75641 | 75822 | 75912
11814 | 2021-11-13 | 22:24 | 11.5896 | 75640 | 75822 | 75912
11815 | 2021-11-13 | 22:24 | 11.5896 | 75639 | 75823 | 75912
11816 | 2021-11-13 | 22:24 | 11.5896 | 75638 | 75824 | 75912
11817 | 2021-11-13 | 22:24 | 11.5897 | 75637 | 75825 | 75912
11818 | 2021-11-13 | 22:24 | 11.5897 | 75636 | 75826 | 75912
11819 | 2021-11-13 | 22:24 | 11.5897 | 75635 | 75827 | 75912
11820 | 2021-11-13 | 22:24 | 11.5898 | 75633 | 75828 | 75912
11821 | 2021-11-13 | 22:24 | 11.5898 | 75632 | 75829 | 75911
11822 | 2021-11-13 | 22:24 | 11.5898 | 75631 | 75830 | 75911
11823 | 2021-11-13 | 22:24 | 11.5898 | 75630 | 75831 | 75911
11824 | 2021-11-13 | 22:24 | 11.5899 | 75629 | 75832 | 75910
11825 | 2021-11-13 | 22:24 | 11.5899 | 75628 | 75833 | 75910
11826 | 2021-11-13 | 22:24 | 11.5899 | 75628 | 75834 | 75909
11827 | 2021-11-13 | 22:24 | 11.59 | 75627 | 75835 | 75909
11828 | 2021-11-13 | 22:24 | 11.59 | 75626 | 75837 | 75908
11829 | 2021-11-13 | 22:24 | 11.59 | 75625 | 75838 | 75908
11830 | 2021-11-13 | 22:24 | 11.59 | 75624 | 75839 | 75907
11831 | 2021-11-13 | 22:24 | 11.5901 | 75623 | 75840 | 75906
11832 | 2021-11-13 | 22:24 | 11.5901 | 75622 | 75841 | 75906
11833 | 2021-11-13 | 22:24 | 11.5901 | 75622 | 75842 | 75905
11834 | 2021-11-13 | 22:24 | 11.5902 | 75621 | 75844 | 75904
11835 | 2021-11-13 | 22:24 | 11.5902 | 75620 | 75845 | 75904
11836 | 2021-11-13 | 22:24 | 11.5902 | 75619 | 75846 | 75903
11837 | 2021-11-13 | 22:24 | 11.5902 | 75619 | 75848 | 75902
11838 | 2021-11-13 | 22:24 | 11.5903 | 75618 | 75849 | 75902
11839 | 2021-11-13 | 22:24 | 11.5903 | 75618 | 75851 | 75901
11840 | 2021-11-13 | 22:24 | 11.5903 | 75617 | 75852 | 75900
11841 | 2021-11-13 | 22:24 | 11.5904 | 75616 | 75853 | 75899
11842 | 2021-11-13 | 22:24 | 11.5904 | 75616 | 75855 | 75899
11843 | 2021-11-13 | 22:24 | 11.5904 | 75615 | 75856 | 75898
11844 | 2021-11-13 | 22:24 | 11.5905 | 75615 | 75857 | 75897
11845 | 2021-11-13 | 22:24 | 11.5905 | 75615 | 75858 | 75896
11846 | 2021-11-13 | 22:24 | 11.5905 | 75614 | 75860 | 75895
11847 | 2021-11-13 | 22:24 | 11.5905 | 75614 | 75861 | 75895
11848 | 2021-11-13 | 22:24 | 11.5906 | 75614 | 75862 | 75894
11849 | 2021-11-13 | 22:24 | 11.5906 | 75613 | 75864 | 75893
11850 | 2021-11-13 | 22:24 | 11.5906 | 75613 | 75865 | 75892
11851 | 2021-11-13 | 22:24 | 11.5907 | 75613 | 75866 | 75891
11852 | 2021-11-13 | 22:24 | 11.5907 | 75613 | 75867 | 75890
11853 | 2021-11-13 | 22:24 | 11.5907 | 75612 | 75868 | 75889
11854 | 2021-11-13 | 22:24 | 11.5907 | 75612 | 75869 | 75889
11855 | 2021-11-13 | 22:24 | 11.5908 | 75612 | 75870 | 75888
11856 | 2021-11-13 | 22:24 | 11.5908 | 75612 | 75871 | 75887
11857 | 2021-11-13 | 22:24 | 11.5908 | 75612 | 75872 | 75886
11858 | 2021-11-13 | 22:24 | 11.5909 | 75612 | 75873 | 75885
11859 | 2021-11-13 | 22:24 | 11.5909 | 75612 | 75874 | 75884
11860 | 2021-11-13 | 22:24 | 11.5909 | 75612 | 75875 | 75883
11861 | 2021-11-13 | 22:24 | 11.5909 | 75612 | 75876 | 75882
11862 | 2021-11-13 | 22:24 | 11.591 | 75612 | 75877 | 75881
11863 | 2021-11-13 | 22:24 | 11.591 | 75612 | 75878 | 75881
11864 | 2021-11-13 | 22:24 | 11.591 | 75613 | 75879 | 75880
11865 | 2021-11-13 | 22:24 | 11.5911 | 75613 | 75880 | 75879
11866 | 2021-11-13 | 22:24 | 11.5911 | 75613 | 75880 | 75878
11867 | 2021-11-13 | 22:24 | 11.5911 | 75613 | 75881 | 75877
11868 | 2021-11-13 | 22:24 | 11.5911 | 75613 | 75881 | 75876
11869 | 2021-11-13 | 22:24 | 11.5912 | 75614 | 75882 | 75875
11870 | 2021-11-13 | 22:24 | 11.5912 | 75614 | 75883 | 75874
11871 | 2021-11-13 | 22:24 | 11.5912 | 75614 | 75883 | 75873
11872 | 2021-11-13 | 22:24 | 11.5913 | 75615 | 75884 | 75872
11873 | 2021-11-13 | 22:24 | 11.5913 | 75615 | 75885 | 75871
11874 | 2021-11-13 | 22:24 | 11.5913 | 75615 | 75885 | 75870
11875 | 2021-11-13 | 22:24 | 11.5913 | 75616 | 75886 | 75869
11876 | 2021-11-13 | 22:24 | 11.5914 | 75616 | 75887 | 75868
11877 | 2021-11-13 | 22:24 | 11.5914 | 75616 | 75887 | 75867
11878 | 2021-11-13 | 22:24 | 11.5914 | 75617 | 75888 | 75866
11879 | 2021-11-13 | 22:24 | 11.5915 | 75617 | 75889 | 75865
11880 | 2021-11-13 | 22:24 | 11.5915 | 75618 | 75890 | 75864
11881 | 2021-11-13 | 22:24 | 11.5915 | 75619 | 75891 | 75863
11882 | 2021-11-13 | 22:24 | 11.5915 | 75619 | 75892 | 75862
11883 | 2021-11-13 | 22:24 | 11.5916 | 75620 | 75892 | 75861
11884 | 2021-11-13 | 22:24 | 11.5916 | 75620 | 75893 | 75860
11885 | 2021-11-13 | 22:24 | 11.5916 | 75621 | 75894 | 75859
11886 | 2021-11-13 | 22:24 | 11.5917 | 75622 | 75894 | 75858
11887 | 2021-11-13 | 22:24 | 11.5917 | 75622 | 75895 | 75857
11888 | 2021-11-13 | 22:24 | 11.5917 | 75623 | 75895 | 75856
11889 | 2021-11-13 | 22:24 | 11.5917 | 75624 | 75895 | 75855
11890 | 2021-11-13 | 22:24 | 11.5918 | 75625 | 75896 | 75854
11891 | 2021-11-13 | 22:24 | 11.5918 | 75625 | 75896 | 75852
11892 | 2021-11-13 | 22:24 | 11.5918 | 75626 | 75897 | 75851
11893 | 2021-11-13 | 22:24 | 11.5919 | 75627 | 75897 | 75850
11894 | 2021-11-13 | 22:24 | 11.5919 | 75628 | 75898 | 75849
11895 | 2021-11-13 | 22:24 | 11.5919 | 75629 | 75898 | 75848
11896 | 2021-11-13 | 22:24 | 11.5919 | 75629 | 75898 | 75847
11897 | 2021-11-13 | 22:24 | 11.592 | 75630 | 75898 | 75846
11898 | 2021-11-13 | 22:24 | 11.592 | 75631 | 75898 | 75845
11899 | 2021-11-13 | 22:24 | 11.592 | 75632 | 75899 | 75844
11900 | 2021-11-13 | 22:24 | 11.5921 | 75633 | 75899 | 75842
11901 | 2021-11-13 | 22:24 | 11.5921 | 75634 | 75899 | 75841
11902 | 2021-11-13 | 22:24 | 11.5921 | 75635 | 75899 | 75840
11903 | 2021-11-13 | 22:24 | 11.5921 | 75636 | 75898 | 75839
11904 | 2021-11-13 | 22:24 | 11.5922 | 75637 | 75898 | 75838
11905 | 2021-11-13 | 22:24 | 11.5922 | 75639 | 75898 | 75837
11906 | 2021-11-13 | 22:24 | 11.5922 | 75640 | 75898 | 75836
11907 | 2021-11-13 | 22:24 | 11.5923 | 75641 | 75898 | 75835
11908 | 2021-11-13 | 22:24 | 11.5923 | 75642 | 75898 | 75834
11909 | 2021-11-13 | 22:24 | 11.5923 | 75643 | 75897 | 75833
11910 | 2021-11-13 | 22:24 | 11.5923 | 75644 | 75897 | 75832
11911 | 2021-11-13 | 22:24 | 11.5924 | 75645 | 75897 | 75831
11912 | 2021-11-13 | 22:24 | 11.5924 | 75646 | 75896 | 75830
11913 | 2021-11-13 | 22:24 | 11.5924 | 75647 | 75896 | 75829
11914 | 2021-11-13 | 22:24 | 11.5925 | 75648 | 75895 | 75828
11915 | 2021-11-13 | 22:24 | 11.5925 | 75650 | 75895 | 75827
11916 | 2021-11-13 | 22:24 | 11.5925 | 75651 | 75894 | 75826
11917 | 2021-11-13 | 22:24 | 11.5925 | 75652 | 75893 | 75825
11918 | 2021-11-13 | 22:24 | 11.5926 | 75653 | 75893 | 75825
11919 | 2021-11-13 | 22:24 | 11.5926 | 75654 | 75892 | 75824
11920 | 2021-11-13 | 22:24 | 11.5926 | 75655 | 75891 | 75823
11921 | 2021-11-13 | 22:24 | 11.5927 | 75656 | 75891 | 75823
11922 | 2021-11-13 | 22:24 | 11.5927 | 75657 | 75890 | 75822
11923 | 2021-11-13 | 22:24 | 11.5927 | 75659 | 75890 | 75821
11924 | 2021-11-13 | 22:24 | 11.5927 | 75660 | 75889 | 75821
11925 | 2021-11-13 | 22:24 | 11.5928 | 75661 | 75889 | 75820
11926 | 2021-11-13 | 22:24 | 11.5928 | 75662 | 75888 | 75820
11927 | 2021-11-13 | 22:24 | 11.5928 | 75663 | 75887 | 75819
11928 | 2021-11-13 | 22:24 | 11.5929 | 75664 | 75886 | 75819
11929 | 2021-11-13 | 22:24 | 11.5929 | 75665 | 75885 | 75818
11930 | 2021-11-13 | 22:24 | 11.5929 | 75666 | 75884 | 75818
11931 | 2021-11-13 | 22:24 | 11.5929 | 75667 | 75883 | 75818
11932 | 2021-11-13 | 22:24 | 11.593 | 75668 | 75882 | 75817
11933 | 2021-11-13 | 22:24 | 11.593 | 75670 | 75881 | 75817
11934 | 2021-11-13 | 22:24 | 11.593 | 75671 | 75880 | 75817
11935 | 2021-11-13 | 22:24 | 11.5931 | 75672 | 75879 | 75816
11936 | 2021-11-13 | 22:24 | 11.5931 | 75673 | 75878 | 75816
11937 | 2021-11-13 | 22:24 | 11.5931 | 75674 | 75877 | 75816
11938 | 2021-11-13 | 22:24 | 11.5932 | 75675 | 75876 | 75816
11939 | 2021-11-13 | 22:24 | 11.5932 | 75676 | 75875 | 75816
11940 | 2021-11-13 | 22:24 | 11.5932 | 75678 | 75874 | 75816
11941 | 2021-11-13 | 22:24 | 11.5932 | 75679 | 75873 | 75815
11942 | 2021-11-13 | 22:24 | 11.5933 | 75680 | 75872 | 75815
11943 | 2021-11-13 | 22:24 | 11.5933 | 75681 | 75871 | 75815
11944 | 2021-11-13 | 22:24 | 11.5933 | 75682 | 75870 | 75815
11945 | 2021-11-13 | 22:24 | 11.5934 | 75683 | 75869 | 75815
11946 | 2021-11-13 | 22:24 | 11.5934 | 75684 | 75868 | 75815
11947 | 2021-11-13 | 22:24 | 11.5934 | 75685 | 75867 | 75816
11948 | 2021-11-13 | 22:24 | 11.5934 | 75686 | 75866 | 75816
11949 | 2021-11-13 | 22:24 | 11.5935 | 75687 | 75865 | 75816
11950 | 2021-11-13 | 22:24 | 11.5935 | 75688 | 75864 | 75816
11951 | 2021-11-13 | 22:24 | 11.5935 | 75689 | 75863 | 75816
11952 | 2021-11-13 | 22:24 | 11.5936 | 75690 | 75862 | 75816
11953 | 2021-11-13 | 22:24 | 11.5936 | 75691 | 75861 | 75817
11954 | 2021-11-13 | 22:24 | 11.5936 | 75692 | 75860 | 75817
11955 | 2021-11-13 | 22:24 | 11.5936 | 75693 | 75859 | 75817
11956 | 2021-11-13 | 22:24 | 11.5937 | 75693 | 75858 | 75818
11957 | 2021-11-13 | 22:24 | 11.5937 | 75694 | 75857 | 75818
11958 | 2021-11-13 | 22:24 | 11.5937 | 75695 | 75856 | 75818
11959 | 2021-11-13 | 22:24 | 11.5938 | 75695 | 75854 | 75819
11960 | 2021-11-13 | 22:24 | 11.5938 | 75696 | 75853 | 75819
11961 | 2021-11-13 | 22:24 | 11.5938 | 75696 | 75852 | 75819
11962 | 2021-11-13 | 22:24 | 11.5938 | 75697 | 75851 | 75820
11963 | 2021-11-13 | 22:24 | 11.5939 | 75698 | 75850 | 75820
11964 | 2021-11-13 | 22:24 | 11.5939 | 75698 | 75849 | 75821
11965 | 2021-11-13 | 22:24 | 11.5939 | 75699 | 75848 | 75822
11966 | 2021-11-13 | 22:24 | 11.594 | 75700 | 75847 | 75822
11967 | 2021-11-13 | 22:24 | 11.594 | 75701 | 75846 | 75823
11968 | 2021-11-13 | 22:24 | 11.594 | 75702 | 75845 | 75823
11969 | 2021-11-13 | 22:24 | 11.594 | 75702 | 75843 | 75824
11970 | 2021-11-13 | 22:24 | 11.5941 | 75703 | 75842 | 75825
11971 | 2021-11-13 | 22:24 | 11.5941 | 75703 | 75841 | 75825
11972 | 2021-11-13 | 22:24 | 11.5941 | 75704 | 75840 | 75826
11973 | 2021-11-13 | 22:24 | 11.5942 | 75704 | 75839 | 75827
11974 | 2021-11-13 | 22:24 | 11.5942 | 75704 | 75838 | 75827
11975 | 2021-11-13 | 22:24 | 11.5942 | 75705 | 75837 | 75828
11976 | 2021-11-13 | 22:24 | 11.5942 | 75705 | 75835 | 75829
11977 | 2021-11-13 | 22:24 | 11.5943 | 75706 | 75834 | 75830
11978 | 2021-11-13 | 22:24 | 11.5943 | 75706 | 75833 | 75830
11979 | 2021-11-13 | 22:24 | 11.5943 | 75706 | 75832 | 75831
11980 | 2021-11-13 | 22:24 | 11.5944 | 75706 | 75831 | 75832
11981 | 2021-11-13 | 22:24 | 11.5944 | 75706 | 75830 | 75833
11982 | 2021-11-13 | 22:24 | 11.5944 | 75707 | 75829 | 75834
11983 | 2021-11-13 | 22:24 | 11.5944 | 75707 | 75828 | 75835
11984 | 2021-11-13 | 22:24 | 11.5945 | 75707 | 75827 | 75836
11985 | 2021-11-13 | 22:24 | 11.5945 | 75707 | 75826 | 75837
11986 | 2021-11-13 | 22:24 | 11.5945 | 75707 | 75825 | 75838
11987 | 2021-11-13 | 22:24 | 11.5946 | 75707 | 75824 | 75839
11988 | 2021-11-13 | 22:24 | 11.5946 | 75707 | 75823 | 75840
11989 | 2021-11-13 | 22:24 | 11.5946 | 75707 | 75822 | 75841
11990 | 2021-11-13 | 22:24 | 11.5946 | 75707 | 75821 | 75842
11991 | 2021-11-13 | 22:24 | 11.5947 | 75706 | 75820 | 75843
11992 | 2021-11-13 | 22:24 | 11.5947 | 75706 | 75819 | 75844
11993 | 2021-11-13 | 22:24 | 11.5947 | 75706 | 75818 | 75845
11994 | 2021-11-13 | 22:24 | 11.5948 | 75706 | 75817 | 75846
11995 | 2021-11-13 | 22:24 | 11.5948 | 75706 | 75816 | 75847
11996 | 2021-11-13 | 22:24 | 11.5948 | 75705 | 75815 | 75849
11997 | 2021-11-13 | 22:24 | 11.5948 | 75705 | 75814 | 75850
11998 | 2021-11-13 | 22:24 | 11.5949 | 75705 | 75813 | 75851
11999 | 2021-11-13 | 22:24 | 11.5949 | 75704 | 75813 | 75852
12000 | 2021-11-13 | 22:24 | 11.5949 | 75703 | 75812 | 75853
12001 | 2021-11-13 | 22:24 | 11.595 | 75702 | 75811 | 75854
12002 | 2021-11-13 | 22:24 | 11.595 | 75701 | 75810 | 75855
12003 | 2021-11-13 | 22:24 | 11.595 | 75701 | 75810 | 75856
12004 | 2021-11-13 | 22:24 | 11.595 | 75700 | 75809 | 75857
12005 | 2021-11-13 | 22:24 | 11.5951 | 75699 | 75808 | 75858
12006 | 2021-11-13 | 22:24 | 11.5951 | 75698 | 75807 | 75859
12007 | 2021-11-13 | 22:24 | 11.5951 | 75698 | 75807 | 75860
12008 | 2021-11-13 | 22:24 | 11.5952 | 75697 | 75806 | 75861
12009 | 2021-11-13 | 22:24 | 11.5952 | 75696 | 75805 | 75862
12010 | 2021-11-13 | 22:24 | 11.5952 | 75695 | 75805 | 75864
12011 | 2021-11-13 | 22:24 | 11.5952 | 75694 | 75804 | 75865
12012 | 2021-11-13 | 22:24 | 11.5953 | 75693 | 75804 | 75866
12013 | 2021-11-13 | 22:24 | 11.5953 | 75692 | 75803 | 75867
12014 | 2021-11-13 | 22:24 | 11.5953 | 75691 | 75803 | 75868
12015 | 2021-11-13 | 22:24 | 11.5954 | 75690 | 75802 | 75869
12016 | 2021-11-13 | 22:24 | 11.5954 | 75689 | 75802 | 75870
12017 | 2021-11-13 | 22:24 | 11.5954 | 75688 | 75802 | 75871
12018 | 2021-11-13 | 22:24 | 11.5954 | 75687 | 75801 | 75872
12019 | 2021-11-13 | 22:24 | 11.5955 | 75686 | 75801 | 75873
12020 | 2021-11-13 | 22:24 | 11.5955 | 75685 | 75801 | 75874
12021 | 2021-11-13 | 22:24 | 11.5955 | 75684 | 75801 | 75875
12022 | 2021-11-13 | 22:24 | 11.5956 | 75683 | 75800 | 75876
12023 | 2021-11-13 | 22:24 | 11.5956 | 75682 | 75800 | 75877
12024 | 2021-11-13 | 22:24 | 11.5956 | 75681 | 75800 | 75878
12025 | 2021-11-13 | 22:24 | 11.5956 | 75680 | 75800 | 75879
12026 | 2021-11-13 | 22:24 | 11.5957 | 75679 | 75800 | 75880
12027 | 2021-11-13 | 22:24 | 11.5957 | 75678 | 75800 | 75881
12028 | 2021-11-13 | 22:24 | 11.5957 | 75677 | 75800 | 75882
12029 | 2021-11-13 | 22:24 | 11.5958 | 75677 | 75800 | 75883
12030 | 2021-11-13 | 22:24 | 11.5958 | 75676 | 75800 | 75884
12031 | 2021-11-13 | 22:24 | 11.5958 | 75675 | 75800 | 75885
12032 | 2021-11-13 | 22:24 | 11.5959 | 75674 | 75800 | 75885
12033 | 2021-11-13 | 22:24 | 11.5959 | 75673 | 75800 | 75886
12034 | 2021-11-13 | 22:24 | 11.5959 | 75672 | 75800 | 75887
12035 | 2021-11-13 | 22:24 | 11.5959 | 75671 | 75801 | 75888
12036 | 2021-11-13 | 22:24 | 11.596 | 75670 | 75801 | 75888
12037 | 2021-11-13 | 22:24 | 11.596 | 75669 | 75801 | 75889
12038 | 2021-11-13 | 22:24 | 11.596 | 75668 | 75801 | 75890
12039 | 2021-11-13 | 22:24 | 11.5961 | 75667 | 75801 | 75891
12040 | 2021-11-13 | 22:24 | 11.5961 | 75666 | 75802 | 75892
12041 | 2021-11-13 | 22:24 | 11.5961 | 75665 | 75802 | 75893
12042 | 2021-11-13 | 22:24 | 11.5961 | 75664 | 75802 | 75894
12043 | 2021-11-13 | 22:24 | 11.5962 | 75663 | 75803 | 75894
12044 | 2021-11-13 | 22:24 | 11.5962 | 75662 | 75803 | 75895
12045 | 2021-11-13 | 22:24 | 11.5962 | 75661 | 75803 | 75896
12046 | 2021-11-13 | 22:24 | 11.5963 | 75660 | 75804 | 75896
12047 | 2021-11-13 | 22:24 | 11.5963 | 75659 | 75804 | 75897
12048 | 2021-11-13 | 22:24 | 11.5963 | 75658 | 75804 | 75898
12049 | 2021-11-13 | 22:24 | 11.5963 | 75657 | 75805 | 75898
12050 | 2021-11-13 | 22:24 | 11.5964 | 75656 | 75805 | 75899
12051 | 2021-11-13 | 22:24 | 11.5964 | 75655 | 75806 | 75900
12052 | 2021-11-13 | 22:24 | 11.5964 | 75654 | 75806 | 75900
12053 | 2021-11-13 | 22:24 | 11.5965 | 75653 | 75807 | 75901
12054 | 2021-11-13 | 22:24 | 11.5965 | 75652 | 75808 | 75902
12055 | 2021-11-13 | 22:24 | 11.5965 | 75651 | 75808 | 75902
12056 | 2021-11-13 | 22:24 | 11.5965 | 75650 | 75809 | 75903
12057 | 2021-11-13 | 22:24 | 11.5966 | 75650 | 75809 | 75904
12058 | 2021-11-13 | 22:24 | 11.5966 | 75649 | 75810 | 75905
12059 | 2021-11-13 | 22:24 | 11.5966 | 75647 | 75811 | 75905
12060 | 2021-11-13 | 22:24 | 11.5967 | 75646 | 75812 | 75906
12061 | 2021-11-13 | 22:24 | 11.5967 | 75645 | 75812 | 75906
12062 | 2021-11-13 | 22:24 | 11.5967 | 75644 | 75813 | 75906
12063 | 2021-11-13 | 22:24 | 11.5967 | 75643 | 75814 | 75907
12064 | 2021-11-13 | 22:24 | 11.5968 | 75642 | 75815 | 75907
12065 | 2021-11-13 | 22:24 | 11.5968 | 75641 | 75815 | 75907
12066 | 2021-11-13 | 22:24 | 11.5968 | 75640 | 75816 | 75908
12067 | 2021-11-13 | 22:24 | 11.5969 | 75637 | 75816 | 75911
12068 | 2021-11-13 | 22:24 | 11.5969 | 75631 | 75813 | 75922
12069 | 2021-11-13 | 22:24 | 11.5969 | 75621 | 75808 | 75941
12070 | 2021-11-13 | 22:24 | 11.5969 | 75609 | 75800 | 75966
12071 | 2021-11-13 | 22:24 | 11.597 | 75596 | 75792 | 75994
12072 | 2021-11-13 | 22:24 | 11.597 | 75583 | 75783 | 76022
12073 | 2021-11-13 | 22:24 | 11.597 | 75572 | 75775 | 76046
12074 | 2021-11-13 | 22:24 | 11.5971 | 75564 | 75770 | 76064
12075 | 2021-11-13 | 22:24 | 11.5971 | 75559 | 75767 | 76075
12076 | 2021-11-13 | 22:24 | 11.5971 | 75556 | 75768 | 76078
12077 | 2021-11-13 | 22:24 | 11.5971 | 75556 | 75770 | 76076
12078 | 2021-11-13 | 22:24 | 11.5972 | 75555 | 75772 | 76073
12079 | 2021-11-13 | 22:24 | 11.5972 | 75550 | 75772 | 76074
12080 | 2021-11-13 | 22:24 | 11.5972 | 75543 | 75768 | 76081
12081 | 2021-11-13 | 22:24 | 11.5973 | 75534 | 75761 | 76092
12082 | 2021-11-13 | 22:24 | 11.5973 | 75524 | 75751 | 76107
12083 | 2021-11-13 | 22:24 | 11.5973 | 75513 | 75739 | 76124
12084 | 2021-11-13 | 22:24 | 11.5973 | 75503 | 75726 | 76142
12085 | 2021-11-13 | 22:24 | 11.5974 | 75493 | 75714 | 76158
12086 | 2021-11-13 | 22:24 | 11.5974 | 75485 | 75705 | 76168
12087 | 2021-11-13 | 22:24 | 11.5974 | 75479 | 75700 | 76172
12088 | 2021-11-13 | 22:24 | 11.5975 | 75476 | 75700 | 76169
12089 | 2021-11-13 | 22:24 | 11.5975 | 75472 | 75702 | 76162
12090 | 2021-11-13 | 22:24 | 11.5975 | 75468 | 75706 | 76156
12091 | 2021-11-13 | 22:24 | 11.5975 | 75463 | 75710 | 76151
12092 | 2021-11-13 | 22:24 | 11.5976 | 75458 | 75712 | 76149
12093 | 2021-11-13 | 22:24 | 11.5976 | 75451 | 75713 | 76149
12094 | 2021-11-13 | 22:24 | 11.5976 | 75444 | 75712 | 76153
12095 | 2021-11-13 | 22:24 | 11.5977 | 75437 | 75711 | 76160
12096 | 2021-11-13 | 22:24 | 11.5977 | 75430 | 75711 | 76166
12097 | 2021-11-13 | 22:24 | 11.5977 | 75425 | 75717 | 76168
12098 | 2021-11-13 | 22:24 | 11.5977 | 75421 | 75729 | 76162
12099 | 2021-11-13 | 22:24 | 11.5978 | 75417 | 75749 | 76150
12100 | 2021-11-13 | 22:24 | 11.5978 | 75414 | 75773 | 76133
12101 | 2021-11-13 | 22:24 | 11.5978 | 75411 | 75798 | 76117
12102 | 2021-11-13 | 22:24 | 11.5979 | 75408 | 75822 | 76102
12103 | 2021-11-13 | 22:24 | 11.5979 | 75405 | 75842 | 76092
12104 | 2021-11-13 | 22:24 | 11.5979 | 75403 | 75857 | 76087
12105 | 2021-11-13 | 22:24 | 11.5979 | 75401 | 75868 | 76086
12106 | 2021-11-13 | 22:24 | 11.598 | 75401 | 75876 | 76089
12107 | 2021-11-13 | 22:24 | 11.598 | 75400 | 75886 | 76090
12108 | 2021-11-13 | 22:24 | 11.598 | 75400 | 75899 | 76087
12109 | 2021-11-13 | 22:24 | 11.5981 | 75400 | 75916 | 76079
12110 | 2021-11-13 | 22:24 | 11.5981 | 75400 | 75939 | 76065
12111 | 2021-11-13 | 22:24 | 11.5981 | 75401 | 75964 | 76049
12112 | 2021-11-13 | 22:24 | 11.5981 | 75401 | 75991 | 76031
12113 | 2021-11-13 | 22:24 | 11.5982 | 75402 | 76016 | 76015
12114 | 2021-11-13 | 22:24 | 11.5982 | 75404 | 76038 | 76000
12115 | 2021-11-13 | 22:24 | 11.5982 | 75406 | 76056 | 75988
12116 | 2021-11-13 | 22:24 | 11.5983 | 75409 | 76069 | 75979
12117 | 2021-11-13 | 22:24 | 11.5983 | 75413 | 76079 | 75972
12118 | 2021-11-13 | 22:24 | 11.5983 | 75417 | 76087 | 75963
12119 | 2021-11-13 | 22:24 | 11.5983 | 75420 | 76095 | 75953
12120 | 2021-11-13 | 22:24 | 11.5984 | 75424 | 76104 | 75940
12121 | 2021-11-13 | 22:24 | 11.5984 | 75427 | 76115 | 75924
12122 | 2021-11-13 | 22:24 | 11.5984 | 75431 | 76128 | 75905
12123 | 2021-11-13 | 22:24 | 11.5985 | 75434 | 76140 | 75885
12124 | 2021-11-13 | 22:24 | 11.5985 | 75437 | 76151 | 75867
12125 | 2021-11-13 | 22:24 | 11.5985 | 75441 | 76158 | 75853
12126 | 2021-11-13 | 22:24 | 11.5986 | 75445 | 76160 | 75843
12127 | 2021-11-13 | 22:24 | 11.5986 | 75449 | 76159 | 75837
12128 | 2021-11-13 | 22:24 | 11.5986 | 75453 | 76153 | 75835
12129 | 2021-11-13 | 22:24 | 11.5986 | 75458 | 76147 | 75835
12130 | 2021-11-13 | 22:24 | 11.5987 | 75461 | 76142 | 75833
12131 | 2021-11-13 | 22:24 | 11.5987 | 75464 | 76141 | 75827
12132 | 2021-11-13 | 22:24 | 11.5987 | 75466 | 76147 | 75818
12133 | 2021-11-13 | 22:24 | 11.5988 | 75467 | 76157 | 75804
12134 | 2021-11-13 | 22:24 | 11.5988 | 75467 | 76172 | 75788
12135 | 2021-11-13 | 22:24 | 11.5988 | 75467 | 76186 | 75773
12136 | 2021-11-13 | 22:24 | 11.5988 | 75466 | 76197 | 75761
12137 | 2021-11-13 | 22:24 | 11.5989 | 75467 | 76204 | 75753
12138 | 2021-11-13 | 22:24 | 11.5989 | 75468 | 76206 | 75749
12139 | 2021-11-13 | 22:24 | 11.5989 | 75470 | 76205 | 75748
12140 | 2021-11-13 | 22:24 | 11.599 | 75471 | 76202 | 75748
12141 | 2021-11-13 | 22:24 | 11.599 | 75472 | 76200 | 75748
12142 | 2021-11-13 | 22:24 | 11.599 | 75471 | 76199 | 75746
12143 | 2021-11-13 | 22:24 | 11.599 | 75469 | 76201 | 75742
12144 | 2021-11-13 | 22:24 | 11.5991 | 75466 | 76206 | 75737
12145 | 2021-11-13 | 22:24 | 11.5991 | 75462 | 76212 | 75732
12146 | 2021-11-13 | 22:24 | 11.5991 | 75457 | 76218 | 75728
12147 | 2021-11-13 | 22:24 | 11.5992 | 75451 | 76223 | 75725
12148 | 2021-11-13 | 22:24 | 11.5992 | 75445 | 76227 | 75724
12149 | 2021-11-13 | 22:24 | 11.5992 | 75438 | 76229 | 75724
12150 | 2021-11-13 | 22:24 | 11.5992 | 75432 | 76231 | 75724
12151 | 2021-11-13 | 22:24 | 11.5993 | 75426 | 76231 | 75724
12152 | 2021-11-13 | 22:24 | 11.5993 | 75419 | 76230 | 75723
12153 | 2021-11-13 | 22:24 | 11.5993 | 75411 | 76231 | 75721
12154 | 2021-11-13 | 22:24 | 11.5994 | 75402 | 76233 | 75717
12155 | 2021-11-13 | 22:24 | 11.5994 | 75391 | 76237 | 75712
12156 | 2021-11-13 | 22:24 | 11.5994 | 75380 | 76242 | 75707
12157 | 2021-11-13 | 22:24 | 11.5994 | 75367 | 76246 | 75702
12158 | 2021-11-13 | 22:24 | 11.5995 | 75355 | 76248 | 75699
12159 | 2021-11-13 | 22:24 | 11.5995 | 75344 | 76246 | 75698
12160 | 2021-11-13 | 22:24 | 11.5995 | 75334 | 76241 | 75699
12161 | 2021-11-13 | 22:24 | 11.5996 | 75326 | 76232 | 75702
12162 | 2021-11-13 | 22:24 | 11.5996 | 75319 | 76220 | 75705
12163 | 2021-11-13 | 22:24 | 11.5996 | 75312 | 76208 | 75709
12164 | 2021-11-13 | 22:24 | 11.5996 | 75303 | 76197 | 75711
12165 | 2021-11-13 | 22:24 | 11.5997 | 75291 | 76190 | 75711
12166 | 2021-11-13 | 22:24 | 11.5997 | 75276 | 76187 | 75709
12167 | 2021-11-13 | 22:24 | 11.5997 | 75258 | 76190 | 75705
12168 | 2021-11-13 | 22:24 | 11.5998 | 75237 | 76196 | 75700
12169 | 2021-11-13 | 22:24 | 11.5998 | 75216 | 76204 | 75695
12170 | 2021-11-13 | 22:24 | 11.5998 | 75195 | 76211 | 75690
12171 | 2021-11-13 | 22:24 | 11.5998 | 75175 | 76217 | 75686
12172 | 2021-11-13 | 22:24 | 11.5999 | 75157 | 76220 | 75682
12173 | 2021-11-13 | 22:24 | 11.5999 | 75139 | 76221 | 75679
12174 | 2021-11-13 | 22:24 | 11.5999 | 75122 | 76220 | 75677
12175 | 2021-11-13 | 22:24 | 11.6 | 75104 | 76219 | 75675
12176 | 2021-11-13 | 22:24 | 11.6 | 75085 | 76218 | 75672
12177 | 2021-11-13 | 22:24 | 11.6 | 75065 | 76218 | 75670
12178 | 2021-11-13 | 22:24 | 11.6 | 75043 | 76219 | 75667
12179 | 2021-11-13 | 22:24 | 11.6001 | 75019 | 76220 | 75665
12180 | 2021-11-13 | 22:24 | 11.6001 | 74995 | 76222 | 75663
12181 | 2021-11-13 | 22:24 | 11.6001 | 74971 | 76224 | 75661
12182 | 2021-11-13 | 22:24 | 11.6002 | 74947 | 76226 | 75659
12183 | 2021-11-13 | 22:24 | 11.6002 | 74924 | 76228 | 75658
12184 | 2021-11-13 | 22:24 | 11.6002 | 74900 | 76229 | 75657
12185 | 2021-11-13 | 22:24 | 11.6002 | 74876 | 76230 | 75656
12186 | 2021-11-13 | 22:24 | 11.6003 | 74850 | 76233 | 75655
12187 | 2021-11-13 | 22:24 | 11.6003 | 74823 | 76236 | 75654
12188 | 2021-11-13 | 22:24 | 11.6003 | 74792 | 76241 | 75653
12189 | 2021-11-13 | 22:24 | 11.6004 | 74760 | 76248 | 75652
12190 | 2021-11-13 | 22:24 | 11.6004 | 74725 | 76255 | 75651
12191 | 2021-11-13 | 22:24 | 11.6004 | 74689 | 76263 | 75650
12192 | 2021-11-13 | 22:24 | 11.6004 | 74653 | 76269 | 75649
12193 | 2021-11-13 | 22:24 | 11.6005 | 74618 | 76273 | 75649
12194 | 2021-11-13 | 22:24 | 11.6005 | 74583 | 76274 | 75649
12195 | 2021-11-13 | 22:24 | 11.6005 | 74549 | 76272 | 75648
12196 | 2021-11-13 | 22:24 | 11.6006 | 74515 | 76267 | 75648
12197 | 2021-11-13 | 22:24 | 11.6006 | 74481 | 76261 | 75648
12198 | 2021-11-13 | 22:24 | 11.6006 | 74446 | 76254 | 75648
12199 | 2021-11-13 | 22:24 | 11.6006 | 74408 | 76248 | 75648
12200 | 2021-11-13 | 22:24 | 11.6007 | 74368 | 76244 | 75648
12201 | 2021-11-13 | 22:24 | 11.6007 | 74324 | 76241 | 75649
12202 | 2021-11-13 | 22:24 | 11.6007 | 74279 | 76239 | 75649
12203 | 2021-11-13 | 22:24 | 11.6008 | 74233 | 76237 | 75649
12204 | 2021-11-13 | 22:24 | 11.6008 | 74185 | 76235 | 75650
12205 | 2021-11-13 | 22:24 | 11.6008 | 74138 | 76233 | 75650
12206 | 2021-11-13 | 22:24 | 11.6008 | 74090 | 76229 | 75650
12207 | 2021-11-13 | 22:24 | 11.6009 | 74041 | 76224 | 75651
12208 | 2021-11-13 | 22:24 | 11.6009 | 73991 | 76219 | 75651
12209 | 2021-11-13 | 22:24 | 11.6009 | 73940 | 76214 | 75651
12210 | 2021-11-13 | 22:24 | 11.601 | 73887 | 76208 | 75651
12211 | 2021-11-13 | 22:24 | 11.601 | 73831 | 76204 | 75652
12212 | 2021-11-13 | 22:24 | 11.601 | 73773 | 76200 | 75652
12213 | 2021-11-13 | 22:24 | 11.601 | 73714 | 76197 | 75654
12214 | 2021-11-13 | 22:24 | 11.6011 | 73653 | 76194 | 75655
12215 | 2021-11-13 | 22:24 | 11.6011 | 73593 | 76190 | 75656
12216 | 2021-11-13 | 22:24 | 11.6011 | 73533 | 76186 | 75657
12217 | 2021-11-13 | 22:24 | 11.6012 | 73473 | 76181 | 75657
12218 | 2021-11-13 | 22:24 | 11.6012 | 73415 | 76175 | 75657
12219 | 2021-11-13 | 22:24 | 11.6012 | 73356 | 76170 | 75657
12220 | 2021-11-13 | 22:24 | 11.6013 | 73296 | 76164 | 75656
12221 | 2021-11-13 | 22:24 | 11.6013 | 73235 | 76159 | 75655
12222 | 2021-11-13 | 22:24 | 11.6013 | 73172 | 76155 | 75655
12223 | 2021-11-13 | 22:24 | 11.6013 | 73107 | 76152 | 75654
12224 | 2021-11-13 | 22:24 | 11.6014 | 73040 | 76150 | 75654
12225 | 2021-11-13 | 22:24 | 11.6014 | 72972 | 76149 | 75655
12226 | 2021-11-13 | 22:24 | 11.6014 | 72902 | 76149 | 75655
12227 | 2021-11-13 | 22:24 | 11.6015 | 72831 | 76148 | 75655
12228 | 2021-11-13 | 22:24 | 11.6015 | 72761 | 76147 | 75654
12229 | 2021-11-13 | 22:24 | 11.6015 | 72692 | 76145 | 75653
12230 | 2021-11-13 | 22:24 | 11.6015 | 72623 | 76141 | 75651
12231 | 2021-11-13 | 22:24 | 11.6016 | 72554 | 76137 | 75648
12232 | 2021-11-13 | 22:24 | 11.6016 | 72484 | 76132 | 75645
12233 | 2021-11-13 | 22:24 | 11.6016 | 72414 | 76127 | 75643
12234 | 2021-11-13 | 22:24 | 11.6017 | 72343 | 76122 | 75640
12235 | 2021-11-13 | 22:24 | 11.6017 | 72271 | 76117 | 75638
12236 | 2021-11-13 | 22:24 | 11.6017 | 72198 | 76112 | 75635
12237 | 2021-11-13 | 22:24 | 11.6017 | 72124 | 76108 | 75633
12238 | 2021-11-13 | 22:24 | 11.6018 | 72049 | 76104 | 75630
12239 | 2021-11-13 | 22:24 | 11.6018 | 71974 | 76099 | 75628
12240 | 2021-11-13 | 22:24 | 11.6018 | 71899 | 76095 | 75625
12241 | 2021-11-13 | 22:24 | 11.6019 | 71824 | 76090 | 75622
12242 | 2021-11-13 | 22:24 | 11.6019 | 71748 | 76085 | 75618
12243 | 2021-11-13 | 22:24 | 11.6019 | 71671 | 76081 | 75615
12244 | 2021-11-13 | 22:24 | 11.6019 | 71593 | 76076 | 75611
12245 | 2021-11-13 | 22:24 | 11.602 | 71514 | 76072 | 75608
12246 | 2021-11-13 | 22:24 | 11.602 | 71434 | 76068 | 75605
12247 | 2021-11-13 | 22:24 | 11.602 | 71353 | 76064 | 75602
12248 | 2021-11-13 | 22:24 | 11.6021 | 71272 | 76060 | 75598
12249 | 2021-11-13 | 22:24 | 11.6021 | 71192 | 76056 | 75594
12250 | 2021-11-13 | 22:24 | 11.6021 | 71112 | 76051 | 75590
12251 | 2021-11-13 | 22:24 | 11.6021 | 71032 | 76047 | 75585
12252 | 2021-11-13 | 22:24 | 11.6022 | 70953 | 76043 | 75579
12253 | 2021-11-13 | 22:24 | 11.6022 | 70874 | 76039 | 75573
12254 | 2021-11-13 | 22:24 | 11.6022 | 70794 | 76036 | 75567
12255 | 2021-11-13 | 22:24 | 11.6023 | 70714 | 76033 | 75561
12256 | 2021-11-13 | 22:24 | 11.6023 | 70633 | 76031 | 75557
12257 | 2021-11-13 | 22:24 | 11.6023 | 70552 | 76029 | 75553
12258 | 2021-11-13 | 22:24 | 11.6023 | 70470 | 76028 | 75549
12259 | 2021-11-13 | 22:24 | 11.6024 | 70389 | 76028 | 75546
12260 | 2021-11-13 | 22:24 | 11.6024 | 70308 | 76027 | 75543
12261 | 2021-11-13 | 22:24 | 11.6024 | 70228 | 76027 | 75540
12262 | 2021-11-13 | 22:24 | 11.6025 | 70150 | 76026 | 75535
12263 | 2021-11-13 | 22:24 | 11.6025 | 70073 | 76025 | 75528
12264 | 2021-11-13 | 22:24 | 11.6025 | 69997 | 76024 | 75521
12265 | 2021-11-13 | 22:24 | 11.6025 | 69922 | 76023 | 75513
12266 | 2021-11-13 | 22:24 | 11.6026 | 69848 | 76023 | 75505
12267 | 2021-11-13 | 22:24 | 11.6026 | 69773 | 76022 | 75497
12268 | 2021-11-13 | 22:24 | 11.6026 | 69699 | 76021 | 75489
12269 | 2021-11-13 | 22:24 | 11.6027 | 69625 | 76021 | 75481
12270 | 2021-11-13 | 22:24 | 11.6027 | 69550 | 76021 | 75474
12271 | 2021-11-13 | 22:24 | 11.6027 | 69477 | 76020 | 75468
12272 | 2021-11-13 | 22:24 | 11.6027 | 69403 | 76020 | 75462
12273 | 2021-11-13 | 22:24 | 11.6028 | 69331 | 76020 | 75456
12274 | 2021-11-13 | 22:24 | 11.6028 | 69259 | 76020 | 75450
12275 | 2021-11-13 | 22:24 | 11.6028 | 69188 | 76020 | 75444
12276 | 2021-11-13 | 22:24 | 11.6029 | 69118 | 76020 | 75437
12277 | 2021-11-13 | 22:24 | 11.6029 | 69048 | 76020 | 75431
12278 | 2021-11-13 | 22:24 | 11.6029 | 68979 | 76019 | 75426
12279 | 2021-11-13 | 22:24 | 11.6029 | 68911 | 76019 | 75421
12280 | 2021-11-13 | 22:24 | 11.603 | 68842 | 76019 | 75416
12281 | 2021-11-13 | 22:24 | 11.603 | 68774 | 76019 | 75412
12282 | 2021-11-13 | 22:24 | 11.603 | 68706 | 76019 | 75407
12283 | 2021-11-13 | 22:24 | 11.6031 | 68639 | 76019 | 75401
12284 | 2021-11-13 | 22:24 | 11.6031 | 68573 | 76019 | 75395
12285 | 2021-11-13 | 22:24 | 11.6031 | 68508 | 76019 | 75388
12286 | 2021-11-13 | 22:24 | 11.6031 | 68443 | 76019 | 75381
12287 | 2021-11-13 | 22:24 | 11.6032 | 68379 | 76019 | 75374
12288 | 2021-11-13 | 22:24 | 11.6032 | 68316 | 76020 | 75366
12289 | 2021-11-13 | 22:24 | 11.6032 | 68253 | 76020 | 75359
12290 | 2021-11-13 | 22:24 | 11.6033 | 68190 | 76021 | 75352
12291 | 2021-11-13 | 22:24 | 11.6033 | 68128 | 76021 | 75345
12292 | 2021-11-13 | 22:24 | 11.6033 | 68066 | 76022 | 75339
12293 | 2021-11-13 | 22:24 | 11.6033 | 68005 | 76022 | 75334
12294 | 2021-11-13 | 22:24 | 11.6034 | 67944 | 76022 | 75328
12295 | 2021-11-13 | 22:24 | 11.6034 | 67885 | 76023 | 75321
12296 | 2021-11-13 | 22:24 | 11.6034 | 67826 | 76024 | 75314
12297 | 2021-11-13 | 22:24 | 11.6035 | 67769 | 76024 | 75307
12298 | 2021-11-13 | 22:24 | 11.6035 | 67712 | 76025 | 75299
12299 | 2021-11-13 | 22:24 | 11.6035 | 67656 | 76026 | 75291
12300 | 2021-11-13 | 22:24 | 11.6035 | 67601 | 76027 | 75283
12301 | 2021-11-13 | 22:24 | 11.6036 | 67547 | 76028 | 75274
12302 | 2021-11-13 | 22:24 | 11.6036 | 67493 | 76029 | 75265
12303 | 2021-11-13 | 22:24 | 11.6036 | 67440 | 76030 | 75257
12304 | 2021-11-13 | 22:24 | 11.6037 | 67388 | 76031 | 75249
12305 | 2021-11-13 | 22:24 | 11.6037 | 67336 | 76032 | 75241
12306 | 2021-11-13 | 22:24 | 11.6037 | 67286 | 76033 | 75232
12307 | 2021-11-13 | 22:24 | 11.6037 | 67236 | 76034 | 75224
12308 | 2021-11-13 | 22:24 | 11.6038 | 67187 | 76035 | 75215
12309 | 2021-11-13 | 22:24 | 11.6038 | 67140 | 76036 | 75206
12310 | 2021-11-13 | 22:24 | 11.6038 | 67093 | 76037 | 75197
12311 | 2021-11-13 | 22:24 | 11.6039 | 67046 | 76038 | 75189
12312 | 2021-11-13 | 22:24 | 11.6039 | 67000 | 76039 | 75181
12313 | 2021-11-13 | 22:24 | 11.6039 | 66954 | 76041 | 75173
12314 | 2021-11-13 | 22:24 | 11.604 | 66909 | 76042 | 75166
12315 | 2021-11-13 | 22:24 | 11.604 | 66865 | 76043 | 75159
12316 | 2021-11-13 | 22:24 | 11.604 | 66822 | 76045 | 75152
12317 | 2021-11-13 | 22:24 | 11.604 | 66780 | 76047 | 75144
12318 | 2021-11-13 | 22:24 | 11.6041 | 66739 | 76050 | 75136
12319 | 2021-11-13 | 22:24 | 11.6041 | 66699 | 76053 | 75128
12320 | 2021-11-13 | 22:24 | 11.6041 | 66661 | 76056 | 75119
12321 | 2021-11-13 | 22:24 | 11.6042 | 66623 | 76060 | 75110
12322 | 2021-11-13 | 22:24 | 11.6042 | 66587 | 76064 | 75102
12323 | 2021-11-13 | 22:24 | 11.6042 | 66552 | 76068 | 75094
12324 | 2021-11-13 | 22:24 | 11.6042 | 66517 | 76073 | 75086
12325 | 2021-11-13 | 22:24 | 11.6043 | 66484 | 76077 | 75080
12326 | 2021-11-13 | 22:24 | 11.6043 | 66451 | 76081 | 75074
12327 | 2021-11-13 | 22:24 | 11.6043 | 66419 | 76086 | 75069
12328 | 2021-11-13 | 22:24 | 11.6044 | 66388 | 76090 | 75065
12329 | 2021-11-13 | 22:24 | 11.6044 | 66358 | 76095 | 75060
12330 | 2021-11-13 | 22:24 | 11.6044 | 66329 | 76099 | 75056
12331 | 2021-11-13 | 22:24 | 11.6044 | 66302 | 76104 | 75051
12332 | 2021-11-13 | 22:24 | 11.6045 | 66276 | 76110 | 75046
12333 | 2021-11-13 | 22:24 | 11.6045 | 66250 | 76115 | 75041
12334 | 2021-11-13 | 22:24 | 11.6045 | 66226 | 76121 | 75036
12335 | 2021-11-13 | 22:24 | 11.6046 | 66203 | 76127 | 75031
12336 | 2021-11-13 | 22:24 | 11.6046 | 66181 | 76132 | 75026
12337 | 2021-11-13 | 22:24 | 11.6046 | 66161 | 76138 | 75021
12338 | 2021-11-13 | 22:24 | 11.6046 | 66141 | 76144 | 75016
12339 | 2021-11-13 | 22:24 | 11.6047 | 66122 | 76150 | 75012
12340 | 2021-11-13 | 22:24 | 11.6047 | 66104 | 76155 | 75007
12341 | 2021-11-13 | 22:24 | 11.6047 | 66087 | 76161 | 75003
12342 | 2021-11-13 | 22:24 | 11.6048 | 66071 | 76166 | 74998
12343 | 2021-11-13 | 22:24 | 11.6048 | 66056 | 76172 | 74994
12344 | 2021-11-13 | 22:24 | 11.6048 | 66042 | 76177 | 74989
12345 | 2021-11-13 | 22:24 | 11.6048 | 66029 | 76182 | 74986
12346 | 2021-11-13 | 22:24 | 11.6049 | 66016 | 76186 | 74982
12347 | 2021-11-13 | 22:24 | 11.6049 | 66004 | 76191 | 74979
12348 | 2021-11-13 | 22:24 | 11.6049 | 65993 | 76195 | 74977
12349 | 2021-11-13 | 22:24 | 11.605 | 65983 | 76199 | 74974
12350 | 2021-11-13 | 22:24 | 11.605 | 65973 | 76203 | 74971
12351 | 2021-11-13 | 22:24 | 11.605 | 65965 | 76207 | 74968
12352 | 2021-11-13 | 22:24 | 11.605 | 65957 | 76211 | 74964
12353 | 2021-11-13 | 22:24 | 11.6051 | 65950 | 76215 | 74960
12354 | 2021-11-13 | 22:24 | 11.6051 | 65944 | 76220 | 74955
12355 | 2021-11-13 | 22:24 | 11.6051 | 65938 | 76225 | 74949
12356 | 2021-11-13 | 22:24 | 11.6052 | 65933 | 76231 | 74944
12357 | 2021-11-13 | 22:24 | 11.6052 | 65929 | 76236 | 74938
12358 | 2021-11-13 | 22:24 | 11.6052 | 65925 | 76242 | 74933
12359 | 2021-11-13 | 22:24 | 11.6052 | 65922 | 76247 | 74928
12360 | 2021-11-13 | 22:24 | 11.6053 | 65920 | 76252 | 74924
12361 | 2021-11-13 | 22:24 | 11.6053 | 65918 | 76256 | 74920
12362 | 2021-11-13 | 22:24 | 11.6053 | 65916 | 76261 | 74916
12363 | 2021-11-13 | 22:24 | 11.6054 | 65915 | 76266 | 74912
12364 | 2021-11-13 | 22:24 | 11.6054 | 65915 | 76272 | 74908
12365 | 2021-11-13 | 22:24 | 11.6054 | 65915 | 76277 | 74903
12366 | 2021-11-13 | 22:24 | 11.6054 | 65916 | 76284 | 74899
12367 | 2021-11-13 | 22:24 | 11.6055 | 65916 | 76290 | 74895
12368 | 2021-11-13 | 22:24 | 11.6055 | 65918 | 76298 | 74891
12369 | 2021-11-13 | 22:24 | 11.6055 | 65919 | 76306 | 74887
12370 | 2021-11-13 | 22:24 | 11.6056 | 65922 | 76315 | 74882
12371 | 2021-11-13 | 22:24 | 11.6056 | 65924 | 76324 | 74878
12372 | 2021-11-13 | 22:24 | 11.6056 | 65927 | 76333 | 74875
12373 | 2021-11-13 | 22:24 | 11.6056 | 65930 | 76343 | 74871
12374 | 2021-11-13 | 22:24 | 11.6057 | 65934 | 76352 | 74867
12375 | 2021-11-13 | 22:24 | 11.6057 | 65937 | 76362 | 74863
12376 | 2021-11-13 | 22:24 | 11.6057 | 65941 | 76371 | 74859
12377 | 2021-11-13 | 22:24 | 11.6058 | 65945 | 76380 | 74855
12378 | 2021-11-13 | 22:24 | 11.6058 | 65949 | 76389 | 74851
12379 | 2021-11-13 | 22:24 | 11.6058 | 65954 | 76397 | 74847
12380 | 2021-11-13 | 22:24 | 11.6058 | 65958 | 76405 | 74844
12381 | 2021-11-13 | 22:24 | 11.6059 | 65963 | 76412 | 74840
12382 | 2021-11-13 | 22:24 | 11.6059 | 65967 | 76420 | 74837
12383 | 2021-11-13 | 22:24 | 11.6059 | 65972 | 76427 | 74834
12384 | 2021-11-13 | 22:24 | 11.606 | 65977 | 76434 | 74831
12385 | 2021-11-13 | 22:24 | 11.606 | 65982 | 76441 | 74827
12386 | 2021-11-13 | 22:24 | 11.606 | 65987 | 76449 | 74824
12387 | 2021-11-13 | 22:24 | 11.606 | 65992 | 76456 | 74820
12388 | 2021-11-13 | 22:24 | 11.6061 | 65997 | 76463 | 74816
12389 | 2021-11-13 | 22:24 | 11.6061 | 66001 | 76470 | 74812
12390 | 2021-11-13 | 22:24 | 11.6061 | 66006 | 76477 | 74807
12391 | 2021-11-13 | 22:24 | 11.6062 | 66010 | 76484 | 74803
12392 | 2021-11-13 | 22:24 | 11.6062 | 66015 | 76489 | 74799
12393 | 2021-11-13 | 22:24 | 11.6062 | 66019 | 76494 | 74794
12394 | 2021-11-13 | 22:24 | 11.6062 | 66023 | 76498 | 74790
12395 | 2021-11-13 | 22:24 | 11.6063 | 66027 | 76501 | 74786
12396 | 2021-11-13 | 22:24 | 11.6063 | 66030 | 76504 | 74781
12397 | 2021-11-13 | 22:24 | 11.6063 | 66033 | 76505 | 74777
12398 | 2021-11-13 | 22:24 | 11.6064 | 66035 | 76506 | 74773
12399 | 2021-11-13 | 22:24 | 11.6064 | 66038 | 76507 | 74768
12400 | 2021-11-13 | 22:24 | 11.6064 | 66040 | 76507 | 74763
12401 | 2021-11-13 | 22:24 | 11.6064 | 66041 | 76508 | 74758
12402 | 2021-11-13 | 22:24 | 11.6065 | 66043 | 76509 | 74754
12403 | 2021-11-13 | 22:24 | 11.6065 | 66044 | 76510 | 74749
12404 | 2021-11-13 | 22:24 | 11.6065 | 66045 | 76511 | 74744
12405 | 2021-11-13 | 22:24 | 11.6066 | 66046 | 76512 | 74740
12406 | 2021-11-13 | 22:24 | 11.6066 | 66045 | 76513 | 74736
12407 | 2021-11-13 | 22:24 | 11.6066 | 66045 | 76514 | 74731
12408 | 2021-11-13 | 22:24 | 11.6067 | 66043 | 76514 | 74727
12409 | 2021-11-13 | 22:24 | 11.6067 | 66041 | 76515 | 74723
12410 | 2021-11-13 | 22:24 | 11.6067 | 66038 | 76515 | 74718
12411 | 2021-11-13 | 22:24 | 11.6067 | 66035 | 76516 | 74714
12412 | 2021-11-13 | 22:24 | 11.6068 | 66031 | 76516 | 74710
12413 | 2021-11-13 | 22:24 | 11.6068 | 66027 | 76516 | 74706
12414 | 2021-11-13 | 22:24 | 11.6068 | 66023 | 76516 | 74702
12415 | 2021-11-13 | 22:24 | 11.6069 | 66017 | 76515 | 74699
12416 | 2021-11-13 | 22:24 | 11.6069 | 66012 | 76515 | 74695
12417 | 2021-11-13 | 22:24 | 11.6069 | 66005 | 76514 | 74692
12418 | 2021-11-13 | 22:24 | 11.6069 | 65997 | 76513 | 74690
12419 | 2021-11-13 | 22:24 | 11.607 | 65989 | 76512 | 74687
12420 | 2021-11-13 | 22:24 | 11.607 | 65980 | 76510 | 74684
12421 | 2021-11-13 | 22:24 | 11.607 | 65969 | 76509 | 74682
12422 | 2021-11-13 | 22:24 | 11.6071 | 65957 | 76507 | 74680
12423 | 2021-11-13 | 22:24 | 11.6071 | 65945 | 76505 | 74678
12424 | 2021-11-13 | 22:24 | 11.6071 | 65931 | 76504 | 74676
12425 | 2021-11-13 | 22:24 | 11.6071 | 65917 | 76502 | 74674
12426 | 2021-11-13 | 22:24 | 11.6072 | 65901 | 76499 | 74672
12427 | 2021-11-13 | 22:24 | 11.6072 | 65885 | 76497 | 74671
12428 | 2021-11-13 | 22:24 | 11.6072 | 65867 | 76495 | 74669
12429 | 2021-11-13 | 22:24 | 11.6073 | 65849 | 76492 | 74668
12430 | 2021-11-13 | 22:24 | 11.6073 | 65829 | 76489 | 74667
12431 | 2021-11-13 | 22:24 | 11.6073 | 65809 | 76487 | 74666
12432 | 2021-11-13 | 22:24 | 11.6073 | 65788 | 76484 | 74665
12433 | 2021-11-13 | 22:24 | 11.6074 | 65766 | 76481 | 74664
12434 | 2021-11-13 | 22:24 | 11.6074 | 65743 | 76477 | 74664
12435 | 2021-11-13 | 22:24 | 11.6074 | 65719 | 76473 | 74663
12436 | 2021-11-13 | 22:24 | 11.6075 | 65694 | 76469 | 74663
12437 | 2021-11-13 | 22:24 | 11.6075 | 65667 | 76465 | 74663
12438 | 2021-11-13 | 22:24 | 11.6075 | 65638 | 76460 | 74663
12439 | 2021-11-13 | 22:24 | 11.6075 | 65609 | 76454 | 74663
12440 | 2021-11-13 | 22:24 | 11.6076 | 65578 | 76449 | 74664
12441 | 2021-11-13 | 22:24 | 11.6076 | 65545 | 76444 | 74664
12442 | 2021-11-13 | 22:24 | 11.6076 | 65511 | 76439 | 74664
12443 | 2021-11-13 | 22:24 | 11.6077 | 65476 | 76433 | 74664
12444 | 2021-11-13 | 22:24 | 11.6077 | 65439 | 76429 | 74664
12445 | 2021-11-13 | 22:24 | 11.6077 | 65402 | 76424 | 74664
12446 | 2021-11-13 | 22:24 | 11.6077 | 65364 | 76419 | 74665
12447 | 2021-11-13 | 22:24 | 11.6078 | 65325 | 76414 | 74665
12448 | 2021-11-13 | 22:24 | 11.6078 | 65284 | 76409 | 74665
12449 | 2021-11-13 | 22:24 | 11.6078 | 65243 | 76405 | 74665
12450 | 2021-11-13 | 22:24 | 11.6079 | 65200 | 76400 | 74666
12451 | 2021-11-13 | 22:24 | 11.6079 | 65156 | 76395 | 74666
12452 | 2021-11-13 | 22:24 | 11.6079 | 65111 | 76390 | 74666
12453 | 2021-11-13 | 22:24 | 11.6079 | 65064 | 76386 | 74666
12454 | 2021-11-13 | 22:24 | 11.608 | 65016 | 76381 | 74666
12455 | 2021-11-13 | 22:24 | 11.608 | 64966 | 76376 | 74667
12456 | 2021-11-13 | 22:24 | 11.608 | 64915 | 76372 | 74667
12457 | 2021-11-13 | 22:24 | 11.6081 | 64863 | 76367 | 74667
12458 | 2021-11-13 | 22:24 | 11.6081 | 64810 | 76363 | 74666
12459 | 2021-11-13 | 22:24 | 11.6081 | 64756 | 76358 | 74666
12460 | 2021-11-13 | 22:24 | 11.6081 | 64700 | 76354 | 74666
12461 | 2021-11-13 | 22:24 | 11.6082 | 64643 | 76349 | 74666
12462 | 2021-11-13 | 22:24 | 11.6082 | 64586 | 76344 | 74665
12463 | 2021-11-13 | 22:24 | 11.6082 | 64527 | 76338 | 74665
12464 | 2021-11-13 | 22:24 | 11.6083 | 64467 | 76333 | 74664
12465 | 2021-11-13 | 22:24 | 11.6083 | 64406 | 76328 | 74663
12466 | 2021-11-13 | 22:24 | 11.6083 | 64344 | 76322 | 74662
12467 | 2021-11-13 | 22:24 | 11.6083 | 64280 | 76316 | 74661
12468 | 2021-11-13 | 22:24 | 11.6084 | 64216 | 76311 | 74660
12469 | 2021-11-13 | 22:24 | 11.6084 | 64151 | 76305 | 74659
12470 | 2021-11-13 | 22:24 | 11.6084 | 64085 | 76299 | 74658
12471 | 2021-11-13 | 22:24 | 11.6085 | 64018 | 76293 | 74657
12472 | 2021-11-13 | 22:24 | 11.6085 | 63950 | 76287 | 74655
12473 | 2021-11-13 | 22:24 | 11.6085 | 63881 | 76281 | 74654
12474 | 2021-11-13 | 22:24 | 11.6085 | 63811 | 76275 | 74652
12475 | 2021-11-13 | 22:24 | 11.6086 | 63741 | 76269 | 74651
12476 | 2021-11-13 | 22:24 | 11.6086 | 63669 | 76263 | 74649
12477 | 2021-11-13 | 22:24 | 11.6086 | 63596 | 76257 | 74647
12478 | 2021-11-13 | 22:24 | 11.6087 | 63523 | 76250 | 74645
12479 | 2021-11-13 | 22:24 | 11.6087 | 63448 | 76244 | 74643
12480 | 2021-11-13 | 22:24 | 11.6087 | 63372 | 76237 | 74640
12481 | 2021-11-13 | 22:24 | 11.6087 | 63295 | 76230 | 74638
12482 | 2021-11-13 | 22:24 | 11.6088 | 63217 | 76223 | 74635
12483 | 2021-11-13 | 22:24 | 11.6088 | 63138 | 76216 | 74633
12484 | 2021-11-13 | 22:24 | 11.6088 | 63058 | 76209 | 74630
12485 | 2021-11-13 | 22:24 | 11.6089 | 62977 | 76202 | 74627
12486 | 2021-11-13 | 22:24 | 11.6089 | 62895 | 76194 | 74625
12487 | 2021-11-13 | 22:24 | 11.6089 | 62813 | 76187 | 74622
12488 | 2021-11-13 | 22:24 | 11.6089 | 62730 | 76180 | 74619
12489 | 2021-11-13 | 22:24 | 11.609 | 62646 | 76173 | 74617
12490 | 2021-11-13 | 22:24 | 11.609 | 62562 | 76166 | 74614
12491 | 2021-11-13 | 22:24 | 11.609 | 62476 | 76159 | 74611
12492 | 2021-11-13 | 22:24 | 11.6091 | 62390 | 76153 | 74609
12493 | 2021-11-13 | 22:24 | 11.6091 | 62303 | 76146 | 74606
12494 | 2021-11-13 | 22:24 | 11.6091 | 62216 | 76139 | 74603
12495 | 2021-11-13 | 22:24 | 11.6091 | 62128 | 76132 | 74600
12496 | 2021-11-13 | 22:24 | 11.6092 | 62039 | 76125 | 74597
12497 | 2021-11-13 | 22:24 | 11.6092 | 61950 | 76118 | 74594
12498 | 2021-11-13 | 22:24 | 11.6092 | 61860 | 76111 | 74591
12499 | 2021-11-13 | 22:24 | 11.6093 | 61770 | 76104 | 74588
12500 | 2021-11-13 | 22:24 | 11.6093 | 61680 | 76097 | 74585
12501 | 2021-11-13 | 22:24 | 11.6093 | 61589 | 76090 | 74582
12502 | 2021-11-13 | 22:24 | 11.6094 | 61497 | 76083 | 74579
12503 | 2021-11-13 | 22:24 | 11.6094 | 61406 | 76076 | 74576
12504 | 2021-11-13 | 22:24 | 11.6094 | 61314 | 76069 | 74573
12505 | 2021-11-13 | 22:24 | 11.6094 | 61222 | 76062 | 74570
12506 | 2021-11-13 | 22:24 | 11.6095 | 61130 | 76055 | 74567
12507 | 2021-11-13 | 22:24 | 11.6095 | 61038 | 76048 | 74564
12508 | 2021-11-13 | 22:24 | 11.6095 | 60946 | 76042 | 74562
12509 | 2021-11-13 | 22:24 | 11.6096 | 60853 | 76036 | 74559
12510 | 2021-11-13 | 22:24 | 11.6096 | 60761 | 76030 | 74557
12511 | 2021-11-13 | 22:24 | 11.6096 | 60669 | 76024 | 74555
12512 | 2021-11-13 | 22:24 | 11.6096 | 60576 | 76018 | 74553
12513 | 2021-11-13 | 22:24 | 11.6097 | 60484 | 76013 | 74551
12514 | 2021-11-13 | 22:24 | 11.6097 | 60392 | 76008 | 74549
12515 | 2021-11-13 | 22:24 | 11.6097 | 60299 | 76002 | 74548
12516 | 2021-11-13 | 22:24 | 11.6098 | 60207 | 75998 | 74547
12517 | 2021-11-13 | 22:24 | 11.6098 | 60116 | 75993 | 74546
12518 | 2021-11-13 | 22:24 | 11.6098 | 60024 | 75988 | 74545
12519 | 2021-11-13 | 22:24 | 11.6098 | 59933 | 75984 | 74544
12520 | 2021-11-13 | 22:24 | 11.6099 | 59843 | 75980 | 74543
12521 | 2021-11-13 | 22:24 | 11.6099 | 59752 | 75976 | 74542
12522 | 2021-11-13 | 22:24 | 11.6099 | 59662 | 75973 | 74541
12523 | 2021-11-13 | 22:24 | 11.61 | 59572 | 75970 | 74539
12524 | 2021-11-13 | 22:24 | 11.61 | 59483 | 75967 | 74538
12525 | 2021-11-13 | 22:24 | 11.61 | 59394 | 75964 | 74537
12526 | 2021-11-13 | 22:24 | 11.61 | 59305 | 75962 | 74536
12527 | 2021-11-13 | 22:24 | 11.6101 | 59217 | 75960 | 74534
12528 | 2021-11-13 | 22:24 | 11.6101 | 59129 | 75958 | 74533
12529 | 2021-11-13 | 22:24 | 11.6101 | 59042 | 75957 | 74532
12530 | 2021-11-13 | 22:24 | 11.6102 | 58955 | 75955 | 74530
12531 | 2021-11-13 | 22:24 | 11.6102 | 58870 | 75954 | 74529
12532 | 2021-11-13 | 22:24 | 11.6102 | 58785 | 75953 | 74527
12533 | 2021-11-13 | 22:24 | 11.6102 | 58701 | 75953 | 74526
12534 | 2021-11-13 | 22:24 | 11.6103 | 58617 | 75952 | 74524
12535 | 2021-11-13 | 22:24 | 11.6103 | 58534 | 75951 | 74522
12536 | 2021-11-13 | 22:24 | 11.6103 | 58453 | 75951 | 74519
12537 | 2021-11-13 | 22:24 | 11.6104 | 58372 | 75951 | 74515
12538 | 2021-11-13 | 22:24 | 11.6104 | 58291 | 75951 | 74511
12539 | 2021-11-13 | 22:24 | 11.6104 | 58212 | 75951 | 74507
12540 | 2021-11-13 | 22:24 | 11.6104 | 58134 | 75951 | 74503
12541 | 2021-11-13 | 22:24 | 11.6105 | 58056 | 75951 | 74498
12542 | 2021-11-13 | 22:24 | 11.6105 | 57980 | 75951 | 74493
12543 | 2021-11-13 | 22:24 | 11.6105 | 57904 | 75952 | 74488
12544 | 2021-11-13 | 22:24 | 11.6106 | 57829 | 75952 | 74483
12545 | 2021-11-13 | 22:24 | 11.6106 | 57755 | 75952 | 74478
12546 | 2021-11-13 | 22:24 | 11.6106 | 57681 | 75953 | 74472
12547 | 2021-11-13 | 22:24 | 11.6106 | 57609 | 75953 | 74466
12548 | 2021-11-13 | 22:24 | 11.6107 | 57538 | 75954 | 74460
12549 | 2021-11-13 | 22:24 | 11.6107 | 57467 | 75954 | 74453
12550 | 2021-11-13 | 22:24 | 11.6107 | 57397 | 75955 | 74446
12551 | 2021-11-13 | 22:24 | 11.6108 | 57328 | 75955 | 74439
12552 | 2021-11-13 | 22:24 | 11.6108 | 57260 | 75956 | 74432
12553 | 2021-11-13 | 22:24 | 11.6108 | 57193 | 75956 | 74425
12554 | 2021-11-13 | 22:24 | 11.6108 | 57127 | 75957 | 74417
12555 | 2021-11-13 | 22:24 | 11.6109 | 57061 | 75957 | 74410
12556 | 2021-11-13 | 22:24 | 11.6109 | 56997 | 75958 | 74402
12557 | 2021-11-13 | 22:24 | 11.6109 | 56933 | 75958 | 74393
12558 | 2021-11-13 | 22:24 | 11.611 | 56870 | 75959 | 74385
12559 | 2021-11-13 | 22:24 | 11.611 | 56808 | 75959 | 74376
12560 | 2021-11-13 | 22:24 | 11.611 | 56747 | 75960 | 74367
12561 | 2021-11-13 | 22:24 | 11.611 | 56686 | 75961 | 74358
12562 | 2021-11-13 | 22:24 | 11.6111 | 56627 | 75961 | 74348
12563 | 2021-11-13 | 22:24 | 11.6111 | 56568 | 75962 | 74339
12564 | 2021-11-13 | 22:24 | 11.6111 | 56510 | 75963 | 74330
12565 | 2021-11-13 | 22:24 | 11.6112 | 56453 | 75964 | 74321
12566 | 2021-11-13 | 22:24 | 11.6112 | 56397 | 75965 | 74312
12567 | 2021-11-13 | 22:24 | 11.6112 | 56342 | 75966 | 74303
12568 | 2021-11-13 | 22:24 | 11.6112 | 56287 | 75967 | 74293
12569 | 2021-11-13 | 22:24 | 11.6113 | 56234 | 75969 | 74284
12570 | 2021-11-13 | 22:24 | 11.6113 | 56181 | 75970 | 74275
12571 | 2021-11-13 | 22:24 | 11.6113 | 56130 | 75972 | 74266
12572 | 2021-11-13 | 22:24 | 11.6114 | 56080 | 75973 | 74258
12573 | 2021-11-13 | 22:24 | 11.6114 | 56031 | 75975 | 74249
12574 | 2021-11-13 | 22:24 | 11.6114 | 55983 | 75977 | 74241
12575 | 2021-11-13 | 22:24 | 11.6114 | 55936 | 75979 | 74233
12576 | 2021-11-13 | 22:24 | 11.6115 | 55890 | 75981 | 74225
12577 | 2021-11-13 | 22:24 | 11.6115 | 55845 | 75983 | 74218
12578 | 2021-11-13 | 22:24 | 11.6115 | 55802 | 75986 | 74211
12579 | 2021-11-13 | 22:24 | 11.6116 | 55762 | 75990 | 74200
12580 | 2021-11-13 | 22:24 | 11.6116 | 55727 | 75997 | 74183
12581 | 2021-11-13 | 22:24 | 11.6116 | 55698 | 76007 | 74157
12582 | 2021-11-13 | 22:24 | 11.6116 | 55674 | 76019 | 74126
12583 | 2021-11-13 | 22:24 | 11.6117 | 55651 | 76033 | 74092
12584 | 2021-11-13 | 22:24 | 11.6117 | 55630 | 76048 | 74058
12585 | 2021-11-13 | 22:24 | 11.6117 | 55608 | 76061 | 74028
12586 | 2021-11-13 | 22:24 | 11.6118 | 55583 | 76073 | 74006
12587 | 2021-11-13 | 22:24 | 11.6118 | 55555 | 76082 | 73990
12588 | 2021-11-13 | 22:24 | 11.6118 | 55525 | 76088 | 73982
12589 | 2021-11-13 | 22:24 | 11.6118 | 55493 | 76093 | 73979
12590 | 2021-11-13 | 22:24 | 11.6119 | 55464 | 76097 | 73978
12591 | 2021-11-13 | 22:24 | 11.6119 | 55440 | 76105 | 73972
12592 | 2021-11-13 | 22:24 | 11.6119 | 55421 | 76116 | 73960
12593 | 2021-11-13 | 22:24 | 11.612 | 55406 | 76131 | 73945
12594 | 2021-11-13 | 22:24 | 11.612 | 55394 | 76148 | 73925
12595 | 2021-11-13 | 22:24 | 11.612 | 55384 | 76168 | 73903
12596 | 2021-11-13 | 22:24 | 11.612 | 55375 | 76189 | 73881
12597 | 2021-11-13 | 22:24 | 11.6121 | 55366 | 76209 | 73860
12598 | 2021-11-13 | 22:24 | 11.6121 | 55356 | 76226 | 73845
12599 | 2021-11-13 | 22:24 | 11.6121 | 55344 | 76240 | 73837
12600 | 2021-11-13 | 22:24 | 11.6122 | 55330 | 76249 | 73836
12601 | 2021-11-13 | 22:24 | 11.6122 | 55317 | 76255 | 73839
12602 | 2021-11-13 | 22:24 | 11.6122 | 55306 | 76260 | 73842
12603 | 2021-11-13 | 22:24 | 11.6123 | 55298 | 76264 | 73843
12604 | 2021-11-13 | 22:24 | 11.6123 | 55292 | 76270 | 73842
12605 | 2021-11-13 | 22:24 | 11.6123 | 55288 | 76277 | 73838
12606 | 2021-11-13 | 22:24 | 11.6123 | 55286 | 76285 | 73830
12607 | 2021-11-13 | 22:24 | 11.6124 | 55285 | 76293 | 73820
12608 | 2021-11-13 | 22:24 | 11.6124 | 55284 | 76299 | 73810
12609 | 2021-11-13 | 22:24 | 11.6124 | 55282 | 76300 | 73804
12610 | 2021-11-13 | 22:24 | 11.6125 | 55280 | 76293 | 73806
12611 | 2021-11-13 | 22:24 | 11.6125 | 55278 | 76279 | 73816
12612 | 2021-11-13 | 22:24 | 11.6125 | 55276 | 76261 | 73829
12613 | 2021-11-13 | 22:24 | 11.6125 | 55274 | 76240 | 73843
12614 | 2021-11-13 | 22:24 | 11.6126 | 55274 | 76222 | 73855
12615 | 2021-11-13 | 22:24 | 11.6126 | 55274 | 76207 | 73862
12616 | 2021-11-13 | 22:24 | 11.6126 | 55274 | 76197 | 73864
12617 | 2021-11-13 | 22:24 | 11.6127 | 55273 | 76191 | 73861
12618 | 2021-11-13 | 22:24 | 11.6127 | 55272 | 76186 | 73856
12619 | 2021-11-13 | 22:24 | 11.6127 | 55271 | 76181 | 73851
12620 | 2021-11-13 | 22:24 | 11.6127 | 55271 | 76172 | 73851
12621 | 2021-11-13 | 22:24 | 11.6128 | 55271 | 76159 | 73856
12622 | 2021-11-13 | 22:24 | 11.6128 | 55271 | 76140 | 73866
12623 | 2021-11-13 | 22:24 | 11.6128 | 55271 | 76119 | 73880
12624 | 2021-11-13 | 22:24 | 11.6129 | 55271 | 76097 | 73894
12625 | 2021-11-13 | 22:24 | 11.6129 | 55271 | 76077 | 73907
12626 | 2021-11-13 | 22:24 | 11.6129 | 55271 | 76060 | 73918
12627 | 2021-11-13 | 22:24 | 11.6129 | 55271 | 76049 | 73927
12628 | 2021-11-13 | 22:24 | 11.613 | 55269 | 76042 | 73932
12629 | 2021-11-13 | 22:24 | 11.613 | 55268 | 76039 | 73936
12630 | 2021-11-13 | 22:24 | 11.613 | 55266 | 76037 | 73941
12631 | 2021-11-13 | 22:24 | 11.6131 | 55265 | 76036 | 73947
12632 | 2021-11-13 | 22:24 | 11.6131 | 55264 | 76033 | 73957
12633 | 2021-11-13 | 22:24 | 11.6131 | 55264 | 76029 | 73970
12634 | 2021-11-13 | 22:24 | 11.6131 | 55263 | 76023 | 73985
12635 | 2021-11-13 | 22:24 | 11.6132 | 55264 | 76018 | 74001
12636 | 2021-11-13 | 22:24 | 11.6132 | 55264 | 76014 | 74016
12637 | 2021-11-13 | 22:24 | 11.6132 | 55264 | 76015 | 74026
12638 | 2021-11-13 | 22:24 | 11.6133 | 55264 | 76021 | 74032
12639 | 2021-11-13 | 22:24 | 11.6133 | 55264 | 76031 | 74034
12640 | 2021-11-13 | 22:24 | 11.6133 | 55263 | 76045 | 74032
12641 | 2021-11-13 | 22:24 | 11.6133 | 55262 | 76061 | 74029
12642 | 2021-11-13 | 22:24 | 11.6134 | 55262 | 76075 | 74027
12643 | 2021-11-13 | 22:24 | 11.6134 | 55264 | 76085 | 74029
12644 | 2021-11-13 | 22:24 | 11.6134 | 55267 | 76090 | 74036
12645 | 2021-11-13 | 22:24 | 11.6135 | 55272 | 76090 | 74047
12646 | 2021-11-13 | 22:24 | 11.6135 | 55277 | 76085 | 74059
12647 | 2021-11-13 | 22:24 | 11.6135 | 55283 | 76080 | 74072
12648 | 2021-11-13 | 22:24 | 11.6135 | 55289 | 76078 | 74081
12649 | 2021-11-13 | 22:24 | 11.6136 | 55294 | 76080 | 74087
12650 | 2021-11-13 | 22:24 | 11.6136 | 55297 | 76085 | 74088
12651 | 2021-11-13 | 22:24 | 11.6136 | 55300 | 76094 | 74086
12652 | 2021-11-13 | 22:24 | 11.6137 | 55302 | 76103 | 74082
12653 | 2021-11-13 | 22:24 | 11.6137 | 55306 | 76111 | 74079
12654 | 2021-11-13 | 22:24 | 11.6137 | 55310 | 76117 | 74078
12655 | 2021-11-13 | 22:24 | 11.6137 | 55317 | 76120 | 74079
12656 | 2021-11-13 | 22:24 | 11.6138 | 55324 | 76120 | 74080
12657 | 2021-11-13 | 22:24 | 11.6138 | 55333 | 76119 | 74081
12658 | 2021-11-13 | 22:24 | 11.6138 | 55343 | 76117 | 74082
12659 | 2021-11-13 | 22:24 | 11.6139 | 55354 | 76115 | 74080
12660 | 2021-11-13 | 22:24 | 11.6139 | 55364 | 76115 | 74078
12661 | 2021-11-13 | 22:24 | 11.6139 | 55374 | 76115 | 74074
12662 | 2021-11-13 | 22:24 | 11.6139 | 55383 | 76117 | 74070
12663 | 2021-11-13 | 22:24 | 11.614 | 55391 | 76118 | 74066
12664 | 2021-11-13 | 22:24 | 11.614 | 55400 | 76119 | 74063
12665 | 2021-11-13 | 22:24 | 11.614 | 55409 | 76119 | 74061
12666 | 2021-11-13 | 22:24 | 11.6141 | 55419 | 76117 | 74061
12667 | 2021-11-13 | 22:24 | 11.6141 | 55430 | 76113 | 74062
12668 | 2021-11-13 | 22:24 | 11.6141 | 55443 | 76107 | 74063
12669 | 2021-11-13 | 22:24 | 11.6141 | 55456 | 76103 | 74064
12670 | 2021-11-13 | 22:24 | 11.6142 | 55467 | 76100 | 74063
12671 | 2021-11-13 | 22:24 | 11.6142 | 55477 | 76100 | 74060
12672 | 2021-11-13 | 22:24 | 11.6142 | 55483 | 76104 | 74055
12673 | 2021-11-13 | 22:24 | 11.6143 | 55486 | 76111 | 74048
12674 | 2021-11-13 | 22:24 | 11.6143 | 55487 | 76121 | 74040
12675 | 2021-11-13 | 22:24 | 11.6143 | 55487 | 76132 | 74033
12676 | 2021-11-13 | 22:24 | 11.6143 | 55487 | 76140 | 74028
12677 | 2021-11-13 | 22:24 | 11.6144 | 55491 | 76145 | 74025
12678 | 2021-11-13 | 22:24 | 11.6144 | 55498 | 76144 | 74024
12679 | 2021-11-13 | 22:24 | 11.6144 | 55507 | 76138 | 74025
12680 | 2021-11-13 | 22:24 | 11.6145 | 55518 | 76129 | 74027
12681 | 2021-11-13 | 22:24 | 11.6145 | 55529 | 76118 | 74030
12682 | 2021-11-13 | 22:24 | 11.6145 | 55539 | 76106 | 74033
12683 | 2021-11-13 | 22:24 | 11.6145 | 55546 | 76097 | 74035
12684 | 2021-11-13 | 22:24 | 11.6146 | 55550 | 76090 | 74036
12685 | 2021-11-13 | 22:24 | 11.6146 | 55552 | 76085 | 74037
12686 | 2021-11-13 | 22:24 | 11.6146 | 55553 | 76082 | 74037
12687 | 2021-11-13 | 22:24 | 11.6147 | 55553 | 76080 | 74038
12688 | 2021-11-13 | 22:24 | 11.6147 | 55554 | 76078 | 74039
12689 | 2021-11-13 | 22:24 | 11.6147 | 55556 | 76074 | 74040
12690 | 2021-11-13 | 22:24 | 11.6147 | 55558 | 76070 | 74041
12691 | 2021-11-13 | 22:24 | 11.6148 | 55561 | 76064 | 74043
12692 | 2021-11-13 | 22:24 | 11.6148 | 55564 | 76058 | 74044
12693 | 2021-11-13 | 22:24 | 11.6148 | 55565 | 76051 | 74046
12694 | 2021-11-13 | 22:24 | 11.6149 | 55564 | 76044 | 74047
12695 | 2021-11-13 | 22:24 | 11.6149 | 55560 | 76036 | 74048
12696 | 2021-11-13 | 22:24 | 11.6149 | 55556 | 76030 | 74049
12697 | 2021-11-13 | 22:24 | 11.615 | 55550 | 76023 | 74049
12698 | 2021-11-13 | 22:24 | 11.615 | 55546 | 76015 | 74050
12699 | 2021-11-13 | 22:24 | 11.615 | 55543 | 76006 | 74051
12700 | 2021-11-13 | 22:24 | 11.615 | 55543 | 75996 | 74052
12701 | 2021-11-13 | 22:24 | 11.6151 | 55544 | 75984 | 74053
12702 | 2021-11-13 | 22:24 | 11.6151 | 55547 | 75972 | 74054
12703 | 2021-11-13 | 22:24 | 11.6151 | 55550 | 75960 | 74055
12704 | 2021-11-13 | 22:24 | 11.6152 | 55552 | 75950 | 74056
12705 | 2021-11-13 | 22:24 | 11.6152 | 55552 | 75943 | 74056
12706 | 2021-11-13 | 22:24 | 11.6152 | 55550 | 75939 | 74057
12707 | 2021-11-13 | 22:24 | 11.6152 | 55545 | 75938 | 74057
12708 | 2021-11-13 | 22:24 | 11.6153 | 55538 | 75940 | 74058
12709 | 2021-11-13 | 22:24 | 11.6153 | 55531 | 75945 | 74058
12710 | 2021-11-13 | 22:24 | 11.6153 | 55524 | 75949 | 74058
12711 | 2021-11-13 | 22:24 | 11.6154 | 55519 | 75954 | 74058
12712 | 2021-11-13 | 22:24 | 11.6154 | 55516 | 75957 | 74058
12713 | 2021-11-13 | 22:24 | 11.6154 | 55515 | 75959 | 74058
12714 | 2021-11-13 | 22:24 | 11.6154 | 55516 | 75960 | 74057
12715 | 2021-11-13 | 22:24 | 11.6155 | 55517 | 75961 | 74057
12716 | 2021-11-13 | 22:24 | 11.6155 | 55518 | 75963 | 74056
12717 | 2021-11-13 | 22:24 | 11.6155 | 55518 | 75965 | 74055
12718 | 2021-11-13 | 22:24 | 11.6156 | 55517 | 75969 | 74055
12719 | 2021-11-13 | 22:24 | 11.6156 | 55516 | 75974 | 74054
12720 | 2021-11-13 | 22:24 | 11.6156 | 55515 | 75980 | 74053
12721 | 2021-11-13 | 22:24 | 11.6156 | 55515 | 75986 | 74052
12722 | 2021-11-13 | 22:24 | 11.6157 | 55516 | 75991 | 74051
12723 | 2021-11-13 | 22:24 | 11.6157 | 55519 | 75996 | 74049
12724 | 2021-11-13 | 22:24 | 11.6157 | 55523 | 76001 | 74047
12725 | 2021-11-13 | 22:24 | 11.6158 | 55528 | 76004 | 74045
12726 | 2021-11-13 | 22:24 | 11.6158 | 55533 | 76007 | 74042
12727 | 2021-11-13 | 22:24 | 11.6158 | 55538 | 76011 | 74039
12728 | 2021-11-13 | 22:24 | 11.6158 | 55541 | 76015 | 74037
12729 | 2021-11-13 | 22:24 | 11.6159 | 55542 | 76020 | 74035
12730 | 2021-11-13 | 22:24 | 11.6159 | 55542 | 76026 | 74033
12731 | 2021-11-13 | 22:24 | 11.6159 | 55540 | 76031 | 74032
12732 | 2021-11-13 | 22:24 | 11.616 | 55539 | 76037 | 74031
12733 | 2021-11-13 | 22:24 | 11.616 | 55538 | 76041 | 74030
12734 | 2021-11-13 | 22:24 | 11.616 | 55538 | 76044 | 74029
12735 | 2021-11-13 | 22:24 | 11.616 | 55539 | 76045 | 74027
12736 | 2021-11-13 | 22:24 | 11.6161 | 55542 | 76045 | 74025
12737 | 2021-11-13 | 22:24 | 11.6161 | 55545 | 76044 | 74022
12738 | 2021-11-13 | 22:24 | 11.6161 | 55549 | 76042 | 74020
12739 | 2021-11-13 | 22:24 | 11.6162 | 55552 | 76040 | 74018
12740 | 2021-11-13 | 22:24 | 11.6162 | 55555 | 76039 | 74016
12741 | 2021-11-13 | 22:24 | 11.6162 | 55555 | 76038 | 74016
12742 | 2021-11-13 | 22:24 | 11.6162 | 55554 | 76038 | 74016
12743 | 2021-11-13 | 22:24 | 11.6163 | 55552 | 76038 | 74016
12744 | 2021-11-13 | 22:24 | 11.6163 | 55549 | 76039 | 74017
12745 | 2021-11-13 | 22:24 | 11.6163 | 55547 | 76041 | 74018
12746 | 2021-11-13 | 22:24 | 11.6164 | 55546 | 76041 | 74019
12747 | 2021-11-13 | 22:24 | 11.6164 | 55545 | 76042 | 74019
12748 | 2021-11-13 | 22:24 | 11.6164 | 55546 | 76041 | 74020
12749 | 2021-11-13 | 22:24 | 11.6164 | 55546 | 76041 | 74020
12750 | 2021-11-13 | 22:24 | 11.6165 | 55547 | 76040 | 74021
12751 | 2021-11-13 | 22:24 | 11.6165 | 55548 | 76040 | 74022
12752 | 2021-11-13 | 22:24 | 11.6165 | 55548 | 76039 | 74022
12753 | 2021-11-13 | 22:24 | 11.6166 | 55548 | 76038 | 74024
12754 | 2021-11-13 | 22:24 | 11.6166 | 55547 | 76037 | 74025
12755 | 2021-11-13 | 22:24 | 11.6166 | 55547 | 76037 | 74026
12756 | 2021-11-13 | 22:24 | 11.6166 | 55549 | 76036 | 74028
12757 | 2021-11-13 | 22:24 | 11.6167 | 55551 | 76035 | 74029
12758 | 2021-11-13 | 22:24 | 11.6167 | 55555 | 76033 | 74030
12759 | 2021-11-13 | 22:24 | 11.6167 | 55559 | 76032 | 74031
12760 | 2021-11-13 | 22:24 | 11.6168 | 55564 | 76030 | 74032
12761 | 2021-11-13 | 22:24 | 11.6168 | 55568 | 76029 | 74033
12762 | 2021-11-13 | 22:24 | 11.6168 | 55571 | 76028 | 74035
12763 | 2021-11-13 | 22:24 | 11.6168 | 55573 | 76027 | 74038
12764 | 2021-11-13 | 22:24 | 11.6169 | 55575 | 76027 | 74042
12765 | 2021-11-13 | 22:24 | 11.6169 | 55577 | 76026 | 74045
12766 | 2021-11-13 | 22:24 | 11.6169 | 55579 | 76025 | 74047
12767 | 2021-11-13 | 22:24 | 11.617 | 55582 | 76023 | 74050
12768 | 2021-11-13 | 22:24 | 11.617 | 55586 | 76021 | 74051
12769 | 2021-11-13 | 22:24 | 11.617 | 55591 | 76019 | 74051
12770 | 2021-11-13 | 22:24 | 11.617 | 55596 | 76016 | 74051
12771 | 2021-11-13 | 22:24 | 11.6171 | 55601 | 76013 | 74050
12772 | 2021-11-13 | 22:24 | 11.6171 | 55606 | 76010 | 74049
12773 | 2021-11-13 | 22:24 | 11.6171 | 55610 | 76008 | 74048
12774 | 2021-11-13 | 22:24 | 11.6172 | 55612 | 76006 | 74048
12775 | 2021-11-13 | 22:24 | 11.6172 | 55613 | 76004 | 74049
12776 | 2021-11-13 | 22:24 | 11.6172 | 55613 | 76003 | 74050
12777 | 2021-11-13 | 22:24 | 11.6172 | 55612 | 76002 | 74052
12778 | 2021-11-13 | 22:24 | 11.6173 | 55611 | 76001 | 74053
12779 | 2021-11-13 | 22:24 | 11.6173 | 55610 | 76000 | 74055
12780 | 2021-11-13 | 22:24 | 11.6173 | 55610 | 75999 | 74056
12781 | 2021-11-13 | 22:24 | 11.6174 | 55610 | 75999 | 74055
12782 | 2021-11-13 | 22:24 | 11.6174 | 55610 | 75998 | 74054
12783 | 2021-11-13 | 22:24 | 11.6174 | 55610 | 75997 | 74052
12784 | 2021-11-13 | 22:24 | 11.6174 | 55611 | 75996 | 74049
12785 | 2021-11-13 | 22:24 | 11.6175 | 55610 | 75996 | 74045
12786 | 2021-11-13 | 22:24 | 11.6175 | 55610 | 75995 | 74042
12787 | 2021-11-13 | 22:24 | 11.6175 | 55609 | 75995 | 74038
12788 | 2021-11-13 | 22:24 | 11.6176 | 55608 | 75995 | 74034
12789 | 2021-11-13 | 22:24 | 11.6176 | 55607 | 75995 | 74029
12790 | 2021-11-13 | 22:24 | 11.6176 | 55607 | 75995 | 74024
12791 | 2021-11-13 | 22:24 | 11.6177 | 55607 | 75995 | 74018
12792 | 2021-11-13 | 22:24 | 11.6177 | 55608 | 75995 | 74011
12793 | 2021-11-13 | 22:24 | 11.6177 | 55609 | 75996 | 74004
12794 | 2021-11-13 | 22:24 | 11.6177 | 55610 | 75996 | 73997
12795 | 2021-11-13 | 22:24 | 11.6178 | 55611 | 75996 | 73990
12796 | 2021-11-13 | 22:24 | 11.6178 | 55611 | 75996 | 73983
12797 | 2021-11-13 | 22:24 | 11.6178 | 55611 | 75996 | 73977
12798 | 2021-11-13 | 22:24 | 11.6179 | 55610 | 75995 | 73971
12799 | 2021-11-13 | 22:24 | 11.6179 | 55610 | 75995 | 73966
12800 | 2021-11-13 | 22:24 | 11.6179 | 55610 | 75995 | 73961
12801 | 2021-11-13 | 22:24 | 11.6179 | 55611 | 75994 | 73955
12802 | 2021-11-13 | 22:24 | 11.618 | 55611 | 75994 | 73949
12803 | 2021-11-13 | 22:24 | 11.618 | 55612 | 75993 | 73942
12804 | 2021-11-13 | 22:24 | 11.618 | 55614 | 75992 | 73934
12805 | 2021-11-13 | 22:24 | 11.6181 | 55616 | 75992 | 73926
12806 | 2021-11-13 | 22:24 | 11.6181 | 55618 | 75991 | 73918
12807 | 2021-11-13 | 22:24 | 11.6181 | 55619 | 75991 | 73911
12808 | 2021-11-13 | 22:24 | 11.6181 | 55620 | 75990 | 73905
12809 | 2021-11-13 | 22:24 | 11.6182 | 55621 | 75989 | 73899
12810 | 2021-11-13 | 22:24 | 11.6182 | 55622 | 75988 | 73894
12811 | 2021-11-13 | 22:24 | 11.6182 | 55623 | 75987 | 73889
12812 | 2021-11-13 | 22:24 | 11.6183 | 55623 | 75986 | 73884
12813 | 2021-11-13 | 22:24 | 11.6183 | 55624 | 75985 | 73880
12814 | 2021-11-13 | 22:24 | 11.6183 | 55625 | 75984 | 73876
12815 | 2021-11-13 | 22:24 | 11.6183 | 55626 | 75983 | 73871
12816 | 2021-11-13 | 22:24 | 11.6184 | 55627 | 75982 | 73866
12817 | 2021-11-13 | 22:24 | 11.6184 | 55629 | 75982 | 73862
12818 | 2021-11-13 | 22:24 | 11.6184 | 55630 | 75981 | 73858
12819 | 2021-11-13 | 22:24 | 11.6185 | 55631 | 75980 | 73855
12820 | 2021-11-13 | 22:24 | 11.6185 | 55632 | 75980 | 73852
12821 | 2021-11-13 | 22:24 | 11.6185 | 55633 | 75979 | 73849
12822 | 2021-11-13 | 22:24 | 11.6185 | 55634 | 75979 | 73847
12823 | 2021-11-13 | 22:24 | 11.6186 | 55635 | 75979 | 73844
12824 | 2021-11-13 | 22:24 | 11.6186 | 55636 | 75979 | 73841
12825 | 2021-11-13 | 22:24 | 11.6186 | 55638 | 75979 | 73838
12826 | 2021-11-13 | 22:24 | 11.6187 | 55641 | 75979 | 73834
12827 | 2021-11-13 | 22:24 | 11.6187 | 55643 | 75979 | 73831
12828 | 2021-11-13 | 22:24 | 11.6187 | 55645 | 75980 | 73828
12829 | 2021-11-13 | 22:24 | 11.6187 | 55647 | 75980 | 73825
12830 | 2021-11-13 | 22:24 | 11.6188 | 55649 | 75979 | 73824
12831 | 2021-11-13 | 22:24 | 11.6188 | 55651 | 75979 | 73824
12832 | 2021-11-13 | 22:24 | 11.6188 | 55652 | 75978 | 73825
12833 | 2021-11-13 | 22:24 | 11.6189 | 55653 | 75977 | 73827
12834 | 2021-11-13 | 22:24 | 11.6189 | 55653 | 75976 | 73828
12835 | 2021-11-13 | 22:24 | 11.6189 | 55654 | 75975 | 73830
12836 | 2021-11-13 | 22:24 | 11.6189 | 55655 | 75975 | 73831
12837 | 2021-11-13 | 22:24 | 11.619 | 55656 | 75975 | 73832
12838 | 2021-11-13 | 22:24 | 11.619 | 55657 | 75975 | 73833
12839 | 2021-11-13 | 22:24 | 11.619 | 55658 | 75976 | 73834
12840 | 2021-11-13 | 22:24 | 11.6191 | 55659 | 75978 | 73835
12841 | 2021-11-13 | 22:24 | 11.6191 | 55660 | 75979 | 73837
12842 | 2021-11-13 | 22:24 | 11.6191 | 55660 | 75981 | 73839
12843 | 2021-11-13 | 22:24 | 11.6191 | 55661 | 75982 | 73841
12844 | 2021-11-13 | 22:24 | 11.6192 | 55661 | 75984 | 73845
12845 | 2021-11-13 | 22:24 | 11.6192 | 55661 | 75985 | 73849
12846 | 2021-11-13 | 22:24 | 11.6192 | 55661 | 75987 | 73854
12847 | 2021-11-13 | 22:24 | 11.6193 | 55661 | 75989 | 73859
12848 | 2021-11-13 | 22:24 | 11.6193 | 55661 | 75991 | 73865
12849 | 2021-11-13 | 22:24 | 11.6193 | 55661 | 75993 | 73870
12850 | 2021-11-13 | 22:24 | 11.6193 | 55661 | 75996 | 73876
12851 | 2021-11-13 | 22:24 | 11.6194 | 55661 | 75999 | 73882
12852 | 2021-11-13 | 22:24 | 11.6194 | 55661 | 76003 | 73888
12853 | 2021-11-13 | 22:24 | 11.6194 | 55660 | 76007 | 73895
12854 | 2021-11-13 | 22:24 | 11.6195 | 55660 | 76011 | 73902
12855 | 2021-11-13 | 22:24 | 11.6195 | 55660 | 76016 | 73910
12856 | 2021-11-13 | 22:24 | 11.6195 | 55660 | 76022 | 73918
12857 | 2021-11-13 | 22:24 | 11.6195 | 55660 | 76028 | 73926
12858 | 2021-11-13 | 22:24 | 11.6196 | 55661 | 76035 | 73934
12859 | 2021-11-13 | 22:24 | 11.6196 | 55661 | 76042 | 73942
12860 | 2021-11-13 | 22:24 | 11.6196 | 55661 | 76050 | 73950
12861 | 2021-11-13 | 22:24 | 11.6197 | 55662 | 76058 | 73959
12862 | 2021-11-13 | 22:24 | 11.6197 | 55662 | 76067 | 73967
12863 | 2021-11-13 | 22:24 | 11.6197 | 55662 | 76075 | 73976
12864 | 2021-11-13 | 22:24 | 11.6197 | 55663 | 76083 | 73986
12865 | 2021-11-13 | 22:24 | 11.6198 | 55663 | 76090 | 73997
12866 | 2021-11-13 | 22:24 | 11.6198 | 55663 | 76098 | 74009
12867 | 2021-11-13 | 22:24 | 11.6198 | 55663 | 76105 | 74021
12868 | 2021-11-13 | 22:24 | 11.6199 | 55663 | 76112 | 74033
12869 | 2021-11-13 | 22:24 | 11.6199 | 55663 | 76119 | 74045
12870 | 2021-11-13 | 22:24 | 11.6199 | 55663 | 76126 | 74057
12871 | 2021-11-13 | 22:24 | 11.6199 | 55663 | 76133 | 74069
12872 | 2021-11-13 | 22:24 | 11.62 | 55663 | 76141 | 74081
12873 | 2021-11-13 | 22:24 | 11.62 | 55663 | 76149 | 74092
12874 | 2021-11-13 | 22:24 | 11.62 | 55663 | 76156 | 74104
12875 | 2021-11-13 | 22:24 | 11.6201 | 55663 | 76164 | 74115
12876 | 2021-11-13 | 22:24 | 11.6201 | 55662 | 76171 | 74126
12877 | 2021-11-13 | 22:24 | 11.6201 | 55662 | 76178 | 74138
12878 | 2021-11-13 | 22:24 | 11.6201 | 55661 | 76184 | 74149
12879 | 2021-11-13 | 22:24 | 11.6202 | 55661 | 76189 | 74161
12880 | 2021-11-13 | 22:24 | 11.6202 | 55660 | 76194 | 74172
12881 | 2021-11-13 | 22:24 | 11.6202 | 55659 | 76199 | 74183
12882 | 2021-11-13 | 22:24 | 11.6203 | 55658 | 76204 | 74194
12883 | 2021-11-13 | 22:24 | 11.6203 | 55657 | 76208 | 74205
12884 | 2021-11-13 | 22:24 | 11.6203 | 55656 | 76211 | 74215
12885 | 2021-11-13 | 22:24 | 11.6204 | 55655 | 76215 | 74225
12886 | 2021-11-13 | 22:24 | 11.6204 | 55654 | 76218 | 74235
12887 | 2021-11-13 | 22:24 | 11.6204 | 55653 | 76221 | 74245
12888 | 2021-11-13 | 22:24 | 11.6204 | 55651 | 76224 | 74255
12889 | 2021-11-13 | 22:24 | 11.6205 | 55650 | 76227 | 74264
12890 | 2021-11-13 | 22:24 | 11.6205 | 55649 | 76230 | 74273
12891 | 2021-11-13 | 22:24 | 11.6205 | 55647 | 76234 | 74281
12892 | 2021-11-13 | 22:24 | 11.6206 | 55646 | 76237 | 74289
12893 | 2021-11-13 | 22:24 | 11.6206 | 55644 | 76241 | 74296
12894 | 2021-11-13 | 22:24 | 11.6206 | 55643 | 76245 | 74303
12895 | 2021-11-13 | 22:24 | 11.6206 | 55641 | 76250 | 74309
12896 | 2021-11-13 | 22:24 | 11.6207 | 55639 | 76254 | 74316
12897 | 2021-11-13 | 22:24 | 11.6207 | 55637 | 76258 | 74322
12898 | 2021-11-13 | 22:24 | 11.6207 | 55635 | 76262 | 74328
12899 | 2021-11-13 | 22:24 | 11.6208 | 55634 | 76266 | 74334
12900 | 2021-11-13 | 22:24 | 11.6208 | 55632 | 76270 | 74340
12901 | 2021-11-13 | 22:24 | 11.6208 | 55631 | 76274 | 74346
12902 | 2021-11-13 | 22:24 | 11.6208 | 55629 | 76277 | 74352
12903 | 2021-11-13 | 22:24 | 11.6209 | 55628 | 76281 | 74358
12904 | 2021-11-13 | 22:24 | 11.6209 | 55626 | 76285 | 74363
12905 | 2021-11-13 | 22:24 | 11.6209 | 55625 | 76289 | 74368
12906 | 2021-11-13 | 22:24 | 11.621 | 55623 | 76293 | 74373
12907 | 2021-11-13 | 22:24 | 11.621 | 55621 | 76297 | 74378
12908 | 2021-11-13 | 22:24 | 11.621 | 55620 | 76301 | 74383
12909 | 2021-11-13 | 22:24 | 11.621 | 55618 | 76306 | 74387
12910 | 2021-11-13 | 22:24 | 11.6211 | 55617 | 76310 | 74392
12911 | 2021-11-13 | 22:24 | 11.6211 | 55616 | 76314 | 74396
12912 | 2021-11-13 | 22:24 | 11.6211 | 55614 | 76317 | 74400
12913 | 2021-11-13 | 22:24 | 11.6212 | 55613 | 76321 | 74404
12914 | 2021-11-13 | 22:24 | 11.6212 | 55611 | 76325 | 74408
12915 | 2021-11-13 | 22:24 | 11.6212 | 55609 | 76328 | 74412
12916 | 2021-11-13 | 22:24 | 11.6212 | 55607 | 76330 | 74416
12917 | 2021-11-13 | 22:24 | 11.6213 | 55605 | 76333 | 74420
12918 | 2021-11-13 | 22:24 | 11.6213 | 55602 | 76335 | 74424
12919 | 2021-11-13 | 22:24 | 11.6213 | 55600 | 76337 | 74429
12920 | 2021-11-13 | 22:24 | 11.6214 | 55598 | 76339 | 74433
12921 | 2021-11-13 | 22:24 | 11.6214 | 55596 | 76341 | 74437
12922 | 2021-11-13 | 22:24 | 11.6214 | 55593 | 76343 | 74441
12923 | 2021-11-13 | 22:24 | 11.6214 | 55591 | 76346 | 74445
12924 | 2021-11-13 | 22:24 | 11.6215 | 55589 | 76348 | 74448
12925 | 2021-11-13 | 22:24 | 11.6215 | 55586 | 76351 | 74452
12926 | 2021-11-13 | 22:24 | 11.6215 | 55583 | 76354 | 74456
12927 | 2021-11-13 | 22:24 | 11.6216 | 55580 | 76358 | 74459
12928 | 2021-11-13 | 22:24 | 11.6216 | 55577 | 76362 | 74462
12929 | 2021-11-13 | 22:24 | 11.6216 | 55574 | 76366 | 74466
12930 | 2021-11-13 | 22:24 | 11.6216 | 55570 | 76371 | 74469
12931 | 2021-11-13 | 22:24 | 11.6217 | 55567 | 76376 | 74472
12932 | 2021-11-13 | 22:24 | 11.6217 | 55564 | 76381 | 74475
12933 | 2021-11-13 | 22:24 | 11.6217 | 55560 | 76386 | 74478
12934 | 2021-11-13 | 22:24 | 11.6218 | 55557 | 76391 | 74481
12935 | 2021-11-13 | 22:24 | 11.6218 | 55554 | 76396 | 74483
12936 | 2021-11-13 | 22:24 | 11.6218 | 55550 | 76401 | 74486
12937 | 2021-11-13 | 22:24 | 11.6218 | 55547 | 76407 | 74489
12938 | 2021-11-13 | 22:24 | 11.6219 | 55543 | 76412 | 74492
12939 | 2021-11-13 | 22:24 | 11.6219 | 55540 | 76418 | 74494
12940 | 2021-11-13 | 22:24 | 11.6219 | 55537 | 76424 | 74497
12941 | 2021-11-13 | 22:24 | 11.622 | 55533 | 76430 | 74499
12942 | 2021-11-13 | 22:24 | 11.622 | 55530 | 76437 | 74502
12943 | 2021-11-13 | 22:24 | 11.622 | 55527 | 76444 | 74504
12944 | 2021-11-13 | 22:24 | 11.622 | 55524 | 76451 | 74506
12945 | 2021-11-13 | 22:24 | 11.6221 | 55521 | 76458 | 74508
12946 | 2021-11-13 | 22:24 | 11.6221 | 55518 | 76466 | 74510
12947 | 2021-11-13 | 22:24 | 11.6221 | 55515 | 76473 | 74512
12948 | 2021-11-13 | 22:24 | 11.6222 | 55512 | 76481 | 74513
12949 | 2021-11-13 | 22:24 | 11.6222 | 55508 | 76489 | 74515
12950 | 2021-11-13 | 22:24 | 11.6222 | 55505 | 76497 | 74517
12951 | 2021-11-13 | 22:24 | 11.6222 | 55503 | 76504 | 74518
12952 | 2021-11-13 | 22:24 | 11.6223 | 55500 | 76512 | 74520
12953 | 2021-11-13 | 22:24 | 11.6223 | 55498 | 76519 | 74521
12954 | 2021-11-13 | 22:24 | 11.6223 | 55495 | 76527 | 74523
12955 | 2021-11-13 | 22:24 | 11.6224 | 55493 | 76534 | 74524
12956 | 2021-11-13 | 22:24 | 11.6224 | 55491 | 76541 | 74526
12957 | 2021-11-13 | 22:24 | 11.6224 | 55489 | 76549 | 74527
12958 | 2021-11-13 | 22:24 | 11.6224 | 55486 | 76556 | 74528
12959 | 2021-11-13 | 22:24 | 11.6225 | 55484 | 76564 | 74529
12960 | 2021-11-13 | 22:24 | 11.6225 | 55481 | 76571 | 74530
12961 | 2021-11-13 | 22:24 | 11.6225 | 55479 | 76579 | 74531
12962 | 2021-11-13 | 22:24 | 11.6226 | 55477 | 76586 | 74531
12963 | 2021-11-13 | 22:24 | 11.6226 | 55474 | 76594 | 74532
12964 | 2021-11-13 | 22:24 | 11.6226 | 55472 | 76601 | 74533
12965 | 2021-11-13 | 22:24 | 11.6226 | 55469 | 76607 | 74533
12966 | 2021-11-13 | 22:24 | 11.6227 | 55467 | 76614 | 74533
12967 | 2021-11-13 | 22:24 | 11.6227 | 55465 | 76620 | 74534
12968 | 2021-11-13 | 22:24 | 11.6227 | 55463 | 76626 | 74534
12969 | 2021-11-13 | 22:24 | 11.6228 | 55460 | 76631 | 74534
12970 | 2021-11-13 | 22:24 | 11.6228 | 55458 | 76637 | 74534
12971 | 2021-11-13 | 22:24 | 11.6228 | 55456 | 76642 | 74534
12972 | 2021-11-13 | 22:24 | 11.6228 | 55454 | 76647 | 74534
12973 | 2021-11-13 | 22:24 | 11.6229 | 55452 | 76653 | 74534
12974 | 2021-11-13 | 22:24 | 11.6229 | 55449 | 76658 | 74533
12975 | 2021-11-13 | 22:24 | 11.6229 | 55447 | 76664 | 74533
12976 | 2021-11-13 | 22:24 | 11.623 | 55444 | 76670 | 74532
12977 | 2021-11-13 | 22:24 | 11.623 | 55441 | 76675 | 74532
12978 | 2021-11-13 | 22:24 | 11.623 | 55438 | 76681 | 74531
12979 | 2021-11-13 | 22:24 | 11.6231 | 55434 | 76687 | 74530
12980 | 2021-11-13 | 22:24 | 11.6231 | 55431 | 76692 | 74529
12981 | 2021-11-13 | 22:24 | 11.6231 | 55427 | 76698 | 74528
12982 | 2021-11-13 | 22:24 | 11.6231 | 55423 | 76704 | 74527
12983 | 2021-11-13 | 22:24 | 11.6232 | 55419 | 76709 | 74526
12984 | 2021-11-13 | 22:24 | 11.6232 | 55415 | 76715 | 74525
12985 | 2021-11-13 | 22:24 | 11.6232 | 55410 | 76720 | 74523
12986 | 2021-11-13 | 22:24 | 11.6233 | 55406 | 76726 | 74522
12987 | 2021-11-13 | 22:24 | 11.6233 | 55401 | 76731 | 74520
12988 | 2021-11-13 | 22:24 | 11.6233 | 55397 | 76737 | 74518
12989 | 2021-11-13 | 22:24 | 11.6233 | 55393 | 76742 | 74517
12990 | 2021-11-13 | 22:24 | 11.6234 | 55388 | 76748 | 74515
12991 | 2021-11-13 | 22:24 | 11.6234 | 55384 | 76753 | 74513
12992 | 2021-11-13 | 22:24 | 11.6234 | 55379 | 76758 | 74511
12993 | 2021-11-13 | 22:24 | 11.6235 | 55374 | 76764 | 74508
12994 | 2021-11-13 | 22:24 | 11.6235 | 55369 | 76769 | 74506
12995 | 2021-11-13 | 22:24 | 11.6235 | 55364 | 76774 | 74504
12996 | 2021-11-13 | 22:24 | 11.6235 | 55358 | 76780 | 74501
12997 | 2021-11-13 | 22:24 | 11.6236 | 55353 | 76785 | 74498
12998 | 2021-11-13 | 22:24 | 11.6236 | 55348 | 76790 | 74496
12999 | 2021-11-13 | 22:24 | 11.6236 | 55343 | 76794 | 74493
13000 | 2021-11-13 | 22:24 | 11.6237 | 55338 | 76799 | 74489
13001 | 2021-11-13 | 22:24 | 11.6237 | 55333 | 76803 | 74486
13002 | 2021-11-13 | 22:24 | 11.6237 | 55328 | 76807 | 74483
13003 | 2021-11-13 | 22:24 | 11.6237 | 55323 | 76811 | 74479
13004 | 2021-11-13 | 22:24 | 11.6238 | 55319 | 76815 | 74475
13005 | 2021-11-13 | 22:24 | 11.6238 | 55314 | 76819 | 74472
13006 | 2021-11-13 | 22:24 | 11.6238 | 55310 | 76822 | 74467
13007 | 2021-11-13 | 22:24 | 11.6239 | 55305 | 76826 | 74463
13008 | 2021-11-13 | 22:24 | 11.6239 | 55301 | 76829 | 74459
13009 | 2021-11-13 | 22:24 | 11.6239 | 55296 | 76832 | 74455
13010 | 2021-11-13 | 22:24 | 11.6239 | 55291 | 76835 | 74451
13011 | 2021-11-13 | 22:24 | 11.624 | 55286 | 76838 | 74446
13012 | 2021-11-13 | 22:24 | 11.624 | 55281 | 76841 | 74442
13013 | 2021-11-13 | 22:24 | 11.624 | 55275 | 76844 | 74437
13014 | 2021-11-13 | 22:24 | 11.6241 | 55270 | 76847 | 74433
13015 | 2021-11-13 | 22:24 | 11.6241 | 55265 | 76849 | 74428
13016 | 2021-11-13 | 22:24 | 11.6241 | 55259 | 76852 | 74423
13017 | 2021-11-13 | 22:24 | 11.6241 | 55253 | 76854 | 74419
13018 | 2021-11-13 | 22:24 | 11.6242 | 55247 | 76856 | 74414
13019 | 2021-11-13 | 22:24 | 11.6242 | 55241 | 76858 | 74409
13020 | 2021-11-13 | 22:24 | 11.6242 | 55236 | 76860 | 74404
13021 | 2021-11-13 | 22:24 | 11.6243 | 55230 | 76861 | 74400
13022 | 2021-11-13 | 22:24 | 11.6243 | 55224 | 76863 | 74395
13023 | 2021-11-13 | 22:24 | 11.6243 | 55218 | 76864 | 74390
13024 | 2021-11-13 | 22:24 | 11.6243 | 55213 | 76865 | 74385
13025 | 2021-11-13 | 22:24 | 11.6244 | 55207 | 76866 | 74380
13026 | 2021-11-13 | 22:24 | 11.6244 | 55202 | 76867 | 74376
13027 | 2021-11-13 | 22:24 | 11.6244 | 55196 | 76868 | 74371
13028 | 2021-11-13 | 22:24 | 11.6245 | 55191 | 76868 | 74366
13029 | 2021-11-13 | 22:24 | 11.6245 | 55186 | 76869 | 74361
13030 | 2021-11-13 | 22:24 | 11.6245 | 55181 | 76870 | 74357
13031 | 2021-11-13 | 22:24 | 11.6245 | 55175 | 76870 | 74353
13032 | 2021-11-13 | 22:24 | 11.6246 | 55170 | 76871 | 74348
13033 | 2021-11-13 | 22:24 | 11.6246 | 55165 | 76871 | 74344
13034 | 2021-11-13 | 22:24 | 11.6246 | 55160 | 76871 | 74340
13035 | 2021-11-13 | 22:24 | 11.6247 | 55155 | 76871 | 74337
13036 | 2021-11-13 | 22:24 | 11.6247 | 55150 | 76871 | 74333
13037 | 2021-11-13 | 22:24 | 11.6247 | 55145 | 76871 | 74330
13038 | 2021-11-13 | 22:24 | 11.6247 | 55140 | 76871 | 74327
13039 | 2021-11-13 | 22:24 | 11.6248 | 55135 | 76871 | 74324
13040 | 2021-11-13 | 22:24 | 11.6248 | 55130 | 76871 | 74321
13041 | 2021-11-13 | 22:24 | 11.6248 | 55125 | 76871 | 74318
13042 | 2021-11-13 | 22:24 | 11.6249 | 55120 | 76871 | 74316
13043 | 2021-11-13 | 22:24 | 11.6249 | 55116 | 76871 | 74314
13044 | 2021-11-13 | 22:24 | 11.6249 | 55112 | 76870 | 74312
13045 | 2021-11-13 | 22:24 | 11.6249 | 55107 | 76870 | 74311
13046 | 2021-11-13 | 22:24 | 11.625 | 55103 | 76870 | 74310
13047 | 2021-11-13 | 22:24 | 11.625 | 55099 | 76870 | 74309
13048 | 2021-11-13 | 22:24 | 11.625 | 55094 | 76870 | 74308
13049 | 2021-11-13 | 22:24 | 11.6251 | 55090 | 76870 | 74308
13050 | 2021-11-13 | 22:24 | 11.6251 | 55086 | 76870 | 74308
13051 | 2021-11-13 | 22:24 | 11.6251 | 55081 | 76870 | 74308
13052 | 2021-11-13 | 22:24 | 11.6251 | 55077 | 76870 | 74308
13053 | 2021-11-13 | 22:24 | 11.6252 | 55073 | 76870 | 74308
13054 | 2021-11-13 | 22:24 | 11.6252 | 55069 | 76871 | 74309
13055 | 2021-11-13 | 22:24 | 11.6252 | 55065 | 76871 | 74310
13056 | 2021-11-13 | 22:24 | 11.6253 | 55061 | 76871 | 74311
13057 | 2021-11-13 | 22:24 | 11.6253 | 55057 | 76871 | 74312
13058 | 2021-11-13 | 22:24 | 11.6253 | 55053 | 76871 | 74313
13059 | 2021-11-13 | 22:24 | 11.6253 | 55049 | 76872 | 74314
13060 | 2021-11-13 | 22:24 | 11.6254 | 55046 | 76872 | 74315
13061 | 2021-11-13 | 22:24 | 11.6254 | 55043 | 76872 | 74316
13062 | 2021-11-13 | 22:24 | 11.6254 | 55040 | 76872 | 74318
13063 | 2021-11-13 | 22:24 | 11.6255 | 55037 | 76872 | 74319
13064 | 2021-11-13 | 22:24 | 11.6255 | 55035 | 76872 | 74320
13065 | 2021-11-13 | 22:24 | 11.6255 | 55033 | 76872 | 74321
13066 | 2021-11-13 | 22:24 | 11.6255 | 55032 | 76871 | 74323
13067 | 2021-11-13 | 22:24 | 11.6256 | 55030 | 76871 | 74324
13068 | 2021-11-13 | 22:24 | 11.6256 | 55029 | 76871 | 74325
13069 | 2021-11-13 | 22:24 | 11.6256 | 55028 | 76870 | 74326
13070 | 2021-11-13 | 22:24 | 11.6257 | 55027 | 76869 | 74327
13071 | 2021-11-13 | 22:24 | 11.6257 | 55027 | 76868 | 74328
13072 | 2021-11-13 | 22:24 | 11.6257 | 55026 | 76867 | 74329
13073 | 2021-11-13 | 22:24 | 11.6258 | 55026 | 76866 | 74330
13074 | 2021-11-13 | 22:24 | 11.6258 | 55026 | 76865 | 74330
13075 | 2021-11-13 | 22:24 | 11.6258 | 55026 | 76863 | 74330
13076 | 2021-11-13 | 22:24 | 11.6258 | 55026 | 76862 | 74330
13077 | 2021-11-13 | 22:24 | 11.6259 | 55026 | 76860 | 74330
13078 | 2021-11-13 | 22:24 | 11.6259 | 55027 | 76858 | 74330
13079 | 2021-11-13 | 22:24 | 11.6259 | 55028 | 76856 | 74329
13080 | 2021-11-13 | 22:24 | 11.626 | 55028 | 76854 | 74328
13081 | 2021-11-13 | 22:24 | 11.626 | 55029 | 76852 | 74327
13082 | 2021-11-13 | 22:24 | 11.626 | 55029 | 76850 | 74326
13083 | 2021-11-13 | 22:24 | 11.626 | 55030 | 76847 | 74325
13084 | 2021-11-13 | 22:24 | 11.6261 | 55030 | 76844 | 74323
13085 | 2021-11-13 | 22:24 | 11.6261 | 55031 | 76841 | 74322
13086 | 2021-11-13 | 22:24 | 11.6261 | 55031 | 76838 | 74321
13087 | 2021-11-13 | 22:24 | 11.6262 | 55032 | 76835 | 74319
13088 | 2021-11-13 | 22:24 | 11.6262 | 55032 | 76832 | 74316
13089 | 2021-11-13 | 22:24 | 11.6262 | 55033 | 76828 | 74314
13090 | 2021-11-13 | 22:24 | 11.6262 | 55033 | 76825 | 74312
13091 | 2021-11-13 | 22:24 | 11.6263 | 55034 | 76821 | 74309
13092 | 2021-11-13 | 22:24 | 11.6263 | 55034 | 76817 | 74306
13093 | 2021-11-13 | 22:24 | 11.6263 | 55034 | 76813 | 74304
13094 | 2021-11-13 | 22:24 | 11.6264 | 55035 | 76809 | 74301
13095 | 2021-11-13 | 22:24 | 11.6264 | 55035 | 76805 | 74299
13096 | 2021-11-13 | 22:24 | 11.6264 | 55035 | 76801 | 74296
13097 | 2021-11-13 | 22:24 | 11.6264 | 55036 | 76796 | 74293
13098 | 2021-11-13 | 22:24 | 11.6265 | 55036 | 76792 | 74290
13099 | 2021-11-13 | 22:24 | 11.6265 | 55037 | 76788 | 74287
13100 | 2021-11-13 | 22:24 | 11.6265 | 55037 | 76783 | 74285
13101 | 2021-11-13 | 22:24 | 11.6266 | 55037 | 76778 | 74282
13102 | 2021-11-13 | 22:24 | 11.6266 | 55037 | 76774 | 74280
13103 | 2021-11-13 | 22:24 | 11.6266 | 55038 | 76769 | 74277
13104 | 2021-11-13 | 22:24 | 11.6266 | 55038 | 76764 | 74275
13105 | 2021-11-13 | 22:24 | 11.6267 | 55038 | 76759 | 74273
13106 | 2021-11-13 | 22:24 | 11.6267 | 55038 | 76754 | 74271
13107 | 2021-11-13 | 22:24 | 11.6267 | 55039 | 76750 | 74269
13108 | 2021-11-13 | 22:24 | 11.6268 | 55039 | 76745 | 74268
13109 | 2021-11-13 | 22:24 | 11.6268 | 55039 | 76740 | 74266
13110 | 2021-11-13 | 22:24 | 11.6268 | 55039 | 76736 | 74265
13111 | 2021-11-13 | 22:24 | 11.6268 | 55040 | 76731 | 74264
13112 | 2021-11-13 | 22:24 | 11.6269 | 55040 | 76727 | 74263
13113 | 2021-11-13 | 22:24 | 11.6269 | 55040 | 76723 | 74262
13114 | 2021-11-13 | 22:24 | 11.6269 | 55040 | 76719 | 74262
13115 | 2021-11-13 | 22:24 | 11.627 | 55040 | 76715 | 74262
13116 | 2021-11-13 | 22:24 | 11.627 | 55040 | 76711 | 74262
13117 | 2021-11-13 | 22:24 | 11.627 | 55040 | 76708 | 74263
13118 | 2021-11-13 | 22:24 | 11.627 | 55041 | 76705 | 74264
13119 | 2021-11-13 | 22:24 | 11.6271 | 55041 | 76702 | 74265
13120 | 2021-11-13 | 22:24 | 11.6271 | 55041 | 76699 | 74266
13121 | 2021-11-13 | 22:24 | 11.6271 | 55041 | 76697 | 74267
13122 | 2021-11-13 | 22:24 | 11.6272 | 55041 | 76694 | 74269
13123 | 2021-11-13 | 22:24 | 11.6272 | 55041 | 76692 | 74270
13124 | 2021-11-13 | 22:24 | 11.6272 | 55041 | 76690 | 74272
13125 | 2021-11-13 | 22:24 | 11.6272 | 55041 | 76688 | 74275
13126 | 2021-11-13 | 22:24 | 11.6273 | 55041 | 76687 | 74278
13127 | 2021-11-13 | 22:24 | 11.6273 | 55041 | 76686 | 74281
13128 | 2021-11-13 | 22:24 | 11.6273 | 55041 | 76685 | 74283
13129 | 2021-11-13 | 22:24 | 11.6274 | 55041 | 76684 | 74287
13130 | 2021-11-13 | 22:24 | 11.6274 | 55041 | 76684 | 74290
13131 | 2021-11-13 | 22:24 | 11.6274 | 55041 | 76683 | 74294
13132 | 2021-11-13 | 22:24 | 11.6274 | 55041 | 76682 | 74298
13133 | 2021-11-13 | 22:24 | 11.6275 | 55040 | 76682 | 74302
13134 | 2021-11-13 | 22:24 | 11.6275 | 55040 | 76681 | 74306
13135 | 2021-11-13 | 22:24 | 11.6275 | 55040 | 76681 | 74311
13136 | 2021-11-13 | 22:24 | 11.6276 | 55040 | 76680 | 74316
13137 | 2021-11-13 | 22:24 | 11.6276 | 55039 | 76680 | 74322
13138 | 2021-11-13 | 22:24 | 11.6276 | 55039 | 76680 | 74327
13139 | 2021-11-13 | 22:24 | 11.6276 | 55038 | 76679 | 74333
13140 | 2021-11-13 | 22:24 | 11.6277 | 55037 | 76678 | 74339
13141 | 2021-11-13 | 22:24 | 11.6277 | 55037 | 76678 | 74345
13142 | 2021-11-13 | 22:24 | 11.6277 | 55036 | 76677 | 74351
13143 | 2021-11-13 | 22:24 | 11.6278 | 55035 | 76677 | 74358
13144 | 2021-11-13 | 22:24 | 11.6278 | 55034 | 76676 | 74364
13145 | 2021-11-13 | 22:24 | 11.6278 | 55033 | 76675 | 74371
13146 | 2021-11-13 | 22:24 | 11.6278 | 55032 | 76674 | 74378
13147 | 2021-11-13 | 22:24 | 11.6279 | 55031 | 76673 | 74385
13148 | 2021-11-13 | 22:24 | 11.6279 | 55030 | 76672 | 74392
13149 | 2021-11-13 | 22:24 | 11.6279 | 55028 | 76670 | 74400
13150 | 2021-11-13 | 22:24 | 11.628 | 55027 | 76669 | 74407
13151 | 2021-11-13 | 22:24 | 11.628 | 55026 | 76667 | 74414
13152 | 2021-11-13 | 22:24 | 11.628 | 55024 | 76666 | 74422
13153 | 2021-11-13 | 22:24 | 11.628 | 55023 | 76664 | 74429
13154 | 2021-11-13 | 22:24 | 11.6281 | 55021 | 76662 | 74436
13155 | 2021-11-13 | 22:24 | 11.6281 | 55019 | 76661 | 74444
13156 | 2021-11-13 | 22:24 | 11.6281 | 55017 | 76659 | 74452
13157 | 2021-11-13 | 22:24 | 11.6282 | 55015 | 76658 | 74459
13158 | 2021-11-13 | 22:24 | 11.6282 | 55013 | 76657 | 74467
13159 | 2021-11-13 | 22:24 | 11.6282 | 55011 | 76656 | 74475
13160 | 2021-11-13 | 22:24 | 11.6282 | 55009 | 76655 | 74483
13161 | 2021-11-13 | 22:24 | 11.6283 | 55007 | 76654 | 74490
13162 | 2021-11-13 | 22:24 | 11.6283 | 55004 | 76653 | 74498
13163 | 2021-11-13 | 22:24 | 11.6283 | 55002 | 76652 | 74505
13164 | 2021-11-13 | 22:24 | 11.6284 | 54999 | 76652 | 74513
13165 | 2021-11-13 | 22:24 | 11.6284 | 54996 | 76651 | 74520
13166 | 2021-11-13 | 22:24 | 11.6284 | 54993 | 76651 | 74528
13167 | 2021-11-13 | 22:24 | 11.6285 | 54990 | 76651 | 74535
13168 | 2021-11-13 | 22:24 | 11.6285 | 54987 | 76651 | 74543
13169 | 2021-11-13 | 22:24 | 11.6285 | 54983 | 76651 | 74551
13170 | 2021-11-13 | 22:24 | 11.6285 | 54980 | 76651 | 74559
13171 | 2021-11-13 | 22:24 | 11.6286 | 54976 | 76651 | 74567
13172 | 2021-11-13 | 22:24 | 11.6286 | 54973 | 76651 | 74574
13173 | 2021-11-13 | 22:24 | 11.6286 | 54969 | 76651 | 74582
13174 | 2021-11-13 | 22:24 | 11.6287 | 54965 | 76651 | 74590
13175 | 2021-11-13 | 22:24 | 11.6287 | 54961 | 76651 | 74598
13176 | 2021-11-13 | 22:24 | 11.6287 | 54957 | 76652 | 74606
13177 | 2021-11-13 | 22:24 | 11.6287 | 54953 | 76652 | 74613
13178 | 2021-11-13 | 22:24 | 11.6288 | 54948 | 76653 | 74621
13179 | 2021-11-13 | 22:24 | 11.6288 | 54944 | 76653 | 74629
13180 | 2021-11-13 | 22:24 | 11.6288 | 54939 | 76653 | 74636
13181 | 2021-11-13 | 22:24 | 11.6289 | 54934 | 76653 | 74644
13182 | 2021-11-13 | 22:24 | 11.6289 | 54929 | 76653 | 74651
13183 | 2021-11-13 | 22:24 | 11.6289 | 54925 | 76653 | 74658
13184 | 2021-11-13 | 22:24 | 11.6289 | 54920 | 76653 | 74665
13185 | 2021-11-13 | 22:24 | 11.629 | 54915 | 76653 | 74672
13186 | 2021-11-13 | 22:24 | 11.629 | 54910 | 76653 | 74679
13187 | 2021-11-13 | 22:24 | 11.629 | 54906 | 76653 | 74685
13188 | 2021-11-13 | 22:24 | 11.6291 | 54901 | 76653 | 74691
13189 | 2021-11-13 | 22:24 | 11.6291 | 54896 | 76653 | 74697
13190 | 2021-11-13 | 22:24 | 11.6291 | 54891 | 76653 | 74703
13191 | 2021-11-13 | 22:24 | 11.6291 | 54886 | 76653 | 74709
13192 | 2021-11-13 | 22:24 | 11.6292 | 54881 | 76653 | 74714
13193 | 2021-11-13 | 22:24 | 11.6292 | 54877 | 76653 | 74720
13194 | 2021-11-13 | 22:24 | 11.6292 | 54872 | 76653 | 74725
13195 | 2021-11-13 | 22:24 | 11.6293 | 54867 | 76653 | 74730
13196 | 2021-11-13 | 22:24 | 11.6293 | 54862 | 76653 | 74734
13197 | 2021-11-13 | 22:24 | 11.6293 | 54857 | 76654 | 74739
13198 | 2021-11-13 | 22:24 | 11.6293 | 54852 | 76654 | 74743
13199 | 2021-11-13 | 22:24 | 11.6294 | 54847 | 76655 | 74747
13200 | 2021-11-13 | 22:24 | 11.6294 | 54842 | 76656 | 74752
13201 | 2021-11-13 | 22:24 | 11.6294 | 54837 | 76657 | 74755
13202 | 2021-11-13 | 22:24 | 11.6295 | 54832 | 76658 | 74759
13203 | 2021-11-13 | 22:24 | 11.6295 | 54827 | 76659 | 74762
13204 | 2021-11-13 | 22:24 | 11.6295 | 54823 | 76660 | 74766
13205 | 2021-11-13 | 22:24 | 11.6295 | 54818 | 76661 | 74769
13206 | 2021-11-13 | 22:24 | 11.6296 | 54814 | 76663 | 74772
13207 | 2021-11-13 | 22:24 | 11.6296 | 54809 | 76665 | 74775
13208 | 2021-11-13 | 22:24 | 11.6296 | 54805 | 76667 | 74778
13209 | 2021-11-13 | 22:24 | 11.6297 | 54800 | 76669 | 74780
13210 | 2021-11-13 | 22:24 | 11.6297 | 54796 | 76671 | 74783
13211 | 2021-11-13 | 22:24 | 11.6297 | 54791 | 76674 | 74785
13212 | 2021-11-13 | 22:24 | 11.6297 | 54787 | 76677 | 74788
13213 | 2021-11-13 | 22:24 | 11.6298 | 54783 | 76679 | 74790
13214 | 2021-11-13 | 22:24 | 11.6298 | 54779 | 76682 | 74792
13215 | 2021-11-13 | 22:24 | 11.6298 | 54775 | 76685 | 74793
13216 | 2021-11-13 | 22:24 | 11.6299 | 54771 | 76689 | 74795
13217 | 2021-11-13 | 22:24 | 11.6299 | 54767 | 76692 | 74796
13218 | 2021-11-13 | 22:24 | 11.6299 | 54763 | 76696 | 74798
13219 | 2021-11-13 | 22:24 | 11.6299 | 54758 | 76700 | 74799
13220 | 2021-11-13 | 22:24 | 11.63 | 54754 | 76704 | 74800
13221 | 2021-11-13 | 22:24 | 11.63 | 54749 | 76709 | 74801
13222 | 2021-11-13 | 22:24 | 11.63 | 54745 | 76713 | 74801
13223 | 2021-11-13 | 22:24 | 11.6301 | 54741 | 76717 | 74802
13224 | 2021-11-13 | 22:24 | 11.6301 | 54736 | 76722 | 74803
13225 | 2021-11-13 | 22:24 | 11.6301 | 54732 | 76727 | 74803
13226 | 2021-11-13 | 22:24 | 11.6301 | 54728 | 76731 | 74803
13227 | 2021-11-13 | 22:24 | 11.6302 | 54724 | 76736 | 74803
13228 | 2021-11-13 | 22:24 | 11.6302 | 54720 | 76741 | 74803
13229 | 2021-11-13 | 22:24 | 11.6302 | 54715 | 76746 | 74803
13230 | 2021-11-13 | 22:24 | 11.6303 | 54711 | 76751 | 74802
13231 | 2021-11-13 | 22:24 | 11.6303 | 54706 | 76756 | 74802
13232 | 2021-11-13 | 22:24 | 11.6303 | 54702 | 76761 | 74801
13233 | 2021-11-13 | 22:24 | 11.6303 | 54698 | 76767 | 74801
13234 | 2021-11-13 | 22:24 | 11.6304 | 54694 | 76772 | 74800
13235 | 2021-11-13 | 22:24 | 11.6304 | 54690 | 76778 | 74799
13236 | 2021-11-13 | 22:24 | 11.6304 | 54686 | 76783 | 74798
13237 | 2021-11-13 | 22:24 | 11.6305 | 54683 | 76788 | 74796
13238 | 2021-11-13 | 22:24 | 11.6305 | 54681 | 76793 | 74795
13239 | 2021-11-13 | 22:24 | 11.6305 | 54681 | 76795 | 74793
13240 | 2021-11-13 | 22:24 | 11.6305 | 54683 | 76796 | 74790
13241 | 2021-11-13 | 22:24 | 11.6306 | 54689 | 76795 | 74787
13242 | 2021-11-13 | 22:24 | 11.6306 | 54698 | 76793 | 74784
13243 | 2021-11-13 | 22:24 | 11.6306 | 54709 | 76789 | 74779
13244 | 2021-11-13 | 22:24 | 11.6307 | 54722 | 76784 | 74775
13245 | 2021-11-13 | 22:24 | 11.6307 | 54735 | 76780 | 74770
13246 | 2021-11-13 | 22:24 | 11.6307 | 54749 | 76775 | 74764
13247 | 2021-11-13 | 22:24 | 11.6307 | 54763 | 76771 | 74758
13248 | 2021-11-13 | 22:24 | 11.6308 | 54777 | 76767 | 74752
13249 | 2021-11-13 | 22:24 | 11.6308 | 54792 | 76763 | 74746
13250 | 2021-11-13 | 22:24 | 11.6308 | 54810 | 76758 | 74739
13251 | 2021-11-13 | 22:24 | 11.6309 | 54829 | 76753 | 74732
13252 | 2021-11-13 | 22:24 | 11.6309 | 54852 | 76746 | 74724
13253 | 2021-11-13 | 22:24 | 11.6309 | 54877 | 76739 | 74716
13254 | 2021-11-13 | 22:24 | 11.6309 | 54904 | 76732 | 74707
13255 | 2021-11-13 | 22:24 | 11.631 | 54933 | 76724 | 74698
13256 | 2021-11-13 | 22:24 | 11.631 | 54964 | 76716 | 74688
13257 | 2021-11-13 | 22:24 | 11.631 | 54997 | 76707 | 74679
13258 | 2021-11-13 | 22:24 | 11.6311 | 55029 | 76699 | 74669
13259 | 2021-11-13 | 22:24 | 11.6311 | 55063 | 76692 | 74659
13260 | 2021-11-13 | 22:24 | 11.6311 | 55099 | 76684 | 74649
13261 | 2021-11-13 | 22:24 | 11.6312 | 55137 | 76677 | 74640
13262 | 2021-11-13 | 22:24 | 11.6312 | 55177 | 76671 | 74630
13263 | 2021-11-13 | 22:24 | 11.6312 | 55221 | 76664 | 74620
13264 | 2021-11-13 | 22:24 | 11.6312 | 55268 | 76658 | 74609
13265 | 2021-11-13 | 22:24 | 11.6313 | 55319 | 76652 | 74598
13266 | 2021-11-13 | 22:24 | 11.6313 | 55373 | 76647 | 74587
13267 | 2021-11-13 | 22:24 | 11.6313 | 55430 | 76643 | 74575
13268 | 2021-11-13 | 22:24 | 11.6314 | 55489 | 76640 | 74564
13269 | 2021-11-13 | 22:24 | 11.6314 | 55549 | 76638 | 74553
13270 | 2021-11-13 | 22:24 | 11.6314 | 55611 | 76638 | 74543
13271 | 2021-11-13 | 22:24 | 11.6314 | 55676 | 76639 | 74533
13272 | 2021-11-13 | 22:24 | 11.6315 | 55744 | 76641 | 74524
13273 | 2021-11-13 | 22:24 | 11.6315 | 55816 | 76645 | 74516
13274 | 2021-11-13 | 22:24 | 11.6315 | 55892 | 76649 | 74507
13275 | 2021-11-13 | 22:24 | 11.6316 | 55971 | 76654 | 74500
13276 | 2021-11-13 | 22:24 | 11.6316 | 56054 | 76659 | 74492
13277 | 2021-11-13 | 22:24 | 11.6316 | 56141 | 76664 | 74485
13278 | 2021-11-13 | 22:24 | 11.6316 | 56230 | 76670 | 74478
13279 | 2021-11-13 | 22:24 | 11.6317 | 56322 | 76677 | 74471
13280 | 2021-11-13 | 22:24 | 11.6317 | 56416 | 76683 | 74466
13281 | 2021-11-13 | 22:24 | 11.6317 | 56513 | 76690 | 74461
13282 | 2021-11-13 | 22:24 | 11.6318 | 56611 | 76698 | 74457
13283 | 2021-11-13 | 22:24 | 11.6318 | 56711 | 76705 | 74454
13284 | 2021-11-13 | 22:24 | 11.6318 | 56811 | 76713 | 74453
13285 | 2021-11-13 | 22:24 | 11.6318 | 56913 | 76721 | 74452
13286 | 2021-11-13 | 22:24 | 11.6319 | 57015 | 76729 | 74452
13287 | 2021-11-13 | 22:24 | 11.6319 | 57118 | 76737 | 74453
13288 | 2021-11-13 | 22:24 | 11.6319 | 57222 | 76744 | 74455
13289 | 2021-11-13 | 22:24 | 11.632 | 57327 | 76751 | 74458
13290 | 2021-11-13 | 22:24 | 11.632 | 57433 | 76758 | 74462
13291 | 2021-11-13 | 22:24 | 11.632 | 57540 | 76764 | 74467
13292 | 2021-11-13 | 22:24 | 11.632 | 57648 | 76770 | 74474
13293 | 2021-11-13 | 22:24 | 11.6321 | 57756 | 76775 | 74481
13294 | 2021-11-13 | 22:24 | 11.6321 | 57865 | 76780 | 74490
13295 | 2021-11-13 | 22:24 | 11.6321 | 57973 | 76785 | 74500
13296 | 2021-11-13 | 22:24 | 11.6322 | 58081 | 76789 | 74510
13297 | 2021-11-13 | 22:24 | 11.6322 | 58187 | 76792 | 74520
13298 | 2021-11-13 | 22:24 | 11.6322 | 58293 | 76795 | 74531
13299 | 2021-11-13 | 22:24 | 11.6322 | 58398 | 76798 | 74541
13300 | 2021-11-13 | 22:24 | 11.6323 | 58501 | 76800 | 74552
13301 | 2021-11-13 | 22:24 | 11.6323 | 58604 | 76802 | 74562
13302 | 2021-11-13 | 22:24 | 11.6323 | 58706 | 76803 | 74573
13303 | 2021-11-13 | 22:24 | 11.6324 | 58807 | 76804 | 74584
13304 | 2021-11-13 | 22:24 | 11.6324 | 58906 | 76805 | 74596
13305 | 2021-11-13 | 22:24 | 11.6324 | 59004 | 76806 | 74607
13306 | 2021-11-13 | 22:24 | 11.6324 | 59099 | 76807 | 74618
13307 | 2021-11-13 | 22:24 | 11.6325 | 59193 | 76807 | 74628
13308 | 2021-11-13 | 22:24 | 11.6325 | 59285 | 76807 | 74638
13309 | 2021-11-13 | 22:24 | 11.6325 | 59375 | 76808 | 74647
13310 | 2021-11-13 | 22:24 | 11.6326 | 59463 | 76808 | 74655
13311 | 2021-11-13 | 22:24 | 11.6326 | 59551 | 76807 | 74663
13312 | 2021-11-13 | 22:24 | 11.6326 | 59636 | 76807 | 74671
13313 | 2021-11-13 | 22:24 | 11.6326 | 59720 | 76807 | 74679
13314 | 2021-11-13 | 22:24 | 11.6327 | 59802 | 76807 | 74686
13315 | 2021-11-13 | 22:24 | 11.6327 | 59882 | 76806 | 74693
13316 | 2021-11-13 | 22:24 | 11.6327 | 59960 | 76806 | 74699
13317 | 2021-11-13 | 22:24 | 11.6328 | 60035 | 76806 | 74704
13318 | 2021-11-13 | 22:24 | 11.6328 | 60108 | 76805 | 74709
13319 | 2021-11-13 | 22:24 | 11.6328 | 60179 | 76805 | 74715
13320 | 2021-11-13 | 22:24 | 11.6328 | 60247 | 76804 | 74720
13321 | 2021-11-13 | 22:24 | 11.6329 | 60313 | 76804 | 74725
13322 | 2021-11-13 | 22:24 | 11.6329 | 60377 | 76803 | 74731
13323 | 2021-11-13 | 22:24 | 11.6329 | 60438 | 76802 | 74738
13324 | 2021-11-13 | 22:24 | 11.633 | 60497 | 76801 | 74745
13325 | 2021-11-13 | 22:24 | 11.633 | 60553 | 76800 | 74751
13326 | 2021-11-13 | 22:24 | 11.633 | 60608 | 76799 | 74759
13327 | 2021-11-13 | 22:24 | 11.633 | 60662 | 76798 | 74765
13328 | 2021-11-13 | 22:24 | 11.6331 | 60714 | 76797 | 74772
13329 | 2021-11-13 | 22:24 | 11.6331 | 60766 | 76796 | 74778
13330 | 2021-11-13 | 22:24 | 11.6331 | 60816 | 76795 | 74784
13331 | 2021-11-13 | 22:24 | 11.6332 | 60867 | 76795 | 74789
13332 | 2021-11-13 | 22:24 | 11.6332 | 60917 | 76794 | 74794
13333 | 2021-11-13 | 22:24 | 11.6332 | 60967 | 76794 | 74798
13334 | 2021-11-13 | 22:24 | 11.6332 | 61016 | 76793 | 74802
13335 | 2021-11-13 | 22:24 | 11.6333 | 61065 | 76793 | 74806
13336 | 2021-11-13 | 22:24 | 11.6333 | 61113 | 76793 | 74810
13337 | 2021-11-13 | 22:24 | 11.6333 | 61160 | 76792 | 74815
13338 | 2021-11-13 | 22:24 | 11.6334 | 61207 | 76792 | 74820
13339 | 2021-11-13 | 22:24 | 11.6334 | 61253 | 76791 | 74826
13340 | 2021-11-13 | 22:24 | 11.6334 | 61298 | 76790 | 74832
13341 | 2021-11-13 | 22:24 | 11.6334 | 61343 | 76789 | 74840
13342 | 2021-11-13 | 22:24 | 11.6335 | 61387 | 76788 | 74849
13343 | 2021-11-13 | 22:24 | 11.6335 | 61429 | 76786 | 74859
13344 | 2021-11-13 | 22:24 | 11.6335 | 61471 | 76784 | 74871
13345 | 2021-11-13 | 22:24 | 11.6336 | 61512 | 76782 | 74883
13346 | 2021-11-13 | 22:24 | 11.6336 | 61551 | 76780 | 74897
13347 | 2021-11-13 | 22:24 | 11.6336 | 61590 | 76777 | 74911
13348 | 2021-11-13 | 22:24 | 11.6336 | 61629 | 76775 | 74925
13349 | 2021-11-13 | 22:24 | 11.6337 | 61667 | 76772 | 74939
13350 | 2021-11-13 | 22:24 | 11.6337 | 61704 | 76770 | 74954
13351 | 2021-11-13 | 22:24 | 11.6337 | 61741 | 76767 | 74968
13352 | 2021-11-13 | 22:24 | 11.6338 | 61778 | 76765 | 74982
13353 | 2021-11-13 | 22:24 | 11.6338 | 61814 | 76763 | 74995
13354 | 2021-11-13 | 22:24 | 11.6338 | 61850 | 76760 | 75009
13355 | 2021-11-13 | 22:24 | 11.6339 | 61885 | 76758 | 75021
13356 | 2021-11-13 | 22:24 | 11.6339 | 61920 | 76755 | 75034
13357 | 2021-11-13 | 22:24 | 11.6339 | 61954 | 76752 | 75046
13358 | 2021-11-13 | 22:24 | 11.6339 | 61986 | 76749 | 75058
13359 | 2021-11-13 | 22:24 | 11.634 | 62018 | 76745 | 75071
13360 | 2021-11-13 | 22:24 | 11.634 | 62050 | 76741 | 75083
13361 | 2021-11-13 | 22:24 | 11.634 | 62080 | 76735 | 75096
13362 | 2021-11-13 | 22:24 | 11.6341 | 62109 | 76730 | 75108
13363 | 2021-11-13 | 22:24 | 11.6341 | 62137 | 76723 | 75121
13364 | 2021-11-13 | 22:24 | 11.6341 | 62164 | 76716 | 75133
13365 | 2021-11-13 | 22:24 | 11.6341 | 62190 | 76709 | 75146
13366 | 2021-11-13 | 22:24 | 11.6342 | 62215 | 76700 | 75157
13367 | 2021-11-13 | 22:24 | 11.6342 | 62239 | 76691 | 75169
13368 | 2021-11-13 | 22:24 | 11.6342 | 62262 | 76682 | 75180
13369 | 2021-11-13 | 22:24 | 11.6343 | 62284 | 76673 | 75191
13370 | 2021-11-13 | 22:24 | 11.6343 | 62305 | 76663 | 75201
13371 | 2021-11-13 | 22:24 | 11.6343 | 62325 | 76653 | 75212
13372 | 2021-11-13 | 22:24 | 11.6343 | 62343 | 76642 | 75222
13373 | 2021-11-13 | 22:24 | 11.6344 | 62361 | 76632 | 75233
13374 | 2021-11-13 | 22:24 | 11.6344 | 62378 | 76622 | 75243
13375 | 2021-11-13 | 22:24 | 11.6344 | 62393 | 76611 | 75253
13376 | 2021-11-13 | 22:24 | 11.6345 | 62407 | 76601 | 75263
13377 | 2021-11-13 | 22:24 | 11.6345 | 62420 | 76590 | 75273
13378 | 2021-11-13 | 22:24 | 11.6345 | 62433 | 76579 | 75283
13379 | 2021-11-13 | 22:24 | 11.6345 | 62444 | 76568 | 75293
13380 | 2021-11-13 | 22:24 | 11.6346 | 62454 | 76557 | 75303
13381 | 2021-11-13 | 22:24 | 11.6346 | 62463 | 76546 | 75313
13382 | 2021-11-13 | 22:24 | 11.6346 | 62471 | 76534 | 75323
13383 | 2021-11-13 | 22:24 | 11.6347 | 62477 | 76522 | 75333
13384 | 2021-11-13 | 22:24 | 11.6347 | 62483 | 76510 | 75342
13385 | 2021-11-13 | 22:24 | 11.6347 | 62488 | 76498 | 75352
13386 | 2021-11-13 | 22:24 | 11.6347 | 62493 | 76486 | 75361
13387 | 2021-11-13 | 22:24 | 11.6348 | 62496 | 76474 | 75371
13388 | 2021-11-13 | 22:24 | 11.6348 | 62499 | 76463 | 75380
13389 | 2021-11-13 | 22:24 | 11.6348 | 62501 | 76452 | 75389
13390 | 2021-11-13 | 22:24 | 11.6349 | 62502 | 76441 | 75398
13391 | 2021-11-13 | 22:24 | 11.6349 | 62503 | 76430 | 75407
13392 | 2021-11-13 | 22:24 | 11.6349 | 62504 | 76420 | 75415
13393 | 2021-11-13 | 22:24 | 11.6349 | 62503 | 76409 | 75424
13394 | 2021-11-13 | 22:24 | 11.635 | 62503 | 76399 | 75432
13395 | 2021-11-13 | 22:24 | 11.635 | 62501 | 76389 | 75440
13396 | 2021-11-13 | 22:24 | 11.635 | 62499 | 76379 | 75448
13397 | 2021-11-13 | 22:24 | 11.6351 | 62497 | 76369 | 75456
13398 | 2021-11-13 | 22:24 | 11.6351 | 62494 | 76359 | 75464
13399 | 2021-11-13 | 22:24 | 11.6351 | 62491 | 76351 | 75472
13400 | 2021-11-13 | 22:24 | 11.6351 | 62487 | 76343 | 75480
13401 | 2021-11-13 | 22:24 | 11.6352 | 62483 | 76335 | 75488
13402 | 2021-11-13 | 22:24 | 11.6352 | 62478 | 76328 | 75496
13403 | 2021-11-13 | 22:24 | 11.6352 | 62473 | 76322 | 75504
13404 | 2021-11-13 | 22:24 | 11.6353 | 62468 | 76316 | 75513
13405 | 2021-11-13 | 22:24 | 11.6353 | 62463 | 76310 | 75522
13406 | 2021-11-13 | 22:24 | 11.6353 | 62457 | 76305 | 75531
13407 | 2021-11-13 | 22:24 | 11.6353 | 62451 | 76299 | 75540
13408 | 2021-11-13 | 22:24 | 11.6354 | 62445 | 76294 | 75549
13409 | 2021-11-13 | 22:24 | 11.6354 | 62439 | 76288 | 75559
13410 | 2021-11-13 | 22:24 | 11.6354 | 62432 | 76283 | 75569
13411 | 2021-11-13 | 22:24 | 11.6355 | 62425 | 76277 | 75580
13412 | 2021-11-13 | 22:24 | 11.6355 | 62419 | 76271 | 75590
13413 | 2021-11-13 | 22:24 | 11.6355 | 62411 | 76266 | 75601
13414 | 2021-11-13 | 22:24 | 11.6355 | 62404 | 76260 | 75612
13415 | 2021-11-13 | 22:24 | 11.6356 | 62397 | 76255 | 75624
13416 | 2021-11-13 | 22:24 | 11.6356 | 62390 | 76250 | 75635
13417 | 2021-11-13 | 22:24 | 11.6356 | 62383 | 76246 | 75647
13418 | 2021-11-13 | 22:24 | 11.6357 | 62376 | 76242 | 75658
13419 | 2021-11-13 | 22:24 | 11.6357 | 62369 | 76240 | 75669
13420 | 2021-11-13 | 22:24 | 11.6357 | 62363 | 76238 | 75680
13421 | 2021-11-13 | 22:24 | 11.6357 | 62356 | 76237 | 75691
13422 | 2021-11-13 | 22:24 | 11.6358 | 62350 | 76237 | 75702
13423 | 2021-11-13 | 22:24 | 11.6358 | 62343 | 76237 | 75713
13424 | 2021-11-13 | 22:24 | 11.6358 | 62337 | 76236 | 75723
13425 | 2021-11-13 | 22:24 | 11.6359 | 62331 | 76236 | 75733
13426 | 2021-11-13 | 22:24 | 11.6359 | 62325 | 76235 | 75743
13427 | 2021-11-13 | 22:24 | 11.6359 | 62319 | 76235 | 75753
13428 | 2021-11-13 | 22:24 | 11.6359 | 62313 | 76234 | 75762
13429 | 2021-11-13 | 22:24 | 11.636 | 62309 | 76232 | 75772
13430 | 2021-11-13 | 22:24 | 11.636 | 62304 | 76231 | 75781
13431 | 2021-11-13 | 22:24 | 11.636 | 62300 | 76230 | 75790
13432 | 2021-11-13 | 22:24 | 11.6361 | 62296 | 76229 | 75800
13433 | 2021-11-13 | 22:24 | 11.6361 | 62293 | 76227 | 75809
13434 | 2021-11-13 | 22:24 | 11.6361 | 62290 | 76226 | 75818
13435 | 2021-11-13 | 22:24 | 11.6361 | 62288 | 76224 | 75828
13436 | 2021-11-13 | 22:24 | 11.6362 | 62286 | 76223 | 75837
13437 | 2021-11-13 | 22:24 | 11.6362 | 62284 | 76222 | 75847
13438 | 2021-11-13 | 22:24 | 11.6362 | 62282 | 76220 | 75856
13439 | 2021-11-13 | 22:24 | 11.6363 | 62281 | 76219 | 75864
13440 | 2021-11-13 | 22:24 | 11.6363 | 62280 | 76218 | 75873
13441 | 2021-11-13 | 22:24 | 11.6363 | 62279 | 76218 | 75881
13442 | 2021-11-13 | 22:24 | 11.6363 | 62280 | 76217 | 75890
13443 | 2021-11-13 | 22:24 | 11.6364 | 62281 | 76217 | 75898
13444 | 2021-11-13 | 22:24 | 11.6364 | 62282 | 76217 | 75905
13445 | 2021-11-13 | 22:24 | 11.6364 | 62284 | 76217 | 75913
13446 | 2021-11-13 | 22:24 | 11.6365 | 62287 | 76218 | 75920
13447 | 2021-11-13 | 22:24 | 11.6365 | 62291 | 76218 | 75927
13448 | 2021-11-13 | 22:24 | 11.6365 | 62295 | 76219 | 75933
13449 | 2021-11-13 | 22:24 | 11.6366 | 62301 | 76220 | 75940
13450 | 2021-11-13 | 22:24 | 11.6366 | 62307 | 76221 | 75946
13451 | 2021-11-13 | 22:24 | 11.6366 | 62313 | 76222 | 75952
13452 | 2021-11-13 | 22:24 | 11.6366 | 62320 | 76222 | 75958
13453 | 2021-11-13 | 22:24 | 11.6367 | 62328 | 76222 | 75963
13454 | 2021-11-13 | 22:24 | 11.6367 | 62336 | 76222 | 75968
13455 | 2021-11-13 | 22:24 | 11.6367 | 62345 | 76222 | 75973
13456 | 2021-11-13 | 22:24 | 11.6368 | 62355 | 76221 | 75978
13457 | 2021-11-13 | 22:24 | 11.6368 | 62365 | 76220 | 75983
13458 | 2021-11-13 | 22:24 | 11.6368 | 62377 | 76220 | 75987
13459 | 2021-11-13 | 22:24 | 11.6368 | 62389 | 76220 | 75991
13460 | 2021-11-13 | 22:24 | 11.6369 | 62402 | 76220 | 75994
13461 | 2021-11-13 | 22:24 | 11.6369 | 62417 | 76221 | 75998
13462 | 2021-11-13 | 22:24 | 11.6369 | 62432 | 76222 | 76001
13463 | 2021-11-13 | 22:24 | 11.637 | 62449 | 76223 | 76003
13464 | 2021-11-13 | 22:24 | 11.637 | 62467 | 76225 | 76006
13465 | 2021-11-13 | 22:24 | 11.637 | 62486 | 76227 | 76009
13466 | 2021-11-13 | 22:24 | 11.637 | 62506 | 76228 | 76011
13467 | 2021-11-13 | 22:24 | 11.6371 | 62527 | 76230 | 76013
13468 | 2021-11-13 | 22:24 | 11.6371 | 62548 | 76231 | 76015
13469 | 2021-11-13 | 22:24 | 11.6371 | 62571 | 76232 | 76017
13470 | 2021-11-13 | 22:24 | 11.6372 | 62595 | 76233 | 76018
13471 | 2021-11-13 | 22:24 | 11.6372 | 62620 | 76234 | 76020
13472 | 2021-11-13 | 22:24 | 11.6372 | 62646 | 76235 | 76021
13473 | 2021-11-13 | 22:24 | 11.6372 | 62673 | 76236 | 76022
13474 | 2021-11-13 | 22:24 | 11.6373 | 62701 | 76237 | 76023
13475 | 2021-11-13 | 22:24 | 11.6373 | 62731 | 76239 | 76024
13476 | 2021-11-13 | 22:24 | 11.6373 | 62762 | 76240 | 76024
13477 | 2021-11-13 | 22:24 | 11.6374 | 62794 | 76242 | 76025
13478 | 2021-11-13 | 22:24 | 11.6374 | 62828 | 76245 | 76025
13479 | 2021-11-13 | 22:24 | 11.6374 | 62862 | 76247 | 76025
13480 | 2021-11-13 | 22:24 | 11.6374 | 62898 | 76250 | 76026
13481 | 2021-11-13 | 22:24 | 11.6375 | 62936 | 76253 | 76026
13482 | 2021-11-13 | 22:24 | 11.6375 | 62974 | 76256 | 76026
13483 | 2021-11-13 | 22:24 | 11.6375 | 63014 | 76259 | 76026
13484 | 2021-11-13 | 22:24 | 11.6376 | 63056 | 76263 | 76026
13485 | 2021-11-13 | 22:24 | 11.6376 | 63098 | 76267 | 76026
13486 | 2021-11-13 | 22:24 | 11.6376 | 63143 | 76271 | 76026
13487 | 2021-11-13 | 22:24 | 11.6376 | 63189 | 76276 | 76026
13488 | 2021-11-13 | 22:24 | 11.6377 | 63236 | 76280 | 76026
13489 | 2021-11-13 | 22:24 | 11.6377 | 63286 | 76285 | 76026
13490 | 2021-11-13 | 22:24 | 11.6377 | 63337 | 76290 | 76025
13491 | 2021-11-13 | 22:24 | 11.6378 | 63389 | 76295 | 76025
13492 | 2021-11-13 | 22:24 | 11.6378 | 63443 | 76301 | 76025
13493 | 2021-11-13 | 22:24 | 11.6378 | 63499 | 76307 | 76025
13494 | 2021-11-13 | 22:24 | 11.6378 | 63556 | 76313 | 76025
13495 | 2021-11-13 | 22:24 | 11.6379 | 63613 | 76319 | 76025
13496 | 2021-11-13 | 22:24 | 11.6379 | 63672 | 76325 | 76025
13497 | 2021-11-13 | 22:24 | 11.6379 | 63732 | 76331 | 76025
13498 | 2021-11-13 | 22:24 | 11.638 | 63793 | 76337 | 76025
13499 | 2021-11-13 | 22:24 | 11.638 | 63855 | 76343 | 76024
13500 | 2021-11-13 | 22:24 | 11.638 | 63917 | 76350 | 76024
13501 | 2021-11-13 | 22:24 | 11.638 | 63981 | 76356 | 76024
13502 | 2021-11-13 | 22:24 | 11.6381 | 64046 | 76363 | 76025
13503 | 2021-11-13 | 22:24 | 11.6381 | 64112 | 76370 | 76025
13504 | 2021-11-13 | 22:24 | 11.6381 | 64180 | 76377 | 76025
13505 | 2021-11-13 | 22:24 | 11.6382 | 64248 | 76384 | 76025
13506 | 2021-11-13 | 22:24 | 11.6382 | 64318 | 76391 | 76026
13507 | 2021-11-13 | 22:24 | 11.6382 | 64388 | 76399 | 76026
13508 | 2021-11-13 | 22:24 | 11.6382 | 64459 | 76406 | 76027
13509 | 2021-11-13 | 22:24 | 11.6383 | 64531 | 76414 | 76027
13510 | 2021-11-13 | 22:24 | 11.6383 | 64603 | 76422 | 76028
13511 | 2021-11-13 | 22:24 | 11.6383 | 64675 | 76430 | 76028
13512 | 2021-11-13 | 22:24 | 11.6384 | 64749 | 76438 | 76029
13513 | 2021-11-13 | 22:24 | 11.6384 | 64822 | 76446 | 76030
13514 | 2021-11-13 | 22:24 | 11.6384 | 64896 | 76454 | 76030
13515 | 2021-11-13 | 22:24 | 11.6384 | 64970 | 76462 | 76031
13516 | 2021-11-13 | 22:24 | 11.6385 | 65045 | 76470 | 76032
13517 | 2021-11-13 | 22:24 | 11.6385 | 65121 | 76478 | 76032
13518 | 2021-11-13 | 22:24 | 11.6385 | 65197 | 76486 | 76033
13519 | 2021-11-13 | 22:24 | 11.6386 | 65274 | 76494 | 76034
13520 | 2021-11-13 | 22:24 | 11.6386 | 65352 | 76502 | 76034
13521 | 2021-11-13 | 22:24 | 11.6386 | 65431 | 76510 | 76035
13522 | 2021-11-13 | 22:24 | 11.6386 | 65510 | 76519 | 76035
13523 | 2021-11-13 | 22:24 | 11.6387 | 65590 | 76527 | 76036
13524 | 2021-11-13 | 22:24 | 11.6387 | 65670 | 76536 | 76036
13525 | 2021-11-13 | 22:24 | 11.6387 | 65751 | 76544 | 76037
13526 | 2021-11-13 | 22:24 | 11.6388 | 65832 | 76553 | 76037
13527 | 2021-11-13 | 22:24 | 11.6388 | 65914 | 76562 | 76037
13528 | 2021-11-13 | 22:24 | 11.6388 | 65996 | 76571 | 76037
13529 | 2021-11-13 | 22:24 | 11.6388 | 66078 | 76580 | 76037
13530 | 2021-11-13 | 22:24 | 11.6389 | 66161 | 76589 | 76037
13531 | 2021-11-13 | 22:24 | 11.6389 | 66244 | 76598 | 76036
13532 | 2021-11-13 | 22:24 | 11.6389 | 66328 | 76607 | 76036
13533 | 2021-11-13 | 22:24 | 11.639 | 66412 | 76616 | 76036
13534 | 2021-11-13 | 22:24 | 11.639 | 66497 | 76625 | 76035
13535 | 2021-11-13 | 22:24 | 11.639 | 66582 | 76634 | 76034
13536 | 2021-11-13 | 22:24 | 11.639 | 66667 | 76642 | 76033
13537 | 2021-11-13 | 22:24 | 11.6391 | 66752 | 76651 | 76032
13538 | 2021-11-13 | 22:24 | 11.6391 | 66838 | 76659 | 76031
13539 | 2021-11-13 | 22:24 | 11.6391 | 66923 | 76668 | 76030
13540 | 2021-11-13 | 22:24 | 11.6392 | 67008 | 76676 | 76029
13541 | 2021-11-13 | 22:24 | 11.6392 | 67093 | 76684 | 76027
13542 | 2021-11-13 | 22:24 | 11.6392 | 67179 | 76692 | 76026
13543 | 2021-11-13 | 22:24 | 11.6393 | 67263 | 76699 | 76024
13544 | 2021-11-13 | 22:24 | 11.6393 | 67348 | 76707 | 76022
13545 | 2021-11-13 | 22:24 | 11.6393 | 67433 | 76714 | 76021
13546 | 2021-11-13 | 22:24 | 11.6393 | 67517 | 76720 | 76019
13547 | 2021-11-13 | 22:24 | 11.6394 | 67601 | 76726 | 76018
13548 | 2021-11-13 | 22:24 | 11.6394 | 67685 | 76732 | 76017
13549 | 2021-11-13 | 22:24 | 11.6394 | 67769 | 76737 | 76016
13550 | 2021-11-13 | 22:24 | 11.6395 | 67852 | 76742 | 76015
13551 | 2021-11-13 | 22:24 | 11.6395 | 67936 | 76747 | 76015
13552 | 2021-11-13 | 22:24 | 11.6395 | 68019 | 76751 | 76014
13553 | 2021-11-13 | 22:24 | 11.6395 | 68101 | 76754 | 76014
13554 | 2021-11-13 | 22:24 | 11.6396 | 68183 | 76757 | 76015
13555 | 2021-11-13 | 22:24 | 11.6396 | 68264 | 76760 | 76015
13556 | 2021-11-13 | 22:24 | 11.6396 | 68345 | 76762 | 76016
13557 | 2021-11-13 | 22:24 | 11.6397 | 68425 | 76764 | 76016
13558 | 2021-11-13 | 22:24 | 11.6397 | 68504 | 76766 | 76018
13559 | 2021-11-13 | 22:24 | 11.6397 | 68583 | 76767 | 76019
13560 | 2021-11-13 | 22:24 | 11.6397 | 68661 | 76768 | 76021
13561 | 2021-11-13 | 22:24 | 11.6398 | 68738 | 76769 | 76024
13562 | 2021-11-13 | 22:24 | 11.6398 | 68815 | 76769 | 76027
13563 | 2021-11-13 | 22:24 | 11.6398 | 68890 | 76769 | 76031
13564 | 2021-11-13 | 22:24 | 11.6399 | 68965 | 76769 | 76036
13565 | 2021-11-13 | 22:24 | 11.6399 | 69039 | 76769 | 76041
13566 | 2021-11-13 | 22:24 | 11.6399 | 69113 | 76768 | 76047
13567 | 2021-11-13 | 22:24 | 11.6399 | 69185 | 76767 | 76053
13568 | 2021-11-13 | 22:24 | 11.64 | 69256 | 76767 | 76060
13569 | 2021-11-13 | 22:24 | 11.64 | 69327 | 76766 | 76067
13570 | 2021-11-13 | 22:24 | 11.64 | 69396 | 76765 | 76075
13571 | 2021-11-13 | 22:24 | 11.6401 | 69465 | 76764 | 76083
13572 | 2021-11-13 | 22:24 | 11.6401 | 69533 | 76763 | 76092
13573 | 2021-11-13 | 22:24 | 11.6401 | 69599 | 76763 | 76102
13574 | 2021-11-13 | 22:24 | 11.6401 | 69665 | 76762 | 76112
13575 | 2021-11-13 | 22:24 | 11.6402 | 69730 | 76761 | 76123
13576 | 2021-11-13 | 22:24 | 11.6402 | 69793 | 76760 | 76135
13577 | 2021-11-13 | 22:24 | 11.6402 | 69856 | 76760 | 76147
13578 | 2021-11-13 | 22:24 | 11.6403 | 69917 | 76759 | 76159
13579 | 2021-11-13 | 22:24 | 11.6403 | 69977 | 76758 | 76171
13580 | 2021-11-13 | 22:24 | 11.6403 | 70037 | 76758 | 76184
13581 | 2021-11-13 | 22:24 | 11.6403 | 70095 | 76757 | 76198
13582 | 2021-11-13 | 22:24 | 11.6404 | 70153 | 76757 | 76212
13583 | 2021-11-13 | 22:24 | 11.6404 | 70209 | 76757 | 76226
13584 | 2021-11-13 | 22:24 | 11.6404 | 70265 | 76756 | 76241
13585 | 2021-11-13 | 22:24 | 11.6405 | 70320 | 76756 | 76256
13586 | 2021-11-13 | 22:24 | 11.6405 | 70374 | 76756 | 76272
13587 | 2021-11-13 | 22:24 | 11.6405 | 70428 | 76755 | 76288
13588 | 2021-11-13 | 22:24 | 11.6405 | 70480 | 76755 | 76304
13589 | 2021-11-13 | 22:24 | 11.6406 | 70532 | 76755 | 76320
13590 | 2021-11-13 | 22:24 | 11.6406 | 70583 | 76754 | 76337
13591 | 2021-11-13 | 22:24 | 11.6406 | 70633 | 76754 | 76354
13592 | 2021-11-13 | 22:24 | 11.6407 | 70683 | 76753 | 76371
13593 | 2021-11-13 | 22:24 | 11.6407 | 70732 | 76752 | 76389
13594 | 2021-11-13 | 22:24 | 11.6407 | 70781 | 76752 | 76406
13595 | 2021-11-13 | 22:24 | 11.6407 | 70828 | 76751 | 76423
13596 | 2021-11-13 | 22:24 | 11.6408 | 70876 | 76750 | 76441
13597 | 2021-11-13 | 22:24 | 11.6408 | 70922 | 76749 | 76458
13598 | 2021-11-13 | 22:24 | 11.6408 | 70967 | 76747 | 76475
13599 | 2021-11-13 | 22:24 | 11.6409 | 71011 | 76746 | 76492
13600 | 2021-11-13 | 22:24 | 11.6409 | 71055 | 76744 | 76510
13601 | 2021-11-13 | 22:24 | 11.6409 | 71098 | 76742 | 76527
13602 | 2021-11-13 | 22:24 | 11.6409 | 71139 | 76740 | 76544
13603 | 2021-11-13 | 22:24 | 11.641 | 71181 | 76738 | 76560
13604 | 2021-11-13 | 22:24 | 11.641 | 71221 | 76735 | 76577
13605 | 2021-11-13 | 22:24 | 11.641 | 71261 | 76732 | 76593
13606 | 2021-11-13 | 22:24 | 11.6411 | 71299 | 76728 | 76609
13607 | 2021-11-13 | 22:24 | 11.6411 | 71337 | 76724 | 76626
13608 | 2021-11-13 | 22:24 | 11.6411 | 71374 | 76720 | 76642
13609 | 2021-11-13 | 22:24 | 11.6411 | 71410 | 76715 | 76658
13610 | 2021-11-13 | 22:24 | 11.6412 | 71445 | 76709 | 76673
13611 | 2021-11-13 | 22:24 | 11.6412 | 71479 | 76704 | 76689
13612 | 2021-11-13 | 22:24 | 11.6412 | 71511 | 76698 | 76704
13613 | 2021-11-13 | 22:24 | 11.6413 | 71543 | 76692 | 76720
13614 | 2021-11-13 | 22:24 | 11.6413 | 71573 | 76686 | 76735
13615 | 2021-11-13 | 22:24 | 11.6413 | 71603 | 76680 | 76750
13616 | 2021-11-13 | 22:24 | 11.6413 | 71631 | 76673 | 76765
13617 | 2021-11-13 | 22:24 | 11.6414 | 71658 | 76667 | 76779
13618 | 2021-11-13 | 22:24 | 11.6414 | 71684 | 76659 | 76794
13619 | 2021-11-13 | 22:24 | 11.6414 | 71709 | 76652 | 76808
13620 | 2021-11-13 | 22:24 | 11.6415 | 71733 | 76644 | 76822
13621 | 2021-11-13 | 22:24 | 11.6415 | 71755 | 76636 | 76836
13622 | 2021-11-13 | 22:24 | 11.6415 | 71777 | 76627 | 76849
13623 | 2021-11-13 | 22:24 | 11.6415 | 71798 | 76618 | 76862
13624 | 2021-11-13 | 22:24 | 11.6416 | 71817 | 76609 | 76875
13625 | 2021-11-13 | 22:24 | 11.6416 | 71836 | 76599 | 76888
13626 | 2021-11-13 | 22:24 | 11.6416 | 71853 | 76590 | 76900
13627 | 2021-11-13 | 22:24 | 11.6417 | 71870 | 76581 | 76911
13628 | 2021-11-13 | 22:24 | 11.6417 | 71885 | 76571 | 76922
13629 | 2021-11-13 | 22:24 | 11.6417 | 71899 | 76562 | 76933
13630 | 2021-11-13 | 22:24 | 11.6417 | 71913 | 76552 | 76944
13631 | 2021-11-13 | 22:24 | 11.6418 | 71925 | 76543 | 76955
13632 | 2021-11-13 | 22:24 | 11.6418 | 71936 | 76534 | 76966
13633 | 2021-11-13 | 22:24 | 11.6418 | 71947 | 76524 | 76976
13634 | 2021-11-13 | 22:24 | 11.6419 | 71956 | 76515 | 76987
13635 | 2021-11-13 | 22:24 | 11.6419 | 71965 | 76506 | 76997
13636 | 2021-11-13 | 22:24 | 11.6419 | 71972 | 76498 | 77008
13637 | 2021-11-13 | 22:24 | 11.642 | 71979 | 76489 | 77017
13638 | 2021-11-13 | 22:24 | 11.642 | 71986 | 76480 | 77027
13639 | 2021-11-13 | 22:24 | 11.642 | 71991 | 76471 | 77036
13640 | 2021-11-13 | 22:24 | 11.642 | 71996 | 76462 | 77045
13641 | 2021-11-13 | 22:24 | 11.6421 | 72000 | 76453 | 77054
13642 | 2021-11-13 | 22:24 | 11.6421 | 72003 | 76444 | 77063
13643 | 2021-11-13 | 22:24 | 11.6421 | 72005 | 76436 | 77072
13644 | 2021-11-13 | 22:24 | 11.6422 | 72007 | 76428 | 77081
13645 | 2021-11-13 | 22:24 | 11.6422 | 72009 | 76420 | 77089
13646 | 2021-11-13 | 22:24 | 11.6422 | 72010 | 76412 | 77097
13647 | 2021-11-13 | 22:24 | 11.6422 | 72010 | 76404 | 77106
13648 | 2021-11-13 | 22:24 | 11.6423 | 72010 | 76396 | 77114
13649 | 2021-11-13 | 22:24 | 11.6423 | 72010 | 76388 | 77121
13650 | 2021-11-13 | 22:24 | 11.6423 | 72009 | 76380 | 77129
13651 | 2021-11-13 | 22:24 | 11.6424 | 72007 | 76372 | 77136
13652 | 2021-11-13 | 22:24 | 11.6424 | 72006 | 76364 | 77143
13653 | 2021-11-13 | 22:24 | 11.6424 | 72004 | 76356 | 77150
13654 | 2021-11-13 | 22:24 | 11.6424 | 72001 | 76348 | 77157
13655 | 2021-11-13 | 22:24 | 11.6425 | 71999 | 76342 | 77165
13656 | 2021-11-13 | 22:24 | 11.6425 | 71996 | 76336 | 77172
13657 | 2021-11-13 | 22:24 | 11.6425 | 71993 | 76330 | 77178
13658 | 2021-11-13 | 22:24 | 11.6426 | 71990 | 76324 | 77185
13659 | 2021-11-13 | 22:24 | 11.6426 | 71986 | 76320 | 77192
13660 | 2021-11-13 | 22:24 | 11.6426 | 71983 | 76315 | 77198
13661 | 2021-11-13 | 22:24 | 11.6426 | 71979 | 76310 | 77205
13662 | 2021-11-13 | 22:24 | 11.6427 | 71975 | 76305 | 77211
13663 | 2021-11-13 | 22:24 | 11.6427 | 71971 | 76301 | 77217
13664 | 2021-11-13 | 22:24 | 11.6427 | 71968 | 76296 | 77223
13665 | 2021-11-13 | 22:24 | 11.6428 | 71964 | 76292 | 77229
13666 | 2021-11-13 | 22:24 | 11.6428 | 71960 | 76287 | 77235
13667 | 2021-11-13 | 22:24 | 11.6428 | 71955 | 76282 | 77241
13668 | 2021-11-13 | 22:24 | 11.6428 | 71951 | 76278 | 77247
13669 | 2021-11-13 | 22:24 | 11.6429 | 71947 | 76273 | 77252
13670 | 2021-11-13 | 22:24 | 11.6429 | 71943 | 76269 | 77257
13671 | 2021-11-13 | 22:24 | 11.6429 | 71939 | 76265 | 77262
13672 | 2021-11-13 | 22:24 | 11.643 | 71935 | 76262 | 77267
13673 | 2021-11-13 | 22:24 | 11.643 | 71930 | 76259 | 77272
13674 | 2021-11-13 | 22:24 | 11.643 | 71927 | 76257 | 77277
13675 | 2021-11-13 | 22:24 | 11.643 | 71923 | 76255 | 77282
13676 | 2021-11-13 | 22:24 | 11.6431 | 71919 | 76254 | 77288
13677 | 2021-11-13 | 22:24 | 11.6431 | 71916 | 76253 | 77294
13678 | 2021-11-13 | 22:24 | 11.6431 | 71913 | 76252 | 77300
13679 | 2021-11-13 | 22:24 | 11.6432 | 71909 | 76251 | 77306
13680 | 2021-11-13 | 22:24 | 11.6432 | 71906 | 76250 | 77311
13681 | 2021-11-13 | 22:24 | 11.6432 | 71903 | 76249 | 77317
13682 | 2021-11-13 | 22:24 | 11.6432 | 71900 | 76248 | 77323
13683 | 2021-11-13 | 22:24 | 11.6433 | 71897 | 76247 | 77330
13684 | 2021-11-13 | 22:24 | 11.6433 | 71894 | 76246 | 77336
13685 | 2021-11-13 | 22:24 | 11.6433 | 71891 | 76245 | 77342
13686 | 2021-11-13 | 22:24 | 11.6434 | 71889 | 76244 | 77349
13687 | 2021-11-13 | 22:24 | 11.6434 | 71887 | 76244 | 77355
13688 | 2021-11-13 | 22:24 | 11.6434 | 71885 | 76243 | 77362
13689 | 2021-11-13 | 22:24 | 11.6434 | 71884 | 76243 | 77369
13690 | 2021-11-13 | 22:24 | 11.6435 | 71882 | 76243 | 77376
13691 | 2021-11-13 | 22:24 | 11.6435 | 71881 | 76243 | 77383
13692 | 2021-11-13 | 22:24 | 11.6435 | 71880 | 76243 | 77391
13693 | 2021-11-13 | 22:24 | 11.6436 | 71879 | 76243 | 77399
13694 | 2021-11-13 | 22:24 | 11.6436 | 71877 | 76243 | 77407
13695 | 2021-11-13 | 22:24 | 11.6436 | 71877 | 76243 | 77415
13696 | 2021-11-13 | 22:24 | 11.6436 | 71876 | 76243 | 77422
13697 | 2021-11-13 | 22:24 | 11.6437 | 71876 | 76243 | 77430
13698 | 2021-11-13 | 22:24 | 11.6437 | 71876 | 76244 | 77437
13699 | 2021-11-13 | 22:24 | 11.6437 | 71876 | 76244 | 77445
13700 | 2021-11-13 | 22:24 | 11.6438 | 71878 | 76245 | 77452
13701 | 2021-11-13 | 22:24 | 11.6438 | 71879 | 76246 | 77459
13702 | 2021-11-13 | 22:24 | 11.6438 | 71882 | 76248 | 77466
13703 | 2021-11-13 | 22:24 | 11.6438 | 71884 | 76250 | 77473
13704 | 2021-11-13 | 22:24 | 11.6439 | 71887 | 76252 | 77480
13705 | 2021-11-13 | 22:24 | 11.6439 | 71891 | 76253 | 77487
13706 | 2021-11-13 | 22:24 | 11.6439 | 71894 | 76256 | 77494
13707 | 2021-11-13 | 22:24 | 11.644 | 71899 | 76258 | 77501
13708 | 2021-11-13 | 22:24 | 11.644 | 71903 | 76260 | 77507
13709 | 2021-11-13 | 22:24 | 11.644 | 71909 | 76261 | 77513
13710 | 2021-11-13 | 22:24 | 11.644 | 71914 | 76263 | 77519
13711 | 2021-11-13 | 22:24 | 11.6441 | 71921 | 76265 | 77525
13712 | 2021-11-13 | 22:24 | 11.6441 | 71927 | 76267 | 77530
13713 | 2021-11-13 | 22:24 | 11.6441 | 71934 | 76268 | 77535
13714 | 2021-11-13 | 22:24 | 11.6442 | 71942 | 76271 | 77540
13715 | 2021-11-13 | 22:24 | 11.6442 | 71951 | 76273 | 77545
13716 | 2021-11-13 | 22:24 | 11.6442 | 71961 | 76276 | 77550
13717 | 2021-11-13 | 22:24 | 11.6442 | 71971 | 76279 | 77554
13718 | 2021-11-13 | 22:24 | 11.6443 | 71983 | 76283 | 77558
13719 | 2021-11-13 | 22:24 | 11.6443 | 71996 | 76287 | 77561
13720 | 2021-11-13 | 22:24 | 11.6443 | 72010 | 76291 | 77565
13721 | 2021-11-13 | 22:24 | 11.6444 | 72025 | 76295 | 77568
13722 | 2021-11-13 | 22:24 | 11.6444 | 72041 | 76300 | 77571
13723 | 2021-11-13 | 22:24 | 11.6444 | 72059 | 76304 | 77574
13724 | 2021-11-13 | 22:24 | 11.6444 | 72077 | 76308 | 77576
13725 | 2021-11-13 | 22:24 | 11.6445 | 72096 | 76313 | 77579
13726 | 2021-11-13 | 22:24 | 11.6445 | 72116 | 76316 | 77581
13727 | 2021-11-13 | 22:24 | 11.6445 | 72137 | 76320 | 77583
13728 | 2021-11-13 | 22:24 | 11.6446 | 72160 | 76323 | 77584
13729 | 2021-11-13 | 22:24 | 11.6446 | 72184 | 76327 | 77586
13730 | 2021-11-13 | 22:24 | 11.6446 | 72210 | 76330 | 77587
13731 | 2021-11-13 | 22:24 | 11.6446 | 72238 | 76333 | 77588
13732 | 2021-11-13 | 22:24 | 11.6447 | 72267 | 76335 | 77589
13733 | 2021-11-13 | 22:24 | 11.6447 | 72298 | 76338 | 77589
13734 | 2021-11-13 | 22:24 | 11.6447 | 72330 | 76341 | 77590
13735 | 2021-11-13 | 22:24 | 11.6448 | 72364 | 76344 | 77590
13736 | 2021-11-13 | 22:24 | 11.6448 | 72399 | 76346 | 77591
13737 | 2021-11-13 | 22:24 | 11.6448 | 72436 | 76349 | 77591
13738 | 2021-11-13 | 22:24 | 11.6449 | 72474 | 76351 | 77591
13739 | 2021-11-13 | 22:24 | 11.6449 | 72513 | 76353 | 77591
13740 | 2021-11-13 | 22:24 | 11.6449 | 72555 | 76355 | 77591
13741 | 2021-11-13 | 22:24 | 11.6449 | 72598 | 76357 | 77591
13742 | 2021-11-13 | 22:24 | 11.645 | 72643 | 76359 | 77591
13743 | 2021-11-13 | 22:24 | 11.645 | 72689 | 76360 | 77591
13744 | 2021-11-13 | 22:24 | 11.645 | 72737 | 76362 | 77591
13745 | 2021-11-13 | 22:24 | 11.6451 | 72787 | 76363 | 77591
13746 | 2021-11-13 | 22:24 | 11.6451 | 72838 | 76364 | 77591
13747 | 2021-11-13 | 22:24 | 11.6451 | 72891 | 76365 | 77591
13748 | 2021-11-13 | 22:24 | 11.6451 | 72946 | 76366 | 77592
13749 | 2021-11-13 | 22:24 | 11.6452 | 73002 | 76368 | 77592
13750 | 2021-11-13 | 22:24 | 11.6452 | 73058 | 76370 | 77593
13751 | 2021-11-13 | 22:24 | 11.6452 | 73114 | 76375 | 77594
13752 | 2021-11-13 | 22:24 | 11.6453 | 73169 | 76381 | 77596
13753 | 2021-11-13 | 22:24 | 11.6453 | 73223 | 76389 | 77598
13754 | 2021-11-13 | 22:24 | 11.6453 | 73277 | 76398 | 77601
13755 | 2021-11-13 | 22:24 | 11.6453 | 73330 | 76409 | 77604
13756 | 2021-11-13 | 22:24 | 11.6454 | 73383 | 76421 | 77608
13757 | 2021-11-13 | 22:24 | 11.6454 | 73437 | 76433 | 77612
13758 | 2021-11-13 | 22:24 | 11.6454 | 73492 | 76446 | 77617
13759 | 2021-11-13 | 22:24 | 11.6455 | 73549 | 76458 | 77622
13760 | 2021-11-13 | 22:24 | 11.6455 | 73607 | 76471 | 77627
13761 | 2021-11-13 | 22:24 | 11.6455 | 73666 | 76484 | 77633
13762 | 2021-11-13 | 22:24 | 11.6455 | 73724 | 76498 | 77640
13763 | 2021-11-13 | 22:24 | 11.6456 | 73783 | 76513 | 77647
13764 | 2021-11-13 | 22:24 | 11.6456 | 73840 | 76529 | 77654
13765 | 2021-11-13 | 22:24 | 11.6456 | 73897 | 76546 | 77662
13766 | 2021-11-13 | 22:24 | 11.6457 | 73954 | 76564 | 77670
13767 | 2021-11-13 | 22:24 | 11.6457 | 74009 | 76583 | 77679
13768 | 2021-11-13 | 22:24 | 11.6457 | 74065 | 76603 | 77688
13769 | 2021-11-13 | 22:24 | 11.6457 | 74121 | 76622 | 77697
13770 | 2021-11-13 | 22:24 | 11.6458 | 74176 | 76642 | 77706
13771 | 2021-11-13 | 22:24 | 11.6458 | 74232 | 76661 | 77715
13772 | 2021-11-13 | 22:24 | 11.6458 | 74286 | 76680 | 77724
13773 | 2021-11-13 | 22:24 | 11.6459 | 74340 | 76699 | 77733
13774 | 2021-11-13 | 22:24 | 11.6459 | 74393 | 76718 | 77742
13775 | 2021-11-13 | 22:24 | 11.6459 | 74444 | 76737 | 77752
13776 | 2021-11-13 | 22:24 | 11.6459 | 74492 | 76756 | 77762
13777 | 2021-11-13 | 22:24 | 11.646 | 74539 | 76774 | 77772
13778 | 2021-11-13 | 22:24 | 11.646 | 74583 | 76792 | 77782
13779 | 2021-11-13 | 22:24 | 11.646 | 74626 | 76810 | 77792
13780 | 2021-11-13 | 22:24 | 11.6461 | 74668 | 76826 | 77802
13781 | 2021-11-13 | 22:24 | 11.6461 | 74709 | 76840 | 77812
13782 | 2021-11-13 | 22:24 | 11.6461 | 74748 | 76853 | 77821
13783 | 2021-11-13 | 22:24 | 11.6461 | 74785 | 76865 | 77829
13784 | 2021-11-13 | 22:24 | 11.6462 | 74820 | 76875 | 77836
13785 | 2021-11-13 | 22:24 | 11.6462 | 74853 | 76884 | 77843
13786 | 2021-11-13 | 22:24 | 11.6462 | 74882 | 76892 | 77849
13787 | 2021-11-13 | 22:24 | 11.6463 | 74908 | 76899 | 77855
13788 | 2021-11-13 | 22:24 | 11.6463 | 74932 | 76906 | 77860
13789 | 2021-11-13 | 22:24 | 11.6463 | 74953 | 76912 | 77866
13790 | 2021-11-13 | 22:24 | 11.6463 | 74971 | 76917 | 77871
13791 | 2021-11-13 | 22:24 | 11.6464 | 74987 | 76922 | 77875
13792 | 2021-11-13 | 22:24 | 11.6464 | 75002 | 76926 | 77879
13793 | 2021-11-13 | 22:24 | 11.6464 | 75014 | 76929 | 77881
13794 | 2021-11-13 | 22:24 | 11.6465 | 75024 | 76932 | 77883
13795 | 2021-11-13 | 22:24 | 11.6465 | 75033 | 76934 | 77884
13796 | 2021-11-13 | 22:24 | 11.6465 | 75041 | 76935 | 77883
13797 | 2021-11-13 | 22:24 | 11.6465 | 75048 | 76936 | 77882
13798 | 2021-11-13 | 22:24 | 11.6466 | 75053 | 76937 | 77880
13799 | 2021-11-13 | 22:24 | 11.6466 | 75058 | 76938 | 77877
13800 | 2021-11-13 | 22:24 | 11.6466 | 75061 | 76938 | 77874
13801 | 2021-11-13 | 22:24 | 11.6467 | 75063 | 76938 | 77870
13802 | 2021-11-13 | 22:24 | 11.6467 | 75063 | 76938 | 77865
13803 | 2021-11-13 | 22:24 | 11.6467 | 75062 | 76939 | 77860
13804 | 2021-11-13 | 22:24 | 11.6467 | 75060 | 76939 | 77853
13805 | 2021-11-13 | 22:24 | 11.6468 | 75057 | 76939 | 77846
13806 | 2021-11-13 | 22:24 | 11.6468 | 75054 | 76939 | 77838
13807 | 2021-11-13 | 22:24 | 11.6468 | 75050 | 76939 | 77830
13808 | 2021-11-13 | 22:24 | 11.6469 | 75047 | 76940 | 77821
13809 | 2021-11-13 | 22:24 | 11.6469 | 75043 | 76940 | 77813
13810 | 2021-11-13 | 22:24 | 11.6469 | 75039 | 76941 | 77805
13811 | 2021-11-13 | 22:24 | 11.6469 | 75036 | 76941 | 77798
13812 | 2021-11-13 | 22:24 | 11.647 | 75032 | 76942 | 77791
13813 | 2021-11-13 | 22:24 | 11.647 | 75028 | 76943 | 77785
13814 | 2021-11-13 | 22:24 | 11.647 | 75024 | 76943 | 77778
13815 | 2021-11-13 | 22:24 | 11.6471 | 75021 | 76944 | 77773
13816 | 2021-11-13 | 22:24 | 11.6471 | 75017 | 76944 | 77768
13817 | 2021-11-13 | 22:24 | 11.6471 | 75015 | 76945 | 77763
13818 | 2021-11-13 | 22:24 | 11.6471 | 75014 | 76945 | 77760
13819 | 2021-11-13 | 22:24 | 11.6472 | 75014 | 76946 | 77759
13820 | 2021-11-13 | 22:24 | 11.6472 | 75015 | 76946 | 77758
13821 | 2021-11-13 | 22:24 | 11.6472 | 75017 | 76946 | 77759
13822 | 2021-11-13 | 22:24 | 11.6473 | 75019 | 76946 | 77761
13823 | 2021-11-13 | 22:24 | 11.6473 | 75022 | 76946 | 77764
13824 | 2021-11-13 | 22:24 | 11.6473 | 75025 | 76946 | 77767
13825 | 2021-11-13 | 22:24 | 11.6473 | 75030 | 76946 | 77772
13826 | 2021-11-13 | 22:24 | 11.6474 | 75035 | 76946 | 77778
13827 | 2021-11-13 | 22:24 | 11.6474 | 75042 | 76946 | 77786
13828 | 2021-11-13 | 22:24 | 11.6474 | 75050 | 76946 | 77795
13829 | 2021-11-13 | 22:24 | 11.6475 | 75059 | 76945 | 77806
13830 | 2021-11-13 | 22:24 | 11.6475 | 75070 | 76945 | 77817
13831 | 2021-11-13 | 22:24 | 11.6475 | 75081 | 76944 | 77830
13832 | 2021-11-13 | 22:24 | 11.6476 | 75095 | 76944 | 77843
13833 | 2021-11-13 | 22:24 | 11.6476 | 75109 | 76944 | 77856
13834 | 2021-11-13 | 22:24 | 11.6476 | 75125 | 76943 | 77869
13835 | 2021-11-13 | 22:24 | 11.6476 | 75142 | 76943 | 77882
13836 | 2021-11-13 | 22:24 | 11.6477 | 75160 | 76943 | 77896
13837 | 2021-11-13 | 22:24 | 11.6477 | 75179 | 76942 | 77910
13838 | 2021-11-13 | 22:24 | 11.6477 | 75199 | 76942 | 77925
13839 | 2021-11-13 | 22:24 | 11.6478 | 75219 | 76942 | 77940
13840 | 2021-11-13 | 22:24 | 11.6478 | 75239 | 76942 | 77956
13841 | 2021-11-13 | 22:24 | 11.6478 | 75260 | 76941 | 77973
13842 | 2021-11-13 | 22:24 | 11.6478 | 75279 | 76941 | 77990
13843 | 2021-11-13 | 22:24 | 11.6479 | 75299 | 76940 | 78008
13844 | 2021-11-13 | 22:24 | 11.6479 | 75317 | 76939 | 78027
13845 | 2021-11-13 | 22:24 | 11.6479 | 75335 | 76938 | 78046
13846 | 2021-11-13 | 22:24 | 11.648 | 75352 | 76936 | 78066
13847 | 2021-11-13 | 22:24 | 11.648 | 75369 | 76935 | 78086
13848 | 2021-11-13 | 22:24 | 11.648 | 75386 | 76933 | 78107
13849 | 2021-11-13 | 22:24 | 11.648 | 75402 | 76931 | 78128
13850 | 2021-11-13 | 22:24 | 11.6481 | 75419 | 76929 | 78148
13851 | 2021-11-13 | 22:24 | 11.6481 | 75434 | 76927 | 78168
13852 | 2021-11-13 | 22:24 | 11.6481 | 75450 | 76925 | 78187
13853 | 2021-11-13 | 22:24 | 11.6482 | 75464 | 76923 | 78204
13854 | 2021-11-13 | 22:24 | 11.6482 | 75479 | 76921 | 78221
13855 | 2021-11-13 | 22:24 | 11.6482 | 75493 | 76919 | 78236
13856 | 2021-11-13 | 22:24 | 11.6482 | 75507 | 76917 | 78250
13857 | 2021-11-13 | 22:24 | 11.6483 | 75520 | 76915 | 78262
13858 | 2021-11-13 | 22:24 | 11.6483 | 75534 | 76913 | 78273
13859 | 2021-11-13 | 22:24 | 11.6483 | 75547 | 76910 | 78284
13860 | 2021-11-13 | 22:24 | 11.6484 | 75559 | 76908 | 78294
13861 | 2021-11-13 | 22:24 | 11.6484 | 75570 | 76904 | 78303
13862 | 2021-11-13 | 22:24 | 11.6484 | 75581 | 76901 | 78311
13863 | 2021-11-13 | 22:24 | 11.6484 | 75591 | 76896 | 78319
13864 | 2021-11-13 | 22:24 | 11.6485 | 75600 | 76892 | 78327
13865 | 2021-11-13 | 22:24 | 11.6485 | 75608 | 76887 | 78335
13866 | 2021-11-13 | 22:24 | 11.6485 | 75616 | 76881 | 78342
13867 | 2021-11-13 | 22:24 | 11.6486 | 75623 | 76875 | 78349
13868 | 2021-11-13 | 22:24 | 11.6486 | 75630 | 76869 | 78356
13869 | 2021-11-13 | 22:24 | 11.6486 | 75635 | 76863 | 78363
13870 | 2021-11-13 | 22:24 | 11.6486 | 75641 | 76857 | 78369
13871 | 2021-11-13 | 22:24 | 11.6487 | 75645 | 76851 | 78374
13872 | 2021-11-13 | 22:24 | 11.6487 | 75650 | 76846 | 78379
13873 | 2021-11-13 | 22:24 | 11.6487 | 75653 | 76841 | 78383
13874 | 2021-11-13 | 22:24 | 11.6488 | 75657 | 76836 | 78386
13875 | 2021-11-13 | 22:24 | 11.6488 | 75660 | 76832 | 78389
13876 | 2021-11-13 | 22:24 | 11.6488 | 75663 | 76827 | 78392
13877 | 2021-11-13 | 22:24 | 11.6488 | 75665 | 76823 | 78394
13878 | 2021-11-13 | 22:24 | 11.6489 | 75667 | 76818 | 78395
13879 | 2021-11-13 | 22:24 | 11.6489 | 75669 | 76814 | 78396
13880 | 2021-11-13 | 22:24 | 11.6489 | 75671 | 76810 | 78397
13881 | 2021-11-13 | 22:24 | 11.649 | 75672 | 76806 | 78397
13882 | 2021-11-13 | 22:24 | 11.649 | 75673 | 76801 | 78397
13883 | 2021-11-13 | 22:24 | 11.649 | 75674 | 76796 | 78396
13884 | 2021-11-13 | 22:24 | 11.649 | 75675 | 76791 | 78395
13885 | 2021-11-13 | 22:24 | 11.6491 | 75676 | 76787 | 78393
13886 | 2021-11-13 | 22:24 | 11.6491 | 75677 | 76782 | 78392
13887 | 2021-11-13 | 22:24 | 11.6491 | 75677 | 76777 | 78390
13888 | 2021-11-13 | 22:24 | 11.6492 | 75678 | 76771 | 78388
13889 | 2021-11-13 | 22:24 | 11.6492 | 75678 | 76766 | 78385
13890 | 2021-11-13 | 22:24 | 11.6492 | 75679 | 76761 | 78382
13891 | 2021-11-13 | 22:24 | 11.6492 | 75679 | 76756 | 78379
13892 | 2021-11-13 | 22:24 | 11.6493 | 75679 | 76752 | 78376
13893 | 2021-11-13 | 22:24 | 11.6493 | 75680 | 76747 | 78373
13894 | 2021-11-13 | 22:24 | 11.6493 | 75681 | 76743 | 78370
13895 | 2021-11-13 | 22:24 | 11.6494 | 75681 | 76738 | 78366
13896 | 2021-11-13 | 22:24 | 11.6494 | 75682 | 76734 | 78362
13897 | 2021-11-13 | 22:24 | 11.6494 | 75682 | 76730 | 78358
13898 | 2021-11-13 | 22:24 | 11.6494 | 75683 | 76726 | 78354
13899 | 2021-11-13 | 22:24 | 11.6495 | 75683 | 76722 | 78350
13900 | 2021-11-13 | 22:24 | 11.6495 | 75684 | 76717 | 78346
13901 | 2021-11-13 | 22:24 | 11.6495 | 75684 | 76713 | 78342
13902 | 2021-11-13 | 22:24 | 11.6496 | 75685 | 76709 | 78339
13903 | 2021-11-13 | 22:24 | 11.6496 | 75685 | 76704 | 78335
13904 | 2021-11-13 | 22:24 | 11.6496 | 75685 | 76699 | 78332
13905 | 2021-11-13 | 22:24 | 11.6496 | 75685 | 76694 | 78329
13906 | 2021-11-13 | 22:24 | 11.6497 | 75685 | 76689 | 78326
13907 | 2021-11-13 | 22:24 | 11.6497 | 75686 | 76684 | 78323
13908 | 2021-11-13 | 22:24 | 11.6497 | 75686 | 76679 | 78321
13909 | 2021-11-13 | 22:24 | 11.6498 | 75686 | 76674 | 78318
13910 | 2021-11-13 | 22:24 | 11.6498 | 75686 | 76669 | 78316
13911 | 2021-11-13 | 22:24 | 11.6498 | 75686 | 76664 | 78314
13912 | 2021-11-13 | 22:24 | 11.6498 | 75686 | 76659 | 78312
13913 | 2021-11-13 | 22:24 | 11.6499 | 75686 | 76654 | 78310
13914 | 2021-11-13 | 22:24 | 11.6499 | 75686 | 76648 | 78308
13915 | 2021-11-13 | 22:24 | 11.6499 | 75686 | 76643 | 78306
13916 | 2021-11-13 | 22:24 | 11.65 | 75686 | 76638 | 78305
13917 | 2021-11-13 | 22:24 | 11.65 | 75686 | 76632 | 78304
13918 | 2021-11-13 | 22:24 | 11.65 | 75686 | 76627 | 78302
13919 | 2021-11-13 | 22:24 | 11.65 | 75686 | 76622 | 78301
13920 | 2021-11-13 | 22:24 | 11.6501 | 75686 | 76617 | 78300
13921 | 2021-11-13 | 22:24 | 11.6501 | 75686 | 76612 | 78299
13922 | 2021-11-13 | 22:24 | 11.6501 | 75686 | 76607 | 78297
13923 | 2021-11-13 | 22:24 | 11.6502 | 75686 | 76603 | 78296
13924 | 2021-11-13 | 22:24 | 11.6502 | 75686 | 76599 | 78294
13925 | 2021-11-13 | 22:24 | 11.6502 | 75686 | 76595 | 78292
13926 | 2021-11-13 | 22:24 | 11.6503 | 75686 | 76592 | 78290
13927 | 2021-11-13 | 22:24 | 11.6503 | 75686 | 76589 | 78287
13928 | 2021-11-13 | 22:24 | 11.6503 | 75686 | 76587 | 78285
13929 | 2021-11-13 | 22:24 | 11.6503 | 75686 | 76585 | 78284
13930 | 2021-11-13 | 22:24 | 11.6504 | 75686 | 76583 | 78282
13931 | 2021-11-13 | 22:24 | 11.6504 | 75686 | 76581 | 78281
13932 | 2021-11-13 | 22:24 | 11.6504 | 75686 | 76580 | 78280
13933 | 2021-11-13 | 22:24 | 11.6505 | 75686 | 76578 | 78280
13934 | 2021-11-13 | 22:24 | 11.6505 | 75686 | 76577 | 78280
13935 | 2021-11-13 | 22:24 | 11.6505 | 75686 | 76577 | 78280
13936 | 2021-11-13 | 22:24 | 11.6505 | 75686 | 76577 | 78281
13937 | 2021-11-13 | 22:24 | 11.6506 | 75686 | 76577 | 78282
13938 | 2021-11-13 | 22:24 | 11.6506 | 75686 | 76578 | 78284
13939 | 2021-11-13 | 22:24 | 11.6506 | 75687 | 76579 | 78285
13940 | 2021-11-13 | 22:24 | 11.6507 | 75687 | 76581 | 78287
13941 | 2021-11-13 | 22:24 | 11.6507 | 75687 | 76583 | 78289
13942 | 2021-11-13 | 22:24 | 11.6507 | 75687 | 76587 | 78291
13943 | 2021-11-13 | 22:24 | 11.6507 | 75687 | 76590 | 78293
13944 | 2021-11-13 | 22:24 | 11.6508 | 75688 | 76594 | 78294
13945 | 2021-11-13 | 22:24 | 11.6508 | 75688 | 76599 | 78296
13946 | 2021-11-13 | 22:24 | 11.6508 | 75689 | 76604 | 78297
13947 | 2021-11-13 | 22:24 | 11.6509 | 75689 | 76610 | 78299
13948 | 2021-11-13 | 22:24 | 11.6509 | 75690 | 76615 | 78301
13949 | 2021-11-13 | 22:24 | 11.6509 | 75691 | 76620 | 78302
13950 | 2021-11-13 | 22:24 | 11.6509 | 75691 | 76625 | 78304
13951 | 2021-11-13 | 22:24 | 11.651 | 75693 | 76631 | 78306
13952 | 2021-11-13 | 22:24 | 11.651 | 75694 | 76635 | 78307
13953 | 2021-11-13 | 22:24 | 11.651 | 75695 | 76640 | 78309
13954 | 2021-11-13 | 22:24 | 11.6511 | 75697 | 76645 | 78311
13955 | 2021-11-13 | 22:24 | 11.6511 | 75699 | 76650 | 78312
13956 | 2021-11-13 | 22:24 | 11.6511 | 75702 | 76655 | 78314
13957 | 2021-11-13 | 22:24 | 11.6511 | 75704 | 76660 | 78315
13958 | 2021-11-13 | 22:24 | 11.6512 | 75707 | 76665 | 78317
13959 | 2021-11-13 | 22:24 | 11.6512 | 75710 | 76671 | 78318
13960 | 2021-11-13 | 22:24 | 11.6512 | 75714 | 76676 | 78320
13961 | 2021-11-13 | 22:24 | 11.6513 | 75717 | 76682 | 78321
13962 | 2021-11-13 | 22:24 | 11.6513 | 75721 | 76688 | 78322
13963 | 2021-11-13 | 22:24 | 11.6513 | 75726 | 76695 | 78323
13964 | 2021-11-13 | 22:24 | 11.6513 | 75730 | 76701 | 78324
13965 | 2021-11-13 | 22:24 | 11.6514 | 75735 | 76709 | 78325
13966 | 2021-11-13 | 22:24 | 11.6514 | 75740 | 76716 | 78326
13967 | 2021-11-13 | 22:24 | 11.6514 | 75745 | 76724 | 78327
13968 | 2021-11-13 | 22:24 | 11.6515 | 75750 | 76732 | 78327
13969 | 2021-11-13 | 22:24 | 11.6515 | 75756 | 76740 | 78328
13970 | 2021-11-13 | 22:24 | 11.6515 | 75762 | 76748 | 78329
13971 | 2021-11-13 | 22:24 | 11.6515 | 75768 | 76757 | 78329
13972 | 2021-11-13 | 22:24 | 11.6516 | 75775 | 76766 | 78329
13973 | 2021-11-13 | 22:24 | 11.6516 | 75782 | 76775 | 78329
13974 | 2021-11-13 | 22:24 | 11.6516 | 75789 | 76784 | 78330
13975 | 2021-11-13 | 22:24 | 11.6517 | 75797 | 76793 | 78330
13976 | 2021-11-13 | 22:24 | 11.6517 | 75805 | 76803 | 78330
13977 | 2021-11-13 | 22:24 | 11.6517 | 75814 | 76813 | 78330
13978 | 2021-11-13 | 22:24 | 11.6517 | 75823 | 76823 | 78329
13979 | 2021-11-13 | 22:24 | 11.6518 | 75833 | 76834 | 78329
13980 | 2021-11-13 | 22:24 | 11.6518 | 75842 | 76844 | 78329
13981 | 2021-11-13 | 22:24 | 11.6518 | 75852 | 76855 | 78329
13982 | 2021-11-13 | 22:24 | 11.6519 | 75862 | 76866 | 78328
13983 | 2021-11-13 | 22:24 | 11.6519 | 75873 | 76877 | 78328
13984 | 2021-11-13 | 22:24 | 11.6519 | 75884 | 76888 | 78328
13985 | 2021-11-13 | 22:24 | 11.6519 | 75895 | 76899 | 78327
13986 | 2021-11-13 | 22:24 | 11.652 | 75906 | 76910 | 78327
13987 | 2021-11-13 | 22:24 | 11.652 | 75918 | 76922 | 78327
13988 | 2021-11-13 | 22:24 | 11.652 | 75930 | 76932 | 78326
13989 | 2021-11-13 | 22:24 | 11.6521 | 75942 | 76943 | 78326
13990 | 2021-11-13 | 22:24 | 11.6521 | 75955 | 76953 | 78326
13991 | 2021-11-13 | 22:24 | 11.6521 | 75969 | 76963 | 78325
13992 | 2021-11-13 | 22:24 | 11.6521 | 75982 | 76973 | 78325
13993 | 2021-11-13 | 22:24 | 11.6522 | 75996 | 76982 | 78325
13994 | 2021-11-13 | 22:24 | 11.6522 | 76010 | 76991 | 78325
13995 | 2021-11-13 | 22:24 | 11.6522 | 76024 | 76999 | 78325
13996 | 2021-11-13 | 22:24 | 11.6523 | 76038 | 77007 | 78325
13997 | 2021-11-13 | 22:24 | 11.6523 | 76053 | 77015 | 78325
13998 | 2021-11-13 | 22:24 | 11.6523 | 76067 | 77021 | 78325
13999 | 2021-11-13 | 22:24 | 11.6523 | 76081 | 77028 | 78325
14000 | 2021-11-13 | 22:24 | 11.6524 | 76096 | 77034 | 78326
14001 | 2021-11-13 | 22:24 | 11.6524 | 76110 | 77040 | 78326
14002 | 2021-11-13 | 22:24 | 11.6524 | 76125 | 77045 | 78327
14003 | 2021-11-13 | 22:24 | 11.6525 | 76140 | 77049 | 78328
14004 | 2021-11-13 | 22:24 | 11.6525 | 76155 | 77054 | 78329
14005 | 2021-11-13 | 22:24 | 11.6525 | 76170 | 77058 | 78330
14006 | 2021-11-13 | 22:24 | 11.6525 | 76185 | 77062 | 78331
14007 | 2021-11-13 | 22:24 | 11.6526 | 76200 | 77065 | 78332
14008 | 2021-11-13 | 22:24 | 11.6526 | 76215 | 77069 | 78333
14009 | 2021-11-13 | 22:24 | 11.6526 | 76231 | 77072 | 78335
14010 | 2021-11-13 | 22:24 | 11.6527 | 76247 | 77075 | 78337
14011 | 2021-11-13 | 22:24 | 11.6527 | 76263 | 77079 | 78339
14012 | 2021-11-13 | 22:24 | 11.6527 | 76279 | 77082 | 78341
14013 | 2021-11-13 | 22:24 | 11.6527 | 76296 | 77085 | 78343
14014 | 2021-11-13 | 22:24 | 11.6528 | 76312 | 77088 | 78346
14015 | 2021-11-13 | 22:24 | 11.6528 | 76329 | 77091 | 78349
14016 | 2021-11-13 | 22:24 | 11.6528 | 76345 | 77094 | 78351
14017 | 2021-11-13 | 22:24 | 11.6529 | 76363 | 77097 | 78355
14018 | 2021-11-13 | 22:24 | 11.6529 | 76380 | 77100 | 78358
14019 | 2021-11-13 | 22:24 | 11.6529 | 76398 | 77104 | 78361
14020 | 2021-11-13 | 22:24 | 11.653 | 76417 | 77106 | 78365
14021 | 2021-11-13 | 22:24 | 11.653 | 76436 | 77110 | 78369
14022 | 2021-11-13 | 22:24 | 11.653 | 76456 | 77113 | 78373
14023 | 2021-11-13 | 22:24 | 11.653 | 76475 | 77116 | 78377
14024 | 2021-11-13 | 22:24 | 11.6531 | 76495 | 77119 | 78381
14025 | 2021-11-13 | 22:24 | 11.6531 | 76515 | 77122 | 78386
14026 | 2021-11-13 | 22:24 | 11.6531 | 76536 | 77125 | 78390
14027 | 2021-11-13 | 22:24 | 11.6532 | 76556 | 77129 | 78395
14028 | 2021-11-13 | 22:24 | 11.6532 | 76577 | 77132 | 78400
14029 | 2021-11-13 | 22:24 | 11.6532 | 76598 | 77136 | 78405
14030 | 2021-11-13 | 22:24 | 11.6532 | 76619 | 77139 | 78410
14031 | 2021-11-13 | 22:24 | 11.6533 | 76640 | 77143 | 78416
14032 | 2021-11-13 | 22:24 | 11.6533 | 76661 | 77147 | 78421
14033 | 2021-11-13 | 22:24 | 11.6533 | 76681 | 77150 | 78427
14034 | 2021-11-13 | 22:24 | 11.6534 | 76702 | 77154 | 78433
14035 | 2021-11-13 | 22:24 | 11.6534 | 76722 | 77157 | 78438
14036 | 2021-11-13 | 22:24 | 11.6534 | 76743 | 77161 | 78445
14037 | 2021-11-13 | 22:24 | 11.6534 | 76763 | 77164 | 78451
14038 | 2021-11-13 | 22:24 | 11.6535 | 76783 | 77167 | 78457
14039 | 2021-11-13 | 22:24 | 11.6535 | 76803 | 77170 | 78464
14040 | 2021-11-13 | 22:24 | 11.6535 | 76823 | 77173 | 78470
14041 | 2021-11-13 | 22:24 | 11.6536 | 76843 | 77176 | 78477
14042 | 2021-11-13 | 22:24 | 11.6536 | 76863 | 77179 | 78484
14043 | 2021-11-13 | 22:24 | 11.6536 | 76882 | 77181 | 78491
14044 | 2021-11-13 | 22:24 | 11.6536 | 76901 | 77184 | 78498
14045 | 2021-11-13 | 22:24 | 11.6537 | 76919 | 77186 | 78504
14046 | 2021-11-13 | 22:24 | 11.6537 | 76937 | 77188 | 78511
14047 | 2021-11-13 | 22:24 | 11.6537 | 76955 | 77190 | 78518
14048 | 2021-11-13 | 22:24 | 11.6538 | 76973 | 77192 | 78525
14049 | 2021-11-13 | 22:24 | 11.6538 | 76990 | 77194 | 78532
14050 | 2021-11-13 | 22:24 | 11.6538 | 77007 | 77196 | 78539
14051 | 2021-11-13 | 22:24 | 11.6538 | 77023 | 77197 | 78546
14052 | 2021-11-13 | 22:24 | 11.6539 | 77039 | 77199 | 78552
14053 | 2021-11-13 | 22:24 | 11.6539 | 77055 | 77200 | 78559
14054 | 2021-11-13 | 22:24 | 11.6539 | 77070 | 77201 | 78566
14055 | 2021-11-13 | 22:24 | 11.654 | 77085 | 77202 | 78572
14056 | 2021-11-13 | 22:24 | 11.654 | 77099 | 77203 | 78579
14057 | 2021-11-13 | 22:24 | 11.654 | 77113 | 77203 | 78585
14058 | 2021-11-13 | 22:24 | 11.654 | 77126 | 77204 | 78592
14059 | 2021-11-13 | 22:24 | 11.6541 | 77140 | 77204 | 78598
14060 | 2021-11-13 | 22:24 | 11.6541 | 77152 | 77205 | 78604
14061 | 2021-11-13 | 22:24 | 11.6541 | 77165 | 77205 | 78610
14062 | 2021-11-13 | 22:24 | 11.6542 | 77177 | 77205 | 78616
14063 | 2021-11-13 | 22:24 | 11.6542 | 77188 | 77206 | 78622
14064 | 2021-11-13 | 22:24 | 11.6542 | 77199 | 77206 | 78628
14065 | 2021-11-13 | 22:24 | 11.6542 | 77210 | 77206 | 78633
14066 | 2021-11-13 | 22:24 | 11.6543 | 77219 | 77206 | 78638
14067 | 2021-11-13 | 22:24 | 11.6543 | 77229 | 77206 | 78643
14068 | 2021-11-13 | 22:24 | 11.6543 | 77238 | 77207 | 78648
14069 | 2021-11-13 | 22:24 | 11.6544 | 77246 | 77207 | 78653
14070 | 2021-11-13 | 22:24 | 11.6544 | 77254 | 77207 | 78658
14071 | 2021-11-13 | 22:24 | 11.6544 | 77261 | 77207 | 78663
14072 | 2021-11-13 | 22:24 | 11.6544 | 77268 | 77207 | 78668
14073 | 2021-11-13 | 22:24 | 11.6545 | 77274 | 77207 | 78672
14074 | 2021-11-13 | 22:24 | 11.6545 | 77280 | 77207 | 78677
14075 | 2021-11-13 | 22:24 | 11.6545 | 77286 | 77207 | 78681
14076 | 2021-11-13 | 22:24 | 11.6546 | 77291 | 77207 | 78685
14077 | 2021-11-13 | 22:24 | 11.6546 | 77296 | 77207 | 78689
14078 | 2021-11-13 | 22:24 | 11.6546 | 77300 | 77207 | 78693
14079 | 2021-11-13 | 22:24 | 11.6546 | 77305 | 77207 | 78697
14080 | 2021-11-13 | 22:24 | 11.6547 | 77309 | 77207 | 78700
14081 | 2021-11-13 | 22:24 | 11.6547 | 77313 | 77207 | 78704
14082 | 2021-11-13 | 22:24 | 11.6547 | 77316 | 77207 | 78708
14083 | 2021-11-13 | 22:24 | 11.6548 | 77320 | 77207 | 78711
14084 | 2021-11-13 | 22:24 | 11.6548 | 77323 | 77207 | 78715
14085 | 2021-11-13 | 22:24 | 11.6548 | 77326 | 77207 | 78719
14086 | 2021-11-13 | 22:24 | 11.6548 | 77329 | 77207 | 78722
14087 | 2021-11-13 | 22:24 | 11.6549 | 77332 | 77207 | 78726
14088 | 2021-11-13 | 22:24 | 11.6549 | 77334 | 77208 | 78730
14089 | 2021-11-13 | 22:24 | 11.6549 | 77337 | 77208 | 78734
14090 | 2021-11-13 | 22:24 | 11.655 | 77339 | 77208 | 78738
14091 | 2021-11-13 | 22:24 | 11.655 | 77342 | 77209 | 78741
14092 | 2021-11-13 | 22:24 | 11.655 | 77344 | 77209 | 78745
14093 | 2021-11-13 | 22:24 | 11.655 | 77346 | 77209 | 78749
14094 | 2021-11-13 | 22:24 | 11.6551 | 77348 | 77210 | 78753
14095 | 2021-11-13 | 22:24 | 11.6551 | 77351 | 77211 | 78757
14096 | 2021-11-13 | 22:24 | 11.6551 | 77353 | 77211 | 78761
14097 | 2021-11-13 | 22:24 | 11.6552 | 77355 | 77212 | 78765
14098 | 2021-11-13 | 22:24 | 11.6552 | 77357 | 77213 | 78769
14099 | 2021-11-13 | 22:24 | 11.6552 | 77359 | 77214 | 78773
14100 | 2021-11-13 | 22:24 | 11.6552 | 77361 | 77215 | 78777
14101 | 2021-11-13 | 22:24 | 11.6553 | 77363 | 77216 | 78781
14102 | 2021-11-13 | 22:24 | 11.6553 | 77365 | 77217 | 78786
14103 | 2021-11-13 | 22:24 | 11.6553 | 77367 | 77218 | 78790
14104 | 2021-11-13 | 22:24 | 11.6554 | 77369 | 77219 | 78794
14105 | 2021-11-13 | 22:24 | 11.6554 | 77370 | 77221 | 78798
14106 | 2021-11-13 | 22:24 | 11.6554 | 77372 | 77222 | 78801
14107 | 2021-11-13 | 22:24 | 11.6554 | 77374 | 77223 | 78805
14108 | 2021-11-13 | 22:24 | 11.6555 | 77375 | 77224 | 78809
14109 | 2021-11-13 | 22:24 | 11.6555 | 77377 | 77225 | 78813
14110 | 2021-11-13 | 22:24 | 11.6555 | 77378 | 77226 | 78816
14111 | 2021-11-13 | 22:24 | 11.6556 | 77380 | 77227 | 78820
14112 | 2021-11-13 | 22:24 | 11.6556 | 77382 | 77228 | 78823
14113 | 2021-11-13 | 22:24 | 11.6556 | 77383 | 77229 | 78827
14114 | 2021-11-13 | 22:24 | 11.6557 | 77385 | 77230 | 78830
14115 | 2021-11-13 | 22:24 | 11.6557 | 77387 | 77230 | 78834
14116 | 2021-11-13 | 22:24 | 11.6557 | 77388 | 77231 | 78837
14117 | 2021-11-13 | 22:24 | 11.6557 | 77390 | 77232 | 78841
14118 | 2021-11-13 | 22:24 | 11.6558 | 77392 | 77233 | 78844
14119 | 2021-11-13 | 22:24 | 11.6558 | 77393 | 77233 | 78847
14120 | 2021-11-13 | 22:24 | 11.6558 | 77395 | 77234 | 78851
14121 | 2021-11-13 | 22:24 | 11.6559 | 77397 | 77235 | 78854
14122 | 2021-11-13 | 22:24 | 11.6559 | 77398 | 77235 | 78857
14123 | 2021-11-13 | 22:24 | 11.6559 | 77400 | 77236 | 78860
14124 | 2021-11-13 | 22:24 | 11.6559 | 77401 | 77236 | 78863
14125 | 2021-11-13 | 22:24 | 11.656 | 77403 | 77236 | 78866
14126 | 2021-11-13 | 22:24 | 11.656 | 77404 | 77237 | 78868
14127 | 2021-11-13 | 22:24 | 11.656 | 77406 | 77237 | 78871
14128 | 2021-11-13 | 22:24 | 11.6561 | 77408 | 77237 | 78874
14129 | 2021-11-13 | 22:24 | 11.6561 | 77409 | 77238 | 78876
14130 | 2021-11-13 | 22:24 | 11.6561 | 77410 | 77238 | 78879
14131 | 2021-11-13 | 22:24 | 11.6561 | 77412 | 77238 | 78882
14132 | 2021-11-13 | 22:24 | 11.6562 | 77413 | 77239 | 78885
14133 | 2021-11-13 | 22:24 | 11.6562 | 77414 | 77240 | 78888
14134 | 2021-11-13 | 22:24 | 11.6562 | 77415 | 77240 | 78890
14135 | 2021-11-13 | 22:24 | 11.6563 | 77416 | 77241 | 78893
14136 | 2021-11-13 | 22:24 | 11.6563 | 77417 | 77243 | 78896
14137 | 2021-11-13 | 22:24 | 11.6563 | 77417 | 77244 | 78899
14138 | 2021-11-13 | 22:24 | 11.6563 | 77418 | 77245 | 78901
14139 | 2021-11-13 | 22:24 | 11.6564 | 77418 | 77247 | 78904
14140 | 2021-11-13 | 22:24 | 11.6564 | 77419 | 77249 | 78906
14141 | 2021-11-13 | 22:24 | 11.6564 | 77419 | 77250 | 78909
14142 | 2021-11-13 | 22:24 | 11.6565 | 77419 | 77252 | 78911
14143 | 2021-11-13 | 22:24 | 11.6565 | 77420 | 77255 | 78914
14144 | 2021-11-13 | 22:24 | 11.6565 | 77420 | 77257 | 78916
14145 | 2021-11-13 | 22:24 | 11.6565 | 77420 | 77259 | 78918
14146 | 2021-11-13 | 22:24 | 11.6566 | 77420 | 77262 | 78921
14147 | 2021-11-13 | 22:24 | 11.6566 | 77420 | 77265 | 78923
14148 | 2021-11-13 | 22:24 | 11.6566 | 77419 | 77268 | 78925
14149 | 2021-11-13 | 22:24 | 11.6567 | 77419 | 77271 | 78926
14150 | 2021-11-13 | 22:24 | 11.6567 | 77419 | 77274 | 78928
14151 | 2021-11-13 | 22:24 | 11.6567 | 77418 | 77278 | 78930
14152 | 2021-11-13 | 22:24 | 11.6567 | 77418 | 77282 | 78931
14153 | 2021-11-13 | 22:24 | 11.6568 | 77417 | 77286 | 78932
14154 | 2021-11-13 | 22:24 | 11.6568 | 77417 | 77291 | 78933
14155 | 2021-11-13 | 22:24 | 11.6568 | 77417 | 77296 | 78934
14156 | 2021-11-13 | 22:24 | 11.6569 | 77416 | 77301 | 78935
14157 | 2021-11-13 | 22:24 | 11.6569 | 77416 | 77306 | 78935
14158 | 2021-11-13 | 22:24 | 11.6569 | 77415 | 77312 | 78936
14159 | 2021-11-13 | 22:24 | 11.6569 | 77415 | 77317 | 78936
14160 | 2021-11-13 | 22:24 | 11.657 | 77414 | 77324 | 78936
14161 | 2021-11-13 | 22:24 | 11.657 | 77414 | 77330 | 78936
14162 | 2021-11-13 | 22:24 | 11.657 | 77414 | 77336 | 78936
14163 | 2021-11-13 | 22:24 | 11.6571 | 77414 | 77343 | 78935
14164 | 2021-11-13 | 22:24 | 11.6571 | 77414 | 77350 | 78935
14165 | 2021-11-13 | 22:24 | 11.6571 | 77414 | 77357 | 78934
14166 | 2021-11-13 | 22:24 | 11.6571 | 77414 | 77365 | 78934
14167 | 2021-11-13 | 22:24 | 11.6572 | 77415 | 77372 | 78932
14168 | 2021-11-13 | 22:24 | 11.6572 | 77415 | 77380 | 78931
14169 | 2021-11-13 | 22:24 | 11.6572 | 77416 | 77388 | 78930
14170 | 2021-11-13 | 22:24 | 11.6573 | 77417 | 77397 | 78927
14171 | 2021-11-13 | 22:24 | 11.6573 | 77418 | 77406 | 78925
14172 | 2021-11-13 | 22:24 | 11.6573 | 77419 | 77415 | 78923
14173 | 2021-11-13 | 22:24 | 11.6573 | 77421 | 77424 | 78921
14174 | 2021-11-13 | 22:24 | 11.6574 | 77423 | 77434 | 78918
14175 | 2021-11-13 | 22:24 | 11.6574 | 77425 | 77444 | 78915
14176 | 2021-11-13 | 22:24 | 11.6574 | 77427 | 77454 | 78913
14177 | 2021-11-13 | 22:24 | 11.6575 | 77429 | 77465 | 78910
14178 | 2021-11-13 | 22:24 | 11.6575 | 77432 | 77476 | 78907
14179 | 2021-11-13 | 22:24 | 11.6575 | 77435 | 77487 | 78904
14180 | 2021-11-13 | 22:24 | 11.6575 | 77438 | 77498 | 78901
14181 | 2021-11-13 | 22:24 | 11.6576 | 77442 | 77510 | 78897
14182 | 2021-11-13 | 22:24 | 11.6576 | 77445 | 77522 | 78894
14183 | 2021-11-13 | 22:24 | 11.6576 | 77449 | 77534 | 78891
14184 | 2021-11-13 | 22:24 | 11.6577 | 77453 | 77546 | 78887
14185 | 2021-11-13 | 22:24 | 11.6577 | 77458 | 77558 | 78884
14186 | 2021-11-13 | 22:24 | 11.6577 | 77462 | 77570 | 78881
14187 | 2021-11-13 | 22:24 | 11.6577 | 77467 | 77582 | 78877
14188 | 2021-11-13 | 22:24 | 11.6578 | 77471 | 77594 | 78874
14189 | 2021-11-13 | 22:24 | 11.6578 | 77476 | 77606 | 78870
14190 | 2021-11-13 | 22:24 | 11.6578 | 77482 | 77618 | 78867
14191 | 2021-11-13 | 22:24 | 11.6579 | 77487 | 77629 | 78864
14192 | 2021-11-13 | 22:24 | 11.6579 | 77492 | 77641 | 78860
14193 | 2021-11-13 | 22:24 | 11.6579 | 77497 | 77652 | 78857
14194 | 2021-11-13 | 22:24 | 11.6579 | 77503 | 77663 | 78854
14195 | 2021-11-13 | 22:24 | 11.658 | 77508 | 77674 | 78850
14196 | 2021-11-13 | 22:24 | 11.658 | 77514 | 77684 | 78847
14197 | 2021-11-13 | 22:24 | 11.658 | 77520 | 77694 | 78844
14198 | 2021-11-13 | 22:24 | 11.6581 | 77525 | 77704 | 78841
14199 | 2021-11-13 | 22:24 | 11.6581 | 77531 | 77714 | 78837
14200 | 2021-11-13 | 22:24 | 11.6581 | 77537 | 77724 | 78834
14201 | 2021-11-13 | 22:24 | 11.6581 | 77543 | 77733 | 78831
14202 | 2021-11-13 | 22:24 | 11.6582 | 77548 | 77743 | 78828
14203 | 2021-11-13 | 22:24 | 11.6582 | 77554 | 77752 | 78824
14204 | 2021-11-13 | 22:24 | 11.6582 | 77560 | 77761 | 78821
14205 | 2021-11-13 | 22:24 | 11.6583 | 77566 | 77770 | 78817
14206 | 2021-11-13 | 22:24 | 11.6583 | 77572 | 77778 | 78814
14207 | 2021-11-13 | 22:24 | 11.6583 | 77578 | 77787 | 78811
14208 | 2021-11-13 | 22:24 | 11.6584 | 77583 | 77796 | 78807
14209 | 2021-11-13 | 22:24 | 11.6584 | 77589 | 77804 | 78804
14210 | 2021-11-13 | 22:24 | 11.6584 | 77595 | 77812 | 78801
14211 | 2021-11-13 | 22:24 | 11.6584 | 77601 | 77820 | 78798
14212 | 2021-11-13 | 22:24 | 11.6585 | 77607 | 77828 | 78795
14213 | 2021-11-13 | 22:24 | 11.6585 | 77613 | 77836 | 78792
14214 | 2021-11-13 | 22:24 | 11.6585 | 77619 | 77844 | 78789
14215 | 2021-11-13 | 22:24 | 11.6586 | 77625 | 77851 | 78786
14216 | 2021-11-13 | 22:24 | 11.6586 | 77631 | 77858 | 78783
14217 | 2021-11-13 | 22:24 | 11.6586 | 77637 | 77866 | 78780
14218 | 2021-11-13 | 22:24 | 11.6586 | 77643 | 77873 | 78777
14219 | 2021-11-13 | 22:24 | 11.6587 | 77649 | 77880 | 78774
14220 | 2021-11-13 | 22:24 | 11.6587 | 77656 | 77886 | 78772
14221 | 2021-11-13 | 22:24 | 11.6587 | 77662 | 77893 | 78769
14222 | 2021-11-13 | 22:24 | 11.6588 | 77669 | 77899 | 78766
14223 | 2021-11-13 | 22:24 | 11.6588 | 77676 | 77906 | 78764
14224 | 2021-11-13 | 22:24 | 11.6588 | 77683 | 77911 | 78761
14225 | 2021-11-13 | 22:24 | 11.6588 | 77690 | 77917 | 78758
14226 | 2021-11-13 | 22:24 | 11.6589 | 77697 | 77923 | 78756
14227 | 2021-11-13 | 22:24 | 11.6589 | 77704 | 77928 | 78753
14228 | 2021-11-13 | 22:24 | 11.6589 | 77712 | 77933 | 78750
14229 | 2021-11-13 | 22:24 | 11.659 | 77720 | 77938 | 78748
14230 | 2021-11-13 | 22:24 | 11.659 | 77729 | 77942 | 78745
14231 | 2021-11-13 | 22:24 | 11.659 | 77737 | 77947 | 78743
14232 | 2021-11-13 | 22:24 | 11.659 | 77746 | 77951 | 78740
14233 | 2021-11-13 | 22:24 | 11.6591 | 77755 | 77955 | 78738
14234 | 2021-11-13 | 22:24 | 11.6591 | 77764 | 77959 | 78735
14235 | 2021-11-13 | 22:24 | 11.6591 | 77774 | 77962 | 78733
14236 | 2021-11-13 | 22:24 | 11.6592 | 77784 | 77965 | 78730
14237 | 2021-11-13 | 22:24 | 11.6592 | 77795 | 77969 | 78728
14238 | 2021-11-13 | 22:24 | 11.6592 | 77806 | 77971 | 78726
14239 | 2021-11-13 | 22:24 | 11.6592 | 77817 | 77974 | 78724
14240 | 2021-11-13 | 22:24 | 11.6593 | 77829 | 77976 | 78722
14241 | 2021-11-13 | 22:24 | 11.6593 | 77841 | 77979 | 78720
14242 | 2021-11-13 | 22:24 | 11.6593 | 77853 | 77980 | 78718
14243 | 2021-11-13 | 22:24 | 11.6594 | 77866 | 77982 | 78716
14244 | 2021-11-13 | 22:24 | 11.6594 | 77879 | 77983 | 78715
14245 | 2021-11-13 | 22:24 | 11.6594 | 77893 | 77984 | 78713
14246 | 2021-11-13 | 22:24 | 11.6594 | 77906 | 77984 | 78712
14247 | 2021-11-13 | 22:24 | 11.6595 | 77920 | 77985 | 78711
14248 | 2021-11-13 | 22:24 | 11.6595 | 77934 | 77985 | 78710
14249 | 2021-11-13 | 22:24 | 11.6595 | 77949 | 77985 | 78710
14250 | 2021-11-13 | 22:24 | 11.6596 | 77964 | 77984 | 78710
14251 | 2021-11-13 | 22:24 | 11.6596 | 77979 | 77984 | 78710
14252 | 2021-11-13 | 22:24 | 11.6596 | 77995 | 77983 | 78710
14253 | 2021-11-13 | 22:24 | 11.6596 | 78010 | 77983 | 78710
14254 | 2021-11-13 | 22:24 | 11.6597 | 78026 | 77982 | 78711
14255 | 2021-11-13 | 22:24 | 11.6597 | 78042 | 77982 | 78712
14256 | 2021-11-13 | 22:24 | 11.6597 | 78058 | 77981 | 78713
14257 | 2021-11-13 | 22:24 | 11.6598 | 78074 | 77980 | 78715
14258 | 2021-11-13 | 22:24 | 11.6598 | 78091 | 77980 | 78717
14259 | 2021-11-13 | 22:24 | 11.6598 | 78107 | 77979 | 78719
14260 | 2021-11-13 | 22:24 | 11.6598 | 78123 | 77978 | 78721
14261 | 2021-11-13 | 22:24 | 11.6599 | 78139 | 77978 | 78724
14262 | 2021-11-13 | 22:24 | 11.6599 | 78155 | 77977 | 78727
14263 | 2021-11-13 | 22:24 | 11.6599 | 78171 | 77976 | 78730
14264 | 2021-11-13 | 22:24 | 11.66 | 78186 | 77975 | 78733
14265 | 2021-11-13 | 22:24 | 11.66 | 78202 | 77974 | 78737
14266 | 2021-11-13 | 22:24 | 11.66 | 78217 | 77973 | 78740
14267 | 2021-11-13 | 22:24 | 11.66 | 78232 | 77972 | 78744
14268 | 2021-11-13 | 22:24 | 11.6601 | 78247 | 77971 | 78748
14269 | 2021-11-13 | 22:24 | 11.6601 | 78262 | 77970 | 78753
14270 | 2021-11-13 | 22:24 | 11.6601 | 78276 | 77969 | 78757
14271 | 2021-11-13 | 22:24 | 11.6602 | 78290 | 77967 | 78762
14272 | 2021-11-13 | 22:24 | 11.6602 | 78304 | 77966 | 78766
14273 | 2021-11-13 | 22:24 | 11.6602 | 78317 | 77965 | 78771
14274 | 2021-11-13 | 22:24 | 11.6602 | 78330 | 77963 | 78776
14275 | 2021-11-13 | 22:24 | 11.6603 | 78343 | 77962 | 78781
14276 | 2021-11-13 | 22:24 | 11.6603 | 78355 | 77960 | 78786
14277 | 2021-11-13 | 22:24 | 11.6603 | 78366 | 77958 | 78791
14278 | 2021-11-13 | 22:24 | 11.6604 | 78377 | 77957 | 78796
14279 | 2021-11-13 | 22:24 | 11.6604 | 78387 | 77955 | 78801
14280 | 2021-11-13 | 22:24 | 11.6604 | 78396 | 77953 | 78806
14281 | 2021-11-13 | 22:24 | 11.6604 | 78405 | 77951 | 78811
14282 | 2021-11-13 | 22:24 | 11.6605 | 78413 | 77949 | 78816
14283 | 2021-11-13 | 22:24 | 11.6605 | 78420 | 77946 | 78821
14284 | 2021-11-13 | 22:24 | 11.6605 | 78427 | 77944 | 78826
14285 | 2021-11-13 | 22:24 | 11.6606 | 78434 | 77942 | 78830
14286 | 2021-11-13 | 22:24 | 11.6606 | 78440 | 77939 | 78835
14287 | 2021-11-13 | 22:24 | 11.6606 | 78446 | 77937 | 78840
14288 | 2021-11-13 | 22:24 | 11.6606 | 78451 | 77934 | 78845
14289 | 2021-11-13 | 22:24 | 11.6607 | 78455 | 77932 | 78849
14290 | 2021-11-13 | 22:24 | 11.6607 | 78459 | 77929 | 78854
14291 | 2021-11-13 | 22:24 | 11.6607 | 78462 | 77926 | 78859
14292 | 2021-11-13 | 22:24 | 11.6608 | 78465 | 77924 | 78863
14293 | 2021-11-13 | 22:24 | 11.6608 | 78467 | 77921 | 78868
14294 | 2021-11-13 | 22:24 | 11.6608 | 78469 | 77918 | 78872
14295 | 2021-11-13 | 22:24 | 11.6608 | 78470 | 77915 | 78876
14296 | 2021-11-13 | 22:24 | 11.6609 | 78471 | 77912 | 78881
14297 | 2021-11-13 | 22:24 | 11.6609 | 78472 | 77909 | 78885
14298 | 2021-11-13 | 22:24 | 11.6609 | 78472 | 77907 | 78890
14299 | 2021-11-13 | 22:24 | 11.661 | 78471 | 77904 | 78894
14300 | 2021-11-13 | 22:24 | 11.661 | 78471 | 77901 | 78898
14301 | 2021-11-13 | 22:24 | 11.661 | 78470 | 77898 | 78902
14302 | 2021-11-13 | 22:24 | 11.6611 | 78468 | 77895 | 78907
14303 | 2021-11-13 | 22:24 | 11.6611 | 78467 | 77892 | 78911
14304 | 2021-11-13 | 22:24 | 11.6611 | 78465 | 77889 | 78915
14305 | 2021-11-13 | 22:24 | 11.6611 | 78462 | 77886 | 78919
14306 | 2021-11-13 | 22:24 | 11.6612 | 78459 | 77883 | 78923
14307 | 2021-11-13 | 22:24 | 11.6612 | 78457 | 77880 | 78928
14308 | 2021-11-13 | 22:24 | 11.6612 | 78454 | 77877 | 78932
14309 | 2021-11-13 | 22:24 | 11.6613 | 78450 | 77874 | 78937
14310 | 2021-11-13 | 22:24 | 11.6613 | 78447 | 77871 | 78942
14311 | 2021-11-13 | 22:24 | 11.6613 | 78444 | 77868 | 78947
14312 | 2021-11-13 | 22:24 | 11.6613 | 78440 | 77865 | 78952
14313 | 2021-11-13 | 22:24 | 11.6614 | 78436 | 77862 | 78957
14314 | 2021-11-13 | 22:24 | 11.6614 | 78433 | 77859 | 78962
14315 | 2021-11-13 | 22:24 | 11.6614 | 78429 | 77857 | 78968
14316 | 2021-11-13 | 22:24 | 11.6615 | 78425 | 77854 | 78974
14317 | 2021-11-13 | 22:24 | 11.6615 | 78422 | 77851 | 78979
14318 | 2021-11-13 | 22:24 | 11.6615 | 78418 | 77849 | 78985
14319 | 2021-11-13 | 22:24 | 11.6615 | 78414 | 77846 | 78992
14320 | 2021-11-13 | 22:24 | 11.6616 | 78410 | 77844 | 78998
14321 | 2021-11-13 | 22:24 | 11.6616 | 78405 | 77842 | 79004
14322 | 2021-11-13 | 22:24 | 11.6616 | 78401 | 77840 | 79010
14323 | 2021-11-13 | 22:24 | 11.6617 | 78397 | 77838 | 79017
14324 | 2021-11-13 | 22:24 | 11.6617 | 78392 | 77836 | 79023
14325 | 2021-11-13 | 22:24 | 11.6617 | 78388 | 77834 | 79030
14326 | 2021-11-13 | 22:24 | 11.6617 | 78383 | 77833 | 79036
14327 | 2021-11-13 | 22:24 | 11.6618 | 78379 | 77831 | 79043
14328 | 2021-11-13 | 22:24 | 11.6618 | 78375 | 77830 | 79050
14329 | 2021-11-13 | 22:24 | 11.6618 | 78370 | 77829 | 79057
14330 | 2021-11-13 | 22:24 | 11.6619 | 78366 | 77828 | 79064
14331 | 2021-11-13 | 22:24 | 11.6619 | 78361 | 77828 | 79071
14332 | 2021-11-13 | 22:24 | 11.6619 | 78356 | 77827 | 79078
14333 | 2021-11-13 | 22:24 | 11.6619 | 78351 | 77827 | 79084
14334 | 2021-11-13 | 22:24 | 11.662 | 78346 | 77827 | 79091
14335 | 2021-11-13 | 22:24 | 11.662 | 78341 | 77827 | 79097
14336 | 2021-11-13 | 22:24 | 11.662 | 78335 | 77827 | 79104
14337 | 2021-11-13 | 22:24 | 11.6621 | 78330 | 77827 | 79110
14338 | 2021-11-13 | 22:24 | 11.6621 | 78324 | 77827 | 79116
14339 | 2021-11-13 | 22:24 | 11.6621 | 78318 | 77828 | 79121
14340 | 2021-11-13 | 22:24 | 11.6621 | 78312 | 77829 | 79127
14341 | 2021-11-13 | 22:24 | 11.6622 | 78306 | 77830 | 79132
14342 | 2021-11-13 | 22:24 | 11.6622 | 78299 | 77831 | 79137
14343 | 2021-11-13 | 22:24 | 11.6622 | 78293 | 77832 | 79141
14344 | 2021-11-13 | 22:24 | 11.6623 | 78286 | 77833 | 79145
14345 | 2021-11-13 | 22:24 | 11.6623 | 78279 | 77835 | 79149
14346 | 2021-11-13 | 22:24 | 11.6623 | 78272 | 77836 | 79153
14347 | 2021-11-13 | 22:24 | 11.6623 | 78265 | 77838 | 79156
14348 | 2021-11-13 | 22:24 | 11.6624 | 78258 | 77839 | 79159
14349 | 2021-11-13 | 22:24 | 11.6624 | 78251 | 77841 | 79161
14350 | 2021-11-13 | 22:24 | 11.6624 | 78244 | 77842 | 79163
14351 | 2021-11-13 | 22:24 | 11.6625 | 78236 | 77844 | 79165
14352 | 2021-11-13 | 22:24 | 11.6625 | 78229 | 77846 | 79167
14353 | 2021-11-13 | 22:24 | 11.6625 | 78222 | 77848 | 79168
14354 | 2021-11-13 | 22:24 | 11.6625 | 78214 | 77849 | 79169
14355 | 2021-11-13 | 22:24 | 11.6626 | 78207 | 77851 | 79169
14356 | 2021-11-13 | 22:24 | 11.6626 | 78199 | 77853 | 79170
14357 | 2021-11-13 | 22:24 | 11.6626 | 78192 | 77855 | 79170
14358 | 2021-11-13 | 22:24 | 11.6627 | 78185 | 77857 | 79169
14359 | 2021-11-13 | 22:24 | 11.6627 | 78177 | 77859 | 79169
14360 | 2021-11-13 | 22:24 | 11.6627 | 78170 | 77861 | 79168
14361 | 2021-11-13 | 22:24 | 11.6627 | 78163 | 77862 | 79167
14362 | 2021-11-13 | 22:24 | 11.6628 | 78155 | 77864 | 79165
14363 | 2021-11-13 | 22:24 | 11.6628 | 78148 | 77866 | 79163
14364 | 2021-11-13 | 22:24 | 11.6628 | 78141 | 77868 | 79160
14365 | 2021-11-13 | 22:24 | 11.6629 | 78134 | 77870 | 79157
14366 | 2021-11-13 | 22:24 | 11.6629 | 78127 | 77872 | 79153
14367 | 2021-11-13 | 22:24 | 11.6629 | 78120 | 77874 | 79150
14368 | 2021-11-13 | 22:24 | 11.6629 | 78113 | 77876 | 79145
14369 | 2021-11-13 | 22:24 | 11.663 | 78107 | 77878 | 79141
14370 | 2021-11-13 | 22:24 | 11.663 | 78100 | 77880 | 79136
14371 | 2021-11-13 | 22:24 | 11.663 | 78094 | 77882 | 79132
14372 | 2021-11-13 | 22:24 | 11.6631 | 78087 | 77884 | 79127
14373 | 2021-11-13 | 22:24 | 11.6631 | 78081 | 77886 | 79122
14374 | 2021-11-13 | 22:24 | 11.6631 | 78075 | 77888 | 79117
14375 | 2021-11-13 | 22:24 | 11.6631 | 78069 | 77891 | 79112
14376 | 2021-11-13 | 22:24 | 11.6632 | 78063 | 77893 | 79107
14377 | 2021-11-13 | 22:24 | 11.6632 | 78057 | 77896 | 79102
14378 | 2021-11-13 | 22:24 | 11.6632 | 78051 | 77898 | 79096
14379 | 2021-11-13 | 22:24 | 11.6633 | 78046 | 77901 | 79091
14380 | 2021-11-13 | 22:24 | 11.6633 | 78040 | 77903 | 79085
14381 | 2021-11-13 | 22:24 | 11.6633 | 78034 | 77906 | 79080
14382 | 2021-11-13 | 22:24 | 11.6633 | 78029 | 77909 | 79074
14383 | 2021-11-13 | 22:24 | 11.6634 | 78024 | 77911 | 79068
14384 | 2021-11-13 | 22:24 | 11.6634 | 78019 | 77913 | 79063
14385 | 2021-11-13 | 22:24 | 11.6634 | 78014 | 77916 | 79058
14386 | 2021-11-13 | 22:24 | 11.6635 | 78009 | 77919 | 79053
14387 | 2021-11-13 | 22:24 | 11.6635 | 78004 | 77921 | 79048
14388 | 2021-11-13 | 22:24 | 11.6635 | 78000 | 77924 | 79042
14389 | 2021-11-13 | 22:24 | 11.6635 | 77995 | 77927 | 79037
14390 | 2021-11-13 | 22:24 | 11.6636 | 77991 | 77930 | 79033
14391 | 2021-11-13 | 22:24 | 11.6636 | 77987 | 77933 | 79028
14392 | 2021-11-13 | 22:24 | 11.6636 | 77983 | 77936 | 79023
14393 | 2021-11-13 | 22:24 | 11.6637 | 77978 | 77940 | 79019
14394 | 2021-11-13 | 22:24 | 11.6637 | 77974 | 77943 | 79014
14395 | 2021-11-13 | 22:24 | 11.6637 | 77971 | 77947 | 79010
14396 | 2021-11-13 | 22:24 | 11.6638 | 77967 | 77951 | 79006
14397 | 2021-11-13 | 22:24 | 11.6638 | 77963 | 77954 | 79003
14398 | 2021-11-13 | 22:24 | 11.6638 | 77960 | 77958 | 78999
14399 | 2021-11-13 | 22:24 | 11.6638 | 77956 | 77962 | 78995
14400 | 2021-11-13 | 22:24 | 11.6639 | 77953 | 77966 | 78991
14401 | 2021-11-13 | 22:24 | 11.6639 | 77950 | 77971 | 78987
14402 | 2021-11-13 | 22:24 | 11.6639 | 77947 | 77975 | 78983
14403 | 2021-11-13 | 22:24 | 11.664 | 77944 | 77980 | 78979
14404 | 2021-11-13 | 22:24 | 11.664 | 77942 | 77984 | 78976
14405 | 2021-11-13 | 22:24 | 11.664 | 77939 | 77989 | 78972
14406 | 2021-11-13 | 22:24 | 11.664 | 77937 | 77994 | 78968
14407 | 2021-11-13 | 22:24 | 11.6641 | 77934 | 78000 | 78965
14408 | 2021-11-13 | 22:24 | 11.6641 | 77932 | 78005 | 78961
14409 | 2021-11-13 | 22:24 | 11.6641 | 77930 | 78011 | 78957
14410 | 2021-11-13 | 22:24 | 11.6642 | 77928 | 78016 | 78953
14411 | 2021-11-13 | 22:24 | 11.6642 | 77927 | 78022 | 78948
14412 | 2021-11-13 | 22:24 | 11.6642 | 77925 | 78028 | 78944
14413 | 2021-11-13 | 22:24 | 11.6642 | 77924 | 78034 | 78940
14414 | 2021-11-13 | 22:24 | 11.6643 | 77923 | 78041 | 78936
14415 | 2021-11-13 | 22:24 | 11.6643 | 77922 | 78047 | 78933
14416 | 2021-11-13 | 22:24 | 11.6643 | 77921 | 78054 | 78929
14417 | 2021-11-13 | 22:24 | 11.6644 | 77920 | 78061 | 78925
14418 | 2021-11-13 | 22:24 | 11.6644 | 77919 | 78068 | 78921
14419 | 2021-11-13 | 22:24 | 11.6644 | 77919 | 78075 | 78918
14420 | 2021-11-13 | 22:24 | 11.6644 | 77919 | 78082 | 78914
14421 | 2021-11-13 | 22:24 | 11.6645 | 77919 | 78089 | 78910
14422 | 2021-11-13 | 22:24 | 11.6645 | 77919 | 78097 | 78907
14423 | 2021-11-13 | 22:24 | 11.6645 | 77919 | 78104 | 78903
14424 | 2021-11-13 | 22:24 | 11.6646 | 77920 | 78112 | 78899
14425 | 2021-11-13 | 22:24 | 11.6646 | 77920 | 78119 | 78895
14426 | 2021-11-13 | 22:24 | 11.6646 | 77921 | 78126 | 78891
14427 | 2021-11-13 | 22:24 | 11.6646 | 77922 | 78134 | 78887
14428 | 2021-11-13 | 22:24 | 11.6647 | 77924 | 78141 | 78883
14429 | 2021-11-13 | 22:24 | 11.6647 | 77925 | 78148 | 78879
14430 | 2021-11-13 | 22:24 | 11.6647 | 77927 | 78156 | 78874
14431 | 2021-11-13 | 22:24 | 11.6648 | 77928 | 78163 | 78870
14432 | 2021-11-13 | 22:24 | 11.6648 | 77930 | 78170 | 78865
14433 | 2021-11-13 | 22:24 | 11.6648 | 77932 | 78178 | 78860
14434 | 2021-11-13 | 22:24 | 11.6648 | 77935 | 78185 | 78856
14435 | 2021-11-13 | 22:24 | 11.6649 | 77937 | 78193 | 78851
14436 | 2021-11-13 | 22:24 | 11.6649 | 77940 | 78200 | 78847
14437 | 2021-11-13 | 22:24 | 11.6649 | 77943 | 78207 | 78842
14438 | 2021-11-13 | 22:24 | 11.665 | 77946 | 78215 | 78837
14439 | 2021-11-13 | 22:24 | 11.665 | 77949 | 78222 | 78832
14440 | 2021-11-13 | 22:24 | 11.665 | 77952 | 78228 | 78827
14441 | 2021-11-13 | 22:24 | 11.665 | 77956 | 78235 | 78822
14442 | 2021-11-13 | 22:24 | 11.6651 | 77960 | 78242 | 78817
14443 | 2021-11-13 | 22:24 | 11.6651 | 77964 | 78248 | 78811
14444 | 2021-11-13 | 22:24 | 11.6651 | 77968 | 78254 | 78806
14445 | 2021-11-13 | 22:24 | 11.6652 | 77972 | 78260 | 78800
14446 | 2021-11-13 | 22:24 | 11.6652 | 77976 | 78265 | 78795
14447 | 2021-11-13 | 22:24 | 11.6652 | 77981 | 78270 | 78789
14448 | 2021-11-13 | 22:24 | 11.6652 | 77985 | 78274 | 78783
14449 | 2021-11-13 | 22:24 | 11.6653 | 77990 | 78279 | 78777
14450 | 2021-11-13 | 22:24 | 11.6653 | 77995 | 78283 | 78771
14451 | 2021-11-13 | 22:24 | 11.6653 | 78000 | 78287 | 78765
14452 | 2021-11-13 | 22:24 | 11.6654 | 78005 | 78290 | 78758
14453 | 2021-11-13 | 22:24 | 11.6654 | 78011 | 78294 | 78752
14454 | 2021-11-13 | 22:24 | 11.6654 | 78016 | 78297 | 78745
14455 | 2021-11-13 | 22:24 | 11.6654 | 78022 | 78300 | 78739
14456 | 2021-11-13 | 22:24 | 11.6655 | 78027 | 78303 | 78732
14457 | 2021-11-13 | 22:24 | 11.6655 | 78033 | 78305 | 78726
14458 | 2021-11-13 | 22:24 | 11.6655 | 78039 | 78307 | 78719
14459 | 2021-11-13 | 22:24 | 11.6656 | 78045 | 78309 | 78712
14460 | 2021-11-13 | 22:24 | 11.6656 | 78051 | 78310 | 78706
14461 | 2021-11-13 | 22:24 | 11.6656 | 78057 | 78311 | 78699
14462 | 2021-11-13 | 22:24 | 11.6656 | 78063 | 78312 | 78692
14463 | 2021-11-13 | 22:24 | 11.6657 | 78070 | 78312 | 78686
14464 | 2021-11-13 | 22:24 | 11.6657 | 78076 | 78313 | 78679
14465 | 2021-11-13 | 22:24 | 11.6657 | 78083 | 78313 | 78672
14466 | 2021-11-13 | 22:24 | 11.6658 | 78090 | 78313 | 78666
14467 | 2021-11-13 | 22:24 | 11.6658 | 78096 | 78313 | 78659
14468 | 2021-11-13 | 22:24 | 11.6658 | 78103 | 78313 | 78653
14469 | 2021-11-13 | 22:24 | 11.6658 | 78110 | 78312 | 78647
14470 | 2021-11-13 | 22:24 | 11.6659 | 78117 | 78311 | 78640
14471 | 2021-11-13 | 22:24 | 11.6659 | 78124 | 78310 | 78634
14472 | 2021-11-13 | 22:24 | 11.6659 | 78131 | 78309 | 78629
14473 | 2021-11-13 | 22:24 | 11.666 | 78138 | 78307 | 78623
14474 | 2021-11-13 | 22:24 | 11.666 | 78145 | 78306 | 78617
14475 | 2021-11-13 | 22:24 | 11.666 | 78152 | 78304 | 78612
14476 | 2021-11-13 | 22:24 | 11.666 | 78159 | 78302 | 78606
14477 | 2021-11-13 | 22:24 | 11.6661 | 78166 | 78299 | 78601
14478 | 2021-11-13 | 22:24 | 11.6661 | 78174 | 78297 | 78596
14479 | 2021-11-13 | 22:24 | 11.6661 | 78181 | 78294 | 78591
14480 | 2021-11-13 | 22:24 | 11.6662 | 78188 | 78291 | 78587
14481 | 2021-11-13 | 22:24 | 11.6662 | 78196 | 78288 | 78582
14482 | 2021-11-13 | 22:24 | 11.6662 | 78204 | 78284 | 78578
14483 | 2021-11-13 | 22:24 | 11.6662 | 78211 | 78281 | 78574
14484 | 2021-11-13 | 22:24 | 11.6663 | 78219 | 78277 | 78570
14485 | 2021-11-13 | 22:24 | 11.6663 | 78227 | 78273 | 78567
14486 | 2021-11-13 | 22:24 | 11.6663 | 78234 | 78269 | 78563
14487 | 2021-11-13 | 22:24 | 11.6664 | 78242 | 78264 | 78560
14488 | 2021-11-13 | 22:24 | 11.6664 | 78249 | 78259 | 78557
14489 | 2021-11-13 | 22:24 | 11.6664 | 78256 | 78254 | 78554
14490 | 2021-11-13 | 22:24 | 11.6665 | 78264 | 78248 | 78551
14491 | 2021-11-13 | 22:24 | 11.6665 | 78271 | 78242 | 78549
14492 | 2021-11-13 | 22:24 | 11.6665 | 78279 | 78236 | 78546
14493 | 2021-11-13 | 22:24 | 11.6665 | 78286 | 78230 | 78544
14494 | 2021-11-13 | 22:24 | 11.6666 | 78294 | 78223 | 78542
14495 | 2021-11-13 | 22:24 | 11.6666 | 78302 | 78216 | 78540
14496 | 2021-11-13 | 22:24 | 11.6666 | 78309 | 78210 | 78538
14497 | 2021-11-13 | 22:24 | 11.6667 | 78317 | 78203 | 78537
14498 | 2021-11-13 | 22:24 | 11.6667 | 78325 | 78195 | 78536
14499 | 2021-11-13 | 22:24 | 11.6667 | 78333 | 78188 | 78534
14500 | 2021-11-13 | 22:24 | 11.6667 | 78340 | 78181 | 78533
14501 | 2021-11-13 | 22:24 | 11.6668 | 78347 | 78173 | 78533
14502 | 2021-11-13 | 22:24 | 11.6668 | 78354 | 78166 | 78532
14503 | 2021-11-13 | 22:24 | 11.6668 | 78361 | 78158 | 78532
14504 | 2021-11-13 | 22:24 | 11.6669 | 78368 | 78151 | 78531
14505 | 2021-11-13 | 22:24 | 11.6669 | 78375 | 78144 | 78531
14506 | 2021-11-13 | 22:24 | 11.6669 | 78383 | 78137 | 78532
14507 | 2021-11-13 | 22:24 | 11.6669 | 78390 | 78131 | 78532
14508 | 2021-11-13 | 22:24 | 11.667 | 78397 | 78124 | 78532
14509 | 2021-11-13 | 22:24 | 11.667 | 78405 | 78118 | 78533
14510 | 2021-11-13 | 22:24 | 11.667 | 78412 | 78112 | 78534
14511 | 2021-11-13 | 22:24 | 11.6671 | 78420 | 78107 | 78535
14512 | 2021-11-13 | 22:24 | 11.6671 | 78427 | 78101 | 78536
14513 | 2021-11-13 | 22:24 | 11.6671 | 78434 | 78095 | 78537
14514 | 2021-11-13 | 22:24 | 11.6671 | 78440 | 78090 | 78539
14515 | 2021-11-13 | 22:24 | 11.6672 | 78446 | 78085 | 78541
14516 | 2021-11-13 | 22:24 | 11.6672 | 78452 | 78079 | 78542
14517 | 2021-11-13 | 22:24 | 11.6672 | 78458 | 78074 | 78544
14518 | 2021-11-13 | 22:24 | 11.6673 | 78463 | 78069 | 78546
14519 | 2021-11-13 | 22:24 | 11.6673 | 78469 | 78064 | 78548
14520 | 2021-11-13 | 22:24 | 11.6673 | 78474 | 78059 | 78551
14521 | 2021-11-13 | 22:24 | 11.6673 | 78478 | 78053 | 78553
14522 | 2021-11-13 | 22:24 | 11.6674 | 78483 | 78048 | 78556
14523 | 2021-11-13 | 22:24 | 11.6674 | 78488 | 78043 | 78558
14524 | 2021-11-13 | 22:24 | 11.6674 | 78492 | 78038 | 78561
14525 | 2021-11-13 | 22:24 | 11.6675 | 78497 | 78032 | 78564
14526 | 2021-11-13 | 22:24 | 11.6675 | 78501 | 78027 | 78567
14527 | 2021-11-13 | 22:24 | 11.6675 | 78505 | 78022 | 78570
14528 | 2021-11-13 | 22:24 | 11.6675 | 78508 | 78016 | 78573
14529 | 2021-11-13 | 22:24 | 11.6676 | 78512 | 78011 | 78576
14530 | 2021-11-13 | 22:24 | 11.6676 | 78514 | 78005 | 78579
14531 | 2021-11-13 | 22:24 | 11.6676 | 78517 | 77999 | 78583
14532 | 2021-11-13 | 22:24 | 11.6677 | 78518 | 77993 | 78586
14533 | 2021-11-13 | 22:24 | 11.6677 | 78519 | 77987 | 78589
14534 | 2021-11-13 | 22:24 | 11.6677 | 78520 | 77981 | 78592
14535 | 2021-11-13 | 22:24 | 11.6677 | 78520 | 77975 | 78595
14536 | 2021-11-13 | 22:24 | 11.6678 | 78520 | 77969 | 78598
14537 | 2021-11-13 | 22:24 | 11.6678 | 78520 | 77962 | 78602
14538 | 2021-11-13 | 22:24 | 11.6678 | 78520 | 77956 | 78605
14539 | 2021-11-13 | 22:24 | 11.6679 | 78520 | 77950 | 78609
14540 | 2021-11-13 | 22:24 | 11.6679 | 78519 | 77944 | 78613
14541 | 2021-11-13 | 22:24 | 11.6679 | 78518 | 77938 | 78616
14542 | 2021-11-13 | 22:24 | 11.6679 | 78516 | 77932 | 78620
14543 | 2021-11-13 | 22:24 | 11.668 | 78514 | 77926 | 78623
14544 | 2021-11-13 | 22:24 | 11.668 | 78511 | 77920 | 78627
14545 | 2021-11-13 | 22:24 | 11.668 | 78509 | 77914 | 78630
14546 | 2021-11-13 | 22:24 | 11.6681 | 78505 | 77908 | 78633
14547 | 2021-11-13 | 22:24 | 11.6681 | 78502 | 77902 | 78637
14548 | 2021-11-13 | 22:24 | 11.6681 | 78499 | 77896 | 78640
14549 | 2021-11-13 | 22:24 | 11.6681 | 78495 | 77891 | 78644
14550 | 2021-11-13 | 22:24 | 11.6682 | 78492 | 77885 | 78647
14551 | 2021-11-13 | 22:24 | 11.6682 | 78488 | 77879 | 78651
14552 | 2021-11-13 | 22:24 | 11.6682 | 78484 | 77874 | 78655
14553 | 2021-11-13 | 22:24 | 11.6683 | 78479 | 77868 | 78659
14554 | 2021-11-13 | 22:24 | 11.6683 | 78475 | 77863 | 78662
14555 | 2021-11-13 | 22:24 | 11.6683 | 78470 | 77858 | 78666
14556 | 2021-11-13 | 22:24 | 11.6683 | 78465 | 77853 | 78670
14557 | 2021-11-13 | 22:24 | 11.6684 | 78460 | 77848 | 78673
14558 | 2021-11-13 | 22:24 | 11.6684 | 78455 | 77843 | 78677
14559 | 2021-11-13 | 22:24 | 11.6684 | 78449 | 77838 | 78680
14560 | 2021-11-13 | 22:24 | 11.6685 | 78443 | 77834 | 78684
14561 | 2021-11-13 | 22:24 | 11.6685 | 78437 | 77829 | 78687
14562 | 2021-11-13 | 22:24 | 11.6685 | 78431 | 77825 | 78691
14563 | 2021-11-13 | 22:24 | 11.6685 | 78424 | 77820 | 78694
14564 | 2021-11-13 | 22:24 | 11.6686 | 78418 | 77816 | 78697
14565 | 2021-11-13 | 22:24 | 11.6686 | 78411 | 77812 | 78701
14566 | 2021-11-13 | 22:24 | 11.6686 | 78405 | 77808 | 78704
14567 | 2021-11-13 | 22:24 | 11.6687 | 78398 | 77805 | 78708
14568 | 2021-11-13 | 22:24 | 11.6687 | 78392 | 77801 | 78712
14569 | 2021-11-13 | 22:24 | 11.6687 | 78386 | 77798 | 78716
14570 | 2021-11-13 | 22:24 | 11.6687 | 78381 | 77795 | 78720
14571 | 2021-11-13 | 22:24 | 11.6688 | 78375 | 77792 | 78723
14572 | 2021-11-13 | 22:24 | 11.6688 | 78369 | 77789 | 78728
14573 | 2021-11-13 | 22:24 | 11.6688 | 78362 | 77786 | 78731
14574 | 2021-11-13 | 22:24 | 11.6689 | 78356 | 77784 | 78735
14575 | 2021-11-13 | 22:24 | 11.6689 | 78350 | 77781 | 78739
14576 | 2021-11-13 | 22:24 | 11.6689 | 78344 | 77779 | 78743
14577 | 2021-11-13 | 22:24 | 11.6689 | 78337 | 77777 | 78747
14578 | 2021-11-13 | 22:24 | 11.669 | 78331 | 77775 | 78750
14579 | 2021-11-13 | 22:24 | 11.669 | 78325 | 77774 | 78754
14580 | 2021-11-13 | 22:24 | 11.669 | 78319 | 77772 | 78758
14581 | 2021-11-13 | 22:24 | 11.6691 | 78313 | 77771 | 78762
14582 | 2021-11-13 | 22:24 | 11.6691 | 78307 | 77770 | 78766
14583 | 2021-11-13 | 22:24 | 11.6691 | 78302 | 77769 | 78770
14584 | 2021-11-13 | 22:24 | 11.6692 | 78297 | 77769 | 78774
14585 | 2021-11-13 | 22:24 | 11.6692 | 78292 | 77768 | 78779
14586 | 2021-11-13 | 22:24 | 11.6692 | 78286 | 77768 | 78783
14587 | 2021-11-13 | 22:24 | 11.6692 | 78281 | 77768 | 78787
14588 | 2021-11-13 | 22:24 | 11.6693 | 78276 | 77767 | 78791
14589 | 2021-11-13 | 22:24 | 11.6693 | 78271 | 77768 | 78795
14590 | 2021-11-13 | 22:24 | 11.6693 | 78266 | 77768 | 78799
14591 | 2021-11-13 | 22:24 | 11.6694 | 78261 | 77768 | 78803
14592 | 2021-11-13 | 22:24 | 11.6694 | 78256 | 77769 | 78807
14593 | 2021-11-13 | 22:24 | 11.6694 | 78251 | 77769 | 78810
14594 | 2021-11-13 | 22:24 | 11.6694 | 78246 | 77770 | 78814
14595 | 2021-11-13 | 22:24 | 11.6695 | 78241 | 77771 | 78817
14596 | 2021-11-13 | 22:24 | 11.6695 | 78236 | 77772 | 78821
14597 | 2021-11-13 | 22:24 | 11.6695 | 78231 | 77773 | 78824
14598 | 2021-11-13 | 22:24 | 11.6696 | 78226 | 77774 | 78827
14599 | 2021-11-13 | 22:24 | 11.6696 | 78222 | 77776 | 78830
14600 | 2021-11-13 | 22:24 | 11.6696 | 78217 | 77777 | 78832
14601 | 2021-11-13 | 22:24 | 11.6696 | 78212 | 77779 | 78835
14602 | 2021-11-13 | 22:24 | 11.6697 | 78208 | 77780 | 78837
14603 | 2021-11-13 | 22:24 | 11.6697 | 78203 | 77782 | 78839
14604 | 2021-11-13 | 22:24 | 11.6697 | 78198 | 77784 | 78841
14605 | 2021-11-13 | 22:24 | 11.6698 | 78193 | 77786 | 78843
14606 | 2021-11-13 | 22:24 | 11.6698 | 78188 | 77787 | 78844
14607 | 2021-11-13 | 22:24 | 11.6698 | 78183 | 77789 | 78845
14608 | 2021-11-13 | 22:24 | 11.6698 | 78178 | 77791 | 78846
14609 | 2021-11-13 | 22:24 | 11.6699 | 78173 | 77793 | 78847
14610 | 2021-11-13 | 22:24 | 11.6699 | 78168 | 77795 | 78848
14611 | 2021-11-13 | 22:24 | 11.6699 | 78163 | 77797 | 78848
14612 | 2021-11-13 | 22:24 | 11.67 | 78158 | 77799 | 78848
14613 | 2021-11-13 | 22:24 | 11.67 | 78152 | 77801 | 78848
14614 | 2021-11-13 | 22:24 | 11.67 | 78147 | 77803 | 78848
14615 | 2021-11-13 | 22:24 | 11.67 | 78142 | 77806 | 78848
14616 | 2021-11-13 | 22:24 | 11.6701 | 78136 | 77808 | 78847
14617 | 2021-11-13 | 22:24 | 11.6701 | 78131 | 77810 | 78846
14618 | 2021-11-13 | 22:24 | 11.6701 | 78125 | 77813 | 78845
14619 | 2021-11-13 | 22:24 | 11.6702 | 78119 | 77815 | 78843
14620 | 2021-11-13 | 22:24 | 11.6702 | 78114 | 77818 | 78841
14621 | 2021-11-13 | 22:24 | 11.6702 | 78108 | 77820 | 78839
14622 | 2021-11-13 | 22:24 | 11.6702 | 78101 | 77823 | 78836
14623 | 2021-11-13 | 22:24 | 11.6703 | 78095 | 77826 | 78833
14624 | 2021-11-13 | 22:24 | 11.6703 | 78089 | 77828 | 78830
14625 | 2021-11-13 | 22:24 | 11.6703 | 78083 | 77831 | 78826
14626 | 2021-11-13 | 22:24 | 11.6704 | 78076 | 77834 | 78823
14627 | 2021-11-13 | 22:24 | 11.6704 | 78070 | 77837 | 78819
14628 | 2021-11-13 | 22:24 | 11.6704 | 78063 | 77841 | 78815
14629 | 2021-11-13 | 22:24 | 11.6704 | 78057 | 77844 | 78811
14630 | 2021-11-13 | 22:24 | 11.6705 | 78050 | 77848 | 78807
14631 | 2021-11-13 | 22:24 | 11.6705 | 78044 | 77851 | 78802
14632 | 2021-11-13 | 22:24 | 11.6705 | 78037 | 77855 | 78797
14633 | 2021-11-13 | 22:24 | 11.6706 | 78031 | 77859 | 78792
14634 | 2021-11-13 | 22:24 | 11.6706 | 78024 | 77863 | 78787
14635 | 2021-11-13 | 22:24 | 11.6706 | 78017 | 77867 | 78782
14636 | 2021-11-13 | 22:24 | 11.6706 | 78011 | 77871 | 78776
14637 | 2021-11-13 | 22:24 | 11.6707 | 78004 | 77875 | 78771
14638 | 2021-11-13 | 22:24 | 11.6707 | 77997 | 77880 | 78765
14639 | 2021-11-13 | 22:24 | 11.6707 | 77991 | 77884 | 78759
14640 | 2021-11-13 | 22:24 | 11.6708 | 77984 | 77889 | 78753
14641 | 2021-11-13 | 22:24 | 11.6708 | 77978 | 77894 | 78747
14642 | 2021-11-13 | 22:24 | 11.6708 | 77972 | 77899 | 78740
14643 | 2021-11-13 | 22:24 | 11.6708 | 77966 | 77904 | 78734
14644 | 2021-11-13 | 22:24 | 11.6709 | 77960 | 77909 | 78728
14645 | 2021-11-13 | 22:24 | 11.6709 | 77954 | 77915 | 78722
14646 | 2021-11-13 | 22:24 | 11.6709 | 77948 | 77920 | 78716
14647 | 2021-11-13 | 22:24 | 11.671 | 77943 | 77926 | 78709
14648 | 2021-11-13 | 22:24 | 11.671 | 77938 | 77932 | 78703
14649 | 2021-11-13 | 22:24 | 11.671 | 77932 | 77938 | 78697
14650 | 2021-11-13 | 22:24 | 11.671 | 77927 | 77944 | 78690
14651 | 2021-11-13 | 22:24 | 11.6711 | 77923 | 77950 | 78684
14652 | 2021-11-13 | 22:24 | 11.6711 | 77918 | 77957 | 78678
14653 | 2021-11-13 | 22:24 | 11.6711 | 77914 | 77963 | 78671
14654 | 2021-11-13 | 22:24 | 11.6712 | 77909 | 77969 | 78665
14655 | 2021-11-13 | 22:24 | 11.6712 | 77906 | 77976 | 78658
14656 | 2021-11-13 | 22:24 | 11.6712 | 77902 | 77983 | 78652
14657 | 2021-11-13 | 22:24 | 11.6712 | 77898 | 77989 | 78645
14658 | 2021-11-13 | 22:24 | 11.6713 | 77895 | 77996 | 78639
14659 | 2021-11-13 | 22:24 | 11.6713 | 77892 | 78003 | 78633
14660 | 2021-11-13 | 22:24 | 11.6713 | 77889 | 78010 | 78626
14661 | 2021-11-13 | 22:24 | 11.6714 | 77886 | 78016 | 78620
14662 | 2021-11-13 | 22:24 | 11.6714 | 77884 | 78023 | 78614
14663 | 2021-11-13 | 22:24 | 11.6714 | 77882 | 78030 | 78607
14664 | 2021-11-13 | 22:24 | 11.6714 | 77880 | 78036 | 78601
14665 | 2021-11-13 | 22:24 | 11.6715 | 77878 | 78043 | 78594
14666 | 2021-11-13 | 22:24 | 11.6715 | 77876 | 78049 | 78588
14667 | 2021-11-13 | 22:24 | 11.6715 | 77875 | 78055 | 78582
14668 | 2021-11-13 | 22:24 | 11.6716 | 77874 | 78062 | 78575
14669 | 2021-11-13 | 22:24 | 11.6716 | 77873 | 78068 | 78569
14670 | 2021-11-13 | 22:24 | 11.6716 | 77872 | 78074 | 78563
14671 | 2021-11-13 | 22:24 | 11.6716 | 77872 | 78080 | 78557
14672 | 2021-11-13 | 22:24 | 11.6717 | 77872 | 78085 | 78551
14673 | 2021-11-13 | 22:24 | 11.6717 | 77871 | 78091 | 78545
14674 | 2021-11-13 | 22:24 | 11.6717 | 77872 | 78096 | 78539
14675 | 2021-11-13 | 22:24 | 11.6718 | 77872 | 78101 | 78533
14676 | 2021-11-13 | 22:24 | 11.6718 | 77872 | 78105 | 78527
14677 | 2021-11-13 | 22:24 | 11.6718 | 77873 | 78110 | 78522
14678 | 2021-11-13 | 22:24 | 11.6719 | 77873 | 78114 | 78516
14679 | 2021-11-13 | 22:24 | 11.6719 | 77874 | 78118 | 78510
14680 | 2021-11-13 | 22:24 | 11.6719 | 77875 | 78122 | 78504
14681 | 2021-11-13 | 22:24 | 11.6719 | 77876 | 78126 | 78499
14682 | 2021-11-13 | 22:24 | 11.672 | 77877 | 78129 | 78493
14683 | 2021-11-13 | 22:24 | 11.672 | 77878 | 78131 | 78487
14684 | 2021-11-13 | 22:24 | 11.672 | 77879 | 78133 | 78481
14685 | 2021-11-13 | 22:24 | 11.6721 | 77880 | 78135 | 78476
14686 | 2021-11-13 | 22:24 | 11.6721 | 77881 | 78137 | 78470
14687 | 2021-11-13 | 22:24 | 11.6721 | 77883 | 78138 | 78464
14688 | 2021-11-13 | 22:24 | 11.6721 | 77884 | 78138 | 78458
14689 | 2021-11-13 | 22:24 | 11.6722 | 77885 | 78139 | 78452
14690 | 2021-11-13 | 22:24 | 11.6722 | 77886 | 78139 | 78446
14691 | 2021-11-13 | 22:24 | 11.6722 | 77888 | 78139 | 78440
14692 | 2021-11-13 | 22:24 | 11.6723 | 77889 | 78138 | 78434
14693 | 2021-11-13 | 22:24 | 11.6723 | 77890 | 78137 | 78428
14694 | 2021-11-13 | 22:24 | 11.6723 | 77891 | 78135 | 78422
14695 | 2021-11-13 | 22:24 | 11.6723 | 77893 | 78133 | 78416
14696 | 2021-11-13 | 22:24 | 11.6724 | 77894 | 78130 | 78409
14697 | 2021-11-13 | 22:24 | 11.6724 | 77895 | 78127 | 78403
14698 | 2021-11-13 | 22:24 | 11.6724 | 77897 | 78124 | 78396
14699 | 2021-11-13 | 22:24 | 11.6725 | 77898 | 78121 | 78389
14700 | 2021-11-13 | 22:24 | 11.6725 | 77899 | 78117 | 78382
14701 | 2021-11-13 | 22:24 | 11.6725 | 77901 | 78112 | 78375
14702 | 2021-11-13 | 22:24 | 11.6725 | 77902 | 78107 | 78368
14703 | 2021-11-13 | 22:24 | 11.6726 | 77904 | 78102 | 78361
14704 | 2021-11-13 | 22:24 | 11.6726 | 77905 | 78097 | 78354
14705 | 2021-11-13 | 22:24 | 11.6726 | 77906 | 78091 | 78346
14706 | 2021-11-13 | 22:24 | 11.6727 | 77908 | 78086 | 78338
14707 | 2021-11-13 | 22:24 | 11.6727 | 77910 | 78080 | 78331
14708 | 2021-11-13 | 22:24 | 11.6727 | 77912 | 78074 | 78323
14709 | 2021-11-13 | 22:24 | 11.6727 | 77914 | 78068 | 78315
14710 | 2021-11-13 | 22:24 | 11.6728 | 77916 | 78063 | 78307
14711 | 2021-11-13 | 22:24 | 11.6728 | 77918 | 78056 | 78299
14712 | 2021-11-13 | 22:24 | 11.6728 | 77920 | 78050 | 78291
14713 | 2021-11-13 | 22:24 | 11.6729 | 77922 | 78044 | 78283
14714 | 2021-11-13 | 22:24 | 11.6729 | 77925 | 78037 | 78274
14715 | 2021-11-13 | 22:24 | 11.6729 | 77928 | 78031 | 78266
14716 | 2021-11-13 | 22:24 | 11.6729 | 77931 | 78025 | 78258
14717 | 2021-11-13 | 22:24 | 11.673 | 77934 | 78018 | 78250
14718 | 2021-11-13 | 22:24 | 11.673 | 77937 | 78012 | 78242
14719 | 2021-11-13 | 22:24 | 11.673 | 77941 | 78006 | 78234
14720 | 2021-11-13 | 22:24 | 11.6731 | 77945 | 78000 | 78226
14721 | 2021-11-13 | 22:24 | 11.6731 | 77950 | 77994 | 78218
14722 | 2021-11-13 | 22:24 | 11.6731 | 77954 | 77988 | 78211
14723 | 2021-11-13 | 22:24 | 11.6731 | 77959 | 77983 | 78204
14724 | 2021-11-13 | 22:24 | 11.6732 | 77964 | 77977 | 78197
14725 | 2021-11-13 | 22:24 | 11.6732 | 77969 | 77971 | 78190
14726 | 2021-11-13 | 22:24 | 11.6732 | 77974 | 77965 | 78183
14727 | 2021-11-13 | 22:24 | 11.6733 | 77980 | 77960 | 78176
14728 | 2021-11-13 | 22:24 | 11.6733 | 77986 | 77955 | 78169
14729 | 2021-11-13 | 22:24 | 11.6733 | 77992 | 77950 | 78163
14730 | 2021-11-13 | 22:24 | 11.6733 | 77998 | 77945 | 78157
14731 | 2021-11-13 | 22:24 | 11.6734 | 78005 | 77940 | 78150
14732 | 2021-11-13 | 22:24 | 11.6734 | 78011 | 77935 | 78145
14733 | 2021-11-13 | 22:24 | 11.6734 | 78019 | 77930 | 78139
14734 | 2021-11-13 | 22:24 | 11.6735 | 78026 | 77925 | 78133
14735 | 2021-11-13 | 22:24 | 11.6735 | 78033 | 77920 | 78128
14736 | 2021-11-13 | 22:24 | 11.6735 | 78041 | 77915 | 78123
14737 | 2021-11-13 | 22:24 | 11.6735 | 78049 | 77910 | 78118
14738 | 2021-11-13 | 22:24 | 11.6736 | 78057 | 77906 | 78113
14739 | 2021-11-13 | 22:24 | 11.6736 | 78066 | 77901 | 78109
14740 | 2021-11-13 | 22:24 | 11.6736 | 78074 | 77896 | 78104
14741 | 2021-11-13 | 22:24 | 11.6737 | 78082 | 77890 | 78100
14742 | 2021-11-13 | 22:24 | 11.6737 | 78091 | 77885 | 78097
14743 | 2021-11-13 | 22:24 | 11.6737 | 78099 | 77879 | 78093
14744 | 2021-11-13 | 22:24 | 11.6737 | 78107 | 77873 | 78090
14745 | 2021-11-13 | 22:24 | 11.6738 | 78115 | 77867 | 78087
14746 | 2021-11-13 | 22:24 | 11.6738 | 78123 | 77861 | 78084
14747 | 2021-11-13 | 22:24 | 11.6738 | 78131 | 77855 | 78081
14748 | 2021-11-13 | 22:24 | 11.6739 | 78139 | 77849 | 78079
14749 | 2021-11-13 | 22:24 | 11.6739 | 78147 | 77843 | 78076
14750 | 2021-11-13 | 22:24 | 11.6739 | 78154 | 77837 | 78074
14751 | 2021-11-13 | 22:24 | 11.6739 | 78162 | 77831 | 78073
14752 | 2021-11-13 | 22:24 | 11.674 | 78169 | 77825 | 78071
14753 | 2021-11-13 | 22:24 | 11.674 | 78175 | 77818 | 78070
14754 | 2021-11-13 | 22:24 | 11.674 | 78182 | 77812 | 78069
14755 | 2021-11-13 | 22:24 | 11.6741 | 78188 | 77806 | 78068
14756 | 2021-11-13 | 22:24 | 11.6741 | 78193 | 77800 | 78067
14757 | 2021-11-13 | 22:24 | 11.6741 | 78198 | 77794 | 78067
14758 | 2021-11-13 | 22:24 | 11.6741 | 78203 | 77789 | 78066
14759 | 2021-11-13 | 22:24 | 11.6742 | 78207 | 77783 | 78066
14760 | 2021-11-13 | 22:24 | 11.6742 | 78211 | 77777 | 78066
14761 | 2021-11-13 | 22:24 | 11.6742 | 78215 | 77771 | 78067
14762 | 2021-11-13 | 22:24 | 11.6743 | 78218 | 77766 | 78067
14763 | 2021-11-13 | 22:24 | 11.6743 | 78221 | 77760 | 78068
14764 | 2021-11-13 | 22:24 | 11.6743 | 78223 | 77754 | 78068
14765 | 2021-11-13 | 22:24 | 11.6743 | 78225 | 77748 | 78069
14766 | 2021-11-13 | 22:24 | 11.6744 | 78226 | 77743 | 78070
14767 | 2021-11-13 | 22:24 | 11.6744 | 78227 | 77737 | 78071
14768 | 2021-11-13 | 22:24 | 11.6744 | 78227 | 77731 | 78072
14769 | 2021-11-13 | 22:24 | 11.6745 | 78227 | 77725 | 78073
14770 | 2021-11-13 | 22:24 | 11.6745 | 78226 | 77719 | 78074
14771 | 2021-11-13 | 22:24 | 11.6745 | 78224 | 77713 | 78076
14772 | 2021-11-13 | 22:24 | 11.6745 | 78222 | 77707 | 78077
14773 | 2021-11-13 | 22:24 | 11.6746 | 78220 | 77700 | 78078
14774 | 2021-11-13 | 22:24 | 11.6746 | 78217 | 77694 | 78080
14775 | 2021-11-13 | 22:24 | 11.6746 | 78214 | 77688 | 78081
14776 | 2021-11-13 | 22:24 | 11.6747 | 78210 | 77682 | 78082
14777 | 2021-11-13 | 22:24 | 11.6747 | 78206 | 77676 | 78084
14778 | 2021-11-13 | 22:24 | 11.6747 | 78201 | 77670 | 78085
14779 | 2021-11-13 | 22:24 | 11.6748 | 78196 | 77663 | 78086
14780 | 2021-11-13 | 22:24 | 11.6748 | 78191 | 77657 | 78087
14781 | 2021-11-13 | 22:24 | 11.6748 | 78185 | 77651 | 78089
14782 | 2021-11-13 | 22:24 | 11.6748 | 78179 | 77645 | 78090
14783 | 2021-11-13 | 22:24 | 11.6749 | 78173 | 77639 | 78091
14784 | 2021-11-13 | 22:24 | 11.6749 | 78166 | 77633 | 78092
14785 | 2021-11-13 | 22:24 | 11.6749 | 78158 | 77626 | 78093
14786 | 2021-11-13 | 22:24 | 11.675 | 78150 | 77620 | 78094
14787 | 2021-11-13 | 22:24 | 11.675 | 78142 | 77614 | 78095
14788 | 2021-11-13 | 22:24 | 11.675 | 78133 | 77607 | 78096
14789 | 2021-11-13 | 22:24 | 11.675 | 78124 | 77601 | 78097
14790 | 2021-11-13 | 22:24 | 11.6751 | 78114 | 77594 | 78098
14791 | 2021-11-13 | 22:24 | 11.6751 | 78105 | 77588 | 78098
14792 | 2021-11-13 | 22:24 | 11.6751 | 78095 | 77582 | 78099
14793 | 2021-11-13 | 22:24 | 11.6752 | 78085 | 77575 | 78100
14794 | 2021-11-13 | 22:24 | 11.6752 | 78075 | 77569 | 78101
14795 | 2021-11-13 | 22:24 | 11.6752 | 78065 | 77563 | 78102
14796 | 2021-11-13 | 22:24 | 11.6752 | 78055 | 77556 | 78103
14797 | 2021-11-13 | 22:24 | 11.6753 | 78045 | 77550 | 78104
14798 | 2021-11-13 | 22:24 | 11.6753 | 78035 | 77544 | 78105
14799 | 2021-11-13 | 22:24 | 11.6753 | 78025 | 77538 | 78106
14800 | 2021-11-13 | 22:24 | 11.6754 | 78014 | 77531 | 78107
14801 | 2021-11-13 | 22:24 | 11.6754 | 78004 | 77525 | 78108
14802 | 2021-11-13 | 22:24 | 11.6754 | 77994 | 77519 | 78109
14803 | 2021-11-13 | 22:24 | 11.6754 | 77984 | 77513 | 78111
14804 | 2021-11-13 | 22:24 | 11.6755 | 77974 | 77507 | 78112
14805 | 2021-11-13 | 22:24 | 11.6755 | 77965 | 77501 | 78114
14806 | 2021-11-13 | 22:24 | 11.6755 | 77955 | 77495 | 78116
14807 | 2021-11-13 | 22:24 | 11.6756 | 77946 | 77489 | 78117
14808 | 2021-11-13 | 22:24 | 11.6756 | 77937 | 77483 | 78120
14809 | 2021-11-13 | 22:24 | 11.6756 | 77928 | 77478 | 78122
14810 | 2021-11-13 | 22:24 | 11.6756 | 77919 | 77472 | 78124
14811 | 2021-11-13 | 22:24 | 11.6757 | 77910 | 77467 | 78126
14812 | 2021-11-13 | 22:24 | 11.6757 | 77902 | 77462 | 78129
14813 | 2021-11-13 | 22:24 | 11.6757 | 77894 | 77457 | 78132
14814 | 2021-11-13 | 22:24 | 11.6758 | 77886 | 77452 | 78135
14815 | 2021-11-13 | 22:24 | 11.6758 | 77878 | 77447 | 78138
14816 | 2021-11-13 | 22:24 | 11.6758 | 77870 | 77442 | 78142
14817 | 2021-11-13 | 22:24 | 11.6758 | 77863 | 77438 | 78146
14818 | 2021-11-13 | 22:24 | 11.6759 | 77856 | 77433 | 78149
14819 | 2021-11-13 | 22:24 | 11.6759 | 77848 | 77429 | 78154
14820 | 2021-11-13 | 22:24 | 11.6759 | 77842 | 77425 | 78158
14821 | 2021-11-13 | 22:24 | 11.676 | 77835 | 77422 | 78162
14822 | 2021-11-13 | 22:24 | 11.676 | 77829 | 77418 | 78167
14823 | 2021-11-13 | 22:24 | 11.676 | 77823 | 77415 | 78172
14824 | 2021-11-13 | 22:24 | 11.676 | 77817 | 77412 | 78177
14825 | 2021-11-13 | 22:24 | 11.6761 | 77812 | 77409 | 78182
14826 | 2021-11-13 | 22:24 | 11.6761 | 77806 | 77406 | 78188
14827 | 2021-11-13 | 22:24 | 11.6761 | 77801 | 77403 | 78193
14828 | 2021-11-13 | 22:24 | 11.6762 | 77796 | 77401 | 78198
14829 | 2021-11-13 | 22:24 | 11.6762 | 77791 | 77399 | 78204
14830 | 2021-11-13 | 22:24 | 11.6762 | 77786 | 77396 | 78209
14831 | 2021-11-13 | 22:24 | 11.6762 | 77781 | 77394 | 78214
14832 | 2021-11-13 | 22:24 | 11.6763 | 77776 | 77393 | 78220
14833 | 2021-11-13 | 22:24 | 11.6763 | 77771 | 77391 | 78225
14834 | 2021-11-13 | 22:24 | 11.6763 | 77766 | 77390 | 78230
14835 | 2021-11-13 | 22:24 | 11.6764 | 77762 | 77389 | 78235
14836 | 2021-11-13 | 22:24 | 11.6764 | 77757 | 77387 | 78240
14837 | 2021-11-13 | 22:24 | 11.6764 | 77753 | 77386 | 78245
14838 | 2021-11-13 | 22:24 | 11.6764 | 77748 | 77386 | 78250
14839 | 2021-11-13 | 22:24 | 11.6765 | 77743 | 77385 | 78255
14840 | 2021-11-13 | 22:24 | 11.6765 | 77739 | 77385 | 78259
14841 | 2021-11-13 | 22:24 | 11.6765 | 77734 | 77384 | 78263
14842 | 2021-11-13 | 22:24 | 11.6766 | 77729 | 77384 | 78267
14843 | 2021-11-13 | 22:24 | 11.6766 | 77724 | 77384 | 78271
14844 | 2021-11-13 | 22:24 | 11.6766 | 77720 | 77384 | 78274
14845 | 2021-11-13 | 22:24 | 11.6766 | 77715 | 77384 | 78277
14846 | 2021-11-13 | 22:24 | 11.6767 | 77710 | 77384 | 78280
14847 | 2021-11-13 | 22:24 | 11.6767 | 77704 | 77384 | 78283
14848 | 2021-11-13 | 22:24 | 11.6767 | 77699 | 77385 | 78285
14849 | 2021-11-13 | 22:24 | 11.6768 | 77694 | 77385 | 78287
14850 | 2021-11-13 | 22:24 | 11.6768 | 77688 | 77386 | 78289
14851 | 2021-11-13 | 22:24 | 11.6768 | 77682 | 77386 | 78290
14852 | 2021-11-13 | 22:24 | 11.6768 | 77676 | 77387 | 78291
14853 | 2021-11-13 | 22:24 | 11.6769 | 77670 | 77388 | 78291
14854 | 2021-11-13 | 22:24 | 11.6769 | 77663 | 77389 | 78292
14855 | 2021-11-13 | 22:24 | 11.6769 | 77657 | 77389 | 78292
14856 | 2021-11-13 | 22:24 | 11.677 | 77650 | 77390 | 78291
14857 | 2021-11-13 | 22:24 | 11.677 | 77643 | 77391 | 78290
14858 | 2021-11-13 | 22:24 | 11.677 | 77636 | 77392 | 78289
14859 | 2021-11-13 | 22:24 | 11.677 | 77629 | 77393 | 78288
14860 | 2021-11-13 | 22:24 | 11.6771 | 77622 | 77395 | 78286
14861 | 2021-11-13 | 22:24 | 11.6771 | 77614 | 77396 | 78283
14862 | 2021-11-13 | 22:24 | 11.6771 | 77607 | 77397 | 78281
14863 | 2021-11-13 | 22:24 | 11.6772 | 77599 | 77398 | 78278
14864 | 2021-11-13 | 22:24 | 11.6772 | 77591 | 77399 | 78274
14865 | 2021-11-13 | 22:24 | 11.6772 | 77584 | 77400 | 78270
14866 | 2021-11-13 | 22:24 | 11.6772 | 77576 | 77402 | 78266
14867 | 2021-11-13 | 22:24 | 11.6773 | 77568 | 77403 | 78262
14868 | 2021-11-13 | 22:24 | 11.6773 | 77560 | 77404 | 78257
14869 | 2021-11-13 | 22:24 | 11.6773 | 77552 | 77405 | 78252
14870 | 2021-11-13 | 22:24 | 11.6774 | 77544 | 77407 | 78246
14871 | 2021-11-13 | 22:24 | 11.6774 | 77536 | 77408 | 78241
14872 | 2021-11-13 | 22:24 | 11.6774 | 77528 | 77409 | 78234
14873 | 2021-11-13 | 22:24 | 11.6775 | 77520 | 77411 | 78228
14874 | 2021-11-13 | 22:24 | 11.6775 | 77512 | 77412 | 78221
14875 | 2021-11-13 | 22:24 | 11.6775 | 77503 | 77414 | 78214
14876 | 2021-11-13 | 22:24 | 11.6775 | 77495 | 77415 | 78207
14877 | 2021-11-13 | 22:24 | 11.6776 | 77487 | 77417 | 78200
14878 | 2021-11-13 | 22:24 | 11.6776 | 77479 | 77418 | 78192
14879 | 2021-11-13 | 22:24 | 11.6776 | 77471 | 77420 | 78184
14880 | 2021-11-13 | 22:24 | 11.6777 | 77463 | 77421 | 78176
14881 | 2021-11-13 | 22:24 | 11.6777 | 77455 | 77423 | 78167
14882 | 2021-11-13 | 22:24 | 11.6777 | 77447 | 77424 | 78159
14883 | 2021-11-13 | 22:24 | 11.6777 | 77439 | 77426 | 78150
14884 | 2021-11-13 | 22:24 | 11.6778 | 77432 | 77428 | 78141
14885 | 2021-11-13 | 22:24 | 11.6778 | 77424 | 77429 | 78133
14886 | 2021-11-13 | 22:24 | 11.6778 | 77417 | 77431 | 78124
14887 | 2021-11-13 | 22:24 | 11.6779 | 77409 | 77433 | 78115
14888 | 2021-11-13 | 22:24 | 11.6779 | 77402 | 77435 | 78106
14889 | 2021-11-13 | 22:24 | 11.6779 | 77395 | 77437 | 78097
14890 | 2021-11-13 | 22:24 | 11.6779 | 77387 | 77439 | 78088
14891 | 2021-11-13 | 22:24 | 11.678 | 77381 | 77441 | 78079
14892 | 2021-11-13 | 22:24 | 11.678 | 77374 | 77443 | 78071
14893 | 2021-11-13 | 22:24 | 11.678 | 77367 | 77445 | 78062
14894 | 2021-11-13 | 22:24 | 11.6781 | 77361 | 77447 | 78053
14895 | 2021-11-13 | 22:24 | 11.6781 | 77354 | 77449 | 78044
14896 | 2021-11-13 | 22:24 | 11.6781 | 77348 | 77451 | 78035
14897 | 2021-11-13 | 22:24 | 11.6781 | 77342 | 77454 | 78026
14898 | 2021-11-13 | 22:24 | 11.6782 | 77336 | 77456 | 78017
14899 | 2021-11-13 | 22:24 | 11.6782 | 77330 | 77459 | 78009
14900 | 2021-11-13 | 22:24 | 11.6782 | 77325 | 77462 | 78000
14901 | 2021-11-13 | 22:24 | 11.6783 | 77319 | 77465 | 77992
14902 | 2021-11-13 | 22:24 | 11.6783 | 77314 | 77468 | 77984
14903 | 2021-11-13 | 22:24 | 11.6783 | 77309 | 77471 | 77975
14904 | 2021-11-13 | 22:24 | 11.6783 | 77305 | 77474 | 77967
14905 | 2021-11-13 | 22:24 | 11.6784 | 77300 | 77477 | 77960
14906 | 2021-11-13 | 22:24 | 11.6784 | 77296 | 77481 | 77952
14907 | 2021-11-13 | 22:24 | 11.6784 | 77292 | 77485 | 77944
14908 | 2021-11-13 | 22:24 | 11.6785 | 77288 | 77488 | 77936
14909 | 2021-11-13 | 22:24 | 11.6785 | 77284 | 77492 | 77928
14910 | 2021-11-13 | 22:24 | 11.6785 | 77281 | 77496 | 77921
14911 | 2021-11-13 | 22:24 | 11.6785 | 77278 | 77500 | 77914
14912 | 2021-11-13 | 22:24 | 11.6786 | 77274 | 77504 | 77907
14913 | 2021-11-13 | 22:24 | 11.6786 | 77272 | 77508 | 77900
14914 | 2021-11-13 | 22:24 | 11.6786 | 77269 | 77512 | 77894
14915 | 2021-11-13 | 22:24 | 11.6787 | 77267 | 77516 | 77887
14916 | 2021-11-13 | 22:24 | 11.6787 | 77264 | 77520 | 77880
14917 | 2021-11-13 | 22:24 | 11.6787 | 77262 | 77523 | 77873
14918 | 2021-11-13 | 22:24 | 11.6787 | 77260 | 77527 | 77867
14919 | 2021-11-13 | 22:24 | 11.6788 | 77259 | 77531 | 77861
14920 | 2021-11-13 | 22:24 | 11.6788 | 77257 | 77534 | 77854
14921 | 2021-11-13 | 22:24 | 11.6788 | 77256 | 77538 | 77848
14922 | 2021-11-13 | 22:24 | 11.6789 | 77255 | 77541 | 77842
14923 | 2021-11-13 | 22:24 | 11.6789 | 77254 | 77544 | 77836
14924 | 2021-11-13 | 22:24 | 11.6789 | 77253 | 77547 | 77830
14925 | 2021-11-13 | 22:24 | 11.6789 | 77252 | 77550 | 77824
14926 | 2021-11-13 | 22:24 | 11.679 | 77252 | 77552 | 77818
14927 | 2021-11-13 | 22:24 | 11.679 | 77251 | 77554 | 77812
14928 | 2021-11-13 | 22:24 | 11.679 | 77251 | 77555 | 77806
14929 | 2021-11-13 | 22:24 | 11.6791 | 77251 | 77557 | 77800
14930 | 2021-11-13 | 22:24 | 11.6791 | 77251 | 77558 | 77794
14931 | 2021-11-13 | 22:24 | 11.6791 | 77251 | 77559 | 77787
14932 | 2021-11-13 | 22:24 | 11.6791 | 77251 | 77560 | 77781
14933 | 2021-11-13 | 22:24 | 11.6792 | 77252 | 77561 | 77775
14934 | 2021-11-13 | 22:24 | 11.6792 | 77252 | 77562 | 77769
14935 | 2021-11-13 | 22:24 | 11.6792 | 77253 | 77562 | 77762
14936 | 2021-11-13 | 22:24 | 11.6793 | 77253 | 77562 | 77756
14937 | 2021-11-13 | 22:24 | 11.6793 | 77254 | 77562 | 77750
14938 | 2021-11-13 | 22:24 | 11.6793 | 77255 | 77561 | 77743
14939 | 2021-11-13 | 22:24 | 11.6793 | 77256 | 77560 | 77736
14940 | 2021-11-13 | 22:24 | 11.6794 | 77257 | 77558 | 77730
14941 | 2021-11-13 | 22:24 | 11.6794 | 77258 | 77557 | 77723
14942 | 2021-11-13 | 22:24 | 11.6794 | 77259 | 77555 | 77717
14943 | 2021-11-13 | 22:24 | 11.6795 | 77260 | 77553 | 77710
14944 | 2021-11-13 | 22:24 | 11.6795 | 77261 | 77551 | 77703
14945 | 2021-11-13 | 22:24 | 11.6795 | 77263 | 77549 | 77696
14946 | 2021-11-13 | 22:24 | 11.6795 | 77264 | 77546 | 77689
14947 | 2021-11-13 | 22:24 | 11.6796 | 77265 | 77543 | 77682
14948 | 2021-11-13 | 22:24 | 11.6796 | 77267 | 77540 | 77675
14949 | 2021-11-13 | 22:24 | 11.6796 | 77268 | 77537 | 77668
14950 | 2021-11-13 | 22:24 | 11.6797 | 77270 | 77533 | 77661
14951 | 2021-11-13 | 22:24 | 11.6797 | 77272 | 77530 | 77654
14952 | 2021-11-13 | 22:24 | 11.6797 | 77273 | 77526 | 77646
14953 | 2021-11-13 | 22:24 | 11.6797 | 77275 | 77522 | 77639
14954 | 2021-11-13 | 22:24 | 11.6798 | 77277 | 77518 | 77632
14955 | 2021-11-13 | 22:24 | 11.6798 | 77279 | 77513 | 77625
14956 | 2021-11-13 | 22:24 | 11.6798 | 77280 | 77508 | 77617
14957 | 2021-11-13 | 22:24 | 11.6799 | 77282 | 77502 | 77610
14958 | 2021-11-13 | 22:24 | 11.6799 | 77284 | 77496 | 77602
14959 | 2021-11-13 | 22:24 | 11.6799 | 77286 | 77490 | 77595
14960 | 2021-11-13 | 22:24 | 11.6799 | 77288 | 77483 | 77587
14961 | 2021-11-13 | 22:24 | 11.68 | 77290 | 77477 | 77580
14962 | 2021-11-13 | 22:24 | 11.68 | 77292 | 77470 | 77572
14963 | 2021-11-13 | 22:24 | 11.68 | 77294 | 77464 | 77564
14964 | 2021-11-13 | 22:24 | 11.6801 | 77296 | 77457 | 77556
14965 | 2021-11-13 | 22:24 | 11.6801 | 77298 | 77451 | 77549
14966 | 2021-11-13 | 22:24 | 11.6801 | 77300 | 77444 | 77541
14967 | 2021-11-13 | 22:24 | 11.6802 | 77303 | 77436 | 77533
14968 | 2021-11-13 | 22:24 | 11.6802 | 77305 | 77429 | 77526
14969 | 2021-11-13 | 22:24 | 11.6802 | 77307 | 77421 | 77518
14970 | 2021-11-13 | 22:24 | 11.6802 | 77309 | 77413 | 77511
14971 | 2021-11-13 | 22:24 | 11.6803 | 77312 | 77406 | 77504
14972 | 2021-11-13 | 22:24 | 11.6803 | 77314 | 77398 | 77497
14973 | 2021-11-13 | 22:24 | 11.6803 | 77317 | 77390 | 77490
14974 | 2021-11-13 | 22:24 | 11.6804 | 77320 | 77383 | 77483
14975 | 2021-11-13 | 22:24 | 11.6804 | 77323 | 77375 | 77476
14976 | 2021-11-13 | 22:24 | 11.6804 | 77326 | 77367 | 77469
14977 | 2021-11-13 | 22:24 | 11.6804 | 77329 | 77359 | 77463
14978 | 2021-11-13 | 22:24 | 11.6805 | 77332 | 77351 | 77457
14979 | 2021-11-13 | 22:24 | 11.6805 | 77335 | 77343 | 77451
14980 | 2021-11-13 | 22:24 | 11.6805 | 77338 | 77335 | 77445
14981 | 2021-11-13 | 22:24 | 11.6806 | 77342 | 77327 | 77439
14982 | 2021-11-13 | 22:24 | 11.6806 | 77345 | 77319 | 77434
14983 | 2021-11-13 | 22:24 | 11.6806 | 77348 | 77311 | 77429
14984 | 2021-11-13 | 22:24 | 11.6806 | 77352 | 77303 | 77424
14985 | 2021-11-13 | 22:24 | 11.6807 | 77355 | 77294 | 77419
14986 | 2021-11-13 | 22:24 | 11.6807 | 77358 | 77286 | 77414
14987 | 2021-11-13 | 22:24 | 11.6807 | 77362 | 77278 | 77410
14988 | 2021-11-13 | 22:24 | 11.6808 | 77365 | 77269 | 77406
14989 | 2021-11-13 | 22:24 | 11.6808 | 77368 | 77261 | 77402
14990 | 2021-11-13 | 22:24 | 11.6808 | 77372 | 77253 | 77398
14991 | 2021-11-13 | 22:24 | 11.6808 | 77375 | 77244 | 77395
14992 | 2021-11-13 | 22:24 | 11.6809 | 77379 | 77236 | 77392
14993 | 2021-11-13 | 22:24 | 11.6809 | 77383 | 77228 | 77388
14994 | 2021-11-13 | 22:24 | 11.6809 | 77387 | 77221 | 77385
14995 | 2021-11-13 | 22:24 | 11.681 | 77391 | 77213 | 77383
14996 | 2021-11-13 | 22:24 | 11.681 | 77394 | 77205 | 77380
14997 | 2021-11-13 | 22:24 | 11.681 | 77398 | 77197 | 77378
14998 | 2021-11-13 | 22:24 | 11.681 | 77401 | 77188 | 77375
14999 | 2021-11-13 | 22:24 | 11.6811 | 77405 | 77180 | 77373
15000 | 2021-11-13 | 22:24 | 11.6811 | 77408 | 77171 | 77372
15001 | 2021-11-13 | 22:24 | 11.6811 | 77410 | 77163 | 77370
15002 | 2021-11-13 | 22:24 | 11.6812 | 77413 | 77154 | 77368
15003 | 2021-11-13 | 22:24 | 11.6812 | 77416 | 77146 | 77367
15004 | 2021-11-13 | 22:24 | 11.6812 | 77419 | 77138 | 77366
15005 | 2021-11-13 | 22:24 | 11.6812 | 77421 | 77130 | 77364
15006 | 2021-11-13 | 22:24 | 11.6813 | 77424 | 77123 | 77363
15007 | 2021-11-13 | 22:24 | 11.6813 | 77426 | 77115 | 77362
15008 | 2021-11-13 | 22:24 | 11.6813 | 77429 | 77108 | 77362
15009 | 2021-11-13 | 22:24 | 11.6814 | 77430 | 77101 | 77361
15010 | 2021-11-13 | 22:24 | 11.6814 | 77432 | 77094 | 77361
15011 | 2021-11-13 | 22:24 | 11.6814 | 77433 | 77087 | 77360
15012 | 2021-11-13 | 22:24 | 11.6814 | 77434 | 77081 | 77360
15013 | 2021-11-13 | 22:24 | 11.6815 | 77435 | 77075 | 77360
15014 | 2021-11-13 | 22:24 | 11.6815 | 77435 | 77068 | 77360
15015 | 2021-11-13 | 22:24 | 11.6815 | 77436 | 77062 | 77360
15016 | 2021-11-13 | 22:24 | 11.6816 | 77436 | 77056 | 77360
15017 | 2021-11-13 | 22:24 | 11.6816 | 77435 | 77050 | 77360
15018 | 2021-11-13 | 22:24 | 11.6816 | 77435 | 77044 | 77360
15019 | 2021-11-13 | 22:24 | 11.6816 | 77434 | 77039 | 77361
15020 | 2021-11-13 | 22:24 | 11.6817 | 77433 | 77033 | 77361
15021 | 2021-11-13 | 22:24 | 11.6817 | 77431 | 77027 | 77362
15022 | 2021-11-13 | 22:24 | 11.6817 | 77429 | 77021 | 77362
15023 | 2021-11-13 | 22:24 | 11.6818 | 77427 | 77015 | 77363
15024 | 2021-11-13 | 22:24 | 11.6818 | 77424 | 77009 | 77363
15025 | 2021-11-13 | 22:24 | 11.6818 | 77421 | 77003 | 77364
15026 | 2021-11-13 | 22:24 | 11.6818 | 77418 | 76997 | 77365
15027 | 2021-11-13 | 22:24 | 11.6819 | 77415 | 76991 | 77365
15028 | 2021-11-13 | 22:24 | 11.6819 | 77411 | 76984 | 77366
15029 | 2021-11-13 | 22:24 | 11.6819 | 77406 | 76978 | 77367
15030 | 2021-11-13 | 22:24 | 11.682 | 77401 | 76971 | 77367
15031 | 2021-11-13 | 22:24 | 11.682 | 77396 | 76965 | 77368
15032 | 2021-11-13 | 22:24 | 11.682 | 77391 | 76958 | 77368
15033 | 2021-11-13 | 22:24 | 11.682 | 77385 | 76952 | 77369
15034 | 2021-11-13 | 22:24 | 11.6821 | 77380 | 76946 | 77369
15035 | 2021-11-13 | 22:24 | 11.6821 | 77374 | 76940 | 77370
15036 | 2021-11-13 | 22:24 | 11.6821 | 77368 | 76933 | 77371
15037 | 2021-11-13 | 22:24 | 11.6822 | 77363 | 76927 | 77371
15038 | 2021-11-13 | 22:24 | 11.6822 | 77357 | 76921 | 77372
15039 | 2021-11-13 | 22:24 | 11.6822 | 77350 | 76915 | 77372
15040 | 2021-11-13 | 22:24 | 11.6822 | 77343 | 76909 | 77373
15041 | 2021-11-13 | 22:24 | 11.6823 | 77336 | 76903 | 77373
15042 | 2021-11-13 | 22:24 | 11.6823 | 77328 | 76896 | 77373
15043 | 2021-11-13 | 22:24 | 11.6823 | 77320 | 76891 | 77373
15044 | 2021-11-13 | 22:24 | 11.6824 | 77312 | 76885 | 77373
15045 | 2021-11-13 | 22:24 | 11.6824 | 77304 | 76879 | 77373
15046 | 2021-11-13 | 22:24 | 11.6824 | 77296 | 76873 | 77373
15047 | 2021-11-13 | 22:24 | 11.6824 | 77288 | 76868 | 77373
15048 | 2021-11-13 | 22:24 | 11.6825 | 77280 | 76862 | 77373
15049 | 2021-11-13 | 22:24 | 11.6825 | 77271 | 76857 | 77373
15050 | 2021-11-13 | 22:24 | 11.6825 | 77263 | 76851 | 77373
15051 | 2021-11-13 | 22:24 | 11.6826 | 77254 | 76846 | 77373
15052 | 2021-11-13 | 22:24 | 11.6826 | 77245 | 76841 | 77373
15053 | 2021-11-13 | 22:24 | 11.6826 | 77236 | 76836 | 77373
15054 | 2021-11-13 | 22:24 | 11.6826 | 77228 | 76831 | 77373
15055 | 2021-11-13 | 22:24 | 11.6827 | 77219 | 76826 | 77373
15056 | 2021-11-13 | 22:24 | 11.6827 | 77211 | 76821 | 77373
15057 | 2021-11-13 | 22:24 | 11.6827 | 77202 | 76817 | 77373
15058 | 2021-11-13 | 22:24 | 11.6828 | 77194 | 76812 | 77374
15059 | 2021-11-13 | 22:24 | 11.6828 | 77185 | 76807 | 77374
15060 | 2021-11-13 | 22:24 | 11.6828 | 77177 | 76803 | 77375
15061 | 2021-11-13 | 22:24 | 11.6829 | 77168 | 76798 | 77375
15062 | 2021-11-13 | 22:24 | 11.6829 | 77159 | 76794 | 77376
15063 | 2021-11-13 | 22:24 | 11.6829 | 77151 | 76789 | 77376
15064 | 2021-11-13 | 22:24 | 11.6829 | 77143 | 76785 | 77376
15065 | 2021-11-13 | 22:24 | 11.683 | 77134 | 76781 | 77377
15066 | 2021-11-13 | 22:24 | 11.683 | 77126 | 76776 | 77378
15067 | 2021-11-13 | 22:24 | 11.683 | 77118 | 76772 | 77379
15068 | 2021-11-13 | 22:24 | 11.6831 | 77110 | 76768 | 77380
15069 | 2021-11-13 | 22:24 | 11.6831 | 77103 | 76764 | 77381
15070 | 2021-11-13 | 22:24 | 11.6831 | 77095 | 76760 | 77382
15071 | 2021-11-13 | 22:24 | 11.6831 | 77087 | 76757 | 77383
15072 | 2021-11-13 | 22:24 | 11.6832 | 77080 | 76753 | 77384
15073 | 2021-11-13 | 22:24 | 11.6832 | 77072 | 76749 | 77385
15074 | 2021-11-13 | 22:24 | 11.6832 | 77065 | 76746 | 77386
15075 | 2021-11-13 | 22:24 | 11.6833 | 77057 | 76743 | 77388
15076 | 2021-11-13 | 22:24 | 11.6833 | 77050 | 76740 | 77389
15077 | 2021-11-13 | 22:24 | 11.6833 | 77043 | 76737 | 77390
15078 | 2021-11-13 | 22:24 | 11.6833 | 77037 | 76734 | 77392
15079 | 2021-11-13 | 22:24 | 11.6834 | 77030 | 76731 | 77394
15080 | 2021-11-13 | 22:24 | 11.6834 | 77024 | 76729 | 77395
15081 | 2021-11-13 | 22:24 | 11.6834 | 77018 | 76727 | 77397
15082 | 2021-11-13 | 22:24 | 11.6835 | 77012 | 76725 | 77399
15083 | 2021-11-13 | 22:24 | 11.6835 | 77006 | 76723 | 77400
15084 | 2021-11-13 | 22:24 | 11.6835 | 76999 | 76721 | 77401
15085 | 2021-11-13 | 22:24 | 11.6835 | 76994 | 76720 | 77402
15086 | 2021-11-13 | 22:24 | 11.6836 | 76988 | 76718 | 77403
15087 | 2021-11-13 | 22:24 | 11.6836 | 76982 | 76717 | 77404
15088 | 2021-11-13 | 22:24 | 11.6836 | 76977 | 76716 | 77404
15089 | 2021-11-13 | 22:24 | 11.6837 | 76971 | 76715 | 77405
15090 | 2021-11-13 | 22:24 | 11.6837 | 76966 | 76714 | 77406
15091 | 2021-11-13 | 22:24 | 11.6837 | 76961 | 76714 | 77406
15092 | 2021-11-13 | 22:24 | 11.6837 | 76956 | 76713 | 77406
15093 | 2021-11-13 | 22:24 | 11.6838 | 76951 | 76713 | 77406
15094 | 2021-11-13 | 22:24 | 11.6838 | 76945 | 76712 | 77405
15095 | 2021-11-13 | 22:24 | 11.6838 | 76940 | 76712 | 77404
15096 | 2021-11-13 | 22:24 | 11.6839 | 76935 | 76712 | 77403
15097 | 2021-11-13 | 22:24 | 11.6839 | 76931 | 76712 | 77402
15098 | 2021-11-13 | 22:24 | 11.6839 | 76926 | 76712 | 77401
15099 | 2021-11-13 | 22:24 | 11.6839 | 76921 | 76712 | 77400
15100 | 2021-11-13 | 22:24 | 11.684 | 76916 | 76712 | 77398
15101 | 2021-11-13 | 22:24 | 11.684 | 76912 | 76712 | 77396
15102 | 2021-11-13 | 22:24 | 11.684 | 76907 | 76712 | 77394
15103 | 2021-11-13 | 22:24 | 11.6841 | 76902 | 76712 | 77391
15104 | 2021-11-13 | 22:24 | 11.6841 | 76897 | 76713 | 77388
15105 | 2021-11-13 | 22:24 | 11.6841 | 76891 | 76713 | 77385
15106 | 2021-11-13 | 22:24 | 11.6841 | 76886 | 76713 | 77381
15107 | 2021-11-13 | 22:24 | 11.6842 | 76881 | 76713 | 77377
15108 | 2021-11-13 | 22:24 | 11.6842 | 76876 | 76713 | 77373
15109 | 2021-11-13 | 22:24 | 11.6842 | 76871 | 76713 | 77369
15110 | 2021-11-13 | 22:24 | 11.6843 | 76866 | 76714 | 77364
15111 | 2021-11-13 | 22:24 | 11.6843 | 76861 | 76714 | 77359
15112 | 2021-11-13 | 22:24 | 11.6843 | 76855 | 76714 | 77354
15113 | 2021-11-13 | 22:24 | 11.6843 | 76850 | 76714 | 77349
15114 | 2021-11-13 | 22:24 | 11.6844 | 76845 | 76714 | 77343
15115 | 2021-11-13 | 22:24 | 11.6844 | 76839 | 76715 | 77337
15116 | 2021-11-13 | 22:24 | 11.6844 | 76834 | 76715 | 77331
15117 | 2021-11-13 | 22:24 | 11.6845 | 76829 | 76715 | 77324
15118 | 2021-11-13 | 22:24 | 11.6845 | 76823 | 76715 | 77318
15119 | 2021-11-13 | 22:24 | 11.6845 | 76818 | 76715 | 77311
15120 | 2021-11-13 | 22:24 | 11.6845 | 76812 | 76716 | 77304
15121 | 2021-11-13 | 22:24 | 11.6846 | 76807 | 76716 | 77298
15122 | 2021-11-13 | 22:24 | 11.6846 | 76802 | 76716 | 77291
15123 | 2021-11-13 | 22:24 | 11.6846 | 76796 | 76716 | 77284
15124 | 2021-11-13 | 22:24 | 11.6847 | 76791 | 76717 | 77277
15125 | 2021-11-13 | 22:24 | 11.6847 | 76786 | 76717 | 77269
15126 | 2021-11-13 | 22:24 | 11.6847 | 76780 | 76718 | 77262
15127 | 2021-11-13 | 22:24 | 11.6847 | 76775 | 76718 | 77255
15128 | 2021-11-13 | 22:24 | 11.6848 | 76769 | 76718 | 77247
15129 | 2021-11-13 | 22:24 | 11.6848 | 76764 | 76719 | 77240
15130 | 2021-11-13 | 22:24 | 11.6848 | 76758 | 76720 | 77232
15131 | 2021-11-13 | 22:24 | 11.6849 | 76753 | 76720 | 77225
15132 | 2021-11-13 | 22:24 | 11.6849 | 76747 | 76721 | 77218
15133 | 2021-11-13 | 22:24 | 11.6849 | 76742 | 76722 | 77210
15134 | 2021-11-13 | 22:24 | 11.6849 | 76736 | 76723 | 77203
15135 | 2021-11-13 | 22:24 | 11.685 | 76731 | 76724 | 77195
15136 | 2021-11-13 | 22:24 | 11.685 | 76725 | 76725 | 77188
15137 | 2021-11-13 | 22:24 | 11.685 | 76720 | 76726 | 77181
15138 | 2021-11-13 | 22:24 | 11.6851 | 76715 | 76727 | 77174
15139 | 2021-11-13 | 22:24 | 11.6851 | 76710 | 76728 | 77167
15140 | 2021-11-13 | 22:24 | 11.6851 | 76704 | 76730 | 77160
15141 | 2021-11-13 | 22:24 | 11.6851 | 76699 | 76731 | 77153
15142 | 2021-11-13 | 22:24 | 11.6852 | 76694 | 76733 | 77146
15143 | 2021-11-13 | 22:24 | 11.6852 | 76689 | 76735 | 77140
15144 | 2021-11-13 | 22:24 | 11.6852 | 76684 | 76737 | 77133
15145 | 2021-11-13 | 22:24 | 11.6853 | 76679 | 76739 | 77127
15146 | 2021-11-13 | 22:24 | 11.6853 | 76674 | 76741 | 77120
15147 | 2021-11-13 | 22:24 | 11.6853 | 76669 | 76743 | 77113
15148 | 2021-11-13 | 22:24 | 11.6853 | 76664 | 76745 | 77107
15149 | 2021-11-13 | 22:24 | 11.6854 | 76660 | 76748 | 77101
15150 | 2021-11-13 | 22:24 | 11.6854 | 76656 | 76750 | 77094
15151 | 2021-11-13 | 22:24 | 11.6854 | 76651 | 76753 | 77088
15152 | 2021-11-13 | 22:24 | 11.6855 | 76647 | 76755 | 77082
15153 | 2021-11-13 | 22:24 | 11.6855 | 76643 | 76758 | 77076
15154 | 2021-11-13 | 22:24 | 11.6855 | 76639 | 76760 | 77070
15155 | 2021-11-13 | 22:24 | 11.6856 | 76636 | 76763 | 77064
15156 | 2021-11-13 | 22:24 | 11.6856 | 76632 | 76765 | 77058
15157 | 2021-11-13 | 22:24 | 11.6856 | 76629 | 76768 | 77052
15158 | 2021-11-13 | 22:24 | 11.6856 | 76626 | 76771 | 77045
15159 | 2021-11-13 | 22:24 | 11.6857 | 76622 | 76773 | 77040
15160 | 2021-11-13 | 22:24 | 11.6857 | 76620 | 76776 | 77033
15161 | 2021-11-13 | 22:24 | 11.6857 | 76617 | 76779 | 77028
15162 | 2021-11-13 | 22:24 | 11.6858 | 76614 | 76781 | 77022
15163 | 2021-11-13 | 22:24 | 11.6858 | 76612 | 76784 | 77016
15164 | 2021-11-13 | 22:24 | 11.6858 | 76610 | 76786 | 77010
15165 | 2021-11-13 | 22:24 | 11.6858 | 76607 | 76789 | 77005
15166 | 2021-11-13 | 22:24 | 11.6859 | 76606 | 76791 | 76999
15167 | 2021-11-13 | 22:24 | 11.6859 | 76604 | 76793 | 76993
15168 | 2021-11-13 | 22:24 | 11.6859 | 76602 | 76794 | 76988
15169 | 2021-11-13 | 22:24 | 11.686 | 76601 | 76796 | 76982
15170 | 2021-11-13 | 22:24 | 11.686 | 76599 | 76797 | 76977
15171 | 2021-11-13 | 22:24 | 11.686 | 76598 | 76798 | 76971
15172 | 2021-11-13 | 22:24 | 11.686 | 76597 | 76799 | 76966
15173 | 2021-11-13 | 22:24 | 11.6861 | 76596 | 76800 | 76960
15174 | 2021-11-13 | 22:24 | 11.6861 | 76595 | 76800 | 76955
15175 | 2021-11-13 | 22:24 | 11.6861 | 76595 | 76801 | 76949
15176 | 2021-11-13 | 22:24 | 11.6862 | 76594 | 76801 | 76944
15177 | 2021-11-13 | 22:24 | 11.6862 | 76594 | 76801 | 76938
15178 | 2021-11-13 | 22:24 | 11.6862 | 76593 | 76800 | 76932
15179 | 2021-11-13 | 22:24 | 11.6862 | 76593 | 76799 | 76927
15180 | 2021-11-13 | 22:24 | 11.6863 | 76593 | 76798 | 76921
15181 | 2021-11-13 | 22:24 | 11.6863 | 76593 | 76796 | 76916
15182 | 2021-11-13 | 22:24 | 11.6863 | 76593 | 76794 | 76910
15183 | 2021-11-13 | 22:24 | 11.6864 | 76593 | 76792 | 76905
15184 | 2021-11-13 | 22:24 | 11.6864 | 76593 | 76790 | 76899
15185 | 2021-11-13 | 22:24 | 11.6864 | 76593 | 76787 | 76894
15186 | 2021-11-13 | 22:24 | 11.6864 | 76593 | 76784 | 76888
15187 | 2021-11-13 | 22:24 | 11.6865 | 76593 | 76781 | 76883
15188 | 2021-11-13 | 22:24 | 11.6865 | 76593 | 76778 | 76877
15189 | 2021-11-13 | 22:24 | 11.6865 | 76593 | 76774 | 76872
15190 | 2021-11-13 | 22:24 | 11.6866 | 76593 | 76770 | 76866
15191 | 2021-11-13 | 22:24 | 11.6866 | 76593 | 76765 | 76861
15192 | 2021-11-13 | 22:24 | 11.6866 | 76593 | 76761 | 76855
15193 | 2021-11-13 | 22:24 | 11.6866 | 76593 | 76755 | 76850
15194 | 2021-11-13 | 22:24 | 11.6867 | 76593 | 76749 | 76844
15195 | 2021-11-13 | 22:24 | 11.6867 | 76593 | 76743 | 76839
15196 | 2021-11-13 | 22:24 | 11.6867 | 76592 | 76736 | 76833
15197 | 2021-11-13 | 22:24 | 11.6868 | 76592 | 76730 | 76828
15198 | 2021-11-13 | 22:24 | 11.6868 | 76592 | 76722 | 76823
15199 | 2021-11-13 | 22:24 | 11.6868 | 76591 | 76715 | 76817
15200 | 2021-11-13 | 22:24 | 11.6868 | 76591 | 76707 | 76812
15201 | 2021-11-13 | 22:24 | 11.6869 | 76590 | 76699 | 76807
15202 | 2021-11-13 | 22:24 | 11.6869 | 76590 | 76691 | 76802
15203 | 2021-11-13 | 22:24 | 11.6869 | 76589 | 76682 | 76797
15204 | 2021-11-13 | 22:24 | 11.687 | 76589 | 76674 | 76792
15205 | 2021-11-13 | 22:24 | 11.687 | 76588 | 76665 | 76786
15206 | 2021-11-13 | 22:24 | 11.687 | 76587 | 76656 | 76781
15207 | 2021-11-13 | 22:24 | 11.687 | 76587 | 76647 | 76776
15208 | 2021-11-13 | 22:24 | 11.6871 | 76586 | 76638 | 76771
15209 | 2021-11-13 | 22:24 | 11.6871 | 76585 | 76629 | 76766
15210 | 2021-11-13 | 22:24 | 11.6871 | 76585 | 76619 | 76761
15211 | 2021-11-13 | 22:24 | 11.6872 | 76584 | 76610 | 76756
15212 | 2021-11-13 | 22:24 | 11.6872 | 76583 | 76600 | 76751
15213 | 2021-11-13 | 22:24 | 11.6872 | 76582 | 76591 | 76746
15214 | 2021-11-13 | 22:24 | 11.6872 | 76582 | 76581 | 76741
15215 | 2021-11-13 | 22:24 | 11.6873 | 76581 | 76572 | 76736
15216 | 2021-11-13 | 22:24 | 11.6873 | 76581 | 76564 | 76731
15217 | 2021-11-13 | 22:24 | 11.6873 | 76580 | 76555 | 76726
15218 | 2021-11-13 | 22:24 | 11.6874 | 76580 | 76547 | 76720
15219 | 2021-11-13 | 22:24 | 11.6874 | 76580 | 76539 | 76715
15220 | 2021-11-13 | 22:24 | 11.6874 | 76579 | 76531 | 76710
15221 | 2021-11-13 | 22:24 | 11.6874 | 76579 | 76524 | 76705
15222 | 2021-11-13 | 22:24 | 11.6875 | 76579 | 76517 | 76700
15223 | 2021-11-13 | 22:24 | 11.6875 | 76580 | 76510 | 76695
15224 | 2021-11-13 | 22:24 | 11.6875 | 76580 | 76504 | 76690
15225 | 2021-11-13 | 22:24 | 11.6876 | 76580 | 76498 | 76685
15226 | 2021-11-13 | 22:24 | 11.6876 | 76581 | 76492 | 76681
15227 | 2021-11-13 | 22:24 | 11.6876 | 76582 | 76486 | 76676
15228 | 2021-11-13 | 22:24 | 11.6876 | 76583 | 76481 | 76671
15229 | 2021-11-13 | 22:24 | 11.6877 | 76584 | 76476 | 76667
15230 | 2021-11-13 | 22:24 | 11.6877 | 76585 | 76470 | 76662
15231 | 2021-11-13 | 22:24 | 11.6877 | 76586 | 76465 | 76658
15232 | 2021-11-13 | 22:24 | 11.6878 | 76588 | 76460 | 76654
15233 | 2021-11-13 | 22:24 | 11.6878 | 76590 | 76455 | 76650
15234 | 2021-11-13 | 22:24 | 11.6878 | 76592 | 76450 | 76646
15235 | 2021-11-13 | 22:24 | 11.6878 | 76594 | 76446 | 76642
15236 | 2021-11-13 | 22:24 | 11.6879 | 76596 | 76441 | 76638
15237 | 2021-11-13 | 22:24 | 11.6879 | 76598 | 76436 | 76634
15238 | 2021-11-13 | 22:24 | 11.6879 | 76600 | 76431 | 76631
15239 | 2021-11-13 | 22:24 | 11.688 | 76603 | 76426 | 76627
15240 | 2021-11-13 | 22:24 | 11.688 | 76605 | 76421 | 76624
15241 | 2021-11-13 | 22:24 | 11.688 | 76608 | 76416 | 76621
15242 | 2021-11-13 | 22:24 | 11.688 | 76610 | 76411 | 76618
15243 | 2021-11-13 | 22:24 | 11.6881 | 76613 | 76406 | 76615
15244 | 2021-11-13 | 22:24 | 11.6881 | 76616 | 76401 | 76613
15245 | 2021-11-13 | 22:24 | 11.6881 | 76619 | 76396 | 76610
15246 | 2021-11-13 | 22:24 | 11.6882 | 76622 | 76392 | 76608
15247 | 2021-11-13 | 22:24 | 11.6882 | 76624 | 76387 | 76605
15248 | 2021-11-13 | 22:24 | 11.6882 | 76627 | 76383 | 76603
15249 | 2021-11-13 | 22:24 | 11.6883 | 76630 | 76379 | 76601
15250 | 2021-11-13 | 22:24 | 11.6883 | 76633 | 76374 | 76600
15251 | 2021-11-13 | 22:24 | 11.6883 | 76636 | 76370 | 76598
15252 | 2021-11-13 | 22:24 | 11.6883 | 76639 | 76366 | 76596
15253 | 2021-11-13 | 22:24 | 11.6884 | 76641 | 76362 | 76595
15254 | 2021-11-13 | 22:24 | 11.6884 | 76644 | 76358 | 76594
15255 | 2021-11-13 | 22:24 | 11.6884 | 76646 | 76354 | 76592
15256 | 2021-11-13 | 22:24 | 11.6885 | 76648 | 76350 | 76591
15257 | 2021-11-13 | 22:24 | 11.6885 | 76650 | 76347 | 76590
15258 | 2021-11-13 | 22:24 | 11.6885 | 76652 | 76343 | 76589
15259 | 2021-11-13 | 22:24 | 11.6885 | 76653 | 76340 | 76588
15260 | 2021-11-13 | 22:24 | 11.6886 | 76655 | 76337 | 76588
15261 | 2021-11-13 | 22:24 | 11.6886 | 76656 | 76333 | 76587
15262 | 2021-11-13 | 22:24 | 11.6886 | 76656 | 76330 | 76587
15263 | 2021-11-13 | 22:24 | 11.6887 | 76657 | 76327 | 76586
15264 | 2021-11-13 | 22:24 | 11.6887 | 76657 | 76324 | 76586
15265 | 2021-11-13 | 22:24 | 11.6887 | 76657 | 76321 | 76586
15266 | 2021-11-13 | 22:24 | 11.6887 | 76657 | 76319 | 76585
15267 | 2021-11-13 | 22:24 | 11.6888 | 76656 | 76316 | 76585
15268 | 2021-11-13 | 22:24 | 11.6888 | 76656 | 76313 | 76585
15269 | 2021-11-13 | 22:24 | 11.6888 | 76655 | 76310 | 76585
15270 | 2021-11-13 | 22:24 | 11.6889 | 76653 | 76307 | 76585
15271 | 2021-11-13 | 22:24 | 11.6889 | 76652 | 76304 | 76585
15272 | 2021-11-13 | 22:24 | 11.6889 | 76650 | 76301 | 76585
15273 | 2021-11-13 | 22:24 | 11.6889 | 76647 | 76297 | 76585
15274 | 2021-11-13 | 22:24 | 11.689 | 76645 | 76294 | 76586
15275 | 2021-11-13 | 22:24 | 11.689 | 76642 | 76290 | 76586
15276 | 2021-11-13 | 22:24 | 11.689 | 76639 | 76287 | 76586
15277 | 2021-11-13 | 22:24 | 11.6891 | 76636 | 76283 | 76586
15278 | 2021-11-13 | 22:24 | 11.6891 | 76632 | 76280 | 76586
15279 | 2021-11-13 | 22:24 | 11.6891 | 76629 | 76276 | 76587
15280 | 2021-11-13 | 22:24 | 11.6891 | 76625 | 76272 | 76587
15281 | 2021-11-13 | 22:24 | 11.6892 | 76620 | 76268 | 76587
15282 | 2021-11-13 | 22:24 | 11.6892 | 76616 | 76264 | 76587
15283 | 2021-11-13 | 22:24 | 11.6892 | 76611 | 76260 | 76587
15284 | 2021-11-13 | 22:24 | 11.6893 | 76606 | 76256 | 76588
15285 | 2021-11-13 | 22:24 | 11.6893 | 76601 | 76252 | 76588
15286 | 2021-11-13 | 22:24 | 11.6893 | 76595 | 76248 | 76588
15287 | 2021-11-13 | 22:24 | 11.6893 | 76590 | 76244 | 76588
15288 | 2021-11-13 | 22:24 | 11.6894 | 76584 | 76240 | 76588
15289 | 2021-11-13 | 22:24 | 11.6894 | 76578 | 76236 | 76588
15290 | 2021-11-13 | 22:24 | 11.6894 | 76572 | 76232 | 76588
15291 | 2021-11-13 | 22:24 | 11.6895 | 76566 | 76229 | 76587
15292 | 2021-11-13 | 22:24 | 11.6895 | 76560 | 76225 | 76587
15293 | 2021-11-13 | 22:24 | 11.6895 | 76554 | 76221 | 76587
15294 | 2021-11-13 | 22:24 | 11.6895 | 76547 | 76217 | 76587
15295 | 2021-11-13 | 22:24 | 11.6896 | 76541 | 76214 | 76587
15296 | 2021-11-13 | 22:24 | 11.6896 | 76534 | 76210 | 76586
15297 | 2021-11-13 | 22:24 | 11.6896 | 76528 | 76207 | 76586
15298 | 2021-11-13 | 22:24 | 11.6897 | 76521 | 76203 | 76586
15299 | 2021-11-13 | 22:24 | 11.6897 | 76514 | 76200 | 76585
15300 | 2021-11-13 | 22:24 | 11.6897 | 76508 | 76197 | 76585
15301 | 2021-11-13 | 22:24 | 11.6897 | 76501 | 76193 | 76585
15302 | 2021-11-13 | 22:24 | 11.6898 | 76494 | 76190 | 76584
15303 | 2021-11-13 | 22:24 | 11.6898 | 76487 | 76187 | 76584
15304 | 2021-11-13 | 22:24 | 11.6898 | 76480 | 76184 | 76584
15305 | 2021-11-13 | 22:24 | 11.6899 | 76473 | 76180 | 76584
15306 | 2021-11-13 | 22:24 | 11.6899 | 76467 | 76177 | 76583
15307 | 2021-11-13 | 22:24 | 11.6899 | 76460 | 76174 | 76583
15308 | 2021-11-13 | 22:24 | 11.6899 | 76453 | 76171 | 76583
15309 | 2021-11-13 | 22:24 | 11.69 | 76447 | 76168 | 76583
15310 | 2021-11-13 | 22:24 | 11.69 | 76440 | 76165 | 76583
15311 | 2021-11-13 | 22:24 | 11.69 | 76434 | 76162 | 76583
15312 | 2021-11-13 | 22:24 | 11.6901 | 76428 | 76159 | 76583
15313 | 2021-11-13 | 22:24 | 11.6901 | 76422 | 76157 | 76583
15314 | 2021-11-13 | 22:24 | 11.6901 | 76416 | 76154 | 76584
15315 | 2021-11-13 | 22:24 | 11.6901 | 76410 | 76151 | 76584
15316 | 2021-11-13 | 22:24 | 11.6902 | 76404 | 76148 | 76584
15317 | 2021-11-13 | 22:24 | 11.6902 | 76398 | 76145 | 76585
15318 | 2021-11-13 | 22:24 | 11.6902 | 76393 | 76143 | 76586
15319 | 2021-11-13 | 22:24 | 11.6903 | 76387 | 76140 | 76586
15320 | 2021-11-13 | 22:24 | 11.6903 | 76382 | 76137 | 76587
15321 | 2021-11-13 | 22:24 | 11.6903 | 76376 | 76135 | 76588
15322 | 2021-11-13 | 22:24 | 11.6903 | 76371 | 76132 | 76589
15323 | 2021-11-13 | 22:24 | 11.6904 | 76366 | 76130 | 76590
15324 | 2021-11-13 | 22:24 | 11.6904 | 76361 | 76127 | 76591
15325 | 2021-11-13 | 22:24 | 11.6904 | 76356 | 76125 | 76592
15326 | 2021-11-13 | 22:24 | 11.6905 | 76351 | 76122 | 76593
15327 | 2021-11-13 | 22:24 | 11.6905 | 76347 | 76120 | 76595
15328 | 2021-11-13 | 22:24 | 11.6905 | 76342 | 76118 | 76596
15329 | 2021-11-13 | 22:24 | 11.6905 | 76338 | 76116 | 76597
15330 | 2021-11-13 | 22:24 | 11.6906 | 76333 | 76114 | 76598
15331 | 2021-11-13 | 22:24 | 11.6906 | 76329 | 76113 | 76600
15332 | 2021-11-13 | 22:24 | 11.6906 | 76325 | 76111 | 76601
15333 | 2021-11-13 | 22:24 | 11.6907 | 76321 | 76109 | 76602
15334 | 2021-11-13 | 22:24 | 11.6907 | 76317 | 76108 | 76603
15335 | 2021-11-13 | 22:24 | 11.6907 | 76313 | 76106 | 76605
15336 | 2021-11-13 | 22:24 | 11.6907 | 76309 | 76105 | 76606
15337 | 2021-11-13 | 22:24 | 11.6908 | 76305 | 76104 | 76607
15338 | 2021-11-13 | 22:24 | 11.6908 | 76302 | 76103 | 76608
15339 | 2021-11-13 | 22:24 | 11.6908 | 76298 | 76102 | 76609
15340 | 2021-11-13 | 22:24 | 11.6909 | 76294 | 76101 | 76610
15341 | 2021-11-13 | 22:24 | 11.6909 | 76290 | 76100 | 76610
15342 | 2021-11-13 | 22:24 | 11.6909 | 76286 | 76099 | 76611
15343 | 2021-11-13 | 22:24 | 11.691 | 76282 | 76099 | 76612
15344 | 2021-11-13 | 22:24 | 11.691 | 76278 | 76098 | 76612
15345 | 2021-11-13 | 22:24 | 11.691 | 76274 | 76098 | 76612
15346 | 2021-11-13 | 22:24 | 11.691 | 76270 | 76097 | 76612
15347 | 2021-11-13 | 22:24 | 11.6911 | 76266 | 76097 | 76612
15348 | 2021-11-13 | 22:24 | 11.6911 | 76261 | 76097 | 76612
15349 | 2021-11-13 | 22:24 | 11.6911 | 76257 | 76097 | 76611
15350 | 2021-11-13 | 22:24 | 11.6912 | 76253 | 76096 | 76610
15351 | 2021-11-13 | 22:24 | 11.6912 | 76248 | 76096 | 76609
15352 | 2021-11-13 | 22:24 | 11.6912 | 76244 | 76096 | 76608
15353 | 2021-11-13 | 22:24 | 11.6912 | 76239 | 76096 | 76606
15354 | 2021-11-13 | 22:24 | 11.6913 | 76235 | 76096 | 76605
15355 | 2021-11-13 | 22:24 | 11.6913 | 76230 | 76096 | 76603
15356 | 2021-11-13 | 22:24 | 11.6913 | 76225 | 76096 | 76601
15357 | 2021-11-13 | 22:24 | 11.6914 | 76220 | 76096 | 76599
15358 | 2021-11-13 | 22:24 | 11.6914 | 76215 | 76096 | 76596
15359 | 2021-11-13 | 22:24 | 11.6914 | 76210 | 76096 | 76594
15360 | 2021-11-13 | 22:24 | 11.6914 | 76204 | 76097 | 76591
15361 | 2021-11-13 | 22:24 | 11.6915 | 76199 | 76097 | 76587
15362 | 2021-11-13 | 22:24 | 11.6915 | 76193 | 76097 | 76584
15363 | 2021-11-13 | 22:24 | 11.6915 | 76188 | 76097 | 76581
15364 | 2021-11-13 | 22:24 | 11.6916 | 76182 | 76097 | 76577
15365 | 2021-11-13 | 22:24 | 11.6916 | 76177 | 76098 | 76573
15366 | 2021-11-13 | 22:24 | 11.6916 | 76171 | 76098 | 76568
15367 | 2021-11-13 | 22:24 | 11.6916 | 76166 | 76098 | 76564
15368 | 2021-11-13 | 22:24 | 11.6917 | 76160 | 76098 | 76559
15369 | 2021-11-13 | 22:24 | 11.6917 | 76154 | 76098 | 76554
15370 | 2021-11-13 | 22:24 | 11.6917 | 76149 | 76099 | 76549
15371 | 2021-11-13 | 22:24 | 11.6918 | 76143 | 76099 | 76544
15372 | 2021-11-13 | 22:24 | 11.6918 | 76138 | 76099 | 76538
15373 | 2021-11-13 | 22:24 | 11.6918 | 76133 | 76099 | 76533
15374 | 2021-11-13 | 22:24 | 11.6918 | 76127 | 76099 | 76527
15375 | 2021-11-13 | 22:24 | 11.6919 | 76122 | 76100 | 76521
15376 | 2021-11-13 | 22:24 | 11.6919 | 76117 | 76100 | 76515
15377 | 2021-11-13 | 22:24 | 11.6919 | 76112 | 76100 | 76510
15378 | 2021-11-13 | 22:24 | 11.692 | 76107 | 76100 | 76504
15379 | 2021-11-13 | 22:24 | 11.692 | 76102 | 76100 | 76498
15380 | 2021-11-13 | 22:24 | 11.692 | 76097 | 76100 | 76491
15381 | 2021-11-13 | 22:24 | 11.692 | 76093 | 76100 | 76485
15382 | 2021-11-13 | 22:24 | 11.6921 | 76088 | 76100 | 76479
15383 | 2021-11-13 | 22:24 | 11.6921 | 76084 | 76099 | 76473
15384 | 2021-11-13 | 22:24 | 11.6921 | 76079 | 76099 | 76467
15385 | 2021-11-13 | 22:24 | 11.6922 | 76075 | 76099 | 76461
15386 | 2021-11-13 | 22:24 | 11.6922 | 76071 | 76099 | 76455
15387 | 2021-11-13 | 22:24 | 11.6922 | 76067 | 76099 | 76448
15388 | 2021-11-13 | 22:24 | 11.6922 | 76063 | 76098 | 76442
15389 | 2021-11-13 | 22:24 | 11.6923 | 76059 | 76098 | 76436
15390 | 2021-11-13 | 22:24 | 11.6923 | 76056 | 76098 | 76430
15391 | 2021-11-13 | 22:24 | 11.6923 | 76052 | 76097 | 76423
15392 | 2021-11-13 | 22:24 | 11.6924 | 76048 | 76097 | 76417
15393 | 2021-11-13 | 22:24 | 11.6924 | 76045 | 76096 | 76411
15394 | 2021-11-13 | 22:24 | 11.6924 | 76042 | 76096 | 76405
15395 | 2021-11-13 | 22:24 | 11.6924 | 76038 | 76096 | 76399
15396 | 2021-11-13 | 22:24 | 11.6925 | 76035 | 76095 | 76393
15397 | 2021-11-13 | 22:24 | 11.6925 | 76032 | 76095 | 76387
15398 | 2021-11-13 | 22:24 | 11.6925 | 76029 | 76095 | 76381
15399 | 2021-11-13 | 22:24 | 11.6926 | 76026 | 76095 | 76376
15400 | 2021-11-13 | 22:24 | 11.6926 | 76023 | 76094 | 76370
15401 | 2021-11-13 | 22:24 | 11.6926 | 76020 | 76094 | 76364
15402 | 2021-11-13 | 22:24 | 11.6926 | 76018 | 76094 | 76358
15403 | 2021-11-13 | 22:24 | 11.6927 | 76015 | 76094 | 76353
15404 | 2021-11-13 | 22:24 | 11.6927 | 76012 | 76094 | 76347
15405 | 2021-11-13 | 22:24 | 11.6927 | 76010 | 76094 | 76342
15406 | 2021-11-13 | 22:24 | 11.6928 | 76007 | 76094 | 76337
15407 | 2021-11-13 | 22:24 | 11.6928 | 76005 | 76094 | 76332
15408 | 2021-11-13 | 22:24 | 11.6928 | 76003 | 76094 | 76326
15409 | 2021-11-13 | 22:24 | 11.6928 | 76000 | 76094 | 76321
15410 | 2021-11-13 | 22:24 | 11.6929 | 75998 | 76094 | 76316
15411 | 2021-11-13 | 22:24 | 11.6929 | 75996 | 76094 | 76311
15412 | 2021-11-13 | 22:24 | 11.6929 | 75994 | 76094 | 76306
15413 | 2021-11-13 | 22:24 | 11.693 | 75992 | 76095 | 76301
15414 | 2021-11-13 | 22:24 | 11.693 | 75991 | 76095 | 76296
15415 | 2021-11-13 | 22:24 | 11.693 | 75989 | 76095 | 76291
15416 | 2021-11-13 | 22:24 | 11.693 | 75987 | 76095 | 76286
15417 | 2021-11-13 | 22:24 | 11.6931 | 75986 | 76095 | 76282
15418 | 2021-11-13 | 22:24 | 11.6931 | 75985 | 76096 | 76277
15419 | 2021-11-13 | 22:24 | 11.6931 | 75983 | 76096 | 76273
15420 | 2021-11-13 | 22:24 | 11.6932 | 75982 | 76096 | 76268
15421 | 2021-11-13 | 22:24 | 11.6932 | 75981 | 76096 | 76264
15422 | 2021-11-13 | 22:24 | 11.6932 | 75980 | 76096 | 76259
15423 | 2021-11-13 | 22:24 | 11.6932 | 75979 | 76095 | 76255
15424 | 2021-11-13 | 22:24 | 11.6933 | 75978 | 76095 | 76250
15425 | 2021-11-13 | 22:24 | 11.6933 | 75977 | 76095 | 76246
15426 | 2021-11-13 | 22:24 | 11.6933 | 75976 | 76094 | 76242
15427 | 2021-11-13 | 22:24 | 11.6934 | 75975 | 76094 | 76238
15428 | 2021-11-13 | 22:24 | 11.6934 | 75975 | 76093 | 76233
15429 | 2021-11-13 | 22:24 | 11.6934 | 75974 | 76092 | 76229
15430 | 2021-11-13 | 22:24 | 11.6934 | 75974 | 76091 | 76225
15431 | 2021-11-13 | 22:24 | 11.6935 | 75973 | 76090 | 76220
15432 | 2021-11-13 | 22:24 | 11.6935 | 75973 | 76089 | 76216
15433 | 2021-11-13 | 22:24 | 11.6935 | 75972 | 76087 | 76211
15434 | 2021-11-13 | 22:24 | 11.6936 | 75972 | 76086 | 76207
15435 | 2021-11-13 | 22:24 | 11.6936 | 75972 | 76084 | 76203
15436 | 2021-11-13 | 22:24 | 11.6936 | 75972 | 76082 | 76198
15437 | 2021-11-13 | 22:24 | 11.6937 | 75971 | 76080 | 76194
15438 | 2021-11-13 | 22:24 | 11.6937 | 75971 | 76078 | 76189
15439 | 2021-11-13 | 22:24 | 11.6937 | 75971 | 76076 | 76185
15440 | 2021-11-13 | 22:24 | 11.6937 | 75971 | 76073 | 76180
15441 | 2021-11-13 | 22:24 | 11.6938 | 75971 | 76071 | 76176
15442 | 2021-11-13 | 22:24 | 11.6938 | 75971 | 76069 | 76172
15443 | 2021-11-13 | 22:24 | 11.6938 | 75971 | 76066 | 76167
15444 | 2021-11-13 | 22:24 | 11.6939 | 75972 | 76063 | 76163
15445 | 2021-11-13 | 22:24 | 11.6939 | 75972 | 76061 | 76159
15446 | 2021-11-13 | 22:24 | 11.6939 | 75972 | 76058 | 76154
15447 | 2021-11-13 | 22:24 | 11.6939 | 75972 | 76055 | 76150
15448 | 2021-11-13 | 22:24 | 11.694 | 75972 | 76052 | 76146
15449 | 2021-11-13 | 22:24 | 11.694 | 75973 | 76048 | 76142
15450 | 2021-11-13 | 22:24 | 11.694 | 75973 | 76045 | 76138
15451 | 2021-11-13 | 22:24 | 11.6941 | 75973 | 76041 | 76134
15452 | 2021-11-13 | 22:24 | 11.6941 | 75973 | 76037 | 76130
15453 | 2021-11-13 | 22:24 | 11.6941 | 75973 | 76034 | 76126
15454 | 2021-11-13 | 22:24 | 11.6941 | 75974 | 76030 | 76122
15455 | 2021-11-13 | 22:24 | 11.6942 | 75974 | 76026 | 76118
15456 | 2021-11-13 | 22:24 | 11.6942 | 75974 | 76022 | 76114
15457 | 2021-11-13 | 22:24 | 11.6942 | 75974 | 76018 | 76111
15458 | 2021-11-13 | 22:24 | 11.6943 | 75975 | 76015 | 76107
15459 | 2021-11-13 | 22:24 | 11.6943 | 75975 | 76011 | 76103
15460 | 2021-11-13 | 22:24 | 11.6943 | 75975 | 76007 | 76100
15461 | 2021-11-13 | 22:24 | 11.6943 | 75975 | 76003 | 76097
15462 | 2021-11-13 | 22:24 | 11.6944 | 75975 | 75999 | 76093
15463 | 2021-11-13 | 22:24 | 11.6944 | 75976 | 75995 | 76090
15464 | 2021-11-13 | 22:24 | 11.6944 | 75976 | 75991 | 76087
15465 | 2021-11-13 | 22:24 | 11.6945 | 75976 | 75986 | 76084
15466 | 2021-11-13 | 22:24 | 11.6945 | 75976 | 75982 | 76080
15467 | 2021-11-13 | 22:24 | 11.6945 | 75976 | 75978 | 76077
15468 | 2021-11-13 | 22:24 | 11.6945 | 75977 | 75973 | 76074
15469 | 2021-11-13 | 22:24 | 11.6946 | 75977 | 75969 | 76071
15470 | 2021-11-13 | 22:24 | 11.6946 | 75977 | 75965 | 76068
15471 | 2021-11-13 | 22:24 | 11.6946 | 75978 | 75960 | 76065
15472 | 2021-11-13 | 22:24 | 11.6947 | 75978 | 75956 | 76062
15473 | 2021-11-13 | 22:24 | 11.6947 | 75978 | 75952 | 76059
15474 | 2021-11-13 | 22:24 | 11.6947 | 75978 | 75947 | 76057
15475 | 2021-11-13 | 22:24 | 11.6947 | 75978 | 75943 | 76054
15476 | 2021-11-13 | 22:24 | 11.6948 | 75979 | 75938 | 76051
15477 | 2021-11-13 | 22:24 | 11.6948 | 75979 | 75934 | 76049
15478 | 2021-11-13 | 22:24 | 11.6948 | 75979 | 75930 | 76046
15479 | 2021-11-13 | 22:24 | 11.6949 | 75980 | 75926 | 76044
15480 | 2021-11-13 | 22:24 | 11.6949 | 75980 | 75921 | 76041
15481 | 2021-11-13 | 22:24 | 11.6949 | 75980 | 75917 | 76039
15482 | 2021-11-13 | 22:24 | 11.6949 | 75981 | 75913 | 76037
15483 | 2021-11-13 | 22:24 | 11.695 | 75981 | 75909 | 76034
15484 | 2021-11-13 | 22:24 | 11.695 | 75981 | 75905 | 76032
15485 | 2021-11-13 | 22:24 | 11.695 | 75981 | 75900 | 76030
15486 | 2021-11-13 | 22:24 | 11.6951 | 75982 | 75896 | 76028
15487 | 2021-11-13 | 22:24 | 11.6951 | 75982 | 75892 | 76026
15488 | 2021-11-13 | 22:24 | 11.6951 | 75982 | 75888 | 76024
15489 | 2021-11-13 | 22:24 | 11.6951 | 75983 | 75884 | 76022
15490 | 2021-11-13 | 22:24 | 11.6952 | 75983 | 75880 | 76021
15491 | 2021-11-13 | 22:24 | 11.6952 | 75983 | 75876 | 76019
15492 | 2021-11-13 | 22:24 | 11.6952 | 75984 | 75872 | 76017
15493 | 2021-11-13 | 22:24 | 11.6953 | 75984 | 75868 | 76016
15494 | 2021-11-13 | 22:24 | 11.6953 | 75984 | 75864 | 76014
15495 | 2021-11-13 | 22:24 | 11.6953 | 75984 | 75859 | 76013
15496 | 2021-11-13 | 22:24 | 11.6953 | 75985 | 75855 | 76011
15497 | 2021-11-13 | 22:24 | 11.6954 | 75985 | 75851 | 76010
15498 | 2021-11-13 | 22:24 | 11.6954 | 75985 | 75847 | 76009
15499 | 2021-11-13 | 22:24 | 11.6954 | 75985 | 75843 | 76007
15500 | 2021-11-13 | 22:24 | 11.6955 | 75985 | 75839 | 76006
15501 | 2021-11-13 | 22:24 | 11.6955 | 75985 | 75835 | 76005
15502 | 2021-11-13 | 22:24 | 11.6955 | 75986 | 75831 | 76004
15503 | 2021-11-13 | 22:24 | 11.6955 | 75986 | 75828 | 76003
15504 | 2021-11-13 | 22:24 | 11.6956 | 75986 | 75824 | 76002
15505 | 2021-11-13 | 22:24 | 11.6956 | 75986 | 75820 | 76002
15506 | 2021-11-13 | 22:24 | 11.6956 | 75986 | 75815 | 76001
15507 | 2021-11-13 | 22:24 | 11.6957 | 75986 | 75811 | 76000
15508 | 2021-11-13 | 22:24 | 11.6957 | 75986 | 75808 | 75999
15509 | 2021-11-13 | 22:24 | 11.6957 | 75986 | 75804 | 75999
15510 | 2021-11-13 | 22:24 | 11.6957 | 75985 | 75800 | 75998
15511 | 2021-11-13 | 22:24 | 11.6958 | 75985 | 75796 | 75998
15512 | 2021-11-13 | 22:24 | 11.6958 | 75985 | 75793 | 75997
15513 | 2021-11-13 | 22:24 | 11.6958 | 75985 | 75789 | 75997
15514 | 2021-11-13 | 22:24 | 11.6959 | 75985 | 75785 | 75996
15515 | 2021-11-13 | 22:24 | 11.6959 | 75984 | 75782 | 75996
15516 | 2021-11-13 | 22:24 | 11.6959 | 75984 | 75778 | 75996
15517 | 2021-11-13 | 22:24 | 11.6959 | 75983 | 75775 | 75995
15518 | 2021-11-13 | 22:24 | 11.696 | 75982 | 75771 | 75995
15519 | 2021-11-13 | 22:24 | 11.696 | 75981 | 75768 | 75995
15520 | 2021-11-13 | 22:24 | 11.696 | 75981 | 75765 | 75995
15521 | 2021-11-13 | 22:24 | 11.6961 | 75980 | 75761 | 75995
15522 | 2021-11-13 | 22:24 | 11.6961 | 75979 | 75758 | 75994
15523 | 2021-11-13 | 22:24 | 11.6961 | 75978 | 75755 | 75994
15524 | 2021-11-13 | 22:24 | 11.6961 | 75977 | 75752 | 75994
15525 | 2021-11-13 | 22:24 | 11.6962 | 75975 | 75749 | 75994
15526 | 2021-11-13 | 22:24 | 11.6962 | 75974 | 75746 | 75994
15527 | 2021-11-13 | 22:24 | 11.6962 | 75972 | 75743 | 75994
15528 | 2021-11-13 | 22:24 | 11.6963 | 75971 | 75740 | 75994
15529 | 2021-11-13 | 22:24 | 11.6963 | 75970 | 75737 | 75995
15530 | 2021-11-13 | 22:24 | 11.6963 | 75968 | 75734 | 75995
15531 | 2021-11-13 | 22:24 | 11.6964 | 75967 | 75731 | 75995
15532 | 2021-11-13 | 22:24 | 11.6964 | 75965 | 75728 | 75995
15533 | 2021-11-13 | 22:24 | 11.6964 | 75964 | 75726 | 75995
15534 | 2021-11-13 | 22:24 | 11.6964 | 75962 | 75723 | 75995
15535 | 2021-11-13 | 22:24 | 11.6965 | 75960 | 75721 | 75995
15536 | 2021-11-13 | 22:24 | 11.6965 | 75958 | 75718 | 75995
15537 | 2021-11-13 | 22:24 | 11.6965 | 75956 | 75716 | 75995
15538 | 2021-11-13 | 22:24 | 11.6966 | 75954 | 75713 | 75995
15539 | 2021-11-13 | 22:24 | 11.6966 | 75951 | 75711 | 75995
15540 | 2021-11-13 | 22:24 | 11.6966 | 75949 | 75709 | 75995
15541 | 2021-11-13 | 22:24 | 11.6966 | 75947 | 75707 | 75995
15542 | 2021-11-13 | 22:24 | 11.6967 | 75945 | 75705 | 75995
15543 | 2021-11-13 | 22:24 | 11.6967 | 75943 | 75702 | 75995
15544 | 2021-11-13 | 22:24 | 11.6967 | 75941 | 75700 | 75995
15545 | 2021-11-13 | 22:24 | 11.6968 | 75939 | 75698 | 75995
15546 | 2021-11-13 | 22:24 | 11.6968 | 75936 | 75697 | 75995
15547 | 2021-11-13 | 22:24 | 11.6968 | 75934 | 75695 | 75995
15548 | 2021-11-13 | 22:24 | 11.6968 | 75931 | 75693 | 75995
15549 | 2021-11-13 | 22:24 | 11.6969 | 75929 | 75691 | 75995
15550 | 2021-11-13 | 22:24 | 11.6969 | 75927 | 75689 | 75995
15551 | 2021-11-13 | 22:24 | 11.6969 | 75924 | 75688 | 75995
15552 | 2021-11-13 | 22:24 | 11.697 | 75922 | 75686 | 75994
15553 | 2021-11-13 | 22:24 | 11.697 | 75920 | 75685 | 75994
15554 | 2021-11-13 | 22:24 | 11.697 | 75918 | 75683 | 75994
15555 | 2021-11-13 | 22:24 | 11.697 | 75916 | 75681 | 75994
15556 | 2021-11-13 | 22:24 | 11.6971 | 75913 | 75680 | 75994
15557 | 2021-11-13 | 22:24 | 11.6971 | 75911 | 75678 | 75994
15558 | 2021-11-13 | 22:24 | 11.6971 | 75908 | 75677 | 75994
15559 | 2021-11-13 | 22:24 | 11.6972 | 75906 | 75675 | 75994
15560 | 2021-11-13 | 22:24 | 11.6972 | 75903 | 75673 | 75994
15561 | 2021-11-13 | 22:24 | 11.6972 | 75901 | 75672 | 75993
15562 | 2021-11-13 | 22:24 | 11.6972 | 75898 | 75670 | 75993
15563 | 2021-11-13 | 22:24 | 11.6973 | 75896 | 75669 | 75993
15564 | 2021-11-13 | 22:24 | 11.6973 | 75894 | 75667 | 75993
15565 | 2021-11-13 | 22:24 | 11.6973 | 75891 | 75666 | 75993
15566 | 2021-11-13 | 22:24 | 11.6974 | 75889 | 75664 | 75993
15567 | 2021-11-13 | 22:24 | 11.6974 | 75886 | 75663 | 75993
15568 | 2021-11-13 | 22:24 | 11.6974 | 75883 | 75661 | 75993
15569 | 2021-11-13 | 22:24 | 11.6974 | 75880 | 75660 | 75993
15570 | 2021-11-13 | 22:24 | 11.6975 | 75877 | 75658 | 75992
15571 | 2021-11-13 | 22:24 | 11.6975 | 75875 | 75657 | 75992
15572 | 2021-11-13 | 22:24 | 11.6975 | 75872 | 75655 | 75992
15573 | 2021-11-13 | 22:24 | 11.6976 | 75869 | 75654 | 75992
15574 | 2021-11-13 | 22:24 | 11.6976 | 75866 | 75652 | 75992
15575 | 2021-11-13 | 22:24 | 11.6976 | 75863 | 75651 | 75992
15576 | 2021-11-13 | 22:24 | 11.6976 | 75860 | 75650 | 75992
15577 | 2021-11-13 | 22:24 | 11.6977 | 75857 | 75648 | 75992
15578 | 2021-11-13 | 22:24 | 11.6977 | 75854 | 75647 | 75991
15579 | 2021-11-13 | 22:24 | 11.6977 | 75851 | 75646 | 75991
15580 | 2021-11-13 | 22:24 | 11.6978 | 75847 | 75644 | 75991
15581 | 2021-11-13 | 22:24 | 11.6978 | 75844 | 75643 | 75990
15582 | 2021-11-13 | 22:24 | 11.6978 | 75841 | 75642 | 75990
15583 | 2021-11-13 | 22:24 | 11.6978 | 75838 | 75641 | 75989
15584 | 2021-11-13 | 22:24 | 11.6979 | 75834 | 75640 | 75989
15585 | 2021-11-13 | 22:24 | 11.6979 | 75831 | 75639 | 75988
15586 | 2021-11-13 | 22:24 | 11.6979 | 75828 | 75638 | 75988
15587 | 2021-11-13 | 22:24 | 11.698 | 75825 | 75637 | 75987
15588 | 2021-11-13 | 22:24 | 11.698 | 75822 | 75636 | 75987
15589 | 2021-11-13 | 22:24 | 11.698 | 75819 | 75636 | 75986
15590 | 2021-11-13 | 22:24 | 11.698 | 75815 | 75635 | 75985
15591 | 2021-11-13 | 22:24 | 11.6981 | 75812 | 75634 | 75984
15592 | 2021-11-13 | 22:24 | 11.6981 | 75809 | 75634 | 75983
15593 | 2021-11-13 | 22:24 | 11.6981 | 75805 | 75633 | 75982
15594 | 2021-11-13 | 22:24 | 11.6982 | 75802 | 75633 | 75981
15595 | 2021-11-13 | 22:24 | 11.6982 | 75799 | 75632 | 75980
15596 | 2021-11-13 | 22:24 | 11.6982 | 75796 | 75632 | 75979
15597 | 2021-11-13 | 22:24 | 11.6982 | 75792 | 75632 | 75978
15598 | 2021-11-13 | 22:24 | 11.6983 | 75789 | 75631 | 75977
15599 | 2021-11-13 | 22:24 | 11.6983 | 75785 | 75631 | 75975
15600 | 2021-11-13 | 22:24 | 11.6983 | 75782 | 75631 | 75973
15601 | 2021-11-13 | 22:24 | 11.6984 | 75778 | 75631 | 75971
15602 | 2021-11-13 | 22:24 | 11.6984 | 75775 | 75631 | 75970
15603 | 2021-11-13 | 22:24 | 11.6984 | 75771 | 75631 | 75968
15604 | 2021-11-13 | 22:24 | 11.6984 | 75768 | 75630 | 75966
15605 | 2021-11-13 | 22:24 | 11.6985 | 75765 | 75630 | 75964
15606 | 2021-11-13 | 22:24 | 11.6985 | 75762 | 75630 | 75962
15607 | 2021-11-13 | 22:24 | 11.6985 | 75759 | 75630 | 75959
15608 | 2021-11-13 | 22:24 | 11.6986 | 75756 | 75630 | 75957
15609 | 2021-11-13 | 22:24 | 11.6986 | 75753 | 75630 | 75955
15610 | 2021-11-13 | 22:24 | 11.6986 | 75750 | 75630 | 75952
15611 | 2021-11-13 | 22:24 | 11.6986 | 75747 | 75630 | 75950
15612 | 2021-11-13 | 22:24 | 11.6987 | 75744 | 75630 | 75947
15613 | 2021-11-13 | 22:24 | 11.6987 | 75742 | 75630 | 75944
15614 | 2021-11-13 | 22:24 | 11.6987 | 75739 | 75630 | 75942
15615 | 2021-11-13 | 22:24 | 11.6988 | 75737 | 75630 | 75939
15616 | 2021-11-13 | 22:24 | 11.6988 | 75735 | 75630 | 75937
15617 | 2021-11-13 | 22:24 | 11.6988 | 75732 | 75630 | 75934
15618 | 2021-11-13 | 22:24 | 11.6988 | 75730 | 75630 | 75931
15619 | 2021-11-13 | 22:24 | 11.6989 | 75728 | 75630 | 75928
15620 | 2021-11-13 | 22:24 | 11.6989 | 75727 | 75630 | 75925
15621 | 2021-11-13 | 22:24 | 11.6989 | 75725 | 75630 | 75922
15622 | 2021-11-13 | 22:24 | 11.699 | 75723 | 75630 | 75919
15623 | 2021-11-13 | 22:24 | 11.699 | 75721 | 75630 | 75916
15624 | 2021-11-13 | 22:24 | 11.699 | 75720 | 75630 | 75912
15625 | 2021-11-13 | 22:24 | 11.6991 | 75718 | 75630 | 75909
15626 | 2021-11-13 | 22:24 | 11.6991 | 75717 | 75630 | 75906
15627 | 2021-11-13 | 22:24 | 11.6991 | 75715 | 75629 | 75903
15628 | 2021-11-13 | 22:24 | 11.6991 | 75714 | 75629 | 75900
15629 | 2021-11-13 | 22:24 | 11.6992 | 75713 | 75629 | 75897
15630 | 2021-11-13 | 22:24 | 11.6992 | 75712 | 75629 | 75893
15631 | 2021-11-13 | 22:24 | 11.6992 | 75710 | 75628 | 75890
15632 | 2021-11-13 | 22:24 | 11.6993 | 75709 | 75628 | 75886
15633 | 2021-11-13 | 22:24 | 11.6993 | 75708 | 75627 | 75883
15634 | 2021-11-13 | 22:24 | 11.6993 | 75707 | 75627 | 75880
15635 | 2021-11-13 | 22:24 | 11.6993 | 75706 | 75626 | 75876
15636 | 2021-11-13 | 22:24 | 11.6994 | 75705 | 75626 | 75873
15637 | 2021-11-13 | 22:24 | 11.6994 | 75704 | 75625 | 75870
15638 | 2021-11-13 | 22:24 | 11.6994 | 75703 | 75625 | 75866
15639 | 2021-11-13 | 22:24 | 11.6995 | 75702 | 75624 | 75863
15640 | 2021-11-13 | 22:24 | 11.6995 | 75701 | 75624 | 75859
15641 | 2021-11-13 | 22:24 | 11.6995 | 75700 | 75623 | 75856
15642 | 2021-11-13 | 22:24 | 11.6995 | 75699 | 75623 | 75852
15643 | 2021-11-13 | 22:24 | 11.6996 | 75698 | 75622 | 75848
15644 | 2021-11-13 | 22:24 | 11.6996 | 75697 | 75621 | 75844
15645 | 2021-11-13 | 22:24 | 11.6996 | 75696 | 75621 | 75840
15646 | 2021-11-13 | 22:24 | 11.6997 | 75695 | 75620 | 75836
15647 | 2021-11-13 | 22:24 | 11.6997 | 75694 | 75619 | 75833
15648 | 2021-11-13 | 22:24 | 11.6997 | 75693 | 75619 | 75829
15649 | 2021-11-13 | 22:24 | 11.6997 | 75692 | 75618 | 75825
15650 | 2021-11-13 | 22:24 | 11.6998 | 75691 | 75617 | 75821
15651 | 2021-11-13 | 22:24 | 11.6998 | 75690 | 75617 | 75817
15652 | 2021-11-13 | 22:24 | 11.6998 | 75690 | 75616 | 75813
15653 | 2021-11-13 | 22:24 | 11.6999 | 75689 | 75615 | 75808
15654 | 2021-11-13 | 22:24 | 11.6999 | 75688 | 75614 | 75804
15655 | 2021-11-13 | 22:24 | 11.6999 | 75687 | 75613 | 75800
15656 | 2021-11-13 | 22:24 | 11.6999 | 75686 | 75612 | 75796
15657 | 2021-11-13 | 22:24 | 11.7 | 75685 | 75611 | 75792
15658 | 2021-11-13 | 22:24 | 11.7 | 75685 | 75610 | 75788
15659 | 2021-11-13 | 22:24 | 11.7 | 75684 | 75610 | 75784
15660 | 2021-11-13 | 22:24 | 11.7001 | 75683 | 75609 | 75780
15661 | 2021-11-13 | 22:24 | 11.7001 | 75682 | 75608 | 75776
15662 | 2021-11-13 | 22:24 | 11.7001 | 75681 | 75607 | 75772
15663 | 2021-11-13 | 22:24 | 11.7001 | 75681 | 75606 | 75767
15664 | 2021-11-13 | 22:24 | 11.7002 | 75680 | 75605 | 75763
15665 | 2021-11-13 | 22:24 | 11.7002 | 75679 | 75604 | 75759
15666 | 2021-11-13 | 22:24 | 11.7002 | 75678 | 75602 | 75755
15667 | 2021-11-13 | 22:24 | 11.7003 | 75677 | 75601 | 75751
15668 | 2021-11-13 | 22:24 | 11.7003 | 75677 | 75600 | 75747
15669 | 2021-11-13 | 22:24 | 11.7003 | 75676 | 75599 | 75743
15670 | 2021-11-13 | 22:24 | 11.7003 | 75675 | 75598 | 75739
15671 | 2021-11-13 | 22:24 | 11.7004 | 75675 | 75596 | 75735
15672 | 2021-11-13 | 22:24 | 11.7004 | 75674 | 75595 | 75731
15673 | 2021-11-13 | 22:24 | 11.7004 | 75673 | 75594 | 75727
15674 | 2021-11-13 | 22:24 | 11.7005 | 75673 | 75592 | 75724
15675 | 2021-11-13 | 22:24 | 11.7005 | 75672 | 75591 | 75720
15676 | 2021-11-13 | 22:24 | 11.7005 | 75672 | 75590 | 75716
15677 | 2021-11-13 | 22:24 | 11.7005 | 75672 | 75588 | 75712
15678 | 2021-11-13 | 22:24 | 11.7006 | 75671 | 75587 | 75709
15679 | 2021-11-13 | 22:24 | 11.7006 | 75671 | 75586 | 75705
15680 | 2021-11-13 | 22:24 | 11.7006 | 75670 | 75585 | 75702
15681 | 2021-11-13 | 22:24 | 11.7007 | 75670 | 75584 | 75698
15682 | 2021-11-13 | 22:24 | 11.7007 | 75670 | 75583 | 75695
15683 | 2021-11-13 | 22:24 | 11.7007 | 75670 | 75582 | 75692
15684 | 2021-11-13 | 22:24 | 11.7007 | 75669 | 75581 | 75688
15685 | 2021-11-13 | 22:24 | 11.7008 | 75669 | 75580 | 75685
15686 | 2021-11-13 | 22:24 | 11.7008 | 75669 | 75579 | 75682
15687 | 2021-11-13 | 22:24 | 11.7008 | 75669 | 75578 | 75679
15688 | 2021-11-13 | 22:24 | 11.7009 | 75669 | 75576 | 75677
15689 | 2021-11-13 | 22:24 | 11.7009 | 75669 | 75575 | 75674
15690 | 2021-11-13 | 22:24 | 11.7009 | 75669 | 75574 | 75671
15691 | 2021-11-13 | 22:24 | 11.7009 | 75669 | 75573 | 75668
15692 | 2021-11-13 | 22:24 | 11.701 | 75669 | 75572 | 75666
15693 | 2021-11-13 | 22:24 | 11.701 | 75668 | 75571 | 75663
15694 | 2021-11-13 | 22:24 | 11.701 | 75668 | 75570 | 75661
15695 | 2021-11-13 | 22:24 | 11.7011 | 75668 | 75569 | 75658
15696 | 2021-11-13 | 22:24 | 11.7011 | 75668 | 75568 | 75656
15697 | 2021-11-13 | 22:24 | 11.7011 | 75668 | 75566 | 75654
15698 | 2021-11-13 | 22:24 | 11.7011 | 75668 | 75565 | 75652
15699 | 2021-11-13 | 22:24 | 11.7012 | 75669 | 75564 | 75649
15700 | 2021-11-13 | 22:24 | 11.7012 | 75669 | 75563 | 75647
15701 | 2021-11-13 | 22:24 | 11.7012 | 75669 | 75562 | 75645
15702 | 2021-11-13 | 22:24 | 11.7013 | 75669 | 75560 | 75644
15703 | 2021-11-13 | 22:24 | 11.7013 | 75669 | 75559 | 75642
15704 | 2021-11-13 | 22:24 | 11.7013 | 75669 | 75557 | 75640
15705 | 2021-11-13 | 22:24 | 11.7013 | 75669 | 75556 | 75639
15706 | 2021-11-13 | 22:24 | 11.7014 | 75669 | 75554 | 75637
15707 | 2021-11-13 | 22:24 | 11.7014 | 75669 | 75552 | 75636
15708 | 2021-11-13 | 22:24 | 11.7014 | 75668 | 75550 | 75634
15709 | 2021-11-13 | 22:24 | 11.7015 | 75668 | 75549 | 75633
15710 | 2021-11-13 | 22:24 | 11.7015 | 75668 | 75547 | 75632
15711 | 2021-11-13 | 22:24 | 11.7015 | 75668 | 75545 | 75630
15712 | 2021-11-13 | 22:24 | 11.7015 | 75668 | 75543 | 75629
15713 | 2021-11-13 | 22:24 | 11.7016 | 75668 | 75541 | 75628
15714 | 2021-11-13 | 22:24 | 11.7016 | 75668 | 75539 | 75626
15715 | 2021-11-13 | 22:24 | 11.7016 | 75668 | 75537 | 75625
15716 | 2021-11-13 | 22:24 | 11.7017 | 75667 | 75535 | 75625
15717 | 2021-11-13 | 22:24 | 11.7017 | 75667 | 75533 | 75624
15718 | 2021-11-13 | 22:24 | 11.7017 | 75667 | 75531 | 75623
15719 | 2021-11-13 | 22:24 | 11.7018 | 75666 | 75529 | 75622
15720 | 2021-11-13 | 22:24 | 11.7018 | 75666 | 75527 | 75621
15721 | 2021-11-13 | 22:24 | 11.7018 | 75665 | 75525 | 75620
15722 | 2021-11-13 | 22:24 | 11.7018 | 75665 | 75523 | 75620
15723 | 2021-11-13 | 22:24 | 11.7019 | 75664 | 75521 | 75619
15724 | 2021-11-13 | 22:24 | 11.7019 | 75664 | 75518 | 75618
15725 | 2021-11-13 | 22:24 | 11.7019 | 75663 | 75516 | 75618
15726 | 2021-11-13 | 22:24 | 11.702 | 75663 | 75514 | 75617
15727 | 2021-11-13 | 22:24 | 11.702 | 75662 | 75512 | 75617
15728 | 2021-11-13 | 22:24 | 11.702 | 75662 | 75510 | 75616
15729 | 2021-11-13 | 22:24 | 11.702 | 75661 | 75507 | 75616
15730 | 2021-11-13 | 22:24 | 11.7021 | 75660 | 75505 | 75615
15731 | 2021-11-13 | 22:24 | 11.7021 | 75660 | 75503 | 75615
15732 | 2021-11-13 | 22:24 | 11.7021 | 75659 | 75501 | 75614
15733 | 2021-11-13 | 22:24 | 11.7022 | 75659 | 75499 | 75614
15734 | 2021-11-13 | 22:24 | 11.7022 | 75658 | 75496 | 75613
15735 | 2021-11-13 | 22:24 | 11.7022 | 75657 | 75494 | 75612
15736 | 2021-11-13 | 22:24 | 11.7022 | 75656 | 75492 | 75612
15737 | 2021-11-13 | 22:24 | 11.7023 | 75656 | 75489 | 75611
15738 | 2021-11-13 | 22:24 | 11.7023 | 75655 | 75487 | 75611
15739 | 2021-11-13 | 22:24 | 11.7023 | 75654 | 75485 | 75611
15740 | 2021-11-13 | 22:24 | 11.7024 | 75654 | 75482 | 75610
15741 | 2021-11-13 | 22:24 | 11.7024 | 75653 | 75480 | 75610
15742 | 2021-11-13 | 22:24 | 11.7024 | 75653 | 75478 | 75609
15743 | 2021-11-13 | 22:24 | 11.7024 | 75652 | 75476 | 75608
15744 | 2021-11-13 | 22:24 | 11.7025 | 75652 | 75474 | 75608
15745 | 2021-11-13 | 22:24 | 11.7025 | 75651 | 75472 | 75608
15746 | 2021-11-13 | 22:24 | 11.7025 | 75650 | 75471 | 75607
15747 | 2021-11-13 | 22:24 | 11.7026 | 75650 | 75469 | 75607
15748 | 2021-11-13 | 22:24 | 11.7026 | 75649 | 75467 | 75606
15749 | 2021-11-13 | 22:24 | 11.7026 | 75649 | 75466 | 75606
15750 | 2021-11-13 | 22:24 | 11.7026 | 75648 | 75464 | 75605
15751 | 2021-11-13 | 22:24 | 11.7027 | 75648 | 75463 | 75605
15752 | 2021-11-13 | 22:24 | 11.7027 | 75648 | 75462 | 75605
15753 | 2021-11-13 | 22:24 | 11.7027 | 75647 | 75461 | 75604
15754 | 2021-11-13 | 22:24 | 11.7028 | 75647 | 75460 | 75604
15755 | 2021-11-13 | 22:24 | 11.7028 | 75647 | 75459 | 75604
15756 | 2021-11-13 | 22:24 | 11.7028 | 75646 | 75458 | 75603
15757 | 2021-11-13 | 22:24 | 11.7028 | 75646 | 75458 | 75603
15758 | 2021-11-13 | 22:24 | 11.7029 | 75646 | 75457 | 75603
15759 | 2021-11-13 | 22:24 | 11.7029 | 75646 | 75456 | 75603
15760 | 2021-11-13 | 22:24 | 11.7029 | 75645 | 75456 | 75602
15761 | 2021-11-13 | 22:24 | 11.703 | 75645 | 75456 | 75602
15762 | 2021-11-13 | 22:24 | 11.703 | 75645 | 75455 | 75602
15763 | 2021-11-13 | 22:24 | 11.703 | 75645 | 75455 | 75602
15764 | 2021-11-13 | 22:24 | 11.703 | 75645 | 75455 | 75601
15765 | 2021-11-13 | 22:24 | 11.7031 | 75645 | 75455 | 75601
15766 | 2021-11-13 | 22:24 | 11.7031 | 75645 | 75455 | 75601
15767 | 2021-11-13 | 22:24 | 11.7031 | 75645 | 75455 | 75601
15768 | 2021-11-13 | 22:24 | 11.7032 | 75645 | 75455 | 75601
15769 | 2021-11-13 | 22:24 | 11.7032 | 75645 | 75455 | 75600
15770 | 2021-11-13 | 22:24 | 11.7032 | 75645 | 75454 | 75600
15771 | 2021-11-13 | 22:24 | 11.7032 | 75646 | 75454 | 75600
15772 | 2021-11-13 | 22:24 | 11.7033 | 75646 | 75454 | 75600
15773 | 2021-11-13 | 22:24 | 11.7033 | 75646 | 75454 | 75600
15774 | 2021-11-13 | 22:24 | 11.7033 | 75646 | 75454 | 75600
15775 | 2021-11-13 | 22:24 | 11.7034 | 75646 | 75454 | 75600
15776 | 2021-11-13 | 22:24 | 11.7034 | 75647 | 75453 | 75600
15777 | 2021-11-13 | 22:24 | 11.7034 | 75647 | 75453 | 75600
15778 | 2021-11-13 | 22:24 | 11.7034 | 75647 | 75453 | 75600
15779 | 2021-11-13 | 22:24 | 11.7035 | 75647 | 75453 | 75600
15780 | 2021-11-13 | 22:24 | 11.7035 | 75647 | 75453 | 75600
15781 | 2021-11-13 | 22:24 | 11.7035 | 75646 | 75453 | 75600
15782 | 2021-11-13 | 22:24 | 11.7036 | 75646 | 75453 | 75600
15783 | 2021-11-13 | 22:24 | 11.7036 | 75646 | 75453 | 75600
15784 | 2021-11-13 | 22:24 | 11.7036 | 75646 | 75453 | 75600
15785 | 2021-11-13 | 22:24 | 11.7036 | 75646 | 75453 | 75600
15786 | 2021-11-13 | 22:24 | 11.7037 | 75646 | 75453 | 75600
15787 | 2021-11-13 | 22:24 | 11.7037 | 75646 | 75453 | 75600
15788 | 2021-11-13 | 22:24 | 11.7037 | 75646 | 75454 | 75600
15789 | 2021-11-13 | 22:24 | 11.7038 | 75645 | 75454 | 75600
15790 | 2021-11-13 | 22:24 | 11.7038 | 75644 | 75454 | 75600
15791 | 2021-11-13 | 22:24 | 11.7038 | 75644 | 75454 | 75600
15792 | 2021-11-13 | 22:24 | 11.7038 | 75643 | 75454 | 75599
15793 | 2021-11-13 | 22:24 | 11.7039 | 75642 | 75455 | 75599
15794 | 2021-11-13 | 22:24 | 11.7039 | 75641 | 75455 | 75599
15795 | 2021-11-13 | 22:24 | 11.7039 | 75640 | 75455 | 75599
15796 | 2021-11-13 | 22:24 | 11.704 | 75639 | 75455 | 75599
15797 | 2021-11-13 | 22:24 | 11.704 | 75638 | 75455 | 75599
15798 | 2021-11-13 | 22:24 | 11.704 | 75637 | 75456 | 75598
15799 | 2021-11-13 | 22:24 | 11.704 | 75635 | 75456 | 75598
15800 | 2021-11-13 | 22:24 | 11.7041 | 75634 | 75456 | 75598
15801 | 2021-11-13 | 22:24 | 11.7041 | 75632 | 75456 | 75597
15802 | 2021-11-13 | 22:24 | 11.7041 | 75630 | 75457 | 75597
15803 | 2021-11-13 | 22:24 | 11.7042 | 75628 | 75457 | 75597
15804 | 2021-11-13 | 22:24 | 11.7042 | 75626 | 75457 | 75596
15805 | 2021-11-13 | 22:24 | 11.7042 | 75624 | 75457 | 75596
15806 | 2021-11-13 | 22:24 | 11.7042 | 75623 | 75457 | 75595
15807 | 2021-11-13 | 22:24 | 11.7043 | 75620 | 75457 | 75595
15808 | 2021-11-13 | 22:24 | 11.7043 | 75618 | 75457 | 75594
15809 | 2021-11-13 | 22:24 | 11.7043 | 75616 | 75457 | 75594
15810 | 2021-11-13 | 22:24 | 11.7044 | 75613 | 75456 | 75593
15811 | 2021-11-13 | 22:24 | 11.7044 | 75611 | 75456 | 75592
15812 | 2021-11-13 | 22:24 | 11.7044 | 75608 | 75456 | 75591
15813 | 2021-11-13 | 22:24 | 11.7045 | 75605 | 75456 | 75590
15814 | 2021-11-13 | 22:24 | 11.7045 | 75602 | 75456 | 75590
15815 | 2021-11-13 | 22:24 | 11.7045 | 75600 | 75455 | 75589
15816 | 2021-11-13 | 22:24 | 11.7045 | 75597 | 75455 | 75588
15817 | 2021-11-13 | 22:24 | 11.7046 | 75594 | 75455 | 75587
15818 | 2021-11-13 | 22:24 | 11.7046 | 75591 | 75455 | 75587
15819 | 2021-11-13 | 22:24 | 11.7046 | 75589 | 75454 | 75586
15820 | 2021-11-13 | 22:24 | 11.7047 | 75585 | 75454 | 75585
15821 | 2021-11-13 | 22:24 | 11.7047 | 75582 | 75454 | 75584
15822 | 2021-11-13 | 22:24 | 11.7047 | 75579 | 75454 | 75583
15823 | 2021-11-13 | 22:24 | 11.7047 | 75576 | 75453 | 75581
15824 | 2021-11-13 | 22:24 | 11.7048 | 75573 | 75453 | 75580
15825 | 2021-11-13 | 22:24 | 11.7048 | 75569 | 75453 | 75579
15826 | 2021-11-13 | 22:24 | 11.7048 | 75566 | 75453 | 75578
15827 | 2021-11-13 | 22:24 | 11.7049 | 75564 | 75452 | 75577
15828 | 2021-11-13 | 22:24 | 11.7049 | 75561 | 75452 | 75576
15829 | 2021-11-13 | 22:24 | 11.7049 | 75558 | 75452 | 75575
15830 | 2021-11-13 | 22:24 | 11.7049 | 75555 | 75452 | 75573
15831 | 2021-11-13 | 22:24 | 11.705 | 75552 | 75452 | 75572
15832 | 2021-11-13 | 22:24 | 11.705 | 75548 | 75452 | 75571
15833 | 2021-11-13 | 22:24 | 11.705 | 75545 | 75452 | 75569
15834 | 2021-11-13 | 22:24 | 11.7051 | 75542 | 75452 | 75567
15835 | 2021-11-13 | 22:24 | 11.7051 | 75539 | 75452 | 75566
15836 | 2021-11-13 | 22:24 | 11.7051 | 75537 | 75452 | 75565
15837 | 2021-11-13 | 22:24 | 11.7051 | 75534 | 75452 | 75563
15838 | 2021-11-13 | 22:24 | 11.7052 | 75531 | 75452 | 75562
15839 | 2021-11-13 | 22:24 | 11.7052 | 75529 | 75452 | 75560
15840 | 2021-11-13 | 22:24 | 11.7052 | 75526 | 75452 | 75559
15841 | 2021-11-13 | 22:24 | 11.7053 | 75524 | 75452 | 75557
15842 | 2021-11-13 | 22:24 | 11.7053 | 75521 | 75452 | 75556
15843 | 2021-11-13 | 22:24 | 11.7053 | 75519 | 75452 | 75554
15844 | 2021-11-13 | 22:24 | 11.7053 | 75516 | 75452 | 75552
15845 | 2021-11-13 | 22:24 | 11.7054 | 75514 | 75452 | 75551
15846 | 2021-11-13 | 22:24 | 11.7054 | 75512 | 75452 | 75549
15847 | 2021-11-13 | 22:24 | 11.7054 | 75510 | 75452 | 75548
15848 | 2021-11-13 | 22:24 | 11.7055 | 75508 | 75452 | 75547
15849 | 2021-11-13 | 22:24 | 11.7055 | 75506 | 75452 | 75545
15850 | 2021-11-13 | 22:24 | 11.7055 | 75505 | 75452 | 75544
15851 | 2021-11-13 | 22:24 | 11.7055 | 75503 | 75452 | 75543
15852 | 2021-11-13 | 22:24 | 11.7056 | 75501 | 75452 | 75541
15853 | 2021-11-13 | 22:24 | 11.7056 | 75499 | 75452 | 75540
15854 | 2021-11-13 | 22:24 | 11.7056 | 75497 | 75452 | 75538
15855 | 2021-11-13 | 22:24 | 11.7057 | 75496 | 75452 | 75537
15856 | 2021-11-13 | 22:24 | 11.7057 | 75494 | 75453 | 75536
15857 | 2021-11-13 | 22:24 | 11.7057 | 75493 | 75453 | 75535
15858 | 2021-11-13 | 22:24 | 11.7057 | 75492 | 75453 | 75533
15859 | 2021-11-13 | 22:24 | 11.7058 | 75491 | 75453 | 75532
15860 | 2021-11-13 | 22:24 | 11.7058 | 75489 | 75453 | 75531
15861 | 2021-11-13 | 22:24 | 11.7058 | 75488 | 75453 | 75530
15862 | 2021-11-13 | 22:24 | 11.7059 | 75487 | 75453 | 75529
15863 | 2021-11-13 | 22:24 | 11.7059 | 75486 | 75453 | 75527
15864 | 2021-11-13 | 22:24 | 11.7059 | 75485 | 75453 | 75526
15865 | 2021-11-13 | 22:24 | 11.7059 | 75485 | 75453 | 75525
15866 | 2021-11-13 | 22:24 | 11.706 | 75484 | 75453 | 75523
15867 | 2021-11-13 | 22:24 | 11.706 | 75483 | 75453 | 75522
15868 | 2021-11-13 | 22:24 | 11.706 | 75483 | 75453 | 75521
15869 | 2021-11-13 | 22:24 | 11.7061 | 75482 | 75453 | 75520
15870 | 2021-11-13 | 22:24 | 11.7061 | 75482 | 75453 | 75519
15871 | 2021-11-13 | 22:24 | 11.7061 | 75481 | 75453 | 75518
15872 | 2021-11-13 | 22:24 | 11.7061 | 75481 | 75453 | 75517
15873 | 2021-11-13 | 22:24 | 11.7062 | 75481 | 75452 | 75515
15874 | 2021-11-13 | 22:24 | 11.7062 | 75480 | 75452 | 75514
15875 | 2021-11-13 | 22:24 | 11.7062 | 75480 | 75452 | 75512
15876 | 2021-11-13 | 22:24 | 11.7063 | 75480 | 75452 | 75511
15877 | 2021-11-13 | 22:24 | 11.7063 | 75480 | 75452 | 75510
15878 | 2021-11-13 | 22:24 | 11.7063 | 75480 | 75452 | 75509
15879 | 2021-11-13 | 22:24 | 11.7063 | 75480 | 75451 | 75508
15880 | 2021-11-13 | 22:24 | 11.7064 | 75480 | 75451 | 75507
15881 | 2021-11-13 | 22:24 | 11.7064 | 75480 | 75451 | 75506
15882 | 2021-11-13 | 22:24 | 11.7064 | 75481 | 75450 | 75504
15883 | 2021-11-13 | 22:24 | 11.7065 | 75481 | 75450 | 75503
15884 | 2021-11-13 | 22:24 | 11.7065 | 75481 | 75450 | 75502
15885 | 2021-11-13 | 22:24 | 11.7065 | 75481 | 75449 | 75501
15886 | 2021-11-13 | 22:24 | 11.7065 | 75481 | 75449 | 75500
15887 | 2021-11-13 | 22:24 | 11.7066 | 75481 | 75448 | 75499
15888 | 2021-11-13 | 22:24 | 11.7066 | 75481 | 75448 | 75497
15889 | 2021-11-13 | 22:24 | 11.7066 | 75481 | 75447 | 75496
15890 | 2021-11-13 | 22:24 | 11.7067 | 75481 | 75447 | 75495
15891 | 2021-11-13 | 22:24 | 11.7067 | 75481 | 75447 | 75494
15892 | 2021-11-13 | 22:24 | 11.7067 | 75481 | 75446 | 75493
15893 | 2021-11-13 | 22:24 | 11.7067 | 75481 | 75446 | 75492
15894 | 2021-11-13 | 22:24 | 11.7068 | 75481 | 75445 | 75490
15895 | 2021-11-13 | 22:24 | 11.7068 | 75481 | 75445 | 75489
15896 | 2021-11-13 | 22:24 | 11.7068 | 75481 | 75444 | 75487
15897 | 2021-11-13 | 22:24 | 11.7069 | 75481 | 75443 | 75485
15898 | 2021-11-13 | 22:24 | 11.7069 | 75481 | 75443 | 75484
15899 | 2021-11-13 | 22:24 | 11.7069 | 75480 | 75442 | 75483
15900 | 2021-11-13 | 22:24 | 11.7069 | 75480 | 75442 | 75481
15901 | 2021-11-13 | 22:24 | 11.707 | 75480 | 75442 | 75480
15902 | 2021-11-13 | 22:24 | 11.707 | 75479 | 75441 | 75478
15903 | 2021-11-13 | 22:24 | 11.707 | 75479 | 75441 | 75477
15904 | 2021-11-13 | 22:24 | 11.7071 | 75479 | 75440 | 75475
15905 | 2021-11-13 | 22:24 | 11.7071 | 75478 | 75440 | 75474
15906 | 2021-11-13 | 22:24 | 11.7071 | 75478 | 75439 | 75472
15907 | 2021-11-13 | 22:24 | 11.7071 | 75477 | 75439 | 75470
15908 | 2021-11-13 | 22:24 | 11.7072 | 75477 | 75438 | 75468
15909 | 2021-11-13 | 22:24 | 11.7072 | 75477 | 75438 | 75467
15910 | 2021-11-13 | 22:24 | 11.7072 | 75476 | 75437 | 75465
15911 | 2021-11-13 | 22:24 | 11.7073 | 75476 | 75437 | 75463
15912 | 2021-11-13 | 22:24 | 11.7073 | 75476 | 75436 | 75462
15913 | 2021-11-13 | 22:24 | 11.7073 | 75475 | 75436 | 75460
15914 | 2021-11-13 | 22:24 | 11.7074 | 75475 | 75435 | 75459
15915 | 2021-11-13 | 22:24 | 11.7074 | 75475 | 75434 | 75457
15916 | 2021-11-13 | 22:24 | 11.7074 | 75474 | 75434 | 75456
15917 | 2021-11-13 | 22:24 | 11.7074 | 75474 | 75433 | 75454
15918 | 2021-11-13 | 22:24 | 11.7075 | 75474 | 75432 | 75452
15919 | 2021-11-13 | 22:24 | 11.7075 | 75474 | 75432 | 75451
15920 | 2021-11-13 | 22:24 | 11.7075 | 75473 | 75431 | 75450
15921 | 2021-11-13 | 22:24 | 11.7076 | 75473 | 75430 | 75448
15922 | 2021-11-13 | 22:24 | 11.7076 | 75473 | 75430 | 75447
15923 | 2021-11-13 | 22:24 | 11.7076 | 75472 | 75429 | 75446
15924 | 2021-11-13 | 22:24 | 11.7076 | 75472 | 75428 | 75444
15925 | 2021-11-13 | 22:24 | 11.7077 | 75472 | 75427 | 75443
15926 | 2021-11-13 | 22:24 | 11.7077 | 75472 | 75427 | 75442
15927 | 2021-11-13 | 22:24 | 11.7077 | 75471 | 75426 | 75440
15928 | 2021-11-13 | 22:24 | 11.7078 | 75471 | 75425 | 75439
15929 | 2021-11-13 | 22:24 | 11.7078 | 75471 | 75424 | 75437
15930 | 2021-11-13 | 22:24 | 11.7078 | 75471 | 75423 | 75436
15931 | 2021-11-13 | 22:24 | 11.7078 | 75471 | 75423 | 75434
15932 | 2021-11-13 | 22:24 | 11.7079 | 75470 | 75422 | 75433
15933 | 2021-11-13 | 22:24 | 11.7079 | 75470 | 75421 | 75432
15934 | 2021-11-13 | 22:24 | 11.7079 | 75470 | 75421 | 75431
15935 | 2021-11-13 | 22:24 | 11.708 | 75470 | 75420 | 75429
15936 | 2021-11-13 | 22:24 | 11.708 | 75470 | 75419 | 75428
15937 | 2021-11-13 | 22:24 | 11.708 | 75470 | 75419 | 75427
15938 | 2021-11-13 | 22:24 | 11.708 | 75469 | 75418 | 75426
15939 | 2021-11-13 | 22:24 | 11.7081 | 75469 | 75418 | 75425
15940 | 2021-11-13 | 22:24 | 11.7081 | 75469 | 75417 | 75424
15941 | 2021-11-13 | 22:24 | 11.7081 | 75469 | 75417 | 75423
15942 | 2021-11-13 | 22:24 | 11.7082 | 75469 | 75416 | 75422
15943 | 2021-11-13 | 22:24 | 11.7082 | 75469 | 75416 | 75422
15944 | 2021-11-13 | 22:24 | 11.7082 | 75469 | 75416 | 75421
15945 | 2021-11-13 | 22:24 | 11.7082 | 75469 | 75415 | 75421
15946 | 2021-11-13 | 22:24 | 11.7083 | 75469 | 75415 | 75420
15947 | 2021-11-13 | 22:24 | 11.7083 | 75469 | 75415 | 75420
15948 | 2021-11-13 | 22:24 | 11.7083 | 75469 | 75414 | 75420
15949 | 2021-11-13 | 22:24 | 11.7084 | 75469 | 75414 | 75420
15950 | 2021-11-13 | 22:24 | 11.7084 | 75469 | 75414 | 75419
15951 | 2021-11-13 | 22:24 | 11.7084 | 75469 | 75414 | 75420
15952 | 2021-11-13 | 22:24 | 11.7084 | 75469 | 75414 | 75420
15953 | 2021-11-13 | 22:24 | 11.7085 | 75469 | 75414 | 75420
15954 | 2021-11-13 | 22:24 | 11.7085 | 75469 | 75413 | 75420
15955 | 2021-11-13 | 22:24 | 11.7085 | 75469 | 75413 | 75420
15956 | 2021-11-13 | 22:24 | 11.7086 | 75469 | 75413 | 75421
15957 | 2021-11-13 | 22:24 | 11.7086 | 75469 | 75413 | 75421
15958 | 2021-11-13 | 22:24 | 11.7086 | 75469 | 75413 | 75421
15959 | 2021-11-13 | 22:24 | 11.7086 | 75469 | 75413 | 75421
15960 | 2021-11-13 | 22:24 | 11.7087 | 75469 | 75412 | 75422
15961 | 2021-11-13 | 22:24 | 11.7087 | 75469 | 75412 | 75422
15962 | 2021-11-13 | 22:24 | 11.7087 | 75469 | 75412 | 75423
15963 | 2021-11-13 | 22:24 | 11.7088 | 75468 | 75412 | 75423
15964 | 2021-11-13 | 22:24 | 11.7088 | 75468 | 75411 | 75424
15965 | 2021-11-13 | 22:24 | 11.7088 | 75468 | 75411 | 75424
15966 | 2021-11-13 | 22:24 | 11.7088 | 75468 | 75411 | 75425
15967 | 2021-11-13 | 22:24 | 11.7089 | 75468 | 75411 | 75425
15968 | 2021-11-13 | 22:24 | 11.7089 | 75468 | 75410 | 75426
15969 | 2021-11-13 | 22:24 | 11.7089 | 75468 | 75410 | 75426
15970 | 2021-11-13 | 22:24 | 11.709 | 75468 | 75409 | 75427
15971 | 2021-11-13 | 22:24 | 11.709 | 75467 | 75409 | 75428
15972 | 2021-11-13 | 22:24 | 11.709 | 75467 | 75409 | 75428
15973 | 2021-11-13 | 22:24 | 11.709 | 75467 | 75408 | 75429
15974 | 2021-11-13 | 22:24 | 11.7091 | 75467 | 75408 | 75429
15975 | 2021-11-13 | 22:24 | 11.7091 | 75466 | 75407 | 75430
15976 | 2021-11-13 | 22:24 | 11.7091 | 75466 | 75407 | 75431
15977 | 2021-11-13 | 22:24 | 11.7092 | 75466 | 75407 | 75431
15978 | 2021-11-13 | 22:24 | 11.7092 | 75466 | 75406 | 75432
15979 | 2021-11-13 | 22:24 | 11.7092 | 75465 | 75406 | 75433
15980 | 2021-11-13 | 22:24 | 11.7092 | 75465 | 75405 | 75434
15981 | 2021-11-13 | 22:24 | 11.7093 | 75464 | 75405 | 75435
15982 | 2021-11-13 | 22:24 | 11.7093 | 75464 | 75404 | 75436
15983 | 2021-11-13 | 22:24 | 11.7093 | 75463 | 75404 | 75436
15984 | 2021-11-13 | 22:24 | 11.7094 | 75463 | 75403 | 75437
15985 | 2021-11-13 | 22:24 | 11.7094 | 75463 | 75403 | 75438
15986 | 2021-11-13 | 22:24 | 11.7094 | 75462 | 75402 | 75439
15987 | 2021-11-13 | 22:24 | 11.7094 | 75462 | 75402 | 75440
15988 | 2021-11-13 | 22:24 | 11.7095 | 75461 | 75401 | 75441
15989 | 2021-11-13 | 22:24 | 11.7095 | 75460 | 75400 | 75442
15990 | 2021-11-13 | 22:24 | 11.7095 | 75460 | 75400 | 75442
15991 | 2021-11-13 | 22:24 | 11.7096 | 75459 | 75399 | 75443
15992 | 2021-11-13 | 22:24 | 11.7096 | 75459 | 75398 | 75444
15993 | 2021-11-13 | 22:24 | 11.7096 | 75458 | 75397 | 75445
15994 | 2021-11-13 | 22:24 | 11.7096 | 75457 | 75397 | 75446
15995 | 2021-11-13 | 22:24 | 11.7097 | 75457 | 75396 | 75447
15996 | 2021-11-13 | 22:24 | 11.7097 | 75457 | 75396 | 75447
15997 | 2021-11-13 | 22:24 | 11.7097 | 75456 | 75395 | 75448
15998 | 2021-11-13 | 22:24 | 11.7098 | 75456 | 75395 | 75449
15999 | 2021-11-13 | 22:24 | 11.7098 | 75455 | 75394 | 75449
16000 | 2021-11-13 | 22:24 | 11.7098 | 75455 | 75394 | 75450
16001 | 2021-11-13 | 22:24 | 11.7098 | 75454 | 75394 | 75451
16002 | 2021-11-13 | 22:24 | 11.7099 | 75454 | 75393 | 75451
16003 | 2021-11-13 | 22:24 | 11.7099 | 75453 | 75393 | 75452
16004 | 2021-11-13 | 22:24 | 11.7099 | 75452 | 75393 | 75452
16005 | 2021-11-13 | 22:24 | 11.71 | 75452 | 75393 | 75453
16006 | 2021-11-13 | 22:24 | 11.71 | 75452 | 75393 | 75453
16007 | 2021-11-13 | 22:24 | 11.71 | 75451 | 75393 | 75454
16008 | 2021-11-13 | 22:24 | 11.7101 | 75451 | 75394 | 75454
16009 | 2021-11-13 | 22:24 | 11.7101 | 75450 | 75394 | 75454
16010 | 2021-11-13 | 22:24 | 11.7101 | 75450 | 75394 | 75455
16011 | 2021-11-13 | 22:24 | 11.7101 | 75449 | 75394 | 75455
16012 | 2021-11-13 | 22:24 | 11.7102 | 75449 | 75395 | 75455
16013 | 2021-11-13 | 22:24 | 11.7102 | 75448 | 75395 | 75456
16014 | 2021-11-13 | 22:24 | 11.7102 | 75448 | 75396 | 75456
16015 | 2021-11-13 | 22:24 | 11.7103 | 75447 | 75397 | 75456
16016 | 2021-11-13 | 22:24 | 11.7103 | 75447 | 75398 | 75456
16017 | 2021-11-13 | 22:24 | 11.7103 | 75446 | 75399 | 75456
16018 | 2021-11-13 | 22:24 | 11.7103 | 75446 | 75400 | 75457
16019 | 2021-11-13 | 22:24 | 11.7104 | 75445 | 75401 | 75457
16020 | 2021-11-13 | 22:24 | 11.7104 | 75445 | 75401 | 75457
16021 | 2021-11-13 | 22:24 | 11.7104 | 75444 | 75402 | 75457
16022 | 2021-11-13 | 22:24 | 11.7105 | 75444 | 75403 | 75457
16023 | 2021-11-13 | 22:24 | 11.7105 | 75444 | 75404 | 75457
16024 | 2021-11-13 | 22:24 | 11.7105 | 75443 | 75405 | 75457
16025 | 2021-11-13 | 22:24 | 11.7105 | 75443 | 75406 | 75458
16026 | 2021-11-13 | 22:24 | 11.7106 | 75442 | 75406 | 75458
16027 | 2021-11-13 | 22:24 | 11.7106 | 75442 | 75407 | 75458
16028 | 2021-11-13 | 22:24 | 11.7106 | 75442 | 75407 | 75458
16029 | 2021-11-13 | 22:24 | 11.7107 | 75442 | 75408 | 75458
16030 | 2021-11-13 | 22:24 | 11.7107 | 75442 | 75408 | 75458
16031 | 2021-11-13 | 22:24 | 11.7107 | 75441 | 75409 | 75458
16032 | 2021-11-13 | 22:24 | 11.7107 | 75441 | 75409 | 75458
16033 | 2021-11-13 | 22:24 | 11.7108 | 75441 | 75409 | 75458
16034 | 2021-11-13 | 22:24 | 11.7108 | 75441 | 75409 | 75458
16035 | 2021-11-13 | 22:24 | 11.7108 | 75441 | 75409 | 75458
16036 | 2021-11-13 | 22:24 | 11.7109 | 75441 | 75409 | 75458
16037 | 2021-11-13 | 22:24 | 11.7109 | 75441 | 75409 | 75458
16038 | 2021-11-13 | 22:24 | 11.7109 | 75441 | 75409 | 75458
16039 | 2021-11-13 | 22:24 | 11.7109 | 75441 | 75409 | 75458
16040 | 2021-11-13 | 22:24 | 11.711 | 75441 | 75409 | 75458
16041 | 2021-11-13 | 22:24 | 11.711 | 75441 | 75409 | 75458
16042 | 2021-11-13 | 22:24 | 11.711 | 75441 | 75409 | 75458
16043 | 2021-11-13 | 22:24 | 11.7111 | 75441 | 75410 | 75458
16044 | 2021-11-13 | 22:24 | 11.7111 | 75441 | 75410 | 75458
16045 | 2021-11-13 | 22:24 | 11.7111 | 75440 | 75410 | 75458
16046 | 2021-11-13 | 22:24 | 11.7111 | 75440 | 75411 | 75458
16047 | 2021-11-13 | 22:24 | 11.7112 | 75440 | 75412 | 75457
16048 | 2021-11-13 | 22:24 | 11.7112 | 75440 | 75412 | 75457
16049 | 2021-11-13 | 22:24 | 11.7112 | 75440 | 75413 | 75457
16050 | 2021-11-13 | 22:24 | 11.7113 | 75440 | 75414 | 75457
16051 | 2021-11-13 | 22:24 | 11.7113 | 75440 | 75414 | 75457
16052 | 2021-11-13 | 22:24 | 11.7113 | 75440 | 75415 | 75456
16053 | 2021-11-13 | 22:24 | 11.7113 | 75440 | 75416 | 75456
16054 | 2021-11-13 | 22:24 | 11.7114 | 75440 | 75417 | 75456
16055 | 2021-11-13 | 22:24 | 11.7114 | 75440 | 75419 | 75455
16056 | 2021-11-13 | 22:24 | 11.7114 | 75439 | 75420 | 75455
16057 | 2021-11-13 | 22:24 | 11.7115 | 75439 | 75421 | 75455
16058 | 2021-11-13 | 22:24 | 11.7115 | 75439 | 75422 | 75454
16059 | 2021-11-13 | 22:24 | 11.7115 | 75439 | 75423 | 75454
16060 | 2021-11-13 | 22:24 | 11.7115 | 75439 | 75424 | 75453
16061 | 2021-11-13 | 22:24 | 11.7116 | 75438 | 75425 | 75453
16062 | 2021-11-13 | 22:24 | 11.7116 | 75438 | 75426 | 75452
16063 | 2021-11-13 | 22:24 | 11.7116 | 75437 | 75427 | 75452
16064 | 2021-11-13 | 22:24 | 11.7117 | 75437 | 75428 | 75451
16065 | 2021-11-13 | 22:24 | 11.7117 | 75436 | 75429 | 75451
16066 | 2021-11-13 | 22:24 | 11.7117 | 75436 | 75430 | 75450
16067 | 2021-11-13 | 22:24 | 11.7117 | 75435 | 75431 | 75449
16068 | 2021-11-13 | 22:24 | 11.7118 | 75435 | 75432 | 75449
16069 | 2021-11-13 | 22:24 | 11.7118 | 75434 | 75432 | 75448
16070 | 2021-11-13 | 22:24 | 11.7118 | 75434 | 75433 | 75447
16071 | 2021-11-13 | 22:24 | 11.7119 | 75433 | 75434 | 75446
16072 | 2021-11-13 | 22:24 | 11.7119 | 75432 | 75434 | 75446
16073 | 2021-11-13 | 22:24 | 11.7119 | 75432 | 75435 | 75445
16074 | 2021-11-13 | 22:24 | 11.7119 | 75431 | 75436 | 75444
16075 | 2021-11-13 | 22:24 | 11.712 | 75430 | 75436 | 75443
16076 | 2021-11-13 | 22:24 | 11.712 | 75429 | 75437 | 75442
16077 | 2021-11-13 | 22:24 | 11.712 | 75428 | 75437 | 75441
16078 | 2021-11-13 | 22:24 | 11.7121 | 75428 | 75438 | 75440
16079 | 2021-11-13 | 22:24 | 11.7121 | 75427 | 75438 | 75439
16080 | 2021-11-13 | 22:24 | 11.7121 | 75426 | 75439 | 75438
16081 | 2021-11-13 | 22:24 | 11.7121 | 75426 | 75439 | 75437
16082 | 2021-11-13 | 22:24 | 11.7122 | 75425 | 75440 | 75435
16083 | 2021-11-13 | 22:24 | 11.7122 | 75425 | 75440 | 75434
16084 | 2021-11-13 | 22:24 | 11.7122 | 75424 | 75441 | 75433
16085 | 2021-11-13 | 22:24 | 11.7123 | 75423 | 75441 | 75431
16086 | 2021-11-13 | 22:24 | 11.7123 | 75423 | 75442 | 75430
16087 | 2021-11-13 | 22:24 | 11.7123 | 75422 | 75443 | 75428
16088 | 2021-11-13 | 22:24 | 11.7123 | 75422 | 75443 | 75427
16089 | 2021-11-13 | 22:24 | 11.7124 | 75421 | 75444 | 75426
16090 | 2021-11-13 | 22:24 | 11.7124 | 75421 | 75445 | 75424
16091 | 2021-11-13 | 22:24 | 11.7124 | 75421 | 75445 | 75423
16092 | 2021-11-13 | 22:24 | 11.7125 | 75421 | 75446 | 75422
16093 | 2021-11-13 | 22:24 | 11.7125 | 75421 | 75447 | 75420
16094 | 2021-11-13 | 22:24 | 11.7125 | 75420 | 75447 | 75419
16095 | 2021-11-13 | 22:24 | 11.7125 | 75420 | 75448 | 75417
16096 | 2021-11-13 | 22:24 | 11.7126 | 75420 | 75449 | 75416
16097 | 2021-11-13 | 22:24 | 11.7126 | 75420 | 75449 | 75414
16098 | 2021-11-13 | 22:24 | 11.7126 | 75420 | 75450 | 75413
16099 | 2021-11-13 | 22:24 | 11.7127 | 75420 | 75451 | 75411
16100 | 2021-11-13 | 22:24 | 11.7127 | 75421 | 75451 | 75410
16101 | 2021-11-13 | 22:24 | 11.7127 | 75421 | 75452 | 75409
16102 | 2021-11-13 | 22:24 | 11.7128 | 75421 | 75453 | 75407
16103 | 2021-11-13 | 22:24 | 11.7128 | 75421 | 75453 | 75406
16104 | 2021-11-13 | 22:24 | 11.7128 | 75422 | 75454 | 75404
16105 | 2021-11-13 | 22:24 | 11.7128 | 75422 | 75454 | 75403
16106 | 2021-11-13 | 22:24 | 11.7129 | 75422 | 75455 | 75401
16107 | 2021-11-13 | 22:24 | 11.7129 | 75423 | 75455 | 75400
16108 | 2021-11-13 | 22:24 | 11.7129 | 75423 | 75456 | 75398
16109 | 2021-11-13 | 22:24 | 11.713 | 75424 | 75456 | 75397
16110 | 2021-11-13 | 22:24 | 11.713 | 75424 | 75456 | 75395
16111 | 2021-11-13 | 22:24 | 11.713 | 75425 | 75457 | 75394
16112 | 2021-11-13 | 22:24 | 11.713 | 75426 | 75457 | 75393
16113 | 2021-11-13 | 22:24 | 11.7131 | 75427 | 75457 | 75392
16114 | 2021-11-13 | 22:24 | 11.7131 | 75428 | 75457 | 75390
16115 | 2021-11-13 | 22:24 | 11.7131 | 75429 | 75457 | 75389
16116 | 2021-11-13 | 22:24 | 11.7132 | 75429 | 75458 | 75388
16117 | 2021-11-13 | 22:24 | 11.7132 | 75430 | 75458 | 75387
16118 | 2021-11-13 | 22:24 | 11.7132 | 75431 | 75458 | 75385
16119 | 2021-11-13 | 22:24 | 11.7132 | 75432 | 75458 | 75384
16120 | 2021-11-13 | 22:24 | 11.7133 | 75432 | 75458 | 75382
16121 | 2021-11-13 | 22:24 | 11.7133 | 75433 | 75458 | 75381
16122 | 2021-11-13 | 22:24 | 11.7133 | 75434 | 75458 | 75380
16123 | 2021-11-13 | 22:24 | 11.7134 | 75435 | 75458 | 75379
16124 | 2021-11-13 | 22:24 | 11.7134 | 75436 | 75458 | 75378
16125 | 2021-11-13 | 22:24 | 11.7134 | 75437 | 75458 | 75376
16126 | 2021-11-13 | 22:24 | 11.7134 | 75437 | 75458 | 75375
16127 | 2021-11-13 | 22:24 | 11.7135 | 75438 | 75458 | 75374
16128 | 2021-11-13 | 22:24 | 11.7135 | 75439 | 75458 | 75373
16129 | 2021-11-13 | 22:24 | 11.7135 | 75440 | 75457 | 75371
16130 | 2021-11-13 | 22:24 | 11.7136 | 75440 | 75457 | 75370
16131 | 2021-11-13 | 22:24 | 11.7136 | 75441 | 75457 | 75369
16132 | 2021-11-13 | 22:24 | 11.7136 | 75442 | 75457 | 75368
16133 | 2021-11-13 | 22:24 | 11.7136 | 75443 | 75457 | 75367
16134 | 2021-11-13 | 22:24 | 11.7137 | 75443 | 75456 | 75366
16135 | 2021-11-13 | 22:24 | 11.7137 | 75444 | 75456 | 75365
16136 | 2021-11-13 | 22:24 | 11.7137 | 75444 | 75456 | 75364
16137 | 2021-11-13 | 22:24 | 11.7138 | 75445 | 75456 | 75363
16138 | 2021-11-13 | 22:24 | 11.7138 | 75446 | 75455 | 75362
16139 | 2021-11-13 | 22:24 | 11.7138 | 75446 | 75455 | 75361
16140 | 2021-11-13 | 22:24 | 11.7138 | 75447 | 75455 | 75360
16141 | 2021-11-13 | 22:24 | 11.7139 | 75447 | 75454 | 75360
16142 | 2021-11-13 | 22:24 | 11.7139 | 75448 | 75454 | 75359
16143 | 2021-11-13 | 22:24 | 11.7139 | 75449 | 75454 | 75358
16144 | 2021-11-13 | 22:24 | 11.714 | 75449 | 75454 | 75358
16145 | 2021-11-13 | 22:24 | 11.714 | 75450 | 75453 | 75357
16146 | 2021-11-13 | 22:24 | 11.714 | 75450 | 75453 | 75357
16147 | 2021-11-13 | 22:24 | 11.714 | 75450 | 75453 | 75356
16148 | 2021-11-13 | 22:24 | 11.7141 | 75451 | 75452 | 75355
16149 | 2021-11-13 | 22:24 | 11.7141 | 75451 | 75452 | 75355
16150 | 2021-11-13 | 22:24 | 11.7141 | 75452 | 75452 | 75354
16151 | 2021-11-13 | 22:24 | 11.7142 | 75452 | 75451 | 75353
16152 | 2021-11-13 | 22:24 | 11.7142 | 75453 | 75451 | 75353
16153 | 2021-11-13 | 22:24 | 11.7142 | 75453 | 75451 | 75353
16154 | 2021-11-13 | 22:24 | 11.7142 | 75454 | 75450 | 75352
16155 | 2021-11-13 | 22:24 | 11.7143 | 75454 | 75450 | 75352
16156 | 2021-11-13 | 22:24 | 11.7143 | 75455 | 75450 | 75352
16157 | 2021-11-13 | 22:24 | 11.7143 | 75455 | 75450 | 75352
16158 | 2021-11-13 | 22:24 | 11.7144 | 75456 | 75449 | 75352
16159 | 2021-11-13 | 22:24 | 11.7144 | 75456 | 75449 | 75351
16160 | 2021-11-13 | 22:24 | 11.7144 | 75457 | 75449 | 75351
16161 | 2021-11-13 | 22:24 | 11.7144 | 75457 | 75449 | 75351
16162 | 2021-11-13 | 22:24 | 11.7145 | 75458 | 75448 | 75351
16163 | 2021-11-13 | 22:24 | 11.7145 | 75458 | 75448 | 75351
16164 | 2021-11-13 | 22:24 | 11.7145 | 75459 | 75448 | 75351
16165 | 2021-11-13 | 22:24 | 11.7146 | 75459 | 75447 | 75351
16166 | 2021-11-13 | 22:24 | 11.7146 | 75460 | 75447 | 75351
16167 | 2021-11-13 | 22:24 | 11.7146 | 75461 | 75447 | 75351
16168 | 2021-11-13 | 22:24 | 11.7146 | 75461 | 75446 | 75351
16169 | 2021-11-13 | 22:24 | 11.7147 | 75462 | 75446 | 75351
16170 | 2021-11-13 | 22:24 | 11.7147 | 75463 | 75445 | 75351
16171 | 2021-11-13 | 22:24 | 11.7147 | 75463 | 75445 | 75351
16172 | 2021-11-13 | 22:24 | 11.7148 | 75464 | 75444 | 75351
16173 | 2021-11-13 | 22:24 | 11.7148 | 75465 | 75444 | 75351
16174 | 2021-11-13 | 22:24 | 11.7148 | 75465 | 75443 | 75351
16175 | 2021-11-13 | 22:24 | 11.7148 | 75466 | 75442 | 75351
16176 | 2021-11-13 | 22:24 | 11.7149 | 75467 | 75442 | 75351
16177 | 2021-11-13 | 22:24 | 11.7149 | 75468 | 75441 | 75352
16178 | 2021-11-13 | 22:24 | 11.7149 | 75468 | 75440 | 75352
16179 | 2021-11-13 | 22:24 | 11.715 | 75469 | 75440 | 75352
16180 | 2021-11-13 | 22:24 | 11.715 | 75470 | 75439 | 75352
16181 | 2021-11-13 | 22:24 | 11.715 | 75470 | 75438 | 75352
16182 | 2021-11-13 | 22:24 | 11.715 | 75471 | 75437 | 75353
16183 | 2021-11-13 | 22:24 | 11.7151 | 75472 | 75436 | 75353
16184 | 2021-11-13 | 22:24 | 11.7151 | 75472 | 75435 | 75353
16185 | 2021-11-13 | 22:24 | 11.7151 | 75473 | 75434 | 75354
16186 | 2021-11-13 | 22:24 | 11.7152 | 75473 | 75433 | 75354
16187 | 2021-11-13 | 22:24 | 11.7152 | 75474 | 75432 | 75355
16188 | 2021-11-13 | 22:24 | 11.7152 | 75474 | 75431 | 75356
16189 | 2021-11-13 | 22:24 | 11.7152 | 75475 | 75430 | 75356
16190 | 2021-11-13 | 22:24 | 11.7153 | 75475 | 75429 | 75356
16191 | 2021-11-13 | 22:24 | 11.7153 | 75476 | 75428 | 75357
16192 | 2021-11-13 | 22:24 | 11.7153 | 75476 | 75427 | 75357
16193 | 2021-11-13 | 22:24 | 11.7154 | 75476 | 75426 | 75358
16194 | 2021-11-13 | 22:24 | 11.7154 | 75477 | 75425 | 75358
16195 | 2021-11-13 | 22:24 | 11.7154 | 75477 | 75424 | 75359
16196 | 2021-11-13 | 22:24 | 11.7155 | 75477 | 75424 | 75359
16197 | 2021-11-13 | 22:24 | 11.7155 | 75477 | 75423 | 75360
16198 | 2021-11-13 | 22:24 | 11.7155 | 75478 | 75422 | 75361
16199 | 2021-11-13 | 22:24 | 11.7155 | 75478 | 75422 | 75361
16200 | 2021-11-13 | 22:24 | 11.7156 | 75478 | 75421 | 75362
16201 | 2021-11-13 | 22:24 | 11.7156 | 75478 | 75421 | 75363
16202 | 2021-11-13 | 22:24 | 11.7156 | 75478 | 75420 | 75364
16203 | 2021-11-13 | 22:24 | 11.7157 | 75478 | 75420 | 75364
16204 | 2021-11-13 | 22:24 | 11.7157 | 75478 | 75419 | 75365
16205 | 2021-11-13 | 22:24 | 11.7157 | 75479 | 75419 | 75366
16206 | 2021-11-13 | 22:24 | 11.7157 | 75479 | 75419 | 75367
16207 | 2021-11-13 | 22:24 | 11.7158 | 75479 | 75419 | 75368
16208 | 2021-11-13 | 22:24 | 11.7158 | 75479 | 75419 | 75369
16209 | 2021-11-13 | 22:24 | 11.7158 | 75479 | 75418 | 75370
16210 | 2021-11-13 | 22:24 | 11.7159 | 75479 | 75418 | 75371
16211 | 2021-11-13 | 22:24 | 11.7159 | 75478 | 75418 | 75371
16212 | 2021-11-13 | 22:24 | 11.7159 | 75478 | 75418 | 75373
16213 | 2021-11-13 | 22:24 | 11.7159 | 75478 | 75418 | 75374
16214 | 2021-11-13 | 22:24 | 11.716 | 75478 | 75418 | 75375
16215 | 2021-11-13 | 22:24 | 11.716 | 75478 | 75418 | 75376
16216 | 2021-11-13 | 22:24 | 11.716 | 75478 | 75418 | 75377
16217 | 2021-11-13 | 22:24 | 11.7161 | 75478 | 75418 | 75378
16218 | 2021-11-13 | 22:24 | 11.7161 | 75477 | 75418 | 75379
16219 | 2021-11-13 | 22:24 | 11.7161 | 75477 | 75418 | 75381
16220 | 2021-11-13 | 22:24 | 11.7161 | 75477 | 75419 | 75382
16221 | 2021-11-13 | 22:24 | 11.7162 | 75477 | 75419 | 75383
16222 | 2021-11-13 | 22:24 | 11.7162 | 75476 | 75419 | 75384
16223 | 2021-11-13 | 22:24 | 11.7162 | 75476 | 75419 | 75386
16224 | 2021-11-13 | 22:24 | 11.7163 | 75476 | 75419 | 75387
16225 | 2021-11-13 | 22:24 | 11.7163 | 75475 | 75419 | 75388
16226 | 2021-11-13 | 22:24 | 11.7163 | 75475 | 75419 | 75389
16227 | 2021-11-13 | 22:24 | 11.7163 | 75475 | 75420 | 75391
16228 | 2021-11-13 | 22:24 | 11.7164 | 75474 | 75420 | 75392
16229 | 2021-11-13 | 22:24 | 11.7164 | 75474 | 75421 | 75393
16230 | 2021-11-13 | 22:24 | 11.7164 | 75474 | 75421 | 75394
16231 | 2021-11-13 | 22:24 | 11.7165 | 75473 | 75421 | 75395
16232 | 2021-11-13 | 22:24 | 11.7165 | 75473 | 75421 | 75397
16233 | 2021-11-13 | 22:24 | 11.7165 | 75473 | 75422 | 75398
16234 | 2021-11-13 | 22:24 | 11.7165 | 75472 | 75422 | 75399
16235 | 2021-11-13 | 22:24 | 11.7166 | 75472 | 75422 | 75400
16236 | 2021-11-13 | 22:24 | 11.7166 | 75471 | 75423 | 75401
16237 | 2021-11-13 | 22:24 | 11.7166 | 75471 | 75424 | 75402
16238 | 2021-11-13 | 22:24 | 11.7167 | 75471 | 75424 | 75404
16239 | 2021-11-13 | 22:24 | 11.7167 | 75470 | 75425 | 75405
16240 | 2021-11-13 | 22:24 | 11.7167 | 75470 | 75425 | 75406
16241 | 2021-11-13 | 22:24 | 11.7167 | 75470 | 75426 | 75407
16242 | 2021-11-13 | 22:24 | 11.7168 | 75469 | 75426 | 75408
16243 | 2021-11-13 | 22:24 | 11.7168 | 75469 | 75427 | 75409
16244 | 2021-11-13 | 22:24 | 11.7168 | 75468 | 75427 | 75410
16245 | 2021-11-13 | 22:24 | 11.7169 | 75468 | 75427 | 75411
16246 | 2021-11-13 | 22:24 | 11.7169 | 75467 | 75428 | 75412
16247 | 2021-11-13 | 22:24 | 11.7169 | 75467 | 75429 | 75414
16248 | 2021-11-13 | 22:24 | 11.7169 | 75467 | 75429 | 75415
16249 | 2021-11-13 | 22:24 | 11.717 | 75466 | 75430 | 75416
16250 | 2021-11-13 | 22:24 | 11.717 | 75466 | 75430 | 75417
16251 | 2021-11-13 | 22:24 | 11.717 | 75465 | 75431 | 75418
16252 | 2021-11-13 | 22:24 | 11.7171 | 75465 | 75432 | 75419
16253 | 2021-11-13 | 22:24 | 11.7171 | 75464 | 75432 | 75420
16254 | 2021-11-13 | 22:24 | 11.7171 | 75464 | 75433 | 75421
16255 | 2021-11-13 | 22:24 | 11.7171 | 75463 | 75434 | 75422
16256 | 2021-11-13 | 22:24 | 11.7172 | 75462 | 75434 | 75423
16257 | 2021-11-13 | 22:24 | 11.7172 | 75462 | 75435 | 75424
16258 | 2021-11-13 | 22:24 | 11.7172 | 75461 | 75436 | 75425
16259 | 2021-11-13 | 22:24 | 11.7173 | 75460 | 75437 | 75426
16260 | 2021-11-13 | 22:24 | 11.7173 | 75460 | 75438 | 75427
16261 | 2021-11-13 | 22:24 | 11.7173 | 75459 | 75439 | 75428
16262 | 2021-11-13 | 22:24 | 11.7173 | 75458 | 75440 | 75428
16263 | 2021-11-13 | 22:24 | 11.7174 | 75457 | 75441 | 75429
16264 | 2021-11-13 | 22:24 | 11.7174 | 75456 | 75442 | 75430
16265 | 2021-11-13 | 22:24 | 11.7174 | 75456 | 75443 | 75431
16266 | 2021-11-13 | 22:24 | 11.7175 | 75455 | 75444 | 75432
16267 | 2021-11-13 | 22:24 | 11.7175 | 75454 | 75446 | 75432
16268 | 2021-11-13 | 22:24 | 11.7175 | 75453 | 75447 | 75433
16269 | 2021-11-13 | 22:24 | 11.7175 | 75452 | 75449 | 75434
16270 | 2021-11-13 | 22:24 | 11.7176 | 75451 | 75451 | 75434
16271 | 2021-11-13 | 22:24 | 11.7176 | 75451 | 75452 | 75435
16272 | 2021-11-13 | 22:24 | 11.7176 | 75450 | 75454 | 75435
16273 | 2021-11-13 | 22:24 | 11.7177 | 75449 | 75456 | 75436
16274 | 2021-11-13 | 22:24 | 11.7177 | 75448 | 75458 | 75437
16275 | 2021-11-13 | 22:24 | 11.7177 | 75446 | 75460 | 75437
16276 | 2021-11-13 | 22:24 | 11.7177 | 75445 | 75461 | 75438
16277 | 2021-11-13 | 22:24 | 11.7178 | 75444 | 75463 | 75438
16278 | 2021-11-13 | 22:24 | 11.7178 | 75443 | 75466 | 75439
16279 | 2021-11-13 | 22:24 | 11.7178 | 75442 | 75468 | 75439
16280 | 2021-11-13 | 22:24 | 11.7179 | 75441 | 75470 | 75439
16281 | 2021-11-13 | 22:24 | 11.7179 | 75441 | 75472 | 75440
16282 | 2021-11-13 | 22:24 | 11.7179 | 75440 | 75474 | 75440
16283 | 2021-11-13 | 22:24 | 11.7179 | 75439 | 75476 | 75440
16284 | 2021-11-13 | 22:24 | 11.718 | 75438 | 75478 | 75441
16285 | 2021-11-13 | 22:24 | 11.718 | 75437 | 75480 | 75441
16286 | 2021-11-13 | 22:24 | 11.718 | 75436 | 75482 | 75441
16287 | 2021-11-13 | 22:24 | 11.7181 | 75435 | 75483 | 75441
16288 | 2021-11-13 | 22:24 | 11.7181 | 75434 | 75485 | 75441
16289 | 2021-11-13 | 22:24 | 11.7181 | 75433 | 75486 | 75441
16290 | 2021-11-13 | 22:24 | 11.7182 | 75432 | 75488 | 75442
16291 | 2021-11-13 | 22:24 | 11.7182 | 75432 | 75489 | 75442
16292 | 2021-11-13 | 22:24 | 11.7182 | 75431 | 75490 | 75442
16293 | 2021-11-13 | 22:24 | 11.7182 | 75430 | 75492 | 75442
16294 | 2021-11-13 | 22:24 | 11.7183 | 75429 | 75493 | 75442
16295 | 2021-11-13 | 22:24 | 11.7183 | 75429 | 75494 | 75442
16296 | 2021-11-13 | 22:24 | 11.7183 | 75428 | 75495 | 75442
16297 | 2021-11-13 | 22:24 | 11.7184 | 75427 | 75496 | 75441
16298 | 2021-11-13 | 22:24 | 11.7184 | 75426 | 75497 | 75441
16299 | 2021-11-13 | 22:24 | 11.7184 | 75425 | 75498 | 75441
16300 | 2021-11-13 | 22:24 | 11.7184 | 75425 | 75499 | 75441
16301 | 2021-11-13 | 22:24 | 11.7185 | 75424 | 75500 | 75441
16302 | 2021-11-13 | 22:24 | 11.7185 | 75424 | 75501 | 75440
16303 | 2021-11-13 | 22:24 | 11.7185 | 75423 | 75502 | 75440
16304 | 2021-11-13 | 22:24 | 11.7186 | 75423 | 75503 | 75440
16305 | 2021-11-13 | 22:24 | 11.7186 | 75422 | 75504 | 75440
16306 | 2021-11-13 | 22:24 | 11.7186 | 75421 | 75505 | 75439
16307 | 2021-11-13 | 22:24 | 11.7186 | 75421 | 75506 | 75439
16308 | 2021-11-13 | 22:24 | 11.7187 | 75421 | 75507 | 75439
16309 | 2021-11-13 | 22:24 | 11.7187 | 75420 | 75509 | 75438
16310 | 2021-11-13 | 22:24 | 11.7187 | 75420 | 75510 | 75438
16311 | 2021-11-13 | 22:24 | 11.7188 | 75420 | 75511 | 75438
16312 | 2021-11-13 | 22:24 | 11.7188 | 75420 | 75512 | 75437
16313 | 2021-11-13 | 22:24 | 11.7188 | 75420 | 75513 | 75437
16314 | 2021-11-13 | 22:24 | 11.7188 | 75420 | 75514 | 75437
16315 | 2021-11-13 | 22:24 | 11.7189 | 75420 | 75515 | 75436
16316 | 2021-11-13 | 22:24 | 11.7189 | 75420 | 75516 | 75436
16317 | 2021-11-13 | 22:24 | 11.7189 | 75420 | 75517 | 75436
16318 | 2021-11-13 | 22:24 | 11.719 | 75420 | 75518 | 75435
16319 | 2021-11-13 | 22:24 | 11.719 | 75420 | 75520 | 75435
16320 | 2021-11-13 | 22:24 | 11.719 | 75420 | 75521 | 75434
16321 | 2021-11-13 | 22:24 | 11.719 | 75421 | 75522 | 75434
16322 | 2021-11-13 | 22:24 | 11.7191 | 75421 | 75523 | 75434
16323 | 2021-11-13 | 22:24 | 11.7191 | 75422 | 75524 | 75433
16324 | 2021-11-13 | 22:24 | 11.7191 | 75422 | 75525 | 75433
16325 | 2021-11-13 | 22:24 | 11.7192 | 75422 | 75527 | 75433
16326 | 2021-11-13 | 22:24 | 11.7192 | 75423 | 75528 | 75432
16327 | 2021-11-13 | 22:24 | 11.7192 | 75423 | 75529 | 75432
16328 | 2021-11-13 | 22:24 | 11.7192 | 75424 | 75530 | 75431
16329 | 2021-11-13 | 22:24 | 11.7193 | 75424 | 75531 | 75431
16330 | 2021-11-13 | 22:24 | 11.7193 | 75425 | 75532 | 75430
16331 | 2021-11-13 | 22:24 | 11.7193 | 75425 | 75533 | 75430
16332 | 2021-11-13 | 22:24 | 11.7194 | 75426 | 75534 | 75429
16333 | 2021-11-13 | 22:24 | 11.7194 | 75427 | 75535 | 75429
16334 | 2021-11-13 | 22:24 | 11.7194 | 75427 | 75536 | 75428
16335 | 2021-11-13 | 22:24 | 11.7194 | 75428 | 75538 | 75428
16336 | 2021-11-13 | 22:24 | 11.7195 | 75429 | 75539 | 75427
16337 | 2021-11-13 | 22:24 | 11.7195 | 75430 | 75540 | 75426
16338 | 2021-11-13 | 22:24 | 11.7195 | 75430 | 75541 | 75426
16339 | 2021-11-13 | 22:24 | 11.7196 | 75431 | 75542 | 75425
16340 | 2021-11-13 | 22:24 | 11.7196 | 75432 | 75543 | 75424
16341 | 2021-11-13 | 22:24 | 11.7196 | 75433 | 75544 | 75424
16342 | 2021-11-13 | 22:24 | 11.7196 | 75434 | 75546 | 75423
16343 | 2021-11-13 | 22:24 | 11.7197 | 75435 | 75547 | 75422
16344 | 2021-11-13 | 22:24 | 11.7197 | 75436 | 75548 | 75422
16345 | 2021-11-13 | 22:24 | 11.7197 | 75438 | 75549 | 75421
16346 | 2021-11-13 | 22:24 | 11.7198 | 75439 | 75550 | 75420
16347 | 2021-11-13 | 22:24 | 11.7198 | 75440 | 75551 | 75419
16348 | 2021-11-13 | 22:24 | 11.7198 | 75440 | 75551 | 75419
16349 | 2021-11-13 | 22:24 | 11.7198 | 75441 | 75552 | 75418
16350 | 2021-11-13 | 22:24 | 11.7199 | 75442 | 75553 | 75417
16351 | 2021-11-13 | 22:24 | 11.7199 | 75444 | 75554 | 75417
16352 | 2021-11-13 | 22:24 | 11.7199 | 75445 | 75555 | 75416
16353 | 2021-11-13 | 22:24 | 11.72 | 75446 | 75556 | 75415
16354 | 2021-11-13 | 22:24 | 11.72 | 75447 | 75557 | 75415
16355 | 2021-11-13 | 22:24 | 11.72 | 75449 | 75557 | 75414
16356 | 2021-11-13 | 22:24 | 11.72 | 75450 | 75558 | 75413
16357 | 2021-11-13 | 22:24 | 11.7201 | 75451 | 75559 | 75412
16358 | 2021-11-13 | 22:24 | 11.7201 | 75452 | 75559 | 75411
16359 | 2021-11-13 | 22:24 | 11.7201 | 75452 | 75560 | 75411
16360 | 2021-11-13 | 22:24 | 11.7202 | 75453 | 75560 | 75410
16361 | 2021-11-13 | 22:24 | 11.7202 | 75454 | 75561 | 75409
16362 | 2021-11-13 | 22:24 | 11.7202 | 75455 | 75561 | 75408
16363 | 2021-11-13 | 22:24 | 11.7202 | 75455 | 75562 | 75407
16364 | 2021-11-13 | 22:24 | 11.7203 | 75456 | 75562 | 75406
16365 | 2021-11-13 | 22:24 | 11.7203 | 75457 | 75562 | 75406
16366 | 2021-11-13 | 22:24 | 11.7203 | 75458 | 75563 | 75405
16367 | 2021-11-13 | 22:24 | 11.7204 | 75459 | 75563 | 75404
16368 | 2021-11-13 | 22:24 | 11.7204 | 75460 | 75563 | 75403
16369 | 2021-11-13 | 22:24 | 11.7204 | 75460 | 75563 | 75402
16370 | 2021-11-13 | 22:24 | 11.7204 | 75461 | 75564 | 75401
16371 | 2021-11-13 | 22:24 | 11.7205 | 75462 | 75564 | 75401
16372 | 2021-11-13 | 22:24 | 11.7205 | 75462 | 75564 | 75400
16373 | 2021-11-13 | 22:24 | 11.7205 | 75463 | 75564 | 75399
16374 | 2021-11-13 | 22:24 | 11.7206 | 75464 | 75564 | 75399
16375 | 2021-11-13 | 22:24 | 11.7206 | 75464 | 75564 | 75398
16376 | 2021-11-13 | 22:24 | 11.7206 | 75465 | 75564 | 75398
16377 | 2021-11-13 | 22:24 | 11.7206 | 75465 | 75564 | 75397
16378 | 2021-11-13 | 22:24 | 11.7207 | 75466 | 75564 | 75397
16379 | 2021-11-13 | 22:24 | 11.7207 | 75466 | 75564 | 75397
16380 | 2021-11-13 | 22:24 | 11.7207 | 75467 | 75564 | 75396
16381 | 2021-11-13 | 22:24 | 11.7208 | 75467 | 75564 | 75396
16382 | 2021-11-13 | 22:24 | 11.7208 | 75468 | 75564 | 75396
16383 | 2021-11-13 | 22:24 | 11.7208 | 75469 | 75564 | 75396
16384 | 2021-11-13 | 22:24 | 11.7209 | 75469 | 75564 | 75396
16385 | 2021-11-13 | 22:24 | 11.7209 | 75470 | 75564 | 75396
16386 | 2021-11-13 | 22:24 | 11.7209 | 75471 | 75564 | 75396
16387 | 2021-11-13 | 22:24 | 11.7209 | 75471 | 75564 | 75396
16388 | 2021-11-13 | 22:24 | 11.721 | 75472 | 75564 | 75396
16389 | 2021-11-13 | 22:24 | 11.721 | 75472 | 75564 | 75396
16390 | 2021-11-13 | 22:24 | 11.721 | 75473 | 75564 | 75396
16391 | 2021-11-13 | 22:24 | 11.7211 | 75473 | 75564 | 75396
16392 | 2021-11-13 | 22:24 | 11.7211 | 75474 | 75563 | 75397
16393 | 2021-11-13 | 22:24 | 11.7211 | 75474 | 75563 | 75397
16394 | 2021-11-13 | 22:24 | 11.7211 | 75474 | 75563 | 75397
16395 | 2021-11-13 | 22:24 | 11.7212 | 75475 | 75563 | 75398
16396 | 2021-11-13 | 22:24 | 11.7212 | 75475 | 75563 | 75399
16397 | 2021-11-13 | 22:24 | 11.7212 | 75476 | 75563 | 75399
16398 | 2021-11-13 | 22:24 | 11.7213 | 75476 | 75563 | 75400
16399 | 2021-11-13 | 22:24 | 11.7213 | 75477 | 75563 | 75401
16400 | 2021-11-13 | 22:24 | 11.7213 | 75477 | 75564 | 75402
16401 | 2021-11-13 | 22:24 | 11.7213 | 75477 | 75564 | 75402
16402 | 2021-11-13 | 22:24 | 11.7214 | 75478 | 75564 | 75403
16403 | 2021-11-13 | 22:24 | 11.7214 | 75478 | 75564 | 75404
16404 | 2021-11-13 | 22:24 | 11.7214 | 75478 | 75564 | 75405
16405 | 2021-11-13 | 22:24 | 11.7215 | 75479 | 75564 | 75406
16406 | 2021-11-13 | 22:24 | 11.7215 | 75479 | 75564 | 75407
16407 | 2021-11-13 | 22:24 | 11.7215 | 75479 | 75564 | 75408
16408 | 2021-11-13 | 22:24 | 11.7215 | 75480 | 75564 | 75408
16409 | 2021-11-13 | 22:24 | 11.7216 | 75480 | 75564 | 75409
16410 | 2021-11-13 | 22:24 | 11.7216 | 75480 | 75564 | 75410
16411 | 2021-11-13 | 22:24 | 11.7216 | 75481 | 75565 | 75411
16412 | 2021-11-13 | 22:24 | 11.7217 | 75481 | 75565 | 75412
16413 | 2021-11-13 | 22:24 | 11.7217 | 75481 | 75565 | 75413
16414 | 2021-11-13 | 22:24 | 11.7217 | 75482 | 75565 | 75414
16415 | 2021-11-13 | 22:24 | 11.7217 | 75482 | 75565 | 75415
16416 | 2021-11-13 | 22:24 | 11.7218 | 75483 | 75565 | 75416
16417 | 2021-11-13 | 22:24 | 11.7218 | 75483 | 75566 | 75418
16418 | 2021-11-13 | 22:24 | 11.7218 | 75483 | 75566 | 75419
16419 | 2021-11-13 | 22:24 | 11.7219 | 75484 | 75566 | 75420
16420 | 2021-11-13 | 22:24 | 11.7219 | 75484 | 75566 | 75421
16421 | 2021-11-13 | 22:24 | 11.7219 | 75485 | 75566 | 75422
16422 | 2021-11-13 | 22:24 | 11.7219 | 75485 | 75566 | 75423
16423 | 2021-11-13 | 22:24 | 11.722 | 75485 | 75566 | 75423
16424 | 2021-11-13 | 22:24 | 11.722 | 75486 | 75566 | 75424
16425 | 2021-11-13 | 22:24 | 11.722 | 75486 | 75566 | 75425
16426 | 2021-11-13 | 22:24 | 11.7221 | 75487 | 75566 | 75426
16427 | 2021-11-13 | 22:24 | 11.7221 | 75487 | 75566 | 75427
16428 | 2021-11-13 | 22:24 | 11.7221 | 75487 | 75566 | 75429
16429 | 2021-11-13 | 22:24 | 11.7221 | 75488 | 75566 | 75430
16430 | 2021-11-13 | 22:24 | 11.7222 | 75489 | 75566 | 75431
16431 | 2021-11-13 | 22:24 | 11.7222 | 75489 | 75565 | 75432
16432 | 2021-11-13 | 22:24 | 11.7222 | 75490 | 75565 | 75433
16433 | 2021-11-13 | 22:24 | 11.7223 | 75490 | 75565 | 75434
16434 | 2021-11-13 | 22:24 | 11.7223 | 75491 | 75564 | 75434
16435 | 2021-11-13 | 22:24 | 11.7223 | 75491 | 75564 | 75435
16436 | 2021-11-13 | 22:24 | 11.7223 | 75492 | 75564 | 75437
16437 | 2021-11-13 | 22:24 | 11.7224 | 75492 | 75563 | 75438
16438 | 2021-11-13 | 22:24 | 11.7224 | 75493 | 75563 | 75439
16439 | 2021-11-13 | 22:24 | 11.7224 | 75493 | 75562 | 75440
16440 | 2021-11-13 | 22:24 | 11.7225 | 75494 | 75562 | 75441
16441 | 2021-11-13 | 22:24 | 11.7225 | 75494 | 75561 | 75442
16442 | 2021-11-13 | 22:24 | 11.7225 | 75495 | 75561 | 75444
16443 | 2021-11-13 | 22:24 | 11.7225 | 75495 | 75560 | 75445
16444 | 2021-11-13 | 22:24 | 11.7226 | 75496 | 75560 | 75446
16445 | 2021-11-13 | 22:24 | 11.7226 | 75496 | 75559 | 75447
16446 | 2021-11-13 | 22:24 | 11.7226 | 75497 | 75558 | 75448
16447 | 2021-11-13 | 22:24 | 11.7227 | 75497 | 75558 | 75450
16448 | 2021-11-13 | 22:24 | 11.7227 | 75498 | 75557 | 75451
16449 | 2021-11-13 | 22:24 | 11.7227 | 75498 | 75557 | 75452
16450 | 2021-11-13 | 22:24 | 11.7227 | 75498 | 75556 | 75453
16451 | 2021-11-13 | 22:24 | 11.7228 | 75499 | 75556 | 75455
16452 | 2021-11-13 | 22:24 | 11.7228 | 75499 | 75555 | 75456
16453 | 2021-11-13 | 22:24 | 11.7228 | 75499 | 75555 | 75457
16454 | 2021-11-13 | 22:24 | 11.7229 | 75499 | 75554 | 75458
16455 | 2021-11-13 | 22:24 | 11.7229 | 75499 | 75554 | 75459
16456 | 2021-11-13 | 22:24 | 11.7229 | 75500 | 75554 | 75461
16457 | 2021-11-13 | 22:24 | 11.7229 | 75500 | 75554 | 75462
16458 | 2021-11-13 | 22:24 | 11.723 | 75500 | 75554 | 75463
16459 | 2021-11-13 | 22:24 | 11.723 | 75500 | 75554 | 75465
16460 | 2021-11-13 | 22:24 | 11.723 | 75500 | 75554 | 75466
16461 | 2021-11-13 | 22:24 | 11.7231 | 75500 | 75554 | 75467
16462 | 2021-11-13 | 22:24 | 11.7231 | 75500 | 75554 | 75469
16463 | 2021-11-13 | 22:24 | 11.7231 | 75500 | 75554 | 75470
16464 | 2021-11-13 | 22:24 | 11.7231 | 75500 | 75554 | 75471
16465 | 2021-11-13 | 22:24 | 11.7232 | 75500 | 75554 | 75472
16466 | 2021-11-13 | 22:24 | 11.7232 | 75500 | 75554 | 75474
16467 | 2021-11-13 | 22:24 | 11.7232 | 75500 | 75555 | 75475
16468 | 2021-11-13 | 22:24 | 11.7233 | 75500 | 75555 | 75476
16469 | 2021-11-13 | 22:24 | 11.7233 | 75500 | 75556 | 75478
16470 | 2021-11-13 | 22:24 | 11.7233 | 75500 | 75556 | 75479
16471 | 2021-11-13 | 22:24 | 11.7233 | 75500 | 75557 | 75480
16472 | 2021-11-13 | 22:24 | 11.7234 | 75500 | 75557 | 75481
16473 | 2021-11-13 | 22:24 | 11.7234 | 75500 | 75558 | 75483
16474 | 2021-11-13 | 22:24 | 11.7234 | 75500 | 75558 | 75484
16475 | 2021-11-13 | 22:24 | 11.7235 | 75500 | 75559 | 75485
16476 | 2021-11-13 | 22:24 | 11.7235 | 75499 | 75560 | 75486
16477 | 2021-11-13 | 22:24 | 11.7235 | 75499 | 75561 | 75488
16478 | 2021-11-13 | 22:24 | 11.7236 | 75499 | 75562 | 75489
16479 | 2021-11-13 | 22:24 | 11.7236 | 75499 | 75563 | 75490
16480 | 2021-11-13 | 22:24 | 11.7236 | 75499 | 75564 | 75491
16481 | 2021-11-13 | 22:24 | 11.7236 | 75499 | 75565 | 75493
16482 | 2021-11-13 | 22:24 | 11.7237 | 75499 | 75566 | 75494
16483 | 2021-11-13 | 22:24 | 11.7237 | 75499 | 75568 | 75495
16484 | 2021-11-13 | 22:24 | 11.7237 | 75499 | 75569 | 75496
16485 | 2021-11-13 | 22:24 | 11.7238 | 75499 | 75570 | 75497
16486 | 2021-11-13 | 22:24 | 11.7238 | 75499 | 75572 | 75498
16487 | 2021-11-13 | 22:24 | 11.7238 | 75500 | 75573 | 75500
16488 | 2021-11-13 | 22:24 | 11.7238 | 75500 | 75575 | 75501
16489 | 2021-11-13 | 22:24 | 11.7239 | 75500 | 75576 | 75502
16490 | 2021-11-13 | 22:24 | 11.7239 | 75500 | 75578 | 75503
16491 | 2021-11-13 | 22:24 | 11.7239 | 75500 | 75579 | 75504
16492 | 2021-11-13 | 22:24 | 11.724 | 75500 | 75581 | 75505
16493 | 2021-11-13 | 22:24 | 11.724 | 75501 | 75583 | 75506
16494 | 2021-11-13 | 22:24 | 11.724 | 75501 | 75584 | 75507
16495 | 2021-11-13 | 22:24 | 11.724 | 75501 | 75586 | 75508
16496 | 2021-11-13 | 22:24 | 11.7241 | 75501 | 75588 | 75509
16497 | 2021-11-13 | 22:24 | 11.7241 | 75501 | 75589 | 75510
16498 | 2021-11-13 | 22:24 | 11.7241 | 75502 | 75591 | 75511
16499 | 2021-11-13 | 22:24 | 11.7242 | 75502 | 75593 | 75512
16500 | 2021-11-13 | 22:24 | 11.7242 | 75502 | 75595 | 75513
16501 | 2021-11-13 | 22:24 | 11.7242 | 75503 | 75596 | 75514
16502 | 2021-11-13 | 22:24 | 11.7242 | 75503 | 75598 | 75516
16503 | 2021-11-13 | 22:24 | 11.7243 | 75503 | 75600 | 75517
16504 | 2021-11-13 | 22:24 | 11.7243 | 75504 | 75602 | 75518
16505 | 2021-11-13 | 22:24 | 11.7243 | 75504 | 75604 | 75519
16506 | 2021-11-13 | 22:24 | 11.7244 | 75504 | 75605 | 75520
16507 | 2021-11-13 | 22:24 | 11.7244 | 75504 | 75607 | 75521
16508 | 2021-11-13 | 22:24 | 11.7244 | 75505 | 75609 | 75522
16509 | 2021-11-13 | 22:24 | 11.7244 | 75505 | 75611 | 75523
16510 | 2021-11-13 | 22:24 | 11.7245 | 75505 | 75613 | 75524
16511 | 2021-11-13 | 22:24 | 11.7245 | 75505 | 75615 | 75525
16512 | 2021-11-13 | 22:24 | 11.7245 | 75506 | 75617 | 75526
16513 | 2021-11-13 | 22:24 | 11.7246 | 75506 | 75620 | 75527
16514 | 2021-11-13 | 22:24 | 11.7246 | 75506 | 75622 | 75528
16515 | 2021-11-13 | 22:24 | 11.7246 | 75506 | 75624 | 75529
16516 | 2021-11-13 | 22:24 | 11.7246 | 75506 | 75626 | 75530
16517 | 2021-11-13 | 22:24 | 11.7247 | 75506 | 75628 | 75531
16518 | 2021-11-13 | 22:24 | 11.7247 | 75506 | 75631 | 75532
16519 | 2021-11-13 | 22:24 | 11.7247 | 75506 | 75633 | 75533
16520 | 2021-11-13 | 22:24 | 11.7248 | 75506 | 75636 | 75534
16521 | 2021-11-13 | 22:24 | 11.7248 | 75506 | 75638 | 75534
16522 | 2021-11-13 | 22:24 | 11.7248 | 75507 | 75641 | 75535
16523 | 2021-11-13 | 22:24 | 11.7248 | 75507 | 75643 | 75536
16524 | 2021-11-13 | 22:24 | 11.7249 | 75507 | 75646 | 75537
16525 | 2021-11-13 | 22:24 | 11.7249 | 75507 | 75648 | 75537
16526 | 2021-11-13 | 22:24 | 11.7249 | 75507 | 75651 | 75538
16527 | 2021-11-13 | 22:24 | 11.725 | 75507 | 75653 | 75539
16528 | 2021-11-13 | 22:24 | 11.725 | 75507 | 75655 | 75539
16529 | 2021-11-13 | 22:24 | 11.725 | 75507 | 75657 | 75540
16530 | 2021-11-13 | 22:24 | 11.725 | 75507 | 75660 | 75541
16531 | 2021-11-13 | 22:24 | 11.7251 | 75507 | 75662 | 75541
16532 | 2021-11-13 | 22:24 | 11.7251 | 75507 | 75665 | 75542
16533 | 2021-11-13 | 22:24 | 11.7251 | 75507 | 75667 | 75542
16534 | 2021-11-13 | 22:24 | 11.7252 | 75507 | 75670 | 75542
16535 | 2021-11-13 | 22:24 | 11.7252 | 75507 | 75673 | 75543
16536 | 2021-11-13 | 22:24 | 11.7252 | 75507 | 75675 | 75543
16537 | 2021-11-13 | 22:24 | 11.7252 | 75507 | 75678 | 75543
16538 | 2021-11-13 | 22:24 | 11.7253 | 75506 | 75680 | 75544
16539 | 2021-11-13 | 22:24 | 11.7253 | 75506 | 75683 | 75544
16540 | 2021-11-13 | 22:24 | 11.7253 | 75506 | 75685 | 75544
16541 | 2021-11-13 | 22:24 | 11.7254 | 75506 | 75688 | 75544
16542 | 2021-11-13 | 22:24 | 11.7254 | 75507 | 75690 | 75544
16543 | 2021-11-13 | 22:24 | 11.7254 | 75507 | 75692 | 75544
16544 | 2021-11-13 | 22:24 | 11.7254 | 75507 | 75694 | 75545
16545 | 2021-11-13 | 22:24 | 11.7255 | 75507 | 75696 | 75545
16546 | 2021-11-13 | 22:24 | 11.7255 | 75507 | 75698 | 75545
16547 | 2021-11-13 | 22:24 | 11.7255 | 75507 | 75700 | 75545
16548 | 2021-11-13 | 22:24 | 11.7256 | 75507 | 75701 | 75545
16549 | 2021-11-13 | 22:24 | 11.7256 | 75508 | 75702 | 75545
16550 | 2021-11-13 | 22:24 | 11.7256 | 75508 | 75704 | 75545
16551 | 2021-11-13 | 22:24 | 11.7256 | 75508 | 75705 | 75545
16552 | 2021-11-13 | 22:24 | 11.7257 | 75509 | 75706 | 75545
16553 | 2021-11-13 | 22:24 | 11.7257 | 75510 | 75707 | 75545
16554 | 2021-11-13 | 22:24 | 11.7257 | 75510 | 75708 | 75545
16555 | 2021-11-13 | 22:24 | 11.7258 | 75511 | 75708 | 75545
16556 | 2021-11-13 | 22:24 | 11.7258 | 75511 | 75709 | 75544
16557 | 2021-11-13 | 22:24 | 11.7258 | 75512 | 75709 | 75544
16558 | 2021-11-13 | 22:24 | 11.7258 | 75512 | 75710 | 75544
16559 | 2021-11-13 | 22:24 | 11.7259 | 75513 | 75710 | 75544
16560 | 2021-11-13 | 22:24 | 11.7259 | 75513 | 75711 | 75544
16561 | 2021-11-13 | 22:24 | 11.7259 | 75514 | 75711 | 75544
16562 | 2021-11-13 | 22:24 | 11.726 | 75515 | 75712 | 75544
16563 | 2021-11-13 | 22:24 | 11.726 | 75516 | 75713 | 75544
16564 | 2021-11-13 | 22:24 | 11.726 | 75517 | 75713 | 75544
16565 | 2021-11-13 | 22:24 | 11.726 | 75518 | 75714 | 75544
16566 | 2021-11-13 | 22:24 | 11.7261 | 75519 | 75714 | 75544
16567 | 2021-11-13 | 22:24 | 11.7261 | 75521 | 75715 | 75544
16568 | 2021-11-13 | 22:24 | 11.7261 | 75522 | 75716 | 75544
16569 | 2021-11-13 | 22:24 | 11.7262 | 75523 | 75716 | 75544
16570 | 2021-11-13 | 22:24 | 11.7262 | 75524 | 75717 | 75544
16571 | 2021-11-13 | 22:24 | 11.7262 | 75525 | 75718 | 75544
16572 | 2021-11-13 | 22:24 | 11.7263 | 75526 | 75719 | 75544
16573 | 2021-11-13 | 22:24 | 11.7263 | 75528 | 75719 | 75544
16574 | 2021-11-13 | 22:24 | 11.7263 | 75529 | 75720 | 75544
16575 | 2021-11-13 | 22:24 | 11.7263 | 75531 | 75721 | 75544
16576 | 2021-11-13 | 22:24 | 11.7264 | 75532 | 75722 | 75545
16577 | 2021-11-13 | 22:24 | 11.7264 | 75534 | 75722 | 75545
16578 | 2021-11-13 | 22:24 | 11.7264 | 75535 | 75723 | 75545
16579 | 2021-11-13 | 22:24 | 11.7265 | 75537 | 75724 | 75545
16580 | 2021-11-13 | 22:24 | 11.7265 | 75539 | 75725 | 75545
16581 | 2021-11-13 | 22:24 | 11.7265 | 75540 | 75726 | 75545
16582 | 2021-11-13 | 22:24 | 11.7265 | 75542 | 75727 | 75545
16583 | 2021-11-13 | 22:24 | 11.7266 | 75544 | 75728 | 75546
16584 | 2021-11-13 | 22:24 | 11.7266 | 75546 | 75728 | 75546
16585 | 2021-11-13 | 22:24 | 11.7266 | 75548 | 75729 | 75546
16586 | 2021-11-13 | 22:24 | 11.7267 | 75550 | 75730 | 75546
16587 | 2021-11-13 | 22:24 | 11.7267 | 75552 | 75731 | 75546
16588 | 2021-11-13 | 22:24 | 11.7267 | 75554 | 75732 | 75546
16589 | 2021-11-13 | 22:24 | 11.7267 | 75556 | 75733 | 75546
16590 | 2021-11-13 | 22:24 | 11.7268 | 75558 | 75733 | 75546
16591 | 2021-11-13 | 22:24 | 11.7268 | 75560 | 75734 | 75546
16592 | 2021-11-13 | 22:24 | 11.7268 | 75562 | 75735 | 75546
16593 | 2021-11-13 | 22:24 | 11.7269 | 75564 | 75736 | 75546
16594 | 2021-11-13 | 22:24 | 11.7269 | 75566 | 75737 | 75546
16595 | 2021-11-13 | 22:24 | 11.7269 | 75568 | 75738 | 75546
16596 | 2021-11-13 | 22:24 | 11.7269 | 75570 | 75739 | 75546
16597 | 2021-11-13 | 22:24 | 11.727 | 75573 | 75740 | 75546
16598 | 2021-11-13 | 22:24 | 11.727 | 75575 | 75741 | 75546
16599 | 2021-11-13 | 22:24 | 11.727 | 75577 | 75742 | 75546
16600 | 2021-11-13 | 22:24 | 11.7271 | 75579 | 75742 | 75546
16601 | 2021-11-13 | 22:24 | 11.7271 | 75581 | 75743 | 75546
16602 | 2021-11-13 | 22:24 | 11.7271 | 75583 | 75744 | 75546
16603 | 2021-11-13 | 22:24 | 11.7271 | 75585 | 75745 | 75546
16604 | 2021-11-13 | 22:24 | 11.7272 | 75588 | 75746 | 75545
16605 | 2021-11-13 | 22:24 | 11.7272 | 75590 | 75747 | 75545
16606 | 2021-11-13 | 22:24 | 11.7272 | 75592 | 75748 | 75545
16607 | 2021-11-13 | 22:24 | 11.7273 | 75594 | 75748 | 75545
16608 | 2021-11-13 | 22:24 | 11.7273 | 75596 | 75749 | 75545
16609 | 2021-11-13 | 22:24 | 11.7273 | 75598 | 75750 | 75545
16610 | 2021-11-13 | 22:24 | 11.7273 | 75600 | 75751 | 75545
16611 | 2021-11-13 | 22:24 | 11.7274 | 75602 | 75751 | 75545
16612 | 2021-11-13 | 22:24 | 11.7274 | 75604 | 75752 | 75544
16613 | 2021-11-13 | 22:24 | 11.7274 | 75606 | 75753 | 75544
16614 | 2021-11-13 | 22:24 | 11.7275 | 75608 | 75753 | 75543
16615 | 2021-11-13 | 22:24 | 11.7275 | 75609 | 75754 | 75543
16616 | 2021-11-13 | 22:24 | 11.7275 | 75611 | 75754 | 75543
16617 | 2021-11-13 | 22:24 | 11.7275 | 75613 | 75755 | 75543
16618 | 2021-11-13 | 22:24 | 11.7276 | 75614 | 75755 | 75542
16619 | 2021-11-13 | 22:24 | 11.7276 | 75616 | 75755 | 75542
16620 | 2021-11-13 | 22:24 | 11.7276 | 75617 | 75756 | 75542
16621 | 2021-11-13 | 22:24 | 11.7277 | 75619 | 75756 | 75541
16622 | 2021-11-13 | 22:24 | 11.7277 | 75620 | 75756 | 75541
16623 | 2021-11-13 | 22:24 | 11.7277 | 75621 | 75757 | 75541
16624 | 2021-11-13 | 22:24 | 11.7277 | 75623 | 75757 | 75540
16625 | 2021-11-13 | 22:24 | 11.7278 | 75624 | 75757 | 75540
16626 | 2021-11-13 | 22:24 | 11.7278 | 75625 | 75757 | 75540
16627 | 2021-11-13 | 22:24 | 11.7278 | 75626 | 75757 | 75540
16628 | 2021-11-13 | 22:24 | 11.7279 | 75628 | 75757 | 75540
16629 | 2021-11-13 | 22:24 | 11.7279 | 75629 | 75757 | 75540
16630 | 2021-11-13 | 22:24 | 11.7279 | 75630 | 75757 | 75540
16631 | 2021-11-13 | 22:24 | 11.7279 | 75631 | 75757 | 75540
16632 | 2021-11-13 | 22:24 | 11.728 | 75632 | 75757 | 75540
16633 | 2021-11-13 | 22:24 | 11.728 | 75633 | 75757 | 75540
16634 | 2021-11-13 | 22:24 | 11.728 | 75634 | 75757 | 75540
16635 | 2021-11-13 | 22:24 | 11.7281 | 75635 | 75757 | 75540
16636 | 2021-11-13 | 22:24 | 11.7281 | 75636 | 75757 | 75541
16637 | 2021-11-13 | 22:24 | 11.7281 | 75637 | 75757 | 75541
16638 | 2021-11-13 | 22:24 | 11.7281 | 75638 | 75757 | 75542
16639 | 2021-11-13 | 22:24 | 11.7282 | 75639 | 75757 | 75543
16640 | 2021-11-13 | 22:24 | 11.7282 | 75640 | 75757 | 75544
16641 | 2021-11-13 | 22:24 | 11.7282 | 75641 | 75757 | 75545
16642 | 2021-11-13 | 22:24 | 11.7283 | 75642 | 75757 | 75546
16643 | 2021-11-13 | 22:24 | 11.7283 | 75643 | 75757 | 75547
16644 | 2021-11-13 | 22:24 | 11.7283 | 75644 | 75758 | 75548
16645 | 2021-11-13 | 22:24 | 11.7283 | 75645 | 75758 | 75549
16646 | 2021-11-13 | 22:24 | 11.7284 | 75646 | 75758 | 75551
16647 | 2021-11-13 | 22:24 | 11.7284 | 75647 | 75758 | 75552
16648 | 2021-11-13 | 22:24 | 11.7284 | 75648 | 75758 | 75554
16649 | 2021-11-13 | 22:24 | 11.7285 | 75649 | 75758 | 75556
16650 | 2021-11-13 | 22:24 | 11.7285 | 75650 | 75758 | 75558
16651 | 2021-11-13 | 22:24 | 11.7285 | 75651 | 75758 | 75560
16652 | 2021-11-13 | 22:24 | 11.7285 | 75652 | 75759 | 75562
16653 | 2021-11-13 | 22:24 | 11.7286 | 75653 | 75759 | 75564
16654 | 2021-11-13 | 22:24 | 11.7286 | 75653 | 75759 | 75566
16655 | 2021-11-13 | 22:24 | 11.7286 | 75654 | 75759 | 75568
16656 | 2021-11-13 | 22:24 | 11.7287 | 75655 | 75760 | 75570
16657 | 2021-11-13 | 22:24 | 11.7287 | 75656 | 75760 | 75573
16658 | 2021-11-13 | 22:24 | 11.7287 | 75657 | 75761 | 75575
16659 | 2021-11-13 | 22:24 | 11.7287 | 75658 | 75761 | 75577
16660 | 2021-11-13 | 22:24 | 11.7288 | 75658 | 75762 | 75580
16661 | 2021-11-13 | 22:24 | 11.7288 | 75659 | 75762 | 75582
16662 | 2021-11-13 | 22:24 | 11.7288 | 75660 | 75762 | 75585
16663 | 2021-11-13 | 22:24 | 11.7289 | 75661 | 75763 | 75587
16664 | 2021-11-13 | 22:24 | 11.7289 | 75661 | 75763 | 75590
16665 | 2021-11-13 | 22:24 | 11.7289 | 75662 | 75764 | 75592
16666 | 2021-11-13 | 22:24 | 11.729 | 75663 | 75764 | 75594
16667 | 2021-11-13 | 22:24 | 11.729 | 75664 | 75765 | 75597
16668 | 2021-11-13 | 22:24 | 11.729 | 75665 | 75766 | 75599
16669 | 2021-11-13 | 22:24 | 11.729 | 75666 | 75766 | 75602
16670 | 2021-11-13 | 22:24 | 11.7291 | 75666 | 75767 | 75604
16671 | 2021-11-13 | 22:24 | 11.7291 | 75667 | 75767 | 75607
16672 | 2021-11-13 | 22:24 | 11.7291 | 75668 | 75768 | 75609
16673 | 2021-11-13 | 22:24 | 11.7292 | 75669 | 75768 | 75611
16674 | 2021-11-13 | 22:24 | 11.7292 | 75670 | 75769 | 75614
16675 | 2021-11-13 | 22:24 | 11.7292 | 75671 | 75769 | 75616
16676 | 2021-11-13 | 22:24 | 11.7292 | 75671 | 75769 | 75618
16677 | 2021-11-13 | 22:24 | 11.7293 | 75672 | 75770 | 75620
16678 | 2021-11-13 | 22:24 | 11.7293 | 75673 | 75770 | 75623
16679 | 2021-11-13 | 22:24 | 11.7293 | 75674 | 75771 | 75625
16680 | 2021-11-13 | 22:24 | 11.7294 | 75675 | 75771 | 75628
16681 | 2021-11-13 | 22:24 | 11.7294 | 75676 | 75771 | 75630
16682 | 2021-11-13 | 22:24 | 11.7294 | 75676 | 75772 | 75633
16683 | 2021-11-13 | 22:24 | 11.7294 | 75677 | 75772 | 75635
16684 | 2021-11-13 | 22:24 | 11.7295 | 75678 | 75772 | 75637
16685 | 2021-11-13 | 22:24 | 11.7295 | 75679 | 75772 | 75639
16686 | 2021-11-13 | 22:24 | 11.7295 | 75680 | 75772 | 75641
16687 | 2021-11-13 | 22:24 | 11.7296 | 75680 | 75772 | 75644
16688 | 2021-11-13 | 22:24 | 11.7296 | 75681 | 75772 | 75646
16689 | 2021-11-13 | 22:24 | 11.7296 | 75682 | 75772 | 75648
16690 | 2021-11-13 | 22:24 | 11.7296 | 75683 | 75773 | 75650
16691 | 2021-11-13 | 22:24 | 11.7297 | 75683 | 75773 | 75652
16692 | 2021-11-13 | 22:24 | 11.7297 | 75684 | 75773 | 75655
16693 | 2021-11-13 | 22:24 | 11.7297 | 75685 | 75773 | 75657
16694 | 2021-11-13 | 22:24 | 11.7298 | 75685 | 75773 | 75659
16695 | 2021-11-13 | 22:24 | 11.7298 | 75686 | 75773 | 75661
16696 | 2021-11-13 | 22:24 | 11.7298 | 75687 | 75773 | 75662
16697 | 2021-11-13 | 22:24 | 11.7298 | 75687 | 75773 | 75664
16698 | 2021-11-13 | 22:24 | 11.7299 | 75688 | 75774 | 75666
16699 | 2021-11-13 | 22:24 | 11.7299 | 75688 | 75774 | 75668
16700 | 2021-11-13 | 22:24 | 11.7299 | 75688 | 75775 | 75670
16701 | 2021-11-13 | 22:24 | 11.73 | 75689 | 75775 | 75671
16702 | 2021-11-13 | 22:24 | 11.73 | 75689 | 75776 | 75673
16703 | 2021-11-13 | 22:24 | 11.73 | 75689 | 75776 | 75675
16704 | 2021-11-13 | 22:24 | 11.73 | 75690 | 75777 | 75677
16705 | 2021-11-13 | 22:24 | 11.7301 | 75690 | 75777 | 75678
16706 | 2021-11-13 | 22:24 | 11.7301 | 75690 | 75778 | 75680
16707 | 2021-11-13 | 22:24 | 11.7301 | 75690 | 75778 | 75681
16708 | 2021-11-13 | 22:24 | 11.7302 | 75690 | 75779 | 75683
16709 | 2021-11-13 | 22:24 | 11.7302 | 75691 | 75780 | 75684
16710 | 2021-11-13 | 22:24 | 11.7302 | 75691 | 75781 | 75686
16711 | 2021-11-13 | 22:24 | 11.7302 | 75691 | 75782 | 75688
16712 | 2021-11-13 | 22:24 | 11.7303 | 75691 | 75783 | 75689
16713 | 2021-11-13 | 22:24 | 11.7303 | 75691 | 75785 | 75691
16714 | 2021-11-13 | 22:24 | 11.7303 | 75691 | 75786 | 75692
16715 | 2021-11-13 | 22:24 | 11.7304 | 75691 | 75787 | 75693
16716 | 2021-11-13 | 22:24 | 11.7304 | 75691 | 75789 | 75695
16717 | 2021-11-13 | 22:24 | 11.7304 | 75691 | 75790 | 75696
16718 | 2021-11-13 | 22:24 | 11.7304 | 75691 | 75792 | 75698
16719 | 2021-11-13 | 22:24 | 11.7305 | 75691 | 75794 | 75699
16720 | 2021-11-13 | 22:24 | 11.7305 | 75691 | 75795 | 75701
16721 | 2021-11-13 | 22:24 | 11.7305 | 75691 | 75797 | 75702
16722 | 2021-11-13 | 22:24 | 11.7306 | 75691 | 75799 | 75703
16723 | 2021-11-13 | 22:24 | 11.7306 | 75691 | 75801 | 75705
16724 | 2021-11-13 | 22:24 | 11.7306 | 75691 | 75803 | 75706
16725 | 2021-11-13 | 22:24 | 11.7306 | 75691 | 75805 | 75707
16726 | 2021-11-13 | 22:24 | 11.7307 | 75691 | 75808 | 75708
16727 | 2021-11-13 | 22:24 | 11.7307 | 75691 | 75810 | 75710
16728 | 2021-11-13 | 22:24 | 11.7307 | 75691 | 75812 | 75711
16729 | 2021-11-13 | 22:24 | 11.7308 | 75691 | 75814 | 75712
16730 | 2021-11-13 | 22:24 | 11.7308 | 75692 | 75817 | 75713
16731 | 2021-11-13 | 22:24 | 11.7308 | 75692 | 75820 | 75714
16732 | 2021-11-13 | 22:24 | 11.7308 | 75692 | 75822 | 75715
16733 | 2021-11-13 | 22:24 | 11.7309 | 75692 | 75825 | 75716
16734 | 2021-11-13 | 22:24 | 11.7309 | 75693 | 75828 | 75717
16735 | 2021-11-13 | 22:24 | 11.7309 | 75693 | 75831 | 75718
16736 | 2021-11-13 | 22:24 | 11.731 | 75693 | 75834 | 75719
16737 | 2021-11-13 | 22:24 | 11.731 | 75694 | 75837 | 75720
16738 | 2021-11-13 | 22:24 | 11.731 | 75694 | 75840 | 75721
16739 | 2021-11-13 | 22:24 | 11.731 | 75695 | 75843 | 75722
16740 | 2021-11-13 | 22:24 | 11.7311 | 75695 | 75846 | 75723
16741 | 2021-11-13 | 22:24 | 11.7311 | 75696 | 75849 | 75724
16742 | 2021-11-13 | 22:24 | 11.7311 | 75696 | 75852 | 75725
16743 | 2021-11-13 | 22:24 | 11.7312 | 75697 | 75856 | 75726
16744 | 2021-11-13 | 22:24 | 11.7312 | 75697 | 75859 | 75726
16745 | 2021-11-13 | 22:24 | 11.7312 | 75698 | 75862 | 75727
16746 | 2021-11-13 | 22:24 | 11.7312 | 75699 | 75866 | 75728
16747 | 2021-11-13 | 22:24 | 11.7313 | 75699 | 75869 | 75729
16748 | 2021-11-13 | 22:24 | 11.7313 | 75700 | 75872 | 75730
16749 | 2021-11-13 | 22:24 | 11.7313 | 75701 | 75875 | 75731
16750 | 2021-11-13 | 22:24 | 11.7314 | 75701 | 75879 | 75732
16751 | 2021-11-13 | 22:24 | 11.7314 | 75702 | 75882 | 75733
16752 | 2021-11-13 | 22:24 | 11.7314 | 75703 | 75885 | 75734
16753 | 2021-11-13 | 22:24 | 11.7314 | 75703 | 75888 | 75735
16754 | 2021-11-13 | 22:24 | 11.7315 | 75704 | 75891 | 75736
16755 | 2021-11-13 | 22:24 | 11.7315 | 75705 | 75894 | 75737
16756 | 2021-11-13 | 22:24 | 11.7315 | 75705 | 75897 | 75738
16757 | 2021-11-13 | 22:24 | 11.7316 | 75706 | 75900 | 75739
16758 | 2021-11-13 | 22:24 | 11.7316 | 75707 | 75903 | 75740
16759 | 2021-11-13 | 22:24 | 11.7316 | 75707 | 75906 | 75741
16760 | 2021-11-13 | 22:24 | 11.7317 | 75708 | 75908 | 75742
16761 | 2021-11-13 | 22:24 | 11.7317 | 75708 | 75911 | 75743
16762 | 2021-11-13 | 22:24 | 11.7317 | 75709 | 75914 | 75744
16763 | 2021-11-13 | 22:24 | 11.7317 | 75710 | 75917 | 75745
16764 | 2021-11-13 | 22:24 | 11.7318 | 75710 | 75919 | 75745
16765 | 2021-11-13 | 22:24 | 11.7318 | 75711 | 75922 | 75746
16766 | 2021-11-13 | 22:24 | 11.7318 | 75712 | 75925 | 75747
16767 | 2021-11-13 | 22:24 | 11.7319 | 75712 | 75928 | 75748
16768 | 2021-11-13 | 22:24 | 11.7319 | 75713 | 75931 | 75749
16769 | 2021-11-13 | 22:24 | 11.7319 | 75713 | 75934 | 75749
16770 | 2021-11-13 | 22:24 | 11.7319 | 75714 | 75936 | 75750
16771 | 2021-11-13 | 22:24 | 11.732 | 75714 | 75939 | 75751
16772 | 2021-11-13 | 22:24 | 11.732 | 75715 | 75942 | 75751
16773 | 2021-11-13 | 22:24 | 11.732 | 75715 | 75944 | 75752
16774 | 2021-11-13 | 22:24 | 11.7321 | 75716 | 75947 | 75752
16775 | 2021-11-13 | 22:24 | 11.7321 | 75716 | 75950 | 75753
16776 | 2021-11-13 | 22:24 | 11.7321 | 75717 | 75952 | 75753
16777 | 2021-11-13 | 22:24 | 11.7321 | 75718 | 75955 | 75754
16778 | 2021-11-13 | 22:24 | 11.7322 | 75718 | 75957 | 75754
16779 | 2021-11-13 | 22:24 | 11.7322 | 75719 | 75960 | 75755
16780 | 2021-11-13 | 22:24 | 11.7322 | 75719 | 75962 | 75755
16781 | 2021-11-13 | 22:24 | 11.7323 | 75720 | 75964 | 75755
16782 | 2021-11-13 | 22:24 | 11.7323 | 75720 | 75966 | 75756
16783 | 2021-11-13 | 22:24 | 11.7323 | 75720 | 75968 | 75756
16784 | 2021-11-13 | 22:24 | 11.7323 | 75721 | 75970 | 75756
16785 | 2021-11-13 | 22:24 | 11.7324 | 75722 | 75972 | 75756
16786 | 2021-11-13 | 22:24 | 11.7324 | 75722 | 75974 | 75756
16787 | 2021-11-13 | 22:24 | 11.7324 | 75723 | 75976 | 75757
16788 | 2021-11-13 | 22:24 | 11.7325 | 75723 | 75978 | 75757
16789 | 2021-11-13 | 22:24 | 11.7325 | 75724 | 75980 | 75757
16790 | 2021-11-13 | 22:24 | 11.7325 | 75725 | 75981 | 75757
16791 | 2021-11-13 | 22:24 | 11.7325 | 75725 | 75983 | 75757
16792 | 2021-11-13 | 22:24 | 11.7326 | 75725 | 75984 | 75757
16793 | 2021-11-13 | 22:24 | 11.7326 | 75726 | 75986 | 75757
16794 | 2021-11-13 | 22:24 | 11.7326 | 75727 | 75988 | 75757
16795 | 2021-11-13 | 22:24 | 11.7327 | 75727 | 75989 | 75757
16796 | 2021-11-13 | 22:24 | 11.7327 | 75728 | 75991 | 75757
16797 | 2021-11-13 | 22:24 | 11.7327 | 75729 | 75992 | 75757
16798 | 2021-11-13 | 22:24 | 11.7327 | 75730 | 75993 | 75757
16799 | 2021-11-13 | 22:24 | 11.7328 | 75731 | 75995 | 75757
16800 | 2021-11-13 | 22:24 | 11.7328 | 75732 | 75996 | 75757
16801 | 2021-11-13 | 22:24 | 11.7328 | 75732 | 75997 | 75757
16802 | 2021-11-13 | 22:24 | 11.7329 | 75733 | 75998 | 75757
16803 | 2021-11-13 | 22:24 | 11.7329 | 75734 | 75998 | 75757
16804 | 2021-11-13 | 22:24 | 11.7329 | 75736 | 75999 | 75757
16805 | 2021-11-13 | 22:24 | 11.7329 | 75737 | 76000 | 75757
16806 | 2021-11-13 | 22:24 | 11.733 | 75738 | 76001 | 75757
16807 | 2021-11-13 | 22:24 | 11.733 | 75740 | 76001 | 75757
16808 | 2021-11-13 | 22:24 | 11.733 | 75741 | 76002 | 75757
16809 | 2021-11-13 | 22:24 | 11.7331 | 75743 | 76002 | 75757
16810 | 2021-11-13 | 22:24 | 11.7331 | 75744 | 76002 | 75757
16811 | 2021-11-13 | 22:24 | 11.7331 | 75746 | 76003 | 75757
16812 | 2021-11-13 | 22:24 | 11.7331 | 75748 | 76003 | 75757
16813 | 2021-11-13 | 22:24 | 11.7332 | 75749 | 76003 | 75757
16814 | 2021-11-13 | 22:24 | 11.7332 | 75751 | 76004 | 75758
16815 | 2021-11-13 | 22:24 | 11.7332 | 75753 | 76004 | 75758
16816 | 2021-11-13 | 22:24 | 11.7333 | 75754 | 76004 | 75758
16817 | 2021-11-13 | 22:24 | 11.7333 | 75756 | 76004 | 75758
16818 | 2021-11-13 | 22:24 | 11.7333 | 75758 | 76005 | 75758
16819 | 2021-11-13 | 22:24 | 11.7333 | 75760 | 76005 | 75759
16820 | 2021-11-13 | 22:24 | 11.7334 | 75762 | 76005 | 75759
16821 | 2021-11-13 | 22:24 | 11.7334 | 75764 | 76006 | 75759
16822 | 2021-11-13 | 22:24 | 11.7334 | 75766 | 76006 | 75759
16823 | 2021-11-13 | 22:24 | 11.7335 | 75768 | 76006 | 75760
16824 | 2021-11-13 | 22:24 | 11.7335 | 75770 | 76007 | 75760
16825 | 2021-11-13 | 22:24 | 11.7335 | 75772 | 76007 | 75760
16826 | 2021-11-13 | 22:24 | 11.7335 | 75774 | 76008 | 75761
16827 | 2021-11-13 | 22:24 | 11.7336 | 75777 | 76008 | 75761
16828 | 2021-11-13 | 22:24 | 11.7336 | 75779 | 76009 | 75762
16829 | 2021-11-13 | 22:24 | 11.7336 | 75781 | 76009 | 75763
16830 | 2021-11-13 | 22:24 | 11.7337 | 75783 | 76009 | 75763
16831 | 2021-11-13 | 22:24 | 11.7337 | 75785 | 76009 | 75764
16832 | 2021-11-13 | 22:24 | 11.7337 | 75787 | 76010 | 75764
16833 | 2021-11-13 | 22:24 | 11.7337 | 75789 | 76010 | 75765
16834 | 2021-11-13 | 22:24 | 11.7338 | 75792 | 76011 | 75765
16835 | 2021-11-13 | 22:24 | 11.7338 | 75794 | 76011 | 75766
16836 | 2021-11-13 | 22:24 | 11.7338 | 75796 | 76011 | 75766
16837 | 2021-11-13 | 22:24 | 11.7339 | 75798 | 76012 | 75767
16838 | 2021-11-13 | 22:24 | 11.7339 | 75801 | 76012 | 75768
16839 | 2021-11-13 | 22:24 | 11.7339 | 75803 | 76012 | 75769
16840 | 2021-11-13 | 22:24 | 11.7339 | 75805 | 76012 | 75769
16841 | 2021-11-13 | 22:24 | 11.734 | 75807 | 76012 | 75770
16842 | 2021-11-13 | 22:24 | 11.734 | 75809 | 76013 | 75771
16843 | 2021-11-13 | 22:24 | 11.734 | 75811 | 76013 | 75771
16844 | 2021-11-13 | 22:24 | 11.7341 | 75813 | 76013 | 75772
16845 | 2021-11-13 | 22:24 | 11.7341 | 75815 | 76014 | 75773
16846 | 2021-11-13 | 22:24 | 11.7341 | 75817 | 76014 | 75774
16847 | 2021-11-13 | 22:24 | 11.7341 | 75819 | 76014 | 75774
16848 | 2021-11-13 | 22:24 | 11.7342 | 75822 | 76014 | 75775
16849 | 2021-11-13 | 22:24 | 11.7342 | 75824 | 76014 | 75776
16850 | 2021-11-13 | 22:24 | 11.7342 | 75825 | 76014 | 75777
16851 | 2021-11-13 | 22:24 | 11.7343 | 75827 | 76015 | 75778
16852 | 2021-11-13 | 22:24 | 11.7343 | 75829 | 76015 | 75779
16853 | 2021-11-13 | 22:24 | 11.7343 | 75830 | 76015 | 75779
16854 | 2021-11-13 | 22:24 | 11.7344 | 75832 | 76015 | 75780
16855 | 2021-11-13 | 22:24 | 11.7344 | 75834 | 76015 | 75781
16856 | 2021-11-13 | 22:24 | 11.7344 | 75835 | 76015 | 75782
16857 | 2021-11-13 | 22:24 | 11.7344 | 75837 | 76015 | 75782
16858 | 2021-11-13 | 22:24 | 11.7345 | 75838 | 76016 | 75783
16859 | 2021-11-13 | 22:24 | 11.7345 | 75840 | 76016 | 75784
16860 | 2021-11-13 | 22:24 | 11.7345 | 75841 | 76016 | 75785
16861 | 2021-11-13 | 22:24 | 11.7346 | 75842 | 76016 | 75785
16862 | 2021-11-13 | 22:24 | 11.7346 | 75843 | 76016 | 75786
16863 | 2021-11-13 | 22:24 | 11.7346 | 75844 | 76016 | 75787
16864 | 2021-11-13 | 22:24 | 11.7346 | 75845 | 76016 | 75787
16865 | 2021-11-13 | 22:24 | 11.7347 | 75846 | 76016 | 75788
16866 | 2021-11-13 | 22:24 | 11.7347 | 75847 | 76016 | 75789
16867 | 2021-11-13 | 22:24 | 11.7347 | 75848 | 76016 | 75790
16868 | 2021-11-13 | 22:24 | 11.7348 | 75849 | 76016 | 75791
16869 | 2021-11-13 | 22:24 | 11.7348 | 75850 | 76016 | 75792
16870 | 2021-11-13 | 22:24 | 11.7348 | 75851 | 76016 | 75793
16871 | 2021-11-13 | 22:24 | 11.7348 | 75852 | 76015 | 75794
16872 | 2021-11-13 | 22:24 | 11.7349 | 75853 | 76015 | 75795
16873 | 2021-11-13 | 22:24 | 11.7349 | 75853 | 76015 | 75796
16874 | 2021-11-13 | 22:24 | 11.7349 | 75854 | 76015 | 75796
16875 | 2021-11-13 | 22:24 | 11.735 | 75855 | 76015 | 75797
16876 | 2021-11-13 | 22:24 | 11.735 | 75855 | 76015 | 75798
16877 | 2021-11-13 | 22:24 | 11.735 | 75855 | 76015 | 75799
16878 | 2021-11-13 | 22:24 | 11.735 | 75856 | 76014 | 75800
16879 | 2021-11-13 | 22:24 | 11.7351 | 75856 | 76014 | 75801
16880 | 2021-11-13 | 22:24 | 11.7351 | 75857 | 76014 | 75803
16881 | 2021-11-13 | 22:24 | 11.7351 | 75858 | 76014 | 75804
16882 | 2021-11-13 | 22:24 | 11.7352 | 75858 | 76014 | 75805
16883 | 2021-11-13 | 22:24 | 11.7352 | 75858 | 76014 | 75807
16884 | 2021-11-13 | 22:24 | 11.7352 | 75858 | 76014 | 75808
16885 | 2021-11-13 | 22:24 | 11.7352 | 75859 | 76014 | 75809
16886 | 2021-11-13 | 22:24 | 11.7353 | 75859 | 76013 | 75811
16887 | 2021-11-13 | 22:24 | 11.7353 | 75859 | 76013 | 75812
16888 | 2021-11-13 | 22:24 | 11.7353 | 75859 | 76013 | 75814
16889 | 2021-11-13 | 22:24 | 11.7354 | 75860 | 76013 | 75816
16890 | 2021-11-13 | 22:24 | 11.7354 | 75860 | 76013 | 75817
16891 | 2021-11-13 | 22:24 | 11.7354 | 75860 | 76013 | 75819
16892 | 2021-11-13 | 22:24 | 11.7354 | 75860 | 76013 | 75821
16893 | 2021-11-13 | 22:24 | 11.7355 | 75861 | 76013 | 75823
16894 | 2021-11-13 | 22:24 | 11.7355 | 75861 | 76013 | 75825
16895 | 2021-11-13 | 22:24 | 11.7355 | 75861 | 76014 | 75826
16896 | 2021-11-13 | 22:24 | 11.7356 | 75861 | 76014 | 75828
16897 | 2021-11-13 | 22:24 | 11.7356 | 75861 | 76014 | 75830
16898 | 2021-11-13 | 22:24 | 11.7356 | 75861 | 76014 | 75832
16899 | 2021-11-13 | 22:24 | 11.7356 | 75862 | 76014 | 75835
16900 | 2021-11-13 | 22:24 | 11.7357 | 75862 | 76015 | 75837
16901 | 2021-11-13 | 22:24 | 11.7357 | 75862 | 76015 | 75839
16902 | 2021-11-13 | 22:24 | 11.7357 | 75862 | 76015 | 75841
16903 | 2021-11-13 | 22:24 | 11.7358 | 75862 | 76015 | 75844
16904 | 2021-11-13 | 22:24 | 11.7358 | 75862 | 76016 | 75846
16905 | 2021-11-13 | 22:24 | 11.7358 | 75863 | 76016 | 75848
16906 | 2021-11-13 | 22:24 | 11.7358 | 75863 | 76017 | 75851
16907 | 2021-11-13 | 22:24 | 11.7359 | 75863 | 76017 | 75853
16908 | 2021-11-13 | 22:24 | 11.7359 | 75863 | 76017 | 75856
16909 | 2021-11-13 | 22:24 | 11.7359 | 75864 | 76018 | 75858
16910 | 2021-11-13 | 22:24 | 11.736 | 75864 | 76019 | 75861
16911 | 2021-11-13 | 22:24 | 11.736 | 75864 | 76019 | 75864
16912 | 2021-11-13 | 22:24 | 11.736 | 75864 | 76020 | 75867
16913 | 2021-11-13 | 22:24 | 11.736 | 75864 | 76020 | 75870
16914 | 2021-11-13 | 22:24 | 11.7361 | 75865 | 76021 | 75872
16915 | 2021-11-13 | 22:24 | 11.7361 | 75865 | 76022 | 75875
16916 | 2021-11-13 | 22:24 | 11.7361 | 75865 | 76022 | 75878
16917 | 2021-11-13 | 22:24 | 11.7362 | 75865 | 76023 | 75881
16918 | 2021-11-13 | 22:24 | 11.7362 | 75865 | 76024 | 75883
16919 | 2021-11-13 | 22:24 | 11.7362 | 75866 | 76024 | 75886
16920 | 2021-11-13 | 22:24 | 11.7362 | 75866 | 76025 | 75889
16921 | 2021-11-13 | 22:24 | 11.7363 | 75866 | 76026 | 75892
16922 | 2021-11-13 | 22:24 | 11.7363 | 75866 | 76027 | 75895
16923 | 2021-11-13 | 22:24 | 11.7363 | 75866 | 76028 | 75898
16924 | 2021-11-13 | 22:24 | 11.7364 | 75866 | 76029 | 75900
16925 | 2021-11-13 | 22:24 | 11.7364 | 75866 | 76030 | 75903
16926 | 2021-11-13 | 22:24 | 11.7364 | 75866 | 76030 | 75905
16927 | 2021-11-13 | 22:24 | 11.7364 | 75867 | 76031 | 75908
16928 | 2021-11-13 | 22:24 | 11.7365 | 75867 | 76032 | 75911
16929 | 2021-11-13 | 22:24 | 11.7365 | 75867 | 76033 | 75913
16930 | 2021-11-13 | 22:24 | 11.7365 | 75867 | 76035 | 75916
16931 | 2021-11-13 | 22:24 | 11.7366 | 75867 | 76036 | 75919
16932 | 2021-11-13 | 22:24 | 11.7366 | 75867 | 76037 | 75921
16933 | 2021-11-13 | 22:24 | 11.7366 | 75867 | 76038 | 75924
16934 | 2021-11-13 | 22:24 | 11.7366 | 75867 | 76040 | 75926
16935 | 2021-11-13 | 22:24 | 11.7367 | 75867 | 76041 | 75929
16936 | 2021-11-13 | 22:24 | 11.7367 | 75867 | 76042 | 75931
16937 | 2021-11-13 | 22:24 | 11.7367 | 75867 | 76043 | 75934
16938 | 2021-11-13 | 22:24 | 11.7368 | 75867 | 76045 | 75936
16939 | 2021-11-13 | 22:24 | 11.7368 | 75867 | 76046 | 75938
16940 | 2021-11-13 | 22:24 | 11.7368 | 75866 | 76047 | 75940
16941 | 2021-11-13 | 22:24 | 11.7368 | 75866 | 76049 | 75942
16942 | 2021-11-13 | 22:24 | 11.7369 | 75866 | 76050 | 75944
16943 | 2021-11-13 | 22:24 | 11.7369 | 75866 | 76051 | 75946
16944 | 2021-11-13 | 22:24 | 11.7369 | 75866 | 76053 | 75948
16945 | 2021-11-13 | 22:24 | 11.737 | 75866 | 76054 | 75950
16946 | 2021-11-13 | 22:24 | 11.737 | 75865 | 76056 | 75952
16947 | 2021-11-13 | 22:24 | 11.737 | 75865 | 76057 | 75953
16948 | 2021-11-13 | 22:24 | 11.737 | 75865 | 76059 | 75955
16949 | 2021-11-13 | 22:24 | 11.7371 | 75865 | 76060 | 75957
16950 | 2021-11-13 | 22:24 | 11.7371 | 75864 | 76062 | 75958
16951 | 2021-11-13 | 22:24 | 11.7371 | 75864 | 76064 | 75960
16952 | 2021-11-13 | 22:24 | 11.7372 | 75864 | 76065 | 75961
16953 | 2021-11-13 | 22:24 | 11.7372 | 75863 | 76067 | 75963
16954 | 2021-11-13 | 22:24 | 11.7372 | 75863 | 76069 | 75964
16955 | 2021-11-13 | 22:24 | 11.7373 | 75863 | 76071 | 75966
16956 | 2021-11-13 | 22:24 | 11.7373 | 75862 | 76072 | 75967
16957 | 2021-11-13 | 22:24 | 11.7373 | 75862 | 76074 | 75968
16958 | 2021-11-13 | 22:24 | 11.7373 | 75862 | 76076 | 75969
16959 | 2021-11-13 | 22:24 | 11.7374 | 75861 | 76077 | 75970
16960 | 2021-11-13 | 22:24 | 11.7374 | 75861 | 76079 | 75971
16961 | 2021-11-13 | 22:24 | 11.7374 | 75861 | 76081 | 75972
16962 | 2021-11-13 | 22:24 | 11.7375 | 75860 | 76083 | 75973
16963 | 2021-11-13 | 22:24 | 11.7375 | 75860 | 76085 | 75974
16964 | 2021-11-13 | 22:24 | 11.7375 | 75860 | 76087 | 75975
16965 | 2021-11-13 | 22:24 | 11.7375 | 75859 | 76089 | 75975
16966 | 2021-11-13 | 22:24 | 11.7376 | 75859 | 76091 | 75976
16967 | 2021-11-13 | 22:24 | 11.7376 | 75859 | 76093 | 75976
16968 | 2021-11-13 | 22:24 | 11.7376 | 75859 | 76095 | 75977
16969 | 2021-11-13 | 22:24 | 11.7377 | 75859 | 76097 | 75977
16970 | 2021-11-13 | 22:24 | 11.7377 | 75858 | 76099 | 75978
16971 | 2021-11-13 | 22:24 | 11.7377 | 75858 | 76101 | 75978
16972 | 2021-11-13 | 22:24 | 11.7377 | 75858 | 76104 | 75978
16973 | 2021-11-13 | 22:24 | 11.7378 | 75858 | 76106 | 75979
16974 | 2021-11-13 | 22:24 | 11.7378 | 75858 | 76108 | 75979
16975 | 2021-11-13 | 22:24 | 11.7378 | 75858 | 76110 | 75979
16976 | 2021-11-13 | 22:24 | 11.7379 | 75858 | 76113 | 75980
16977 | 2021-11-13 | 22:24 | 11.7379 | 75858 | 76115 | 75980
16978 | 2021-11-13 | 22:24 | 11.7379 | 75858 | 76118 | 75980
16979 | 2021-11-13 | 22:24 | 11.7379 | 75858 | 76120 | 75980
16980 | 2021-11-13 | 22:24 | 11.738 | 75858 | 76123 | 75981
16981 | 2021-11-13 | 22:24 | 11.738 | 75859 | 76125 | 75981
16982 | 2021-11-13 | 22:24 | 11.738 | 75859 | 76128 | 75982
16983 | 2021-11-13 | 22:24 | 11.7381 | 75859 | 76131 | 75982
16984 | 2021-11-13 | 22:24 | 11.7381 | 75859 | 76133 | 75982
16985 | 2021-11-13 | 22:24 | 11.7381 | 75860 | 76136 | 75982
16986 | 2021-11-13 | 22:24 | 11.7381 | 75860 | 76139 | 75983
16987 | 2021-11-13 | 22:24 | 11.7382 | 75860 | 76142 | 75983
16988 | 2021-11-13 | 22:24 | 11.7382 | 75861 | 76144 | 75983
16989 | 2021-11-13 | 22:24 | 11.7382 | 75861 | 76147 | 75983
16990 | 2021-11-13 | 22:24 | 11.7383 | 75862 | 76150 | 75983
16991 | 2021-11-13 | 22:24 | 11.7383 | 75862 | 76153 | 75984
16992 | 2021-11-13 | 22:24 | 11.7383 | 75863 | 76156 | 75984
16993 | 2021-11-13 | 22:24 | 11.7383 | 75863 | 76159 | 75984
16994 | 2021-11-13 | 22:24 | 11.7384 | 75864 | 76162 | 75984
16995 | 2021-11-13 | 22:24 | 11.7384 | 75864 | 76165 | 75985
16996 | 2021-11-13 | 22:24 | 11.7384 | 75865 | 76168 | 75985
16997 | 2021-11-13 | 22:24 | 11.7385 | 75866 | 76171 | 75985
16998 | 2021-11-13 | 22:24 | 11.7385 | 75866 | 76175 | 75986
16999 | 2021-11-13 | 22:24 | 11.7385 | 75867 | 76178 | 75986
17000 | 2021-11-13 | 22:24 | 11.7385 | 75868 | 76181 | 75986
17001 | 2021-11-13 | 22:24 | 11.7386 | 75869 | 76184 | 75986
17002 | 2021-11-13 | 22:24 | 11.7386 | 75870 | 76187 | 75987
17003 | 2021-11-13 | 22:24 | 11.7386 | 75871 | 76190 | 75987
17004 | 2021-11-13 | 22:24 | 11.7387 | 75871 | 76193 | 75987
17005 | 2021-11-13 | 22:24 | 11.7387 | 75872 | 76195 | 75987
17006 | 2021-11-13 | 22:24 | 11.7387 | 75873 | 76198 | 75987
17007 | 2021-11-13 | 22:24 | 11.7387 | 75874 | 76201 | 75987
17008 | 2021-11-13 | 22:24 | 11.7388 | 75875 | 76203 | 75987
17009 | 2021-11-13 | 22:24 | 11.7388 | 75876 | 76206 | 75987
17010 | 2021-11-13 | 22:24 | 11.7388 | 75877 | 76208 | 75987
17011 | 2021-11-13 | 22:24 | 11.7389 | 75878 | 76210 | 75987
17012 | 2021-11-13 | 22:24 | 11.7389 | 75879 | 76213 | 75987
17013 | 2021-11-13 | 22:24 | 11.7389 | 75880 | 76215 | 75987
17014 | 2021-11-13 | 22:24 | 11.7389 | 75881 | 76217 | 75987
17015 | 2021-11-13 | 22:24 | 11.739 | 75882 | 76219 | 75987
17016 | 2021-11-13 | 22:24 | 11.739 | 75883 | 76222 | 75987
17017 | 2021-11-13 | 22:24 | 11.739 | 75884 | 76224 | 75987
17018 | 2021-11-13 | 22:24 | 11.7391 | 75885 | 76226 | 75987
17019 | 2021-11-13 | 22:24 | 11.7391 | 75887 | 76228 | 75987
17020 | 2021-11-13 | 22:24 | 11.7391 | 75888 | 76230 | 75987
17021 | 2021-11-13 | 22:24 | 11.7391 | 75889 | 76231 | 75987
17022 | 2021-11-13 | 22:24 | 11.7392 | 75891 | 76233 | 75987
17023 | 2021-11-13 | 22:24 | 11.7392 | 75892 | 76235 | 75986
17024 | 2021-11-13 | 22:24 | 11.7392 | 75893 | 76237 | 75986
17025 | 2021-11-13 | 22:24 | 11.7393 | 75895 | 76239 | 75986
17026 | 2021-11-13 | 22:24 | 11.7393 | 75896 | 76240 | 75986
17027 | 2021-11-13 | 22:24 | 11.7393 | 75897 | 76242 | 75986
17028 | 2021-11-13 | 22:24 | 11.7393 | 75899 | 76244 | 75985
17029 | 2021-11-13 | 22:24 | 11.7394 | 75900 | 76245 | 75985
17030 | 2021-11-13 | 22:24 | 11.7394 | 75901 | 76247 | 75985
17031 | 2021-11-13 | 22:24 | 11.7394 | 75903 | 76249 | 75985
17032 | 2021-11-13 | 22:24 | 11.7395 | 75904 | 76250 | 75984
17033 | 2021-11-13 | 22:24 | 11.7395 | 75905 | 76251 | 75984
17034 | 2021-11-13 | 22:24 | 11.7395 | 75907 | 76253 | 75984
17035 | 2021-11-13 | 22:24 | 11.7395 | 75908 | 76255 | 75983
17036 | 2021-11-13 | 22:24 | 11.7396 | 75909 | 76256 | 75983
17037 | 2021-11-13 | 22:24 | 11.7396 | 75911 | 76258 | 75983
17038 | 2021-11-13 | 22:24 | 11.7396 | 75913 | 76260 | 75982
17039 | 2021-11-13 | 22:24 | 11.7397 | 75914 | 76261 | 75982
17040 | 2021-11-13 | 22:24 | 11.7397 | 75916 | 76263 | 75981
17041 | 2021-11-13 | 22:24 | 11.7397 | 75917 | 76264 | 75981
17042 | 2021-11-13 | 22:24 | 11.7397 | 75919 | 76265 | 75981
17043 | 2021-11-13 | 22:24 | 11.7398 | 75921 | 76266 | 75981
17044 | 2021-11-13 | 22:24 | 11.7398 | 75922 | 76267 | 75980
17045 | 2021-11-13 | 22:24 | 11.7398 | 75924 | 76268 | 75980
17046 | 2021-11-13 | 22:24 | 11.7399 | 75925 | 76269 | 75980
17047 | 2021-11-13 | 22:24 | 11.7399 | 75927 | 76270 | 75980
17048 | 2021-11-13 | 22:24 | 11.7399 | 75929 | 76271 | 75979
17049 | 2021-11-13 | 22:24 | 11.74 | 75931 | 76271 | 75979
17050 | 2021-11-13 | 22:24 | 11.74 | 75932 | 76272 | 75979
17051 | 2021-11-13 | 22:24 | 11.74 | 75934 | 76272 | 75979
17052 | 2021-11-13 | 22:24 | 11.74 | 75936 | 76273 | 75978
17053 | 2021-11-13 | 22:24 | 11.7401 | 75938 | 76273 | 75978
17054 | 2021-11-13 | 22:24 | 11.7401 | 75940 | 76273 | 75978
17055 | 2021-11-13 | 22:24 | 11.7401 | 75941 | 76274 | 75978
17056 | 2021-11-13 | 22:24 | 11.7402 | 75943 | 76274 | 75978
17057 | 2021-11-13 | 22:24 | 11.7402 | 75945 | 76274 | 75978
17058 | 2021-11-13 | 22:24 | 11.7402 | 75947 | 76275 | 75978
17059 | 2021-11-13 | 22:24 | 11.7402 | 75949 | 76275 | 75978
17060 | 2021-11-13 | 22:24 | 11.7403 | 75951 | 76275 | 75977
17061 | 2021-11-13 | 22:24 | 11.7403 | 75953 | 76275 | 75977
17062 | 2021-11-13 | 22:24 | 11.7403 | 75955 | 76275 | 75977
17063 | 2021-11-13 | 22:24 | 11.7404 | 75957 | 76275 | 75978
17064 | 2021-11-13 | 22:24 | 11.7404 | 75959 | 76275 | 75978
17065 | 2021-11-13 | 22:24 | 11.7404 | 75962 | 76275 | 75978
17066 | 2021-11-13 | 22:24 | 11.7404 | 75964 | 76275 | 75978
17067 | 2021-11-13 | 22:24 | 11.7405 | 75966 | 76274 | 75978
17068 | 2021-11-13 | 22:24 | 11.7405 | 75968 | 76274 | 75978
17069 | 2021-11-13 | 22:24 | 11.7405 | 75971 | 76274 | 75978
17070 | 2021-11-13 | 22:24 | 11.7406 | 75973 | 76274 | 75979
17071 | 2021-11-13 | 22:24 | 11.7406 | 75976 | 76274 | 75979
17072 | 2021-11-13 | 22:24 | 11.7406 | 75978 | 76274 | 75979
17073 | 2021-11-13 | 22:24 | 11.7406 | 75980 | 76274 | 75980
17074 | 2021-11-13 | 22:24 | 11.7407 | 75982 | 76273 | 75980
17075 | 2021-11-13 | 22:24 | 11.7407 | 75985 | 76273 | 75980
17076 | 2021-11-13 | 22:24 | 11.7407 | 75987 | 76273 | 75981
17077 | 2021-11-13 | 22:24 | 11.7408 | 75989 | 76273 | 75981
17078 | 2021-11-13 | 22:24 | 11.7408 | 75992 | 76272 | 75982
17079 | 2021-11-13 | 22:24 | 11.7408 | 75994 | 76272 | 75982
17080 | 2021-11-13 | 22:24 | 11.7408 | 75997 | 76272 | 75983
17081 | 2021-11-13 | 22:24 | 11.7409 | 75999 | 76272 | 75984
17082 | 2021-11-13 | 22:24 | 11.7409 | 76002 | 76272 | 75985
17083 | 2021-11-13 | 22:24 | 11.7409 | 76005 | 76271 | 75985
17084 | 2021-11-13 | 22:24 | 11.741 | 76007 | 76271 | 75986
17085 | 2021-11-13 | 22:24 | 11.741 | 76009 | 76271 | 75987
17086 | 2021-11-13 | 22:24 | 11.741 | 76012 | 76271 | 75988
17087 | 2021-11-13 | 22:24 | 11.741 | 76014 | 76270 | 75989
17088 | 2021-11-13 | 22:24 | 11.7411 | 76017 | 76270 | 75989
17089 | 2021-11-13 | 22:24 | 11.7411 | 76019 | 76270 | 75990
17090 | 2021-11-13 | 22:24 | 11.7411 | 76022 | 76269 | 75991
17091 | 2021-11-13 | 22:24 | 11.7412 | 76024 | 76269 | 75992
17092 | 2021-11-13 | 22:24 | 11.7412 | 76026 | 76269 | 75994
17093 | 2021-11-13 | 22:24 | 11.7412 | 76028 | 76268 | 75995
17094 | 2021-11-13 | 22:24 | 11.7412 | 76031 | 76267 | 75996
17095 | 2021-11-13 | 22:24 | 11.7413 | 76033 | 76267 | 75997
17096 | 2021-11-13 | 22:24 | 11.7413 | 76035 | 76267 | 75998
17097 | 2021-11-13 | 22:24 | 11.7413 | 76037 | 76266 | 75999
17098 | 2021-11-13 | 22:24 | 11.7414 | 76039 | 76266 | 76001
17099 | 2021-11-13 | 22:24 | 11.7414 | 76041 | 76265 | 76002
17100 | 2021-11-13 | 22:24 | 11.7414 | 76043 | 76265 | 76003
17101 | 2021-11-13 | 22:24 | 11.7414 | 76045 | 76264 | 76005
17102 | 2021-11-13 | 22:24 | 11.7415 | 76047 | 76264 | 76006
17103 | 2021-11-13 | 22:24 | 11.7415 | 76049 | 76263 | 76008
17104 | 2021-11-13 | 22:24 | 11.7415 | 76051 | 76262 | 76009
17105 | 2021-11-13 | 22:24 | 11.7416 | 76052 | 76262 | 76011
17106 | 2021-11-13 | 22:24 | 11.7416 | 76054 | 76261 | 76012
17107 | 2021-11-13 | 22:24 | 11.7416 | 76055 | 76260 | 76013
17108 | 2021-11-13 | 22:24 | 11.7416 | 76057 | 76259 | 76015
17109 | 2021-11-13 | 22:24 | 11.7417 | 76058 | 76259 | 76016
17110 | 2021-11-13 | 22:24 | 11.7417 | 76060 | 76258 | 76018
17111 | 2021-11-13 | 22:24 | 11.7417 | 76061 | 76257 | 76020
17112 | 2021-11-13 | 22:24 | 11.7418 | 76062 | 76257 | 76021
17113 | 2021-11-13 | 22:24 | 11.7418 | 76064 | 76256 | 76023
17114 | 2021-11-13 | 22:24 | 11.7418 | 76065 | 76255 | 76025
17115 | 2021-11-13 | 22:24 | 11.7418 | 76066 | 76254 | 76026
17116 | 2021-11-13 | 22:24 | 11.7419 | 76067 | 76254 | 76028
17117 | 2021-11-13 | 22:24 | 11.7419 | 76067 | 76253 | 76030
17118 | 2021-11-13 | 22:24 | 11.7419 | 76068 | 76252 | 76031
17119 | 2021-11-13 | 22:24 | 11.742 | 76069 | 76252 | 76033
17120 | 2021-11-13 | 22:24 | 11.742 | 76070 | 76251 | 76035
17121 | 2021-11-13 | 22:24 | 11.742 | 76070 | 76250 | 76037
17122 | 2021-11-13 | 22:24 | 11.742 | 76071 | 76249 | 76039
17123 | 2021-11-13 | 22:24 | 11.7421 | 76072 | 76249 | 76041
17124 | 2021-11-13 | 22:24 | 11.7421 | 76072 | 76248 | 76043
17125 | 2021-11-13 | 22:24 | 11.7421 | 76073 | 76248 | 76045
17126 | 2021-11-13 | 22:24 | 11.7422 | 76073 | 76247 | 76047
17127 | 2021-11-13 | 22:24 | 11.7422 | 76074 | 76246 | 76049
17128 | 2021-11-13 | 22:24 | 11.7422 | 76074 | 76246 | 76052
17129 | 2021-11-13 | 22:24 | 11.7422 | 76075 | 76245 | 76054
17130 | 2021-11-13 | 22:24 | 11.7423 | 76075 | 76245 | 76056
17131 | 2021-11-13 | 22:24 | 11.7423 | 76076 | 76244 | 76058
17132 | 2021-11-13 | 22:24 | 11.7423 | 76076 | 76244 | 76061
17133 | 2021-11-13 | 22:24 | 11.7424 | 76077 | 76243 | 76063
17134 | 2021-11-13 | 22:24 | 11.7424 | 76077 | 76243 | 76065
17135 | 2021-11-13 | 22:24 | 11.7424 | 76077 | 76242 | 76068
17136 | 2021-11-13 | 22:24 | 11.7424 | 76077 | 76242 | 76070
17137 | 2021-11-13 | 22:24 | 11.7425 | 76077 | 76242 | 76072
17138 | 2021-11-13 | 22:24 | 11.7425 | 76077 | 76241 | 76075
17139 | 2021-11-13 | 22:24 | 11.7425 | 76077 | 76241 | 76077
17140 | 2021-11-13 | 22:24 | 11.7426 | 76078 | 76241 | 76079
17141 | 2021-11-13 | 22:24 | 11.7426 | 76078 | 76241 | 76082
17142 | 2021-11-13 | 22:24 | 11.7426 | 76078 | 76240 | 76084
17143 | 2021-11-13 | 22:24 | 11.7427 | 76078 | 76240 | 76087
17144 | 2021-11-13 | 22:24 | 11.7427 | 76078 | 76240 | 76090
17145 | 2021-11-13 | 22:24 | 11.7427 | 76078 | 76240 | 76093
17146 | 2021-11-13 | 22:24 | 11.7427 | 76077 | 76240 | 76095
17147 | 2021-11-13 | 22:24 | 11.7428 | 76077 | 76240 | 76098
17148 | 2021-11-13 | 22:24 | 11.7428 | 76077 | 76240 | 76101
17149 | 2021-11-13 | 22:24 | 11.7428 | 76076 | 76240 | 76103
17150 | 2021-11-13 | 22:24 | 11.7429 | 76076 | 76241 | 76106
17151 | 2021-11-13 | 22:24 | 11.7429 | 76076 | 76241 | 76109
17152 | 2021-11-13 | 22:24 | 11.7429 | 76075 | 76241 | 76111
17153 | 2021-11-13 | 22:24 | 11.7429 | 76074 | 76241 | 76114
17154 | 2021-11-13 | 22:24 | 11.743 | 76074 | 76242 | 76117
17155 | 2021-11-13 | 22:24 | 11.743 | 76073 | 76242 | 76120
17156 | 2021-11-13 | 22:24 | 11.743 | 76072 | 76243 | 76122
17157 | 2021-11-13 | 22:24 | 11.7431 | 76071 | 76243 | 76125
17158 | 2021-11-13 | 22:24 | 11.7431 | 76071 | 76244 | 76127
17159 | 2021-11-13 | 22:24 | 11.7431 | 76070 | 76244 | 76130
17160 | 2021-11-13 | 22:24 | 11.7431 | 76069 | 76245 | 76132
17161 | 2021-11-13 | 22:24 | 11.7432 | 76068 | 76246 | 76134
17162 | 2021-11-13 | 22:24 | 11.7432 | 76068 | 76246 | 76137
17163 | 2021-11-13 | 22:24 | 11.7432 | 76067 | 76247 | 76139
17164 | 2021-11-13 | 22:24 | 11.7433 | 76066 | 76248 | 76142
17165 | 2021-11-13 | 22:24 | 11.7433 | 76065 | 76249 | 76144
17166 | 2021-11-13 | 22:24 | 11.7433 | 76064 | 76249 | 76146
17167 | 2021-11-13 | 22:24 | 11.7433 | 76063 | 76250 | 76149
17168 | 2021-11-13 | 22:24 | 11.7434 | 76062 | 76251 | 76151
17169 | 2021-11-13 | 22:24 | 11.7434 | 76061 | 76252 | 76153
17170 | 2021-11-13 | 22:24 | 11.7434 | 76060 | 76253 | 76155
17171 | 2021-11-13 | 22:24 | 11.7435 | 76059 | 76254 | 76157
17172 | 2021-11-13 | 22:24 | 11.7435 | 76058 | 76255 | 76159
17173 | 2021-11-13 | 22:24 | 11.7435 | 76057 | 76256 | 76161
17174 | 2021-11-13 | 22:24 | 11.7435 | 76056 | 76257 | 76162
17175 | 2021-11-13 | 22:24 | 11.7436 | 76054 | 76258 | 76164
17176 | 2021-11-13 | 22:24 | 11.7436 | 76053 | 76259 | 76166
17177 | 2021-11-13 | 22:24 | 11.7436 | 76052 | 76260 | 76168
17178 | 2021-11-13 | 22:24 | 11.7437 | 76051 | 76261 | 76169
17179 | 2021-11-13 | 22:24 | 11.7437 | 76050 | 76262 | 76171
17180 | 2021-11-13 | 22:24 | 11.7437 | 76048 | 76263 | 76172
17181 | 2021-11-13 | 22:24 | 11.7437 | 76047 | 76264 | 76173
17182 | 2021-11-13 | 22:24 | 11.7438 | 76046 | 76265 | 76174
17183 | 2021-11-13 | 22:24 | 11.7438 | 76045 | 76267 | 76175
17184 | 2021-11-13 | 22:24 | 11.7438 | 76043 | 76268 | 76177
17185 | 2021-11-13 | 22:24 | 11.7439 | 76042 | 76269 | 76177
17186 | 2021-11-13 | 22:24 | 11.7439 | 76041 | 76271 | 76178
17187 | 2021-11-13 | 22:24 | 11.7439 | 76040 | 76272 | 76180
17188 | 2021-11-13 | 22:24 | 11.7439 | 76038 | 76273 | 76180
17189 | 2021-11-13 | 22:24 | 11.744 | 76037 | 76275 | 76181
17190 | 2021-11-13 | 22:24 | 11.744 | 76036 | 76276 | 76182
17191 | 2021-11-13 | 22:24 | 11.744 | 76034 | 76278 | 76182
17192 | 2021-11-13 | 22:24 | 11.7441 | 76033 | 76279 | 76183
17193 | 2021-11-13 | 22:24 | 11.7441 | 76032 | 76281 | 76184
17194 | 2021-11-13 | 22:24 | 11.7441 | 76031 | 76283 | 76184
17195 | 2021-11-13 | 22:24 | 11.7441 | 76029 | 76284 | 76185
17196 | 2021-11-13 | 22:24 | 11.7442 | 76028 | 76286 | 76185
17197 | 2021-11-13 | 22:24 | 11.7442 | 76027 | 76288 | 76186
17198 | 2021-11-13 | 22:24 | 11.7442 | 76026 | 76289 | 76186
17199 | 2021-11-13 | 22:24 | 11.7443 | 76025 | 76291 | 76186
17200 | 2021-11-13 | 22:24 | 11.7443 | 76024 | 76293 | 76186
17201 | 2021-11-13 | 22:24 | 11.7443 | 76023 | 76295 | 76186
17202 | 2021-11-13 | 22:24 | 11.7443 | 76022 | 76297 | 76186
17203 | 2021-11-13 | 22:24 | 11.7444 | 76021 | 76299 | 76187
17204 | 2021-11-13 | 22:24 | 11.7444 | 76020 | 76301 | 76187
17205 | 2021-11-13 | 22:24 | 11.7444 | 76019 | 76303 | 76187
17206 | 2021-11-13 | 22:24 | 11.7445 | 76018 | 76305 | 76187
17207 | 2021-11-13 | 22:24 | 11.7445 | 76017 | 76307 | 76188
17208 | 2021-11-13 | 22:24 | 11.7445 | 76016 | 76309 | 76188
17209 | 2021-11-13 | 22:24 | 11.7445 | 76015 | 76311 | 76188
17210 | 2021-11-13 | 22:24 | 11.7446 | 76015 | 76313 | 76188
17211 | 2021-11-13 | 22:24 | 11.7446 | 76014 | 76315 | 76189
17212 | 2021-11-13 | 22:24 | 11.7446 | 76013 | 76317 | 76189
17213 | 2021-11-13 | 22:24 | 11.7447 | 76013 | 76319 | 76189
17214 | 2021-11-13 | 22:24 | 11.7447 | 76012 | 76321 | 76189
17215 | 2021-11-13 | 22:24 | 11.7447 | 76011 | 76323 | 76189
17216 | 2021-11-13 | 22:24 | 11.7447 | 76011 | 76325 | 76189
17217 | 2021-11-13 | 22:24 | 11.7448 | 76010 | 76328 | 76189
17218 | 2021-11-13 | 22:24 | 11.7448 | 76010 | 76330 | 76189
17219 | 2021-11-13 | 22:24 | 11.7448 | 76009 | 76332 | 76190
17220 | 2021-11-13 | 22:24 | 11.7449 | 76009 | 76334 | 76190
17221 | 2021-11-13 | 22:24 | 11.7449 | 76008 | 76336 | 76189
17222 | 2021-11-13 | 22:24 | 11.7449 | 76008 | 76338 | 76189
17223 | 2021-11-13 | 22:24 | 11.7449 | 76008 | 76340 | 76189
17224 | 2021-11-13 | 22:24 | 11.745 | 76007 | 76342 | 76189
17225 | 2021-11-13 | 22:24 | 11.745 | 76007 | 76344 | 76189
17226 | 2021-11-13 | 22:24 | 11.745 | 76007 | 76347 | 76189
17227 | 2021-11-13 | 22:24 | 11.7451 | 76007 | 76349 | 76188
17228 | 2021-11-13 | 22:24 | 11.7451 | 76007 | 76351 | 76188
17229 | 2021-11-13 | 22:24 | 11.7451 | 76007 | 76353 | 76188
17230 | 2021-11-13 | 22:24 | 11.7451 | 76007 | 76355 | 76188
17231 | 2021-11-13 | 22:24 | 11.7452 | 76007 | 76358 | 76187
17232 | 2021-11-13 | 22:24 | 11.7452 | 76007 | 76360 | 76187
17233 | 2021-11-13 | 22:24 | 11.7452 | 76007 | 76362 | 76187
17234 | 2021-11-13 | 22:24 | 11.7453 | 76007 | 76364 | 76187
17235 | 2021-11-13 | 22:24 | 11.7453 | 76007 | 76367 | 76186
17236 | 2021-11-13 | 22:24 | 11.7453 | 76007 | 76369 | 76186
17237 | 2021-11-13 | 22:24 | 11.7454 | 76007 | 76372 | 76185
17238 | 2021-11-13 | 22:24 | 11.7454 | 76007 | 76374 | 76185
17239 | 2021-11-13 | 22:24 | 11.7454 | 76008 | 76376 | 76185
17240 | 2021-11-13 | 22:24 | 11.7454 | 76008 | 76378 | 76184
17241 | 2021-11-13 | 22:24 | 11.7455 | 76008 | 76380 | 76184
17242 | 2021-11-13 | 22:24 | 11.7455 | 76009 | 76382 | 76183
17243 | 2021-11-13 | 22:24 | 11.7455 | 76009 | 76384 | 76183
17244 | 2021-11-13 | 22:24 | 11.7456 | 76009 | 76386 | 76182
17245 | 2021-11-13 | 22:24 | 11.7456 | 76010 | 76388 | 76182
17246 | 2021-11-13 | 22:24 | 11.7456 | 76010 | 76390 | 76181
17247 | 2021-11-13 | 22:24 | 11.7456 | 76011 | 76392 | 76180
17248 | 2021-11-13 | 22:24 | 11.7457 | 76012 | 76394 | 76180
17249 | 2021-11-13 | 22:24 | 11.7457 | 76012 | 76396 | 76179
17250 | 2021-11-13 | 22:24 | 11.7457 | 76013 | 76398 | 76178
17251 | 2021-11-13 | 22:24 | 11.7458 | 76014 | 76400 | 76177
17252 | 2021-11-13 | 22:24 | 11.7458 | 76014 | 76402 | 76177
17253 | 2021-11-13 | 22:24 | 11.7458 | 76015 | 76404 | 76176
17254 | 2021-11-13 | 22:24 | 11.7458 | 76016 | 76406 | 76175
17255 | 2021-11-13 | 22:24 | 11.7459 | 76017 | 76407 | 76174
17256 | 2021-11-13 | 22:24 | 11.7459 | 76018 | 76409 | 76173
17257 | 2021-11-13 | 22:24 | 11.7459 | 76018 | 76411 | 76172
17258 | 2021-11-13 | 22:24 | 11.746 | 76019 | 76412 | 76171
17259 | 2021-11-13 | 22:24 | 11.746 | 76020 | 76414 | 76170
17260 | 2021-11-13 | 22:24 | 11.746 | 76021 | 76415 | 76169
17261 | 2021-11-13 | 22:24 | 11.746 | 76022 | 76416 | 76168
17262 | 2021-11-13 | 22:24 | 11.7461 | 76023 | 76417 | 76167
17263 | 2021-11-13 | 22:24 | 11.7461 | 76024 | 76418 | 76166
17264 | 2021-11-13 | 22:24 | 11.7461 | 76026 | 76419 | 76164
17265 | 2021-11-13 | 22:24 | 11.7462 | 76027 | 76420 | 76163
17266 | 2021-11-13 | 22:24 | 11.7462 | 76028 | 76421 | 76162
17267 | 2021-11-13 | 22:24 | 11.7462 | 76029 | 76422 | 76161
17268 | 2021-11-13 | 22:24 | 11.7462 | 76030 | 76423 | 76159
17269 | 2021-11-13 | 22:24 | 11.7463 | 76032 | 76424 | 76158
17270 | 2021-11-13 | 22:24 | 11.7463 | 76033 | 76425 | 76157
17271 | 2021-11-13 | 22:24 | 11.7463 | 76034 | 76426 | 76155
17272 | 2021-11-13 | 22:24 | 11.7464 | 76036 | 76427 | 76154
17273 | 2021-11-13 | 22:24 | 11.7464 | 76037 | 76428 | 76153
17274 | 2021-11-13 | 22:24 | 11.7464 | 76039 | 76429 | 76151
17275 | 2021-11-13 | 22:24 | 11.7464 | 76040 | 76429 | 76150
17276 | 2021-11-13 | 22:24 | 11.7465 | 76042 | 76430 | 76148
17277 | 2021-11-13 | 22:24 | 11.7465 | 76043 | 76431 | 76147
17278 | 2021-11-13 | 22:24 | 11.7465 | 76045 | 76431 | 76146
17279 | 2021-11-13 | 22:24 | 11.7466 | 76047 | 76432 | 76144
17280 | 2021-11-13 | 22:24 | 11.7466 | 76048 | 76432 | 76143
17281 | 2021-11-13 | 22:24 | 11.7466 | 76050 | 76432 | 76142
17282 | 2021-11-13 | 22:24 | 11.7466 | 76052 | 76433 | 76141
17283 | 2021-11-13 | 22:24 | 11.7467 | 76054 | 76433 | 76139
17284 | 2021-11-13 | 22:24 | 11.7467 | 76055 | 76433 | 76138
17285 | 2021-11-13 | 22:24 | 11.7467 | 76057 | 76433 | 76137
17286 | 2021-11-13 | 22:24 | 11.7468 | 76059 | 76433 | 76136
17287 | 2021-11-13 | 22:24 | 11.7468 | 76060 | 76433 | 76135
17288 | 2021-11-13 | 22:24 | 11.7468 | 76062 | 76433 | 76134
17289 | 2021-11-13 | 22:24 | 11.7468 | 76064 | 76433 | 76132
17290 | 2021-11-13 | 22:24 | 11.7469 | 76066 | 76433 | 76131
17291 | 2021-11-13 | 22:24 | 11.7469 | 76068 | 76433 | 76130
17292 | 2021-11-13 | 22:24 | 11.7469 | 76070 | 76433 | 76129
17293 | 2021-11-13 | 22:24 | 11.747 | 76072 | 76433 | 76128
17294 | 2021-11-13 | 22:24 | 11.747 | 76074 | 76433 | 76127
17295 | 2021-11-13 | 22:24 | 11.747 | 76076 | 76432 | 76126
17296 | 2021-11-13 | 22:24 | 11.747 | 76078 | 76432 | 76125
17297 | 2021-11-13 | 22:24 | 11.7471 | 76079 | 76431 | 76124
17298 | 2021-11-13 | 22:24 | 11.7471 | 76081 | 76431 | 76124
17299 | 2021-11-13 | 22:24 | 11.7471 | 76083 | 76430 | 76123
17300 | 2021-11-13 | 22:24 | 11.7472 | 76085 | 76429 | 76122
17301 | 2021-11-13 | 22:24 | 11.7472 | 76087 | 76428 | 76121
17302 | 2021-11-13 | 22:24 | 11.7472 | 76089 | 76427 | 76121
17303 | 2021-11-13 | 22:24 | 11.7472 | 76091 | 76426 | 76120
17304 | 2021-11-13 | 22:24 | 11.7473 | 76093 | 76424 | 76120
17305 | 2021-11-13 | 22:24 | 11.7473 | 76095 | 76423 | 76119
17306 | 2021-11-13 | 22:24 | 11.7473 | 76096 | 76422 | 76119
17307 | 2021-11-13 | 22:24 | 11.7474 | 76098 | 76420 | 76118
17308 | 2021-11-13 | 22:24 | 11.7474 | 76100 | 76418 | 76118
17309 | 2021-11-13 | 22:24 | 11.7474 | 76102 | 76417 | 76117
17310 | 2021-11-13 | 22:24 | 11.7474 | 76103 | 76415 | 76117
17311 | 2021-11-13 | 22:24 | 11.7475 | 76105 | 76414 | 76117
17312 | 2021-11-13 | 22:24 | 11.7475 | 76107 | 76412 | 76117
17313 | 2021-11-13 | 22:24 | 11.7475 | 76108 | 76410 | 76116
17314 | 2021-11-13 | 22:24 | 11.7476 | 76110 | 76409 | 76116
17315 | 2021-11-13 | 22:24 | 11.7476 | 76112 | 76407 | 76116
17316 | 2021-11-13 | 22:24 | 11.7476 | 76113 | 76405 | 76116
17317 | 2021-11-13 | 22:24 | 11.7476 | 76115 | 76404 | 76116
17318 | 2021-11-13 | 22:24 | 11.7477 | 76117 | 76402 | 76116
17319 | 2021-11-13 | 22:24 | 11.7477 | 76118 | 76401 | 76116
17320 | 2021-11-13 | 22:24 | 11.7477 | 76120 | 76400 | 76116
17321 | 2021-11-13 | 22:24 | 11.7478 | 76121 | 76398 | 76117
17322 | 2021-11-13 | 22:24 | 11.7478 | 76123 | 76397 | 76117
17323 | 2021-11-13 | 22:24 | 11.7478 | 76124 | 76396 | 76117
17324 | 2021-11-13 | 22:24 | 11.7478 | 76126 | 76394 | 76117
17325 | 2021-11-13 | 22:24 | 11.7479 | 76127 | 76393 | 76118
17326 | 2021-11-13 | 22:24 | 11.7479 | 76128 | 76392 | 76118
17327 | 2021-11-13 | 22:24 | 11.7479 | 76130 | 76391 | 76118
17328 | 2021-11-13 | 22:24 | 11.748 | 76131 | 76390 | 76119
17329 | 2021-11-13 | 22:24 | 11.748 | 76132 | 76388 | 76119
17330 | 2021-11-13 | 22:24 | 11.748 | 76133 | 76387 | 76120
17331 | 2021-11-13 | 22:24 | 11.7481 | 76134 | 76386 | 76120
17332 | 2021-11-13 | 22:24 | 11.7481 | 76136 | 76385 | 76121
17333 | 2021-11-13 | 22:24 | 11.7481 | 76137 | 76383 | 76122
17334 | 2021-11-13 | 22:24 | 11.7481 | 76138 | 76382 | 76122
17335 | 2021-11-13 | 22:24 | 11.7482 | 76139 | 76381 | 76123
17336 | 2021-11-13 | 22:24 | 11.7482 | 76140 | 76379 | 76124
17337 | 2021-11-13 | 22:24 | 11.7482 | 76141 | 76378 | 76125
17338 | 2021-11-13 | 22:24 | 11.7483 | 76142 | 76377 | 76125
17339 | 2021-11-13 | 22:24 | 11.7483 | 76143 | 76375 | 76126
17340 | 2021-11-13 | 22:24 | 11.7483 | 76144 | 76374 | 76127
17341 | 2021-11-13 | 22:24 | 11.7483 | 76145 | 76372 | 76128
17342 | 2021-11-13 | 22:24 | 11.7484 | 76146 | 76371 | 76129
17343 | 2021-11-13 | 22:24 | 11.7484 | 76147 | 76369 | 76130
17344 | 2021-11-13 | 22:24 | 11.7484 | 76147 | 76368 | 76131
17345 | 2021-11-13 | 22:24 | 11.7485 | 76148 | 76366 | 76132
17346 | 2021-11-13 | 22:24 | 11.7485 | 76149 | 76364 | 76133
17347 | 2021-11-13 | 22:24 | 11.7485 | 76149 | 76363 | 76134
17348 | 2021-11-13 | 22:24 | 11.7485 | 76150 | 76361 | 76135
17349 | 2021-11-13 | 22:24 | 11.7486 | 76150 | 76359 | 76136
17350 | 2021-11-13 | 22:24 | 11.7486 | 76151 | 76358 | 76138
17351 | 2021-11-13 | 22:24 | 11.7486 | 76151 | 76356 | 76139
17352 | 2021-11-13 | 22:24 | 11.7487 | 76152 | 76354 | 76140
17353 | 2021-11-13 | 22:24 | 11.7487 | 76152 | 76353 | 76141
17354 | 2021-11-13 | 22:24 | 11.7487 | 76153 | 76351 | 76143
17355 | 2021-11-13 | 22:24 | 11.7487 | 76153 | 76349 | 76144
17356 | 2021-11-13 | 22:24 | 11.7488 | 76154 | 76348 | 76145
17357 | 2021-11-13 | 22:24 | 11.7488 | 76154 | 76346 | 76147
17358 | 2021-11-13 | 22:24 | 11.7488 | 76154 | 76344 | 76148
17359 | 2021-11-13 | 22:24 | 11.7489 | 76155 | 76343 | 76150
17360 | 2021-11-13 | 22:24 | 11.7489 | 76155 | 76341 | 76151
17361 | 2021-11-13 | 22:24 | 11.7489 | 76155 | 76340 | 76153
17362 | 2021-11-13 | 22:24 | 11.7489 | 76156 | 76338 | 76155
17363 | 2021-11-13 | 22:24 | 11.749 | 76156 | 76337 | 76156
17364 | 2021-11-13 | 22:24 | 11.749 | 76156 | 76335 | 76158
17365 | 2021-11-13 | 22:24 | 11.749 | 76156 | 76334 | 76160
17366 | 2021-11-13 | 22:24 | 11.7491 | 76156 | 76332 | 76162
17367 | 2021-11-13 | 22:24 | 11.7491 | 76156 | 76331 | 76164
17368 | 2021-11-13 | 22:24 | 11.7491 | 76156 | 76329 | 76166
17369 | 2021-11-13 | 22:24 | 11.7491 | 76156 | 76328 | 76167
17370 | 2021-11-13 | 22:24 | 11.7492 | 76155 | 76327 | 76169
17371 | 2021-11-13 | 22:24 | 11.7492 | 76155 | 76325 | 76171
17372 | 2021-11-13 | 22:24 | 11.7492 | 76155 | 76324 | 76173
17373 | 2021-11-13 | 22:24 | 11.7493 | 76155 | 76323 | 76175
17374 | 2021-11-13 | 22:24 | 11.7493 | 76155 | 76322 | 76177
17375 | 2021-11-13 | 22:24 | 11.7493 | 76154 | 76321 | 76180
17376 | 2021-11-13 | 22:24 | 11.7493 | 76154 | 76319 | 76182
17377 | 2021-11-13 | 22:24 | 11.7494 | 76154 | 76318 | 76184
17378 | 2021-11-13 | 22:24 | 11.7494 | 76153 | 76317 | 76186
17379 | 2021-11-13 | 22:24 | 11.7494 | 76153 | 76316 | 76188
17380 | 2021-11-13 | 22:24 | 11.7495 | 76152 | 76315 | 76190
17381 | 2021-11-13 | 22:24 | 11.7495 | 76151 | 76314 | 76193
17382 | 2021-11-13 | 22:24 | 11.7495 | 76151 | 76313 | 76195
17383 | 2021-11-13 | 22:24 | 11.7495 | 76150 | 76312 | 76197
17384 | 2021-11-13 | 22:24 | 11.7496 | 76150 | 76312 | 76199
17385 | 2021-11-13 | 22:24 | 11.7496 | 76149 | 76311 | 76201
17386 | 2021-11-13 | 22:24 | 11.7496 | 76149 | 76310 | 76204
17387 | 2021-11-13 | 22:24 | 11.7497 | 76148 | 76309 | 76206
17388 | 2021-11-13 | 22:24 | 11.7497 | 76147 | 76309 | 76208
17389 | 2021-11-13 | 22:24 | 11.7497 | 76146 | 76308 | 76210
17390 | 2021-11-13 | 22:24 | 11.7497 | 76145 | 76307 | 76212
17391 | 2021-11-13 | 22:24 | 11.7498 | 76144 | 76307 | 76214
17392 | 2021-11-13 | 22:24 | 11.7498 | 76143 | 76306 | 76216
17393 | 2021-11-13 | 22:24 | 11.7498 | 76142 | 76306 | 76218
17394 | 2021-11-13 | 22:24 | 11.7499 | 76141 | 76306 | 76219
17395 | 2021-11-13 | 22:24 | 11.7499 | 76140 | 76305 | 76221
17396 | 2021-11-13 | 22:24 | 11.7499 | 76139 | 76305 | 76223
17397 | 2021-11-13 | 22:24 | 11.7499 | 76138 | 76305 | 76225
17398 | 2021-11-13 | 22:24 | 11.75 | 76136 | 76305 | 76227
17399 | 2021-11-13 | 22:24 | 11.75 | 76135 | 76305 | 76229
17400 | 2021-11-13 | 22:24 | 11.75 | 76134 | 76304 | 76230
17401 | 2021-11-13 | 22:24 | 11.7501 | 76133 | 76304 | 76232
17402 | 2021-11-13 | 22:24 | 11.7501 | 76131 | 76304 | 76234
17403 | 2021-11-13 | 22:24 | 11.7501 | 76130 | 76305 | 76236
17404 | 2021-11-13 | 22:24 | 11.7501 | 76129 | 76305 | 76237
17405 | 2021-11-13 | 22:24 | 11.7502 | 76127 | 76305 | 76239
17406 | 2021-11-13 | 22:24 | 11.7502 | 76125 | 76305 | 76241
17407 | 2021-11-13 | 22:24 | 11.7502 | 76124 | 76305 | 76243
17408 | 2021-11-13 | 22:24 | 11.7503 | 76122 | 76305 | 76245

## F20211103-1
In GMT
Date | Time | Freq
2021-11-03 | 6:59 | 50.162
2021-11-03 | 6:59 | 50.164
2021-11-03 | 6:59 | 50.166
2021-11-03 | 6:59 | 50.167
2021-11-03 | 6:59 | 50.172
2021-11-03 | 6:59 | 50.174
2021-11-03 | 6:59 | 50.179
2021-11-03 | 6:59 | 50.184
2021-11-03 | 6:59 | 50.189
2021-11-03 | 6:59 | 50.193
2021-11-03 | 6:59 | 50.199
2021-11-03 | 6:59 | 50.201
2021-11-03 | 6:59 | 50.206
2021-11-03 | 6:59 | 50.21
2021-11-03 | 6:59 | 50.214
2021-11-03 | 6:59 | 50.215
2021-11-03 | 6:59 | 50.215
2021-11-03 | 6:59 | 50.216
2021-11-03 | 6:59 | 50.214
2021-11-03 | 6:59 | 50.215
2021-11-03 | 6:59 | 50.216
2021-11-03 | 6:59 | 50.215
2021-11-03 | 6:59 | 50.216
2021-11-03 | 6:59 | 50.219
2021-11-03 | 6:59 | 50.22
2021-11-03 | 6:59 | 50.22
2021-11-03 | 6:59 | 50.218
2021-11-03 | 6:59 | 50.216
2021-11-03 | 6:59 | 50.214
2021-11-03 | 6:59 | 50.217
2021-11-03 | 6:59 | 50.22
2021-11-03 | 7:00 | 50.222
2021-11-03 | 7:00 | 50.223
2021-11-03 | 7:00 | 50.226
2021-11-03 | 7:00 | 50.226
2021-11-03 | 7:00 | 50.23
2021-11-03 | 7:00 | 50.233
2021-11-03 | 7:00 | 50.236
2021-11-03 | 7:00 | 50.237
2021-11-03 | 7:00 | 50.239
2021-11-03 | 7:00 | 50.237
2021-11-03 | 7:00 | 50.236
2021-11-03 | 7:00 | 50.234
2021-11-03 | 7:00 | 50.233
2021-11-03 | 7:00 | 50.232
2021-11-03 | 7:00 | 50.231
2021-11-03 | 7:00 | 50.228
2021-11-03 | 7:00 | 50.231
2021-11-03 | 7:00 | 50.228
2021-11-03 | 7:00 | 50.23
2021-11-03 | 7:00 | 50.234
2021-11-03 | 7:00 | 50.238
2021-11-03 | 7:00 | 50.243
2021-11-03 | 7:00 | 50.249
2021-11-03 | 7:00 | 50.254
2021-11-03 | 7:00 | 50.26
2021-11-03 | 7:00 | 50.265
2021-11-03 | 7:00 | 50.269
2021-11-03 | 7:00 | 50.273
2021-11-03 | 7:00 | 50.277
2021-11-03 | 7:00 | 50.277
2021-11-03 | 7:00 | 50.279
2021-11-03 | 7:00 | 50.284
2021-11-03 | 7:00 | 50.284
2021-11-03 | 7:00 | 50.287
2021-11-03 | 7:00 | 50.29
2021-11-03 | 7:00 | 50.291
2021-11-03 | 7:00 | 50.292
2021-11-03 | 7:00 | 50.294
2021-11-03 | 7:00 | 50.296
2021-11-03 | 7:00 | 50.299
2021-11-03 | 7:00 | 50.301
2021-11-03 | 7:00 | 50.303
2021-11-03 | 7:00 | 50.306
2021-11-03 | 7:00 | 50.308
2021-11-03 | 7:00 | 50.308
2021-11-03 | 7:00 | 50.306
2021-11-03 | 7:00 | 50.302
2021-11-03 | 7:00 | 50.299
2021-11-03 | 7:00 | 50.292
2021-11-03 | 7:00 | 50.289
2021-11-03 | 7:00 | 50.282
2021-11-03 | 7:00 | 50.278
2021-11-03 | 7:00 | 50.273
2021-11-03 | 7:00 | 50.263
2021-11-03 | 7:00 | 50.252
2021-11-03 | 7:00 | 50.241
2021-11-03 | 7:00 | 50.231
2021-11-03 | 7:00 | 50.225
2021-11-03 | 7:00 | 50.217
2021-11-03 | 7:01 | 50.211
2021-11-03 | 7:01 | 50.206
2021-11-03 | 7:01 | 50.2
2021-11-03 | 7:01 | 50.195
2021-11-03 | 7:01 | 50.189
2021-11-03 | 7:01 | 50.188
2021-11-03 | 7:01 | 50.185
2021-11-03 | 7:01 | 50.183
2021-11-03 | 7:01 | 50.183
2021-11-03 | 7:01 | 50.18
2021-11-03 | 7:01 | 50.183
2021-11-03 | 7:01 | 50.187
2021-11-03 | 7:01 | 50.19
2021-11-03 | 7:01 | 50.193
2021-11-03 | 7:01 | 50.195
2021-11-03 | 7:01 | 50.196
2021-11-03 | 7:01 | 50.197
2021-11-03 | 7:01 | 50.198
2021-11-03 | 7:01 | 50.198
2021-11-03 | 7:01 | 50.198
2021-11-03 | 7:01 | 50.196
2021-11-03 | 7:01 | 50.191
2021-11-03 | 7:01 | 50.191
2021-11-03 | 7:01 | 50.19
2021-11-03 | 7:01 | 50.189
2021-11-03 | 7:01 | 50.187
2021-11-03 | 7:01 | 50.187
2021-11-03 | 7:01 | 50.187
2021-11-03 | 7:01 | 50.187
2021-11-03 | 7:01 | 50.189
2021-11-03 | 7:01 | 50.188
2021-11-03 | 7:01 | 50.184
2021-11-03 | 7:01 | 50.182
2021-11-03 | 7:01 | 50.184
2021-11-03 | 7:01 | 50.184
2021-11-03 | 7:01 | 50.188
2021-11-03 | 7:01 | 50.188
2021-11-03 | 7:01 | 50.189
2021-11-03 | 7:01 | 50.194
2021-11-03 | 7:01 | 50.193
2021-11-03 | 7:01 | 50.192
2021-11-03 | 7:01 | 50.193
2021-11-03 | 7:01 | 50.193
2021-11-03 | 7:01 | 50.191
2021-11-03 | 7:01 | 50.192
2021-11-03 | 7:01 | 50.191
2021-11-03 | 7:01 | 50.19
2021-11-03 | 7:01 | 50.189
2021-11-03 | 7:01 | 50.191
2021-11-03 | 7:01 | 50.192
2021-11-03 | 7:01 | 50.194
2021-11-03 | 7:01 | 50.195
2021-11-03 | 7:01 | 50.197
2021-11-03 | 7:01 | 50.201
2021-11-03 | 7:01 | 50.202
2021-11-03 | 7:01 | 50.205
2021-11-03 | 7:01 | 50.207
2021-11-03 | 7:01 | 50.204
2021-11-03 | 7:01 | 50.199
2021-11-03 | 7:01 | 50.193
2021-11-03 | 7:01 | 50.187
2021-11-03 | 7:02 | 50.184
2021-11-03 | 7:02 | 50.18
2021-11-03 | 7:02 | 50.175
2021-11-03 | 7:02 | 50.171
2021-11-03 | 7:02 | 50.168
2021-11-03 | 7:02 | 50.164
2021-11-03 | 7:02 | 50.164
2021-11-03 | 7:02 | 50.16
2021-11-03 | 7:02 | 50.158
2021-11-03 | 7:02 | 50.154
2021-11-03 | 7:02 | 50.151
2021-11-03 | 7:02 | 50.148
2021-11-03 | 7:02 | 50.144
2021-11-03 | 7:02 | 50.142
2021-11-03 | 7:02 | 50.139
2021-11-03 | 7:02 | 50.138
2021-11-03 | 7:02 | 50.135
2021-11-03 | 7:02 | 50.133
2021-11-03 | 7:02 | 50.131
2021-11-03 | 7:02 | 50.13
2021-11-03 | 7:02 | 50.129
2021-11-03 | 7:02 | 50.128
2021-11-03 | 7:02 | 50.127
2021-11-03 | 7:02 | 50.125
2021-11-03 | 7:02 | 50.123
2021-11-03 | 7:02 | 50.123
2021-11-03 | 7:02 | 50.119
2021-11-03 | 7:02 | 50.116
2021-11-03 | 7:02 | 50.114
2021-11-03 | 7:02 | 50.11
2021-11-03 | 7:02 | 50.104
2021-11-03 | 7:02 | 50.1
2021-11-03 | 7:02 | 50.094
2021-11-03 | 7:02 | 50.092
2021-11-03 | 7:02 | 50.087
2021-11-03 | 7:02 | 50.083
2021-11-03 | 7:02 | 50.082
2021-11-03 | 7:02 | 50.079
2021-11-03 | 7:02 | 50.077
2021-11-03 | 7:02 | 50.075
2021-11-03 | 7:02 | 50.072
2021-11-03 | 7:02 | 50.07
2021-11-03 | 7:02 | 50.068
2021-11-03 | 7:02 | 50.067
2021-11-03 | 7:02 | 50.064
2021-11-03 | 7:02 | 50.062
2021-11-03 | 7:02 | 50.058
2021-11-03 | 7:02 | 50.053
2021-11-03 | 7:02 | 50.05
2021-11-03 | 7:02 | 50.046
2021-11-03 | 7:02 | 50.043
2021-11-03 | 7:02 | 50.041
2021-11-03 | 7:02 | 50.039
2021-11-03 | 7:02 | 50.036
2021-11-03 | 7:02 | 50.035
2021-11-03 | 7:02 | 50.032
2021-11-03 | 7:02 | 50.031
2021-11-03 | 7:02 | 50.03
2021-11-03 | 7:02 | 50.031
2021-11-03 | 7:03 | 50.033
2021-11-03 | 7:03 | 50.034
2021-11-03 | 7:03 | 50.036
2021-11-03 | 7:03 | 50.037
2021-11-03 | 7:03 | 50.042
2021-11-03 | 7:03 | 50.044
2021-11-03 | 7:03 | 50.045
2021-11-03 | 7:03 | 50.044
2021-11-03 | 7:03 | 50.045
2021-11-03 | 7:03 | 50.044
2021-11-03 | 7:03 | 50.041
2021-11-03 | 7:03 | 50.038
2021-11-03 | 7:03 | 50.035
2021-11-03 | 7:03 | 50.033
2021-11-03 | 7:03 | 50.029
2021-11-03 | 7:03 | 50.028
2021-11-03 | 7:03 | 50.025
2021-11-03 | 7:03 | 50.023
2021-11-03 | 7:03 | 50.022
2021-11-03 | 7:03 | 50.023
2021-11-03 | 7:03 | 50.025
2021-11-03 | 7:03 | 50.031
2021-11-03 | 7:03 | 50.036
2021-11-03 | 7:03 | 50.036
2021-11-03 | 7:03 | 50.035
2021-11-03 | 7:03 | 50.033
2021-11-03 | 7:03 | 50.028
2021-11-03 | 7:03 | 50.025
2021-11-03 | 7:03 | 50.018
2021-11-03 | 7:03 | 50.013
2021-11-03 | 7:03 | 50.008
2021-11-03 | 7:03 | 50.005
2021-11-03 | 7:03 | 49.996
2021-11-03 | 7:03 | 49.99
2021-11-03 | 7:03 | 49.984
2021-11-03 | 7:03 | 49.98
2021-11-03 | 7:03 | 49.976
2021-11-03 | 7:03 | 49.972
2021-11-03 | 7:03 | 49.973
2021-11-03 | 7:03 | 49.971
2021-11-03 | 7:03 | 49.972
2021-11-03 | 7:03 | 49.97
2021-11-03 | 7:03 | 49.97
2021-11-03 | 7:03 | 49.948
2021-11-03 | 7:03 | 49.934
2021-11-03 | 7:03 | 49.922
2021-11-03 | 7:03 | 49.906
2021-11-03 | 7:03 | 49.894
2021-11-03 | 7:03 | 49.887
2021-11-03 | 7:03 | 49.881
2021-11-03 | 7:03 | 49.877
2021-11-03 | 7:03 | 49.872
2021-11-03 | 7:03 | 49.869
2021-11-03 | 7:03 | 49.864
2021-11-03 | 7:03 | 49.86
2021-11-03 | 7:03 | 49.855
2021-11-03 | 7:03 | 49.849
2021-11-03 | 7:03 | 49.842
2021-11-03 | 7:03 | 49.835
2021-11-03 | 7:03 | 49.831
2021-11-03 | 7:03 | 49.825
2021-11-03 | 7:04 | 49.822
2021-11-03 | 7:04 | 49.817
2021-11-03 | 7:04 | 49.815
2021-11-03 | 7:04 | 49.815
2021-11-03 | 7:04 | 49.816
2021-11-03 | 7:04 | 49.816
2021-11-03 | 7:04 | 49.815
2021-11-03 | 7:04 | 49.814
2021-11-03 | 7:04 | 49.815
2021-11-03 | 7:04 | 49.815
2021-11-03 | 7:04 | 49.816
2021-11-03 | 7:04 | 49.818
2021-11-03 | 7:04 | 49.82
2021-11-03 | 7:04 | 49.823
2021-11-03 | 7:04 | 49.825
2021-11-03 | 7:04 | 49.826
2021-11-03 | 7:04 | 49.827
2021-11-03 | 7:04 | 49.829
2021-11-03 | 7:04 | 49.831
2021-11-03 | 7:04 | 49.831
2021-11-03 | 7:04 | 49.832
2021-11-03 | 7:04 | 49.831
2021-11-03 | 7:04 | 49.832
2021-11-03 | 7:04 | 49.831
2021-11-03 | 7:04 | 49.829
2021-11-03 | 7:04 | 49.827
2021-11-03 | 7:04 | 49.823
2021-11-03 | 7:04 | 49.817
2021-11-03 | 7:04 | 49.813

## F20211103-2
In GMT
Date | Time | Freq
2021-11-03 | 7:02 | 50.11
2021-11-03 | 7:02 | 50.104
2021-11-03 | 7:02 | 50.1
2021-11-03 | 7:02 | 50.094
2021-11-03 | 7:02 | 50.092
2021-11-03 | 7:02 | 50.087
2021-11-03 | 7:02 | 50.083
2021-11-03 | 7:02 | 50.082
2021-11-03 | 7:02 | 50.079
2021-11-03 | 7:02 | 50.077
2021-11-03 | 7:02 | 50.075
2021-11-03 | 7:02 | 50.072
2021-11-03 | 7:02 | 50.07
2021-11-03 | 7:02 | 50.068
2021-11-03 | 7:02 | 50.067
2021-11-03 | 7:02 | 50.064
2021-11-03 | 7:02 | 50.062
2021-11-03 | 7:02 | 50.058
2021-11-03 | 7:02 | 50.053
2021-11-03 | 7:02 | 50.05
2021-11-03 | 7:02 | 50.046
2021-11-03 | 7:02 | 50.043
2021-11-03 | 7:02 | 50.041
2021-11-03 | 7:02 | 50.039
2021-11-03 | 7:02 | 50.036
2021-11-03 | 7:02 | 50.035
2021-11-03 | 7:02 | 50.032
2021-11-03 | 7:02 | 50.031
2021-11-03 | 7:02 | 50.03
2021-11-03 | 7:02 | 50.031
2021-11-03 | 7:03 | 50.033
2021-11-03 | 7:03 | 50.034
2021-11-03 | 7:03 | 50.036
2021-11-03 | 7:03 | 50.037
2021-11-03 | 7:03 | 50.042
2021-11-03 | 7:03 | 50.044
2021-11-03 | 7:03 | 50.045
2021-11-03 | 7:03 | 50.044
2021-11-03 | 7:03 | 50.045
2021-11-03 | 7:03 | 50.044
2021-11-03 | 7:03 | 50.041
2021-11-03 | 7:03 | 50.038
2021-11-03 | 7:03 | 50.035
2021-11-03 | 7:03 | 50.033
2021-11-03 | 7:03 | 50.029
2021-11-03 | 7:03 | 50.028
2021-11-03 | 7:03 | 50.025
2021-11-03 | 7:03 | 50.023
2021-11-03 | 7:03 | 50.022
2021-11-03 | 7:03 | 50.023
2021-11-03 | 7:03 | 50.025
2021-11-03 | 7:03 | 50.031
2021-11-03 | 7:03 | 50.036
2021-11-03 | 7:03 | 50.036
2021-11-03 | 7:03 | 50.035
2021-11-03 | 7:03 | 50.033
2021-11-03 | 7:03 | 50.028
2021-11-03 | 7:03 | 50.025
2021-11-03 | 7:03 | 50.018
2021-11-03 | 7:03 | 50.013
2021-11-03 | 7:03 | 50.008
2021-11-03 | 7:03 | 50.005
2021-11-03 | 7:03 | 49.996
2021-11-03 | 7:03 | 49.99
2021-11-03 | 7:03 | 49.984
2021-11-03 | 7:03 | 49.98
2021-11-03 | 7:03 | 49.976
2021-11-03 | 7:03 | 49.972
2021-11-03 | 7:03 | 49.973
2021-11-03 | 7:03 | 49.971
2021-11-03 | 7:03 | 49.972
2021-11-03 | 7:03 | 49.97
2021-11-03 | 7:03 | 49.97
2021-11-03 | 7:03 | 49.948
2021-11-03 | 7:03 | 49.934
2021-11-03 | 7:03 | 49.922
2021-11-03 | 7:03 | 49.906
2021-11-03 | 7:03 | 49.894
2021-11-03 | 7:03 | 49.887
2021-11-03 | 7:03 | 49.881
2021-11-03 | 7:03 | 49.877
2021-11-03 | 7:03 | 49.872
2021-11-03 | 7:03 | 49.869
2021-11-03 | 7:03 | 49.864
2021-11-03 | 7:03 | 49.86
2021-11-03 | 7:03 | 49.855
2021-11-03 | 7:03 | 49.849
2021-11-03 | 7:03 | 49.842
2021-11-03 | 7:03 | 49.835
2021-11-03 | 7:03 | 49.831
2021-11-03 | 7:03 | 49.825
2021-11-03 | 7:04 | 49.822
2021-11-03 | 7:04 | 49.817
2021-11-03 | 7:04 | 49.815
2021-11-03 | 7:04 | 49.815
2021-11-03 | 7:04 | 49.816
2021-11-03 | 7:04 | 49.816
2021-11-03 | 7:04 | 49.815
2021-11-03 | 7:04 | 49.814
2021-11-03 | 7:04 | 49.815
2021-11-03 | 7:04 | 49.815
2021-11-03 | 7:04 | 49.816
2021-11-03 | 7:04 | 49.818
2021-11-03 | 7:04 | 49.82
2021-11-03 | 7:04 | 49.823
2021-11-03 | 7:04 | 49.825
2021-11-03 | 7:04 | 49.826
2021-11-03 | 7:04 | 49.827
2021-11-03 | 7:04 | 49.829
2021-11-03 | 7:04 | 49.831
2021-11-03 | 7:04 | 49.831
2021-11-03 | 7:04 | 49.832
2021-11-03 | 7:04 | 49.831
2021-11-03 | 7:04 | 49.832
2021-11-03 | 7:04 | 49.831
2021-11-03 | 7:04 | 49.829
2021-11-03 | 7:04 | 49.827
2021-11-03 | 7:04 | 49.823
2021-11-03 | 7:04 | 49.817
2021-11-03 | 7:04 | 49.813
2021-11-03 | 7:04 | 49.81
2021-11-03 | 7:04 | 49.807
2021-11-03 | 7:04 | 49.803
2021-11-03 | 7:04 | 49.8
2021-11-03 | 7:04 | 49.794
2021-11-03 | 7:04 | 49.789
2021-11-03 | 7:04 | 49.781
2021-11-03 | 7:04 | 49.777
2021-11-03 | 7:04 | 49.771
2021-11-03 | 7:04 | 49.767
2021-11-03 | 7:04 | 49.768
2021-11-03 | 7:04 | 49.766
2021-11-03 | 7:04 | 49.767
2021-11-03 | 7:04 | 49.767
2021-11-03 | 7:04 | 49.766
2021-11-03 | 7:04 | 49.766
2021-11-03 | 7:04 | 49.764
2021-11-03 | 7:04 | 49.765
2021-11-03 | 7:04 | 49.764
2021-11-03 | 7:04 | 49.765
2021-11-03 | 7:04 | 49.766
2021-11-03 | 7:04 | 49.766
2021-11-03 | 7:04 | 49.764
2021-11-03 | 7:04 | 49.764
2021-11-03 | 7:04 | 49.763
2021-11-03 | 7:04 | 49.762
2021-11-03 | 7:04 | 49.76
2021-11-03 | 7:04 | 49.758
2021-11-03 | 7:04 | 49.755
2021-11-03 | 7:04 | 49.752
2021-11-03 | 7:05 | 49.751
2021-11-03 | 7:05 | 49.748
2021-11-03 | 7:05 | 49.747
2021-11-03 | 7:05 | 49.745
2021-11-03 | 7:05 | 49.747
2021-11-03 | 7:05 | 49.748
2021-11-03 | 7:05 | 49.752
2021-11-03 | 7:05 | 49.755
2021-11-03 | 7:05 | 49.758
2021-11-03 | 7:05 | 49.76
2021-11-03 | 7:05 | 49.764
2021-11-03 | 7:05 | 49.766
2021-11-03 | 7:05 | 49.769
2021-11-03 | 7:05 | 49.769
2021-11-03 | 7:05 | 49.772
2021-11-03 | 7:05 | 49.773
2021-11-03 | 7:05 | 49.776
2021-11-03 | 7:05 | 49.778
2021-11-03 | 7:05 | 49.779
2021-11-03 | 7:05 | 49.78
2021-11-03 | 7:05 | 49.78
2021-11-03 | 7:05 | 49.78
2021-11-03 | 7:05 | 49.778
2021-11-03 | 7:05 | 49.775
2021-11-03 | 7:05 | 49.774
2021-11-03 | 7:05 | 49.772
2021-11-03 | 7:05 | 49.772
2021-11-03 | 7:05 | 49.768
2021-11-03 | 7:05 | 49.767
2021-11-03 | 7:05 | 49.763
2021-11-03 | 7:05 | 49.763
2021-11-03 | 7:05 | 49.761
2021-11-03 | 7:05 | 49.757
2021-11-03 | 7:05 | 49.756
2021-11-03 | 7:05 | 49.755
2021-11-03 | 7:05 | 49.755
2021-11-03 | 7:05 | 49.754
2021-11-03 | 7:05 | 49.754
2021-11-03 | 7:05 | 49.754
2021-11-03 | 7:05 | 49.752
2021-11-03 | 7:05 | 49.751
2021-11-03 | 7:05 | 49.75
2021-11-03 | 7:05 | 49.749
2021-11-03 | 7:05 | 49.749
2021-11-03 | 7:05 | 49.749
2021-11-03 | 7:05 | 49.748
2021-11-03 | 7:05 | 49.75
2021-11-03 | 7:05 | 49.747
2021-11-03 | 7:05 | 49.741
2021-11-03 | 7:05 | 49.736
2021-11-03 | 7:05 | 49.732
2021-11-03 | 7:05 | 49.731
2021-11-03 | 7:05 | 49.729
2021-11-03 | 7:05 | 49.729
2021-11-03 | 7:05 | 49.729
2021-11-03 | 7:05 | 49.729
2021-11-03 | 7:05 | 49.728
2021-11-03 | 7:05 | 49.726
2021-11-03 | 7:05 | 49.724
2021-11-03 | 7:05 | 49.721
2021-11-03 | 7:05 | 49.718
2021-11-03 | 7:06 | 49.714
2021-11-03 | 7:06 | 49.71
2021-11-03 | 7:06 | 49.708
2021-11-03 | 7:06 | 49.707
2021-11-03 | 7:06 | 49.708
2021-11-03 | 7:06 | 49.709
2021-11-03 | 7:06 | 49.711
2021-11-03 | 7:06 | 49.711
2021-11-03 | 7:06 | 49.713
2021-11-03 | 7:06 | 49.714
2021-11-03 | 7:06 | 49.72
2021-11-03 | 7:06 | 49.722
2021-11-03 | 7:06 | 49.726
2021-11-03 | 7:06 | 49.728
2021-11-03 | 7:06 | 49.733
2021-11-03 | 7:06 | 49.736
2021-11-03 | 7:06 | 49.741
2021-11-03 | 7:06 | 49.742
2021-11-03 | 7:06 | 49.746
2021-11-03 | 7:06 | 49.748
2021-11-03 | 7:06 | 49.747
2021-11-03 | 7:06 | 49.748
2021-11-03 | 7:06 | 49.75
2021-11-03 | 7:06 | 49.749
2021-11-03 | 7:06 | 49.748
2021-11-03 | 7:06 | 49.747
2021-11-03 | 7:06 | 49.745
2021-11-03 | 7:06 | 49.745
2021-11-03 | 7:06 | 49.743
2021-11-03 | 7:06 | 49.744
2021-11-03 | 7:06 | 49.745
2021-11-03 | 7:06 | 49.75
2021-11-03 | 7:06 | 49.754
2021-11-03 | 7:06 | 49.758
2021-11-03 | 7:06 | 49.759
2021-11-03 | 7:06 | 49.759
2021-11-03 | 7:06 | 49.758
2021-11-03 | 7:06 | 49.756
2021-11-03 | 7:06 | 49.753
2021-11-03 | 7:06 | 49.751
2021-11-03 | 7:06 | 49.748
2021-11-03 | 7:06 | 49.745
2021-11-03 | 7:06 | 49.742
2021-11-03 | 7:06 | 49.742
2021-11-03 | 7:06 | 49.74
2021-11-03 | 7:06 | 49.739
2021-11-03 | 7:06 | 49.741
2021-11-03 | 7:06 | 49.745
2021-11-03 | 7:06 | 49.75
2021-11-03 | 7:06 | 49.758
2021-11-03 | 7:06 | 49.765
2021-11-03 | 7:06 | 49.772
2021-11-03 | 7:06 | 49.778
2021-11-03 | 7:06 | 49.785
2021-11-03 | 7:06 | 49.791
2021-11-03 | 7:06 | 49.796
2021-11-03 | 7:06 | 49.798
2021-11-03 | 7:06 | 49.8
2021-11-03 | 7:06 | 49.802
2021-11-03 | 7:07 | 49.803
2021-11-03 | 7:07 | 49.804
2021-11-03 | 7:07 | 49.805
2021-11-03 | 7:07 | 49.806
2021-11-03 | 7:07 | 49.806
2021-11-03 | 7:07 | 49.807
2021-11-03 | 7:07 | 49.807
2021-11-03 | 7:07 | 49.809
2021-11-03 | 7:07 | 49.809
2021-11-03 | 7:07 | 49.81
2021-11-03 | 7:07 | 49.813
2021-11-03 | 7:07 | 49.816
2021-11-03 | 7:07 | 49.818
2021-11-03 | 7:07 | 49.819
2021-11-03 | 7:07 | 49.822
2021-11-03 | 7:07 | 49.824
2021-11-03 | 7:07 | 49.827
2021-11-03 | 7:07 | 49.831
2021-11-03 | 7:07 | 49.834
2021-11-03 | 7:07 | 49.837
2021-11-03 | 7:07 | 49.841
2021-11-03 | 7:07 | 49.844
2021-11-03 | 7:07 | 49.844
2021-11-03 | 7:07 | 49.846
2021-11-03 | 7:07 | 49.847
2021-11-03 | 7:07 | 49.847
2021-11-03 | 7:07 | 49.849
2021-11-03 | 7:07 | 49.851
2021-11-03 | 7:07 | 49.851
2021-11-03 | 7:07 | 49.853
2021-11-03 | 7:07 | 49.857
2021-11-03 | 7:07 | 49.858
2021-11-03 | 7:07 | 49.86
2021-11-03 | 7:07 | 49.861
2021-11-03 | 7:07 | 49.863
2021-11-03 | 7:07 | 49.866
2021-11-03 | 7:07 | 49.867
2021-11-03 | 7:07 | 49.872
2021-11-03 | 7:07 | 49.872
2021-11-03 | 7:07 | 49.872
2021-11-03 | 7:07 | 49.87
2021-11-03 | 7:07 | 49.867
2021-11-03 | 7:07 | 49.865
2021-11-03 | 7:07 | 49.861
2021-11-03 | 7:07 | 49.859
2021-11-03 | 7:07 | 49.856
2021-11-03 | 7:07 | 49.855
2021-11-03 | 7:07 | 49.853
2021-11-03 | 7:07 | 49.852
2021-11-03 | 7:07 | 49.851
2021-11-03 | 7:07 | 49.85
2021-11-03 | 7:07 | 49.848
2021-11-03 | 7:07 | 49.848
2021-11-03 | 7:07 | 49.848
2021-11-03 | 7:07 | 49.847
2021-11-03 | 7:07 | 49.847
2021-11-03 | 7:07 | 49.846
2021-11-03 | 7:07 | 49.847
2021-11-03 | 7:07 | 49.847
2021-11-03 | 7:07 | 49.847
2021-11-03 | 7:08 | 49.845
2021-11-03 | 7:08 | 49.845
2021-11-03 | 7:08 | 49.844
2021-11-03 | 7:08 | 49.846
2021-11-03 | 7:08 | 49.848
2021-11-03 | 7:08 | 49.85
2021-11-03 | 7:08 | 49.856
2021-11-03 | 7:08 | 49.857
2021-11-03 | 7:08 | 49.86
2021-11-03 | 7:08 | 49.862
2021-11-03 | 7:08 | 49.861
2021-11-03 | 7:08 | 49.861
2021-11-03 | 7:08 | 49.86
2021-11-03 | 7:08 | 49.859
2021-11-03 | 7:08 | 49.859
2021-11-03 | 7:08 | 49.859
2021-11-03 | 7:08 | 49.859
2021-11-03 | 7:08 | 49.862
2021-11-03 | 7:08 | 49.864
2021-11-03 | 7:08 | 49.866
2021-11-03 | 7:08 | 49.868
2021-11-03 | 7:08 | 49.867
2021-11-03 | 7:08 | 49.868
2021-11-03 | 7:08 | 49.868
2021-11-03 | 7:08 | 49.866
2021-11-03 | 7:08 | 49.864
2021-11-03 | 7:08 | 49.862
2021-11-03 | 7:08 | 49.858
2021-11-03 | 7:08 | 49.858
2021-11-03 | 7:08 | 49.857
2021-11-03 | 7:08 | 49.856
2021-11-03 | 7:08 | 49.855
2021-11-03 | 7:08 | 49.855
2021-11-03 | 7:08 | 49.855
2021-11-03 | 7:08 | 49.856
2021-11-03 | 7:08 | 49.857
2021-11-03 | 7:08 | 49.858
2021-11-03 | 7:08 | 49.862
2021-11-03 | 7:08 | 49.866
2021-11-03 | 7:08 | 49.868
2021-11-03 | 7:08 | 49.868
2021-11-03 | 7:08 | 49.869
2021-11-03 | 7:08 | 49.869
2021-11-03 | 7:08 | 49.868
2021-11-03 | 7:08 | 49.868
2021-11-03 | 7:08 | 49.867
2021-11-03 | 7:08 | 49.866
2021-11-03 | 7:08 | 49.866
2021-11-03 | 7:08 | 49.866
2021-11-03 | 7:08 | 49.868
2021-11-03 | 7:08 | 49.868
2021-11-03 | 7:08 | 49.871
2021-11-03 | 7:08 | 49.874
2021-11-03 | 7:08 | 49.875
2021-11-03 | 7:08 | 49.878
2021-11-03 | 7:08 | 49.881
2021-11-03 | 7:08 | 49.882
2021-11-03 | 7:08 | 49.882
2021-11-03 | 7:08 | 49.885
2021-11-03 | 7:08 | 49.885
2021-11-03 | 7:08 | 49.884
2021-11-03 | 7:09 | 49.879
2021-11-03 | 7:09 | 49.878
2021-11-03 | 7:09 | 49.875
2021-11-03 | 7:09 | 49.872
2021-11-03 | 7:09 | 49.869
2021-11-03 | 7:09 | 49.867
2021-11-03 | 7:09 | 49.867
2021-11-03 | 7:09 | 49.868
2021-11-03 | 7:09 | 49.871
2021-11-03 | 7:09 | 49.871
2021-11-03 | 7:09 | 49.873
2021-11-03 | 7:09 | 49.872
2021-11-03 | 7:09 | 49.871
2021-11-03 | 7:09 | 49.87
2021-11-03 | 7:09 | 49.869
2021-11-03 | 7:09 | 49.866
2021-11-03 | 7:09 | 49.866
2021-11-03 | 7:09 | 49.865
2021-11-03 | 7:09 | 49.866
2021-11-03 | 7:09 | 49.863
2021-11-03 | 7:09 | 49.858
2021-11-03 | 7:09 | 49.857
2021-11-03 | 7:09 | 49.854
2021-11-03 | 7:09 | 49.851
2021-11-03 | 7:09 | 49.849
2021-11-03 | 7:09 | 49.849
2021-11-03 | 7:09 | 49.846
2021-11-03 | 7:09 | 49.845
2021-11-03 | 7:09 | 49.844
2021-11-03 | 7:09 | 49.841
2021-11-03 | 7:09 | 49.837
2021-11-03 | 7:09 | 49.833
2021-11-03 | 7:09 | 49.829
2021-11-03 | 7:09 | 49.825
2021-11-03 | 7:09 | 49.824
2021-11-03 | 7:09 | 49.82
2021-11-03 | 7:09 | 49.819
2021-11-03 | 7:09 | 49.818
2021-11-03 | 7:09 | 49.821
2021-11-03 | 7:09 | 49.821
2021-11-03 | 7:09 | 49.822
2021-11-03 | 7:09 | 49.823
2021-11-03 | 7:09 | 49.826
2021-11-03 | 7:09 | 49.831
2021-11-03 | 7:09 | 49.837
2021-11-03 | 7:09 | 49.841
2021-11-03 | 7:09 | 49.845
2021-11-03 | 7:09 | 49.848
2021-11-03 | 7:09 | 49.853
2021-11-03 | 7:09 | 49.857
2021-11-03 | 7:09 | 49.859
2021-11-03 | 7:09 | 49.86
2021-11-03 | 7:09 | 49.86
2021-11-03 | 7:09 | 49.862
2021-11-03 | 7:09 | 49.861
2021-11-03 | 7:09 | 49.861
2021-11-03 | 7:09 | 49.863
2021-11-03 | 7:09 | 49.863
2021-11-03 | 7:09 | 49.864
2021-11-03 | 7:10 | 49.861
2021-11-03 | 7:10 | 49.863
2021-11-03 | 7:10 | 49.861
2021-11-03 | 7:10 | 49.86
2021-11-03 | 7:10 | 49.862
2021-11-03 | 7:10 | 49.862
2021-11-03 | 7:10 | 49.859
2021-11-03 | 7:10 | 49.855
2021-11-03 | 7:10 | 49.855
2021-11-03 | 7:10 | 49.854
2021-11-03 | 7:10 | 49.856
2021-11-03 | 7:10 | 49.855
2021-11-03 | 7:10 | 49.858
2021-11-03 | 7:10 | 49.857
2021-11-03 | 7:10 | 49.858
2021-11-03 | 7:10 | 49.859
2021-11-03 | 7:10 | 49.861
2021-11-03 | 7:10 | 49.862
2021-11-03 | 7:10 | 49.865
2021-11-03 | 7:10 | 49.868
2021-11-03 | 7:10 | 49.869
2021-11-03 | 7:10 | 49.871
2021-11-03 | 7:10 | 49.868
2021-11-03 | 7:10 | 49.867
2021-11-03 | 7:10 | 49.863
2021-11-03 | 7:10 | 49.861
2021-11-03 | 7:10 | 49.86
2021-11-03 | 7:10 | 49.858
2021-11-03 | 7:10 | 49.856
2021-11-03 | 7:10 | 49.853
2021-11-03 | 7:10 | 49.853
2021-11-03 | 7:10 | 49.85
2021-11-03 | 7:10 | 49.845
2021-11-03 | 7:10 | 49.841
2021-11-03 | 7:10 | 49.839
2021-11-03 | 7:10 | 49.837
2021-11-03 | 7:10 | 49.837
2021-11-03 | 7:10 | 49.836
2021-11-03 | 7:10 | 49.837
2021-11-03 | 7:10 | 49.838
2021-11-03 | 7:10 | 49.841
2021-11-03 | 7:10 | 49.841
2021-11-03 | 7:10 | 49.842
2021-11-03 | 7:10 | 49.843
2021-11-03 | 7:10 | 49.842
2021-11-03 | 7:10 | 49.841
2021-11-03 | 7:10 | 49.841
2021-11-03 | 7:10 | 49.838
2021-11-03 | 7:10 | 49.836
2021-11-03 | 7:10 | 49.833
2021-11-03 | 7:10 | 49.832
2021-11-03 | 7:10 | 49.83
2021-11-03 | 7:10 | 49.832
2021-11-03 | 7:10 | 49.836
2021-11-03 | 7:10 | 49.84
2021-11-03 | 7:10 | 49.842
2021-11-03 | 7:10 | 49.845
2021-11-03 | 7:10 | 49.845
2021-11-03 | 7:10 | 49.846
2021-11-03 | 7:10 | 49.846
2021-11-03 | 7:10 | 49.844
2021-11-03 | 7:11 | 49.843
2021-11-03 | 7:11 | 49.841
2021-11-03 | 7:11 | 49.839
2021-11-03 | 7:11 | 49.839
2021-11-03 | 7:11 | 49.841
2021-11-03 | 7:11 | 49.841
2021-11-03 | 7:11 | 49.842
2021-11-03 | 7:11 | 49.841
2021-11-03 | 7:11 | 49.842
2021-11-03 | 7:11 | 49.842
2021-11-03 | 7:11 | 49.845
2021-11-03 | 7:11 | 49.847
2021-11-03 | 7:11 | 49.853
2021-11-03 | 7:11 | 49.858
2021-11-03 | 7:11 | 49.864
2021-11-03 | 7:11 | 49.868
2021-11-03 | 7:11 | 49.871
2021-11-03 | 7:11 | 49.875
2021-11-03 | 7:11 | 49.876
2021-11-03 | 7:11 | 49.879
2021-11-03 | 7:11 | 49.881
2021-11-03 | 7:11 | 49.885
2021-11-03 | 7:11 | 49.89
2021-11-03 | 7:11 | 49.894
2021-11-03 | 7:11 | 49.896
2021-11-03 | 7:11 | 49.898
2021-11-03 | 7:11 | 49.898
2021-11-03 | 7:11 | 49.9
2021-11-03 | 7:11 | 49.9
2021-11-03 | 7:11 | 49.899
2021-11-03 | 7:11 | 49.894
2021-11-03 | 7:11 | 49.891
2021-11-03 | 7:11 | 49.887
2021-11-03 | 7:11 | 49.881
2021-11-03 | 7:11 | 49.876
2021-11-03 | 7:11 | 49.875
2021-11-03 | 7:11 | 49.873
2021-11-03 | 7:11 | 49.873
2021-11-03 | 7:11 | 49.872
2021-11-03 | 7:11 | 49.874
2021-11-03 | 7:11 | 49.874
2021-11-03 | 7:11 | 49.874
2021-11-03 | 7:11 | 49.879
2021-11-03 | 7:11 | 49.884
2021-11-03 | 7:11 | 49.893
2021-11-03 | 7:11 | 49.9
2021-11-03 | 7:11 | 49.905
2021-11-03 | 7:11 | 49.911
2021-11-03 | 7:11 | 49.922
2021-11-03 | 7:11 | 49.928
2021-11-03 | 7:11 | 49.938
2021-11-03 | 7:11 | 49.947
2021-11-03 | 7:11 | 49.953
2021-11-03 | 7:11 | 49.962
2021-11-03 | 7:11 | 49.968
2021-11-03 | 7:11 | 49.972
2021-11-03 | 7:11 | 49.976
2021-11-03 | 7:11 | 49.98
2021-11-03 | 7:11 | 49.981
2021-11-03 | 7:12 | 49.983
2021-11-03 | 7:12 | 49.983
2021-11-03 | 7:12 | 49.98
2021-11-03 | 7:12 | 49.979
2021-11-03 | 7:12 | 49.978
2021-11-03 | 7:12 | 49.979
2021-11-03 | 7:12 | 49.979
2021-11-03 | 7:12 | 49.98
2021-11-03 | 7:12 | 49.982
2021-11-03 | 7:12 | 49.982
2021-11-03 | 7:12 | 49.98
2021-11-03 | 7:12 | 49.978
2021-11-03 | 7:12 | 49.978
2021-11-03 | 7:12 | 49.979
2021-11-03 | 7:12 | 49.979
2021-11-03 | 7:12 | 49.979
2021-11-03 | 7:12 | 49.98
2021-11-03 | 7:12 | 49.98
2021-11-03 | 7:12 | 49.981
2021-11-03 | 7:12 | 49.983
2021-11-03 | 7:12 | 49.982
2021-11-03 | 7:12 | 49.984
2021-11-03 | 7:12 | 49.985
2021-11-03 | 7:12 | 49.986
2021-11-03 | 7:12 | 49.99
2021-11-03 | 7:12 | 49.99
2021-11-03 | 7:12 | 49.993
2021-11-03 | 7:12 | 49.996
2021-11-03 | 7:12 | 49.998
2021-11-03 | 7:12 | 49.999
2021-11-03 | 7:12 | 50.004
2021-11-03 | 7:12 | 50.004
2021-11-03 | 7:12 | 50.006
2021-11-03 | 7:12 | 50.007
2021-11-03 | 7:12 | 50.007
2021-11-03 | 7:12 | 50.008
2021-11-03 | 7:12 | 50.006
2021-11-03 | 7:12 | 50.006
2021-11-03 | 7:12 | 50.006
2021-11-03 | 7:12 | 50.006
2021-11-03 | 7:12 | 50.003
2021-11-03 | 7:12 | 50.001
2021-11-03 | 7:12 | 50
2021-11-03 | 7:12 | 50.001
2021-11-03 | 7:12 | 50.001
2021-11-03 | 7:12 | 49.999
2021-11-03 | 7:12 | 49.999
2021-11-03 | 7:12 | 49.997
2021-11-03 | 7:12 | 49.994
2021-11-03 | 7:12 | 49.993
2021-11-03 | 7:12 | 49.992
2021-11-03 | 7:12 | 49.99
2021-11-03 | 7:12 | 49.988
2021-11-03 | 7:12 | 49.99
2021-11-03 | 7:12 | 49.993
2021-11-03 | 7:12 | 49.996
2021-11-03 | 7:12 | 49.999
2021-11-03 | 7:12 | 50.001
2021-11-03 | 7:12 | 50.002
2021-11-03 | 7:12 | 50.003
2021-11-03 | 7:12 | 50.005
2021-11-03 | 7:13 | 50.005
2021-11-03 | 7:13 | 50.005
2021-11-03 | 7:13 | 50.005
2021-11-03 | 7:13 | 50
2021-11-03 | 7:13 | 49.995
2021-11-03 | 7:13 | 49.99
2021-11-03 | 7:13 | 49.982
2021-11-03 | 7:13 | 49.977
2021-11-03 | 7:13 | 49.974
2021-11-03 | 7:13 | 49.975
2021-11-03 | 7:13 | 49.975
2021-11-03 | 7:13 | 49.975
2021-11-03 | 7:13 | 49.976
2021-11-03 | 7:13 | 49.978
2021-11-03 | 7:13 | 49.978
2021-11-03 | 7:13 | 49.979
2021-11-03 | 7:13 | 49.981
2021-11-03 | 7:13 | 49.981
2021-11-03 | 7:13 | 49.98
2021-11-03 | 7:13 | 49.977
2021-11-03 | 7:13 | 49.975
2021-11-03 | 7:13 | 49.974
2021-11-03 | 7:13 | 49.973
2021-11-03 | 7:13 | 49.974
2021-11-03 | 7:13 | 49.975
2021-11-03 | 7:13 | 49.975
2021-11-03 | 7:13 | 49.977
2021-11-03 | 7:13 | 49.98
2021-11-03 | 7:13 | 49.982
2021-11-03 | 7:13 | 49.983
2021-11-03 | 7:13 | 49.983
2021-11-03 | 7:13 | 49.984
2021-11-03 | 7:13 | 49.985
2021-11-03 | 7:13 | 49.985
2021-11-03 | 7:13 | 49.985
2021-11-03 | 7:13 | 49.984
2021-11-03 | 7:13 | 49.982
2021-11-03 | 7:13 | 49.981
2021-11-03 | 7:13 | 49.981
2021-11-03 | 7:13 | 49.98
2021-11-03 | 7:13 | 49.979
2021-11-03 | 7:13 | 49.978
2021-11-03 | 7:13 | 49.976
2021-11-03 | 7:13 | 49.976
2021-11-03 | 7:13 | 49.975
2021-11-03 | 7:13 | 49.974
2021-11-03 | 7:13 | 49.973
2021-11-03 | 7:13 | 49.972
2021-11-03 | 7:13 | 49.973
2021-11-03 | 7:13 | 49.975
2021-11-03 | 7:13 | 49.975
2021-11-03 | 7:13 | 49.976
2021-11-03 | 7:13 | 49.975
2021-11-03 | 7:13 | 49.974
2021-11-03 | 7:13 | 49.974
2021-11-03 | 7:13 | 49.975
2021-11-03 | 7:13 | 49.977
2021-11-03 | 7:13 | 49.979
2021-11-03 | 7:13 | 49.981
2021-11-03 | 7:14 | 49.981
2021-11-03 | 7:14 | 49.983
2021-11-03 | 7:14 | 49.984
2021-11-03 | 7:14 | 49.984
2021-11-03 | 7:14 | 49.983
2021-11-03 | 7:14 | 49.985
2021-11-03 | 7:14 | 49.985
2021-11-03 | 7:14 | 49.986
2021-11-03 | 7:14 | 49.983
2021-11-03 | 7:14 | 49.984
2021-11-03 | 7:14 | 49.985
2021-11-03 | 7:14 | 49.987
2021-11-03 | 7:14 | 49.987
2021-11-03 | 7:14 | 49.989
2021-11-03 | 7:14 | 49.99
2021-11-03 | 7:14 | 49.99
2021-11-03 | 7:14 | 49.988
2021-11-03 | 7:14 | 49.986
2021-11-03 | 7:14 | 49.986
2021-11-03 | 7:14 | 49.988
2021-11-03 | 7:14 | 49.989
2021-11-03 | 7:14 | 49.992
2021-11-03 | 7:14 | 49.992
2021-11-03 | 7:14 | 49.991
2021-11-03 | 7:14 | 49.989
2021-11-03 | 7:14 | 49.988
2021-11-03 | 7:14 | 49.987
2021-11-03 | 7:14 | 49.988
2021-11-03 | 7:14 | 49.987
2021-11-03 | 7:14 | 49.986
2021-11-03 | 7:14 | 49.985
2021-11-03 | 7:14 | 49.985
2021-11-03 | 7:14 | 49.985
2021-11-03 | 7:14 | 49.984
2021-11-03 | 7:14 | 49.985
2021-11-03 | 7:14 | 49.985
2021-11-03 | 7:14 | 49.986
2021-11-03 | 7:14 | 49.987
2021-11-03 | 7:14 | 49.989
2021-11-03 | 7:14 | 49.99
2021-11-03 | 7:14 | 49.992
2021-11-03 | 7:14 | 49.994
2021-11-03 | 7:14 | 49.996
2021-11-03 | 7:14 | 49.997
2021-11-03 | 7:14 | 49.997
2021-11-03 | 7:14 | 49.998
2021-11-03 | 7:14 | 49.997
2021-11-03 | 7:14 | 49.996
2021-11-03 | 7:14 | 49.993
2021-11-03 | 7:14 | 49.991
2021-11-03 | 7:14 | 49.989
2021-11-03 | 7:14 | 49.989
2021-11-03 | 7:14 | 49.989
2021-11-03 | 7:14 | 49.99
2021-11-03 | 7:14 | 49.991
2021-11-03 | 7:14 | 49.991
2021-11-03 | 7:14 | 49.992
2021-11-03 | 7:14 | 49.992
2021-11-03 | 7:14 | 49.993
2021-11-03 | 7:14 | 49.993
2021-11-03 | 7:14 | 49.993
2021-11-03 | 7:15 | 49.992
2021-11-03 | 7:15 | 49.992
2021-11-03 | 7:15 | 49.993
2021-11-03 | 7:15 | 49.995
2021-11-03 | 7:15 | 49.996
2021-11-03 | 7:15 | 49.997
2021-11-03 | 7:15 | 50.002
2021-11-03 | 7:15 | 50.009
2021-11-03 | 7:15 | 50.014
2021-11-03 | 7:15 | 50.018
2021-11-03 | 7:15 | 50.021
2021-11-03 | 7:15 | 50.023
2021-11-03 | 7:15 | 50.024
2021-11-03 | 7:15 | 50.024
2021-11-03 | 7:15 | 50.025
2021-11-03 | 7:15 | 50.025
2021-11-03 | 7:15 | 50.025
2021-11-03 | 7:15 | 50.026
2021-11-03 | 7:15 | 50.029
2021-11-03 | 7:15 | 50.036
2021-11-03 | 7:15 | 50.038
2021-11-03 | 7:15 | 50.04
2021-11-03 | 7:15 | 50.04
2021-11-03 | 7:15 | 50.041
2021-11-03 | 7:15 | 50.041
2021-11-03 | 7:15 | 50.042
2021-11-03 | 7:15 | 50.04
2021-11-03 | 7:15 | 50.039
2021-11-03 | 7:15 | 50.036

## F20211105-2
In GMT
Date | Time | Freq
2021-11-05 | 5:47 | 50.063
2021-11-05 | 5:47 | 50.064
2021-11-05 | 5:47 | 50.063
2021-11-05 | 5:47 | 50.064
2021-11-05 | 5:47 | 50.062
2021-11-05 | 5:47 | 50.064
2021-11-05 | 5:47 | 50.065
2021-11-05 | 5:47 | 50.066
2021-11-05 | 5:47 | 50.065
2021-11-05 | 5:47 | 50.065
2021-11-05 | 5:47 | 50.066
2021-11-05 | 5:47 | 50.065
2021-11-05 | 5:47 | 50.066
2021-11-05 | 5:47 | 50.067
2021-11-05 | 5:47 | 50.066
2021-11-05 | 5:47 | 50.066
2021-11-05 | 5:47 | 50.069
2021-11-05 | 5:47 | 50.07
2021-11-05 | 5:47 | 50.073
2021-11-05 | 5:47 | 50.075
2021-11-05 | 5:47 | 50.077
2021-11-05 | 5:47 | 50.081
2021-11-05 | 5:47 | 50.083
2021-11-05 | 5:47 | 50.084
2021-11-05 | 5:47 | 50.085
2021-11-05 | 5:47 | 50.087
2021-11-05 | 5:47 | 50.088
2021-11-05 | 5:47 | 50.089
2021-11-05 | 5:47 | 50.09
2021-11-05 | 5:47 | 50.09
2021-11-05 | 5:47 | 50.092
2021-11-05 | 5:48 | 50.093
2021-11-05 | 5:48 | 50.095
2021-11-05 | 5:48 | 50.096
2021-11-05 | 5:48 | 50.096
2021-11-05 | 5:48 | 50.098
2021-11-05 | 5:48 | 50.097
2021-11-05 | 5:48 | 50.096
2021-11-05 | 5:48 | 50.094
2021-11-05 | 5:48 | 50.092
2021-11-05 | 5:48 | 50.089
2021-11-05 | 5:48 | 50.087
2021-11-05 | 5:48 | 50.086
2021-11-05 | 5:48 | 50.084
2021-11-05 | 5:48 | 50.082
2021-11-05 | 5:48 | 50.081
2021-11-05 | 5:48 | 50.08
2021-11-05 | 5:48 | 50.077
2021-11-05 | 5:48 | 50.078
2021-11-05 | 5:48 | 50.077
2021-11-05 | 5:48 | 50.076
2021-11-05 | 5:48 | 50.076
2021-11-05 | 5:48 | 50.078
2021-11-05 | 5:48 | 50.081
2021-11-05 | 5:48 | 50.085
2021-11-05 | 5:48 | 50.086
2021-11-05 | 5:48 | 50.087
2021-11-05 | 5:48 | 50.088
2021-11-05 | 5:48 | 50.089
2021-11-05 | 5:48 | 50.089
2021-11-05 | 5:48 | 50.088
2021-11-05 | 5:48 | 50.088
2021-11-05 | 5:48 | 50.087
2021-11-05 | 5:48 | 50.085
2021-11-05 | 5:48 | 50.085
2021-11-05 | 5:48 | 50.085
2021-11-05 | 5:48 | 50.085
2021-11-05 | 5:48 | 50.084
2021-11-05 | 5:48 | 50.085
2021-11-05 | 5:48 | 50.085
2021-11-05 | 5:48 | 50.085
2021-11-05 | 5:48 | 50.086
2021-11-05 | 5:48 | 50.084
2021-11-05 | 5:48 | 50.084
2021-11-05 | 5:48 | 50.084
2021-11-05 | 5:48 | 50.085
2021-11-05 | 5:48 | 50.085
2021-11-05 | 5:48 | 50.085
2021-11-05 | 5:48 | 50.086
2021-11-05 | 5:48 | 50.09
2021-11-05 | 5:48 | 50.095
2021-11-05 | 5:48 | 50.099
2021-11-05 | 5:48 | 50.103
2021-11-05 | 5:48 | 50.107
2021-11-05 | 5:48 | 50.106
2021-11-05 | 5:48 | 50.104
2021-11-05 | 5:48 | 50.103
2021-11-05 | 5:48 | 50.104
2021-11-05 | 5:48 | 50.101
2021-11-05 | 5:48 | 50.101
2021-11-05 | 5:49 | 50.101
2021-11-05 | 5:49 | 50.099
2021-11-05 | 5:49 | 50.098
2021-11-05 | 5:49 | 50.096
2021-11-05 | 5:49 | 50.094
2021-11-05 | 5:49 | 50.092
2021-11-05 | 5:49 | 50.091
2021-11-05 | 5:49 | 50.092
2021-11-05 | 5:49 | 50.094
2021-11-05 | 5:49 | 50.096
2021-11-05 | 5:49 | 50.097
2021-11-05 | 5:49 | 50.098
2021-11-05 | 5:49 | 50.098
2021-11-05 | 5:49 | 50.099
2021-11-05 | 5:49 | 50.099
2021-11-05 | 5:49 | 50.098
2021-11-05 | 5:49 | 50.098
2021-11-05 | 5:49 | 50.098
2021-11-05 | 5:49 | 50.096
2021-11-05 | 5:49 | 50.095
2021-11-05 | 5:49 | 50.094
2021-11-05 | 5:49 | 50.092
2021-11-05 | 5:49 | 50.079
2021-11-05 | 5:49 | 50.067
2021-11-05 | 5:49 | 50.056
2021-11-05 | 5:49 | 50.046
2021-11-05 | 5:49 | 50.039
2021-11-05 | 5:49 | 50.037
2021-11-05 | 5:49 | 50.033
2021-11-05 | 5:49 | 50.029
2021-11-05 | 5:49 | 50.02
2021-11-05 | 5:49 | 50.012
2021-11-05 | 5:49 | 50.008
2021-11-05 | 5:49 | 50.007
2021-11-05 | 5:49 | 50.007
2021-11-05 | 5:49 | 50.008
2021-11-05 | 5:49 | 50.01
2021-11-05 | 5:49 | 50.011
2021-11-05 | 5:49 | 50.013
2021-11-05 | 5:49 | 50.015
2021-11-05 | 5:49 | 50.015
2021-11-05 | 5:49 | 50.017
2021-11-05 | 5:49 | 50.017
2021-11-05 | 5:49 | 50.016
2021-11-05 | 5:49 | 50.015
2021-11-05 | 5:49 | 50.015
2021-11-05 | 5:49 | 50.014
2021-11-05 | 5:49 | 50.013
2021-11-05 | 5:49 | 50.015
2021-11-05 | 5:49 | 50.017
2021-11-05 | 5:49 | 50.02
2021-11-05 | 5:49 | 50.023
2021-11-05 | 5:49 | 50.025
2021-11-05 | 5:49 | 50.025
2021-11-05 | 5:49 | 50.026
2021-11-05 | 5:49 | 50.026
2021-11-05 | 5:49 | 50.025
2021-11-05 | 5:49 | 50.025
2021-11-05 | 5:49 | 50.023
2021-11-05 | 5:49 | 50.023
2021-11-05 | 5:49 | 50.02
2021-11-05 | 5:50 | 50.02
2021-11-05 | 5:50 | 50.02
2021-11-05 | 5:50 | 50.017
2021-11-05 | 5:50 | 50.014
2021-11-05 | 5:50 | 50.012
2021-11-05 | 5:50 | 50.011
2021-11-05 | 5:50 | 50.01
2021-11-05 | 5:50 | 50.011
2021-11-05 | 5:50 | 50.011
2021-11-05 | 5:50 | 50.014
2021-11-05 | 5:50 | 50.016
2021-11-05 | 5:50 | 50.014
2021-11-05 | 5:50 | 50.013
2021-11-05 | 5:50 | 50.014
2021-11-05 | 5:50 | 50.014
2021-11-05 | 5:50 | 50.011
2021-11-05 | 5:50 | 50.01
2021-11-05 | 5:50 | 50.012
2021-11-05 | 5:50 | 50.014
2021-11-05 | 5:50 | 50.015
2021-11-05 | 5:50 | 50.016
2021-11-05 | 5:50 | 50.014
2021-11-05 | 5:50 | 50.013
2021-11-05 | 5:50 | 50.011
2021-11-05 | 5:50 | 50.011
2021-11-05 | 5:50 | 50.01
2021-11-05 | 5:50 | 50.009
2021-11-05 | 5:50 | 50.009
2021-11-05 | 5:50 | 50.007
2021-11-05 | 5:50 | 50.006
2021-11-05 | 5:50 | 50.004
2021-11-05 | 5:50 | 50.001
2021-11-05 | 5:50 | 50
2021-11-05 | 5:50 | 49.999
2021-11-05 | 5:50 | 50
2021-11-05 | 5:50 | 50.001
2021-11-05 | 5:50 | 50.003
2021-11-05 | 5:50 | 50.005
2021-11-05 | 5:50 | 50.006
2021-11-05 | 5:50 | 50.007
2021-11-05 | 5:50 | 50.008
2021-11-05 | 5:50 | 50.008
2021-11-05 | 5:50 | 50.007
2021-11-05 | 5:50 | 50.007
2021-11-05 | 5:50 | 50.007
2021-11-05 | 5:50 | 50.007
2021-11-05 | 5:50 | 50.006
2021-11-05 | 5:50 | 50.008
2021-11-05 | 5:50 | 50.01
2021-11-05 | 5:50 | 50.01
2021-11-05 | 5:50 | 50.01
2021-11-05 | 5:50 | 50.01
2021-11-05 | 5:50 | 50.011
2021-11-05 | 5:50 | 50.01
2021-11-05 | 5:50 | 50.009
2021-11-05 | 5:50 | 50.009
2021-11-05 | 5:50 | 50.007
2021-11-05 | 5:50 | 50.007
2021-11-05 | 5:50 | 50.011
2021-11-05 | 5:51 | 50.014
2021-11-05 | 5:51 | 50.015
2021-11-05 | 5:51 | 50.017
2021-11-05 | 5:51 | 50.017
2021-11-05 | 5:51 | 50.017
2021-11-05 | 5:51 | 50.016
2021-11-05 | 5:51 | 50.015
2021-11-05 | 5:51 | 50.015
2021-11-05 | 5:51 | 50.015
2021-11-05 | 5:51 | 50.016
2021-11-05 | 5:51 | 50.017
2021-11-05 | 5:51 | 50.016
2021-11-05 | 5:51 | 50.015
2021-11-05 | 5:51 | 50.015
2021-11-05 | 5:51 | 50.015
2021-11-05 | 5:51 | 50.013
2021-11-05 | 5:51 | 50.012
2021-11-05 | 5:51 | 50.01
2021-11-05 | 5:51 | 50.009
2021-11-05 | 5:51 | 50.009
2021-11-05 | 5:51 | 50.01
2021-11-05 | 5:51 | 50.011
2021-11-05 | 5:51 | 50.012
2021-11-05 | 5:51 | 50.014
2021-11-05 | 5:51 | 50.016
2021-11-05 | 5:51 | 50.017
2021-11-05 | 5:51 | 50.019
2021-11-05 | 5:51 | 50.019
2021-11-05 | 5:51 | 50.019
2021-11-05 | 5:51 | 50.021
2021-11-05 | 5:51 | 50.02
2021-11-05 | 5:51 | 50.018
2021-11-05 | 5:51 | 50.017
2021-11-05 | 5:51 | 50.016
2021-11-05 | 5:51 | 50.012
2021-11-05 | 5:51 | 50.01
2021-11-05 | 5:51 | 50.007
2021-11-05 | 5:51 | 50.006
2021-11-05 | 5:51 | 50.002
2021-11-05 | 5:51 | 50
2021-11-05 | 5:51 | 49.998
2021-11-05 | 5:51 | 49.996
2021-11-05 | 5:51 | 49.994
2021-11-05 | 5:51 | 49.994
2021-11-05 | 5:51 | 49.995
2021-11-05 | 5:51 | 49.995
2021-11-05 | 5:51 | 49.995
2021-11-05 | 5:51 | 49.997
2021-11-05 | 5:51 | 49.999
2021-11-05 | 5:51 | 50
2021-11-05 | 5:51 | 50.003
2021-11-05 | 5:51 | 50.005
2021-11-05 | 5:51 | 50.006
2021-11-05 | 5:51 | 50.007
2021-11-05 | 5:51 | 50.008
2021-11-05 | 5:51 | 50.006
2021-11-05 | 5:51 | 50.006
2021-11-05 | 5:51 | 50.005
2021-11-05 | 5:51 | 50.008
2021-11-05 | 5:51 | 50.01
2021-11-05 | 5:51 | 50.011
2021-11-05 | 5:52 | 50.011
2021-11-05 | 5:52 | 50.013
2021-11-05 | 5:52 | 50.014
2021-11-05 | 5:52 | 50.017
2021-11-05 | 5:52 | 50.019
2021-11-05 | 5:52 | 50.019
2021-11-05 | 5:52 | 50.019
2021-11-05 | 5:52 | 50.019
2021-11-05 | 5:52 | 50.019
2021-11-05 | 5:52 | 50.021
2021-11-05 | 5:52 | 50.021
2021-11-05 | 5:52 | 50.023
2021-11-05 | 5:52 | 50.024
2021-11-05 | 5:52 | 50.025
2021-11-05 | 5:52 | 50.026
2021-11-05 | 5:52 | 50.028
2021-11-05 | 5:52 | 50.027
2021-11-05 | 5:52 | 50.026
2021-11-05 | 5:52 | 50.025
2021-11-05 | 5:52 | 50.024
2021-11-05 | 5:52 | 50.027
2021-11-05 | 5:52 | 50.029
2021-11-05 | 5:52 | 50.028
2021-11-05 | 5:52 | 50.027
2021-11-05 | 5:52 | 50.026
2021-11-05 | 5:52 | 50.026
2021-11-05 | 5:52 | 50.026
2021-11-05 | 5:52 | 50.026
2021-11-05 | 5:52 | 50.028

## F20211109-1
In GMT
Date | Time | Freq
2021-11-09 | 17:27 | 50.036
2021-11-09 | 17:27 | 50.037
2021-11-09 | 17:27 | 50.038
2021-11-09 | 17:27 | 50.04
2021-11-09 | 17:27 | 50.037
2021-11-09 | 17:27 | 50.038
2021-11-09 | 17:27 | 50.037
2021-11-09 | 17:27 | 50.036
2021-11-09 | 17:27 | 50.034
2021-11-09 | 17:27 | 50.034
2021-11-09 | 17:27 | 50.035
2021-11-09 | 17:27 | 50.036
2021-11-09 | 17:27 | 50.037
2021-11-09 | 17:27 | 50.037
2021-11-09 | 17:27 | 50.035
2021-11-09 | 17:27 | 50.036
2021-11-09 | 17:27 | 50.033
2021-11-09 | 17:27 | 50.033
2021-11-09 | 17:27 | 50.032
2021-11-09 | 17:27 | 50.03
2021-11-09 | 17:27 | 50.032
2021-11-09 | 17:27 | 50.03
2021-11-09 | 17:27 | 50.029
2021-11-09 | 17:27 | 50.03
2021-11-09 | 17:27 | 50.029
2021-11-09 | 17:27 | 50.029
2021-11-09 | 17:27 | 50.029
2021-11-09 | 17:27 | 50.029
2021-11-09 | 17:27 | 50.029
2021-11-09 | 17:27 | 50.029
2021-11-09 | 17:28 | 50.028
2021-11-09 | 17:28 | 50.028
2021-11-09 | 17:28 | 50.027
2021-11-09 | 17:28 | 50.024
2021-11-09 | 17:28 | 50.025
2021-11-09 | 17:28 | 50.02
2021-11-09 | 17:28 | 50.017
2021-11-09 | 17:28 | 50.013
2021-11-09 | 17:28 | 50.011
2021-11-09 | 17:28 | 50.009
2021-11-09 | 17:28 | 50.009
2021-11-09 | 17:28 | 50.007
2021-11-09 | 17:28 | 50.007
2021-11-09 | 17:28 | 50.008
2021-11-09 | 17:28 | 50.009
2021-11-09 | 17:28 | 50.01
2021-11-09 | 17:28 | 50.015
2021-11-09 | 17:28 | 50.019
2021-11-09 | 17:28 | 50.022
2021-11-09 | 17:28 | 50.024
2021-11-09 | 17:28 | 50.028
2021-11-09 | 17:28 | 50.029
2021-11-09 | 17:28 | 50.029
2021-11-09 | 17:28 | 50.028
2021-11-09 | 17:28 | 50.029
2021-11-09 | 17:28 | 50.031
2021-11-09 | 17:28 | 50.032
2021-11-09 | 17:28 | 50.031
2021-11-09 | 17:28 | 50.034
2021-11-09 | 17:28 | 50.033
2021-11-09 | 17:28 | 50.033
2021-11-09 | 17:28 | 50.031
2021-11-09 | 17:28 | 50.029
2021-11-09 | 17:28 | 50.028
2021-11-09 | 17:28 | 50.028
2021-11-09 | 17:28 | 50.028
2021-11-09 | 17:28 | 50.028
2021-11-09 | 17:28 | 49.984
2021-11-09 | 17:28 | 49.941
2021-11-09 | 17:28 | 49.899
2021-11-09 | 17:28 | 49.866
2021-11-09 | 17:28 | 49.84
2021-11-09 | 17:28 | 49.819
2021-11-09 | 17:28 | 49.803
2021-11-09 | 17:28 | 49.788
2021-11-09 | 17:28 | 49.777
2021-11-09 | 17:28 | 49.769
2021-11-09 | 17:28 | 49.759
2021-11-09 | 17:28 | 49.753
2021-11-09 | 17:28 | 49.747
2021-11-09 | 17:28 | 49.744
2021-11-09 | 17:28 | 49.745
2021-11-09 | 17:28 | 49.746
2021-11-09 | 17:28 | 49.747
2021-11-09 | 17:28 | 49.749
2021-11-09 | 17:28 | 49.751
2021-11-09 | 17:28 | 49.754
2021-11-09 | 17:28 | 49.755
2021-11-09 | 17:28 | 49.756
2021-11-09 | 17:28 | 49.757
2021-11-09 | 17:28 | 49.755
2021-11-09 | 17:29 | 49.755
2021-11-09 | 17:29 | 49.754
2021-11-09 | 17:29 | 49.753
2021-11-09 | 17:29 | 49.751
2021-11-09 | 17:29 | 49.749
2021-11-09 | 17:29 | 49.749
2021-11-09 | 17:29 | 49.749
2021-11-09 | 17:29 | 49.75
2021-11-09 | 17:29 | 49.754
2021-11-09 | 17:29 | 49.757
2021-11-09 | 17:29 | 49.759
2021-11-09 | 17:29 | 49.764
2021-11-09 | 17:29 | 49.767
2021-11-09 | 17:29 | 49.77
2021-11-09 | 17:29 | 49.773
2021-11-09 | 17:29 | 49.773
2021-11-09 | 17:29 | 49.771
2021-11-09 | 17:29 | 49.769
2021-11-09 | 17:29 | 49.767
2021-11-09 | 17:29 | 49.767
2021-11-09 | 17:29 | 49.768
2021-11-09 | 17:29 | 49.767
2021-11-09 | 17:29 | 49.768
2021-11-09 | 17:29 | 49.768
2021-11-09 | 17:29 | 49.766
2021-11-09 | 17:29 | 49.764
2021-11-09 | 17:29 | 49.762
2021-11-09 | 17:29 | 49.759
2021-11-09 | 17:29 | 49.756
2021-11-09 | 17:29 | 49.753
2021-11-09 | 17:29 | 49.749
2021-11-09 | 17:29 | 49.749
2021-11-09 | 17:29 | 49.752
2021-11-09 | 17:29 | 49.756
2021-11-09 | 17:29 | 49.758
2021-11-09 | 17:29 | 49.755
2021-11-09 | 17:29 | 49.754
2021-11-09 | 17:29 | 49.749
2021-11-09 | 17:29 | 49.745
2021-11-09 | 17:29 | 49.744
2021-11-09 | 17:29 | 49.743
2021-11-09 | 17:29 | 49.74
2021-11-09 | 17:29 | 49.739
2021-11-09 | 17:29 | 49.737
2021-11-09 | 17:29 | 49.735
2021-11-09 | 17:29 | 49.736
2021-11-09 | 17:29 | 49.735
2021-11-09 | 17:29 | 49.739
2021-11-09 | 17:29 | 49.744
2021-11-09 | 17:29 | 49.754
2021-11-09 | 17:29 | 49.761
2021-11-09 | 17:29 | 49.769
2021-11-09 | 17:29 | 49.776
2021-11-09 | 17:29 | 49.784
2021-11-09 | 17:29 | 49.789
2021-11-09 | 17:29 | 49.795
2021-11-09 | 17:29 | 49.802
2021-11-09 | 17:29 | 49.808
2021-11-09 | 17:29 | 49.814
2021-11-09 | 17:30 | 49.818
2021-11-09 | 17:30 | 49.823
2021-11-09 | 17:30 | 49.83
2021-11-09 | 17:30 | 49.836
2021-11-09 | 17:30 | 49.842
2021-11-09 | 17:30 | 49.852
2021-11-09 | 17:30 | 49.862
2021-11-09 | 17:30 | 49.872
2021-11-09 | 17:30 | 49.88
2021-11-09 | 17:30 | 49.889
2021-11-09 | 17:30 | 49.895
2021-11-09 | 17:30 | 49.903
2021-11-09 | 17:30 | 49.908
2021-11-09 | 17:30 | 49.911
2021-11-09 | 17:30 | 49.913
2021-11-09 | 17:30 | 49.913
2021-11-09 | 17:30 | 49.913
2021-11-09 | 17:30 | 49.913
2021-11-09 | 17:30 | 49.914
2021-11-09 | 17:30 | 49.917
2021-11-09 | 17:30 | 49.918
2021-11-09 | 17:30 | 49.917
2021-11-09 | 17:30 | 49.915
2021-11-09 | 17:30 | 49.915
2021-11-09 | 17:30 | 49.913
2021-11-09 | 17:30 | 49.91
2021-11-09 | 17:30 | 49.907
2021-11-09 | 17:30 | 49.905
2021-11-09 | 17:30 | 49.903
2021-11-09 | 17:30 | 49.902
2021-11-09 | 17:30 | 49.898
2021-11-09 | 17:30 | 49.893
2021-11-09 | 17:30 | 49.888
2021-11-09 | 17:30 | 49.883
2021-11-09 | 17:30 | 49.88
2021-11-09 | 17:30 | 49.877
2021-11-09 | 17:30 | 49.877
2021-11-09 | 17:30 | 49.877
2021-11-09 | 17:30 | 49.877
2021-11-09 | 17:30 | 49.877
2021-11-09 | 17:30 | 49.879
2021-11-09 | 17:30 | 49.879
2021-11-09 | 17:30 | 49.879
2021-11-09 | 17:30 | 49.879
2021-11-09 | 17:30 | 49.876
2021-11-09 | 17:30 | 49.874
2021-11-09 | 17:30 | 49.872
2021-11-09 | 17:30 | 49.87
2021-11-09 | 17:30 | 49.869
2021-11-09 | 17:30 | 49.871
2021-11-09 | 17:30 | 49.876
2021-11-09 | 17:30 | 49.881
2021-11-09 | 17:30 | 49.886
2021-11-09 | 17:30 | 49.89
2021-11-09 | 17:30 | 49.894
2021-11-09 | 17:30 | 49.895
2021-11-09 | 17:30 | 49.898
2021-11-09 | 17:30 | 49.899
2021-11-09 | 17:30 | 49.9
2021-11-09 | 17:30 | 49.898
2021-11-09 | 17:31 | 49.9
2021-11-09 | 17:31 | 49.902
2021-11-09 | 17:31 | 49.901
2021-11-09 | 17:31 | 49.901
2021-11-09 | 17:31 | 49.902
2021-11-09 | 17:31 | 49.901
2021-11-09 | 17:31 | 49.9
2021-11-09 | 17:31 | 49.898
2021-11-09 | 17:31 | 49.899
2021-11-09 | 17:31 | 49.896
2021-11-09 | 17:31 | 49.896
2021-11-09 | 17:31 | 49.894
2021-11-09 | 17:31 | 49.89
2021-11-09 | 17:31 | 49.886
2021-11-09 | 17:31 | 49.882
2021-11-09 | 17:31 | 49.883
2021-11-09 | 17:31 | 49.884
2021-11-09 | 17:31 | 49.885
2021-11-09 | 17:31 | 49.887
2021-11-09 | 17:31 | 49.888
2021-11-09 | 17:31 | 49.889
2021-11-09 | 17:31 | 49.89
2021-11-09 | 17:31 | 49.889
2021-11-09 | 17:31 | 49.888
2021-11-09 | 17:31 | 49.887
2021-11-09 | 17:31 | 49.882
2021-11-09 | 17:31 | 49.878
2021-11-09 | 17:31 | 49.878
2021-11-09 | 17:31 | 49.878
2021-11-09 | 17:31 | 49.879
2021-11-09 | 17:31 | 49.879
2021-11-09 | 17:31 | 49.879
2021-11-09 | 17:31 | 49.878
2021-11-09 | 17:31 | 49.877
2021-11-09 | 17:31 | 49.878
2021-11-09 | 17:31 | 49.878
2021-11-09 | 17:31 | 49.878
2021-11-09 | 17:31 | 49.877
2021-11-09 | 17:31 | 49.873
2021-11-09 | 17:31 | 49.87
2021-11-09 | 17:31 | 49.866
2021-11-09 | 17:31 | 49.862
2021-11-09 | 17:31 | 49.86
2021-11-09 | 17:31 | 49.859
2021-11-09 | 17:31 | 49.857
2021-11-09 | 17:31 | 49.855
2021-11-09 | 17:31 | 49.856
2021-11-09 | 17:31 | 49.857
2021-11-09 | 17:31 | 49.857
2021-11-09 | 17:31 | 49.858
2021-11-09 | 17:31 | 49.859
2021-11-09 | 17:31 | 49.861
2021-11-09 | 17:31 | 49.862
2021-11-09 | 17:31 | 49.861
2021-11-09 | 17:31 | 49.862
2021-11-09 | 17:31 | 49.863
2021-11-09 | 17:31 | 49.864
2021-11-09 | 17:31 | 49.865
2021-11-09 | 17:31 | 49.865
2021-11-09 | 17:31 | 49.865
2021-11-09 | 17:31 | 49.865
2021-11-09 | 17:32 | 49.866
2021-11-09 | 17:32 | 49.868
2021-11-09 | 17:32 | 49.869
2021-11-09 | 17:32 | 49.87
2021-11-09 | 17:32 | 49.87
2021-11-09 | 17:32 | 49.87
2021-11-09 | 17:32 | 49.87
2021-11-09 | 17:32 | 49.869
2021-11-09 | 17:32 | 49.869
2021-11-09 | 17:32 | 49.871
2021-11-09 | 17:32 | 49.873
2021-11-09 | 17:32 | 49.874
2021-11-09 | 17:32 | 49.873
2021-11-09 | 17:32 | 49.874
2021-11-09 | 17:32 | 49.873
2021-11-09 | 17:32 | 49.872
2021-11-09 | 17:32 | 49.871
2021-11-09 | 17:32 | 49.871
2021-11-09 | 17:32 | 49.869
2021-11-09 | 17:32 | 49.868
2021-11-09 | 17:32 | 49.868
2021-11-09 | 17:32 | 49.869
2021-11-09 | 17:32 | 49.87
2021-11-09 | 17:32 | 49.869
2021-11-09 | 17:32 | 49.87
2021-11-09 | 17:32 | 49.869
2021-11-09 | 17:32 | 49.87
2021-11-09 | 17:32 | 49.867
2021-11-09 | 17:32 | 49.867
2021-11-09 | 17:32 | 49.866
2021-11-09 | 17:32 | 49.865
2021-11-09 | 17:32 | 49.862
2021-11-09 | 17:32 | 49.861
2021-11-09 | 17:32 | 49.858
2021-11-09 | 17:32 | 49.858
2021-11-09 | 17:32 | 49.855
2021-11-09 | 17:32 | 49.855
2021-11-09 | 17:32 | 49.852
2021-11-09 | 17:32 | 49.849
2021-11-09 | 17:32 | 49.846
2021-11-09 | 17:32 | 49.845
2021-11-09 | 17:32 | 49.841
2021-11-09 | 17:32 | 49.84
2021-11-09 | 17:32 | 49.836
2021-11-09 | 17:32 | 49.836
2021-11-09 | 17:32 | 49.836
2021-11-09 | 17:32 | 49.836
2021-11-09 | 17:32 | 49.838
2021-11-09 | 17:32 | 49.84
2021-11-09 | 17:32 | 49.841
2021-11-09 | 17:32 | 49.842
2021-11-09 | 17:32 | 49.843
2021-11-09 | 17:32 | 49.843
2021-11-09 | 17:32 | 49.844
2021-11-09 | 17:32 | 49.845
2021-11-09 | 17:32 | 49.844
2021-11-09 | 17:32 | 49.842
2021-11-09 | 17:32 | 49.842
2021-11-09 | 17:32 | 49.842
2021-11-09 | 17:33 | 49.841
2021-11-09 | 17:33 | 49.841
2021-11-09 | 17:33 | 49.839
2021-11-09 | 17:33 | 49.836
2021-11-09 | 17:33 | 49.834
2021-11-09 | 17:33 | 49.832
2021-11-09 | 17:33 | 49.831
2021-11-09 | 17:33 | 49.834
2021-11-09 | 17:33 | 49.835
2021-11-09 | 17:33 | 49.835
2021-11-09 | 17:33 | 49.837
2021-11-09 | 17:33 | 49.84
2021-11-09 | 17:33 | 49.842
2021-11-09 | 17:33 | 49.843
2021-11-09 | 17:33 | 49.846
2021-11-09 | 17:33 | 49.846
2021-11-09 | 17:33 | 49.846
2021-11-09 | 17:33 | 49.846
2021-11-09 | 17:33 | 49.846
2021-11-09 | 17:33 | 49.846
2021-11-09 | 17:33 | 49.845
2021-11-09 | 17:33 | 49.848
2021-11-09 | 17:33 | 49.851
2021-11-09 | 17:33 | 49.851
2021-11-09 | 17:33 | 49.853
2021-11-09 | 17:33 | 49.853
2021-11-09 | 17:33 | 49.853
2021-11-09 | 17:33 | 49.855
2021-11-09 | 17:33 | 49.857
2021-11-09 | 17:33 | 49.857
2021-11-09 | 17:33 | 49.861
2021-11-09 | 17:33 | 49.863
2021-11-09 | 17:33 | 49.866
2021-11-09 | 17:33 | 49.865
2021-11-09 | 17:33 | 49.867
2021-11-09 | 17:33 | 49.867
2021-11-09 | 17:33 | 49.869
2021-11-09 | 17:33 | 49.871
2021-11-09 | 17:33 | 49.872
2021-11-09 | 17:33 | 49.875
2021-11-09 | 17:33 | 49.873
2021-11-09 | 17:33 | 49.876
2021-11-09 | 17:33 | 49.876
2021-11-09 | 17:33 | 49.878
2021-11-09 | 17:33 | 49.879
2021-11-09 | 17:33 | 49.882
2021-11-09 | 17:33 | 49.883
2021-11-09 | 17:33 | 49.887
2021-11-09 | 17:33 | 49.888
2021-11-09 | 17:33 | 49.894
2021-11-09 | 17:33 | 49.895
2021-11-09 | 17:33 | 49.897
2021-11-09 | 17:33 | 49.898
2021-11-09 | 17:33 | 49.9
2021-11-09 | 17:33 | 49.9
2021-11-09 | 17:33 | 49.903
2021-11-09 | 17:33 | 49.903
2021-11-09 | 17:33 | 49.905
2021-11-09 | 17:33 | 49.906
2021-11-09 | 17:33 | 49.906
2021-11-09 | 17:33 | 49.909
2021-11-09 | 17:34 | 49.912
2021-11-09 | 17:34 | 49.915
2021-11-09 | 17:34 | 49.917
2021-11-09 | 17:34 | 49.918
2021-11-09 | 17:34 | 49.919
2021-11-09 | 17:34 | 49.918
2021-11-09 | 17:34 | 49.92
2021-11-09 | 17:34 | 49.919
2021-11-09 | 17:34 | 49.918
2021-11-09 | 17:34 | 49.92
2021-11-09 | 17:34 | 49.919
2021-11-09 | 17:34 | 49.921
2021-11-09 | 17:34 | 49.921
2021-11-09 | 17:34 | 49.922
2021-11-09 | 17:34 | 49.921
2021-11-09 | 17:34 | 49.923
2021-11-09 | 17:34 | 49.923
2021-11-09 | 17:34 | 49.925
2021-11-09 | 17:34 | 49.929
2021-11-09 | 17:34 | 49.93
2021-11-09 | 17:34 | 49.931
2021-11-09 | 17:34 | 49.934
2021-11-09 | 17:34 | 49.935
2021-11-09 | 17:34 | 49.934
2021-11-09 | 17:34 | 49.934
2021-11-09 | 17:34 | 49.935
2021-11-09 | 17:34 | 49.933
2021-11-09 | 17:34 | 49.932
2021-11-09 | 17:34 | 49.929
2021-11-09 | 17:34 | 49.93
2021-11-09 | 17:34 | 49.931
2021-11-09 | 17:34 | 49.931
2021-11-09 | 17:34 | 49.929
2021-11-09 | 17:34 | 49.927
2021-11-09 | 17:34 | 49.928
2021-11-09 | 17:34 | 49.928
2021-11-09 | 17:34 | 49.928
2021-11-09 | 17:34 | 49.93
2021-11-09 | 17:34 | 49.93
2021-11-09 | 17:34 | 49.936
2021-11-09 | 17:34 | 49.94
2021-11-09 | 17:34 | 49.944
2021-11-09 | 17:34 | 49.948
2021-11-09 | 17:34 | 49.947
2021-11-09 | 17:34 | 49.947
2021-11-09 | 17:34 | 49.947
2021-11-09 | 17:34 | 49.943
2021-11-09 | 17:34 | 49.943
2021-11-09 | 17:34 | 49.941
2021-11-09 | 17:34 | 49.939
2021-11-09 | 17:34 | 49.936
2021-11-09 | 17:34 | 49.933
2021-11-09 | 17:34 | 49.929
2021-11-09 | 17:34 | 49.924
2021-11-09 | 17:34 | 49.922
2021-11-09 | 17:34 | 49.921
2021-11-09 | 17:34 | 49.921
2021-11-09 | 17:34 | 49.921
2021-11-09 | 17:34 | 49.923
2021-11-09 | 17:35 | 49.926
2021-11-09 | 17:35 | 49.928
2021-11-09 | 17:35 | 49.93
2021-11-09 | 17:35 | 49.933
2021-11-09 | 17:35 | 49.932
2021-11-09 | 17:35 | 49.933
2021-11-09 | 17:35 | 49.931
2021-11-09 | 17:35 | 49.934
2021-11-09 | 17:35 | 49.936
2021-11-09 | 17:35 | 49.94
2021-11-09 | 17:35 | 49.943
2021-11-09 | 17:35 | 49.948
2021-11-09 | 17:35 | 49.948
2021-11-09 | 17:35 | 49.951
2021-11-09 | 17:35 | 49.953
2021-11-09 | 17:35 | 49.955
2021-11-09 | 17:35 | 49.957
2021-11-09 | 17:35 | 49.959
2021-11-09 | 17:35 | 49.959
2021-11-09 | 17:35 | 49.958
2021-11-09 | 17:35 | 49.959
2021-11-09 | 17:35 | 49.956
2021-11-09 | 17:35 | 49.955
2021-11-09 | 17:35 | 49.954
2021-11-09 | 17:35 | 49.956
2021-11-09 | 17:35 | 49.96
2021-11-09 | 17:35 | 49.964
2021-11-09 | 17:35 | 49.967
2021-11-09 | 17:35 | 49.968
2021-11-09 | 17:35 | 49.968
2021-11-09 | 17:35 | 49.971
2021-11-09 | 17:35 | 49.97
2021-11-09 | 17:35 | 49.967
2021-11-09 | 17:35 | 49.965
2021-11-09 | 17:35 | 49.961
2021-11-09 | 17:35 | 49.96
2021-11-09 | 17:35 | 49.956
2021-11-09 | 17:35 | 49.956
2021-11-09 | 17:35 | 49.955
2021-11-09 | 17:35 | 49.955
2021-11-09 | 17:35 | 49.96
2021-11-09 | 17:35 | 49.963
2021-11-09 | 17:35 | 49.969
2021-11-09 | 17:35 | 49.973
2021-11-09 | 17:35 | 49.978
2021-11-09 | 17:35 | 49.982
2021-11-09 | 17:35 | 49.988
2021-11-09 | 17:35 | 49.993
2021-11-09 | 17:35 | 49.996
2021-11-09 | 17:35 | 49.999
2021-11-09 | 17:35 | 50.004
2021-11-09 | 17:35 | 50.005
2021-11-09 | 17:35 | 50.006
2021-11-09 | 17:35 | 50.004
2021-11-09 | 17:35 | 50.005
2021-11-09 | 17:35 | 50.003
2021-11-09 | 17:35 | 50.003
2021-11-09 | 17:35 | 50.005
2021-11-09 | 17:35 | 50.004
2021-11-09 | 17:35 | 50.006
2021-11-09 | 17:35 | 50.008
2021-11-09 | 17:36 | 50.01
2021-11-09 | 17:36 | 50.01
2021-11-09 | 17:36 | 50.009
2021-11-09 | 17:36 | 50.01
2021-11-09 | 17:36 | 50.01
2021-11-09 | 17:36 | 50.009
2021-11-09 | 17:36 | 50.01
2021-11-09 | 17:36 | 50.011
2021-11-09 | 17:36 | 50.011
2021-11-09 | 17:36 | 50.012
2021-11-09 | 17:36 | 50.011
2021-11-09 | 17:36 | 50.009
2021-11-09 | 17:36 | 50.009
2021-11-09 | 17:36 | 50.007
2021-11-09 | 17:36 | 50.006
2021-11-09 | 17:36 | 50.004
2021-11-09 | 17:36 | 50.001
2021-11-09 | 17:36 | 49.999
2021-11-09 | 17:36 | 49.996
2021-11-09 | 17:36 | 49.994
2021-11-09 | 17:36 | 49.993
2021-11-09 | 17:36 | 49.992
2021-11-09 | 17:36 | 49.99
2021-11-09 | 17:36 | 49.989
2021-11-09 | 17:36 | 49.992
2021-11-09 | 17:36 | 49.992
2021-11-09 | 17:36 | 49.992
2021-11-09 | 17:36 | 49.993
2021-11-09 | 17:36 | 49.992

## F20211119-1
In GMT
Date | Time | Freq
2021-11-19 | 10:09 | 50.057
2021-11-19 | 10:09 | 50.057
2021-11-19 | 10:09 | 50.056
2021-11-19 | 10:09 | 50.057
2021-11-19 | 10:09 | 50.058
2021-11-19 | 10:09 | 50.058
2021-11-19 | 10:09 | 50.062
2021-11-19 | 10:09 | 50.063
2021-11-19 | 10:09 | 50.066
2021-11-19 | 10:09 | 50.065
2021-11-19 | 10:09 | 50.066
2021-11-19 | 10:09 | 50.065
2021-11-19 | 10:09 | 50.063
2021-11-19 | 10:09 | 50.062
2021-11-19 | 10:09 | 50.059
2021-11-19 | 10:09 | 50.056
2021-11-19 | 10:09 | 50.056
2021-11-19 | 10:09 | 50.056
2021-11-19 | 10:09 | 50.057
2021-11-19 | 10:09 | 50.059
2021-11-19 | 10:09 | 50.058
2021-11-19 | 10:09 | 50.058
2021-11-19 | 10:09 | 50.057
2021-11-19 | 10:09 | 50.059
2021-11-19 | 10:09 | 50.059
2021-11-19 | 10:09 | 50.061
2021-11-19 | 10:09 | 50.065
2021-11-19 | 10:09 | 50.069
2021-11-19 | 10:09 | 50.072
2021-11-19 | 10:09 | 50.075
2021-11-19 | 10:10 | 50.077
2021-11-19 | 10:10 | 50.076
2021-11-19 | 10:10 | 50.075
2021-11-19 | 10:10 | 50.075
2021-11-19 | 10:10 | 50.073
2021-11-19 | 10:10 | 50.075
2021-11-19 | 10:10 | 50.077
2021-11-19 | 10:10 | 50.077
2021-11-19 | 10:10 | 50.081
2021-11-19 | 10:10 | 50.081
2021-11-19 | 10:10 | 50.08
2021-11-19 | 10:10 | 50.082
2021-11-19 | 10:10 | 50.081
2021-11-19 | 10:10 | 50.082
2021-11-19 | 10:10 | 50.082
2021-11-19 | 10:10 | 50.081
2021-11-19 | 10:10 | 50.081
2021-11-19 | 10:10 | 50.078
2021-11-19 | 10:10 | 50.076
2021-11-19 | 10:10 | 50.073
2021-11-19 | 10:10 | 50.075
2021-11-19 | 10:10 | 50.073
2021-11-19 | 10:10 | 50.071
2021-11-19 | 10:10 | 50.068
2021-11-19 | 10:10 | 50.067
2021-11-19 | 10:10 | 50.066
2021-11-19 | 10:10 | 50.066
2021-11-19 | 10:10 | 50.067
2021-11-19 | 10:10 | 50.07
2021-11-19 | 10:10 | 50.072
2021-11-19 | 10:10 | 50.075
2021-11-19 | 10:10 | 50.075
2021-11-19 | 10:10 | 50.075
2021-11-19 | 10:10 | 50.075
2021-11-19 | 10:10 | 50.079
2021-11-19 | 10:10 | 50.063
2021-11-19 | 10:10 | 50.041
2021-11-19 | 10:10 | 50.024
2021-11-19 | 10:10 | 50.009
2021-11-19 | 10:10 | 50.001
2021-11-19 | 10:10 | 49.994
2021-11-19 | 10:10 | 49.99
2021-11-19 | 10:10 | 49.987
2021-11-19 | 10:10 | 49.986
2021-11-19 | 10:10 | 49.986
2021-11-19 | 10:10 | 49.987
2021-11-19 | 10:10 | 49.989
2021-11-19 | 10:10 | 49.989
2021-11-19 | 10:10 | 49.99
2021-11-19 | 10:10 | 49.99
2021-11-19 | 10:10 | 49.992
2021-11-19 | 10:10 | 49.994
2021-11-19 | 10:10 | 49.997
2021-11-19 | 10:10 | 49.998
2021-11-19 | 10:10 | 50.002
2021-11-19 | 10:10 | 50.001
2021-11-19 | 10:10 | 50
2021-11-19 | 10:10 | 50
2021-11-19 | 10:10 | 49.999
2021-11-19 | 10:10 | 50.002
2021-11-19 | 10:10 | 50.002
2021-11-19 | 10:11 | 50.004
2021-11-19 | 10:11 | 50.005
2021-11-19 | 10:11 | 50.009
2021-11-19 | 10:11 | 50.013
2021-11-19 | 10:11 | 50.016
2021-11-19 | 10:11 | 50.02
2021-11-19 | 10:11 | 50.026
2021-11-19 | 10:11 | 50.028
2021-11-19 | 10:11 | 50.031
2021-11-19 | 10:11 | 50.03
2021-11-19 | 10:11 | 50.032
2021-11-19 | 10:11 | 50.032
2021-11-19 | 10:11 | 50.032
2021-11-19 | 10:11 | 50.033
2021-11-19 | 10:11 | 50.034
2021-11-19 | 10:11 | 50.035
2021-11-19 | 10:11 | 50.033
2021-11-19 | 10:11 | 50.035
2021-11-19 | 10:11 | 50.033
2021-11-19 | 10:11 | 50.03
2021-11-19 | 10:11 | 50.026
2021-11-19 | 10:11 | 50.025
2021-11-19 | 10:11 | 50.022
2021-11-19 | 10:11 | 50.02
2021-11-19 | 10:11 | 50.018
2021-11-19 | 10:11 | 50.016
2021-11-19 | 10:11 | 50.018
2021-11-19 | 10:11 | 50.019
2021-11-19 | 10:11 | 50.02
2021-11-19 | 10:11 | 50.017
2021-11-19 | 10:11 | 50.018
2021-11-19 | 10:11 | 50.018
2021-11-19 | 10:11 | 50.019
2021-11-19 | 10:11 | 50.02
2021-11-19 | 10:11 | 50.02
2021-11-19 | 10:11 | 50.019
2021-11-19 | 10:11 | 50.018
2021-11-19 | 10:11 | 50.016
2021-11-19 | 10:11 | 50.011
2021-11-19 | 10:11 | 50.009
2021-11-19 | 10:11 | 50.007
2021-11-19 | 10:11 | 50.008
2021-11-19 | 10:11 | 50.006
2021-11-19 | 10:11 | 50.005
2021-11-19 | 10:11 | 50.006
2021-11-19 | 10:11 | 50.006
2021-11-19 | 10:11 | 50.006
2021-11-19 | 10:11 | 50.005
2021-11-19 | 10:11 | 50.006
2021-11-19 | 10:11 | 50.006
2021-11-19 | 10:11 | 50.009
2021-11-19 | 10:11 | 50.011
2021-11-19 | 10:11 | 50.009
2021-11-19 | 10:11 | 50.007
2021-11-19 | 10:11 | 50.004
2021-11-19 | 10:11 | 50.005
2021-11-19 | 10:11 | 50.009
2021-11-19 | 10:11 | 50.014
2021-11-19 | 10:11 | 50.019
2021-11-19 | 10:12 | 50.024
2021-11-19 | 10:12 | 50.029
2021-11-19 | 10:12 | 50.034
2021-11-19 | 10:12 | 50.035
2021-11-19 | 10:12 | 50.038
2021-11-19 | 10:12 | 50.039
2021-11-19 | 10:12 | 50.042
2021-11-19 | 10:12 | 50.044
2021-11-19 | 10:12 | 50.046
2021-11-19 | 10:12 | 50.048
2021-11-19 | 10:12 | 50.047
2021-11-19 | 10:12 | 50.041
2021-11-19 | 10:12 | 50.037
2021-11-19 | 10:12 | 50.035
2021-11-19 | 10:12 | 50.032
2021-11-19 | 10:12 | 50.035
2021-11-19 | 10:12 | 50.034
2021-11-19 | 10:12 | 50.035
2021-11-19 | 10:12 | 50.039
2021-11-19 | 10:12 | 50.039
2021-11-19 | 10:12 | 50.039
2021-11-19 | 10:12 | 50.041
2021-11-19 | 10:12 | 50.038
2021-11-19 | 10:12 | 50.038
2021-11-19 | 10:12 | 50.032
2021-11-19 | 10:12 | 50.029
2021-11-19 | 10:12 | 50.025
2021-11-19 | 10:12 | 50.021
2021-11-19 | 10:12 | 50.02
2021-11-19 | 10:12 | 50.023
2021-11-19 | 10:12 | 50.025
2021-11-19 | 10:12 | 50.025
2021-11-19 | 10:12 | 50.028
2021-11-19 | 10:12 | 50.03
2021-11-19 | 10:12 | 50.032
2021-11-19 | 10:12 | 50.036
2021-11-19 | 10:12 | 50.04
2021-11-19 | 10:12 | 50.041
2021-11-19 | 10:12 | 50.044
2021-11-19 | 10:12 | 50.045
2021-11-19 | 10:12 | 50.045
2021-11-19 | 10:12 | 50.05
2021-11-19 | 10:12 | 50.054
2021-11-19 | 10:12 | 50.058
2021-11-19 | 10:12 | 50.062
2021-11-19 | 10:12 | 50.063
2021-11-19 | 10:12 | 50.062
2021-11-19 | 10:12 | 50.061
2021-11-19 | 10:12 | 50.06
2021-11-19 | 10:12 | 50.061
2021-11-19 | 10:12 | 50.06
2021-11-19 | 10:12 | 50.06
2021-11-19 | 10:12 | 50.062
2021-11-19 | 10:12 | 50.062
2021-11-19 | 10:12 | 50.062
2021-11-19 | 10:12 | 50.059
2021-11-19 | 10:12 | 50.061
2021-11-19 | 10:12 | 50.06
2021-11-19 | 10:12 | 50.064
2021-11-19 | 10:12 | 50.065
2021-11-19 | 10:12 | 50.066
2021-11-19 | 10:13 | 50.069
2021-11-19 | 10:13 | 50.069
2021-11-19 | 10:13 | 50.068
2021-11-19 | 10:13 | 50.067
2021-11-19 | 10:13 | 50.063
2021-11-19 | 10:13 | 50.061
2021-11-19 | 10:13 | 50.058
2021-11-19 | 10:13 | 50.057
2021-11-19 | 10:13 | 50.054
2021-11-19 | 10:13 | 50.053
2021-11-19 | 10:13 | 50.052
2021-11-19 | 10:13 | 50.053
2021-11-19 | 10:13 | 50.055
2021-11-19 | 10:13 | 50.055
2021-11-19 | 10:13 | 50.058
2021-11-19 | 10:13 | 50.06
2021-11-19 | 10:13 | 50.06
2021-11-19 | 10:13 | 50.063
2021-11-19 | 10:13 | 50.065
2021-11-19 | 10:13 | 50.066
2021-11-19 | 10:13 | 50.067
2021-11-19 | 10:13 | 50.065
2021-11-19 | 10:13 | 50.064
2021-11-19 | 10:13 | 50.064
2021-11-19 | 10:13 | 50.063
2021-11-19 | 10:13 | 50.062
2021-11-19 | 10:13 | 50.062
2021-11-19 | 10:13 | 50.059
2021-11-19 | 10:13 | 50.057
2021-11-19 | 10:13 | 50.054
2021-11-19 | 10:13 | 50.052
2021-11-19 | 10:13 | 50.051
2021-11-19 | 10:13 | 50.048
2021-11-19 | 10:13 | 50.046
2021-11-19 | 10:13 | 50.045
2021-11-19 | 10:13 | 50.043
2021-11-19 | 10:13 | 50.043
2021-11-19 | 10:13 | 50.04
2021-11-19 | 10:13 | 50.037
2021-11-19 | 10:13 | 50.036
2021-11-19 | 10:13 | 50.036
2021-11-19 | 10:13 | 50.034
2021-11-19 | 10:13 | 50.033
2021-11-19 | 10:13 | 50.033
2021-11-19 | 10:13 | 50.034
2021-11-19 | 10:13 | 50.036
2021-11-19 | 10:13 | 50.036
2021-11-19 | 10:13 | 50.036
2021-11-19 | 10:13 | 50.035
2021-11-19 | 10:13 | 50.035
2021-11-19 | 10:13 | 50.035
2021-11-19 | 10:13 | 50.035
2021-11-19 | 10:13 | 50.038
2021-11-19 | 10:13 | 50.038
2021-11-19 | 10:13 | 50.04
2021-11-19 | 10:13 | 50.043
2021-11-19 | 10:13 | 50.046
2021-11-19 | 10:13 | 50.047
2021-11-19 | 10:13 | 50.047
2021-11-19 | 10:14 | 50.047
2021-11-19 | 10:14 | 50.046
2021-11-19 | 10:14 | 50.046
2021-11-19 | 10:14 | 50.046
2021-11-19 | 10:14 | 50.043
2021-11-19 | 10:14 | 50.041
2021-11-19 | 10:14 | 50.039
2021-11-19 | 10:14 | 50.036
2021-11-19 | 10:14 | 50.036
2021-11-19 | 10:14 | 50.035
2021-11-19 | 10:14 | 50.031
2021-11-19 | 10:14 | 50.029
2021-11-19 | 10:14 | 50.026
2021-11-19 | 10:14 | 50.024
2021-11-19 | 10:14 | 50.02
2021-11-19 | 10:14 | 50.017
2021-11-19 | 10:14 | 50.016
2021-11-19 | 10:14 | 50.014
2021-11-19 | 10:14 | 50.015
2021-11-19 | 10:14 | 50.016
2021-11-19 | 10:14 | 50.016
2021-11-19 | 10:14 | 50.016
2021-11-19 | 10:14 | 50.013
2021-11-19 | 10:14 | 50.015
2021-11-19 | 10:14 | 50.017
2021-11-19 | 10:14 | 50.019
2021-11-19 | 10:14 | 50.021
2021-11-19 | 10:14 | 50.02
2021-11-19 | 10:14 | 50.02
2021-11-19 | 10:14 | 50.02
2021-11-19 | 10:14 | 50.019
2021-11-19 | 10:14 | 50.014
2021-11-19 | 10:14 | 50.008
2021-11-19 | 10:14 | 50.007
2021-11-19 | 10:14 | 50.009
2021-11-19 | 10:14 | 50.011
2021-11-19 | 10:14 | 50.015
2021-11-19 | 10:14 | 50.019
2021-11-19 | 10:14 | 50.02
2021-11-19 | 10:14 | 50.022
2021-11-19 | 10:14 | 50.023
2021-11-19 | 10:14 | 50.025
2021-11-19 | 10:14 | 50.023
2021-11-19 | 10:14 | 50.023
2021-11-19 | 10:14 | 50.02
2021-11-19 | 10:14 | 50.015
2021-11-19 | 10:14 | 50.013
2021-11-19 | 10:14 | 50.014
2021-11-19 | 10:14 | 50.016
2021-11-19 | 10:14 | 50.018
2021-11-19 | 10:14 | 50.02
2021-11-19 | 10:14 | 50.022
2021-11-19 | 10:14 | 50.023
2021-11-19 | 10:14 | 50.026
2021-11-19 | 10:14 | 50.028
2021-11-19 | 10:14 | 50.029
2021-11-19 | 10:14 | 50.029
2021-11-19 | 10:14 | 50.031
2021-11-19 | 10:14 | 50.033
2021-11-19 | 10:14 | 50.035
2021-11-19 | 10:14 | 50.035
2021-11-19 | 10:15 | 50.033
2021-11-19 | 10:15 | 50.033
2021-11-19 | 10:15 | 50.028
2021-11-19 | 10:15 | 50.027
2021-11-19 | 10:15 | 50.026
2021-11-19 | 10:15 | 50.025
2021-11-19 | 10:15 | 50.025
2021-11-19 | 10:15 | 50.026
2021-11-19 | 10:15 | 50.029
2021-11-19 | 10:15 | 50.032
2021-11-19 | 10:15 | 50.035
2021-11-19 | 10:15 | 50.035
2021-11-19 | 10:15 | 50.032
2021-11-19 | 10:15 | 50.028
2021-11-19 | 10:15 | 50.027
2021-11-19 | 10:15 | 50.026
2021-11-19 | 10:15 | 50.024
2021-11-19 | 10:15 | 50.021
2021-11-19 | 10:15 | 50.019
2021-11-19 | 10:15 | 50.013
2021-11-19 | 10:15 | 50.009
2021-11-19 | 10:15 | 50.007
2021-11-19 | 10:15 | 50.007
2021-11-19 | 10:15 | 50.007
2021-11-19 | 10:15 | 50.008
2021-11-19 | 10:15 | 50.009
2021-11-19 | 10:15 | 50.011
2021-11-19 | 10:15 | 50.014
2021-11-19 | 10:15 | 50.018

## F20211119-2
In GMT
Date | Time | Freq
2021-11-19 | 10:17 | 50.023
2021-11-19 | 10:17 | 50.021
2021-11-19 | 10:17 | 50.018
2021-11-19 | 10:17 | 50.016
2021-11-19 | 10:17 | 50.015
2021-11-19 | 10:17 | 50.013
2021-11-19 | 10:17 | 50.012
2021-11-19 | 10:17 | 50.012
2021-11-19 | 10:17 | 50.013
2021-11-19 | 10:17 | 50.013
2021-11-19 | 10:17 | 50.015
2021-11-19 | 10:17 | 50.019
2021-11-19 | 10:17 | 50.023
2021-11-19 | 10:17 | 50.026
2021-11-19 | 10:17 | 50.028
2021-11-19 | 10:17 | 50.032
2021-11-19 | 10:17 | 50.034
2021-11-19 | 10:17 | 50.034
2021-11-19 | 10:17 | 50.033
2021-11-19 | 10:17 | 50.032
2021-11-19 | 10:17 | 50.031
2021-11-19 | 10:17 | 50.029
2021-11-19 | 10:17 | 50.029
2021-11-19 | 10:17 | 50.03
2021-11-19 | 10:17 | 50.028
2021-11-19 | 10:17 | 50.026
2021-11-19 | 10:17 | 50.027
2021-11-19 | 10:17 | 50.028
2021-11-19 | 10:17 | 50.029
2021-11-19 | 10:17 | 50.03
2021-11-19 | 10:17 | 50.03
2021-11-19 | 10:18 | 50.031
2021-11-19 | 10:18 | 50.035
2021-11-19 | 10:18 | 50.04
2021-11-19 | 10:18 | 50.043
2021-11-19 | 10:18 | 50.044
2021-11-19 | 10:18 | 50.045
2021-11-19 | 10:18 | 50.047
2021-11-19 | 10:18 | 50.048
2021-11-19 | 10:18 | 50.047
2021-11-19 | 10:18 | 50.047
2021-11-19 | 10:18 | 50.046
2021-11-19 | 10:18 | 50.042
2021-11-19 | 10:18 | 50.04
2021-11-19 | 10:18 | 50.037
2021-11-19 | 10:18 | 50.033
2021-11-19 | 10:18 | 50.027
2021-11-19 | 10:18 | 50.023
2021-11-19 | 10:18 | 50.019
2021-11-19 | 10:18 | 50.018
2021-11-19 | 10:18 | 50.019
2021-11-19 | 10:18 | 50.023
2021-11-19 | 10:18 | 50.027
2021-11-19 | 10:18 | 50.031
2021-11-19 | 10:18 | 50.034
2021-11-19 | 10:18 | 50.037
2021-11-19 | 10:18 | 50.039
2021-11-19 | 10:18 | 50.039
2021-11-19 | 10:18 | 50.038
2021-11-19 | 10:18 | 50.037
2021-11-19 | 10:18 | 50.035
2021-11-19 | 10:18 | 50.033
2021-11-19 | 10:18 | 50.033
2021-11-19 | 10:18 | 50.035
2021-11-19 | 10:18 | 50.036
2021-11-19 | 10:18 | 50.036
2021-11-19 | 10:18 | 50.035
2021-11-19 | 10:18 | 50.033
2021-11-19 | 10:18 | 50.029
2021-11-19 | 10:18 | 50.028
2021-11-19 | 10:18 | 50.027
2021-11-19 | 10:18 | 50.024
2021-11-19 | 10:18 | 50.024
2021-11-19 | 10:18 | 50.024
2021-11-19 | 10:18 | 50.025
2021-11-19 | 10:18 | 50.025
2021-11-19 | 10:18 | 50.028
2021-11-19 | 10:18 | 50.028
2021-11-19 | 10:18 | 50.028
2021-11-19 | 10:18 | 50.027
2021-11-19 | 10:18 | 50.028
2021-11-19 | 10:18 | 50.029
2021-11-19 | 10:18 | 50.029
2021-11-19 | 10:18 | 50.03
2021-11-19 | 10:18 | 50.03
2021-11-19 | 10:18 | 50.028
2021-11-19 | 10:18 | 50.028
2021-11-19 | 10:18 | 50.028
2021-11-19 | 10:18 | 50.026
2021-11-19 | 10:18 | 50.025
2021-11-19 | 10:19 | 50.023
2021-11-19 | 10:19 | 50.023
2021-11-19 | 10:19 | 50.021
2021-11-19 | 10:19 | 50.02
2021-11-19 | 10:19 | 50.062
2021-11-19 | 10:19 | 50.13
2021-11-19 | 10:19 | 50.191
2021-11-19 | 10:19 | 50.232
2021-11-19 | 10:19 | 50.256
2021-11-19 | 10:19 | 50.269
2021-11-19 | 10:19 | 50.271
2021-11-19 | 10:19 | 50.272
2021-11-19 | 10:19 | 50.269
2021-11-19 | 10:19 | 50.268
2021-11-19 | 10:19 | 50.263
2021-11-19 | 10:19 | 50.257
2021-11-19 | 10:19 | 50.252
2021-11-19 | 10:19 | 50.249
2021-11-19 | 10:19 | 50.247
2021-11-19 | 10:19 | 50.244
2021-11-19 | 10:19 | 50.24
2021-11-19 | 10:19 | 50.237
2021-11-19 | 10:19 | 50.235
2021-11-19 | 10:19 | 50.235
2021-11-19 | 10:19 | 50.234
2021-11-19 | 10:19 | 50.23
2021-11-19 | 10:19 | 50.228
2021-11-19 | 10:19 | 50.226
2021-11-19 | 10:19 | 50.223
2021-11-19 | 10:19 | 50.223
2021-11-19 | 10:19 | 50.223
2021-11-19 | 10:19 | 50.223
2021-11-19 | 10:19 | 50.224
2021-11-19 | 10:19 | 50.228
2021-11-19 | 10:19 | 50.23
2021-11-19 | 10:19 | 50.231
2021-11-19 | 10:19 | 50.232
2021-11-19 | 10:19 | 50.23
2021-11-19 | 10:19 | 50.229
2021-11-19 | 10:19 | 50.227
2021-11-19 | 10:19 | 50.226
2021-11-19 | 10:19 | 50.226
2021-11-19 | 10:19 | 50.227
2021-11-19 | 10:19 | 50.227
2021-11-19 | 10:19 | 50.229
2021-11-19 | 10:19 | 50.229
2021-11-19 | 10:19 | 50.227
2021-11-19 | 10:19 | 50.227
2021-11-19 | 10:19 | 50.226
2021-11-19 | 10:19 | 50.225
2021-11-19 | 10:19 | 50.225
2021-11-19 | 10:19 | 50.224
2021-11-19 | 10:19 | 50.223
2021-11-19 | 10:19 | 50.222
2021-11-19 | 10:19 | 50.224
2021-11-19 | 10:19 | 50.227
2021-11-19 | 10:19 | 50.231
2021-11-19 | 10:19 | 50.233
2021-11-19 | 10:19 | 50.237
2021-11-19 | 10:19 | 50.237
2021-11-19 | 10:19 | 50.24
2021-11-19 | 10:20 | 50.243
2021-11-19 | 10:20 | 50.245
2021-11-19 | 10:20 | 50.249
2021-11-19 | 10:20 | 50.251
2021-11-19 | 10:20 | 50.252
2021-11-19 | 10:20 | 50.254
2021-11-19 | 10:20 | 50.258
2021-11-19 | 10:20 | 50.258
2021-11-19 | 10:20 | 50.258
2021-11-19 | 10:20 | 50.258
2021-11-19 | 10:20 | 50.257
2021-11-19 | 10:20 | 50.258
2021-11-19 | 10:20 | 50.258
2021-11-19 | 10:20 | 50.259
2021-11-19 | 10:20 | 50.257
2021-11-19 | 10:20 | 50.256
2021-11-19 | 10:20 | 50.257
2021-11-19 | 10:20 | 50.26
2021-11-19 | 10:20 | 50.261
2021-11-19 | 10:20 | 50.263
2021-11-19 | 10:20 | 50.267
2021-11-19 | 10:20 | 50.267
2021-11-19 | 10:20 | 50.266
2021-11-19 | 10:20 | 50.266
2021-11-19 | 10:20 | 50.265
2021-11-19 | 10:20 | 50.267
2021-11-19 | 10:20 | 50.269
2021-11-19 | 10:20 | 50.273
2021-11-19 | 10:20 | 50.277
2021-11-19 | 10:20 | 50.278
2021-11-19 | 10:20 | 50.277
2021-11-19 | 10:20 | 50.276
2021-11-19 | 10:20 | 50.278
2021-11-19 | 10:20 | 50.276
2021-11-19 | 10:20 | 50.272
2021-11-19 | 10:20 | 50.271
2021-11-19 | 10:20 | 50.268
2021-11-19 | 10:20 | 50.269
2021-11-19 | 10:20 | 50.272
2021-11-19 | 10:20 | 50.275
2021-11-19 | 10:20 | 50.278
2021-11-19 | 10:20 | 50.281
2021-11-19 | 10:20 | 50.283
2021-11-19 | 10:20 | 50.286
2021-11-19 | 10:20 | 50.287
2021-11-19 | 10:20 | 50.29
2021-11-19 | 10:20 | 50.29
2021-11-19 | 10:20 | 50.29
2021-11-19 | 10:20 | 50.288
2021-11-19 | 10:20 | 50.288
2021-11-19 | 10:20 | 50.287
2021-11-19 | 10:20 | 50.283
2021-11-19 | 10:20 | 50.28
2021-11-19 | 10:20 | 50.278
2021-11-19 | 10:20 | 50.275
2021-11-19 | 10:20 | 50.272
2021-11-19 | 10:20 | 50.272
2021-11-19 | 10:20 | 50.271
2021-11-19 | 10:20 | 50.271
2021-11-19 | 10:21 | 50.271
2021-11-19 | 10:21 | 50.272
2021-11-19 | 10:21 | 50.274
2021-11-19 | 10:21 | 50.276
2021-11-19 | 10:21 | 50.278
2021-11-19 | 10:21 | 50.279
2021-11-19 | 10:21 | 50.282
2021-11-19 | 10:21 | 50.282
2021-11-19 | 10:21 | 50.279
2021-11-19 | 10:21 | 50.28
2021-11-19 | 10:21 | 50.28
2021-11-19 | 10:21 | 50.281
2021-11-19 | 10:21 | 50.283
2021-11-19 | 10:21 | 50.283
2021-11-19 | 10:21 | 50.284
2021-11-19 | 10:21 | 50.285
2021-11-19 | 10:21 | 50.286
2021-11-19 | 10:21 | 50.284
2021-11-19 | 10:21 | 50.284
2021-11-19 | 10:21 | 50.282
2021-11-19 | 10:21 | 50.282
2021-11-19 | 10:21 | 50.284
2021-11-19 | 10:21 | 50.287
2021-11-19 | 10:21 | 50.287
2021-11-19 | 10:21 | 50.286
2021-11-19 | 10:21 | 50.283
2021-11-19 | 10:21 | 50.278
2021-11-19 | 10:21 | 50.273
2021-11-19 | 10:21 | 50.271
2021-11-19 | 10:21 | 50.268
2021-11-19 | 10:21 | 50.267
2021-11-19 | 10:21 | 50.266
2021-11-19 | 10:21 | 50.266
2021-11-19 | 10:21 | 50.266
2021-11-19 | 10:21 | 50.268
2021-11-19 | 10:21 | 50.268
2021-11-19 | 10:21 | 50.267
2021-11-19 | 10:21 | 50.266
2021-11-19 | 10:21 | 50.267
2021-11-19 | 10:21 | 50.267
2021-11-19 | 10:21 | 50.268
2021-11-19 | 10:21 | 50.27
2021-11-19 | 10:21 | 50.271
2021-11-19 | 10:21 | 50.271
2021-11-19 | 10:21 | 50.272
2021-11-19 | 10:21 | 50.271
2021-11-19 | 10:21 | 50.272
2021-11-19 | 10:21 | 50.27
2021-11-19 | 10:21 | 50.268
2021-11-19 | 10:21 | 50.267
2021-11-19 | 10:21 | 50.262
2021-11-19 | 10:21 | 50.261
2021-11-19 | 10:21 | 50.261
2021-11-19 | 10:21 | 50.259
2021-11-19 | 10:21 | 50.258
2021-11-19 | 10:21 | 50.26
2021-11-19 | 10:21 | 50.26
2021-11-19 | 10:21 | 50.261
2021-11-19 | 10:21 | 50.262
2021-11-19 | 10:21 | 50.261
2021-11-19 | 10:21 | 50.264
2021-11-19 | 10:22 | 50.266
2021-11-19 | 10:22 | 50.269
2021-11-19 | 10:22 | 50.273
2021-11-19 | 10:22 | 50.276
2021-11-19 | 10:22 | 50.276
2021-11-19 | 10:22 | 50.276
2021-11-19 | 10:22 | 50.273
2021-11-19 | 10:22 | 50.273
2021-11-19 | 10:22 | 50.273
2021-11-19 | 10:22 | 50.274
2021-11-19 | 10:22 | 50.275
2021-11-19 | 10:22 | 50.275
2021-11-19 | 10:22 | 50.275
2021-11-19 | 10:22 | 50.275
2021-11-19 | 10:22 | 50.277
2021-11-19 | 10:22 | 50.276
2021-11-19 | 10:22 | 50.274
2021-11-19 | 10:22 | 50.27
2021-11-19 | 10:22 | 50.27
2021-11-19 | 10:22 | 50.271
2021-11-19 | 10:22 | 50.272
2021-11-19 | 10:22 | 50.27
2021-11-19 | 10:22 | 50.274
2021-11-19 | 10:22 | 50.274
2021-11-19 | 10:22 | 50.276
2021-11-19 | 10:22 | 50.273
2021-11-19 | 10:22 | 50.268
2021-11-19 | 10:22 | 50.265
2021-11-19 | 10:22 | 50.263
2021-11-19 | 10:22 | 50.262
2021-11-19 | 10:22 | 50.261
2021-11-19 | 10:22 | 50.258
2021-11-19 | 10:22 | 50.255
2021-11-19 | 10:22 | 50.252
2021-11-19 | 10:22 | 50.252
2021-11-19 | 10:22 | 50.254
2021-11-19 | 10:22 | 50.256
2021-11-19 | 10:22 | 50.257
2021-11-19 | 10:22 | 50.258
2021-11-19 | 10:22 | 50.258
2021-11-19 | 10:22 | 50.256
2021-11-19 | 10:22 | 50.257
2021-11-19 | 10:22 | 50.259
2021-11-19 | 10:22 | 50.259
2021-11-19 | 10:22 | 50.263
2021-11-19 | 10:22 | 50.263
2021-11-19 | 10:22 | 50.265
2021-11-19 | 10:22 | 50.262
2021-11-19 | 10:22 | 50.263
2021-11-19 | 10:22 | 50.261
2021-11-19 | 10:22 | 50.259
2021-11-19 | 10:22 | 50.256
2021-11-19 | 10:22 | 50.253
2021-11-19 | 10:22 | 50.249
2021-11-19 | 10:22 | 50.249
2021-11-19 | 10:22 | 50.248
2021-11-19 | 10:22 | 50.247
2021-11-19 | 10:22 | 50.247
2021-11-19 | 10:22 | 50.245
2021-11-19 | 10:23 | 50.241
2021-11-19 | 10:23 | 50.24
2021-11-19 | 10:23 | 50.234
2021-11-19 | 10:23 | 50.23
2021-11-19 | 10:23 | 50.228
2021-11-19 | 10:23 | 50.225
2021-11-19 | 10:23 | 50.225
2021-11-19 | 10:23 | 50.223
2021-11-19 | 10:23 | 50.224
2021-11-19 | 10:23 | 50.224
2021-11-19 | 10:23 | 50.225
2021-11-19 | 10:23 | 50.225
2021-11-19 | 10:23 | 50.22
2021-11-19 | 10:23 | 50.215
2021-11-19 | 10:23 | 50.207
2021-11-19 | 10:23 | 50.201
2021-11-19 | 10:23 | 50.196
2021-11-19 | 10:23 | 50.193
2021-11-19 | 10:23 | 50.19
2021-11-19 | 10:23 | 50.192
2021-11-19 | 10:23 | 50.194
2021-11-19 | 10:23 | 50.196
2021-11-19 | 10:23 | 50.197
2021-11-19 | 10:23 | 50.199
2021-11-19 | 10:23 | 50.198
2021-11-19 | 10:23 | 50.198
2021-11-19 | 10:23 | 50.196
2021-11-19 | 10:23 | 50.198
2021-11-19 | 10:23 | 50.199
2021-11-19 | 10:23 | 50.199
2021-11-19 | 10:23 | 50.2
2021-11-19 | 10:23 | 50.204
2021-11-19 | 10:23 | 50.208
2021-11-19 | 10:23 | 50.211
2021-11-19 | 10:23 | 50.213
2021-11-19 | 10:23 | 50.213
2021-11-19 | 10:23 | 50.213
2021-11-19 | 10:23 | 50.212
2021-11-19 | 10:23 | 50.209
2021-11-19 | 10:23 | 50.208
2021-11-19 | 10:23 | 50.204
2021-11-19 | 10:23 | 50.201
2021-11-19 | 10:23 | 50.198
2021-11-19 | 10:23 | 50.195
2021-11-19 | 10:23 | 50.191
2021-11-19 | 10:23 | 50.187
2021-11-19 | 10:23 | 50.185
2021-11-19 | 10:23 | 50.182
2021-11-19 | 10:23 | 50.181
2021-11-19 | 10:23 | 50.182
2021-11-19 | 10:23 | 50.182
2021-11-19 | 10:23 | 50.182
2021-11-19 | 10:23 | 50.181
2021-11-19 | 10:23 | 50.182
2021-11-19 | 10:23 | 50.181
2021-11-19 | 10:23 | 50.182
2021-11-19 | 10:23 | 50.181
2021-11-19 | 10:23 | 50.18
2021-11-19 | 10:23 | 50.179
2021-11-19 | 10:23 | 50.177
2021-11-19 | 10:23 | 50.177
2021-11-19 | 10:24 | 50.176
2021-11-19 | 10:24 | 50.175
2021-11-19 | 10:24 | 50.173
2021-11-19 | 10:24 | 50.17
2021-11-19 | 10:24 | 50.169
2021-11-19 | 10:24 | 50.168
2021-11-19 | 10:24 | 50.169
2021-11-19 | 10:24 | 50.168
2021-11-19 | 10:24 | 50.166
2021-11-19 | 10:24 | 50.165
2021-11-19 | 10:24 | 50.163
2021-11-19 | 10:24 | 50.163
2021-11-19 | 10:24 | 50.166
2021-11-19 | 10:24 | 50.167
2021-11-19 | 10:24 | 50.169
2021-11-19 | 10:24 | 50.168
2021-11-19 | 10:24 | 50.165
2021-11-19 | 10:24 | 50.163
2021-11-19 | 10:24 | 50.161
2021-11-19 | 10:24 | 50.159
2021-11-19 | 10:24 | 50.156
2021-11-19 | 10:24 | 50.153
2021-11-19 | 10:24 | 50.152
2021-11-19 | 10:24 | 50.149
2021-11-19 | 10:24 | 50.146
2021-11-19 | 10:24 | 50.144
2021-11-19 | 10:24 | 50.142
2021-11-19 | 10:24 | 50.14
2021-11-19 | 10:24 | 50.14
2021-11-19 | 10:24 | 50.139
2021-11-19 | 10:24 | 50.135
2021-11-19 | 10:24 | 50.131
2021-11-19 | 10:24 | 50.128
2021-11-19 | 10:24 | 50.128
2021-11-19 | 10:24 | 50.129
2021-11-19 | 10:24 | 50.13
2021-11-19 | 10:24 | 50.131
2021-11-19 | 10:24 | 50.131
2021-11-19 | 10:24 | 50.129
2021-11-19 | 10:24 | 50.127
2021-11-19 | 10:24 | 50.125
2021-11-19 | 10:24 | 50.123
2021-11-19 | 10:24 | 50.121
2021-11-19 | 10:24 | 50.121
2021-11-19 | 10:24 | 50.119
2021-11-19 | 10:24 | 50.118
2021-11-19 | 10:24 | 50.117
2021-11-19 | 10:24 | 50.116
2021-11-19 | 10:24 | 50.115
2021-11-19 | 10:24 | 50.116
2021-11-19 | 10:24 | 50.117
2021-11-19 | 10:24 | 50.116
2021-11-19 | 10:24 | 50.116
2021-11-19 | 10:24 | 50.114
2021-11-19 | 10:24 | 50.116
2021-11-19 | 10:24 | 50.116
2021-11-19 | 10:24 | 50.117
2021-11-19 | 10:24 | 50.118
2021-11-19 | 10:24 | 50.118
2021-11-19 | 10:25 | 50.115
2021-11-19 | 10:25 | 50.115
2021-11-19 | 10:25 | 50.113
2021-11-19 | 10:25 | 50.11
2021-11-19 | 10:25 | 50.109
2021-11-19 | 10:25 | 50.106
2021-11-19 | 10:25 | 50.103
2021-11-19 | 10:25 | 50.1
2021-11-19 | 10:25 | 50.098
2021-11-19 | 10:25 | 50.098
2021-11-19 | 10:25 | 50.096
2021-11-19 | 10:25 | 50.096
2021-11-19 | 10:25 | 50.094
2021-11-19 | 10:25 | 50.096
2021-11-19 | 10:25 | 50.097
2021-11-19 | 10:25 | 50.096
2021-11-19 | 10:25 | 50.098
2021-11-19 | 10:25 | 50.098
2021-11-19 | 10:25 | 50.1
2021-11-19 | 10:25 | 50.102
2021-11-19 | 10:25 | 50.102
2021-11-19 | 10:25 | 50.102
2021-11-19 | 10:25 | 50.099
2021-11-19 | 10:25 | 50.097
2021-11-19 | 10:25 | 50.097
2021-11-19 | 10:25 | 50.095
2021-11-19 | 10:25 | 50.097
2021-11-19 | 10:25 | 50.1
2021-11-19 | 10:25 | 50.105
2021-11-19 | 10:25 | 50.108
2021-11-19 | 10:25 | 50.109
2021-11-19 | 10:25 | 50.107
2021-11-19 | 10:25 | 50.107
2021-11-19 | 10:25 | 50.107
2021-11-19 | 10:25 | 50.108
2021-11-19 | 10:25 | 50.11
2021-11-19 | 10:25 | 50.112
2021-11-19 | 10:25 | 50.113
2021-11-19 | 10:25 | 50.114
2021-11-19 | 10:25 | 50.116
2021-11-19 | 10:25 | 50.114
2021-11-19 | 10:25 | 50.112
2021-11-19 | 10:25 | 50.11
2021-11-19 | 10:25 | 50.108
2021-11-19 | 10:25 | 50.105
2021-11-19 | 10:25 | 50.106
2021-11-19 | 10:25 | 50.103
2021-11-19 | 10:25 | 50.1
2021-11-19 | 10:25 | 50.1
2021-11-19 | 10:25 | 50.098
2021-11-19 | 10:25 | 50.098
2021-11-19 | 10:25 | 50.097
2021-11-19 | 10:25 | 50.093
2021-11-19 | 10:25 | 50.092
2021-11-19 | 10:25 | 50.089
2021-11-19 | 10:25 | 50.089
2021-11-19 | 10:25 | 50.089
2021-11-19 | 10:25 | 50.09
2021-11-19 | 10:25 | 50.091
2021-11-19 | 10:25 | 50.092
2021-11-19 | 10:26 | 50.093
2021-11-19 | 10:26 | 50.093
2021-11-19 | 10:26 | 50.093
2021-11-19 | 10:26 | 50.093
2021-11-19 | 10:26 | 50.094
2021-11-19 | 10:26 | 50.096
2021-11-19 | 10:26 | 50.095
2021-11-19 | 10:26 | 50.095
2021-11-19 | 10:26 | 50.095
2021-11-19 | 10:26 | 50.096
2021-11-19 | 10:26 | 50.099
2021-11-19 | 10:26 | 50.099
2021-11-19 | 10:26 | 50.102
2021-11-19 | 10:26 | 50.103
2021-11-19 | 10:26 | 50.104
2021-11-19 | 10:26 | 50.105
2021-11-19 | 10:26 | 50.107
2021-11-19 | 10:26 | 50.109
2021-11-19 | 10:26 | 50.111
2021-11-19 | 10:26 | 50.112
2021-11-19 | 10:26 | 50.11
2021-11-19 | 10:26 | 50.11
2021-11-19 | 10:26 | 50.108
2021-11-19 | 10:26 | 50.106
2021-11-19 | 10:26 | 50.103
2021-11-19 | 10:26 | 50.099
2021-11-19 | 10:26 | 50.095
2021-11-19 | 10:26 | 50.09
2021-11-19 | 10:26 | 50.086
2021-11-19 | 10:26 | 50.083
2021-11-19 | 10:26 | 50.08
2021-11-19 | 10:26 | 50.078
2021-11-19 | 10:26 | 50.077
2021-11-19 | 10:26 | 50.077
2021-11-19 | 10:26 | 50.078
2021-11-19 | 10:26 | 50.076
2021-11-19 | 10:26 | 50.076
2021-11-19 | 10:26 | 50.074
2021-11-19 | 10:26 | 50.074
2021-11-19 | 10:26 | 50.073
2021-11-19 | 10:26 | 50.068
2021-11-19 | 10:26 | 50.065
2021-11-19 | 10:26 | 50.06
2021-11-19 | 10:26 | 50.057
2021-11-19 | 10:26 | 50.056
2021-11-19 | 10:26 | 50.055
2021-11-19 | 10:26 | 50.057
2021-11-19 | 10:26 | 50.06
2021-11-19 | 10:26 | 50.064
2021-11-19 | 10:26 | 50.067
2021-11-19 | 10:26 | 50.069
2021-11-19 | 10:26 | 50.071
2021-11-19 | 10:26 | 50.072
2021-11-19 | 10:26 | 50.073
2021-11-19 | 10:26 | 50.074
2021-11-19 | 10:26 | 50.075
2021-11-19 | 10:26 | 50.076
2021-11-19 | 10:26 | 50.076
2021-11-19 | 10:26 | 50.078
2021-11-19 | 10:26 | 50.081
2021-11-19 | 10:26 | 50.085
2021-11-19 | 10:27 | 50.089
2021-11-19 | 10:27 | 50.092
2021-11-19 | 10:27 | 50.093
2021-11-19 | 10:27 | 50.092
2021-11-19 | 10:27 | 50.089
2021-11-19 | 10:27 | 50.086
2021-11-19 | 10:27 | 50.084
2021-11-19 | 10:27 | 50.082
2021-11-19 | 10:27 | 50.081
2021-11-19 | 10:27 | 50.079
2021-11-19 | 10:27 | 50.078
2021-11-19 | 10:27 | 50.074
2021-11-19 | 10:27 | 50.071
2021-11-19 | 10:27 | 50.067
2021-11-19 | 10:27 | 50.065
2021-11-19 | 10:27 | 50.064
2021-11-19 | 10:27 | 50.062
2021-11-19 | 10:27 | 50.059
2021-11-19 | 10:27 | 50.059
2021-11-19 | 10:27 | 50.058
2021-11-19 | 10:27 | 50.059
2021-11-19 | 10:27 | 50.059
2021-11-19 | 10:27 | 50.06
2021-11-19 | 10:27 | 50.06
2021-11-19 | 10:27 | 50.061
2021-11-19 | 10:27 | 50.062
2021-11-19 | 10:27 | 50.064
2021-11-19 | 10:27 | 50.066
2021-11-19 | 10:27 | 50.069
2021-11-19 | 10:27 | 50.071
2021-11-19 | 10:27 | 50.071
2021-11-19 | 10:27 | 50.07
2021-11-19 | 10:27 | 50.067
2021-11-19 | 10:27 | 50.065
2021-11-19 | 10:27 | 50.063
2021-11-19 | 10:27 | 50.061
2021-11-19 | 10:27 | 50.06
2021-11-19 | 10:27 | 50.061
2021-11-19 | 10:27 | 50.06
2021-11-19 | 10:27 | 50.06
2021-11-19 | 10:27 | 50.061
2021-11-19 | 10:27 | 50.062
2021-11-19 | 10:27 | 50.064
2021-11-19 | 10:27 | 50.064
2021-11-19 | 10:27 | 50.065
2021-11-19 | 10:27 | 50.065
2021-11-19 | 10:27 | 50.066
2021-11-19 | 10:27 | 50.067
2021-11-19 | 10:27 | 50.066
2021-11-19 | 10:27 | 50.067
2021-11-19 | 10:27 | 50.068
2021-11-19 | 10:27 | 50.067
2021-11-19 | 10:27 | 50.067
2021-11-19 | 10:27 | 50.067
2021-11-19 | 10:27 | 50.067
2021-11-19 | 10:27 | 50.068
2021-11-19 | 10:27 | 50.07
2021-11-19 | 10:27 | 50.072
2021-11-19 | 10:27 | 50.076
2021-11-19 | 10:28 | 50.077
2021-11-19 | 10:28 | 50.077
2021-11-19 | 10:28 | 50.074
2021-11-19 | 10:28 | 50.072
2021-11-19 | 10:28 | 50.068
2021-11-19 | 10:28 | 50.062
2021-11-19 | 10:28 | 50.056
2021-11-19 | 10:28 | 50.048
2021-11-19 | 10:28 | 50.044
2021-11-19 | 10:28 | 50.042
2021-11-19 | 10:28 | 50.041
2021-11-19 | 10:28 | 50.041
2021-11-19 | 10:28 | 50.044
2021-11-19 | 10:28 | 50.046
2021-11-19 | 10:28 | 50.054
2021-11-19 | 10:28 | 50.06
2021-11-19 | 10:28 | 50.066
2021-11-19 | 10:28 | 50.071
2021-11-19 | 10:28 | 50.075
2021-11-19 | 10:28 | 50.077
2021-11-19 | 10:28 | 50.077
2021-11-19 | 10:28 | 50.079
2021-11-19 | 10:28 | 50.075
2021-11-19 | 10:28 | 50.071
2021-11-19 | 10:28 | 50.064
2021-11-19 | 10:28 | 50.059
2021-11-19 | 10:28 | 50.053
2021-11-19 | 10:28 | 50.05
2021-11-19 | 10:28 | 50.047
2021-11-19 | 10:28 | 50.046
2021-11-19 | 10:28 | 50.046
2021-11-19 | 10:28 | 50.044
2021-11-19 | 10:28 | 50.044
2021-11-19 | 10:28 | 50.044
2021-11-19 | 10:28 | 50.047
2021-11-19 | 10:28 | 50.05
2021-11-19 | 10:28 | 50.054
2021-11-19 | 10:28 | 50.057
2021-11-19 | 10:28 | 50.06
2021-11-19 | 10:28 | 50.062
2021-11-19 | 10:28 | 50.063
2021-11-19 | 10:28 | 50.064
2021-11-19 | 10:28 | 50.065
2021-11-19 | 10:28 | 50.065
2021-11-19 | 10:28 | 50.066
2021-11-19 | 10:28 | 50.065
2021-11-19 | 10:28 | 50.066
2021-11-19 | 10:28 | 50.067
2021-11-19 | 10:28 | 50.066
2021-11-19 | 10:28 | 50.062
2021-11-19 | 10:28 | 50.06
2021-11-19 | 10:28 | 50.056
2021-11-19 | 10:28 | 50.053
2021-11-19 | 10:28 | 50.052
2021-11-19 | 10:28 | 50.053
2021-11-19 | 10:28 | 50.051
2021-11-19 | 10:28 | 50.049
2021-11-19 | 10:28 | 50.05
2021-11-19 | 10:28 | 50.051
2021-11-19 | 10:28 | 50.055
2021-11-19 | 10:28 | 50.06
2021-11-19 | 10:29 | 50.062
2021-11-19 | 10:29 | 50.067
2021-11-19 | 10:29 | 50.069
2021-11-19 | 10:29 | 50.069
2021-11-19 | 10:29 | 50.068
2021-11-19 | 10:29 | 50.069
2021-11-19 | 10:29 | 50.069
2021-11-19 | 10:29 | 50.069
2021-11-19 | 10:29 | 50.067
2021-11-19 | 10:29 | 50.067
2021-11-19 | 10:29 | 50.066
2021-11-19 | 10:29 | 50.065
2021-11-19 | 10:29 | 50.063
2021-11-19 | 10:29 | 50.06
2021-11-19 | 10:29 | 50.057
2021-11-19 | 10:29 | 50.054
2021-11-19 | 10:29 | 50.052
2021-11-19 | 10:29 | 50.05
2021-11-19 | 10:29 | 50.046
2021-11-19 | 10:29 | 50.044
2021-11-19 | 10:29 | 50.042
2021-11-19 | 10:29 | 50.039
2021-11-19 | 10:29 | 50.038
2021-11-19 | 10:29 | 50.038
2021-11-19 | 10:29 | 50.038
2021-11-19 | 10:29 | 50.038
2021-11-19 | 10:29 | 50.037
2021-11-19 | 10:29 | 50.037
2021-11-19 | 10:29 | 50.033
2021-11-19 | 10:29 | 50.028
2021-11-19 | 10:29 | 50.024
2021-11-19 | 10:29 | 50.021
2021-11-19 | 10:29 | 50.021
2021-11-19 | 10:29 | 50.021
2021-11-19 | 10:29 | 50.02
2021-11-19 | 10:29 | 50.022
2021-11-19 | 10:29 | 50.023
2021-11-19 | 10:29 | 50.026
2021-11-19 | 10:29 | 50.029
2021-11-19 | 10:29 | 50.029
2021-11-19 | 10:29 | 50.029
2021-11-19 | 10:29 | 50.03
2021-11-19 | 10:29 | 50.031
2021-11-19 | 10:29 | 50.031
2021-11-19 | 10:29 | 50.032
2021-11-19 | 10:29 | 50.031
2021-11-19 | 10:29 | 50.028
2021-11-19 | 10:29 | 50.024
2021-11-19 | 10:29 | 50.023
2021-11-19 | 10:29 | 50.02
2021-11-19 | 10:29 | 50.019
2021-11-19 | 10:29 | 50.017
2021-11-19 | 10:29 | 50.015
2021-11-19 | 10:29 | 50.018
2021-11-19 | 10:29 | 50.02
2021-11-19 | 10:29 | 50.024
2021-11-19 | 10:29 | 50.025
2021-11-19 | 10:29 | 50.027
2021-11-19 | 10:29 | 50.029
2021-11-19 | 10:30 | 50.029
2021-11-19 | 10:30 | 50.032
2021-11-19 | 10:30 | 50.035
2021-11-19 | 10:30 | 50.036
2021-11-19 | 10:30 | 50.035
2021-11-19 | 10:30 | 50.034
2021-11-19 | 10:30 | 50.032
2021-11-19 | 10:30 | 50.03
2021-11-19 | 10:30 | 50.028
2021-11-19 | 10:30 | 50.025
2021-11-19 | 10:30 | 50.023
2021-11-19 | 10:30 | 50.021
2021-11-19 | 10:30 | 50.018
2021-11-19 | 10:30 | 50.017
2021-11-19 | 10:30 | 50.018
2021-11-19 | 10:30 | 50.02
2021-11-19 | 10:30 | 50.02
2021-11-19 | 10:30 | 50.019
2021-11-19 | 10:30 | 50.014
2021-11-19 | 10:30 | 50.012
2021-11-19 | 10:30 | 50.01
2021-11-19 | 10:30 | 50.011
2021-11-19 | 10:30 | 50.009
2021-11-19 | 10:30 | 50.009
2021-11-19 | 10:30 | 50.009
2021-11-19 | 10:30 | 50.01
2021-11-19 | 10:30 | 50.013
2021-11-19 | 10:30 | 50.014
2021-11-19 | 10:30 | 50.016
2021-11-19 | 10:30 | 50.016
2021-11-19 | 10:30 | 50.015
2021-11-19 | 10:30 | 50.017
2021-11-19 | 10:30 | 50.017
2021-11-19 | 10:30 | 50.017
2021-11-19 | 10:30 | 50.015
2021-11-19 | 10:30 | 50.013
2021-11-19 | 10:30 | 50.009
2021-11-19 | 10:30 | 50.008
2021-11-19 | 10:30 | 50.008
2021-11-19 | 10:30 | 50.01
2021-11-19 | 10:30 | 50.01
2021-11-19 | 10:30 | 50.012
2021-11-19 | 10:30 | 50.013
2021-11-19 | 10:30 | 50.014
2021-11-19 | 10:30 | 50.016
2021-11-19 | 10:30 | 50.015
2021-11-19 | 10:30 | 50.014
2021-11-19 | 10:30 | 50.014
2021-11-19 | 10:30 | 50.014
2021-11-19 | 10:30 | 50.014
2021-11-19 | 10:30 | 50.012
2021-11-19 | 10:30 | 50.014
2021-11-19 | 10:30 | 50.015
2021-11-19 | 10:30 | 50.016
2021-11-19 | 10:30 | 50.016
2021-11-19 | 10:30 | 50.016
2021-11-19 | 10:30 | 50.015
2021-11-19 | 10:30 | 50.012
2021-11-19 | 10:30 | 50.009
2021-11-19 | 10:30 | 50.007
2021-11-19 | 10:30 | 50.007
2021-11-19 | 10:31 | 50.008
2021-11-19 | 10:31 | 50.007
2021-11-19 | 10:31 | 50.007
2021-11-19 | 10:31 | 50.008
2021-11-19 | 10:31 | 50.013
2021-11-19 | 10:31 | 50.013
2021-11-19 | 10:31 | 50.014
2021-11-19 | 10:31 | 50.015
2021-11-19 | 10:31 | 50.018
2021-11-19 | 10:31 | 50.02
2021-11-19 | 10:31 | 50.022
2021-11-19 | 10:31 | 50.026
2021-11-19 | 10:31 | 50.028
2021-11-19 | 10:31 | 50.033
2021-11-19 | 10:31 | 50.034
2021-11-19 | 10:31 | 50.036
2021-11-19 | 10:31 | 50.035
2021-11-19 | 10:31 | 50.034
2021-11-19 | 10:31 | 50.034
2021-11-19 | 10:31 | 50.033
2021-11-19 | 10:31 | 50.032
2021-11-19 | 10:31 | 50.033
2021-11-19 | 10:31 | 50.032
2021-11-19 | 10:31 | 50.03
2021-11-19 | 10:31 | 50.029
2021-11-19 | 10:31 | 50.026
2021-11-19 | 10:31 | 50.025
2021-11-19 | 10:31 | 50.024
2021-11-19 | 10:31 | 50.022
2021-11-19 | 10:31 | 50.021
2021-11-19 | 10:31 | 50.021
2021-11-19 | 10:31 | 50.021
2021-11-19 | 10:31 | 50.02
2021-11-19 | 10:31 | 50.02
2021-11-19 | 10:31 | 50.02
2021-11-19 | 10:31 | 50.019
2021-11-19 | 10:31 | 50.016
2021-11-19 | 10:31 | 50.013
2021-11-19 | 10:31 | 50.012
2021-11-19 | 10:31 | 50.009
2021-11-19 | 10:31 | 50.007
2021-11-19 | 10:31 | 50.004
2021-11-19 | 10:31 | 50.001
2021-11-19 | 10:31 | 49.996
2021-11-19 | 10:31 | 49.994
2021-11-19 | 10:31 | 49.991
2021-11-19 | 10:31 | 49.987
2021-11-19 | 10:31 | 49.984
2021-11-19 | 10:31 | 49.978
2021-11-19 | 10:31 | 49.975
2021-11-19 | 10:31 | 49.968
2021-11-19 | 10:31 | 49.963
2021-11-19 | 10:31 | 49.958
2021-11-19 | 10:31 | 49.954
2021-11-19 | 10:31 | 49.951
2021-11-19 | 10:31 | 49.949
2021-11-19 | 10:31 | 49.947
2021-11-19 | 10:31 | 49.947
2021-11-19 | 10:31 | 49.949
2021-11-19 | 10:32 | 49.95
2021-11-19 | 10:32 | 49.95
2021-11-19 | 10:32 | 49.951
2021-11-19 | 10:32 | 49.952
2021-11-19 | 10:32 | 49.952
2021-11-19 | 10:32 | 49.95
2021-11-19 | 10:32 | 49.949
2021-11-19 | 10:32 | 49.949
2021-11-19 | 10:32 | 49.951
2021-11-19 | 10:32 | 49.956
2021-11-19 | 10:32 | 49.961
2021-11-19 | 10:32 | 49.965
2021-11-19 | 10:32 | 49.971
2021-11-19 | 10:32 | 49.973
2021-11-19 | 10:32 | 49.972
2021-11-19 | 10:32 | 49.971
2021-11-19 | 10:32 | 49.97
2021-11-19 | 10:32 | 49.97
2021-11-19 | 10:32 | 49.969
2021-11-19 | 10:32 | 49.966
2021-11-19 | 10:32 | 49.967
2021-11-19 | 10:32 | 49.967
2021-11-19 | 10:32 | 49.966
2021-11-19 | 10:32 | 49.967
2021-11-19 | 10:32 | 49.967
2021-11-19 | 10:32 | 49.969
2021-11-19 | 10:32 | 49.969
2021-11-19 | 10:32 | 49.972
2021-11-19 | 10:32 | 49.973
2021-11-19 | 10:32 | 49.975

## F20211119-3
In GMT
Date | Time | Freq
2021-11-19 | 15:35 | 50.091
2021-11-19 | 15:35 | 50.09
2021-11-19 | 15:35 | 50.089
2021-11-19 | 15:35 | 50.087
2021-11-19 | 15:35 | 50.084
2021-11-19 | 15:35 | 50.081
2021-11-19 | 15:35 | 50.078
2021-11-19 | 15:35 | 50.076
2021-11-19 | 15:35 | 50.077
2021-11-19 | 15:35 | 50.078
2021-11-19 | 15:35 | 50.083
2021-11-19 | 15:35 | 50.088
2021-11-19 | 15:35 | 50.09
2021-11-19 | 15:35 | 50.092
2021-11-19 | 15:35 | 50.092
2021-11-19 | 15:35 | 50.093
2021-11-19 | 15:35 | 50.091
2021-11-19 | 15:35 | 50.091
2021-11-19 | 15:35 | 50.089
2021-11-19 | 15:35 | 50.087
2021-11-19 | 15:35 | 50.086
2021-11-19 | 15:35 | 50.084
2021-11-19 | 15:35 | 50.084
2021-11-19 | 15:35 | 50.083
2021-11-19 | 15:35 | 50.085
2021-11-19 | 15:35 | 50.087
2021-11-19 | 15:35 | 50.089
2021-11-19 | 15:35 | 50.091
2021-11-19 | 15:35 | 50.093
2021-11-19 | 15:35 | 50.094
2021-11-19 | 15:36 | 50.094
2021-11-19 | 15:36 | 50.094
2021-11-19 | 15:36 | 50.092
2021-11-19 | 15:36 | 50.093
2021-11-19 | 15:36 | 50.094
2021-11-19 | 15:36 | 50.096
2021-11-19 | 15:36 | 50.097
2021-11-19 | 15:36 | 50.098
2021-11-19 | 15:36 | 50.096
2021-11-19 | 15:36 | 50.095
2021-11-19 | 15:36 | 50.095
2021-11-19 | 15:36 | 50.093
2021-11-19 | 15:36 | 50.089
2021-11-19 | 15:36 | 50.087
2021-11-19 | 15:36 | 50.084
2021-11-19 | 15:36 | 50.082
2021-11-19 | 15:36 | 50.08
2021-11-19 | 15:36 | 50.078
2021-11-19 | 15:36 | 50.077
2021-11-19 | 15:36 | 50.077
2021-11-19 | 15:36 | 50.077
2021-11-19 | 15:36 | 50.076
2021-11-19 | 15:36 | 50.077
2021-11-19 | 15:36 | 50.078
2021-11-19 | 15:36 | 50.081
2021-11-19 | 15:36 | 50.086
2021-11-19 | 15:36 | 50.089
2021-11-19 | 15:36 | 50.089
2021-11-19 | 15:36 | 50.09
2021-11-19 | 15:36 | 50.089
2021-11-19 | 15:36 | 50.088
2021-11-19 | 15:36 | 50.084
2021-11-19 | 15:36 | 50.083
2021-11-19 | 15:36 | 50.081
2021-11-19 | 15:36 | 50.077
2021-11-19 | 15:36 | 50.076
2021-11-19 | 15:36 | 50.075
2021-11-19 | 15:36 | 50.072
2021-11-19 | 15:36 | 50.07
2021-11-19 | 15:36 | 50.069
2021-11-19 | 15:36 | 50.067
2021-11-19 | 15:36 | 50.064
2021-11-19 | 15:36 | 50.062
2021-11-19 | 15:36 | 50.06
2021-11-19 | 15:36 | 50.059
2021-11-19 | 15:36 | 50.031
2021-11-19 | 15:36 | 50.006
2021-11-19 | 15:36 | 49.986
2021-11-19 | 15:36 | 49.968
2021-11-19 | 15:36 | 49.955
2021-11-19 | 15:36 | 49.947
2021-11-19 | 15:36 | 49.942
2021-11-19 | 15:36 | 49.941
2021-11-19 | 15:36 | 49.941
2021-11-19 | 15:36 | 49.941
2021-11-19 | 15:36 | 49.943
2021-11-19 | 15:36 | 49.946
2021-11-19 | 15:36 | 49.948
2021-11-19 | 15:36 | 49.945
2021-11-19 | 15:36 | 49.945
2021-11-19 | 15:36 | 49.94
2021-11-19 | 15:37 | 49.934
2021-11-19 | 15:37 | 49.929
2021-11-19 | 15:37 | 49.928
2021-11-19 | 15:37 | 49.929
2021-11-19 | 15:37 | 49.928
2021-11-19 | 15:37 | 49.926
2021-11-19 | 15:37 | 49.924
2021-11-19 | 15:37 | 49.925
2021-11-19 | 15:37 | 49.926
2021-11-19 | 15:37 | 49.926
2021-11-19 | 15:37 | 49.922
2021-11-19 | 15:37 | 49.923
2021-11-19 | 15:37 | 49.921
2021-11-19 | 15:37 | 49.919
2021-11-19 | 15:37 | 49.922
2021-11-19 | 15:37 | 49.924
2021-11-19 | 15:37 | 49.926
2021-11-19 | 15:37 | 49.925
2021-11-19 | 15:37 | 49.925
2021-11-19 | 15:37 | 49.925
2021-11-19 | 15:37 | 49.926
2021-11-19 | 15:37 | 49.92
2021-11-19 | 15:37 | 49.916
2021-11-19 | 15:37 | 49.914
2021-11-19 | 15:37 | 49.912
2021-11-19 | 15:37 | 49.909
2021-11-19 | 15:37 | 49.911
2021-11-19 | 15:37 | 49.906
2021-11-19 | 15:37 | 49.905
2021-11-19 | 15:37 | 49.906
2021-11-19 | 15:37 | 49.905
2021-11-19 | 15:37 | 49.904
2021-11-19 | 15:37 | 49.904
2021-11-19 | 15:37 | 49.907
2021-11-19 | 15:37 | 49.904
2021-11-19 | 15:37 | 49.906
2021-11-19 | 15:37 | 49.903
2021-11-19 | 15:37 | 49.901
2021-11-19 | 15:37 | 49.901
2021-11-19 | 15:37 | 49.9
2021-11-19 | 15:37 | 49.903
2021-11-19 | 15:37 | 49.905
2021-11-19 | 15:37 | 49.906
2021-11-19 | 15:37 | 49.91
2021-11-19 | 15:37 | 49.911
2021-11-19 | 15:37 | 49.913
2021-11-19 | 15:37 | 49.915
2021-11-19 | 15:37 | 49.916
2021-11-19 | 15:37 | 49.92
2021-11-19 | 15:37 | 49.922
2021-11-19 | 15:37 | 49.922
2021-11-19 | 15:37 | 49.919
2021-11-19 | 15:37 | 49.923
2021-11-19 | 15:37 | 49.918
2021-11-19 | 15:37 | 49.919
2021-11-19 | 15:37 | 49.921
2021-11-19 | 15:37 | 49.924
2021-11-19 | 15:37 | 49.924
2021-11-19 | 15:37 | 49.925
2021-11-19 | 15:38 | 49.927
2021-11-19 | 15:38 | 49.93
2021-11-19 | 15:38 | 49.932
2021-11-19 | 15:38 | 49.933
2021-11-19 | 15:38 | 49.935
2021-11-19 | 15:38 | 49.936
2021-11-19 | 15:38 | 49.932
2021-11-19 | 15:38 | 49.936
2021-11-19 | 15:38 | 49.931
2021-11-19 | 15:38 | 49.931
2021-11-19 | 15:38 | 49.927
2021-11-19 | 15:38 | 49.925
2021-11-19 | 15:38 | 49.921
2021-11-19 | 15:38 | 49.919
2021-11-19 | 15:38 | 49.917
2021-11-19 | 15:38 | 49.913
2021-11-19 | 15:38 | 49.912
2021-11-19 | 15:38 | 49.906
2021-11-19 | 15:38 | 49.904
2021-11-19 | 15:38 | 49.903
2021-11-19 | 15:38 | 49.902
2021-11-19 | 15:38 | 49.899
2021-11-19 | 15:38 | 49.9
2021-11-19 | 15:38 | 49.901
2021-11-19 | 15:38 | 49.902
2021-11-19 | 15:38 | 49.903
2021-11-19 | 15:38 | 49.906
2021-11-19 | 15:38 | 49.906
2021-11-19 | 15:38 | 49.904
2021-11-19 | 15:38 | 49.903
2021-11-19 | 15:38 | 49.9
2021-11-19 | 15:38 | 49.902
2021-11-19 | 15:38 | 49.902
2021-11-19 | 15:38 | 49.904
2021-11-19 | 15:38 | 49.905
2021-11-19 | 15:38 | 49.908
2021-11-19 | 15:38 | 49.909
2021-11-19 | 15:38 | 49.911
2021-11-19 | 15:38 | 49.91
2021-11-19 | 15:38 | 49.913
2021-11-19 | 15:38 | 49.915
2021-11-19 | 15:38 | 49.915
2021-11-19 | 15:38 | 49.913
2021-11-19 | 15:38 | 49.912
2021-11-19 | 15:38 | 49.913
2021-11-19 | 15:38 | 49.916
2021-11-19 | 15:38 | 49.919
2021-11-19 | 15:38 | 49.922
2021-11-19 | 15:38 | 49.92
2021-11-19 | 15:38 | 49.921
2021-11-19 | 15:38 | 49.921
2021-11-19 | 15:38 | 49.922
2021-11-19 | 15:38 | 49.921
2021-11-19 | 15:38 | 49.923
2021-11-19 | 15:38 | 49.928
2021-11-19 | 15:38 | 49.932
2021-11-19 | 15:38 | 49.936
2021-11-19 | 15:38 | 49.938
2021-11-19 | 15:38 | 49.941
2021-11-19 | 15:38 | 49.939
2021-11-19 | 15:38 | 49.939
2021-11-19 | 15:39 | 49.939
2021-11-19 | 15:39 | 49.939
2021-11-19 | 15:39 | 49.938
2021-11-19 | 15:39 | 49.938
2021-11-19 | 15:39 | 49.937
2021-11-19 | 15:39 | 49.937
2021-11-19 | 15:39 | 49.934
2021-11-19 | 15:39 | 49.934
2021-11-19 | 15:39 | 49.933
2021-11-19 | 15:39 | 49.929
2021-11-19 | 15:39 | 49.929
2021-11-19 | 15:39 | 49.932
2021-11-19 | 15:39 | 49.936
2021-11-19 | 15:39 | 49.939
2021-11-19 | 15:39 | 49.941
2021-11-19 | 15:39 | 49.944
2021-11-19 | 15:39 | 49.945
2021-11-19 | 15:39 | 49.945
2021-11-19 | 15:39 | 49.946
2021-11-19 | 15:39 | 49.945
2021-11-19 | 15:39 | 49.943
2021-11-19 | 15:39 | 49.941
2021-11-19 | 15:39 | 49.939
2021-11-19 | 15:39 | 49.935
2021-11-19 | 15:39 | 49.93
2021-11-19 | 15:39 | 49.925
2021-11-19 | 15:39 | 49.923
2021-11-19 | 15:39 | 49.923
2021-11-19 | 15:39 | 49.924
2021-11-19 | 15:39 | 49.925
2021-11-19 | 15:39 | 49.93
2021-11-19 | 15:39 | 49.936
2021-11-19 | 15:39 | 49.938
2021-11-19 | 15:39 | 49.939
2021-11-19 | 15:39 | 49.941
2021-11-19 | 15:39 | 49.945
2021-11-19 | 15:39 | 49.946
2021-11-19 | 15:39 | 49.942
2021-11-19 | 15:39 | 49.941
2021-11-19 | 15:39 | 49.937
2021-11-19 | 15:39 | 49.933
2021-11-19 | 15:39 | 49.934
2021-11-19 | 15:39 | 49.933
2021-11-19 | 15:39 | 49.93
2021-11-19 | 15:39 | 49.928
2021-11-19 | 15:39 | 49.923
2021-11-19 | 15:39 | 49.922
2021-11-19 | 15:39 | 49.918
2021-11-19 | 15:39 | 49.916
2021-11-19 | 15:39 | 49.917
2021-11-19 | 15:39 | 49.915
2021-11-19 | 15:39 | 49.913
2021-11-19 | 15:39 | 49.913
2021-11-19 | 15:39 | 49.915
2021-11-19 | 15:39 | 49.918
2021-11-19 | 15:39 | 49.916
2021-11-19 | 15:39 | 49.916
2021-11-19 | 15:39 | 49.914
2021-11-19 | 15:39 | 49.911
2021-11-19 | 15:40 | 49.909
2021-11-19 | 15:40 | 49.911
2021-11-19 | 15:40 | 49.912
2021-11-19 | 15:40 | 49.912
2021-11-19 | 15:40 | 49.913
2021-11-19 | 15:40 | 49.914
2021-11-19 | 15:40 | 49.914
2021-11-19 | 15:40 | 49.914
2021-11-19 | 15:40 | 49.913
2021-11-19 | 15:40 | 49.914
2021-11-19 | 15:40 | 49.915
2021-11-19 | 15:40 | 49.915
2021-11-19 | 15:40 | 49.915
2021-11-19 | 15:40 | 49.914
2021-11-19 | 15:40 | 49.914
2021-11-19 | 15:40 | 49.913
2021-11-19 | 15:40 | 49.913
2021-11-19 | 15:40 | 49.911
2021-11-19 | 15:40 | 49.91
2021-11-19 | 15:40 | 49.908
2021-11-19 | 15:40 | 49.907
2021-11-19 | 15:40 | 49.907
2021-11-19 | 15:40 | 49.906
2021-11-19 | 15:40 | 49.907
2021-11-19 | 15:40 | 49.908
2021-11-19 | 15:40 | 49.907
2021-11-19 | 15:40 | 49.907
2021-11-19 | 15:40 | 49.905
2021-11-19 | 15:40 | 49.903
2021-11-19 | 15:40 | 49.903
2021-11-19 | 15:40 | 49.903
2021-11-19 | 15:40 | 49.9
2021-11-19 | 15:40 | 49.898
2021-11-19 | 15:40 | 49.897
2021-11-19 | 15:40 | 49.894
2021-11-19 | 15:40 | 49.894
2021-11-19 | 15:40 | 49.896
2021-11-19 | 15:40 | 49.897
2021-11-19 | 15:40 | 49.895
2021-11-19 | 15:40 | 49.896
2021-11-19 | 15:40 | 49.896
2021-11-19 | 15:40 | 49.895
2021-11-19 | 15:40 | 49.898
2021-11-19 | 15:40 | 49.899
2021-11-19 | 15:40 | 49.897
2021-11-19 | 15:40 | 49.895
2021-11-19 | 15:40 | 49.894
2021-11-19 | 15:40 | 49.894
2021-11-19 | 15:40 | 49.892
2021-11-19 | 15:40 | 49.894
2021-11-19 | 15:40 | 49.893
2021-11-19 | 15:40 | 49.895
2021-11-19 | 15:40 | 49.896
2021-11-19 | 15:40 | 49.894
2021-11-19 | 15:40 | 49.896
2021-11-19 | 15:40 | 49.894
2021-11-19 | 15:40 | 49.896
2021-11-19 | 15:40 | 49.898
2021-11-19 | 15:40 | 49.899
2021-11-19 | 15:40 | 49.896
2021-11-19 | 15:40 | 49.892
2021-11-19 | 15:41 | 49.887
2021-11-19 | 15:41 | 49.88
2021-11-19 | 15:41 | 49.877
2021-11-19 | 15:41 | 49.876
2021-11-19 | 15:41 | 49.875
2021-11-19 | 15:41 | 49.876
2021-11-19 | 15:41 | 49.877
2021-11-19 | 15:41 | 49.879
2021-11-19 | 15:41 | 49.88
2021-11-19 | 15:41 | 49.879
2021-11-19 | 15:41 | 49.875
2021-11-19 | 15:41 | 49.875
2021-11-19 | 15:41 | 49.875
2021-11-19 | 15:41 | 49.874
2021-11-19 | 15:41 | 49.869
2021-11-19 | 15:41 | 49.865
2021-11-19 | 15:41 | 49.858
2021-11-19 | 15:41 | 49.853
2021-11-19 | 15:41 | 49.85
2021-11-19 | 15:41 | 49.849
2021-11-19 | 15:41 | 49.847
2021-11-19 | 15:41 | 49.85
2021-11-19 | 15:41 | 49.851
2021-11-19 | 15:41 | 49.853
2021-11-19 | 15:41 | 49.851
2021-11-19 | 15:41 | 49.851
2021-11-19 | 15:41 | 49.852
2021-11-19 | 15:41 | 49.852
2021-11-19 | 15:41 | 49.853
2021-11-19 | 15:41 | 49.854
2021-11-19 | 15:41 | 49.853
2021-11-19 | 15:41 | 49.852
2021-11-19 | 15:41 | 49.854
2021-11-19 | 15:41 | 49.856
2021-11-19 | 15:41 | 49.859
2021-11-19 | 15:41 | 49.863
2021-11-19 | 15:41 | 49.867
2021-11-19 | 15:41 | 49.872
2021-11-19 | 15:41 | 49.876
2021-11-19 | 15:41 | 49.877
2021-11-19 | 15:41 | 49.878
2021-11-19 | 15:41 | 49.882
2021-11-19 | 15:41 | 49.883
2021-11-19 | 15:41 | 49.889
2021-11-19 | 15:41 | 49.895
2021-11-19 | 15:41 | 49.9
2021-11-19 | 15:41 | 49.9
2021-11-19 | 15:41 | 49.901
2021-11-19 | 15:41 | 49.901
2021-11-19 | 15:41 | 49.899
2021-11-19 | 15:41 | 49.901
2021-11-19 | 15:41 | 49.897
2021-11-19 | 15:41 | 49.898
2021-11-19 | 15:41 | 49.897
2021-11-19 | 15:41 | 49.895
2021-11-19 | 15:41 | 49.898
2021-11-19 | 15:41 | 49.9
2021-11-19 | 15:41 | 49.901
2021-11-19 | 15:41 | 49.902
2021-11-19 | 15:41 | 49.905
2021-11-19 | 15:42 | 49.909
2021-11-19 | 15:42 | 49.912
2021-11-19 | 15:42 | 49.916
2021-11-19 | 15:42 | 49.92
2021-11-19 | 15:42 | 49.922
2021-11-19 | 15:42 | 49.924
2021-11-19 | 15:42 | 49.923
2021-11-19 | 15:42 | 49.922
2021-11-19 | 15:42 | 49.923
2021-11-19 | 15:42 | 49.923
2021-11-19 | 15:42 | 49.921
2021-11-19 | 15:42 | 49.922
2021-11-19 | 15:42 | 49.923
2021-11-19 | 15:42 | 49.923
2021-11-19 | 15:42 | 49.922
2021-11-19 | 15:42 | 49.922
2021-11-19 | 15:42 | 49.923
2021-11-19 | 15:42 | 49.922
2021-11-19 | 15:42 | 49.922
2021-11-19 | 15:42 | 49.921
2021-11-19 | 15:42 | 49.92
2021-11-19 | 15:42 | 49.922
2021-11-19 | 15:42 | 49.922
2021-11-19 | 15:42 | 49.922
2021-11-19 | 15:42 | 49.922
2021-11-19 | 15:42 | 49.923
2021-11-19 | 15:42 | 49.921
2021-11-19 | 15:42 | 49.921
2021-11-19 | 15:42 | 49.918
2021-11-19 | 15:42 | 49.915
2021-11-19 | 15:42 | 49.916
2021-11-19 | 15:42 | 49.918
2021-11-19 | 15:42 | 49.92
2021-11-19 | 15:42 | 49.923
2021-11-19 | 15:42 | 49.929
2021-11-19 | 15:42 | 49.933
2021-11-19 | 15:42 | 49.937
2021-11-19 | 15:42 | 49.944
2021-11-19 | 15:42 | 49.95
2021-11-19 | 15:42 | 49.954
2021-11-19 | 15:42 | 49.96
2021-11-19 | 15:42 | 49.961
2021-11-19 | 15:42 | 49.964
2021-11-19 | 15:42 | 49.966
2021-11-19 | 15:42 | 49.968
2021-11-19 | 15:42 | 49.968
2021-11-19 | 15:42 | 49.963
2021-11-19 | 15:42 | 49.961
2021-11-19 | 15:42 | 49.959
2021-11-19 | 15:42 | 49.958
2021-11-19 | 15:42 | 49.959
2021-11-19 | 15:42 | 49.961
2021-11-19 | 15:42 | 49.961
2021-11-19 | 15:42 | 49.961
2021-11-19 | 15:42 | 49.961
2021-11-19 | 15:42 | 49.962
2021-11-19 | 15:42 | 49.959
2021-11-19 | 15:42 | 49.956
2021-11-19 | 15:42 | 49.954
2021-11-19 | 15:43 | 49.951
2021-11-19 | 15:43 | 49.948
2021-11-19 | 15:43 | 49.947
2021-11-19 | 15:43 | 49.946
2021-11-19 | 15:43 | 49.946
2021-11-19 | 15:43 | 49.949
2021-11-19 | 15:43 | 49.951
2021-11-19 | 15:43 | 49.951
2021-11-19 | 15:43 | 49.952
2021-11-19 | 15:43 | 49.951
2021-11-19 | 15:43 | 49.952
2021-11-19 | 15:43 | 49.951
2021-11-19 | 15:43 | 49.95
2021-11-19 | 15:43 | 49.947
2021-11-19 | 15:43 | 49.945
2021-11-19 | 15:43 | 49.942
2021-11-19 | 15:43 | 49.938
2021-11-19 | 15:43 | 49.936
2021-11-19 | 15:43 | 49.932
2021-11-19 | 15:43 | 49.932
2021-11-19 | 15:43 | 49.933
2021-11-19 | 15:43 | 49.935
2021-11-19 | 15:43 | 49.938
2021-11-19 | 15:43 | 49.939
2021-11-19 | 15:43 | 49.94
2021-11-19 | 15:43 | 49.943
2021-11-19 | 15:43 | 49.944
2021-11-19 | 15:43 | 49.945
2021-11-19 | 15:43 | 49.946
2021-11-19 | 15:43 | 49.948
2021-11-19 | 15:43 | 49.95
2021-11-19 | 15:43 | 49.949
2021-11-19 | 15:43 | 49.951
2021-11-19 | 15:43 | 49.95
2021-11-19 | 15:43 | 49.951
2021-11-19 | 15:43 | 49.951
2021-11-19 | 15:43 | 49.954
2021-11-19 | 15:43 | 49.957
2021-11-19 | 15:43 | 49.96
2021-11-19 | 15:43 | 49.963
2021-11-19 | 15:43 | 49.965
2021-11-19 | 15:43 | 49.966
2021-11-19 | 15:43 | 49.969
2021-11-19 | 15:43 | 49.967
2021-11-19 | 15:43 | 49.967
2021-11-19 | 15:43 | 49.966
2021-11-19 | 15:43 | 49.965
2021-11-19 | 15:43 | 49.962
2021-11-19 | 15:43 | 49.961
2021-11-19 | 15:43 | 49.961
2021-11-19 | 15:43 | 49.959
2021-11-19 | 15:43 | 49.956
2021-11-19 | 15:43 | 49.952
2021-11-19 | 15:43 | 49.949
2021-11-19 | 15:43 | 49.946
2021-11-19 | 15:43 | 49.944
2021-11-19 | 15:43 | 49.943
2021-11-19 | 15:43 | 49.944
2021-11-19 | 15:43 | 49.945
2021-11-19 | 15:43 | 49.944
2021-11-19 | 15:43 | 49.947
2021-11-19 | 15:44 | 49.948
2021-11-19 | 15:44 | 49.948
2021-11-19 | 15:44 | 49.95
2021-11-19 | 15:44 | 49.949
2021-11-19 | 15:44 | 49.953
2021-11-19 | 15:44 | 49.955
2021-11-19 | 15:44 | 49.957
2021-11-19 | 15:44 | 49.958
2021-11-19 | 15:44 | 49.959
2021-11-19 | 15:44 | 49.961
2021-11-19 | 15:44 | 49.962
2021-11-19 | 15:44 | 49.965
2021-11-19 | 15:44 | 49.968
2021-11-19 | 15:44 | 49.973
2021-11-19 | 15:44 | 49.976
2021-11-19 | 15:44 | 49.98
2021-11-19 | 15:44 | 49.982
2021-11-19 | 15:44 | 49.984
2021-11-19 | 15:44 | 49.985
2021-11-19 | 15:44 | 49.985
2021-11-19 | 15:44 | 49.987
2021-11-19 | 15:44 | 49.988
2021-11-19 | 15:44 | 49.986
2021-11-19 | 15:44 | 49.984
2021-11-19 | 15:44 | 49.983
2021-11-19 | 15:44 | 49.982
2021-11-19 | 15:44 | 49.981
2021-11-19 | 15:44 | 49.98
2021-11-19 | 15:44 | 49.98
2021-11-19 | 15:44 | 49.98
2021-11-19 | 15:44 | 49.979
2021-11-19 | 15:44 | 49.979
2021-11-19 | 15:44 | 49.978
2021-11-19 | 15:44 | 49.98
2021-11-19 | 15:44 | 49.979
2021-11-19 | 15:44 | 49.98
2021-11-19 | 15:44 | 49.98
2021-11-19 | 15:44 | 49.983
2021-11-19 | 15:44 | 49.985
2021-11-19 | 15:44 | 49.987
2021-11-19 | 15:44 | 49.986
2021-11-19 | 15:44 | 49.983
2021-11-19 | 15:44 | 49.977
2021-11-19 | 15:44 | 49.972
2021-11-19 | 15:44 | 49.967
2021-11-19 | 15:44 | 49.963
2021-11-19 | 15:44 | 49.961
2021-11-19 | 15:44 | 49.957
2021-11-19 | 15:44 | 49.955
2021-11-19 | 15:44 | 49.954
2021-11-19 | 15:44 | 49.953
2021-11-19 | 15:44 | 49.952
2021-11-19 | 15:44 | 49.953
2021-11-19 | 15:44 | 49.954
2021-11-19 | 15:44 | 49.953
2021-11-19 | 15:44 | 49.952
2021-11-19 | 15:44 | 49.949
2021-11-19 | 15:44 | 49.947
2021-11-19 | 15:44 | 49.945
2021-11-19 | 15:45 | 49.947
2021-11-19 | 15:45 | 49.95
2021-11-19 | 15:45 | 49.951
2021-11-19 | 15:45 | 49.951
2021-11-19 | 15:45 | 49.952
2021-11-19 | 15:45 | 49.952
2021-11-19 | 15:45 | 49.95
2021-11-19 | 15:45 | 49.95
2021-11-19 | 15:45 | 49.949
2021-11-19 | 15:45 | 49.948
2021-11-19 | 15:45 | 49.946
2021-11-19 | 15:45 | 49.942
2021-11-19 | 15:45 | 49.937
2021-11-19 | 15:45 | 49.93
2021-11-19 | 15:45 | 49.927
2021-11-19 | 15:45 | 49.924
2021-11-19 | 15:45 | 49.926
2021-11-19 | 15:45 | 49.927
2021-11-19 | 15:45 | 49.931
2021-11-19 | 15:45 | 49.935
2021-11-19 | 15:45 | 49.94
2021-11-19 | 15:45 | 49.942
2021-11-19 | 15:45 | 49.944
2021-11-19 | 15:45 | 49.945
2021-11-19 | 15:45 | 49.947
2021-11-19 | 15:45 | 49.949
2021-11-19 | 15:45 | 49.949
2021-11-19 | 15:45 | 49.946
2021-11-19 | 15:45 | 49.942
2021-11-19 | 15:45 | 49.936
2021-11-19 | 15:45 | 49.929
2021-11-19 | 15:45 | 49.924
2021-11-19 | 15:45 | 49.92
2021-11-19 | 15:45 | 49.916
2021-11-19 | 15:45 | 49.913
2021-11-19 | 15:45 | 49.913
2021-11-19 | 15:45 | 49.914
2021-11-19 | 15:45 | 49.916
2021-11-19 | 15:45 | 49.919
2021-11-19 | 15:45 | 49.92
2021-11-19 | 15:45 | 49.924
2021-11-19 | 15:45 | 49.925
2021-11-19 | 15:45 | 49.924
2021-11-19 | 15:45 | 49.923
2021-11-19 | 15:45 | 49.925
2021-11-19 | 15:45 | 49.925
2021-11-19 | 15:45 | 49.925
2021-11-19 | 15:45 | 49.924
2021-11-19 | 15:45 | 49.922
2021-11-19 | 15:45 | 49.919
2021-11-19 | 15:45 | 49.917
2021-11-19 | 15:45 | 49.917
2021-11-19 | 15:45 | 49.916
2021-11-19 | 15:45 | 49.915
2021-11-19 | 15:45 | 49.913
2021-11-19 | 15:45 | 49.912
2021-11-19 | 15:45 | 49.914
2021-11-19 | 15:45 | 49.915
2021-11-19 | 15:45 | 49.917
2021-11-19 | 15:45 | 49.918
2021-11-19 | 15:45 | 49.918
2021-11-19 | 15:46 | 49.916
2021-11-19 | 15:46 | 49.915
2021-11-19 | 15:46 | 49.913
2021-11-19 | 15:46 | 49.913
2021-11-19 | 15:46 | 49.912
2021-11-19 | 15:46 | 49.913
2021-11-19 | 15:46 | 49.914
2021-11-19 | 15:46 | 49.914
2021-11-19 | 15:46 | 49.914
2021-11-19 | 15:46 | 49.913
2021-11-19 | 15:46 | 49.912
2021-11-19 | 15:46 | 49.914
2021-11-19 | 15:46 | 49.914
2021-11-19 | 15:46 | 49.915
2021-11-19 | 15:46 | 49.916
2021-11-19 | 15:46 | 49.917
2021-11-19 | 15:46 | 49.916
2021-11-19 | 15:46 | 49.915
2021-11-19 | 15:46 | 49.917
2021-11-19 | 15:46 | 49.917
2021-11-19 | 15:46 | 49.92
2021-11-19 | 15:46 | 49.925
2021-11-19 | 15:46 | 49.927
2021-11-19 | 15:46 | 49.923
2021-11-19 | 15:46 | 49.918
2021-11-19 | 15:46 | 49.91
2021-11-19 | 15:46 | 49.901
2021-11-19 | 15:46 | 49.892
2021-11-19 | 15:46 | 49.883
2021-11-19 | 15:46 | 49.875
2021-11-19 | 15:46 | 49.869
2021-11-19 | 15:46 | 49.866
2021-11-19 | 15:46 | 49.863
2021-11-19 | 15:46 | 49.86
2021-11-19 | 15:46 | 49.859
2021-11-19 | 15:46 | 49.858
2021-11-19 | 15:46 | 49.857
2021-11-19 | 15:46 | 49.854
2021-11-19 | 15:46 | 49.852
2021-11-19 | 15:46 | 49.849
2021-11-19 | 15:46 | 49.85
2021-11-19 | 15:46 | 49.849
2021-11-19 | 15:46 | 49.85
2021-11-19 | 15:46 | 49.848
2021-11-19 | 15:46 | 49.847
2021-11-19 | 15:46 | 49.845
2021-11-19 | 15:46 | 49.844
2021-11-19 | 15:46 | 49.843
2021-11-19 | 15:46 | 49.84
2021-11-19 | 15:46 | 49.838
2021-11-19 | 15:46 | 49.838
2021-11-19 | 15:46 | 49.838
2021-11-19 | 15:46 | 49.838
2021-11-19 | 15:46 | 49.837
2021-11-19 | 15:46 | 49.836
2021-11-19 | 15:46 | 49.835
2021-11-19 | 15:46 | 49.834
2021-11-19 | 15:46 | 49.834
2021-11-19 | 15:46 | 49.833
2021-11-19 | 15:47 | 49.831
2021-11-19 | 15:47 | 49.828
2021-11-19 | 15:47 | 49.825
2021-11-19 | 15:47 | 49.825
2021-11-19 | 15:47 | 49.824
2021-11-19 | 15:47 | 49.824
2021-11-19 | 15:47 | 49.823
2021-11-19 | 15:47 | 49.823
2021-11-19 | 15:47 | 49.822
2021-11-19 | 15:47 | 49.825
2021-11-19 | 15:47 | 49.827
2021-11-19 | 15:47 | 49.829
2021-11-19 | 15:47 | 49.829
2021-11-19 | 15:47 | 49.828
2021-11-19 | 15:47 | 49.825
2021-11-19 | 15:47 | 49.823
2021-11-19 | 15:47 | 49.823
2021-11-19 | 15:47 | 49.823
2021-11-19 | 15:47 | 49.824
2021-11-19 | 15:47 | 49.823
2021-11-19 | 15:47 | 49.823
2021-11-19 | 15:47 | 49.823
2021-11-19 | 15:47 | 49.822
2021-11-19 | 15:47 | 49.821
2021-11-19 | 15:47 | 49.821
2021-11-19 | 15:47 | 49.821
2021-11-19 | 15:47 | 49.822
2021-11-19 | 15:47 | 49.826
2021-11-19 | 15:47 | 49.829
2021-11-19 | 15:47 | 49.831
2021-11-19 | 15:47 | 49.833
2021-11-19 | 15:47 | 49.833
2021-11-19 | 15:47 | 49.834
2021-11-19 | 15:47 | 49.833
2021-11-19 | 15:47 | 49.832
2021-11-19 | 15:47 | 49.827
2021-11-19 | 15:47 | 49.824
2021-11-19 | 15:47 | 49.821
2021-11-19 | 15:47 | 49.815
2021-11-19 | 15:47 | 49.814
2021-11-19 | 15:47 | 49.814
2021-11-19 | 15:47 | 49.818
2021-11-19 | 15:47 | 49.822
2021-11-19 | 15:47 | 49.824
2021-11-19 | 15:47 | 49.829
2021-11-19 | 15:47 | 49.833
2021-11-19 | 15:47 | 49.838
2021-11-19 | 15:47 | 49.842
2021-11-19 | 15:47 | 49.847
2021-11-19 | 15:47 | 49.851
2021-11-19 | 15:47 | 49.855
2021-11-19 | 15:47 | 49.86
2021-11-19 | 15:47 | 49.866
2021-11-19 | 15:47 | 49.869
2021-11-19 | 15:47 | 49.876
2021-11-19 | 15:47 | 49.883
2021-11-19 | 15:47 | 49.889
2021-11-19 | 15:47 | 49.895
2021-11-19 | 15:47 | 49.9
2021-11-19 | 15:47 | 49.904
2021-11-19 | 15:47 | 49.908
2021-11-19 | 15:48 | 49.912
2021-11-19 | 15:48 | 49.917
2021-11-19 | 15:48 | 49.92
2021-11-19 | 15:48 | 49.922
2021-11-19 | 15:48 | 49.922
2021-11-19 | 15:48 | 49.922
2021-11-19 | 15:48 | 49.92
2021-11-19 | 15:48 | 49.918
2021-11-19 | 15:48 | 49.917
2021-11-19 | 15:48 | 49.919
2021-11-19 | 15:48 | 49.918
2021-11-19 | 15:48 | 49.92
2021-11-19 | 15:48 | 49.921
2021-11-19 | 15:48 | 49.922
2021-11-19 | 15:48 | 49.924
2021-11-19 | 15:48 | 49.926
2021-11-19 | 15:48 | 49.929
2021-11-19 | 15:48 | 49.931
2021-11-19 | 15:48 | 49.931
2021-11-19 | 15:48 | 49.934
2021-11-19 | 15:48 | 49.935
2021-11-19 | 15:48 | 49.937
2021-11-19 | 15:48 | 49.939
2021-11-19 | 15:48 | 49.938
2021-11-19 | 15:48 | 49.94
2021-11-19 | 15:48 | 49.941
2021-11-19 | 15:48 | 49.942
2021-11-19 | 15:48 | 49.942
2021-11-19 | 15:48 | 49.943
2021-11-19 | 15:48 | 49.946
2021-11-19 | 15:48 | 49.95
2021-11-19 | 15:48 | 49.952
2021-11-19 | 15:48 | 49.954
2021-11-19 | 15:48 | 49.958
2021-11-19 | 15:48 | 49.959
2021-11-19 | 15:48 | 49.961
2021-11-19 | 15:48 | 49.961
2021-11-19 | 15:48 | 49.962
2021-11-19 | 15:48 | 49.964
2021-11-19 | 15:48 | 49.965
2021-11-19 | 15:48 | 49.965
2021-11-19 | 15:48 | 49.963
2021-11-19 | 15:48 | 49.963
2021-11-19 | 15:48 | 49.961
2021-11-19 | 15:48 | 49.96
2021-11-19 | 15:48 | 49.957
2021-11-19 | 15:48 | 49.958
2021-11-19 | 15:48 | 49.954
2021-11-19 | 15:48 | 49.954
2021-11-19 | 15:48 | 49.953
2021-11-19 | 15:48 | 49.953
2021-11-19 | 15:48 | 49.952
2021-11-19 | 15:48 | 49.953
2021-11-19 | 15:48 | 49.954
2021-11-19 | 15:48 | 49.952
2021-11-19 | 15:48 | 49.949
2021-11-19 | 15:48 | 49.949
2021-11-19 | 15:48 | 49.946
2021-11-19 | 15:48 | 49.945
2021-11-19 | 15:49 | 49.942
2021-11-19 | 15:49 | 49.94
2021-11-19 | 15:49 | 49.939
2021-11-19 | 15:49 | 49.939
2021-11-19 | 15:49 | 49.939
2021-11-19 | 15:49 | 49.94
2021-11-19 | 15:49 | 49.941
2021-11-19 | 15:49 | 49.94
2021-11-19 | 15:49 | 49.94
2021-11-19 | 15:49 | 49.939
2021-11-19 | 15:49 | 49.936
2021-11-19 | 15:49 | 49.935
2021-11-19 | 15:49 | 49.933
2021-11-19 | 15:49 | 49.933
2021-11-19 | 15:49 | 49.933
2021-11-19 | 15:49 | 49.933
2021-11-19 | 15:49 | 49.933
2021-11-19 | 15:49 | 49.934
2021-11-19 | 15:49 | 49.935
2021-11-19 | 15:49 | 49.937
2021-11-19 | 15:49 | 49.934
2021-11-19 | 15:49 | 49.934
2021-11-19 | 15:49 | 49.936
2021-11-19 | 15:49 | 49.938
2021-11-19 | 15:49 | 49.939
2021-11-19 | 15:49 | 49.942
2021-11-19 | 15:49 | 49.943
2021-11-19 | 15:49 | 49.946
2021-11-19 | 15:49 | 49.949
2021-11-19 | 15:49 | 49.95
2021-11-19 | 15:49 | 49.95
2021-11-19 | 15:49 | 49.952
2021-11-19 | 15:49 | 49.952
2021-11-19 | 15:49 | 49.955
2021-11-19 | 15:49 | 49.956
2021-11-19 | 15:49 | 49.958
2021-11-19 | 15:49 | 49.958
2021-11-19 | 15:49 | 49.957
2021-11-19 | 15:49 | 49.954
2021-11-19 | 15:49 | 49.952
2021-11-19 | 15:49 | 49.949
2021-11-19 | 15:49 | 49.948
2021-11-19 | 15:49 | 49.946
2021-11-19 | 15:49 | 49.946
2021-11-19 | 15:49 | 49.947
2021-11-19 | 15:49 | 49.944
2021-11-19 | 15:49 | 49.942
2021-11-19 | 15:49 | 49.941
2021-11-19 | 15:49 | 49.942
2021-11-19 | 15:49 | 49.945
2021-11-19 | 15:49 | 49.949
2021-11-19 | 15:49 | 49.954
2021-11-19 | 15:49 | 49.958
2021-11-19 | 15:49 | 49.963
2021-11-19 | 15:49 | 49.967
2021-11-19 | 15:49 | 49.972
2021-11-19 | 15:49 | 49.973
2021-11-19 | 15:49 | 49.976
2021-11-19 | 15:49 | 49.978
2021-11-19 | 15:49 | 49.982
2021-11-19 | 15:50 | 49.987
2021-11-19 | 15:50 | 49.993
2021-11-19 | 15:50 | 49.999
2021-11-19 | 15:50 | 50.006
2021-11-19 | 15:50 | 50.015
2021-11-19 | 15:50 | 50.027
2021-11-19 | 15:50 | 50.035
2021-11-19 | 15:50 | 50.042
2021-11-19 | 15:50 | 50.048
2021-11-19 | 15:50 | 50.054
2021-11-19 | 15:50 | 50.057
2021-11-19 | 15:50 | 50.058
2021-11-19 | 15:50 | 50.061
2021-11-19 | 15:50 | 50.063
2021-11-19 | 15:50 | 50.067
2021-11-19 | 15:50 | 50.068
2021-11-19 | 15:50 | 50.068
2021-11-19 | 15:50 | 50.068
2021-11-19 | 15:50 | 50.068
2021-11-19 | 15:50 | 50.069
2021-11-19 | 15:50 | 50.07
2021-11-19 | 15:50 | 50.073
2021-11-19 | 15:50 | 50.074
2021-11-19 | 15:50 | 50.078
2021-11-19 | 15:50 | 50.082
2021-11-19 | 15:50 | 50.086
2021-11-19 | 15:50 | 50.088
2021-11-19 | 15:50 | 50.091
2021-11-19 | 15:50 | 50.093
2021-11-19 | 15:50 | 50.093

## F20211125-1
In GMT
Date | Time | Freq
2021-11-25 | 18:40 | 49.955
2021-11-25 | 18:40 | 49.954
2021-11-25 | 18:40 | 49.952
2021-11-25 | 18:40 | 49.948
2021-11-25 | 18:40 | 49.947
2021-11-25 | 18:40 | 49.944
2021-11-25 | 18:40 | 49.945
2021-11-25 | 18:40 | 49.945
2021-11-25 | 18:40 | 49.945
2021-11-25 | 18:40 | 49.944
2021-11-25 | 18:40 | 49.944
2021-11-25 | 18:40 | 49.945
2021-11-25 | 18:40 | 49.946
2021-11-25 | 18:40 | 49.948
2021-11-25 | 18:40 | 49.948
2021-11-25 | 18:40 | 49.95
2021-11-25 | 18:40 | 49.951
2021-11-25 | 18:40 | 49.955
2021-11-25 | 18:40 | 49.958
2021-11-25 | 18:40 | 49.96
2021-11-25 | 18:40 | 49.962
2021-11-25 | 18:40 | 49.966
2021-11-25 | 18:40 | 49.97
2021-11-25 | 18:40 | 49.973
2021-11-25 | 18:40 | 49.976
2021-11-25 | 18:40 | 49.979
2021-11-25 | 18:40 | 49.982
2021-11-25 | 18:40 | 49.986
2021-11-25 | 18:40 | 49.988
2021-11-25 | 18:40 | 49.99
2021-11-25 | 18:40 | 49.991
2021-11-25 | 18:41 | 49.991
2021-11-25 | 18:41 | 49.989
2021-11-25 | 18:41 | 49.986
2021-11-25 | 18:41 | 49.983
2021-11-25 | 18:41 | 49.982
2021-11-25 | 18:41 | 49.982
2021-11-25 | 18:41 | 49.981
2021-11-25 | 18:41 | 49.978
2021-11-25 | 18:41 | 49.976
2021-11-25 | 18:41 | 49.974
2021-11-25 | 18:41 | 49.972
2021-11-25 | 18:41 | 49.969
2021-11-25 | 18:41 | 49.966
2021-11-25 | 18:41 | 49.965
2021-11-25 | 18:41 | 49.964
2021-11-25 | 18:41 | 49.963
2021-11-25 | 18:41 | 49.963
2021-11-25 | 18:41 | 49.962
2021-11-25 | 18:41 | 49.962
2021-11-25 | 18:41 | 49.96
2021-11-25 | 18:41 | 49.961
2021-11-25 | 18:41 | 49.96
2021-11-25 | 18:41 | 49.959
2021-11-25 | 18:41 | 49.957
2021-11-25 | 18:41 | 49.956
2021-11-25 | 18:41 | 49.956
2021-11-25 | 18:41 | 49.956
2021-11-25 | 18:41 | 49.956
2021-11-25 | 18:41 | 49.956
2021-11-25 | 18:41 | 49.955
2021-11-25 | 18:41 | 49.952
2021-11-25 | 18:41 | 49.95
2021-11-25 | 18:41 | 49.948
2021-11-25 | 18:41 | 49.949
2021-11-25 | 18:41 | 49.949
2021-11-25 | 18:41 | 49.95
2021-11-25 | 18:41 | 49.951
2021-11-25 | 18:41 | 49.951
2021-11-25 | 18:41 | 49.95
2021-11-25 | 18:41 | 49.949
2021-11-25 | 18:41 | 49.947
2021-11-25 | 18:41 | 49.945
2021-11-25 | 18:41 | 49.943
2021-11-25 | 18:41 | 49.938
2021-11-25 | 18:41 | 49.917
2021-11-25 | 18:41 | 49.898
2021-11-25 | 18:41 | 49.877
2021-11-25 | 18:41 | 49.861
2021-11-25 | 18:41 | 49.85
2021-11-25 | 18:41 | 49.842
2021-11-25 | 18:41 | 49.837
2021-11-25 | 18:41 | 49.832
2021-11-25 | 18:41 | 49.83
2021-11-25 | 18:41 | 49.829
2021-11-25 | 18:41 | 49.829
2021-11-25 | 18:41 | 49.83
2021-11-25 | 18:41 | 49.831
2021-11-25 | 18:41 | 49.833
2021-11-25 | 18:41 | 49.836
2021-11-25 | 18:41 | 49.838
2021-11-25 | 18:42 | 49.837
2021-11-25 | 18:42 | 49.837
2021-11-25 | 18:42 | 49.836
2021-11-25 | 18:42 | 49.838
2021-11-25 | 18:42 | 49.841
2021-11-25 | 18:42 | 49.844
2021-11-25 | 18:42 | 49.845
2021-11-25 | 18:42 | 49.845
2021-11-25 | 18:42 | 49.844
2021-11-25 | 18:42 | 49.842
2021-11-25 | 18:42 | 49.841
2021-11-25 | 18:42 | 49.841
2021-11-25 | 18:42 | 49.841
2021-11-25 | 18:42 | 49.84
2021-11-25 | 18:42 | 49.837
2021-11-25 | 18:42 | 49.835
2021-11-25 | 18:42 | 49.834
2021-11-25 | 18:42 | 49.835
2021-11-25 | 18:42 | 49.837
2021-11-25 | 18:42 | 49.842
2021-11-25 | 18:42 | 49.846
2021-11-25 | 18:42 | 49.849
2021-11-25 | 18:42 | 49.85
2021-11-25 | 18:42 | 49.851
2021-11-25 | 18:42 | 49.849
2021-11-25 | 18:42 | 49.848
2021-11-25 | 18:42 | 49.846
2021-11-25 | 18:42 | 49.843
2021-11-25 | 18:42 | 49.841
2021-11-25 | 18:42 | 49.84
2021-11-25 | 18:42 | 49.838
2021-11-25 | 18:42 | 49.834
2021-11-25 | 18:42 | 49.831
2021-11-25 | 18:42 | 49.83
2021-11-25 | 18:42 | 49.831
2021-11-25 | 18:42 | 49.834
2021-11-25 | 18:42 | 49.836
2021-11-25 | 18:42 | 49.838
2021-11-25 | 18:42 | 49.84
2021-11-25 | 18:42 | 49.843
2021-11-25 | 18:42 | 49.846
2021-11-25 | 18:42 | 49.849
2021-11-25 | 18:42 | 49.849
2021-11-25 | 18:42 | 49.848
2021-11-25 | 18:42 | 49.847
2021-11-25 | 18:42 | 49.846
2021-11-25 | 18:42 | 49.847
2021-11-25 | 18:42 | 49.846
2021-11-25 | 18:42 | 49.847
2021-11-25 | 18:42 | 49.845
2021-11-25 | 18:42 | 49.845
2021-11-25 | 18:42 | 49.845
2021-11-25 | 18:42 | 49.846
2021-11-25 | 18:42 | 49.848
2021-11-25 | 18:42 | 49.851
2021-11-25 | 18:42 | 49.856
2021-11-25 | 18:42 | 49.86
2021-11-25 | 18:42 | 49.865
2021-11-25 | 18:42 | 49.867
2021-11-25 | 18:42 | 49.868
2021-11-25 | 18:43 | 49.87
2021-11-25 | 18:43 | 49.87
2021-11-25 | 18:43 | 49.873
2021-11-25 | 18:43 | 49.876
2021-11-25 | 18:43 | 49.88
2021-11-25 | 18:43 | 49.883
2021-11-25 | 18:43 | 49.889
2021-11-25 | 18:43 | 49.893
2021-11-25 | 18:43 | 49.9
2021-11-25 | 18:43 | 49.906
2021-11-25 | 18:43 | 49.913
2021-11-25 | 18:43 | 49.922
2021-11-25 | 18:43 | 49.93
2021-11-25 | 18:43 | 49.938
2021-11-25 | 18:43 | 49.946
2021-11-25 | 18:43 | 49.953
2021-11-25 | 18:43 | 49.957
2021-11-25 | 18:43 | 49.96
2021-11-25 | 18:43 | 49.963
2021-11-25 | 18:43 | 49.966
2021-11-25 | 18:43 | 49.968
2021-11-25 | 18:43 | 49.971
2021-11-25 | 18:43 | 49.974
2021-11-25 | 18:43 | 49.977
2021-11-25 | 18:43 | 49.98
2021-11-25 | 18:43 | 49.982
2021-11-25 | 18:43 | 49.983
2021-11-25 | 18:43 | 49.981
2021-11-25 | 18:43 | 49.98
2021-11-25 | 18:43 | 49.978
2021-11-25 | 18:43 | 49.978
2021-11-25 | 18:43 | 49.978
2021-11-25 | 18:43 | 49.978
2021-11-25 | 18:43 | 49.98
2021-11-25 | 18:43 | 49.981
2021-11-25 | 18:43 | 49.981
2021-11-25 | 18:43 | 49.982
2021-11-25 | 18:43 | 49.982
2021-11-25 | 18:43 | 49.982
2021-11-25 | 18:43 | 49.981
2021-11-25 | 18:43 | 49.981
2021-11-25 | 18:43 | 49.982
2021-11-25 | 18:43 | 49.983
2021-11-25 | 18:43 | 49.984
2021-11-25 | 18:43 | 49.985
2021-11-25 | 18:43 | 49.984
2021-11-25 | 18:43 | 49.984
2021-11-25 | 18:43 | 49.983
2021-11-25 | 18:43 | 49.982
2021-11-25 | 18:43 | 49.98
2021-11-25 | 18:43 | 49.98
2021-11-25 | 18:43 | 49.979
2021-11-25 | 18:43 | 49.979
2021-11-25 | 18:43 | 49.98
2021-11-25 | 18:43 | 49.981
2021-11-25 | 18:43 | 49.982
2021-11-25 | 18:43 | 49.981
2021-11-25 | 18:43 | 49.98
2021-11-25 | 18:43 | 49.981
2021-11-25 | 18:43 | 49.981
2021-11-25 | 18:44 | 49.981
2021-11-25 | 18:44 | 49.983
2021-11-25 | 18:44 | 49.986
2021-11-25 | 18:44 | 49.989
2021-11-25 | 18:44 | 49.991
2021-11-25 | 18:44 | 49.995
2021-11-25 | 18:44 | 49.997
2021-11-25 | 18:44 | 50
2021-11-25 | 18:44 | 50.003
2021-11-25 | 18:44 | 50.007
2021-11-25 | 18:44 | 50.009
2021-11-25 | 18:44 | 50.012
2021-11-25 | 18:44 | 50.015
2021-11-25 | 18:44 | 50.016
2021-11-25 | 18:44 | 50.019
2021-11-25 | 18:44 | 50.021
2021-11-25 | 18:44 | 50.024
2021-11-25 | 18:44 | 50.028
2021-11-25 | 18:44 | 50.031
2021-11-25 | 18:44 | 50.032
2021-11-25 | 18:44 | 50.033
2021-11-25 | 18:44 | 50.034
2021-11-25 | 18:44 | 50.034
2021-11-25 | 18:44 | 50.034
2021-11-25 | 18:44 | 50.031
2021-11-25 | 18:44 | 50.028
2021-11-25 | 18:44 | 50.025
2021-11-25 | 18:44 | 50.022
2021-11-25 | 18:44 | 50.021

## F20211127-1
In GMT
Date | Time | Freq
2021-11-27 | 7:13 | 50.113
2021-11-27 | 7:13 | 50.112
2021-11-27 | 7:13 | 50.112
2021-11-27 | 7:13 | 50.112
2021-11-27 | 7:13 | 50.11
2021-11-27 | 7:13 | 50.109
2021-11-27 | 7:13 | 50.109
2021-11-27 | 7:13 | 50.108
2021-11-27 | 7:13 | 50.108
2021-11-27 | 7:13 | 50.108
2021-11-27 | 7:13 | 50.108
2021-11-27 | 7:13 | 50.109
2021-11-27 | 7:13 | 50.109
2021-11-27 | 7:13 | 50.111
2021-11-27 | 7:13 | 50.112
2021-11-27 | 7:13 | 50.112
2021-11-27 | 7:13 | 50.111
2021-11-27 | 7:13 | 50.109
2021-11-27 | 7:13 | 50.107
2021-11-27 | 7:13 | 50.104
2021-11-27 | 7:13 | 50.101
2021-11-27 | 7:13 | 50.099
2021-11-27 | 7:13 | 50.098
2021-11-27 | 7:13 | 50.096
2021-11-27 | 7:13 | 50.095
2021-11-27 | 7:13 | 50.093
2021-11-27 | 7:13 | 50.091
2021-11-27 | 7:13 | 50.089
2021-11-27 | 7:13 | 50.084
2021-11-27 | 7:13 | 50.08
2021-11-27 | 7:14 | 50.075
2021-11-27 | 7:14 | 50.072
2021-11-27 | 7:14 | 50.071
2021-11-27 | 7:14 | 50.069
2021-11-27 | 7:14 | 50.068
2021-11-27 | 7:14 | 50.068
2021-11-27 | 7:14 | 50.07
2021-11-27 | 7:14 | 50.071
2021-11-27 | 7:14 | 50.074
2021-11-27 | 7:14 | 50.072
2021-11-27 | 7:14 | 50.071
2021-11-27 | 7:14 | 50.072
2021-11-27 | 7:14 | 50.074
2021-11-27 | 7:14 | 50.075
2021-11-27 | 7:14 | 50.075
2021-11-27 | 7:14 | 50.075
2021-11-27 | 7:14 | 50.074
2021-11-27 | 7:14 | 50.071
2021-11-27 | 7:14 | 50.069
2021-11-27 | 7:14 | 50.068
2021-11-27 | 7:14 | 50.067
2021-11-27 | 7:14 | 50.066
2021-11-27 | 7:14 | 50.067
2021-11-27 | 7:14 | 50.069
2021-11-27 | 7:14 | 50.068
2021-11-27 | 7:14 | 50.068
2021-11-27 | 7:14 | 50.067
2021-11-27 | 7:14 | 50.069
2021-11-27 | 7:14 | 50.071
2021-11-27 | 7:14 | 50.073
2021-11-27 | 7:14 | 50.076
2021-11-27 | 7:14 | 50.078
2021-11-27 | 7:14 | 50.078
2021-11-27 | 7:14 | 50.076
2021-11-27 | 7:14 | 50.074
2021-11-27 | 7:14 | 50.072
2021-11-27 | 7:14 | 50.071
2021-11-27 | 7:14 | 50.07
2021-11-27 | 7:14 | 50.069
2021-11-27 | 7:14 | 50.068
2021-11-27 | 7:14 | 50.067
2021-11-27 | 7:14 | 50.064
2021-11-27 | 7:14 | 50.062
2021-11-27 | 7:14 | 50.061
2021-11-27 | 7:14 | 50.06
2021-11-27 | 7:14 | 50.059
2021-11-27 | 7:14 | 50.06
2021-11-27 | 7:14 | 50.063
2021-11-27 | 7:14 | 50.068
2021-11-27 | 7:14 | 50.072
2021-11-27 | 7:14 | 50.075
2021-11-27 | 7:14 | 50.077
2021-11-27 | 7:14 | 50.078
2021-11-27 | 7:14 | 50.077
2021-11-27 | 7:14 | 50.074
2021-11-27 | 7:14 | 50.074
2021-11-27 | 7:14 | 50.073
2021-11-27 | 7:14 | 50.072
2021-11-27 | 7:14 | 50.071
2021-11-27 | 7:14 | 50.07
2021-11-27 | 7:14 | 50.066
2021-11-27 | 7:15 | 50.062
2021-11-27 | 7:15 | 50.061
2021-11-27 | 7:15 | 50.036
2021-11-27 | 7:15 | 49.983
2021-11-27 | 7:15 | 49.949
2021-11-27 | 7:15 | 49.928
2021-11-27 | 7:15 | 49.915
2021-11-27 | 7:15 | 49.909
2021-11-27 | 7:15 | 49.908
2021-11-27 | 7:15 | 49.911
2021-11-27 | 7:15 | 49.916
2021-11-27 | 7:15 | 49.923
2021-11-27 | 7:15 | 49.929
2021-11-27 | 7:15 | 49.933
2021-11-27 | 7:15 | 49.937
2021-11-27 | 7:15 | 49.939
2021-11-27 | 7:15 | 49.94
2021-11-27 | 7:15 | 49.94
2021-11-27 | 7:15 | 49.939
2021-11-27 | 7:15 | 49.937
2021-11-27 | 7:15 | 49.935
2021-11-27 | 7:15 | 49.933
2021-11-27 | 7:15 | 49.933
2021-11-27 | 7:15 | 49.929
2021-11-27 | 7:15 | 49.926
2021-11-27 | 7:15 | 49.926
2021-11-27 | 7:15 | 49.927
2021-11-27 | 7:15 | 49.928
2021-11-27 | 7:15 | 49.928
2021-11-27 | 7:15 | 49.929
2021-11-27 | 7:15 | 49.929
2021-11-27 | 7:15 | 49.93
2021-11-27 | 7:15 | 49.932
2021-11-27 | 7:15 | 49.934
2021-11-27 | 7:15 | 49.936
2021-11-27 | 7:15 | 49.936
2021-11-27 | 7:15 | 49.936
2021-11-27 | 7:15 | 49.936
2021-11-27 | 7:15 | 49.936
2021-11-27 | 7:15 | 49.935
2021-11-27 | 7:15 | 49.935
2021-11-27 | 7:15 | 49.932
2021-11-27 | 7:15 | 49.928
2021-11-27 | 7:15 | 49.926
2021-11-27 | 7:15 | 49.924
2021-11-27 | 7:15 | 49.925
2021-11-27 | 7:15 | 49.925
2021-11-27 | 7:15 | 49.927
2021-11-27 | 7:15 | 49.929
2021-11-27 | 7:15 | 49.933
2021-11-27 | 7:15 | 49.934
2021-11-27 | 7:15 | 49.934
2021-11-27 | 7:15 | 49.935
2021-11-27 | 7:15 | 49.936
2021-11-27 | 7:15 | 49.935
2021-11-27 | 7:15 | 49.936
2021-11-27 | 7:15 | 49.937
2021-11-27 | 7:15 | 49.936
2021-11-27 | 7:15 | 49.935
2021-11-27 | 7:16 | 49.935
2021-11-27 | 7:16 | 49.937
2021-11-27 | 7:16 | 49.938
2021-11-27 | 7:16 | 49.939
2021-11-27 | 7:16 | 49.94
2021-11-27 | 7:16 | 49.941
2021-11-27 | 7:16 | 49.941
2021-11-27 | 7:16 | 49.94
2021-11-27 | 7:16 | 49.939
2021-11-27 | 7:16 | 49.935
2021-11-27 | 7:16 | 49.93
2021-11-27 | 7:16 | 49.93
2021-11-27 | 7:16 | 49.928
2021-11-27 | 7:16 | 49.926
2021-11-27 | 7:16 | 49.923
2021-11-27 | 7:16 | 49.92
2021-11-27 | 7:16 | 49.917
2021-11-27 | 7:16 | 49.916
2021-11-27 | 7:16 | 49.916
2021-11-27 | 7:16 | 49.913
2021-11-27 | 7:16 | 49.909
2021-11-27 | 7:16 | 49.909
2021-11-27 | 7:16 | 49.907
2021-11-27 | 7:16 | 49.905
2021-11-27 | 7:16 | 49.904
2021-11-27 | 7:16 | 49.903
2021-11-27 | 7:16 | 49.904
2021-11-27 | 7:16 | 49.904
2021-11-27 | 7:16 | 49.904
2021-11-27 | 7:16 | 49.904
2021-11-27 | 7:16 | 49.904
2021-11-27 | 7:16 | 49.902
2021-11-27 | 7:16 | 49.901
2021-11-27 | 7:16 | 49.899
2021-11-27 | 7:16 | 49.897
2021-11-27 | 7:16 | 49.893
2021-11-27 | 7:16 | 49.893
2021-11-27 | 7:16 | 49.893
2021-11-27 | 7:16 | 49.893
2021-11-27 | 7:16 | 49.892
2021-11-27 | 7:16 | 49.893
2021-11-27 | 7:16 | 49.894
2021-11-27 | 7:16 | 49.895
2021-11-27 | 7:16 | 49.895
2021-11-27 | 7:16 | 49.895
2021-11-27 | 7:16 | 49.893
2021-11-27 | 7:16 | 49.892
2021-11-27 | 7:16 | 49.892
2021-11-27 | 7:16 | 49.891
2021-11-27 | 7:16 | 49.889
2021-11-27 | 7:16 | 49.89
2021-11-27 | 7:16 | 49.89
2021-11-27 | 7:16 | 49.889
2021-11-27 | 7:16 | 49.887
2021-11-27 | 7:16 | 49.886
2021-11-27 | 7:16 | 49.885
2021-11-27 | 7:16 | 49.883
2021-11-27 | 7:16 | 49.883
2021-11-27 | 7:16 | 49.883
2021-11-27 | 7:16 | 49.882
2021-11-27 | 7:16 | 49.88
2021-11-27 | 7:17 | 49.88
2021-11-27 | 7:17 | 49.877
2021-11-27 | 7:17 | 49.879
2021-11-27 | 7:17 | 49.88
2021-11-27 | 7:17 | 49.879
2021-11-27 | 7:17 | 49.878
2021-11-27 | 7:17 | 49.877
2021-11-27 | 7:17 | 49.876
2021-11-27 | 7:17 | 49.875
2021-11-27 | 7:17 | 49.874
2021-11-27 | 7:17 | 49.874
2021-11-27 | 7:17 | 49.873
2021-11-27 | 7:17 | 49.87
2021-11-27 | 7:17 | 49.866
2021-11-27 | 7:17 | 49.864
2021-11-27 | 7:17 | 49.864
2021-11-27 | 7:17 | 49.864
2021-11-27 | 7:17 | 49.863
2021-11-27 | 7:17 | 49.86
2021-11-27 | 7:17 | 49.856
2021-11-27 | 7:17 | 49.851
2021-11-27 | 7:17 | 49.85
2021-11-27 | 7:17 | 49.847
2021-11-27 | 7:17 | 49.843
2021-11-27 | 7:17 | 49.842
2021-11-27 | 7:17 | 49.841
2021-11-27 | 7:17 | 49.842
2021-11-27 | 7:17 | 49.842
2021-11-27 | 7:17 | 49.843
2021-11-27 | 7:17 | 49.843
2021-11-27 | 7:17 | 49.842
2021-11-27 | 7:17 | 49.841
2021-11-27 | 7:17 | 49.841
2021-11-27 | 7:17 | 49.84
2021-11-27 | 7:17 | 49.84
2021-11-27 | 7:17 | 49.839
2021-11-27 | 7:17 | 49.84
2021-11-27 | 7:17 | 49.84
2021-11-27 | 7:17 | 49.839
2021-11-27 | 7:17 | 49.839
2021-11-27 | 7:17 | 49.839
2021-11-27 | 7:17 | 49.839
2021-11-27 | 7:17 | 49.839
2021-11-27 | 7:17 | 49.839
2021-11-27 | 7:17 | 49.836
2021-11-27 | 7:17 | 49.831
2021-11-27 | 7:17 | 49.828
2021-11-27 | 7:17 | 49.827
2021-11-27 | 7:17 | 49.825
2021-11-27 | 7:17 | 49.824
2021-11-27 | 7:17 | 49.822
2021-11-27 | 7:17 | 49.819
2021-11-27 | 7:17 | 49.818
2021-11-27 | 7:17 | 49.816
2021-11-27 | 7:17 | 49.815
2021-11-27 | 7:17 | 49.815
2021-11-27 | 7:17 | 49.818
2021-11-27 | 7:17 | 49.822
2021-11-27 | 7:17 | 49.825
2021-11-27 | 7:18 | 49.827
2021-11-27 | 7:18 | 49.832
2021-11-27 | 7:18 | 49.835
2021-11-27 | 7:18 | 49.838
2021-11-27 | 7:18 | 49.839
2021-11-27 | 7:18 | 49.843
2021-11-27 | 7:18 | 49.845
2021-11-27 | 7:18 | 49.844
2021-11-27 | 7:18 | 49.843
2021-11-27 | 7:18 | 49.843
2021-11-27 | 7:18 | 49.843
2021-11-27 | 7:18 | 49.844
2021-11-27 | 7:18 | 49.845
2021-11-27 | 7:18 | 49.846
2021-11-27 | 7:18 | 49.847
2021-11-27 | 7:18 | 49.848
2021-11-27 | 7:18 | 49.848
2021-11-27 | 7:18 | 49.848
2021-11-27 | 7:18 | 49.847
2021-11-27 | 7:18 | 49.846
2021-11-27 | 7:18 | 49.848
2021-11-27 | 7:18 | 49.849
2021-11-27 | 7:18 | 49.852
2021-11-27 | 7:18 | 49.853
2021-11-27 | 7:18 | 49.853
2021-11-27 | 7:18 | 49.853
2021-11-27 | 7:18 | 49.855
2021-11-27 | 7:18 | 49.86
2021-11-27 | 7:18 | 49.864
2021-11-27 | 7:18 | 49.867
2021-11-27 | 7:18 | 49.868
2021-11-27 | 7:18 | 49.868
2021-11-27 | 7:18 | 49.869
2021-11-27 | 7:18 | 49.872
2021-11-27 | 7:18 | 49.874
2021-11-27 | 7:18 | 49.875
2021-11-27 | 7:18 | 49.873
2021-11-27 | 7:18 | 49.872
2021-11-27 | 7:18 | 49.872
2021-11-27 | 7:18 | 49.871
2021-11-27 | 7:18 | 49.87
2021-11-27 | 7:18 | 49.87
2021-11-27 | 7:18 | 49.871
2021-11-27 | 7:18 | 49.87
2021-11-27 | 7:18 | 49.867
2021-11-27 | 7:18 | 49.867
2021-11-27 | 7:18 | 49.867
2021-11-27 | 7:18 | 49.866
2021-11-27 | 7:18 | 49.865
2021-11-27 | 7:18 | 49.867
2021-11-27 | 7:18 | 49.868
2021-11-27 | 7:18 | 49.87
2021-11-27 | 7:18 | 49.871
2021-11-27 | 7:18 | 49.872
2021-11-27 | 7:18 | 49.873
2021-11-27 | 7:18 | 49.874
2021-11-27 | 7:18 | 49.874
2021-11-27 | 7:18 | 49.872
2021-11-27 | 7:18 | 49.87
2021-11-27 | 7:18 | 49.87
2021-11-27 | 7:19 | 49.868
2021-11-27 | 7:19 | 49.866
2021-11-27 | 7:19 | 49.865
2021-11-27 | 7:19 | 49.864
2021-11-27 | 7:19 | 49.863
2021-11-27 | 7:19 | 49.863
2021-11-27 | 7:19 | 49.863
2021-11-27 | 7:19 | 49.865
2021-11-27 | 7:19 | 49.866
2021-11-27 | 7:19 | 49.866
2021-11-27 | 7:19 | 49.865
2021-11-27 | 7:19 | 49.867
2021-11-27 | 7:19 | 49.869
2021-11-27 | 7:19 | 49.873
2021-11-27 | 7:19 | 49.874
2021-11-27 | 7:19 | 49.874
2021-11-27 | 7:19 | 49.876
2021-11-27 | 7:19 | 49.878
2021-11-27 | 7:19 | 49.88
2021-11-27 | 7:19 | 49.881
2021-11-27 | 7:19 | 49.882
2021-11-27 | 7:19 | 49.88
2021-11-27 | 7:19 | 49.881
2021-11-27 | 7:19 | 49.881
2021-11-27 | 7:19 | 49.882
2021-11-27 | 7:19 | 49.883
2021-11-27 | 7:19 | 49.885
2021-11-27 | 7:19 | 49.885
2021-11-27 | 7:19 | 49.883
2021-11-27 | 7:19 | 49.881
2021-11-27 | 7:19 | 49.877
2021-11-27 | 7:19 | 49.877
2021-11-27 | 7:19 | 49.876
2021-11-27 | 7:19 | 49.875
2021-11-27 | 7:19 | 49.874
2021-11-27 | 7:19 | 49.874
2021-11-27 | 7:19 | 49.872
2021-11-27 | 7:19 | 49.871
2021-11-27 | 7:19 | 49.867
2021-11-27 | 7:19 | 49.863
2021-11-27 | 7:19 | 49.86
2021-11-27 | 7:19 | 49.859
2021-11-27 | 7:19 | 49.856
2021-11-27 | 7:19 | 49.855
2021-11-27 | 7:19 | 49.856
2021-11-27 | 7:19 | 49.855
2021-11-27 | 7:19 | 49.854
2021-11-27 | 7:19 | 49.855
2021-11-27 | 7:19 | 49.854
2021-11-27 | 7:19 | 49.853
2021-11-27 | 7:19 | 49.856
2021-11-27 | 7:19 | 49.858
2021-11-27 | 7:19 | 49.858
2021-11-27 | 7:19 | 49.857
2021-11-27 | 7:19 | 49.856
2021-11-27 | 7:19 | 49.858
2021-11-27 | 7:19 | 49.861
2021-11-27 | 7:19 | 49.863
2021-11-27 | 7:19 | 49.864
2021-11-27 | 7:19 | 49.866
2021-11-27 | 7:19 | 49.863
2021-11-27 | 7:20 | 49.865
2021-11-27 | 7:20 | 49.866
2021-11-27 | 7:20 | 49.867
2021-11-27 | 7:20 | 49.867
2021-11-27 | 7:20 | 49.868
2021-11-27 | 7:20 | 49.868
2021-11-27 | 7:20 | 49.87
2021-11-27 | 7:20 | 49.874
2021-11-27 | 7:20 | 49.879
2021-11-27 | 7:20 | 49.882
2021-11-27 | 7:20 | 49.883
2021-11-27 | 7:20 | 49.886
2021-11-27 | 7:20 | 49.891
2021-11-27 | 7:20 | 49.897
2021-11-27 | 7:20 | 49.901
2021-11-27 | 7:20 | 49.906
2021-11-27 | 7:20 | 49.909
2021-11-27 | 7:20 | 49.91
2021-11-27 | 7:20 | 49.914
2021-11-27 | 7:20 | 49.917
2021-11-27 | 7:20 | 49.917
2021-11-27 | 7:20 | 49.919
2021-11-27 | 7:20 | 49.921
2021-11-27 | 7:20 | 49.918
2021-11-27 | 7:20 | 49.918
2021-11-27 | 7:20 | 49.92
2021-11-27 | 7:20 | 49.921
2021-11-27 | 7:20 | 49.922
2021-11-27 | 7:20 | 49.922
2021-11-27 | 7:20 | 49.922
2021-11-27 | 7:20 | 49.921
2021-11-27 | 7:20 | 49.918
2021-11-27 | 7:20 | 49.915
2021-11-27 | 7:20 | 49.915
2021-11-27 | 7:20 | 49.915
2021-11-27 | 7:20 | 49.917
2021-11-27 | 7:20 | 49.92
2021-11-27 | 7:20 | 49.921
2021-11-27 | 7:20 | 49.92
2021-11-27 | 7:20 | 49.921
2021-11-27 | 7:20 | 49.924
2021-11-27 | 7:20 | 49.927
2021-11-27 | 7:20 | 49.93
2021-11-27 | 7:20 | 49.932
2021-11-27 | 7:20 | 49.933
2021-11-27 | 7:20 | 49.933
2021-11-27 | 7:20 | 49.934
2021-11-27 | 7:20 | 49.933
2021-11-27 | 7:20 | 49.932
2021-11-27 | 7:20 | 49.931
2021-11-27 | 7:20 | 49.928
2021-11-27 | 7:20 | 49.927
2021-11-27 | 7:20 | 49.927
2021-11-27 | 7:20 | 49.924
2021-11-27 | 7:20 | 49.925
2021-11-27 | 7:20 | 49.927
2021-11-27 | 7:20 | 49.927
2021-11-27 | 7:20 | 49.928
2021-11-27 | 7:20 | 49.922
2021-11-27 | 7:21 | 49.917
2021-11-27 | 7:21 | 49.911
2021-11-27 | 7:21 | 49.906
2021-11-27 | 7:21 | 49.903
2021-11-27 | 7:21 | 49.901
2021-11-27 | 7:21 | 49.9
2021-11-27 | 7:21 | 49.901
2021-11-27 | 7:21 | 49.902
2021-11-27 | 7:21 | 49.904
2021-11-27 | 7:21 | 49.904
2021-11-27 | 7:21 | 49.906
2021-11-27 | 7:21 | 49.908
2021-11-27 | 7:21 | 49.912
2021-11-27 | 7:21 | 49.917
2021-11-27 | 7:21 | 49.916
2021-11-27 | 7:21 | 49.915
2021-11-27 | 7:21 | 49.916
2021-11-27 | 7:21 | 49.917
2021-11-27 | 7:21 | 49.916
2021-11-27 | 7:21 | 49.916
2021-11-27 | 7:21 | 49.918
2021-11-27 | 7:21 | 49.924
2021-11-27 | 7:21 | 49.929
2021-11-27 | 7:21 | 49.93
2021-11-27 | 7:21 | 49.928
2021-11-27 | 7:21 | 49.924
2021-11-27 | 7:21 | 49.922
2021-11-27 | 7:21 | 49.921
2021-11-27 | 7:21 | 49.921
2021-11-27 | 7:21 | 49.923
2021-11-27 | 7:21 | 49.926
2021-11-27 | 7:21 | 49.927
2021-11-27 | 7:21 | 49.928
2021-11-27 | 7:21 | 49.929
2021-11-27 | 7:21 | 49.929
2021-11-27 | 7:21 | 49.93
2021-11-27 | 7:21 | 49.927
2021-11-27 | 7:21 | 49.928
2021-11-27 | 7:21 | 49.928
2021-11-27 | 7:21 | 49.929
2021-11-27 | 7:21 | 49.928
2021-11-27 | 7:21 | 49.928
2021-11-27 | 7:21 | 49.93
2021-11-27 | 7:21 | 49.931
2021-11-27 | 7:21 | 49.933
2021-11-27 | 7:21 | 49.934
2021-11-27 | 7:21 | 49.935
2021-11-27 | 7:21 | 49.936
2021-11-27 | 7:21 | 49.937
2021-11-27 | 7:21 | 49.937
2021-11-27 | 7:21 | 49.938
2021-11-27 | 7:21 | 49.937
2021-11-27 | 7:21 | 49.939
2021-11-27 | 7:21 | 49.941
2021-11-27 | 7:21 | 49.939
2021-11-27 | 7:21 | 49.939
2021-11-27 | 7:21 | 49.938
2021-11-27 | 7:21 | 49.94
2021-11-27 | 7:21 | 49.942
2021-11-27 | 7:21 | 49.945
2021-11-27 | 7:21 | 49.946
2021-11-27 | 7:22 | 49.947
2021-11-27 | 7:22 | 49.95
2021-11-27 | 7:22 | 49.952
2021-11-27 | 7:22 | 49.953
2021-11-27 | 7:22 | 49.956
2021-11-27 | 7:22 | 49.96
2021-11-27 | 7:22 | 49.961
2021-11-27 | 7:22 | 49.964
2021-11-27 | 7:22 | 49.964
2021-11-27 | 7:22 | 49.963
2021-11-27 | 7:22 | 49.965
2021-11-27 | 7:22 | 49.963
2021-11-27 | 7:22 | 49.962
2021-11-27 | 7:22 | 49.961
2021-11-27 | 7:22 | 49.958
2021-11-27 | 7:22 | 49.957
2021-11-27 | 7:22 | 49.957
2021-11-27 | 7:22 | 49.956
2021-11-27 | 7:22 | 49.956
2021-11-27 | 7:22 | 49.957
2021-11-27 | 7:22 | 49.958
2021-11-27 | 7:22 | 49.958
2021-11-27 | 7:22 | 49.959
2021-11-27 | 7:22 | 49.958
2021-11-27 | 7:22 | 49.958
2021-11-27 | 7:22 | 49.958
2021-11-27 | 7:22 | 49.96
2021-11-27 | 7:22 | 49.959
2021-11-27 | 7:22 | 49.956
2021-11-27 | 7:22 | 49.954
2021-11-27 | 7:22 | 49.951
2021-11-27 | 7:22 | 49.948
2021-11-27 | 7:22 | 49.946
2021-11-27 | 7:22 | 49.945
2021-11-27 | 7:22 | 49.942
2021-11-27 | 7:22 | 49.941
2021-11-27 | 7:22 | 49.941
2021-11-27 | 7:22 | 49.939
2021-11-27 | 7:22 | 49.937
2021-11-27 | 7:22 | 49.937
2021-11-27 | 7:22 | 49.94
2021-11-27 | 7:22 | 49.944
2021-11-27 | 7:22 | 49.945
2021-11-27 | 7:22 | 49.947
2021-11-27 | 7:22 | 49.945
2021-11-27 | 7:22 | 49.945
2021-11-27 | 7:22 | 49.942
2021-11-27 | 7:22 | 49.939
2021-11-27 | 7:22 | 49.937
2021-11-27 | 7:22 | 49.934
2021-11-27 | 7:22 | 49.932
2021-11-27 | 7:22 | 49.932
2021-11-27 | 7:22 | 49.932
2021-11-27 | 7:22 | 49.929
2021-11-27 | 7:22 | 49.927
2021-11-27 | 7:22 | 49.925
2021-11-27 | 7:22 | 49.927
2021-11-27 | 7:22 | 49.928
2021-11-27 | 7:22 | 49.929
2021-11-27 | 7:23 | 49.932
2021-11-27 | 7:23 | 49.933
2021-11-27 | 7:23 | 49.934
2021-11-27 | 7:23 | 49.936
2021-11-27 | 7:23 | 49.936
2021-11-27 | 7:23 | 49.936
2021-11-27 | 7:23 | 49.934
2021-11-27 | 7:23 | 49.932
2021-11-27 | 7:23 | 49.931
2021-11-27 | 7:23 | 49.932
2021-11-27 | 7:23 | 49.932
2021-11-27 | 7:23 | 49.933
2021-11-27 | 7:23 | 49.933
2021-11-27 | 7:23 | 49.933
2021-11-27 | 7:23 | 49.932
2021-11-27 | 7:23 | 49.932
2021-11-27 | 7:23 | 49.93
2021-11-27 | 7:23 | 49.932
2021-11-27 | 7:23 | 49.936
2021-11-27 | 7:23 | 49.937
2021-11-27 | 7:23 | 49.937
2021-11-27 | 7:23 | 49.939
2021-11-27 | 7:23 | 49.94
2021-11-27 | 7:23 | 49.941
2021-11-27 | 7:23 | 49.941
2021-11-27 | 7:23 | 49.944
2021-11-27 | 7:23 | 49.946
2021-11-27 | 7:23 | 49.947
2021-11-27 | 7:23 | 49.949
2021-11-27 | 7:23 | 49.952
2021-11-27 | 7:23 | 49.954
2021-11-27 | 7:23 | 49.955
2021-11-27 | 7:23 | 49.956
2021-11-27 | 7:23 | 49.954
2021-11-27 | 7:23 | 49.949
2021-11-27 | 7:23 | 49.946
2021-11-27 | 7:23 | 49.945
2021-11-27 | 7:23 | 49.945
2021-11-27 | 7:23 | 49.943
2021-11-27 | 7:23 | 49.942
2021-11-27 | 7:23 | 49.943
2021-11-27 | 7:23 | 49.944
2021-11-27 | 7:23 | 49.946
2021-11-27 | 7:23 | 49.946
2021-11-27 | 7:23 | 49.945
2021-11-27 | 7:23 | 49.948
2021-11-27 | 7:23 | 49.949
2021-11-27 | 7:23 | 49.949
2021-11-27 | 7:23 | 49.953
2021-11-27 | 7:23 | 49.955
2021-11-27 | 7:23 | 49.956
2021-11-27 | 7:23 | 49.955
2021-11-27 | 7:23 | 49.956
2021-11-27 | 7:23 | 49.957
2021-11-27 | 7:23 | 49.959
2021-11-27 | 7:23 | 49.964
2021-11-27 | 7:23 | 49.965
2021-11-27 | 7:23 | 49.966
2021-11-27 | 7:23 | 49.966
2021-11-27 | 7:23 | 49.967
2021-11-27 | 7:23 | 49.971
2021-11-27 | 7:24 | 49.973
2021-11-27 | 7:24 | 49.974
2021-11-27 | 7:24 | 49.973
2021-11-27 | 7:24 | 49.973
2021-11-27 | 7:24 | 49.973
2021-11-27 | 7:24 | 49.972
2021-11-27 | 7:24 | 49.97
2021-11-27 | 7:24 | 49.968
2021-11-27 | 7:24 | 49.967
2021-11-27 | 7:24 | 49.964
2021-11-27 | 7:24 | 49.961
2021-11-27 | 7:24 | 49.958
2021-11-27 | 7:24 | 49.955
2021-11-27 | 7:24 | 49.952
2021-11-27 | 7:24 | 49.951
2021-11-27 | 7:24 | 49.952
2021-11-27 | 7:24 | 49.955
2021-11-27 | 7:24 | 49.955
2021-11-27 | 7:24 | 49.954
2021-11-27 | 7:24 | 49.954
2021-11-27 | 7:24 | 49.956
2021-11-27 | 7:24 | 49.96
2021-11-27 | 7:24 | 49.962
2021-11-27 | 7:24 | 49.962
2021-11-27 | 7:24 | 49.964
2021-11-27 | 7:24 | 49.965
2021-11-27 | 7:24 | 49.969
2021-11-27 | 7:24 | 49.969
2021-11-27 | 7:24 | 49.971
2021-11-27 | 7:24 | 49.973
2021-11-27 | 7:24 | 49.971
2021-11-27 | 7:24 | 49.969
2021-11-27 | 7:24 | 49.967
2021-11-27 | 7:24 | 49.967
2021-11-27 | 7:24 | 49.965
2021-11-27 | 7:24 | 49.963
2021-11-27 | 7:24 | 49.961
2021-11-27 | 7:24 | 49.956
2021-11-27 | 7:24 | 49.953
2021-11-27 | 7:24 | 49.952
2021-11-27 | 7:24 | 49.953
2021-11-27 | 7:24 | 49.955
2021-11-27 | 7:24 | 49.957
2021-11-27 | 7:24 | 49.957
2021-11-27 | 7:24 | 49.96
2021-11-27 | 7:24 | 49.963
2021-11-27 | 7:24 | 49.963
2021-11-27 | 7:24 | 49.963
2021-11-27 | 7:24 | 49.962
2021-11-27 | 7:24 | 49.959
2021-11-27 | 7:24 | 49.958
2021-11-27 | 7:24 | 49.96
2021-11-27 | 7:24 | 49.961
2021-11-27 | 7:24 | 49.961
2021-11-27 | 7:24 | 49.962
2021-11-27 | 7:24 | 49.962
2021-11-27 | 7:24 | 49.963
2021-11-27 | 7:24 | 49.962
2021-11-27 | 7:24 | 49.96
2021-11-27 | 7:25 | 49.957
2021-11-27 | 7:25 | 49.955
2021-11-27 | 7:25 | 49.95
2021-11-27 | 7:25 | 49.944
2021-11-27 | 7:25 | 49.941
2021-11-27 | 7:25 | 49.938
2021-11-27 | 7:25 | 49.935
2021-11-27 | 7:25 | 49.933
2021-11-27 | 7:25 | 49.929
2021-11-27 | 7:25 | 49.924
2021-11-27 | 7:25 | 49.924
2021-11-27 | 7:25 | 49.926
2021-11-27 | 7:25 | 49.93
2021-11-27 | 7:25 | 49.932
2021-11-27 | 7:25 | 49.94
2021-11-27 | 7:25 | 49.944
2021-11-27 | 7:25 | 49.948
2021-11-27 | 7:25 | 49.952
2021-11-27 | 7:25 | 49.954
2021-11-27 | 7:25 | 49.956
2021-11-27 | 7:25 | 49.956
2021-11-27 | 7:25 | 49.956
2021-11-27 | 7:25 | 49.953
2021-11-27 | 7:25 | 49.952
2021-11-27 | 7:25 | 49.951
2021-11-27 | 7:25 | 49.949
2021-11-27 | 7:25 | 49.948
2021-11-27 | 7:25 | 49.949
2021-11-27 | 7:25 | 49.949
2021-11-27 | 7:25 | 49.947
2021-11-27 | 7:25 | 49.946
2021-11-27 | 7:25 | 49.943
2021-11-27 | 7:25 | 49.942
2021-11-27 | 7:25 | 49.942
2021-11-27 | 7:25 | 49.944
2021-11-27 | 7:25 | 49.946
2021-11-27 | 7:25 | 49.944
2021-11-27 | 7:25 | 49.942
2021-11-27 | 7:25 | 49.94
2021-11-27 | 7:25 | 49.939
2021-11-27 | 7:25 | 49.938
2021-11-27 | 7:25 | 49.94
2021-11-27 | 7:25 | 49.943
2021-11-27 | 7:25 | 49.945
2021-11-27 | 7:25 | 49.946
2021-11-27 | 7:25 | 49.948
2021-11-27 | 7:25 | 49.95
2021-11-27 | 7:25 | 49.951
2021-11-27 | 7:25 | 49.951
2021-11-27 | 7:25 | 49.951
2021-11-27 | 7:25 | 49.951
2021-11-27 | 7:25 | 49.953
2021-11-27 | 7:25 | 49.954
2021-11-27 | 7:25 | 49.954
2021-11-27 | 7:25 | 49.955
2021-11-27 | 7:25 | 49.955
2021-11-27 | 7:25 | 49.955
2021-11-27 | 7:25 | 49.955
2021-11-27 | 7:25 | 49.955
2021-11-27 | 7:25 | 49.956
2021-11-27 | 7:26 | 49.956
2021-11-27 | 7:26 | 49.955
2021-11-27 | 7:26 | 49.956
2021-11-27 | 7:26 | 49.955
2021-11-27 | 7:26 | 49.954
2021-11-27 | 7:26 | 49.954
2021-11-27 | 7:26 | 49.954
2021-11-27 | 7:26 | 49.955
2021-11-27 | 7:26 | 49.954
2021-11-27 | 7:26 | 49.953
2021-11-27 | 7:26 | 49.952
2021-11-27 | 7:26 | 49.951
2021-11-27 | 7:26 | 49.949
2021-11-27 | 7:26 | 49.949
2021-11-27 | 7:26 | 49.951
2021-11-27 | 7:26 | 49.951
2021-11-27 | 7:26 | 49.951
2021-11-27 | 7:26 | 49.952
2021-11-27 | 7:26 | 49.951
2021-11-27 | 7:26 | 49.951
2021-11-27 | 7:26 | 49.951
2021-11-27 | 7:26 | 49.95
2021-11-27 | 7:26 | 49.947
2021-11-27 | 7:26 | 49.945
2021-11-27 | 7:26 | 49.942
2021-11-27 | 7:26 | 49.938
2021-11-27 | 7:26 | 49.937
2021-11-27 | 7:26 | 49.937
2021-11-27 | 7:26 | 49.936
2021-11-27 | 7:26 | 49.934
2021-11-27 | 7:26 | 49.931
2021-11-27 | 7:26 | 49.93
2021-11-27 | 7:26 | 49.928
2021-11-27 | 7:26 | 49.928
2021-11-27 | 7:26 | 49.923
2021-11-27 | 7:26 | 49.923
2021-11-27 | 7:26 | 49.924
2021-11-27 | 7:26 | 49.924
2021-11-27 | 7:26 | 49.924
2021-11-27 | 7:26 | 49.924
2021-11-27 | 7:26 | 49.924
2021-11-27 | 7:26 | 49.927
2021-11-27 | 7:26 | 49.927
2021-11-27 | 7:26 | 49.928
2021-11-27 | 7:26 | 49.931
2021-11-27 | 7:26 | 49.931
2021-11-27 | 7:26 | 49.931
2021-11-27 | 7:26 | 49.929
2021-11-27 | 7:26 | 49.928
2021-11-27 | 7:26 | 49.927
2021-11-27 | 7:26 | 49.925
2021-11-27 | 7:26 | 49.923
2021-11-27 | 7:26 | 49.92
2021-11-27 | 7:26 | 49.919
2021-11-27 | 7:26 | 49.918
2021-11-27 | 7:26 | 49.918
2021-11-27 | 7:26 | 49.918
2021-11-27 | 7:26 | 49.918
2021-11-27 | 7:26 | 49.919
2021-11-27 | 7:26 | 49.921
2021-11-27 | 7:26 | 49.924
2021-11-27 | 7:27 | 49.928
2021-11-27 | 7:27 | 49.931
2021-11-27 | 7:27 | 49.935
2021-11-27 | 7:27 | 49.935
2021-11-27 | 7:27 | 49.935
2021-11-27 | 7:27 | 49.934
2021-11-27 | 7:27 | 49.932
2021-11-27 | 7:27 | 49.93
2021-11-27 | 7:27 | 49.928
2021-11-27 | 7:27 | 49.926
2021-11-27 | 7:27 | 49.924
2021-11-27 | 7:27 | 49.922
2021-11-27 | 7:27 | 49.92
2021-11-27 | 7:27 | 49.919
2021-11-27 | 7:27 | 49.917
2021-11-27 | 7:27 | 49.918
2021-11-27 | 7:27 | 49.918
2021-11-27 | 7:27 | 49.916
2021-11-27 | 7:27 | 49.916
2021-11-27 | 7:27 | 49.917
2021-11-27 | 7:27 | 49.918
2021-11-27 | 7:27 | 49.919
2021-11-27 | 7:27 | 49.919
2021-11-27 | 7:27 | 49.921
2021-11-27 | 7:27 | 49.922
2021-11-27 | 7:27 | 49.924
2021-11-27 | 7:27 | 49.924
2021-11-27 | 7:27 | 49.925
2021-11-27 | 7:27 | 49.924
2021-11-27 | 7:27 | 49.922
2021-11-27 | 7:27 | 49.919
2021-11-27 | 7:27 | 49.916
2021-11-27 | 7:27 | 49.912
2021-11-27 | 7:27 | 49.911
2021-11-27 | 7:27 | 49.91
2021-11-27 | 7:27 | 49.911
2021-11-27 | 7:27 | 49.913
2021-11-27 | 7:27 | 49.913
2021-11-27 | 7:27 | 49.914
2021-11-27 | 7:27 | 49.917
2021-11-27 | 7:27 | 49.92
2021-11-27 | 7:27 | 49.922
2021-11-27 | 7:27 | 49.922
2021-11-27 | 7:27 | 49.922
2021-11-27 | 7:27 | 49.923
2021-11-27 | 7:27 | 49.924
2021-11-27 | 7:27 | 49.927
2021-11-27 | 7:27 | 49.926
2021-11-27 | 7:27 | 49.927
2021-11-27 | 7:27 | 49.928
2021-11-27 | 7:27 | 49.927
2021-11-27 | 7:27 | 49.926
2021-11-27 | 7:27 | 49.925
2021-11-27 | 7:27 | 49.924
2021-11-27 | 7:27 | 49.925
2021-11-27 | 7:27 | 49.924
2021-11-27 | 7:27 | 49.924
2021-11-27 | 7:27 | 49.924
2021-11-27 | 7:27 | 49.927
2021-11-27 | 7:28 | 49.929
2021-11-27 | 7:28 | 49.932
2021-11-27 | 7:28 | 49.934
2021-11-27 | 7:28 | 49.936
2021-11-27 | 7:28 | 49.938
2021-11-27 | 7:28 | 49.938
2021-11-27 | 7:28 | 49.938
2021-11-27 | 7:28 | 49.936
2021-11-27 | 7:28 | 49.936
2021-11-27 | 7:28 | 49.935
2021-11-27 | 7:28 | 49.935
2021-11-27 | 7:28 | 49.934
2021-11-27 | 7:28 | 49.934
2021-11-27 | 7:28 | 49.931
2021-11-27 | 7:28 | 49.93
2021-11-27 | 7:28 | 49.929
2021-11-27 | 7:28 | 49.932
2021-11-27 | 7:28 | 49.933
2021-11-27 | 7:28 | 49.933
2021-11-27 | 7:28 | 49.932
2021-11-27 | 7:28 | 49.932
2021-11-27 | 7:28 | 49.931
2021-11-27 | 7:28 | 49.929
2021-11-27 | 7:28 | 49.926
2021-11-27 | 7:28 | 49.923
2021-11-27 | 7:28 | 49.924
2021-11-27 | 7:28 | 49.926
2021-11-27 | 7:28 | 49.926
2021-11-27 | 7:28 | 49.927
2021-11-27 | 7:28 | 49.928
2021-11-27 | 7:28 | 49.929
2021-11-27 | 7:28 | 49.926
2021-11-27 | 7:28 | 49.926
2021-11-27 | 7:28 | 49.926
2021-11-27 | 7:28 | 49.927
2021-11-27 | 7:28 | 49.929
2021-11-27 | 7:28 | 49.929
2021-11-27 | 7:28 | 49.93
2021-11-27 | 7:28 | 49.93
2021-11-27 | 7:28 | 49.93
2021-11-27 | 7:28 | 49.931
2021-11-27 | 7:28 | 49.928
2021-11-27 | 7:28 | 49.929
2021-11-27 | 7:28 | 49.927
2021-11-27 | 7:28 | 49.927
2021-11-27 | 7:28 | 49.926
2021-11-27 | 7:28 | 49.924
2021-11-27 | 7:28 | 49.925
2021-11-27 | 7:28 | 49.925
2021-11-27 | 7:28 | 49.926
2021-11-27 | 7:28 | 49.927
2021-11-27 | 7:28 | 49.928
2021-11-27 | 7:28 | 49.927
2021-11-27 | 7:28 | 49.929
2021-11-27 | 7:28 | 49.933
2021-11-27 | 7:28 | 49.935
2021-11-27 | 7:28 | 49.937
2021-11-27 | 7:28 | 49.937
2021-11-27 | 7:28 | 49.939
2021-11-27 | 7:28 | 49.938
2021-11-27 | 7:28 | 49.941
2021-11-27 | 7:29 | 49.943
2021-11-27 | 7:29 | 49.948
2021-11-27 | 7:29 | 49.952
2021-11-27 | 7:29 | 49.955
2021-11-27 | 7:29 | 49.957
2021-11-27 | 7:29 | 49.959
2021-11-27 | 7:29 | 49.959
2021-11-27 | 7:29 | 49.959
2021-11-27 | 7:29 | 49.959
2021-11-27 | 7:29 | 49.962
2021-11-27 | 7:29 | 49.96
2021-11-27 | 7:29 | 49.961
2021-11-27 | 7:29 | 49.968
2021-11-27 | 7:29 | 49.975
2021-11-27 | 7:29 | 49.978
2021-11-27 | 7:29 | 49.98
2021-11-27 | 7:29 | 49.982
2021-11-27 | 7:29 | 49.983
2021-11-27 | 7:29 | 49.984
2021-11-27 | 7:29 | 49.985
2021-11-27 | 7:29 | 49.984
2021-11-27 | 7:29 | 49.988
2021-11-27 | 7:29 | 49.99
2021-11-27 | 7:29 | 49.992
2021-11-27 | 7:29 | 49.994
2021-11-27 | 7:29 | 49.995
2021-11-27 | 7:29 | 49.997
2021-11-27 | 7:29 | 50.001
2021-11-27 | 7:29 | 50.004

## F20211127-2
In GMT
Date | Time | Freq
2021-11-27 | 9:39 | 49.923
2021-11-27 | 9:39 | 49.922
2021-11-27 | 9:39 | 49.923
2021-11-27 | 9:39 | 49.921
2021-11-27 | 9:39 | 49.92
2021-11-27 | 9:39 | 49.921
2021-11-27 | 9:39 | 49.922
2021-11-27 | 9:39 | 49.922
2021-11-27 | 9:39 | 49.922
2021-11-27 | 9:39 | 49.92
2021-11-27 | 9:39 | 49.922
2021-11-27 | 9:39 | 49.921
2021-11-27 | 9:39 | 49.923
2021-11-27 | 9:39 | 49.922
2021-11-27 | 9:39 | 49.92
2021-11-27 | 9:39 | 49.921
2021-11-27 | 9:39 | 49.922
2021-11-27 | 9:39 | 49.922
2021-11-27 | 9:39 | 49.922
2021-11-27 | 9:39 | 49.92
2021-11-27 | 9:39 | 49.92
2021-11-27 | 9:39 | 49.921
2021-11-27 | 9:39 | 49.921
2021-11-27 | 9:39 | 49.922
2021-11-27 | 9:39 | 49.922
2021-11-27 | 9:39 | 49.92
2021-11-27 | 9:39 | 49.921
2021-11-27 | 9:39 | 49.921
2021-11-27 | 9:39 | 49.922
2021-11-27 | 9:39 | 49.919
2021-11-27 | 9:40 | 49.919
2021-11-27 | 9:40 | 49.919
2021-11-27 | 9:40 | 49.921
2021-11-27 | 9:40 | 49.921
2021-11-27 | 9:40 | 49.922
2021-11-27 | 9:40 | 49.923
2021-11-27 | 9:40 | 49.923
2021-11-27 | 9:40 | 49.924
2021-11-27 | 9:40 | 49.927
2021-11-27 | 9:40 | 49.93
2021-11-27 | 9:40 | 49.933
2021-11-27 | 9:40 | 49.936
2021-11-27 | 9:40 | 49.941
2021-11-27 | 9:40 | 49.945
2021-11-27 | 9:40 | 49.95
2021-11-27 | 9:40 | 49.951
2021-11-27 | 9:40 | 49.952
2021-11-27 | 9:40 | 49.95
2021-11-27 | 9:40 | 49.949
2021-11-27 | 9:40 | 49.946
2021-11-27 | 9:40 | 49.945
2021-11-27 | 9:40 | 49.945
2021-11-27 | 9:40 | 49.944
2021-11-27 | 9:40 | 49.943
2021-11-27 | 9:40 | 49.944
2021-11-27 | 9:40 | 49.946
2021-11-27 | 9:40 | 49.95
2021-11-27 | 9:40 | 49.953
2021-11-27 | 9:40 | 49.954
2021-11-27 | 9:40 | 49.955
2021-11-27 | 9:40 | 49.957
2021-11-27 | 9:40 | 49.96
2021-11-27 | 9:40 | 49.96
2021-11-27 | 9:40 | 49.961
2021-11-27 | 9:40 | 49.96
2021-11-27 | 9:40 | 49.957
2021-11-27 | 9:40 | 49.955
2021-11-27 | 9:40 | 49.952
2021-11-27 | 9:40 | 49.951
2021-11-27 | 9:40 | 49.953
2021-11-27 | 9:40 | 49.955
2021-11-27 | 9:40 | 49.959
2021-11-27 | 9:40 | 49.961
2021-11-27 | 9:40 | 49.964
2021-11-27 | 9:40 | 49.963
2021-11-27 | 9:40 | 49.956
2021-11-27 | 9:40 | 49.928
2021-11-27 | 9:40 | 49.901
2021-11-27 | 9:40 | 49.891
2021-11-27 | 9:40 | 49.886
2021-11-27 | 9:40 | 49.881
2021-11-27 | 9:40 | 49.881
2021-11-27 | 9:40 | 49.88
2021-11-27 | 9:40 | 49.88
2021-11-27 | 9:40 | 49.881
2021-11-27 | 9:40 | 49.882
2021-11-27 | 9:40 | 49.881
2021-11-27 | 9:40 | 49.88
2021-11-27 | 9:40 | 49.879
2021-11-27 | 9:40 | 49.878
2021-11-27 | 9:40 | 49.876
2021-11-27 | 9:41 | 49.875
2021-11-27 | 9:41 | 49.875
2021-11-27 | 9:41 | 49.877
2021-11-27 | 9:41 | 49.877
2021-11-27 | 9:41 | 49.875
2021-11-27 | 9:41 | 49.872
2021-11-27 | 9:41 | 49.867
2021-11-27 | 9:41 | 49.864
2021-11-27 | 9:41 | 49.859
2021-11-27 | 9:41 | 49.856
2021-11-27 | 9:41 | 49.854
2021-11-27 | 9:41 | 49.852
2021-11-27 | 9:41 | 49.852
2021-11-27 | 9:41 | 49.853
2021-11-27 | 9:41 | 49.854
2021-11-27 | 9:41 | 49.855
2021-11-27 | 9:41 | 49.857
2021-11-27 | 9:41 | 49.86
2021-11-27 | 9:41 | 49.864
2021-11-27 | 9:41 | 49.865
2021-11-27 | 9:41 | 49.868
2021-11-27 | 9:41 | 49.87
2021-11-27 | 9:41 | 49.872
2021-11-27 | 9:41 | 49.874
2021-11-27 | 9:41 | 49.876
2021-11-27 | 9:41 | 49.878
2021-11-27 | 9:41 | 49.881
2021-11-27 | 9:41 | 49.882
2021-11-27 | 9:41 | 49.882
2021-11-27 | 9:41 | 49.883
2021-11-27 | 9:41 | 49.883
2021-11-27 | 9:41 | 49.883
2021-11-27 | 9:41 | 49.881
2021-11-27 | 9:41 | 49.879
2021-11-27 | 9:41 | 49.877
2021-11-27 | 9:41 | 49.877
2021-11-27 | 9:41 | 49.876
2021-11-27 | 9:41 | 49.874
2021-11-27 | 9:41 | 49.874
2021-11-27 | 9:41 | 49.872
2021-11-27 | 9:41 | 49.87
2021-11-27 | 9:41 | 49.868
2021-11-27 | 9:41 | 49.868
2021-11-27 | 9:41 | 49.869
2021-11-27 | 9:41 | 49.872
2021-11-27 | 9:41 | 49.876
2021-11-27 | 9:41 | 49.878
2021-11-27 | 9:41 | 49.882
2021-11-27 | 9:41 | 49.885
2021-11-27 | 9:41 | 49.887
2021-11-27 | 9:41 | 49.888
2021-11-27 | 9:41 | 49.888
2021-11-27 | 9:41 | 49.889
2021-11-27 | 9:41 | 49.888
2021-11-27 | 9:41 | 49.886
2021-11-27 | 9:41 | 49.886
2021-11-27 | 9:41 | 49.884
2021-11-27 | 9:41 | 49.883
2021-11-27 | 9:41 | 49.883
2021-11-27 | 9:41 | 49.884
2021-11-27 | 9:42 | 49.884
2021-11-27 | 9:42 | 49.885
2021-11-27 | 9:42 | 49.889
2021-11-27 | 9:42 | 49.892
2021-11-27 | 9:42 | 49.894
2021-11-27 | 9:42 | 49.894
2021-11-27 | 9:42 | 49.897
2021-11-27 | 9:42 | 49.9
2021-11-27 | 9:42 | 49.902
2021-11-27 | 9:42 | 49.903
2021-11-27 | 9:42 | 49.906
2021-11-27 | 9:42 | 49.908
2021-11-27 | 9:42 | 49.91
2021-11-27 | 9:42 | 49.911
2021-11-27 | 9:42 | 49.909
2021-11-27 | 9:42 | 49.909
2021-11-27 | 9:42 | 49.908
2021-11-27 | 9:42 | 49.907
2021-11-27 | 9:42 | 49.907
2021-11-27 | 9:42 | 49.906
2021-11-27 | 9:42 | 49.906
2021-11-27 | 9:42 | 49.908
2021-11-27 | 9:42 | 49.907
2021-11-27 | 9:42 | 49.909
2021-11-27 | 9:42 | 49.91
2021-11-27 | 9:42 | 49.909
2021-11-27 | 9:42 | 49.911
2021-11-27 | 9:42 | 49.91
2021-11-27 | 9:42 | 49.908
2021-11-27 | 9:42 | 49.905
2021-11-27 | 9:42 | 49.903
2021-11-27 | 9:42 | 49.901
2021-11-27 | 9:42 | 49.899
2021-11-27 | 9:42 | 49.901
2021-11-27 | 9:42 | 49.902
2021-11-27 | 9:42 | 49.902
2021-11-27 | 9:42 | 49.901
2021-11-27 | 9:42 | 49.903
2021-11-27 | 9:42 | 49.903
2021-11-27 | 9:42 | 49.905
2021-11-27 | 9:42 | 49.906
2021-11-27 | 9:42 | 49.909
2021-11-27 | 9:42 | 49.912
2021-11-27 | 9:42 | 49.915
2021-11-27 | 9:42 | 49.918
2021-11-27 | 9:42 | 49.921
2021-11-27 | 9:42 | 49.923
2021-11-27 | 9:42 | 49.923
2021-11-27 | 9:42 | 49.925
2021-11-27 | 9:42 | 49.923
2021-11-27 | 9:42 | 49.921
2021-11-27 | 9:42 | 49.92
2021-11-27 | 9:42 | 49.919
2021-11-27 | 9:42 | 49.918
2021-11-27 | 9:42 | 49.917
2021-11-27 | 9:42 | 49.918
2021-11-27 | 9:42 | 49.915
2021-11-27 | 9:42 | 49.913
2021-11-27 | 9:42 | 49.914
2021-11-27 | 9:43 | 49.914
2021-11-27 | 9:43 | 49.913
2021-11-27 | 9:43 | 49.917
2021-11-27 | 9:43 | 49.92
2021-11-27 | 9:43 | 49.924
2021-11-27 | 9:43 | 49.926
2021-11-27 | 9:43 | 49.928
2021-11-27 | 9:43 | 49.93
2021-11-27 | 9:43 | 49.931
2021-11-27 | 9:43 | 49.932
2021-11-27 | 9:43 | 49.93
2021-11-27 | 9:43 | 49.929
2021-11-27 | 9:43 | 49.927
2021-11-27 | 9:43 | 49.926
2021-11-27 | 9:43 | 49.926
2021-11-27 | 9:43 | 49.924
2021-11-27 | 9:43 | 49.921
2021-11-27 | 9:43 | 49.919
2021-11-27 | 9:43 | 49.919
2021-11-27 | 9:43 | 49.919
2021-11-27 | 9:43 | 49.921
2021-11-27 | 9:43 | 49.922
2021-11-27 | 9:43 | 49.925
2021-11-27 | 9:43 | 49.928
2021-11-27 | 9:43 | 49.93
2021-11-27 | 9:43 | 49.931
2021-11-27 | 9:43 | 49.931
2021-11-27 | 9:43 | 49.933
2021-11-27 | 9:43 | 49.936
2021-11-27 | 9:43 | 49.936
2021-11-27 | 9:43 | 49.934
2021-11-27 | 9:43 | 49.933
2021-11-27 | 9:43 | 49.933
2021-11-27 | 9:43 | 49.934
2021-11-27 | 9:43 | 49.933
2021-11-27 | 9:43 | 49.933
2021-11-27 | 9:43 | 49.934
2021-11-27 | 9:43 | 49.938
2021-11-27 | 9:43 | 49.941
2021-11-27 | 9:43 | 49.944
2021-11-27 | 9:43 | 49.947
2021-11-27 | 9:43 | 49.948
2021-11-27 | 9:43 | 49.949
2021-11-27 | 9:43 | 49.949
2021-11-27 | 9:43 | 49.947
2021-11-27 | 9:43 | 49.946
2021-11-27 | 9:43 | 49.943
2021-11-27 | 9:43 | 49.941
2021-11-27 | 9:43 | 49.941
2021-11-27 | 9:43 | 49.938
2021-11-27 | 9:43 | 49.937
2021-11-27 | 9:43 | 49.936
2021-11-27 | 9:43 | 49.937
2021-11-27 | 9:43 | 49.938
2021-11-27 | 9:43 | 49.937
2021-11-27 | 9:43 | 49.934
2021-11-27 | 9:43 | 49.932
2021-11-27 | 9:43 | 49.931
2021-11-27 | 9:43 | 49.93
2021-11-27 | 9:43 | 49.929
2021-11-27 | 9:43 | 49.93
2021-11-27 | 9:44 | 49.931
2021-11-27 | 9:44 | 49.933
2021-11-27 | 9:44 | 49.934
2021-11-27 | 9:44 | 49.935
2021-11-27 | 9:44 | 49.935
2021-11-27 | 9:44 | 49.934
2021-11-27 | 9:44 | 49.935
2021-11-27 | 9:44 | 49.939
2021-11-27 | 9:44 | 49.941
2021-11-27 | 9:44 | 49.942
2021-11-27 | 9:44 | 49.943
2021-11-27 | 9:44 | 49.947
2021-11-27 | 9:44 | 49.949
2021-11-27 | 9:44 | 49.95
2021-11-27 | 9:44 | 49.951
2021-11-27 | 9:44 | 49.952
2021-11-27 | 9:44 | 49.953
2021-11-27 | 9:44 | 49.955
2021-11-27 | 9:44 | 49.958
2021-11-27 | 9:44 | 49.96
2021-11-27 | 9:44 | 49.962
2021-11-27 | 9:44 | 49.963
2021-11-27 | 9:44 | 49.964
2021-11-27 | 9:44 | 49.963
2021-11-27 | 9:44 | 49.963
2021-11-27 | 9:44 | 49.963
2021-11-27 | 9:44 | 49.964
2021-11-27 | 9:44 | 49.966
2021-11-27 | 9:44 | 49.969
2021-11-27 | 9:44 | 49.97
2021-11-27 | 9:44 | 49.97
2021-11-27 | 9:44 | 49.969
2021-11-27 | 9:44 | 49.968
2021-11-27 | 9:44 | 49.966
2021-11-27 | 9:44 | 49.963
2021-11-27 | 9:44 | 49.962
2021-11-27 | 9:44 | 49.963
2021-11-27 | 9:44 | 49.961
2021-11-27 | 9:44 | 49.959
2021-11-27 | 9:44 | 49.958
2021-11-27 | 9:44 | 49.957
2021-11-27 | 9:44 | 49.959
2021-11-27 | 9:44 | 49.961
2021-11-27 | 9:44 | 49.965
2021-11-27 | 9:44 | 49.967
2021-11-27 | 9:44 | 49.966
2021-11-27 | 9:44 | 49.965
2021-11-27 | 9:44 | 49.965
2021-11-27 | 9:44 | 49.963
2021-11-27 | 9:44 | 49.962
2021-11-27 | 9:44 | 49.959
2021-11-27 | 9:44 | 49.957
2021-11-27 | 9:44 | 49.954
2021-11-27 | 9:44 | 49.955
2021-11-27 | 9:44 | 49.954
2021-11-27 | 9:44 | 49.956
2021-11-27 | 9:44 | 49.956
2021-11-27 | 9:44 | 49.956
2021-11-27 | 9:44 | 49.955
2021-11-27 | 9:45 | 49.956
2021-11-27 | 9:45 | 49.957
2021-11-27 | 9:45 | 49.959
2021-11-27 | 9:45 | 49.961
2021-11-27 | 9:45 | 49.964
2021-11-27 | 9:45 | 49.964
2021-11-27 | 9:45 | 49.964
2021-11-27 | 9:45 | 49.968
2021-11-27 | 9:45 | 49.968
2021-11-27 | 9:45 | 49.97
2021-11-27 | 9:45 | 49.972
2021-11-27 | 9:45 | 49.973
2021-11-27 | 9:45 | 49.976
2021-11-27 | 9:45 | 49.977
2021-11-27 | 9:45 | 49.979
2021-11-27 | 9:45 | 49.981
2021-11-27 | 9:45 | 49.98
2021-11-27 | 9:45 | 49.979
2021-11-27 | 9:45 | 49.982
2021-11-27 | 9:45 | 49.985
2021-11-27 | 9:45 | 49.985
2021-11-27 | 9:45 | 49.985
2021-11-27 | 9:45 | 49.987
2021-11-27 | 9:45 | 49.987
2021-11-27 | 9:45 | 49.988
2021-11-27 | 9:45 | 49.985
2021-11-27 | 9:45 | 49.985
2021-11-27 | 9:45 | 49.987
2021-11-27 | 9:45 | 49.987
2021-11-27 | 9:45 | 49.987
2021-11-27 | 9:45 | 49.986
2021-11-27 | 9:45 | 49.984
2021-11-27 | 9:45 | 49.984
2021-11-27 | 9:45 | 49.98
2021-11-27 | 9:45 | 49.981
2021-11-27 | 9:45 | 49.979
2021-11-27 | 9:45 | 49.978
2021-11-27 | 9:45 | 49.977
2021-11-27 | 9:45 | 49.976
2021-11-27 | 9:45 | 49.975
2021-11-27 | 9:45 | 49.972
2021-11-27 | 9:45 | 49.97
2021-11-27 | 9:45 | 49.969
2021-11-27 | 9:45 | 49.969
2021-11-27 | 9:45 | 49.969
2021-11-27 | 9:45 | 49.97
2021-11-27 | 9:45 | 49.972
2021-11-27 | 9:45 | 49.973
2021-11-27 | 9:45 | 49.974
2021-11-27 | 9:45 | 49.975
2021-11-27 | 9:45 | 49.974
2021-11-27 | 9:45 | 49.972
2021-11-27 | 9:45 | 49.971
2021-11-27 | 9:45 | 49.97
2021-11-27 | 9:45 | 49.966
2021-11-27 | 9:45 | 49.962
2021-11-27 | 9:45 | 49.956
2021-11-27 | 9:45 | 49.952
2021-11-27 | 9:45 | 49.947
2021-11-27 | 9:45 | 49.941
2021-11-27 | 9:45 | 49.939
2021-11-27 | 9:46 | 49.94
2021-11-27 | 9:46 | 49.94
2021-11-27 | 9:46 | 49.941
2021-11-27 | 9:46 | 49.941
2021-11-27 | 9:46 | 49.939
2021-11-27 | 9:46 | 49.938
2021-11-27 | 9:46 | 49.937
2021-11-27 | 9:46 | 49.936
2021-11-27 | 9:46 | 49.936
2021-11-27 | 9:46 | 49.934
2021-11-27 | 9:46 | 49.933
2021-11-27 | 9:46 | 49.93
2021-11-27 | 9:46 | 49.931
2021-11-27 | 9:46 | 49.931
2021-11-27 | 9:46 | 49.932
2021-11-27 | 9:46 | 49.93
2021-11-27 | 9:46 | 49.929
2021-11-27 | 9:46 | 49.929
2021-11-27 | 9:46 | 49.93
2021-11-27 | 9:46 | 49.929
2021-11-27 | 9:46 | 49.928
2021-11-27 | 9:46 | 49.929
2021-11-27 | 9:46 | 49.931
2021-11-27 | 9:46 | 49.933
2021-11-27 | 9:46 | 49.932
2021-11-27 | 9:46 | 49.932
2021-11-27 | 9:46 | 49.933
2021-11-27 | 9:46 | 49.932
2021-11-27 | 9:46 | 49.93
2021-11-27 | 9:46 | 49.93
2021-11-27 | 9:46 | 49.93
2021-11-27 | 9:46 | 49.93
2021-11-27 | 9:46 | 49.929
2021-11-27 | 9:46 | 49.931
2021-11-27 | 9:46 | 49.929
2021-11-27 | 9:46 | 49.928
2021-11-27 | 9:46 | 49.926
2021-11-27 | 9:46 | 49.925
2021-11-27 | 9:46 | 49.924
2021-11-27 | 9:46 | 49.926
2021-11-27 | 9:46 | 49.927
2021-11-27 | 9:46 | 49.929
2021-11-27 | 9:46 | 49.933
2021-11-27 | 9:46 | 49.936
2021-11-27 | 9:46 | 49.938
2021-11-27 | 9:46 | 49.94
2021-11-27 | 9:46 | 49.941
2021-11-27 | 9:46 | 49.942
2021-11-27 | 9:46 | 49.942
2021-11-27 | 9:46 | 49.944
2021-11-27 | 9:46 | 49.944
2021-11-27 | 9:46 | 49.946
2021-11-27 | 9:46 | 49.945
2021-11-27 | 9:46 | 49.943
2021-11-27 | 9:46 | 49.941
2021-11-27 | 9:46 | 49.94
2021-11-27 | 9:46 | 49.94
2021-11-27 | 9:46 | 49.939
2021-11-27 | 9:46 | 49.937
2021-11-27 | 9:47 | 49.937
2021-11-27 | 9:47 | 49.936
2021-11-27 | 9:47 | 49.935
2021-11-27 | 9:47 | 49.935
2021-11-27 | 9:47 | 49.935
2021-11-27 | 9:47 | 49.934
2021-11-27 | 9:47 | 49.933
2021-11-27 | 9:47 | 49.934
2021-11-27 | 9:47 | 49.934
2021-11-27 | 9:47 | 49.932
2021-11-27 | 9:47 | 49.929
2021-11-27 | 9:47 | 49.93
2021-11-27 | 9:47 | 49.932
2021-11-27 | 9:47 | 49.935
2021-11-27 | 9:47 | 49.938
2021-11-27 | 9:47 | 49.937
2021-11-27 | 9:47 | 49.936
2021-11-27 | 9:47 | 49.932
2021-11-27 | 9:47 | 49.927
2021-11-27 | 9:47 | 49.923
2021-11-27 | 9:47 | 49.919
2021-11-27 | 9:47 | 49.916
2021-11-27 | 9:47 | 49.914
2021-11-27 | 9:47 | 49.913
2021-11-27 | 9:47 | 49.911
2021-11-27 | 9:47 | 49.913
2021-11-27 | 9:47 | 49.915
2021-11-27 | 9:47 | 49.916
2021-11-27 | 9:47 | 49.918
2021-11-27 | 9:47 | 49.921
2021-11-27 | 9:47 | 49.927
2021-11-27 | 9:47 | 49.931
2021-11-27 | 9:47 | 49.935
2021-11-27 | 9:47 | 49.939
2021-11-27 | 9:47 | 49.944
2021-11-27 | 9:47 | 49.95
2021-11-27 | 9:47 | 49.957
2021-11-27 | 9:47 | 49.961
2021-11-27 | 9:47 | 49.964
2021-11-27 | 9:47 | 49.966
2021-11-27 | 9:47 | 49.967
2021-11-27 | 9:47 | 49.965
2021-11-27 | 9:47 | 49.964
2021-11-27 | 9:47 | 49.962
2021-11-27 | 9:47 | 49.963
2021-11-27 | 9:47 | 49.962
2021-11-27 | 9:47 | 49.961
2021-11-27 | 9:47 | 49.96
2021-11-27 | 9:47 | 49.959
2021-11-27 | 9:47 | 49.956
2021-11-27 | 9:47 | 49.954
2021-11-27 | 9:47 | 49.953
2021-11-27 | 9:47 | 49.954
2021-11-27 | 9:47 | 49.954
2021-11-27 | 9:47 | 49.955
2021-11-27 | 9:47 | 49.956
2021-11-27 | 9:47 | 49.956
2021-11-27 | 9:47 | 49.955
2021-11-27 | 9:47 | 49.953
2021-11-27 | 9:47 | 49.952
2021-11-27 | 9:47 | 49.951
2021-11-27 | 9:48 | 49.95
2021-11-27 | 9:48 | 49.95
2021-11-27 | 9:48 | 49.951
2021-11-27 | 9:48 | 49.951
2021-11-27 | 9:48 | 49.948
2021-11-27 | 9:48 | 49.947
2021-11-27 | 9:48 | 49.946
2021-11-27 | 9:48 | 49.946
2021-11-27 | 9:48 | 49.945
2021-11-27 | 9:48 | 49.945
2021-11-27 | 9:48 | 49.943
2021-11-27 | 9:48 | 49.941
2021-11-27 | 9:48 | 49.941
2021-11-27 | 9:48 | 49.941
2021-11-27 | 9:48 | 49.939
2021-11-27 | 9:48 | 49.937
2021-11-27 | 9:48 | 49.934
2021-11-27 | 9:48 | 49.934
2021-11-27 | 9:48 | 49.935
2021-11-27 | 9:48 | 49.933
2021-11-27 | 9:48 | 49.931
2021-11-27 | 9:48 | 49.931
2021-11-27 | 9:48 | 49.931
2021-11-27 | 9:48 | 49.931
2021-11-27 | 9:48 | 49.932
2021-11-27 | 9:48 | 49.933
2021-11-27 | 9:48 | 49.933
2021-11-27 | 9:48 | 49.933
2021-11-27 | 9:48 | 49.932
2021-11-27 | 9:48 | 49.932
2021-11-27 | 9:48 | 49.93
2021-11-27 | 9:48 | 49.93
2021-11-27 | 9:48 | 49.933
2021-11-27 | 9:48 | 49.933
2021-11-27 | 9:48 | 49.933
2021-11-27 | 9:48 | 49.934
2021-11-27 | 9:48 | 49.935
2021-11-27 | 9:48 | 49.935
2021-11-27 | 9:48 | 49.935
2021-11-27 | 9:48 | 49.935
2021-11-27 | 9:48 | 49.933
2021-11-27 | 9:48 | 49.932
2021-11-27 | 9:48 | 49.932
2021-11-27 | 9:48 | 49.933
2021-11-27 | 9:48 | 49.931
2021-11-27 | 9:48 | 49.931
2021-11-27 | 9:48 | 49.931
2021-11-27 | 9:48 | 49.931
2021-11-27 | 9:48 | 49.932
2021-11-27 | 9:48 | 49.934
2021-11-27 | 9:48 | 49.933
2021-11-27 | 9:48 | 49.933
2021-11-27 | 9:48 | 49.932
2021-11-27 | 9:48 | 49.931
2021-11-27 | 9:48 | 49.93
2021-11-27 | 9:48 | 49.928
2021-11-27 | 9:48 | 49.927
2021-11-27 | 9:48 | 49.924
2021-11-27 | 9:48 | 49.922
2021-11-27 | 9:49 | 49.921
2021-11-27 | 9:49 | 49.92
2021-11-27 | 9:49 | 49.921
2021-11-27 | 9:49 | 49.923
2021-11-27 | 9:49 | 49.923
2021-11-27 | 9:49 | 49.926
2021-11-27 | 9:49 | 49.928
2021-11-27 | 9:49 | 49.932
2021-11-27 | 9:49 | 49.934
2021-11-27 | 9:49 | 49.935
2021-11-27 | 9:49 | 49.935
2021-11-27 | 9:49 | 49.933
2021-11-27 | 9:49 | 49.932
2021-11-27 | 9:49 | 49.93
2021-11-27 | 9:49 | 49.931
2021-11-27 | 9:49 | 49.929
2021-11-27 | 9:49 | 49.926
2021-11-27 | 9:49 | 49.924
2021-11-27 | 9:49 | 49.921
2021-11-27 | 9:49 | 49.919
2021-11-27 | 9:49 | 49.917
2021-11-27 | 9:49 | 49.914
2021-11-27 | 9:49 | 49.914
2021-11-27 | 9:49 | 49.916
2021-11-27 | 9:49 | 49.917
2021-11-27 | 9:49 | 49.919
2021-11-27 | 9:49 | 49.923
2021-11-27 | 9:49 | 49.923
2021-11-27 | 9:49 | 49.924
2021-11-27 | 9:49 | 49.925
2021-11-27 | 9:49 | 49.923
2021-11-27 | 9:49 | 49.921
2021-11-27 | 9:49 | 49.922
2021-11-27 | 9:49 | 49.923
2021-11-27 | 9:49 | 49.924
2021-11-27 | 9:49 | 49.926
2021-11-27 | 9:49 | 49.928
2021-11-27 | 9:49 | 49.93
2021-11-27 | 9:49 | 49.933
2021-11-27 | 9:49 | 49.931
2021-11-27 | 9:49 | 49.931
2021-11-27 | 9:49 | 49.93
2021-11-27 | 9:49 | 49.931
2021-11-27 | 9:49 | 49.93
2021-11-27 | 9:49 | 49.929
2021-11-27 | 9:49 | 49.931
2021-11-27 | 9:49 | 49.935
2021-11-27 | 9:49 | 49.94
2021-11-27 | 9:49 | 49.943
2021-11-27 | 9:49 | 49.948
2021-11-27 | 9:49 | 49.95
2021-11-27 | 9:49 | 49.95
2021-11-27 | 9:49 | 49.949
2021-11-27 | 9:49 | 49.945
2021-11-27 | 9:49 | 49.943
2021-11-27 | 9:49 | 49.942
2021-11-27 | 9:49 | 49.942
2021-11-27 | 9:49 | 49.94
2021-11-27 | 9:49 | 49.94
2021-11-27 | 9:49 | 49.94
2021-11-27 | 9:50 | 49.94
2021-11-27 | 9:50 | 49.94
2021-11-27 | 9:50 | 49.94
2021-11-27 | 9:50 | 49.938
2021-11-27 | 9:50 | 49.938
2021-11-27 | 9:50 | 49.942
2021-11-27 | 9:50 | 49.946
2021-11-27 | 9:50 | 49.949
2021-11-27 | 9:50 | 49.95
2021-11-27 | 9:50 | 49.948
2021-11-27 | 9:50 | 49.947
2021-11-27 | 9:50 | 49.945
2021-11-27 | 9:50 | 49.943
2021-11-27 | 9:50 | 49.941
2021-11-27 | 9:50 | 49.94
2021-11-27 | 9:50 | 49.939
2021-11-27 | 9:50 | 49.941
2021-11-27 | 9:50 | 49.943
2021-11-27 | 9:50 | 49.944
2021-11-27 | 9:50 | 49.944
2021-11-27 | 9:50 | 49.946
2021-11-27 | 9:50 | 49.947
2021-11-27 | 9:50 | 49.95
2021-11-27 | 9:50 | 49.951
2021-11-27 | 9:50 | 49.951
2021-11-27 | 9:50 | 49.953
2021-11-27 | 9:50 | 49.954
2021-11-27 | 9:50 | 49.956
2021-11-27 | 9:50 | 49.957
2021-11-27 | 9:50 | 49.958
2021-11-27 | 9:50 | 49.96
2021-11-27 | 9:50 | 49.959
2021-11-27 | 9:50 | 49.957
2021-11-27 | 9:50 | 49.954
2021-11-27 | 9:50 | 49.953
2021-11-27 | 9:50 | 49.951
2021-11-27 | 9:50 | 49.948
2021-11-27 | 9:50 | 49.945
2021-11-27 | 9:50 | 49.94
2021-11-27 | 9:50 | 49.936
2021-11-27 | 9:50 | 49.933
2021-11-27 | 9:50 | 49.932
2021-11-27 | 9:50 | 49.932
2021-11-27 | 9:50 | 49.93
2021-11-27 | 9:50 | 49.929
2021-11-27 | 9:50 | 49.923
2021-11-27 | 9:50 | 49.921
2021-11-27 | 9:50 | 49.918
2021-11-27 | 9:50 | 49.915
2021-11-27 | 9:50 | 49.914
2021-11-27 | 9:50 | 49.914
2021-11-27 | 9:50 | 49.917
2021-11-27 | 9:50 | 49.919
2021-11-27 | 9:50 | 49.921
2021-11-27 | 9:50 | 49.921
2021-11-27 | 9:50 | 49.921
2021-11-27 | 9:50 | 49.921
2021-11-27 | 9:50 | 49.922
2021-11-27 | 9:50 | 49.923
2021-11-27 | 9:50 | 49.921
2021-11-27 | 9:50 | 49.92
2021-11-27 | 9:51 | 49.918
2021-11-27 | 9:51 | 49.916
2021-11-27 | 9:51 | 49.913
2021-11-27 | 9:51 | 49.909
2021-11-27 | 9:51 | 49.907
2021-11-27 | 9:51 | 49.907
2021-11-27 | 9:51 | 49.906
2021-11-27 | 9:51 | 49.907
2021-11-27 | 9:51 | 49.909
2021-11-27 | 9:51 | 49.91
2021-11-27 | 9:51 | 49.912
2021-11-27 | 9:51 | 49.911
2021-11-27 | 9:51 | 49.911
2021-11-27 | 9:51 | 49.909
2021-11-27 | 9:51 | 49.909
2021-11-27 | 9:51 | 49.907
2021-11-27 | 9:51 | 49.907
2021-11-27 | 9:51 | 49.906
2021-11-27 | 9:51 | 49.908
2021-11-27 | 9:51 | 49.911
2021-11-27 | 9:51 | 49.913
2021-11-27 | 9:51 | 49.916
2021-11-27 | 9:51 | 49.918
2021-11-27 | 9:51 | 49.92
2021-11-27 | 9:51 | 49.922
2021-11-27 | 9:51 | 49.922
2021-11-27 | 9:51 | 49.919
2021-11-27 | 9:51 | 49.918
2021-11-27 | 9:51 | 49.914
2021-11-27 | 9:51 | 49.911
2021-11-27 | 9:51 | 49.909
2021-11-27 | 9:51 | 49.904
2021-11-27 | 9:51 | 49.902
2021-11-27 | 9:51 | 49.902
2021-11-27 | 9:51 | 49.903
2021-11-27 | 9:51 | 49.904
2021-11-27 | 9:51 | 49.906
2021-11-27 | 9:51 | 49.906
2021-11-27 | 9:51 | 49.905
2021-11-27 | 9:51 | 49.907
2021-11-27 | 9:51 | 49.908
2021-11-27 | 9:51 | 49.911
2021-11-27 | 9:51 | 49.913
2021-11-27 | 9:51 | 49.915
2021-11-27 | 9:51 | 49.916
2021-11-27 | 9:51 | 49.916
2021-11-27 | 9:51 | 49.913
2021-11-27 | 9:51 | 49.909
2021-11-27 | 9:51 | 49.903
2021-11-27 | 9:51 | 49.899
2021-11-27 | 9:51 | 49.895
2021-11-27 | 9:51 | 49.891
2021-11-27 | 9:51 | 49.89
2021-11-27 | 9:51 | 49.888
2021-11-27 | 9:51 | 49.888
2021-11-27 | 9:51 | 49.888
2021-11-27 | 9:51 | 49.886
2021-11-27 | 9:51 | 49.885
2021-11-27 | 9:51 | 49.884
2021-11-27 | 9:52 | 49.884
2021-11-27 | 9:52 | 49.886
2021-11-27 | 9:52 | 49.888
2021-11-27 | 9:52 | 49.888
2021-11-27 | 9:52 | 49.888
2021-11-27 | 9:52 | 49.886
2021-11-27 | 9:52 | 49.884
2021-11-27 | 9:52 | 49.879
2021-11-27 | 9:52 | 49.874
2021-11-27 | 9:52 | 49.871
2021-11-27 | 9:52 | 49.869
2021-11-27 | 9:52 | 49.868
2021-11-27 | 9:52 | 49.867
2021-11-27 | 9:52 | 49.867
2021-11-27 | 9:52 | 49.868
2021-11-27 | 9:52 | 49.871
2021-11-27 | 9:52 | 49.871
2021-11-27 | 9:52 | 49.873
2021-11-27 | 9:52 | 49.873
2021-11-27 | 9:52 | 49.872
2021-11-27 | 9:52 | 49.872
2021-11-27 | 9:52 | 49.873
2021-11-27 | 9:52 | 49.873
2021-11-27 | 9:52 | 49.872
2021-11-27 | 9:52 | 49.87
2021-11-27 | 9:52 | 49.868
2021-11-27 | 9:52 | 49.866
2021-11-27 | 9:52 | 49.865
2021-11-27 | 9:52 | 49.864
2021-11-27 | 9:52 | 49.864
2021-11-27 | 9:52 | 49.865
2021-11-27 | 9:52 | 49.866
2021-11-27 | 9:52 | 49.865
2021-11-27 | 9:52 | 49.866
2021-11-27 | 9:52 | 49.866
2021-11-27 | 9:52 | 49.868
2021-11-27 | 9:52 | 49.867
2021-11-27 | 9:52 | 49.866
2021-11-27 | 9:52 | 49.862
2021-11-27 | 9:52 | 49.859
2021-11-27 | 9:52 | 49.856
2021-11-27 | 9:52 | 49.855
2021-11-27 | 9:52 | 49.854
2021-11-27 | 9:52 | 49.852
2021-11-27 | 9:52 | 49.849
2021-11-27 | 9:52 | 49.849
2021-11-27 | 9:52 | 49.848
2021-11-27 | 9:52 | 49.848
2021-11-27 | 9:52 | 49.845
2021-11-27 | 9:52 | 49.844
2021-11-27 | 9:52 | 49.841
2021-11-27 | 9:52 | 49.841
2021-11-27 | 9:52 | 49.84
2021-11-27 | 9:52 | 49.837
2021-11-27 | 9:52 | 49.836
2021-11-27 | 9:52 | 49.835
2021-11-27 | 9:52 | 49.835
2021-11-27 | 9:52 | 49.834
2021-11-27 | 9:52 | 49.833
2021-11-27 | 9:52 | 49.833
2021-11-27 | 9:52 | 49.833
2021-11-27 | 9:53 | 49.836
2021-11-27 | 9:53 | 49.84
2021-11-27 | 9:53 | 49.845
2021-11-27 | 9:53 | 49.852
2021-11-27 | 9:53 | 49.86
2021-11-27 | 9:53 | 49.866
2021-11-27 | 9:53 | 49.869
2021-11-27 | 9:53 | 49.873
2021-11-27 | 9:53 | 49.878
2021-11-27 | 9:53 | 49.884
2021-11-27 | 9:53 | 49.889
2021-11-27 | 9:53 | 49.893
2021-11-27 | 9:53 | 49.896
2021-11-27 | 9:53 | 49.897
2021-11-27 | 9:53 | 49.897
2021-11-27 | 9:53 | 49.897
2021-11-27 | 9:53 | 49.898
2021-11-27 | 9:53 | 49.896
2021-11-27 | 9:53 | 49.892
2021-11-27 | 9:53 | 49.889
2021-11-27 | 9:53 | 49.887
2021-11-27 | 9:53 | 49.885
2021-11-27 | 9:53 | 49.884
2021-11-27 | 9:53 | 49.884
2021-11-27 | 9:53 | 49.886
2021-11-27 | 9:53 | 49.888
2021-11-27 | 9:53 | 49.889
2021-11-27 | 9:53 | 49.887
2021-11-27 | 9:53 | 49.887
2021-11-27 | 9:53 | 49.887
2021-11-27 | 9:53 | 49.887
2021-11-27 | 9:53 | 49.886
2021-11-27 | 9:53 | 49.886
2021-11-27 | 9:53 | 49.885
2021-11-27 | 9:53 | 49.886
2021-11-27 | 9:53 | 49.889
2021-11-27 | 9:53 | 49.889
2021-11-27 | 9:53 | 49.891
2021-11-27 | 9:53 | 49.892
2021-11-27 | 9:53 | 49.893
2021-11-27 | 9:53 | 49.895
2021-11-27 | 9:53 | 49.896
2021-11-27 | 9:53 | 49.898
2021-11-27 | 9:53 | 49.898
2021-11-27 | 9:53 | 49.9
2021-11-27 | 9:53 | 49.901
2021-11-27 | 9:53 | 49.9
2021-11-27 | 9:53 | 49.901
2021-11-27 | 9:53 | 49.9
2021-11-27 | 9:53 | 49.899
2021-11-27 | 9:53 | 49.901
2021-11-27 | 9:53 | 49.905
2021-11-27 | 9:53 | 49.908
2021-11-27 | 9:53 | 49.912
2021-11-27 | 9:53 | 49.916
2021-11-27 | 9:53 | 49.921
2021-11-27 | 9:53 | 49.921
2021-11-27 | 9:53 | 49.921
2021-11-27 | 9:53 | 49.92
2021-11-27 | 9:54 | 49.919
2021-11-27 | 9:54 | 49.92
2021-11-27 | 9:54 | 49.92
2021-11-27 | 9:54 | 49.918
2021-11-27 | 9:54 | 49.918
2021-11-27 | 9:54 | 49.917
2021-11-27 | 9:54 | 49.915
2021-11-27 | 9:54 | 49.914
2021-11-27 | 9:54 | 49.914
2021-11-27 | 9:54 | 49.913
2021-11-27 | 9:54 | 49.913
2021-11-27 | 9:54 | 49.913
2021-11-27 | 9:54 | 49.913
2021-11-27 | 9:54 | 49.915
2021-11-27 | 9:54 | 49.916
2021-11-27 | 9:54 | 49.916
2021-11-27 | 9:54 | 49.914
2021-11-27 | 9:54 | 49.914
2021-11-27 | 9:54 | 49.914
2021-11-27 | 9:54 | 49.913
2021-11-27 | 9:54 | 49.913
2021-11-27 | 9:54 | 49.911
2021-11-27 | 9:54 | 49.911
2021-11-27 | 9:54 | 49.911
2021-11-27 | 9:54 | 49.911
2021-11-27 | 9:54 | 49.912
2021-11-27 | 9:54 | 49.914
2021-11-27 | 9:54 | 49.916
2021-11-27 | 9:54 | 49.917
2021-11-27 | 9:54 | 49.917
2021-11-27 | 9:54 | 49.915
2021-11-27 | 9:54 | 49.914
2021-11-27 | 9:54 | 49.913
2021-11-27 | 9:54 | 49.912
2021-11-27 | 9:54 | 49.913
2021-11-27 | 9:54 | 49.914
2021-11-27 | 9:54 | 49.915
2021-11-27 | 9:54 | 49.916
2021-11-27 | 9:54 | 49.918
2021-11-27 | 9:54 | 49.92
2021-11-27 | 9:54 | 49.921
2021-11-27 | 9:54 | 49.922
2021-11-27 | 9:54 | 49.922
2021-11-27 | 9:54 | 49.92
2021-11-27 | 9:54 | 49.919
2021-11-27 | 9:54 | 49.918
2021-11-27 | 9:54 | 49.917
2021-11-27 | 9:54 | 49.917
2021-11-27 | 9:54 | 49.918
2021-11-27 | 9:54 | 49.921
2021-11-27 | 9:54 | 49.925
2021-11-27 | 9:54 | 49.927
2021-11-27 | 9:54 | 49.928
2021-11-27 | 9:54 | 49.931
2021-11-27 | 9:54 | 49.932
2021-11-27 | 9:54 | 49.933
2021-11-27 | 9:54 | 49.934
2021-11-27 | 9:54 | 49.934
2021-11-27 | 9:54 | 49.935
2021-11-27 | 9:54 | 49.935
2021-11-27 | 9:54 | 49.938
2021-11-27 | 9:55 | 49.94
2021-11-27 | 9:55 | 49.942
2021-11-27 | 9:55 | 49.942
2021-11-27 | 9:55 | 49.947
2021-11-27 | 9:55 | 49.95
2021-11-27 | 9:55 | 49.95
2021-11-27 | 9:55 | 49.953
2021-11-27 | 9:55 | 49.95
2021-11-27 | 9:55 | 49.95
2021-11-27 | 9:55 | 49.947
2021-11-27 | 9:55 | 49.945
2021-11-27 | 9:55 | 49.944
2021-11-27 | 9:55 | 49.941
2021-11-27 | 9:55 | 49.938
2021-11-27 | 9:55 | 49.935
2021-11-27 | 9:55 | 49.933
2021-11-27 | 9:55 | 49.927
2021-11-27 | 9:55 | 49.92
2021-11-27 | 9:55 | 49.913
2021-11-27 | 9:55 | 49.907
2021-11-27 | 9:55 | 49.899
2021-11-27 | 9:55 | 49.888
2021-11-27 | 9:55 | 49.88
2021-11-27 | 9:55 | 49.876
2021-11-27 | 9:55 | 49.879
2021-11-27 | 9:55 | 49.888
2021-11-27 | 9:55 | 49.899
2021-11-27 | 9:55 | 49.911
2021-11-27 | 9:55 | 49.918
2021-11-27 | 9:55 | 49.919
2021-11-27 | 9:55 | 49.923
2021-11-27 | 9:55 | 49.926
2021-11-27 | 9:55 | 49.929
2021-11-27 | 9:55 | 49.936
2021-11-27 | 9:55 | 49.944
2021-11-27 | 9:55 | 49.949
2021-11-27 | 9:55 | 49.956
2021-11-27 | 9:55 | 49.958
2021-11-27 | 9:55 | 49.957
2021-11-27 | 9:55 | 49.959
2021-11-27 | 9:55 | 49.956
2021-11-27 | 9:55 | 49.956
2021-11-27 | 9:55 | 49.957
2021-11-27 | 9:55 | 49.956
2021-11-27 | 9:55 | 49.955
2021-11-27 | 9:55 | 49.953
2021-11-27 | 9:55 | 49.951
2021-11-27 | 9:55 | 49.947
2021-11-27 | 9:55 | 49.945
2021-11-27 | 9:55 | 49.942
2021-11-27 | 9:55 | 49.938
2021-11-27 | 9:55 | 49.935
2021-11-27 | 9:55 | 49.932
2021-11-27 | 9:55 | 49.929
2021-11-27 | 9:55 | 49.926
2021-11-27 | 9:55 | 49.923
2021-11-27 | 9:55 | 49.919
2021-11-27 | 9:55 | 49.917
2021-11-27 | 9:55 | 49.914
2021-11-27 | 9:56 | 49.913
2021-11-27 | 9:56 | 49.914
2021-11-27 | 9:56 | 49.916
2021-11-27 | 9:56 | 49.92
2021-11-27 | 9:56 | 49.926
2021-11-27 | 9:56 | 49.932
2021-11-27 | 9:56 | 49.938
2021-11-27 | 9:56 | 49.945
2021-11-27 | 9:56 | 49.949
2021-11-27 | 9:56 | 49.952
2021-11-27 | 9:56 | 49.953
2021-11-27 | 9:56 | 49.955
2021-11-27 | 9:56 | 49.956
2021-11-27 | 9:56 | 49.955
2021-11-27 | 9:56 | 49.954
2021-11-27 | 9:56 | 49.954
2021-11-27 | 9:56 | 49.954
2021-11-27 | 9:56 | 49.955
2021-11-27 | 9:56 | 49.955
2021-11-27 | 9:56 | 49.956
2021-11-27 | 9:56 | 49.957
2021-11-27 | 9:56 | 49.956
2021-11-27 | 9:56 | 49.956
2021-11-27 | 9:56 | 49.956
2021-11-27 | 9:56 | 49.957
2021-11-27 | 9:56 | 49.957
2021-11-27 | 9:56 | 49.958
2021-11-27 | 9:56 | 49.957
2021-11-27 | 9:56 | 49.957
2021-11-27 | 9:56 | 49.955
2021-11-27 | 9:56 | 49.954
2021-11-27 | 9:56 | 49.955
2021-11-27 | 9:56 | 49.956
2021-11-27 | 9:56 | 49.958
2021-11-27 | 9:56 | 49.959
2021-11-27 | 9:56 | 49.961
2021-11-27 | 9:56 | 49.962
2021-11-27 | 9:56 | 49.962
2021-11-27 | 9:56 | 49.958
2021-11-27 | 9:56 | 49.953
2021-11-27 | 9:56 | 49.949
2021-11-27 | 9:56 | 49.945
2021-11-27 | 9:56 | 49.94
2021-11-27 | 9:56 | 49.935
2021-11-27 | 9:56 | 49.932
2021-11-27 | 9:56 | 49.931
2021-11-27 | 9:56 | 49.929
2021-11-27 | 9:56 | 49.929
2021-11-27 | 9:56 | 49.931
2021-11-27 | 9:56 | 49.933
2021-11-27 | 9:56 | 49.941
2021-11-27 | 9:56 | 49.947
2021-11-27 | 9:56 | 49.953
2021-11-27 | 9:56 | 49.957
2021-11-27 | 9:56 | 49.961
2021-11-27 | 9:56 | 49.963
2021-11-27 | 9:56 | 49.964
2021-11-27 | 9:56 | 49.965
2021-11-27 | 9:56 | 49.966
2021-11-27 | 9:56 | 49.966
2021-11-27 | 9:56 | 49.966
2021-11-27 | 9:57 | 49.965
2021-11-27 | 9:57 | 49.963
2021-11-27 | 9:57 | 49.96
2021-11-27 | 9:57 | 49.958
2021-11-27 | 9:57 | 49.955
2021-11-27 | 9:57 | 49.952
2021-11-27 | 9:57 | 49.95
2021-11-27 | 9:57 | 49.949
2021-11-27 | 9:57 | 49.946
2021-11-27 | 9:57 | 49.943
2021-11-27 | 9:57 | 49.942
2021-11-27 | 9:57 | 49.939
2021-11-27 | 9:57 | 49.938
2021-11-27 | 9:57 | 49.936
2021-11-27 | 9:57 | 49.934
2021-11-27 | 9:57 | 49.932
2021-11-27 | 9:57 | 49.929
2021-11-27 | 9:57 | 49.929
2021-11-27 | 9:57 | 49.929
2021-11-27 | 9:57 | 49.927
2021-11-27 | 9:57 | 49.927
2021-11-27 | 9:57 | 49.925
2021-11-27 | 9:57 | 49.923
2021-11-27 | 9:57 | 49.924
2021-11-27 | 9:57 | 49.926
2021-11-27 | 9:57 | 49.927
2021-11-27 | 9:57 | 49.928
2021-11-27 | 9:57 | 49.931
2021-11-27 | 9:57 | 49.933
2021-11-27 | 9:57 | 49.937
2021-11-27 | 9:57 | 49.939
2021-11-27 | 9:57 | 49.941
2021-11-27 | 9:57 | 49.942
2021-11-27 | 9:57 | 49.941
2021-11-27 | 9:57 | 49.942
2021-11-27 | 9:57 | 49.943
2021-11-27 | 9:57 | 49.944
2021-11-27 | 9:57 | 49.944
2021-11-27 | 9:57 | 49.946
2021-11-27 | 9:57 | 49.945
2021-11-27 | 9:57 | 49.944
2021-11-27 | 9:57 | 49.943
2021-11-27 | 9:57 | 49.94
2021-11-27 | 9:57 | 49.938
2021-11-27 | 9:57 | 49.934
2021-11-27 | 9:57 | 49.933
2021-11-27 | 9:57 | 49.93
2021-11-27 | 9:57 | 49.929
2021-11-27 | 9:57 | 49.928
2021-11-27 | 9:57 | 49.928
2021-11-27 | 9:57 | 49.928
2021-11-27 | 9:57 | 49.927
2021-11-27 | 9:57 | 49.927
2021-11-27 | 9:57 | 49.928
2021-11-27 | 9:57 | 49.93
2021-11-27 | 9:57 | 49.931
2021-11-27 | 9:57 | 49.932
2021-11-27 | 9:57 | 49.933
2021-11-27 | 9:57 | 49.932
2021-11-27 | 9:58 | 49.93
2021-11-27 | 9:58 | 49.932
2021-11-27 | 9:58 | 49.93
2021-11-27 | 9:58 | 49.93
2021-11-27 | 9:58 | 49.93
2021-11-27 | 9:58 | 49.931
2021-11-27 | 9:58 | 49.933
2021-11-27 | 9:58 | 49.935
2021-11-27 | 9:58 | 49.938
2021-11-27 | 9:58 | 49.94
2021-11-27 | 9:58 | 49.942
2021-11-27 | 9:58 | 49.943
2021-11-27 | 9:58 | 49.943
2021-11-27 | 9:58 | 49.944
2021-11-27 | 9:58 | 49.946
2021-11-27 | 9:58 | 49.947
2021-11-27 | 9:58 | 49.948
2021-11-27 | 9:58 | 49.949
2021-11-27 | 9:58 | 49.949
2021-11-27 | 9:58 | 49.951
2021-11-27 | 9:58 | 49.954
2021-11-27 | 9:58 | 49.956
2021-11-27 | 9:58 | 49.957
2021-11-27 | 9:58 | 49.957
2021-11-27 | 9:58 | 49.954
2021-11-27 | 9:58 | 49.954
2021-11-27 | 9:58 | 49.951
2021-11-27 | 9:58 | 49.949
2021-11-27 | 9:58 | 49.947
2021-11-27 | 9:58 | 49.947
2021-11-27 | 9:58 | 49.946
2021-11-27 | 9:58 | 49.945
2021-11-27 | 9:58 | 49.944
2021-11-27 | 9:58 | 49.944
2021-11-27 | 9:58 | 49.946
2021-11-27 | 9:58 | 49.947
2021-11-27 | 9:58 | 49.95
2021-11-27 | 9:58 | 49.951
2021-11-27 | 9:58 | 49.952
2021-11-27 | 9:58 | 49.954
2021-11-27 | 9:58 | 49.956
2021-11-27 | 9:58 | 49.959
2021-11-27 | 9:58 | 49.96
2021-11-27 | 9:58 | 49.96
2021-11-27 | 9:58 | 49.961
2021-11-27 | 9:58 | 49.962
2021-11-27 | 9:58 | 49.962
2021-11-27 | 9:58 | 49.963
2021-11-27 | 9:58 | 49.962
2021-11-27 | 9:58 | 49.962
2021-11-27 | 9:58 | 49.961
2021-11-27 | 9:58 | 49.959
2021-11-27 | 9:58 | 49.96
2021-11-27 | 9:58 | 49.959
2021-11-27 | 9:58 | 49.957
2021-11-27 | 9:58 | 49.957
2021-11-27 | 9:58 | 49.957
2021-11-27 | 9:58 | 49.955
2021-11-27 | 9:58 | 49.952
2021-11-27 | 9:58 | 49.951
2021-11-27 | 9:58 | 49.949
2021-11-27 | 9:59 | 49.948
2021-11-27 | 9:59 | 49.946
2021-11-27 | 9:59 | 49.943
2021-11-27 | 9:59 | 49.939
2021-11-27 | 9:59 | 49.935
2021-11-27 | 9:59 | 49.933
2021-11-27 | 9:59 | 49.929
2021-11-27 | 9:59 | 49.925
2021-11-27 | 9:59 | 49.923
2021-11-27 | 9:59 | 49.921
2021-11-27 | 9:59 | 49.919
2021-11-27 | 9:59 | 49.917
2021-11-27 | 9:59 | 49.917
2021-11-27 | 9:59 | 49.915
2021-11-27 | 9:59 | 49.914
2021-11-27 | 9:59 | 49.912
2021-11-27 | 9:59 | 49.91
2021-11-27 | 9:59 | 49.908
2021-11-27 | 9:59 | 49.907
2021-11-27 | 9:59 | 49.906
2021-11-27 | 9:59 | 49.905
2021-11-27 | 9:59 | 49.905
2021-11-27 | 9:59 | 49.905
2021-11-27 | 9:59 | 49.907
2021-11-27 | 9:59 | 49.908
2021-11-27 | 9:59 | 49.909
2021-11-27 | 9:59 | 49.909
2021-11-27 | 9:59 | 49.91
2021-11-27 | 9:59 | 49.911
2021-11-27 | 9:59 | 49.911
2021-11-27 | 9:59 | 49.911
2021-11-27 | 9:59 | 49.908
2021-11-27 | 9:59 | 49.904
2021-11-27 | 9:59 | 49.904
2021-11-27 | 9:59 | 49.903
2021-11-27 | 9:59 | 49.901
2021-11-27 | 9:59 | 49.897
2021-11-27 | 9:59 | 49.894
2021-11-27 | 9:59 | 49.893
2021-11-27 | 9:59 | 49.892
2021-11-27 | 9:59 | 49.892
2021-11-27 | 9:59 | 49.891
2021-11-27 | 9:59 | 49.892
2021-11-27 | 9:59 | 49.896
2021-11-27 | 9:59 | 49.9
2021-11-27 | 9:59 | 49.902
2021-11-27 | 9:59 | 49.905
2021-11-27 | 9:59 | 49.907
2021-11-27 | 9:59 | 49.907
2021-11-27 | 9:59 | 49.908
2021-11-27 | 9:59 | 49.908
2021-11-27 | 9:59 | 49.908
2021-11-27 | 9:59 | 49.909
2021-11-27 | 9:59 | 49.908
2021-11-27 | 9:59 | 49.907
2021-11-27 | 9:59 | 49.907
2021-11-27 | 9:59 | 49.906
2021-11-27 | 9:59 | 49.904
2021-11-27 | 9:59 | 49.905
2021-11-27 | 9:59 | 49.905
2021-11-27 | 10:00 | 49.905
2021-11-27 | 10:00 | 49.906
2021-11-27 | 10:00 | 49.909
2021-11-27 | 10:00 | 49.91
2021-11-27 | 10:00 | 49.911
2021-11-27 | 10:00 | 49.912
2021-11-27 | 10:00 | 49.911
2021-11-27 | 10:00 | 49.911
2021-11-27 | 10:00 | 49.913
2021-11-27 | 10:00 | 49.913
2021-11-27 | 10:00 | 49.916
2021-11-27 | 10:00 | 49.918
2021-11-27 | 10:00 | 49.922
2021-11-27 | 10:00 | 49.924
2021-11-27 | 10:00 | 49.927
2021-11-27 | 10:00 | 49.928
2021-11-27 | 10:00 | 49.929
2021-11-27 | 10:00 | 49.929
2021-11-27 | 10:00 | 49.932
2021-11-27 | 10:00 | 49.933
2021-11-27 | 10:00 | 49.938
2021-11-27 | 10:00 | 49.94
2021-11-27 | 10:00 | 49.943
2021-11-27 | 10:00 | 49.947
2021-11-27 | 10:00 | 49.95
2021-11-27 | 10:00 | 49.954
2021-11-27 | 10:00 | 49.955
2021-11-27 | 10:00 | 49.957
2021-11-27 | 10:00 | 49.96
2021-11-27 | 10:00 | 49.961
2021-11-27 | 10:00 | 49.962
2021-11-27 | 10:00 | 49.961
2021-11-27 | 10:00 | 49.961
2021-11-27 | 10:00 | 49.961
2021-11-27 | 10:00 | 49.962
2021-11-27 | 10:00 | 49.963
2021-11-27 | 10:00 | 49.964
2021-11-27 | 10:00 | 49.966
2021-11-27 | 10:00 | 49.967
2021-11-27 | 10:00 | 49.968
2021-11-27 | 10:00 | 49.971
2021-11-27 | 10:00 | 49.972
2021-11-27 | 10:00 | 49.973
2021-11-27 | 10:00 | 49.975
2021-11-27 | 10:00 | 49.976
2021-11-27 | 10:00 | 49.976
2021-11-27 | 10:00 | 49.976
2021-11-27 | 10:00 | 49.974
2021-11-27 | 10:00 | 49.974
2021-11-27 | 10:00 | 49.972
2021-11-27 | 10:00 | 49.97
2021-11-27 | 10:00 | 49.97
2021-11-27 | 10:00 | 49.97
2021-11-27 | 10:00 | 49.974
2021-11-27 | 10:00 | 49.977
2021-11-27 | 10:00 | 49.979
2021-11-27 | 10:00 | 49.98
2021-11-27 | 10:00 | 49.979
2021-11-27 | 10:00 | 49.979
2021-11-27 | 10:01 | 49.98
2021-11-27 | 10:01 | 49.979
2021-11-27 | 10:01 | 49.978
2021-11-27 | 10:01 | 49.979
2021-11-27 | 10:01 | 49.979
2021-11-27 | 10:01 | 49.981
2021-11-27 | 10:01 | 49.981
2021-11-27 | 10:01 | 49.983
2021-11-27 | 10:01 | 49.987
2021-11-27 | 10:01 | 49.99
2021-11-27 | 10:01 | 49.992
2021-11-27 | 10:01 | 49.994
2021-11-27 | 10:01 | 49.995
2021-11-27 | 10:01 | 49.996
2021-11-27 | 10:01 | 49.996
2021-11-27 | 10:01 | 49.997
2021-11-27 | 10:01 | 49.998
2021-11-27 | 10:01 | 49.999
2021-11-27 | 10:01 | 50
2021-11-27 | 10:01 | 50.003
2021-11-27 | 10:01 | 50.009
2021-11-27 | 10:01 | 50.012
2021-11-27 | 10:01 | 50.016
2021-11-27 | 10:01 | 50.019
2021-11-27 | 10:01 | 50.021
2021-11-27 | 10:01 | 50.024
2021-11-27 | 10:01 | 50.023
2021-11-27 | 10:01 | 50.021
2021-11-27 | 10:01 | 50.018
2021-11-27 | 10:01 | 50.016

## F20211129-1
In GMT
Date | Time | Freq
2021-11-29 | 17:30 | 50.067
2021-11-29 | 17:30 | 50.065
2021-11-29 | 17:30 | 50.061
2021-11-29 | 17:30 | 50.057
2021-11-29 | 17:30 | 50.055
2021-11-29 | 17:30 | 50.051
2021-11-29 | 17:30 | 50.048
2021-11-29 | 17:30 | 50.047
2021-11-29 | 17:30 | 50.047
2021-11-29 | 17:30 | 50.047
2021-11-29 | 17:30 | 50.049
2021-11-29 | 17:30 | 50.049
2021-11-29 | 17:30 | 50.048
2021-11-29 | 17:30 | 50.048
2021-11-29 | 17:30 | 50.049
2021-11-29 | 17:30 | 50.048
2021-11-29 | 17:30 | 50.05
2021-11-29 | 17:30 | 50.05
2021-11-29 | 17:30 | 50.049
2021-11-29 | 17:30 | 50.048
2021-11-29 | 17:30 | 50.048
2021-11-29 | 17:30 | 50.047
2021-11-29 | 17:30 | 50.047
2021-11-29 | 17:30 | 50.048
2021-11-29 | 17:30 | 50.047
2021-11-29 | 17:30 | 50.05
2021-11-29 | 17:30 | 50.05
2021-11-29 | 17:30 | 50.046
2021-11-29 | 17:30 | 50.048
2021-11-29 | 17:30 | 50.046
2021-11-29 | 17:31 | 50.045
2021-11-29 | 17:31 | 50.043
2021-11-29 | 17:31 | 50.043
2021-11-29 | 17:31 | 50.043
2021-11-29 | 17:31 | 50.041
2021-11-29 | 17:31 | 50.037
2021-11-29 | 17:31 | 50.033
2021-11-29 | 17:31 | 50.031
2021-11-29 | 17:31 | 50.032
2021-11-29 | 17:31 | 50.031
2021-11-29 | 17:31 | 50.033
2021-11-29 | 17:31 | 50.036
2021-11-29 | 17:31 | 50.038
2021-11-29 | 17:31 | 50.04
2021-11-29 | 17:31 | 50.042
2021-11-29 | 17:31 | 50.043
2021-11-29 | 17:31 | 50.047
2021-11-29 | 17:31 | 50.048
2021-11-29 | 17:31 | 50.046
2021-11-29 | 17:31 | 50.046
2021-11-29 | 17:31 | 50.046
2021-11-29 | 17:31 | 50.046
2021-11-29 | 17:31 | 50.044
2021-11-29 | 17:31 | 50.044
2021-11-29 | 17:31 | 50.043
2021-11-29 | 17:31 | 50.04
2021-11-29 | 17:31 | 50.035
2021-11-29 | 17:31 | 50.028
2021-11-29 | 17:31 | 50.023
2021-11-29 | 17:31 | 50.015
2021-11-29 | 17:31 | 50.007
2021-11-29 | 17:31 | 50
2021-11-29 | 17:31 | 49.994
2021-11-29 | 17:31 | 49.99
2021-11-29 | 17:31 | 49.985
2021-11-29 | 17:31 | 49.982
2021-11-29 | 17:31 | 49.978
2021-11-29 | 17:31 | 49.976
2021-11-29 | 17:31 | 49.973
2021-11-29 | 17:31 | 49.969
2021-11-29 | 17:31 | 49.966
2021-11-29 | 17:31 | 49.962
2021-11-29 | 17:31 | 49.959
2021-11-29 | 17:31 | 49.959
2021-11-29 | 17:31 | 49.956
2021-11-29 | 17:31 | 49.951
2021-11-29 | 17:31 | 49.951
2021-11-29 | 17:31 | 49.948
2021-11-29 | 17:31 | 49.949
2021-11-29 | 17:31 | 49.948
2021-11-29 | 17:31 | 49.946
2021-11-29 | 17:31 | 49.946
2021-11-29 | 17:31 | 49.946
2021-11-29 | 17:31 | 49.947
2021-11-29 | 17:31 | 49.946
2021-11-29 | 17:31 | 49.948
2021-11-29 | 17:31 | 49.948
2021-11-29 | 17:31 | 49.949
2021-11-29 | 17:31 | 49.949
2021-11-29 | 17:31 | 49.948
2021-11-29 | 17:31 | 49.948
2021-11-29 | 17:32 | 49.948
2021-11-29 | 17:32 | 49.948
2021-11-29 | 17:32 | 49.947
2021-11-29 | 17:32 | 49.947
2021-11-29 | 17:32 | 49.948
2021-11-29 | 17:32 | 49.949
2021-11-29 | 17:32 | 49.95
2021-11-29 | 17:32 | 49.951
2021-11-29 | 17:32 | 49.951
2021-11-29 | 17:32 | 49.954
2021-11-29 | 17:32 | 49.957
2021-11-29 | 17:32 | 49.958
2021-11-29 | 17:32 | 49.962
2021-11-29 | 17:32 | 49.964
2021-11-29 | 17:32 | 49.966
2021-11-29 | 17:32 | 49.966
2021-11-29 | 17:32 | 49.966
2021-11-29 | 17:32 | 49.946
2021-11-29 | 17:32 | 49.93
2021-11-29 | 17:32 | 49.916
2021-11-29 | 17:32 | 49.897
2021-11-29 | 17:32 | 49.88
2021-11-29 | 17:32 | 49.866
2021-11-29 | 17:32 | 49.851
2021-11-29 | 17:32 | 49.843
2021-11-29 | 17:32 | 49.835
2021-11-29 | 17:32 | 49.831
2021-11-29 | 17:32 | 49.83
2021-11-29 | 17:32 | 49.826
2021-11-29 | 17:32 | 49.826
2021-11-29 | 17:32 | 49.826
2021-11-29 | 17:32 | 49.827
2021-11-29 | 17:32 | 49.828
2021-11-29 | 17:32 | 49.831
2021-11-29 | 17:32 | 49.833
2021-11-29 | 17:32 | 49.835
2021-11-29 | 17:32 | 49.837
2021-11-29 | 17:32 | 49.837
2021-11-29 | 17:32 | 49.837
2021-11-29 | 17:32 | 49.837
2021-11-29 | 17:32 | 49.835
2021-11-29 | 17:32 | 49.835
2021-11-29 | 17:32 | 49.835
2021-11-29 | 17:32 | 49.833
2021-11-29 | 17:32 | 49.835
2021-11-29 | 17:32 | 49.834
2021-11-29 | 17:32 | 49.835
2021-11-29 | 17:32 | 49.835
2021-11-29 | 17:32 | 49.832
2021-11-29 | 17:32 | 49.827
2021-11-29 | 17:32 | 49.828
2021-11-29 | 17:32 | 49.826
2021-11-29 | 17:32 | 49.826
2021-11-29 | 17:32 | 49.824
2021-11-29 | 17:32 | 49.823
2021-11-29 | 17:32 | 49.82
2021-11-29 | 17:32 | 49.82
2021-11-29 | 17:32 | 49.817
2021-11-29 | 17:32 | 49.817
2021-11-29 | 17:33 | 49.816
2021-11-29 | 17:33 | 49.815
2021-11-29 | 17:33 | 49.816
2021-11-29 | 17:33 | 49.817
2021-11-29 | 17:33 | 49.82
2021-11-29 | 17:33 | 49.824
2021-11-29 | 17:33 | 49.826
2021-11-29 | 17:33 | 49.827
2021-11-29 | 17:33 | 49.829
2021-11-29 | 17:33 | 49.83
2021-11-29 | 17:33 | 49.831
2021-11-29 | 17:33 | 49.831
2021-11-29 | 17:33 | 49.833
2021-11-29 | 17:33 | 49.833
2021-11-29 | 17:33 | 49.834
2021-11-29 | 17:33 | 49.836
2021-11-29 | 17:33 | 49.837
2021-11-29 | 17:33 | 49.839
2021-11-29 | 17:33 | 49.841
2021-11-29 | 17:33 | 49.843
2021-11-29 | 17:33 | 49.846
2021-11-29 | 17:33 | 49.847
2021-11-29 | 17:33 | 49.849
2021-11-29 | 17:33 | 49.853
2021-11-29 | 17:33 | 49.853
2021-11-29 | 17:33 | 49.853
2021-11-29 | 17:33 | 49.854
2021-11-29 | 17:33 | 49.854
2021-11-29 | 17:33 | 49.855
2021-11-29 | 17:33 | 49.855
2021-11-29 | 17:33 | 49.854
2021-11-29 | 17:33 | 49.852
2021-11-29 | 17:33 | 49.852
2021-11-29 | 17:33 | 49.851
2021-11-29 | 17:33 | 49.849
2021-11-29 | 17:33 | 49.849
2021-11-29 | 17:33 | 49.85
2021-11-29 | 17:33 | 49.85
2021-11-29 | 17:33 | 49.853
2021-11-29 | 17:33 | 49.854
2021-11-29 | 17:33 | 49.858
2021-11-29 | 17:33 | 49.863
2021-11-29 | 17:33 | 49.868
2021-11-29 | 17:33 | 49.874
2021-11-29 | 17:33 | 49.879
2021-11-29 | 17:33 | 49.884
2021-11-29 | 17:33 | 49.889
2021-11-29 | 17:33 | 49.892
2021-11-29 | 17:33 | 49.894
2021-11-29 | 17:33 | 49.898
2021-11-29 | 17:33 | 49.901
2021-11-29 | 17:33 | 49.904
2021-11-29 | 17:33 | 49.907
2021-11-29 | 17:33 | 49.911
2021-11-29 | 17:33 | 49.916
2021-11-29 | 17:33 | 49.918
2021-11-29 | 17:33 | 49.921
2021-11-29 | 17:33 | 49.924
2021-11-29 | 17:33 | 49.927
2021-11-29 | 17:33 | 49.927
2021-11-29 | 17:33 | 49.929
2021-11-29 | 17:34 | 49.932
2021-11-29 | 17:34 | 49.935
2021-11-29 | 17:34 | 49.939
2021-11-29 | 17:34 | 49.941
2021-11-29 | 17:34 | 49.942
2021-11-29 | 17:34 | 49.944
2021-11-29 | 17:34 | 49.946
2021-11-29 | 17:34 | 49.949
2021-11-29 | 17:34 | 49.953
2021-11-29 | 17:34 | 49.956
2021-11-29 | 17:34 | 49.961
2021-11-29 | 17:34 | 49.966
2021-11-29 | 17:34 | 49.972
2021-11-29 | 17:34 | 49.979
2021-11-29 | 17:34 | 49.988
2021-11-29 | 17:34 | 49.994
2021-11-29 | 17:34 | 50.002
2021-11-29 | 17:34 | 50.007
2021-11-29 | 17:34 | 50.012
2021-11-29 | 17:34 | 50.015
2021-11-29 | 17:34 | 50.016
2021-11-29 | 17:34 | 50.018
2021-11-29 | 17:34 | 50.018
2021-11-29 | 17:34 | 50.019
2021-11-29 | 17:34 | 50.019
2021-11-29 | 17:34 | 50.021
2021-11-29 | 17:34 | 50.021
2021-11-29 | 17:34 | 50.021
2021-11-29 | 17:34 | 50.019