## Slide 1: Emergency and Restoration Code – Phase II Workgroup 8 – GC0148 22 February 2022

## Slide 2: Agenda
Actions from previous meeting and purpose of Meeting
Implications of time frames on Statutory Instrument SI 533 2019
Consultation Document and Time Frame
  Overall solution including
    Terms of Reference and Solution
      Low Frequency Demand Disconnection / Netted Demand
      Storage under Low System Frequencies
      Treatment of Non-CUSC Parties
      Communications
      Critical Tools and Facilities
      Distributed Re-Start
System Defence, System Restoration and Test Plans
Notification Letter
Control Telephony Standard
Distributed Re-Start
AOB

## Slide 3: Actions and Purpose of Meeting
See Spreadsheet - Actions and Minutes following last meeting
Purpose of Meeting
  To review the draft Workgroup Consultation and supporting material
  Actions prior to issue of Workgroup Consultation
  Workgroup Consultation due to be issued on 28 February 2022

## Slide 4: Implications of Statutory Instrument SI 533 2019
Statutory Instrument SI 533 2019 is the Statutory Instrument used to transition the EU Emergency and Restoration Code into UK Law
As part of its implementation it has been noted that Article 55 has been removed
  Article 55 States
  “This Regulation shall enter into force on the twentieth day following that of its publication in the Official Journal of the European Union.
  Article 15(5) to (8), Article 41 and Article 42(1), (2) and (5) shall apply from 18 December 2022.
  This Regulation shall be binding in its entirety and directly applicable in all Member States”
  National Grid ESO has held a discussion with Ofgem on this issue. The advice is to progress with the modification as currently planned. Further guidance is to be provided on this issue.

## Slide 5: Consultation Document
Draft Consultation Document circulated in advance of the Meeting
  Terms of Reference and Solutions
  Low Frequency Demand Disconnection and Netted Demand
  Treatment of Storage under Low Frequency Conditions
  Treatment of Non-CUSC Parties and how they fall under the EU NCER
  Communications and the Control Telephony Standard
  Critical Tools and Facilities (eg State Estimation and ability to control assets during Blackout Conditions)
  Distributed Re-Start
  Legal Text
    Low Frequency Demand Disconnection / Netted Demand
    Treatment of Electricity Storage Modules during low System Frequencies under an importing mode of operation
    Distributed Re-Start

## Slide 6: GC0148 – Solution (1)
Terms of Reference | Proposed Approach
Consider how Articles 15(5) – 15(8) of the EU NCER can be implemented in the GB Grid Code | This relates to Netted Demand for Low Frequency Demand Disconnection. The legal text has been updated to address this issue
Consider how Article 41 of the EU NCER can be implemented in the GB Grid Code | This relates to Communication Systems. The Control Telephony Standard is being updated to address this issue. The Control Telephony Standard is one of the suite of documents which falls under the Relevant Electrical Standards and is subject to its own Governance Arrangements under the Grid Code.
Consider how Article 42(1)(2) and (5) of the EU NCER can be implemented in the GB Grid Code | This issue relates to Critical Tools and Facilities and is covered through updates to the System Defence Plan, System Restoration Plan and Test Plan. All these plans are referenced in the Grid Code
Consider how Article 15(9) of the EU NCER can be implemented in the GB Grid Code | Article 15(9) refers to Article 15(8) which relates to netted demand disconnection based on a frequency gradient. Article 15(8) is not a mandatory requirement and it is not proposed to use a frequency gradient for the LFDD Scheme. Therefore, this requirement is not necessary.
Consider how Article 48(3) of the EU NCER can be implemented in the GB Grid Code | Article 48(3) relates to the formulation of a Test Plan. The Test Plan is being updated as part of this modification and is included as an Annex within this consultation document. The Grid Code Glossary and Definitions will be updated to refer to the Test Plan.

## Slide 7: GC0148 – Solution (2)
Terms of Reference | Proposed Approach
Consider how Article 50 of the EU NCER can be implemented in the GB Grid Code | Article 50 relates to Compliance Testing and Periodic Review of the System Defence Plan. The System Defence Plan is being updated as part of this modification and is referenced in the Grid Code.
Consider how the EU NCER would apply to Non-CUSC Parties. | As part of this solution Non-CUSC Parties would fall under the requirements of the EU NCER where they have a contract with National Grid ESO to provide a Defence Service (ie they are a Defence Service Provider) or a Restoration Service (ie they are a Restoration Service Provider). A condition of these contracts would bind them to the appropriate requirements of the Grid Code and therefore they would be caught under the requirements of the EU NCER.
Consider how the requirements applicable to Electricity Storage Modules when transitioning from an import mode of operation to an export mode of operation during low system frequencies | The Grid Code Legal Text has been updated to address this issue.
Where time allows and the Workgroup believe it is appropriate and efficient, then the Workgroup may consider it is expedient to include elements of the Distributed Re-start project in this modification | The requirements of the Distributed Re-Start Project have been included in this Consultation and the accompanying Legal Text has also been provided. The legal Text has been segregated so the Workgroup can make the decision if they decide to raise an alternative such that Distributed Re-Start can be treated separately if required.

## Slide 8: GC0148 – Solution (2)
Terms of Reference | Proposed Approach
Following the 9th August 2019 System frequency incident, the Workgroup should be aware of the E3C’s work on the low frequency demand disconnection (LFDD) scheme and ensure that the solution developed in GC0148 is, as far as is reasonably practicable, compatible with any ongoing work in this area. | As part of the solution a meeting has been held with those involved in the E3C work to ensure their solution is consistent with the development of the GC0148 solution. We welcome any comments from them as part of this Workgroup Consultation.
If established as a joint workgroup (as recommended by the Proposer), consider the impact on the Distribution Code and G99. | The Workgroup is a joint Grid Code / D Code Workgroup. The Distribution Code and G99 has been updated in respect of Distributed Re-Start and Storage though some further updates may be required. Any additional work required on the Distribution Code is raised as a Consultation question.
Consider any other cross codes impacts. | This question has been raised throughout the workgroup and reflected through the actions on the Code Administrator. There are Cross Code Impacts for Distributed Re-Start which has resulted in changes for the STC, CUSC and BSC.
Consider how Article 50 of the EU NCER can be implemented in the GB Grid Code | Article 50 relates to Compliance Testing and Periodic Review of the System Defence Plan. The System Defence Plan is being updated as part of this modification and is referenced in the Grid Code.

## Slide 9: System Defence Plan, System Restoration Plan and Test Plan
Updated in line with comments received from the workgroup last year and circulated
See attached document with associated comments
See also the proposed solution from the Terms and Conditions in the Consultation Document
Once these outstanding issues have been addressed we can amend the formatting

## Slide 10: Notification Letter
Two Letters Prepared
  In respect of Defence Service Providers
  In respect of Restoration Service Providers
Final views sought from the workgroup on the letter
Aim for the letters to be issued to the industry as soon as possible

## Slide 11: Control Telephony
In the process of being updated in line with comments received
Needs to reflect modern communications technology whilst at the same time ensuring a robust and resilient solution
The updated Control Telephony Standard will be included in the Consultation Document

## Slide 12: Critical Tools and Facilities
This relates to Article 42
Critical Tools and Facilities include (but not limited to)
  monitoring the state of the Transmission System, including state estimation,
  the ability to operate items of plant remotely – eg switchgear, transformer taps and other equipment for the safe functioning of the Transmission System
  telemetry and alarm management,
  the ability to communicate with Control Rooms and other TSO’s for System operation and facilitating cross border operations which are essential during a black out state.
  the ability of Transmission Licensees to operate Critical Tools and Facilities (this requires further assessment but many of the requirements are believed to be covered in the STC)
  The ability of Restoration Service Providers to receive instructions and operate their Plant and Apparatus during a Total or Partial System Shutdown

## Slide 13: Distributed Re-Start
The solution provides for Distributed Re Start
The Consultation includes the legal text for Distributed Re-Start
A recorded presentation has been circulated with this pack for Workgroup Members to review prior to the meeting
Any questions on Distributed Re-Start can be discussed at the meeting
CAN WORKGROUP MEMBERS MAKE EVERY EFFORT TO REVIEW THIS MATERIAL BEFORE THE MEETING

## Slide 14: Current Position and Next Steps
The draft consultation document has been circulated with this pack for information.
Some further refinement will be required for the consultation
The Workgroup Consultation is due to be released on 28th February
The Draft legal text requires a little more refining but largely covers the solution
  Amendments to Glossary and Definitions
  Additions to Planning Code
  Data and Registration Code
  Tying up of loose ends
High level comments are sought on the System Defence, System Restoration and Test Plan
  Some thought is being given to the Assurance Framework which would fit within the Test Plan