## Version
Date | Version | Details
2022-04-22 | 1 | This file only contains the indicative reporting associated with draft data for GC151 for April 2022. This file will be updated in May to reflect the full data set.
2022-05-16 | 2 | This file only contains the indicative reporting associated with data for GC151 for April 2022.
2022-05-17 | 3 | This file only contains the reporting associated with data for GC0105 & GC151 for April 2022.

## Notes
Subject | Notes
RoCoF | RoCoF=(frequency_500ms - frequency_0ms)/500ms RoCoF is calculated using 500ms sliding window. Note that smaller losses will have less accurate ROCOF calculations The RoCoF figure in this report is from external service
System Inertia | Monitoring which transmission-connected generators are running and adding an estimate of inertia from embedded generation and demand
Data 'N/A' | N/A: data not applicable or potentially unreliable. For example, there maybe events when the loss of infeed or exfeed is not instantaneous (over long time period), the calculated RoCoF may not be indicative. For some events, during a disturbance the data may potentially be unreliable. NGESO will apply engineering judgement to determine whether the derived/calculated data is suitable for sharing.

## System Incidents (GC0105)
|  |  | Date and time of the incident | System frequency trace (1-second interval) for the incident | System frequency immediately before the incident | System frequency immediately after the incident | Maximum/Minimum rate of change of frequency (RoCoF) of the incident | System inertia at the time of the incident | Where known, MW trip/loss of all generation/ interconnection related to the incident |  | Where known, MW trip/loss of all Embedded Generation(EG) related to the incident | Where known, MW trip/loss of all DNO demand related to the incident; | Transmission fault associated with the incident; | Any transient voltage dip (loss % and duration) at the local substation associated with the incident | Any other data to gain a clearer understanding of the incident and its potential implications
Reference | Name | Notes | Date Time | System Frequency (Refer to sheet) | Pre-Event Frequency (Hz) | Post-Event Frequency (Hz) | RoCoF (Hz/s) | System Inertia (GVAs) | Generation/Interconnection (MW) |  | EG (MW) | Demand (MW) | Transmission fault | Voltage Dip | Additional data
20220401-1 | Trip IFA 1 |  | 2022-04-01 01:35 | 20220401-1 | 49.952 | 50.327 | 0.14383 | 182 | IFA 1 | -999
20220401-2 | Trip IFA 1 |  | 2022-04-01 08:09 | 20220401-2 | 49.812 | 50.21 | 0.085992 | 287 | IFA 1 | -1000
20220401-3 | Trip IFA 1 |  | 2022-04-01 10:45 | 20220401-3 | 50.024 | 50.306 | 0.092337 | 278 | IFA 1 | -1000
20220409-1 | Trip of PEMB-21 |  | 2022-04-09 11:14 | 20220409-1 | 50.006 | 49.861 | -0.028226 | 193 | PEMB-21 | 440
20220418-1 | Trip of SIZE units |  | 2022-04-18 17:25 | 20220418-1 | 50.023 | 49.641 | -0.13191 | 256 | SIZE-1 SIZE-2 | 600 600
20220421-1 | Trip IFA 1 |  | 2022-04-21 05:09 | 20220421-1 | 49.96 | 50.305 | 0.12005 | 208 | IFA 1 | -1000
20220426-1 | Trip IFA 1 |  | 2022-04-26 00:20 | 20220426-1 | 50.045 | 50.326 | 0.10011 | 257 | IFA 1 | -1014
20220428-1 | Trip DRAX-4 |  | 2022-04-28 09:10 | 20220428-1 | 49.941 | 49.661 | -0.061258 | 284 | DRAX-4 | 645
20220429-1 | Trip of IFA 1 |  | 2022-04-29 06:10 | 20220429-1 | 50.106 | 50.34 | 0.090806 | 272 | IFA 1 | -1028
20220430-1 | Trip of IFA 1 |  | 2022-04-30 05:31 | 20220430-1 | 50.03 | 50.314 | 0.095257 | 258 | IFA 1 | -1028

## Transmission Faults (GC0151)
Location | Network Operator | Date Time | Voltage Trace (Refer to sheet) | Notes
TAUNTON - ALVERDISCOTT - INDIAN QUEENS 2 400KV CIRCUIT AND ALVERDISCOTT SGT2 Trip and DAR | NGET | 2022-04-07 02:23
Trip of Main Busbar 2 at Rugeley 400kV substation | NGET | 2022-04-15 04:17
Port Ann - Crossaig (PR2) 132kV cct trip and DAR | SHETL | 2022-04-17 07:59
Lackenby - Thornton 2 | NGET | 2022-04-20 02:25
Rugeley 400kV Reserve Busbar 1/2, SGT1, SGT4, Rugeley - Drakelow | NGET | 2022-04-21 22:30 | V20220421-1
Rugeley 400kV Reserve Busbar 1/2, SGT1, SGT4, Rugeley - Drakelow | NGET | 2022-04-24 01:32
Bramford SGT4 | NGET | 2022-04-25 09:44

## V20220421-1
>DATE(0/DATE) | TIME(1/TIME) | Time in S | VOLTAGE_L1-N(4/V) | VOLTAGE_L2-N(4/V) | VOLTAGE_L3-N(4/V)
04/21/2022 | 21:30 | 44.144 | 229432.328 | 230494 | 231900.641 | 0.001
04/21/2022 | 21:30 | 44.145 | 229414.656 | 230501.141 | 231907.984
04/21/2022 | 21:30 | 44.146 | 229396.766 | 230498.641 | 231907.313
04/21/2022 | 21:30 | 44.147 | 229388.609 | 230513.656 | 231901.172
04/21/2022 | 21:30 | 44.148 | 229384.859 | 230520.25 | 231879.453
04/21/2022 | 21:30 | 44.149 | 229391.656 | 230523.422 | 231860.563
04/21/2022 | 21:30 | 44.15 | 229419.984 | 230521.109 | 231846.156
04/21/2022 | 21:30 | 44.151 | 229433.984 | 230512.234 | 231863.641
04/21/2022 | 21:30 | 44.152 | 229438.547 | 230494.859 | 231882.344
04/21/2022 | 21:30 | 44.153 | 229434.094 | 230481.281 | 231898.625
04/21/2022 | 21:30 | 44.154 | 229423.281 | 230480.563 | 231908.906
04/21/2022 | 21:30 | 44.155 | 229412.375 | 230489.109 | 231918.734
04/21/2022 | 21:30 | 44.156 | 229397.828 | 230505.891 | 231917.922
04/21/2022 | 21:30 | 44.157 | 229383 | 230531.266 | 231909.359
04/21/2022 | 21:30 | 44.158 | 229374.766 | 230540.609 | 231898.266
04/21/2022 | 21:30 | 44.159 | 229372.719 | 230542.813 | 231883.266
04/21/2022 | 21:30 | 44.16 | 229377.609 | 230536.797 | 231872.656
04/21/2022 | 21:30 | 44.161 | 229399.547 | 230515.938 | 231882.188
04/21/2022 | 21:30 | 44.162 | 229403.859 | 230494.109 | 231891.922
04/21/2022 | 21:30 | 44.163 | 229400.969 | 230469.016 | 231906.953
04/21/2022 | 21:30 | 44.164 | 229383.625 | 230468.281 | 231922.141
04/21/2022 | 21:30 | 44.165 | 229378.953 | 230466.141 | 231931.531
04/21/2022 | 21:30 | 44.166 | 229369.016 | 230499.078 | 231930.078
04/21/2022 | 21:30 | 44.167 | 229366.031 | 230514.578 | 231924.484
04/21/2022 | 21:30 | 44.168 | 229369.781 | 230526.969 | 231913.406
04/21/2022 | 21:30 | 44.169 | 229389.547 | 230528.344 | 231904.297
04/21/2022 | 21:30 | 44.17 | 229395.547 | 230518.297 | 231894.453
04/21/2022 | 21:30 | 44.171 | 229401.656 | 230502.875 | 231894.453
04/21/2022 | 21:30 | 44.172 | 229405.172 | 230480.5 | 231912.422
04/21/2022 | 21:30 | 44.173 | 229400.859 | 230484.563 | 231919.953
04/21/2022 | 21:30 | 44.174 | 229393.344 | 230482.375 | 231937.844
04/21/2022 | 21:30 | 44.175 | 229375.188 | 230487.359 | 231945.922
04/21/2022 | 21:30 | 44.176 | 229378.484 | 230492.344 | 231944.656
04/21/2022 | 21:30 | 44.177 | 229377.75 | 230510.234 | 231936.922
04/21/2022 | 21:30 | 44.178 | 229391.984 | 230527.891 | 231925.344
04/21/2022 | 21:30 | 44.179 | 229407.656 | 230529.156 | 231905.813
04/21/2022 | 21:30 | 44.18 | 229432.734 | 230522.469 | 231897.469
04/21/2022 | 21:30 | 44.181 | 229436.703 | 230510.922 | 231890.328
04/21/2022 | 21:30 | 44.182 | 229442.672 | 230500.859 | 231894.828
04/21/2022 | 21:30 | 44.183 | 229438.484 | 230501.531 | 231907.984
04/21/2022 | 21:30 | 44.184 | 229432.281 | 230497.875 | 231920.516
04/21/2022 | 21:30 | 44.185 | 229417.75 | 230514.969 | 231931.766
04/21/2022 | 21:30 | 44.186 | 229407.172 | 230519.328 | 231931.156
04/21/2022 | 21:30 | 44.187 | 229396.781 | 230536.734 | 231921.313
04/21/2022 | 21:30 | 44.188 | 229399.781 | 230543.359 | 231906.891
04/21/2022 | 21:30 | 44.189 | 229408.656 | 230545.313 | 231897.781
04/21/2022 | 21:30 | 44.19 | 229423.938 | 230539.891 | 231889.453
04/21/2022 | 21:30 | 44.191 | 229434.75 | 230518.75 | 231887.063
04/21/2022 | 21:30 | 44.192 | 229441.156 | 230502.547 | 231886.313
04/21/2022 | 21:30 | 44.193 | 229436.266 | 230481.516 | 231898.859
04/21/2022 | 21:30 | 44.194 | 229424.531 | 230482.25 | 231910.531
04/21/2022 | 21:30 | 44.195 | 229403.313 | 230497.219 | 231920
04/21/2022 | 21:30 | 44.196 | 229372.906 | 230513.406 | 231919.406
04/21/2022 | 21:30 | 44.197 | 229365.5 | 230522.844 | 231906.125
04/21/2022 | 21:30 | 44.198 | 229367 | 230522.563 | 231887.844
04/21/2022 | 21:30 | 44.199 | 229378.578 | 230524.672 | 231873.516
04/21/2022 | 21:30 | 44.2 | 229385.141 | 230515.922 | 231875.031
04/21/2022 | 21:30 | 44.201 | 229400.297 | 230498.625 | 231894.109
04/21/2022 | 21:30 | 44.202 | 229405.906 | 230482.422 | 231908.344
04/21/2022 | 21:30 | 44.203 | 229402.781 | 230469.547 | 231929.047
04/21/2022 | 21:30 | 44.204 | 229392.359 | 230473.938 | 231945.203
04/21/2022 | 21:30 | 44.205 | 229374.734 | 230466.813 | 231951.984
04/21/2022 | 21:30 | 44.206 | 229354.234 | 230494.828 | 231951.438
04/21/2022 | 21:30 | 44.207 | 229351.281 | 230510.406 | 231940.844
04/21/2022 | 21:30 | 44.208 | 229370.047 | 230521.188 | 231913.484
04/21/2022 | 21:30 | 44.209 | 229381.641 | 230523.656 | 231897.234
04/21/2022 | 21:30 | 44.21 | 229402.422 | 230516.844 | 231894.969
04/21/2022 | 21:30 | 44.211 | 229430.281 | 230509.953 | 231899.734
04/21/2022 | 21:30 | 44.212 | 229436.859 | 230497.672 | 231910.234
04/21/2022 | 21:30 | 44.213 | 229432.938 | 230480.719 | 231926.563
04/21/2022 | 21:30 | 44.214 | 229418.313 | 230546.703 | 231935.094
04/21/2022 | 21:30 | 44.215 | 231373.422 | 221968.328 | 233214.594
04/21/2022 | 21:30 | 44.216 | 234361.484 | 213240.766 | 233502.719
04/21/2022 | 21:30 | 44.217 | 236412.531 | 208029.484 | 232740.922
04/21/2022 | 21:30 | 44.218 | 237661.609 | 206243.188 | 232067.625
04/21/2022 | 21:30 | 44.219 | 237514.828 | 206193.016 | 232744.234
04/21/2022 | 21:30 | 44.22 | 236644.234 | 205461.25 | 234494.781
04/21/2022 | 21:30 | 44.221 | 235629.094 | 201881.797 | 237293.875
04/21/2022 | 21:30 | 44.222 | 235295.656 | 194086.672 | 240740.531
04/21/2022 | 21:30 | 44.223 | 235909.359 | 182005.906 | 244501.828
04/21/2022 | 21:30 | 44.224 | 237522.453 | 166810.906 | 247498.875
04/21/2022 | 21:30 | 44.225 | 239977.203 | 150999.953 | 249097.828
04/21/2022 | 21:30 | 44.226 | 242628.391 | 137705.625 | 249237.594
04/21/2022 | 21:30 | 44.227 | 244734.031 | 129489.766 | 248688.031
04/21/2022 | 21:30 | 44.228 | 245576.328 | 126566.828 | 248404.578
04/21/2022 | 21:30 | 44.229 | 245139.813 | 126507.742 | 248804.984
04/21/2022 | 21:30 | 44.23 | 243953.969 | 125369.414 | 250321.234
04/21/2022 | 21:30 | 44.231 | 242964.5 | 119479.352 | 252545.578
04/21/2022 | 21:30 | 44.232 | 242627.25 | 105855.984 | 255447.172
04/21/2022 | 21:30 | 44.233 | 243238.313 | 81681.07 | 258751.188
04/21/2022 | 21:30 | 44.234 | 244622.516 | 36636.691 | 261761.516
04/21/2022 | 21:30 | 44.235 | 244468.141 | 13716.395 | 262256.969
04/21/2022 | 21:30 | 44.236 | 243403.188 | 12205.299 | 262165.031
04/21/2022 | 21:30 | 44.237 | 243042.203 | 11893.027 | 262236.281
04/21/2022 | 21:30 | 44.238 | 242727.406 | 11172.89 | 262146.781
04/21/2022 | 21:30 | 44.239 | 242756.813 | 10972.186 | 261010.969
04/21/2022 | 21:30 | 44.24 | 242704.125 | 11030.322 | 259060.313
04/21/2022 | 21:30 | 44.241 | 242838.375 | 11091.999 | 256695.828
04/21/2022 | 21:30 | 44.242 | 242887.234 | 11127.555 | 255051.859
04/21/2022 | 21:30 | 44.243 | 242633.797 | 11189.252 | 254260.859
04/21/2022 | 21:30 | 44.244 | 242036.75 | 11292.963 | 254191.344
04/21/2022 | 21:30 | 44.245 | 241157.781 | 11320.051 | 254346.656
04/21/2022 | 21:30 | 44.246 | 240234.703 | 11152.642 | 254441.703
04/21/2022 | 21:30 | 44.247 | 239377.156 | 10843.631 | 254316.641
04/21/2022 | 21:30 | 44.248 | 238957.516 | 10407.013 | 253924.875
04/21/2022 | 21:30 | 44.249 | 238905.234 | 9881.91 | 253105.078
04/21/2022 | 21:30 | 44.25 | 239080.109 | 9267.927 | 251401.531
04/21/2022 | 21:30 | 44.251 | 239206.5 | 8607.264 | 249622.141
04/21/2022 | 21:30 | 44.252 | 239269.531 | 7879.628 | 248109.281
04/21/2022 | 21:30 | 44.253 | 239007.578 | 7171.318 | 247077.141
04/21/2022 | 21:30 | 44.254 | 238518.672 | 6582.301 | 246391
04/21/2022 | 21:30 | 44.255 | 238332.625 | 6255.307 | 246181.781
04/21/2022 | 21:30 | 44.256 | 238337.531 | 6127.254 | 246186.547
04/21/2022 | 21:30 | 44.257 | 238195.313 | 6068.076 | 246125
04/21/2022 | 21:30 | 44.258 | 237887.328 | 6005.998 | 245991.938
04/21/2022 | 21:30 | 44.259 | 237711.859 | 5934.52 | 246159.578
04/21/2022 | 21:30 | 44.26 | 237873.609 | 5837.378 | 246768.313
04/21/2022 | 21:30 | 44.261 | 238042.734 | 5735.351 | 247614.391
04/21/2022 | 21:30 | 44.262 | 238088.359 | 5625.069 | 248155.531
04/21/2022 | 21:30 | 44.263 | 238011.141 | 5486.092 | 248332.547
04/21/2022 | 21:30 | 44.264 | 237805.281 | 5215.958 | 248336.531
04/21/2022 | 21:30 | 44.265 | 237660.188 | 4804.165 | 248326.313
04/21/2022 | 21:30 | 44.266 | 237721.219 | 4394.462 | 248341.688
04/21/2022 | 21:30 | 44.267 | 238082.734 | 4002.289 | 248248.703
04/21/2022 | 21:30 | 44.268 | 238588.063 | 3684.117 | 248053.813
04/21/2022 | 21:30 | 44.269 | 239168.156 | 3408.26 | 248270.313
04/21/2022 | 21:30 | 44.27 | 239605.797 | 3220.603 | 249167.094
04/21/2022 | 21:30 | 44.271 | 239835 | 3124.001 | 250306.391
04/21/2022 | 21:30 | 44.272 | 239878.328 | 3091.56 | 251439.359
04/21/2022 | 21:30 | 44.273 | 239807.047 | 3082.535 | 252206.797
04/21/2022 | 21:30 | 44.274 | 239837.828 | 3110.304 | 252709.281
04/21/2022 | 21:30 | 44.275 | 239956.641 | 3166.613 | 252958.531
04/21/2022 | 21:30 | 44.276 | 240203.797 | 3224.722 | 253041.875
04/21/2022 | 21:30 | 44.277 | 240435.438 | 3273.627 | 252947.156
04/21/2022 | 21:30 | 44.278 | 240657.703 | 3300.209 | 252824.953
04/21/2022 | 21:30 | 44.279 | 240797.516 | 3312.447 | 252811.031
04/21/2022 | 21:30 | 44.28 | 240684.641 | 3317.406 | 253119.422
04/21/2022 | 21:30 | 44.281 | 240582.594 | 3302.417 | 253557.453
04/21/2022 | 21:30 | 44.282 | 240531.5 | 3277.945 | 254023.281
04/21/2022 | 21:30 | 44.283 | 240679.328 | 3261.129 | 254364.625
04/21/2022 | 21:30 | 44.284 | 240511.469 | 3263.164 | 254238.297
04/21/2022 | 21:30 | 44.285 | 239281.234 | 3223.297 | 253621.125
04/21/2022 | 21:30 | 44.286 | 237810.141 | 3174.927 | 253507.094
04/21/2022 | 21:30 | 44.287 | 236401.797 | 3176.84 | 253564.031
04/21/2022 | 21:30 | 44.288 | 235515.438 | 3215.352 | 253484.938
04/21/2022 | 21:30 | 44.289 | 235544.828 | 3272.864 | 252971.703
04/21/2022 | 21:30 | 44.29 | 236116.922 | 3332.883 | 252591.766
04/21/2022 | 21:30 | 44.291 | 236797.016 | 3365.599 | 252254.172
04/21/2022 | 21:30 | 44.292 | 237025.969 | 3379.744 | 252111.813
04/21/2022 | 21:30 | 44.293 | 236743.547 | 3381.986 | 251818.641
04/21/2022 | 21:30 | 44.294 | 235915.859 | 3355.171 | 251469.297
04/21/2022 | 21:30 | 44.295 | 234730.875 | 3267.35 | 251252.406
04/21/2022 | 21:30 | 44.296 | 233415.719 | 3156.349 | 251183.141
04/21/2022 | 21:30 | 44.297 | 232595.172 | 3039.048 | 251219.391
04/21/2022 | 21:30 | 44.298 | 232471.922 | 2953.026 | 251244.875
04/21/2022 | 21:30 | 44.299 | 233151.391 | 2903.279 | 251241.953
04/21/2022 | 21:30 | 44.3 | 234214.438 | 2880.296 | 251477.109
04/21/2022 | 21:30 | 44.301 | 235016.953 | 2882.693 | 251816.719
04/21/2022 | 21:30 | 44.302 | 235287.922 | 2974.055 | 251941.563
04/21/2022 | 21:30 | 44.303 | 234902.75 | 4103.086 | 251986.188
04/21/2022 | 21:30 | 44.304 | 234176.688 | 12740.961 | 251495.688
04/21/2022 | 21:30 | 44.305 | 233146.672 | 56607.691 | 250687.344
04/21/2022 | 21:30 | 44.306 | 232176.719 | 83422.484 | 250544.141
04/21/2022 | 21:30 | 44.307 | 232085 | 97942.086 | 251013.391
04/21/2022 | 21:30 | 44.308 | 232169.281 | 104265.297 | 251680.375
04/21/2022 | 21:30 | 44.309 | 233009.859 | 104611.242 | 251526.438
04/21/2022 | 21:30 | 44.31 | 233751.922 | 105427.672 | 251101.375
04/21/2022 | 21:30 | 44.311 | 234520.953 | 111826.891 | 249637.469
04/21/2022 | 21:30 | 44.312 | 234874.609 | 124722.219 | 247341.109
04/21/2022 | 21:30 | 44.313 | 234733.266 | 141895.875 | 245031.063
04/21/2022 | 21:30 | 44.314 | 234063.984 | 160918.453 | 242721.422
04/21/2022 | 21:30 | 44.315 | 233147.297 | 176557.906 | 241499.203
04/21/2022 | 21:30 | 44.316 | 231913.734 | 188418.688 | 241293.516
04/21/2022 | 21:30 | 44.317 | 231101.453 | 195116.5 | 241760.344
04/21/2022 | 21:30 | 44.318 | 230862.797 | 197635.266 | 242217.078
04/21/2022 | 21:30 | 44.319 | 231025.625 | 197870.75 | 242229.781
04/21/2022 | 21:30 | 44.32 | 231885.344 | 198406.313 | 241208.5
04/21/2022 | 21:30 | 44.321 | 232533.594 | 201591.734 | 239789.641
04/21/2022 | 21:30 | 44.322 | 232844.813 | 208923.922 | 237399.891
04/21/2022 | 21:30 | 44.323 | 232690.531 | 219756.75 | 234481.938
04/21/2022 | 21:30 | 44.324 | 232516.188 | 232017.531 | 232647.453
04/21/2022 | 21:30 | 44.325 | 233072.891 | 237372.328 | 232555.453
04/21/2022 | 21:30 | 44.326 | 233709.016 | 238505.594 | 232556.531
04/21/2022 | 21:30 | 44.327 | 233711.953 | 238605.203 | 232633.656
04/21/2022 | 21:30 | 44.328 | 234039.141 | 238128.063 | 232633.203
04/21/2022 | 21:30 | 44.329 | 233723.266 | 238196.828 | 233373.156
04/21/2022 | 21:30 | 44.33 | 233723.844 | 238188.469 | 233689.891
04/21/2022 | 21:30 | 44.331 | 233444.188 | 237842.297 | 234364.25
04/21/2022 | 21:30 | 44.332 | 233263.484 | 237367.906 | 234936.234
04/21/2022 | 21:30 | 44.333 | 233316.594 | 237098.938 | 235006.172
04/21/2022 | 21:30 | 44.334 | 233694.859 | 236221.719 | 235206.938
04/21/2022 | 21:30 | 44.335 | 233971.984 | 235944.047 | 235093.766
04/21/2022 | 21:30 | 44.336 | 234372.969 | 235284.859 | 235092.781
04/21/2022 | 21:30 | 44.337 | 234513.625 | 234942.313 | 235190.703
04/21/2022 | 21:30 | 44.338 | 234453.719 | 234747.781 | 235414.344
04/21/2022 | 21:30 | 44.339 | 234379.891 | 234662.891 | 235544.422
04/21/2022 | 21:30 | 44.34 | 234010.531 | 234733.531 | 235874.109
04/21/2022 | 21:30 | 44.341 | 233835.813 | 234974.188 | 235792.078
04/21/2022 | 21:30 | 44.342 | 233707.297 | 235123.203 | 235854.047
04/21/2022 | 21:30 | 44.343 | 233748.703 | 235175.672 | 235781.109
04/21/2022 | 21:30 | 44.344 | 233850.172 | 234970.031 | 235659.813
04/21/2022 | 21:30 | 44.345 | 233998.375 | 234457.141 | 235638.078
04/21/2022 | 21:30 | 44.346 | 233937.516 | 234142.438 | 235637
04/21/2022 | 21:30 | 44.347 | 234005.016 | 233788.203 | 235645.234
04/21/2022 | 21:30 | 44.348 | 233897.719 | 233548.063 | 235703.109
04/21/2022 | 21:30 | 44.349 | 233757.078 | 233466.875 | 235711.297
04/21/2022 | 21:30 | 44.35 | 233628.156 | 233592.75 | 235616.859
04/21/2022 | 21:30 | 44.351 | 233508.094 | 233838.719 | 235554.813
04/21/2022 | 21:30 | 44.352 | 233481.594 | 234260.313 | 235367.656
04/21/2022 | 21:30 | 44.353 | 233499.859 | 234643.766 | 235273.328
04/21/2022 | 21:30 | 44.354 | 233536.859 | 235013.047 | 235151.688
04/21/2022 | 21:30 | 44.355 | 233553.422 | 235243.953 | 235078.828
04/21/2022 | 21:30 | 44.356 | 233579.359 | 235357.281 | 235078.359
04/21/2022 | 21:30 | 44.357 | 233514.516 | 235444.094 | 235142.625
04/21/2022 | 21:30 | 44.358 | 233426.078 | 235442.328 | 235210.391
04/21/2022 | 21:30 | 44.359 | 233303.328 | 235445.016 | 235314.5
04/21/2022 | 21:30 | 44.36 | 233205.75 | 235431.219 | 235354.266
04/21/2022 | 21:30 | 44.361 | 233135.938 | 235380.484 | 235322.422
04/21/2022 | 21:30 | 44.362 | 233107.813 | 235282.531 | 235279.984
04/21/2022 | 21:30 | 44.363 | 233114.031 | 235168.375 | 235239.375
04/21/2022 | 21:30 | 44.364 | 233141.75 | 234980.578 | 235233.266
04/21/2022 | 21:30 | 44.365 | 233167.922 | 234854.422 | 235220.734
04/21/2022 | 21:30 | 44.366 | 233221.172 | 234723.391 | 235220.797
04/21/2022 | 21:30 | 44.367 | 233274.297 | 234558.797 | 235252.078
04/21/2022 | 21:30 | 44.368 | 233278.813 | 234442.469 | 235326.188
04/21/2022 | 21:30 | 44.369 | 233253.344 | 234408.922 | 235422.453
04/21/2022 | 21:30 | 44.37 | 233197.656 | 234451.641 | 235502.688
04/21/2022 | 21:30 | 44.371 | 233147.703 | 234535.422 | 235484.422
04/21/2022 | 21:30 | 44.372 | 233132.563 | 234588.734 | 235416.344
04/21/2022 | 21:30 | 44.373 | 233137.5 | 234596.813 | 235379.688
04/21/2022 | 21:30 | 44.374 | 233131.297 | 234593.141 | 235360.453
04/21/2022 | 21:30 | 44.375 | 233150.422 | 234636.844 | 235360.203
04/21/2022 | 21:30 | 44.376 | 233160.172 | 234684.156 | 235360.266
04/21/2022 | 21:30 | 44.377 | 233193.359 | 234666.578 | 235386.531
04/21/2022 | 21:30 | 44.378 | 233222.594 | 234636.531 | 235453.891
04/21/2022 | 21:30 | 44.379 | 233187.531 | 234625.438 | 235556.047
04/21/2022 | 21:30 | 44.38 | 233138.719 | 234646.891 | 235616.906
04/21/2022 | 21:30 | 44.381 | 233091.984 | 234688.219 | 235617.703
04/21/2022 | 21:30 | 44.382 | 233081.016 | 234726.875 | 235581.438
04/21/2022 | 21:30 | 44.383 | 233084.641 | 234718.156 | 235543.547
04/21/2022 | 21:30 | 44.384 | 233094.234 | 234715.234 | 235524.828
04/21/2022 | 21:30 | 44.385 | 233108.344 | 234710.219 | 235517.25
04/21/2022 | 21:30 | 44.386 | 233144.828 | 234712.125 | 235517.313
04/21/2022 | 21:30 | 44.387 | 233158.125 | 234701.891 | 235526.922
04/21/2022 | 21:30 | 44.388 | 233152.125 | 234689.875 | 235553.297
04/21/2022 | 21:30 | 44.389 | 233136.984 | 234684.891 | 235597.797
04/21/2022 | 21:30 | 44.39 | 233106.703 | 234698.156 | 235648.906
04/21/2022 | 21:30 | 44.391 | 233086.609 | 234729.391 | 235654.469
04/21/2022 | 21:30 | 44.392 | 233075.703 | 234760.484 | 235652.953
04/21/2022 | 21:30 | 44.393 | 233078.531 | 234777.281 | 235626.031
04/21/2022 | 21:30 | 44.394 | 233082.875 | 234762.625 | 235602.188
04/21/2022 | 21:30 | 44.395 | 233092.469 | 234727.531 | 235595.609
04/21/2022 | 21:30 | 44.396 | 233115.25 | 234714.906 | 235595.688
04/21/2022 | 21:30 | 44.397 | 233133.703 | 234692.984 | 235601.125
04/21/2022 | 21:30 | 44.398 | 233118.703 | 234678.063 | 235614.094
04/21/2022 | 21:30 | 44.399 | 233100.172 | 234674.594 | 235631.281
04/21/2022 | 21:30 | 44.4 | 233074.422 | 234685.719 | 235641.063
04/21/2022 | 21:30 | 44.401 | 233048.359 | 234705.938 | 235640.266
04/21/2022 | 21:30 | 44.402 | 233037.656 | 234732.688 | 235630.469
04/21/2022 | 21:30 | 44.403 | 233040.063 | 234746.109 | 235614.438
04/21/2022 | 21:30 | 44.404 | 233043.172 | 234732.203 | 235598.563
04/21/2022 | 21:30 | 44.405 | 233041.656 | 234711.469 | 235594.422
04/21/2022 | 21:30 | 44.406 | 233048.172 | 234703.266 | 235594.438
04/21/2022 | 21:30 | 44.407 | 233057.047 | 234678.953 | 235598.141
04/21/2022 | 21:30 | 44.408 | 233047.297 | 234669.016 | 235607.875
04/21/2022 | 21:30 | 44.409 | 233041.781 | 234665.906 | 235621.875
04/21/2022 | 21:30 | 44.41 | 233024.422 | 234670.625 | 235599.313
04/21/2022 | 21:30 | 44.411 | 233000.984 | 234661.047 | 235585.813
04/21/2022 | 21:30 | 44.412 | 232994.359 | 234677.453 | 235560.922
04/21/2022 | 21:30 | 44.413 | 232996.969 | 234685.516 | 235577.594
04/21/2022 | 21:30 | 44.414 | 233001.313 | 234702.375 | 235580.859
04/21/2022 | 21:30 | 44.415 | 232987.688 | 234694.5 | 235578.672
04/21/2022 | 21:30 | 44.416 | 232986.375 | 234712.188 | 235578.641
04/21/2022 | 21:30 | 44.417 | 232995.984 | 234714.125 | 235581.859
04/21/2022 | 21:30 | 44.418 | 233004.984 | 234718.516 | 235584.641
04/21/2022 | 21:30 | 44.419 | 233037.281 | 234718.922 | 235598.672
04/21/2022 | 21:30 | 44.42 | 233065.844 | 234718.609 | 235599.422
04/21/2022 | 21:30 | 44.421 | 233086.609 | 234711.25 | 235596.234
04/21/2022 | 21:30 | 44.422 | 233083.672 | 234697.594 | 235599.25
04/21/2022 | 21:30 | 44.423 | 233083.75 | 234733.188 | 235630.672
04/21/2022 | 21:30 | 44.424 | 233093.063 | 234796.156 | 235657.766
04/21/2022 | 21:30 | 44.425 | 233078.953 | 234831.188 | 235668.5
04/21/2022 | 21:30 | 44.426 | 233078.953 | 234866.516 | 235668.438
04/21/2022 | 21:30 | 44.427 | 233085.609 | 234883.031 | 235667.438
04/21/2022 | 21:30 | 44.428 | 233114.172 | 234900.266 | 235669.297
04/21/2022 | 21:30 | 44.429 | 233146.5 | 234903.375 | 235674.391
04/21/2022 | 21:30 | 44.43 | 233191.328 | 234896.625 | 235677.391
04/21/2022 | 21:30 | 44.431 | 233212.859 | 234892.219 | 235717.891
04/21/2022 | 21:30 | 44.432 | 233214.547 | 234891.672 | 235741.25
04/21/2022 | 21:30 | 44.433 | 233211.703 | 234912.516 | 235756.641
04/21/2022 | 21:30 | 44.434 | 233218.219 | 234950.625 | 235770.656
04/21/2022 | 21:30 | 44.435 | 233227.297 | 234999.281 | 235782.359
04/21/2022 | 21:30 | 44.436 | 233239.672 | 235026.422 | 235782.281
04/21/2022 | 21:30 | 44.437 | 233233.016 | 235034.203 | 235778.078
04/21/2022 | 21:30 | 44.438 | 233265.281 | 235047.078 | 235780.859
04/21/2022 | 21:30 | 44.439 | 233290.703 | 235048.531 | 235784.047
04/21/2022 | 21:30 | 44.44 | 233308.641 | 235043.359 | 235795.328
04/21/2022 | 21:30 | 44.441 | 233321.125 | 235046.281 | 235829.5
04/21/2022 | 21:30 | 44.442 | 233329.141 | 235044.109 | 235834.781
04/21/2022 | 21:30 | 44.443 | 233325.75 | 235041.422 | 235832.859
04/21/2022 | 21:30 | 44.444 | 233321.406 | 235052.422 | 235824.906
04/21/2022 | 21:30 | 44.445 | 233330.969 | 235064.563 | 235831.016
04/21/2022 | 21:30 | 44.446 | 233336.188 | 235083.516 | 235831
04/21/2022 | 21:30 | 44.447 | 233330.266 | 235087.391 | 235832.234
04/21/2022 | 21:30 | 44.448 | 233350.563 | 235082.422 | 235838.25
04/21/2022 | 21:30 | 44.449 | 233354 | 235080.422 | 235855.453

## 20220401-1
In GMT
Date | Time | Freq
2022-04-01 | 0:34 | 49.964
2022-04-01 | 0:34 | 49.963
2022-04-01 | 0:34 | 49.957
2022-04-01 | 0:34 | 49.955
2022-04-01 | 0:34 | 49.955
2022-04-01 | 0:34 | 49.955
2022-04-01 | 0:34 | 49.955
2022-04-01 | 0:34 | 49.956
2022-04-01 | 0:34 | 49.957
2022-04-01 | 0:34 | 49.956
2022-04-01 | 0:34 | 49.956
2022-04-01 | 0:34 | 49.956
2022-04-01 | 0:34 | 49.96
2022-04-01 | 0:34 | 49.962
2022-04-01 | 0:34 | 49.963
2022-04-01 | 0:34 | 49.966
2022-04-01 | 0:34 | 49.967
2022-04-01 | 0:34 | 49.969
2022-04-01 | 0:34 | 49.969
2022-04-01 | 0:34 | 49.968
2022-04-01 | 0:34 | 49.969
2022-04-01 | 0:34 | 49.968
2022-04-01 | 0:34 | 49.966
2022-04-01 | 0:34 | 49.967
2022-04-01 | 0:34 | 49.968
2022-04-01 | 0:34 | 49.968
2022-04-01 | 0:34 | 49.967
2022-04-01 | 0:34 | 49.963
2022-04-01 | 0:34 | 49.971
2022-04-01 | 0:34 | 49.968
2022-04-01 | 0:34 | 49.962
2022-04-01 | 0:35 | 49.956
2022-04-01 | 0:35 | 49.954
2022-04-01 | 0:35 | 49.952
2022-04-01 | 0:35 | 50.027
2022-04-01 | 0:35 | 50.145
2022-04-01 | 0:35 | 50.231
2022-04-01 | 0:35 | 50.284
2022-04-01 | 0:35 | 50.306
2022-04-01 | 0:35 | 50.313
2022-04-01 | 0:35 | 50.313
2022-04-01 | 0:35 | 50.313
2022-04-01 | 0:35 | 50.311
2022-04-01 | 0:35 | 50.306
2022-04-01 | 0:35 | 50.3
2022-04-01 | 0:35 | 50.295
2022-04-01 | 0:35 | 50.293
2022-04-01 | 0:35 | 50.29
2022-04-01 | 0:35 | 50.289
2022-04-01 | 0:35 | 50.29
2022-04-01 | 0:35 | 50.294
2022-04-01 | 0:35 | 50.296
2022-04-01 | 0:35 | 50.295
2022-04-01 | 0:35 | 50.294
2022-04-01 | 0:35 | 50.294
2022-04-01 | 0:35 | 50.295
2022-04-01 | 0:35 | 50.297
2022-04-01 | 0:35 | 50.296
2022-04-01 | 0:35 | 50.297
2022-04-01 | 0:35 | 50.299
2022-04-01 | 0:35 | 50.299
2022-04-01 | 0:35 | 50.298
2022-04-01 | 0:35 | 50.299
2022-04-01 | 0:35 | 50.3
2022-04-01 | 0:35 | 50.3
2022-04-01 | 0:35 | 50.302
2022-04-01 | 0:35 | 50.306
2022-04-01 | 0:35 | 50.31
2022-04-01 | 0:35 | 50.311
2022-04-01 | 0:35 | 50.312
2022-04-01 | 0:35 | 50.313
2022-04-01 | 0:35 | 50.315
2022-04-01 | 0:35 | 50.316
2022-04-01 | 0:35 | 50.317
2022-04-01 | 0:35 | 50.32
2022-04-01 | 0:35 | 50.321
2022-04-01 | 0:35 | 50.322
2022-04-01 | 0:35 | 50.322
2022-04-01 | 0:35 | 50.323
2022-04-01 | 0:35 | 50.322
2022-04-01 | 0:35 | 50.322
2022-04-01 | 0:35 | 50.321
2022-04-01 | 0:35 | 50.323
2022-04-01 | 0:35 | 50.328
2022-04-01 | 0:35 | 50.328
2022-04-01 | 0:35 | 50.327
2022-04-01 | 0:35 | 50.325
2022-04-01 | 0:35 | 50.326
2022-04-01 | 0:35 | 50.325
2022-04-01 | 0:35 | 50.326
2022-04-01 | 0:36 | 50.324
2022-04-01 | 0:36 | 50.324
2022-04-01 | 0:36 | 50.322
2022-04-01 | 0:36 | 50.321
2022-04-01 | 0:36 | 50.319
2022-04-01 | 0:36 | 50.319
2022-04-01 | 0:36 | 50.32
2022-04-01 | 0:36 | 50.319
2022-04-01 | 0:36 | 50.318
2022-04-01 | 0:36 | 50.316
2022-04-01 | 0:36 | 50.317
2022-04-01 | 0:36 | 50.314
2022-04-01 | 0:36 | 50.312
2022-04-01 | 0:36 | 50.31
2022-04-01 | 0:36 | 50.311
2022-04-01 | 0:36 | 50.31
2022-04-01 | 0:36 | 50.306
2022-04-01 | 0:36 | 50.304
2022-04-01 | 0:36 | 50.304
2022-04-01 | 0:36 | 50.303
2022-04-01 | 0:36 | 50.3
2022-04-01 | 0:36 | 50.298
2022-04-01 | 0:36 | 50.299
2022-04-01 | 0:36 | 50.299
2022-04-01 | 0:36 | 50.296
2022-04-01 | 0:36 | 50.296
2022-04-01 | 0:36 | 50.295
2022-04-01 | 0:36 | 50.294
2022-04-01 | 0:36 | 50.293
2022-04-01 | 0:36 | 50.291
2022-04-01 | 0:36 | 50.291
2022-04-01 | 0:36 | 50.291
2022-04-01 | 0:36 | 50.291
2022-04-01 | 0:36 | 50.289
2022-04-01 | 0:36 | 50.289
2022-04-01 | 0:36 | 50.288
2022-04-01 | 0:36 | 50.288
2022-04-01 | 0:36 | 50.286
2022-04-01 | 0:36 | 50.282
2022-04-01 | 0:36 | 50.282
2022-04-01 | 0:36 | 50.28
2022-04-01 | 0:36 | 50.279
2022-04-01 | 0:36 | 50.277
2022-04-01 | 0:36 | 50.277
2022-04-01 | 0:36 | 50.274
2022-04-01 | 0:36 | 50.273
2022-04-01 | 0:36 | 50.269
2022-04-01 | 0:36 | 50.269
2022-04-01 | 0:36 | 50.269
2022-04-01 | 0:36 | 50.266
2022-04-01 | 0:36 | 50.263
2022-04-01 | 0:36 | 50.262
2022-04-01 | 0:36 | 50.262
2022-04-01 | 0:36 | 50.262
2022-04-01 | 0:36 | 50.26
2022-04-01 | 0:36 | 50.259
2022-04-01 | 0:36 | 50.259
2022-04-01 | 0:36 | 50.259
2022-04-01 | 0:36 | 50.257
2022-04-01 | 0:36 | 50.255
2022-04-01 | 0:36 | 50.256
2022-04-01 | 0:37 | 50.258
2022-04-01 | 0:37 | 50.258
2022-04-01 | 0:37 | 50.258
2022-04-01 | 0:37 | 50.26
2022-04-01 | 0:37 | 50.259
2022-04-01 | 0:37 | 50.257
2022-04-01 | 0:37 | 50.255
2022-04-01 | 0:37 | 50.255
2022-04-01 | 0:37 | 50.254
2022-04-01 | 0:37 | 50.254
2022-04-01 | 0:37 | 50.251
2022-04-01 | 0:37 | 50.248
2022-04-01 | 0:37 | 50.249
2022-04-01 | 0:37 | 50.249
2022-04-01 | 0:37 | 50.247
2022-04-01 | 0:37 | 50.248
2022-04-01 | 0:37 | 50.249
2022-04-01 | 0:37 | 50.248
2022-04-01 | 0:37 | 50.246
2022-04-01 | 0:37 | 50.244
2022-04-01 | 0:37 | 50.245
2022-04-01 | 0:37 | 50.245
2022-04-01 | 0:37 | 50.242
2022-04-01 | 0:37 | 50.24
2022-04-01 | 0:37 | 50.241
2022-04-01 | 0:37 | 50.239
2022-04-01 | 0:37 | 50.237
2022-04-01 | 0:37 | 50.235
2022-04-01 | 0:37 | 50.235
2022-04-01 | 0:37 | 50.236
2022-04-01 | 0:37 | 50.234
2022-04-01 | 0:37 | 50.232
2022-04-01 | 0:37 | 50.23
2022-04-01 | 0:37 | 50.231
2022-04-01 | 0:37 | 50.232
2022-04-01 | 0:37 | 50.231
2022-04-01 | 0:37 | 50.231
2022-04-01 | 0:37 | 50.232
2022-04-01 | 0:37 | 50.233
2022-04-01 | 0:37 | 50.232
2022-04-01 | 0:37 | 50.231
2022-04-01 | 0:37 | 50.231
2022-04-01 | 0:37 | 50.228
2022-04-01 | 0:37 | 50.226
2022-04-01 | 0:37 | 50.225
2022-04-01 | 0:37 | 50.225
2022-04-01 | 0:37 | 50.221
2022-04-01 | 0:37 | 50.22
2022-04-01 | 0:37 | 50.218
2022-04-01 | 0:37 | 50.219
2022-04-01 | 0:37 | 50.217
2022-04-01 | 0:37 | 50.215
2022-04-01 | 0:37 | 50.215
2022-04-01 | 0:37 | 50.218
2022-04-01 | 0:37 | 50.22
2022-04-01 | 0:37 | 50.22
2022-04-01 | 0:37 | 50.219
2022-04-01 | 0:37 | 50.217
2022-04-01 | 0:37 | 50.216
2022-04-01 | 0:38 | 50.215
2022-04-01 | 0:38 | 50.213
2022-04-01 | 0:38 | 50.213
2022-04-01 | 0:38 | 50.211
2022-04-01 | 0:38 | 50.209
2022-04-01 | 0:38 | 50.206
2022-04-01 | 0:38 | 50.202
2022-04-01 | 0:38 | 50.2
2022-04-01 | 0:38 | 50.197
2022-04-01 | 0:38 | 50.195
2022-04-01 | 0:38 | 50.192
2022-04-01 | 0:38 | 50.193
2022-04-01 | 0:38 | 50.192
2022-04-01 | 0:38 | 50.19
2022-04-01 | 0:38 | 50.19
2022-04-01 | 0:38 | 50.189
2022-04-01 | 0:38 | 50.191
2022-04-01 | 0:38 | 50.191
2022-04-01 | 0:38 | 50.19
2022-04-01 | 0:38 | 50.189
2022-04-01 | 0:38 | 50.188
2022-04-01 | 0:38 | 50.188
2022-04-01 | 0:38 | 50.188
2022-04-01 | 0:38 | 50.187
2022-04-01 | 0:38 | 50.186
2022-04-01 | 0:38 | 50.187
2022-04-01 | 0:38 | 50.185
2022-04-01 | 0:38 | 50.185
2022-04-01 | 0:38 | 50.182
2022-04-01 | 0:38 | 50.181
2022-04-01 | 0:38 | 50.181
2022-04-01 | 0:38 | 50.179
2022-04-01 | 0:38 | 50.178
2022-04-01 | 0:38 | 50.177
2022-04-01 | 0:38 | 50.176
2022-04-01 | 0:38 | 50.175
2022-04-01 | 0:38 | 50.175
2022-04-01 | 0:38 | 50.175
2022-04-01 | 0:38 | 50.172
2022-04-01 | 0:38 | 50.171
2022-04-01 | 0:38 | 50.169
2022-04-01 | 0:38 | 50.171
2022-04-01 | 0:38 | 50.171
2022-04-01 | 0:38 | 50.17
2022-04-01 | 0:38 | 50.169
2022-04-01 | 0:38 | 50.173
2022-04-01 | 0:38 | 50.174
2022-04-01 | 0:38 | 50.174
2022-04-01 | 0:38 | 50.173
2022-04-01 | 0:38 | 50.174
2022-04-01 | 0:38 | 50.174
2022-04-01 | 0:38 | 50.171
2022-04-01 | 0:38 | 50.167
2022-04-01 | 0:38 | 50.163
2022-04-01 | 0:38 | 50.162
2022-04-01 | 0:38 | 50.162
2022-04-01 | 0:38 | 50.161
2022-04-01 | 0:38 | 50.161
2022-04-01 | 0:38 | 50.163
2022-04-01 | 0:38 | 50.163
2022-04-01 | 0:38 | 50.163
2022-04-01 | 0:39 | 50.159
2022-04-01 | 0:39 | 50.158
2022-04-01 | 0:39 | 50.16
2022-04-01 | 0:39 | 50.16
2022-04-01 | 0:39 | 50.16
2022-04-01 | 0:39 | 50.158
2022-04-01 | 0:39 | 50.159
2022-04-01 | 0:39 | 50.157
2022-04-01 | 0:39 | 50.155
2022-04-01 | 0:39 | 50.152
2022-04-01 | 0:39 | 50.148
2022-04-01 | 0:39 | 50.144
2022-04-01 | 0:39 | 50.143
2022-04-01 | 0:39 | 50.143
2022-04-01 | 0:39 | 50.144
2022-04-01 | 0:39 | 50.144
2022-04-01 | 0:39 | 50.144
2022-04-01 | 0:39 | 50.143
2022-04-01 | 0:39 | 50.144
2022-04-01 | 0:39 | 50.142
2022-04-01 | 0:39 | 50.142
2022-04-01 | 0:39 | 50.14
2022-04-01 | 0:39 | 50.14
2022-04-01 | 0:39 | 50.139
2022-04-01 | 0:39 | 50.137
2022-04-01 | 0:39 | 50.133
2022-04-01 | 0:39 | 50.13
2022-04-01 | 0:39 | 50.126
2022-04-01 | 0:39 | 50.123
2022-04-01 | 0:39 | 50.12
2022-04-01 | 0:39 | 50.119
2022-04-01 | 0:39 | 50.118
2022-04-01 | 0:39 | 50.117
2022-04-01 | 0:39 | 50.117
2022-04-01 | 0:39 | 50.118
2022-04-01 | 0:39 | 50.121
2022-04-01 | 0:39 | 50.12
2022-04-01 | 0:39 | 50.12
2022-04-01 | 0:39 | 50.12
2022-04-01 | 0:39 | 50.121
2022-04-01 | 0:39 | 50.12
2022-04-01 | 0:39 | 50.115
2022-04-01 | 0:39 | 50.112
2022-04-01 | 0:39 | 50.112
2022-04-01 | 0:39 | 50.111
2022-04-01 | 0:39 | 50.109
2022-04-01 | 0:39 | 50.104
2022-04-01 | 0:39 | 50.104
2022-04-01 | 0:39 | 50.102
2022-04-01 | 0:39 | 50.101
2022-04-01 | 0:39 | 50.099
2022-04-01 | 0:39 | 50.097
2022-04-01 | 0:39 | 50.093
2022-04-01 | 0:39 | 50.092
2022-04-01 | 0:39 | 50.093
2022-04-01 | 0:39 | 50.092
2022-04-01 | 0:39 | 50.093
2022-04-01 | 0:39 | 50.095
2022-04-01 | 0:39 | 50.093
2022-04-01 | 0:40 | 50.092
2022-04-01 | 0:40 | 50.091
2022-04-01 | 0:40 | 50.089
2022-04-01 | 0:40 | 50.085
2022-04-01 | 0:40 | 50.084
2022-04-01 | 0:40 | 50.087
2022-04-01 | 0:40 | 50.087
2022-04-01 | 0:40 | 50.088
2022-04-01 | 0:40 | 50.087
2022-04-01 | 0:40 | 50.087
2022-04-01 | 0:40 | 50.086
2022-04-01 | 0:40 | 50.085
2022-04-01 | 0:40 | 50.083
2022-04-01 | 0:40 | 50.082
2022-04-01 | 0:40 | 50.081
2022-04-01 | 0:40 | 50.083
2022-04-01 | 0:40 | 50.081
2022-04-01 | 0:40 | 50.082
2022-04-01 | 0:40 | 50.082
2022-04-01 | 0:40 | 50.081
2022-04-01 | 0:40 | 50.079
2022-04-01 | 0:40 | 50.075
2022-04-01 | 0:40 | 50.075
2022-04-01 | 0:40 | 50.074
2022-04-01 | 0:40 | 50.072
2022-04-01 | 0:40 | 50.069
2022-04-01 | 0:40 | 50.067
2022-04-01 | 0:40 | 50.066
2022-04-01 | 0:40 | 50.063
2022-04-01 | 0:40 | 50.064
2022-04-01 | 0:40 | 50.067
2022-04-01 | 0:40 | 50.065
2022-04-01 | 0:40 | 50.062
2022-04-01 | 0:40 | 50.057
2022-04-01 | 0:40 | 50.056
2022-04-01 | 0:40 | 50.055
2022-04-01 | 0:40 | 50.055
2022-04-01 | 0:40 | 50.054
2022-04-01 | 0:40 | 50.055
2022-04-01 | 0:40 | 50.057
2022-04-01 | 0:40 | 50.057
2022-04-01 | 0:40 | 50.057
2022-04-01 | 0:40 | 50.057
2022-04-01 | 0:40 | 50.057
2022-04-01 | 0:40 | 50.056
2022-04-01 | 0:40 | 50.056
2022-04-01 | 0:40 | 50.055
2022-04-01 | 0:40 | 50.055
2022-04-01 | 0:40 | 50.05
2022-04-01 | 0:40 | 50.046
2022-04-01 | 0:40 | 50.044
2022-04-01 | 0:40 | 50.043
2022-04-01 | 0:40 | 50.041
2022-04-01 | 0:40 | 50.039
2022-04-01 | 0:40 | 50.036
2022-04-01 | 0:40 | 50.036
2022-04-01 | 0:40 | 50.034
2022-04-01 | 0:40 | 50.033
2022-04-01 | 0:40 | 50.035
2022-04-01 | 0:40 | 50.037
2022-04-01 | 0:40 | 50.037
2022-04-01 | 0:41 | 50.039
2022-04-01 | 0:41 | 50.04
2022-04-01 | 0:41 | 50.041
2022-04-01 | 0:41 | 50.04
2022-04-01 | 0:41 | 50.043
2022-04-01 | 0:41 | 50.043
2022-04-01 | 0:41 | 50.043
2022-04-01 | 0:41 | 50.041
2022-04-01 | 0:41 | 50.041
2022-04-01 | 0:41 | 50.041
2022-04-01 | 0:41 | 50.039
2022-04-01 | 0:41 | 50.036
2022-04-01 | 0:41 | 50.035
2022-04-01 | 0:41 | 50.035
2022-04-01 | 0:41 | 50.034
2022-04-01 | 0:41 | 50.033
2022-04-01 | 0:41 | 50.034
2022-04-01 | 0:41 | 50.031
2022-04-01 | 0:41 | 50.029
2022-04-01 | 0:41 | 50.027
2022-04-01 | 0:41 | 50.024
2022-04-01 | 0:41 | 50.025
2022-04-01 | 0:41 | 50.023
2022-04-01 | 0:41 | 50.023
2022-04-01 | 0:41 | 50.025
2022-04-01 | 0:41 | 50.027
2022-04-01 | 0:41 | 50.029
2022-04-01 | 0:41 | 50.03
2022-04-01 | 0:41 | 50.031
2022-04-01 | 0:41 | 50.032
2022-04-01 | 0:41 | 50.032
2022-04-01 | 0:41 | 50.031
2022-04-01 | 0:41 | 50.03
2022-04-01 | 0:41 | 50.032
2022-04-01 | 0:41 | 50.029
2022-04-01 | 0:41 | 50.029
2022-04-01 | 0:41 | 50.03
2022-04-01 | 0:41 | 50.029
2022-04-01 | 0:41 | 50.028
2022-04-01 | 0:41 | 50.028
2022-04-01 | 0:41 | 50.029
2022-04-01 | 0:41 | 50.029
2022-04-01 | 0:41 | 50.029
2022-04-01 | 0:41 | 50.031
2022-04-01 | 0:41 | 50.032
2022-04-01 | 0:41 | 50.032
2022-04-01 | 0:41 | 50.031
2022-04-01 | 0:41 | 50.03
2022-04-01 | 0:41 | 50.033
2022-04-01 | 0:41 | 50.03
2022-04-01 | 0:41 | 50.03
2022-04-01 | 0:41 | 50.031
2022-04-01 | 0:41 | 50.033
2022-04-01 | 0:41 | 50.033
2022-04-01 | 0:41 | 50.032
2022-04-01 | 0:41 | 50.031
2022-04-01 | 0:41 | 50.032
2022-04-01 | 0:41 | 50.03
2022-04-01 | 0:41 | 50.028
2022-04-01 | 0:42 | 50.025
2022-04-01 | 0:42 | 50.024
2022-04-01 | 0:42 | 50.02
2022-04-01 | 0:42 | 50.019
2022-04-01 | 0:42 | 50.018
2022-04-01 | 0:42 | 50.019
2022-04-01 | 0:42 | 50.017
2022-04-01 | 0:42 | 50.017
2022-04-01 | 0:42 | 50.017
2022-04-01 | 0:42 | 50.015
2022-04-01 | 0:42 | 50.011
2022-04-01 | 0:42 | 50.012
2022-04-01 | 0:42 | 50.013
2022-04-01 | 0:42 | 50.015
2022-04-01 | 0:42 | 50.014
2022-04-01 | 0:42 | 50.02
2022-04-01 | 0:42 | 50.02
2022-04-01 | 0:42 | 50.019
2022-04-01 | 0:42 | 50.019
2022-04-01 | 0:42 | 50.021
2022-04-01 | 0:42 | 50.021
2022-04-01 | 0:42 | 50.019
2022-04-01 | 0:42 | 50.017
2022-04-01 | 0:42 | 50.018
2022-04-01 | 0:42 | 50.02
2022-04-01 | 0:42 | 50.022
2022-04-01 | 0:42 | 50.024
2022-04-01 | 0:42 | 50.025
2022-04-01 | 0:42 | 50.024
2022-04-01 | 0:42 | 50.023
2022-04-01 | 0:42 | 50.021
2022-04-01 | 0:42 | 50.018
2022-04-01 | 0:42 | 50.017
2022-04-01 | 0:42 | 50.014
2022-04-01 | 0:42 | 50.014
2022-04-01 | 0:42 | 50.014
2022-04-01 | 0:42 | 50.013
2022-04-01 | 0:42 | 50.011
2022-04-01 | 0:42 | 50.012
2022-04-01 | 0:42 | 50.014
2022-04-01 | 0:42 | 50.015
2022-04-01 | 0:42 | 50.014
2022-04-01 | 0:42 | 50.015
2022-04-01 | 0:42 | 50.014
2022-04-01 | 0:42 | 50.015
2022-04-01 | 0:42 | 50.016
2022-04-01 | 0:42 | 50.017
2022-04-01 | 0:42 | 50.02
2022-04-01 | 0:42 | 50.02
2022-04-01 | 0:42 | 50.021
2022-04-01 | 0:42 | 50.02
2022-04-01 | 0:42 | 50.022
2022-04-01 | 0:42 | 50.021
2022-04-01 | 0:42 | 50.019
2022-04-01 | 0:42 | 50.017
2022-04-01 | 0:42 | 50.017
2022-04-01 | 0:42 | 50.015
2022-04-01 | 0:42 | 50.013
2022-04-01 | 0:42 | 50.013
2022-04-01 | 0:42 | 50.012
2022-04-01 | 0:43 | 50.012
2022-04-01 | 0:43 | 50.012
2022-04-01 | 0:43 | 50.013
2022-04-01 | 0:43 | 50.014
2022-04-01 | 0:43 | 50.012
2022-04-01 | 0:43 | 50.015
2022-04-01 | 0:43 | 50.015
2022-04-01 | 0:43 | 50.014
2022-04-01 | 0:43 | 50.014
2022-04-01 | 0:43 | 50.013
2022-04-01 | 0:43 | 50.014
2022-04-01 | 0:43 | 50.013
2022-04-01 | 0:43 | 50.014
2022-04-01 | 0:43 | 50.015
2022-04-01 | 0:43 | 50.014
2022-04-01 | 0:43 | 50.013
2022-04-01 | 0:43 | 50.012
2022-04-01 | 0:43 | 50.013
2022-04-01 | 0:43 | 50.013
2022-04-01 | 0:43 | 50.015
2022-04-01 | 0:43 | 50.015
2022-04-01 | 0:43 | 50.015
2022-04-01 | 0:43 | 50.015
2022-04-01 | 0:43 | 50.014
2022-04-01 | 0:43 | 50.014
2022-04-01 | 0:43 | 50.016
2022-04-01 | 0:43 | 50.015
2022-04-01 | 0:43 | 50.014
2022-04-01 | 0:43 | 50.012
2022-04-01 | 0:43 | 50.013
2022-04-01 | 0:43 | 50.013
2022-04-01 | 0:43 | 50.011
2022-04-01 | 0:43 | 50.009
2022-04-01 | 0:43 | 50.01
2022-04-01 | 0:43 | 50.009
2022-04-01 | 0:43 | 50.009
2022-04-01 | 0:43 | 50.008
2022-04-01 | 0:43 | 50.007
2022-04-01 | 0:43 | 50.007
2022-04-01 | 0:43 | 50.003
2022-04-01 | 0:43 | 50.001
2022-04-01 | 0:43 | 50.001
2022-04-01 | 0:43 | 50.001
2022-04-01 | 0:43 | 49.999
2022-04-01 | 0:43 | 49.999
2022-04-01 | 0:43 | 50.001
2022-04-01 | 0:43 | 50.001
2022-04-01 | 0:43 | 50.003
2022-04-01 | 0:43 | 50.004
2022-04-01 | 0:43 | 50.006
2022-04-01 | 0:43 | 50.005
2022-04-01 | 0:43 | 50.007
2022-04-01 | 0:43 | 50.01
2022-04-01 | 0:43 | 50.011
2022-04-01 | 0:43 | 50.01
2022-04-01 | 0:43 | 50.008
2022-04-01 | 0:43 | 50.007
2022-04-01 | 0:43 | 50.007
2022-04-01 | 0:43 | 50.006
2022-04-01 | 0:43 | 50.006
2022-04-01 | 0:44 | 50.006
2022-04-01 | 0:44 | 50.006
2022-04-01 | 0:44 | 50.006
2022-04-01 | 0:44 | 50.008
2022-04-01 | 0:44 | 50.008
2022-04-01 | 0:44 | 50.01
2022-04-01 | 0:44 | 50.008
2022-04-01 | 0:44 | 50.007
2022-04-01 | 0:44 | 50.006
2022-04-01 | 0:44 | 50.007
2022-04-01 | 0:44 | 50.006
2022-04-01 | 0:44 | 50.006
2022-04-01 | 0:44 | 50.006
2022-04-01 | 0:44 | 50.005
2022-04-01 | 0:44 | 50.004
2022-04-01 | 0:44 | 50.002
2022-04-01 | 0:44 | 50.001
2022-04-01 | 0:44 | 50.001
2022-04-01 | 0:44 | 49.998
2022-04-01 | 0:44 | 49.996
2022-04-01 | 0:44 | 49.993
2022-04-01 | 0:44 | 49.994
2022-04-01 | 0:44 | 49.995
2022-04-01 | 0:44 | 49.995
2022-04-01 | 0:44 | 49.996
2022-04-01 | 0:44 | 49.995
2022-04-01 | 0:44 | 49.996
2022-04-01 | 0:44 | 49.997
2022-04-01 | 0:44 | 50
2022-04-01 | 0:44 | 50.002
2022-04-01 | 0:44 | 50
2021-07-07 | 8:44 | 49.969
2021-07-07 | 8:44 | 49.967
2021-07-07 | 8:44 | 49.966
2021-07-07 | 8:44 | 49.962
2021-07-07 | 8:44 | 49.957
2021-07-07 | 8:44 | 49.951
2021-07-07 | 8:44 | 49.943
2021-07-07 | 8:44 | 49.938
2021-07-07 | 8:44 | 49.934
2021-07-07 | 8:44 | 49.93
2021-07-07 | 8:44 | 49.928
2021-07-07 | 8:44 | 49.928
2021-07-07 | 8:44 | 49.931
2021-07-07 | 8:44 | 49.934
2021-07-07 | 8:44 | 49.94
2021-07-07 | 8:44 | 49.947
2021-07-07 | 8:44 | 49.956
2021-07-07 | 8:44 | 49.964
2021-07-07 | 8:44 | 49.97
2021-07-07 | 8:44 | 49.978
2021-07-07 | 8:44 | 49.985
2021-07-07 | 8:44 | 49.99
2021-07-07 | 8:44 | 49.995
2021-07-07 | 8:44 | 49.998
2021-07-07 | 8:44 | 50.001
2021-07-07 | 8:44 | 50.001
2021-07-07 | 8:44 | 50.002
2021-07-07 | 8:44 | 50.003
2021-07-07 | 8:44 | 50.004
2021-07-07 | 8:44 | 50.005
2021-07-07 | 8:45 | 50.003
2021-07-07 | 8:45 | 50.002
2021-07-07 | 8:45 | 50.003
2021-07-07 | 8:45 | 50
2021-07-07 | 8:45 | 49.999
2021-07-07 | 8:45 | 49.995
2021-07-07 | 8:45 | 49.99
2021-07-07 | 8:45 | 49.988
2021-07-07 | 8:45 | 49.984
2021-07-07 | 8:45 | 49.981
2021-07-07 | 8:45 | 49.98
2021-07-07 | 8:45 | 49.977
2021-07-07 | 8:45 | 49.974
2021-07-07 | 8:45 | 49.969
2021-07-07 | 8:45 | 49.968
2021-07-07 | 8:45 | 49.968
2021-07-07 | 8:45 | 49.966
2021-07-07 | 8:45 | 49.965
2021-07-07 | 8:45 | 49.963
2021-07-07 | 8:45 | 49.962
2021-07-07 | 8:45 | 49.966
2021-07-07 | 8:45 | 49.969
2021-07-07 | 8:45 | 49.97
2021-07-07 | 8:45 | 49.97
2021-07-07 | 8:45 | 49.97
2021-07-07 | 8:45 | 49.971
2021-07-07 | 8:45 | 49.973
2021-07-07 | 8:45 | 49.974
2021-07-07 | 8:45 | 49.977

## 20220401-2
In GMT
Date | Time | Freq
2022-04-01 | 7:04 | 49.869
2022-04-01 | 7:04 | 49.866
2022-04-01 | 7:04 | 49.864
2022-04-01 | 7:04 | 49.863
2022-04-01 | 7:04 | 49.862
2022-04-01 | 7:04 | 49.862
2022-04-01 | 7:04 | 49.864
2022-04-01 | 7:04 | 49.865
2022-04-01 | 7:04 | 49.864
2022-04-01 | 7:04 | 49.864
2022-04-01 | 7:04 | 49.863
2022-04-01 | 7:04 | 49.861
2022-04-01 | 7:04 | 49.86
2022-04-01 | 7:04 | 49.86
2022-04-01 | 7:04 | 49.86
2022-04-01 | 7:04 | 49.861
2022-04-01 | 7:04 | 49.858
2022-04-01 | 7:04 | 49.856
2022-04-01 | 7:04 | 49.853
2022-04-01 | 7:04 | 49.851
2022-04-01 | 7:04 | 49.846
2022-04-01 | 7:04 | 49.84
2022-04-01 | 7:04 | 49.837
2022-04-01 | 7:04 | 49.833
2022-04-01 | 7:04 | 49.832
2022-04-01 | 7:04 | 49.828
2022-04-01 | 7:04 | 49.825
2022-04-01 | 7:04 | 49.82
2022-04-01 | 7:04 | 49.817
2022-04-01 | 7:04 | 49.813
2022-04-01 | 7:04 | 49.809
2022-04-01 | 7:05 | 49.807
2022-04-01 | 7:05 | 49.805
2022-04-01 | 7:05 | 49.804
2022-04-01 | 7:05 | 49.801
2022-04-01 | 7:05 | 49.799
2022-04-01 | 7:05 | 49.798
2022-04-01 | 7:05 | 49.799
2022-04-01 | 7:05 | 49.8
2022-04-01 | 7:05 | 49.803
2022-04-01 | 7:05 | 49.804
2022-04-01 | 7:05 | 49.805
2022-04-01 | 7:05 | 49.805
2022-04-01 | 7:05 | 49.805
2022-04-01 | 7:05 | 49.806
2022-04-01 | 7:05 | 49.806
2022-04-01 | 7:05 | 49.806
2022-04-01 | 7:05 | 49.809
2022-04-01 | 7:05 | 49.811
2022-04-01 | 7:05 | 49.811
2022-04-01 | 7:05 | 49.813
2022-04-01 | 7:05 | 49.814
2022-04-01 | 7:05 | 49.814
2022-04-01 | 7:05 | 49.814
2022-04-01 | 7:05 | 49.816
2022-04-01 | 7:05 | 49.816
2022-04-01 | 7:05 | 49.819
2022-04-01 | 7:05 | 49.821
2022-04-01 | 7:05 | 49.823
2022-04-01 | 7:05 | 49.823
2022-04-01 | 7:05 | 49.822
2022-04-01 | 7:05 | 49.822
2022-04-01 | 7:05 | 49.82
2022-04-01 | 7:05 | 49.818
2022-04-01 | 7:05 | 49.817
2022-04-01 | 7:05 | 49.813
2022-04-01 | 7:05 | 49.81
2022-04-01 | 7:05 | 49.807
2022-04-01 | 7:05 | 49.803
2022-04-01 | 7:05 | 49.8
2022-04-01 | 7:05 | 49.795
2022-04-01 | 7:05 | 49.792
2022-04-01 | 7:05 | 49.792
2022-04-01 | 7:05 | 49.791
2022-04-01 | 7:05 | 49.792
2022-04-01 | 7:05 | 49.794
2022-04-01 | 7:05 | 49.796
2022-04-01 | 7:05 | 49.798
2022-04-01 | 7:05 | 49.801
2022-04-01 | 7:05 | 49.803
2022-04-01 | 7:05 | 49.805
2022-04-01 | 7:05 | 49.805
2022-04-01 | 7:05 | 49.808
2022-04-01 | 7:05 | 49.808
2022-04-01 | 7:05 | 49.806
2022-04-01 | 7:05 | 49.805
2022-04-01 | 7:05 | 49.804
2022-04-01 | 7:05 | 49.809
2022-04-01 | 7:05 | 49.813
2022-04-01 | 7:05 | 49.817
2022-04-01 | 7:06 | 49.82
2022-04-01 | 7:06 | 49.825
2022-04-01 | 7:06 | 49.834
2022-04-01 | 7:06 | 49.839
2022-04-01 | 7:06 | 49.848
2022-04-01 | 7:06 | 49.855
2022-04-01 | 7:06 | 49.863
2022-04-01 | 7:06 | 49.869
2022-04-01 | 7:06 | 49.874
2022-04-01 | 7:06 | 49.88
2022-04-01 | 7:06 | 49.88
2022-04-01 | 7:06 | 49.881
2022-04-01 | 7:06 | 49.879
2022-04-01 | 7:06 | 49.879
2022-04-01 | 7:06 | 49.876
2022-04-01 | 7:06 | 49.875
2022-04-01 | 7:06 | 49.871
2022-04-01 | 7:06 | 49.87
2022-04-01 | 7:06 | 49.868
2022-04-01 | 7:06 | 49.865
2022-04-01 | 7:06 | 49.856
2022-04-01 | 7:06 | 49.851
2022-04-01 | 7:06 | 49.846
2022-04-01 | 7:06 | 49.844
2022-04-01 | 7:06 | 49.842
2022-04-01 | 7:06 | 49.84
2022-04-01 | 7:06 | 49.839
2022-04-01 | 7:06 | 49.837
2022-04-01 | 7:06 | 49.839
2022-04-01 | 7:06 | 49.839
2022-04-01 | 7:06 | 49.837
2022-04-01 | 7:06 | 49.836
2022-04-01 | 7:06 | 49.834
2022-04-01 | 7:06 | 49.833
2022-04-01 | 7:06 | 49.832
2022-04-01 | 7:06 | 49.831
2022-04-01 | 7:06 | 49.831
2022-04-01 | 7:06 | 49.829
2022-04-01 | 7:06 | 49.827
2022-04-01 | 7:06 | 49.828
2022-04-01 | 7:06 | 49.827
2022-04-01 | 7:06 | 49.829
2022-04-01 | 7:06 | 49.828
2022-04-01 | 7:06 | 49.827
2022-04-01 | 7:06 | 49.828
2022-04-01 | 7:06 | 49.829
2022-04-01 | 7:06 | 49.831
2022-04-01 | 7:06 | 49.834
2022-04-01 | 7:06 | 49.835
2022-04-01 | 7:06 | 49.837
2022-04-01 | 7:06 | 49.841
2022-04-01 | 7:06 | 49.843
2022-04-01 | 7:06 | 49.847
2022-04-01 | 7:06 | 49.848
2022-04-01 | 7:06 | 49.853
2022-04-01 | 7:06 | 49.857
2022-04-01 | 7:06 | 49.859
2022-04-01 | 7:06 | 49.862
2022-04-01 | 7:06 | 49.862
2022-04-01 | 7:06 | 49.86
2022-04-01 | 7:06 | 49.861
2022-04-01 | 7:07 | 49.86
2022-04-01 | 7:07 | 49.86
2022-04-01 | 7:07 | 49.861
2022-04-01 | 7:07 | 49.864
2022-04-01 | 7:07 | 49.865
2022-04-01 | 7:07 | 49.867
2022-04-01 | 7:07 | 49.866
2022-04-01 | 7:07 | 49.866
2022-04-01 | 7:07 | 49.865
2022-04-01 | 7:07 | 49.864
2022-04-01 | 7:07 | 49.864
2022-04-01 | 7:07 | 49.864
2022-04-01 | 7:07 | 49.864
2022-04-01 | 7:07 | 49.868
2022-04-01 | 7:07 | 49.87
2022-04-01 | 7:07 | 49.872
2022-04-01 | 7:07 | 49.869
2022-04-01 | 7:07 | 49.871
2022-04-01 | 7:07 | 49.87
2022-04-01 | 7:07 | 49.87
2022-04-01 | 7:07 | 49.87
2022-04-01 | 7:07 | 49.87
2022-04-01 | 7:07 | 49.871
2022-04-01 | 7:07 | 49.874
2022-04-01 | 7:07 | 49.878
2022-04-01 | 7:07 | 49.881
2022-04-01 | 7:07 | 49.885
2022-04-01 | 7:07 | 49.885
2022-04-01 | 7:07 | 49.886
2022-04-01 | 7:07 | 49.886
2022-04-01 | 7:07 | 49.886
2022-04-01 | 7:07 | 49.886
2022-04-01 | 7:07 | 49.885
2022-04-01 | 7:07 | 49.884
2022-04-01 | 7:07 | 49.884
2022-04-01 | 7:07 | 49.886
2022-04-01 | 7:07 | 49.888
2022-04-01 | 7:07 | 49.891
2022-04-01 | 7:07 | 49.889
2022-04-01 | 7:07 | 49.888
2022-04-01 | 7:07 | 49.886
2022-04-01 | 7:07 | 49.885
2022-04-01 | 7:07 | 49.884
2022-04-01 | 7:07 | 49.88
2022-04-01 | 7:07 | 49.879
2022-04-01 | 7:07 | 49.878
2022-04-01 | 7:07 | 49.877
2022-04-01 | 7:07 | 49.877
2022-04-01 | 7:07 | 49.878
2022-04-01 | 7:07 | 49.882
2022-04-01 | 7:07 | 49.882
2022-04-01 | 7:07 | 49.883
2022-04-01 | 7:07 | 49.882
2022-04-01 | 7:07 | 49.883
2022-04-01 | 7:07 | 49.882
2022-04-01 | 7:07 | 49.882
2022-04-01 | 7:07 | 49.877
2022-04-01 | 7:07 | 49.875
2022-04-01 | 7:07 | 49.871
2022-04-01 | 7:08 | 49.867
2022-04-01 | 7:08 | 49.864
2022-04-01 | 7:08 | 49.86
2022-04-01 | 7:08 | 49.857
2022-04-01 | 7:08 | 49.857
2022-04-01 | 7:08 | 49.854
2022-04-01 | 7:08 | 49.853
2022-04-01 | 7:08 | 49.85
2022-04-01 | 7:08 | 49.849
2022-04-01 | 7:08 | 49.849
2022-04-01 | 7:08 | 49.849
2022-04-01 | 7:08 | 49.851
2022-04-01 | 7:08 | 49.854
2022-04-01 | 7:08 | 49.853
2022-04-01 | 7:08 | 49.857
2022-04-01 | 7:08 | 49.858
2022-04-01 | 7:08 | 49.857
2022-04-01 | 7:08 | 49.86
2022-04-01 | 7:08 | 49.862
2022-04-01 | 7:08 | 49.864
2022-04-01 | 7:08 | 49.868
2022-04-01 | 7:08 | 49.87
2022-04-01 | 7:08 | 49.871
2022-04-01 | 7:08 | 49.871
2022-04-01 | 7:08 | 49.871
2022-04-01 | 7:08 | 49.869
2022-04-01 | 7:08 | 49.869
2022-04-01 | 7:08 | 49.871
2022-04-01 | 7:08 | 49.871
2022-04-01 | 7:08 | 49.872
2022-04-01 | 7:08 | 49.874
2022-04-01 | 7:08 | 49.874
2022-04-01 | 7:08 | 49.875
2022-04-01 | 7:08 | 49.874
2022-04-01 | 7:08 | 49.871
2022-04-01 | 7:08 | 49.868
2022-04-01 | 7:08 | 49.868
2022-04-01 | 7:08 | 49.867
2022-04-01 | 7:08 | 49.866
2022-04-01 | 7:08 | 49.863
2022-04-01 | 7:08 | 49.863
2022-04-01 | 7:08 | 49.864
2022-04-01 | 7:08 | 49.862
2022-04-01 | 7:08 | 49.863
2022-04-01 | 7:08 | 49.863
2022-04-01 | 7:08 | 49.861
2022-04-01 | 7:08 | 49.859
2022-04-01 | 7:08 | 49.861
2022-04-01 | 7:08 | 49.861
2022-04-01 | 7:08 | 49.86
2022-04-01 | 7:08 | 49.861
2022-04-01 | 7:08 | 49.858
2022-04-01 | 7:08 | 49.859
2022-04-01 | 7:08 | 49.858
2022-04-01 | 7:08 | 49.857
2022-04-01 | 7:08 | 49.859
2022-04-01 | 7:08 | 49.858
2022-04-01 | 7:08 | 49.855
2022-04-01 | 7:08 | 49.854
2022-04-01 | 7:08 | 49.854
2022-04-01 | 7:08 | 49.853
2022-04-01 | 7:09 | 49.852
2022-04-01 | 7:09 | 49.852
2022-04-01 | 7:09 | 49.853
2022-04-01 | 7:09 | 49.855
2022-04-01 | 7:09 | 49.857
2022-04-01 | 7:09 | 49.857
2022-04-01 | 7:09 | 49.861
2022-04-01 | 7:09 | 49.861
2022-04-01 | 7:09 | 49.862
2022-04-01 | 7:09 | 49.863
2022-04-01 | 7:09 | 49.864
2022-04-01 | 7:09 | 49.865
2022-04-01 | 7:09 | 49.864
2022-04-01 | 7:09 | 49.864
2022-04-01 | 7:09 | 49.865
2022-04-01 | 7:09 | 49.865
2022-04-01 | 7:09 | 49.864
2022-04-01 | 7:09 | 49.864
2022-04-01 | 7:09 | 49.864
2022-04-01 | 7:09 | 49.862
2022-04-01 | 7:09 | 49.863
2022-04-01 | 7:09 | 49.863
2022-04-01 | 7:09 | 49.863
2022-04-01 | 7:09 | 49.859
2022-04-01 | 7:09 | 49.855
2022-04-01 | 7:09 | 49.85
2022-04-01 | 7:09 | 49.846
2022-04-01 | 7:09 | 49.84
2022-04-01 | 7:09 | 49.838
2022-04-01 | 7:09 | 49.833
2022-04-01 | 7:09 | 49.833
2022-04-01 | 7:09 | 49.831
2022-04-01 | 7:09 | 49.825
2022-04-01 | 7:09 | 49.83
2022-04-01 | 7:09 | 49.827
2022-04-01 | 7:09 | 49.825
2022-04-01 | 7:09 | 49.821
2022-04-01 | 7:09 | 49.819
2022-04-01 | 7:09 | 49.816
2022-04-01 | 7:09 | 49.812
2022-04-01 | 7:09 | 49.847
2022-04-01 | 7:09 | 49.9
2022-04-01 | 7:09 | 49.972
2022-04-01 | 7:09 | 50.01
2022-04-01 | 7:09 | 50.051
2022-04-01 | 7:09 | 50.071
2022-04-01 | 7:09 | 50.092
2022-04-01 | 7:09 | 50.103
2022-04-01 | 7:09 | 50.111
2022-04-01 | 7:09 | 50.113
2022-04-01 | 7:09 | 50.117
2022-04-01 | 7:09 | 50.115
2022-04-01 | 7:09 | 50.113
2022-04-01 | 7:09 | 50.107
2022-04-01 | 7:09 | 50.104
2022-04-01 | 7:09 | 50.099
2022-04-01 | 7:09 | 50.095
2022-04-01 | 7:09 | 50.093
2022-04-01 | 7:09 | 50.092
2022-04-01 | 7:10 | 50.089
2022-04-01 | 7:10 | 50.088
2022-04-01 | 7:10 | 50.084
2022-04-01 | 7:10 | 50.084
2022-04-01 | 7:10 | 50.084
2022-04-01 | 7:10 | 50.087
2022-04-01 | 7:10 | 50.093
2022-04-01 | 7:10 | 50.099
2022-04-01 | 7:10 | 50.102
2022-04-01 | 7:10 | 50.109
2022-04-01 | 7:10 | 50.113
2022-04-01 | 7:10 | 50.119
2022-04-01 | 7:10 | 50.121
2022-04-01 | 7:10 | 50.125
2022-04-01 | 7:10 | 50.129
2022-04-01 | 7:10 | 50.132
2022-04-01 | 7:10 | 50.137
2022-04-01 | 7:10 | 50.142
2022-04-01 | 7:10 | 50.147
2022-04-01 | 7:10 | 50.153
2022-04-01 | 7:10 | 50.156
2022-04-01 | 7:10 | 50.16
2022-04-01 | 7:10 | 50.16
2022-04-01 | 7:10 | 50.161
2022-04-01 | 7:10 | 50.161
2022-04-01 | 7:10 | 50.162
2022-04-01 | 7:10 | 50.16
2022-04-01 | 7:10 | 50.156
2022-04-01 | 7:10 | 50.155
2022-04-01 | 7:10 | 50.152
2022-04-01 | 7:10 | 50.151
2022-04-01 | 7:10 | 50.152
2022-04-01 | 7:10 | 50.153
2022-04-01 | 7:10 | 50.152
2022-04-01 | 7:10 | 50.155
2022-04-01 | 7:10 | 50.155
2022-04-01 | 7:10 | 50.155
2022-04-01 | 7:10 | 50.155
2022-04-01 | 7:10 | 50.152
2022-04-01 | 7:10 | 50.15
2022-04-01 | 7:10 | 50.147
2022-04-01 | 7:10 | 50.146
2022-04-01 | 7:10 | 50.142
2022-04-01 | 7:10 | 50.14
2022-04-01 | 7:10 | 50.136
2022-04-01 | 7:10 | 50.133
2022-04-01 | 7:10 | 50.132
2022-04-01 | 7:10 | 50.131
2022-04-01 | 7:10 | 50.133
2022-04-01 | 7:10 | 50.134
2022-04-01 | 7:10 | 50.134
2022-04-01 | 7:10 | 50.132
2022-04-01 | 7:10 | 50.132
2022-04-01 | 7:10 | 50.131
2022-04-01 | 7:10 | 50.131
2022-04-01 | 7:10 | 50.133
2022-04-01 | 7:10 | 50.135
2022-04-01 | 7:10 | 50.137
2022-04-01 | 7:10 | 50.14
2022-04-01 | 7:10 | 50.142
2022-04-01 | 7:10 | 50.144
2022-04-01 | 7:11 | 50.145
2022-04-01 | 7:11 | 50.149
2022-04-01 | 7:11 | 50.15
2022-04-01 | 7:11 | 50.153
2022-04-01 | 7:11 | 50.15
2022-04-01 | 7:11 | 50.152
2022-04-01 | 7:11 | 50.153
2022-04-01 | 7:11 | 50.154
2022-04-01 | 7:11 | 50.155
2022-04-01 | 7:11 | 50.157
2022-04-01 | 7:11 | 50.156
2022-04-01 | 7:11 | 50.155
2022-04-01 | 7:11 | 50.154
2022-04-01 | 7:11 | 50.153
2022-04-01 | 7:11 | 50.15
2022-04-01 | 7:11 | 50.154
2022-04-01 | 7:11 | 50.157
2022-04-01 | 7:11 | 50.158
2022-04-01 | 7:11 | 50.159
2022-04-01 | 7:11 | 50.159
2022-04-01 | 7:11 | 50.159
2022-04-01 | 7:11 | 50.159
2022-04-01 | 7:11 | 50.16
2022-04-01 | 7:11 | 50.157
2022-04-01 | 7:11 | 50.158
2022-04-01 | 7:11 | 50.156
2022-04-01 | 7:11 | 50.155
2022-04-01 | 7:11 | 50.156
2022-04-01 | 7:11 | 50.155
2022-04-01 | 7:11 | 50.154
2022-04-01 | 7:11 | 50.155
2022-04-01 | 7:11 | 50.154
2022-04-01 | 7:11 | 50.155
2022-04-01 | 7:11 | 50.154
2022-04-01 | 7:11 | 50.154
2022-04-01 | 7:11 | 50.153
2022-04-01 | 7:11 | 50.151
2022-04-01 | 7:11 | 50.151
2022-04-01 | 7:11 | 50.15
2022-04-01 | 7:11 | 50.151
2022-04-01 | 7:11 | 50.149
2022-04-01 | 7:11 | 50.149
2022-04-01 | 7:11 | 50.147
2022-04-01 | 7:11 | 50.149
2022-04-01 | 7:11 | 50.15
2022-04-01 | 7:11 | 50.153
2022-04-01 | 7:11 | 50.157
2022-04-01 | 7:11 | 50.161
2022-04-01 | 7:11 | 50.163
2022-04-01 | 7:11 | 50.164
2022-04-01 | 7:11 | 50.162
2022-04-01 | 7:11 | 50.161
2022-04-01 | 7:11 | 50.161
2022-04-01 | 7:11 | 50.161
2022-04-01 | 7:11 | 50.162
2022-04-01 | 7:11 | 50.162
2022-04-01 | 7:11 | 50.163
2022-04-01 | 7:11 | 50.166
2022-04-01 | 7:11 | 50.167
2022-04-01 | 7:12 | 50.166
2022-04-01 | 7:12 | 50.171
2022-04-01 | 7:12 | 50.172
2022-04-01 | 7:12 | 50.171
2022-04-01 | 7:12 | 50.171
2022-04-01 | 7:12 | 50.17
2022-04-01 | 7:12 | 50.171
2022-04-01 | 7:12 | 50.173
2022-04-01 | 7:12 | 50.179
2022-04-01 | 7:12 | 50.183
2022-04-01 | 7:12 | 50.186
2022-04-01 | 7:12 | 50.188
2022-04-01 | 7:12 | 50.187
2022-04-01 | 7:12 | 50.186
2022-04-01 | 7:12 | 50.183
2022-04-01 | 7:12 | 50.179
2022-04-01 | 7:12 | 50.177
2022-04-01 | 7:12 | 50.174
2022-04-01 | 7:12 | 50.174
2022-04-01 | 7:12 | 50.176
2022-04-01 | 7:12 | 50.178
2022-04-01 | 7:12 | 50.182
2022-04-01 | 7:12 | 50.187
2022-04-01 | 7:12 | 50.19
2022-04-01 | 7:12 | 50.195
2022-04-01 | 7:12 | 50.197
2022-04-01 | 7:12 | 50.2
2022-04-01 | 7:12 | 50.201
2022-04-01 | 7:12 | 50.202
2022-04-01 | 7:12 | 50.199
2022-04-01 | 7:12 | 50.195
2022-04-01 | 7:12 | 50.189
2022-04-01 | 7:12 | 50.183
2022-04-01 | 7:12 | 50.176
2022-04-01 | 7:12 | 50.171
2022-04-01 | 7:12 | 50.166
2022-04-01 | 7:12 | 50.159
2022-04-01 | 7:12 | 50.151
2022-04-01 | 7:12 | 50.143
2022-04-01 | 7:12 | 50.133
2022-04-01 | 7:12 | 50.124
2022-04-01 | 7:12 | 50.115
2022-04-01 | 7:12 | 50.107
2022-04-01 | 7:12 | 50.1
2022-04-01 | 7:12 | 50.096
2022-04-01 | 7:12 | 50.093
2022-04-01 | 7:12 | 50.09
2022-04-01 | 7:12 | 50.09
2022-04-01 | 7:12 | 50.09
2022-04-01 | 7:12 | 50.092
2022-04-01 | 7:12 | 50.095
2022-04-01 | 7:12 | 50.096
2022-04-01 | 7:12 | 50.097
2022-04-01 | 7:12 | 50.099
2022-04-01 | 7:12 | 50.101
2022-04-01 | 7:12 | 50.104
2022-04-01 | 7:12 | 50.103
2022-04-01 | 7:12 | 50.101
2022-04-01 | 7:12 | 50.1
2022-04-01 | 7:12 | 50.1
2022-04-01 | 7:12 | 50.098
2022-04-01 | 7:13 | 50.097
2022-04-01 | 7:13 | 50.095
2022-04-01 | 7:13 | 50.094
2022-04-01 | 7:13 | 50.093
2022-04-01 | 7:13 | 50.092
2022-04-01 | 7:13 | 50.09
2022-04-01 | 7:13 | 50.087
2022-04-01 | 7:13 | 50.085
2022-04-01 | 7:13 | 50.081
2022-04-01 | 7:13 | 50.081
2022-04-01 | 7:13 | 50.08
2022-04-01 | 7:13 | 50.079
2022-04-01 | 7:13 | 50.08
2022-04-01 | 7:13 | 50.078
2022-04-01 | 7:13 | 50.081
2022-04-01 | 7:13 | 50.084
2022-04-01 | 7:13 | 50.086
2022-04-01 | 7:13 | 50.086
2022-04-01 | 7:13 | 50.085
2022-04-01 | 7:13 | 50.086
2022-04-01 | 7:13 | 50.088
2022-04-01 | 7:13 | 50.089
2022-04-01 | 7:13 | 50.09
2022-04-01 | 7:13 | 50.091
2022-04-01 | 7:13 | 50.09
2022-04-01 | 7:13 | 50.088
2022-04-01 | 7:13 | 50.087
2022-04-01 | 7:13 | 50.087
2022-04-01 | 7:13 | 50.091
2022-04-01 | 7:13 | 50.091
2022-04-01 | 7:13 | 50.092
2022-04-01 | 7:13 | 50.093
2022-04-01 | 7:13 | 50.091
2022-04-01 | 7:13 | 50.091
2022-04-01 | 7:13 | 50.091
2022-04-01 | 7:13 | 50.089
2022-04-01 | 7:13 | 50.087
2022-04-01 | 7:13 | 50.086
2022-04-01 | 7:13 | 50.086
2022-04-01 | 7:13 | 50.082
2022-04-01 | 7:13 | 50.082
2022-04-01 | 7:13 | 50.082
2022-04-01 | 7:13 | 50.081
2022-04-01 | 7:13 | 50.082
2022-04-01 | 7:13 | 50.082
2022-04-01 | 7:13 | 50.081
2022-04-01 | 7:13 | 50.081
2022-04-01 | 7:13 | 50.083
2022-04-01 | 7:13 | 50.085
2022-04-01 | 7:13 | 50.089
2022-04-01 | 7:13 | 50.092
2022-04-01 | 7:13 | 50.096
2022-04-01 | 7:13 | 50.099
2022-04-01 | 7:13 | 50.102
2022-04-01 | 7:13 | 50.103
2022-04-01 | 7:13 | 50.106
2022-04-01 | 7:13 | 50.107
2022-04-01 | 7:13 | 50.109
2022-04-01 | 7:13 | 50.112
2022-04-01 | 7:14 | 50.109
2022-04-01 | 7:14 | 50.111
2022-04-01 | 7:14 | 50.112
2022-04-01 | 7:14 | 50.111
2022-04-01 | 7:14 | 50.11
2022-04-01 | 7:14 | 50.11
2022-04-01 | 7:14 | 50.106
2022-04-01 | 7:14 | 50.106
2022-04-01 | 7:14 | 50.103
2022-04-01 | 7:14 | 50.101
2022-04-01 | 7:14 | 50.099
2022-04-01 | 7:14 | 50.098
2022-04-01 | 7:14 | 50.097
2022-04-01 | 7:14 | 50.095
2022-04-01 | 7:14 | 50.094
2022-04-01 | 7:14 | 50.093
2022-04-01 | 7:14 | 50.093
2022-04-01 | 7:14 | 50.092
2022-04-01 | 7:14 | 50.094
2022-04-01 | 7:14 | 50.094
2022-04-01 | 7:14 | 50.094
2022-04-01 | 7:14 | 50.095
2022-04-01 | 7:14 | 50.095
2022-04-01 | 7:14 | 50.1
2022-04-01 | 7:14 | 50.102
2022-04-01 | 7:14 | 50.104
2022-04-01 | 7:14 | 50.105
2022-04-01 | 7:14 | 50.107
2022-04-01 | 7:14 | 50.108
2022-04-01 | 7:14 | 50.108
2022-04-01 | 7:14 | 50.109
2022-04-01 | 7:14 | 50.108
2022-04-01 | 7:14 | 50.109
2022-04-01 | 7:14 | 50.11
2022-04-01 | 7:14 | 50.111
2022-04-01 | 7:14 | 50.114
2022-04-01 | 7:14 | 50.114
2022-04-01 | 7:14 | 50.113
2022-04-01 | 7:14 | 50.113
2022-04-01 | 7:14 | 50.113
2022-04-01 | 7:14 | 50.11
2022-04-01 | 7:14 | 50.107
2022-04-01 | 7:14 | 50.107
2022-04-01 | 7:14 | 50.106
2022-04-01 | 7:14 | 50.107
2022-04-01 | 7:14 | 50.102
2022-04-01 | 7:14 | 50.098
2022-04-01 | 7:14 | 50.09
2022-04-01 | 7:14 | 50.085
2022-04-01 | 7:14 | 50.079
2022-04-01 | 7:14 | 50.075
2022-04-01 | 7:14 | 50.069
2022-04-01 | 7:14 | 50.064
2022-04-01 | 7:14 | 50.063
2022-04-01 | 7:14 | 50.058
2022-04-01 | 7:14 | 50.057
2022-04-01 | 7:14 | 50.056
2022-04-01 | 7:14 | 50.058
2022-04-01 | 7:14 | 50.058
2022-04-01 | 7:14 | 50.061
2022-04-01 | 7:14 | 50.061
2022-04-01 | 7:15 | 50.062
2022-04-01 | 7:15 | 50.063
2022-04-01 | 7:15 | 50.064
2022-04-01 | 7:15 | 50.062
2022-04-01 | 7:15 | 50.063
2022-04-01 | 7:15 | 50.062
2022-04-01 | 7:15 | 50.059
2022-04-01 | 7:15 | 50.057
2022-04-01 | 7:15 | 50.057
2022-04-01 | 7:15 | 50.058
2022-04-01 | 7:15 | 50.06
2022-04-01 | 7:15 | 50.063
2022-04-01 | 7:15 | 50.065
2022-04-01 | 7:15 | 50.067
2022-04-01 | 7:15 | 50.069
2022-04-01 | 7:15 | 50.072
2022-04-01 | 7:15 | 50.074
2022-04-01 | 7:15 | 50.077
2022-04-01 | 7:15 | 50.081
2022-04-01 | 7:15 | 50.082
2022-04-01 | 7:15 | 50.085
2022-04-01 | 7:15 | 50.086
2022-04-01 | 7:15 | 50.088
2022-04-01 | 7:15 | 50.084
2022-04-01 | 7:15 | 50.084
2022-04-01 | 7:15 | 50.082
2022-04-01 | 7:15 | 50.084
2022-04-01 | 7:15 | 50.082
2022-04-01 | 7:15 | 50.083
2022-04-01 | 7:15 | 50.082

## 20220401-3
In GMT
Date | Time | Freq
2022-04-01 | 9:41 | 50.082
2022-04-01 | 9:41 | 50.076
2022-04-01 | 9:41 | 50.071
2022-04-01 | 9:41 | 50.063
2022-04-01 | 9:41 | 50.058
2022-04-01 | 9:41 | 50.053
2022-04-01 | 9:41 | 50.047
2022-04-01 | 9:41 | 50.044
2022-04-01 | 9:41 | 50.045
2022-04-01 | 9:41 | 50.048
2022-04-01 | 9:41 | 50.054
2022-04-01 | 9:41 | 50.059
2022-04-01 | 9:41 | 50.063
2022-04-01 | 9:41 | 50.067
2022-04-01 | 9:41 | 50.072
2022-04-01 | 9:41 | 50.074
2022-04-01 | 9:41 | 50.075
2022-04-01 | 9:41 | 50.074
2022-04-01 | 9:41 | 50.073
2022-04-01 | 9:41 | 50.074
2022-04-01 | 9:41 | 50.076
2022-04-01 | 9:41 | 50.075
2022-04-01 | 9:41 | 50.076
2022-04-01 | 9:41 | 50.079
2022-04-01 | 9:41 | 50.081
2022-04-01 | 9:41 | 50.083
2022-04-01 | 9:41 | 50.087
2022-04-01 | 9:41 | 50.087
2022-04-01 | 9:41 | 50.088
2022-04-01 | 9:41 | 50.086
2022-04-01 | 9:42 | 50.084
2022-04-01 | 9:42 | 50.079
2022-04-01 | 9:42 | 50.073
2022-04-01 | 9:42 | 50.069
2022-04-01 | 9:42 | 50.067
2022-04-01 | 9:42 | 50.063
2022-04-01 | 9:42 | 50.058
2022-04-01 | 9:42 | 50.052
2022-04-01 | 9:42 | 50.048
2022-04-01 | 9:42 | 50.043
2022-04-01 | 9:42 | 50.038
2022-04-01 | 9:42 | 50.034
2022-04-01 | 9:42 | 50.032
2022-04-01 | 9:42 | 50.028
2022-04-01 | 9:42 | 50.026
2022-04-01 | 9:42 | 50.024
2022-04-01 | 9:42 | 50.024
2022-04-01 | 9:42 | 50.021
2022-04-01 | 9:42 | 50.016
2022-04-01 | 9:42 | 50.012
2022-04-01 | 9:42 | 50.008
2022-04-01 | 9:42 | 50.008
2022-04-01 | 9:42 | 50.007
2022-04-01 | 9:42 | 50.007
2022-04-01 | 9:42 | 50.009
2022-04-01 | 9:42 | 50.012
2022-04-01 | 9:42 | 50.017
2022-04-01 | 9:42 | 50.017
2022-04-01 | 9:42 | 50.018
2022-04-01 | 9:42 | 50.019
2022-04-01 | 9:42 | 50.021
2022-04-01 | 9:42 | 50.021
2022-04-01 | 9:42 | 50.019
2022-04-01 | 9:42 | 50.019
2022-04-01 | 9:42 | 50.022
2022-04-01 | 9:42 | 50.023
2022-04-01 | 9:42 | 50.022
2022-04-01 | 9:42 | 50.023
2022-04-01 | 9:42 | 50.021
2022-04-01 | 9:42 | 50.019
2022-04-01 | 9:42 | 50.018
2022-04-01 | 9:42 | 50.018
2022-04-01 | 9:42 | 50.017
2022-04-01 | 9:42 | 50.017
2022-04-01 | 9:42 | 50.016
2022-04-01 | 9:42 | 50.016
2022-04-01 | 9:42 | 50.015
2022-04-01 | 9:42 | 50.015
2022-04-01 | 9:42 | 50.016
2022-04-01 | 9:42 | 50.018
2022-04-01 | 9:42 | 50.02
2022-04-01 | 9:42 | 50.021
2022-04-01 | 9:42 | 50.019
2022-04-01 | 9:42 | 50.018
2022-04-01 | 9:42 | 50.018
2022-04-01 | 9:42 | 50.016
2022-04-01 | 9:42 | 50.014
2022-04-01 | 9:42 | 50.013
2022-04-01 | 9:42 | 50.011
2022-04-01 | 9:42 | 50.01
2022-04-01 | 9:42 | 50.009
2022-04-01 | 9:43 | 50.01
2022-04-01 | 9:43 | 50.011
2022-04-01 | 9:43 | 50.013
2022-04-01 | 9:43 | 50.015
2022-04-01 | 9:43 | 50.015
2022-04-01 | 9:43 | 50.014
2022-04-01 | 9:43 | 50.012
2022-04-01 | 9:43 | 50.014
2022-04-01 | 9:43 | 50.013
2022-04-01 | 9:43 | 50.014
2022-04-01 | 9:43 | 50.016
2022-04-01 | 9:43 | 50.016
2022-04-01 | 9:43 | 50.016
2022-04-01 | 9:43 | 50.013
2022-04-01 | 9:43 | 50.014
2022-04-01 | 9:43 | 50.013
2022-04-01 | 9:43 | 50.013
2022-04-01 | 9:43 | 50.014
2022-04-01 | 9:43 | 50.015
2022-04-01 | 9:43 | 50.015
2022-04-01 | 9:43 | 50.013
2022-04-01 | 9:43 | 50.017
2022-04-01 | 9:43 | 50.023
2022-04-01 | 9:43 | 50.026
2022-04-01 | 9:43 | 50.027
2022-04-01 | 9:43 | 50.028
2022-04-01 | 9:43 | 50.03
2022-04-01 | 9:43 | 50.027
2022-04-01 | 9:43 | 50.026
2022-04-01 | 9:43 | 50.025
2022-04-01 | 9:43 | 50.023
2022-04-01 | 9:43 | 50.021
2022-04-01 | 9:43 | 50.017
2022-04-01 | 9:43 | 50.015
2022-04-01 | 9:43 | 50.014
2022-04-01 | 9:43 | 50.012
2022-04-01 | 9:43 | 50.009
2022-04-01 | 9:43 | 50.008
2022-04-01 | 9:43 | 50.005
2022-04-01 | 9:43 | 50.007
2022-04-01 | 9:43 | 50.008
2022-04-01 | 9:43 | 50.008
2022-04-01 | 9:43 | 50.009
2022-04-01 | 9:43 | 50.008
2022-04-01 | 9:43 | 50.007
2022-04-01 | 9:43 | 50.003
2022-04-01 | 9:43 | 50.003
2022-04-01 | 9:43 | 50.003
2022-04-01 | 9:43 | 50.006
2022-04-01 | 9:43 | 50.01
2022-04-01 | 9:43 | 50.012
2022-04-01 | 9:43 | 50.016
2022-04-01 | 9:43 | 50.02
2022-04-01 | 9:43 | 50.019
2022-04-01 | 9:43 | 50.018
2022-04-01 | 9:43 | 50.014
2022-04-01 | 9:43 | 50.011
2022-04-01 | 9:43 | 50.007
2022-04-01 | 9:43 | 50.004
2022-04-01 | 9:44 | 50.003
2022-04-01 | 9:44 | 50.002
2022-04-01 | 9:44 | 50
2022-04-01 | 9:44 | 49.997
2022-04-01 | 9:44 | 49.999
2022-04-01 | 9:44 | 50.001
2022-04-01 | 9:44 | 50.002
2022-04-01 | 9:44 | 50.004
2022-04-01 | 9:44 | 50.007
2022-04-01 | 9:44 | 50.014
2022-04-01 | 9:44 | 50.018
2022-04-01 | 9:44 | 50.02
2022-04-01 | 9:44 | 50.024
2022-04-01 | 9:44 | 50.026
2022-04-01 | 9:44 | 50.027
2022-04-01 | 9:44 | 50.027
2022-04-01 | 9:44 | 50.024
2022-04-01 | 9:44 | 50.021
2022-04-01 | 9:44 | 50.019
2022-04-01 | 9:44 | 50.017
2022-04-01 | 9:44 | 50.017
2022-04-01 | 9:44 | 50.018
2022-04-01 | 9:44 | 50.017
2022-04-01 | 9:44 | 50.016
2022-04-01 | 9:44 | 50.015
2022-04-01 | 9:44 | 50.013
2022-04-01 | 9:44 | 50.012
2022-04-01 | 9:44 | 50.013
2022-04-01 | 9:44 | 50.011
2022-04-01 | 9:44 | 50.009
2022-04-01 | 9:44 | 50.01
2022-04-01 | 9:44 | 50.014
2022-04-01 | 9:44 | 50.015
2022-04-01 | 9:44 | 50.017
2022-04-01 | 9:44 | 50.019
2022-04-01 | 9:44 | 50.024
2022-04-01 | 9:44 | 50.026
2022-04-01 | 9:44 | 50.028
2022-04-01 | 9:44 | 50.029
2022-04-01 | 9:44 | 50.03
2022-04-01 | 9:44 | 50.031
2022-04-01 | 9:44 | 50.03
2022-04-01 | 9:44 | 50.029
2022-04-01 | 9:44 | 50.029
2022-04-01 | 9:44 | 50.025
2022-04-01 | 9:44 | 50.024
2022-04-01 | 9:44 | 50.021
2022-04-01 | 9:44 | 50.02
2022-04-01 | 9:44 | 50.021
2022-04-01 | 9:44 | 50.023
2022-04-01 | 9:44 | 50.023
2022-04-01 | 9:44 | 50.022
2022-04-01 | 9:44 | 50.02
2022-04-01 | 9:44 | 50.02
2022-04-01 | 9:44 | 50.02
2022-04-01 | 9:44 | 50.018
2022-04-01 | 9:44 | 50.018
2022-04-01 | 9:44 | 50.016
2022-04-01 | 9:44 | 50.016
2022-04-01 | 9:44 | 50.015
2022-04-01 | 9:44 | 50.015
2022-04-01 | 9:45 | 50.018
2022-04-01 | 9:45 | 50.019
2022-04-01 | 9:45 | 50.02
2022-04-01 | 9:45 | 50.02
2022-04-01 | 9:45 | 50.021
2022-04-01 | 9:45 | 50.024
2022-04-01 | 9:45 | 50.027
2022-04-01 | 9:45 | 50.028
2022-04-01 | 9:45 | 50.027
2022-04-01 | 9:45 | 50.028
2022-04-01 | 9:45 | 50.031
2022-04-01 | 9:45 | 50.037
2022-04-01 | 9:45 | 50.041
2022-04-01 | 9:45 | 50.044
2022-04-01 | 9:45 | 50.046
2022-04-01 | 9:45 | 50.047
2022-04-01 | 9:45 | 50.047
2022-04-01 | 9:45 | 50.045
2022-04-01 | 9:45 | 50.045
2022-04-01 | 9:45 | 50.044
2022-04-01 | 9:45 | 50.045
2022-04-01 | 9:45 | 50.045
2022-04-01 | 9:45 | 50.046
2022-04-01 | 9:45 | 50.045
2022-04-01 | 9:45 | 50.044
2022-04-01 | 9:45 | 50.05
2022-04-01 | 9:45 | 50.051
2022-04-01 | 9:45 | 50.048
2022-04-01 | 9:45 | 50.045
2022-04-01 | 9:45 | 50.042
2022-04-01 | 9:45 | 50.062
2022-04-01 | 9:45 | 50.118
2022-04-01 | 9:45 | 50.187
2022-04-01 | 9:45 | 50.237
2022-04-01 | 9:45 | 50.265
2022-04-01 | 9:45 | 50.278
2022-04-01 | 9:45 | 50.279
2022-04-01 | 9:45 | 50.277
2022-04-01 | 9:45 | 50.273
2022-04-01 | 9:45 | 50.269
2022-04-01 | 9:45 | 50.265
2022-04-01 | 9:45 | 50.261
2022-04-01 | 9:45 | 50.259
2022-04-01 | 9:45 | 50.257
2022-04-01 | 9:45 | 50.254
2022-04-01 | 9:45 | 50.251
2022-04-01 | 9:45 | 50.249
2022-04-01 | 9:45 | 50.248
2022-04-01 | 9:45 | 50.247
2022-04-01 | 9:45 | 50.249
2022-04-01 | 9:45 | 50.249
2022-04-01 | 9:45 | 50.25
2022-04-01 | 9:45 | 50.249
2022-04-01 | 9:45 | 50.249
2022-04-01 | 9:45 | 50.249
2022-04-01 | 9:45 | 50.248
2022-04-01 | 9:45 | 50.247
2022-04-01 | 9:45 | 50.246
2022-04-01 | 9:45 | 50.248
2022-04-01 | 9:46 | 50.251
2022-04-01 | 9:46 | 50.252
2022-04-01 | 9:46 | 50.254
2022-04-01 | 9:46 | 50.257
2022-04-01 | 9:46 | 50.255
2022-04-01 | 9:46 | 50.253
2022-04-01 | 9:46 | 50.253
2022-04-01 | 9:46 | 50.253
2022-04-01 | 9:46 | 50.254
2022-04-01 | 9:46 | 50.255
2022-04-01 | 9:46 | 50.255
2022-04-01 | 9:46 | 50.255
2022-04-01 | 9:46 | 50.255
2022-04-01 | 9:46 | 50.256
2022-04-01 | 9:46 | 50.258
2022-04-01 | 9:46 | 50.26
2022-04-01 | 9:46 | 50.259
2022-04-01 | 9:46 | 50.258
2022-04-01 | 9:46 | 50.26
2022-04-01 | 9:46 | 50.26
2022-04-01 | 9:46 | 50.26
2022-04-01 | 9:46 | 50.259
2022-04-01 | 9:46 | 50.258
2022-04-01 | 9:46 | 50.253
2022-04-01 | 9:46 | 50.251
2022-04-01 | 9:46 | 50.25
2022-04-01 | 9:46 | 50.248
2022-04-01 | 9:46 | 50.25
2022-04-01 | 9:46 | 50.252
2022-04-01 | 9:46 | 50.251
2022-04-01 | 9:46 | 50.253
2022-04-01 | 9:46 | 50.251
2022-04-01 | 9:46 | 50.252
2022-04-01 | 9:46 | 50.252
2022-04-01 | 9:46 | 50.251
2022-04-01 | 9:46 | 50.25
2022-04-01 | 9:46 | 50.248
2022-04-01 | 9:46 | 50.247
2022-04-01 | 9:46 | 50.246
2022-04-01 | 9:46 | 50.246
2022-04-01 | 9:46 | 50.247
2022-04-01 | 9:46 | 50.251
2022-04-01 | 9:46 | 50.251
2022-04-01 | 9:46 | 50.254
2022-04-01 | 9:46 | 50.255
2022-04-01 | 9:46 | 50.256
2022-04-01 | 9:46 | 50.259
2022-04-01 | 9:46 | 50.263
2022-04-01 | 9:46 | 50.266
2022-04-01 | 9:46 | 50.264
2022-04-01 | 9:46 | 50.266
2022-04-01 | 9:46 | 50.268
2022-04-01 | 9:46 | 50.271
2022-04-01 | 9:46 | 50.268
2022-04-01 | 9:46 | 50.27
2022-04-01 | 9:46 | 50.271
2022-04-01 | 9:46 | 50.273
2022-04-01 | 9:46 | 50.275
2022-04-01 | 9:46 | 50.275
2022-04-01 | 9:46 | 50.276
2022-04-01 | 9:46 | 50.276
2022-04-01 | 9:47 | 50.274
2022-04-01 | 9:47 | 50.276
2022-04-01 | 9:47 | 50.278
2022-04-01 | 9:47 | 50.279
2022-04-01 | 9:47 | 50.282
2022-04-01 | 9:47 | 50.282
2022-04-01 | 9:47 | 50.282
2022-04-01 | 9:47 | 50.281
2022-04-01 | 9:47 | 50.282
2022-04-01 | 9:47 | 50.284
2022-04-01 | 9:47 | 50.285
2022-04-01 | 9:47 | 50.288
2022-04-01 | 9:47 | 50.292
2022-04-01 | 9:47 | 50.297
2022-04-01 | 9:47 | 50.3
2022-04-01 | 9:47 | 50.303
2022-04-01 | 9:47 | 50.305
2022-04-01 | 9:47 | 50.306
2022-04-01 | 9:47 | 50.308
2022-04-01 | 9:47 | 50.306
2022-04-01 | 9:47 | 50.304
2022-04-01 | 9:47 | 50.302
2022-04-01 | 9:47 | 50.3
2022-04-01 | 9:47 | 50.301
2022-04-01 | 9:47 | 50.3
2022-04-01 | 9:47 | 50.297
2022-04-01 | 9:47 | 50.297
2022-04-01 | 9:47 | 50.295
2022-04-01 | 9:47 | 50.293
2022-04-01 | 9:47 | 50.291
2022-04-01 | 9:47 | 50.288
2022-04-01 | 9:47 | 50.288
2022-04-01 | 9:47 | 50.29
2022-04-01 | 9:47 | 50.292
2022-04-01 | 9:47 | 50.295
2022-04-01 | 9:47 | 50.297
2022-04-01 | 9:47 | 50.296
2022-04-01 | 9:47 | 50.295
2022-04-01 | 9:47 | 50.295
2022-04-01 | 9:47 | 50.295
2022-04-01 | 9:47 | 50.295
2022-04-01 | 9:47 | 50.294
2022-04-01 | 9:47 | 50.295
2022-04-01 | 9:47 | 50.295
2022-04-01 | 9:47 | 50.295
2022-04-01 | 9:47 | 50.295
2022-04-01 | 9:47 | 50.297
2022-04-01 | 9:47 | 50.297
2022-04-01 | 9:47 | 50.3
2022-04-01 | 9:47 | 50.299
2022-04-01 | 9:47 | 50.299
2022-04-01 | 9:47 | 50.3
2022-04-01 | 9:47 | 50.299
2022-04-01 | 9:47 | 50.299
2022-04-01 | 9:47 | 50.301
2022-04-01 | 9:47 | 50.301
2022-04-01 | 9:47 | 50.3
2022-04-01 | 9:47 | 50.295
2022-04-01 | 9:47 | 50.294
2022-04-01 | 9:48 | 50.291
2022-04-01 | 9:48 | 50.29
2022-04-01 | 9:48 | 50.29
2022-04-01 | 9:48 | 50.29
2022-04-01 | 9:48 | 50.291
2022-04-01 | 9:48 | 50.292
2022-04-01 | 9:48 | 50.292
2022-04-01 | 9:48 | 50.292
2022-04-01 | 9:48 | 50.296
2022-04-01 | 9:48 | 50.296
2022-04-01 | 9:48 | 50.298
2022-04-01 | 9:48 | 50.296
2022-04-01 | 9:48 | 50.299
2022-04-01 | 9:48 | 50.298
2022-04-01 | 9:48 | 50.296
2022-04-01 | 9:48 | 50.3
2022-04-01 | 9:48 | 50.302
2022-04-01 | 9:48 | 50.302
2022-04-01 | 9:48 | 50.299
2022-04-01 | 9:48 | 50.298
2022-04-01 | 9:48 | 50.296
2022-04-01 | 9:48 | 50.291
2022-04-01 | 9:48 | 50.289
2022-04-01 | 9:48 | 50.289
2022-04-01 | 9:48 | 50.288
2022-04-01 | 9:48 | 50.287
2022-04-01 | 9:48 | 50.288
2022-04-01 | 9:48 | 50.288
2022-04-01 | 9:48 | 50.287
2022-04-01 | 9:48 | 50.283
2022-04-01 | 9:48 | 50.279
2022-04-01 | 9:48 | 50.275
2022-04-01 | 9:48 | 50.274
2022-04-01 | 9:48 | 50.273
2022-04-01 | 9:48 | 50.275
2022-04-01 | 9:48 | 50.278
2022-04-01 | 9:48 | 50.276
2022-04-01 | 9:48 | 50.277
2022-04-01 | 9:48 | 50.278
2022-04-01 | 9:48 | 50.275
2022-04-01 | 9:48 | 50.275
2022-04-01 | 9:48 | 50.27
2022-04-01 | 9:48 | 50.267
2022-04-01 | 9:48 | 50.263
2022-04-01 | 9:48 | 50.259
2022-04-01 | 9:48 | 50.252
2022-04-01 | 9:48 | 50.253
2022-04-01 | 9:48 | 50.254
2022-04-01 | 9:48 | 50.254
2022-04-01 | 9:48 | 50.258
2022-04-01 | 9:48 | 50.26
2022-04-01 | 9:48 | 50.264
2022-04-01 | 9:48 | 50.265
2022-04-01 | 9:48 | 50.267
2022-04-01 | 9:48 | 50.269
2022-04-01 | 9:48 | 50.268
2022-04-01 | 9:48 | 50.27
2022-04-01 | 9:48 | 50.269
2022-04-01 | 9:48 | 50.268
2022-04-01 | 9:48 | 50.27
2022-04-01 | 9:48 | 50.267
2022-04-01 | 9:49 | 50.265
2022-04-01 | 9:49 | 50.265
2022-04-01 | 9:49 | 50.265
2022-04-01 | 9:49 | 50.261
2022-04-01 | 9:49 | 50.26
2022-04-01 | 9:49 | 50.258
2022-04-01 | 9:49 | 50.255
2022-04-01 | 9:49 | 50.254
2022-04-01 | 9:49 | 50.255
2022-04-01 | 9:49 | 50.254
2022-04-01 | 9:49 | 50.253
2022-04-01 | 9:49 | 50.253
2022-04-01 | 9:49 | 50.253
2022-04-01 | 9:49 | 50.256
2022-04-01 | 9:49 | 50.256
2022-04-01 | 9:49 | 50.256
2022-04-01 | 9:49 | 50.254
2022-04-01 | 9:49 | 50.252
2022-04-01 | 9:49 | 50.25
2022-04-01 | 9:49 | 50.247
2022-04-01 | 9:49 | 50.244
2022-04-01 | 9:49 | 50.242
2022-04-01 | 9:49 | 50.237
2022-04-01 | 9:49 | 50.235
2022-04-01 | 9:49 | 50.232
2022-04-01 | 9:49 | 50.229
2022-04-01 | 9:49 | 50.229
2022-04-01 | 9:49 | 50.229
2022-04-01 | 9:49 | 50.228
2022-04-01 | 9:49 | 50.226
2022-04-01 | 9:49 | 50.225
2022-04-01 | 9:49 | 50.224
2022-04-01 | 9:49 | 50.223
2022-04-01 | 9:49 | 50.22
2022-04-01 | 9:49 | 50.221
2022-04-01 | 9:49 | 50.221
2022-04-01 | 9:49 | 50.221
2022-04-01 | 9:49 | 50.22
2022-04-01 | 9:49 | 50.22
2022-04-01 | 9:49 | 50.219
2022-04-01 | 9:49 | 50.218
2022-04-01 | 9:49 | 50.218
2022-04-01 | 9:49 | 50.217
2022-04-01 | 9:49 | 50.219
2022-04-01 | 9:49 | 50.22
2022-04-01 | 9:49 | 50.219
2022-04-01 | 9:49 | 50.219
2022-04-01 | 9:49 | 50.218
2022-04-01 | 9:49 | 50.216
2022-04-01 | 9:49 | 50.211
2022-04-01 | 9:49 | 50.208
2022-04-01 | 9:49 | 50.204
2022-04-01 | 9:49 | 50.202
2022-04-01 | 9:49 | 50.201
2022-04-01 | 9:49 | 50.2
2022-04-01 | 9:49 | 50.199
2022-04-01 | 9:49 | 50.197
2022-04-01 | 9:49 | 50.197
2022-04-01 | 9:49 | 50.197
2022-04-01 | 9:50 | 50.195
2022-04-01 | 9:50 | 50.192
2022-04-01 | 9:50 | 50.189
2022-04-01 | 9:50 | 50.191
2022-04-01 | 9:50 | 50.19
2022-04-01 | 9:50 | 50.19
2022-04-01 | 9:50 | 50.192
2022-04-01 | 9:50 | 50.195
2022-04-01 | 9:50 | 50.194
2022-04-01 | 9:50 | 50.195
2022-04-01 | 9:50 | 50.192
2022-04-01 | 9:50 | 50.187
2022-04-01 | 9:50 | 50.183
2022-04-01 | 9:50 | 50.18
2022-04-01 | 9:50 | 50.178
2022-04-01 | 9:50 | 50.177
2022-04-01 | 9:50 | 50.174
2022-04-01 | 9:50 | 50.171
2022-04-01 | 9:50 | 50.17
2022-04-01 | 9:50 | 50.169
2022-04-01 | 9:50 | 50.167
2022-04-01 | 9:50 | 50.165
2022-04-01 | 9:50 | 50.162
2022-04-01 | 9:50 | 50.162
2022-04-01 | 9:50 | 50.163
2022-04-01 | 9:50 | 50.162
2022-04-01 | 9:50 | 50.16
2022-04-01 | 9:50 | 50.159
2022-04-01 | 9:50 | 50.157
2022-04-01 | 9:50 | 50.157
2022-04-01 | 9:50 | 50.156
2022-04-01 | 9:50 | 50.152
2022-04-01 | 9:50 | 50.151
2022-04-01 | 9:50 | 50.149
2022-04-01 | 9:50 | 50.147
2022-04-01 | 9:50 | 50.148
2022-04-01 | 9:50 | 50.148
2022-04-01 | 9:50 | 50.15
2022-04-01 | 9:50 | 50.15
2022-04-01 | 9:50 | 50.151
2022-04-01 | 9:50 | 50.15
2022-04-01 | 9:50 | 50.15
2022-04-01 | 9:50 | 50.151
2022-04-01 | 9:50 | 50.15
2022-04-01 | 9:50 | 50.151
2022-04-01 | 9:50 | 50.152
2022-04-01 | 9:50 | 50.152
2022-04-01 | 9:50 | 50.152
2022-04-01 | 9:50 | 50.15
2022-04-01 | 9:50 | 50.147
2022-04-01 | 9:50 | 50.145
2022-04-01 | 9:50 | 50.144
2022-04-01 | 9:50 | 50.142
2022-04-01 | 9:50 | 50.142
2022-04-01 | 9:50 | 50.143
2022-04-01 | 9:50 | 50.142
2022-04-01 | 9:50 | 50.145
2022-04-01 | 9:50 | 50.145
2022-04-01 | 9:50 | 50.143
2022-04-01 | 9:50 | 50.141
2022-04-01 | 9:50 | 50.14
2022-04-01 | 9:51 | 50.138
2022-04-01 | 9:51 | 50.136
2022-04-01 | 9:51 | 50.135
2022-04-01 | 9:51 | 50.136
2022-04-01 | 9:51 | 50.137
2022-04-01 | 9:51 | 50.139
2022-04-01 | 9:51 | 50.139
2022-04-01 | 9:51 | 50.14
2022-04-01 | 9:51 | 50.14
2022-04-01 | 9:51 | 50.138
2022-04-01 | 9:51 | 50.134
2022-04-01 | 9:51 | 50.129
2022-04-01 | 9:51 | 50.127
2022-04-01 | 9:51 | 50.128
2022-04-01 | 9:51 | 50.127
2022-04-01 | 9:51 | 50.128
2022-04-01 | 9:51 | 50.128
2022-04-01 | 9:51 | 50.129
2022-04-01 | 9:51 | 50.128
2022-04-01 | 9:51 | 50.128
2022-04-01 | 9:51 | 50.129
2022-04-01 | 9:51 | 50.13
2022-04-01 | 9:51 | 50.13
2022-04-01 | 9:51 | 50.133
2022-04-01 | 9:51 | 50.134
2022-04-01 | 9:51 | 50.133
2022-04-01 | 9:51 | 50.135
2022-04-01 | 9:51 | 50.135
2022-04-01 | 9:51 | 50.136
2022-04-01 | 9:51 | 50.136
2022-04-01 | 9:51 | 50.133
2022-04-01 | 9:51 | 50.133
2022-04-01 | 9:51 | 50.133
2022-04-01 | 9:51 | 50.131
2022-04-01 | 9:51 | 50.128
2022-04-01 | 9:51 | 50.124
2022-04-01 | 9:51 | 50.12
2022-04-01 | 9:51 | 50.117
2022-04-01 | 9:51 | 50.114
2022-04-01 | 9:51 | 50.113
2022-04-01 | 9:51 | 50.11
2022-04-01 | 9:51 | 50.109
2022-04-01 | 9:51 | 50.108
2022-04-01 | 9:51 | 50.107
2022-04-01 | 9:51 | 50.108
2022-04-01 | 9:51 | 50.106
2022-04-01 | 9:51 | 50.106
2022-04-01 | 9:51 | 50.106
2022-04-01 | 9:51 | 50.105
2022-04-01 | 9:51 | 50.103
2022-04-01 | 9:51 | 50.102
2022-04-01 | 9:51 | 50.101
2022-04-01 | 9:51 | 50.1
2022-04-01 | 9:51 | 50.098
2022-04-01 | 9:51 | 50.103
2022-04-01 | 9:51 | 50.106
2022-04-01 | 9:51 | 50.109
2022-04-01 | 9:51 | 50.111
2022-04-01 | 9:51 | 50.112
2022-04-01 | 9:52 | 50.113
2022-04-01 | 9:52 | 50.117
2022-04-01 | 9:52 | 50.119
2022-04-01 | 9:52 | 50.121
2022-04-01 | 9:52 | 50.12
2022-04-01 | 9:52 | 50.118
2022-04-01 | 9:52 | 50.114
2022-04-01 | 9:52 | 50.11
2022-04-01 | 9:52 | 50.106
2022-04-01 | 9:52 | 50.106
2022-04-01 | 9:52 | 50.104
2022-04-01 | 9:52 | 50.102
2022-04-01 | 9:52 | 50.099
2022-04-01 | 9:52 | 50.095
2022-04-01 | 9:52 | 50.094
2022-04-01 | 9:52 | 50.093
2022-04-01 | 9:52 | 50.093
2022-04-01 | 9:52 | 50.094
2022-04-01 | 9:52 | 50.095
2022-04-01 | 9:52 | 50.092
2022-04-01 | 9:52 | 50.091
2022-04-01 | 9:52 | 50.088
2022-04-01 | 9:52 | 50.086
2022-04-01 | 9:52 | 50.084
2022-04-01 | 9:52 | 50.08
2022-04-01 | 9:52 | 50.077
2022-04-01 | 9:52 | 50.071
2022-04-01 | 9:52 | 50.069
2022-04-01 | 9:52 | 50.067
2022-04-01 | 9:52 | 50.065
2022-04-01 | 9:52 | 50.062
2022-04-01 | 9:52 | 50.062
2022-04-01 | 9:52 | 50.059
2022-04-01 | 9:52 | 50.058
2022-04-01 | 9:52 | 50.058
2022-04-01 | 9:52 | 50.057
2022-04-01 | 9:52 | 50.056
2022-04-01 | 9:52 | 50.055
2022-04-01 | 9:52 | 50.054
2022-04-01 | 9:52 | 50.055
2022-04-01 | 9:52 | 50.057
2022-04-01 | 9:52 | 50.058
2022-04-01 | 9:52 | 50.061
2022-04-01 | 9:52 | 50.062
2022-04-01 | 9:52 | 50.064
2022-04-01 | 9:52 | 50.065
2022-04-01 | 9:52 | 50.068
2022-04-01 | 9:52 | 50.071
2022-04-01 | 9:52 | 50.072
2022-04-01 | 9:52 | 50.071
2022-04-01 | 9:52 | 50.067
2022-04-01 | 9:52 | 50.064
2022-04-01 | 9:52 | 50.063
2022-04-01 | 9:52 | 50.062
2022-04-01 | 9:52 | 50.059
2022-04-01 | 9:52 | 50.057
2022-04-01 | 9:52 | 50.055
2022-04-01 | 9:52 | 50.056
2022-04-01 | 9:52 | 50.056
2022-04-01 | 9:52 | 50.057
2022-04-01 | 9:52 | 50.059
2022-04-01 | 9:53 | 50.062
2022-04-01 | 9:53 | 50.064
2022-04-01 | 9:53 | 50.065
2022-04-01 | 9:53 | 50.065
2022-04-01 | 9:53 | 50.066
2022-04-01 | 9:53 | 50.064
2022-04-01 | 9:53 | 50.065
2022-04-01 | 9:53 | 50.063
2022-04-01 | 9:53 | 50.061
2022-04-01 | 9:53 | 50.059
2022-04-01 | 9:53 | 50.058
2022-04-01 | 9:53 | 50.056
2022-04-01 | 9:53 | 50.053
2022-04-01 | 9:53 | 50.052
2022-04-01 | 9:53 | 50.052
2022-04-01 | 9:53 | 50.054
2022-04-01 | 9:53 | 50.055
2022-04-01 | 9:53 | 50.055
2022-04-01 | 9:53 | 50.055
2022-04-01 | 9:53 | 50.055
2022-04-01 | 9:53 | 50.051
2022-04-01 | 9:53 | 50.05
2022-04-01 | 9:53 | 50.049
2022-04-01 | 9:53 | 50.047
2022-04-01 | 9:53 | 50.049
2022-04-01 | 9:53 | 50.052
2022-04-01 | 9:53 | 50.052
2022-04-01 | 9:53 | 50.056
2022-04-01 | 9:53 | 50.058
2022-04-01 | 9:53 | 50.06
2022-04-01 | 9:53 | 50.058
2022-04-01 | 9:53 | 50.057
2022-04-01 | 9:53 | 50.058
2022-04-01 | 9:53 | 50.06
2022-04-01 | 9:53 | 50.062
2022-04-01 | 9:53 | 50.066
2022-04-01 | 9:53 | 50.067
2022-04-01 | 9:53 | 50.065
2022-04-01 | 9:53 | 50.064
2022-04-01 | 9:53 | 50.064
2022-04-01 | 9:53 | 50.064
2022-04-01 | 9:53 | 50.062
2022-04-01 | 9:53 | 50.061
2022-04-01 | 9:53 | 50.063
2022-04-01 | 9:53 | 50.064
2022-04-01 | 9:53 | 50.065
2022-04-01 | 9:53 | 50.063
2022-04-01 | 9:53 | 50.06
2022-04-01 | 9:53 | 50.058
2022-04-01 | 9:53 | 50.056
2022-04-01 | 9:53 | 50.057
2022-04-01 | 9:53 | 50.056
2022-04-01 | 9:53 | 50.056
2022-04-01 | 9:53 | 50.054
2022-04-01 | 9:53 | 50.052
2022-04-01 | 9:53 | 50.049
2022-04-01 | 9:53 | 50.047
2022-04-01 | 9:53 | 50.045
2022-04-01 | 9:53 | 50.045
2022-04-01 | 9:54 | 50.046
2022-04-01 | 9:54 | 50.047
2022-04-01 | 9:54 | 50.051
2022-04-01 | 9:54 | 50.053
2022-04-01 | 9:54 | 50.053
2022-04-01 | 9:54 | 50.053
2022-04-01 | 9:54 | 50.053
2022-04-01 | 9:54 | 50.056
2022-04-01 | 9:54 | 50.057
2022-04-01 | 9:54 | 50.056
2022-04-01 | 9:54 | 50.05
2022-04-01 | 9:54 | 50.047
2022-04-01 | 9:54 | 50.044
2022-04-01 | 9:54 | 50.044
2022-04-01 | 9:54 | 50.044
2022-04-01 | 9:54 | 50.046
2022-04-01 | 9:54 | 50.047
2022-04-01 | 9:54 | 50.047
2022-04-01 | 9:54 | 50.047
2022-04-01 | 9:54 | 50.048
2022-04-01 | 9:54 | 50.051
2022-04-01 | 9:54 | 50.052
2022-04-01 | 9:54 | 50.052
2022-04-01 | 9:54 | 50.05
2022-04-01 | 9:54 | 50.049
2022-04-01 | 9:54 | 50.053
2022-04-01 | 9:54 | 50.056
2022-04-01 | 9:54 | 50.059
2022-04-01 | 9:54 | 50.06
2022-04-01 | 9:54 | 50.061
2022-04-01 | 9:54 | 50.061

## 20220409-1
In GMT
Date | Time | Freq
2022-04-09 | 10:10 | 50.192
2022-04-09 | 10:10 | 50.19
2022-04-09 | 10:10 | 50.188
2022-04-09 | 10:10 | 50.185
2022-04-09 | 10:10 | 50.184
2022-04-09 | 10:10 | 50.182
2022-04-09 | 10:10 | 50.179
2022-04-09 | 10:10 | 50.177
2022-04-09 | 10:10 | 50.175
2022-04-09 | 10:10 | 50.175
2022-04-09 | 10:10 | 50.173
2022-04-09 | 10:10 | 50.17
2022-04-09 | 10:10 | 50.168
2022-04-09 | 10:10 | 50.164
2022-04-09 | 10:10 | 50.16
2022-04-09 | 10:10 | 50.158
2022-04-09 | 10:10 | 50.156
2022-04-09 | 10:10 | 50.157
2022-04-09 | 10:10 | 50.16
2022-04-09 | 10:10 | 50.161
2022-04-09 | 10:10 | 50.16
2022-04-09 | 10:10 | 50.159
2022-04-09 | 10:10 | 50.158
2022-04-09 | 10:10 | 50.156
2022-04-09 | 10:10 | 50.154
2022-04-09 | 10:10 | 50.152
2022-04-09 | 10:10 | 50.151
2022-04-09 | 10:10 | 50.149
2022-04-09 | 10:10 | 50.149
2022-04-09 | 10:10 | 50.148
2022-04-09 | 10:11 | 50.149
2022-04-09 | 10:11 | 50.153
2022-04-09 | 10:11 | 50.157
2022-04-09 | 10:11 | 50.162
2022-04-09 | 10:11 | 50.167
2022-04-09 | 10:11 | 50.169
2022-04-09 | 10:11 | 50.168
2022-04-09 | 10:11 | 50.167
2022-04-09 | 10:11 | 50.167
2022-04-09 | 10:11 | 50.168
2022-04-09 | 10:11 | 50.168
2022-04-09 | 10:11 | 50.166
2022-04-09 | 10:11 | 50.166
2022-04-09 | 10:11 | 50.166
2022-04-09 | 10:11 | 50.165
2022-04-09 | 10:11 | 50.165
2022-04-09 | 10:11 | 50.164
2022-04-09 | 10:11 | 50.168
2022-04-09 | 10:11 | 50.172
2022-04-09 | 10:11 | 50.175
2022-04-09 | 10:11 | 50.176
2022-04-09 | 10:11 | 50.18
2022-04-09 | 10:11 | 50.181
2022-04-09 | 10:11 | 50.181
2022-04-09 | 10:11 | 50.181
2022-04-09 | 10:11 | 50.181
2022-04-09 | 10:11 | 50.182
2022-04-09 | 10:11 | 50.181
2022-04-09 | 10:11 | 50.18
2022-04-09 | 10:11 | 50.179
2022-04-09 | 10:11 | 50.179
2022-04-09 | 10:11 | 50.177
2022-04-09 | 10:11 | 50.176
2022-04-09 | 10:11 | 50.174
2022-04-09 | 10:11 | 50.171
2022-04-09 | 10:11 | 50.168
2022-04-09 | 10:11 | 50.162
2022-04-09 | 10:11 | 50.157
2022-04-09 | 10:11 | 50.152
2022-04-09 | 10:11 | 50.149
2022-04-09 | 10:11 | 50.147
2022-04-09 | 10:11 | 50.148
2022-04-09 | 10:11 | 50.147
2022-04-09 | 10:11 | 50.146
2022-04-09 | 10:11 | 50.143
2022-04-09 | 10:11 | 50.141
2022-04-09 | 10:11 | 50.141
2022-04-09 | 10:11 | 50.144
2022-04-09 | 10:11 | 50.147
2022-04-09 | 10:11 | 50.148
2022-04-09 | 10:11 | 50.149
2022-04-09 | 10:11 | 50.152
2022-04-09 | 10:11 | 50.155
2022-04-09 | 10:11 | 50.16
2022-04-09 | 10:11 | 50.165
2022-04-09 | 10:11 | 50.168
2022-04-09 | 10:11 | 50.17
2022-04-09 | 10:11 | 50.172
2022-04-09 | 10:11 | 50.171
2022-04-09 | 10:11 | 50.172
2022-04-09 | 10:12 | 50.173
2022-04-09 | 10:12 | 50.175
2022-04-09 | 10:12 | 50.176
2022-04-09 | 10:12 | 50.175
2022-04-09 | 10:12 | 50.174
2022-04-09 | 10:12 | 50.173
2022-04-09 | 10:12 | 50.171
2022-04-09 | 10:12 | 50.175
2022-04-09 | 10:12 | 50.179
2022-04-09 | 10:12 | 50.185
2022-04-09 | 10:12 | 50.189
2022-04-09 | 10:12 | 50.191
2022-04-09 | 10:12 | 50.193
2022-04-09 | 10:12 | 50.191
2022-04-09 | 10:12 | 50.186
2022-04-09 | 10:12 | 50.183
2022-04-09 | 10:12 | 50.182
2022-04-09 | 10:12 | 50.183
2022-04-09 | 10:12 | 50.184
2022-04-09 | 10:12 | 50.182
2022-04-09 | 10:12 | 50.183
2022-04-09 | 10:12 | 50.182
2022-04-09 | 10:12 | 50.178
2022-04-09 | 10:12 | 50.178
2022-04-09 | 10:12 | 50.181
2022-04-09 | 10:12 | 50.181
2022-04-09 | 10:12 | 50.181
2022-04-09 | 10:12 | 50.181
2022-04-09 | 10:12 | 50.183
2022-04-09 | 10:12 | 50.183
2022-04-09 | 10:12 | 50.184
2022-04-09 | 10:12 | 50.182
2022-04-09 | 10:12 | 50.184
2022-04-09 | 10:12 | 50.186
2022-04-09 | 10:12 | 50.187
2022-04-09 | 10:12 | 50.186
2022-04-09 | 10:12 | 50.188
2022-04-09 | 10:12 | 50.186
2022-04-09 | 10:12 | 50.185
2022-04-09 | 10:12 | 50.179
2022-04-09 | 10:12 | 50.177
2022-04-09 | 10:12 | 50.176
2022-04-09 | 10:12 | 50.177
2022-04-09 | 10:12 | 50.178
2022-04-09 | 10:12 | 50.183
2022-04-09 | 10:12 | 50.189
2022-04-09 | 10:12 | 50.191
2022-04-09 | 10:12 | 50.189
2022-04-09 | 10:12 | 50.187
2022-04-09 | 10:12 | 50.184
2022-04-09 | 10:12 | 50.184
2022-04-09 | 10:12 | 50.179
2022-04-09 | 10:12 | 50.174
2022-04-09 | 10:12 | 50.167
2022-04-09 | 10:12 | 50.16
2022-04-09 | 10:12 | 50.152
2022-04-09 | 10:12 | 50.144
2022-04-09 | 10:12 | 50.141
2022-04-09 | 10:12 | 50.14
2022-04-09 | 10:12 | 50.141
2022-04-09 | 10:13 | 50.142
2022-04-09 | 10:13 | 50.142
2022-04-09 | 10:13 | 50.145
2022-04-09 | 10:13 | 50.147
2022-04-09 | 10:13 | 50.147
2022-04-09 | 10:13 | 50.146
2022-04-09 | 10:13 | 50.146
2022-04-09 | 10:13 | 50.145
2022-04-09 | 10:13 | 50.143
2022-04-09 | 10:13 | 50.14
2022-04-09 | 10:13 | 50.142
2022-04-09 | 10:13 | 50.14
2022-04-09 | 10:13 | 50.14
2022-04-09 | 10:13 | 50.14
2022-04-09 | 10:13 | 50.141
2022-04-09 | 10:13 | 50.145
2022-04-09 | 10:13 | 50.144
2022-04-09 | 10:13 | 50.143
2022-04-09 | 10:13 | 50.142
2022-04-09 | 10:13 | 50.142
2022-04-09 | 10:13 | 50.142
2022-04-09 | 10:13 | 50.139
2022-04-09 | 10:13 | 50.136
2022-04-09 | 10:13 | 50.135
2022-04-09 | 10:13 | 50.137
2022-04-09 | 10:13 | 50.135
2022-04-09 | 10:13 | 50.133
2022-04-09 | 10:13 | 50.13
2022-04-09 | 10:13 | 50.127
2022-04-09 | 10:13 | 50.124
2022-04-09 | 10:13 | 50.121
2022-04-09 | 10:13 | 50.118
2022-04-09 | 10:13 | 50.117
2022-04-09 | 10:13 | 50.114
2022-04-09 | 10:13 | 50.11
2022-04-09 | 10:13 | 50.11
2022-04-09 | 10:13 | 50.11
2022-04-09 | 10:13 | 50.11
2022-04-09 | 10:13 | 50.107
2022-04-09 | 10:13 | 50.104
2022-04-09 | 10:13 | 50.102
2022-04-09 | 10:13 | 50.098
2022-04-09 | 10:13 | 50.092
2022-04-09 | 10:13 | 50.085
2022-04-09 | 10:13 | 50.082
2022-04-09 | 10:13 | 50.078
2022-04-09 | 10:13 | 50.071
2022-04-09 | 10:13 | 50.067
2022-04-09 | 10:13 | 50.062
2022-04-09 | 10:13 | 50.062
2022-04-09 | 10:13 | 50.059
2022-04-09 | 10:13 | 50.059
2022-04-09 | 10:13 | 50.061
2022-04-09 | 10:13 | 50.061
2022-04-09 | 10:13 | 50.06
2022-04-09 | 10:13 | 50.056
2022-04-09 | 10:13 | 50.05
2022-04-09 | 10:13 | 50.047
2022-04-09 | 10:13 | 50.044
2022-04-09 | 10:13 | 50.047
2022-04-09 | 10:14 | 50.048
2022-04-09 | 10:14 | 50.049
2022-04-09 | 10:14 | 50.047
2022-04-09 | 10:14 | 50.045
2022-04-09 | 10:14 | 50.043
2022-04-09 | 10:14 | 50.041
2022-04-09 | 10:14 | 50.038
2022-04-09 | 10:14 | 50.033
2022-04-09 | 10:14 | 50.031
2022-04-09 | 10:14 | 50.03
2022-04-09 | 10:14 | 50.027
2022-04-09 | 10:14 | 50.024
2022-04-09 | 10:14 | 50.021
2022-04-09 | 10:14 | 50.02
2022-04-09 | 10:14 | 50.022
2022-04-09 | 10:14 | 50.023
2022-04-09 | 10:14 | 50.023
2022-04-09 | 10:14 | 50.022
2022-04-09 | 10:14 | 50.021
2022-04-09 | 10:14 | 50.018
2022-04-09 | 10:14 | 50.017
2022-04-09 | 10:14 | 50.017
2022-04-09 | 10:14 | 50.013
2022-04-09 | 10:14 | 50.013
2022-04-09 | 10:14 | 50.011
2022-04-09 | 10:14 | 50.006
2022-04-09 | 10:14 | 49.984
2022-04-09 | 10:14 | 49.962
2022-04-09 | 10:14 | 49.943
2022-04-09 | 10:14 | 49.93
2022-04-09 | 10:14 | 49.922
2022-04-09 | 10:14 | 49.918
2022-04-09 | 10:14 | 49.913
2022-04-09 | 10:14 | 49.91
2022-04-09 | 10:14 | 49.91
2022-04-09 | 10:14 | 49.913
2022-04-09 | 10:14 | 49.913
2022-04-09 | 10:14 | 49.912
2022-04-09 | 10:14 | 49.911
2022-04-09 | 10:14 | 49.91
2022-04-09 | 10:14 | 49.908
2022-04-09 | 10:14 | 49.904
2022-04-09 | 10:14 | 49.902
2022-04-09 | 10:14 | 49.9
2022-04-09 | 10:14 | 49.899
2022-04-09 | 10:14 | 49.895
2022-04-09 | 10:14 | 49.895
2022-04-09 | 10:14 | 49.898
2022-04-09 | 10:14 | 49.899
2022-04-09 | 10:14 | 49.898
2022-04-09 | 10:14 | 49.897
2022-04-09 | 10:14 | 49.894
2022-04-09 | 10:14 | 49.891
2022-04-09 | 10:14 | 49.887
2022-04-09 | 10:14 | 49.884
2022-04-09 | 10:14 | 49.881
2022-04-09 | 10:14 | 49.875
2022-04-09 | 10:14 | 49.869
2022-04-09 | 10:14 | 49.864
2022-04-09 | 10:14 | 49.863
2022-04-09 | 10:14 | 49.864
2022-04-09 | 10:15 | 49.863
2022-04-09 | 10:15 | 49.863
2022-04-09 | 10:15 | 49.861
2022-04-09 | 10:15 | 49.861
2022-04-09 | 10:15 | 49.861
2022-04-09 | 10:15 | 49.861
2022-04-09 | 10:15 | 49.863
2022-04-09 | 10:15 | 49.865
2022-04-09 | 10:15 | 49.866
2022-04-09 | 10:15 | 49.866
2022-04-09 | 10:15 | 49.867
2022-04-09 | 10:15 | 49.868
2022-04-09 | 10:15 | 49.871
2022-04-09 | 10:15 | 49.87
2022-04-09 | 10:15 | 49.867
2022-04-09 | 10:15 | 49.865
2022-04-09 | 10:15 | 49.866
2022-04-09 | 10:15 | 49.867
2022-04-09 | 10:15 | 49.867
2022-04-09 | 10:15 | 49.867
2022-04-09 | 10:15 | 49.867
2022-04-09 | 10:15 | 49.866
2022-04-09 | 10:15 | 49.866
2022-04-09 | 10:15 | 49.868
2022-04-09 | 10:15 | 49.87
2022-04-09 | 10:15 | 49.873
2022-04-09 | 10:15 | 49.875
2022-04-09 | 10:15 | 49.881
2022-04-09 | 10:15 | 49.885
2022-04-09 | 10:15 | 49.887
2022-04-09 | 10:15 | 49.883
2022-04-09 | 10:15 | 49.879
2022-04-09 | 10:15 | 49.873
2022-04-09 | 10:15 | 49.868
2022-04-09 | 10:15 | 49.864
2022-04-09 | 10:15 | 49.862
2022-04-09 | 10:15 | 49.861
2022-04-09 | 10:15 | 49.864
2022-04-09 | 10:15 | 49.868
2022-04-09 | 10:15 | 49.871
2022-04-09 | 10:15 | 49.871
2022-04-09 | 10:15 | 49.871
2022-04-09 | 10:15 | 49.872
2022-04-09 | 10:15 | 49.875
2022-04-09 | 10:15 | 49.878
2022-04-09 | 10:15 | 49.883
2022-04-09 | 10:15 | 49.889
2022-04-09 | 10:15 | 49.893
2022-04-09 | 10:15 | 49.895
2022-04-09 | 10:15 | 49.899
2022-04-09 | 10:15 | 49.9
2022-04-09 | 10:15 | 49.902
2022-04-09 | 10:15 | 49.901
2022-04-09 | 10:15 | 49.899
2022-04-09 | 10:15 | 49.898
2022-04-09 | 10:15 | 49.897
2022-04-09 | 10:15 | 49.899
2022-04-09 | 10:15 | 49.904
2022-04-09 | 10:15 | 49.909
2022-04-09 | 10:16 | 49.913
2022-04-09 | 10:16 | 49.919
2022-04-09 | 10:16 | 49.926
2022-04-09 | 10:16 | 49.929
2022-04-09 | 10:16 | 49.933
2022-04-09 | 10:16 | 49.937
2022-04-09 | 10:16 | 49.939
2022-04-09 | 10:16 | 49.943
2022-04-09 | 10:16 | 49.943
2022-04-09 | 10:16 | 49.945
2022-04-09 | 10:16 | 49.947
2022-04-09 | 10:16 | 49.947
2022-04-09 | 10:16 | 49.952
2022-04-09 | 10:16 | 49.955
2022-04-09 | 10:16 | 49.955
2022-04-09 | 10:16 | 49.955
2022-04-09 | 10:16 | 49.956
2022-04-09 | 10:16 | 49.955
2022-04-09 | 10:16 | 49.954
2022-04-09 | 10:16 | 49.952
2022-04-09 | 10:16 | 49.953
2022-04-09 | 10:16 | 49.95
2022-04-09 | 10:16 | 49.95
2022-04-09 | 10:16 | 49.947
2022-04-09 | 10:16 | 49.945
2022-04-09 | 10:16 | 49.946
2022-04-09 | 10:16 | 49.954
2022-04-09 | 10:16 | 49.964
2022-04-09 | 10:16 | 49.972
2022-04-09 | 10:16 | 49.977
2022-04-09 | 10:16 | 49.98
2022-04-09 | 10:16 | 49.982
2022-04-09 | 10:16 | 49.983
2022-04-09 | 10:16 | 49.986
2022-04-09 | 10:16 | 49.984
2022-04-09 | 10:16 | 49.982
2022-04-09 | 10:16 | 49.978
2022-04-09 | 10:16 | 49.975
2022-04-09 | 10:16 | 49.974
2022-04-09 | 10:16 | 49.974
2022-04-09 | 10:16 | 49.974
2022-04-09 | 10:16 | 49.972
2022-04-09 | 10:16 | 49.972
2022-04-09 | 10:16 | 49.971
2022-04-09 | 10:16 | 49.971
2022-04-09 | 10:16 | 49.971
2022-04-09 | 10:16 | 49.973
2022-04-09 | 10:16 | 49.973
2022-04-09 | 10:16 | 49.974
2022-04-09 | 10:16 | 49.975
2022-04-09 | 10:16 | 49.977
2022-04-09 | 10:16 | 49.977
2022-04-09 | 10:16 | 49.974
2022-04-09 | 10:16 | 49.974
2022-04-09 | 10:16 | 49.971
2022-04-09 | 10:16 | 49.971
2022-04-09 | 10:16 | 49.971
2022-04-09 | 10:16 | 49.972
2022-04-09 | 10:16 | 49.971
2022-04-09 | 10:16 | 49.969
2022-04-09 | 10:16 | 49.97
2022-04-09 | 10:17 | 49.973
2022-04-09 | 10:17 | 49.975
2022-04-09 | 10:17 | 49.974
2022-04-09 | 10:17 | 49.971
2022-04-09 | 10:17 | 49.968
2022-04-09 | 10:17 | 49.966
2022-04-09 | 10:17 | 49.965
2022-04-09 | 10:17 | 49.966
2022-04-09 | 10:17 | 49.968
2022-04-09 | 10:17 | 49.971
2022-04-09 | 10:17 | 49.967
2022-04-09 | 10:17 | 49.965
2022-04-09 | 10:17 | 49.959
2022-04-09 | 10:17 | 49.956
2022-04-09 | 10:17 | 49.952
2022-04-09 | 10:17 | 49.949
2022-04-09 | 10:17 | 49.945
2022-04-09 | 10:17 | 49.942
2022-04-09 | 10:17 | 49.94
2022-04-09 | 10:17 | 49.939
2022-04-09 | 10:17 | 49.942
2022-04-09 | 10:17 | 49.943
2022-04-09 | 10:17 | 49.945
2022-04-09 | 10:17 | 49.947
2022-04-09 | 10:17 | 49.947
2022-04-09 | 10:17 | 49.946
2022-04-09 | 10:17 | 49.946
2022-04-09 | 10:17 | 49.947
2022-04-09 | 10:17 | 49.946
2022-04-09 | 10:17 | 49.943
2022-04-09 | 10:17 | 49.939
2022-04-09 | 10:17 | 49.938
2022-04-09 | 10:17 | 49.935
2022-04-09 | 10:17 | 49.933
2022-04-09 | 10:17 | 49.93
2022-04-09 | 10:17 | 49.929
2022-04-09 | 10:17 | 49.928
2022-04-09 | 10:17 | 49.927
2022-04-09 | 10:17 | 49.929
2022-04-09 | 10:17 | 49.933
2022-04-09 | 10:17 | 49.94
2022-04-09 | 10:17 | 49.945
2022-04-09 | 10:17 | 49.948
2022-04-09 | 10:17 | 49.948
2022-04-09 | 10:17 | 49.946
2022-04-09 | 10:17 | 49.943
2022-04-09 | 10:17 | 49.941
2022-04-09 | 10:17 | 49.939
2022-04-09 | 10:17 | 49.938
2022-04-09 | 10:17 | 49.933
2022-04-09 | 10:17 | 49.93
2022-04-09 | 10:17 | 49.928
2022-04-09 | 10:17 | 49.926
2022-04-09 | 10:17 | 49.923
2022-04-09 | 10:17 | 49.919
2022-04-09 | 10:17 | 49.919
2022-04-09 | 10:17 | 49.918
2022-04-09 | 10:17 | 49.921
2022-04-09 | 10:17 | 49.922
2022-04-09 | 10:18 | 49.925
2022-04-09 | 10:18 | 49.933
2022-04-09 | 10:18 | 49.937
2022-04-09 | 10:18 | 49.939
2022-04-09 | 10:18 | 49.939
2022-04-09 | 10:18 | 49.94
2022-04-09 | 10:18 | 49.939
2022-04-09 | 10:18 | 49.94
2022-04-09 | 10:18 | 49.94
2022-04-09 | 10:18 | 49.943
2022-04-09 | 10:18 | 49.945
2022-04-09 | 10:18 | 49.944
2022-04-09 | 10:18 | 49.944
2022-04-09 | 10:18 | 49.943
2022-04-09 | 10:18 | 49.937
2022-04-09 | 10:18 | 49.933
2022-04-09 | 10:18 | 49.93
2022-04-09 | 10:18 | 49.927
2022-04-09 | 10:18 | 49.925
2022-04-09 | 10:18 | 49.924
2022-04-09 | 10:18 | 49.923
2022-04-09 | 10:18 | 49.922
2022-04-09 | 10:18 | 49.922
2022-04-09 | 10:18 | 49.922
2022-04-09 | 10:18 | 49.919
2022-04-09 | 10:18 | 49.918
2022-04-09 | 10:18 | 49.917
2022-04-09 | 10:18 | 49.914
2022-04-09 | 10:18 | 49.911
2022-04-09 | 10:18 | 49.91
2022-04-09 | 10:18 | 49.907
2022-04-09 | 10:18 | 49.904
2022-04-09 | 10:18 | 49.9
2022-04-09 | 10:18 | 49.899
2022-04-09 | 10:18 | 49.903
2022-04-09 | 10:18 | 49.902
2022-04-09 | 10:18 | 49.901
2022-04-09 | 10:18 | 49.903
2022-04-09 | 10:18 | 49.905
2022-04-09 | 10:18 | 49.906
2022-04-09 | 10:18 | 49.908
2022-04-09 | 10:18 | 49.909
2022-04-09 | 10:18 | 49.91
2022-04-09 | 10:18 | 49.913
2022-04-09 | 10:18 | 49.914
2022-04-09 | 10:18 | 49.918
2022-04-09 | 10:18 | 49.923
2022-04-09 | 10:18 | 49.929
2022-04-09 | 10:18 | 49.93
2022-04-09 | 10:18 | 49.929
2022-04-09 | 10:18 | 49.928
2022-04-09 | 10:18 | 49.928
2022-04-09 | 10:18 | 49.927
2022-04-09 | 10:18 | 49.928
2022-04-09 | 10:18 | 49.924
2022-04-09 | 10:18 | 49.915
2022-04-09 | 10:18 | 49.904
2022-04-09 | 10:18 | 49.894
2022-04-09 | 10:18 | 49.884
2022-04-09 | 10:18 | 49.876
2022-04-09 | 10:18 | 49.869
2022-04-09 | 10:19 | 49.863
2022-04-09 | 10:19 | 49.858
2022-04-09 | 10:19 | 49.857
2022-04-09 | 10:19 | 49.858
2022-04-09 | 10:19 | 49.859
2022-04-09 | 10:19 | 49.861
2022-04-09 | 10:19 | 49.869
2022-04-09 | 10:19 | 49.875
2022-04-09 | 10:19 | 49.88
2022-04-09 | 10:19 | 49.885
2022-04-09 | 10:19 | 49.889
2022-04-09 | 10:19 | 49.89
2022-04-09 | 10:19 | 49.894
2022-04-09 | 10:19 | 49.896
2022-04-09 | 10:19 | 49.898
2022-04-09 | 10:19 | 49.896
2022-04-09 | 10:19 | 49.898
2022-04-09 | 10:19 | 49.903
2022-04-09 | 10:19 | 49.906
2022-04-09 | 10:19 | 49.908
2022-04-09 | 10:19 | 49.908
2022-04-09 | 10:19 | 49.907
2022-04-09 | 10:19 | 49.907
2022-04-09 | 10:19 | 49.907
2022-04-09 | 10:19 | 49.905
2022-04-09 | 10:19 | 49.901
2022-04-09 | 10:19 | 49.9
2022-04-09 | 10:19 | 49.898
2022-04-09 | 10:19 | 49.901
2022-04-09 | 10:19 | 49.902
2022-04-09 | 10:19 | 49.901
2022-04-09 | 10:19 | 49.899
2022-04-09 | 10:19 | 49.895
2022-04-09 | 10:19 | 49.891
2022-04-09 | 10:19 | 49.888
2022-04-09 | 10:19 | 49.886
2022-04-09 | 10:19 | 49.881
2022-04-09 | 10:19 | 49.876
2022-04-09 | 10:19 | 49.873
2022-04-09 | 10:19 | 49.869
2022-04-09 | 10:19 | 49.869
2022-04-09 | 10:19 | 49.869
2022-04-09 | 10:19 | 49.868
2022-04-09 | 10:19 | 49.87
2022-04-09 | 10:19 | 49.871
2022-04-09 | 10:19 | 49.872
2022-04-09 | 10:19 | 49.872
2022-04-09 | 10:19 | 49.874
2022-04-09 | 10:19 | 49.877
2022-04-09 | 10:19 | 49.877
2022-04-09 | 10:19 | 49.874
2022-04-09 | 10:19 | 49.873
2022-04-09 | 10:19 | 49.868
2022-04-09 | 10:19 | 49.866
2022-04-09 | 10:19 | 49.864
2022-04-09 | 10:19 | 49.863
2022-04-09 | 10:19 | 49.859
2022-04-09 | 10:19 | 49.858
2022-04-09 | 10:19 | 49.856
2022-04-09 | 10:20 | 49.857
2022-04-09 | 10:20 | 49.857
2022-04-09 | 10:20 | 49.857
2022-04-09 | 10:20 | 49.859
2022-04-09 | 10:20 | 49.863
2022-04-09 | 10:20 | 49.869
2022-04-09 | 10:20 | 49.873
2022-04-09 | 10:20 | 49.878
2022-04-09 | 10:20 | 49.881
2022-04-09 | 10:20 | 49.881
2022-04-09 | 10:20 | 49.881
2022-04-09 | 10:20 | 49.879
2022-04-09 | 10:20 | 49.877
2022-04-09 | 10:20 | 49.877
2022-04-09 | 10:20 | 49.878
2022-04-09 | 10:20 | 49.878
2022-04-09 | 10:20 | 49.875
2022-04-09 | 10:20 | 49.872
2022-04-09 | 10:20 | 49.871
2022-04-09 | 10:20 | 49.869
2022-04-09 | 10:20 | 49.871
2022-04-09 | 10:20 | 49.873
2022-04-09 | 10:20 | 49.873
2022-04-09 | 10:20 | 49.874
2022-04-09 | 10:20 | 49.873
2022-04-09 | 10:20 | 49.874
2022-04-09 | 10:20 | 49.877
2022-04-09 | 10:20 | 49.882
2022-04-09 | 10:20 | 49.888
2022-04-09 | 10:20 | 49.892
2022-04-09 | 10:20 | 49.896
2022-04-09 | 10:20 | 49.896
2022-04-09 | 10:20 | 49.897
2022-04-09 | 10:20 | 49.895
2022-04-09 | 10:20 | 49.895
2022-04-09 | 10:20 | 49.893
2022-04-09 | 10:20 | 49.89
2022-04-09 | 10:20 | 49.884
2022-04-09 | 10:20 | 49.878
2022-04-09 | 10:20 | 49.877
2022-04-09 | 10:20 | 49.878
2022-04-09 | 10:20 | 49.881
2022-04-09 | 10:20 | 49.887
2022-04-09 | 10:20 | 49.894
2022-04-09 | 10:20 | 49.901
2022-04-09 | 10:20 | 49.907
2022-04-09 | 10:20 | 49.907
2022-04-09 | 10:20 | 49.906
2022-04-09 | 10:20 | 49.906
2022-04-09 | 10:20 | 49.905
2022-04-09 | 10:20 | 49.907
2022-04-09 | 10:20 | 49.907
2022-04-09 | 10:20 | 49.908
2022-04-09 | 10:20 | 49.909
2022-04-09 | 10:20 | 49.911
2022-04-09 | 10:20 | 49.912
2022-04-09 | 10:20 | 49.914
2022-04-09 | 10:20 | 49.914
2022-04-09 | 10:20 | 49.914
2022-04-09 | 10:20 | 49.916
2022-04-09 | 10:20 | 49.92
2022-04-09 | 10:21 | 49.925
2022-04-09 | 10:21 | 49.929
2022-04-09 | 10:21 | 49.929
2022-04-09 | 10:21 | 49.93
2022-04-09 | 10:21 | 49.931
2022-04-09 | 10:21 | 49.932
2022-04-09 | 10:21 | 49.931
2022-04-09 | 10:21 | 49.931
2022-04-09 | 10:21 | 49.933
2022-04-09 | 10:21 | 49.936
2022-04-09 | 10:21 | 49.936
2022-04-09 | 10:21 | 49.936
2022-04-09 | 10:21 | 49.937
2022-04-09 | 10:21 | 49.937
2022-04-09 | 10:21 | 49.938
2022-04-09 | 10:21 | 49.939
2022-04-09 | 10:21 | 49.942
2022-04-09 | 10:21 | 49.946
2022-04-09 | 10:21 | 49.946
2022-04-09 | 10:21 | 49.946
2022-04-09 | 10:21 | 49.947
2022-04-09 | 10:21 | 49.946
2022-04-09 | 10:21 | 49.949
2022-04-09 | 10:21 | 49.947
2022-04-09 | 10:21 | 49.946
2022-04-09 | 10:21 | 49.946
2022-04-09 | 10:21 | 49.945
2022-04-09 | 10:21 | 49.945
2022-04-09 | 10:21 | 49.943
2022-04-09 | 10:21 | 49.941
2022-04-09 | 10:21 | 49.942
2022-04-09 | 10:21 | 49.941
2022-04-09 | 10:21 | 49.94
2022-04-09 | 10:21 | 49.945
2022-04-09 | 10:21 | 49.951
2022-04-09 | 10:21 | 49.954
2022-04-09 | 10:21 | 49.957
2022-04-09 | 10:21 | 49.959
2022-04-09 | 10:21 | 49.964
2022-04-09 | 10:21 | 49.966
2022-04-09 | 10:21 | 49.967
2022-04-09 | 10:21 | 49.97
2022-04-09 | 10:21 | 49.971
2022-04-09 | 10:21 | 49.972
2022-04-09 | 10:21 | 49.975
2022-04-09 | 10:21 | 49.977
2022-04-09 | 10:21 | 49.976
2022-04-09 | 10:21 | 49.972
2022-04-09 | 10:21 | 49.969
2022-04-09 | 10:21 | 49.965
2022-04-09 | 10:21 | 49.965
2022-04-09 | 10:21 | 49.965
2022-04-09 | 10:21 | 49.967
2022-04-09 | 10:21 | 49.967
2022-04-09 | 10:21 | 49.968
2022-04-09 | 10:21 | 49.968
2022-04-09 | 10:21 | 49.968
2022-04-09 | 10:21 | 49.965
2022-04-09 | 10:21 | 49.963
2022-04-09 | 10:22 | 49.963
2022-04-09 | 10:22 | 49.959
2022-04-09 | 10:22 | 49.954
2022-04-09 | 10:22 | 49.953
2022-04-09 | 10:22 | 49.952
2022-04-09 | 10:22 | 49.95
2022-04-09 | 10:22 | 49.946
2022-04-09 | 10:22 | 49.946
2022-04-09 | 10:22 | 49.945
2022-04-09 | 10:22 | 49.948
2022-04-09 | 10:22 | 49.95
2022-04-09 | 10:22 | 49.95
2022-04-09 | 10:22 | 49.954
2022-04-09 | 10:22 | 49.962
2022-04-09 | 10:22 | 49.968
2022-04-09 | 10:22 | 49.977
2022-04-09 | 10:22 | 49.985
2022-04-09 | 10:22 | 49.989
2022-04-09 | 10:22 | 49.988
2022-04-09 | 10:22 | 49.985
2022-04-09 | 10:22 | 49.982
2022-04-09 | 10:22 | 49.982
2022-04-09 | 10:22 | 49.982
2022-04-09 | 10:22 | 49.979
2022-04-09 | 10:22 | 49.976
2022-04-09 | 10:22 | 49.975
2022-04-09 | 10:22 | 49.972
2022-04-09 | 10:22 | 49.97
2022-04-09 | 10:22 | 49.967
2022-04-09 | 10:22 | 49.969
2022-04-09 | 10:22 | 49.966
2022-04-09 | 10:22 | 49.965
2022-04-09 | 10:22 | 49.964
2022-04-09 | 10:22 | 49.966
2022-04-09 | 10:22 | 49.968
2022-04-09 | 10:22 | 49.972
2022-04-09 | 10:22 | 49.973
2022-04-09 | 10:22 | 49.976
2022-04-09 | 10:22 | 49.977
2022-04-09 | 10:22 | 49.977
2022-04-09 | 10:22 | 49.978
2022-04-09 | 10:22 | 49.979
2022-04-09 | 10:22 | 49.982
2022-04-09 | 10:22 | 49.982
2022-04-09 | 10:22 | 49.986
2022-04-09 | 10:22 | 49.986
2022-04-09 | 10:22 | 49.987
2022-04-09 | 10:22 | 49.99
2022-04-09 | 10:22 | 49.988
2022-04-09 | 10:22 | 49.987
2022-04-09 | 10:22 | 49.988
2022-04-09 | 10:22 | 49.988
2022-04-09 | 10:22 | 49.985
2022-04-09 | 10:22 | 49.983
2022-04-09 | 10:22 | 49.985
2022-04-09 | 10:22 | 49.985
2022-04-09 | 10:22 | 49.983
2022-04-09 | 10:22 | 49.982
2022-04-09 | 10:22 | 49.98
2022-04-09 | 10:22 | 49.982
2022-04-09 | 10:22 | 49.979
2022-04-09 | 10:23 | 49.978
2022-04-09 | 10:23 | 49.977
2022-04-09 | 10:23 | 49.976
2022-04-09 | 10:23 | 49.973
2022-04-09 | 10:23 | 49.974
2022-04-09 | 10:23 | 49.972
2022-04-09 | 10:23 | 49.971
2022-04-09 | 10:23 | 49.968
2022-04-09 | 10:23 | 49.965
2022-04-09 | 10:23 | 49.963
2022-04-09 | 10:23 | 49.96
2022-04-09 | 10:23 | 49.96
2022-04-09 | 10:23 | 49.96
2022-04-09 | 10:23 | 49.958
2022-04-09 | 10:23 | 49.963
2022-04-09 | 10:23 | 49.965
2022-04-09 | 10:23 | 49.97
2022-04-09 | 10:23 | 49.973
2022-04-09 | 10:23 | 49.977
2022-04-09 | 10:23 | 49.98
2022-04-09 | 10:23 | 49.984
2022-04-09 | 10:23 | 49.986
2022-04-09 | 10:23 | 49.991
2022-04-09 | 10:23 | 49.994
2022-04-09 | 10:23 | 49.994
2022-04-09 | 10:23 | 49.992
2022-04-09 | 10:23 | 49.992
2022-04-09 | 10:23 | 49.993
2022-04-09 | 10:23 | 49.996
2022-04-09 | 10:23 | 49.999
2022-04-09 | 10:23 | 50.001
2022-04-09 | 10:23 | 50.002
2022-04-09 | 10:23 | 50.003
2022-04-09 | 10:23 | 50.003
2022-04-09 | 10:23 | 50.004
2022-04-09 | 10:23 | 50.006
2022-04-09 | 10:23 | 50.007
2022-04-09 | 10:23 | 50.004
2022-04-09 | 10:23 | 50.008
2022-04-09 | 10:23 | 50.013
2022-04-09 | 10:23 | 50.021
2022-04-09 | 10:23 | 50.025
2022-04-09 | 10:23 | 50.028
2022-04-09 | 10:23 | 50.033
2022-04-09 | 10:23 | 50.04
2022-04-09 | 10:23 | 50.043
2022-04-09 | 10:23 | 50.045
2022-04-09 | 10:23 | 50.046
2022-04-09 | 10:23 | 50.047
2022-04-09 | 10:23 | 50.046
2022-04-09 | 10:23 | 50.044
2022-04-09 | 10:23 | 50.043
2022-04-09 | 10:23 | 50.043
2022-04-09 | 10:23 | 50.041
2022-04-09 | 10:23 | 50.04
2022-04-09 | 10:23 | 50.04
2022-04-09 | 10:23 | 50.043
2022-04-09 | 10:23 | 50.046
2022-04-09 | 10:23 | 50.048
2022-04-09 | 10:24 | 50.049
2022-04-09 | 10:24 | 50.05
2022-04-09 | 10:24 | 50.052
2022-04-09 | 10:24 | 50.055
2022-04-09 | 10:24 | 50.053
2022-04-09 | 10:24 | 50.053
2022-04-09 | 10:24 | 50.052
2022-04-09 | 10:24 | 50.051
2022-04-09 | 10:24 | 50.047
2022-04-09 | 10:24 | 50.045
2022-04-09 | 10:24 | 50.044
2022-04-09 | 10:24 | 50.042
2022-04-09 | 10:24 | 50.036
2022-04-09 | 10:24 | 50.032
2022-04-09 | 10:24 | 50.033
2022-04-09 | 10:24 | 50.035
2022-04-09 | 10:24 | 50.036
2022-04-09 | 10:24 | 50.039
2022-04-09 | 10:24 | 50.04
2022-04-09 | 10:24 | 50.041
2022-04-09 | 10:24 | 50.041
2022-04-09 | 10:24 | 50.042
2022-04-09 | 10:24 | 50.044
2022-04-09 | 10:24 | 50.047
2022-04-09 | 10:24 | 50.054
2022-04-09 | 10:24 | 50.063
2022-04-09 | 10:24 | 50.067
2022-04-09 | 10:24 | 50.073
2022-04-09 | 10:24 | 50.074
2022-04-09 | 10:24 | 50.075
2022-04-09 | 10:24 | 50.075
2022-04-09 | 10:24 | 50.074
2022-04-09 | 10:24 | 50.071
2022-04-09 | 10:24 | 50.067
2022-04-09 | 10:24 | 50.067
2022-04-09 | 10:24 | 50.07
2022-04-09 | 10:24 | 50.07
2022-04-09 | 10:24 | 50.069
2022-04-09 | 10:24 | 50.066
2022-04-09 | 10:24 | 50.065
2022-04-09 | 10:24 | 50.061
2022-04-09 | 10:24 | 50.06
2022-04-09 | 10:24 | 50.059
2022-04-09 | 10:24 | 50.065
2022-04-09 | 10:24 | 50.071
2022-04-09 | 10:24 | 50.077
2022-04-09 | 10:24 | 50.083
2022-04-09 | 10:24 | 50.089
2022-04-09 | 10:24 | 50.092
2022-04-09 | 10:24 | 50.096
2022-04-09 | 10:24 | 50.094
2022-04-09 | 10:24 | 50.093
2022-04-09 | 10:24 | 50.091
2022-04-09 | 10:24 | 50.087
2022-04-09 | 10:24 | 50.081
2022-04-09 | 10:24 | 50.077
2022-04-09 | 10:24 | 50.076
2022-04-09 | 10:24 | 50.076
2022-04-09 | 10:24 | 50.076
2022-04-09 | 10:24 | 50.075
2022-04-09 | 10:24 | 50.076
2022-04-09 | 10:25 | 50.077
2022-04-09 | 10:25 | 50.076
2022-04-09 | 10:25 | 50.074
2022-04-09 | 10:25 | 50.076
2022-04-09 | 10:25 | 50.079
2022-04-09 | 10:25 | 50.08
2022-04-09 | 10:25 | 50.081
2022-04-09 | 10:25 | 50.082
2022-04-09 | 10:25 | 50.081
2022-04-09 | 10:25 | 50.082
2022-04-09 | 10:25 | 50.083
2022-04-09 | 10:25 | 50.085
2022-04-09 | 10:25 | 50.089
2022-04-09 | 10:25 | 50.092
2022-04-09 | 10:25 | 50.09
2022-04-09 | 10:25 | 50.089
2022-04-09 | 10:25 | 50.087
2022-04-09 | 10:25 | 50.082
2022-04-09 | 10:25 | 50.083
2022-04-09 | 10:25 | 50.084
2022-04-09 | 10:25 | 50.088
2022-04-09 | 10:25 | 50.09
2022-04-09 | 10:25 | 50.089
2022-04-09 | 10:25 | 50.087
2022-04-09 | 10:25 | 50.086
2022-04-09 | 10:25 | 50.084
2022-04-09 | 10:25 | 50.085
2022-04-09 | 10:25 | 50.085
2022-04-09 | 10:25 | 50.086
2022-04-09 | 10:25 | 50.089

## 20220412-1
In GMT
Date | Time | Freq
2021-07-20 | 20:59 | 50.13
2021-07-20 | 20:59 | 50.131
2021-07-20 | 20:59 | 50.132
2021-07-20 | 20:59 | 50.13
2021-07-20 | 20:59 | 50.13
2021-07-20 | 20:59 | 50.125
2021-07-20 | 20:59 | 50.119
2021-07-20 | 20:59 | 50.115
2021-07-20 | 20:59 | 50.108
2021-07-20 | 20:59 | 50.104
2021-07-20 | 20:59 | 50.104
2021-07-20 | 20:59 | 50.103
2021-07-20 | 20:59 | 50.105
2021-07-20 | 20:59 | 50.111
2021-07-20 | 20:59 | 50.114
2021-07-20 | 20:59 | 50.116
2021-07-20 | 20:59 | 50.117
2021-07-20 | 20:59 | 50.12
2021-07-20 | 20:59 | 50.121
2021-07-20 | 20:59 | 50.123
2021-07-20 | 20:59 | 50.123
2021-07-20 | 20:59 | 50.122
2021-07-20 | 20:59 | 50.119
2021-07-20 | 20:59 | 50.117
2021-07-20 | 20:59 | 50.114
2021-07-20 | 20:59 | 50.111
2021-07-20 | 20:59 | 50.107
2021-07-20 | 20:59 | 50.107
2021-07-20 | 20:59 | 50.106
2021-07-20 | 20:59 | 50.107
2021-07-20 | 21:00 | 50.104
2021-07-20 | 21:00 | 50.105
2021-07-20 | 21:00 | 50.106
2021-07-20 | 21:00 | 50.106
2021-07-20 | 21:00 | 50.106
2021-07-20 | 21:00 | 50.105
2021-07-20 | 21:00 | 50.107
2021-07-20 | 21:00 | 50.109
2021-07-20 | 21:00 | 50.11
2021-07-20 | 21:00 | 50.111
2021-07-20 | 21:00 | 50.111
2021-07-20 | 21:00 | 50.112
2021-07-20 | 21:00 | 50.112
2021-07-20 | 21:00 | 50.113
2021-07-20 | 21:00 | 50.114
2021-07-20 | 21:00 | 50.112
2021-07-20 | 21:00 | 50.111
2021-07-20 | 21:00 | 50.111
2021-07-20 | 21:00 | 50.112
2021-07-20 | 21:00 | 50.11
2021-07-20 | 21:00 | 50.111
2021-07-20 | 21:00 | 50.111
2021-07-20 | 21:00 | 50.109
2021-07-20 | 21:00 | 50.105
2021-07-20 | 21:00 | 50.101
2021-07-20 | 21:00 | 50.095
2021-07-20 | 21:00 | 50.091
2021-07-20 | 21:00 | 50.085
2021-07-20 | 21:00 | 50.078
2021-07-20 | 21:00 | 50.07
2021-07-20 | 21:00 | 50.062
2021-07-20 | 21:00 | 50.052
2021-07-20 | 21:00 | 50.041
2021-07-20 | 21:00 | 50.034
2021-07-20 | 21:00 | 50.025
2021-07-20 | 21:00 | 50.023
2021-07-20 | 21:00 | 50.021
2021-07-20 | 21:00 | 50.024
2021-07-20 | 21:00 | 50.027
2021-07-20 | 21:00 | 50.031
2021-07-20 | 21:00 | 50.035
2021-07-20 | 21:00 | 50.041
2021-07-20 | 21:00 | 50.044
2021-07-20 | 21:00 | 50.05
2021-07-20 | 21:00 | 50.053
2021-07-20 | 21:00 | 50.056
2021-07-20 | 21:00 | 50.057
2021-07-20 | 21:00 | 50.054
2021-07-20 | 21:00 | 50.051
2021-07-20 | 21:00 | 50.024
2021-07-20 | 21:00 | 50.001
2021-07-20 | 21:00 | 49.98
2021-07-20 | 21:00 | 49.963
2021-07-20 | 21:00 | 49.952
2021-07-20 | 21:00 | 49.946
2021-07-20 | 21:00 | 49.941
2021-07-20 | 21:00 | 49.938
2021-07-20 | 21:00 | 49.935
2021-07-20 | 21:00 | 49.935
2021-07-20 | 21:00 | 49.93
2021-07-20 | 21:00 | 49.924
2021-07-20 | 21:01 | 49.913
2021-07-20 | 21:01 | 49.902
2021-07-20 | 21:01 | 49.89
2021-07-20 | 21:01 | 49.88
2021-07-20 | 21:01 | 49.876
2021-07-20 | 21:01 | 49.879
2021-07-20 | 21:01 | 49.887
2021-07-20 | 21:01 | 49.896
2021-07-20 | 21:01 | 49.903
2021-07-20 | 21:01 | 49.91
2021-07-20 | 21:01 | 49.916
2021-07-20 | 21:01 | 49.922
2021-07-20 | 21:01 | 49.926
2021-07-20 | 21:01 | 49.927
2021-07-20 | 21:01 | 49.931
2021-07-20 | 21:01 | 49.934
2021-07-20 | 21:01 | 49.936
2021-07-20 | 21:01 | 49.937
2021-07-20 | 21:01 | 49.939
2021-07-20 | 21:01 | 49.939
2021-07-20 | 21:01 | 49.938
2021-07-20 | 21:01 | 49.935
2021-07-20 | 21:01 | 49.931
2021-07-20 | 21:01 | 49.927
2021-07-20 | 21:01 | 49.924
2021-07-20 | 21:01 | 49.92
2021-07-20 | 21:01 | 49.919
2021-07-20 | 21:01 | 49.916
2021-07-20 | 21:01 | 49.915
2021-07-20 | 21:01 | 49.912
2021-07-20 | 21:01 | 49.912
2021-07-20 | 21:01 | 49.909
2021-07-20 | 21:01 | 49.907
2021-07-20 | 21:01 | 49.905
2021-07-20 | 21:01 | 49.905
2021-07-20 | 21:01 | 49.905
2021-07-20 | 21:01 | 49.909
2021-07-20 | 21:01 | 49.912
2021-07-20 | 21:01 | 49.914
2021-07-20 | 21:01 | 49.916
2021-07-20 | 21:01 | 49.918
2021-07-20 | 21:01 | 49.919
2021-07-20 | 21:01 | 49.92
2021-07-20 | 21:01 | 49.92
2021-07-20 | 21:01 | 49.92
2021-07-20 | 21:01 | 49.917
2021-07-20 | 21:01 | 49.914
2021-07-20 | 21:01 | 49.91
2021-07-20 | 21:01 | 49.906
2021-07-20 | 21:01 | 49.903
2021-07-20 | 21:01 | 49.9
2021-07-20 | 21:01 | 49.898
2021-07-20 | 21:01 | 49.895
2021-07-20 | 21:01 | 49.894
2021-07-20 | 21:01 | 49.894
2021-07-20 | 21:01 | 49.894
2021-07-20 | 21:01 | 49.894
2021-07-20 | 21:01 | 49.894
2021-07-20 | 21:01 | 49.895
2021-07-20 | 21:02 | 49.895
2021-07-20 | 21:02 | 49.895
2021-07-20 | 21:02 | 49.892
2021-07-20 | 21:02 | 49.891
2021-07-20 | 21:02 | 49.89
2021-07-20 | 21:02 | 49.889
2021-07-20 | 21:02 | 49.89
2021-07-20 | 21:02 | 49.892
2021-07-20 | 21:02 | 49.895
2021-07-20 | 21:02 | 49.897
2021-07-20 | 21:02 | 49.897
2021-07-20 | 21:02 | 49.9
2021-07-20 | 21:02 | 49.901
2021-07-20 | 21:02 | 49.903
2021-07-20 | 21:02 | 49.905
2021-07-20 | 21:02 | 49.906
2021-07-20 | 21:02 | 49.909
2021-07-20 | 21:02 | 49.912
2021-07-20 | 21:02 | 49.913
2021-07-20 | 21:02 | 49.915
2021-07-20 | 21:02 | 49.917
2021-07-20 | 21:02 | 49.918
2021-07-20 | 21:02 | 49.92
2021-07-20 | 21:02 | 49.921
2021-07-20 | 21:02 | 49.924
2021-07-20 | 21:02 | 49.926
2021-07-20 | 21:02 | 49.928
2021-07-20 | 21:02 | 49.93
2021-07-20 | 21:02 | 49.931
2021-07-20 | 21:02 | 49.931
2021-07-20 | 21:02 | 49.93
2021-07-20 | 21:02 | 49.928
2021-07-20 | 21:02 | 49.926
2021-07-20 | 21:02 | 49.924
2021-07-20 | 21:02 | 49.922
2021-07-20 | 21:02 | 49.92
2021-07-20 | 21:02 | 49.917
2021-07-20 | 21:02 | 49.917
2021-07-20 | 21:02 | 49.914
2021-07-20 | 21:02 | 49.913
2021-07-20 | 21:02 | 49.91
2021-07-20 | 21:02 | 49.91
2021-07-20 | 21:02 | 49.909
2021-07-20 | 21:02 | 49.91
2021-07-20 | 21:02 | 49.91
2021-07-20 | 21:02 | 49.908
2021-07-20 | 21:02 | 49.905
2021-07-20 | 21:02 | 49.904
2021-07-20 | 21:02 | 49.904
2021-07-20 | 21:02 | 49.904
2021-07-20 | 21:02 | 49.907
2021-07-20 | 21:02 | 49.907
2021-07-20 | 21:02 | 49.909
2021-07-20 | 21:02 | 49.91
2021-07-20 | 21:02 | 49.911
2021-07-20 | 21:02 | 49.911
2021-07-20 | 21:02 | 49.909
2021-07-20 | 21:02 | 49.908
2021-07-20 | 21:02 | 49.909
2021-07-20 | 21:02 | 49.911
2021-07-20 | 21:02 | 49.911
2021-07-20 | 21:03 | 49.914
2021-07-20 | 21:03 | 49.916
2021-07-20 | 21:03 | 49.92
2021-07-20 | 21:03 | 49.923
2021-07-20 | 21:03 | 49.928
2021-07-20 | 21:03 | 49.93
2021-07-20 | 21:03 | 49.93
2021-07-20 | 21:03 | 49.93
2021-07-20 | 21:03 | 49.929
2021-07-20 | 21:03 | 49.929
2021-07-20 | 21:03 | 49.927
2021-07-20 | 21:03 | 49.926
2021-07-20 | 21:03 | 49.926
2021-07-20 | 21:03 | 49.926
2021-07-20 | 21:03 | 49.925
2021-07-20 | 21:03 | 49.925
2021-07-20 | 21:03 | 49.926
2021-07-20 | 21:03 | 49.925
2021-07-20 | 21:03 | 49.924
2021-07-20 | 21:03 | 49.925
2021-07-20 | 21:03 | 49.923
2021-07-20 | 21:03 | 49.921
2021-07-20 | 21:03 | 49.919
2021-07-20 | 21:03 | 49.915
2021-07-20 | 21:03 | 49.914
2021-07-20 | 21:03 | 49.913
2021-07-20 | 21:03 | 49.911
2021-07-20 | 21:03 | 49.91
2021-07-20 | 21:03 | 49.909
2021-07-20 | 21:03 | 49.907
2021-07-20 | 21:03 | 49.904
2021-07-20 | 21:03 | 49.901
2021-07-20 | 21:03 | 49.898
2021-07-20 | 21:03 | 49.899
2021-07-20 | 21:03 | 49.899
2021-07-20 | 21:03 | 49.901
2021-07-20 | 21:03 | 49.904
2021-07-20 | 21:03 | 49.906
2021-07-20 | 21:03 | 49.908
2021-07-20 | 21:03 | 49.908
2021-07-20 | 21:03 | 49.908
2021-07-20 | 21:03 | 49.91
2021-07-20 | 21:03 | 49.911
2021-07-20 | 21:03 | 49.91
2021-07-20 | 21:03 | 49.911
2021-07-20 | 21:03 | 49.908
2021-07-20 | 21:03 | 49.906
2021-07-20 | 21:03 | 49.904
2021-07-20 | 21:03 | 49.904
2021-07-20 | 21:03 | 49.904
2021-07-20 | 21:03 | 49.903
2021-07-20 | 21:03 | 49.904
2021-07-20 | 21:03 | 49.905
2021-07-20 | 21:03 | 49.908
2021-07-20 | 21:03 | 49.91
2021-07-20 | 21:03 | 49.912
2021-07-20 | 21:03 | 49.913
2021-07-20 | 21:03 | 49.911
2021-07-20 | 21:03 | 49.91
2021-07-20 | 21:04 | 49.907
2021-07-20 | 21:04 | 49.908
2021-07-20 | 21:04 | 49.91
2021-07-20 | 21:04 | 49.91
2021-07-20 | 21:04 | 49.91
2021-07-20 | 21:04 | 49.911
2021-07-20 | 21:04 | 49.911
2021-07-20 | 21:04 | 49.911
2021-07-20 | 21:04 | 49.912
2021-07-20 | 21:04 | 49.913
2021-07-20 | 21:04 | 49.913
2021-07-20 | 21:04 | 49.912
2021-07-20 | 21:04 | 49.911
2021-07-20 | 21:04 | 49.911
2021-07-20 | 21:04 | 49.909
2021-07-20 | 21:04 | 49.909
2021-07-20 | 21:04 | 49.909
2021-07-20 | 21:04 | 49.912
2021-07-20 | 21:04 | 49.915
2021-07-20 | 21:04 | 49.918
2021-07-20 | 21:04 | 49.921
2021-07-20 | 21:04 | 49.922
2021-07-20 | 21:04 | 49.923
2021-07-20 | 21:04 | 49.925
2021-07-20 | 21:04 | 49.925
2021-07-20 | 21:04 | 49.926
2021-07-20 | 21:04 | 49.925
2021-07-20 | 21:04 | 49.924
2021-07-20 | 21:04 | 49.923
2021-07-20 | 21:04 | 49.923
2021-07-20 | 21:04 | 49.923
2021-07-20 | 21:04 | 49.921
2021-07-20 | 21:04 | 49.921
2021-07-20 | 21:04 | 49.921
2021-07-20 | 21:04 | 49.921
2021-07-20 | 21:04 | 49.922
2021-07-20 | 21:04 | 49.923
2021-07-20 | 21:04 | 49.924
2021-07-20 | 21:04 | 49.927
2021-07-20 | 21:04 | 49.928
2021-07-20 | 21:04 | 49.931
2021-07-20 | 21:04 | 49.935
2021-07-20 | 21:04 | 49.937
2021-07-20 | 21:04 | 49.94
2021-07-20 | 21:04 | 49.942
2021-07-20 | 21:04 | 49.944
2021-07-20 | 21:04 | 49.945
2021-07-20 | 21:04 | 49.944
2021-07-20 | 21:04 | 49.947
2021-07-20 | 21:04 | 49.948
2021-07-20 | 21:04 | 49.948
2021-07-20 | 21:04 | 49.949
2021-07-20 | 21:04 | 49.948
2021-07-20 | 21:04 | 49.946
2021-07-20 | 21:04 | 49.945
2021-07-20 | 21:04 | 49.944
2021-07-20 | 21:04 | 49.944
2021-07-20 | 21:04 | 49.943
2021-07-20 | 21:04 | 49.943
2021-07-20 | 21:04 | 49.942
2021-07-20 | 21:04 | 49.942
2021-07-20 | 21:05 | 49.942
2021-07-20 | 21:05 | 49.944
2021-07-20 | 21:05 | 49.942
2021-07-20 | 21:05 | 49.94
2021-07-20 | 21:05 | 49.937
2021-07-20 | 21:05 | 49.937
2021-07-20 | 21:05 | 49.937
2021-07-20 | 21:05 | 49.936
2021-07-20 | 21:05 | 49.934
2021-07-20 | 21:05 | 49.931
2021-07-20 | 21:05 | 49.93
2021-07-20 | 21:05 | 49.928
2021-07-20 | 21:05 | 49.926
2021-07-20 | 21:05 | 49.923
2021-07-20 | 21:05 | 49.921
2021-07-20 | 21:05 | 49.922
2021-07-20 | 21:05 | 49.923
2021-07-20 | 21:05 | 49.924
2021-07-20 | 21:05 | 49.924
2021-07-20 | 21:05 | 49.924
2021-07-20 | 21:05 | 49.923
2021-07-20 | 21:05 | 49.922
2021-07-20 | 21:05 | 49.919
2021-07-20 | 21:05 | 49.916
2021-07-20 | 21:05 | 49.914
2021-07-20 | 21:05 | 49.914
2021-07-20 | 21:05 | 49.914
2021-07-20 | 21:05 | 49.914
2021-07-20 | 21:05 | 49.912
2021-07-20 | 21:05 | 49.91
2021-07-20 | 21:05 | 49.908
2021-07-20 | 21:05 | 49.904
2021-07-20 | 21:05 | 49.903
2021-07-20 | 21:05 | 49.902
2021-07-20 | 21:05 | 49.904
2021-07-20 | 21:05 | 49.904
2021-07-20 | 21:05 | 49.905
2021-07-20 | 21:05 | 49.902
2021-07-20 | 21:05 | 49.9
2021-07-20 | 21:05 | 49.898
2021-07-20 | 21:05 | 49.893
2021-07-20 | 21:05 | 49.891
2021-07-20 | 21:05 | 49.892
2021-07-20 | 21:05 | 49.894
2021-07-20 | 21:05 | 49.896
2021-07-20 | 21:05 | 49.899
2021-07-20 | 21:05 | 49.899
2021-07-20 | 21:05 | 49.899
2021-07-20 | 21:05 | 49.896
2021-07-20 | 21:05 | 49.896
2021-07-20 | 21:05 | 49.895
2021-07-20 | 21:05 | 49.896
2021-07-20 | 21:05 | 49.895
2021-07-20 | 21:05 | 49.895
2021-07-20 | 21:05 | 49.894
2021-07-20 | 21:05 | 49.894
2021-07-20 | 21:05 | 49.892
2021-07-20 | 21:05 | 49.892
2021-07-20 | 21:05 | 49.894
2021-07-20 | 21:06 | 49.898
2021-07-20 | 21:06 | 49.903
2021-07-20 | 21:06 | 49.909
2021-07-20 | 21:06 | 49.912
2021-07-20 | 21:06 | 49.916
2021-07-20 | 21:06 | 49.919
2021-07-20 | 21:06 | 49.923
2021-07-20 | 21:06 | 49.926
2021-07-20 | 21:06 | 49.928
2021-07-20 | 21:06 | 49.927
2021-07-20 | 21:06 | 49.928
2021-07-20 | 21:06 | 49.928
2021-07-20 | 21:06 | 49.929
2021-07-20 | 21:06 | 49.932
2021-07-20 | 21:06 | 49.933
2021-07-20 | 21:06 | 49.932
2021-07-20 | 21:06 | 49.931
2021-07-20 | 21:06 | 49.931
2021-07-20 | 21:06 | 49.927
2021-07-20 | 21:06 | 49.926
2021-07-20 | 21:06 | 49.924
2021-07-20 | 21:06 | 49.921
2021-07-20 | 21:06 | 49.918
2021-07-20 | 21:06 | 49.916
2021-07-20 | 21:06 | 49.915
2021-07-20 | 21:06 | 49.916
2021-07-20 | 21:06 | 49.917
2021-07-20 | 21:06 | 49.919
2021-07-20 | 21:06 | 49.922
2021-07-20 | 21:06 | 49.927
2021-07-20 | 21:06 | 49.931
2021-07-20 | 21:06 | 49.934
2021-07-20 | 21:06 | 49.936
2021-07-20 | 21:06 | 49.934
2021-07-20 | 21:06 | 49.934
2021-07-20 | 21:06 | 49.932
2021-07-20 | 21:06 | 49.928
2021-07-20 | 21:06 | 49.925
2021-07-20 | 21:06 | 49.92
2021-07-20 | 21:06 | 49.917
2021-07-20 | 21:06 | 49.914
2021-07-20 | 21:06 | 49.912
2021-07-20 | 21:06 | 49.907
2021-07-20 | 21:06 | 49.906
2021-07-20 | 21:06 | 49.904
2021-07-20 | 21:06 | 49.904
2021-07-20 | 21:06 | 49.902
2021-07-20 | 21:06 | 49.898
2021-07-20 | 21:06 | 49.896
2021-07-20 | 21:06 | 49.894
2021-07-20 | 21:06 | 49.895
2021-07-20 | 21:06 | 49.896
2021-07-20 | 21:06 | 49.897
2021-07-20 | 21:06 | 49.899
2021-07-20 | 21:06 | 49.901
2021-07-20 | 21:06 | 49.9
2021-07-20 | 21:06 | 49.899
2021-07-20 | 21:06 | 49.898
2021-07-20 | 21:06 | 49.897
2021-07-20 | 21:06 | 49.897
2021-07-20 | 21:06 | 49.896
2021-07-20 | 21:07 | 49.897
2021-07-20 | 21:07 | 49.899
2021-07-20 | 21:07 | 49.903
2021-07-20 | 21:07 | 49.904
2021-07-20 | 21:07 | 49.907
2021-07-20 | 21:07 | 49.911
2021-07-20 | 21:07 | 49.914
2021-07-20 | 21:07 | 49.92
2021-07-20 | 21:07 | 49.926
2021-07-20 | 21:07 | 49.931
2021-07-20 | 21:07 | 49.935
2021-07-20 | 21:07 | 49.937
2021-07-20 | 21:07 | 49.937
2021-07-20 | 21:07 | 49.938
2021-07-20 | 21:07 | 49.94
2021-07-20 | 21:07 | 49.939
2021-07-20 | 21:07 | 49.939
2021-07-20 | 21:07 | 49.936
2021-07-20 | 21:07 | 49.934
2021-07-20 | 21:07 | 49.931
2021-07-20 | 21:07 | 49.929
2021-07-20 | 21:07 | 49.927
2021-07-20 | 21:07 | 49.925
2021-07-20 | 21:07 | 49.922
2021-07-20 | 21:07 | 49.921
2021-07-20 | 21:07 | 49.921
2021-07-20 | 21:07 | 49.92
2021-07-20 | 21:07 | 49.92
2021-07-20 | 21:07 | 49.919
2021-07-20 | 21:07 | 49.918
2021-07-20 | 21:07 | 49.919
2021-07-20 | 21:07 | 49.919
2021-07-20 | 21:07 | 49.917
2021-07-20 | 21:07 | 49.916
2021-07-20 | 21:07 | 49.914
2021-07-20 | 21:07 | 49.914
2021-07-20 | 21:07 | 49.911
2021-07-20 | 21:07 | 49.91
2021-07-20 | 21:07 | 49.909
2021-07-20 | 21:07 | 49.908
2021-07-20 | 21:07 | 49.907
2021-07-20 | 21:07 | 49.906
2021-07-20 | 21:07 | 49.906
2021-07-20 | 21:07 | 49.906
2021-07-20 | 21:07 | 49.91
2021-07-20 | 21:07 | 49.914
2021-07-20 | 21:07 | 49.918
2021-07-20 | 21:07 | 49.921
2021-07-20 | 21:07 | 49.921
2021-07-20 | 21:07 | 49.922
2021-07-20 | 21:07 | 49.921
2021-07-20 | 21:07 | 49.922
2021-07-20 | 21:07 | 49.922
2021-07-20 | 21:07 | 49.919
2021-07-20 | 21:07 | 49.917
2021-07-20 | 21:07 | 49.913
2021-07-20 | 21:07 | 49.913
2021-07-20 | 21:07 | 49.913
2021-07-20 | 21:07 | 49.916
2021-07-20 | 21:08 | 49.919
2021-07-20 | 21:08 | 49.923
2021-07-20 | 21:08 | 49.924
2021-07-20 | 21:08 | 49.924
2021-07-20 | 21:08 | 49.925
2021-07-20 | 21:08 | 49.926
2021-07-20 | 21:08 | 49.927
2021-07-20 | 21:08 | 49.928
2021-07-20 | 21:08 | 49.927
2021-07-20 | 21:08 | 49.926
2021-07-20 | 21:08 | 49.924
2021-07-20 | 21:08 | 49.922
2021-07-20 | 21:08 | 49.924
2021-07-20 | 21:08 | 49.923
2021-07-20 | 21:08 | 49.925
2021-07-20 | 21:08 | 49.926
2021-07-20 | 21:08 | 49.927
2021-07-20 | 21:08 | 49.93
2021-07-20 | 21:08 | 49.935
2021-07-20 | 21:08 | 49.937
2021-07-20 | 21:08 | 49.938
2021-07-20 | 21:08 | 49.939
2021-07-20 | 21:08 | 49.94
2021-07-20 | 21:08 | 49.94
2021-07-20 | 21:08 | 49.94
2021-07-20 | 21:08 | 49.937
2021-07-20 | 21:08 | 49.935
2021-07-20 | 21:08 | 49.933
2021-07-20 | 21:08 | 49.934
2021-07-20 | 21:08 | 49.932
2021-07-20 | 21:08 | 49.93
2021-07-20 | 21:08 | 49.929
2021-07-20 | 21:08 | 49.93
2021-07-20 | 21:08 | 49.93
2021-07-20 | 21:08 | 49.932
2021-07-20 | 21:08 | 49.934
2021-07-20 | 21:08 | 49.933
2021-07-20 | 21:08 | 49.936
2021-07-20 | 21:08 | 49.937
2021-07-20 | 21:08 | 49.938
2021-07-20 | 21:08 | 49.939
2021-07-20 | 21:08 | 49.939
2021-07-20 | 21:08 | 49.936
2021-07-20 | 21:08 | 49.936
2021-07-20 | 21:08 | 49.933
2021-07-20 | 21:08 | 49.931
2021-07-20 | 21:08 | 49.932
2021-07-20 | 21:08 | 49.929
2021-07-20 | 21:08 | 49.929
2021-07-20 | 21:08 | 49.927
2021-07-20 | 21:08 | 49.925
2021-07-20 | 21:08 | 49.923
2021-07-20 | 21:08 | 49.925
2021-07-20 | 21:08 | 49.925
2021-07-20 | 21:08 | 49.927
2021-07-20 | 21:08 | 49.928
2021-07-20 | 21:08 | 49.928
2021-07-20 | 21:08 | 49.928
2021-07-20 | 21:08 | 49.927
2021-07-20 | 21:08 | 49.928
2021-07-20 | 21:08 | 49.926
2021-07-20 | 21:09 | 49.927
2021-07-20 | 21:09 | 49.929
2021-07-20 | 21:09 | 49.929
2021-07-20 | 21:09 | 49.929
2021-07-20 | 21:09 | 49.93
2021-07-20 | 21:09 | 49.932
2021-07-20 | 21:09 | 49.938
2021-07-20 | 21:09 | 49.94
2021-07-20 | 21:09 | 49.942
2021-07-20 | 21:09 | 49.944
2021-07-20 | 21:09 | 49.945
2021-07-20 | 21:09 | 49.943
2021-07-20 | 21:09 | 49.944
2021-07-20 | 21:09 | 49.942
2021-07-20 | 21:09 | 49.943
2021-07-20 | 21:09 | 49.944
2021-07-20 | 21:09 | 49.948
2021-07-20 | 21:09 | 49.952
2021-07-20 | 21:09 | 49.955
2021-07-20 | 21:09 | 49.956
2021-07-20 | 21:09 | 49.956
2021-07-20 | 21:09 | 49.959
2021-07-20 | 21:09 | 49.96
2021-07-20 | 21:09 | 49.96
2021-07-20 | 21:09 | 49.962
2021-07-20 | 21:09 | 49.962
2021-07-20 | 21:09 | 49.963
2021-07-20 | 21:09 | 49.963
2021-07-20 | 21:09 | 49.965
2021-07-20 | 21:09 | 49.966
2021-07-20 | 21:09 | 49.966
2021-07-20 | 21:09 | 49.965
2021-07-20 | 21:09 | 49.966
2021-07-20 | 21:09 | 49.966
2021-07-20 | 21:09 | 49.962
2021-07-20 | 21:09 | 49.961
2021-07-20 | 21:09 | 49.958
2021-07-20 | 21:09 | 49.957
2021-07-20 | 21:09 | 49.952
2021-07-20 | 21:09 | 49.947
2021-07-20 | 21:09 | 49.942
2021-07-20 | 21:09 | 49.938
2021-07-20 | 21:09 | 49.931
2021-07-20 | 21:09 | 49.927
2021-07-20 | 21:09 | 49.926
2021-07-20 | 21:09 | 49.926
2021-07-20 | 21:09 | 49.928
2021-07-20 | 21:09 | 49.928
2021-07-20 | 21:09 | 49.928
2021-07-20 | 21:09 | 49.929
2021-07-20 | 21:09 | 49.929
2021-07-20 | 21:09 | 49.928
2021-07-20 | 21:09 | 49.928
2021-07-20 | 21:09 | 49.927
2021-07-20 | 21:09 | 49.929
2021-07-20 | 21:09 | 49.929
2021-07-20 | 21:09 | 49.932
2021-07-20 | 21:09 | 49.933
2021-07-20 | 21:09 | 49.936
2021-07-20 | 21:10 | 49.944
2021-07-20 | 21:10 | 49.95
2021-07-20 | 21:10 | 49.957
2021-07-20 | 21:10 | 49.963
2021-07-20 | 21:10 | 49.967
2021-07-20 | 21:10 | 49.97
2021-07-20 | 21:10 | 49.972
2021-07-20 | 21:10 | 49.971
2021-07-20 | 21:10 | 49.967
2021-07-20 | 21:10 | 49.964
2021-07-20 | 21:10 | 49.962
2021-07-20 | 21:10 | 49.962
2021-07-20 | 21:10 | 49.967
2021-07-20 | 21:10 | 49.97
2021-07-20 | 21:10 | 49.975
2021-07-20 | 21:10 | 49.981
2021-07-20 | 21:10 | 49.985
2021-07-20 | 21:10 | 49.987
2021-07-20 | 21:10 | 49.988
2021-07-20 | 21:10 | 49.988
2021-07-20 | 21:10 | 49.985
2021-07-20 | 21:10 | 49.983
2021-07-20 | 21:10 | 49.98
2021-07-20 | 21:10 | 49.976
2021-07-20 | 21:10 | 49.972
2021-07-20 | 21:10 | 49.962
2021-07-20 | 21:10 | 49.954
2021-07-20 | 21:10 | 49.951
2021-07-20 | 21:10 | 49.949
2021-07-20 | 21:10 | 49.948
2021-07-20 | 21:10 | 49.945
2021-07-20 | 21:10 | 49.943
2021-07-20 | 21:10 | 49.939
2021-07-20 | 21:10 | 49.938
2021-07-20 | 21:10 | 49.937
2021-07-20 | 21:10 | 49.936
2021-07-20 | 21:10 | 49.934
2021-07-20 | 21:10 | 49.931
2021-07-20 | 21:10 | 49.927
2021-07-20 | 21:10 | 49.925
2021-07-20 | 21:10 | 49.92
2021-07-20 | 21:10 | 49.917
2021-07-20 | 21:10 | 49.915
2021-07-20 | 21:10 | 49.915
2021-07-20 | 21:10 | 49.914
2021-07-20 | 21:10 | 49.913
2021-07-20 | 21:10 | 49.914
2021-07-20 | 21:10 | 49.915
2021-07-20 | 21:10 | 49.914
2021-07-20 | 21:10 | 49.912
2021-07-20 | 21:10 | 49.912
2021-07-20 | 21:10 | 49.91
2021-07-20 | 21:10 | 49.908
2021-07-20 | 21:10 | 49.908
2021-07-20 | 21:10 | 49.906
2021-07-20 | 21:10 | 49.903
2021-07-20 | 21:10 | 49.902
2021-07-20 | 21:10 | 49.899
2021-07-20 | 21:10 | 49.899
2021-07-20 | 21:10 | 49.897
2021-07-20 | 21:10 | 49.896
2021-07-20 | 21:11 | 49.898
2021-07-20 | 21:11 | 49.9
2021-07-20 | 21:11 | 49.901
2021-07-20 | 21:11 | 49.903
2021-07-20 | 21:11 | 49.904
2021-07-20 | 21:11 | 49.906
2021-07-20 | 21:11 | 49.91
2021-07-20 | 21:11 | 49.91
2021-07-20 | 21:11 | 49.91
2021-07-20 | 21:11 | 49.91
2021-07-20 | 21:11 | 49.911
2021-07-20 | 21:11 | 49.911
2021-07-20 | 21:11 | 49.91
2021-07-20 | 21:11 | 49.908
2021-07-20 | 21:11 | 49.907
2021-07-20 | 21:11 | 49.907
2021-07-20 | 21:11 | 49.907
2021-07-20 | 21:11 | 49.904
2021-07-20 | 21:11 | 49.904
2021-07-20 | 21:11 | 49.903
2021-07-20 | 21:11 | 49.905
2021-07-20 | 21:11 | 49.907
2021-07-20 | 21:11 | 49.907
2021-07-20 | 21:11 | 49.907
2021-07-20 | 21:11 | 49.908
2021-07-20 | 21:11 | 49.906
2021-07-20 | 21:11 | 49.906
2021-07-20 | 21:11 | 49.906
2021-07-20 | 21:11 | 49.908
2021-07-20 | 21:11 | 49.909
2021-07-20 | 21:11 | 49.909
2021-07-20 | 21:11 | 49.908
2021-07-20 | 21:11 | 49.906
2021-07-20 | 21:11 | 49.903
2021-07-20 | 21:11 | 49.901
2021-07-20 | 21:11 | 49.9
2021-07-20 | 21:11 | 49.9
2021-07-20 | 21:11 | 49.9
2021-07-20 | 21:11 | 49.903
2021-07-20 | 21:11 | 49.903
2021-07-20 | 21:11 | 49.907
2021-07-20 | 21:11 | 49.909
2021-07-20 | 21:11 | 49.911
2021-07-20 | 21:11 | 49.911
2021-07-20 | 21:11 | 49.911
2021-07-20 | 21:11 | 49.914
2021-07-20 | 21:11 | 49.914
2021-07-20 | 21:11 | 49.916
2021-07-20 | 21:11 | 49.918
2021-07-20 | 21:11 | 49.92
2021-07-20 | 21:11 | 49.922
2021-07-20 | 21:11 | 49.927
2021-07-20 | 21:11 | 49.93
2021-07-20 | 21:11 | 49.933
2021-07-20 | 21:11 | 49.935
2021-07-20 | 21:11 | 49.935
2021-07-20 | 21:11 | 49.935
2021-07-20 | 21:11 | 49.934
2021-07-20 | 21:11 | 49.932
2021-07-20 | 21:12 | 49.926
2021-07-20 | 21:12 | 49.92
2021-07-20 | 21:12 | 49.916
2021-07-20 | 21:12 | 49.912
2021-07-20 | 21:12 | 49.91
2021-07-20 | 21:12 | 49.909
2021-07-20 | 21:12 | 49.911
2021-07-20 | 21:12 | 49.913
2021-07-20 | 21:12 | 49.914
2021-07-20 | 21:12 | 49.913
2021-07-20 | 21:12 | 49.92
2021-07-20 | 21:12 | 49.914
2021-07-20 | 21:12 | 49.91
2021-07-20 | 21:12 | 49.91
2021-07-20 | 21:12 | 49.907
2021-07-20 | 21:12 | 49.908
2021-07-20 | 21:12 | 49.909
2021-07-20 | 21:12 | 49.91
2021-07-20 | 21:12 | 49.913
2021-07-20 | 21:12 | 49.913
2021-07-20 | 21:12 | 49.913
2021-07-20 | 21:12 | 49.913
2021-07-20 | 21:12 | 49.91
2021-07-20 | 21:12 | 49.91
2021-07-20 | 21:12 | 49.908
2021-07-20 | 21:12 | 49.903
2021-07-20 | 21:12 | 49.901
2021-07-20 | 21:12 | 49.898
2021-07-20 | 21:12 | 49.893
2021-07-20 | 21:12 | 49.893
2021-07-20 | 21:12 | 49.893
2021-07-20 | 21:12 | 49.895
2021-07-20 | 21:12 | 49.898
2021-07-20 | 21:12 | 49.905
2021-07-20 | 21:12 | 49.907
2021-07-20 | 21:12 | 49.916
2021-07-20 | 21:12 | 49.921
2021-07-20 | 21:12 | 49.927
2021-07-20 | 21:12 | 49.93
2021-07-20 | 21:12 | 49.931
2021-07-20 | 21:12 | 49.93
2021-07-20 | 21:12 | 49.928
2021-07-20 | 21:12 | 49.923
2021-07-20 | 21:12 | 49.918
2021-07-20 | 21:12 | 49.915
2021-07-20 | 21:12 | 49.915
2021-07-20 | 21:12 | 49.913
2021-07-20 | 21:12 | 49.911
2021-07-20 | 21:12 | 49.912
2021-07-20 | 21:12 | 49.911
2021-07-20 | 21:12 | 49.914
2021-07-20 | 21:12 | 49.915
2021-07-20 | 21:12 | 49.915
2021-07-20 | 21:12 | 49.913
2021-07-20 | 21:12 | 49.911
2021-07-20 | 21:12 | 49.91
2021-07-20 | 21:12 | 49.91
2021-07-20 | 21:12 | 49.909
2021-07-20 | 21:12 | 49.912
2021-07-20 | 21:12 | 49.911
2021-07-20 | 21:12 | 49.911
2021-07-20 | 21:13 | 49.911
2021-07-20 | 21:13 | 49.909
2021-07-20 | 21:13 | 49.912
2021-07-20 | 21:13 | 49.913
2021-07-20 | 21:13 | 49.917
2021-07-20 | 21:13 | 49.919
2021-07-20 | 21:13 | 49.921
2021-07-20 | 21:13 | 49.925
2021-07-20 | 21:13 | 49.928
2021-07-20 | 21:13 | 49.93
2021-07-20 | 21:13 | 49.934
2021-07-20 | 21:13 | 49.936
2021-07-20 | 21:13 | 49.941
2021-07-20 | 21:13 | 49.944
2021-07-20 | 21:13 | 49.949
2021-07-20 | 21:13 | 49.954
2021-07-20 | 21:13 | 49.959
2021-07-20 | 21:13 | 49.963
2021-07-20 | 21:13 | 49.966
2021-07-20 | 21:13 | 49.968
2021-07-20 | 21:13 | 49.967
2021-07-20 | 21:13 | 49.967
2021-07-20 | 21:13 | 49.964
2021-07-20 | 21:13 | 49.962
2021-07-20 | 21:13 | 49.96
2021-07-20 | 21:13 | 49.96
2021-07-20 | 21:13 | 49.957
2021-07-20 | 21:13 | 49.956
2021-07-20 | 21:13 | 49.955
2021-07-20 | 21:13 | 49.951
2021-07-20 | 21:13 | 49.948
2021-07-20 | 21:13 | 49.945
2021-07-20 | 21:13 | 49.942
2021-07-20 | 21:13 | 49.945
2021-07-20 | 21:13 | 49.946
2021-07-20 | 21:13 | 49.947
2021-07-20 | 21:13 | 49.95
2021-07-20 | 21:13 | 49.949
2021-07-20 | 21:13 | 49.949
2021-07-20 | 21:13 | 49.95
2021-07-20 | 21:13 | 49.951
2021-07-20 | 21:13 | 49.952
2021-07-20 | 21:13 | 49.95
2021-07-20 | 21:13 | 49.95
2021-07-20 | 21:13 | 49.951
2021-07-20 | 21:13 | 49.951
2021-07-20 | 21:13 | 49.95
2021-07-20 | 21:13 | 49.95
2021-07-20 | 21:13 | 49.954
2021-07-20 | 21:13 | 49.953
2021-07-20 | 21:13 | 49.956
2021-07-20 | 21:13 | 49.954
2021-07-20 | 21:13 | 49.953
2021-07-20 | 21:13 | 49.95
2021-07-20 | 21:13 | 49.948
2021-07-20 | 21:13 | 49.945
2021-07-20 | 21:13 | 49.942
2021-07-20 | 21:13 | 49.939
2021-07-20 | 21:13 | 49.937
2021-07-20 | 21:14 | 49.934
2021-07-20 | 21:14 | 49.931
2021-07-20 | 21:14 | 49.932
2021-07-20 | 21:14 | 49.932
2021-07-20 | 21:14 | 49.931
2021-07-20 | 21:14 | 49.929
2021-07-20 | 21:14 | 49.926
2021-07-20 | 21:14 | 49.923
2021-07-20 | 21:14 | 49.922
2021-07-20 | 21:14 | 49.922
2021-07-20 | 21:14 | 49.921
2021-07-20 | 21:14 | 49.923
2021-07-20 | 21:14 | 49.923
2021-07-20 | 21:14 | 49.924
2021-07-20 | 21:14 | 49.924
2021-07-20 | 21:14 | 49.925
2021-07-20 | 21:14 | 49.927
2021-07-20 | 21:14 | 49.927
2021-07-20 | 21:14 | 49.927
2021-07-20 | 21:14 | 49.926
2021-07-20 | 21:14 | 49.927
2021-07-20 | 21:14 | 49.929
2021-07-20 | 21:14 | 49.928
2021-07-20 | 21:14 | 49.928
2021-07-20 | 21:14 | 49.928
2021-07-20 | 21:14 | 49.926
2021-07-20 | 21:14 | 49.925
2021-07-20 | 21:14 | 49.922
2021-07-20 | 21:14 | 49.92
2021-07-20 | 21:14 | 49.916
2021-07-20 | 21:14 | 49.916
2021-07-20 | 21:14 | 49.914
2021-07-20 | 21:14 | 49.913
2021-07-20 | 21:14 | 49.915
2021-07-20 | 21:14 | 49.917
2021-07-20 | 21:14 | 49.92
2021-07-20 | 21:14 | 49.924
2021-07-20 | 21:14 | 49.928
2021-07-20 | 21:14 | 49.933
2021-07-20 | 21:14 | 49.939
2021-07-20 | 21:14 | 49.942
2021-07-20 | 21:14 | 49.945
2021-07-20 | 21:14 | 49.948
2021-07-20 | 21:14 | 49.948
2021-07-20 | 21:14 | 49.948
2021-07-20 | 21:14 | 49.948
2021-07-20 | 21:14 | 49.948
2021-07-20 | 21:14 | 49.948
2021-07-20 | 21:14 | 49.947
2021-07-20 | 21:14 | 49.945
2021-07-20 | 21:14 | 49.945
2021-07-20 | 21:14 | 49.943
2021-07-20 | 21:14 | 49.942
2021-07-20 | 21:14 | 49.942
2021-07-20 | 21:14 | 49.942
2021-07-20 | 21:14 | 49.941
2021-07-20 | 21:14 | 49.94
2021-07-20 | 21:14 | 49.941
2021-07-20 | 21:14 | 49.942
2021-07-20 | 21:14 | 49.942
2021-07-20 | 21:14 | 49.941
2021-07-20 | 21:15 | 49.941
2021-07-20 | 21:15 | 49.944
2021-07-20 | 21:15 | 49.947
2021-07-20 | 21:15 | 49.949
2021-07-20 | 21:15 | 49.948
2021-07-20 | 21:15 | 49.948
2021-07-20 | 21:15 | 49.949
2021-07-20 | 21:15 | 49.949
2021-07-20 | 21:15 | 49.95
2021-07-20 | 21:15 | 49.95
2021-07-20 | 21:15 | 49.95
2021-07-20 | 21:15 | 49.949
2021-07-20 | 21:15 | 49.948
2021-07-20 | 21:15 | 49.947
2021-07-20 | 21:15 | 49.949
2021-07-20 | 21:15 | 49.948
2021-07-20 | 21:15 | 49.949
2021-07-20 | 21:15 | 49.948
2021-07-20 | 21:15 | 49.948
2021-07-20 | 21:15 | 49.95
2021-07-20 | 21:15 | 49.953
2021-07-20 | 21:15 | 49.957
2021-07-20 | 21:15 | 49.961
2021-07-20 | 21:15 | 49.96
2021-07-20 | 21:15 | 49.964
2021-07-20 | 21:15 | 49.964
2021-07-20 | 21:15 | 49.966
2021-07-20 | 21:15 | 49.966
2021-07-20 | 21:15 | 49.964
2021-07-20 | 21:15 | 49.963
2021-07-20 | 21:15 | 49.96
2021-07-20 | 21:15 | 49.959
2021-07-20 | 21:15 | 49.961
2021-07-20 | 21:15 | 49.963
2021-07-20 | 21:15 | 49.966
2021-07-20 | 21:15 | 49.968
2021-07-20 | 21:15 | 49.971
2021-07-20 | 21:15 | 49.974
2021-07-20 | 21:15 | 49.975
2021-07-20 | 21:15 | 49.977
2021-07-20 | 21:15 | 49.977
2021-07-20 | 21:15 | 49.979
2021-07-20 | 21:15 | 49.975
2021-07-20 | 21:15 | 49.971
2021-07-20 | 21:15 | 49.968
2021-07-20 | 21:15 | 49.965
2021-07-20 | 21:15 | 49.962
2021-07-20 | 21:15 | 49.961
2021-07-20 | 21:15 | 49.962
2021-07-20 | 21:15 | 49.965
2021-07-20 | 21:15 | 49.967
2021-07-20 | 21:15 | 49.969
2021-07-20 | 21:15 | 49.969
2021-07-20 | 21:15 | 49.969
2021-07-20 | 21:15 | 49.969
2021-07-20 | 21:15 | 49.967
2021-07-20 | 21:15 | 49.971
2021-07-20 | 21:15 | 49.973
2021-07-20 | 21:15 | 49.974
2021-07-20 | 21:16 | 49.972
2021-07-20 | 21:16 | 49.971
2021-07-20 | 21:16 | 49.97
2021-07-20 | 21:16 | 49.97
2021-07-20 | 21:16 | 49.97
2021-07-20 | 21:16 | 49.972
2021-07-20 | 21:16 | 49.972
2021-07-20 | 21:16 | 49.969
2021-07-20 | 21:16 | 49.967
2021-07-20 | 21:16 | 49.968
2021-07-20 | 21:16 | 49.967
2021-07-20 | 21:16 | 49.967
2021-07-20 | 21:16 | 49.966
2021-07-20 | 21:16 | 49.966
2021-07-20 | 21:16 | 49.967
2021-07-20 | 21:16 | 49.968
2021-07-20 | 21:16 | 49.968
2021-07-20 | 21:16 | 49.968
2021-07-20 | 21:16 | 49.967
2021-07-20 | 21:16 | 49.97
2021-07-20 | 21:16 | 49.97
2021-07-20 | 21:16 | 49.971
2021-07-20 | 21:16 | 49.97
2021-07-20 | 21:16 | 49.972
2021-07-20 | 21:16 | 49.971
2021-07-20 | 21:16 | 49.971
2021-07-20 | 21:16 | 49.967
2021-07-20 | 21:16 | 49.964
2021-07-20 | 21:16 | 49.96
2021-07-20 | 21:16 | 49.959
2021-07-20 | 21:16 | 49.956
2021-07-20 | 21:16 | 49.957
2021-07-20 | 21:16 | 49.957
2021-07-20 | 21:16 | 49.959
2021-07-20 | 21:16 | 49.959
2021-07-20 | 21:16 | 49.96
2021-07-20 | 21:16 | 49.959
2021-07-20 | 21:16 | 49.96
2021-07-20 | 21:16 | 49.96
2021-07-20 | 21:16 | 49.964
2021-07-20 | 21:16 | 49.965
2021-07-20 | 21:16 | 49.967
2021-07-20 | 21:16 | 49.969
2021-07-20 | 21:16 | 49.971
2021-07-20 | 21:16 | 49.971
2021-07-20 | 21:16 | 49.968
2021-07-20 | 21:16 | 49.965
2021-07-20 | 21:16 | 49.963
2021-07-20 | 21:16 | 49.959
2021-07-20 | 21:16 | 49.956
2021-07-20 | 21:16 | 49.95
2021-07-20 | 21:16 | 49.948
2021-07-20 | 21:16 | 49.943
2021-07-20 | 21:16 | 49.939
2021-07-20 | 21:16 | 49.939
2021-07-20 | 21:16 | 49.939
2021-07-20 | 21:16 | 49.94
2021-07-20 | 21:16 | 49.944
2021-07-20 | 21:16 | 49.945
2021-07-20 | 21:16 | 49.947
2021-07-20 | 21:16 | 49.95
2021-07-20 | 21:17 | 49.954
2021-07-20 | 21:17 | 49.955
2021-07-20 | 21:17 | 49.958
2021-07-20 | 21:17 | 49.96
2021-07-20 | 21:17 | 49.96
2021-07-20 | 21:17 | 49.958
2021-07-20 | 21:17 | 49.957
2021-07-20 | 21:17 | 49.955
2021-07-20 | 21:17 | 49.954
2021-07-20 | 21:17 | 49.953
2021-07-20 | 21:17 | 49.952
2021-07-20 | 21:17 | 49.951
2021-07-20 | 21:17 | 49.951
2021-07-20 | 21:17 | 49.949
2021-07-20 | 21:17 | 49.951
2021-07-20 | 21:17 | 49.952
2021-07-20 | 21:17 | 49.952
2021-07-20 | 21:17 | 49.955
2021-07-20 | 21:17 | 49.957
2021-07-20 | 21:17 | 49.959
2021-07-20 | 21:17 | 49.961
2021-07-20 | 21:17 | 49.961
2021-07-20 | 21:17 | 49.961
2021-07-20 | 21:17 | 49.96
2021-07-20 | 21:17 | 49.96
2021-07-20 | 21:17 | 49.96
2021-07-20 | 21:17 | 49.961
2021-07-20 | 21:17 | 49.962
2021-07-20 | 21:17 | 49.963
2021-07-20 | 21:17 | 49.964
2021-07-20 | 21:17 | 49.964
2021-07-20 | 21:17 | 49.961
2021-07-20 | 21:17 | 49.959
2021-07-20 | 21:17 | 49.959
2021-07-20 | 21:17 | 49.96
2021-07-20 | 21:17 | 49.96
2021-07-20 | 21:17 | 49.961
2021-07-20 | 21:17 | 49.961
2021-07-20 | 21:17 | 49.965
2021-07-20 | 21:17 | 49.968
2021-07-20 | 21:17 | 49.972
2021-07-20 | 21:17 | 49.974
2021-07-20 | 21:17 | 49.975
2021-07-20 | 21:17 | 49.975
2021-07-20 | 21:17 | 49.975
2021-07-20 | 21:17 | 49.977
2021-07-20 | 21:17 | 49.979
2021-07-20 | 21:17 | 49.981
2021-07-20 | 21:17 | 49.982
2021-07-20 | 21:17 | 49.981
2021-07-20 | 21:17 | 49.981
2021-07-20 | 21:17 | 49.982
2021-07-20 | 21:17 | 49.983
2021-07-20 | 21:17 | 49.982
2021-07-20 | 21:17 | 49.981
2021-07-20 | 21:17 | 49.979
2021-07-20 | 21:17 | 49.974
2021-07-20 | 21:17 | 49.968
2021-07-20 | 21:17 | 49.965
2021-07-20 | 21:18 | 49.962
2021-07-20 | 21:18 | 49.963
2021-07-20 | 21:18 | 49.964
2021-07-20 | 21:18 | 49.967
2021-07-20 | 21:18 | 49.969
2021-07-20 | 21:18 | 49.972
2021-07-20 | 21:18 | 49.974
2021-07-20 | 21:18 | 49.976
2021-07-20 | 21:18 | 49.977
2021-07-20 | 21:18 | 49.978
2021-07-20 | 21:18 | 49.978
2021-07-20 | 21:18 | 49.981
2021-07-20 | 21:18 | 49.981
2021-07-20 | 21:18 | 49.981
2021-07-20 | 21:18 | 49.979
2021-07-20 | 21:18 | 49.979
2021-07-20 | 21:18 | 49.981
2021-07-20 | 21:18 | 49.982
2021-07-20 | 21:18 | 49.983
2021-07-20 | 21:18 | 49.985
2021-07-20 | 21:18 | 49.989
2021-07-20 | 21:18 | 49.99
2021-07-20 | 21:18 | 49.989
2021-07-20 | 21:18 | 49.989
2021-07-20 | 21:18 | 49.987
2021-07-20 | 21:18 | 49.988
2021-07-20 | 21:18 | 49.989
2021-07-20 | 21:18 | 49.991
2021-07-20 | 21:18 | 49.992
2021-07-20 | 21:18 | 49.994
2021-07-20 | 21:18 | 49.994
2021-07-20 | 21:18 | 49.993
2021-07-20 | 21:18 | 49.994
2021-07-20 | 21:18 | 49.997
2021-07-20 | 21:18 | 49.997
2021-07-20 | 21:18 | 50.001
2021-07-20 | 21:18 | 50.003
2021-07-20 | 21:18 | 50.005
2021-07-20 | 21:18 | 50.009
2021-07-20 | 21:18 | 50.012
2021-07-20 | 21:18 | 50.014
2021-07-20 | 21:18 | 50.015
2021-07-20 | 21:18 | 50.018
2021-07-20 | 21:18 | 50.021
2021-07-20 | 21:18 | 50.022
2021-07-20 | 21:18 | 50.023
2021-07-20 | 21:18 | 50.024
2021-07-20 | 21:18 | 50.022
2021-07-20 | 21:18 | 50.021
2021-07-20 | 21:18 | 50.019
2021-07-20 | 21:18 | 50.016
2021-07-20 | 21:18 | 50.013
2021-07-20 | 21:18 | 50.01
2021-07-20 | 21:18 | 50.008
2021-07-20 | 21:18 | 50.007
2021-07-20 | 21:18 | 50.008
2021-07-20 | 21:18 | 50.008
2021-07-20 | 21:18 | 50.008
2021-07-20 | 21:18 | 50.007
2021-07-20 | 21:18 | 50.005
2021-07-20 | 21:18 | 50.005
2021-07-20 | 21:19 | 50.002
2021-07-20 | 21:19 | 50.002
2021-07-20 | 21:19 | 50
2021-07-20 | 21:19 | 49.999
2021-07-20 | 21:19 | 49.997
2021-07-20 | 21:19 | 49.996
2021-07-20 | 21:19 | 49.994
2021-07-20 | 21:19 | 49.993
2021-07-20 | 21:19 | 49.992
2021-07-20 | 21:19 | 49.993
2021-07-20 | 21:19 | 49.993
2021-07-20 | 21:19 | 49.993
2021-07-20 | 21:19 | 49.994
2021-07-20 | 21:19 | 49.996
2021-07-20 | 21:19 | 49.996
2021-07-20 | 21:19 | 49.997
2021-07-20 | 21:19 | 49.998
2021-07-20 | 21:19 | 49.998
2021-07-20 | 21:19 | 49.998
2021-07-20 | 21:19 | 49.999
2021-07-20 | 21:19 | 50.001
2021-07-20 | 21:19 | 50.003
2021-07-20 | 21:19 | 50.004
2021-07-20 | 21:19 | 50.006
2021-07-20 | 21:19 | 50.008
2021-07-20 | 21:19 | 50.007
2021-07-20 | 21:19 | 50.006
2021-07-20 | 21:19 | 50.008
2021-07-20 | 21:19 | 50.006

## 20220418-1
In GMT
Date | Time | Freq
2022-04-18 | 16:20 | 49.961
2022-04-18 | 16:20 | 49.961
2022-04-18 | 16:20 | 49.96
2022-04-18 | 16:20 | 49.96
2022-04-18 | 16:20 | 49.958
2022-04-18 | 16:20 | 49.959
2022-04-18 | 16:20 | 49.958
2022-04-18 | 16:20 | 49.959
2022-04-18 | 16:20 | 49.96
2022-04-18 | 16:20 | 49.962
2022-04-18 | 16:20 | 49.963
2022-04-18 | 16:20 | 49.963
2022-04-18 | 16:20 | 49.966
2022-04-18 | 16:20 | 49.966
2022-04-18 | 16:20 | 49.966
2022-04-18 | 16:20 | 49.966
2022-04-18 | 16:21 | 49.966
2022-04-18 | 16:21 | 49.968
2022-04-18 | 16:21 | 49.974
2022-04-18 | 16:21 | 49.976
2022-04-18 | 16:21 | 49.98
2022-04-18 | 16:21 | 49.982
2022-04-18 | 16:21 | 49.985
2022-04-18 | 16:21 | 49.988
2022-04-18 | 16:21 | 49.991
2022-04-18 | 16:21 | 49.996
2022-04-18 | 16:21 | 49.999
2022-04-18 | 16:21 | 50.003
2022-04-18 | 16:21 | 50.006
2022-04-18 | 16:21 | 50.013
2022-04-18 | 16:21 | 50.016
2022-04-18 | 16:21 | 50.021
2022-04-18 | 16:21 | 50.023
2022-04-18 | 16:21 | 50.027
2022-04-18 | 16:21 | 50.028
2022-04-18 | 16:21 | 50.033
2022-04-18 | 16:21 | 50.032
2022-04-18 | 16:21 | 50.031
2022-04-18 | 16:21 | 50.031
2022-04-18 | 16:21 | 50.026
2022-04-18 | 16:21 | 50.023
2022-04-18 | 16:21 | 50.02
2022-04-18 | 16:21 | 50.018
2022-04-18 | 16:21 | 50.015
2022-04-18 | 16:21 | 50.014
2022-04-18 | 16:21 | 50.015
2022-04-18 | 16:21 | 50.017
2022-04-18 | 16:21 | 50.018
2022-04-18 | 16:21 | 50.022
2022-04-18 | 16:21 | 50.027
2022-04-18 | 16:21 | 50.027
2022-04-18 | 16:21 | 50.03
2022-04-18 | 16:21 | 50.031
2022-04-18 | 16:21 | 50.035
2022-04-18 | 16:21 | 50.038
2022-04-18 | 16:21 | 50.042
2022-04-18 | 16:21 | 50.045
2022-04-18 | 16:21 | 50.048
2022-04-18 | 16:21 | 50.049
2022-04-18 | 16:21 | 50.048
2022-04-18 | 16:21 | 50.046
2022-04-18 | 16:21 | 50.045
2022-04-18 | 16:21 | 50.044
2022-04-18 | 16:21 | 50.041
2022-04-18 | 16:21 | 50.04
2022-04-18 | 16:21 | 50.036
2022-04-18 | 16:21 | 50.034
2022-04-18 | 16:21 | 50.029
2022-04-18 | 16:21 | 50.026
2022-04-18 | 16:21 | 50.025
2022-04-18 | 16:21 | 50.02
2022-04-18 | 16:21 | 50.021
2022-04-18 | 16:21 | 50.022
2022-04-18 | 16:21 | 50.02
2022-04-18 | 16:21 | 50.018
2022-04-18 | 16:22 | 50.016
2022-04-18 | 16:22 | 50.012
2022-04-18 | 16:22 | 50.012
2022-04-18 | 16:22 | 50.01
2022-04-18 | 16:22 | 50.006
2022-04-18 | 16:22 | 50.008
2022-04-18 | 16:22 | 50.007
2022-04-18 | 16:22 | 50.008
2022-04-18 | 16:22 | 50.008
2022-04-18 | 16:22 | 50.011
2022-04-18 | 16:22 | 50.013
2022-04-18 | 16:22 | 50.014
2022-04-18 | 16:22 | 50.015
2022-04-18 | 16:22 | 50.015
2022-04-18 | 16:22 | 50.016
2022-04-18 | 16:22 | 50.015
2022-04-18 | 16:22 | 50.015
2022-04-18 | 16:22 | 50.018
2022-04-18 | 16:22 | 50.02
2022-04-18 | 16:22 | 50.022
2022-04-18 | 16:22 | 50.023
2022-04-18 | 16:22 | 50.023
2022-04-18 | 16:22 | 50.025
2022-04-18 | 16:22 | 50.024
2022-04-18 | 16:22 | 50.025
2022-04-18 | 16:22 | 50.027
2022-04-18 | 16:22 | 50.028
2022-04-18 | 16:22 | 50.027
2022-04-18 | 16:22 | 50.023
2022-04-18 | 16:22 | 50.018
2022-04-18 | 16:22 | 50.014
2022-04-18 | 16:22 | 50.013
2022-04-18 | 16:22 | 50.01
2022-04-18 | 16:22 | 50.011
2022-04-18 | 16:22 | 50.013
2022-04-18 | 16:22 | 50.014
2022-04-18 | 16:22 | 50.016
2022-04-18 | 16:22 | 50.017
2022-04-18 | 16:22 | 50.018
2022-04-18 | 16:22 | 50.019
2022-04-18 | 16:22 | 50.021
2022-04-18 | 16:22 | 50.025
2022-04-18 | 16:22 | 50.025
2022-04-18 | 16:22 | 50.027
2022-04-18 | 16:22 | 50.023
2022-04-18 | 16:22 | 50.021
2022-04-18 | 16:22 | 50.018
2022-04-18 | 16:22 | 50.017
2022-04-18 | 16:22 | 50.02
2022-04-18 | 16:22 | 50.025
2022-04-18 | 16:22 | 50.028
2022-04-18 | 16:22 | 50.029
2022-04-18 | 16:22 | 50.031
2022-04-18 | 16:22 | 50.032
2022-04-18 | 16:22 | 50.035
2022-04-18 | 16:22 | 50.035
2022-04-18 | 16:22 | 50.036
2022-04-18 | 16:22 | 50.036
2022-04-18 | 16:22 | 50.033
2022-04-18 | 16:22 | 50.035
2022-04-18 | 16:22 | 50.033
2022-04-18 | 16:23 | 50.037
2022-04-18 | 16:23 | 50.035
2022-04-18 | 16:23 | 50.034
2022-04-18 | 16:23 | 50.033
2022-04-18 | 16:23 | 50.031
2022-04-18 | 16:23 | 50.031
2022-04-18 | 16:23 | 50.031
2022-04-18 | 16:23 | 50.033
2022-04-18 | 16:23 | 50.034
2022-04-18 | 16:23 | 50.036
2022-04-18 | 16:23 | 50.037
2022-04-18 | 16:23 | 50.038
2022-04-18 | 16:23 | 50.038
2022-04-18 | 16:23 | 50.037
2022-04-18 | 16:23 | 50.038
2022-04-18 | 16:23 | 50.036
2022-04-18 | 16:23 | 50.036
2022-04-18 | 16:23 | 50.036
2022-04-18 | 16:23 | 50.037
2022-04-18 | 16:23 | 50.039
2022-04-18 | 16:23 | 50.037
2022-04-18 | 16:23 | 50.038
2022-04-18 | 16:23 | 50.035
2022-04-18 | 16:23 | 50.035
2022-04-18 | 16:23 | 50.031
2022-04-18 | 16:23 | 50.032
2022-04-18 | 16:23 | 50.032
2022-04-18 | 16:23 | 50.032
2022-04-18 | 16:23 | 50.031
2022-04-18 | 16:23 | 50.03
2022-04-18 | 16:23 | 50.029
2022-04-18 | 16:23 | 50.027
2022-04-18 | 16:23 | 50.027
2022-04-18 | 16:23 | 50.026
2022-04-18 | 16:23 | 50.028
2022-04-18 | 16:23 | 50.03
2022-04-18 | 16:23 | 50.031
2022-04-18 | 16:23 | 50.035
2022-04-18 | 16:23 | 50.036
2022-04-18 | 16:23 | 50.036
2022-04-18 | 16:23 | 50.037
2022-04-18 | 16:23 | 50.039
2022-04-18 | 16:23 | 50.038
2022-04-18 | 16:23 | 50.036
2022-04-18 | 16:23 | 50.035
2022-04-18 | 16:23 | 50.033
2022-04-18 | 16:23 | 50.03
2022-04-18 | 16:23 | 50.028
2022-04-18 | 16:23 | 50.025
2022-04-18 | 16:23 | 50.023
2022-04-18 | 16:23 | 50.023
2022-04-18 | 16:23 | 50.021
2022-04-18 | 16:23 | 50.019
2022-04-18 | 16:23 | 50.016
2022-04-18 | 16:23 | 50.016
2022-04-18 | 16:23 | 50.015
2022-04-18 | 16:23 | 50.015
2022-04-18 | 16:23 | 50.015
2022-04-18 | 16:23 | 50.016
2022-04-18 | 16:24 | 50.015
2022-04-18 | 16:24 | 50.013
2022-04-18 | 16:24 | 50.012
2022-04-18 | 16:24 | 50.012
2022-04-18 | 16:24 | 50.008
2022-04-18 | 16:24 | 50.008
2022-04-18 | 16:24 | 50.006
2022-04-18 | 16:24 | 50.008
2022-04-18 | 16:24 | 50.008
2022-04-18 | 16:24 | 50.01
2022-04-18 | 16:24 | 50.009
2022-04-18 | 16:24 | 50.009
2022-04-18 | 16:24 | 50.007
2022-04-18 | 16:24 | 50.004
2022-04-18 | 16:24 | 50.004
2022-04-18 | 16:24 | 50.004
2022-04-18 | 16:24 | 50.002
2022-04-18 | 16:24 | 50.003
2022-04-18 | 16:24 | 50.004
2022-04-18 | 16:24 | 50.002
2022-04-18 | 16:24 | 50.003
2022-04-18 | 16:24 | 49.999
2022-04-18 | 16:24 | 49.996
2022-04-18 | 16:24 | 49.992
2022-04-18 | 16:24 | 49.99
2022-04-18 | 16:24 | 49.983
2022-04-18 | 16:24 | 49.977
2022-04-18 | 16:24 | 49.974
2022-04-18 | 16:24 | 49.97
2022-04-18 | 16:24 | 49.97
2022-04-18 | 16:24 | 49.969
2022-04-18 | 16:24 | 49.97
2022-04-18 | 16:24 | 49.97
2022-04-18 | 16:24 | 49.97
2022-04-18 | 16:24 | 49.971
2022-04-18 | 16:24 | 49.97
2022-04-18 | 16:24 | 49.97
2022-04-18 | 16:24 | 49.969
2022-04-18 | 16:24 | 49.967
2022-04-18 | 16:24 | 49.966
2022-04-18 | 16:24 | 49.964
2022-04-18 | 16:24 | 49.961
2022-04-18 | 16:24 | 49.962
2022-04-18 | 16:24 | 49.962
2022-04-18 | 16:24 | 49.965
2022-04-18 | 16:24 | 49.969
2022-04-18 | 16:24 | 49.973
2022-04-18 | 16:24 | 49.976
2022-04-18 | 16:24 | 49.977
2022-04-18 | 16:24 | 49.98
2022-04-18 | 16:24 | 49.983
2022-04-18 | 16:24 | 49.986
2022-04-18 | 16:24 | 49.987
2022-04-18 | 16:24 | 49.988
2022-04-18 | 16:24 | 49.987
2022-04-18 | 16:24 | 49.989
2022-04-18 | 16:24 | 49.992
2022-04-18 | 16:24 | 49.993
2022-04-18 | 16:24 | 49.996
2022-04-18 | 16:24 | 49.998
2022-04-18 | 16:25 | 50.002
2022-04-18 | 16:25 | 50.009
2022-04-18 | 16:25 | 50.016
2022-04-18 | 16:25 | 50.023
2022-04-18 | 16:25 | 50.029
2022-04-18 | 16:25 | 50.035
2022-04-18 | 16:25 | 50.042
2022-04-18 | 16:25 | 50.048
2022-04-18 | 16:25 | 50.054
2022-04-18 | 16:25 | 50.057
2022-04-18 | 16:25 | 50.059
2022-04-18 | 16:25 | 50.059
2022-04-18 | 16:25 | 50.059
2022-04-18 | 16:25 | 50.055
2022-04-18 | 16:25 | 50.051
2022-04-18 | 16:25 | 50.048
2022-04-18 | 16:25 | 50.043
2022-04-18 | 16:25 | 50.04
2022-04-18 | 16:25 | 50.037
2022-04-18 | 16:25 | 50.037
2022-04-18 | 16:25 | 50.036
2022-04-18 | 16:25 | 50.035
2022-04-18 | 16:25 | 50.034
2022-04-18 | 16:25 | 50.031
2022-04-18 | 16:25 | 50.031
2022-04-18 | 16:25 | 50.031
2022-04-18 | 16:25 | 50.03
2022-04-18 | 16:25 | 50.029
2022-04-18 | 16:25 | 50.028
2022-04-18 | 16:25 | 50.028
2022-04-18 | 16:25 | 50.027
2022-04-18 | 16:25 | 50.026
2022-04-18 | 16:25 | 50.026
2022-04-18 | 16:25 | 50.025
2022-04-18 | 16:25 | 50.025
2022-04-18 | 16:25 | 50.025
2022-04-18 | 16:25 | 50.023
2022-04-18 | 16:25 | 49.984
2022-04-18 | 16:25 | 49.877
2022-04-18 | 16:25 | 49.776
2022-04-18 | 16:25 | 49.703
2022-04-18 | 16:25 | 49.663
2022-04-18 | 16:25 | 49.645
2022-04-18 | 16:25 | 49.641
2022-04-18 | 16:25 | 49.644
2022-04-18 | 16:25 | 49.651
2022-04-18 | 16:25 | 49.658
2022-04-18 | 16:25 | 49.663
2022-04-18 | 16:25 | 49.665
2022-04-18 | 16:25 | 49.667
2022-04-18 | 16:25 | 49.666
2022-04-18 | 16:25 | 49.666
2022-04-18 | 16:25 | 49.665
2022-04-18 | 16:25 | 49.663
2022-04-18 | 16:25 | 49.662
2022-04-18 | 16:25 | 49.661
2022-04-18 | 16:25 | 49.662
2022-04-18 | 16:25 | 49.66
2022-04-18 | 16:25 | 49.662
2022-04-18 | 16:25 | 49.664
2022-04-18 | 16:26 | 49.663
2022-04-18 | 16:26 | 49.665
2022-04-18 | 16:26 | 49.667
2022-04-18 | 16:26 | 49.668
2022-04-18 | 16:26 | 49.669
2022-04-18 | 16:26 | 49.671
2022-04-18 | 16:26 | 49.674
2022-04-18 | 16:26 | 49.676
2022-04-18 | 16:26 | 49.677
2022-04-18 | 16:26 | 49.677
2022-04-18 | 16:26 | 49.678
2022-04-18 | 16:26 | 49.677
2022-04-18 | 16:26 | 49.676
2022-04-18 | 16:26 | 49.677
2022-04-18 | 16:26 | 49.675
2022-04-18 | 16:26 | 49.677
2022-04-18 | 16:26 | 49.677
2022-04-18 | 16:26 | 49.676
2022-04-18 | 16:26 | 49.673
2022-04-18 | 16:26 | 49.672
2022-04-18 | 16:26 | 49.671
2022-04-18 | 16:26 | 49.674
2022-04-18 | 16:26 | 49.675
2022-04-18 | 16:26 | 49.679
2022-04-18 | 16:26 | 49.681
2022-04-18 | 16:26 | 49.682
2022-04-18 | 16:26 | 49.684
2022-04-18 | 16:26 | 49.684
2022-04-18 | 16:26 | 49.683
2022-04-18 | 16:26 | 49.682
2022-04-18 | 16:26 | 49.68
2022-04-18 | 16:26 | 49.677
2022-04-18 | 16:26 | 49.673
2022-04-18 | 16:26 | 49.67
2022-04-18 | 16:26 | 49.672
2022-04-18 | 16:26 | 49.678
2022-04-18 | 16:26 | 49.684
2022-04-18 | 16:26 | 49.687
2022-04-18 | 16:26 | 49.689
2022-04-18 | 16:26 | 49.689
2022-04-18 | 16:26 | 49.688
2022-04-18 | 16:26 | 49.688
2022-04-18 | 16:26 | 49.686
2022-04-18 | 16:26 | 49.686
2022-04-18 | 16:26 | 49.686
2022-04-18 | 16:26 | 49.685
2022-04-18 | 16:26 | 49.684
2022-04-18 | 16:26 | 49.681
2022-04-18 | 16:26 | 49.678
2022-04-18 | 16:26 | 49.676
2022-04-18 | 16:26 | 49.675
2022-04-18 | 16:26 | 49.674
2022-04-18 | 16:26 | 49.674
2022-04-18 | 16:26 | 49.674
2022-04-18 | 16:26 | 49.677
2022-04-18 | 16:26 | 49.682
2022-04-18 | 16:26 | 49.685
2022-04-18 | 16:26 | 49.686
2022-04-18 | 16:26 | 49.687
2022-04-18 | 16:26 | 49.687
2022-04-18 | 16:26 | 49.688
2022-04-18 | 16:27 | 49.687
2022-04-18 | 16:27 | 49.688
2022-04-18 | 16:27 | 49.686
2022-04-18 | 16:27 | 49.685
2022-04-18 | 16:27 | 49.682
2022-04-18 | 16:27 | 49.681
2022-04-18 | 16:27 | 49.682
2022-04-18 | 16:27 | 49.682
2022-04-18 | 16:27 | 49.681
2022-04-18 | 16:27 | 49.683
2022-04-18 | 16:27 | 49.683
2022-04-18 | 16:27 | 49.683
2022-04-18 | 16:27 | 49.682
2022-04-18 | 16:27 | 49.679
2022-04-18 | 16:27 | 49.675
2022-04-18 | 16:27 | 49.674
2022-04-18 | 16:27 | 49.676
2022-04-18 | 16:27 | 49.676
2022-04-18 | 16:27 | 49.675
2022-04-18 | 16:27 | 49.676
2022-04-18 | 16:27 | 49.675
2022-04-18 | 16:27 | 49.674
2022-04-18 | 16:27 | 49.675
2022-04-18 | 16:27 | 49.673
2022-04-18 | 16:27 | 49.672
2022-04-18 | 16:27 | 49.674
2022-04-18 | 16:27 | 49.672
2022-04-18 | 16:27 | 49.673
2022-04-18 | 16:27 | 49.67
2022-04-18 | 16:27 | 49.668
2022-04-18 | 16:27 | 49.667
2022-04-18 | 16:27 | 49.664
2022-04-18 | 16:27 | 49.663
2022-04-18 | 16:27 | 49.664
2022-04-18 | 16:27 | 49.663
2022-04-18 | 16:27 | 49.664
2022-04-18 | 16:27 | 49.666
2022-04-18 | 16:27 | 49.667
2022-04-18 | 16:27 | 49.67
2022-04-18 | 16:27 | 49.671
2022-04-18 | 16:27 | 49.673
2022-04-18 | 16:27 | 49.675
2022-04-18 | 16:27 | 49.676
2022-04-18 | 16:27 | 49.677
2022-04-18 | 16:27 | 49.68
2022-04-18 | 16:27 | 49.68
2022-04-18 | 16:27 | 49.681
2022-04-18 | 16:27 | 49.685
2022-04-18 | 16:27 | 49.687
2022-04-18 | 16:27 | 49.69
2022-04-18 | 16:27 | 49.693
2022-04-18 | 16:27 | 49.697
2022-04-18 | 16:27 | 49.703
2022-04-18 | 16:27 | 49.709
2022-04-18 | 16:27 | 49.713
2022-04-18 | 16:27 | 49.718
2022-04-18 | 16:27 | 49.723
2022-04-18 | 16:27 | 49.725
2022-04-18 | 16:27 | 49.731
2022-04-18 | 16:27 | 49.735
2022-04-18 | 16:28 | 49.737
2022-04-18 | 16:28 | 49.739
2022-04-18 | 16:28 | 49.738
2022-04-18 | 16:28 | 49.737
2022-04-18 | 16:28 | 49.735
2022-04-18 | 16:28 | 49.733
2022-04-18 | 16:28 | 49.73
2022-04-18 | 16:28 | 49.728
2022-04-18 | 16:28 | 49.725
2022-04-18 | 16:28 | 49.724
2022-04-18 | 16:28 | 49.723
2022-04-18 | 16:28 | 49.723
2022-04-18 | 16:28 | 49.724
2022-04-18 | 16:28 | 49.724
2022-04-18 | 16:28 | 49.721
2022-04-18 | 16:28 | 49.721
2022-04-18 | 16:28 | 49.721
2022-04-18 | 16:28 | 49.721
2022-04-18 | 16:28 | 49.72
2022-04-18 | 16:28 | 49.718
2022-04-18 | 16:28 | 49.715
2022-04-18 | 16:28 | 49.712
2022-04-18 | 16:28 | 49.711
2022-04-18 | 16:28 | 49.711
2022-04-18 | 16:28 | 49.713
2022-04-18 | 16:28 | 49.712
2022-04-18 | 16:28 | 49.712
2022-04-18 | 16:28 | 49.711
2022-04-18 | 16:28 | 49.713
2022-04-18 | 16:28 | 49.712
2022-04-18 | 16:28 | 49.711
2022-04-18 | 16:28 | 49.713
2022-04-18 | 16:28 | 49.713
2022-04-18 | 16:28 | 49.712
2022-04-18 | 16:28 | 49.709
2022-04-18 | 16:28 | 49.708
2022-04-18 | 16:28 | 49.711
2022-04-18 | 16:28 | 49.714
2022-04-18 | 16:28 | 49.718
2022-04-18 | 16:28 | 49.724
2022-04-18 | 16:28 | 49.729
2022-04-18 | 16:28 | 49.733
2022-04-18 | 16:28 | 49.738
2022-04-18 | 16:28 | 49.741
2022-04-18 | 16:28 | 49.744
2022-04-18 | 16:28 | 49.745
2022-04-18 | 16:28 | 49.746
2022-04-18 | 16:28 | 49.752
2022-04-18 | 16:28 | 49.754
2022-04-18 | 16:28 | 49.757
2022-04-18 | 16:28 | 49.759
2022-04-18 | 16:28 | 49.759
2022-04-18 | 16:28 | 49.76
2022-04-18 | 16:28 | 49.76
2022-04-18 | 16:28 | 49.762
2022-04-18 | 16:28 | 49.763
2022-04-18 | 16:28 | 49.764
2022-04-18 | 16:28 | 49.765
2022-04-18 | 16:28 | 49.767
2022-04-18 | 16:29 | 49.768
2022-04-18 | 16:29 | 49.768
2022-04-18 | 16:29 | 49.769
2022-04-18 | 16:29 | 49.77
2022-04-18 | 16:29 | 49.77
2022-04-18 | 16:29 | 49.771
2022-04-18 | 16:29 | 49.775
2022-04-18 | 16:29 | 49.778
2022-04-18 | 16:29 | 49.781
2022-04-18 | 16:29 | 49.782
2022-04-18 | 16:29 | 49.782
2022-04-18 | 16:29 | 49.783
2022-04-18 | 16:29 | 49.783
2022-04-18 | 16:29 | 49.786
2022-04-18 | 16:29 | 49.787
2022-04-18 | 16:29 | 49.789
2022-04-18 | 16:29 | 49.791
2022-04-18 | 16:29 | 49.794
2022-04-18 | 16:29 | 49.792
2022-04-18 | 16:29 | 49.796
2022-04-18 | 16:29 | 49.797
2022-04-18 | 16:29 | 49.798
2022-04-18 | 16:29 | 49.8
2022-04-18 | 16:29 | 49.797
2022-04-18 | 16:29 | 49.796
2022-04-18 | 16:29 | 49.794
2022-04-18 | 16:29 | 49.795
2022-04-18 | 16:29 | 49.79
2022-04-18 | 16:29 | 49.791
2022-04-18 | 16:29 | 49.791
2022-04-18 | 16:29 | 49.791
2022-04-18 | 16:29 | 49.792
2022-04-18 | 16:29 | 49.791
2022-04-18 | 16:29 | 49.791
2022-04-18 | 16:29 | 49.793
2022-04-18 | 16:29 | 49.79
2022-04-18 | 16:29 | 49.791
2022-04-18 | 16:29 | 49.791
2022-04-18 | 16:29 | 49.79
2022-04-18 | 16:29 | 49.789
2022-04-18 | 16:29 | 49.793
2022-04-18 | 16:29 | 49.796
2022-04-18 | 16:29 | 49.799
2022-04-18 | 16:29 | 49.801
2022-04-18 | 16:29 | 49.803
2022-04-18 | 16:29 | 49.804
2022-04-18 | 16:29 | 49.804
2022-04-18 | 16:29 | 49.803
2022-04-18 | 16:29 | 49.802
2022-04-18 | 16:29 | 49.801
2022-04-18 | 16:29 | 49.8
2022-04-18 | 16:29 | 49.799
2022-04-18 | 16:29 | 49.804
2022-04-18 | 16:29 | 49.804
2022-04-18 | 16:29 | 49.806
2022-04-18 | 16:29 | 49.806
2022-04-18 | 16:29 | 49.807
2022-04-18 | 16:29 | 49.805
2022-04-18 | 16:29 | 49.805
2022-04-18 | 16:29 | 49.804
2022-04-18 | 16:30 | 49.805
2022-04-18 | 16:30 | 49.804
2022-04-18 | 16:30 | 49.805
2022-04-18 | 16:30 | 49.803
2022-04-18 | 16:30 | 49.801
2022-04-18 | 16:30 | 49.797
2022-04-18 | 16:30 | 49.797
2022-04-18 | 16:30 | 49.799
2022-04-18 | 16:30 | 49.798
2022-04-18 | 16:30 | 49.799
2022-04-18 | 16:30 | 49.801
2022-04-18 | 16:30 | 49.803
2022-04-18 | 16:30 | 49.803
2022-04-18 | 16:30 | 49.803
2022-04-18 | 16:30 | 49.805
2022-04-18 | 16:30 | 49.806
2022-04-18 | 16:30 | 49.805
2022-04-18 | 16:30 | 49.809
2022-04-18 | 16:30 | 49.812
2022-04-18 | 16:30 | 49.816
2022-04-18 | 16:30 | 49.817
2022-04-18 | 16:30 | 49.819
2022-04-18 | 16:30 | 49.82
2022-04-18 | 16:30 | 49.823
2022-04-18 | 16:30 | 49.824
2022-04-18 | 16:30 | 49.823
2022-04-18 | 16:30 | 49.821
2022-04-18 | 16:30 | 49.817
2022-04-18 | 16:30 | 49.814
2022-04-18 | 16:30 | 49.812
2022-04-18 | 16:30 | 49.811
2022-04-18 | 16:30 | 49.809
2022-04-18 | 16:30 | 49.809
2022-04-18 | 16:30 | 49.811
2022-04-18 | 16:30 | 49.816
2022-04-18 | 16:30 | 49.817
2022-04-18 | 16:30 | 49.817
2022-04-18 | 16:30 | 49.82
2022-04-18 | 16:30 | 49.821
2022-04-18 | 16:30 | 49.821
2022-04-18 | 16:30 | 49.824
2022-04-18 | 16:30 | 49.827
2022-04-18 | 16:30 | 49.825
2022-04-18 | 16:30 | 49.826
2022-04-18 | 16:30 | 49.827
2022-04-18 | 16:30 | 49.828
2022-04-18 | 16:30 | 49.828
2022-04-18 | 16:30 | 49.829
2022-04-18 | 16:30 | 49.832
2022-04-18 | 16:30 | 49.837
2022-04-18 | 16:30 | 49.84
2022-04-18 | 16:30 | 49.842
2022-04-18 | 16:30 | 49.841
2022-04-18 | 16:30 | 49.842
2022-04-18 | 16:30 | 49.843
2022-04-18 | 16:30 | 49.843
2022-04-18 | 16:30 | 49.842
2022-04-18 | 16:30 | 49.842
2022-04-18 | 16:30 | 49.843
2022-04-18 | 16:30 | 49.847
2022-04-18 | 16:30 | 49.85
2022-04-18 | 16:31 | 49.852
2022-04-18 | 16:31 | 49.855
2022-04-18 | 16:31 | 49.861
2022-04-18 | 16:31 | 49.864
2022-04-18 | 16:31 | 49.865
2022-04-18 | 16:31 | 49.867
2022-04-18 | 16:31 | 49.868
2022-04-18 | 16:31 | 49.872
2022-04-18 | 16:31 | 49.876
2022-04-18 | 16:31 | 49.875
2022-04-18 | 16:31 | 49.874
2022-04-18 | 16:31 | 49.876
2022-04-18 | 16:31 | 49.877
2022-04-18 | 16:31 | 49.879
2022-04-18 | 16:31 | 49.88
2022-04-18 | 16:31 | 49.879
2022-04-18 | 16:31 | 49.88
2022-04-18 | 16:31 | 49.878
2022-04-18 | 16:31 | 49.875
2022-04-18 | 16:31 | 49.873
2022-04-18 | 16:31 | 49.87
2022-04-18 | 16:31 | 49.868
2022-04-18 | 16:31 | 49.865
2022-04-18 | 16:31 | 49.867
2022-04-18 | 16:31 | 49.865
2022-04-18 | 16:31 | 49.865
2022-04-18 | 16:31 | 49.864
2022-04-18 | 16:31 | 49.867
2022-04-18 | 16:31 | 49.865
2022-04-18 | 16:31 | 49.866
2022-04-18 | 16:31 | 49.861
2022-04-18 | 16:31 | 49.863
2022-04-18 | 16:31 | 49.86
2022-04-18 | 16:31 | 49.863
2022-04-18 | 16:31 | 49.862
2022-04-18 | 16:31 | 49.864
2022-04-18 | 16:31 | 49.863
2022-04-18 | 16:31 | 49.866
2022-04-18 | 16:31 | 49.863
2022-04-18 | 16:31 | 49.865
2022-04-18 | 16:31 | 49.864
2022-04-18 | 16:31 | 49.865
2022-04-18 | 16:31 | 49.867
2022-04-18 | 16:31 | 49.866
2022-04-18 | 16:31 | 49.867
2022-04-18 | 16:31 | 49.868
2022-04-18 | 16:31 | 49.868
2022-04-18 | 16:31 | 49.867
2022-04-18 | 16:31 | 49.866
2022-04-18 | 16:31 | 49.867
2022-04-18 | 16:31 | 49.863
2022-04-18 | 16:31 | 49.865
2022-04-18 | 16:31 | 49.864
2022-04-18 | 16:31 | 49.865
2022-04-18 | 16:31 | 49.866
2022-04-18 | 16:31 | 49.868
2022-04-18 | 16:31 | 49.868
2022-04-18 | 16:31 | 49.871
2022-04-18 | 16:31 | 49.87
2022-04-18 | 16:31 | 49.873
2022-04-18 | 16:32 | 49.868
2022-04-18 | 16:32 | 49.869
2022-04-18 | 16:32 | 49.867
2022-04-18 | 16:32 | 49.865
2022-04-18 | 16:32 | 49.866
2022-04-18 | 16:32 | 49.864
2022-04-18 | 16:32 | 49.863
2022-04-18 | 16:32 | 49.863
2022-04-18 | 16:32 | 49.862
2022-04-18 | 16:32 | 49.867
2022-04-18 | 16:32 | 49.868
2022-04-18 | 16:32 | 49.872
2022-04-18 | 16:32 | 49.875
2022-04-18 | 16:32 | 49.876
2022-04-18 | 16:32 | 49.88
2022-04-18 | 16:32 | 49.88
2022-04-18 | 16:32 | 49.88
2022-04-18 | 16:32 | 49.878
2022-04-18 | 16:32 | 49.876
2022-04-18 | 16:32 | 49.875
2022-04-18 | 16:32 | 49.877
2022-04-18 | 16:32 | 49.878
2022-04-18 | 16:32 | 49.88
2022-04-18 | 16:32 | 49.879
2022-04-18 | 16:32 | 49.879
2022-04-18 | 16:32 | 49.878
2022-04-18 | 16:32 | 49.878
2022-04-18 | 16:32 | 49.88
2022-04-18 | 16:32 | 49.881
2022-04-18 | 16:32 | 49.886
2022-04-18 | 16:32 | 49.887
2022-04-18 | 16:32 | 49.887
2022-04-18 | 16:32 | 49.888
2022-04-18 | 16:32 | 49.884
2022-04-18 | 16:32 | 49.884
2022-04-18 | 16:32 | 49.886
2022-04-18 | 16:32 | 49.884
2022-04-18 | 16:32 | 49.883
2022-04-18 | 16:32 | 49.884
2022-04-18 | 16:32 | 49.886
2022-04-18 | 16:32 | 49.886
2022-04-18 | 16:32 | 49.887
2022-04-18 | 16:32 | 49.89
2022-04-18 | 16:32 | 49.892
2022-04-18 | 16:32 | 49.893
2022-04-18 | 16:32 | 49.893
2022-04-18 | 16:32 | 49.894
2022-04-18 | 16:32 | 49.896
2022-04-18 | 16:32 | 49.896
2022-04-18 | 16:32 | 49.896
2022-04-18 | 16:32 | 49.896
2022-04-18 | 16:32 | 49.896
2022-04-18 | 16:32 | 49.898
2022-04-18 | 16:32 | 49.899
2022-04-18 | 16:32 | 49.9
2022-04-18 | 16:32 | 49.901
2022-04-18 | 16:32 | 49.903
2022-04-18 | 16:32 | 49.903
2022-04-18 | 16:32 | 49.905
2022-04-18 | 16:33 | 49.907
2022-04-18 | 16:33 | 49.911
2022-04-18 | 16:33 | 49.914
2022-04-18 | 16:33 | 49.919
2022-04-18 | 16:33 | 49.922
2022-04-18 | 16:33 | 49.925
2022-04-18 | 16:33 | 49.928
2022-04-18 | 16:33 | 49.931
2022-04-18 | 16:33 | 49.933
2022-04-18 | 16:33 | 49.936
2022-04-18 | 16:33 | 49.937
2022-04-18 | 16:33 | 49.938
2022-04-18 | 16:33 | 49.938
2022-04-18 | 16:33 | 49.937
2022-04-18 | 16:33 | 49.937
2022-04-18 | 16:33 | 49.94
2022-04-18 | 16:33 | 49.942
2022-04-18 | 16:33 | 49.943
2022-04-18 | 16:33 | 49.946
2022-04-18 | 16:33 | 49.95
2022-04-18 | 16:33 | 49.953
2022-04-18 | 16:33 | 49.957
2022-04-18 | 16:33 | 49.962
2022-04-18 | 16:33 | 49.964
2022-04-18 | 16:33 | 49.965
2022-04-18 | 16:33 | 49.965
2022-04-18 | 16:33 | 49.964
2022-04-18 | 16:33 | 49.965
2022-04-18 | 16:33 | 49.964
2022-04-18 | 16:33 | 49.963
2022-04-18 | 16:33 | 49.961
2022-04-18 | 16:33 | 49.96
2022-04-18 | 16:33 | 49.959
2022-04-18 | 16:33 | 49.96
2022-04-18 | 16:33 | 49.962
2022-04-18 | 16:33 | 49.964
2022-04-18 | 16:33 | 49.966
2022-04-18 | 16:33 | 49.969
2022-04-18 | 16:33 | 49.972
2022-04-18 | 16:33 | 49.973
2022-04-18 | 16:33 | 49.975
2022-04-18 | 16:33 | 49.976
2022-04-18 | 16:33 | 49.975
2022-04-18 | 16:33 | 49.975
2022-04-18 | 16:33 | 49.978
2022-04-18 | 16:33 | 49.979
2022-04-18 | 16:33 | 49.981
2022-04-18 | 16:33 | 49.983
2022-04-18 | 16:33 | 49.98
2022-04-18 | 16:33 | 49.981
2022-04-18 | 16:33 | 49.98
2022-04-18 | 16:33 | 49.977
2022-04-18 | 16:33 | 49.975
2022-04-18 | 16:33 | 49.972
2022-04-18 | 16:33 | 49.97
2022-04-18 | 16:33 | 49.971
2022-04-18 | 16:33 | 49.972
2022-04-18 | 16:33 | 49.978
2022-04-18 | 16:33 | 49.98
2022-04-18 | 16:33 | 49.984
2022-04-18 | 16:34 | 49.984
2022-04-18 | 16:34 | 49.983
2022-04-18 | 16:34 | 49.983
2022-04-18 | 16:34 | 49.98
2022-04-18 | 16:34 | 49.978
2022-04-18 | 16:34 | 49.976
2022-04-18 | 16:34 | 49.973
2022-04-18 | 16:34 | 49.97
2022-04-18 | 16:34 | 49.969
2022-04-18 | 16:34 | 49.967
2022-04-18 | 16:34 | 49.968
2022-04-18 | 16:34 | 49.968
2022-04-18 | 16:34 | 49.971
2022-04-18 | 16:34 | 49.972
2022-04-18 | 16:34 | 49.97
2022-04-18 | 16:34 | 49.971
2022-04-18 | 16:34 | 49.969
2022-04-18 | 16:34 | 49.967
2022-04-18 | 16:34 | 49.966
2022-04-18 | 16:34 | 49.964
2022-04-18 | 16:34 | 49.96
2022-04-18 | 16:34 | 49.956
2022-04-18 | 16:34 | 49.952
2022-04-18 | 16:34 | 49.949
2022-04-18 | 16:34 | 49.949
2022-04-18 | 16:34 | 49.952
2022-04-18 | 16:34 | 49.955
2022-04-18 | 16:34 | 49.952
2022-04-18 | 16:34 | 49.951
2022-04-18 | 16:34 | 49.949
2022-04-18 | 16:34 | 49.947
2022-04-18 | 16:34 | 49.95
2022-04-18 | 16:34 | 49.951
2022-04-18 | 16:34 | 49.952
2022-04-18 | 16:34 | 49.949
2022-04-18 | 16:34 | 49.948
2022-04-18 | 16:34 | 49.945
2022-04-18 | 16:34 | 49.941
2022-04-18 | 16:34 | 49.94
2022-04-18 | 16:34 | 49.939
2022-04-18 | 16:34 | 49.938
2022-04-18 | 16:34 | 49.941
2022-04-18 | 16:34 | 49.945
2022-04-18 | 16:34 | 49.951
2022-04-18 | 16:34 | 49.953
2022-04-18 | 16:34 | 49.956
2022-04-18 | 16:34 | 49.957
2022-04-18 | 16:34 | 49.961
2022-04-18 | 16:34 | 49.965
2022-04-18 | 16:34 | 49.972
2022-04-18 | 16:34 | 49.977
2022-04-18 | 16:34 | 49.979
2022-04-18 | 16:34 | 49.983
2022-04-18 | 16:34 | 49.982
2022-04-18 | 16:34 | 49.987
2022-04-18 | 16:34 | 49.988
2022-04-18 | 16:34 | 49.992
2022-04-18 | 16:34 | 49.994
2022-04-18 | 16:34 | 49.994
2022-04-18 | 16:34 | 49.995
2022-04-18 | 16:34 | 49.996
2022-04-18 | 16:35 | 49.998
2022-04-18 | 16:35 | 49.998
2022-04-18 | 16:35 | 50
2022-04-18 | 16:35 | 50
2022-04-18 | 16:35 | 50.003
2022-04-18 | 16:35 | 50.005
2022-04-18 | 16:35 | 50.011
2022-04-18 | 16:35 | 50.016
2022-04-18 | 16:35 | 50.02
2022-04-18 | 16:35 | 50.022
2022-04-18 | 16:35 | 50.022
2022-04-18 | 16:35 | 50.02
2022-04-18 | 16:35 | 50.022
2022-04-18 | 16:35 | 50.026
2022-04-18 | 16:35 | 50.031
2022-04-18 | 16:35 | 50.03
2022-04-18 | 16:35 | 50.029
2022-04-18 | 16:35 | 50.029
2022-04-18 | 16:35 | 50.03
2022-04-18 | 16:35 | 50.032
2022-04-18 | 16:35 | 50.031
2022-04-18 | 16:35 | 50.032
2022-04-18 | 16:35 | 50.032
2022-04-18 | 16:35 | 50.032
2022-04-18 | 16:35 | 50.032
2022-04-18 | 16:35 | 50.033
2022-04-18 | 16:35 | 50.035
2022-04-18 | 16:35 | 50.034
2022-04-18 | 16:35 | 50.034
2022-04-18 | 16:35 | 50.037

## 20220421-1
In GMT
Date | Time | Freq
2022-04-21 | 4:08 | 49.952
2022-04-21 | 4:08 | 49.95
2022-04-21 | 4:08 | 49.952
2022-04-21 | 4:08 | 49.955
2022-04-21 | 4:08 | 49.957
2022-04-21 | 4:08 | 49.96
2022-04-21 | 4:08 | 49.962
2022-04-21 | 4:08 | 49.963
2022-04-21 | 4:08 | 49.965
2022-04-21 | 4:08 | 49.966
2022-04-21 | 4:08 | 49.966
2022-04-21 | 4:08 | 49.967
2022-04-21 | 4:08 | 49.966
2022-04-21 | 4:08 | 49.963
2022-04-21 | 4:08 | 49.962
2022-04-21 | 4:08 | 49.961
2022-04-21 | 4:08 | 49.959
2022-04-21 | 4:08 | 49.958
2022-04-21 | 4:08 | 49.957
2022-04-21 | 4:08 | 49.956
2022-04-21 | 4:08 | 49.956
2022-04-21 | 4:08 | 49.955
2022-04-21 | 4:08 | 49.956
2022-04-21 | 4:08 | 49.955
2022-04-21 | 4:08 | 49.955
2022-04-21 | 4:08 | 49.956
2022-04-21 | 4:08 | 49.957
2022-04-21 | 4:08 | 49.959
2022-04-21 | 4:08 | 49.96
2022-04-21 | 4:08 | 49.959
2022-04-21 | 4:08 | 49.96
2022-04-21 | 4:09 | 49.963
2022-04-21 | 4:09 | 49.963
2022-04-21 | 4:09 | 49.965
2022-04-21 | 4:09 | 49.968
2022-04-21 | 4:09 | 49.973
2022-04-21 | 4:09 | 49.978
2022-04-21 | 4:09 | 49.98
2022-04-21 | 4:09 | 49.982
2022-04-21 | 4:09 | 49.984
2022-04-21 | 4:09 | 49.984
2022-04-21 | 4:09 | 49.982
2022-04-21 | 4:09 | 49.983
2022-04-21 | 4:09 | 49.984
2022-04-21 | 4:09 | 49.986
2022-04-21 | 4:09 | 49.986
2022-04-21 | 4:09 | 49.984
2022-04-21 | 4:09 | 49.982
2022-04-21 | 4:09 | 49.98
2022-04-21 | 4:09 | 49.978
2022-04-21 | 4:09 | 49.975
2022-04-21 | 4:09 | 49.974
2022-04-21 | 4:09 | 49.975
2022-04-21 | 4:09 | 49.975
2022-04-21 | 4:09 | 49.976
2022-04-21 | 4:09 | 49.976
2022-04-21 | 4:09 | 49.978
2022-04-21 | 4:09 | 49.978
2022-04-21 | 4:09 | 49.976
2022-04-21 | 4:09 | 49.972
2022-04-21 | 4:09 | 49.968
2022-04-21 | 4:09 | 49.964
2022-04-21 | 4:09 | 49.961
2022-04-21 | 4:09 | 49.96
2022-04-21 | 4:09 | 49.96
2022-04-21 | 4:09 | 49.96
2022-04-21 | 4:09 | 49.961
2022-04-21 | 4:09 | 49.961
2022-04-21 | 4:09 | 49.962
2022-04-21 | 4:09 | 49.965
2022-04-21 | 4:09 | 49.966
2022-04-21 | 4:09 | 49.967
2022-04-21 | 4:09 | 49.967
2022-04-21 | 4:09 | 49.966
2022-04-21 | 4:09 | 49.965
2022-04-21 | 4:09 | 49.964
2022-04-21 | 4:09 | 49.962
2022-04-21 | 4:09 | 49.96
2022-04-21 | 4:09 | 49.959
2022-04-21 | 4:09 | 49.957
2022-04-21 | 4:09 | 49.957
2022-04-21 | 4:09 | 49.96
2022-04-21 | 4:09 | 49.964
2022-04-21 | 4:09 | 49.969
2022-04-21 | 4:09 | 49.972
2022-04-21 | 4:09 | 50.043
2022-04-21 | 4:09 | 50.142
2022-04-21 | 4:09 | 50.208
2022-04-21 | 4:09 | 50.254
2022-04-21 | 4:09 | 50.278
2022-04-21 | 4:10 | 50.288
2022-04-21 | 4:10 | 50.292
2022-04-21 | 4:10 | 50.293
2022-04-21 | 4:10 | 50.293
2022-04-21 | 4:10 | 50.293
2022-04-21 | 4:10 | 50.292
2022-04-21 | 4:10 | 50.293
2022-04-21 | 4:10 | 50.292
2022-04-21 | 4:10 | 50.291
2022-04-21 | 4:10 | 50.292
2022-04-21 | 4:10 | 50.289
2022-04-21 | 4:10 | 50.289
2022-04-21 | 4:10 | 50.287
2022-04-21 | 4:10 | 50.284
2022-04-21 | 4:10 | 50.284
2022-04-21 | 4:10 | 50.287
2022-04-21 | 4:10 | 50.287
2022-04-21 | 4:10 | 50.287
2022-04-21 | 4:10 | 50.287
2022-04-21 | 4:10 | 50.286
2022-04-21 | 4:10 | 50.287
2022-04-21 | 4:10 | 50.288
2022-04-21 | 4:10 | 50.287
2022-04-21 | 4:10 | 50.286
2022-04-21 | 4:10 | 50.285
2022-04-21 | 4:10 | 50.283
2022-04-21 | 4:10 | 50.285
2022-04-21 | 4:10 | 50.285
2022-04-21 | 4:10 | 50.284
2022-04-21 | 4:10 | 50.285
2022-04-21 | 4:10 | 50.284
2022-04-21 | 4:10 | 50.283
2022-04-21 | 4:10 | 50.283
2022-04-21 | 4:10 | 50.282
2022-04-21 | 4:10 | 50.282
2022-04-21 | 4:10 | 50.284
2022-04-21 | 4:10 | 50.286
2022-04-21 | 4:10 | 50.289
2022-04-21 | 4:10 | 50.289
2022-04-21 | 4:10 | 50.288
2022-04-21 | 4:10 | 50.288
2022-04-21 | 4:10 | 50.291
2022-04-21 | 4:10 | 50.294
2022-04-21 | 4:10 | 50.296
2022-04-21 | 4:10 | 50.297
2022-04-21 | 4:10 | 50.299
2022-04-21 | 4:10 | 50.299
2022-04-21 | 4:10 | 50.3
2022-04-21 | 4:10 | 50.298
2022-04-21 | 4:10 | 50.301
2022-04-21 | 4:10 | 50.301
2022-04-21 | 4:10 | 50.303
2022-04-21 | 4:10 | 50.303
2022-04-21 | 4:10 | 50.306
2022-04-21 | 4:10 | 50.306
2022-04-21 | 4:10 | 50.306
2022-04-21 | 4:10 | 50.307
2022-04-21 | 4:10 | 50.305
2022-04-21 | 4:10 | 50.306
2022-04-21 | 4:10 | 50.304
2022-04-21 | 4:10 | 50.303
2022-04-21 | 4:11 | 50.302
2022-04-21 | 4:11 | 50.297
2022-04-21 | 4:11 | 50.285
2022-04-21 | 4:11 | 50.272
2022-04-21 | 4:11 | 50.263
2022-04-21 | 4:11 | 50.256
2022-04-21 | 4:11 | 50.25
2022-04-21 | 4:11 | 50.244
2022-04-21 | 4:11 | 50.241
2022-04-21 | 4:11 | 50.235
2022-04-21 | 4:11 | 50.233
2022-04-21 | 4:11 | 50.23
2022-04-21 | 4:11 | 50.229
2022-04-21 | 4:11 | 50.228
2022-04-21 | 4:11 | 50.226
2022-04-21 | 4:11 | 50.224
2022-04-21 | 4:11 | 50.222
2022-04-21 | 4:11 | 50.223
2022-04-21 | 4:11 | 50.225
2022-04-21 | 4:11 | 50.227
2022-04-21 | 4:11 | 50.229
2022-04-21 | 4:11 | 50.231
2022-04-21 | 4:11 | 50.231
2022-04-21 | 4:11 | 50.232
2022-04-21 | 4:11 | 50.231
2022-04-21 | 4:11 | 50.23
2022-04-21 | 4:11 | 50.229
2022-04-21 | 4:11 | 50.229
2022-04-21 | 4:11 | 50.229
2022-04-21 | 4:11 | 50.23
2022-04-21 | 4:11 | 50.228
2022-04-21 | 4:11 | 50.227
2022-04-21 | 4:11 | 50.225
2022-04-21 | 4:11 | 50.226
2022-04-21 | 4:11 | 50.228
2022-04-21 | 4:11 | 50.227
2022-04-21 | 4:11 | 50.228
2022-04-21 | 4:11 | 50.229
2022-04-21 | 4:11 | 50.231
2022-04-21 | 4:11 | 50.234
2022-04-21 | 4:11 | 50.237
2022-04-21 | 4:11 | 50.237
2022-04-21 | 4:11 | 50.237
2022-04-21 | 4:11 | 50.235
2022-04-21 | 4:11 | 50.234
2022-04-21 | 4:11 | 50.231
2022-04-21 | 4:11 | 50.229
2022-04-21 | 4:11 | 50.224
2022-04-21 | 4:11 | 50.223
2022-04-21 | 4:11 | 50.221
2022-04-21 | 4:11 | 50.219
2022-04-21 | 4:11 | 50.22
2022-04-21 | 4:11 | 50.218
2022-04-21 | 4:11 | 50.217
2022-04-21 | 4:11 | 50.214
2022-04-21 | 4:11 | 50.217
2022-04-21 | 4:11 | 50.215
2022-04-21 | 4:11 | 50.216
2022-04-21 | 4:11 | 50.215
2022-04-21 | 4:12 | 50.215
2022-04-21 | 4:12 | 50.217
2022-04-21 | 4:12 | 50.218
2022-04-21 | 4:12 | 50.219
2022-04-21 | 4:12 | 50.218
2022-04-21 | 4:12 | 50.217
2022-04-21 | 4:12 | 50.217
2022-04-21 | 4:12 | 50.217
2022-04-21 | 4:12 | 50.216
2022-04-21 | 4:12 | 50.215
2022-04-21 | 4:12 | 50.215
2022-04-21 | 4:12 | 50.213
2022-04-21 | 4:12 | 50.213
2022-04-21 | 4:12 | 50.213
2022-04-21 | 4:12 | 50.213
2022-04-21 | 4:12 | 50.214
2022-04-21 | 4:12 | 50.216
2022-04-21 | 4:12 | 50.215
2022-04-21 | 4:12 | 50.214
2022-04-21 | 4:12 | 50.214
2022-04-21 | 4:12 | 50.215
2022-04-21 | 4:12 | 50.215
2022-04-21 | 4:12 | 50.217
2022-04-21 | 4:12 | 50.217
2022-04-21 | 4:12 | 50.218
2022-04-21 | 4:12 | 50.218
2022-04-21 | 4:12 | 50.216
2022-04-21 | 4:12 | 50.215
2022-04-21 | 4:12 | 50.216
2022-04-21 | 4:12 | 50.214
2022-04-21 | 4:12 | 50.213
2022-04-21 | 4:12 | 50.213
2022-04-21 | 4:12 | 50.213
2022-04-21 | 4:12 | 50.212
2022-04-21 | 4:12 | 50.211
2022-04-21 | 4:12 | 50.21
2022-04-21 | 4:12 | 50.212
2022-04-21 | 4:12 | 50.212
2022-04-21 | 4:12 | 50.213
2022-04-21 | 4:12 | 50.213
2022-04-21 | 4:12 | 50.215
2022-04-21 | 4:12 | 50.215
2022-04-21 | 4:12 | 50.215
2022-04-21 | 4:12 | 50.214
2022-04-21 | 4:12 | 50.211
2022-04-21 | 4:12 | 50.209
2022-04-21 | 4:12 | 50.207
2022-04-21 | 4:12 | 50.204
2022-04-21 | 4:12 | 50.205
2022-04-21 | 4:12 | 50.206
2022-04-21 | 4:12 | 50.206
2022-04-21 | 4:12 | 50.204
2022-04-21 | 4:12 | 50.203
2022-04-21 | 4:12 | 50.201
2022-04-21 | 4:12 | 50.199
2022-04-21 | 4:12 | 50.195
2022-04-21 | 4:12 | 50.191
2022-04-21 | 4:12 | 50.184
2022-04-21 | 4:12 | 50.181
2022-04-21 | 4:12 | 50.179
2022-04-21 | 4:12 | 50.178
2022-04-21 | 4:13 | 50.179
2022-04-21 | 4:13 | 50.181
2022-04-21 | 4:13 | 50.182
2022-04-21 | 4:13 | 50.183
2022-04-21 | 4:13 | 50.183
2022-04-21 | 4:13 | 50.182
2022-04-21 | 4:13 | 50.181
2022-04-21 | 4:13 | 50.179
2022-04-21 | 4:13 | 50.176
2022-04-21 | 4:13 | 50.173
2022-04-21 | 4:13 | 50.17
2022-04-21 | 4:13 | 50.166
2022-04-21 | 4:13 | 50.163
2022-04-21 | 4:13 | 50.162
2022-04-21 | 4:13 | 50.159
2022-04-21 | 4:13 | 50.156
2022-04-21 | 4:13 | 50.155
2022-04-21 | 4:13 | 50.153
2022-04-21 | 4:13 | 50.154
2022-04-21 | 4:13 | 50.155
2022-04-21 | 4:13 | 50.157
2022-04-21 | 4:13 | 50.157
2022-04-21 | 4:13 | 50.158
2022-04-21 | 4:13 | 50.16
2022-04-21 | 4:13 | 50.159
2022-04-21 | 4:13 | 50.157
2022-04-21 | 4:13 | 50.153
2022-04-21 | 4:13 | 50.15
2022-04-21 | 4:13 | 50.146
2022-04-21 | 4:13 | 50.143
2022-04-21 | 4:13 | 50.138
2022-04-21 | 4:13 | 50.137
2022-04-21 | 4:13 | 50.134
2022-04-21 | 4:13 | 50.135
2022-04-21 | 4:13 | 50.132
2022-04-21 | 4:13 | 50.133
2022-04-21 | 4:13 | 50.133
2022-04-21 | 4:13 | 50.13
2022-04-21 | 4:13 | 50.13
2022-04-21 | 4:13 | 50.129
2022-04-21 | 4:13 | 50.128
2022-04-21 | 4:13 | 50.129
2022-04-21 | 4:13 | 50.129
2022-04-21 | 4:13 | 50.127
2022-04-21 | 4:13 | 50.125
2022-04-21 | 4:13 | 50.124
2022-04-21 | 4:13 | 50.122
2022-04-21 | 4:13 | 50.12
2022-04-21 | 4:13 | 50.12
2022-04-21 | 4:13 | 50.12
2022-04-21 | 4:13 | 50.121
2022-04-21 | 4:13 | 50.12
2022-04-21 | 4:13 | 50.119
2022-04-21 | 4:13 | 50.119
2022-04-21 | 4:13 | 50.117
2022-04-21 | 4:13 | 50.115
2022-04-21 | 4:13 | 50.115
2022-04-21 | 4:13 | 50.111
2022-04-21 | 4:13 | 50.109
2022-04-21 | 4:13 | 50.106
2022-04-21 | 4:14 | 50.103
2022-04-21 | 4:14 | 50.101
2022-04-21 | 4:14 | 50.099
2022-04-21 | 4:14 | 50.097
2022-04-21 | 4:14 | 50.096
2022-04-21 | 4:14 | 50.096
2022-04-21 | 4:14 | 50.096
2022-04-21 | 4:14 | 50.096
2022-04-21 | 4:14 | 50.096
2022-04-21 | 4:14 | 50.098
2022-04-21 | 4:14 | 50.099
2022-04-21 | 4:14 | 50.1
2022-04-21 | 4:14 | 50.098
2022-04-21 | 4:14 | 50.096
2022-04-21 | 4:14 | 50.094
2022-04-21 | 4:14 | 50.092
2022-04-21 | 4:14 | 50.09
2022-04-21 | 4:14 | 50.087
2022-04-21 | 4:14 | 50.085
2022-04-21 | 4:14 | 50.082
2022-04-21 | 4:14 | 50.078
2022-04-21 | 4:14 | 50.075
2022-04-21 | 4:14 | 50.075
2022-04-21 | 4:14 | 50.073
2022-04-21 | 4:14 | 50.073
2022-04-21 | 4:14 | 50.072
2022-04-21 | 4:14 | 50.071
2022-04-21 | 4:14 | 50.067
2022-04-21 | 4:14 | 50.063
2022-04-21 | 4:14 | 50.061
2022-04-21 | 4:14 | 50.059
2022-04-21 | 4:14 | 50.058
2022-04-21 | 4:14 | 50.058
2022-04-21 | 4:14 | 50.058
2022-04-21 | 4:14 | 50.058
2022-04-21 | 4:14 | 50.057
2022-04-21 | 4:14 | 50.056
2022-04-21 | 4:14 | 50.053
2022-04-21 | 4:14 | 50.049
2022-04-21 | 4:14 | 50.044
2022-04-21 | 4:14 | 50.038
2022-04-21 | 4:14 | 50.033
2022-04-21 | 4:14 | 50.029
2022-04-21 | 4:14 | 50.026
2022-04-21 | 4:14 | 50.025
2022-04-21 | 4:14 | 50.025
2022-04-21 | 4:14 | 50.022
2022-04-21 | 4:14 | 50.02
2022-04-21 | 4:14 | 50.019
2022-04-21 | 4:14 | 50.019
2022-04-21 | 4:14 | 50.019
2022-04-21 | 4:14 | 50.017
2022-04-21 | 4:14 | 50.017
2022-04-21 | 4:14 | 50.016
2022-04-21 | 4:14 | 50.013
2022-04-21 | 4:14 | 50.01
2022-04-21 | 4:14 | 50.004
2022-04-21 | 4:14 | 49.998
2022-04-21 | 4:14 | 49.992
2022-04-21 | 4:14 | 49.988
2022-04-21 | 4:15 | 49.981
2022-04-21 | 4:15 | 49.979
2022-04-21 | 4:15 | 49.979
2022-04-21 | 4:15 | 49.981
2022-04-21 | 4:15 | 49.981
2022-04-21 | 4:15 | 49.983
2022-04-21 | 4:15 | 49.985
2022-04-21 | 4:15 | 49.986
2022-04-21 | 4:15 | 49.987
2022-04-21 | 4:15 | 49.986
2022-04-21 | 4:15 | 49.985
2022-04-21 | 4:15 | 49.984
2022-04-21 | 4:15 | 49.983
2022-04-21 | 4:15 | 49.984
2022-04-21 | 4:15 | 49.984
2022-04-21 | 4:15 | 49.986
2022-04-21 | 4:15 | 49.986
2022-04-21 | 4:15 | 49.985
2022-04-21 | 4:15 | 49.986
2022-04-21 | 4:15 | 49.987
2022-04-21 | 4:15 | 49.99
2022-04-21 | 4:15 | 49.991
2022-04-21 | 4:15 | 49.991
2022-04-21 | 4:15 | 49.991
2022-04-21 | 4:15 | 49.995
2022-04-21 | 4:15 | 49.998
2022-04-21 | 4:15 | 50.001
2022-04-21 | 4:15 | 50.001
2022-04-21 | 4:15 | 50
2022-04-21 | 4:15 | 49.997

## 20220426-1
In GMT
Date | Time | Freq
2022-04-25 | 23:19 | 50.081
2022-04-25 | 23:19 | 50.082
2022-04-25 | 23:19 | 50.082
2022-04-25 | 23:19 | 50.082
2022-04-25 | 23:19 | 50.083
2022-04-25 | 23:19 | 50.085
2022-04-25 | 23:19 | 50.087
2022-04-25 | 23:19 | 50.087
2022-04-25 | 23:19 | 50.088
2022-04-25 | 23:19 | 50.088
2022-04-25 | 23:19 | 50.087
2022-04-25 | 23:19 | 50.087
2022-04-25 | 23:19 | 50.087
2022-04-25 | 23:19 | 50.086
2022-04-25 | 23:19 | 50.086
2022-04-25 | 23:19 | 50.084
2022-04-25 | 23:19 | 50.084
2022-04-25 | 23:19 | 50.083
2022-04-25 | 23:19 | 50.083
2022-04-25 | 23:19 | 50.081
2022-04-25 | 23:19 | 50.08
2022-04-25 | 23:19 | 50.078
2022-04-25 | 23:19 | 50.076
2022-04-25 | 23:19 | 50.075
2022-04-25 | 23:19 | 50.075
2022-04-25 | 23:19 | 50.073
2022-04-25 | 23:19 | 50.071
2022-04-25 | 23:19 | 50.071
2022-04-25 | 23:19 | 50.07
2022-04-25 | 23:19 | 50.069
2022-04-25 | 23:20 | 50.068
2022-04-25 | 23:20 | 50.066
2022-04-25 | 23:20 | 50.065
2022-04-25 | 23:20 | 50.063
2022-04-25 | 23:20 | 50.064
2022-04-25 | 23:20 | 50.067
2022-04-25 | 23:20 | 50.067
2022-04-25 | 23:20 | 50.069
2022-04-25 | 23:20 | 50.071
2022-04-25 | 23:20 | 50.073
2022-04-25 | 23:20 | 50.075
2022-04-25 | 23:20 | 50.074
2022-04-25 | 23:20 | 50.074
2022-04-25 | 23:20 | 50.073
2022-04-25 | 23:20 | 50.07
2022-04-25 | 23:20 | 50.07
2022-04-25 | 23:20 | 50.066
2022-04-25 | 23:20 | 50.061
2022-04-25 | 23:20 | 50.057
2022-04-25 | 23:20 | 50.052
2022-04-25 | 23:20 | 50.048
2022-04-25 | 23:20 | 50.046
2022-04-25 | 23:20 | 50.045
2022-04-25 | 23:20 | 50.045
2022-04-25 | 23:20 | 50.046
2022-04-25 | 23:20 | 50.047
2022-04-25 | 23:20 | 50.046
2022-04-25 | 23:20 | 50.048
2022-04-25 | 23:20 | 50.049
2022-04-25 | 23:20 | 50.052
2022-04-25 | 23:20 | 50.085
2022-04-25 | 23:20 | 50.16
2022-04-25 | 23:20 | 50.23
2022-04-25 | 23:20 | 50.28
2022-04-25 | 23:20 | 50.313
2022-04-25 | 23:20 | 50.325
2022-04-25 | 23:20 | 50.326
2022-04-25 | 23:20 | 50.322
2022-04-25 | 23:20 | 50.322
2022-04-25 | 23:20 | 50.319
2022-04-25 | 23:20 | 50.317
2022-04-25 | 23:20 | 50.313
2022-04-25 | 23:20 | 50.31
2022-04-25 | 23:20 | 50.309
2022-04-25 | 23:20 | 50.307
2022-04-25 | 23:20 | 50.308
2022-04-25 | 23:20 | 50.309
2022-04-25 | 23:20 | 50.311
2022-04-25 | 23:20 | 50.311
2022-04-25 | 23:20 | 50.312
2022-04-25 | 23:20 | 50.313
2022-04-25 | 23:20 | 50.315
2022-04-25 | 23:20 | 50.314
2022-04-25 | 23:20 | 50.314
2022-04-25 | 23:20 | 50.314
2022-04-25 | 23:20 | 50.314
2022-04-25 | 23:20 | 50.312
2022-04-25 | 23:20 | 50.312
2022-04-25 | 23:20 | 50.312
2022-04-25 | 23:20 | 50.315
2022-04-25 | 23:20 | 50.313
2022-04-25 | 23:21 | 50.311
2022-04-25 | 23:21 | 50.31
2022-04-25 | 23:21 | 50.308
2022-04-25 | 23:21 | 50.31
2022-04-25 | 23:21 | 50.309
2022-04-25 | 23:21 | 50.311
2022-04-25 | 23:21 | 50.314
2022-04-25 | 23:21 | 50.314
2022-04-25 | 23:21 | 50.313
2022-04-25 | 23:21 | 50.313
2022-04-25 | 23:21 | 50.311
2022-04-25 | 23:21 | 50.311
2022-04-25 | 23:21 | 50.31
2022-04-25 | 23:21 | 50.308
2022-04-25 | 23:21 | 50.306
2022-04-25 | 23:21 | 50.304
2022-04-25 | 23:21 | 50.304
2022-04-25 | 23:21 | 50.304
2022-04-25 | 23:21 | 50.301
2022-04-25 | 23:21 | 50.295
2022-04-25 | 23:21 | 50.286
2022-04-25 | 23:21 | 50.279
2022-04-25 | 23:21 | 50.27
2022-04-25 | 23:21 | 50.266
2022-04-25 | 23:21 | 50.261
2022-04-25 | 23:21 | 50.257
2022-04-25 | 23:21 | 50.256
2022-04-25 | 23:21 | 50.256
2022-04-25 | 23:21 | 50.258
2022-04-25 | 23:21 | 50.259
2022-04-25 | 23:21 | 50.259
2022-04-25 | 23:21 | 50.259
2022-04-25 | 23:21 | 50.26
2022-04-25 | 23:21 | 50.261
2022-04-25 | 23:21 | 50.264
2022-04-25 | 23:21 | 50.267
2022-04-25 | 23:21 | 50.269
2022-04-25 | 23:21 | 50.271
2022-04-25 | 23:21 | 50.272
2022-04-25 | 23:21 | 50.274
2022-04-25 | 23:21 | 50.275
2022-04-25 | 23:21 | 50.274
2022-04-25 | 23:21 | 50.272
2022-04-25 | 23:21 | 50.269
2022-04-25 | 23:21 | 50.267
2022-04-25 | 23:21 | 50.264
2022-04-25 | 23:21 | 50.263
2022-04-25 | 23:21 | 50.262
2022-04-25 | 23:21 | 50.261
2022-04-25 | 23:21 | 50.262
2022-04-25 | 23:21 | 50.262
2022-04-25 | 23:21 | 50.265
2022-04-25 | 23:21 | 50.265
2022-04-25 | 23:21 | 50.267
2022-04-25 | 23:21 | 50.27
2022-04-25 | 23:21 | 50.272
2022-04-25 | 23:21 | 50.273
2022-04-25 | 23:21 | 50.275
2022-04-25 | 23:21 | 50.276
2022-04-25 | 23:22 | 50.278
2022-04-25 | 23:22 | 50.28
2022-04-25 | 23:22 | 50.281
2022-04-25 | 23:22 | 50.281
2022-04-25 | 23:22 | 50.28
2022-04-25 | 23:22 | 50.281
2022-04-25 | 23:22 | 50.281
2022-04-25 | 23:22 | 50.281
2022-04-25 | 23:22 | 50.282
2022-04-25 | 23:22 | 50.282
2022-04-25 | 23:22 | 50.28
2022-04-25 | 23:22 | 50.278
2022-04-25 | 23:22 | 50.277
2022-04-25 | 23:22 | 50.278
2022-04-25 | 23:22 | 50.281
2022-04-25 | 23:22 | 50.282
2022-04-25 | 23:22 | 50.285
2022-04-25 | 23:22 | 50.286
2022-04-25 | 23:22 | 50.288
2022-04-25 | 23:22 | 50.288
2022-04-25 | 23:22 | 50.287
2022-04-25 | 23:22 | 50.285
2022-04-25 | 23:22 | 50.285
2022-04-25 | 23:22 | 50.282
2022-04-25 | 23:22 | 50.282
2022-04-25 | 23:22 | 50.281
2022-04-25 | 23:22 | 50.281
2022-04-25 | 23:22 | 50.279
2022-04-25 | 23:22 | 50.278
2022-04-25 | 23:22 | 50.278
2022-04-25 | 23:22 | 50.277
2022-04-25 | 23:22 | 50.276
2022-04-25 | 23:22 | 50.274
2022-04-25 | 23:22 | 50.274
2022-04-25 | 23:22 | 50.272
2022-04-25 | 23:22 | 50.272
2022-04-25 | 23:22 | 50.271
2022-04-25 | 23:22 | 50.271
2022-04-25 | 23:22 | 50.271
2022-04-25 | 23:22 | 50.27
2022-04-25 | 23:22 | 50.272
2022-04-25 | 23:22 | 50.274
2022-04-25 | 23:22 | 50.276
2022-04-25 | 23:22 | 50.276
2022-04-25 | 23:22 | 50.275
2022-04-25 | 23:22 | 50.274
2022-04-25 | 23:22 | 50.275
2022-04-25 | 23:22 | 50.277
2022-04-25 | 23:22 | 50.276
2022-04-25 | 23:22 | 50.274
2022-04-25 | 23:22 | 50.273
2022-04-25 | 23:22 | 50.274
2022-04-25 | 23:22 | 50.274
2022-04-25 | 23:22 | 50.273
2022-04-25 | 23:22 | 50.272
2022-04-25 | 23:22 | 50.272
2022-04-25 | 23:22 | 50.272
2022-04-25 | 23:22 | 50.272
2022-04-25 | 23:22 | 50.273
2022-04-25 | 23:22 | 50.272
2022-04-25 | 23:22 | 50.273
2022-04-25 | 23:23 | 50.273
2022-04-25 | 23:23 | 50.273
2022-04-25 | 23:23 | 50.272
2022-04-25 | 23:23 | 50.269
2022-04-25 | 23:23 | 50.266
2022-04-25 | 23:23 | 50.265
2022-04-25 | 23:23 | 50.264
2022-04-25 | 23:23 | 50.26
2022-04-25 | 23:23 | 50.257
2022-04-25 | 23:23 | 50.255
2022-04-25 | 23:23 | 50.255
2022-04-25 | 23:23 | 50.254
2022-04-25 | 23:23 | 50.255
2022-04-25 | 23:23 | 50.256
2022-04-25 | 23:23 | 50.256
2022-04-25 | 23:23 | 50.258
2022-04-25 | 23:23 | 50.257
2022-04-25 | 23:23 | 50.256
2022-04-25 | 23:23 | 50.256
2022-04-25 | 23:23 | 50.258
2022-04-25 | 23:23 | 50.259
2022-04-25 | 23:23 | 50.26
2022-04-25 | 23:23 | 50.263
2022-04-25 | 23:23 | 50.261
2022-04-25 | 23:23 | 50.261
2022-04-25 | 23:23 | 50.261
2022-04-25 | 23:23 | 50.258
2022-04-25 | 23:23 | 50.254
2022-04-25 | 23:23 | 50.253
2022-04-25 | 23:23 | 50.251
2022-04-25 | 23:23 | 50.252
2022-04-25 | 23:23 | 50.252
2022-04-25 | 23:23 | 50.251
2022-04-25 | 23:23 | 50.251
2022-04-25 | 23:23 | 50.25
2022-04-25 | 23:23 | 50.25
2022-04-25 | 23:23 | 50.248
2022-04-25 | 23:23 | 50.248
2022-04-25 | 23:23 | 50.248
2022-04-25 | 23:23 | 50.247
2022-04-25 | 23:23 | 50.247
2022-04-25 | 23:23 | 50.247
2022-04-25 | 23:23 | 50.247
2022-04-25 | 23:23 | 50.247
2022-04-25 | 23:23 | 50.247
2022-04-25 | 23:23 | 50.246
2022-04-25 | 23:23 | 50.245
2022-04-25 | 23:23 | 50.246
2022-04-25 | 23:23 | 50.244
2022-04-25 | 23:23 | 50.243
2022-04-25 | 23:23 | 50.243
2022-04-25 | 23:23 | 50.244
2022-04-25 | 23:23 | 50.243
2022-04-25 | 23:23 | 50.244
2022-04-25 | 23:23 | 50.243
2022-04-25 | 23:23 | 50.241
2022-04-25 | 23:23 | 50.239
2022-04-25 | 23:23 | 50.237
2022-04-25 | 23:23 | 50.237
2022-04-25 | 23:24 | 50.236
2022-04-25 | 23:24 | 50.236
2022-04-25 | 23:24 | 50.235
2022-04-25 | 23:24 | 50.234
2022-04-25 | 23:24 | 50.232
2022-04-25 | 23:24 | 50.233
2022-04-25 | 23:24 | 50.233
2022-04-25 | 23:24 | 50.232
2022-04-25 | 23:24 | 50.232
2022-04-25 | 23:24 | 50.23
2022-04-25 | 23:24 | 50.23
2022-04-25 | 23:24 | 50.229
2022-04-25 | 23:24 | 50.228
2022-04-25 | 23:24 | 50.23
2022-04-25 | 23:24 | 50.232
2022-04-25 | 23:24 | 50.231
2022-04-25 | 23:24 | 50.231
2022-04-25 | 23:24 | 50.231
2022-04-25 | 23:24 | 50.231
2022-04-25 | 23:24 | 50.23
2022-04-25 | 23:24 | 50.229
2022-04-25 | 23:24 | 50.228
2022-04-25 | 23:24 | 50.226
2022-04-25 | 23:24 | 50.226
2022-04-25 | 23:24 | 50.225
2022-04-25 | 23:24 | 50.224
2022-04-25 | 23:24 | 50.224
2022-04-25 | 23:24 | 50.224
2022-04-25 | 23:24 | 50.223
2022-04-25 | 23:24 | 50.225
2022-04-25 | 23:24 | 50.225
2022-04-25 | 23:24 | 50.224
2022-04-25 | 23:24 | 50.222
2022-04-25 | 23:24 | 50.22
2022-04-25 | 23:24 | 50.22
2022-04-25 | 23:24 | 50.219
2022-04-25 | 23:24 | 50.217
2022-04-25 | 23:24 | 50.217
2022-04-25 | 23:24 | 50.217
2022-04-25 | 23:24 | 50.217
2022-04-25 | 23:24 | 50.215
2022-04-25 | 23:24 | 50.213
2022-04-25 | 23:24 | 50.212
2022-04-25 | 23:24 | 50.214
2022-04-25 | 23:24 | 50.215
2022-04-25 | 23:24 | 50.214
2022-04-25 | 23:24 | 50.211
2022-04-25 | 23:24 | 50.209
2022-04-25 | 23:24 | 50.208
2022-04-25 | 23:24 | 50.203
2022-04-25 | 23:24 | 50.199
2022-04-25 | 23:24 | 50.195
2022-04-25 | 23:24 | 50.194
2022-04-25 | 23:24 | 50.193
2022-04-25 | 23:24 | 50.191
2022-04-25 | 23:24 | 50.192
2022-04-25 | 23:24 | 50.192
2022-04-25 | 23:24 | 50.19
2022-04-25 | 23:24 | 50.19
2022-04-25 | 23:24 | 50.191
2022-04-25 | 23:24 | 50.189
2022-04-25 | 23:25 | 50.187
2022-04-25 | 23:25 | 50.185
2022-04-25 | 23:25 | 50.184
2022-04-25 | 23:25 | 50.181
2022-04-25 | 23:25 | 50.178
2022-04-25 | 23:25 | 50.177
2022-04-25 | 23:25 | 50.175
2022-04-25 | 23:25 | 50.172
2022-04-25 | 23:25 | 50.168
2022-04-25 | 23:25 | 50.165
2022-04-25 | 23:25 | 50.163
2022-04-25 | 23:25 | 50.161
2022-04-25 | 23:25 | 50.161
2022-04-25 | 23:25 | 50.161
2022-04-25 | 23:25 | 50.16
2022-04-25 | 23:25 | 50.159
2022-04-25 | 23:25 | 50.157
2022-04-25 | 23:25 | 50.156
2022-04-25 | 23:25 | 50.155
2022-04-25 | 23:25 | 50.153
2022-04-25 | 23:25 | 50.152
2022-04-25 | 23:25 | 50.151
2022-04-25 | 23:25 | 50.149
2022-04-25 | 23:25 | 50.146
2022-04-25 | 23:25 | 50.145
2022-04-25 | 23:25 | 50.144
2022-04-25 | 23:25 | 50.143
2022-04-25 | 23:25 | 50.143
2022-04-25 | 23:25 | 50.141
2022-04-25 | 23:25 | 50.138
2022-04-25 | 23:25 | 50.134
2022-04-25 | 23:25 | 50.129
2022-04-25 | 23:25 | 50.125
2022-04-25 | 23:25 | 50.121
2022-04-25 | 23:25 | 50.118
2022-04-25 | 23:25 | 50.118
2022-04-25 | 23:25 | 50.117
2022-04-25 | 23:25 | 50.116
2022-04-25 | 23:25 | 50.117
2022-04-25 | 23:25 | 50.118
2022-04-25 | 23:25 | 50.118
2022-04-25 | 23:25 | 50.12
2022-04-25 | 23:25 | 50.121
2022-04-25 | 23:25 | 50.123
2022-04-25 | 23:25 | 50.124
2022-04-25 | 23:25 | 50.125
2022-04-25 | 23:25 | 50.124
2022-04-25 | 23:25 | 50.123
2022-04-25 | 23:25 | 50.124
2022-04-25 | 23:25 | 50.124
2022-04-25 | 23:25 | 50.126
2022-04-25 | 23:25 | 50.127
2022-04-25 | 23:25 | 50.128
2022-04-25 | 23:25 | 50.13
2022-04-25 | 23:25 | 50.13
2022-04-25 | 23:25 | 50.129
2022-04-25 | 23:25 | 50.128
2022-04-25 | 23:25 | 50.129
2022-04-25 | 23:25 | 50.129
2022-04-25 | 23:26 | 50.127
2022-04-25 | 23:26 | 50.125
2022-04-25 | 23:26 | 50.123
2022-04-25 | 23:26 | 50.123
2022-04-25 | 23:26 | 50.126
2022-04-25 | 23:26 | 50.129
2022-04-25 | 23:26 | 50.129
2022-04-25 | 23:26 | 50.13
2022-04-25 | 23:26 | 50.13
2022-04-25 | 23:26 | 50.134
2022-04-25 | 23:26 | 50.136
2022-04-25 | 23:26 | 50.136
2022-04-25 | 23:26 | 50.137
2022-04-25 | 23:26 | 50.137
2022-04-25 | 23:26 | 50.139
2022-04-25 | 23:26 | 50.139
2022-04-25 | 23:26 | 50.138
2022-04-25 | 23:26 | 50.139
2022-04-25 | 23:26 | 50.137
2022-04-25 | 23:26 | 50.136
2022-04-25 | 23:26 | 50.133
2022-04-25 | 23:26 | 50.132
2022-04-25 | 23:26 | 50.129
2022-04-25 | 23:26 | 50.126
2022-04-25 | 23:26 | 50.122
2022-04-25 | 23:26 | 50.12
2022-04-25 | 23:26 | 50.118
2022-04-25 | 23:26 | 50.118
2022-04-25 | 23:26 | 50.118
2022-04-25 | 23:26 | 50.118
2022-04-25 | 23:26 | 50.118
2022-04-25 | 23:26 | 50.119
2022-04-25 | 23:26 | 50.118
2022-04-25 | 23:26 | 50.119
2022-04-25 | 23:26 | 50.122
2022-04-25 | 23:26 | 50.122
2022-04-25 | 23:26 | 50.123
2022-04-25 | 23:26 | 50.124
2022-04-25 | 23:26 | 50.122
2022-04-25 | 23:26 | 50.122
2022-04-25 | 23:26 | 50.122
2022-04-25 | 23:26 | 50.124
2022-04-25 | 23:26 | 50.124
2022-04-25 | 23:26 | 50.122
2022-04-25 | 23:26 | 50.123
2022-04-25 | 23:26 | 50.121
2022-04-25 | 23:26 | 50.117
2022-04-25 | 23:26 | 50.114
2022-04-25 | 23:26 | 50.112
2022-04-25 | 23:26 | 50.107
2022-04-25 | 23:26 | 50.107
2022-04-25 | 23:26 | 50.106
2022-04-25 | 23:26 | 50.108
2022-04-25 | 23:26 | 50.108
2022-04-25 | 23:26 | 50.11
2022-04-25 | 23:26 | 50.108
2022-04-25 | 23:26 | 50.106
2022-04-25 | 23:26 | 50.106
2022-04-25 | 23:26 | 50.108
2022-04-25 | 23:26 | 50.109
2022-04-25 | 23:26 | 50.109
2022-04-25 | 23:27 | 50.109
2022-04-25 | 23:27 | 50.107
2022-04-25 | 23:27 | 50.106
2022-04-25 | 23:27 | 50.104
2022-04-25 | 23:27 | 50.103
2022-04-25 | 23:27 | 50.101
2022-04-25 | 23:27 | 50.099
2022-04-25 | 23:27 | 50.098
2022-04-25 | 23:27 | 50.095
2022-04-25 | 23:27 | 50.092
2022-04-25 | 23:27 | 50.091
2022-04-25 | 23:27 | 50.088
2022-04-25 | 23:27 | 50.088
2022-04-25 | 23:27 | 50.087
2022-04-25 | 23:27 | 50.085
2022-04-25 | 23:27 | 50.082
2022-04-25 | 23:27 | 50.08
2022-04-25 | 23:27 | 50.079
2022-04-25 | 23:27 | 50.078
2022-04-25 | 23:27 | 50.077
2022-04-25 | 23:27 | 50.078
2022-04-25 | 23:27 | 50.078
2022-04-25 | 23:27 | 50.08
2022-04-25 | 23:27 | 50.081
2022-04-25 | 23:27 | 50.083
2022-04-25 | 23:27 | 50.087
2022-04-25 | 23:27 | 50.089
2022-04-25 | 23:27 | 50.09
2022-04-25 | 23:27 | 50.093
2022-04-25 | 23:27 | 50.093
2022-04-25 | 23:27 | 50.093
2022-04-25 | 23:27 | 50.093
2022-04-25 | 23:27 | 50.094
2022-04-25 | 23:27 | 50.095
2022-04-25 | 23:27 | 50.096
2022-04-25 | 23:27 | 50.097
2022-04-25 | 23:27 | 50.096
2022-04-25 | 23:27 | 50.094
2022-04-25 | 23:27 | 50.092
2022-04-25 | 23:27 | 50.092
2022-04-25 | 23:27 | 50.093
2022-04-25 | 23:27 | 50.094
2022-04-25 | 23:27 | 50.095
2022-04-25 | 23:27 | 50.095
2022-04-25 | 23:27 | 50.095
2022-04-25 | 23:27 | 50.096
2022-04-25 | 23:27 | 50.098
2022-04-25 | 23:27 | 50.099
2022-04-25 | 23:27 | 50.099
2022-04-25 | 23:27 | 50.101
2022-04-25 | 23:27 | 50.101
2022-04-25 | 23:27 | 50.101
2022-04-25 | 23:27 | 50.101
2022-04-25 | 23:27 | 50.101
2022-04-25 | 23:27 | 50.1
2022-04-25 | 23:27 | 50.102
2022-04-25 | 23:27 | 50.103
2022-04-25 | 23:27 | 50.104
2022-04-25 | 23:27 | 50.105
2022-04-25 | 23:27 | 50.108
2022-04-25 | 23:28 | 50.109
2022-04-25 | 23:28 | 50.111
2022-04-25 | 23:28 | 50.111
2022-04-25 | 23:28 | 50.111
2022-04-25 | 23:28 | 50.111
2022-04-25 | 23:28 | 50.111
2022-04-25 | 23:28 | 50.111
2022-04-25 | 23:28 | 50.11
2022-04-25 | 23:28 | 50.11
2022-04-25 | 23:28 | 50.109
2022-04-25 | 23:28 | 50.109
2022-04-25 | 23:28 | 50.108
2022-04-25 | 23:28 | 50.108
2022-04-25 | 23:28 | 50.109
2022-04-25 | 23:28 | 50.11
2022-04-25 | 23:28 | 50.11
2022-04-25 | 23:28 | 50.11
2022-04-25 | 23:28 | 50.111
2022-04-25 | 23:28 | 50.112
2022-04-25 | 23:28 | 50.113
2022-04-25 | 23:28 | 50.113
2022-04-25 | 23:28 | 50.114
2022-04-25 | 23:28 | 50.113
2022-04-25 | 23:28 | 50.114
2022-04-25 | 23:28 | 50.117
2022-04-25 | 23:28 | 50.117
2022-04-25 | 23:28 | 50.118
2022-04-25 | 23:28 | 50.117
2022-04-25 | 23:28 | 50.116
2022-04-25 | 23:28 | 50.115
2022-04-25 | 23:28 | 50.112
2022-04-25 | 23:28 | 50.11
2022-04-25 | 23:28 | 50.106
2022-04-25 | 23:28 | 50.104
2022-04-25 | 23:28 | 50.104
2022-04-25 | 23:28 | 50.104
2022-04-25 | 23:28 | 50.104
2022-04-25 | 23:28 | 50.103
2022-04-25 | 23:28 | 50.103
2022-04-25 | 23:28 | 50.104
2022-04-25 | 23:28 | 50.104
2022-04-25 | 23:28 | 50.104
2022-04-25 | 23:28 | 50.107
2022-04-25 | 23:28 | 50.11
2022-04-25 | 23:28 | 50.116
2022-04-25 | 23:28 | 50.12
2022-04-25 | 23:28 | 50.126
2022-04-25 | 23:28 | 50.133
2022-04-25 | 23:28 | 50.134
2022-04-25 | 23:28 | 50.135
2022-04-25 | 23:28 | 50.134
2022-04-25 | 23:28 | 50.133
2022-04-25 | 23:28 | 50.131
2022-04-25 | 23:28 | 50.131
2022-04-25 | 23:28 | 50.13
2022-04-25 | 23:28 | 50.126
2022-04-25 | 23:28 | 50.125
2022-04-25 | 23:28 | 50.124
2022-04-25 | 23:28 | 50.124
2022-04-25 | 23:28 | 50.121
2022-04-25 | 23:29 | 50.121
2022-04-25 | 23:29 | 50.121
2022-04-25 | 23:29 | 50.119
2022-04-25 | 23:29 | 50.119
2022-04-25 | 23:29 | 50.118
2022-04-25 | 23:29 | 50.118
2022-04-25 | 23:29 | 50.116
2022-04-25 | 23:29 | 50.116
2022-04-25 | 23:29 | 50.114
2022-04-25 | 23:29 | 50.114
2022-04-25 | 23:29 | 50.115
2022-04-25 | 23:29 | 50.114
2022-04-25 | 23:29 | 50.114
2022-04-25 | 23:29 | 50.116
2022-04-25 | 23:29 | 50.118
2022-04-25 | 23:29 | 50.12
2022-04-25 | 23:29 | 50.122
2022-04-25 | 23:29 | 50.124
2022-04-25 | 23:29 | 50.128
2022-04-25 | 23:29 | 50.132
2022-04-25 | 23:29 | 50.132
2022-04-25 | 23:29 | 50.134
2022-04-25 | 23:29 | 50.136
2022-04-25 | 23:29 | 50.136
2022-04-25 | 23:29 | 50.136
2022-04-25 | 23:29 | 50.134
2022-04-25 | 23:29 | 50.133
2022-04-25 | 23:29 | 50.131
2022-04-25 | 23:29 | 50.13
2022-04-25 | 23:29 | 50.128
2022-04-25 | 23:29 | 50.126
2022-04-25 | 23:29 | 50.125
2022-04-25 | 23:29 | 50.123
2022-04-25 | 23:29 | 50.123
2022-04-25 | 23:29 | 50.127
2022-04-25 | 23:29 | 50.128
2022-04-25 | 23:29 | 50.129
2022-04-25 | 23:29 | 50.131
2022-04-25 | 23:29 | 50.131
2022-04-25 | 23:29 | 50.132
2022-04-25 | 23:29 | 50.133
2022-04-25 | 23:29 | 50.133
2022-04-25 | 23:29 | 50.133
2022-04-25 | 23:29 | 50.132
2022-04-25 | 23:29 | 50.131
2022-04-25 | 23:29 | 50.132
2022-04-25 | 23:29 | 50.13
2022-04-25 | 23:29 | 50.129
2022-04-25 | 23:29 | 50.128
2022-04-25 | 23:29 | 50.128
2022-04-25 | 23:29 | 50.129
2022-04-25 | 23:29 | 50.128
2022-04-25 | 23:29 | 50.127
2022-04-25 | 23:29 | 50.127
2022-04-25 | 23:29 | 50.128
2022-04-25 | 23:29 | 50.129
2022-04-25 | 23:29 | 50.13
2022-04-25 | 23:29 | 50.131
2022-04-25 | 23:29 | 50.132
2022-04-25 | 23:30 | 50.133
2022-04-25 | 23:30 | 50.133
2022-04-25 | 23:30 | 50.133
2022-04-25 | 23:30 | 50.131
2022-04-25 | 23:30 | 50.13
2022-04-25 | 23:30 | 50.127
2022-04-25 | 23:30 | 50.126
2022-04-25 | 23:30 | 50.125
2022-04-25 | 23:30 | 50.125
2022-04-25 | 23:30 | 50.125
2022-04-25 | 23:30 | 50.127
2022-04-25 | 23:30 | 50.127
2022-04-25 | 23:30 | 50.127
2022-04-25 | 23:30 | 50.128
2022-04-25 | 23:30 | 50.13
2022-04-25 | 23:30 | 50.129
2022-04-25 | 23:30 | 50.129
2022-04-25 | 23:30 | 50.128
2022-04-25 | 23:30 | 50.128
2022-04-25 | 23:30 | 50.129
2022-04-25 | 23:30 | 50.128
2022-04-25 | 23:30 | 50.129
2022-04-25 | 23:30 | 50.129
2022-04-25 | 23:30 | 50.129
2022-04-25 | 23:30 | 50.129
2022-04-25 | 23:30 | 50.129
2022-04-25 | 23:30 | 50.128
2022-04-25 | 23:30 | 50.124
2022-04-25 | 23:30 | 50.118
2022-04-25 | 23:30 | 50.114
2022-04-25 | 23:30 | 50.11
2022-04-25 | 23:30 | 50.104
2022-04-25 | 23:30 | 50.099
2022-04-25 | 23:30 | 50.095
2022-04-25 | 23:30 | 50.089
2022-04-25 | 23:30 | 50.085
2022-04-25 | 23:30 | 50.08
2022-04-25 | 23:30 | 50.075
2022-04-25 | 23:30 | 50.07
2022-04-25 | 23:30 | 50.066
2022-04-25 | 23:30 | 50.063
2022-04-25 | 23:30 | 50.061
2022-04-25 | 23:30 | 50.06
2022-04-25 | 23:30 | 50.059
2022-04-25 | 23:30 | 50.06
2022-04-25 | 23:30 | 50.063
2022-04-25 | 23:30 | 50.065
2022-04-25 | 23:30 | 50.067
2022-04-25 | 23:30 | 50.067
2022-04-25 | 23:30 | 50.067
2022-04-25 | 23:30 | 50.067
2022-04-25 | 23:30 | 50.068
2022-04-25 | 23:30 | 50.065
2022-04-25 | 23:30 | 50.064
2022-04-25 | 23:30 | 50.062
2022-04-25 | 23:30 | 50.06
2022-04-25 | 23:30 | 50.056
2022-04-25 | 23:30 | 50.054
2022-04-25 | 23:30 | 50.051
2022-04-25 | 23:30 | 50.049
2022-04-25 | 23:30 | 50.048
2022-04-25 | 23:31 | 50.047
2022-04-25 | 23:31 | 50.048
2022-04-25 | 23:31 | 50.048
2022-04-25 | 23:31 | 50.049
2022-04-25 | 23:31 | 50.051
2022-04-25 | 23:31 | 50.051
2022-04-25 | 23:31 | 50.051
2022-04-25 | 23:31 | 50.05
2022-04-25 | 23:31 | 50.051
2022-04-25 | 23:31 | 50.05
2022-04-25 | 23:31 | 50.051
2022-04-25 | 23:31 | 50.05
2022-04-25 | 23:31 | 50.051
2022-04-25 | 23:31 | 50.05
2022-04-25 | 23:31 | 50.051
2022-04-25 | 23:31 | 50.051
2022-04-25 | 23:31 | 50.051
2022-04-25 | 23:31 | 50.051
2022-04-25 | 23:31 | 50.051
2022-04-25 | 23:31 | 50.051
2022-04-25 | 23:31 | 50.051
2022-04-25 | 23:31 | 50.05
2022-04-25 | 23:31 | 50.051
2022-04-25 | 23:31 | 50.051
2022-04-25 | 23:31 | 50.05
2022-04-25 | 23:31 | 50.05
2022-04-25 | 23:31 | 50.05
2022-04-25 | 23:31 | 50.049
2022-04-25 | 23:31 | 50.049
2022-04-25 | 23:31 | 50.049
2022-04-25 | 23:31 | 50.05
2022-04-25 | 23:31 | 50.048
2022-04-25 | 23:31 | 50.048
2022-04-25 | 23:31 | 50.048
2022-04-25 | 23:31 | 50.049
2022-04-25 | 23:31 | 50.049
2022-04-25 | 23:31 | 50.047
2022-04-25 | 23:31 | 50.046
2022-04-25 | 23:31 | 50.044
2022-04-25 | 23:31 | 50.045
2022-04-25 | 23:31 | 50.046
2022-04-25 | 23:31 | 50.047
2022-04-25 | 23:31 | 50.048
2022-04-25 | 23:31 | 50.049
2022-04-25 | 23:31 | 50.049
2022-04-25 | 23:31 | 50.049
2022-04-25 | 23:31 | 50.05
2022-04-25 | 23:31 | 50.048
2022-04-25 | 23:31 | 50.05
2022-04-25 | 23:31 | 50.049
2022-04-25 | 23:31 | 50.05
2022-04-25 | 23:31 | 50.05
2022-04-25 | 23:31 | 50.051
2022-04-25 | 23:31 | 50.051
2022-04-25 | 23:31 | 50.051
2022-04-25 | 23:31 | 50.05
2022-04-25 | 23:31 | 50.05
2022-04-25 | 23:31 | 50.047
2022-04-25 | 23:31 | 50.045
2022-04-25 | 23:31 | 50.044
2022-04-25 | 23:32 | 50.044
2022-04-25 | 23:32 | 50.044
2022-04-25 | 23:32 | 50.043
2022-04-25 | 23:32 | 50.043
2022-04-25 | 23:32 | 50.044
2022-04-25 | 23:32 | 50.042
2022-04-25 | 23:32 | 50.042
2022-04-25 | 23:32 | 50.044
2022-04-25 | 23:32 | 50.045
2022-04-25 | 23:32 | 50.045
2022-04-25 | 23:32 | 50.045
2022-04-25 | 23:32 | 50.046
2022-04-25 | 23:32 | 50.046
2022-04-25 | 23:32 | 50.046
2022-04-25 | 23:32 | 50.045
2022-04-25 | 23:32 | 50.043
2022-04-25 | 23:32 | 50.043
2022-04-25 | 23:32 | 50.043
2022-04-25 | 23:32 | 50.043
2022-04-25 | 23:32 | 50.043
2022-04-25 | 23:32 | 50.043
2022-04-25 | 23:32 | 50.044
2022-04-25 | 23:32 | 50.045
2022-04-25 | 23:32 | 50.048
2022-04-25 | 23:32 | 50.051
2022-04-25 | 23:32 | 50.052
2022-04-25 | 23:32 | 50.052
2022-04-25 | 23:32 | 50.051
2022-04-25 | 23:32 | 50.05
2022-04-25 | 23:32 | 50.049
2022-04-25 | 23:32 | 50.048
2022-04-25 | 23:32 | 50.046
2022-04-25 | 23:32 | 50.044
2022-04-25 | 23:32 | 50.041
2022-04-25 | 23:32 | 50.039
2022-04-25 | 23:32 | 50.036
2022-04-25 | 23:32 | 50.035
2022-04-25 | 23:32 | 50.035
2022-04-25 | 23:32 | 50.036
2022-04-25 | 23:32 | 50.037
2022-04-25 | 23:32 | 50.039
2022-04-25 | 23:32 | 50.04
2022-04-25 | 23:32 | 50.041
2022-04-25 | 23:32 | 50.041
2022-04-25 | 23:32 | 50.041
2022-04-25 | 23:32 | 50.042
2022-04-25 | 23:32 | 50.045
2022-04-25 | 23:32 | 50.046
2022-04-25 | 23:32 | 50.048
2022-04-25 | 23:32 | 50.048
2022-04-25 | 23:32 | 50.049
2022-04-25 | 23:32 | 50.048
2022-04-25 | 23:32 | 50.047
2022-04-25 | 23:32 | 50.046
2022-04-25 | 23:32 | 50.046
2022-04-25 | 23:32 | 50.046
2022-04-25 | 23:32 | 50.047
2022-04-25 | 23:32 | 50.049
2022-04-25 | 23:32 | 50.049
2022-04-25 | 23:32 | 50.05
2022-04-25 | 23:33 | 50.051
2022-04-25 | 23:33 | 50.049
2022-04-25 | 23:33 | 50.048
2022-04-25 | 23:33 | 50.048
2022-04-25 | 23:33 | 50.046
2022-04-25 | 23:33 | 50.044
2022-04-25 | 23:33 | 50.043
2022-04-25 | 23:33 | 50.041
2022-04-25 | 23:33 | 50.041
2022-04-25 | 23:33 | 50.043
2022-04-25 | 23:33 | 50.045
2022-04-25 | 23:33 | 50.047
2022-04-25 | 23:33 | 50.048
2022-04-25 | 23:33 | 50.05
2022-04-25 | 23:33 | 50.052
2022-04-25 | 23:33 | 50.053
2022-04-25 | 23:33 | 50.054
2022-04-25 | 23:33 | 50.055
2022-04-25 | 23:33 | 50.056
2022-04-25 | 23:33 | 50.055
2022-04-25 | 23:33 | 50.053
2022-04-25 | 23:33 | 50.053
2022-04-25 | 23:33 | 50.05
2022-04-25 | 23:33 | 50.05
2022-04-25 | 23:33 | 50.051
2022-04-25 | 23:33 | 50.051
2022-04-25 | 23:33 | 50.052
2022-04-25 | 23:33 | 50.051
2022-04-25 | 23:33 | 50.052
2022-04-25 | 23:33 | 50.052
2022-04-25 | 23:33 | 50.052
2022-04-25 | 23:33 | 50.053
2022-04-25 | 23:33 | 50.054
2022-04-25 | 23:33 | 50.056
2022-04-25 | 23:33 | 50.057
2022-04-25 | 23:33 | 50.057
2022-04-25 | 23:33 | 50.057
2022-04-25 | 23:33 | 50.057
2022-04-25 | 23:33 | 50.058
2022-04-25 | 23:33 | 50.06
2022-04-25 | 23:33 | 50.062
2022-04-25 | 23:33 | 50.063
2022-04-25 | 23:33 | 50.063
2022-04-25 | 23:33 | 50.063
2022-04-25 | 23:33 | 50.063
2022-04-25 | 23:33 | 50.062
2022-04-25 | 23:33 | 50.062
2022-04-25 | 23:33 | 50.063
2022-04-25 | 23:33 | 50.064
2022-04-25 | 23:33 | 50.064
2022-04-25 | 23:33 | 50.065
2022-04-25 | 23:33 | 50.066
2022-04-25 | 23:33 | 50.066
2022-04-25 | 23:33 | 50.065
2022-04-25 | 23:33 | 50.063
2022-04-25 | 23:33 | 50.061
2022-04-25 | 23:33 | 50.06
2022-04-25 | 23:33 | 50.059
2022-04-25 | 23:33 | 50.057
2022-04-25 | 23:34 | 50.057
2022-04-25 | 23:34 | 50.057
2022-04-25 | 23:34 | 50.057
2022-04-25 | 23:34 | 50.058
2022-04-25 | 23:34 | 50.058
2022-04-25 | 23:34 | 50.058
2022-04-25 | 23:34 | 50.056
2022-04-25 | 23:34 | 50.056
2022-04-25 | 23:34 | 50.056
2022-04-25 | 23:34 | 50.055
2022-04-25 | 23:34 | 50.055
2022-04-25 | 23:34 | 50.056
2022-04-25 | 23:34 | 50.057
2022-04-25 | 23:34 | 50.056
2022-04-25 | 23:34 | 50.057
2022-04-25 | 23:34 | 50.057
2022-04-25 | 23:34 | 50.058
2022-04-25 | 23:34 | 50.059
2022-04-25 | 23:34 | 50.061
2022-04-25 | 23:34 | 50.061
2022-04-25 | 23:34 | 50.062
2022-04-25 | 23:34 | 50.06
2022-04-25 | 23:34 | 50.058
2022-04-25 | 23:34 | 50.058
2022-04-25 | 23:34 | 50.057
2022-04-25 | 23:34 | 50.056
2022-04-25 | 23:34 | 50.055
2022-04-25 | 23:34 | 50.052
2022-04-25 | 23:34 | 50.052
2022-04-25 | 23:34 | 50.049
2022-04-25 | 23:34 | 50.047
2022-04-25 | 23:34 | 50.044
2022-04-25 | 23:34 | 50.04
2022-04-25 | 23:34 | 50.038
2022-04-25 | 23:34 | 50.036
2022-04-25 | 23:34 | 50.035
2022-04-25 | 23:34 | 50.032
2022-04-25 | 23:34 | 50.033
2022-04-25 | 23:34 | 50.031
2022-04-25 | 23:34 | 50.032
2022-04-25 | 23:34 | 50.032
2022-04-25 | 23:34 | 50.033
2022-04-25 | 23:34 | 50.034
2022-04-25 | 23:34 | 50.037
2022-04-25 | 23:34 | 50.038
2022-04-25 | 23:34 | 50.038
2022-04-25 | 23:34 | 50.038
2022-04-25 | 23:34 | 50.036
2022-04-25 | 23:34 | 50.034
2022-04-25 | 23:34 | 50.032
2022-04-25 | 23:34 | 50.032
2022-04-25 | 23:34 | 50.033
2022-04-25 | 23:34 | 50.033
2022-04-25 | 23:34 | 50.035
2022-04-25 | 23:34 | 50.035
2022-04-25 | 23:34 | 50.037
2022-04-25 | 23:34 | 50.038
2022-04-25 | 23:34 | 50.04
2022-04-25 | 23:34 | 50.041
2022-04-25 | 23:34 | 50.041
2022-04-25 | 23:34 | 50.04
2022-04-25 | 23:35 | 50.04
2022-04-25 | 23:35 | 50.04
2022-04-25 | 23:35 | 50.038
2022-04-25 | 23:35 | 50.038
2022-04-25 | 23:35 | 50.039
2022-04-25 | 23:35 | 50.039
2022-04-25 | 23:35 | 50.038
2022-04-25 | 23:35 | 50.038
2022-04-25 | 23:35 | 50.039
2022-04-25 | 23:35 | 50.039
2022-04-25 | 23:35 | 50.04
2022-04-25 | 23:35 | 50.041
2022-04-25 | 23:35 | 50.042
2022-04-25 | 23:35 | 50.043
2022-04-25 | 23:35 | 50.042
2022-04-25 | 23:35 | 50.041
2022-04-25 | 23:35 | 50.04
2022-04-25 | 23:35 | 50.039
2022-04-25 | 23:35 | 50.04
2022-04-25 | 23:35 | 50.04
2022-04-25 | 23:35 | 50.04
2022-04-25 | 23:35 | 50.039
2022-04-25 | 23:35 | 50.039
2022-04-25 | 23:35 | 50.039
2022-04-25 | 23:35 | 50.039
2022-04-25 | 23:35 | 50.039
2022-04-25 | 23:35 | 50.04
2022-04-25 | 23:35 | 50.042
2022-04-25 | 23:35 | 50.042
2022-04-25 | 23:35 | 50.042
2022-04-25 | 23:35 | 50.041
2022-04-25 | 23:35 | 50.04
2022-04-25 | 23:35 | 50.04
2022-04-25 | 23:35 | 50.039
2022-04-25 | 23:35 | 50.037
2022-04-25 | 23:35 | 50.035
2022-04-25 | 23:35 | 50.033
2022-04-25 | 23:35 | 50.031
2022-04-25 | 23:35 | 50.028
2022-04-25 | 23:35 | 50.028
2022-04-25 | 23:35 | 50.027
2022-04-25 | 23:35 | 50.027
2022-04-25 | 23:35 | 50.027
2022-04-25 | 23:35 | 50.026
2022-04-25 | 23:35 | 50.027
2022-04-25 | 23:35 | 50.025
2022-04-25 | 23:35 | 50.024
2022-04-25 | 23:35 | 50.024
2022-04-25 | 23:35 | 50.023
2022-04-25 | 23:35 | 50.024
2022-04-25 | 23:35 | 50.024
2022-04-25 | 23:35 | 50.025
2022-04-25 | 23:35 | 50.025
2022-04-25 | 23:35 | 50.025
2022-04-25 | 23:35 | 50.023
2022-04-25 | 23:35 | 50.023
2022-04-25 | 23:35 | 50.023
2022-04-25 | 23:35 | 50.023
2022-04-25 | 23:35 | 50.023
2022-04-25 | 23:35 | 50.023
2022-04-25 | 23:36 | 50.022
2022-04-25 | 23:36 | 50.021
2022-04-25 | 23:36 | 50.02
2022-04-25 | 23:36 | 50.019
2022-04-25 | 23:36 | 50.017
2022-04-25 | 23:36 | 50.017
2022-04-25 | 23:36 | 50.017
2022-04-25 | 23:36 | 50.017
2022-04-25 | 23:36 | 50.017
2022-04-25 | 23:36 | 50.018
2022-04-25 | 23:36 | 50.017
2022-04-25 | 23:36 | 50.017
2022-04-25 | 23:36 | 50.016
2022-04-25 | 23:36 | 50.015
2022-04-25 | 23:36 | 50.016
2022-04-25 | 23:36 | 50.016
2022-04-25 | 23:36 | 50.016
2022-04-25 | 23:36 | 50.016
2022-04-25 | 23:36 | 50.015
2022-04-25 | 23:36 | 50.015
2022-04-25 | 23:36 | 50.015
2022-04-25 | 23:36 | 50.015
2022-04-25 | 23:36 | 50.014
2022-04-25 | 23:36 | 50.013
2022-04-25 | 23:36 | 50.013
2022-04-25 | 23:36 | 50.011
2022-04-25 | 23:36 | 50.008
2022-04-25 | 23:36 | 50.006
2022-04-25 | 23:36 | 50.004
2022-04-25 | 23:36 | 50.002
2022-04-25 | 23:36 | 49.998
2022-04-25 | 23:36 | 49.993
2022-04-25 | 23:36 | 49.991
2022-04-25 | 23:36 | 49.99
2022-04-25 | 23:36 | 49.988
2022-04-25 | 23:36 | 49.986
2022-04-25 | 23:36 | 49.984
2022-04-25 | 23:36 | 49.985
2022-04-25 | 23:36 | 49.986
2022-04-25 | 23:36 | 49.988
2022-04-25 | 23:36 | 49.989
2022-04-25 | 23:36 | 49.99
2022-04-25 | 23:36 | 49.99
2022-04-25 | 23:36 | 49.991
2022-04-25 | 23:36 | 49.99
2022-04-25 | 23:36 | 49.99
2022-04-25 | 23:36 | 49.99
2022-04-25 | 23:36 | 49.989
2022-04-25 | 23:36 | 49.988
2022-04-25 | 23:36 | 49.988
2022-04-25 | 23:36 | 49.989
2022-04-25 | 23:36 | 49.989
2022-04-25 | 23:36 | 49.99
2022-04-25 | 23:36 | 49.991
2022-04-25 | 23:36 | 49.991
2022-04-25 | 23:36 | 49.993
2022-04-25 | 23:36 | 49.994
2022-04-25 | 23:36 | 49.995
2022-04-25 | 23:36 | 49.996
2022-04-25 | 23:36 | 49.995
2022-04-25 | 23:37 | 49.994
2022-04-25 | 23:37 | 49.994
2022-04-25 | 23:37 | 49.994
2022-04-25 | 23:37 | 49.995
2022-04-25 | 23:37 | 49.995
2022-04-25 | 23:37 | 49.995
2022-04-25 | 23:37 | 49.996
2022-04-25 | 23:37 | 49.995
2022-04-25 | 23:37 | 49.995
2022-04-25 | 23:37 | 49.996
2022-04-25 | 23:37 | 49.997
2022-04-25 | 23:37 | 49.998
2022-04-25 | 23:37 | 49.999
2022-04-25 | 23:37 | 50.001
2022-04-25 | 23:37 | 50.002
2022-04-25 | 23:37 | 50.004
2022-04-25 | 23:37 | 50.005
2022-04-25 | 23:37 | 50.007
2022-04-25 | 23:37 | 50.008
2022-04-25 | 23:37 | 50.01
2022-04-25 | 23:37 | 50.009
2022-04-25 | 23:37 | 50.009
2022-04-25 | 23:37 | 50.007
2022-04-25 | 23:37 | 50.007
2022-04-25 | 23:37 | 50.006
2022-04-25 | 23:37 | 50.005
2022-04-25 | 23:37 | 50.005
2022-04-25 | 23:37 | 50.004
2022-04-25 | 23:37 | 50.004
2022-04-25 | 23:37 | 50.002

## 20220428-1
In GMT
Date | Time | Freq
2022-04-28 | 8:09 | 49.929
2022-04-28 | 8:09 | 49.929
2022-04-28 | 8:09 | 49.93
2022-04-28 | 8:09 | 49.931
2022-04-28 | 8:09 | 49.933
2022-04-28 | 8:09 | 49.934
2022-04-28 | 8:09 | 49.936
2022-04-28 | 8:09 | 49.937
2022-04-28 | 8:09 | 49.938
2022-04-28 | 8:09 | 49.937
2022-04-28 | 8:09 | 49.937
2022-04-28 | 8:09 | 49.935
2022-04-28 | 8:09 | 49.936
2022-04-28 | 8:09 | 49.934
2022-04-28 | 8:09 | 49.935
2022-04-28 | 8:09 | 49.933
2022-04-28 | 8:09 | 49.932
2022-04-28 | 8:09 | 49.93
2022-04-28 | 8:09 | 49.928
2022-04-28 | 8:09 | 49.926
2022-04-28 | 8:09 | 49.926
2022-04-28 | 8:09 | 49.928
2022-04-28 | 8:09 | 49.928
2022-04-28 | 8:09 | 49.929
2022-04-28 | 8:09 | 49.932
2022-04-28 | 8:09 | 49.934
2022-04-28 | 8:09 | 49.938
2022-04-28 | 8:09 | 49.938
2022-04-28 | 8:09 | 49.943
2022-04-28 | 8:09 | 49.943
2022-04-28 | 8:10 | 49.945
2022-04-28 | 8:10 | 49.946
2022-04-28 | 8:10 | 49.945
2022-04-28 | 8:10 | 49.942
2022-04-28 | 8:10 | 49.939
2022-04-28 | 8:10 | 49.937
2022-04-28 | 8:10 | 49.935
2022-04-28 | 8:10 | 49.935
2022-04-28 | 8:10 | 49.936
2022-04-28 | 8:10 | 49.936
2022-04-28 | 8:10 | 49.937
2022-04-28 | 8:10 | 49.936
2022-04-28 | 8:10 | 49.936
2022-04-28 | 8:10 | 49.933
2022-04-28 | 8:10 | 49.931
2022-04-28 | 8:10 | 49.93
2022-04-28 | 8:10 | 49.931
2022-04-28 | 8:10 | 49.932
2022-04-28 | 8:10 | 49.932
2022-04-28 | 8:10 | 49.933
2022-04-28 | 8:10 | 49.934
2022-04-28 | 8:10 | 49.936
2022-04-28 | 8:10 | 49.938
2022-04-28 | 8:10 | 49.939
2022-04-28 | 8:10 | 49.94
2022-04-28 | 8:10 | 49.941
2022-04-28 | 8:10 | 49.941
2022-04-28 | 8:10 | 49.942
2022-04-28 | 8:10 | 49.942
2022-04-28 | 8:10 | 49.941
2022-04-28 | 8:10 | 49.939
2022-04-28 | 8:10 | 49.935
2022-04-28 | 8:10 | 49.931
2022-04-28 | 8:10 | 49.928
2022-04-28 | 8:10 | 49.925
2022-04-28 | 8:10 | 49.921
2022-04-28 | 8:10 | 49.917
2022-04-28 | 8:10 | 49.913
2022-04-28 | 8:10 | 49.909
2022-04-28 | 8:10 | 49.906
2022-04-28 | 8:10 | 49.88
2022-04-28 | 8:10 | 49.828
2022-04-28 | 8:10 | 49.781
2022-04-28 | 8:10 | 49.742
2022-04-28 | 8:10 | 49.711
2022-04-28 | 8:10 | 49.69
2022-04-28 | 8:10 | 49.678
2022-04-28 | 8:10 | 49.671
2022-04-28 | 8:10 | 49.664
2022-04-28 | 8:10 | 49.662
2022-04-28 | 8:10 | 49.661
2022-04-28 | 8:10 | 49.661
2022-04-28 | 8:10 | 49.661
2022-04-28 | 8:10 | 49.663
2022-04-28 | 8:10 | 49.664
2022-04-28 | 8:10 | 49.667
2022-04-28 | 8:10 | 49.668
2022-04-28 | 8:10 | 49.67
2022-04-28 | 8:10 | 49.671
2022-04-28 | 8:10 | 49.673
2022-04-28 | 8:10 | 49.677
2022-04-28 | 8:11 | 49.68
2022-04-28 | 8:11 | 49.683
2022-04-28 | 8:11 | 49.687
2022-04-28 | 8:11 | 49.691
2022-04-28 | 8:11 | 49.695
2022-04-28 | 8:11 | 49.7
2022-04-28 | 8:11 | 49.706
2022-04-28 | 8:11 | 49.712
2022-04-28 | 8:11 | 49.718
2022-04-28 | 8:11 | 49.725
2022-04-28 | 8:11 | 49.731
2022-04-28 | 8:11 | 49.737
2022-04-28 | 8:11 | 49.743
2022-04-28 | 8:11 | 49.75
2022-04-28 | 8:11 | 49.757
2022-04-28 | 8:11 | 49.761
2022-04-28 | 8:11 | 49.766
2022-04-28 | 8:11 | 49.767
2022-04-28 | 8:11 | 49.771
2022-04-28 | 8:11 | 49.774
2022-04-28 | 8:11 | 49.774
2022-04-28 | 8:11 | 49.774
2022-04-28 | 8:11 | 49.775
2022-04-28 | 8:11 | 49.777
2022-04-28 | 8:11 | 49.776
2022-04-28 | 8:11 | 49.776
2022-04-28 | 8:11 | 49.773
2022-04-28 | 8:11 | 49.773
2022-04-28 | 8:11 | 49.773
2022-04-28 | 8:11 | 49.774
2022-04-28 | 8:11 | 49.774
2022-04-28 | 8:11 | 49.774
2022-04-28 | 8:11 | 49.776
2022-04-28 | 8:11 | 49.776
2022-04-28 | 8:11 | 49.777
2022-04-28 | 8:11 | 49.777
2022-04-28 | 8:11 | 49.776
2022-04-28 | 8:11 | 49.777
2022-04-28 | 8:11 | 49.778
2022-04-28 | 8:11 | 49.78
2022-04-28 | 8:11 | 49.783
2022-04-28 | 8:11 | 49.786
2022-04-28 | 8:11 | 49.787
2022-04-28 | 8:11 | 49.789
2022-04-28 | 8:11 | 49.79
2022-04-28 | 8:11 | 49.792
2022-04-28 | 8:11 | 49.793
2022-04-28 | 8:11 | 49.794
2022-04-28 | 8:11 | 49.797
2022-04-28 | 8:11 | 49.8
2022-04-28 | 8:11 | 49.801
2022-04-28 | 8:11 | 49.803
2022-04-28 | 8:11 | 49.804
2022-04-28 | 8:11 | 49.807
2022-04-28 | 8:11 | 49.809
2022-04-28 | 8:11 | 49.813
2022-04-28 | 8:11 | 49.817
2022-04-28 | 8:11 | 49.821
2022-04-28 | 8:11 | 49.827
2022-04-28 | 8:12 | 49.832
2022-04-28 | 8:12 | 49.839
2022-04-28 | 8:12 | 49.848
2022-04-28 | 8:12 | 49.857
2022-04-28 | 8:12 | 49.868
2022-04-28 | 8:12 | 49.878
2022-04-28 | 8:12 | 49.888
2022-04-28 | 8:12 | 49.898
2022-04-28 | 8:12 | 49.905
2022-04-28 | 8:12 | 49.915
2022-04-28 | 8:12 | 49.923
2022-04-28 | 8:12 | 49.93
2022-04-28 | 8:12 | 49.939
2022-04-28 | 8:12 | 49.946
2022-04-28 | 8:12 | 49.953
2022-04-28 | 8:12 | 49.959
2022-04-28 | 8:12 | 49.963
2022-04-28 | 8:12 | 49.968
2022-04-28 | 8:12 | 49.972
2022-04-28 | 8:12 | 49.975
2022-04-28 | 8:12 | 49.977
2022-04-28 | 8:12 | 49.978
2022-04-28 | 8:12 | 49.978
2022-04-28 | 8:12 | 49.978
2022-04-28 | 8:12 | 49.976
2022-04-28 | 8:12 | 49.977
2022-04-28 | 8:12 | 49.978
2022-04-28 | 8:12 | 49.979
2022-04-28 | 8:12 | 49.979
2022-04-28 | 8:12 | 49.979
2022-04-28 | 8:12 | 49.979
2022-04-28 | 8:12 | 49.98
2022-04-28 | 8:12 | 49.981
2022-04-28 | 8:12 | 49.983
2022-04-28 | 8:12 | 49.985
2022-04-28 | 8:12 | 49.986
2022-04-28 | 8:12 | 49.989
2022-04-28 | 8:12 | 49.99
2022-04-28 | 8:12 | 49.993
2022-04-28 | 8:12 | 49.996
2022-04-28 | 8:12 | 49.998
2022-04-28 | 8:12 | 49.998
2022-04-28 | 8:12 | 49.996
2022-04-28 | 8:12 | 49.997
2022-04-28 | 8:12 | 49.999
2022-04-28 | 8:12 | 50.003
2022-04-28 | 8:12 | 50.005
2022-04-28 | 8:12 | 50.004
2022-04-28 | 8:12 | 50
2022-04-28 | 8:12 | 49.994
2022-04-28 | 8:12 | 49.989
2022-04-28 | 8:12 | 49.98
2022-04-28 | 8:12 | 49.975
2022-04-28 | 8:12 | 49.971
2022-04-28 | 8:12 | 49.966
2022-04-28 | 8:12 | 49.963
2022-04-28 | 8:12 | 49.963
2022-04-28 | 8:12 | 49.962
2022-04-28 | 8:12 | 49.962
2022-04-28 | 8:12 | 49.964
2022-04-28 | 8:12 | 49.967
2022-04-28 | 8:13 | 49.969
2022-04-28 | 8:13 | 49.972
2022-04-28 | 8:13 | 49.976
2022-04-28 | 8:13 | 49.979
2022-04-28 | 8:13 | 49.98
2022-04-28 | 8:13 | 49.981
2022-04-28 | 8:13 | 49.979
2022-04-28 | 8:13 | 49.979
2022-04-28 | 8:13 | 49.98
2022-04-28 | 8:13 | 49.976
2022-04-28 | 8:13 | 49.975
2022-04-28 | 8:13 | 49.971
2022-04-28 | 8:13 | 49.97
2022-04-28 | 8:13 | 49.971
2022-04-28 | 8:13 | 49.973
2022-04-28 | 8:13 | 49.974
2022-04-28 | 8:13 | 49.977
2022-04-28 | 8:13 | 49.98
2022-04-28 | 8:13 | 49.984
2022-04-28 | 8:13 | 49.987
2022-04-28 | 8:13 | 49.989
2022-04-28 | 8:13 | 49.989
2022-04-28 | 8:13 | 49.986
2022-04-28 | 8:13 | 49.985
2022-04-28 | 8:13 | 49.983
2022-04-28 | 8:13 | 49.983
2022-04-28 | 8:13 | 49.982
2022-04-28 | 8:13 | 49.981
2022-04-28 | 8:13 | 49.982
2022-04-28 | 8:13 | 49.981
2022-04-28 | 8:13 | 49.978
2022-04-28 | 8:13 | 49.975
2022-04-28 | 8:13 | 49.973
2022-04-28 | 8:13 | 49.971
2022-04-28 | 8:13 | 49.973
2022-04-28 | 8:13 | 49.973
2022-04-28 | 8:13 | 49.974
2022-04-28 | 8:13 | 49.978
2022-04-28 | 8:13 | 49.981
2022-04-28 | 8:13 | 49.981
2022-04-28 | 8:13 | 49.982
2022-04-28 | 8:13 | 49.982
2022-04-28 | 8:13 | 49.982
2022-04-28 | 8:13 | 49.982
2022-04-28 | 8:13 | 49.98
2022-04-28 | 8:13 | 49.978
2022-04-28 | 8:13 | 49.977
2022-04-28 | 8:13 | 49.974
2022-04-28 | 8:13 | 49.974
2022-04-28 | 8:13 | 49.972
2022-04-28 | 8:13 | 49.971
2022-04-28 | 8:13 | 49.97
2022-04-28 | 8:13 | 49.97
2022-04-28 | 8:13 | 49.97
2022-04-28 | 8:13 | 49.97
2022-04-28 | 8:13 | 49.97
2022-04-28 | 8:13 | 49.971
2022-04-28 | 8:13 | 49.972
2022-04-28 | 8:13 | 49.973
2022-04-28 | 8:14 | 49.973
2022-04-28 | 8:14 | 49.976
2022-04-28 | 8:14 | 49.975
2022-04-28 | 8:14 | 49.976
2022-04-28 | 8:14 | 49.978
2022-04-28 | 8:14 | 49.978
2022-04-28 | 8:14 | 49.977
2022-04-28 | 8:14 | 49.978
2022-04-28 | 8:14 | 49.979
2022-04-28 | 8:14 | 49.98
2022-04-28 | 8:14 | 49.98
2022-04-28 | 8:14 | 49.979
2022-04-28 | 8:14 | 49.979
2022-04-28 | 8:14 | 49.976
2022-04-28 | 8:14 | 49.975
2022-04-28 | 8:14 | 49.974
2022-04-28 | 8:14 | 49.973
2022-04-28 | 8:14 | 49.972
2022-04-28 | 8:14 | 49.971
2022-04-28 | 8:14 | 49.972
2022-04-28 | 8:14 | 49.972
2022-04-28 | 8:14 | 49.971
2022-04-28 | 8:14 | 49.971
2022-04-28 | 8:14 | 49.971
2022-04-28 | 8:14 | 49.972
2022-04-28 | 8:14 | 49.972
2022-04-28 | 8:14 | 49.972
2022-04-28 | 8:14 | 49.973
2022-04-28 | 8:14 | 49.974
2022-04-28 | 8:14 | 49.974
2022-04-28 | 8:14 | 49.974
2022-04-28 | 8:14 | 49.974
2022-04-28 | 8:14 | 49.973
2022-04-28 | 8:14 | 49.971
2022-04-28 | 8:14 | 49.972
2022-04-28 | 8:14 | 49.971
2022-04-28 | 8:14 | 49.968
2022-04-28 | 8:14 | 49.967
2022-04-28 | 8:14 | 49.965
2022-04-28 | 8:14 | 49.963
2022-04-28 | 8:14 | 49.962
2022-04-28 | 8:14 | 49.962
2022-04-28 | 8:14 | 49.962
2022-04-28 | 8:14 | 49.964
2022-04-28 | 8:14 | 49.965
2022-04-28 | 8:14 | 49.967
2022-04-28 | 8:14 | 49.967
2022-04-28 | 8:14 | 49.968
2022-04-28 | 8:14 | 49.969
2022-04-28 | 8:14 | 49.971
2022-04-28 | 8:14 | 49.974
2022-04-28 | 8:14 | 49.978
2022-04-28 | 8:14 | 49.981
2022-04-28 | 8:14 | 49.981
2022-04-28 | 8:14 | 49.98
2022-04-28 | 8:14 | 49.981
2022-04-28 | 8:14 | 49.98
2022-04-28 | 8:14 | 49.978
2022-04-28 | 8:14 | 49.978
2022-04-28 | 8:14 | 49.977
2022-04-28 | 8:14 | 49.978
2022-04-28 | 8:15 | 49.978
2022-04-28 | 8:15 | 49.977
2022-04-28 | 8:15 | 49.976
2022-04-28 | 8:15 | 49.975
2022-04-28 | 8:15 | 49.978
2022-04-28 | 8:15 | 49.979
2022-04-28 | 8:15 | 49.982
2022-04-28 | 8:15 | 49.984
2022-04-28 | 8:15 | 49.985
2022-04-28 | 8:15 | 49.987
2022-04-28 | 8:15 | 49.99
2022-04-28 | 8:15 | 49.99
2022-04-28 | 8:15 | 49.991
2022-04-28 | 8:15 | 49.991
2022-04-28 | 8:15 | 49.994
2022-04-28 | 8:15 | 49.996
2022-04-28 | 8:15 | 50
2022-04-28 | 8:15 | 50.001
2022-04-28 | 8:15 | 50.005
2022-04-28 | 8:15 | 50.009
2022-04-28 | 8:15 | 50.011
2022-04-28 | 8:15 | 50.012
2022-04-28 | 8:15 | 50.015
2022-04-28 | 8:15 | 50.016
2022-04-28 | 8:15 | 50.018
2022-04-28 | 8:15 | 50.02
2022-04-28 | 8:15 | 50.023
2022-04-28 | 8:15 | 50.024
2022-04-28 | 8:15 | 50.027
2022-04-28 | 8:15 | 50.03
2022-04-28 | 8:15 | 50.03
2022-04-28 | 8:15 | 50.03
2022-04-28 | 8:15 | 50.03
2022-04-28 | 8:15 | 50.027
2022-04-28 | 8:15 | 50.026
2022-04-28 | 8:15 | 50.024
2022-04-28 | 8:15 | 50.021
2022-04-28 | 8:15 | 50.017
2022-04-28 | 8:15 | 50.013
2022-04-28 | 8:15 | 50.012
2022-04-28 | 8:15 | 50.012
2022-04-28 | 8:15 | 50.009
2022-04-28 | 8:15 | 50.008
2022-04-28 | 8:15 | 50.009
2022-04-28 | 8:15 | 50.012
2022-04-28 | 8:15 | 50.015
2022-04-28 | 8:15 | 50.019
2022-04-28 | 8:15 | 50.021
2022-04-28 | 8:15 | 50.024
2022-04-28 | 8:15 | 50.025
2022-04-28 | 8:15 | 50.027
2022-04-28 | 8:15 | 50.028
2022-04-28 | 8:15 | 50.03
2022-04-28 | 8:15 | 50.03
2022-04-28 | 8:15 | 50.032
2022-04-28 | 8:15 | 50.032
2022-04-28 | 8:15 | 50.033
2022-04-28 | 8:15 | 50.034
2022-04-28 | 8:15 | 50.035
2022-04-28 | 8:16 | 50.035
2022-04-28 | 8:16 | 50.032
2022-04-28 | 8:16 | 50.029
2022-04-28 | 8:16 | 50.027
2022-04-28 | 8:16 | 50.025
2022-04-28 | 8:16 | 50.026
2022-04-28 | 8:16 | 50.026
2022-04-28 | 8:16 | 50.027
2022-04-28 | 8:16 | 50.027
2022-04-28 | 8:16 | 50.028
2022-04-28 | 8:16 | 50.027
2022-04-28 | 8:16 | 50.025
2022-04-28 | 8:16 | 50.023
2022-04-28 | 8:16 | 50.02
2022-04-28 | 8:16 | 50.018
2022-04-28 | 8:16 | 50.02
2022-04-28 | 8:16 | 50.02
2022-04-28 | 8:16 | 50.022
2022-04-28 | 8:16 | 50.023
2022-04-28 | 8:16 | 50.024
2022-04-28 | 8:16 | 50.022
2022-04-28 | 8:16 | 50.024
2022-04-28 | 8:16 | 50.026
2022-04-28 | 8:16 | 50.028
2022-04-28 | 8:16 | 50.03
2022-04-28 | 8:16 | 50.034
2022-04-28 | 8:16 | 50.037
2022-04-28 | 8:16 | 50.04
2022-04-28 | 8:16 | 50.041
2022-04-28 | 8:16 | 50.042
2022-04-28 | 8:16 | 50.041
2022-04-28 | 8:16 | 50.041
2022-04-28 | 8:16 | 50.041
2022-04-28 | 8:16 | 50.04
2022-04-28 | 8:16 | 50.039
2022-04-28 | 8:16 | 50.039
2022-04-28 | 8:16 | 50.04
2022-04-28 | 8:16 | 50.037
2022-04-28 | 8:16 | 50.035
2022-04-28 | 8:16 | 50.032
2022-04-28 | 8:16 | 50.032
2022-04-28 | 8:16 | 50.031
2022-04-28 | 8:16 | 50.03
2022-04-28 | 8:16 | 50.03
2022-04-28 | 8:16 | 50.029
2022-04-28 | 8:16 | 50.028
2022-04-28 | 8:16 | 50.026
2022-04-28 | 8:16 | 50.026
2022-04-28 | 8:16 | 50.026
2022-04-28 | 8:16 | 50.026
2022-04-28 | 8:16 | 50.028
2022-04-28 | 8:16 | 50.029
2022-04-28 | 8:16 | 50.031
2022-04-28 | 8:16 | 50.032
2022-04-28 | 8:16 | 50.033
2022-04-28 | 8:16 | 50.03
2022-04-28 | 8:16 | 50.029
2022-04-28 | 8:16 | 50.027
2022-04-28 | 8:16 | 50.024
2022-04-28 | 8:16 | 50.023
2022-04-28 | 8:16 | 50.02
2022-04-28 | 8:17 | 50.018
2022-04-28 | 8:17 | 50.018
2022-04-28 | 8:17 | 50.016
2022-04-28 | 8:17 | 50.014
2022-04-28 | 8:17 | 50.013
2022-04-28 | 8:17 | 50.01
2022-04-28 | 8:17 | 50.009
2022-04-28 | 8:17 | 50.009
2022-04-28 | 8:17 | 50.01
2022-04-28 | 8:17 | 50.01
2022-04-28 | 8:17 | 50.008
2022-04-28 | 8:17 | 50.005
2022-04-28 | 8:17 | 50.006
2022-04-28 | 8:17 | 50.007
2022-04-28 | 8:17 | 50.007
2022-04-28 | 8:17 | 50.009
2022-04-28 | 8:17 | 50.011
2022-04-28 | 8:17 | 50.011
2022-04-28 | 8:17 | 50.009
2022-04-28 | 8:17 | 50.008
2022-04-28 | 8:17 | 50.007
2022-04-28 | 8:17 | 50.004
2022-04-28 | 8:17 | 50.001
2022-04-28 | 8:17 | 49.997
2022-04-28 | 8:17 | 49.994
2022-04-28 | 8:17 | 49.989
2022-04-28 | 8:17 | 49.986
2022-04-28 | 8:17 | 49.982
2022-04-28 | 8:17 | 49.98
2022-04-28 | 8:17 | 49.979
2022-04-28 | 8:17 | 49.978
2022-04-28 | 8:17 | 49.977
2022-04-28 | 8:17 | 49.977
2022-04-28 | 8:17 | 49.976
2022-04-28 | 8:17 | 49.977
2022-04-28 | 8:17 | 49.977
2022-04-28 | 8:17 | 49.978
2022-04-28 | 8:17 | 49.976
2022-04-28 | 8:17 | 49.976
2022-04-28 | 8:17 | 49.975
2022-04-28 | 8:17 | 49.975
2022-04-28 | 8:17 | 49.976
2022-04-28 | 8:17 | 49.976
2022-04-28 | 8:17 | 49.976
2022-04-28 | 8:17 | 49.977
2022-04-28 | 8:17 | 49.98
2022-04-28 | 8:17 | 49.982
2022-04-28 | 8:17 | 49.984
2022-04-28 | 8:17 | 49.988
2022-04-28 | 8:17 | 49.989
2022-04-28 | 8:17 | 49.992
2022-04-28 | 8:17 | 49.993
2022-04-28 | 8:17 | 49.993
2022-04-28 | 8:17 | 49.992
2022-04-28 | 8:17 | 49.992
2022-04-28 | 8:17 | 49.994
2022-04-28 | 8:17 | 49.995
2022-04-28 | 8:17 | 49.995
2022-04-28 | 8:17 | 49.995
2022-04-28 | 8:18 | 49.994
2022-04-28 | 8:18 | 49.994
2022-04-28 | 8:18 | 49.994
2022-04-28 | 8:18 | 49.996
2022-04-28 | 8:18 | 49.999
2022-04-28 | 8:18 | 50.002
2022-04-28 | 8:18 | 50.004
2022-04-28 | 8:18 | 50.006
2022-04-28 | 8:18 | 50.009
2022-04-28 | 8:18 | 50.012
2022-04-28 | 8:18 | 50.016
2022-04-28 | 8:18 | 50.02
2022-04-28 | 8:18 | 50.023
2022-04-28 | 8:18 | 50.028
2022-04-28 | 8:18 | 50.03
2022-04-28 | 8:18 | 50.03
2022-04-28 | 8:18 | 50.029
2022-04-28 | 8:18 | 50.03
2022-04-28 | 8:18 | 50.027
2022-04-28 | 8:18 | 50.023
2022-04-28 | 8:18 | 50.022
2022-04-28 | 8:18 | 50.022
2022-04-28 | 8:18 | 50.02
2022-04-28 | 8:18 | 50.018
2022-04-28 | 8:18 | 50.018
2022-04-28 | 8:18 | 50.019
2022-04-28 | 8:18 | 50.022
2022-04-28 | 8:18 | 50.024
2022-04-28 | 8:18 | 50.026
2022-04-28 | 8:18 | 50.027
2022-04-28 | 8:18 | 50.031

## 20220429-1
In GMT
Date | Time | Freq
2022-04-29 | 5:08 | 50.018
2022-04-29 | 5:08 | 50.017
2022-04-29 | 5:08 | 50.017
2022-04-29 | 5:08 | 50.015
2022-04-29 | 5:08 | 50.018
2022-04-29 | 5:08 | 50.018
2022-04-29 | 5:08 | 50.021
2022-04-29 | 5:08 | 50.022
2022-04-29 | 5:08 | 50.026
2022-04-29 | 5:08 | 50.027
2022-04-29 | 5:08 | 50.03
2022-04-29 | 5:08 | 50.031
2022-04-29 | 5:08 | 50.033
2022-04-29 | 5:08 | 50.034
2022-04-29 | 5:08 | 50.036
2022-04-29 | 5:08 | 50.036
2022-04-29 | 5:08 | 50.038
2022-04-29 | 5:08 | 50.038
2022-04-29 | 5:08 | 50.039
2022-04-29 | 5:08 | 50.037
2022-04-29 | 5:08 | 50.038
2022-04-29 | 5:08 | 50.036
2022-04-29 | 5:08 | 50.037
2022-04-29 | 5:08 | 50.036
2022-04-29 | 5:08 | 50.038
2022-04-29 | 5:08 | 50.039
2022-04-29 | 5:08 | 50.04
2022-04-29 | 5:08 | 50.04
2022-04-29 | 5:08 | 50.042
2022-04-29 | 5:08 | 50.046
2022-04-29 | 5:08 | 50.05
2022-04-29 | 5:09 | 50.054
2022-04-29 | 5:09 | 50.058
2022-04-29 | 5:09 | 50.059
2022-04-29 | 5:09 | 50.061
2022-04-29 | 5:09 | 50.06
2022-04-29 | 5:09 | 50.059
2022-04-29 | 5:09 | 50.058
2022-04-29 | 5:09 | 50.056
2022-04-29 | 5:09 | 50.055
2022-04-29 | 5:09 | 50.056
2022-04-29 | 5:09 | 50.056
2022-04-29 | 5:09 | 50.054
2022-04-29 | 5:09 | 50.054
2022-04-29 | 5:09 | 50.057
2022-04-29 | 5:09 | 50.058
2022-04-29 | 5:09 | 50.061
2022-04-29 | 5:09 | 50.065
2022-04-29 | 5:09 | 50.067
2022-04-29 | 5:09 | 50.067
2022-04-29 | 5:09 | 50.068
2022-04-29 | 5:09 | 50.07
2022-04-29 | 5:09 | 50.07
2022-04-29 | 5:09 | 50.07
2022-04-29 | 5:09 | 50.072
2022-04-29 | 5:09 | 50.072
2022-04-29 | 5:09 | 50.074
2022-04-29 | 5:09 | 50.077
2022-04-29 | 5:09 | 50.08
2022-04-29 | 5:09 | 50.081
2022-04-29 | 5:09 | 50.084
2022-04-29 | 5:09 | 50.085
2022-04-29 | 5:09 | 50.085
2022-04-29 | 5:09 | 50.087
2022-04-29 | 5:09 | 50.088
2022-04-29 | 5:09 | 50.087
2022-04-29 | 5:09 | 50.085
2022-04-29 | 5:09 | 50.086
2022-04-29 | 5:09 | 50.084
2022-04-29 | 5:09 | 50.081
2022-04-29 | 5:09 | 50.081
2022-04-29 | 5:09 | 50.08
2022-04-29 | 5:09 | 50.08
2022-04-29 | 5:09 | 50.08
2022-04-29 | 5:09 | 50.083
2022-04-29 | 5:09 | 50.087
2022-04-29 | 5:09 | 50.091
2022-04-29 | 5:09 | 50.095
2022-04-29 | 5:09 | 50.098
2022-04-29 | 5:09 | 50.101
2022-04-29 | 5:09 | 50.104
2022-04-29 | 5:09 | 50.104
2022-04-29 | 5:09 | 50.103
2022-04-29 | 5:09 | 50.104
2022-04-29 | 5:09 | 50.106
2022-04-29 | 5:09 | 50.105
2022-04-29 | 5:09 | 50.105
2022-04-29 | 5:09 | 50.107
2022-04-29 | 5:09 | 50.108
2022-04-29 | 5:09 | 50.108
2022-04-29 | 5:10 | 50.11
2022-04-29 | 5:10 | 50.109
2022-04-29 | 5:10 | 50.112
2022-04-29 | 5:10 | 50.115
2022-04-29 | 5:10 | 50.117
2022-04-29 | 5:10 | 50.121
2022-04-29 | 5:10 | 50.121
2022-04-29 | 5:10 | 50.123
2022-04-29 | 5:10 | 50.129
2022-04-29 | 5:10 | 50.131
2022-04-29 | 5:10 | 50.134
2022-04-29 | 5:10 | 50.136
2022-04-29 | 5:10 | 50.137
2022-04-29 | 5:10 | 50.137
2022-04-29 | 5:10 | 50.134
2022-04-29 | 5:10 | 50.135
2022-04-29 | 5:10 | 50.132
2022-04-29 | 5:10 | 50.133
2022-04-29 | 5:10 | 50.132
2022-04-29 | 5:10 | 50.132
2022-04-29 | 5:10 | 50.133
2022-04-29 | 5:10 | 50.131
2022-04-29 | 5:10 | 50.133
2022-04-29 | 5:10 | 50.131
2022-04-29 | 5:10 | 50.132
2022-04-29 | 5:10 | 50.132
2022-04-29 | 5:10 | 50.132
2022-04-29 | 5:10 | 50.133
2022-04-29 | 5:10 | 50.132
2022-04-29 | 5:10 | 50.131
2022-04-29 | 5:10 | 50.128
2022-04-29 | 5:10 | 50.128
2022-04-29 | 5:10 | 50.125
2022-04-29 | 5:10 | 50.123
2022-04-29 | 5:10 | 50.12
2022-04-29 | 5:10 | 50.122
2022-04-29 | 5:10 | 50.123
2022-04-29 | 5:10 | 50.124
2022-04-29 | 5:10 | 50.125
2022-04-29 | 5:10 | 50.126
2022-04-29 | 5:10 | 50.127
2022-04-29 | 5:10 | 50.124
2022-04-29 | 5:10 | 50.124
2022-04-29 | 5:10 | 50.123
2022-04-29 | 5:10 | 50.118
2022-04-29 | 5:10 | 50.116
2022-04-29 | 5:10 | 50.112
2022-04-29 | 5:10 | 50.109
2022-04-29 | 5:10 | 50.106
2022-04-29 | 5:10 | 50.105
2022-04-29 | 5:10 | 50.105
2022-04-29 | 5:10 | 50.105
2022-04-29 | 5:10 | 50.106
2022-04-29 | 5:10 | 50.11
2022-04-29 | 5:10 | 50.111
2022-04-29 | 5:10 | 50.112
2022-04-29 | 5:10 | 50.112
2022-04-29 | 5:10 | 50.145
2022-04-29 | 5:10 | 50.21
2022-04-29 | 5:10 | 50.272
2022-04-29 | 5:10 | 50.317
2022-04-29 | 5:11 | 50.334
2022-04-29 | 5:11 | 50.34
2022-04-29 | 5:11 | 50.337
2022-04-29 | 5:11 | 50.333
2022-04-29 | 5:11 | 50.326
2022-04-29 | 5:11 | 50.323
2022-04-29 | 5:11 | 50.324
2022-04-29 | 5:11 | 50.323
2022-04-29 | 5:11 | 50.326
2022-04-29 | 5:11 | 50.33
2022-04-29 | 5:11 | 50.331
2022-04-29 | 5:11 | 50.334
2022-04-29 | 5:11 | 50.335
2022-04-29 | 5:11 | 50.337
2022-04-29 | 5:11 | 50.336
2022-04-29 | 5:11 | 50.334
2022-04-29 | 5:11 | 50.334
2022-04-29 | 5:11 | 50.331
2022-04-29 | 5:11 | 50.329
2022-04-29 | 5:11 | 50.329
2022-04-29 | 5:11 | 50.328
2022-04-29 | 5:11 | 50.329
2022-04-29 | 5:11 | 50.331
2022-04-29 | 5:11 | 50.329
2022-04-29 | 5:11 | 50.331
2022-04-29 | 5:11 | 50.332
2022-04-29 | 5:11 | 50.33
2022-04-29 | 5:11 | 50.331
2022-04-29 | 5:11 | 50.331
2022-04-29 | 5:11 | 50.329
2022-04-29 | 5:11 | 50.329
2022-04-29 | 5:11 | 50.328
2022-04-29 | 5:11 | 50.326
2022-04-29 | 5:11 | 50.328
2022-04-29 | 5:11 | 50.328
2022-04-29 | 5:11 | 50.326
2022-04-29 | 5:11 | 50.326
2022-04-29 | 5:11 | 50.328
2022-04-29 | 5:11 | 50.327
2022-04-29 | 5:11 | 50.327
2022-04-29 | 5:11 | 50.329
2022-04-29 | 5:11 | 50.327
2022-04-29 | 5:11 | 50.327
2022-04-29 | 5:11 | 50.326
2022-04-29 | 5:11 | 50.324
2022-04-29 | 5:11 | 50.326
2022-04-29 | 5:11 | 50.326
2022-04-29 | 5:11 | 50.324
2022-04-29 | 5:11 | 50.323
2022-04-29 | 5:11 | 50.322
2022-04-29 | 5:11 | 50.324
2022-04-29 | 5:11 | 50.324
2022-04-29 | 5:11 | 50.326
2022-04-29 | 5:11 | 50.324
2022-04-29 | 5:11 | 50.323
2022-04-29 | 5:11 | 50.323
2022-04-29 | 5:11 | 50.323
2022-04-29 | 5:11 | 50.32
2022-04-29 | 5:11 | 50.318
2022-04-29 | 5:12 | 50.317
2022-04-29 | 5:12 | 50.317
2022-04-29 | 5:12 | 50.315
2022-04-29 | 5:12 | 50.314
2022-04-29 | 5:12 | 50.313
2022-04-29 | 5:12 | 50.312
2022-04-29 | 5:12 | 50.312
2022-04-29 | 5:12 | 50.31
2022-04-29 | 5:12 | 50.306
2022-04-29 | 5:12 | 50.306
2022-04-29 | 5:12 | 50.308
2022-04-29 | 5:12 | 50.308
2022-04-29 | 5:12 | 50.312
2022-04-29 | 5:12 | 50.314
2022-04-29 | 5:12 | 50.319
2022-04-29 | 5:12 | 50.323
2022-04-29 | 5:12 | 50.324
2022-04-29 | 5:12 | 50.327
2022-04-29 | 5:12 | 50.325
2022-04-29 | 5:12 | 50.327
2022-04-29 | 5:12 | 50.327
2022-04-29 | 5:12 | 50.328
2022-04-29 | 5:12 | 50.325
2022-04-29 | 5:12 | 50.323
2022-04-29 | 5:12 | 50.322
2022-04-29 | 5:12 | 50.321
2022-04-29 | 5:12 | 50.32
2022-04-29 | 5:12 | 50.318
2022-04-29 | 5:12 | 50.319
2022-04-29 | 5:12 | 50.317
2022-04-29 | 5:12 | 50.316
2022-04-29 | 5:12 | 50.318
2022-04-29 | 5:12 | 50.316
2022-04-29 | 5:12 | 50.314
2022-04-29 | 5:12 | 50.312
2022-04-29 | 5:12 | 50.311
2022-04-29 | 5:12 | 50.31
2022-04-29 | 5:12 | 50.306
2022-04-29 | 5:12 | 50.307
2022-04-29 | 5:12 | 50.305
2022-04-29 | 5:12 | 50.303
2022-04-29 | 5:12 | 50.3
2022-04-29 | 5:12 | 50.3
2022-04-29 | 5:12 | 50.299
2022-04-29 | 5:12 | 50.297
2022-04-29 | 5:12 | 50.294
2022-04-29 | 5:12 | 50.292
2022-04-29 | 5:12 | 50.292
2022-04-29 | 5:12 | 50.291
2022-04-29 | 5:12 | 50.289
2022-04-29 | 5:12 | 50.286
2022-04-29 | 5:12 | 50.281
2022-04-29 | 5:12 | 50.276
2022-04-29 | 5:12 | 50.271
2022-04-29 | 5:12 | 50.268
2022-04-29 | 5:12 | 50.27
2022-04-29 | 5:12 | 50.268
2022-04-29 | 5:12 | 50.267
2022-04-29 | 5:12 | 50.266
2022-04-29 | 5:12 | 50.264
2022-04-29 | 5:12 | 50.26
2022-04-29 | 5:13 | 50.258
2022-04-29 | 5:13 | 50.258
2022-04-29 | 5:13 | 50.256
2022-04-29 | 5:13 | 50.255
2022-04-29 | 5:13 | 50.253
2022-04-29 | 5:13 | 50.252
2022-04-29 | 5:13 | 50.251
2022-04-29 | 5:13 | 50.253
2022-04-29 | 5:13 | 50.256
2022-04-29 | 5:13 | 50.256
2022-04-29 | 5:13 | 50.254
2022-04-29 | 5:13 | 50.253
2022-04-29 | 5:13 | 50.25
2022-04-29 | 5:13 | 50.249
2022-04-29 | 5:13 | 50.246
2022-04-29 | 5:13 | 50.243
2022-04-29 | 5:13 | 50.24
2022-04-29 | 5:13 | 50.236
2022-04-29 | 5:13 | 50.235
2022-04-29 | 5:13 | 50.233
2022-04-29 | 5:13 | 50.234
2022-04-29 | 5:13 | 50.234
2022-04-29 | 5:13 | 50.231
2022-04-29 | 5:13 | 50.23
2022-04-29 | 5:13 | 50.229
2022-04-29 | 5:13 | 50.231
2022-04-29 | 5:13 | 50.231
2022-04-29 | 5:13 | 50.232
2022-04-29 | 5:13 | 50.234
2022-04-29 | 5:13 | 50.236
2022-04-29 | 5:13 | 50.236
2022-04-29 | 5:13 | 50.236
2022-04-29 | 5:13 | 50.236
2022-04-29 | 5:13 | 50.238
2022-04-29 | 5:13 | 50.238
2022-04-29 | 5:13 | 50.236
2022-04-29 | 5:13 | 50.236
2022-04-29 | 5:13 | 50.236
2022-04-29 | 5:13 | 50.235
2022-04-29 | 5:13 | 50.233
2022-04-29 | 5:13 | 50.233
2022-04-29 | 5:13 | 50.231
2022-04-29 | 5:13 | 50.231
2022-04-29 | 5:13 | 50.23
2022-04-29 | 5:13 | 50.229
2022-04-29 | 5:13 | 50.229
2022-04-29 | 5:13 | 50.228
2022-04-29 | 5:13 | 50.229
2022-04-29 | 5:13 | 50.227
2022-04-29 | 5:13 | 50.23
2022-04-29 | 5:13 | 50.228
2022-04-29 | 5:13 | 50.229
2022-04-29 | 5:13 | 50.229
2022-04-29 | 5:13 | 50.228
2022-04-29 | 5:13 | 50.224
2022-04-29 | 5:13 | 50.223
2022-04-29 | 5:13 | 50.22
2022-04-29 | 5:13 | 50.218
2022-04-29 | 5:13 | 50.217
2022-04-29 | 5:13 | 50.214
2022-04-29 | 5:14 | 50.213
2022-04-29 | 5:14 | 50.211
2022-04-29 | 5:14 | 50.206
2022-04-29 | 5:14 | 50.205
2022-04-29 | 5:14 | 50.204
2022-04-29 | 5:14 | 50.204
2022-04-29 | 5:14 | 50.202
2022-04-29 | 5:14 | 50.201
2022-04-29 | 5:14 | 50.202
2022-04-29 | 5:14 | 50.202
2022-04-29 | 5:14 | 50.203
2022-04-29 | 5:14 | 50.203
2022-04-29 | 5:14 | 50.202
2022-04-29 | 5:14 | 50.2
2022-04-29 | 5:14 | 50.198
2022-04-29 | 5:14 | 50.198
2022-04-29 | 5:14 | 50.198
2022-04-29 | 5:14 | 50.196
2022-04-29 | 5:14 | 50.196
2022-04-29 | 5:14 | 50.196
2022-04-29 | 5:14 | 50.194
2022-04-29 | 5:14 | 50.19
2022-04-29 | 5:14 | 50.187
2022-04-29 | 5:14 | 50.183
2022-04-29 | 5:14 | 50.179
2022-04-29 | 5:14 | 50.177
2022-04-29 | 5:14 | 50.176
2022-04-29 | 5:14 | 50.174
2022-04-29 | 5:14 | 50.172
2022-04-29 | 5:14 | 50.167
2022-04-29 | 5:14 | 50.162
2022-04-29 | 5:14 | 50.161
2022-04-29 | 5:14 | 50.157
2022-04-29 | 5:14 | 50.154
2022-04-29 | 5:14 | 50.151
2022-04-29 | 5:14 | 50.149
2022-04-29 | 5:14 | 50.146
2022-04-29 | 5:14 | 50.143
2022-04-29 | 5:14 | 50.14
2022-04-29 | 5:14 | 50.14
2022-04-29 | 5:14 | 50.138
2022-04-29 | 5:14 | 50.136
2022-04-29 | 5:14 | 50.134
2022-04-29 | 5:14 | 50.13
2022-04-29 | 5:14 | 50.126
2022-04-29 | 5:14 | 50.12
2022-04-29 | 5:14 | 50.116
2022-04-29 | 5:14 | 50.113
2022-04-29 | 5:14 | 50.108
2022-04-29 | 5:14 | 50.106
2022-04-29 | 5:14 | 50.103
2022-04-29 | 5:14 | 50.1
2022-04-29 | 5:14 | 50.094
2022-04-29 | 5:14 | 50.09
2022-04-29 | 5:14 | 50.085
2022-04-29 | 5:14 | 50.082
2022-04-29 | 5:14 | 50.079
2022-04-29 | 5:14 | 50.078
2022-04-29 | 5:14 | 50.078
2022-04-29 | 5:14 | 50.078
2022-04-29 | 5:15 | 50.074
2022-04-29 | 5:15 | 50.071
2022-04-29 | 5:15 | 50.068
2022-04-29 | 5:15 | 50.068
2022-04-29 | 5:15 | 50.065
2022-04-29 | 5:15 | 50.065
2022-04-29 | 5:15 | 50.064
2022-04-29 | 5:15 | 50.063
2022-04-29 | 5:15 | 50.062
2022-04-29 | 5:15 | 50.062
2022-04-29 | 5:15 | 50.065
2022-04-29 | 5:15 | 50.065
2022-04-29 | 5:15 | 50.066
2022-04-29 | 5:15 | 50.067
2022-04-29 | 5:15 | 50.068
2022-04-29 | 5:15 | 50.068
2022-04-29 | 5:15 | 50.069
2022-04-29 | 5:15 | 50.069
2022-04-29 | 5:15 | 50.071
2022-04-29 | 5:15 | 50.071
2022-04-29 | 5:15 | 50.07
2022-04-29 | 5:15 | 50.069
2022-04-29 | 5:15 | 50.066
2022-04-29 | 5:15 | 50.064
2022-04-29 | 5:15 | 50.061
2022-04-29 | 5:15 | 50.057
2022-04-29 | 5:15 | 50.054
2022-04-29 | 5:15 | 50.048
2022-04-29 | 5:15 | 50.042
2022-04-29 | 5:15 | 50.036
2022-04-29 | 5:15 | 50.027
2022-04-29 | 5:15 | 50.021
2022-04-29 | 5:15 | 50.018
2022-04-29 | 5:15 | 50.016
2022-04-29 | 5:15 | 50.013
2022-04-29 | 5:15 | 50.012
2022-04-29 | 5:15 | 50.012
2022-04-29 | 5:15 | 50.011
2022-04-29 | 5:15 | 50.009
2022-04-29 | 5:15 | 50.005
2022-04-29 | 5:15 | 50.004
2022-04-29 | 5:15 | 50.002
2022-04-29 | 5:15 | 50.001
2022-04-29 | 5:15 | 49.997
2022-04-29 | 5:15 | 49.994
2022-04-29 | 5:15 | 49.989
2022-04-29 | 5:15 | 49.983
2022-04-29 | 5:15 | 49.978
2022-04-29 | 5:15 | 49.974
2022-04-29 | 5:15 | 49.972
2022-04-29 | 5:15 | 49.97
2022-04-29 | 5:15 | 49.969
2022-04-29 | 5:15 | 49.968
2022-04-29 | 5:15 | 49.966
2022-04-29 | 5:15 | 49.965
2022-04-29 | 5:15 | 49.963
2022-04-29 | 5:15 | 49.963
2022-04-29 | 5:15 | 49.964
2022-04-29 | 5:15 | 49.963
2022-04-29 | 5:16 | 49.965
2022-04-29 | 5:16 | 49.968
2022-04-29 | 5:16 | 49.971
2022-04-29 | 5:16 | 49.973
2022-04-29 | 5:16 | 49.976
2022-04-29 | 5:16 | 49.977
2022-04-29 | 5:16 | 49.979
2022-04-29 | 5:16 | 49.979
2022-04-29 | 5:16 | 49.98
2022-04-29 | 5:16 | 49.981
2022-04-29 | 5:16 | 49.981
2022-04-29 | 5:16 | 49.979
2022-04-29 | 5:16 | 49.978
2022-04-29 | 5:16 | 49.977
2022-04-29 | 5:16 | 49.974
2022-04-29 | 5:16 | 49.972
2022-04-29 | 5:16 | 49.972
2022-04-29 | 5:16 | 49.972
2022-04-29 | 5:16 | 49.97
2022-04-29 | 5:16 | 49.969
2022-04-29 | 5:16 | 49.967
2022-04-29 | 5:16 | 49.968
2022-04-29 | 5:16 | 49.967
2022-04-29 | 5:16 | 49.968
2022-04-29 | 5:16 | 49.967
2022-04-29 | 5:16 | 49.967
2022-04-29 | 5:16 | 49.964
2022-04-29 | 5:16 | 49.962
2022-04-29 | 5:16 | 49.962
2022-04-29 | 5:16 | 49.959
2022-04-29 | 5:16 | 49.954

## 20220430-1
In GMT
Date | Time | Freq
2022-04-30 | 4:29 | 50.05
2022-04-30 | 4:29 | 50.051
2022-04-30 | 4:29 | 50.048
2022-04-30 | 4:29 | 50.047
2022-04-30 | 4:29 | 50.048
2022-04-30 | 4:29 | 50.047
2022-04-30 | 4:29 | 50.045
2022-04-30 | 4:29 | 50.044
2022-04-30 | 4:29 | 50.045
2022-04-30 | 4:29 | 50.045
2022-04-30 | 4:29 | 50.045
2022-04-30 | 4:29 | 50.045
2022-04-30 | 4:29 | 50.046
2022-04-30 | 4:29 | 50.045
2022-04-30 | 4:29 | 50.045
2022-04-30 | 4:29 | 50.047
2022-04-30 | 4:29 | 50.048
2022-04-30 | 4:29 | 50.05
2022-04-30 | 4:29 | 50.052
2022-04-30 | 4:29 | 50.052
2022-04-30 | 4:29 | 50.052
2022-04-30 | 4:29 | 50.053
2022-04-30 | 4:29 | 50.053
2022-04-30 | 4:29 | 50.054
2022-04-30 | 4:29 | 50.054
2022-04-30 | 4:29 | 50.055
2022-04-30 | 4:29 | 50.054
2022-04-30 | 4:29 | 50.054
2022-04-30 | 4:29 | 50.055
2022-04-30 | 4:29 | 50.054
2022-04-30 | 4:29 | 50.054
2022-04-30 | 4:30 | 50.054
2022-04-30 | 4:30 | 50.054
2022-04-30 | 4:30 | 50.055
2022-04-30 | 4:30 | 50.054
2022-04-30 | 4:30 | 50.054
2022-04-30 | 4:30 | 50.055
2022-04-30 | 4:30 | 50.056
2022-04-30 | 4:30 | 50.055
2022-04-30 | 4:30 | 50.056
2022-04-30 | 4:30 | 50.056
2022-04-30 | 4:30 | 50.055
2022-04-30 | 4:30 | 50.053
2022-04-30 | 4:30 | 50.051
2022-04-30 | 4:30 | 50.048
2022-04-30 | 4:30 | 50.048
2022-04-30 | 4:30 | 50.045
2022-04-30 | 4:30 | 50.045
2022-04-30 | 4:30 | 50.045
2022-04-30 | 4:30 | 50.043
2022-04-30 | 4:30 | 50.042
2022-04-30 | 4:30 | 50.042
2022-04-30 | 4:30 | 50.041
2022-04-30 | 4:30 | 50.04
2022-04-30 | 4:30 | 50.039
2022-04-30 | 4:30 | 50.039
2022-04-30 | 4:30 | 50.038
2022-04-30 | 4:30 | 50.037
2022-04-30 | 4:30 | 50.036
2022-04-30 | 4:30 | 50.033
2022-04-30 | 4:30 | 50.033
2022-04-30 | 4:30 | 50.031
2022-04-30 | 4:30 | 50.031
2022-04-30 | 4:30 | 50.029
2022-04-30 | 4:30 | 50.027
2022-04-30 | 4:30 | 50.028
2022-04-30 | 4:30 | 50.032
2022-04-30 | 4:30 | 50.033
2022-04-30 | 4:30 | 50.034
2022-04-30 | 4:30 | 50.033
2022-04-30 | 4:30 | 50.036
2022-04-30 | 4:30 | 50.035
2022-04-30 | 4:30 | 50.034
2022-04-30 | 4:30 | 50.034
2022-04-30 | 4:30 | 50.035
2022-04-30 | 4:30 | 50.039
2022-04-30 | 4:30 | 50.038
2022-04-30 | 4:30 | 50.041
2022-04-30 | 4:30 | 50.041
2022-04-30 | 4:30 | 50.04
2022-04-30 | 4:30 | 50.04
2022-04-30 | 4:30 | 50.04
2022-04-30 | 4:30 | 50.04
2022-04-30 | 4:30 | 50.037
2022-04-30 | 4:30 | 50.037
2022-04-30 | 4:30 | 50.034
2022-04-30 | 4:30 | 50.035
2022-04-30 | 4:30 | 50.034
2022-04-30 | 4:30 | 50.034
2022-04-30 | 4:30 | 50.038
2022-04-30 | 4:30 | 50.04
2022-04-30 | 4:31 | 50.04
2022-04-30 | 4:31 | 50.042
2022-04-30 | 4:31 | 50.042
2022-04-30 | 4:31 | 50.043
2022-04-30 | 4:31 | 50.043
2022-04-30 | 4:31 | 50.041
2022-04-30 | 4:31 | 50.039
2022-04-30 | 4:31 | 50.037
2022-04-30 | 4:31 | 50.037
2022-04-30 | 4:31 | 50.035
2022-04-30 | 4:31 | 50.037
2022-04-30 | 4:31 | 50.04
2022-04-30 | 4:31 | 50.043
2022-04-30 | 4:31 | 50.044
2022-04-30 | 4:31 | 50.047
2022-04-30 | 4:31 | 50.048
2022-04-30 | 4:31 | 50.049
2022-04-30 | 4:31 | 50.05
2022-04-30 | 4:31 | 50.052
2022-04-30 | 4:31 | 50.05
2022-04-30 | 4:31 | 50.052
2022-04-30 | 4:31 | 50.051
2022-04-30 | 4:31 | 50.097
2022-04-30 | 4:31 | 50.173
2022-04-30 | 4:31 | 50.232
2022-04-30 | 4:31 | 50.274
2022-04-30 | 4:31 | 50.296
2022-04-30 | 4:31 | 50.306
2022-04-30 | 4:31 | 50.308
2022-04-30 | 4:31 | 50.305
2022-04-30 | 4:31 | 50.301
2022-04-30 | 4:31 | 50.297
2022-04-30 | 4:31 | 50.292
2022-04-30 | 4:31 | 50.288
2022-04-30 | 4:31 | 50.287
2022-04-30 | 4:31 | 50.284
2022-04-30 | 4:31 | 50.283
2022-04-30 | 4:31 | 50.281
2022-04-30 | 4:31 | 50.281
2022-04-30 | 4:31 | 50.279
2022-04-30 | 4:31 | 50.276
2022-04-30 | 4:31 | 50.275
2022-04-30 | 4:31 | 50.276
2022-04-30 | 4:31 | 50.274
2022-04-30 | 4:31 | 50.274
2022-04-30 | 4:31 | 50.277
2022-04-30 | 4:31 | 50.278
2022-04-30 | 4:31 | 50.28
2022-04-30 | 4:31 | 50.282
2022-04-30 | 4:31 | 50.285
2022-04-30 | 4:31 | 50.286
2022-04-30 | 4:31 | 50.286
2022-04-30 | 4:31 | 50.288
2022-04-30 | 4:31 | 50.291
2022-04-30 | 4:31 | 50.293
2022-04-30 | 4:31 | 50.295
2022-04-30 | 4:31 | 50.295
2022-04-30 | 4:31 | 50.297
2022-04-30 | 4:31 | 50.297
2022-04-30 | 4:32 | 50.298
2022-04-30 | 4:32 | 50.3
2022-04-30 | 4:32 | 50.301
2022-04-30 | 4:32 | 50.301
2022-04-30 | 4:32 | 50.302
2022-04-30 | 4:32 | 50.304
2022-04-30 | 4:32 | 50.305
2022-04-30 | 4:32 | 50.305
2022-04-30 | 4:32 | 50.303
2022-04-30 | 4:32 | 50.304
2022-04-30 | 4:32 | 50.303
2022-04-30 | 4:32 | 50.302
2022-04-30 | 4:32 | 50.3
2022-04-30 | 4:32 | 50.298
2022-04-30 | 4:32 | 50.298
2022-04-30 | 4:32 | 50.296
2022-04-30 | 4:32 | 50.294
2022-04-30 | 4:32 | 50.294
2022-04-30 | 4:32 | 50.294
2022-04-30 | 4:32 | 50.294
2022-04-30 | 4:32 | 50.295
2022-04-30 | 4:32 | 50.296
2022-04-30 | 4:32 | 50.296
2022-04-30 | 4:32 | 50.296
2022-04-30 | 4:32 | 50.298
2022-04-30 | 4:32 | 50.301
2022-04-30 | 4:32 | 50.302
2022-04-30 | 4:32 | 50.302
2022-04-30 | 4:32 | 50.303
2022-04-30 | 4:32 | 50.304
2022-04-30 | 4:32 | 50.306
2022-04-30 | 4:32 | 50.305
2022-04-30 | 4:32 | 50.305
2022-04-30 | 4:32 | 50.306
2022-04-30 | 4:32 | 50.304
2022-04-30 | 4:32 | 50.305
2022-04-30 | 4:32 | 50.305
2022-04-30 | 4:32 | 50.304
2022-04-30 | 4:32 | 50.303
2022-04-30 | 4:32 | 50.302
2022-04-30 | 4:32 | 50.302
2022-04-30 | 4:32 | 50.302
2022-04-30 | 4:32 | 50.301
2022-04-30 | 4:32 | 50.302
2022-04-30 | 4:32 | 50.304
2022-04-30 | 4:32 | 50.304
2022-04-30 | 4:32 | 50.304
2022-04-30 | 4:32 | 50.304
2022-04-30 | 4:32 | 50.307
2022-04-30 | 4:32 | 50.308
2022-04-30 | 4:32 | 50.307
2022-04-30 | 4:32 | 50.308
2022-04-30 | 4:32 | 50.306
2022-04-30 | 4:32 | 50.306
2022-04-30 | 4:32 | 50.305
2022-04-30 | 4:32 | 50.305
2022-04-30 | 4:32 | 50.307
2022-04-30 | 4:32 | 50.31
2022-04-30 | 4:32 | 50.311
2022-04-30 | 4:32 | 50.312
2022-04-30 | 4:33 | 50.312
2022-04-30 | 4:33 | 50.31
2022-04-30 | 4:33 | 50.308
2022-04-30 | 4:33 | 50.309
2022-04-30 | 4:33 | 50.309
2022-04-30 | 4:33 | 50.307
2022-04-30 | 4:33 | 50.305
2022-04-30 | 4:33 | 50.305
2022-04-30 | 4:33 | 50.304
2022-04-30 | 4:33 | 50.304
2022-04-30 | 4:33 | 50.305
2022-04-30 | 4:33 | 50.306
2022-04-30 | 4:33 | 50.307
2022-04-30 | 4:33 | 50.307
2022-04-30 | 4:33 | 50.31
2022-04-30 | 4:33 | 50.312
2022-04-30 | 4:33 | 50.313
2022-04-30 | 4:33 | 50.313
2022-04-30 | 4:33 | 50.315
2022-04-30 | 4:33 | 50.315
2022-04-30 | 4:33 | 50.315
2022-04-30 | 4:33 | 50.314
2022-04-30 | 4:33 | 50.313
2022-04-30 | 4:33 | 50.314
2022-04-30 | 4:33 | 50.314
2022-04-30 | 4:33 | 50.312
2022-04-30 | 4:33 | 50.311
2022-04-30 | 4:33 | 50.312
2022-04-30 | 4:33 | 50.312
2022-04-30 | 4:33 | 50.31
2022-04-30 | 4:33 | 50.308
2022-04-30 | 4:33 | 50.308
2022-04-30 | 4:33 | 50.305
2022-04-30 | 4:33 | 50.304
2022-04-30 | 4:33 | 50.304
2022-04-30 | 4:33 | 50.307
2022-04-30 | 4:33 | 50.306
2022-04-30 | 4:33 | 50.306
2022-04-30 | 4:33 | 50.307
2022-04-30 | 4:33 | 50.306
2022-04-30 | 4:33 | 50.305
2022-04-30 | 4:33 | 50.303
2022-04-30 | 4:33 | 50.301
2022-04-30 | 4:33 | 50.3
2022-04-30 | 4:33 | 50.298
2022-04-30 | 4:33 | 50.297
2022-04-30 | 4:33 | 50.297
2022-04-30 | 4:33 | 50.298
2022-04-30 | 4:33 | 50.299
2022-04-30 | 4:33 | 50.302
2022-04-30 | 4:33 | 50.303
2022-04-30 | 4:33 | 50.303
2022-04-30 | 4:33 | 50.303
2022-04-30 | 4:33 | 50.303
2022-04-30 | 4:33 | 50.303
2022-04-30 | 4:33 | 50.301
2022-04-30 | 4:33 | 50.301
2022-04-30 | 4:33 | 50.299
2022-04-30 | 4:33 | 50.298
2022-04-30 | 4:33 | 50.296
2022-04-30 | 4:34 | 50.292
2022-04-30 | 4:34 | 50.289
2022-04-30 | 4:34 | 50.289
2022-04-30 | 4:34 | 50.288
2022-04-30 | 4:34 | 50.287
2022-04-30 | 4:34 | 50.289
2022-04-30 | 4:34 | 50.29
2022-04-30 | 4:34 | 50.292
2022-04-30 | 4:34 | 50.295
2022-04-30 | 4:34 | 50.298
2022-04-30 | 4:34 | 50.302
2022-04-30 | 4:34 | 50.302
2022-04-30 | 4:34 | 50.302
2022-04-30 | 4:34 | 50.305
2022-04-30 | 4:34 | 50.303
2022-04-30 | 4:34 | 50.3
2022-04-30 | 4:34 | 50.298
2022-04-30 | 4:34 | 50.294
2022-04-30 | 4:34 | 50.292
2022-04-30 | 4:34 | 50.288
2022-04-30 | 4:34 | 50.284
2022-04-30 | 4:34 | 50.282
2022-04-30 | 4:34 | 50.281
2022-04-30 | 4:34 | 50.28
2022-04-30 | 4:34 | 50.283
2022-04-30 | 4:34 | 50.284
2022-04-30 | 4:34 | 50.283
2022-04-30 | 4:34 | 50.283
2022-04-30 | 4:34 | 50.282
2022-04-30 | 4:34 | 50.284
2022-04-30 | 4:34 | 50.283
2022-04-30 | 4:34 | 50.281
2022-04-30 | 4:34 | 50.279
2022-04-30 | 4:34 | 50.277
2022-04-30 | 4:34 | 50.276
2022-04-30 | 4:34 | 50.274
2022-04-30 | 4:34 | 50.272
2022-04-30 | 4:34 | 50.273
2022-04-30 | 4:34 | 50.272
2022-04-30 | 4:34 | 50.271
2022-04-30 | 4:34 | 50.271
2022-04-30 | 4:34 | 50.269
2022-04-30 | 4:34 | 50.269
2022-04-30 | 4:34 | 50.267
2022-04-30 | 4:34 | 50.268
2022-04-30 | 4:34 | 50.268
2022-04-30 | 4:34 | 50.268
2022-04-30 | 4:34 | 50.267
2022-04-30 | 4:34 | 50.266
2022-04-30 | 4:34 | 50.264
2022-04-30 | 4:34 | 50.263
2022-04-30 | 4:34 | 50.26
2022-04-30 | 4:34 | 50.258
2022-04-30 | 4:34 | 50.258
2022-04-30 | 4:34 | 50.256
2022-04-30 | 4:34 | 50.252
2022-04-30 | 4:34 | 50.252
2022-04-30 | 4:34 | 50.25
2022-04-30 | 4:34 | 50.249
2022-04-30 | 4:34 | 50.248
2022-04-30 | 4:34 | 50.249
2022-04-30 | 4:35 | 50.248
2022-04-30 | 4:35 | 50.249
2022-04-30 | 4:35 | 50.247
2022-04-30 | 4:35 | 50.247
2022-04-30 | 4:35 | 50.247
2022-04-30 | 4:35 | 50.246
2022-04-30 | 4:35 | 50.244
2022-04-30 | 4:35 | 50.244
2022-04-30 | 4:35 | 50.244
2022-04-30 | 4:35 | 50.244
2022-04-30 | 4:35 | 50.241
2022-04-30 | 4:35 | 50.24
2022-04-30 | 4:35 | 50.239
2022-04-30 | 4:35 | 50.239
2022-04-30 | 4:35 | 50.237
2022-04-30 | 4:35 | 50.236
2022-04-30 | 4:35 | 50.234
2022-04-30 | 4:35 | 50.238
2022-04-30 | 4:35 | 50.242
2022-04-30 | 4:35 | 50.244
2022-04-30 | 4:35 | 50.244
2022-04-30 | 4:35 | 50.244
2022-04-30 | 4:35 | 50.244
2022-04-30 | 4:35 | 50.241
2022-04-30 | 4:35 | 50.238
2022-04-30 | 4:35 | 50.235
2022-04-30 | 4:35 | 50.232
2022-04-30 | 4:35 | 50.228
2022-04-30 | 4:35 | 50.224
2022-04-30 | 4:35 | 50.223
2022-04-30 | 4:35 | 50.22
2022-04-30 | 4:35 | 50.219
2022-04-30 | 4:35 | 50.216
2022-04-30 | 4:35 | 50.215
2022-04-30 | 4:35 | 50.215
2022-04-30 | 4:35 | 50.214
2022-04-30 | 4:35 | 50.213
2022-04-30 | 4:35 | 50.211
2022-04-30 | 4:35 | 50.21
2022-04-30 | 4:35 | 50.211
2022-04-30 | 4:35 | 50.21
2022-04-30 | 4:35 | 50.21
2022-04-30 | 4:35 | 50.21
2022-04-30 | 4:35 | 50.208
2022-04-30 | 4:35 | 50.207
2022-04-30 | 4:35 | 50.205
2022-04-30 | 4:35 | 50.206
2022-04-30 | 4:35 | 50.205
2022-04-30 | 4:35 | 50.205
2022-04-30 | 4:35 | 50.205
2022-04-30 | 4:35 | 50.206
2022-04-30 | 4:35 | 50.206
2022-04-30 | 4:35 | 50.207
2022-04-30 | 4:35 | 50.206
2022-04-30 | 4:35 | 50.207
2022-04-30 | 4:35 | 50.206
2022-04-30 | 4:35 | 50.205
2022-04-30 | 4:35 | 50.204
2022-04-30 | 4:35 | 50.202
2022-04-30 | 4:36 | 50.199
2022-04-30 | 4:36 | 50.196
2022-04-30 | 4:36 | 50.195
2022-04-30 | 4:36 | 50.194
2022-04-30 | 4:36 | 50.194
2022-04-30 | 4:36 | 50.193
2022-04-30 | 4:36 | 50.192
2022-04-30 | 4:36 | 50.192
2022-04-30 | 4:36 | 50.191
2022-04-30 | 4:36 | 50.191
2022-04-30 | 4:36 | 50.189
2022-04-30 | 4:36 | 50.185
2022-04-30 | 4:36 | 50.181
2022-04-30 | 4:36 | 50.177
2022-04-30 | 4:36 | 50.175
2022-04-30 | 4:36 | 50.173
2022-04-30 | 4:36 | 50.173
2022-04-30 | 4:36 | 50.176
2022-04-30 | 4:36 | 50.177
2022-04-30 | 4:36 | 50.177
2022-04-30 | 4:36 | 50.176
2022-04-30 | 4:36 | 50.178
2022-04-30 | 4:36 | 50.178
2022-04-30 | 4:36 | 50.175
2022-04-30 | 4:36 | 50.175
2022-04-30 | 4:36 | 50.175
2022-04-30 | 4:36 | 50.175
2022-04-30 | 4:36 | 50.173
2022-04-30 | 4:36 | 50.171
2022-04-30 | 4:36 | 50.17
2022-04-30 | 4:36 | 50.168
2022-04-30 | 4:36 | 50.166
2022-04-30 | 4:36 | 50.162
2022-04-30 | 4:36 | 50.161
2022-04-30 | 4:36 | 50.159
2022-04-30 | 4:36 | 50.159
2022-04-30 | 4:36 | 50.16
2022-04-30 | 4:36 | 50.163
2022-04-30 | 4:36 | 50.163
2022-04-30 | 4:36 | 50.163
2022-04-30 | 4:36 | 50.163
2022-04-30 | 4:36 | 50.164
2022-04-30 | 4:36 | 50.163
2022-04-30 | 4:36 | 50.161
2022-04-30 | 4:36 | 50.158
2022-04-30 | 4:36 | 50.157
2022-04-30 | 4:36 | 50.153
2022-04-30 | 4:36 | 50.153
2022-04-30 | 4:36 | 50.152
2022-04-30 | 4:36 | 50.152
2022-04-30 | 4:36 | 50.151
2022-04-30 | 4:36 | 50.151
2022-04-30 | 4:36 | 50.153
2022-04-30 | 4:36 | 50.155
2022-04-30 | 4:36 | 50.155
2022-04-30 | 4:36 | 50.156
2022-04-30 | 4:36 | 50.157
2022-04-30 | 4:36 | 50.157
2022-04-30 | 4:36 | 50.157
2022-04-30 | 4:36 | 50.158
2022-04-30 | 4:36 | 50.159
2022-04-30 | 4:37 | 50.16
2022-04-30 | 4:37 | 50.159
2022-04-30 | 4:37 | 50.16
2022-04-30 | 4:37 | 50.16
2022-04-30 | 4:37 | 50.159
2022-04-30 | 4:37 | 50.157
2022-04-30 | 4:37 | 50.156
2022-04-30 | 4:37 | 50.156
2022-04-30 | 4:37 | 50.155
2022-04-30 | 4:37 | 50.153
2022-04-30 | 4:37 | 50.15
2022-04-30 | 4:37 | 50.148
2022-04-30 | 4:37 | 50.143
2022-04-30 | 4:37 | 50.136
2022-04-30 | 4:37 | 50.131
2022-04-30 | 4:37 | 50.124
2022-04-30 | 4:37 | 50.119
2022-04-30 | 4:37 | 50.115
2022-04-30 | 4:37 | 50.111
2022-04-30 | 4:37 | 50.111
2022-04-30 | 4:37 | 50.107
2022-04-30 | 4:37 | 50.106
2022-04-30 | 4:37 | 50.106
2022-04-30 | 4:37 | 50.106
2022-04-30 | 4:37 | 50.106
2022-04-30 | 4:37 | 50.108
2022-04-30 | 4:37 | 50.11
2022-04-30 | 4:37 | 50.114
2022-04-30 | 4:37 | 50.115
2022-04-30 | 4:37 | 50.116
2022-04-30 | 4:37 | 50.115
2022-04-30 | 4:37 | 50.115
2022-04-30 | 4:37 | 50.115
2022-04-30 | 4:37 | 50.115
2022-04-30 | 4:37 | 50.117
2022-04-30 | 4:37 | 50.119
2022-04-30 | 4:37 | 50.119
2022-04-30 | 4:37 | 50.12
2022-04-30 | 4:37 | 50.121
2022-04-30 | 4:37 | 50.122
2022-04-30 | 4:37 | 50.123
2022-04-30 | 4:37 | 50.124
2022-04-30 | 4:37 | 50.124
2022-04-30 | 4:37 | 50.124
2022-04-30 | 4:37 | 50.121
2022-04-30 | 4:37 | 50.121
2022-04-30 | 4:37 | 50.119
2022-04-30 | 4:37 | 50.117
2022-04-30 | 4:37 | 50.115
2022-04-30 | 4:37 | 50.112
2022-04-30 | 4:37 | 50.111
2022-04-30 | 4:37 | 50.109
2022-04-30 | 4:37 | 50.109
2022-04-30 | 4:37 | 50.108
2022-04-30 | 4:37 | 50.107
2022-04-30 | 4:37 | 50.104
2022-04-30 | 4:37 | 50.103
2022-04-30 | 4:37 | 50.101
2022-04-30 | 4:37 | 50.1
2022-04-30 | 4:38 | 50.099
2022-04-30 | 4:38 | 50.099
2022-04-30 | 4:38 | 50.098
2022-04-30 | 4:38 | 50.097
2022-04-30 | 4:38 | 50.097
2022-04-30 | 4:38 | 50.096
2022-04-30 | 4:38 | 50.097
2022-04-30 | 4:38 | 50.096
2022-04-30 | 4:38 | 50.096
2022-04-30 | 4:38 | 50.096
2022-04-30 | 4:38 | 50.095
2022-04-30 | 4:38 | 50.095
2022-04-30 | 4:38 | 50.092
2022-04-30 | 4:38 | 50.09
2022-04-30 | 4:38 | 50.088
2022-04-30 | 4:38 | 50.086
2022-04-30 | 4:38 | 50.085
2022-04-30 | 4:38 | 50.086
2022-04-30 | 4:38 | 50.088
2022-04-30 | 4:38 | 50.091
2022-04-30 | 4:38 | 50.092
2022-04-30 | 4:38 | 50.095
2022-04-30 | 4:38 | 50.097
2022-04-30 | 4:38 | 50.099
2022-04-30 | 4:38 | 50.097
2022-04-30 | 4:38 | 50.098
2022-04-30 | 4:38 | 50.099
2022-04-30 | 4:38 | 50.098
2022-04-30 | 4:38 | 50.096
2022-04-30 | 4:38 | 50.096
2022-04-30 | 4:38 | 50.093
2022-04-30 | 4:38 | 50.09
2022-04-30 | 4:38 | 50.087
2022-04-30 | 4:38 | 50.088
2022-04-30 | 4:38 | 50.087
2022-04-30 | 4:38 | 50.089
2022-04-30 | 4:38 | 50.09
2022-04-30 | 4:38 | 50.093
2022-04-30 | 4:38 | 50.096
2022-04-30 | 4:38 | 50.095
2022-04-30 | 4:38 | 50.095
2022-04-30 | 4:38 | 50.096
2022-04-30 | 4:38 | 50.095
2022-04-30 | 4:38 | 50.092
2022-04-30 | 4:38 | 50.089
2022-04-30 | 4:38 | 50.088
2022-04-30 | 4:38 | 50.086
2022-04-30 | 4:38 | 50.085
2022-04-30 | 4:38 | 50.086
2022-04-30 | 4:38 | 50.086
2022-04-30 | 4:38 | 50.087
2022-04-30 | 4:38 | 50.087
2022-04-30 | 4:38 | 50.087
2022-04-30 | 4:38 | 50.085
2022-04-30 | 4:38 | 50.084
2022-04-30 | 4:38 | 50.084
2022-04-30 | 4:38 | 50.082
2022-04-30 | 4:38 | 50.082
2022-04-30 | 4:38 | 50.08
2022-04-30 | 4:38 | 50.075
2022-04-30 | 4:38 | 50.072
2022-04-30 | 4:39 | 50.071
2022-04-30 | 4:39 | 50.068
2022-04-30 | 4:39 | 50.067
2022-04-30 | 4:39 | 50.069
2022-04-30 | 4:39 | 50.069
2022-04-30 | 4:39 | 50.073
2022-04-30 | 4:39 | 50.075
2022-04-30 | 4:39 | 50.078
2022-04-30 | 4:39 | 50.082
2022-04-30 | 4:39 | 50.082
2022-04-30 | 4:39 | 50.083
2022-04-30 | 4:39 | 50.084
2022-04-30 | 4:39 | 50.084
2022-04-30 | 4:39 | 50.084
2022-04-30 | 4:39 | 50.083
2022-04-30 | 4:39 | 50.082
2022-04-30 | 4:39 | 50.081
2022-04-30 | 4:39 | 50.08
2022-04-30 | 4:39 | 50.08
2022-04-30 | 4:39 | 50.08
2022-04-30 | 4:39 | 50.08
2022-04-30 | 4:39 | 50.079
2022-04-30 | 4:39 | 50.081
2022-04-30 | 4:39 | 50.082
2022-04-30 | 4:39 | 50.083
2022-04-30 | 4:39 | 50.083
2022-04-30 | 4:39 | 50.083
2022-04-30 | 4:39 | 50.084
2022-04-30 | 4:39 | 50.084
2022-04-30 | 4:39 | 50.084
2022-04-30 | 4:39 | 50.084
2022-04-30 | 4:39 | 50.086
2022-04-30 | 4:39 | 50.086
2022-04-30 | 4:39 | 50.084
2022-04-30 | 4:39 | 50.084
2022-04-30 | 4:39 | 50.082
2022-04-30 | 4:39 | 50.08
2022-04-30 | 4:39 | 50.077
2022-04-30 | 4:39 | 50.077
2022-04-30 | 4:39 | 50.075
2022-04-30 | 4:39 | 50.074
2022-04-30 | 4:39 | 50.074
2022-04-30 | 4:39 | 50.072
2022-04-30 | 4:39 | 50.072
2022-04-30 | 4:39 | 50.071
2022-04-30 | 4:39 | 50.07
2022-04-30 | 4:39 | 50.07
2022-04-30 | 4:39 | 50.07
2022-04-30 | 4:39 | 50.071
2022-04-30 | 4:39 | 50.072
2022-04-30 | 4:39 | 50.074
2022-04-30 | 4:39 | 50.074
2022-04-30 | 4:39 | 50.076
2022-04-30 | 4:39 | 50.076
2022-04-30 | 4:39 | 50.076
2022-04-30 | 4:39 | 50.077
2022-04-30 | 4:39 | 50.075
2022-04-30 | 4:39 | 50.075
2022-04-30 | 4:39 | 50.077
2022-04-30 | 4:40 | 50.074
2022-04-30 | 4:40 | 50.072
2022-04-30 | 4:40 | 50.069
2022-04-30 | 4:40 | 50.068
2022-04-30 | 4:40 | 50.067
2022-04-30 | 4:40 | 50.066
2022-04-30 | 4:40 | 50.066
2022-04-30 | 4:40 | 50.064
2022-04-30 | 4:40 | 50.067
2022-04-30 | 4:40 | 50.066
2022-04-30 | 4:40 | 50.067
2022-04-30 | 4:40 | 50.067
2022-04-30 | 4:40 | 50.065
2022-04-30 | 4:40 | 50.064
2022-04-30 | 4:40 | 50.065
2022-04-30 | 4:40 | 50.066
2022-04-30 | 4:40 | 50.068
2022-04-30 | 4:40 | 50.067
2022-04-30 | 4:40 | 50.067
2022-04-30 | 4:40 | 50.067
2022-04-30 | 4:40 | 50.064
2022-04-30 | 4:40 | 50.063
2022-04-30 | 4:40 | 50.061
2022-04-30 | 4:40 | 50.06
2022-04-30 | 4:40 | 50.057
2022-04-30 | 4:40 | 50.055
2022-04-30 | 4:40 | 50.054
2022-04-30 | 4:40 | 50.054
2022-04-30 | 4:40 | 50.052
2022-04-30 | 4:40 | 50.051
2022-04-30 | 4:40 | 50.048
2022-04-30 | 4:40 | 50.047
2022-04-30 | 4:40 | 50.046
2022-04-30 | 4:40 | 50.045
2022-04-30 | 4:40 | 50.043
2022-04-30 | 4:40 | 50.041
2022-04-30 | 4:40 | 50.04
2022-04-30 | 4:40 | 50.04
2022-04-30 | 4:40 | 50.04
2022-04-30 | 4:40 | 50.04
2022-04-30 | 4:40 | 50.041
2022-04-30 | 4:40 | 50.045
2022-04-30 | 4:40 | 50.049
2022-04-30 | 4:40 | 50.049
2022-04-30 | 4:40 | 50.051
2022-04-30 | 4:40 | 50.055
2022-04-30 | 4:40 | 50.055
2022-04-30 | 4:40 | 50.054
2022-04-30 | 4:40 | 50.053
2022-04-30 | 4:40 | 50.054
2022-04-30 | 4:40 | 50.052
2022-04-30 | 4:40 | 50.051
2022-04-30 | 4:40 | 50.05
2022-04-30 | 4:40 | 50.048
2022-04-30 | 4:40 | 50.047
2022-04-30 | 4:40 | 50.045
2022-04-30 | 4:40 | 50.044
2022-04-30 | 4:40 | 50.045
2022-04-30 | 4:40 | 50.044
2022-04-30 | 4:40 | 50.043
2022-04-30 | 4:40 | 50.042
2022-04-30 | 4:41 | 50.043
2022-04-30 | 4:41 | 50.043
2022-04-30 | 4:41 | 50.043
2022-04-30 | 4:41 | 50.043
2022-04-30 | 4:41 | 50.042
2022-04-30 | 4:41 | 50.038
2022-04-30 | 4:41 | 50.038
2022-04-30 | 4:41 | 50.039
2022-04-30 | 4:41 | 50.042
2022-04-30 | 4:41 | 50.043
2022-04-30 | 4:41 | 50.044
2022-04-30 | 4:41 | 50.046
2022-04-30 | 4:41 | 50.049
2022-04-30 | 4:41 | 50.05
2022-04-30 | 4:41 | 50.052
2022-04-30 | 4:41 | 50.053
2022-04-30 | 4:41 | 50.052
2022-04-30 | 4:41 | 50.05
2022-04-30 | 4:41 | 50.049
2022-04-30 | 4:41 | 50.046
2022-04-30 | 4:41 | 50.044
2022-04-30 | 4:41 | 50.039
2022-04-30 | 4:41 | 50.036
2022-04-30 | 4:41 | 50.034
2022-04-30 | 4:41 | 50.033
2022-04-30 | 4:41 | 50.03
2022-04-30 | 4:41 | 50.03
2022-04-30 | 4:41 | 50.031
2022-04-30 | 4:41 | 50.034
2022-04-30 | 4:41 | 50.035
2022-04-30 | 4:41 | 50.036
2022-04-30 | 4:41 | 50.037
2022-04-30 | 4:41 | 50.036
2022-04-30 | 4:41 | 50.036
2022-04-30 | 4:41 | 50.035
2022-04-30 | 4:41 | 50.035
2022-04-30 | 4:41 | 50.032
2022-04-30 | 4:41 | 50.03
2022-04-30 | 4:41 | 50.03
2022-04-30 | 4:41 | 50.029
2022-04-30 | 4:41 | 50.028
2022-04-30 | 4:41 | 50.027
2022-04-30 | 4:41 | 50.028
2022-04-30 | 4:41 | 50.027
2022-04-30 | 4:41 | 50.027
2022-04-30 | 4:41 | 50.027
2022-04-30 | 4:41 | 50.029
2022-04-30 | 4:41 | 50.03
2022-04-30 | 4:41 | 50.03
2022-04-30 | 4:41 | 50.032
2022-04-30 | 4:41 | 50.033
2022-04-30 | 4:41 | 50.034
2022-04-30 | 4:41 | 50.037
2022-04-30 | 4:41 | 50.037
2022-04-30 | 4:41 | 50.039
2022-04-30 | 4:41 | 50.04
2022-04-30 | 4:41 | 50.039
2022-04-30 | 4:41 | 50.041
2022-04-30 | 4:41 | 50.041
2022-04-30 | 4:42 | 50.041
2022-04-30 | 4:42 | 50.042
2022-04-30 | 4:42 | 50.044
2022-04-30 | 4:42 | 50.047
2022-04-30 | 4:42 | 50.048
2022-04-30 | 4:42 | 50.05
2022-04-30 | 4:42 | 50.051
2022-04-30 | 4:42 | 50.052
2022-04-30 | 4:42 | 50.051
2022-04-30 | 4:42 | 50.05
2022-04-30 | 4:42 | 50.049
2022-04-30 | 4:42 | 50.049
2022-04-30 | 4:42 | 50.05
2022-04-30 | 4:42 | 50.051
2022-04-30 | 4:42 | 50.053
2022-04-30 | 4:42 | 50.054
2022-04-30 | 4:42 | 50.054
2022-04-30 | 4:42 | 50.053
2022-04-30 | 4:42 | 50.054
2022-04-30 | 4:42 | 50.054
2022-04-30 | 4:42 | 50.052
2022-04-30 | 4:42 | 50.05
2022-04-30 | 4:42 | 50.049
2022-04-30 | 4:42 | 50.049
2022-04-30 | 4:42 | 50.046
2022-04-30 | 4:42 | 50.044
2022-04-30 | 4:42 | 50.043
2022-04-30 | 4:42 | 50.043
2022-04-30 | 4:42 | 50.04
2022-04-30 | 4:42 | 50.039
2022-04-30 | 4:42 | 50.041
2022-04-30 | 4:42 | 50.041
2022-04-30 | 4:42 | 50.041
2022-04-30 | 4:42 | 50.04
2022-04-30 | 4:42 | 50.041
2022-04-30 | 4:42 | 50.04
2022-04-30 | 4:42 | 50.039
2022-04-30 | 4:42 | 50.037
2022-04-30 | 4:42 | 50.037
2022-04-30 | 4:42 | 50.037
2022-04-30 | 4:42 | 50.037
2022-04-30 | 4:42 | 50.036
2022-04-30 | 4:42 | 50.035
2022-04-30 | 4:42 | 50.035
2022-04-30 | 4:42 | 50.034
2022-04-30 | 4:42 | 50.033
2022-04-30 | 4:42 | 50.033
2022-04-30 | 4:42 | 50.03
2022-04-30 | 4:42 | 50.029
2022-04-30 | 4:42 | 50.028
2022-04-30 | 4:42 | 50.028
2022-04-30 | 4:42 | 50.026
2022-04-30 | 4:42 | 50.024
2022-04-30 | 4:42 | 50.024
2022-04-30 | 4:42 | 50.024
2022-04-30 | 4:42 | 50.025
2022-04-30 | 4:42 | 50.026
2022-04-30 | 4:42 | 50.028
2022-04-30 | 4:42 | 50.028
2022-04-30 | 4:42 | 50.03
2022-04-30 | 4:42 | 50.031
2022-04-30 | 4:43 | 50.032
2022-04-30 | 4:43 | 50.032
2022-04-30 | 4:43 | 50.031
2022-04-30 | 4:43 | 50.03
2022-04-30 | 4:43 | 50.032
2022-04-30 | 4:43 | 50.033
2022-04-30 | 4:43 | 50.034
2022-04-30 | 4:43 | 50.034
2022-04-30 | 4:43 | 50.035
2022-04-30 | 4:43 | 50.036
2022-04-30 | 4:43 | 50.036
2022-04-30 | 4:43 | 50.035
2022-04-30 | 4:43 | 50.034
2022-04-30 | 4:43 | 50.032
2022-04-30 | 4:43 | 50.03
2022-04-30 | 4:43 | 50.029
2022-04-30 | 4:43 | 50.027
2022-04-30 | 4:43 | 50.023
2022-04-30 | 4:43 | 50.021
2022-04-30 | 4:43 | 50.021
2022-04-30 | 4:43 | 50.022
2022-04-30 | 4:43 | 50.023
2022-04-30 | 4:43 | 50.022
2022-04-30 | 4:43 | 50.024
2022-04-30 | 4:43 | 50.024
2022-04-30 | 4:43 | 50.024
2022-04-30 | 4:43 | 50.024
2022-04-30 | 4:43 | 50.021
2022-04-30 | 4:43 | 50.019
2022-04-30 | 4:43 | 50.016
2022-04-30 | 4:43 | 50.015
2022-04-30 | 4:43 | 50.015
2022-04-30 | 4:43 | 50.016
2022-04-30 | 4:43 | 50.018
2022-04-30 | 4:43 | 50.021
2022-04-30 | 4:43 | 50.025
2022-04-30 | 4:43 | 50.029
2022-04-30 | 4:43 | 50.032
2022-04-30 | 4:43 | 50.035
2022-04-30 | 4:43 | 50.037
2022-04-30 | 4:43 | 50.039
2022-04-30 | 4:43 | 50.041
2022-04-30 | 4:43 | 50.042
2022-04-30 | 4:43 | 50.044
2022-04-30 | 4:43 | 50.043
2022-04-30 | 4:43 | 50.039
2022-04-30 | 4:43 | 50.036
2022-04-30 | 4:43 | 50.035
2022-04-30 | 4:43 | 50.033
2022-04-30 | 4:43 | 50.03
2022-04-30 | 4:43 | 50.03
2022-04-30 | 4:43 | 50.03
2022-04-30 | 4:43 | 50.032
2022-04-30 | 4:43 | 50.033
2022-04-30 | 4:43 | 50.035
2022-04-30 | 4:43 | 50.037
2022-04-30 | 4:43 | 50.036
2022-04-30 | 4:43 | 50.038
2022-04-30 | 4:43 | 50.039
2022-04-30 | 4:44 | 50.038
2022-04-30 | 4:44 | 50.038
2022-04-30 | 4:44 | 50.037
2022-04-30 | 4:44 | 50.038
2022-04-30 | 4:44 | 50.04
2022-04-30 | 4:44 | 50.04
2022-04-30 | 4:44 | 50.039
2022-04-30 | 4:44 | 50.038
2022-04-30 | 4:44 | 50.038
2022-04-30 | 4:44 | 50.037
2022-04-30 | 4:44 | 50.038
2022-04-30 | 4:44 | 50.04
2022-04-30 | 4:44 | 50.04
2022-04-30 | 4:44 | 50.039
2022-04-30 | 4:44 | 50.04
2022-04-30 | 4:44 | 50.041
2022-04-30 | 4:44 | 50.04
2022-04-30 | 4:44 | 50.043
2022-04-30 | 4:44 | 50.044
2022-04-30 | 4:44 | 50.049
2022-04-30 | 4:44 | 50.053
2022-04-30 | 4:44 | 50.054
2022-04-30 | 4:44 | 50.057
2022-04-30 | 4:44 | 50.06
2022-04-30 | 4:44 | 50.06
2022-04-30 | 4:44 | 50.06
2022-04-30 | 4:44 | 50.061
2022-04-30 | 4:44 | 50.061
2022-04-30 | 4:44 | 50.059
2022-04-30 | 4:44 | 50.058
2022-04-30 | 4:44 | 50.058
2022-04-30 | 4:44 | 50.057
2022-04-30 | 4:44 | 50.057
2022-04-30 | 4:44 | 50.056
2022-04-30 | 4:44 | 50.057
2022-04-30 | 4:44 | 50.057
2022-04-30 | 4:44 | 50.056
2022-04-30 | 4:44 | 50.055
2022-04-30 | 4:44 | 50.055
2022-04-30 | 4:44 | 50.056
2022-04-30 | 4:44 | 50.056
2022-04-30 | 4:44 | 50.058
2022-04-30 | 4:44 | 50.058
2022-04-30 | 4:44 | 50.057
2022-04-30 | 4:44 | 50.057
2022-04-30 | 4:44 | 50.057
2022-04-30 | 4:44 | 50.058
2022-04-30 | 4:44 | 50.058
2022-04-30 | 4:44 | 50.057
2022-04-30 | 4:44 | 50.056
2022-04-30 | 4:44 | 50.056
2022-04-30 | 4:44 | 50.057
2022-04-30 | 4:44 | 50.057
2022-04-30 | 4:44 | 50.059
2022-04-30 | 4:44 | 50.06
2022-04-30 | 4:44 | 50.062
2022-04-30 | 4:44 | 50.061
2022-04-30 | 4:44 | 50.064
2022-04-30 | 4:44 | 50.063
2022-04-30 | 4:44 | 50.061
2022-04-30 | 4:44 | 50.06
2022-04-30 | 4:45 | 50.06
2022-04-30 | 4:45 | 50.058
2022-04-30 | 4:45 | 50.055
2022-04-30 | 4:45 | 50.055
2022-04-30 | 4:45 | 50.055
2022-04-30 | 4:45 | 50.054
2022-04-30 | 4:45 | 50.055
2022-04-30 | 4:45 | 50.059
2022-04-30 | 4:45 | 50.066
2022-04-30 | 4:45 | 50.07
2022-04-30 | 4:45 | 50.072
2022-04-30 | 4:45 | 50.073
2022-04-30 | 4:45 | 50.072
2022-04-30 | 4:45 | 50.071
2022-04-30 | 4:45 | 50.069
2022-04-30 | 4:45 | 50.068
2022-04-30 | 4:45 | 50.067
2022-04-30 | 4:45 | 50.066
2022-04-30 | 4:45 | 50.064
2022-04-30 | 4:45 | 50.062
2022-04-30 | 4:45 | 50.06
2022-04-30 | 4:45 | 50.06
2022-04-30 | 4:45 | 50.059
2022-04-30 | 4:45 | 50.061
2022-04-30 | 4:45 | 50.062
2022-04-30 | 4:45 | 50.064
2022-04-30 | 4:45 | 50.064
2022-04-30 | 4:45 | 50.065
2022-04-30 | 4:45 | 50.066
2022-04-30 | 4:45 | 50.067