## Front
Dynamic Moderation Low and High Performance example spreadsheet
DISCLAIMER: Please note, this file is for illustrative purposes ONLY and should not be relied on, or treated as a substitute for the Service Terms.
Purpose: | To demonstrate how to calculate the k factor for a Settlement period SP with regards to dynamic moderation low and high performance monitoring
Sheets: | Using Excel formulae | Performance monitoring with formulae
| Response | Plot of both the upper and lower bounds of the performance algorithm
| Errors | Plot of scaled errors and rolling_min errors for DML and DMH
| Frequency | Plot of the frequency trace
| Frequency window | Plot of the frequency trace with lower and upper frequency window
Notes: | Example data shown is to demonstrate validation
Green fields are modifiable
Gray fields are NOT modifiable
Variables: | t | Time (s)
| f_hz | Frequency (Hz)
| lfw | Lower frequency window (Hz) | This is a lagged rolling minimum calculation
| unr | Upper bound without ramp limits (MW) | This is the response curve applied to the lower frequency window
| ubw | Upper bound without contracted volume factor (MW) | This is unr with the ramp limit applied to decreases
| ub | Upper bound (MW) | This is ubw with contracted volume factor
| ufw | Upper frequency window (Hz) | This is a lagged rolling maximum calculation
| lnr | Lower bound without ramp limits (MW) | This is the response curve applied to the upper frequency window
| lbw | Lower bound without contracted volume factor (MW) | This is lnr with the ramp limit applied to increases
| lb | Lower bound (MW) | This is lbw with contracted volume factor
| target | Middle of bounds (MW) | This is (ub+lb)/2
| p_mw | p_mw from performance files (MW)
| baseline_mw | Baseline from performance files (MW)
| availability | Availability flag from performance files
| H_availability | Segregated availability for High
| L_availability | Segregated availability for Low
| r | Total response | This is p_mw - baseline_mw
| volume_error | Contracted volume used to calculate the errors | Q or P
| errors | Errors for Low and High | This is: if lfw>50 then error/Q ; if ufw<50 then error/P ; otherwise error/max(P,Q)
| errors rolling | Rolling minimum errors for Low and High over 0.2s

## Using Excel formulae
t | f_hz | lfw | unr | ubw | ub | ufw | lnr | lbw | lb | target | p_mw | baseline_mw | availability | H_availability | L_availability | r | volume_error | errors | rolling_errors |  |  | f_hz | R % | R MW | [10 empty] | .
0 | 50 | 50 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0 |  |  | 49.8 | 100% | 10 | DML | 10 | P |  | K factor cal | error | k |  | Decimal | Bit
0.05 | 50 | 50 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0 |  |  | 49.9 | 5% | 0.5 | DMH | 10 | Q |  | A- | 0 | 1 | Low service | 4 | 4
0.1 | 50 | 50 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0 |  |  | 49.985 | 0% | 0 | ramp | 0.1 | t*rrmin |  | A | 0.03 | 1 | High service | 8 | 3
0.15 | 50 | 50 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0 |  |  | 50.015 | 0% | 0 | service type | 12 | DMLH |  | B | 0.07 | 0
0.2 | 50 | 50 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0 |  |  | 50.1 | -5% | 0.5 |  |  |  |  | B+ | 0.1 | 0
0.25 | 50 | 50 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0 |  |  | 50.2 | -100% | 10
0.3 | 50 | 50 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
0.35 | 50 | 50 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0 | 0.55 Grace period | 0
0.4 | 50 | 50 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
0.45 | 50 | 50 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0 | Contracted availability Low | AVAILABLE
0.5 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0 | Contracted availability High | AVAILABLE
0.55 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
0.6 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0 | SP Results
0.65 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0 | error | 0
0.7 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0 | K factor | 1
0.75 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0 | Availability for H | 1
0.8 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0 | Final K for H | 1
0.85 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0 | Availability for L | 1
0.9 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0 | Final K for L | 1
0.95 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1.05 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.1 | 1 | 5.5 | 5.5 | 0 | 12 | 1 | 1 | 5.5 | 10 | 0 | 0
1.1 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.2 | 2 | 6 | 6 | 0 | 12 | 1 | 1 | 6 | 10 | 0 | 0
1.15 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.3 | 3 | 6.5 | 6.5 | 0 | 12 | 1 | 1 | 6.5 | 10 | 0 | 0
1.2 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.4 | 4 | 7 | 7 | 0 | 12 | 1 | 1 | 7 | 10 | 0 | 0
1.25 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.5 | 5 | 7.5 | 7.5 | 0 | 12 | 1 | 1 | 7.5 | 10 | 0 | 0
1.3 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.6 | 6 | 8 | 8 | 0 | 12 | 1 | 1 | 8 | 10 | 0 | 0
1.35 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.7 | 7 | 8.5 | 8.5 | 0 | 12 | 1 | 1 | 8.5 | 10 | 0 | 0
1.4 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.8 | 8 | 9 | 9 | 0 | 12 | 1 | 1 | 9 | 10 | 0 | 0
1.45 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.9 | 9 | 9.5 | 9.5 | 0 | 12 | 1 | 1 | 9.5 | 10 | 0 | 0
1.5 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1.55 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1.6 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1.65 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1.7 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1.75 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1.8 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1.85 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1.9 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1.95 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
2 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
2.05 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
2.1 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
2.15 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
2.2 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
2.25 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
2.3 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
2.35 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
2.4 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
2.45 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
2.5 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
2.55 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
2.6 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
2.65 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
2.7 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
2.75 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
2.8 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
2.85 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
2.9 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
2.95 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
3 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
3.05 | 50.5 | 50.5 | -1 | 0.9 | 9 | 50.5 | -1 | -1 | -10 | -0.5 | -0.5 | 0 | 12 | 1 | 1 | -0.5 | 10 | 0 | 0
3.1 | 50.5 | 50.5 | -1 | 0.8 | 8 | 50.5 | -1 | -1 | -10 | -1 | -1 | 0 | 12 | 1 | 1 | -1 | 10 | 0 | 0
3.15 | 50.5 | 50.5 | -1 | 0.7 | 7 | 50.5 | -1 | -1 | -10 | -1.5 | -1.5 | 0 | 12 | 1 | 1 | -1.5 | 10 | 0 | 0
3.2 | 50.5 | 50.5 | -1 | 0.6 | 6 | 50.5 | -1 | -1 | -10 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
3.25 | 50.5 | 50.5 | -1 | 0.5 | 5 | 50.5 | -1 | -1 | -10 | -2.5 | -2.5 | 0 | 12 | 1 | 1 | -2.5 | 10 | 0 | 0
3.3 | 50.5 | 50.5 | -1 | 0.4 | 4 | 50.5 | -1 | -1 | -10 | -3 | -3 | 0 | 12 | 1 | 1 | -3 | 10 | 0 | 0
3.35 | 50.5 | 50.5 | -1 | 0.3 | 3 | 50.5 | -1 | -1 | -10 | -3.5 | -3.5 | 0 | 12 | 1 | 1 | -3.5 | 10 | 0 | 0
3.4 | 50.5 | 50.5 | -1 | 0.2 | 2 | 50.5 | -1 | -1 | -10 | -4 | -4 | 0 | 12 | 1 | 1 | -4 | 10 | 0 | 0
3.45 | 50.5 | 50.5 | -1 | 0.1 | 1 | 50.5 | -1 | -1 | -10 | -4.5 | -4.5 | 0 | 12 | 1 | 1 | -4.5 | 10 | 0 | 0
3.5 | 50.5 | 50.5 | -1 | 0 | 0 | 50.5 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
3.55 | 50.5 | 50.5 | -1 | -0.1 | -1 | 50.5 | -1 | -1 | -10 | -5.5 | -5.5 | 0 | 12 | 1 | 1 | -5.5 | 10 | 0 | 0
3.6 | 50.5 | 50.5 | -1 | -0.2 | -2 | 50.5 | -1 | -1 | -10 | -6 | -6 | 0 | 12 | 1 | 1 | -6 | 10 | 0 | 0
3.65 | 50.5 | 50.5 | -1 | -0.3 | -3 | 50.5 | -1 | -1 | -10 | -6.5 | -6.5 | 0 | 12 | 1 | 1 | -6.5 | 10 | 0 | 0
3.7 | 50.5 | 50.5 | -1 | -0.4 | -4 | 50.5 | -1 | -1 | -10 | -7 | -7 | 0 | 12 | 1 | 1 | -7 | 10 | 0 | 0
3.75 | 50.5 | 50.5 | -1 | -0.5 | -5 | 50.5 | -1 | -1 | -10 | -7.5 | -7.5 | 0 | 12 | 1 | 1 | -7.5 | 10 | 0 | 0
3.8 | 50.5 | 50.5 | -1 | -0.6 | -6 | 50.5 | -1 | -1 | -10 | -8 | -8 | 0 | 12 | 1 | 1 | -8 | 10 | 0 | 0
3.85 | 50.5 | 50.5 | -1 | -0.7 | -7 | 50.5 | -1 | -1 | -10 | -8.5 | -8.5 | 0 | 12 | 1 | 1 | -8.5 | 10 | 0 | 0
3.9 | 50.5 | 50.5 | -1 | -0.8 | -8 | 50.5 | -1 | -1 | -10 | -9 | -9 | 0 | 12 | 1 | 1 | -9 | 10 | 0 | 0
3.95 | 50.5 | 50.5 | -1 | -0.9 | -9 | 50.5 | -1 | -1 | -10 | -9.5 | -9.5 | 0 | 12 | 1 | 1 | -9.5 | 10 | 0 | 0
4 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
4.05 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
4.1 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
4.15 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
4.2 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
4.25 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
4.3 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
4.35 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
4.4 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
4.45 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
4.5 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
4.55 | 50.47 | 50.47 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
4.6 | 50.45 | 50.45 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
4.65 | 50.42 | 50.42 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
4.7 | 50.4 | 50.4 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
4.75 | 50.37 | 50.37 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
4.8 | 50.35 | 50.35 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
4.85 | 50.32 | 50.32 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
4.9 | 50.29 | 50.29 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
4.95 | 50.27 | 50.27 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
5 | 50.24 | 50.24 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
5.05 | 50.22 | 50.22 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
5.1 | 50.19 | 50.19 | -0.905 | -0.905 | -9.05 | 50.47 | -1 | -1 | -10 | -9.525 | -9.525 | 0 | 12 | 1 | 1 | -9.525 | 10 | 0 | 0
5.15 | 50.17 | 50.17 | -0.715 | -0.715 | -7.15 | 50.45 | -1 | -1 | -10 | -8.575 | -8.575 | 0 | 12 | 1 | 1 | -8.575 | 10 | 0 | 0
5.2 | 50.14 | 50.14 | -0.43 | -0.43 | -4.3 | 50.42 | -1 | -1 | -10 | -7.15 | -7.15 | 0 | 12 | 1 | 1 | -7.15 | 10 | 0 | 0
5.25 | 50.12 | 50.12 | -0.24 | -0.24 | -2.4 | 50.4 | -1 | -1 | -10 | -6.2 | -6.2 | 0 | 12 | 1 | 1 | -6.2 | 10 | 0 | 0
5.3 | 50.09 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 50.37 | -1 | -1 | -10 | -5.2206 | -5.2206 | 0 | 12 | 1 | 1 | -5.2206 | 10 | 0 | 0
5.35 | 50.06 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.35 | -1 | -1 | -10 | -5.1324 | -5.1324 | 0 | 12 | 1 | 1 | -5.1324 | 10 | 0 | 0
5.4 | 50.04 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.32 | -1 | -1 | -10 | -5.0735 | -5.0735 | 0 | 12 | 1 | 1 | -5.0735 | 10 | 0 | 0
5.45 | 50.01 | 50.01 | 0 | 0 | 0 | 50.29 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
5.5 | 49.99 | 49.99 | 0 | 0 | 0 | 50.27 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
5.55 | 49.96 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.24 | -1 | -1 | -10 | -4.9265 | -4.9265 | 0 | 12 | 1 | 1 | -4.9265 | 10 | 0 | 0
5.6 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.22 | -1 | -1 | -10 | -4.8676 | -4.8676 | 0 | 12 | 1 | 1 | -4.8676 | 10 | 0 | 0
5.65 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.19 | -0.905 | -0.905 | -9.05 | -4.3044 | -4.3044 | 0 | 12 | 1 | 1 | -4.3044 | 10 | 0 | 0
5.7 | 49.88 | 49.88 | 0.24 | 0.24 | 2.4 | 50.17 | -0.715 | -0.805 | -8.05 | -2.825 | -2.825 | 0 | 12 | 1 | 1 | -2.825 | 10 | 0 | 0
5.75 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.14 | -0.43 | -0.705 | -7.05 | -1.375 | -1.375 | 0 | 12 | 1 | 1 | -1.375 | 10 | 0 | 0
5.8 | 49.83 | 49.83 | 0.715 | 0.715 | 7.15 | 50.12 | -0.24 | -0.605 | -6.05 | 0.55 | 0.55 | 0 | 12 | 1 | 1 | 0.55 | 10 | 0 | 0 | [6 empty] | error H | ub<0 | lfw>50
5.85 | 49.81 | 49.81 | 0.905 | 0.905 | 9.05 | 50.09 | -0.044118 | -0.505 | -5.05 | 2 | 2 | 0 | 12 | 1 | 1 | 2 | 10 | 0 | 0 | [6 empty] | error L | lb>0 | ufw<50
5.9 | 49.78 | 49.78 | 1 | 1 | 10 | 50.06 | -0.026471 | -0.405 | -4.05 | 2.975 | 2.975 | 0 | 12 | 1 | 1 | 2.975 | 10 | 0 | 0
5.95 | 49.76 | 49.76 | 1 | 1 | 10 | 50.04 | -0.014706 | -0.305 | -3.05 | 3.475 | 3.475 | 0 | 12 | 1 | 1 | 3.475 | 10 | 0 | 0
6 | 49.73 | 49.73 | 1 | 1 | 10 | 50.01 | 0 | -0.205 | -2.05 | 3.975 | 3.975 | 0 | 12 | 1 | 1 | 3.975 | 10 | 0 | 0
6.05 | 49.71 | 49.71 | 1 | 1 | 10 | 49.99 | 0 | -0.105 | -1.05 | 4.475 | 4.475 | 0 | 12 | 1 | 1 | 4.475 | 10 | 0 | 0
6.1 | 49.68 | 49.68 | 1 | 1 | 10 | 49.96 | 0.014706 | -0.005 | -0.05 | 4.975 | 4.975 | 0 | 12 | 1 | 1 | 4.975 | 10 | 0 | 0
6.15 | 49.65 | 49.65 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
6.2 | 49.63 | 49.63 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
6.25 | 49.6 | 49.6 | 1 | 1 | 10 | 49.88 | 0.24 | 0.14412 | 1.4412 | 5.7206 | 5.7206 | 0 | 12 | 1 | 1 | 5.7206 | 10 | 0 | 0
6.3 | 49.58 | 49.58 | 1 | 1 | 10 | 49.86 | 0.43 | 0.24412 | 2.4412 | 6.2206 | 6.2206 | 0 | 12 | 1 | 1 | 6.2206 | 10 | 0 | 0
6.35 | 49.55 | 49.55 | 1 | 1 | 10 | 49.83 | 0.715 | 0.34412 | 3.4412 | 6.7206 | 6.7206 | 0 | 12 | 1 | 1 | 6.7206 | 10 | 0 | 0
6.4 | 49.53 | 49.53 | 1 | 1 | 10 | 49.81 | 0.905 | 0.44412 | 4.4412 | 7.2206 | 7.2206 | 0 | 12 | 1 | 1 | 7.2206 | 10 | 0 | 0
6.45 | 49.5 | 49.5 | 1 | 1 | 10 | 49.78 | 1 | 0.54412 | 5.4412 | 7.7206 | 7.7206 | 0 | 12 | 1 | 1 | 7.7206 | 10 | 0 | 0
6.5 | 49.5 | 49.5 | 1 | 1 | 10 | 49.76 | 1 | 0.64412 | 6.4412 | 8.2206 | 8.2206 | 0 | 12 | 1 | 1 | 8.2206 | 10 | 0 | 0
6.55 | 49.53 | 49.5 | 1 | 1 | 10 | 49.73 | 1 | 0.74412 | 7.4412 | 8.7206 | 8.7206 | 0 | 12 | 1 | 1 | 8.7206 | 10 | 0 | 0
6.6 | 49.55 | 49.5 | 1 | 1 | 10 | 49.71 | 1 | 0.84412 | 8.4412 | 9.2206 | 9.2206 | 0 | 12 | 1 | 1 | 9.2206 | 10 | 0 | 0
6.65 | 49.58 | 49.5 | 1 | 1 | 10 | 49.68 | 1 | 0.94412 | 9.4412 | 9.7206 | 9.7206 | 0 | 12 | 1 | 1 | 9.7206 | 10 | 0 | 0
6.7 | 49.6 | 49.5 | 1 | 1 | 10 | 49.65 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
6.75 | 49.63 | 49.5 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
6.8 | 49.65 | 49.5 | 1 | 1 | 10 | 49.65 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
6.85 | 49.68 | 49.5 | 1 | 1 | 10 | 49.68 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
6.9 | 49.71 | 49.5 | 1 | 1 | 10 | 49.71 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
6.95 | 49.73 | 49.5 | 1 | 1 | 10 | 49.73 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
7 | 49.76 | 49.5 | 1 | 1 | 10 | 49.76 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
7.05 | 49.78 | 49.5 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
7.1 | 49.81 | 49.53 | 1 | 1 | 10 | 49.81 | 0.905 | 0.905 | 9.05 | 9.525 | 9.525 | 0 | 12 | 1 | 1 | 9.525 | 10 | 0 | 0
7.15 | 49.83 | 49.55 | 1 | 1 | 10 | 49.83 | 0.715 | 0.715 | 7.15 | 8.575 | 8.575 | 0 | 12 | 1 | 1 | 8.575 | 10 | 0 | 0
7.2 | 49.86 | 49.58 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
7.25 | 49.88 | 49.6 | 1 | 1 | 10 | 49.88 | 0.24 | 0.24 | 2.4 | 6.2 | 6.2 | 0 | 12 | 1 | 1 | 6.2 | 10 | 0 | 0
7.3 | 49.91 | 49.63 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
7.35 | 49.94 | 49.65 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
7.4 | 49.96 | 49.68 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
7.45 | 49.99 | 49.71 | 1 | 1 | 10 | 49.99 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
7.5 | 50.01 | 49.73 | 1 | 1 | 10 | 50.01 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
7.55 | 50.04 | 49.76 | 1 | 1 | 10 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 4.9265 | 4.9265 | 0 | 12 | 1 | 1 | 4.9265 | 10 | 0 | 0
7.6 | 50.06 | 49.78 | 1 | 1 | 10 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 4.8676 | 4.8676 | 0 | 12 | 1 | 1 | 4.8676 | 10 | 0 | 0
7.65 | 50.09 | 49.81 | 0.905 | 0.905 | 9.05 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 4.3044 | 4.3044 | 0 | 12 | 1 | 1 | 4.3044 | 10 | 0 | 0
7.7 | 50.12 | 49.83 | 0.715 | 0.805 | 8.05 | 50.12 | -0.24 | -0.24 | -2.4 | 2.825 | 2.825 | 0 | 12 | 1 | 1 | 2.825 | 10 | 0 | 0
7.75 | 50.14 | 49.86 | 0.43 | 0.705 | 7.05 | 50.14 | -0.43 | -0.43 | -4.3 | 1.375 | 1.375 | 0 | 12 | 1 | 1 | 1.375 | 10 | 0 | 0
7.8 | 50.17 | 49.88 | 0.24 | 0.605 | 6.05 | 50.17 | -0.715 | -0.715 | -7.15 | -0.55 | -0.55 | 0 | 12 | 1 | 1 | -0.55 | 10 | 0 | 0
7.85 | 50.19 | 49.91 | 0.044118 | 0.505 | 5.05 | 50.19 | -0.905 | -0.905 | -9.05 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
7.9 | 50.22 | 49.94 | 0.026471 | 0.405 | 4.05 | 50.22 | -1 | -1 | -10 | -2.975 | -2.975 | 0 | 12 | 1 | 1 | -2.975 | 10 | 0 | 0
7.95 | 50.24 | 49.96 | 0.014706 | 0.305 | 3.05 | 50.24 | -1 | -1 | -10 | -3.475 | -3.475 | 0 | 12 | 1 | 1 | -3.475 | 10 | 0 | 0
8 | 50.27 | 49.99 | 0 | 0.205 | 2.05 | 50.27 | -1 | -1 | -10 | -3.975 | -3.975 | 0 | 12 | 1 | 1 | -3.975 | 10 | 0 | 0
8.05 | 50.29 | 50.01 | 0 | 0.105 | 1.05 | 50.29 | -1 | -1 | -10 | -4.475 | -4.475 | 0 | 12 | 1 | 1 | -4.475 | 10 | 0 | 0
8.1 | 50.32 | 50.04 | -0.014706 | 0.005 | 0.05 | 50.32 | -1 | -1 | -10 | -4.975 | -4.975 | 0 | 12 | 1 | 1 | -4.975 | 10 | 0 | 0
8.15 | 50.35 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.35 | -1 | -1 | -10 | -5.1324 | -5.1324 | 0 | 12 | 1 | 1 | -5.1324 | 10 | 0 | 0
8.2 | 50.37 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 50.37 | -1 | -1 | -10 | -5.2206 | -5.2206 | 0 | 12 | 1 | 1 | -5.2206 | 10 | 0 | 0
8.25 | 50.4 | 50.12 | -0.24 | -0.14412 | -1.4412 | 50.4 | -1 | -1 | -10 | -5.7206 | -5.7206 | 0 | 12 | 1 | 1 | -5.7206 | 10 | 0 | 0
8.3 | 50.42 | 50.14 | -0.43 | -0.24412 | -2.4412 | 50.42 | -1 | -1 | -10 | -6.2206 | -6.2206 | 0 | 12 | 1 | 1 | -6.2206 | 10 | 0 | 0
8.35 | 50.45 | 50.17 | -0.715 | -0.34412 | -3.4412 | 50.45 | -1 | -1 | -10 | -6.7206 | -6.7206 | 0 | 12 | 1 | 1 | -6.7206 | 10 | 0 | 0
8.4 | 50.47 | 50.19 | -0.905 | -0.44412 | -4.4412 | 50.47 | -1 | -1 | -10 | -7.2206 | -7.2206 | 0 | 12 | 1 | 1 | -7.2206 | 10 | 0 | 0
8.45 | 50.5 | 50.22 | -1 | -0.54412 | -5.4412 | 50.5 | -1 | -1 | -10 | -7.7206 | -7.7206 | 0 | 12 | 1 | 1 | -7.7206 | 10 | 0 | 0
8.5 | 50.5 | 50.24 | -1 | -0.64412 | -6.4412 | 50.5 | -1 | -1 | -10 | -8.2206 | -8.2206 | 0 | 12 | 1 | 1 | -8.2206 | 10 | 0 | 0
8.55 | 50.47 | 50.27 | -1 | -0.74412 | -7.4412 | 50.5 | -1 | -1 | -10 | -8.7206 | -8.7206 | 0 | 12 | 1 | 1 | -8.7206 | 10 | 0 | 0
8.6 | 50.45 | 50.29 | -1 | -0.84412 | -8.4412 | 50.5 | -1 | -1 | -10 | -9.2206 | -9.2206 | 0 | 12 | 1 | 1 | -9.2206 | 10 | 0 | 0
8.65 | 50.42 | 50.32 | -1 | -0.94412 | -9.4412 | 50.5 | -1 | -1 | -10 | -9.7206 | -9.7206 | 0 | 12 | 1 | 1 | -9.7206 | 10 | 0 | 0
8.7 | 50.39 | 50.35 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
8.75 | 50.37 | 50.37 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
8.8 | 50.34 | 50.34 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
8.85 | 50.32 | 50.32 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
8.9 | 50.29 | 50.29 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
8.95 | 50.26 | 50.26 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
9 | 50.24 | 50.24 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
9.05 | 50.21 | 50.21 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
9.1 | 50.18 | 50.18 | -0.81 | -0.81 | -8.1 | 50.47 | -1 | -1 | -10 | -9.05 | -9.05 | 0 | 12 | 1 | 1 | -9.05 | 10 | 0 | 0
9.15 | 50.16 | 50.16 | -0.62 | -0.62 | -6.2 | 50.45 | -1 | -1 | -10 | -8.1 | -8.1 | 0 | 12 | 1 | 1 | -8.1 | 10 | 0 | 0
9.2 | 50.13 | 50.13 | -0.335 | -0.335 | -3.35 | 50.42 | -1 | -1 | -10 | -6.675 | -6.675 | 0 | 12 | 1 | 1 | -6.675 | 10 | 0 | 0
9.25 | 50.11 | 50.11 | -0.145 | -0.145 | -1.45 | 50.39 | -1 | -1 | -10 | -5.725 | -5.725 | 0 | 12 | 1 | 1 | -5.725 | 10 | 0 | 0
9.3 | 50.08 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 50.37 | -1 | -1 | -10 | -5.1912 | -5.1912 | 0 | 12 | 1 | 1 | -5.1912 | 10 | 0 | 0
9.35 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.34 | -1 | -1 | -10 | -5.1029 | -5.1029 | 0 | 12 | 1 | 1 | -5.1029 | 10 | 0 | 0
9.4 | 50.03 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 50.32 | -1 | -1 | -10 | -5.0441 | -5.0441 | 0 | 12 | 1 | 1 | -5.0441 | 10 | 0 | 0
9.45 | 50 | 50 | 0 | 0 | 0 | 50.29 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
9.5 | 50 | 50 | 0 | 0 | 0 | 50.26 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
9.55 | 50 | 50 | 0 | 0 | 0 | 50.24 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
9.6 | 50 | 50 | 0 | 0 | 0 | 50.21 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
9.65 | 50 | 50 | 0 | 0 | 0 | 50.18 | -0.81 | -0.9 | -9 | -4.5 | -4.5 | 0 | 12 | 1 | 1 | -4.5 | 10 | 0 | 0
9.7 | 50 | 50 | 0 | 0 | 0 | 50.16 | -0.62 | -0.8 | -8 | -4 | -4 | 0 | 12 | 1 | 1 | -4 | 10 | 0 | 0
9.75 | 50 | 50 | 0 | 0 | 0 | 50.13 | -0.335 | -0.7 | -7 | -3.5 | -3.5 | 0 | 12 | 1 | 1 | -3.5 | 10 | 0 | 0
9.8 | 50.01 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.6 | -6 | -3 | -3 | 0 | 12 | 1 | 1 | -3 | 10 | 0 | 0
9.85 | 50.01 | 50 | 0 | 0 | 0 | 50.08 | -0.038235 | -0.5 | -5 | -2.5 | -2.5 | 0 | 12 | 1 | 1 | -2.5 | 10 | 0 | 0
9.9 | 49.99 | 49.99 | 0 | 0 | 0 | 50.05 | -0.020588 | -0.4 | -4 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
9.95 | 49.99 | 49.99 | 0 | 0 | 0 | 50.03 | -0.0088235 | -0.3 | -3 | -1.5 | -1.5 | 0 | 12 | 1 | 1 | -1.5 | 10 | 0 | 0
10 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | -0.2 | -2 | -0.83824 | -0.83824 | 0 | 12 | 1 | 1 | -0.83824 | 10 | 0 | 0
10.05 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | -0.1 | -1 | -0.33824 | -0.33824 | 0 | 12 | 1 | 1 | -0.33824 | 10 | 0 | 0
10.1 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
10.15 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
10.2 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
10.25 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
10.3 | 49.89 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
10.35 | 49.89 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
10.4 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50.01 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
10.45 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
10.5 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
10.55 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 2.7868 | 2.7868 | 0 | 12 | 1 | 1 | 2.7868 | 10 | 0 | 0
10.6 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 2.7868 | 2.7868 | 0 | 12 | 1 | 1 | 2.7868 | 10 | 0 | 0
10.65 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 2.8456 | 2.8456 | 0 | 12 | 1 | 1 | 2.8456 | 10 | 0 | 0
10.7 | 49.94 | 49.85 | 0.525 | 0.525 | 5.25 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 2.7574 | 2.7574 | 0 | 12 | 1 | 1 | 2.7574 | 10 | 0 | 0
10.75 | 49.94 | 49.85 | 0.525 | 0.525 | 5.25 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 2.7574 | 2.7574 | 0 | 12 | 1 | 1 | 2.7574 | 10 | 0 | 0
10.8 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
10.85 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
10.9 | 49.93 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
10.95 | 49.93 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
11 | 49.96 | 49.85 | 0.525 | 0.525 | 5.25 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 2.6985 | 2.6985 | 0 | 12 | 1 | 1 | 2.6985 | 10 | 0 | 0
11.05 | 49.96 | 49.85 | 0.525 | 0.525 | 5.25 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 2.6985 | 2.6985 | 0 | 12 | 1 | 1 | 2.6985 | 10 | 0 | 0
11.1 | 49.99 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
11.15 | 49.99 | 49.91 | 0.044118 | 0.425 | 4.25 | 49.99 | 0 | 0 | 0 | 2.125 | 2.125 | 0 | 12 | 1 | 1 | 2.125 | 10 | 0 | 0
11.2 | 49.99 | 49.91 | 0.044118 | 0.325 | 3.25 | 49.99 | 0 | 0 | 0 | 1.625 | 1.625 | 0 | 12 | 1 | 1 | 1.625 | 10 | 0 | 0
11.25 | 49.99 | 49.93 | 0.032353 | 0.225 | 2.25 | 49.99 | 0 | 0 | 0 | 1.125 | 1.125 | 0 | 12 | 1 | 1 | 1.125 | 10 | 0 | 0
11.3 | 49.96 | 49.93 | 0.032353 | 0.125 | 1.25 | 49.99 | 0 | 0 | 0 | 0.625 | 0.625 | 0 | 12 | 1 | 1 | 0.625 | 10 | 0 | 0
11.35 | 49.96 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 49.99 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
11.4 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
11.45 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
11.5 | 50.05 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.058824 | 0.058824 | 0 | 12 | 1 | 1 | 0.058824 | 10 | 0 | 0
11.55 | 50.05 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
11.6 | 49.97 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
11.65 | 49.97 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
11.7 | 49.92 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
11.75 | 49.92 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
11.8 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
11.85 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
11.9 | 49.94 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
11.95 | 49.94 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
12 | 50.01 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
12.05 | 50.01 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
12.1 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
12.15 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
12.2 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
12.25 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
12.3 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
12.35 | 49.95 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
12.4 | 49.97 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
12.45 | 49.97 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
12.5 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
12.55 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
12.6 | 49.87 | 49.87 | 0.335 | 0.335 | 3.35 | 50.01 | 0 | 0 | 0 | 1.675 | 1.675 | 0 | 12 | 1 | 1 | 1.675 | 10 | 0 | 0
12.65 | 49.87 | 49.87 | 0.335 | 0.335 | 3.35 | 49.99 | 0 | 0 | 0 | 1.675 | 1.675 | 0 | 12 | 1 | 1 | 1.675 | 10 | 0 | 0
12.7 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
12.75 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 2.6691 | 2.6691 | 0 | 12 | 1 | 1 | 2.6691 | 10 | 0 | 0
12.8 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
12.85 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
12.9 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
12.95 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
13 | 49.84 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
13.05 | 49.84 | 49.79 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
13.1 | 49.89 | 49.79 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
13.15 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.12647 | 1.2647 | 5.6324 | 5.6324 | 0 | 12 | 1 | 1 | 5.6324 | 10 | 0 | 0
13.2 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.145 | 1.45 | 5.725 | 5.725 | 0 | 12 | 1 | 1 | 5.725 | 10 | 0 | 0
13.25 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.145 | 1.45 | 5.725 | 5.725 | 0 | 12 | 1 | 1 | 5.725 | 10 | 0 | 0
13.3 | 49.96 | 49.79 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
13.35 | 49.96 | 49.79 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
13.4 | 50.02 | 49.79 | 1 | 1 | 10 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 4.9853 | 4.9853 | 0 | 12 | 1 | 1 | 4.9853 | 10 | 0 | 0
13.45 | 50.02 | 49.79 | 1 | 1 | 10 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 4.9853 | 4.9853 | 0 | 12 | 1 | 1 | 4.9853 | 10 | 0 | 0
13.5 | 50.03 | 49.79 | 1 | 1 | 10 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.9559 | 4.9559 | 0 | 12 | 1 | 1 | 4.9559 | 10 | 0 | 0
13.55 | 50.03 | 49.84 | 0.62 | 0.9 | 9 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.4559 | 4.4559 | 0 | 12 | 1 | 1 | 4.4559 | 10 | 0 | 0
13.6 | 50.02 | 49.84 | 0.62 | 0.8 | 8 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 3.9559 | 3.9559 | 0 | 12 | 1 | 1 | 3.9559 | 10 | 0 | 0
13.65 | 50.02 | 49.89 | 0.145 | 0.7 | 7 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 3.4559 | 3.4559 | 0 | 12 | 1 | 1 | 3.4559 | 10 | 0 | 0
13.7 | 50.08 | 49.89 | 0.145 | 0.6 | 6 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 2.8088 | 2.8088 | 0 | 12 | 1 | 1 | 2.8088 | 10 | 0 | 0
13.75 | 50.08 | 49.89 | 0.145 | 0.5 | 5 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 2.3088 | 2.3088 | 0 | 12 | 1 | 1 | 2.3088 | 10 | 0 | 0
13.8 | 50.01 | 49.89 | 0.145 | 0.4 | 4 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 1.8088 | 1.8088 | 0 | 12 | 1 | 1 | 1.8088 | 10 | 0 | 0
13.85 | 50.01 | 49.96 | 0.014706 | 0.3 | 3 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 1.3088 | 1.3088 | 0 | 12 | 1 | 1 | 1.3088 | 10 | 0 | 0
13.9 | 49.94 | 49.94 | 0.026471 | 0.2 | 2 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.80882 | 0.80882 | 0 | 12 | 1 | 1 | 0.80882 | 10 | 0 | 0
13.95 | 49.94 | 49.94 | 0.026471 | 0.1 | 1 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.30882 | 0.30882 | 0 | 12 | 1 | 1 | 0.30882 | 10 | 0 | 0
14 | 50 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
14.05 | 50 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
14.1 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
14.15 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
14.2 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
14.25 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
14.3 | 49.92 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
14.35 | 49.92 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
14.4 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50.01 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
14.45 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
14.5 | 49.92 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
14.55 | 49.92 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
14.6 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
14.65 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
14.7 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
14.75 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
14.8 | 49.87 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
14.85 | 49.87 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
14.9 | 49.8 | 49.8 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
14.95 | 49.8 | 49.8 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
15 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
15.05 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
15.1 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
15.15 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
15.2 | 49.72 | 49.72 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
15.25 | 49.72 | 49.72 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
15.3 | 49.67 | 49.67 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
15.35 | 49.67 | 49.67 | 1 | 1 | 10 | 49.87 | 0.335 | 0.14412 | 1.4412 | 5.7206 | 5.7206 | 0 | 12 | 1 | 1 | 5.7206 | 10 | 0 | 0
15.4 | 49.65 | 49.65 | 1 | 1 | 10 | 49.87 | 0.335 | 0.24412 | 2.4412 | 6.2206 | 6.2206 | 0 | 12 | 1 | 1 | 6.2206 | 10 | 0 | 0
15.45 | 49.65 | 49.65 | 1 | 1 | 10 | 49.8 | 1 | 0.34412 | 3.4412 | 6.7206 | 6.7206 | 0 | 12 | 1 | 1 | 6.7206 | 10 | 0 | 0
15.5 | 49.59 | 49.59 | 1 | 1 | 10 | 49.8 | 1 | 0.44412 | 4.4412 | 7.2206 | 7.2206 | 0 | 12 | 1 | 1 | 7.2206 | 10 | 0 | 0
15.55 | 49.59 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.54412 | 5.4412 | 7.7206 | 7.7206 | 0 | 12 | 1 | 1 | 7.7206 | 10 | 0 | 0
15.6 | 49.66 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.64412 | 6.4412 | 8.2206 | 8.2206 | 0 | 12 | 1 | 1 | 8.2206 | 10 | 0 | 0
15.65 | 49.66 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.74412 | 7.4412 | 8.7206 | 8.7206 | 0 | 12 | 1 | 1 | 8.7206 | 10 | 0 | 0
15.7 | 49.63 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.84412 | 8.4412 | 9.2206 | 9.2206 | 0 | 12 | 1 | 1 | 9.2206 | 10 | 0 | 0
15.75 | 49.63 | 49.59 | 1 | 1 | 10 | 49.72 | 1 | 0.94412 | 9.4412 | 9.7206 | 9.7206 | 0 | 12 | 1 | 1 | 9.7206 | 10 | 0 | 0
15.8 | 49.61 | 49.59 | 1 | 1 | 10 | 49.72 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
15.85 | 49.61 | 49.59 | 1 | 1 | 10 | 49.67 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
15.9 | 49.54 | 49.54 | 1 | 1 | 10 | 49.67 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
15.95 | 49.54 | 49.54 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
16 | 49.46 | 49.46 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
16.05 | 49.46 | 49.46 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
16.1 | 49.45 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
16.15 | 49.45 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
16.2 | 49.51 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
16.25 | 49.51 | 49.45 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
16.3 | 49.5 | 49.45 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
16.35 | 49.5 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
16.4 | 49.54 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
16.45 | 49.54 | 49.45 | 1 | 1 | 10 | 49.54 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
16.5 | 49.59 | 49.45 | 1 | 1 | 10 | 49.59 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
16.55 | 49.59 | 49.45 | 1 | 1 | 10 | 49.59 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
16.6 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
16.65 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
16.7 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
16.75 | 49.61 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
16.8 | 49.53 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
16.85 | 49.53 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
16.9 | 49.54 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
16.95 | 49.54 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
17 | 49.61 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
17.05 | 49.61 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
17.1 | 49.66 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
17.15 | 49.66 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
17.2 | 49.64 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
17.25 | 49.64 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
17.3 | 49.69 | 49.53 | 1 | 1 | 10 | 49.69 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
17.35 | 49.69 | 49.53 | 1 | 1 | 10 | 49.69 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
17.4 | 49.74 | 49.53 | 1 | 1 | 10 | 49.74 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
17.45 | 49.74 | 49.54 | 1 | 1 | 10 | 49.74 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
17.5 | 49.78 | 49.54 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
17.55 | 49.78 | 49.61 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
17.6 | 49.82 | 49.61 | 1 | 1 | 10 | 49.82 | 0.81 | 0.81 | 8.1 | 9.05 | 9.05 | 0 | 12 | 1 | 1 | 9.05 | 10 | 0 | 0
17.65 | 49.82 | 49.64 | 1 | 1 | 10 | 49.82 | 0.81 | 0.81 | 8.1 | 9.05 | 9.05 | 0 | 12 | 1 | 1 | 9.05 | 10 | 0 | 0
17.7 | 49.86 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
17.75 | 49.86 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
17.8 | 49.84 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
17.85 | 49.84 | 49.69 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
17.9 | 49.91 | 49.69 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
17.95 | 49.91 | 49.74 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
18 | 49.97 | 49.74 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
18.05 | 49.97 | 49.78 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
18.1 | 50.03 | 49.78 | 1 | 1 | 10 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.9559 | 4.9559 | 0 | 12 | 1 | 1 | 4.9559 | 10 | 0 | 0
18.15 | 50.03 | 49.82 | 0.81 | 0.9 | 9 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.4559 | 4.4559 | 0 | 12 | 1 | 1 | 4.4559 | 10 | 0 | 0
18.2 | 50.05 | 49.82 | 0.81 | 0.81 | 8.1 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 3.9471 | 3.9471 | 0 | 12 | 1 | 1 | 3.9471 | 10 | 0 | 0
18.25 | 50.05 | 49.84 | 0.62 | 0.71 | 7.1 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 3.4471 | 3.4471 | 0 | 12 | 1 | 1 | 3.4471 | 10 | 0 | 0
18.3 | 50.01 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
18.35 | 50.01 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
18.4 | 49.95 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
18.45 | 49.95 | 49.91 | 0.044118 | 0.52 | 5.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.4971 | 2.4971 | 0 | 12 | 1 | 1 | 2.4971 | 10 | 0 | 0
18.5 | 49.99 | 49.91 | 0.044118 | 0.42 | 4.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 1.9971 | 1.9971 | 0 | 12 | 1 | 1 | 1.9971 | 10 | 0 | 0
18.55 | 49.99 | 49.95 | 0.020588 | 0.32 | 3.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 1.4971 | 1.4971 | 0 | 12 | 1 | 1 | 1.4971 | 10 | 0 | 0
18.6 | 49.92 | 49.92 | 0.038235 | 0.22 | 2.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.99706 | 0.99706 | 0 | 12 | 1 | 1 | 0.99706 | 10 | 0 | 0
18.65 | 49.92 | 49.92 | 0.038235 | 0.12 | 1.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.49706 | 0.49706 | 0 | 12 | 1 | 1 | 0.49706 | 10 | 0 | 0
18.7 | 49.97 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
18.75 | 49.97 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
18.8 | 50.02 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
18.85 | 50.02 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.17647 | 0.17647 | 0 | 12 | 1 | 1 | 0.17647 | 10 | 0 | 0
18.9 | 50.07 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
18.95 | 50.07 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
19 | 50.06 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
19.05 | 50.06 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
19.1 | 50.13 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
19.15 | 50.13 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
19.2 | 50.09 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
19.25 | 50.09 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6309 | -1.6309 | 0 | 12 | 1 | 1 | -1.6309 | 10 | 0 | 0
19.3 | 50.07 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6309 | -1.6309 | 0 | 12 | 1 | 1 | -1.6309 | 10 | 0 | 0
19.35 | 50.07 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6897 | -1.6897 | 0 | 12 | 1 | 1 | -1.6897 | 10 | 0 | 0
19.4 | 50.07 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6897 | -1.6897 | 0 | 12 | 1 | 1 | -1.6897 | 10 | 0 | 0
19.45 | 50.07 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.13 | -0.335 | -0.335 | -3.35 | -1.8074 | -1.8074 | 0 | 12 | 1 | 1 | -1.8074 | 10 | 0 | 0
19.5 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.13 | -0.335 | -0.335 | -3.35 | -1.7779 | -1.7779 | 0 | 12 | 1 | 1 | -1.7779 | 10 | 0 | 0
19.55 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.13 | -0.335 | -0.335 | -3.35 | -1.7779 | -1.7779 | 0 | 12 | 1 | 1 | -1.7779 | 10 | 0 | 0
19.6 | 50.01 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
19.65 | 50.01 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
19.7 | 50.07 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
19.75 | 50.07 | 50.01 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.235 | -2.35 | -1.175 | -1.175 | 0 | 12 | 1 | 1 | -1.175 | 10 | 0 | 0
19.8 | 50.05 | 50.01 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.135 | -1.35 | -0.675 | -0.675 | 0 | 12 | 1 | 1 | -0.675 | 10 | 0 | 0
19.85 | 50.05 | 50.01 | 0 | 0 | 0 | 50.07 | -0.032353 | -0.035 | -0.35 | -0.175 | -0.175 | 0 | 12 | 1 | 1 | -0.175 | 10 | 0 | 0
19.9 | 50.1 | 50.01 | 0 | 0 | 0 | 50.1 | -0.05 | -0.05 | -0.5 | -0.25 | -0.25 | 0 | 12 | 1 | 1 | -0.25 | 10 | 0 | 0
19.95 | 50.1 | 50.01 | 0 | 0 | 0 | 50.1 | -0.05 | -0.05 | -0.5 | -0.25 | -0.25 | 0 | 12 | 1 | 1 | -0.25 | 10 | 0 | 0
20 | 50.11 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
20.05 | 50.11 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
20.1 | 50.06 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
20.15 | 50.06 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
20.2 | 50.04 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
20.25 | 50.04 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
20.3 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
20.35 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
20.4 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
20.45 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
20.5 | 50.11 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
20.55 | 50.11 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
20.6 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
20.65 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
20.7 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
20.75 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
20.8 | 50.02 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.11 | -0.145 | -0.145 | -1.45 | -0.73971 | -0.73971 | 0 | 12 | 1 | 1 | -0.73971 | 10 | 0 | 0
20.85 | 50.02 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.11 | -0.145 | -0.145 | -1.45 | -0.73971 | -0.73971 | 0 | 12 | 1 | 1 | -0.73971 | 10 | 0 | 0
20.9 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
20.95 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
21 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
21.05 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
21.1 | 50.01 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
21.15 | 50.01 | 50 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.045 | -0.45 | -0.225 | -0.225 | 0 | 12 | 1 | 1 | -0.225 | 10 | 0 | 0
21.2 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
21.25 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
21.3 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
21.35 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
21.4 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.14706 | 0.14706 | 0 | 12 | 1 | 1 | 0.14706 | 10 | 0 | 0
21.45 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
21.5 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
21.55 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
21.6 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
21.65 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
21.7 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
21.75 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
21.8 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
21.85 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
21.9 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
21.95 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
22 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
22.05 | 50 | 50 | 0 | 0 | 0 | 50.01 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
22.1 | 49.5 | 49.5 | 1 | 1 | 10 | 50.01 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
22.15 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
22.2 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
22.25 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
22.3 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
22.35 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
22.4 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
22.45 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
22.5 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
22.55 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
22.6 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
22.65 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.1 | 1 | 5.5 | 5.5 | 0 | 12 | 1 | 1 | 5.5 | 10 | 0 | 0
22.7 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.2 | 2 | 6 | 6 | 0 | 12 | 1 | 1 | 6 | 10 | 0 | 0
22.75 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.3 | 3 | 6.5 | 6.5 | 0 | 12 | 1 | 1 | 6.5 | 10 | 0 | 0
22.8 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.4 | 4 | 7 | 7 | 0 | 12 | 1 | 1 | 7 | 10 | 0 | 0
22.85 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.5 | 5 | 7.5 | 7.5 | 0 | 12 | 1 | 1 | 7.5 | 10 | 0 | 0
22.9 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.6 | 6 | 8 | 8 | 0 | 12 | 1 | 1 | 8 | 10 | 0 | 0
22.95 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.7 | 7 | 8.5 | 8.5 | 0 | 12 | 1 | 1 | 8.5 | 10 | 0 | 0
23 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.8 | 8 | 9 | 9 | 0 | 12 | 1 | 1 | 9 | 10 | 0 | 0
23.05 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.9 | 9 | 9.5 | 9.5 | 0 | 12 | 1 | 1 | 9.5 | 10 | 0 | 0
23.1 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
23.15 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
23.2 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
23.25 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
23.3 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
23.35 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
23.4 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
23.45 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
23.5 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
23.55 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
23.6 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
23.65 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
23.7 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
23.75 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
23.8 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
23.85 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
23.9 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
23.95 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
24 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
24.05 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
24.1 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
24.15 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
24.2 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
24.25 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
24.3 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
24.35 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
24.4 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
24.45 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
24.5 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
24.55 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
24.6 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
24.65 | 50.5 | 50.5 | -1 | 0.9 | 9 | 50.5 | -1 | -1 | -10 | -0.5 | -0.5 | 0 | 12 | 1 | 1 | -0.5 | 10 | 0 | 0
24.7 | 50.5 | 50.5 | -1 | 0.8 | 8 | 50.5 | -1 | -1 | -10 | -1 | -1 | 0 | 12 | 1 | 1 | -1 | 10 | 0 | 0
24.75 | 50.5 | 50.5 | -1 | 0.7 | 7 | 50.5 | -1 | -1 | -10 | -1.5 | -1.5 | 0 | 12 | 1 | 1 | -1.5 | 10 | 0 | 0
24.8 | 50.5 | 50.5 | -1 | 0.6 | 6 | 50.5 | -1 | -1 | -10 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
24.85 | 50.5 | 50.5 | -1 | 0.5 | 5 | 50.5 | -1 | -1 | -10 | -2.5 | -2.5 | 0 | 12 | 1 | 1 | -2.5 | 10 | 0 | 0
24.9 | 50.5 | 50.5 | -1 | 0.4 | 4 | 50.5 | -1 | -1 | -10 | -3 | -3 | 0 | 12 | 1 | 1 | -3 | 10 | 0 | 0
24.95 | 50.5 | 50.5 | -1 | 0.3 | 3 | 50.5 | -1 | -1 | -10 | -3.5 | -3.5 | 0 | 12 | 1 | 1 | -3.5 | 10 | 0 | 0
25 | 50.5 | 50.5 | -1 | 0.2 | 2 | 50.5 | -1 | -1 | -10 | -4 | -4 | 0 | 12 | 1 | 1 | -4 | 10 | 0 | 0
25.05 | 50.5 | 50.5 | -1 | 0.1 | 1 | 50.5 | -1 | -1 | -10 | -4.5 | -4.5 | 0 | 12 | 1 | 1 | -4.5 | 10 | 0 | 0
25.1 | 50.5 | 50.5 | -1 | 0 | 0 | 50.5 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
25.15 | 50.5 | 50.5 | -1 | -0.1 | -1 | 50.5 | -1 | -1 | -10 | -5.5 | -5.5 | 0 | 12 | 1 | 1 | -5.5 | 10 | 0 | 0
25.2 | 50.5 | 50.5 | -1 | -0.2 | -2 | 50.5 | -1 | -1 | -10 | -6 | -6 | 0 | 12 | 1 | 1 | -6 | 10 | 0 | 0
25.25 | 50.5 | 50.5 | -1 | -0.3 | -3 | 50.5 | -1 | -1 | -10 | -6.5 | -6.5 | 0 | 12 | 1 | 1 | -6.5 | 10 | 0 | 0
25.3 | 50.5 | 50.5 | -1 | -0.4 | -4 | 50.5 | -1 | -1 | -10 | -7 | -7 | 0 | 12 | 1 | 1 | -7 | 10 | 0 | 0
25.35 | 50.5 | 50.5 | -1 | -0.5 | -5 | 50.5 | -1 | -1 | -10 | -7.5 | -7.5 | 0 | 12 | 1 | 1 | -7.5 | 10 | 0 | 0
25.4 | 50.5 | 50.5 | -1 | -0.6 | -6 | 50.5 | -1 | -1 | -10 | -8 | -8 | 0 | 12 | 1 | 1 | -8 | 10 | 0 | 0
25.45 | 50.5 | 50.5 | -1 | -0.7 | -7 | 50.5 | -1 | -1 | -10 | -8.5 | -8.5 | 0 | 12 | 1 | 1 | -8.5 | 10 | 0 | 0
25.5 | 50.5 | 50.5 | -1 | -0.8 | -8 | 50.5 | -1 | -1 | -10 | -9 | -9 | 0 | 12 | 1 | 1 | -9 | 10 | 0 | 0
25.55 | 50.5 | 50.5 | -1 | -0.9 | -9 | 50.5 | -1 | -1 | -10 | -9.5 | -9.5 | 0 | 12 | 1 | 1 | -9.5 | 10 | 0 | 0
25.6 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
25.65 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
25.7 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
25.75 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
25.8 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
25.85 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
25.9 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
25.95 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
26 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
26.05 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
26.1 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
26.15 | 50.47 | 50.47 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
26.2 | 50.45 | 50.45 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
26.25 | 50.42 | 50.42 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
26.3 | 50.4 | 50.4 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
26.35 | 50.37 | 50.37 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
26.4 | 50.35 | 50.35 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
26.45 | 50.32 | 50.32 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
26.5 | 50.29 | 50.29 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
26.55 | 50.27 | 50.27 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
26.6 | 50.24 | 50.24 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
26.65 | 50.22 | 50.22 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
26.7 | 50.19 | 50.19 | -0.905 | -0.905 | -9.05 | 50.47 | -1 | -1 | -10 | -9.525 | -9.525 | 0 | 12 | 1 | 1 | -9.525 | 10 | 0 | 0
26.75 | 50.17 | 50.17 | -0.715 | -0.715 | -7.15 | 50.45 | -1 | -1 | -10 | -8.575 | -8.575 | 0 | 12 | 1 | 1 | -8.575 | 10 | 0 | 0
26.8 | 50.14 | 50.14 | -0.43 | -0.43 | -4.3 | 50.42 | -1 | -1 | -10 | -7.15 | -7.15 | 0 | 12 | 1 | 1 | -7.15 | 10 | 0 | 0
26.85 | 50.12 | 50.12 | -0.24 | -0.24 | -2.4 | 50.4 | -1 | -1 | -10 | -6.2 | -6.2 | 0 | 12 | 1 | 1 | -6.2 | 10 | 0 | 0
26.9 | 50.09 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 50.37 | -1 | -1 | -10 | -5.2206 | -5.2206 | 0 | 12 | 1 | 1 | -5.2206 | 10 | 0 | 0
26.95 | 50.06 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.35 | -1 | -1 | -10 | -5.1324 | -5.1324 | 0 | 12 | 1 | 1 | -5.1324 | 10 | 0 | 0
27 | 50.04 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.32 | -1 | -1 | -10 | -5.0735 | -5.0735 | 0 | 12 | 1 | 1 | -5.0735 | 10 | 0 | 0
27.05 | 50.01 | 50.01 | 0 | 0 | 0 | 50.29 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
27.1 | 49.99 | 49.99 | 0 | 0 | 0 | 50.27 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
27.15 | 49.96 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.24 | -1 | -1 | -10 | -4.9265 | -4.9265 | 0 | 12 | 1 | 1 | -4.9265 | 10 | 0 | 0
27.2 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.22 | -1 | -1 | -10 | -4.8676 | -4.8676 | 0 | 12 | 1 | 1 | -4.8676 | 10 | 0 | 0
27.25 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.19 | -0.905 | -0.905 | -9.05 | -4.3044 | -4.3044 | 0 | 12 | 1 | 1 | -4.3044 | 10 | 0 | 0
27.3 | 49.88 | 49.88 | 0.24 | 0.24 | 2.4 | 50.17 | -0.715 | -0.805 | -8.05 | -2.825 | -2.825 | 0 | 12 | 1 | 1 | -2.825 | 10 | 0 | 0
27.35 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.14 | -0.43 | -0.705 | -7.05 | -1.375 | -1.375 | 0 | 12 | 1 | 1 | -1.375 | 10 | 0 | 0
27.4 | 49.83 | 49.83 | 0.715 | 0.715 | 7.15 | 50.12 | -0.24 | -0.605 | -6.05 | 0.55 | 0.55 | 0 | 12 | 1 | 1 | 0.55 | 10 | 0 | 0
27.45 | 49.81 | 49.81 | 0.905 | 0.905 | 9.05 | 50.09 | -0.044118 | -0.505 | -5.05 | 2 | 2 | 0 | 12 | 1 | 1 | 2 | 10 | 0 | 0
27.5 | 49.78 | 49.78 | 1 | 1 | 10 | 50.06 | -0.026471 | -0.405 | -4.05 | 2.975 | 2.975 | 0 | 12 | 1 | 1 | 2.975 | 10 | 0 | 0
27.55 | 49.76 | 49.76 | 1 | 1 | 10 | 50.04 | -0.014706 | -0.305 | -3.05 | 3.475 | 3.475 | 0 | 12 | 1 | 1 | 3.475 | 10 | 0 | 0
27.6 | 49.73 | 49.73 | 1 | 1 | 10 | 50.01 | 0 | -0.205 | -2.05 | 3.975 | 3.975 | 0 | 12 | 1 | 1 | 3.975 | 10 | 0 | 0
27.65 | 49.71 | 49.71 | 1 | 1 | 10 | 49.99 | 0 | -0.105 | -1.05 | 4.475 | 4.475 | 0 | 12 | 1 | 1 | 4.475 | 10 | 0 | 0
27.7 | 49.68 | 49.68 | 1 | 1 | 10 | 49.96 | 0.014706 | -0.005 | -0.05 | 4.975 | 4.975 | 0 | 12 | 1 | 1 | 4.975 | 10 | 0 | 0
27.75 | 49.65 | 49.65 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
27.8 | 49.63 | 49.63 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
27.85 | 49.6 | 49.6 | 1 | 1 | 10 | 49.88 | 0.24 | 0.14412 | 1.4412 | 5.7206 | 5.7206 | 0 | 12 | 1 | 1 | 5.7206 | 10 | 0 | 0
27.9 | 49.58 | 49.58 | 1 | 1 | 10 | 49.86 | 0.43 | 0.24412 | 2.4412 | 6.2206 | 6.2206 | 0 | 12 | 1 | 1 | 6.2206 | 10 | 0 | 0
27.95 | 49.55 | 49.55 | 1 | 1 | 10 | 49.83 | 0.715 | 0.34412 | 3.4412 | 6.7206 | 6.7206 | 0 | 12 | 1 | 1 | 6.7206 | 10 | 0 | 0
28 | 49.53 | 49.53 | 1 | 1 | 10 | 49.81 | 0.905 | 0.44412 | 4.4412 | 7.2206 | 7.2206 | 0 | 12 | 1 | 1 | 7.2206 | 10 | 0 | 0
28.05 | 49.5 | 49.5 | 1 | 1 | 10 | 49.78 | 1 | 0.54412 | 5.4412 | 7.7206 | 7.7206 | 0 | 12 | 1 | 1 | 7.7206 | 10 | 0 | 0
28.1 | 49.5 | 49.5 | 1 | 1 | 10 | 49.76 | 1 | 0.64412 | 6.4412 | 8.2206 | 8.2206 | 0 | 12 | 1 | 1 | 8.2206 | 10 | 0 | 0
28.15 | 49.53 | 49.5 | 1 | 1 | 10 | 49.73 | 1 | 0.74412 | 7.4412 | 8.7206 | 8.7206 | 0 | 12 | 1 | 1 | 8.7206 | 10 | 0 | 0
28.2 | 49.55 | 49.5 | 1 | 1 | 10 | 49.71 | 1 | 0.84412 | 8.4412 | 9.2206 | 9.2206 | 0 | 12 | 1 | 1 | 9.2206 | 10 | 0 | 0
28.25 | 49.58 | 49.5 | 1 | 1 | 10 | 49.68 | 1 | 0.94412 | 9.4412 | 9.7206 | 9.7206 | 0 | 12 | 1 | 1 | 9.7206 | 10 | 0 | 0
28.3 | 49.6 | 49.5 | 1 | 1 | 10 | 49.65 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
28.35 | 49.63 | 49.5 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
28.4 | 49.65 | 49.5 | 1 | 1 | 10 | 49.65 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
28.45 | 49.68 | 49.5 | 1 | 1 | 10 | 49.68 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
28.5 | 49.71 | 49.5 | 1 | 1 | 10 | 49.71 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
28.55 | 49.73 | 49.5 | 1 | 1 | 10 | 49.73 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
28.6 | 49.76 | 49.5 | 1 | 1 | 10 | 49.76 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
28.65 | 49.78 | 49.5 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
28.7 | 49.81 | 49.53 | 1 | 1 | 10 | 49.81 | 0.905 | 0.905 | 9.05 | 9.525 | 9.525 | 0 | 12 | 1 | 1 | 9.525 | 10 | 0 | 0
28.75 | 49.83 | 49.55 | 1 | 1 | 10 | 49.83 | 0.715 | 0.715 | 7.15 | 8.575 | 8.575 | 0 | 12 | 1 | 1 | 8.575 | 10 | 0 | 0
28.8 | 49.86 | 49.58 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
28.85 | 49.88 | 49.6 | 1 | 1 | 10 | 49.88 | 0.24 | 0.24 | 2.4 | 6.2 | 6.2 | 0 | 12 | 1 | 1 | 6.2 | 10 | 0 | 0
28.9 | 49.91 | 49.63 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
28.95 | 49.94 | 49.65 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
29 | 49.96 | 49.68 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
29.05 | 49.99 | 49.71 | 1 | 1 | 10 | 49.99 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
29.1 | 50.01 | 49.73 | 1 | 1 | 10 | 50.01 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
29.15 | 50.04 | 49.76 | 1 | 1 | 10 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 4.9265 | 4.9265 | 0 | 12 | 1 | 1 | 4.9265 | 10 | 0 | 0
29.2 | 50.06 | 49.78 | 1 | 1 | 10 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 4.8676 | 4.8676 | 0 | 12 | 1 | 1 | 4.8676 | 10 | 0 | 0
29.25 | 50.09 | 49.81 | 0.905 | 0.905 | 9.05 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 4.3044 | 4.3044 | 0 | 12 | 1 | 1 | 4.3044 | 10 | 0 | 0
29.3 | 50.12 | 49.83 | 0.715 | 0.805 | 8.05 | 50.12 | -0.24 | -0.24 | -2.4 | 2.825 | 2.825 | 0 | 12 | 1 | 1 | 2.825 | 10 | 0 | 0
29.35 | 50.14 | 49.86 | 0.43 | 0.705 | 7.05 | 50.14 | -0.43 | -0.43 | -4.3 | 1.375 | 1.375 | 0 | 12 | 1 | 1 | 1.375 | 10 | 0 | 0
29.4 | 50.17 | 49.88 | 0.24 | 0.605 | 6.05 | 50.17 | -0.715 | -0.715 | -7.15 | -0.55 | -0.55 | 0 | 12 | 1 | 1 | -0.55 | 10 | 0 | 0
29.45 | 50.19 | 49.91 | 0.044118 | 0.505 | 5.05 | 50.19 | -0.905 | -0.905 | -9.05 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
29.5 | 50.22 | 49.94 | 0.026471 | 0.405 | 4.05 | 50.22 | -1 | -1 | -10 | -2.975 | -2.975 | 0 | 12 | 1 | 1 | -2.975 | 10 | 0 | 0
29.55 | 50.24 | 49.96 | 0.014706 | 0.305 | 3.05 | 50.24 | -1 | -1 | -10 | -3.475 | -3.475 | 0 | 12 | 1 | 1 | -3.475 | 10 | 0 | 0
29.6 | 50.27 | 49.99 | 0 | 0.205 | 2.05 | 50.27 | -1 | -1 | -10 | -3.975 | -3.975 | 0 | 12 | 1 | 1 | -3.975 | 10 | 0 | 0
29.65 | 50.29 | 50.01 | 0 | 0.105 | 1.05 | 50.29 | -1 | -1 | -10 | -4.475 | -4.475 | 0 | 12 | 1 | 1 | -4.475 | 10 | 0 | 0
29.7 | 50.32 | 50.04 | -0.014706 | 0.005 | 0.05 | 50.32 | -1 | -1 | -10 | -4.975 | -4.975 | 0 | 12 | 1 | 1 | -4.975 | 10 | 0 | 0
29.75 | 50.35 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.35 | -1 | -1 | -10 | -5.1324 | -5.1324 | 0 | 12 | 1 | 1 | -5.1324 | 10 | 0 | 0
29.8 | 50.37 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 50.37 | -1 | -1 | -10 | -5.2206 | -5.2206 | 0 | 12 | 1 | 1 | -5.2206 | 10 | 0 | 0
29.85 | 50.4 | 50.12 | -0.24 | -0.14412 | -1.4412 | 50.4 | -1 | -1 | -10 | -5.7206 | -5.7206 | 0 | 12 | 1 | 1 | -5.7206 | 10 | 0 | 0
29.9 | 50.42 | 50.14 | -0.43 | -0.24412 | -2.4412 | 50.42 | -1 | -1 | -10 | -6.2206 | -6.2206 | 0 | 12 | 1 | 1 | -6.2206 | 10 | 0 | 0
29.95 | 50.45 | 50.17 | -0.715 | -0.34412 | -3.4412 | 50.45 | -1 | -1 | -10 | -6.7206 | -6.7206 | 0 | 12 | 1 | 1 | -6.7206 | 10 | 0 | 0
30 | 50.47 | 50.19 | -0.905 | -0.44412 | -4.4412 | 50.47 | -1 | -1 | -10 | -7.2206 | -7.2206 | 0 | 12 | 1 | 1 | -7.2206 | 10 | 0 | 0
30.05 | 50.5 | 50.22 | -1 | -0.54412 | -5.4412 | 50.5 | -1 | -1 | -10 | -7.7206 | -7.7206 | 0 | 12 | 1 | 1 | -7.7206 | 10 | 0 | 0
30.1 | 50.5 | 50.24 | -1 | -0.64412 | -6.4412 | 50.5 | -1 | -1 | -10 | -8.2206 | -8.2206 | 0 | 12 | 1 | 1 | -8.2206 | 10 | 0 | 0
30.15 | 50.47 | 50.27 | -1 | -0.74412 | -7.4412 | 50.5 | -1 | -1 | -10 | -8.7206 | -8.7206 | 0 | 12 | 1 | 1 | -8.7206 | 10 | 0 | 0
30.2 | 50.45 | 50.29 | -1 | -0.84412 | -8.4412 | 50.5 | -1 | -1 | -10 | -9.2206 | -9.2206 | 0 | 12 | 1 | 1 | -9.2206 | 10 | 0 | 0
30.25 | 50.42 | 50.32 | -1 | -0.94412 | -9.4412 | 50.5 | -1 | -1 | -10 | -9.7206 | -9.7206 | 0 | 12 | 1 | 1 | -9.7206 | 10 | 0 | 0
30.3 | 50.39 | 50.35 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
30.35 | 50.37 | 50.37 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
30.4 | 50.34 | 50.34 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
30.45 | 50.32 | 50.32 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
30.5 | 50.29 | 50.29 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
30.55 | 50.26 | 50.26 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
30.6 | 50.24 | 50.24 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
30.65 | 50.21 | 50.21 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
30.7 | 50.18 | 50.18 | -0.81 | -0.81 | -8.1 | 50.47 | -1 | -1 | -10 | -9.05 | -9.05 | 0 | 12 | 1 | 1 | -9.05 | 10 | 0 | 0
30.75 | 50.16 | 50.16 | -0.62 | -0.62 | -6.2 | 50.45 | -1 | -1 | -10 | -8.1 | -8.1 | 0 | 12 | 1 | 1 | -8.1 | 10 | 0 | 0
30.8 | 50.13 | 50.13 | -0.335 | -0.335 | -3.35 | 50.42 | -1 | -1 | -10 | -6.675 | -6.675 | 0 | 12 | 1 | 1 | -6.675 | 10 | 0 | 0
30.85 | 50.11 | 50.11 | -0.145 | -0.145 | -1.45 | 50.39 | -1 | -1 | -10 | -5.725 | -5.725 | 0 | 12 | 1 | 1 | -5.725 | 10 | 0 | 0
30.9 | 50.08 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 50.37 | -1 | -1 | -10 | -5.1912 | -5.1912 | 0 | 12 | 1 | 1 | -5.1912 | 10 | 0 | 0
30.95 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.34 | -1 | -1 | -10 | -5.1029 | -5.1029 | 0 | 12 | 1 | 1 | -5.1029 | 10 | 0 | 0
31 | 50.03 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 50.32 | -1 | -1 | -10 | -5.0441 | -5.0441 | 0 | 12 | 1 | 1 | -5.0441 | 10 | 0 | 0
31.05 | 50 | 50 | 0 | 0 | 0 | 50.29 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
31.1 | 50 | 50 | 0 | 0 | 0 | 50.26 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
31.15 | 50 | 50 | 0 | 0 | 0 | 50.24 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
31.2 | 50 | 50 | 0 | 0 | 0 | 50.21 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
31.25 | 50 | 50 | 0 | 0 | 0 | 50.18 | -0.81 | -0.9 | -9 | -4.5 | -4.5 | 0 | 12 | 1 | 1 | -4.5 | 10 | 0 | 0
31.3 | 50 | 50 | 0 | 0 | 0 | 50.16 | -0.62 | -0.8 | -8 | -4 | -4 | 0 | 12 | 1 | 1 | -4 | 10 | 0 | 0
31.35 | 50 | 50 | 0 | 0 | 0 | 50.13 | -0.335 | -0.7 | -7 | -3.5 | -3.5 | 0 | 12 | 1 | 1 | -3.5 | 10 | 0 | 0
31.4 | 50.01 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.6 | -6 | -3 | -3 | 0 | 12 | 1 | 1 | -3 | 10 | 0 | 0
31.45 | 50.01 | 50 | 0 | 0 | 0 | 50.08 | -0.038235 | -0.5 | -5 | -2.5 | -2.5 | 0 | 12 | 1 | 1 | -2.5 | 10 | 0 | 0
31.5 | 49.99 | 49.99 | 0 | 0 | 0 | 50.05 | -0.020588 | -0.4 | -4 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
31.55 | 49.99 | 49.99 | 0 | 0 | 0 | 50.03 | -0.0088235 | -0.3 | -3 | -1.5 | -1.5 | 0 | 12 | 1 | 1 | -1.5 | 10 | 0 | 0
31.6 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | -0.2 | -2 | -0.83824 | -0.83824 | 0 | 12 | 1 | 1 | -0.83824 | 10 | 0 | 0
31.65 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | -0.1 | -1 | -0.33824 | -0.33824 | 0 | 12 | 1 | 1 | -0.33824 | 10 | 0 | 0
31.7 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
31.75 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
31.8 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
31.85 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
31.9 | 49.89 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
31.95 | 49.89 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
32 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50.01 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
32.05 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
32.1 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
32.15 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 2.7868 | 2.7868 | 0 | 12 | 1 | 1 | 2.7868 | 10 | 0 | 0
32.2 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 2.7868 | 2.7868 | 0 | 12 | 1 | 1 | 2.7868 | 10 | 0 | 0
32.25 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 2.8456 | 2.8456 | 0 | 12 | 1 | 1 | 2.8456 | 10 | 0 | 0
32.3 | 49.94 | 49.85 | 0.525 | 0.525 | 5.25 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 2.7574 | 2.7574 | 0 | 12 | 1 | 1 | 2.7574 | 10 | 0 | 0
32.35 | 49.94 | 49.85 | 0.525 | 0.525 | 5.25 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 2.7574 | 2.7574 | 0 | 12 | 1 | 1 | 2.7574 | 10 | 0 | 0
32.4 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
32.45 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
32.5 | 49.93 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
32.55 | 49.93 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
32.6 | 49.96 | 49.85 | 0.525 | 0.525 | 5.25 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 2.6985 | 2.6985 | 0 | 12 | 1 | 1 | 2.6985 | 10 | 0 | 0
32.65 | 49.96 | 49.85 | 0.525 | 0.525 | 5.25 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 2.6985 | 2.6985 | 0 | 12 | 1 | 1 | 2.6985 | 10 | 0 | 0
32.7 | 49.99 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
32.75 | 49.99 | 49.91 | 0.044118 | 0.425 | 4.25 | 49.99 | 0 | 0 | 0 | 2.125 | 2.125 | 0 | 12 | 1 | 1 | 2.125 | 10 | 0 | 0
32.8 | 49.99 | 49.91 | 0.044118 | 0.325 | 3.25 | 49.99 | 0 | 0 | 0 | 1.625 | 1.625 | 0 | 12 | 1 | 1 | 1.625 | 10 | 0 | 0
32.85 | 49.99 | 49.93 | 0.032353 | 0.225 | 2.25 | 49.99 | 0 | 0 | 0 | 1.125 | 1.125 | 0 | 12 | 1 | 1 | 1.125 | 10 | 0 | 0
32.9 | 49.96 | 49.93 | 0.032353 | 0.125 | 1.25 | 49.99 | 0 | 0 | 0 | 0.625 | 0.625 | 0 | 12 | 1 | 1 | 0.625 | 10 | 0 | 0
32.95 | 49.96 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 49.99 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
33 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
33.05 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
33.1 | 50.05 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.058824 | 0.058824 | 0 | 12 | 1 | 1 | 0.058824 | 10 | 0 | 0
33.15 | 50.05 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
33.2 | 49.97 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
33.25 | 49.97 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
33.3 | 49.92 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
33.35 | 49.92 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
33.4 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
33.45 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
33.5 | 49.94 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
33.55 | 49.94 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
33.6 | 50.01 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
33.65 | 50.01 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
33.7 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
33.75 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
33.8 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
33.85 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
33.9 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
33.95 | 49.95 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
34 | 49.97 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
34.05 | 49.97 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
34.1 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
34.15 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
34.2 | 49.87 | 49.87 | 0.335 | 0.335 | 3.35 | 50.01 | 0 | 0 | 0 | 1.675 | 1.675 | 0 | 12 | 1 | 1 | 1.675 | 10 | 0 | 0
34.25 | 49.87 | 49.87 | 0.335 | 0.335 | 3.35 | 49.99 | 0 | 0 | 0 | 1.675 | 1.675 | 0 | 12 | 1 | 1 | 1.675 | 10 | 0 | 0
34.3 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
34.35 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 2.6691 | 2.6691 | 0 | 12 | 1 | 1 | 2.6691 | 10 | 0 | 0
34.4 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
34.45 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
34.5 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
34.55 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
34.6 | 49.84 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
34.65 | 49.84 | 49.79 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
34.7 | 49.89 | 49.79 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
34.75 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.12647 | 1.2647 | 5.6324 | 5.6324 | 0 | 12 | 1 | 1 | 5.6324 | 10 | 0 | 0
34.8 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.145 | 1.45 | 5.725 | 5.725 | 0 | 12 | 1 | 1 | 5.725 | 10 | 0 | 0
34.85 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.145 | 1.45 | 5.725 | 5.725 | 0 | 12 | 1 | 1 | 5.725 | 10 | 0 | 0
34.9 | 49.96 | 49.79 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
34.95 | 49.96 | 49.79 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
35 | 50.02 | 49.79 | 1 | 1 | 10 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 4.9853 | 4.9853 | 0 | 12 | 1 | 1 | 4.9853 | 10 | 0 | 0
35.05 | 50.02 | 49.79 | 1 | 1 | 10 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 4.9853 | 4.9853 | 0 | 12 | 1 | 1 | 4.9853 | 10 | 0 | 0
35.1 | 50.03 | 49.79 | 1 | 1 | 10 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.9559 | 4.9559 | 0 | 12 | 1 | 1 | 4.9559 | 10 | 0 | 0
35.15 | 50.03 | 49.84 | 0.62 | 0.9 | 9 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.4559 | 4.4559 | 0 | 12 | 1 | 1 | 4.4559 | 10 | 0 | 0
35.2 | 50.02 | 49.84 | 0.62 | 0.8 | 8 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 3.9559 | 3.9559 | 0 | 12 | 1 | 1 | 3.9559 | 10 | 0 | 0
35.25 | 50.02 | 49.89 | 0.145 | 0.7 | 7 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 3.4559 | 3.4559 | 0 | 12 | 1 | 1 | 3.4559 | 10 | 0 | 0
35.3 | 50.08 | 49.89 | 0.145 | 0.6 | 6 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 2.8088 | 2.8088 | 0 | 12 | 1 | 1 | 2.8088 | 10 | 0 | 0
35.35 | 50.08 | 49.89 | 0.145 | 0.5 | 5 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 2.3088 | 2.3088 | 0 | 12 | 1 | 1 | 2.3088 | 10 | 0 | 0
35.4 | 50.01 | 49.89 | 0.145 | 0.4 | 4 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 1.8088 | 1.8088 | 0 | 12 | 1 | 1 | 1.8088 | 10 | 0 | 0
35.45 | 50.01 | 49.96 | 0.014706 | 0.3 | 3 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 1.3088 | 1.3088 | 0 | 12 | 1 | 1 | 1.3088 | 10 | 0 | 0
35.5 | 49.94 | 49.94 | 0.026471 | 0.2 | 2 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.80882 | 0.80882 | 0 | 12 | 1 | 1 | 0.80882 | 10 | 0 | 0
35.55 | 49.94 | 49.94 | 0.026471 | 0.1 | 1 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.30882 | 0.30882 | 0 | 12 | 1 | 1 | 0.30882 | 10 | 0 | 0
35.6 | 50 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
35.65 | 50 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
35.7 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
35.75 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
35.8 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
35.85 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
35.9 | 49.92 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
35.95 | 49.92 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
36 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50.01 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
36.05 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
36.1 | 49.92 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
36.15 | 49.92 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
36.2 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
36.25 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
36.3 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
36.35 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
36.4 | 49.87 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
36.45 | 49.87 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
36.5 | 49.8 | 49.8 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
36.55 | 49.8 | 49.8 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
36.6 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
36.65 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
36.7 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
36.75 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
36.8 | 49.72 | 49.72 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
36.85 | 49.72 | 49.72 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
36.9 | 49.67 | 49.67 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
36.95 | 49.67 | 49.67 | 1 | 1 | 10 | 49.87 | 0.335 | 0.14412 | 1.4412 | 5.7206 | 5.7206 | 0 | 12 | 1 | 1 | 5.7206 | 10 | 0 | 0
37 | 49.65 | 49.65 | 1 | 1 | 10 | 49.87 | 0.335 | 0.24412 | 2.4412 | 6.2206 | 6.2206 | 0 | 12 | 1 | 1 | 6.2206 | 10 | 0 | 0
37.05 | 49.65 | 49.65 | 1 | 1 | 10 | 49.8 | 1 | 0.34412 | 3.4412 | 6.7206 | 6.7206 | 0 | 12 | 1 | 1 | 6.7206 | 10 | 0 | 0
37.1 | 49.59 | 49.59 | 1 | 1 | 10 | 49.8 | 1 | 0.44412 | 4.4412 | 7.2206 | 7.2206 | 0 | 12 | 1 | 1 | 7.2206 | 10 | 0 | 0
37.15 | 49.59 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.54412 | 5.4412 | 7.7206 | 7.7206 | 0 | 12 | 1 | 1 | 7.7206 | 10 | 0 | 0
37.2 | 49.66 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.64412 | 6.4412 | 8.2206 | 8.2206 | 0 | 12 | 1 | 1 | 8.2206 | 10 | 0 | 0
37.25 | 49.66 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.74412 | 7.4412 | 8.7206 | 8.7206 | 0 | 12 | 1 | 1 | 8.7206 | 10 | 0 | 0
37.3 | 49.63 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.84412 | 8.4412 | 9.2206 | 9.2206 | 0 | 12 | 1 | 1 | 9.2206 | 10 | 0 | 0
37.35 | 49.63 | 49.59 | 1 | 1 | 10 | 49.72 | 1 | 0.94412 | 9.4412 | 9.7206 | 9.7206 | 0 | 12 | 1 | 1 | 9.7206 | 10 | 0 | 0
37.4 | 49.61 | 49.59 | 1 | 1 | 10 | 49.72 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
37.45 | 49.61 | 49.59 | 1 | 1 | 10 | 49.67 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
37.5 | 49.54 | 49.54 | 1 | 1 | 10 | 49.67 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
37.55 | 49.54 | 49.54 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
37.6 | 49.46 | 49.46 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
37.65 | 49.46 | 49.46 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
37.7 | 49.45 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
37.75 | 49.45 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
37.8 | 49.51 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
37.85 | 49.51 | 49.45 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
37.9 | 49.5 | 49.45 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
37.95 | 49.5 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
38 | 49.54 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
38.05 | 49.54 | 49.45 | 1 | 1 | 10 | 49.54 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
38.1 | 49.59 | 49.45 | 1 | 1 | 10 | 49.59 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
38.15 | 49.59 | 49.45 | 1 | 1 | 10 | 49.59 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
38.2 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
38.25 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
38.3 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
38.35 | 49.61 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
38.4 | 49.53 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
38.45 | 49.53 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
38.5 | 49.54 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
38.55 | 49.54 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
38.6 | 49.61 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
38.65 | 49.61 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
38.7 | 49.66 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
38.75 | 49.66 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
38.8 | 49.64 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
38.85 | 49.64 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
38.9 | 49.69 | 49.53 | 1 | 1 | 10 | 49.69 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
38.95 | 49.69 | 49.53 | 1 | 1 | 10 | 49.69 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
39 | 49.74 | 49.53 | 1 | 1 | 10 | 49.74 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
39.05 | 49.74 | 49.54 | 1 | 1 | 10 | 49.74 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
39.1 | 49.78 | 49.54 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
39.15 | 49.78 | 49.61 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
39.2 | 49.82 | 49.61 | 1 | 1 | 10 | 49.82 | 0.81 | 0.81 | 8.1 | 9.05 | 9.05 | 0 | 12 | 1 | 1 | 9.05 | 10 | 0 | 0
39.25 | 49.82 | 49.64 | 1 | 1 | 10 | 49.82 | 0.81 | 0.81 | 8.1 | 9.05 | 9.05 | 0 | 12 | 1 | 1 | 9.05 | 10 | 0 | 0
39.3 | 49.86 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
39.35 | 49.86 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
39.4 | 49.84 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
39.45 | 49.84 | 49.69 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
39.5 | 49.91 | 49.69 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
39.55 | 49.91 | 49.74 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
39.6 | 49.97 | 49.74 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
39.65 | 49.97 | 49.78 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
39.7 | 50.03 | 49.78 | 1 | 1 | 10 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.9559 | 4.9559 | 0 | 12 | 1 | 1 | 4.9559 | 10 | 0 | 0
39.75 | 50.03 | 49.82 | 0.81 | 0.9 | 9 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.4559 | 4.4559 | 0 | 12 | 1 | 1 | 4.4559 | 10 | 0 | 0
39.8 | 50.05 | 49.82 | 0.81 | 0.81 | 8.1 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 3.9471 | 3.9471 | 0 | 12 | 1 | 1 | 3.9471 | 10 | 0 | 0
39.85 | 50.05 | 49.84 | 0.62 | 0.71 | 7.1 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 3.4471 | 3.4471 | 0 | 12 | 1 | 1 | 3.4471 | 10 | 0 | 0
39.9 | 50.01 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
39.95 | 50.01 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
40 | 49.95 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
40.05 | 49.95 | 49.91 | 0.044118 | 0.52 | 5.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.4971 | 2.4971 | 0 | 12 | 1 | 1 | 2.4971 | 10 | 0 | 0
40.1 | 49.99 | 49.91 | 0.044118 | 0.42 | 4.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 1.9971 | 1.9971 | 0 | 12 | 1 | 1 | 1.9971 | 10 | 0 | 0
40.15 | 49.99 | 49.95 | 0.020588 | 0.32 | 3.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 1.4971 | 1.4971 | 0 | 12 | 1 | 1 | 1.4971 | 10 | 0 | 0
40.2 | 49.92 | 49.92 | 0.038235 | 0.22 | 2.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.99706 | 0.99706 | 0 | 12 | 1 | 1 | 0.99706 | 10 | 0 | 0
40.25 | 49.92 | 49.92 | 0.038235 | 0.12 | 1.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.49706 | 0.49706 | 0 | 12 | 1 | 1 | 0.49706 | 10 | 0 | 0
40.3 | 49.97 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
40.35 | 49.97 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
40.4 | 50.02 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
40.45 | 50.02 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.17647 | 0.17647 | 0 | 12 | 1 | 1 | 0.17647 | 10 | 0 | 0
40.5 | 50.07 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
40.55 | 50.07 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
40.6 | 50.06 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
40.65 | 50.06 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
40.7 | 50.13 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
40.75 | 50.13 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
40.8 | 50.09 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
40.85 | 50.09 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6309 | -1.6309 | 0 | 12 | 1 | 1 | -1.6309 | 10 | 0 | 0
40.9 | 50.07 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6309 | -1.6309 | 0 | 12 | 1 | 1 | -1.6309 | 10 | 0 | 0
40.95 | 50.07 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6897 | -1.6897 | 0 | 12 | 1 | 1 | -1.6897 | 10 | 0 | 0
41 | 50.07 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6897 | -1.6897 | 0 | 12 | 1 | 1 | -1.6897 | 10 | 0 | 0
41.05 | 50.07 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.13 | -0.335 | -0.335 | -3.35 | -1.8074 | -1.8074 | 0 | 12 | 1 | 1 | -1.8074 | 10 | 0 | 0
41.1 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.13 | -0.335 | -0.335 | -3.35 | -1.7779 | -1.7779 | 0 | 12 | 1 | 1 | -1.7779 | 10 | 0 | 0
41.15 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.13 | -0.335 | -0.335 | -3.35 | -1.7779 | -1.7779 | 0 | 12 | 1 | 1 | -1.7779 | 10 | 0 | 0
41.2 | 50.01 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
41.25 | 50.01 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
41.3 | 50.07 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
41.35 | 50.07 | 50.01 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.235 | -2.35 | -1.175 | -1.175 | 0 | 12 | 1 | 1 | -1.175 | 10 | 0 | 0
41.4 | 50.05 | 50.01 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.135 | -1.35 | -0.675 | -0.675 | 0 | 12 | 1 | 1 | -0.675 | 10 | 0 | 0
41.45 | 50.05 | 50.01 | 0 | 0 | 0 | 50.07 | -0.032353 | -0.035 | -0.35 | -0.175 | -0.175 | 0 | 12 | 1 | 1 | -0.175 | 10 | 0 | 0
41.5 | 50.1 | 50.01 | 0 | 0 | 0 | 50.1 | -0.05 | -0.05 | -0.5 | -0.25 | -0.25 | 0 | 12 | 1 | 1 | -0.25 | 10 | 0 | 0
41.55 | 50.1 | 50.01 | 0 | 0 | 0 | 50.1 | -0.05 | -0.05 | -0.5 | -0.25 | -0.25 | 0 | 12 | 1 | 1 | -0.25 | 10 | 0 | 0
41.6 | 50.11 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
41.65 | 50.11 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
41.7 | 50.06 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
41.75 | 50.06 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
41.8 | 50.04 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
41.85 | 50.04 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
41.9 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
41.95 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
42 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
42.05 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
42.1 | 50.11 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
42.15 | 50.11 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
42.2 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
42.25 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
42.3 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
42.35 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
42.4 | 50.02 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.11 | -0.145 | -0.145 | -1.45 | -0.73971 | -0.73971 | 0 | 12 | 1 | 1 | -0.73971 | 10 | 0 | 0
42.45 | 50.02 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.11 | -0.145 | -0.145 | -1.45 | -0.73971 | -0.73971 | 0 | 12 | 1 | 1 | -0.73971 | 10 | 0 | 0
42.5 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
42.55 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
42.6 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
42.65 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
42.7 | 50.01 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
42.75 | 50.01 | 50 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.045 | -0.45 | -0.225 | -0.225 | 0 | 12 | 1 | 1 | -0.225 | 10 | 0 | 0
42.8 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
42.85 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
42.9 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
42.95 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
43 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.14706 | 0.14706 | 0 | 12 | 1 | 1 | 0.14706 | 10 | 0 | 0
43.05 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
43.1 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
43.15 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
43.2 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
43.25 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
43.3 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
43.35 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
43.4 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
43.45 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
43.5 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
43.55 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
43.6 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
43.65 | 50 | 50 | 0 | 0 | 0 | 50.01 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
43.7 | 49.5 | 49.5 | 1 | 1 | 10 | 50.01 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
43.75 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
43.8 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
43.85 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
43.9 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
43.95 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
44 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
44.05 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
44.1 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
44.15 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
44.2 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
44.25 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.1 | 1 | 5.5 | 5.5 | 0 | 12 | 1 | 1 | 5.5 | 10 | 0 | 0
44.3 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.2 | 2 | 6 | 6 | 0 | 12 | 1 | 1 | 6 | 10 | 0 | 0
44.35 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.3 | 3 | 6.5 | 6.5 | 0 | 12 | 1 | 1 | 6.5 | 10 | 0 | 0
44.4 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.4 | 4 | 7 | 7 | 0 | 12 | 1 | 1 | 7 | 10 | 0 | 0
44.45 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.5 | 5 | 7.5 | 7.5 | 0 | 12 | 1 | 1 | 7.5 | 10 | 0 | 0
44.5 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.6 | 6 | 8 | 8 | 0 | 12 | 1 | 1 | 8 | 10 | 0 | 0
44.55 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.7 | 7 | 8.5 | 8.5 | 0 | 12 | 1 | 1 | 8.5 | 10 | 0 | 0
44.6 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.8 | 8 | 9 | 9 | 0 | 12 | 1 | 1 | 9 | 10 | 0 | 0
44.65 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.9 | 9 | 9.5 | 9.5 | 0 | 12 | 1 | 1 | 9.5 | 10 | 0 | 0
44.7 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
44.75 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
44.8 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
44.85 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
44.9 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
44.95 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
45 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
45.05 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
45.1 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
45.15 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
45.2 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
45.25 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
45.3 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
45.35 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
45.4 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
45.45 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
45.5 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
45.55 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
45.6 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
45.65 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
45.7 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
45.75 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
45.8 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
45.85 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
45.9 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
45.95 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
46 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
46.05 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
46.1 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
46.15 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
46.2 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
46.25 | 50.5 | 50.5 | -1 | 0.9 | 9 | 50.5 | -1 | -1 | -10 | -0.5 | -0.5 | 0 | 12 | 1 | 1 | -0.5 | 10 | 0 | 0
46.3 | 50.5 | 50.5 | -1 | 0.8 | 8 | 50.5 | -1 | -1 | -10 | -1 | -1 | 0 | 12 | 1 | 1 | -1 | 10 | 0 | 0
46.35 | 50.5 | 50.5 | -1 | 0.7 | 7 | 50.5 | -1 | -1 | -10 | -1.5 | -1.5 | 0 | 12 | 1 | 1 | -1.5 | 10 | 0 | 0
46.4 | 50.5 | 50.5 | -1 | 0.6 | 6 | 50.5 | -1 | -1 | -10 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
46.45 | 50.5 | 50.5 | -1 | 0.5 | 5 | 50.5 | -1 | -1 | -10 | -2.5 | -2.5 | 0 | 12 | 1 | 1 | -2.5 | 10 | 0 | 0
46.5 | 50.5 | 50.5 | -1 | 0.4 | 4 | 50.5 | -1 | -1 | -10 | -3 | -3 | 0 | 12 | 1 | 1 | -3 | 10 | 0 | 0
46.55 | 50.5 | 50.5 | -1 | 0.3 | 3 | 50.5 | -1 | -1 | -10 | -3.5 | -3.5 | 0 | 12 | 1 | 1 | -3.5 | 10 | 0 | 0
46.6 | 50.5 | 50.5 | -1 | 0.2 | 2 | 50.5 | -1 | -1 | -10 | -4 | -4 | 0 | 12 | 1 | 1 | -4 | 10 | 0 | 0
46.65 | 50.5 | 50.5 | -1 | 0.1 | 1 | 50.5 | -1 | -1 | -10 | -4.5 | -4.5 | 0 | 12 | 1 | 1 | -4.5 | 10 | 0 | 0
46.7 | 50.5 | 50.5 | -1 | 0 | 0 | 50.5 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
46.75 | 50.5 | 50.5 | -1 | -0.1 | -1 | 50.5 | -1 | -1 | -10 | -5.5 | -5.5 | 0 | 12 | 1 | 1 | -5.5 | 10 | 0 | 0
46.8 | 50.5 | 50.5 | -1 | -0.2 | -2 | 50.5 | -1 | -1 | -10 | -6 | -6 | 0 | 12 | 1 | 1 | -6 | 10 | 0 | 0
46.85 | 50.5 | 50.5 | -1 | -0.3 | -3 | 50.5 | -1 | -1 | -10 | -6.5 | -6.5 | 0 | 12 | 1 | 1 | -6.5 | 10 | 0 | 0
46.9 | 50.5 | 50.5 | -1 | -0.4 | -4 | 50.5 | -1 | -1 | -10 | -7 | -7 | 0 | 12 | 1 | 1 | -7 | 10 | 0 | 0
46.95 | 50.5 | 50.5 | -1 | -0.5 | -5 | 50.5 | -1 | -1 | -10 | -7.5 | -7.5 | 0 | 12 | 1 | 1 | -7.5 | 10 | 0 | 0
47 | 50.5 | 50.5 | -1 | -0.6 | -6 | 50.5 | -1 | -1 | -10 | -8 | -8 | 0 | 12 | 1 | 1 | -8 | 10 | 0 | 0
47.05 | 50.5 | 50.5 | -1 | -0.7 | -7 | 50.5 | -1 | -1 | -10 | -8.5 | -8.5 | 0 | 12 | 1 | 1 | -8.5 | 10 | 0 | 0
47.1 | 50.5 | 50.5 | -1 | -0.8 | -8 | 50.5 | -1 | -1 | -10 | -9 | -9 | 0 | 12 | 1 | 1 | -9 | 10 | 0 | 0
47.15 | 50.5 | 50.5 | -1 | -0.9 | -9 | 50.5 | -1 | -1 | -10 | -9.5 | -9.5 | 0 | 12 | 1 | 1 | -9.5 | 10 | 0 | 0
47.2 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
47.25 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
47.3 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
47.35 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
47.4 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
47.45 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
47.5 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
47.55 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
47.6 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
47.65 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
47.7 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
47.75 | 50.47 | 50.47 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
47.8 | 50.45 | 50.45 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
47.85 | 50.42 | 50.42 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
47.9 | 50.4 | 50.4 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
47.95 | 50.37 | 50.37 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
48 | 50.35 | 50.35 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
48.05 | 50.32 | 50.32 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
48.1 | 50.29 | 50.29 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
48.15 | 50.27 | 50.27 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
48.2 | 50.24 | 50.24 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
48.25 | 50.22 | 50.22 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
48.3 | 50.19 | 50.19 | -0.905 | -0.905 | -9.05 | 50.47 | -1 | -1 | -10 | -9.525 | -9.525 | 0 | 12 | 1 | 1 | -9.525 | 10 | 0 | 0
48.35 | 50.17 | 50.17 | -0.715 | -0.715 | -7.15 | 50.45 | -1 | -1 | -10 | -8.575 | -8.575 | 0 | 12 | 1 | 1 | -8.575 | 10 | 0 | 0
48.4 | 50.14 | 50.14 | -0.43 | -0.43 | -4.3 | 50.42 | -1 | -1 | -10 | -7.15 | -7.15 | 0 | 12 | 1 | 1 | -7.15 | 10 | 0 | 0
48.45 | 50.12 | 50.12 | -0.24 | -0.24 | -2.4 | 50.4 | -1 | -1 | -10 | -6.2 | -6.2 | 0 | 12 | 1 | 1 | -6.2 | 10 | 0 | 0
48.5 | 50.09 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 50.37 | -1 | -1 | -10 | -5.2206 | -5.2206 | 0 | 12 | 1 | 1 | -5.2206 | 10 | 0 | 0
48.55 | 50.06 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.35 | -1 | -1 | -10 | -5.1324 | -5.1324 | 0 | 12 | 1 | 1 | -5.1324 | 10 | 0 | 0
48.6 | 50.04 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.32 | -1 | -1 | -10 | -5.0735 | -5.0735 | 0 | 12 | 1 | 1 | -5.0735 | 10 | 0 | 0
48.65 | 50.01 | 50.01 | 0 | 0 | 0 | 50.29 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
48.7 | 49.99 | 49.99 | 0 | 0 | 0 | 50.27 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
48.75 | 49.96 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.24 | -1 | -1 | -10 | -4.9265 | -4.9265 | 0 | 12 | 1 | 1 | -4.9265 | 10 | 0 | 0
48.8 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.22 | -1 | -1 | -10 | -4.8676 | -4.8676 | 0 | 12 | 1 | 1 | -4.8676 | 10 | 0 | 0
48.85 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.19 | -0.905 | -0.905 | -9.05 | -4.3044 | -4.3044 | 0 | 12 | 1 | 1 | -4.3044 | 10 | 0 | 0
48.9 | 49.88 | 49.88 | 0.24 | 0.24 | 2.4 | 50.17 | -0.715 | -0.805 | -8.05 | -2.825 | -2.825 | 0 | 12 | 1 | 1 | -2.825 | 10 | 0 | 0
48.95 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.14 | -0.43 | -0.705 | -7.05 | -1.375 | -1.375 | 0 | 12 | 1 | 1 | -1.375 | 10 | 0 | 0
49 | 49.83 | 49.83 | 0.715 | 0.715 | 7.15 | 50.12 | -0.24 | -0.605 | -6.05 | 0.55 | 0.55 | 0 | 12 | 1 | 1 | 0.55 | 10 | 0 | 0
49.05 | 49.81 | 49.81 | 0.905 | 0.905 | 9.05 | 50.09 | -0.044118 | -0.505 | -5.05 | 2 | 2 | 0 | 12 | 1 | 1 | 2 | 10 | 0 | 0
49.1 | 49.78 | 49.78 | 1 | 1 | 10 | 50.06 | -0.026471 | -0.405 | -4.05 | 2.975 | 2.975 | 0 | 12 | 1 | 1 | 2.975 | 10 | 0 | 0
49.15 | 49.76 | 49.76 | 1 | 1 | 10 | 50.04 | -0.014706 | -0.305 | -3.05 | 3.475 | 3.475 | 0 | 12 | 1 | 1 | 3.475 | 10 | 0 | 0
49.2 | 49.73 | 49.73 | 1 | 1 | 10 | 50.01 | 0 | -0.205 | -2.05 | 3.975 | 3.975 | 0 | 12 | 1 | 1 | 3.975 | 10 | 0 | 0
49.25 | 49.71 | 49.71 | 1 | 1 | 10 | 49.99 | 0 | -0.105 | -1.05 | 4.475 | 4.475 | 0 | 12 | 1 | 1 | 4.475 | 10 | 0 | 0
49.3 | 49.68 | 49.68 | 1 | 1 | 10 | 49.96 | 0.014706 | -0.005 | -0.05 | 4.975 | 4.975 | 0 | 12 | 1 | 1 | 4.975 | 10 | 0 | 0
49.35 | 49.65 | 49.65 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
49.4 | 49.63 | 49.63 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
49.45 | 49.6 | 49.6 | 1 | 1 | 10 | 49.88 | 0.24 | 0.14412 | 1.4412 | 5.7206 | 5.7206 | 0 | 12 | 1 | 1 | 5.7206 | 10 | 0 | 0
49.5 | 49.58 | 49.58 | 1 | 1 | 10 | 49.86 | 0.43 | 0.24412 | 2.4412 | 6.2206 | 6.2206 | 0 | 12 | 1 | 1 | 6.2206 | 10 | 0 | 0
49.55 | 49.55 | 49.55 | 1 | 1 | 10 | 49.83 | 0.715 | 0.34412 | 3.4412 | 6.7206 | 6.7206 | 0 | 12 | 1 | 1 | 6.7206 | 10 | 0 | 0
49.6 | 49.53 | 49.53 | 1 | 1 | 10 | 49.81 | 0.905 | 0.44412 | 4.4412 | 7.2206 | 7.2206 | 0 | 12 | 1 | 1 | 7.2206 | 10 | 0 | 0
49.65 | 49.5 | 49.5 | 1 | 1 | 10 | 49.78 | 1 | 0.54412 | 5.4412 | 7.7206 | 7.7206 | 0 | 12 | 1 | 1 | 7.7206 | 10 | 0 | 0
49.7 | 49.5 | 49.5 | 1 | 1 | 10 | 49.76 | 1 | 0.64412 | 6.4412 | 8.2206 | 8.2206 | 0 | 12 | 1 | 1 | 8.2206 | 10 | 0 | 0
49.75 | 49.53 | 49.5 | 1 | 1 | 10 | 49.73 | 1 | 0.74412 | 7.4412 | 8.7206 | 8.7206 | 0 | 12 | 1 | 1 | 8.7206 | 10 | 0 | 0
49.8 | 49.55 | 49.5 | 1 | 1 | 10 | 49.71 | 1 | 0.84412 | 8.4412 | 9.2206 | 9.2206 | 0 | 12 | 1 | 1 | 9.2206 | 10 | 0 | 0
49.85 | 49.58 | 49.5 | 1 | 1 | 10 | 49.68 | 1 | 0.94412 | 9.4412 | 9.7206 | 9.7206 | 0 | 12 | 1 | 1 | 9.7206 | 10 | 0 | 0
49.9 | 49.6 | 49.5 | 1 | 1 | 10 | 49.65 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
49.95 | 49.63 | 49.5 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
50 | 49.65 | 49.5 | 1 | 1 | 10 | 49.65 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
50.05 | 49.68 | 49.5 | 1 | 1 | 10 | 49.68 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
50.1 | 49.71 | 49.5 | 1 | 1 | 10 | 49.71 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
50.15 | 49.73 | 49.5 | 1 | 1 | 10 | 49.73 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
50.2 | 49.76 | 49.5 | 1 | 1 | 10 | 49.76 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
50.25 | 49.78 | 49.5 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
50.3 | 49.81 | 49.53 | 1 | 1 | 10 | 49.81 | 0.905 | 0.905 | 9.05 | 9.525 | 9.525 | 0 | 12 | 1 | 1 | 9.525 | 10 | 0 | 0
50.35 | 49.83 | 49.55 | 1 | 1 | 10 | 49.83 | 0.715 | 0.715 | 7.15 | 8.575 | 8.575 | 0 | 12 | 1 | 1 | 8.575 | 10 | 0 | 0
50.4 | 49.86 | 49.58 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
50.45 | 49.88 | 49.6 | 1 | 1 | 10 | 49.88 | 0.24 | 0.24 | 2.4 | 6.2 | 6.2 | 0 | 12 | 1 | 1 | 6.2 | 10 | 0 | 0
50.5 | 49.91 | 49.63 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
50.55 | 49.94 | 49.65 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
50.6 | 49.96 | 49.68 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
50.65 | 49.99 | 49.71 | 1 | 1 | 10 | 49.99 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
50.7 | 50.01 | 49.73 | 1 | 1 | 10 | 50.01 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
50.75 | 50.04 | 49.76 | 1 | 1 | 10 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 4.9265 | 4.9265 | 0 | 12 | 1 | 1 | 4.9265 | 10 | 0 | 0
50.8 | 50.06 | 49.78 | 1 | 1 | 10 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 4.8676 | 4.8676 | 0 | 12 | 1 | 1 | 4.8676 | 10 | 0 | 0
50.85 | 50.09 | 49.81 | 0.905 | 0.905 | 9.05 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 4.3044 | 4.3044 | 0 | 12 | 1 | 1 | 4.3044 | 10 | 0 | 0
50.9 | 50.12 | 49.83 | 0.715 | 0.805 | 8.05 | 50.12 | -0.24 | -0.24 | -2.4 | 2.825 | 2.825 | 0 | 12 | 1 | 1 | 2.825 | 10 | 0 | 0
50.95 | 50.14 | 49.86 | 0.43 | 0.705 | 7.05 | 50.14 | -0.43 | -0.43 | -4.3 | 1.375 | 1.375 | 0 | 12 | 1 | 1 | 1.375 | 10 | 0 | 0
51 | 50.17 | 49.88 | 0.24 | 0.605 | 6.05 | 50.17 | -0.715 | -0.715 | -7.15 | -0.55 | -0.55 | 0 | 12 | 1 | 1 | -0.55 | 10 | 0 | 0
51.05 | 50.19 | 49.91 | 0.044118 | 0.505 | 5.05 | 50.19 | -0.905 | -0.905 | -9.05 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
51.1 | 50.22 | 49.94 | 0.026471 | 0.405 | 4.05 | 50.22 | -1 | -1 | -10 | -2.975 | -2.975 | 0 | 12 | 1 | 1 | -2.975 | 10 | 0 | 0
51.15 | 50.24 | 49.96 | 0.014706 | 0.305 | 3.05 | 50.24 | -1 | -1 | -10 | -3.475 | -3.475 | 0 | 12 | 1 | 1 | -3.475 | 10 | 0 | 0
51.2 | 50.27 | 49.99 | 0 | 0.205 | 2.05 | 50.27 | -1 | -1 | -10 | -3.975 | -3.975 | 0 | 12 | 1 | 1 | -3.975 | 10 | 0 | 0
51.25 | 50.29 | 50.01 | 0 | 0.105 | 1.05 | 50.29 | -1 | -1 | -10 | -4.475 | -4.475 | 0 | 12 | 1 | 1 | -4.475 | 10 | 0 | 0
51.3 | 50.32 | 50.04 | -0.014706 | 0.005 | 0.05 | 50.32 | -1 | -1 | -10 | -4.975 | -4.975 | 0 | 12 | 1 | 1 | -4.975 | 10 | 0 | 0
51.35 | 50.35 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.35 | -1 | -1 | -10 | -5.1324 | -5.1324 | 0 | 12 | 1 | 1 | -5.1324 | 10 | 0 | 0
51.4 | 50.37 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 50.37 | -1 | -1 | -10 | -5.2206 | -5.2206 | 0 | 12 | 1 | 1 | -5.2206 | 10 | 0 | 0
51.45 | 50.4 | 50.12 | -0.24 | -0.14412 | -1.4412 | 50.4 | -1 | -1 | -10 | -5.7206 | -5.7206 | 0 | 12 | 1 | 1 | -5.7206 | 10 | 0 | 0
51.5 | 50.42 | 50.14 | -0.43 | -0.24412 | -2.4412 | 50.42 | -1 | -1 | -10 | -6.2206 | -6.2206 | 0 | 12 | 1 | 1 | -6.2206 | 10 | 0 | 0
51.55 | 50.45 | 50.17 | -0.715 | -0.34412 | -3.4412 | 50.45 | -1 | -1 | -10 | -6.7206 | -6.7206 | 0 | 12 | 1 | 1 | -6.7206 | 10 | 0 | 0
51.6 | 50.47 | 50.19 | -0.905 | -0.44412 | -4.4412 | 50.47 | -1 | -1 | -10 | -7.2206 | -7.2206 | 0 | 12 | 1 | 1 | -7.2206 | 10 | 0 | 0
51.65 | 50.5 | 50.22 | -1 | -0.54412 | -5.4412 | 50.5 | -1 | -1 | -10 | -7.7206 | -7.7206 | 0 | 12 | 1 | 1 | -7.7206 | 10 | 0 | 0
51.7 | 50.5 | 50.24 | -1 | -0.64412 | -6.4412 | 50.5 | -1 | -1 | -10 | -8.2206 | -8.2206 | 0 | 12 | 1 | 1 | -8.2206 | 10 | 0 | 0
51.75 | 50.47 | 50.27 | -1 | -0.74412 | -7.4412 | 50.5 | -1 | -1 | -10 | -8.7206 | -8.7206 | 0 | 12 | 1 | 1 | -8.7206 | 10 | 0 | 0
51.8 | 50.45 | 50.29 | -1 | -0.84412 | -8.4412 | 50.5 | -1 | -1 | -10 | -9.2206 | -9.2206 | 0 | 12 | 1 | 1 | -9.2206 | 10 | 0 | 0
51.85 | 50.42 | 50.32 | -1 | -0.94412 | -9.4412 | 50.5 | -1 | -1 | -10 | -9.7206 | -9.7206 | 0 | 12 | 1 | 1 | -9.7206 | 10 | 0 | 0
51.9 | 50.39 | 50.35 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
51.95 | 50.37 | 50.37 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
52 | 50.34 | 50.34 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
52.05 | 50.32 | 50.32 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
52.1 | 50.29 | 50.29 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
52.15 | 50.26 | 50.26 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
52.2 | 50.24 | 50.24 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
52.25 | 50.21 | 50.21 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
52.3 | 50.18 | 50.18 | -0.81 | -0.81 | -8.1 | 50.47 | -1 | -1 | -10 | -9.05 | -9.05 | 0 | 12 | 1 | 1 | -9.05 | 10 | 0 | 0
52.35 | 50.16 | 50.16 | -0.62 | -0.62 | -6.2 | 50.45 | -1 | -1 | -10 | -8.1 | -8.1 | 0 | 12 | 1 | 1 | -8.1 | 10 | 0 | 0
52.4 | 50.13 | 50.13 | -0.335 | -0.335 | -3.35 | 50.42 | -1 | -1 | -10 | -6.675 | -6.675 | 0 | 12 | 1 | 1 | -6.675 | 10 | 0 | 0
52.45 | 50.11 | 50.11 | -0.145 | -0.145 | -1.45 | 50.39 | -1 | -1 | -10 | -5.725 | -5.725 | 0 | 12 | 1 | 1 | -5.725 | 10 | 0 | 0
52.5 | 50.08 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 50.37 | -1 | -1 | -10 | -5.1912 | -5.1912 | 0 | 12 | 1 | 1 | -5.1912 | 10 | 0 | 0
52.55 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.34 | -1 | -1 | -10 | -5.1029 | -5.1029 | 0 | 12 | 1 | 1 | -5.1029 | 10 | 0 | 0
52.6 | 50.03 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 50.32 | -1 | -1 | -10 | -5.0441 | -5.0441 | 0 | 12 | 1 | 1 | -5.0441 | 10 | 0 | 0
52.65 | 50 | 50 | 0 | 0 | 0 | 50.29 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
52.7 | 50 | 50 | 0 | 0 | 0 | 50.26 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
52.75 | 50 | 50 | 0 | 0 | 0 | 50.24 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
52.8 | 50 | 50 | 0 | 0 | 0 | 50.21 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
52.85 | 50 | 50 | 0 | 0 | 0 | 50.18 | -0.81 | -0.9 | -9 | -4.5 | -4.5 | 0 | 12 | 1 | 1 | -4.5 | 10 | 0 | 0
52.9 | 50 | 50 | 0 | 0 | 0 | 50.16 | -0.62 | -0.8 | -8 | -4 | -4 | 0 | 12 | 1 | 1 | -4 | 10 | 0 | 0
52.95 | 50 | 50 | 0 | 0 | 0 | 50.13 | -0.335 | -0.7 | -7 | -3.5 | -3.5 | 0 | 12 | 1 | 1 | -3.5 | 10 | 0 | 0
53 | 50.01 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.6 | -6 | -3 | -3 | 0 | 12 | 1 | 1 | -3 | 10 | 0 | 0
53.05 | 50.01 | 50 | 0 | 0 | 0 | 50.08 | -0.038235 | -0.5 | -5 | -2.5 | -2.5 | 0 | 12 | 1 | 1 | -2.5 | 10 | 0 | 0
53.1 | 49.99 | 49.99 | 0 | 0 | 0 | 50.05 | -0.020588 | -0.4 | -4 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
53.15 | 49.99 | 49.99 | 0 | 0 | 0 | 50.03 | -0.0088235 | -0.3 | -3 | -1.5 | -1.5 | 0 | 12 | 1 | 1 | -1.5 | 10 | 0 | 0
53.2 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | -0.2 | -2 | -0.83824 | -0.83824 | 0 | 12 | 1 | 1 | -0.83824 | 10 | 0 | 0
53.25 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | -0.1 | -1 | -0.33824 | -0.33824 | 0 | 12 | 1 | 1 | -0.33824 | 10 | 0 | 0
53.3 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
53.35 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
53.4 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
53.45 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
53.5 | 49.89 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
53.55 | 49.89 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
53.6 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50.01 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
53.65 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
53.7 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
53.75 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 2.7868 | 2.7868 | 0 | 12 | 1 | 1 | 2.7868 | 10 | 0 | 0
53.8 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 2.7868 | 2.7868 | 0 | 12 | 1 | 1 | 2.7868 | 10 | 0 | 0
53.85 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 2.8456 | 2.8456 | 0 | 12 | 1 | 1 | 2.8456 | 10 | 0 | 0
53.9 | 49.94 | 49.85 | 0.525 | 0.525 | 5.25 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 2.7574 | 2.7574 | 0 | 12 | 1 | 1 | 2.7574 | 10 | 0 | 0
53.95 | 49.94 | 49.85 | 0.525 | 0.525 | 5.25 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 2.7574 | 2.7574 | 0 | 12 | 1 | 1 | 2.7574 | 10 | 0 | 0
54 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
54.05 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
54.1 | 49.93 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
54.15 | 49.93 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
54.2 | 49.96 | 49.85 | 0.525 | 0.525 | 5.25 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 2.6985 | 2.6985 | 0 | 12 | 1 | 1 | 2.6985 | 10 | 0 | 0
54.25 | 49.96 | 49.85 | 0.525 | 0.525 | 5.25 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 2.6985 | 2.6985 | 0 | 12 | 1 | 1 | 2.6985 | 10 | 0 | 0
54.3 | 49.99 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
54.35 | 49.99 | 49.91 | 0.044118 | 0.425 | 4.25 | 49.99 | 0 | 0 | 0 | 2.125 | 2.125 | 0 | 12 | 1 | 1 | 2.125 | 10 | 0 | 0
54.4 | 49.99 | 49.91 | 0.044118 | 0.325 | 3.25 | 49.99 | 0 | 0 | 0 | 1.625 | 1.625 | 0 | 12 | 1 | 1 | 1.625 | 10 | 0 | 0
54.45 | 49.99 | 49.93 | 0.032353 | 0.225 | 2.25 | 49.99 | 0 | 0 | 0 | 1.125 | 1.125 | 0 | 12 | 1 | 1 | 1.125 | 10 | 0 | 0
54.5 | 49.96 | 49.93 | 0.032353 | 0.125 | 1.25 | 49.99 | 0 | 0 | 0 | 0.625 | 0.625 | 0 | 12 | 1 | 1 | 0.625 | 10 | 0 | 0
54.55 | 49.96 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 49.99 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
54.6 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
54.65 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
54.7 | 50.05 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.058824 | 0.058824 | 0 | 12 | 1 | 1 | 0.058824 | 10 | 0 | 0
54.75 | 50.05 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
54.8 | 49.97 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
54.85 | 49.97 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
54.9 | 49.92 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
54.95 | 49.92 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
55 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
55.05 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
55.1 | 49.94 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
55.15 | 49.94 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
55.2 | 50.01 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
55.25 | 50.01 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
55.3 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
55.35 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
55.4 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
55.45 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
55.5 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
55.55 | 49.95 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
55.6 | 49.97 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
55.65 | 49.97 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
55.7 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
55.75 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
55.8 | 49.87 | 49.87 | 0.335 | 0.335 | 3.35 | 50.01 | 0 | 0 | 0 | 1.675 | 1.675 | 0 | 12 | 1 | 1 | 1.675 | 10 | 0 | 0
55.85 | 49.87 | 49.87 | 0.335 | 0.335 | 3.35 | 49.99 | 0 | 0 | 0 | 1.675 | 1.675 | 0 | 12 | 1 | 1 | 1.675 | 10 | 0 | 0
55.9 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
55.95 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 2.6691 | 2.6691 | 0 | 12 | 1 | 1 | 2.6691 | 10 | 0 | 0
56 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
56.05 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
56.1 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
56.15 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
56.2 | 49.84 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
56.25 | 49.84 | 49.79 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
56.3 | 49.89 | 49.79 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
56.35 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.12647 | 1.2647 | 5.6324 | 5.6324 | 0 | 12 | 1 | 1 | 5.6324 | 10 | 0 | 0
56.4 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.145 | 1.45 | 5.725 | 5.725 | 0 | 12 | 1 | 1 | 5.725 | 10 | 0 | 0
56.45 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.145 | 1.45 | 5.725 | 5.725 | 0 | 12 | 1 | 1 | 5.725 | 10 | 0 | 0
56.5 | 49.96 | 49.79 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
56.55 | 49.96 | 49.79 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
56.6 | 50.02 | 49.79 | 1 | 1 | 10 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 4.9853 | 4.9853 | 0 | 12 | 1 | 1 | 4.9853 | 10 | 0 | 0
56.65 | 50.02 | 49.79 | 1 | 1 | 10 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 4.9853 | 4.9853 | 0 | 12 | 1 | 1 | 4.9853 | 10 | 0 | 0
56.7 | 50.03 | 49.79 | 1 | 1 | 10 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.9559 | 4.9559 | 0 | 12 | 1 | 1 | 4.9559 | 10 | 0 | 0
56.75 | 50.03 | 49.84 | 0.62 | 0.9 | 9 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.4559 | 4.4559 | 0 | 12 | 1 | 1 | 4.4559 | 10 | 0 | 0
56.8 | 50.02 | 49.84 | 0.62 | 0.8 | 8 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 3.9559 | 3.9559 | 0 | 12 | 1 | 1 | 3.9559 | 10 | 0 | 0
56.85 | 50.02 | 49.89 | 0.145 | 0.7 | 7 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 3.4559 | 3.4559 | 0 | 12 | 1 | 1 | 3.4559 | 10 | 0 | 0
56.9 | 50.08 | 49.89 | 0.145 | 0.6 | 6 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 2.8088 | 2.8088 | 0 | 12 | 1 | 1 | 2.8088 | 10 | 0 | 0
56.95 | 50.08 | 49.89 | 0.145 | 0.5 | 5 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 2.3088 | 2.3088 | 0 | 12 | 1 | 1 | 2.3088 | 10 | 0 | 0
57 | 50.01 | 49.89 | 0.145 | 0.4 | 4 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 1.8088 | 1.8088 | 0 | 12 | 1 | 1 | 1.8088 | 10 | 0 | 0
57.05 | 50.01 | 49.96 | 0.014706 | 0.3 | 3 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 1.3088 | 1.3088 | 0 | 12 | 1 | 1 | 1.3088 | 10 | 0 | 0
57.1 | 49.94 | 49.94 | 0.026471 | 0.2 | 2 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.80882 | 0.80882 | 0 | 12 | 1 | 1 | 0.80882 | 10 | 0 | 0
57.15 | 49.94 | 49.94 | 0.026471 | 0.1 | 1 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.30882 | 0.30882 | 0 | 12 | 1 | 1 | 0.30882 | 10 | 0 | 0
57.2 | 50 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
57.25 | 50 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
57.3 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
57.35 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
57.4 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
57.45 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
57.5 | 49.92 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
57.55 | 49.92 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
57.6 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50.01 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
57.65 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
57.7 | 49.92 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
57.75 | 49.92 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
57.8 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
57.85 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
57.9 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
57.95 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
58 | 49.87 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
58.05 | 49.87 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
58.1 | 49.8 | 49.8 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
58.15 | 49.8 | 49.8 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
58.2 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
58.25 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
58.3 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
58.35 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
58.4 | 49.72 | 49.72 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
58.45 | 49.72 | 49.72 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
58.5 | 49.67 | 49.67 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
58.55 | 49.67 | 49.67 | 1 | 1 | 10 | 49.87 | 0.335 | 0.14412 | 1.4412 | 5.7206 | 5.7206 | 0 | 12 | 1 | 1 | 5.7206 | 10 | 0 | 0
58.6 | 49.65 | 49.65 | 1 | 1 | 10 | 49.87 | 0.335 | 0.24412 | 2.4412 | 6.2206 | 6.2206 | 0 | 12 | 1 | 1 | 6.2206 | 10 | 0 | 0
58.65 | 49.65 | 49.65 | 1 | 1 | 10 | 49.8 | 1 | 0.34412 | 3.4412 | 6.7206 | 6.7206 | 0 | 12 | 1 | 1 | 6.7206 | 10 | 0 | 0
58.7 | 49.59 | 49.59 | 1 | 1 | 10 | 49.8 | 1 | 0.44412 | 4.4412 | 7.2206 | 7.2206 | 0 | 12 | 1 | 1 | 7.2206 | 10 | 0 | 0
58.75 | 49.59 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.54412 | 5.4412 | 7.7206 | 7.7206 | 0 | 12 | 1 | 1 | 7.7206 | 10 | 0 | 0
58.8 | 49.66 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.64412 | 6.4412 | 8.2206 | 8.2206 | 0 | 12 | 1 | 1 | 8.2206 | 10 | 0 | 0
58.85 | 49.66 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.74412 | 7.4412 | 8.7206 | 8.7206 | 0 | 12 | 1 | 1 | 8.7206 | 10 | 0 | 0
58.9 | 49.63 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.84412 | 8.4412 | 9.2206 | 9.2206 | 0 | 12 | 1 | 1 | 9.2206 | 10 | 0 | 0
58.95 | 49.63 | 49.59 | 1 | 1 | 10 | 49.72 | 1 | 0.94412 | 9.4412 | 9.7206 | 9.7206 | 0 | 12 | 1 | 1 | 9.7206 | 10 | 0 | 0
59 | 49.61 | 49.59 | 1 | 1 | 10 | 49.72 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
59.05 | 49.61 | 49.59 | 1 | 1 | 10 | 49.67 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
59.1 | 49.54 | 49.54 | 1 | 1 | 10 | 49.67 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
59.15 | 49.54 | 49.54 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
59.2 | 49.46 | 49.46 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
59.25 | 49.46 | 49.46 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
59.3 | 49.45 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
59.35 | 49.45 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
59.4 | 49.51 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
59.45 | 49.51 | 49.45 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
59.5 | 49.5 | 49.45 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
59.55 | 49.5 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
59.6 | 49.54 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
59.65 | 49.54 | 49.45 | 1 | 1 | 10 | 49.54 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
59.7 | 49.59 | 49.45 | 1 | 1 | 10 | 49.59 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
59.75 | 49.59 | 49.45 | 1 | 1 | 10 | 49.59 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
59.8 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
59.85 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
59.9 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
59.95 | 49.61 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
60 | 49.53 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
60.05 | 49.53 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
60.1 | 49.54 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
60.15 | 49.54 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
60.2 | 49.61 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
60.25 | 49.61 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
60.3 | 49.66 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
60.35 | 49.66 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
60.4 | 49.64 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
60.45 | 49.64 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
60.5 | 49.69 | 49.53 | 1 | 1 | 10 | 49.69 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
60.55 | 49.69 | 49.53 | 1 | 1 | 10 | 49.69 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
60.6 | 49.74 | 49.53 | 1 | 1 | 10 | 49.74 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
60.65 | 49.74 | 49.54 | 1 | 1 | 10 | 49.74 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
60.7 | 49.78 | 49.54 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
60.75 | 49.78 | 49.61 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
60.8 | 49.82 | 49.61 | 1 | 1 | 10 | 49.82 | 0.81 | 0.81 | 8.1 | 9.05 | 9.05 | 0 | 12 | 1 | 1 | 9.05 | 10 | 0 | 0
60.85 | 49.82 | 49.64 | 1 | 1 | 10 | 49.82 | 0.81 | 0.81 | 8.1 | 9.05 | 9.05 | 0 | 12 | 1 | 1 | 9.05 | 10 | 0 | 0
60.9 | 49.86 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
60.95 | 49.86 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
61 | 49.84 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
61.05 | 49.84 | 49.69 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
61.1 | 49.91 | 49.69 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
61.15 | 49.91 | 49.74 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
61.2 | 49.97 | 49.74 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
61.25 | 49.97 | 49.78 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
61.3 | 50.03 | 49.78 | 1 | 1 | 10 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.9559 | 4.9559 | 0 | 12 | 1 | 1 | 4.9559 | 10 | 0 | 0
61.35 | 50.03 | 49.82 | 0.81 | 0.9 | 9 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.4559 | 4.4559 | 0 | 12 | 1 | 1 | 4.4559 | 10 | 0 | 0
61.4 | 50.05 | 49.82 | 0.81 | 0.81 | 8.1 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 3.9471 | 3.9471 | 0 | 12 | 1 | 1 | 3.9471 | 10 | 0 | 0
61.45 | 50.05 | 49.84 | 0.62 | 0.71 | 7.1 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 3.4471 | 3.4471 | 0 | 12 | 1 | 1 | 3.4471 | 10 | 0 | 0
61.5 | 50.01 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
61.55 | 50.01 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
61.6 | 49.95 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
61.65 | 49.95 | 49.91 | 0.044118 | 0.52 | 5.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.4971 | 2.4971 | 0 | 12 | 1 | 1 | 2.4971 | 10 | 0 | 0
61.7 | 49.99 | 49.91 | 0.044118 | 0.42 | 4.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 1.9971 | 1.9971 | 0 | 12 | 1 | 1 | 1.9971 | 10 | 0 | 0
61.75 | 49.99 | 49.95 | 0.020588 | 0.32 | 3.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 1.4971 | 1.4971 | 0 | 12 | 1 | 1 | 1.4971 | 10 | 0 | 0
61.8 | 49.92 | 49.92 | 0.038235 | 0.22 | 2.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.99706 | 0.99706 | 0 | 12 | 1 | 1 | 0.99706 | 10 | 0 | 0
61.85 | 49.92 | 49.92 | 0.038235 | 0.12 | 1.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.49706 | 0.49706 | 0 | 12 | 1 | 1 | 0.49706 | 10 | 0 | 0
61.9 | 49.97 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
61.95 | 49.97 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
62 | 50.02 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
62.05 | 50.02 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.17647 | 0.17647 | 0 | 12 | 1 | 1 | 0.17647 | 10 | 0 | 0
62.1 | 50.07 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
62.15 | 50.07 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
62.2 | 50.06 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
62.25 | 50.06 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
62.3 | 50.13 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
62.35 | 50.13 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
62.4 | 50.09 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
62.45 | 50.09 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6309 | -1.6309 | 0 | 12 | 1 | 1 | -1.6309 | 10 | 0 | 0
62.5 | 50.07 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6309 | -1.6309 | 0 | 12 | 1 | 1 | -1.6309 | 10 | 0 | 0
62.55 | 50.07 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6897 | -1.6897 | 0 | 12 | 1 | 1 | -1.6897 | 10 | 0 | 0
62.6 | 50.07 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6897 | -1.6897 | 0 | 12 | 1 | 1 | -1.6897 | 10 | 0 | 0
62.65 | 50.07 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.13 | -0.335 | -0.335 | -3.35 | -1.8074 | -1.8074 | 0 | 12 | 1 | 1 | -1.8074 | 10 | 0 | 0
62.7 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.13 | -0.335 | -0.335 | -3.35 | -1.7779 | -1.7779 | 0 | 12 | 1 | 1 | -1.7779 | 10 | 0 | 0
62.75 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.13 | -0.335 | -0.335 | -3.35 | -1.7779 | -1.7779 | 0 | 12 | 1 | 1 | -1.7779 | 10 | 0 | 0
62.8 | 50.01 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
62.85 | 50.01 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
62.9 | 50.07 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
62.95 | 50.07 | 50.01 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.235 | -2.35 | -1.175 | -1.175 | 0 | 12 | 1 | 1 | -1.175 | 10 | 0 | 0
63 | 50.05 | 50.01 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.135 | -1.35 | -0.675 | -0.675 | 0 | 12 | 1 | 1 | -0.675 | 10 | 0 | 0
63.05 | 50.05 | 50.01 | 0 | 0 | 0 | 50.07 | -0.032353 | -0.035 | -0.35 | -0.175 | -0.175 | 0 | 12 | 1 | 1 | -0.175 | 10 | 0 | 0
63.1 | 50.1 | 50.01 | 0 | 0 | 0 | 50.1 | -0.05 | -0.05 | -0.5 | -0.25 | -0.25 | 0 | 12 | 1 | 1 | -0.25 | 10 | 0 | 0
63.15 | 50.1 | 50.01 | 0 | 0 | 0 | 50.1 | -0.05 | -0.05 | -0.5 | -0.25 | -0.25 | 0 | 12 | 1 | 1 | -0.25 | 10 | 0 | 0
63.2 | 50.11 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
63.25 | 50.11 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
63.3 | 50.06 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
63.35 | 50.06 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
63.4 | 50.04 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
63.45 | 50.04 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
63.5 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
63.55 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
63.6 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
63.65 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
63.7 | 50.11 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
63.75 | 50.11 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
63.8 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
63.85 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
63.9 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
63.95 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
64 | 50.02 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.11 | -0.145 | -0.145 | -1.45 | -0.73971 | -0.73971 | 0 | 12 | 1 | 1 | -0.73971 | 10 | 0 | 0
64.05 | 50.02 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.11 | -0.145 | -0.145 | -1.45 | -0.73971 | -0.73971 | 0 | 12 | 1 | 1 | -0.73971 | 10 | 0 | 0
64.1 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
64.15 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
64.2 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
64.25 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
64.3 | 50.01 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
64.35 | 50.01 | 50 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.045 | -0.45 | -0.225 | -0.225 | 0 | 12 | 1 | 1 | -0.225 | 10 | 0 | 0
64.4 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
64.45 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
64.5 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
64.55 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
64.6 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.14706 | 0.14706 | 0 | 12 | 1 | 1 | 0.14706 | 10 | 0 | 0
64.65 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
64.7 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
64.75 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
64.8 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
64.85 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
64.9 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
64.95 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
65 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
65.05 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
65.1 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
65.15 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
65.2 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
65.25 | 50 | 50 | 0 | 0 | 0 | 50.01 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
65.3 | 49.5 | 49.5 | 1 | 1 | 10 | 50.01 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
65.35 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
65.4 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
65.45 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
65.5 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
65.55 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
65.6 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
65.65 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
65.7 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
65.75 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
65.8 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
65.85 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.1 | 1 | 5.5 | 5.5 | 0 | 12 | 1 | 1 | 5.5 | 10 | 0 | 0
65.9 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.2 | 2 | 6 | 6 | 0 | 12 | 1 | 1 | 6 | 10 | 0 | 0
65.95 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.3 | 3 | 6.5 | 6.5 | 0 | 12 | 1 | 1 | 6.5 | 10 | 0 | 0
66 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.4 | 4 | 7 | 7 | 0 | 12 | 1 | 1 | 7 | 10 | 0 | 0
66.05 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.5 | 5 | 7.5 | 7.5 | 0 | 12 | 1 | 1 | 7.5 | 10 | 0 | 0
66.1 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.6 | 6 | 8 | 8 | 0 | 12 | 1 | 1 | 8 | 10 | 0 | 0
66.15 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.7 | 7 | 8.5 | 8.5 | 0 | 12 | 1 | 1 | 8.5 | 10 | 0 | 0
66.2 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.8 | 8 | 9 | 9 | 0 | 12 | 1 | 1 | 9 | 10 | 0 | 0
66.25 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.9 | 9 | 9.5 | 9.5 | 0 | 12 | 1 | 1 | 9.5 | 10 | 0 | 0
66.3 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
66.35 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
66.4 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
66.45 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
66.5 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
66.55 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
66.6 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
66.65 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
66.7 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
66.75 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
66.8 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
66.85 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
66.9 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
66.95 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
67 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
67.05 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
67.1 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
67.15 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
67.2 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
67.25 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
67.3 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
67.35 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
67.4 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
67.45 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
67.5 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
67.55 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
67.6 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
67.65 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
67.7 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
67.75 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
67.8 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
67.85 | 50.5 | 50.5 | -1 | 0.9 | 9 | 50.5 | -1 | -1 | -10 | -0.5 | -0.5 | 0 | 12 | 1 | 1 | -0.5 | 10 | 0 | 0
67.9 | 50.5 | 50.5 | -1 | 0.8 | 8 | 50.5 | -1 | -1 | -10 | -1 | -1 | 0 | 12 | 1 | 1 | -1 | 10 | 0 | 0
67.95 | 50.5 | 50.5 | -1 | 0.7 | 7 | 50.5 | -1 | -1 | -10 | -1.5 | -1.5 | 0 | 12 | 1 | 1 | -1.5 | 10 | 0 | 0
68 | 50.5 | 50.5 | -1 | 0.6 | 6 | 50.5 | -1 | -1 | -10 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
68.05 | 50.5 | 50.5 | -1 | 0.5 | 5 | 50.5 | -1 | -1 | -10 | -2.5 | -2.5 | 0 | 12 | 1 | 1 | -2.5 | 10 | 0 | 0
68.1 | 50.5 | 50.5 | -1 | 0.4 | 4 | 50.5 | -1 | -1 | -10 | -3 | -3 | 0 | 12 | 1 | 1 | -3 | 10 | 0 | 0
68.15 | 50.5 | 50.5 | -1 | 0.3 | 3 | 50.5 | -1 | -1 | -10 | -3.5 | -3.5 | 0 | 12 | 1 | 1 | -3.5 | 10 | 0 | 0
68.2 | 50.5 | 50.5 | -1 | 0.2 | 2 | 50.5 | -1 | -1 | -10 | -4 | -4 | 0 | 12 | 1 | 1 | -4 | 10 | 0 | 0
68.25 | 50.5 | 50.5 | -1 | 0.1 | 1 | 50.5 | -1 | -1 | -10 | -4.5 | -4.5 | 0 | 12 | 1 | 1 | -4.5 | 10 | 0 | 0
68.3 | 50.5 | 50.5 | -1 | 0 | 0 | 50.5 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
68.35 | 50.5 | 50.5 | -1 | -0.1 | -1 | 50.5 | -1 | -1 | -10 | -5.5 | -5.5 | 0 | 12 | 1 | 1 | -5.5 | 10 | 0 | 0
68.4 | 50.5 | 50.5 | -1 | -0.2 | -2 | 50.5 | -1 | -1 | -10 | -6 | -6 | 0 | 12 | 1 | 1 | -6 | 10 | 0 | 0
68.45 | 50.5 | 50.5 | -1 | -0.3 | -3 | 50.5 | -1 | -1 | -10 | -6.5 | -6.5 | 0 | 12 | 1 | 1 | -6.5 | 10 | 0 | 0
68.5 | 50.5 | 50.5 | -1 | -0.4 | -4 | 50.5 | -1 | -1 | -10 | -7 | -7 | 0 | 12 | 1 | 1 | -7 | 10 | 0 | 0
68.55 | 50.5 | 50.5 | -1 | -0.5 | -5 | 50.5 | -1 | -1 | -10 | -7.5 | -7.5 | 0 | 12 | 1 | 1 | -7.5 | 10 | 0 | 0
68.6 | 50.5 | 50.5 | -1 | -0.6 | -6 | 50.5 | -1 | -1 | -10 | -8 | -8 | 0 | 12 | 1 | 1 | -8 | 10 | 0 | 0
68.65 | 50.5 | 50.5 | -1 | -0.7 | -7 | 50.5 | -1 | -1 | -10 | -8.5 | -8.5 | 0 | 12 | 1 | 1 | -8.5 | 10 | 0 | 0
68.7 | 50.5 | 50.5 | -1 | -0.8 | -8 | 50.5 | -1 | -1 | -10 | -9 | -9 | 0 | 12 | 1 | 1 | -9 | 10 | 0 | 0
68.75 | 50.5 | 50.5 | -1 | -0.9 | -9 | 50.5 | -1 | -1 | -10 | -9.5 | -9.5 | 0 | 12 | 1 | 1 | -9.5 | 10 | 0 | 0
68.8 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
68.85 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
68.9 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
68.95 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
69 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
69.05 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
69.1 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
69.15 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
69.2 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
69.25 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
69.3 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
69.35 | 50.47 | 50.47 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
69.4 | 50.45 | 50.45 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
69.45 | 50.42 | 50.42 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
69.5 | 50.4 | 50.4 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
69.55 | 50.37 | 50.37 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
69.6 | 50.35 | 50.35 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
69.65 | 50.32 | 50.32 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
69.7 | 50.29 | 50.29 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
69.75 | 50.27 | 50.27 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
69.8 | 50.24 | 50.24 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
69.85 | 50.22 | 50.22 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
69.9 | 50.19 | 50.19 | -0.905 | -0.905 | -9.05 | 50.47 | -1 | -1 | -10 | -9.525 | -9.525 | 0 | 12 | 1 | 1 | -9.525 | 10 | 0 | 0
69.95 | 50.17 | 50.17 | -0.715 | -0.715 | -7.15 | 50.45 | -1 | -1 | -10 | -8.575 | -8.575 | 0 | 12 | 1 | 1 | -8.575 | 10 | 0 | 0
70 | 50.14 | 50.14 | -0.43 | -0.43 | -4.3 | 50.42 | -1 | -1 | -10 | -7.15 | -7.15 | 0 | 12 | 1 | 1 | -7.15 | 10 | 0 | 0
70.05 | 50.12 | 50.12 | -0.24 | -0.24 | -2.4 | 50.4 | -1 | -1 | -10 | -6.2 | -6.2 | 0 | 12 | 1 | 1 | -6.2 | 10 | 0 | 0
70.1 | 50.09 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 50.37 | -1 | -1 | -10 | -5.2206 | -5.2206 | 0 | 12 | 1 | 1 | -5.2206 | 10 | 0 | 0
70.15 | 50.06 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.35 | -1 | -1 | -10 | -5.1324 | -5.1324 | 0 | 12 | 1 | 1 | -5.1324 | 10 | 0 | 0
70.2 | 50.04 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.32 | -1 | -1 | -10 | -5.0735 | -5.0735 | 0 | 12 | 1 | 1 | -5.0735 | 10 | 0 | 0
70.25 | 50.01 | 50.01 | 0 | 0 | 0 | 50.29 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
70.3 | 49.99 | 49.99 | 0 | 0 | 0 | 50.27 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
70.35 | 49.96 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.24 | -1 | -1 | -10 | -4.9265 | -4.9265 | 0 | 12 | 1 | 1 | -4.9265 | 10 | 0 | 0
70.4 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.22 | -1 | -1 | -10 | -4.8676 | -4.8676 | 0 | 12 | 1 | 1 | -4.8676 | 10 | 0 | 0
70.45 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.19 | -0.905 | -0.905 | -9.05 | -4.3044 | -4.3044 | 0 | 12 | 1 | 1 | -4.3044 | 10 | 0 | 0
70.5 | 49.88 | 49.88 | 0.24 | 0.24 | 2.4 | 50.17 | -0.715 | -0.805 | -8.05 | -2.825 | -2.825 | 0 | 12 | 1 | 1 | -2.825 | 10 | 0 | 0
70.55 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.14 | -0.43 | -0.705 | -7.05 | -1.375 | -1.375 | 0 | 12 | 1 | 1 | -1.375 | 10 | 0 | 0
70.6 | 49.83 | 49.83 | 0.715 | 0.715 | 7.15 | 50.12 | -0.24 | -0.605 | -6.05 | 0.55 | 0.55 | 0 | 12 | 1 | 1 | 0.55 | 10 | 0 | 0
70.65 | 49.81 | 49.81 | 0.905 | 0.905 | 9.05 | 50.09 | -0.044118 | -0.505 | -5.05 | 2 | 2 | 0 | 12 | 1 | 1 | 2 | 10 | 0 | 0
70.7 | 49.78 | 49.78 | 1 | 1 | 10 | 50.06 | -0.026471 | -0.405 | -4.05 | 2.975 | 2.975 | 0 | 12 | 1 | 1 | 2.975 | 10 | 0 | 0
70.75 | 49.76 | 49.76 | 1 | 1 | 10 | 50.04 | -0.014706 | -0.305 | -3.05 | 3.475 | 3.475 | 0 | 12 | 1 | 1 | 3.475 | 10 | 0 | 0
70.8 | 49.73 | 49.73 | 1 | 1 | 10 | 50.01 | 0 | -0.205 | -2.05 | 3.975 | 3.975 | 0 | 12 | 1 | 1 | 3.975 | 10 | 0 | 0
70.85 | 49.71 | 49.71 | 1 | 1 | 10 | 49.99 | 0 | -0.105 | -1.05 | 4.475 | 4.475 | 0 | 12 | 1 | 1 | 4.475 | 10 | 0 | 0
70.9 | 49.68 | 49.68 | 1 | 1 | 10 | 49.96 | 0.014706 | -0.005 | -0.05 | 4.975 | 4.975 | 0 | 12 | 1 | 1 | 4.975 | 10 | 0 | 0
70.95 | 49.65 | 49.65 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
71 | 49.63 | 49.63 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
71.05 | 49.6 | 49.6 | 1 | 1 | 10 | 49.88 | 0.24 | 0.14412 | 1.4412 | 5.7206 | 5.7206 | 0 | 12 | 1 | 1 | 5.7206 | 10 | 0 | 0
71.1 | 49.58 | 49.58 | 1 | 1 | 10 | 49.86 | 0.43 | 0.24412 | 2.4412 | 6.2206 | 6.2206 | 0 | 12 | 1 | 1 | 6.2206 | 10 | 0 | 0
71.15 | 49.55 | 49.55 | 1 | 1 | 10 | 49.83 | 0.715 | 0.34412 | 3.4412 | 6.7206 | 6.7206 | 0 | 12 | 1 | 1 | 6.7206 | 10 | 0 | 0
71.2 | 49.53 | 49.53 | 1 | 1 | 10 | 49.81 | 0.905 | 0.44412 | 4.4412 | 7.2206 | 7.2206 | 0 | 12 | 1 | 1 | 7.2206 | 10 | 0 | 0
71.25 | 49.5 | 49.5 | 1 | 1 | 10 | 49.78 | 1 | 0.54412 | 5.4412 | 7.7206 | 7.7206 | 0 | 12 | 1 | 1 | 7.7206 | 10 | 0 | 0
71.3 | 49.5 | 49.5 | 1 | 1 | 10 | 49.76 | 1 | 0.64412 | 6.4412 | 8.2206 | 8.2206 | 0 | 12 | 1 | 1 | 8.2206 | 10 | 0 | 0
71.35 | 49.53 | 49.5 | 1 | 1 | 10 | 49.73 | 1 | 0.74412 | 7.4412 | 8.7206 | 8.7206 | 0 | 12 | 1 | 1 | 8.7206 | 10 | 0 | 0
71.4 | 49.55 | 49.5 | 1 | 1 | 10 | 49.71 | 1 | 0.84412 | 8.4412 | 9.2206 | 9.2206 | 0 | 12 | 1 | 1 | 9.2206 | 10 | 0 | 0
71.45 | 49.58 | 49.5 | 1 | 1 | 10 | 49.68 | 1 | 0.94412 | 9.4412 | 9.7206 | 9.7206 | 0 | 12 | 1 | 1 | 9.7206 | 10 | 0 | 0
71.5 | 49.6 | 49.5 | 1 | 1 | 10 | 49.65 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
71.55 | 49.63 | 49.5 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
71.6 | 49.65 | 49.5 | 1 | 1 | 10 | 49.65 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
71.65 | 49.68 | 49.5 | 1 | 1 | 10 | 49.68 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
71.7 | 49.71 | 49.5 | 1 | 1 | 10 | 49.71 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
71.75 | 49.73 | 49.5 | 1 | 1 | 10 | 49.73 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
71.8 | 49.76 | 49.5 | 1 | 1 | 10 | 49.76 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
71.85 | 49.78 | 49.5 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
71.9 | 49.81 | 49.53 | 1 | 1 | 10 | 49.81 | 0.905 | 0.905 | 9.05 | 9.525 | 9.525 | 0 | 12 | 1 | 1 | 9.525 | 10 | 0 | 0
71.95 | 49.83 | 49.55 | 1 | 1 | 10 | 49.83 | 0.715 | 0.715 | 7.15 | 8.575 | 8.575 | 0 | 12 | 1 | 1 | 8.575 | 10 | 0 | 0
72 | 49.86 | 49.58 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
72.05 | 49.88 | 49.6 | 1 | 1 | 10 | 49.88 | 0.24 | 0.24 | 2.4 | 6.2 | 6.2 | 0 | 12 | 1 | 1 | 6.2 | 10 | 0 | 0
72.1 | 49.91 | 49.63 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
72.15 | 49.94 | 49.65 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
72.2 | 49.96 | 49.68 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
72.25 | 49.99 | 49.71 | 1 | 1 | 10 | 49.99 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
72.3 | 50.01 | 49.73 | 1 | 1 | 10 | 50.01 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
72.35 | 50.04 | 49.76 | 1 | 1 | 10 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 4.9265 | 4.9265 | 0 | 12 | 1 | 1 | 4.9265 | 10 | 0 | 0
72.4 | 50.06 | 49.78 | 1 | 1 | 10 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 4.8676 | 4.8676 | 0 | 12 | 1 | 1 | 4.8676 | 10 | 0 | 0
72.45 | 50.09 | 49.81 | 0.905 | 0.905 | 9.05 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 4.3044 | 4.3044 | 0 | 12 | 1 | 1 | 4.3044 | 10 | 0 | 0
72.5 | 50.12 | 49.83 | 0.715 | 0.805 | 8.05 | 50.12 | -0.24 | -0.24 | -2.4 | 2.825 | 2.825 | 0 | 12 | 1 | 1 | 2.825 | 10 | 0 | 0
72.55 | 50.14 | 49.86 | 0.43 | 0.705 | 7.05 | 50.14 | -0.43 | -0.43 | -4.3 | 1.375 | 1.375 | 0 | 12 | 1 | 1 | 1.375 | 10 | 0 | 0
72.6 | 50.17 | 49.88 | 0.24 | 0.605 | 6.05 | 50.17 | -0.715 | -0.715 | -7.15 | -0.55 | -0.55 | 0 | 12 | 1 | 1 | -0.55 | 10 | 0 | 0
72.65 | 50.19 | 49.91 | 0.044118 | 0.505 | 5.05 | 50.19 | -0.905 | -0.905 | -9.05 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
72.7 | 50.22 | 49.94 | 0.026471 | 0.405 | 4.05 | 50.22 | -1 | -1 | -10 | -2.975 | -2.975 | 0 | 12 | 1 | 1 | -2.975 | 10 | 0 | 0
72.75 | 50.24 | 49.96 | 0.014706 | 0.305 | 3.05 | 50.24 | -1 | -1 | -10 | -3.475 | -3.475 | 0 | 12 | 1 | 1 | -3.475 | 10 | 0 | 0
72.8 | 50.27 | 49.99 | 0 | 0.205 | 2.05 | 50.27 | -1 | -1 | -10 | -3.975 | -3.975 | 0 | 12 | 1 | 1 | -3.975 | 10 | 0 | 0
72.85 | 50.29 | 50.01 | 0 | 0.105 | 1.05 | 50.29 | -1 | -1 | -10 | -4.475 | -4.475 | 0 | 12 | 1 | 1 | -4.475 | 10 | 0 | 0
72.9 | 50.32 | 50.04 | -0.014706 | 0.005 | 0.05 | 50.32 | -1 | -1 | -10 | -4.975 | -4.975 | 0 | 12 | 1 | 1 | -4.975 | 10 | 0 | 0
72.95 | 50.35 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.35 | -1 | -1 | -10 | -5.1324 | -5.1324 | 0 | 12 | 1 | 1 | -5.1324 | 10 | 0 | 0
73 | 50.37 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 50.37 | -1 | -1 | -10 | -5.2206 | -5.2206 | 0 | 12 | 1 | 1 | -5.2206 | 10 | 0 | 0
73.05 | 50.4 | 50.12 | -0.24 | -0.14412 | -1.4412 | 50.4 | -1 | -1 | -10 | -5.7206 | -5.7206 | 0 | 12 | 1 | 1 | -5.7206 | 10 | 0 | 0
73.1 | 50.42 | 50.14 | -0.43 | -0.24412 | -2.4412 | 50.42 | -1 | -1 | -10 | -6.2206 | -6.2206 | 0 | 12 | 1 | 1 | -6.2206 | 10 | 0 | 0
73.15 | 50.45 | 50.17 | -0.715 | -0.34412 | -3.4412 | 50.45 | -1 | -1 | -10 | -6.7206 | -6.7206 | 0 | 12 | 1 | 1 | -6.7206 | 10 | 0 | 0
73.2 | 50.47 | 50.19 | -0.905 | -0.44412 | -4.4412 | 50.47 | -1 | -1 | -10 | -7.2206 | -7.2206 | 0 | 12 | 1 | 1 | -7.2206 | 10 | 0 | 0
73.25 | 50.5 | 50.22 | -1 | -0.54412 | -5.4412 | 50.5 | -1 | -1 | -10 | -7.7206 | -7.7206 | 0 | 12 | 1 | 1 | -7.7206 | 10 | 0 | 0
73.3 | 50.5 | 50.24 | -1 | -0.64412 | -6.4412 | 50.5 | -1 | -1 | -10 | -8.2206 | -8.2206 | 0 | 12 | 1 | 1 | -8.2206 | 10 | 0 | 0
73.35 | 50.47 | 50.27 | -1 | -0.74412 | -7.4412 | 50.5 | -1 | -1 | -10 | -8.7206 | -8.7206 | 0 | 12 | 1 | 1 | -8.7206 | 10 | 0 | 0
73.4 | 50.45 | 50.29 | -1 | -0.84412 | -8.4412 | 50.5 | -1 | -1 | -10 | -9.2206 | -9.2206 | 0 | 12 | 1 | 1 | -9.2206 | 10 | 0 | 0
73.45 | 50.42 | 50.32 | -1 | -0.94412 | -9.4412 | 50.5 | -1 | -1 | -10 | -9.7206 | -9.7206 | 0 | 12 | 1 | 1 | -9.7206 | 10 | 0 | 0
73.5 | 50.39 | 50.35 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
73.55 | 50.37 | 50.37 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
73.6 | 50.34 | 50.34 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
73.65 | 50.32 | 50.32 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
73.7 | 50.29 | 50.29 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
73.75 | 50.26 | 50.26 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
73.8 | 50.24 | 50.24 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
73.85 | 50.21 | 50.21 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
73.9 | 50.18 | 50.18 | -0.81 | -0.81 | -8.1 | 50.47 | -1 | -1 | -10 | -9.05 | -9.05 | 0 | 12 | 1 | 1 | -9.05 | 10 | 0 | 0
73.95 | 50.16 | 50.16 | -0.62 | -0.62 | -6.2 | 50.45 | -1 | -1 | -10 | -8.1 | -8.1 | 0 | 12 | 1 | 1 | -8.1 | 10 | 0 | 0
74 | 50.13 | 50.13 | -0.335 | -0.335 | -3.35 | 50.42 | -1 | -1 | -10 | -6.675 | -6.675 | 0 | 12 | 1 | 1 | -6.675 | 10 | 0 | 0
74.05 | 50.11 | 50.11 | -0.145 | -0.145 | -1.45 | 50.39 | -1 | -1 | -10 | -5.725 | -5.725 | 0 | 12 | 1 | 1 | -5.725 | 10 | 0 | 0
74.1 | 50.08 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 50.37 | -1 | -1 | -10 | -5.1912 | -5.1912 | 0 | 12 | 1 | 1 | -5.1912 | 10 | 0 | 0
74.15 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.34 | -1 | -1 | -10 | -5.1029 | -5.1029 | 0 | 12 | 1 | 1 | -5.1029 | 10 | 0 | 0
74.2 | 50.03 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 50.32 | -1 | -1 | -10 | -5.0441 | -5.0441 | 0 | 12 | 1 | 1 | -5.0441 | 10 | 0 | 0
74.25 | 50 | 50 | 0 | 0 | 0 | 50.29 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
74.3 | 50 | 50 | 0 | 0 | 0 | 50.26 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
74.35 | 50 | 50 | 0 | 0 | 0 | 50.24 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
74.4 | 50 | 50 | 0 | 0 | 0 | 50.21 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
74.45 | 50 | 50 | 0 | 0 | 0 | 50.18 | -0.81 | -0.9 | -9 | -4.5 | -4.5 | 0 | 12 | 1 | 1 | -4.5 | 10 | 0 | 0
74.5 | 50 | 50 | 0 | 0 | 0 | 50.16 | -0.62 | -0.8 | -8 | -4 | -4 | 0 | 12 | 1 | 1 | -4 | 10 | 0 | 0
74.55 | 50 | 50 | 0 | 0 | 0 | 50.13 | -0.335 | -0.7 | -7 | -3.5 | -3.5 | 0 | 12 | 1 | 1 | -3.5 | 10 | 0 | 0
74.6 | 50.01 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.6 | -6 | -3 | -3 | 0 | 12 | 1 | 1 | -3 | 10 | 0 | 0
74.65 | 50.01 | 50 | 0 | 0 | 0 | 50.08 | -0.038235 | -0.5 | -5 | -2.5 | -2.5 | 0 | 12 | 1 | 1 | -2.5 | 10 | 0 | 0
74.7 | 49.99 | 49.99 | 0 | 0 | 0 | 50.05 | -0.020588 | -0.4 | -4 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
74.75 | 49.99 | 49.99 | 0 | 0 | 0 | 50.03 | -0.0088235 | -0.3 | -3 | -1.5 | -1.5 | 0 | 12 | 1 | 1 | -1.5 | 10 | 0 | 0
74.8 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | -0.2 | -2 | -0.83824 | -0.83824 | 0 | 12 | 1 | 1 | -0.83824 | 10 | 0 | 0
74.85 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | -0.1 | -1 | -0.33824 | -0.33824 | 0 | 12 | 1 | 1 | -0.33824 | 10 | 0 | 0
74.9 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
74.95 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
75 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
75.05 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
75.1 | 49.89 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
75.15 | 49.89 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
75.2 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50.01 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
75.25 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
75.3 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
75.35 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 2.7868 | 2.7868 | 0 | 12 | 1 | 1 | 2.7868 | 10 | 0 | 0
75.4 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 2.7868 | 2.7868 | 0 | 12 | 1 | 1 | 2.7868 | 10 | 0 | 0
75.45 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 2.8456 | 2.8456 | 0 | 12 | 1 | 1 | 2.8456 | 10 | 0 | 0
75.5 | 49.94 | 49.85 | 0.525 | 0.525 | 5.25 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 2.7574 | 2.7574 | 0 | 12 | 1 | 1 | 2.7574 | 10 | 0 | 0
75.55 | 49.94 | 49.85 | 0.525 | 0.525 | 5.25 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 2.7574 | 2.7574 | 0 | 12 | 1 | 1 | 2.7574 | 10 | 0 | 0
75.6 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
75.65 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
75.7 | 49.93 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
75.75 | 49.93 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
75.8 | 49.96 | 49.85 | 0.525 | 0.525 | 5.25 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 2.6985 | 2.6985 | 0 | 12 | 1 | 1 | 2.6985 | 10 | 0 | 0
75.85 | 49.96 | 49.85 | 0.525 | 0.525 | 5.25 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 2.6985 | 2.6985 | 0 | 12 | 1 | 1 | 2.6985 | 10 | 0 | 0
75.9 | 49.99 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
75.95 | 49.99 | 49.91 | 0.044118 | 0.425 | 4.25 | 49.99 | 0 | 0 | 0 | 2.125 | 2.125 | 0 | 12 | 1 | 1 | 2.125 | 10 | 0 | 0
76 | 49.99 | 49.91 | 0.044118 | 0.325 | 3.25 | 49.99 | 0 | 0 | 0 | 1.625 | 1.625 | 0 | 12 | 1 | 1 | 1.625 | 10 | 0 | 0
76.05 | 49.99 | 49.93 | 0.032353 | 0.225 | 2.25 | 49.99 | 0 | 0 | 0 | 1.125 | 1.125 | 0 | 12 | 1 | 1 | 1.125 | 10 | 0 | 0
76.1 | 49.96 | 49.93 | 0.032353 | 0.125 | 1.25 | 49.99 | 0 | 0 | 0 | 0.625 | 0.625 | 0 | 12 | 1 | 1 | 0.625 | 10 | 0 | 0
76.15 | 49.96 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 49.99 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
76.2 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
76.25 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
76.3 | 50.05 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.058824 | 0.058824 | 0 | 12 | 1 | 1 | 0.058824 | 10 | 0 | 0
76.35 | 50.05 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
76.4 | 49.97 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
76.45 | 49.97 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
76.5 | 49.92 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
76.55 | 49.92 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
76.6 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
76.65 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
76.7 | 49.94 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
76.75 | 49.94 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
76.8 | 50.01 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
76.85 | 50.01 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
76.9 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
76.95 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
77 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
77.05 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
77.1 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
77.15 | 49.95 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
77.2 | 49.97 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
77.25 | 49.97 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
77.3 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
77.35 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
77.4 | 49.87 | 49.87 | 0.335 | 0.335 | 3.35 | 50.01 | 0 | 0 | 0 | 1.675 | 1.675 | 0 | 12 | 1 | 1 | 1.675 | 10 | 0 | 0
77.45 | 49.87 | 49.87 | 0.335 | 0.335 | 3.35 | 49.99 | 0 | 0 | 0 | 1.675 | 1.675 | 0 | 12 | 1 | 1 | 1.675 | 10 | 0 | 0
77.5 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
77.55 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 2.6691 | 2.6691 | 0 | 12 | 1 | 1 | 2.6691 | 10 | 0 | 0
77.6 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
77.65 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
77.7 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
77.75 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
77.8 | 49.84 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
77.85 | 49.84 | 49.79 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
77.9 | 49.89 | 49.79 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
77.95 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.12647 | 1.2647 | 5.6324 | 5.6324 | 0 | 12 | 1 | 1 | 5.6324 | 10 | 0 | 0
78 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.145 | 1.45 | 5.725 | 5.725 | 0 | 12 | 1 | 1 | 5.725 | 10 | 0 | 0
78.05 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.145 | 1.45 | 5.725 | 5.725 | 0 | 12 | 1 | 1 | 5.725 | 10 | 0 | 0
78.1 | 49.96 | 49.79 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
78.15 | 49.96 | 49.79 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
78.2 | 50.02 | 49.79 | 1 | 1 | 10 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 4.9853 | 4.9853 | 0 | 12 | 1 | 1 | 4.9853 | 10 | 0 | 0
78.25 | 50.02 | 49.79 | 1 | 1 | 10 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 4.9853 | 4.9853 | 0 | 12 | 1 | 1 | 4.9853 | 10 | 0 | 0
78.3 | 50.03 | 49.79 | 1 | 1 | 10 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.9559 | 4.9559 | 0 | 12 | 1 | 1 | 4.9559 | 10 | 0 | 0
78.35 | 50.03 | 49.84 | 0.62 | 0.9 | 9 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.4559 | 4.4559 | 0 | 12 | 1 | 1 | 4.4559 | 10 | 0 | 0
78.4 | 50.02 | 49.84 | 0.62 | 0.8 | 8 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 3.9559 | 3.9559 | 0 | 12 | 1 | 1 | 3.9559 | 10 | 0 | 0
78.45 | 50.02 | 49.89 | 0.145 | 0.7 | 7 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 3.4559 | 3.4559 | 0 | 12 | 1 | 1 | 3.4559 | 10 | 0 | 0
78.5 | 50.08 | 49.89 | 0.145 | 0.6 | 6 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 2.8088 | 2.8088 | 0 | 12 | 1 | 1 | 2.8088 | 10 | 0 | 0
78.55 | 50.08 | 49.89 | 0.145 | 0.5 | 5 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 2.3088 | 2.3088 | 0 | 12 | 1 | 1 | 2.3088 | 10 | 0 | 0
78.6 | 50.01 | 49.89 | 0.145 | 0.4 | 4 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 1.8088 | 1.8088 | 0 | 12 | 1 | 1 | 1.8088 | 10 | 0 | 0
78.65 | 50.01 | 49.96 | 0.014706 | 0.3 | 3 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 1.3088 | 1.3088 | 0 | 12 | 1 | 1 | 1.3088 | 10 | 0 | 0
78.7 | 49.94 | 49.94 | 0.026471 | 0.2 | 2 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.80882 | 0.80882 | 0 | 12 | 1 | 1 | 0.80882 | 10 | 0 | 0
78.75 | 49.94 | 49.94 | 0.026471 | 0.1 | 1 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.30882 | 0.30882 | 0 | 12 | 1 | 1 | 0.30882 | 10 | 0 | 0
78.8 | 50 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
78.85 | 50 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
78.9 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
78.95 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
79 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
79.05 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
79.1 | 49.92 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
79.15 | 49.92 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
79.2 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50.01 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
79.25 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
79.3 | 49.92 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
79.35 | 49.92 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
79.4 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
79.45 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
79.5 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
79.55 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
79.6 | 49.87 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
79.65 | 49.87 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
79.7 | 49.8 | 49.8 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
79.75 | 49.8 | 49.8 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
79.8 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
79.85 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
79.9 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
79.95 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
80 | 49.72 | 49.72 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
80.05 | 49.72 | 49.72 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
80.1 | 49.67 | 49.67 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
80.15 | 49.67 | 49.67 | 1 | 1 | 10 | 49.87 | 0.335 | 0.14412 | 1.4412 | 5.7206 | 5.7206 | 0 | 12 | 1 | 1 | 5.7206 | 10 | 0 | 0
80.2 | 49.65 | 49.65 | 1 | 1 | 10 | 49.87 | 0.335 | 0.24412 | 2.4412 | 6.2206 | 6.2206 | 0 | 12 | 1 | 1 | 6.2206 | 10 | 0 | 0
80.25 | 49.65 | 49.65 | 1 | 1 | 10 | 49.8 | 1 | 0.34412 | 3.4412 | 6.7206 | 6.7206 | 0 | 12 | 1 | 1 | 6.7206 | 10 | 0 | 0
80.3 | 49.59 | 49.59 | 1 | 1 | 10 | 49.8 | 1 | 0.44412 | 4.4412 | 7.2206 | 7.2206 | 0 | 12 | 1 | 1 | 7.2206 | 10 | 0 | 0
80.35 | 49.59 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.54412 | 5.4412 | 7.7206 | 7.7206 | 0 | 12 | 1 | 1 | 7.7206 | 10 | 0 | 0
80.4 | 49.66 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.64412 | 6.4412 | 8.2206 | 8.2206 | 0 | 12 | 1 | 1 | 8.2206 | 10 | 0 | 0
80.45 | 49.66 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.74412 | 7.4412 | 8.7206 | 8.7206 | 0 | 12 | 1 | 1 | 8.7206 | 10 | 0 | 0
80.5 | 49.63 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.84412 | 8.4412 | 9.2206 | 9.2206 | 0 | 12 | 1 | 1 | 9.2206 | 10 | 0 | 0
80.55 | 49.63 | 49.59 | 1 | 1 | 10 | 49.72 | 1 | 0.94412 | 9.4412 | 9.7206 | 9.7206 | 0 | 12 | 1 | 1 | 9.7206 | 10 | 0 | 0
80.6 | 49.61 | 49.59 | 1 | 1 | 10 | 49.72 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
80.65 | 49.61 | 49.59 | 1 | 1 | 10 | 49.67 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
80.7 | 49.54 | 49.54 | 1 | 1 | 10 | 49.67 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
80.75 | 49.54 | 49.54 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
80.8 | 49.46 | 49.46 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
80.85 | 49.46 | 49.46 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
80.9 | 49.45 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
80.95 | 49.45 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
81 | 49.51 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
81.05 | 49.51 | 49.45 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
81.1 | 49.5 | 49.45 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
81.15 | 49.5 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
81.2 | 49.54 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
81.25 | 49.54 | 49.45 | 1 | 1 | 10 | 49.54 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
81.3 | 49.59 | 49.45 | 1 | 1 | 10 | 49.59 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
81.35 | 49.59 | 49.45 | 1 | 1 | 10 | 49.59 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
81.4 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
81.45 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
81.5 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
81.55 | 49.61 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
81.6 | 49.53 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
81.65 | 49.53 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
81.7 | 49.54 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
81.75 | 49.54 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
81.8 | 49.61 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
81.85 | 49.61 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
81.9 | 49.66 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
81.95 | 49.66 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
82 | 49.64 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
82.05 | 49.64 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
82.1 | 49.69 | 49.53 | 1 | 1 | 10 | 49.69 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
82.15 | 49.69 | 49.53 | 1 | 1 | 10 | 49.69 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
82.2 | 49.74 | 49.53 | 1 | 1 | 10 | 49.74 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
82.25 | 49.74 | 49.54 | 1 | 1 | 10 | 49.74 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
82.3 | 49.78 | 49.54 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
82.35 | 49.78 | 49.61 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
82.4 | 49.82 | 49.61 | 1 | 1 | 10 | 49.82 | 0.81 | 0.81 | 8.1 | 9.05 | 9.05 | 0 | 12 | 1 | 1 | 9.05 | 10 | 0 | 0
82.45 | 49.82 | 49.64 | 1 | 1 | 10 | 49.82 | 0.81 | 0.81 | 8.1 | 9.05 | 9.05 | 0 | 12 | 1 | 1 | 9.05 | 10 | 0 | 0
82.5 | 49.86 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
82.55 | 49.86 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
82.6 | 49.84 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
82.65 | 49.84 | 49.69 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
82.7 | 49.91 | 49.69 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
82.75 | 49.91 | 49.74 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
82.8 | 49.97 | 49.74 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
82.85 | 49.97 | 49.78 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
82.9 | 50.03 | 49.78 | 1 | 1 | 10 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.9559 | 4.9559 | 0 | 12 | 1 | 1 | 4.9559 | 10 | 0 | 0
82.95 | 50.03 | 49.82 | 0.81 | 0.9 | 9 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.4559 | 4.4559 | 0 | 12 | 1 | 1 | 4.4559 | 10 | 0 | 0
83 | 50.05 | 49.82 | 0.81 | 0.81 | 8.1 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 3.9471 | 3.9471 | 0 | 12 | 1 | 1 | 3.9471 | 10 | 0 | 0
83.05 | 50.05 | 49.84 | 0.62 | 0.71 | 7.1 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 3.4471 | 3.4471 | 0 | 12 | 1 | 1 | 3.4471 | 10 | 0 | 0
83.1 | 50.01 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
83.15 | 50.01 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
83.2 | 49.95 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
83.25 | 49.95 | 49.91 | 0.044118 | 0.52 | 5.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.4971 | 2.4971 | 0 | 12 | 1 | 1 | 2.4971 | 10 | 0 | 0
83.3 | 49.99 | 49.91 | 0.044118 | 0.42 | 4.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 1.9971 | 1.9971 | 0 | 12 | 1 | 1 | 1.9971 | 10 | 0 | 0
83.35 | 49.99 | 49.95 | 0.020588 | 0.32 | 3.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 1.4971 | 1.4971 | 0 | 12 | 1 | 1 | 1.4971 | 10 | 0 | 0
83.4 | 49.92 | 49.92 | 0.038235 | 0.22 | 2.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.99706 | 0.99706 | 0 | 12 | 1 | 1 | 0.99706 | 10 | 0 | 0
83.45 | 49.92 | 49.92 | 0.038235 | 0.12 | 1.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.49706 | 0.49706 | 0 | 12 | 1 | 1 | 0.49706 | 10 | 0 | 0
83.5 | 49.97 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
83.55 | 49.97 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
83.6 | 50.02 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
83.65 | 50.02 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.17647 | 0.17647 | 0 | 12 | 1 | 1 | 0.17647 | 10 | 0 | 0
83.7 | 50.07 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
83.75 | 50.07 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
83.8 | 50.06 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
83.85 | 50.06 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
83.9 | 50.13 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
83.95 | 50.13 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
84 | 50.09 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
84.05 | 50.09 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6309 | -1.6309 | 0 | 12 | 1 | 1 | -1.6309 | 10 | 0 | 0
84.1 | 50.07 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6309 | -1.6309 | 0 | 12 | 1 | 1 | -1.6309 | 10 | 0 | 0
84.15 | 50.07 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6897 | -1.6897 | 0 | 12 | 1 | 1 | -1.6897 | 10 | 0 | 0
84.2 | 50.07 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6897 | -1.6897 | 0 | 12 | 1 | 1 | -1.6897 | 10 | 0 | 0
84.25 | 50.07 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.13 | -0.335 | -0.335 | -3.35 | -1.8074 | -1.8074 | 0 | 12 | 1 | 1 | -1.8074 | 10 | 0 | 0
84.3 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.13 | -0.335 | -0.335 | -3.35 | -1.7779 | -1.7779 | 0 | 12 | 1 | 1 | -1.7779 | 10 | 0 | 0
84.35 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.13 | -0.335 | -0.335 | -3.35 | -1.7779 | -1.7779 | 0 | 12 | 1 | 1 | -1.7779 | 10 | 0 | 0
84.4 | 50.01 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
84.45 | 50.01 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
84.5 | 50.07 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
84.55 | 50.07 | 50.01 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.235 | -2.35 | -1.175 | -1.175 | 0 | 12 | 1 | 1 | -1.175 | 10 | 0 | 0
84.6 | 50.05 | 50.01 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.135 | -1.35 | -0.675 | -0.675 | 0 | 12 | 1 | 1 | -0.675 | 10 | 0 | 0
84.65 | 50.05 | 50.01 | 0 | 0 | 0 | 50.07 | -0.032353 | -0.035 | -0.35 | -0.175 | -0.175 | 0 | 12 | 1 | 1 | -0.175 | 10 | 0 | 0
84.7 | 50.1 | 50.01 | 0 | 0 | 0 | 50.1 | -0.05 | -0.05 | -0.5 | -0.25 | -0.25 | 0 | 12 | 1 | 1 | -0.25 | 10 | 0 | 0
84.75 | 50.1 | 50.01 | 0 | 0 | 0 | 50.1 | -0.05 | -0.05 | -0.5 | -0.25 | -0.25 | 0 | 12 | 1 | 1 | -0.25 | 10 | 0 | 0
84.8 | 50.11 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
84.85 | 50.11 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
84.9 | 50.06 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
84.95 | 50.06 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
85 | 50.04 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
85.05 | 50.04 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
85.1 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
85.15 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
85.2 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
85.25 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
85.3 | 50.11 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
85.35 | 50.11 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
85.4 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
85.45 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
85.5 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
85.55 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
85.6 | 50.02 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.11 | -0.145 | -0.145 | -1.45 | -0.73971 | -0.73971 | 0 | 12 | 1 | 1 | -0.73971 | 10 | 0 | 0
85.65 | 50.02 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.11 | -0.145 | -0.145 | -1.45 | -0.73971 | -0.73971 | 0 | 12 | 1 | 1 | -0.73971 | 10 | 0 | 0
85.7 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
85.75 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
85.8 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
85.85 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
85.9 | 50.01 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
85.95 | 50.01 | 50 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.045 | -0.45 | -0.225 | -0.225 | 0 | 12 | 1 | 1 | -0.225 | 10 | 0 | 0
86 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
86.05 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
86.1 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
86.15 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
86.2 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.14706 | 0.14706 | 0 | 12 | 1 | 1 | 0.14706 | 10 | 0 | 0
86.25 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
86.3 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
86.35 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
86.4 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
86.45 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
86.5 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
86.55 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
86.6 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
86.65 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
86.7 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
86.75 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
86.8 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
86.85 | 50 | 50 | 0 | 0 | 0 | 50.01 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
86.9 | 49.5 | 49.5 | 1 | 1 | 10 | 50.01 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
86.95 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
87 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
87.05 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
87.1 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
87.15 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
87.2 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
87.25 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
87.3 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
87.35 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
87.4 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
87.45 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.1 | 1 | 5.5 | 5.5 | 0 | 12 | 1 | 1 | 5.5 | 10 | 0 | 0
87.5 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.2 | 2 | 6 | 6 | 0 | 12 | 1 | 1 | 6 | 10 | 0 | 0
87.55 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.3 | 3 | 6.5 | 6.5 | 0 | 12 | 1 | 1 | 6.5 | 10 | 0 | 0
87.6 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.4 | 4 | 7 | 7 | 0 | 12 | 1 | 1 | 7 | 10 | 0 | 0
87.65 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.5 | 5 | 7.5 | 7.5 | 0 | 12 | 1 | 1 | 7.5 | 10 | 0 | 0
87.7 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.6 | 6 | 8 | 8 | 0 | 12 | 1 | 1 | 8 | 10 | 0 | 0
87.75 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.7 | 7 | 8.5 | 8.5 | 0 | 12 | 1 | 1 | 8.5 | 10 | 0 | 0
87.8 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.8 | 8 | 9 | 9 | 0 | 12 | 1 | 1 | 9 | 10 | 0 | 0
87.85 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.9 | 9 | 9.5 | 9.5 | 0 | 12 | 1 | 1 | 9.5 | 10 | 0 | 0
87.9 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
87.95 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
88 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
88.05 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
88.1 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
88.15 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
88.2 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
88.25 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
88.3 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
88.35 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
88.4 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
88.45 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
88.5 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
88.55 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
88.6 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
88.65 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
88.7 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
88.75 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
88.8 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
88.85 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
88.9 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
88.95 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
89 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
89.05 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
89.1 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
89.15 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
89.2 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
89.25 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
89.3 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
89.35 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
89.4 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
89.45 | 50.5 | 50.5 | -1 | 0.9 | 9 | 50.5 | -1 | -1 | -10 | -0.5 | -0.5 | 0 | 12 | 1 | 1 | -0.5 | 10 | 0 | 0
89.5 | 50.5 | 50.5 | -1 | 0.8 | 8 | 50.5 | -1 | -1 | -10 | -1 | -1 | 0 | 12 | 1 | 1 | -1 | 10 | 0 | 0
89.55 | 50.5 | 50.5 | -1 | 0.7 | 7 | 50.5 | -1 | -1 | -10 | -1.5 | -1.5 | 0 | 12 | 1 | 1 | -1.5 | 10 | 0 | 0
89.6 | 50.5 | 50.5 | -1 | 0.6 | 6 | 50.5 | -1 | -1 | -10 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
89.65 | 50.5 | 50.5 | -1 | 0.5 | 5 | 50.5 | -1 | -1 | -10 | -2.5 | -2.5 | 0 | 12 | 1 | 1 | -2.5 | 10 | 0 | 0
89.7 | 50.5 | 50.5 | -1 | 0.4 | 4 | 50.5 | -1 | -1 | -10 | -3 | -3 | 0 | 12 | 1 | 1 | -3 | 10 | 0 | 0
89.75 | 50.5 | 50.5 | -1 | 0.3 | 3 | 50.5 | -1 | -1 | -10 | -3.5 | -3.5 | 0 | 12 | 1 | 1 | -3.5 | 10 | 0 | 0
89.8 | 50.5 | 50.5 | -1 | 0.2 | 2 | 50.5 | -1 | -1 | -10 | -4 | -4 | 0 | 12 | 1 | 1 | -4 | 10 | 0 | 0
89.85 | 50.5 | 50.5 | -1 | 0.1 | 1 | 50.5 | -1 | -1 | -10 | -4.5 | -4.5 | 0 | 12 | 1 | 1 | -4.5 | 10 | 0 | 0
89.9 | 50.5 | 50.5 | -1 | 0 | 0 | 50.5 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
89.95 | 50.5 | 50.5 | -1 | -0.1 | -1 | 50.5 | -1 | -1 | -10 | -5.5 | -5.5 | 0 | 12 | 1 | 1 | -5.5 | 10 | 0 | 0
90 | 50.5 | 50.5 | -1 | -0.2 | -2 | 50.5 | -1 | -1 | -10 | -6 | -6 | 0 | 12 | 1 | 1 | -6 | 10 | 0 | 0
90.05 | 50.5 | 50.5 | -1 | -0.3 | -3 | 50.5 | -1 | -1 | -10 | -6.5 | -6.5 | 0 | 12 | 1 | 1 | -6.5 | 10 | 0 | 0
90.1 | 50.5 | 50.5 | -1 | -0.4 | -4 | 50.5 | -1 | -1 | -10 | -7 | -7 | 0 | 12 | 1 | 1 | -7 | 10 | 0 | 0
90.15 | 50.5 | 50.5 | -1 | -0.5 | -5 | 50.5 | -1 | -1 | -10 | -7.5 | -7.5 | 0 | 12 | 1 | 1 | -7.5 | 10 | 0 | 0
90.2 | 50.5 | 50.5 | -1 | -0.6 | -6 | 50.5 | -1 | -1 | -10 | -8 | -8 | 0 | 12 | 1 | 1 | -8 | 10 | 0 | 0
90.25 | 50.5 | 50.5 | -1 | -0.7 | -7 | 50.5 | -1 | -1 | -10 | -8.5 | -8.5 | 0 | 12 | 1 | 1 | -8.5 | 10 | 0 | 0
90.3 | 50.5 | 50.5 | -1 | -0.8 | -8 | 50.5 | -1 | -1 | -10 | -9 | -9 | 0 | 12 | 1 | 1 | -9 | 10 | 0 | 0
90.35 | 50.5 | 50.5 | -1 | -0.9 | -9 | 50.5 | -1 | -1 | -10 | -9.5 | -9.5 | 0 | 12 | 1 | 1 | -9.5 | 10 | 0 | 0
90.4 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
90.45 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
90.5 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
90.55 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
90.6 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
90.65 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
90.7 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
90.75 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
90.8 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
90.85 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
90.9 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
90.95 | 50.47 | 50.47 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
91 | 50.45 | 50.45 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
91.05 | 50.42 | 50.42 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
91.1 | 50.4 | 50.4 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
91.15 | 50.37 | 50.37 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
91.2 | 50.35 | 50.35 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
91.25 | 50.32 | 50.32 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
91.3 | 50.29 | 50.29 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
91.35 | 50.27 | 50.27 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
91.4 | 50.24 | 50.24 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
91.45 | 50.22 | 50.22 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
91.5 | 50.19 | 50.19 | -0.905 | -0.905 | -9.05 | 50.47 | -1 | -1 | -10 | -9.525 | -9.525 | 0 | 12 | 1 | 1 | -9.525 | 10 | 0 | 0
91.55 | 50.17 | 50.17 | -0.715 | -0.715 | -7.15 | 50.45 | -1 | -1 | -10 | -8.575 | -8.575 | 0 | 12 | 1 | 1 | -8.575 | 10 | 0 | 0
91.6 | 50.14 | 50.14 | -0.43 | -0.43 | -4.3 | 50.42 | -1 | -1 | -10 | -7.15 | -7.15 | 0 | 12 | 1 | 1 | -7.15 | 10 | 0 | 0
91.65 | 50.12 | 50.12 | -0.24 | -0.24 | -2.4 | 50.4 | -1 | -1 | -10 | -6.2 | -6.2 | 0 | 12 | 1 | 1 | -6.2 | 10 | 0 | 0
91.7 | 50.09 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 50.37 | -1 | -1 | -10 | -5.2206 | -5.2206 | 0 | 12 | 1 | 1 | -5.2206 | 10 | 0 | 0
91.75 | 50.06 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.35 | -1 | -1 | -10 | -5.1324 | -5.1324 | 0 | 12 | 1 | 1 | -5.1324 | 10 | 0 | 0
91.8 | 50.04 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.32 | -1 | -1 | -10 | -5.0735 | -5.0735 | 0 | 12 | 1 | 1 | -5.0735 | 10 | 0 | 0
91.85 | 50.01 | 50.01 | 0 | 0 | 0 | 50.29 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
91.9 | 49.99 | 49.99 | 0 | 0 | 0 | 50.27 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
91.95 | 49.96 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.24 | -1 | -1 | -10 | -4.9265 | -4.9265 | 0 | 12 | 1 | 1 | -4.9265 | 10 | 0 | 0
92 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.22 | -1 | -1 | -10 | -4.8676 | -4.8676 | 0 | 12 | 1 | 1 | -4.8676 | 10 | 0 | 0
92.05 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.19 | -0.905 | -0.905 | -9.05 | -4.3044 | -4.3044 | 0 | 12 | 1 | 1 | -4.3044 | 10 | 0 | 0
92.1 | 49.88 | 49.88 | 0.24 | 0.24 | 2.4 | 50.17 | -0.715 | -0.805 | -8.05 | -2.825 | -2.825 | 0 | 12 | 1 | 1 | -2.825 | 10 | 0 | 0
92.15 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.14 | -0.43 | -0.705 | -7.05 | -1.375 | -1.375 | 0 | 12 | 1 | 1 | -1.375 | 10 | 0 | 0
92.2 | 49.83 | 49.83 | 0.715 | 0.715 | 7.15 | 50.12 | -0.24 | -0.605 | -6.05 | 0.55 | 0.55 | 0 | 12 | 1 | 1 | 0.55 | 10 | 0 | 0
92.25 | 49.81 | 49.81 | 0.905 | 0.905 | 9.05 | 50.09 | -0.044118 | -0.505 | -5.05 | 2 | 2 | 0 | 12 | 1 | 1 | 2 | 10 | 0 | 0
92.3 | 49.78 | 49.78 | 1 | 1 | 10 | 50.06 | -0.026471 | -0.405 | -4.05 | 2.975 | 2.975 | 0 | 12 | 1 | 1 | 2.975 | 10 | 0 | 0
92.35 | 49.76 | 49.76 | 1 | 1 | 10 | 50.04 | -0.014706 | -0.305 | -3.05 | 3.475 | 3.475 | 0 | 12 | 1 | 1 | 3.475 | 10 | 0 | 0
92.4 | 49.73 | 49.73 | 1 | 1 | 10 | 50.01 | 0 | -0.205 | -2.05 | 3.975 | 3.975 | 0 | 12 | 1 | 1 | 3.975 | 10 | 0 | 0
92.45 | 49.71 | 49.71 | 1 | 1 | 10 | 49.99 | 0 | -0.105 | -1.05 | 4.475 | 4.475 | 0 | 12 | 1 | 1 | 4.475 | 10 | 0 | 0
92.5 | 49.68 | 49.68 | 1 | 1 | 10 | 49.96 | 0.014706 | -0.005 | -0.05 | 4.975 | 4.975 | 0 | 12 | 1 | 1 | 4.975 | 10 | 0 | 0
92.55 | 49.65 | 49.65 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
92.6 | 49.63 | 49.63 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
92.65 | 49.6 | 49.6 | 1 | 1 | 10 | 49.88 | 0.24 | 0.14412 | 1.4412 | 5.7206 | 5.7206 | 0 | 12 | 1 | 1 | 5.7206 | 10 | 0 | 0
92.7 | 49.58 | 49.58 | 1 | 1 | 10 | 49.86 | 0.43 | 0.24412 | 2.4412 | 6.2206 | 6.2206 | 0 | 12 | 1 | 1 | 6.2206 | 10 | 0 | 0
92.75 | 49.55 | 49.55 | 1 | 1 | 10 | 49.83 | 0.715 | 0.34412 | 3.4412 | 6.7206 | 6.7206 | 0 | 12 | 1 | 1 | 6.7206 | 10 | 0 | 0
92.8 | 49.53 | 49.53 | 1 | 1 | 10 | 49.81 | 0.905 | 0.44412 | 4.4412 | 7.2206 | 7.2206 | 0 | 12 | 1 | 1 | 7.2206 | 10 | 0 | 0
92.85 | 49.5 | 49.5 | 1 | 1 | 10 | 49.78 | 1 | 0.54412 | 5.4412 | 7.7206 | 7.7206 | 0 | 12 | 1 | 1 | 7.7206 | 10 | 0 | 0
92.9 | 49.5 | 49.5 | 1 | 1 | 10 | 49.76 | 1 | 0.64412 | 6.4412 | 8.2206 | 8.2206 | 0 | 12 | 1 | 1 | 8.2206 | 10 | 0 | 0
92.95 | 49.53 | 49.5 | 1 | 1 | 10 | 49.73 | 1 | 0.74412 | 7.4412 | 8.7206 | 8.7206 | 0 | 12 | 1 | 1 | 8.7206 | 10 | 0 | 0
93 | 49.55 | 49.5 | 1 | 1 | 10 | 49.71 | 1 | 0.84412 | 8.4412 | 9.2206 | 9.2206 | 0 | 12 | 1 | 1 | 9.2206 | 10 | 0 | 0
93.05 | 49.58 | 49.5 | 1 | 1 | 10 | 49.68 | 1 | 0.94412 | 9.4412 | 9.7206 | 9.7206 | 0 | 12 | 1 | 1 | 9.7206 | 10 | 0 | 0
93.1 | 49.6 | 49.5 | 1 | 1 | 10 | 49.65 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
93.15 | 49.63 | 49.5 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
93.2 | 49.65 | 49.5 | 1 | 1 | 10 | 49.65 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
93.25 | 49.68 | 49.5 | 1 | 1 | 10 | 49.68 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
93.3 | 49.71 | 49.5 | 1 | 1 | 10 | 49.71 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
93.35 | 49.73 | 49.5 | 1 | 1 | 10 | 49.73 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
93.4 | 49.76 | 49.5 | 1 | 1 | 10 | 49.76 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
93.45 | 49.78 | 49.5 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
93.5 | 49.81 | 49.53 | 1 | 1 | 10 | 49.81 | 0.905 | 0.905 | 9.05 | 9.525 | 9.525 | 0 | 12 | 1 | 1 | 9.525 | 10 | 0 | 0
93.55 | 49.83 | 49.55 | 1 | 1 | 10 | 49.83 | 0.715 | 0.715 | 7.15 | 8.575 | 8.575 | 0 | 12 | 1 | 1 | 8.575 | 10 | 0 | 0
93.6 | 49.86 | 49.58 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
93.65 | 49.88 | 49.6 | 1 | 1 | 10 | 49.88 | 0.24 | 0.24 | 2.4 | 6.2 | 6.2 | 0 | 12 | 1 | 1 | 6.2 | 10 | 0 | 0
93.7 | 49.91 | 49.63 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
93.75 | 49.94 | 49.65 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
93.8 | 49.96 | 49.68 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
93.85 | 49.99 | 49.71 | 1 | 1 | 10 | 49.99 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
93.9 | 50.01 | 49.73 | 1 | 1 | 10 | 50.01 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
93.95 | 50.04 | 49.76 | 1 | 1 | 10 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 4.9265 | 4.9265 | 0 | 12 | 1 | 1 | 4.9265 | 10 | 0 | 0
94 | 50.06 | 49.78 | 1 | 1 | 10 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 4.8676 | 4.8676 | 0 | 12 | 1 | 1 | 4.8676 | 10 | 0 | 0
94.05 | 50.09 | 49.81 | 0.905 | 0.905 | 9.05 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 4.3044 | 4.3044 | 0 | 12 | 1 | 1 | 4.3044 | 10 | 0 | 0
94.1 | 50.12 | 49.83 | 0.715 | 0.805 | 8.05 | 50.12 | -0.24 | -0.24 | -2.4 | 2.825 | 2.825 | 0 | 12 | 1 | 1 | 2.825 | 10 | 0 | 0
94.15 | 50.14 | 49.86 | 0.43 | 0.705 | 7.05 | 50.14 | -0.43 | -0.43 | -4.3 | 1.375 | 1.375 | 0 | 12 | 1 | 1 | 1.375 | 10 | 0 | 0
94.2 | 50.17 | 49.88 | 0.24 | 0.605 | 6.05 | 50.17 | -0.715 | -0.715 | -7.15 | -0.55 | -0.55 | 0 | 12 | 1 | 1 | -0.55 | 10 | 0 | 0
94.25 | 50.19 | 49.91 | 0.044118 | 0.505 | 5.05 | 50.19 | -0.905 | -0.905 | -9.05 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
94.3 | 50.22 | 49.94 | 0.026471 | 0.405 | 4.05 | 50.22 | -1 | -1 | -10 | -2.975 | -2.975 | 0 | 12 | 1 | 1 | -2.975 | 10 | 0 | 0
94.35 | 50.24 | 49.96 | 0.014706 | 0.305 | 3.05 | 50.24 | -1 | -1 | -10 | -3.475 | -3.475 | 0 | 12 | 1 | 1 | -3.475 | 10 | 0 | 0
94.4 | 50.27 | 49.99 | 0 | 0.205 | 2.05 | 50.27 | -1 | -1 | -10 | -3.975 | -3.975 | 0 | 12 | 1 | 1 | -3.975 | 10 | 0 | 0
94.45 | 50.29 | 50.01 | 0 | 0.105 | 1.05 | 50.29 | -1 | -1 | -10 | -4.475 | -4.475 | 0 | 12 | 1 | 1 | -4.475 | 10 | 0 | 0
94.5 | 50.32 | 50.04 | -0.014706 | 0.005 | 0.05 | 50.32 | -1 | -1 | -10 | -4.975 | -4.975 | 0 | 12 | 1 | 1 | -4.975 | 10 | 0 | 0
94.55 | 50.35 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.35 | -1 | -1 | -10 | -5.1324 | -5.1324 | 0 | 12 | 1 | 1 | -5.1324 | 10 | 0 | 0
94.6 | 50.37 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 50.37 | -1 | -1 | -10 | -5.2206 | -5.2206 | 0 | 12 | 1 | 1 | -5.2206 | 10 | 0 | 0
94.65 | 50.4 | 50.12 | -0.24 | -0.14412 | -1.4412 | 50.4 | -1 | -1 | -10 | -5.7206 | -5.7206 | 0 | 12 | 1 | 1 | -5.7206 | 10 | 0 | 0
94.7 | 50.42 | 50.14 | -0.43 | -0.24412 | -2.4412 | 50.42 | -1 | -1 | -10 | -6.2206 | -6.2206 | 0 | 12 | 1 | 1 | -6.2206 | 10 | 0 | 0
94.75 | 50.45 | 50.17 | -0.715 | -0.34412 | -3.4412 | 50.45 | -1 | -1 | -10 | -6.7206 | -6.7206 | 0 | 12 | 1 | 1 | -6.7206 | 10 | 0 | 0
94.8 | 50.47 | 50.19 | -0.905 | -0.44412 | -4.4412 | 50.47 | -1 | -1 | -10 | -7.2206 | -7.2206 | 0 | 12 | 1 | 1 | -7.2206 | 10 | 0 | 0
94.85 | 50.5 | 50.22 | -1 | -0.54412 | -5.4412 | 50.5 | -1 | -1 | -10 | -7.7206 | -7.7206 | 0 | 12 | 1 | 1 | -7.7206 | 10 | 0 | 0
94.9 | 50.5 | 50.24 | -1 | -0.64412 | -6.4412 | 50.5 | -1 | -1 | -10 | -8.2206 | -8.2206 | 0 | 12 | 1 | 1 | -8.2206 | 10 | 0 | 0
94.95 | 50.47 | 50.27 | -1 | -0.74412 | -7.4412 | 50.5 | -1 | -1 | -10 | -8.7206 | -8.7206 | 0 | 12 | 1 | 1 | -8.7206 | 10 | 0 | 0
95 | 50.45 | 50.29 | -1 | -0.84412 | -8.4412 | 50.5 | -1 | -1 | -10 | -9.2206 | -9.2206 | 0 | 12 | 1 | 1 | -9.2206 | 10 | 0 | 0
95.05 | 50.42 | 50.32 | -1 | -0.94412 | -9.4412 | 50.5 | -1 | -1 | -10 | -9.7206 | -9.7206 | 0 | 12 | 1 | 1 | -9.7206 | 10 | 0 | 0
95.1 | 50.39 | 50.35 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
95.15 | 50.37 | 50.37 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
95.2 | 50.34 | 50.34 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
95.25 | 50.32 | 50.32 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
95.3 | 50.29 | 50.29 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
95.35 | 50.26 | 50.26 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
95.4 | 50.24 | 50.24 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
95.45 | 50.21 | 50.21 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
95.5 | 50.18 | 50.18 | -0.81 | -0.81 | -8.1 | 50.47 | -1 | -1 | -10 | -9.05 | -9.05 | 0 | 12 | 1 | 1 | -9.05 | 10 | 0 | 0
95.55 | 50.16 | 50.16 | -0.62 | -0.62 | -6.2 | 50.45 | -1 | -1 | -10 | -8.1 | -8.1 | 0 | 12 | 1 | 1 | -8.1 | 10 | 0 | 0
95.6 | 50.13 | 50.13 | -0.335 | -0.335 | -3.35 | 50.42 | -1 | -1 | -10 | -6.675 | -6.675 | 0 | 12 | 1 | 1 | -6.675 | 10 | 0 | 0
95.65 | 50.11 | 50.11 | -0.145 | -0.145 | -1.45 | 50.39 | -1 | -1 | -10 | -5.725 | -5.725 | 0 | 12 | 1 | 1 | -5.725 | 10 | 0 | 0
95.7 | 50.08 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 50.37 | -1 | -1 | -10 | -5.1912 | -5.1912 | 0 | 12 | 1 | 1 | -5.1912 | 10 | 0 | 0
95.75 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.34 | -1 | -1 | -10 | -5.1029 | -5.1029 | 0 | 12 | 1 | 1 | -5.1029 | 10 | 0 | 0
95.8 | 50.03 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 50.32 | -1 | -1 | -10 | -5.0441 | -5.0441 | 0 | 12 | 1 | 1 | -5.0441 | 10 | 0 | 0
95.85 | 50 | 50 | 0 | 0 | 0 | 50.29 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
95.9 | 50 | 50 | 0 | 0 | 0 | 50.26 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
95.95 | 50 | 50 | 0 | 0 | 0 | 50.24 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
96 | 50 | 50 | 0 | 0 | 0 | 50.21 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
96.05 | 50 | 50 | 0 | 0 | 0 | 50.18 | -0.81 | -0.9 | -9 | -4.5 | -4.5 | 0 | 12 | 1 | 1 | -4.5 | 10 | 0 | 0
96.1 | 50 | 50 | 0 | 0 | 0 | 50.16 | -0.62 | -0.8 | -8 | -4 | -4 | 0 | 12 | 1 | 1 | -4 | 10 | 0 | 0
96.15 | 50 | 50 | 0 | 0 | 0 | 50.13 | -0.335 | -0.7 | -7 | -3.5 | -3.5 | 0 | 12 | 1 | 1 | -3.5 | 10 | 0 | 0
96.2 | 50.01 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.6 | -6 | -3 | -3 | 0 | 12 | 1 | 1 | -3 | 10 | 0 | 0
96.25 | 50.01 | 50 | 0 | 0 | 0 | 50.08 | -0.038235 | -0.5 | -5 | -2.5 | -2.5 | 0 | 12 | 1 | 1 | -2.5 | 10 | 0 | 0
96.3 | 49.99 | 49.99 | 0 | 0 | 0 | 50.05 | -0.020588 | -0.4 | -4 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
96.35 | 49.99 | 49.99 | 0 | 0 | 0 | 50.03 | -0.0088235 | -0.3 | -3 | -1.5 | -1.5 | 0 | 12 | 1 | 1 | -1.5 | 10 | 0 | 0
96.4 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | -0.2 | -2 | -0.83824 | -0.83824 | 0 | 12 | 1 | 1 | -0.83824 | 10 | 0 | 0
96.45 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | -0.1 | -1 | -0.33824 | -0.33824 | 0 | 12 | 1 | 1 | -0.33824 | 10 | 0 | 0
96.5 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
96.55 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
96.6 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
96.65 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
96.7 | 49.89 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
96.75 | 49.89 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
96.8 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50.01 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
96.85 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
96.9 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
96.95 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 2.7868 | 2.7868 | 0 | 12 | 1 | 1 | 2.7868 | 10 | 0 | 0
97 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 2.7868 | 2.7868 | 0 | 12 | 1 | 1 | 2.7868 | 10 | 0 | 0
97.05 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 2.8456 | 2.8456 | 0 | 12 | 1 | 1 | 2.8456 | 10 | 0 | 0
97.1 | 49.94 | 49.85 | 0.525 | 0.525 | 5.25 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 2.7574 | 2.7574 | 0 | 12 | 1 | 1 | 2.7574 | 10 | 0 | 0
97.15 | 49.94 | 49.85 | 0.525 | 0.525 | 5.25 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 2.7574 | 2.7574 | 0 | 12 | 1 | 1 | 2.7574 | 10 | 0 | 0
97.2 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
97.25 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
97.3 | 49.93 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
97.35 | 49.93 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
97.4 | 49.96 | 49.85 | 0.525 | 0.525 | 5.25 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 2.6985 | 2.6985 | 0 | 12 | 1 | 1 | 2.6985 | 10 | 0 | 0
97.45 | 49.96 | 49.85 | 0.525 | 0.525 | 5.25 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 2.6985 | 2.6985 | 0 | 12 | 1 | 1 | 2.6985 | 10 | 0 | 0
97.5 | 49.99 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
97.55 | 49.99 | 49.91 | 0.044118 | 0.425 | 4.25 | 49.99 | 0 | 0 | 0 | 2.125 | 2.125 | 0 | 12 | 1 | 1 | 2.125 | 10 | 0 | 0
97.6 | 49.99 | 49.91 | 0.044118 | 0.325 | 3.25 | 49.99 | 0 | 0 | 0 | 1.625 | 1.625 | 0 | 12 | 1 | 1 | 1.625 | 10 | 0 | 0
97.65 | 49.99 | 49.93 | 0.032353 | 0.225 | 2.25 | 49.99 | 0 | 0 | 0 | 1.125 | 1.125 | 0 | 12 | 1 | 1 | 1.125 | 10 | 0 | 0
97.7 | 49.96 | 49.93 | 0.032353 | 0.125 | 1.25 | 49.99 | 0 | 0 | 0 | 0.625 | 0.625 | 0 | 12 | 1 | 1 | 0.625 | 10 | 0 | 0
97.75 | 49.96 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 49.99 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
97.8 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
97.85 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
97.9 | 50.05 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.058824 | 0.058824 | 0 | 12 | 1 | 1 | 0.058824 | 10 | 0 | 0
97.95 | 50.05 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
98 | 49.97 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
98.05 | 49.97 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
98.1 | 49.92 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
98.15 | 49.92 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
98.2 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
98.25 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
98.3 | 49.94 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
98.35 | 49.94 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
98.4 | 50.01 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
98.45 | 50.01 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
98.5 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
98.55 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
98.6 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
98.65 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
98.7 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
98.75 | 49.95 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
98.8 | 49.97 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
98.85 | 49.97 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
98.9 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
98.95 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
99 | 49.87 | 49.87 | 0.335 | 0.335 | 3.35 | 50.01 | 0 | 0 | 0 | 1.675 | 1.675 | 0 | 12 | 1 | 1 | 1.675 | 10 | 0 | 0
99.05 | 49.87 | 49.87 | 0.335 | 0.335 | 3.35 | 49.99 | 0 | 0 | 0 | 1.675 | 1.675 | 0 | 12 | 1 | 1 | 1.675 | 10 | 0 | 0
99.1 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
99.15 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 2.6691 | 2.6691 | 0 | 12 | 1 | 1 | 2.6691 | 10 | 0 | 0
99.2 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
99.25 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
99.3 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
99.35 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
99.4 | 49.84 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
99.45 | 49.84 | 49.79 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
99.5 | 49.89 | 49.79 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
99.55 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.12647 | 1.2647 | 5.6324 | 5.6324 | 0 | 12 | 1 | 1 | 5.6324 | 10 | 0 | 0
99.6 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.145 | 1.45 | 5.725 | 5.725 | 0 | 12 | 1 | 1 | 5.725 | 10 | 0 | 0
99.65 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.145 | 1.45 | 5.725 | 5.725 | 0 | 12 | 1 | 1 | 5.725 | 10 | 0 | 0
99.7 | 49.96 | 49.79 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
99.75 | 49.96 | 49.79 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
99.8 | 50.02 | 49.79 | 1 | 1 | 10 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 4.9853 | 4.9853 | 0 | 12 | 1 | 1 | 4.9853 | 10 | 0 | 0
99.85 | 50.02 | 49.79 | 1 | 1 | 10 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 4.9853 | 4.9853 | 0 | 12 | 1 | 1 | 4.9853 | 10 | 0 | 0
99.9 | 50.03 | 49.79 | 1 | 1 | 10 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.9559 | 4.9559 | 0 | 12 | 1 | 1 | 4.9559 | 10 | 0 | 0
99.95 | 50.03 | 49.84 | 0.62 | 0.9 | 9 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.4559 | 4.4559 | 0 | 12 | 1 | 1 | 4.4559 | 10 | 0 | 0
100 | 50.02 | 49.84 | 0.62 | 0.8 | 8 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 3.9559 | 3.9559 | 0 | 12 | 1 | 1 | 3.9559 | 10 | 0 | 0
100.05 | 50.02 | 49.89 | 0.145 | 0.7 | 7 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 3.4559 | 3.4559 | 0 | 12 | 1 | 1 | 3.4559 | 10 | 0 | 0
100.1 | 50.08 | 49.89 | 0.145 | 0.6 | 6 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 2.8088 | 2.8088 | 0 | 12 | 1 | 1 | 2.8088 | 10 | 0 | 0
100.15 | 50.08 | 49.89 | 0.145 | 0.5 | 5 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 2.3088 | 2.3088 | 0 | 12 | 1 | 1 | 2.3088 | 10 | 0 | 0
100.2 | 50.01 | 49.89 | 0.145 | 0.4 | 4 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 1.8088 | 1.8088 | 0 | 12 | 1 | 1 | 1.8088 | 10 | 0 | 0
100.25 | 50.01 | 49.96 | 0.014706 | 0.3 | 3 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 1.3088 | 1.3088 | 0 | 12 | 1 | 1 | 1.3088 | 10 | 0 | 0
100.3 | 49.94 | 49.94 | 0.026471 | 0.2 | 2 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.80882 | 0.80882 | 0 | 12 | 1 | 1 | 0.80882 | 10 | 0 | 0
100.35 | 49.94 | 49.94 | 0.026471 | 0.1 | 1 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.30882 | 0.30882 | 0 | 12 | 1 | 1 | 0.30882 | 10 | 0 | 0
100.4 | 50 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
100.45 | 50 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
100.5 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
100.55 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
100.6 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
100.65 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
100.7 | 49.92 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
100.75 | 49.92 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
100.8 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50.01 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
100.85 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
100.9 | 49.92 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
100.95 | 49.92 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
101 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
101.05 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
101.1 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
101.15 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
101.2 | 49.87 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
101.25 | 49.87 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
101.3 | 49.8 | 49.8 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
101.35 | 49.8 | 49.8 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
101.4 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
101.45 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
101.5 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
101.55 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
101.6 | 49.72 | 49.72 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
101.65 | 49.72 | 49.72 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
101.7 | 49.67 | 49.67 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
101.75 | 49.67 | 49.67 | 1 | 1 | 10 | 49.87 | 0.335 | 0.14412 | 1.4412 | 5.7206 | 5.7206 | 0 | 12 | 1 | 1 | 5.7206 | 10 | 0 | 0
101.8 | 49.65 | 49.65 | 1 | 1 | 10 | 49.87 | 0.335 | 0.24412 | 2.4412 | 6.2206 | 6.2206 | 0 | 12 | 1 | 1 | 6.2206 | 10 | 0 | 0
101.85 | 49.65 | 49.65 | 1 | 1 | 10 | 49.8 | 1 | 0.34412 | 3.4412 | 6.7206 | 6.7206 | 0 | 12 | 1 | 1 | 6.7206 | 10 | 0 | 0
101.9 | 49.59 | 49.59 | 1 | 1 | 10 | 49.8 | 1 | 0.44412 | 4.4412 | 7.2206 | 7.2206 | 0 | 12 | 1 | 1 | 7.2206 | 10 | 0 | 0
101.95 | 49.59 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.54412 | 5.4412 | 7.7206 | 7.7206 | 0 | 12 | 1 | 1 | 7.7206 | 10 | 0 | 0
102 | 49.66 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.64412 | 6.4412 | 8.2206 | 8.2206 | 0 | 12 | 1 | 1 | 8.2206 | 10 | 0 | 0
102.05 | 49.66 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.74412 | 7.4412 | 8.7206 | 8.7206 | 0 | 12 | 1 | 1 | 8.7206 | 10 | 0 | 0
102.1 | 49.63 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.84412 | 8.4412 | 9.2206 | 9.2206 | 0 | 12 | 1 | 1 | 9.2206 | 10 | 0 | 0
102.15 | 49.63 | 49.59 | 1 | 1 | 10 | 49.72 | 1 | 0.94412 | 9.4412 | 9.7206 | 9.7206 | 0 | 12 | 1 | 1 | 9.7206 | 10 | 0 | 0
102.2 | 49.61 | 49.59 | 1 | 1 | 10 | 49.72 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
102.25 | 49.61 | 49.59 | 1 | 1 | 10 | 49.67 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
102.3 | 49.54 | 49.54 | 1 | 1 | 10 | 49.67 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
102.35 | 49.54 | 49.54 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
102.4 | 49.46 | 49.46 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
102.45 | 49.46 | 49.46 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
102.5 | 49.45 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
102.55 | 49.45 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
102.6 | 49.51 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
102.65 | 49.51 | 49.45 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
102.7 | 49.5 | 49.45 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
102.75 | 49.5 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
102.8 | 49.54 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
102.85 | 49.54 | 49.45 | 1 | 1 | 10 | 49.54 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
102.9 | 49.59 | 49.45 | 1 | 1 | 10 | 49.59 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
102.95 | 49.59 | 49.45 | 1 | 1 | 10 | 49.59 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
103 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
103.05 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
103.1 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
103.15 | 49.61 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
103.2 | 49.53 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
103.25 | 49.53 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
103.3 | 49.54 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
103.35 | 49.54 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
103.4 | 49.61 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
103.45 | 49.61 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
103.5 | 49.66 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
103.55 | 49.66 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
103.6 | 49.64 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
103.65 | 49.64 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
103.7 | 49.69 | 49.53 | 1 | 1 | 10 | 49.69 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
103.75 | 49.69 | 49.53 | 1 | 1 | 10 | 49.69 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
103.8 | 49.74 | 49.53 | 1 | 1 | 10 | 49.74 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
103.85 | 49.74 | 49.54 | 1 | 1 | 10 | 49.74 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
103.9 | 49.78 | 49.54 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
103.95 | 49.78 | 49.61 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
104 | 49.82 | 49.61 | 1 | 1 | 10 | 49.82 | 0.81 | 0.81 | 8.1 | 9.05 | 9.05 | 0 | 12 | 1 | 1 | 9.05 | 10 | 0 | 0
104.05 | 49.82 | 49.64 | 1 | 1 | 10 | 49.82 | 0.81 | 0.81 | 8.1 | 9.05 | 9.05 | 0 | 12 | 1 | 1 | 9.05 | 10 | 0 | 0
104.1 | 49.86 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
104.15 | 49.86 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
104.2 | 49.84 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
104.25 | 49.84 | 49.69 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
104.3 | 49.91 | 49.69 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
104.35 | 49.91 | 49.74 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
104.4 | 49.97 | 49.74 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
104.45 | 49.97 | 49.78 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
104.5 | 50.03 | 49.78 | 1 | 1 | 10 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.9559 | 4.9559 | 0 | 12 | 1 | 1 | 4.9559 | 10 | 0 | 0
104.55 | 50.03 | 49.82 | 0.81 | 0.9 | 9 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.4559 | 4.4559 | 0 | 12 | 1 | 1 | 4.4559 | 10 | 0 | 0
104.6 | 50.05 | 49.82 | 0.81 | 0.81 | 8.1 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 3.9471 | 3.9471 | 0 | 12 | 1 | 1 | 3.9471 | 10 | 0 | 0
104.65 | 50.05 | 49.84 | 0.62 | 0.71 | 7.1 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 3.4471 | 3.4471 | 0 | 12 | 1 | 1 | 3.4471 | 10 | 0 | 0
104.7 | 50.01 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
104.75 | 50.01 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
104.8 | 49.95 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
104.85 | 49.95 | 49.91 | 0.044118 | 0.52 | 5.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.4971 | 2.4971 | 0 | 12 | 1 | 1 | 2.4971 | 10 | 0 | 0
104.9 | 49.99 | 49.91 | 0.044118 | 0.42 | 4.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 1.9971 | 1.9971 | 0 | 12 | 1 | 1 | 1.9971 | 10 | 0 | 0
104.95 | 49.99 | 49.95 | 0.020588 | 0.32 | 3.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 1.4971 | 1.4971 | 0 | 12 | 1 | 1 | 1.4971 | 10 | 0 | 0
105 | 49.92 | 49.92 | 0.038235 | 0.22 | 2.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.99706 | 0.99706 | 0 | 12 | 1 | 1 | 0.99706 | 10 | 0 | 0
105.05 | 49.92 | 49.92 | 0.038235 | 0.12 | 1.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.49706 | 0.49706 | 0 | 12 | 1 | 1 | 0.49706 | 10 | 0 | 0
105.1 | 49.97 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
105.15 | 49.97 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
105.2 | 50.02 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
105.25 | 50.02 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.17647 | 0.17647 | 0 | 12 | 1 | 1 | 0.17647 | 10 | 0 | 0
105.3 | 50.07 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
105.35 | 50.07 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
105.4 | 50.06 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
105.45 | 50.06 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
105.5 | 50.13 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
105.55 | 50.13 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
105.6 | 50.09 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
105.65 | 50.09 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6309 | -1.6309 | 0 | 12 | 1 | 1 | -1.6309 | 10 | 0 | 0
105.7 | 50.07 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6309 | -1.6309 | 0 | 12 | 1 | 1 | -1.6309 | 10 | 0 | 0
105.75 | 50.07 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6897 | -1.6897 | 0 | 12 | 1 | 1 | -1.6897 | 10 | 0 | 0
105.8 | 50.07 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6897 | -1.6897 | 0 | 12 | 1 | 1 | -1.6897 | 10 | 0 | 0
105.85 | 50.07 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.13 | -0.335 | -0.335 | -3.35 | -1.8074 | -1.8074 | 0 | 12 | 1 | 1 | -1.8074 | 10 | 0 | 0
105.9 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.13 | -0.335 | -0.335 | -3.35 | -1.7779 | -1.7779 | 0 | 12 | 1 | 1 | -1.7779 | 10 | 0 | 0
105.95 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.13 | -0.335 | -0.335 | -3.35 | -1.7779 | -1.7779 | 0 | 12 | 1 | 1 | -1.7779 | 10 | 0 | 0
106 | 50.01 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
106.05 | 50.01 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
106.1 | 50.07 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
106.15 | 50.07 | 50.01 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.235 | -2.35 | -1.175 | -1.175 | 0 | 12 | 1 | 1 | -1.175 | 10 | 0 | 0
106.2 | 50.05 | 50.01 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.135 | -1.35 | -0.675 | -0.675 | 0 | 12 | 1 | 1 | -0.675 | 10 | 0 | 0
106.25 | 50.05 | 50.01 | 0 | 0 | 0 | 50.07 | -0.032353 | -0.035 | -0.35 | -0.175 | -0.175 | 0 | 12 | 1 | 1 | -0.175 | 10 | 0 | 0
106.3 | 50.1 | 50.01 | 0 | 0 | 0 | 50.1 | -0.05 | -0.05 | -0.5 | -0.25 | -0.25 | 0 | 12 | 1 | 1 | -0.25 | 10 | 0 | 0
106.35 | 50.1 | 50.01 | 0 | 0 | 0 | 50.1 | -0.05 | -0.05 | -0.5 | -0.25 | -0.25 | 0 | 12 | 1 | 1 | -0.25 | 10 | 0 | 0
106.4 | 50.11 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
106.45 | 50.11 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
106.5 | 50.06 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
106.55 | 50.06 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
106.6 | 50.04 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
106.65 | 50.04 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
106.7 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
106.75 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
106.8 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
106.85 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
106.9 | 50.11 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
106.95 | 50.11 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
107 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
107.05 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
107.1 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
107.15 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
107.2 | 50.02 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.11 | -0.145 | -0.145 | -1.45 | -0.73971 | -0.73971 | 0 | 12 | 1 | 1 | -0.73971 | 10 | 0 | 0
107.25 | 50.02 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.11 | -0.145 | -0.145 | -1.45 | -0.73971 | -0.73971 | 0 | 12 | 1 | 1 | -0.73971 | 10 | 0 | 0
107.3 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
107.35 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
107.4 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
107.45 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
107.5 | 50.01 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
107.55 | 50.01 | 50 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.045 | -0.45 | -0.225 | -0.225 | 0 | 12 | 1 | 1 | -0.225 | 10 | 0 | 0
107.6 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
107.65 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
107.7 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
107.75 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
107.8 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.14706 | 0.14706 | 0 | 12 | 1 | 1 | 0.14706 | 10 | 0 | 0
107.85 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
107.9 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
107.95 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
108 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
108.05 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
108.1 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
108.15 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
108.2 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
108.25 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
108.3 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
108.35 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
108.4 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
108.45 | 50 | 50 | 0 | 0 | 0 | 50.01 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
108.5 | 49.5 | 49.5 | 1 | 1 | 10 | 50.01 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
108.55 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
108.6 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
108.65 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
108.7 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
108.75 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
108.8 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
108.85 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
108.9 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
108.95 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
109 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
109.05 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.1 | 1 | 5.5 | 5.5 | 0 | 12 | 1 | 1 | 5.5 | 10 | 0 | 0
109.1 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.2 | 2 | 6 | 6 | 0 | 12 | 1 | 1 | 6 | 10 | 0 | 0
109.15 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.3 | 3 | 6.5 | 6.5 | 0 | 12 | 1 | 1 | 6.5 | 10 | 0 | 0
109.2 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.4 | 4 | 7 | 7 | 0 | 12 | 1 | 1 | 7 | 10 | 0 | 0
109.25 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.5 | 5 | 7.5 | 7.5 | 0 | 12 | 1 | 1 | 7.5 | 10 | 0 | 0
109.3 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.6 | 6 | 8 | 8 | 0 | 12 | 1 | 1 | 8 | 10 | 0 | 0
109.35 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.7 | 7 | 8.5 | 8.5 | 0 | 12 | 1 | 1 | 8.5 | 10 | 0 | 0
109.4 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.8 | 8 | 9 | 9 | 0 | 12 | 1 | 1 | 9 | 10 | 0 | 0
109.45 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.9 | 9 | 9.5 | 9.5 | 0 | 12 | 1 | 1 | 9.5 | 10 | 0 | 0
109.5 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
109.55 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
109.6 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
109.65 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
109.7 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
109.75 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
109.8 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
109.85 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
109.9 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
109.95 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
110 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
110.05 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
110.1 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
110.15 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
110.2 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
110.25 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
110.3 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
110.35 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
110.4 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
110.45 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
110.5 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
110.55 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
110.6 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
110.65 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
110.7 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
110.75 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
110.8 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
110.85 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
110.9 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
110.95 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
111 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
111.05 | 50.5 | 50.5 | -1 | 0.9 | 9 | 50.5 | -1 | -1 | -10 | -0.5 | -0.5 | 0 | 12 | 1 | 1 | -0.5 | 10 | 0 | 0
111.1 | 50.5 | 50.5 | -1 | 0.8 | 8 | 50.5 | -1 | -1 | -10 | -1 | -1 | 0 | 12 | 1 | 1 | -1 | 10 | 0 | 0
111.15 | 50.5 | 50.5 | -1 | 0.7 | 7 | 50.5 | -1 | -1 | -10 | -1.5 | -1.5 | 0 | 12 | 1 | 1 | -1.5 | 10 | 0 | 0
111.2 | 50.5 | 50.5 | -1 | 0.6 | 6 | 50.5 | -1 | -1 | -10 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
111.25 | 50.5 | 50.5 | -1 | 0.5 | 5 | 50.5 | -1 | -1 | -10 | -2.5 | -2.5 | 0 | 12 | 1 | 1 | -2.5 | 10 | 0 | 0
111.3 | 50.5 | 50.5 | -1 | 0.4 | 4 | 50.5 | -1 | -1 | -10 | -3 | -3 | 0 | 12 | 1 | 1 | -3 | 10 | 0 | 0
111.35 | 50.5 | 50.5 | -1 | 0.3 | 3 | 50.5 | -1 | -1 | -10 | -3.5 | -3.5 | 0 | 12 | 1 | 1 | -3.5 | 10 | 0 | 0
111.4 | 50.5 | 50.5 | -1 | 0.2 | 2 | 50.5 | -1 | -1 | -10 | -4 | -4 | 0 | 12 | 1 | 1 | -4 | 10 | 0 | 0
111.45 | 50.5 | 50.5 | -1 | 0.1 | 1 | 50.5 | -1 | -1 | -10 | -4.5 | -4.5 | 0 | 12 | 1 | 1 | -4.5 | 10 | 0 | 0
111.5 | 50.5 | 50.5 | -1 | 0 | 0 | 50.5 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
111.55 | 50.5 | 50.5 | -1 | -0.1 | -1 | 50.5 | -1 | -1 | -10 | -5.5 | -5.5 | 0 | 12 | 1 | 1 | -5.5 | 10 | 0 | 0
111.6 | 50.5 | 50.5 | -1 | -0.2 | -2 | 50.5 | -1 | -1 | -10 | -6 | -6 | 0 | 12 | 1 | 1 | -6 | 10 | 0 | 0
111.65 | 50.5 | 50.5 | -1 | -0.3 | -3 | 50.5 | -1 | -1 | -10 | -6.5 | -6.5 | 0 | 12 | 1 | 1 | -6.5 | 10 | 0 | 0
111.7 | 50.5 | 50.5 | -1 | -0.4 | -4 | 50.5 | -1 | -1 | -10 | -7 | -7 | 0 | 12 | 1 | 1 | -7 | 10 | 0 | 0
111.75 | 50.5 | 50.5 | -1 | -0.5 | -5 | 50.5 | -1 | -1 | -10 | -7.5 | -7.5 | 0 | 12 | 1 | 1 | -7.5 | 10 | 0 | 0
111.8 | 50.5 | 50.5 | -1 | -0.6 | -6 | 50.5 | -1 | -1 | -10 | -8 | -8 | 0 | 12 | 1 | 1 | -8 | 10 | 0 | 0
111.85 | 50.5 | 50.5 | -1 | -0.7 | -7 | 50.5 | -1 | -1 | -10 | -8.5 | -8.5 | 0 | 12 | 1 | 1 | -8.5 | 10 | 0 | 0
111.9 | 50.5 | 50.5 | -1 | -0.8 | -8 | 50.5 | -1 | -1 | -10 | -9 | -9 | 0 | 12 | 1 | 1 | -9 | 10 | 0 | 0
111.95 | 50.5 | 50.5 | -1 | -0.9 | -9 | 50.5 | -1 | -1 | -10 | -9.5 | -9.5 | 0 | 12 | 1 | 1 | -9.5 | 10 | 0 | 0
112 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
112.05 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
112.1 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
112.15 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
112.2 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
112.25 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
112.3 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
112.35 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
112.4 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
112.45 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
112.5 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
112.55 | 50.47 | 50.47 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
112.6 | 50.45 | 50.45 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
112.65 | 50.42 | 50.42 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
112.7 | 50.4 | 50.4 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
112.75 | 50.37 | 50.37 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
112.8 | 50.35 | 50.35 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
112.85 | 50.32 | 50.32 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
112.9 | 50.29 | 50.29 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
112.95 | 50.27 | 50.27 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
113 | 50.24 | 50.24 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
113.05 | 50.22 | 50.22 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
113.1 | 50.19 | 50.19 | -0.905 | -0.905 | -9.05 | 50.47 | -1 | -1 | -10 | -9.525 | -9.525 | 0 | 12 | 1 | 1 | -9.525 | 10 | 0 | 0
113.15 | 50.17 | 50.17 | -0.715 | -0.715 | -7.15 | 50.45 | -1 | -1 | -10 | -8.575 | -8.575 | 0 | 12 | 1 | 1 | -8.575 | 10 | 0 | 0
113.2 | 50.14 | 50.14 | -0.43 | -0.43 | -4.3 | 50.42 | -1 | -1 | -10 | -7.15 | -7.15 | 0 | 12 | 1 | 1 | -7.15 | 10 | 0 | 0
113.25 | 50.12 | 50.12 | -0.24 | -0.24 | -2.4 | 50.4 | -1 | -1 | -10 | -6.2 | -6.2 | 0 | 12 | 1 | 1 | -6.2 | 10 | 0 | 0
113.3 | 50.09 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 50.37 | -1 | -1 | -10 | -5.2206 | -5.2206 | 0 | 12 | 1 | 1 | -5.2206 | 10 | 0 | 0
113.35 | 50.06 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.35 | -1 | -1 | -10 | -5.1324 | -5.1324 | 0 | 12 | 1 | 1 | -5.1324 | 10 | 0 | 0
113.4 | 50.04 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.32 | -1 | -1 | -10 | -5.0735 | -5.0735 | 0 | 12 | 1 | 1 | -5.0735 | 10 | 0 | 0
113.45 | 50.01 | 50.01 | 0 | 0 | 0 | 50.29 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
113.5 | 49.99 | 49.99 | 0 | 0 | 0 | 50.27 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
113.55 | 49.96 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.24 | -1 | -1 | -10 | -4.9265 | -4.9265 | 0 | 12 | 1 | 1 | -4.9265 | 10 | 0 | 0
113.6 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.22 | -1 | -1 | -10 | -4.8676 | -4.8676 | 0 | 12 | 1 | 1 | -4.8676 | 10 | 0 | 0
113.65 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.19 | -0.905 | -0.905 | -9.05 | -4.3044 | -4.3044 | 0 | 12 | 1 | 1 | -4.3044 | 10 | 0 | 0
113.7 | 49.88 | 49.88 | 0.24 | 0.24 | 2.4 | 50.17 | -0.715 | -0.805 | -8.05 | -2.825 | -2.825 | 0 | 12 | 1 | 1 | -2.825 | 10 | 0 | 0
113.75 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.14 | -0.43 | -0.705 | -7.05 | -1.375 | -1.375 | 0 | 12 | 1 | 1 | -1.375 | 10 | 0 | 0
113.8 | 49.83 | 49.83 | 0.715 | 0.715 | 7.15 | 50.12 | -0.24 | -0.605 | -6.05 | 0.55 | 0.55 | 0 | 12 | 1 | 1 | 0.55 | 10 | 0 | 0
113.85 | 49.81 | 49.81 | 0.905 | 0.905 | 9.05 | 50.09 | -0.044118 | -0.505 | -5.05 | 2 | 2 | 0 | 12 | 1 | 1 | 2 | 10 | 0 | 0
113.9 | 49.78 | 49.78 | 1 | 1 | 10 | 50.06 | -0.026471 | -0.405 | -4.05 | 2.975 | 2.975 | 0 | 12 | 1 | 1 | 2.975 | 10 | 0 | 0
113.95 | 49.76 | 49.76 | 1 | 1 | 10 | 50.04 | -0.014706 | -0.305 | -3.05 | 3.475 | 3.475 | 0 | 12 | 1 | 1 | 3.475 | 10 | 0 | 0
114 | 49.73 | 49.73 | 1 | 1 | 10 | 50.01 | 0 | -0.205 | -2.05 | 3.975 | 3.975 | 0 | 12 | 1 | 1 | 3.975 | 10 | 0 | 0
114.05 | 49.71 | 49.71 | 1 | 1 | 10 | 49.99 | 0 | -0.105 | -1.05 | 4.475 | 4.475 | 0 | 12 | 1 | 1 | 4.475 | 10 | 0 | 0
114.1 | 49.68 | 49.68 | 1 | 1 | 10 | 49.96 | 0.014706 | -0.005 | -0.05 | 4.975 | 4.975 | 0 | 12 | 1 | 1 | 4.975 | 10 | 0 | 0
114.15 | 49.65 | 49.65 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
114.2 | 49.63 | 49.63 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
114.25 | 49.6 | 49.6 | 1 | 1 | 10 | 49.88 | 0.24 | 0.14412 | 1.4412 | 5.7206 | 5.7206 | 0 | 12 | 1 | 1 | 5.7206 | 10 | 0 | 0
114.3 | 49.58 | 49.58 | 1 | 1 | 10 | 49.86 | 0.43 | 0.24412 | 2.4412 | 6.2206 | 6.2206 | 0 | 12 | 1 | 1 | 6.2206 | 10 | 0 | 0
114.35 | 49.55 | 49.55 | 1 | 1 | 10 | 49.83 | 0.715 | 0.34412 | 3.4412 | 6.7206 | 6.7206 | 0 | 12 | 1 | 1 | 6.7206 | 10 | 0 | 0
114.4 | 49.53 | 49.53 | 1 | 1 | 10 | 49.81 | 0.905 | 0.44412 | 4.4412 | 7.2206 | 7.2206 | 0 | 12 | 1 | 1 | 7.2206 | 10 | 0 | 0
114.45 | 49.5 | 49.5 | 1 | 1 | 10 | 49.78 | 1 | 0.54412 | 5.4412 | 7.7206 | 7.7206 | 0 | 12 | 1 | 1 | 7.7206 | 10 | 0 | 0
114.5 | 49.5 | 49.5 | 1 | 1 | 10 | 49.76 | 1 | 0.64412 | 6.4412 | 8.2206 | 8.2206 | 0 | 12 | 1 | 1 | 8.2206 | 10 | 0 | 0
114.55 | 49.53 | 49.5 | 1 | 1 | 10 | 49.73 | 1 | 0.74412 | 7.4412 | 8.7206 | 8.7206 | 0 | 12 | 1 | 1 | 8.7206 | 10 | 0 | 0
114.6 | 49.55 | 49.5 | 1 | 1 | 10 | 49.71 | 1 | 0.84412 | 8.4412 | 9.2206 | 9.2206 | 0 | 12 | 1 | 1 | 9.2206 | 10 | 0 | 0
114.65 | 49.58 | 49.5 | 1 | 1 | 10 | 49.68 | 1 | 0.94412 | 9.4412 | 9.7206 | 9.7206 | 0 | 12 | 1 | 1 | 9.7206 | 10 | 0 | 0
114.7 | 49.6 | 49.5 | 1 | 1 | 10 | 49.65 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
114.75 | 49.63 | 49.5 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
114.8 | 49.65 | 49.5 | 1 | 1 | 10 | 49.65 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
114.85 | 49.68 | 49.5 | 1 | 1 | 10 | 49.68 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
114.9 | 49.71 | 49.5 | 1 | 1 | 10 | 49.71 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
114.95 | 49.73 | 49.5 | 1 | 1 | 10 | 49.73 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
115 | 49.76 | 49.5 | 1 | 1 | 10 | 49.76 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
115.05 | 49.78 | 49.5 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
115.1 | 49.81 | 49.53 | 1 | 1 | 10 | 49.81 | 0.905 | 0.905 | 9.05 | 9.525 | 9.525 | 0 | 12 | 1 | 1 | 9.525 | 10 | 0 | 0
115.15 | 49.83 | 49.55 | 1 | 1 | 10 | 49.83 | 0.715 | 0.715 | 7.15 | 8.575 | 8.575 | 0 | 12 | 1 | 1 | 8.575 | 10 | 0 | 0
115.2 | 49.86 | 49.58 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
115.25 | 49.88 | 49.6 | 1 | 1 | 10 | 49.88 | 0.24 | 0.24 | 2.4 | 6.2 | 6.2 | 0 | 12 | 1 | 1 | 6.2 | 10 | 0 | 0
115.3 | 49.91 | 49.63 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
115.35 | 49.94 | 49.65 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
115.4 | 49.96 | 49.68 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
115.45 | 49.99 | 49.71 | 1 | 1 | 10 | 49.99 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
115.5 | 50.01 | 49.73 | 1 | 1 | 10 | 50.01 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
115.55 | 50.04 | 49.76 | 1 | 1 | 10 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 4.9265 | 4.9265 | 0 | 12 | 1 | 1 | 4.9265 | 10 | 0 | 0
115.6 | 50.06 | 49.78 | 1 | 1 | 10 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 4.8676 | 4.8676 | 0 | 12 | 1 | 1 | 4.8676 | 10 | 0 | 0
115.65 | 50.09 | 49.81 | 0.905 | 0.905 | 9.05 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 4.3044 | 4.3044 | 0 | 12 | 1 | 1 | 4.3044 | 10 | 0 | 0
115.7 | 50.12 | 49.83 | 0.715 | 0.805 | 8.05 | 50.12 | -0.24 | -0.24 | -2.4 | 2.825 | 2.825 | 0 | 12 | 1 | 1 | 2.825 | 10 | 0 | 0
115.75 | 50.14 | 49.86 | 0.43 | 0.705 | 7.05 | 50.14 | -0.43 | -0.43 | -4.3 | 1.375 | 1.375 | 0 | 12 | 1 | 1 | 1.375 | 10 | 0 | 0
115.8 | 50.17 | 49.88 | 0.24 | 0.605 | 6.05 | 50.17 | -0.715 | -0.715 | -7.15 | -0.55 | -0.55 | 0 | 12 | 1 | 1 | -0.55 | 10 | 0 | 0
115.85 | 50.19 | 49.91 | 0.044118 | 0.505 | 5.05 | 50.19 | -0.905 | -0.905 | -9.05 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
115.9 | 50.22 | 49.94 | 0.026471 | 0.405 | 4.05 | 50.22 | -1 | -1 | -10 | -2.975 | -2.975 | 0 | 12 | 1 | 1 | -2.975 | 10 | 0 | 0
115.95 | 50.24 | 49.96 | 0.014706 | 0.305 | 3.05 | 50.24 | -1 | -1 | -10 | -3.475 | -3.475 | 0 | 12 | 1 | 1 | -3.475 | 10 | 0 | 0
116 | 50.27 | 49.99 | 0 | 0.205 | 2.05 | 50.27 | -1 | -1 | -10 | -3.975 | -3.975 | 0 | 12 | 1 | 1 | -3.975 | 10 | 0 | 0
116.05 | 50.29 | 50.01 | 0 | 0.105 | 1.05 | 50.29 | -1 | -1 | -10 | -4.475 | -4.475 | 0 | 12 | 1 | 1 | -4.475 | 10 | 0 | 0
116.1 | 50.32 | 50.04 | -0.014706 | 0.005 | 0.05 | 50.32 | -1 | -1 | -10 | -4.975 | -4.975 | 0 | 12 | 1 | 1 | -4.975 | 10 | 0 | 0
116.15 | 50.35 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.35 | -1 | -1 | -10 | -5.1324 | -5.1324 | 0 | 12 | 1 | 1 | -5.1324 | 10 | 0 | 0
116.2 | 50.37 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 50.37 | -1 | -1 | -10 | -5.2206 | -5.2206 | 0 | 12 | 1 | 1 | -5.2206 | 10 | 0 | 0
116.25 | 50.4 | 50.12 | -0.24 | -0.14412 | -1.4412 | 50.4 | -1 | -1 | -10 | -5.7206 | -5.7206 | 0 | 12 | 1 | 1 | -5.7206 | 10 | 0 | 0
116.3 | 50.42 | 50.14 | -0.43 | -0.24412 | -2.4412 | 50.42 | -1 | -1 | -10 | -6.2206 | -6.2206 | 0 | 12 | 1 | 1 | -6.2206 | 10 | 0 | 0
116.35 | 50.45 | 50.17 | -0.715 | -0.34412 | -3.4412 | 50.45 | -1 | -1 | -10 | -6.7206 | -6.7206 | 0 | 12 | 1 | 1 | -6.7206 | 10 | 0 | 0
116.4 | 50.47 | 50.19 | -0.905 | -0.44412 | -4.4412 | 50.47 | -1 | -1 | -10 | -7.2206 | -7.2206 | 0 | 12 | 1 | 1 | -7.2206 | 10 | 0 | 0
116.45 | 50.5 | 50.22 | -1 | -0.54412 | -5.4412 | 50.5 | -1 | -1 | -10 | -7.7206 | -7.7206 | 0 | 12 | 1 | 1 | -7.7206 | 10 | 0 | 0
116.5 | 50.5 | 50.24 | -1 | -0.64412 | -6.4412 | 50.5 | -1 | -1 | -10 | -8.2206 | -8.2206 | 0 | 12 | 1 | 1 | -8.2206 | 10 | 0 | 0
116.55 | 50.47 | 50.27 | -1 | -0.74412 | -7.4412 | 50.5 | -1 | -1 | -10 | -8.7206 | -8.7206 | 0 | 12 | 1 | 1 | -8.7206 | 10 | 0 | 0
116.6 | 50.45 | 50.29 | -1 | -0.84412 | -8.4412 | 50.5 | -1 | -1 | -10 | -9.2206 | -9.2206 | 0 | 12 | 1 | 1 | -9.2206 | 10 | 0 | 0
116.65 | 50.42 | 50.32 | -1 | -0.94412 | -9.4412 | 50.5 | -1 | -1 | -10 | -9.7206 | -9.7206 | 0 | 12 | 1 | 1 | -9.7206 | 10 | 0 | 0
116.7 | 50.39 | 50.35 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
116.75 | 50.37 | 50.37 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
116.8 | 50.34 | 50.34 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
116.85 | 50.32 | 50.32 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
116.9 | 50.29 | 50.29 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
116.95 | 50.26 | 50.26 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
117 | 50.24 | 50.24 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
117.05 | 50.21 | 50.21 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
117.1 | 50.18 | 50.18 | -0.81 | -0.81 | -8.1 | 50.47 | -1 | -1 | -10 | -9.05 | -9.05 | 0 | 12 | 1 | 1 | -9.05 | 10 | 0 | 0
117.15 | 50.16 | 50.16 | -0.62 | -0.62 | -6.2 | 50.45 | -1 | -1 | -10 | -8.1 | -8.1 | 0 | 12 | 1 | 1 | -8.1 | 10 | 0 | 0
117.2 | 50.13 | 50.13 | -0.335 | -0.335 | -3.35 | 50.42 | -1 | -1 | -10 | -6.675 | -6.675 | 0 | 12 | 1 | 1 | -6.675 | 10 | 0 | 0
117.25 | 50.11 | 50.11 | -0.145 | -0.145 | -1.45 | 50.39 | -1 | -1 | -10 | -5.725 | -5.725 | 0 | 12 | 1 | 1 | -5.725 | 10 | 0 | 0
117.3 | 50.08 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 50.37 | -1 | -1 | -10 | -5.1912 | -5.1912 | 0 | 12 | 1 | 1 | -5.1912 | 10 | 0 | 0
117.35 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.34 | -1 | -1 | -10 | -5.1029 | -5.1029 | 0 | 12 | 1 | 1 | -5.1029 | 10 | 0 | 0
117.4 | 50.03 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 50.32 | -1 | -1 | -10 | -5.0441 | -5.0441 | 0 | 12 | 1 | 1 | -5.0441 | 10 | 0 | 0
117.45 | 50 | 50 | 0 | 0 | 0 | 50.29 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
117.5 | 50 | 50 | 0 | 0 | 0 | 50.26 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
117.55 | 50 | 50 | 0 | 0 | 0 | 50.24 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
117.6 | 50 | 50 | 0 | 0 | 0 | 50.21 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
117.65 | 50 | 50 | 0 | 0 | 0 | 50.18 | -0.81 | -0.9 | -9 | -4.5 | -4.5 | 0 | 12 | 1 | 1 | -4.5 | 10 | 0 | 0
117.7 | 50 | 50 | 0 | 0 | 0 | 50.16 | -0.62 | -0.8 | -8 | -4 | -4 | 0 | 12 | 1 | 1 | -4 | 10 | 0 | 0
117.75 | 50 | 50 | 0 | 0 | 0 | 50.13 | -0.335 | -0.7 | -7 | -3.5 | -3.5 | 0 | 12 | 1 | 1 | -3.5 | 10 | 0 | 0
117.8 | 50.01 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.6 | -6 | -3 | -3 | 0 | 12 | 1 | 1 | -3 | 10 | 0 | 0
117.85 | 50.01 | 50 | 0 | 0 | 0 | 50.08 | -0.038235 | -0.5 | -5 | -2.5 | -2.5 | 0 | 12 | 1 | 1 | -2.5 | 10 | 0 | 0
117.9 | 49.99 | 49.99 | 0 | 0 | 0 | 50.05 | -0.020588 | -0.4 | -4 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
117.95 | 49.99 | 49.99 | 0 | 0 | 0 | 50.03 | -0.0088235 | -0.3 | -3 | -1.5 | -1.5 | 0 | 12 | 1 | 1 | -1.5 | 10 | 0 | 0
118 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | -0.2 | -2 | -0.83824 | -0.83824 | 0 | 12 | 1 | 1 | -0.83824 | 10 | 0 | 0
118.05 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | -0.1 | -1 | -0.33824 | -0.33824 | 0 | 12 | 1 | 1 | -0.33824 | 10 | 0 | 0
118.1 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
118.15 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
118.2 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
118.25 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
118.3 | 49.89 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
118.35 | 49.89 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
118.4 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50.01 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
118.45 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
118.5 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
118.55 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 2.7868 | 2.7868 | 0 | 12 | 1 | 1 | 2.7868 | 10 | 0 | 0
118.6 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 2.7868 | 2.7868 | 0 | 12 | 1 | 1 | 2.7868 | 10 | 0 | 0
118.65 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 2.8456 | 2.8456 | 0 | 12 | 1 | 1 | 2.8456 | 10 | 0 | 0
118.7 | 49.94 | 49.85 | 0.525 | 0.525 | 5.25 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 2.7574 | 2.7574 | 0 | 12 | 1 | 1 | 2.7574 | 10 | 0 | 0
118.75 | 49.94 | 49.85 | 0.525 | 0.525 | 5.25 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 2.7574 | 2.7574 | 0 | 12 | 1 | 1 | 2.7574 | 10 | 0 | 0
118.8 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
118.85 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
118.9 | 49.93 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
118.95 | 49.93 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
119 | 49.96 | 49.85 | 0.525 | 0.525 | 5.25 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 2.6985 | 2.6985 | 0 | 12 | 1 | 1 | 2.6985 | 10 | 0 | 0
119.05 | 49.96 | 49.85 | 0.525 | 0.525 | 5.25 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 2.6985 | 2.6985 | 0 | 12 | 1 | 1 | 2.6985 | 10 | 0 | 0
119.1 | 49.99 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
119.15 | 49.99 | 49.91 | 0.044118 | 0.425 | 4.25 | 49.99 | 0 | 0 | 0 | 2.125 | 2.125 | 0 | 12 | 1 | 1 | 2.125 | 10 | 0 | 0
119.2 | 49.99 | 49.91 | 0.044118 | 0.325 | 3.25 | 49.99 | 0 | 0 | 0 | 1.625 | 1.625 | 0 | 12 | 1 | 1 | 1.625 | 10 | 0 | 0
119.25 | 49.99 | 49.93 | 0.032353 | 0.225 | 2.25 | 49.99 | 0 | 0 | 0 | 1.125 | 1.125 | 0 | 12 | 1 | 1 | 1.125 | 10 | 0 | 0
119.3 | 49.96 | 49.93 | 0.032353 | 0.125 | 1.25 | 49.99 | 0 | 0 | 0 | 0.625 | 0.625 | 0 | 12 | 1 | 1 | 0.625 | 10 | 0 | 0
119.35 | 49.96 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 49.99 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
119.4 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
119.45 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
119.5 | 50.05 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.058824 | 0.058824 | 0 | 12 | 1 | 1 | 0.058824 | 10 | 0 | 0
119.55 | 50.05 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
119.6 | 49.97 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
119.65 | 49.97 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
119.7 | 49.92 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
119.75 | 49.92 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
119.8 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
119.85 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
119.9 | 49.94 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
119.95 | 49.94 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
120 | 50.01 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
120.05 | 50.01 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
120.1 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
120.15 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
120.2 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
120.25 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
120.3 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
120.35 | 49.95 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
120.4 | 49.97 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
120.45 | 49.97 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
120.5 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
120.55 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
120.6 | 49.87 | 49.87 | 0.335 | 0.335 | 3.35 | 50.01 | 0 | 0 | 0 | 1.675 | 1.675 | 0 | 12 | 1 | 1 | 1.675 | 10 | 0 | 0
120.65 | 49.87 | 49.87 | 0.335 | 0.335 | 3.35 | 49.99 | 0 | 0 | 0 | 1.675 | 1.675 | 0 | 12 | 1 | 1 | 1.675 | 10 | 0 | 0
120.7 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
120.75 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 2.6691 | 2.6691 | 0 | 12 | 1 | 1 | 2.6691 | 10 | 0 | 0
120.8 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
120.85 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
120.9 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
120.95 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
121 | 49.84 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
121.05 | 49.84 | 49.79 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
121.1 | 49.89 | 49.79 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
121.15 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.12647 | 1.2647 | 5.6324 | 5.6324 | 0 | 12 | 1 | 1 | 5.6324 | 10 | 0 | 0
121.2 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.145 | 1.45 | 5.725 | 5.725 | 0 | 12 | 1 | 1 | 5.725 | 10 | 0 | 0
121.25 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.145 | 1.45 | 5.725 | 5.725 | 0 | 12 | 1 | 1 | 5.725 | 10 | 0 | 0
121.3 | 49.96 | 49.79 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
121.35 | 49.96 | 49.79 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
121.4 | 50.02 | 49.79 | 1 | 1 | 10 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 4.9853 | 4.9853 | 0 | 12 | 1 | 1 | 4.9853 | 10 | 0 | 0
121.45 | 50.02 | 49.79 | 1 | 1 | 10 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 4.9853 | 4.9853 | 0 | 12 | 1 | 1 | 4.9853 | 10 | 0 | 0
121.5 | 50.03 | 49.79 | 1 | 1 | 10 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.9559 | 4.9559 | 0 | 12 | 1 | 1 | 4.9559 | 10 | 0 | 0
121.55 | 50.03 | 49.84 | 0.62 | 0.9 | 9 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.4559 | 4.4559 | 0 | 12 | 1 | 1 | 4.4559 | 10 | 0 | 0
121.6 | 50.02 | 49.84 | 0.62 | 0.8 | 8 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 3.9559 | 3.9559 | 0 | 12 | 1 | 1 | 3.9559 | 10 | 0 | 0
121.65 | 50.02 | 49.89 | 0.145 | 0.7 | 7 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 3.4559 | 3.4559 | 0 | 12 | 1 | 1 | 3.4559 | 10 | 0 | 0
121.7 | 50.08 | 49.89 | 0.145 | 0.6 | 6 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 2.8088 | 2.8088 | 0 | 12 | 1 | 1 | 2.8088 | 10 | 0 | 0
121.75 | 50.08 | 49.89 | 0.145 | 0.5 | 5 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 2.3088 | 2.3088 | 0 | 12 | 1 | 1 | 2.3088 | 10 | 0 | 0
121.8 | 50.01 | 49.89 | 0.145 | 0.4 | 4 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 1.8088 | 1.8088 | 0 | 12 | 1 | 1 | 1.8088 | 10 | 0 | 0
121.85 | 50.01 | 49.96 | 0.014706 | 0.3 | 3 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 1.3088 | 1.3088 | 0 | 12 | 1 | 1 | 1.3088 | 10 | 0 | 0
121.9 | 49.94 | 49.94 | 0.026471 | 0.2 | 2 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.80882 | 0.80882 | 0 | 12 | 1 | 1 | 0.80882 | 10 | 0 | 0
121.95 | 49.94 | 49.94 | 0.026471 | 0.1 | 1 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.30882 | 0.30882 | 0 | 12 | 1 | 1 | 0.30882 | 10 | 0 | 0
122 | 50 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
122.05 | 50 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
122.1 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
122.15 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
122.2 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
122.25 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
122.3 | 49.92 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
122.35 | 49.92 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
122.4 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50.01 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
122.45 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
122.5 | 49.92 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
122.55 | 49.92 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
122.6 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
122.65 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
122.7 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
122.75 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
122.8 | 49.87 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
122.85 | 49.87 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
122.9 | 49.8 | 49.8 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
122.95 | 49.8 | 49.8 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
123 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
123.05 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
123.1 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
123.15 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
123.2 | 49.72 | 49.72 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
123.25 | 49.72 | 49.72 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
123.3 | 49.67 | 49.67 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
123.35 | 49.67 | 49.67 | 1 | 1 | 10 | 49.87 | 0.335 | 0.14412 | 1.4412 | 5.7206 | 5.7206 | 0 | 12 | 1 | 1 | 5.7206 | 10 | 0 | 0
123.4 | 49.65 | 49.65 | 1 | 1 | 10 | 49.87 | 0.335 | 0.24412 | 2.4412 | 6.2206 | 6.2206 | 0 | 12 | 1 | 1 | 6.2206 | 10 | 0 | 0
123.45 | 49.65 | 49.65 | 1 | 1 | 10 | 49.8 | 1 | 0.34412 | 3.4412 | 6.7206 | 6.7206 | 0 | 12 | 1 | 1 | 6.7206 | 10 | 0 | 0
123.5 | 49.59 | 49.59 | 1 | 1 | 10 | 49.8 | 1 | 0.44412 | 4.4412 | 7.2206 | 7.2206 | 0 | 12 | 1 | 1 | 7.2206 | 10 | 0 | 0
123.55 | 49.59 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.54412 | 5.4412 | 7.7206 | 7.7206 | 0 | 12 | 1 | 1 | 7.7206 | 10 | 0 | 0
123.6 | 49.66 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.64412 | 6.4412 | 8.2206 | 8.2206 | 0 | 12 | 1 | 1 | 8.2206 | 10 | 0 | 0
123.65 | 49.66 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.74412 | 7.4412 | 8.7206 | 8.7206 | 0 | 12 | 1 | 1 | 8.7206 | 10 | 0 | 0
123.7 | 49.63 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.84412 | 8.4412 | 9.2206 | 9.2206 | 0 | 12 | 1 | 1 | 9.2206 | 10 | 0 | 0
123.75 | 49.63 | 49.59 | 1 | 1 | 10 | 49.72 | 1 | 0.94412 | 9.4412 | 9.7206 | 9.7206 | 0 | 12 | 1 | 1 | 9.7206 | 10 | 0 | 0
123.8 | 49.61 | 49.59 | 1 | 1 | 10 | 49.72 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
123.85 | 49.61 | 49.59 | 1 | 1 | 10 | 49.67 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
123.9 | 49.54 | 49.54 | 1 | 1 | 10 | 49.67 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
123.95 | 49.54 | 49.54 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
124 | 49.46 | 49.46 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
124.05 | 49.46 | 49.46 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
124.1 | 49.45 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
124.15 | 49.45 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
124.2 | 49.51 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
124.25 | 49.51 | 49.45 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
124.3 | 49.5 | 49.45 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
124.35 | 49.5 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
124.4 | 49.54 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
124.45 | 49.54 | 49.45 | 1 | 1 | 10 | 49.54 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
124.5 | 49.59 | 49.45 | 1 | 1 | 10 | 49.59 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
124.55 | 49.59 | 49.45 | 1 | 1 | 10 | 49.59 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
124.6 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
124.65 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
124.7 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
124.75 | 49.61 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
124.8 | 49.53 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
124.85 | 49.53 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
124.9 | 49.54 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
124.95 | 49.54 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
125 | 49.61 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
125.05 | 49.61 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
125.1 | 49.66 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
125.15 | 49.66 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
125.2 | 49.64 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
125.25 | 49.64 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
125.3 | 49.69 | 49.53 | 1 | 1 | 10 | 49.69 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
125.35 | 49.69 | 49.53 | 1 | 1 | 10 | 49.69 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
125.4 | 49.74 | 49.53 | 1 | 1 | 10 | 49.74 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
125.45 | 49.74 | 49.54 | 1 | 1 | 10 | 49.74 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
125.5 | 49.78 | 49.54 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
125.55 | 49.78 | 49.61 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
125.6 | 49.82 | 49.61 | 1 | 1 | 10 | 49.82 | 0.81 | 0.81 | 8.1 | 9.05 | 9.05 | 0 | 12 | 1 | 1 | 9.05 | 10 | 0 | 0
125.65 | 49.82 | 49.64 | 1 | 1 | 10 | 49.82 | 0.81 | 0.81 | 8.1 | 9.05 | 9.05 | 0 | 12 | 1 | 1 | 9.05 | 10 | 0 | 0
125.7 | 49.86 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
125.75 | 49.86 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
125.8 | 49.84 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
125.85 | 49.84 | 49.69 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
125.9 | 49.91 | 49.69 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
125.95 | 49.91 | 49.74 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
126 | 49.97 | 49.74 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
126.05 | 49.97 | 49.78 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
126.1 | 50.03 | 49.78 | 1 | 1 | 10 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.9559 | 4.9559 | 0 | 12 | 1 | 1 | 4.9559 | 10 | 0 | 0
126.15 | 50.03 | 49.82 | 0.81 | 0.9 | 9 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.4559 | 4.4559 | 0 | 12 | 1 | 1 | 4.4559 | 10 | 0 | 0
126.2 | 50.05 | 49.82 | 0.81 | 0.81 | 8.1 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 3.9471 | 3.9471 | 0 | 12 | 1 | 1 | 3.9471 | 10 | 0 | 0
126.25 | 50.05 | 49.84 | 0.62 | 0.71 | 7.1 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 3.4471 | 3.4471 | 0 | 12 | 1 | 1 | 3.4471 | 10 | 0 | 0
126.3 | 50.01 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
126.35 | 50.01 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
126.4 | 49.95 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
126.45 | 49.95 | 49.91 | 0.044118 | 0.52 | 5.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.4971 | 2.4971 | 0 | 12 | 1 | 1 | 2.4971 | 10 | 0 | 0
126.5 | 49.99 | 49.91 | 0.044118 | 0.42 | 4.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 1.9971 | 1.9971 | 0 | 12 | 1 | 1 | 1.9971 | 10 | 0 | 0
126.55 | 49.99 | 49.95 | 0.020588 | 0.32 | 3.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 1.4971 | 1.4971 | 0 | 12 | 1 | 1 | 1.4971 | 10 | 0 | 0
126.6 | 49.92 | 49.92 | 0.038235 | 0.22 | 2.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.99706 | 0.99706 | 0 | 12 | 1 | 1 | 0.99706 | 10 | 0 | 0
126.65 | 49.92 | 49.92 | 0.038235 | 0.12 | 1.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.49706 | 0.49706 | 0 | 12 | 1 | 1 | 0.49706 | 10 | 0 | 0
126.7 | 49.97 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
126.75 | 49.97 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
126.8 | 50.02 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
126.85 | 50.02 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.17647 | 0.17647 | 0 | 12 | 1 | 1 | 0.17647 | 10 | 0 | 0
126.9 | 50.07 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
126.95 | 50.07 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
127 | 50.06 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
127.05 | 50.06 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
127.1 | 50.13 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
127.15 | 50.13 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
127.2 | 50.09 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
127.25 | 50.09 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6309 | -1.6309 | 0 | 12 | 1 | 1 | -1.6309 | 10 | 0 | 0
127.3 | 50.07 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6309 | -1.6309 | 0 | 12 | 1 | 1 | -1.6309 | 10 | 0 | 0
127.35 | 50.07 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6897 | -1.6897 | 0 | 12 | 1 | 1 | -1.6897 | 10 | 0 | 0
127.4 | 50.07 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6897 | -1.6897 | 0 | 12 | 1 | 1 | -1.6897 | 10 | 0 | 0
127.45 | 50.07 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.13 | -0.335 | -0.335 | -3.35 | -1.8074 | -1.8074 | 0 | 12 | 1 | 1 | -1.8074 | 10 | 0 | 0
127.5 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.13 | -0.335 | -0.335 | -3.35 | -1.7779 | -1.7779 | 0 | 12 | 1 | 1 | -1.7779 | 10 | 0 | 0
127.55 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.13 | -0.335 | -0.335 | -3.35 | -1.7779 | -1.7779 | 0 | 12 | 1 | 1 | -1.7779 | 10 | 0 | 0
127.6 | 50.01 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
127.65 | 50.01 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
127.7 | 50.07 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
127.75 | 50.07 | 50.01 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.235 | -2.35 | -1.175 | -1.175 | 0 | 12 | 1 | 1 | -1.175 | 10 | 0 | 0
127.8 | 50.05 | 50.01 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.135 | -1.35 | -0.675 | -0.675 | 0 | 12 | 1 | 1 | -0.675 | 10 | 0 | 0
127.85 | 50.05 | 50.01 | 0 | 0 | 0 | 50.07 | -0.032353 | -0.035 | -0.35 | -0.175 | -0.175 | 0 | 12 | 1 | 1 | -0.175 | 10 | 0 | 0
127.9 | 50.1 | 50.01 | 0 | 0 | 0 | 50.1 | -0.05 | -0.05 | -0.5 | -0.25 | -0.25 | 0 | 12 | 1 | 1 | -0.25 | 10 | 0 | 0
127.95 | 50.1 | 50.01 | 0 | 0 | 0 | 50.1 | -0.05 | -0.05 | -0.5 | -0.25 | -0.25 | 0 | 12 | 1 | 1 | -0.25 | 10 | 0 | 0
128 | 50.11 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
128.05 | 50.11 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
128.1 | 50.06 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
128.15 | 50.06 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
128.2 | 50.04 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
128.25 | 50.04 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
128.3 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
128.35 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
128.4 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
128.45 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
128.5 | 50.11 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
128.55 | 50.11 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
128.6 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
128.65 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
128.7 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
128.75 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
128.8 | 50.02 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.11 | -0.145 | -0.145 | -1.45 | -0.73971 | -0.73971 | 0 | 12 | 1 | 1 | -0.73971 | 10 | 0 | 0
128.85 | 50.02 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.11 | -0.145 | -0.145 | -1.45 | -0.73971 | -0.73971 | 0 | 12 | 1 | 1 | -0.73971 | 10 | 0 | 0
128.9 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
128.95 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
129 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
129.05 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
129.1 | 50.01 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
129.15 | 50.01 | 50 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.045 | -0.45 | -0.225 | -0.225 | 0 | 12 | 1 | 1 | -0.225 | 10 | 0 | 0
129.2 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
129.25 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
129.3 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
129.35 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
129.4 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.14706 | 0.14706 | 0 | 12 | 1 | 1 | 0.14706 | 10 | 0 | 0
129.45 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
129.5 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
129.55 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
129.6 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
129.65 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
129.7 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
129.75 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
129.8 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
129.85 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
129.9 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
129.95 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
130 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
130.05 | 50 | 50 | 0 | 0 | 0 | 50.01 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
130.1 | 49.5 | 49.5 | 1 | 1 | 10 | 50.01 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
130.15 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
130.2 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
130.25 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
130.3 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
130.35 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
130.4 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
130.45 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
130.5 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
130.55 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
130.6 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
130.65 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.1 | 1 | 5.5 | 5.5 | 0 | 12 | 1 | 1 | 5.5 | 10 | 0 | 0
130.7 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.2 | 2 | 6 | 6 | 0 | 12 | 1 | 1 | 6 | 10 | 0 | 0
130.75 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.3 | 3 | 6.5 | 6.5 | 0 | 12 | 1 | 1 | 6.5 | 10 | 0 | 0
130.8 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.4 | 4 | 7 | 7 | 0 | 12 | 1 | 1 | 7 | 10 | 0 | 0
130.85 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.5 | 5 | 7.5 | 7.5 | 0 | 12 | 1 | 1 | 7.5 | 10 | 0 | 0
130.9 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.6 | 6 | 8 | 8 | 0 | 12 | 1 | 1 | 8 | 10 | 0 | 0
130.95 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.7 | 7 | 8.5 | 8.5 | 0 | 12 | 1 | 1 | 8.5 | 10 | 0 | 0
131 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.8 | 8 | 9 | 9 | 0 | 12 | 1 | 1 | 9 | 10 | 0 | 0
131.05 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.9 | 9 | 9.5 | 9.5 | 0 | 12 | 1 | 1 | 9.5 | 10 | 0 | 0
131.1 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
131.15 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
131.2 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
131.25 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
131.3 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
131.35 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
131.4 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
131.45 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
131.5 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
131.55 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
131.6 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
131.65 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
131.7 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
131.75 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
131.8 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
131.85 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
131.9 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
131.95 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
132 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
132.05 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
132.1 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
132.15 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
132.2 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
132.25 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
132.3 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
132.35 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
132.4 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
132.45 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
132.5 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
132.55 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
132.6 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
132.65 | 50.5 | 50.5 | -1 | 0.9 | 9 | 50.5 | -1 | -1 | -10 | -0.5 | -0.5 | 0 | 12 | 1 | 1 | -0.5 | 10 | 0 | 0
132.7 | 50.5 | 50.5 | -1 | 0.8 | 8 | 50.5 | -1 | -1 | -10 | -1 | -1 | 0 | 12 | 1 | 1 | -1 | 10 | 0 | 0
132.75 | 50.5 | 50.5 | -1 | 0.7 | 7 | 50.5 | -1 | -1 | -10 | -1.5 | -1.5 | 0 | 12 | 1 | 1 | -1.5 | 10 | 0 | 0
132.8 | 50.5 | 50.5 | -1 | 0.6 | 6 | 50.5 | -1 | -1 | -10 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
132.85 | 50.5 | 50.5 | -1 | 0.5 | 5 | 50.5 | -1 | -1 | -10 | -2.5 | -2.5 | 0 | 12 | 1 | 1 | -2.5 | 10 | 0 | 0
132.9 | 50.5 | 50.5 | -1 | 0.4 | 4 | 50.5 | -1 | -1 | -10 | -3 | -3 | 0 | 12 | 1 | 1 | -3 | 10 | 0 | 0
132.95 | 50.5 | 50.5 | -1 | 0.3 | 3 | 50.5 | -1 | -1 | -10 | -3.5 | -3.5 | 0 | 12 | 1 | 1 | -3.5 | 10 | 0 | 0
133 | 50.5 | 50.5 | -1 | 0.2 | 2 | 50.5 | -1 | -1 | -10 | -4 | -4 | 0 | 12 | 1 | 1 | -4 | 10 | 0 | 0
133.05 | 50.5 | 50.5 | -1 | 0.1 | 1 | 50.5 | -1 | -1 | -10 | -4.5 | -4.5 | 0 | 12 | 1 | 1 | -4.5 | 10 | 0 | 0
133.1 | 50.5 | 50.5 | -1 | 0 | 0 | 50.5 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
133.15 | 50.5 | 50.5 | -1 | -0.1 | -1 | 50.5 | -1 | -1 | -10 | -5.5 | -5.5 | 0 | 12 | 1 | 1 | -5.5 | 10 | 0 | 0
133.2 | 50.5 | 50.5 | -1 | -0.2 | -2 | 50.5 | -1 | -1 | -10 | -6 | -6 | 0 | 12 | 1 | 1 | -6 | 10 | 0 | 0
133.25 | 50.5 | 50.5 | -1 | -0.3 | -3 | 50.5 | -1 | -1 | -10 | -6.5 | -6.5 | 0 | 12 | 1 | 1 | -6.5 | 10 | 0 | 0
133.3 | 50.5 | 50.5 | -1 | -0.4 | -4 | 50.5 | -1 | -1 | -10 | -7 | -7 | 0 | 12 | 1 | 1 | -7 | 10 | 0 | 0
133.35 | 50.5 | 50.5 | -1 | -0.5 | -5 | 50.5 | -1 | -1 | -10 | -7.5 | -7.5 | 0 | 12 | 1 | 1 | -7.5 | 10 | 0 | 0
133.4 | 50.5 | 50.5 | -1 | -0.6 | -6 | 50.5 | -1 | -1 | -10 | -8 | -8 | 0 | 12 | 1 | 1 | -8 | 10 | 0 | 0
133.45 | 50.5 | 50.5 | -1 | -0.7 | -7 | 50.5 | -1 | -1 | -10 | -8.5 | -8.5 | 0 | 12 | 1 | 1 | -8.5 | 10 | 0 | 0
133.5 | 50.5 | 50.5 | -1 | -0.8 | -8 | 50.5 | -1 | -1 | -10 | -9 | -9 | 0 | 12 | 1 | 1 | -9 | 10 | 0 | 0
133.55 | 50.5 | 50.5 | -1 | -0.9 | -9 | 50.5 | -1 | -1 | -10 | -9.5 | -9.5 | 0 | 12 | 1 | 1 | -9.5 | 10 | 0 | 0
133.6 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
133.65 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
133.7 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
133.75 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
133.8 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
133.85 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
133.9 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
133.95 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
134 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
134.05 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
134.1 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
134.15 | 50.47 | 50.47 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
134.2 | 50.45 | 50.45 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
134.25 | 50.42 | 50.42 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
134.3 | 50.4 | 50.4 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
134.35 | 50.37 | 50.37 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
134.4 | 50.35 | 50.35 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
134.45 | 50.32 | 50.32 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
134.5 | 50.29 | 50.29 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
134.55 | 50.27 | 50.27 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
134.6 | 50.24 | 50.24 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
134.65 | 50.22 | 50.22 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
134.7 | 50.19 | 50.19 | -0.905 | -0.905 | -9.05 | 50.47 | -1 | -1 | -10 | -9.525 | -9.525 | 0 | 12 | 1 | 1 | -9.525 | 10 | 0 | 0
134.75 | 50.17 | 50.17 | -0.715 | -0.715 | -7.15 | 50.45 | -1 | -1 | -10 | -8.575 | -8.575 | 0 | 12 | 1 | 1 | -8.575 | 10 | 0 | 0
134.8 | 50.14 | 50.14 | -0.43 | -0.43 | -4.3 | 50.42 | -1 | -1 | -10 | -7.15 | -7.15 | 0 | 12 | 1 | 1 | -7.15 | 10 | 0 | 0
134.85 | 50.12 | 50.12 | -0.24 | -0.24 | -2.4 | 50.4 | -1 | -1 | -10 | -6.2 | -6.2 | 0 | 12 | 1 | 1 | -6.2 | 10 | 0 | 0
134.9 | 50.09 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 50.37 | -1 | -1 | -10 | -5.2206 | -5.2206 | 0 | 12 | 1 | 1 | -5.2206 | 10 | 0 | 0
134.95 | 50.06 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.35 | -1 | -1 | -10 | -5.1324 | -5.1324 | 0 | 12 | 1 | 1 | -5.1324 | 10 | 0 | 0
135 | 50.04 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.32 | -1 | -1 | -10 | -5.0735 | -5.0735 | 0 | 12 | 1 | 1 | -5.0735 | 10 | 0 | 0
135.05 | 50.01 | 50.01 | 0 | 0 | 0 | 50.29 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
135.1 | 49.99 | 49.99 | 0 | 0 | 0 | 50.27 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
135.15 | 49.96 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.24 | -1 | -1 | -10 | -4.9265 | -4.9265 | 0 | 12 | 1 | 1 | -4.9265 | 10 | 0 | 0
135.2 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.22 | -1 | -1 | -10 | -4.8676 | -4.8676 | 0 | 12 | 1 | 1 | -4.8676 | 10 | 0 | 0
135.25 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.19 | -0.905 | -0.905 | -9.05 | -4.3044 | -4.3044 | 0 | 12 | 1 | 1 | -4.3044 | 10 | 0 | 0
135.3 | 49.88 | 49.88 | 0.24 | 0.24 | 2.4 | 50.17 | -0.715 | -0.805 | -8.05 | -2.825 | -2.825 | 0 | 12 | 1 | 1 | -2.825 | 10 | 0 | 0
135.35 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.14 | -0.43 | -0.705 | -7.05 | -1.375 | -1.375 | 0 | 12 | 1 | 1 | -1.375 | 10 | 0 | 0
135.4 | 49.83 | 49.83 | 0.715 | 0.715 | 7.15 | 50.12 | -0.24 | -0.605 | -6.05 | 0.55 | 0.55 | 0 | 12 | 1 | 1 | 0.55 | 10 | 0 | 0
135.45 | 49.81 | 49.81 | 0.905 | 0.905 | 9.05 | 50.09 | -0.044118 | -0.505 | -5.05 | 2 | 2 | 0 | 12 | 1 | 1 | 2 | 10 | 0 | 0
135.5 | 49.78 | 49.78 | 1 | 1 | 10 | 50.06 | -0.026471 | -0.405 | -4.05 | 2.975 | 2.975 | 0 | 12 | 1 | 1 | 2.975 | 10 | 0 | 0
135.55 | 49.76 | 49.76 | 1 | 1 | 10 | 50.04 | -0.014706 | -0.305 | -3.05 | 3.475 | 3.475 | 0 | 12 | 1 | 1 | 3.475 | 10 | 0 | 0
135.6 | 49.73 | 49.73 | 1 | 1 | 10 | 50.01 | 0 | -0.205 | -2.05 | 3.975 | 3.975 | 0 | 12 | 1 | 1 | 3.975 | 10 | 0 | 0
135.65 | 49.71 | 49.71 | 1 | 1 | 10 | 49.99 | 0 | -0.105 | -1.05 | 4.475 | 4.475 | 0 | 12 | 1 | 1 | 4.475 | 10 | 0 | 0
135.7 | 49.68 | 49.68 | 1 | 1 | 10 | 49.96 | 0.014706 | -0.005 | -0.05 | 4.975 | 4.975 | 0 | 12 | 1 | 1 | 4.975 | 10 | 0 | 0
135.75 | 49.65 | 49.65 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
135.8 | 49.63 | 49.63 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
135.85 | 49.6 | 49.6 | 1 | 1 | 10 | 49.88 | 0.24 | 0.14412 | 1.4412 | 5.7206 | 5.7206 | 0 | 12 | 1 | 1 | 5.7206 | 10 | 0 | 0
135.9 | 49.58 | 49.58 | 1 | 1 | 10 | 49.86 | 0.43 | 0.24412 | 2.4412 | 6.2206 | 6.2206 | 0 | 12 | 1 | 1 | 6.2206 | 10 | 0 | 0
135.95 | 49.55 | 49.55 | 1 | 1 | 10 | 49.83 | 0.715 | 0.34412 | 3.4412 | 6.7206 | 6.7206 | 0 | 12 | 1 | 1 | 6.7206 | 10 | 0 | 0
136 | 49.53 | 49.53 | 1 | 1 | 10 | 49.81 | 0.905 | 0.44412 | 4.4412 | 7.2206 | 7.2206 | 0 | 12 | 1 | 1 | 7.2206 | 10 | 0 | 0
136.05 | 49.5 | 49.5 | 1 | 1 | 10 | 49.78 | 1 | 0.54412 | 5.4412 | 7.7206 | 7.7206 | 0 | 12 | 1 | 1 | 7.7206 | 10 | 0 | 0
136.1 | 49.5 | 49.5 | 1 | 1 | 10 | 49.76 | 1 | 0.64412 | 6.4412 | 8.2206 | 8.2206 | 0 | 12 | 1 | 1 | 8.2206 | 10 | 0 | 0
136.15 | 49.53 | 49.5 | 1 | 1 | 10 | 49.73 | 1 | 0.74412 | 7.4412 | 8.7206 | 8.7206 | 0 | 12 | 1 | 1 | 8.7206 | 10 | 0 | 0
136.2 | 49.55 | 49.5 | 1 | 1 | 10 | 49.71 | 1 | 0.84412 | 8.4412 | 9.2206 | 9.2206 | 0 | 12 | 1 | 1 | 9.2206 | 10 | 0 | 0
136.25 | 49.58 | 49.5 | 1 | 1 | 10 | 49.68 | 1 | 0.94412 | 9.4412 | 9.7206 | 9.7206 | 0 | 12 | 1 | 1 | 9.7206 | 10 | 0 | 0
136.3 | 49.6 | 49.5 | 1 | 1 | 10 | 49.65 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
136.35 | 49.63 | 49.5 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
136.4 | 49.65 | 49.5 | 1 | 1 | 10 | 49.65 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
136.45 | 49.68 | 49.5 | 1 | 1 | 10 | 49.68 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
136.5 | 49.71 | 49.5 | 1 | 1 | 10 | 49.71 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
136.55 | 49.73 | 49.5 | 1 | 1 | 10 | 49.73 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
136.6 | 49.76 | 49.5 | 1 | 1 | 10 | 49.76 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
136.65 | 49.78 | 49.5 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
136.7 | 49.81 | 49.53 | 1 | 1 | 10 | 49.81 | 0.905 | 0.905 | 9.05 | 9.525 | 9.525 | 0 | 12 | 1 | 1 | 9.525 | 10 | 0 | 0
136.75 | 49.83 | 49.55 | 1 | 1 | 10 | 49.83 | 0.715 | 0.715 | 7.15 | 8.575 | 8.575 | 0 | 12 | 1 | 1 | 8.575 | 10 | 0 | 0
136.8 | 49.86 | 49.58 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
136.85 | 49.88 | 49.6 | 1 | 1 | 10 | 49.88 | 0.24 | 0.24 | 2.4 | 6.2 | 6.2 | 0 | 12 | 1 | 1 | 6.2 | 10 | 0 | 0
136.9 | 49.91 | 49.63 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
136.95 | 49.94 | 49.65 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
137 | 49.96 | 49.68 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
137.05 | 49.99 | 49.71 | 1 | 1 | 10 | 49.99 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
137.1 | 50.01 | 49.73 | 1 | 1 | 10 | 50.01 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
137.15 | 50.04 | 49.76 | 1 | 1 | 10 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 4.9265 | 4.9265 | 0 | 12 | 1 | 1 | 4.9265 | 10 | 0 | 0
137.2 | 50.06 | 49.78 | 1 | 1 | 10 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 4.8676 | 4.8676 | 0 | 12 | 1 | 1 | 4.8676 | 10 | 0 | 0
137.25 | 50.09 | 49.81 | 0.905 | 0.905 | 9.05 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 4.3044 | 4.3044 | 0 | 12 | 1 | 1 | 4.3044 | 10 | 0 | 0
137.3 | 50.12 | 49.83 | 0.715 | 0.805 | 8.05 | 50.12 | -0.24 | -0.24 | -2.4 | 2.825 | 2.825 | 0 | 12 | 1 | 1 | 2.825 | 10 | 0 | 0
137.35 | 50.14 | 49.86 | 0.43 | 0.705 | 7.05 | 50.14 | -0.43 | -0.43 | -4.3 | 1.375 | 1.375 | 0 | 12 | 1 | 1 | 1.375 | 10 | 0 | 0
137.4 | 50.17 | 49.88 | 0.24 | 0.605 | 6.05 | 50.17 | -0.715 | -0.715 | -7.15 | -0.55 | -0.55 | 0 | 12 | 1 | 1 | -0.55 | 10 | 0 | 0
137.45 | 50.19 | 49.91 | 0.044118 | 0.505 | 5.05 | 50.19 | -0.905 | -0.905 | -9.05 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
137.5 | 50.22 | 49.94 | 0.026471 | 0.405 | 4.05 | 50.22 | -1 | -1 | -10 | -2.975 | -2.975 | 0 | 12 | 1 | 1 | -2.975 | 10 | 0 | 0
137.55 | 50.24 | 49.96 | 0.014706 | 0.305 | 3.05 | 50.24 | -1 | -1 | -10 | -3.475 | -3.475 | 0 | 12 | 1 | 1 | -3.475 | 10 | 0 | 0
137.6 | 50.27 | 49.99 | 0 | 0.205 | 2.05 | 50.27 | -1 | -1 | -10 | -3.975 | -3.975 | 0 | 12 | 1 | 1 | -3.975 | 10 | 0 | 0
137.65 | 50.29 | 50.01 | 0 | 0.105 | 1.05 | 50.29 | -1 | -1 | -10 | -4.475 | -4.475 | 0 | 12 | 1 | 1 | -4.475 | 10 | 0 | 0
137.7 | 50.32 | 50.04 | -0.014706 | 0.005 | 0.05 | 50.32 | -1 | -1 | -10 | -4.975 | -4.975 | 0 | 12 | 1 | 1 | -4.975 | 10 | 0 | 0
137.75 | 50.35 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.35 | -1 | -1 | -10 | -5.1324 | -5.1324 | 0 | 12 | 1 | 1 | -5.1324 | 10 | 0 | 0
137.8 | 50.37 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 50.37 | -1 | -1 | -10 | -5.2206 | -5.2206 | 0 | 12 | 1 | 1 | -5.2206 | 10 | 0 | 0
137.85 | 50.4 | 50.12 | -0.24 | -0.14412 | -1.4412 | 50.4 | -1 | -1 | -10 | -5.7206 | -5.7206 | 0 | 12 | 1 | 1 | -5.7206 | 10 | 0 | 0
137.9 | 50.42 | 50.14 | -0.43 | -0.24412 | -2.4412 | 50.42 | -1 | -1 | -10 | -6.2206 | -6.2206 | 0 | 12 | 1 | 1 | -6.2206 | 10 | 0 | 0
137.95 | 50.45 | 50.17 | -0.715 | -0.34412 | -3.4412 | 50.45 | -1 | -1 | -10 | -6.7206 | -6.7206 | 0 | 12 | 1 | 1 | -6.7206 | 10 | 0 | 0
138 | 50.47 | 50.19 | -0.905 | -0.44412 | -4.4412 | 50.47 | -1 | -1 | -10 | -7.2206 | -7.2206 | 0 | 12 | 1 | 1 | -7.2206 | 10 | 0 | 0
138.05 | 50.5 | 50.22 | -1 | -0.54412 | -5.4412 | 50.5 | -1 | -1 | -10 | -7.7206 | -7.7206 | 0 | 12 | 1 | 1 | -7.7206 | 10 | 0 | 0
138.1 | 50.5 | 50.24 | -1 | -0.64412 | -6.4412 | 50.5 | -1 | -1 | -10 | -8.2206 | -8.2206 | 0 | 12 | 1 | 1 | -8.2206 | 10 | 0 | 0
138.15 | 50.47 | 50.27 | -1 | -0.74412 | -7.4412 | 50.5 | -1 | -1 | -10 | -8.7206 | -8.7206 | 0 | 12 | 1 | 1 | -8.7206 | 10 | 0 | 0
138.2 | 50.45 | 50.29 | -1 | -0.84412 | -8.4412 | 50.5 | -1 | -1 | -10 | -9.2206 | -9.2206 | 0 | 12 | 1 | 1 | -9.2206 | 10 | 0 | 0
138.25 | 50.42 | 50.32 | -1 | -0.94412 | -9.4412 | 50.5 | -1 | -1 | -10 | -9.7206 | -9.7206 | 0 | 12 | 1 | 1 | -9.7206 | 10 | 0 | 0
138.3 | 50.39 | 50.35 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
138.35 | 50.37 | 50.37 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
138.4 | 50.34 | 50.34 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
138.45 | 50.32 | 50.32 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
138.5 | 50.29 | 50.29 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
138.55 | 50.26 | 50.26 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
138.6 | 50.24 | 50.24 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
138.65 | 50.21 | 50.21 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
138.7 | 50.18 | 50.18 | -0.81 | -0.81 | -8.1 | 50.47 | -1 | -1 | -10 | -9.05 | -9.05 | 0 | 12 | 1 | 1 | -9.05 | 10 | 0 | 0
138.75 | 50.16 | 50.16 | -0.62 | -0.62 | -6.2 | 50.45 | -1 | -1 | -10 | -8.1 | -8.1 | 0 | 12 | 1 | 1 | -8.1 | 10 | 0 | 0
138.8 | 50.13 | 50.13 | -0.335 | -0.335 | -3.35 | 50.42 | -1 | -1 | -10 | -6.675 | -6.675 | 0 | 12 | 1 | 1 | -6.675 | 10 | 0 | 0
138.85 | 50.11 | 50.11 | -0.145 | -0.145 | -1.45 | 50.39 | -1 | -1 | -10 | -5.725 | -5.725 | 0 | 12 | 1 | 1 | -5.725 | 10 | 0 | 0
138.9 | 50.08 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 50.37 | -1 | -1 | -10 | -5.1912 | -5.1912 | 0 | 12 | 1 | 1 | -5.1912 | 10 | 0 | 0
138.95 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.34 | -1 | -1 | -10 | -5.1029 | -5.1029 | 0 | 12 | 1 | 1 | -5.1029 | 10 | 0 | 0
139 | 50.03 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 50.32 | -1 | -1 | -10 | -5.0441 | -5.0441 | 0 | 12 | 1 | 1 | -5.0441 | 10 | 0 | 0
139.05 | 50 | 50 | 0 | 0 | 0 | 50.29 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
139.1 | 50 | 50 | 0 | 0 | 0 | 50.26 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
139.15 | 50 | 50 | 0 | 0 | 0 | 50.24 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
139.2 | 50 | 50 | 0 | 0 | 0 | 50.21 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
139.25 | 50 | 50 | 0 | 0 | 0 | 50.18 | -0.81 | -0.9 | -9 | -4.5 | -4.5 | 0 | 12 | 1 | 1 | -4.5 | 10 | 0 | 0
139.3 | 50 | 50 | 0 | 0 | 0 | 50.16 | -0.62 | -0.8 | -8 | -4 | -4 | 0 | 12 | 1 | 1 | -4 | 10 | 0 | 0
139.35 | 50 | 50 | 0 | 0 | 0 | 50.13 | -0.335 | -0.7 | -7 | -3.5 | -3.5 | 0 | 12 | 1 | 1 | -3.5 | 10 | 0 | 0
139.4 | 50.01 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.6 | -6 | -3 | -3 | 0 | 12 | 1 | 1 | -3 | 10 | 0 | 0
139.45 | 50.01 | 50 | 0 | 0 | 0 | 50.08 | -0.038235 | -0.5 | -5 | -2.5 | -2.5 | 0 | 12 | 1 | 1 | -2.5 | 10 | 0 | 0
139.5 | 49.99 | 49.99 | 0 | 0 | 0 | 50.05 | -0.020588 | -0.4 | -4 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
139.55 | 49.99 | 49.99 | 0 | 0 | 0 | 50.03 | -0.0088235 | -0.3 | -3 | -1.5 | -1.5 | 0 | 12 | 1 | 1 | -1.5 | 10 | 0 | 0
139.6 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | -0.2 | -2 | -0.83824 | -0.83824 | 0 | 12 | 1 | 1 | -0.83824 | 10 | 0 | 0
139.65 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | -0.1 | -1 | -0.33824 | -0.33824 | 0 | 12 | 1 | 1 | -0.33824 | 10 | 0 | 0
139.7 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
139.75 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
139.8 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
139.85 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
139.9 | 49.89 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
139.95 | 49.89 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
140 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50.01 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
140.05 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
140.1 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
140.15 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 2.7868 | 2.7868 | 0 | 12 | 1 | 1 | 2.7868 | 10 | 0 | 0
140.2 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 2.7868 | 2.7868 | 0 | 12 | 1 | 1 | 2.7868 | 10 | 0 | 0
140.25 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 2.8456 | 2.8456 | 0 | 12 | 1 | 1 | 2.8456 | 10 | 0 | 0
140.3 | 49.94 | 49.85 | 0.525 | 0.525 | 5.25 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 2.7574 | 2.7574 | 0 | 12 | 1 | 1 | 2.7574 | 10 | 0 | 0
140.35 | 49.94 | 49.85 | 0.525 | 0.525 | 5.25 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 2.7574 | 2.7574 | 0 | 12 | 1 | 1 | 2.7574 | 10 | 0 | 0
140.4 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
140.45 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
140.5 | 49.93 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
140.55 | 49.93 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
140.6 | 49.96 | 49.85 | 0.525 | 0.525 | 5.25 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 2.6985 | 2.6985 | 0 | 12 | 1 | 1 | 2.6985 | 10 | 0 | 0
140.65 | 49.96 | 49.85 | 0.525 | 0.525 | 5.25 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 2.6985 | 2.6985 | 0 | 12 | 1 | 1 | 2.6985 | 10 | 0 | 0
140.7 | 49.99 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
140.75 | 49.99 | 49.91 | 0.044118 | 0.425 | 4.25 | 49.99 | 0 | 0 | 0 | 2.125 | 2.125 | 0 | 12 | 1 | 1 | 2.125 | 10 | 0 | 0
140.8 | 49.99 | 49.91 | 0.044118 | 0.325 | 3.25 | 49.99 | 0 | 0 | 0 | 1.625 | 1.625 | 0 | 12 | 1 | 1 | 1.625 | 10 | 0 | 0
140.85 | 49.99 | 49.93 | 0.032353 | 0.225 | 2.25 | 49.99 | 0 | 0 | 0 | 1.125 | 1.125 | 0 | 12 | 1 | 1 | 1.125 | 10 | 0 | 0
140.9 | 49.96 | 49.93 | 0.032353 | 0.125 | 1.25 | 49.99 | 0 | 0 | 0 | 0.625 | 0.625 | 0 | 12 | 1 | 1 | 0.625 | 10 | 0 | 0
140.95 | 49.96 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 49.99 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
141 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
141.05 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
141.1 | 50.05 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.058824 | 0.058824 | 0 | 12 | 1 | 1 | 0.058824 | 10 | 0 | 0
141.15 | 50.05 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
141.2 | 49.97 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
141.25 | 49.97 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
141.3 | 49.92 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
141.35 | 49.92 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
141.4 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
141.45 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
141.5 | 49.94 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
141.55 | 49.94 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
141.6 | 50.01 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
141.65 | 50.01 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
141.7 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
141.75 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
141.8 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
141.85 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
141.9 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
141.95 | 49.95 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
142 | 49.97 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
142.05 | 49.97 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
142.1 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
142.15 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
142.2 | 49.87 | 49.87 | 0.335 | 0.335 | 3.35 | 50.01 | 0 | 0 | 0 | 1.675 | 1.675 | 0 | 12 | 1 | 1 | 1.675 | 10 | 0 | 0
142.25 | 49.87 | 49.87 | 0.335 | 0.335 | 3.35 | 49.99 | 0 | 0 | 0 | 1.675 | 1.675 | 0 | 12 | 1 | 1 | 1.675 | 10 | 0 | 0
142.3 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
142.35 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 2.6691 | 2.6691 | 0 | 12 | 1 | 1 | 2.6691 | 10 | 0 | 0
142.4 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
142.45 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
142.5 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
142.55 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
142.6 | 49.84 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
142.65 | 49.84 | 49.79 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
142.7 | 49.89 | 49.79 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
142.75 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.12647 | 1.2647 | 5.6324 | 5.6324 | 0 | 12 | 1 | 1 | 5.6324 | 10 | 0 | 0
142.8 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.145 | 1.45 | 5.725 | 5.725 | 0 | 12 | 1 | 1 | 5.725 | 10 | 0 | 0
142.85 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.145 | 1.45 | 5.725 | 5.725 | 0 | 12 | 1 | 1 | 5.725 | 10 | 0 | 0
142.9 | 49.96 | 49.79 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
142.95 | 49.96 | 49.79 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
143 | 50.02 | 49.79 | 1 | 1 | 10 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 4.9853 | 4.9853 | 0 | 12 | 1 | 1 | 4.9853 | 10 | 0 | 0
143.05 | 50.02 | 49.79 | 1 | 1 | 10 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 4.9853 | 4.9853 | 0 | 12 | 1 | 1 | 4.9853 | 10 | 0 | 0
143.1 | 50.03 | 49.79 | 1 | 1 | 10 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.9559 | 4.9559 | 0 | 12 | 1 | 1 | 4.9559 | 10 | 0 | 0
143.15 | 50.03 | 49.84 | 0.62 | 0.9 | 9 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.4559 | 4.4559 | 0 | 12 | 1 | 1 | 4.4559 | 10 | 0 | 0
143.2 | 50.02 | 49.84 | 0.62 | 0.8 | 8 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 3.9559 | 3.9559 | 0 | 12 | 1 | 1 | 3.9559 | 10 | 0 | 0
143.25 | 50.02 | 49.89 | 0.145 | 0.7 | 7 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 3.4559 | 3.4559 | 0 | 12 | 1 | 1 | 3.4559 | 10 | 0 | 0
143.3 | 50.08 | 49.89 | 0.145 | 0.6 | 6 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 2.8088 | 2.8088 | 0 | 12 | 1 | 1 | 2.8088 | 10 | 0 | 0
143.35 | 50.08 | 49.89 | 0.145 | 0.5 | 5 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 2.3088 | 2.3088 | 0 | 12 | 1 | 1 | 2.3088 | 10 | 0 | 0
143.4 | 50.01 | 49.89 | 0.145 | 0.4 | 4 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 1.8088 | 1.8088 | 0 | 12 | 1 | 1 | 1.8088 | 10 | 0 | 0
143.45 | 50.01 | 49.96 | 0.014706 | 0.3 | 3 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 1.3088 | 1.3088 | 0 | 12 | 1 | 1 | 1.3088 | 10 | 0 | 0
143.5 | 49.94 | 49.94 | 0.026471 | 0.2 | 2 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.80882 | 0.80882 | 0 | 12 | 1 | 1 | 0.80882 | 10 | 0 | 0
143.55 | 49.94 | 49.94 | 0.026471 | 0.1 | 1 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.30882 | 0.30882 | 0 | 12 | 1 | 1 | 0.30882 | 10 | 0 | 0
143.6 | 50 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
143.65 | 50 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
143.7 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
143.75 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
143.8 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
143.85 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
143.9 | 49.92 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
143.95 | 49.92 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
144 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50.01 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
144.05 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
144.1 | 49.92 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
144.15 | 49.92 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
144.2 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
144.25 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
144.3 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
144.35 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
144.4 | 49.87 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
144.45 | 49.87 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
144.5 | 49.8 | 49.8 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
144.55 | 49.8 | 49.8 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
144.6 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
144.65 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
144.7 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
144.75 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
144.8 | 49.72 | 49.72 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
144.85 | 49.72 | 49.72 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
144.9 | 49.67 | 49.67 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
144.95 | 49.67 | 49.67 | 1 | 1 | 10 | 49.87 | 0.335 | 0.14412 | 1.4412 | 5.7206 | 5.7206 | 0 | 12 | 1 | 1 | 5.7206 | 10 | 0 | 0
145 | 49.65 | 49.65 | 1 | 1 | 10 | 49.87 | 0.335 | 0.24412 | 2.4412 | 6.2206 | 6.2206 | 0 | 12 | 1 | 1 | 6.2206 | 10 | 0 | 0
145.05 | 49.65 | 49.65 | 1 | 1 | 10 | 49.8 | 1 | 0.34412 | 3.4412 | 6.7206 | 6.7206 | 0 | 12 | 1 | 1 | 6.7206 | 10 | 0 | 0
145.1 | 49.59 | 49.59 | 1 | 1 | 10 | 49.8 | 1 | 0.44412 | 4.4412 | 7.2206 | 7.2206 | 0 | 12 | 1 | 1 | 7.2206 | 10 | 0 | 0
145.15 | 49.59 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.54412 | 5.4412 | 7.7206 | 7.7206 | 0 | 12 | 1 | 1 | 7.7206 | 10 | 0 | 0
145.2 | 49.66 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.64412 | 6.4412 | 8.2206 | 8.2206 | 0 | 12 | 1 | 1 | 8.2206 | 10 | 0 | 0
145.25 | 49.66 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.74412 | 7.4412 | 8.7206 | 8.7206 | 0 | 12 | 1 | 1 | 8.7206 | 10 | 0 | 0
145.3 | 49.63 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.84412 | 8.4412 | 9.2206 | 9.2206 | 0 | 12 | 1 | 1 | 9.2206 | 10 | 0 | 0
145.35 | 49.63 | 49.59 | 1 | 1 | 10 | 49.72 | 1 | 0.94412 | 9.4412 | 9.7206 | 9.7206 | 0 | 12 | 1 | 1 | 9.7206 | 10 | 0 | 0
145.4 | 49.61 | 49.59 | 1 | 1 | 10 | 49.72 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
145.45 | 49.61 | 49.59 | 1 | 1 | 10 | 49.67 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
145.5 | 49.54 | 49.54 | 1 | 1 | 10 | 49.67 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
145.55 | 49.54 | 49.54 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
145.6 | 49.46 | 49.46 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
145.65 | 49.46 | 49.46 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
145.7 | 49.45 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
145.75 | 49.45 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
145.8 | 49.51 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
145.85 | 49.51 | 49.45 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
145.9 | 49.5 | 49.45 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
145.95 | 49.5 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
146 | 49.54 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
146.05 | 49.54 | 49.45 | 1 | 1 | 10 | 49.54 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
146.1 | 49.59 | 49.45 | 1 | 1 | 10 | 49.59 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
146.15 | 49.59 | 49.45 | 1 | 1 | 10 | 49.59 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
146.2 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
146.25 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
146.3 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
146.35 | 49.61 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
146.4 | 49.53 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
146.45 | 49.53 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
146.5 | 49.54 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
146.55 | 49.54 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
146.6 | 49.61 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
146.65 | 49.61 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
146.7 | 49.66 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
146.75 | 49.66 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
146.8 | 49.64 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
146.85 | 49.64 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
146.9 | 49.69 | 49.53 | 1 | 1 | 10 | 49.69 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
146.95 | 49.69 | 49.53 | 1 | 1 | 10 | 49.69 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
147 | 49.74 | 49.53 | 1 | 1 | 10 | 49.74 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
147.05 | 49.74 | 49.54 | 1 | 1 | 10 | 49.74 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
147.1 | 49.78 | 49.54 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
147.15 | 49.78 | 49.61 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
147.2 | 49.82 | 49.61 | 1 | 1 | 10 | 49.82 | 0.81 | 0.81 | 8.1 | 9.05 | 9.05 | 0 | 12 | 1 | 1 | 9.05 | 10 | 0 | 0
147.25 | 49.82 | 49.64 | 1 | 1 | 10 | 49.82 | 0.81 | 0.81 | 8.1 | 9.05 | 9.05 | 0 | 12 | 1 | 1 | 9.05 | 10 | 0 | 0
147.3 | 49.86 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
147.35 | 49.86 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
147.4 | 49.84 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
147.45 | 49.84 | 49.69 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
147.5 | 49.91 | 49.69 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
147.55 | 49.91 | 49.74 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
147.6 | 49.97 | 49.74 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
147.65 | 49.97 | 49.78 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
147.7 | 50.03 | 49.78 | 1 | 1 | 10 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.9559 | 4.9559 | 0 | 12 | 1 | 1 | 4.9559 | 10 | 0 | 0
147.75 | 50.03 | 49.82 | 0.81 | 0.9 | 9 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.4559 | 4.4559 | 0 | 12 | 1 | 1 | 4.4559 | 10 | 0 | 0
147.8 | 50.05 | 49.82 | 0.81 | 0.81 | 8.1 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 3.9471 | 3.9471 | 0 | 12 | 1 | 1 | 3.9471 | 10 | 0 | 0
147.85 | 50.05 | 49.84 | 0.62 | 0.71 | 7.1 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 3.4471 | 3.4471 | 0 | 12 | 1 | 1 | 3.4471 | 10 | 0 | 0
147.9 | 50.01 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
147.95 | 50.01 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
148 | 49.95 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
148.05 | 49.95 | 49.91 | 0.044118 | 0.52 | 5.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.4971 | 2.4971 | 0 | 12 | 1 | 1 | 2.4971 | 10 | 0 | 0
148.1 | 49.99 | 49.91 | 0.044118 | 0.42 | 4.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 1.9971 | 1.9971 | 0 | 12 | 1 | 1 | 1.9971 | 10 | 0 | 0
148.15 | 49.99 | 49.95 | 0.020588 | 0.32 | 3.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 1.4971 | 1.4971 | 0 | 12 | 1 | 1 | 1.4971 | 10 | 0 | 0
148.2 | 49.92 | 49.92 | 0.038235 | 0.22 | 2.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.99706 | 0.99706 | 0 | 12 | 1 | 1 | 0.99706 | 10 | 0 | 0
148.25 | 49.92 | 49.92 | 0.038235 | 0.12 | 1.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.49706 | 0.49706 | 0 | 12 | 1 | 1 | 0.49706 | 10 | 0 | 0
148.3 | 49.97 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
148.35 | 49.97 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
148.4 | 50.02 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
148.45 | 50.02 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.17647 | 0.17647 | 0 | 12 | 1 | 1 | 0.17647 | 10 | 0 | 0
148.5 | 50.07 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
148.55 | 50.07 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
148.6 | 50.06 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
148.65 | 50.06 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
148.7 | 50.13 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
148.75 | 50.13 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
148.8 | 50.09 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
148.85 | 50.09 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6309 | -1.6309 | 0 | 12 | 1 | 1 | -1.6309 | 10 | 0 | 0
148.9 | 50.07 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6309 | -1.6309 | 0 | 12 | 1 | 1 | -1.6309 | 10 | 0 | 0
148.95 | 50.07 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6897 | -1.6897 | 0 | 12 | 1 | 1 | -1.6897 | 10 | 0 | 0
149 | 50.07 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6897 | -1.6897 | 0 | 12 | 1 | 1 | -1.6897 | 10 | 0 | 0
149.05 | 50.07 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.13 | -0.335 | -0.335 | -3.35 | -1.8074 | -1.8074 | 0 | 12 | 1 | 1 | -1.8074 | 10 | 0 | 0
149.1 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.13 | -0.335 | -0.335 | -3.35 | -1.7779 | -1.7779 | 0 | 12 | 1 | 1 | -1.7779 | 10 | 0 | 0
149.15 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.13 | -0.335 | -0.335 | -3.35 | -1.7779 | -1.7779 | 0 | 12 | 1 | 1 | -1.7779 | 10 | 0 | 0
149.2 | 50.01 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
149.25 | 50.01 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
149.3 | 50.07 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
149.35 | 50.07 | 50.01 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.235 | -2.35 | -1.175 | -1.175 | 0 | 12 | 1 | 1 | -1.175 | 10 | 0 | 0
149.4 | 50.05 | 50.01 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.135 | -1.35 | -0.675 | -0.675 | 0 | 12 | 1 | 1 | -0.675 | 10 | 0 | 0
149.45 | 50.05 | 50.01 | 0 | 0 | 0 | 50.07 | -0.032353 | -0.035 | -0.35 | -0.175 | -0.175 | 0 | 12 | 1 | 1 | -0.175 | 10 | 0 | 0
149.5 | 50.1 | 50.01 | 0 | 0 | 0 | 50.1 | -0.05 | -0.05 | -0.5 | -0.25 | -0.25 | 0 | 12 | 1 | 1 | -0.25 | 10 | 0 | 0
149.55 | 50.1 | 50.01 | 0 | 0 | 0 | 50.1 | -0.05 | -0.05 | -0.5 | -0.25 | -0.25 | 0 | 12 | 1 | 1 | -0.25 | 10 | 0 | 0
149.6 | 50.11 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
149.65 | 50.11 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
149.7 | 50.06 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
149.75 | 50.06 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
149.8 | 50.04 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
149.85 | 50.04 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
149.9 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
149.95 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
150 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
150.05 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
150.1 | 50.11 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
150.15 | 50.11 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
150.2 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
150.25 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
150.3 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
150.35 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
150.4 | 50.02 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.11 | -0.145 | -0.145 | -1.45 | -0.73971 | -0.73971 | 0 | 12 | 1 | 1 | -0.73971 | 10 | 0 | 0
150.45 | 50.02 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.11 | -0.145 | -0.145 | -1.45 | -0.73971 | -0.73971 | 0 | 12 | 1 | 1 | -0.73971 | 10 | 0 | 0
150.5 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
150.55 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
150.6 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
150.65 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
150.7 | 50.01 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
150.75 | 50.01 | 50 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.045 | -0.45 | -0.225 | -0.225 | 0 | 12 | 1 | 1 | -0.225 | 10 | 0 | 0
150.8 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
150.85 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
150.9 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
150.95 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
151 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.14706 | 0.14706 | 0 | 12 | 1 | 1 | 0.14706 | 10 | 0 | 0
151.05 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
151.1 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
151.15 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
151.2 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
151.25 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
151.3 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
151.35 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
151.4 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
151.45 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
151.5 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
151.55 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
151.6 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
151.65 | 50 | 50 | 0 | 0 | 0 | 50.01 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
151.7 | 49.5 | 49.5 | 1 | 1 | 10 | 50.01 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
151.75 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
151.8 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
151.85 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
151.9 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
151.95 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
152 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
152.05 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
152.1 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
152.15 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
152.2 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
152.25 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.1 | 1 | 5.5 | 5.5 | 0 | 12 | 1 | 1 | 5.5 | 10 | 0 | 0
152.3 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.2 | 2 | 6 | 6 | 0 | 12 | 1 | 1 | 6 | 10 | 0 | 0
152.35 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.3 | 3 | 6.5 | 6.5 | 0 | 12 | 1 | 1 | 6.5 | 10 | 0 | 0
152.4 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.4 | 4 | 7 | 7 | 0 | 12 | 1 | 1 | 7 | 10 | 0 | 0
152.45 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.5 | 5 | 7.5 | 7.5 | 0 | 12 | 1 | 1 | 7.5 | 10 | 0 | 0
152.5 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.6 | 6 | 8 | 8 | 0 | 12 | 1 | 1 | 8 | 10 | 0 | 0
152.55 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.7 | 7 | 8.5 | 8.5 | 0 | 12 | 1 | 1 | 8.5 | 10 | 0 | 0
152.6 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.8 | 8 | 9 | 9 | 0 | 12 | 1 | 1 | 9 | 10 | 0 | 0
152.65 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.9 | 9 | 9.5 | 9.5 | 0 | 12 | 1 | 1 | 9.5 | 10 | 0 | 0
152.7 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
152.75 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
152.8 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
152.85 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
152.9 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
152.95 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
153 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
153.05 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
153.1 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
153.15 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
153.2 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
153.25 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
153.3 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
153.35 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
153.4 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
153.45 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
153.5 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
153.55 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
153.6 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
153.65 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
153.7 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
153.75 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
153.8 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
153.85 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
153.9 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
153.95 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
154 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
154.05 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
154.1 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
154.15 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
154.2 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
154.25 | 50.5 | 50.5 | -1 | 0.9 | 9 | 50.5 | -1 | -1 | -10 | -0.5 | -0.5 | 0 | 12 | 1 | 1 | -0.5 | 10 | 0 | 0
154.3 | 50.5 | 50.5 | -1 | 0.8 | 8 | 50.5 | -1 | -1 | -10 | -1 | -1 | 0 | 12 | 1 | 1 | -1 | 10 | 0 | 0
154.35 | 50.5 | 50.5 | -1 | 0.7 | 7 | 50.5 | -1 | -1 | -10 | -1.5 | -1.5 | 0 | 12 | 1 | 1 | -1.5 | 10 | 0 | 0
154.4 | 50.5 | 50.5 | -1 | 0.6 | 6 | 50.5 | -1 | -1 | -10 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
154.45 | 50.5 | 50.5 | -1 | 0.5 | 5 | 50.5 | -1 | -1 | -10 | -2.5 | -2.5 | 0 | 12 | 1 | 1 | -2.5 | 10 | 0 | 0
154.5 | 50.5 | 50.5 | -1 | 0.4 | 4 | 50.5 | -1 | -1 | -10 | -3 | -3 | 0 | 12 | 1 | 1 | -3 | 10 | 0 | 0
154.55 | 50.5 | 50.5 | -1 | 0.3 | 3 | 50.5 | -1 | -1 | -10 | -3.5 | -3.5 | 0 | 12 | 1 | 1 | -3.5 | 10 | 0 | 0
154.6 | 50.5 | 50.5 | -1 | 0.2 | 2 | 50.5 | -1 | -1 | -10 | -4 | -4 | 0 | 12 | 1 | 1 | -4 | 10 | 0 | 0
154.65 | 50.5 | 50.5 | -1 | 0.1 | 1 | 50.5 | -1 | -1 | -10 | -4.5 | -4.5 | 0 | 12 | 1 | 1 | -4.5 | 10 | 0 | 0
154.7 | 50.5 | 50.5 | -1 | 0 | 0 | 50.5 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
154.75 | 50.5 | 50.5 | -1 | -0.1 | -1 | 50.5 | -1 | -1 | -10 | -5.5 | -5.5 | 0 | 12 | 1 | 1 | -5.5 | 10 | 0 | 0
154.8 | 50.5 | 50.5 | -1 | -0.2 | -2 | 50.5 | -1 | -1 | -10 | -6 | -6 | 0 | 12 | 1 | 1 | -6 | 10 | 0 | 0
154.85 | 50.5 | 50.5 | -1 | -0.3 | -3 | 50.5 | -1 | -1 | -10 | -6.5 | -6.5 | 0 | 12 | 1 | 1 | -6.5 | 10 | 0 | 0
154.9 | 50.5 | 50.5 | -1 | -0.4 | -4 | 50.5 | -1 | -1 | -10 | -7 | -7 | 0 | 12 | 1 | 1 | -7 | 10 | 0 | 0
154.95 | 50.5 | 50.5 | -1 | -0.5 | -5 | 50.5 | -1 | -1 | -10 | -7.5 | -7.5 | 0 | 12 | 1 | 1 | -7.5 | 10 | 0 | 0
155 | 50.5 | 50.5 | -1 | -0.6 | -6 | 50.5 | -1 | -1 | -10 | -8 | -8 | 0 | 12 | 1 | 1 | -8 | 10 | 0 | 0
155.05 | 50.5 | 50.5 | -1 | -0.7 | -7 | 50.5 | -1 | -1 | -10 | -8.5 | -8.5 | 0 | 12 | 1 | 1 | -8.5 | 10 | 0 | 0
155.1 | 50.5 | 50.5 | -1 | -0.8 | -8 | 50.5 | -1 | -1 | -10 | -9 | -9 | 0 | 12 | 1 | 1 | -9 | 10 | 0 | 0
155.15 | 50.5 | 50.5 | -1 | -0.9 | -9 | 50.5 | -1 | -1 | -10 | -9.5 | -9.5 | 0 | 12 | 1 | 1 | -9.5 | 10 | 0 | 0
155.2 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
155.25 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
155.3 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
155.35 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
155.4 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
155.45 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
155.5 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
155.55 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
155.6 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
155.65 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
155.7 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
155.75 | 50.47 | 50.47 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
155.8 | 50.45 | 50.45 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
155.85 | 50.42 | 50.42 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
155.9 | 50.4 | 50.4 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
155.95 | 50.37 | 50.37 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
156 | 50.35 | 50.35 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
156.05 | 50.32 | 50.32 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
156.1 | 50.29 | 50.29 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
156.15 | 50.27 | 50.27 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
156.2 | 50.24 | 50.24 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
156.25 | 50.22 | 50.22 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
156.3 | 50.19 | 50.19 | -0.905 | -0.905 | -9.05 | 50.47 | -1 | -1 | -10 | -9.525 | -9.525 | 0 | 12 | 1 | 1 | -9.525 | 10 | 0 | 0
156.35 | 50.17 | 50.17 | -0.715 | -0.715 | -7.15 | 50.45 | -1 | -1 | -10 | -8.575 | -8.575 | 0 | 12 | 1 | 1 | -8.575 | 10 | 0 | 0
156.4 | 50.14 | 50.14 | -0.43 | -0.43 | -4.3 | 50.42 | -1 | -1 | -10 | -7.15 | -7.15 | 0 | 12 | 1 | 1 | -7.15 | 10 | 0 | 0
156.45 | 50.12 | 50.12 | -0.24 | -0.24 | -2.4 | 50.4 | -1 | -1 | -10 | -6.2 | -6.2 | 0 | 12 | 1 | 1 | -6.2 | 10 | 0 | 0
156.5 | 50.09 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 50.37 | -1 | -1 | -10 | -5.2206 | -5.2206 | 0 | 12 | 1 | 1 | -5.2206 | 10 | 0 | 0
156.55 | 50.06 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.35 | -1 | -1 | -10 | -5.1324 | -5.1324 | 0 | 12 | 1 | 1 | -5.1324 | 10 | 0 | 0
156.6 | 50.04 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.32 | -1 | -1 | -10 | -5.0735 | -5.0735 | 0 | 12 | 1 | 1 | -5.0735 | 10 | 0 | 0
156.65 | 50.01 | 50.01 | 0 | 0 | 0 | 50.29 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
156.7 | 49.99 | 49.99 | 0 | 0 | 0 | 50.27 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
156.75 | 49.96 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.24 | -1 | -1 | -10 | -4.9265 | -4.9265 | 0 | 12 | 1 | 1 | -4.9265 | 10 | 0 | 0
156.8 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.22 | -1 | -1 | -10 | -4.8676 | -4.8676 | 0 | 12 | 1 | 1 | -4.8676 | 10 | 0 | 0
156.85 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.19 | -0.905 | -0.905 | -9.05 | -4.3044 | -4.3044 | 0 | 12 | 1 | 1 | -4.3044 | 10 | 0 | 0
156.9 | 49.88 | 49.88 | 0.24 | 0.24 | 2.4 | 50.17 | -0.715 | -0.805 | -8.05 | -2.825 | -2.825 | 0 | 12 | 1 | 1 | -2.825 | 10 | 0 | 0
156.95 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.14 | -0.43 | -0.705 | -7.05 | -1.375 | -1.375 | 0 | 12 | 1 | 1 | -1.375 | 10 | 0 | 0
157 | 49.83 | 49.83 | 0.715 | 0.715 | 7.15 | 50.12 | -0.24 | -0.605 | -6.05 | 0.55 | 0.55 | 0 | 12 | 1 | 1 | 0.55 | 10 | 0 | 0
157.05 | 49.81 | 49.81 | 0.905 | 0.905 | 9.05 | 50.09 | -0.044118 | -0.505 | -5.05 | 2 | 2 | 0 | 12 | 1 | 1 | 2 | 10 | 0 | 0
157.1 | 49.78 | 49.78 | 1 | 1 | 10 | 50.06 | -0.026471 | -0.405 | -4.05 | 2.975 | 2.975 | 0 | 12 | 1 | 1 | 2.975 | 10 | 0 | 0
157.15 | 49.76 | 49.76 | 1 | 1 | 10 | 50.04 | -0.014706 | -0.305 | -3.05 | 3.475 | 3.475 | 0 | 12 | 1 | 1 | 3.475 | 10 | 0 | 0
157.2 | 49.73 | 49.73 | 1 | 1 | 10 | 50.01 | 0 | -0.205 | -2.05 | 3.975 | 3.975 | 0 | 12 | 1 | 1 | 3.975 | 10 | 0 | 0
157.25 | 49.71 | 49.71 | 1 | 1 | 10 | 49.99 | 0 | -0.105 | -1.05 | 4.475 | 4.475 | 0 | 12 | 1 | 1 | 4.475 | 10 | 0 | 0
157.3 | 49.68 | 49.68 | 1 | 1 | 10 | 49.96 | 0.014706 | -0.005 | -0.05 | 4.975 | 4.975 | 0 | 12 | 1 | 1 | 4.975 | 10 | 0 | 0
157.35 | 49.65 | 49.65 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
157.4 | 49.63 | 49.63 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
157.45 | 49.6 | 49.6 | 1 | 1 | 10 | 49.88 | 0.24 | 0.14412 | 1.4412 | 5.7206 | 5.7206 | 0 | 12 | 1 | 1 | 5.7206 | 10 | 0 | 0
157.5 | 49.58 | 49.58 | 1 | 1 | 10 | 49.86 | 0.43 | 0.24412 | 2.4412 | 6.2206 | 6.2206 | 0 | 12 | 1 | 1 | 6.2206 | 10 | 0 | 0
157.55 | 49.55 | 49.55 | 1 | 1 | 10 | 49.83 | 0.715 | 0.34412 | 3.4412 | 6.7206 | 6.7206 | 0 | 12 | 1 | 1 | 6.7206 | 10 | 0 | 0
157.6 | 49.53 | 49.53 | 1 | 1 | 10 | 49.81 | 0.905 | 0.44412 | 4.4412 | 7.2206 | 7.2206 | 0 | 12 | 1 | 1 | 7.2206 | 10 | 0 | 0
157.65 | 49.5 | 49.5 | 1 | 1 | 10 | 49.78 | 1 | 0.54412 | 5.4412 | 7.7206 | 7.7206 | 0 | 12 | 1 | 1 | 7.7206 | 10 | 0 | 0
157.7 | 49.5 | 49.5 | 1 | 1 | 10 | 49.76 | 1 | 0.64412 | 6.4412 | 8.2206 | 8.2206 | 0 | 12 | 1 | 1 | 8.2206 | 10 | 0 | 0
157.75 | 49.53 | 49.5 | 1 | 1 | 10 | 49.73 | 1 | 0.74412 | 7.4412 | 8.7206 | 8.7206 | 0 | 12 | 1 | 1 | 8.7206 | 10 | 0 | 0
157.8 | 49.55 | 49.5 | 1 | 1 | 10 | 49.71 | 1 | 0.84412 | 8.4412 | 9.2206 | 9.2206 | 0 | 12 | 1 | 1 | 9.2206 | 10 | 0 | 0
157.85 | 49.58 | 49.5 | 1 | 1 | 10 | 49.68 | 1 | 0.94412 | 9.4412 | 9.7206 | 9.7206 | 0 | 12 | 1 | 1 | 9.7206 | 10 | 0 | 0
157.9 | 49.6 | 49.5 | 1 | 1 | 10 | 49.65 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
157.95 | 49.63 | 49.5 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
158 | 49.65 | 49.5 | 1 | 1 | 10 | 49.65 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
158.05 | 49.68 | 49.5 | 1 | 1 | 10 | 49.68 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
158.1 | 49.71 | 49.5 | 1 | 1 | 10 | 49.71 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
158.15 | 49.73 | 49.5 | 1 | 1 | 10 | 49.73 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
158.2 | 49.76 | 49.5 | 1 | 1 | 10 | 49.76 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
158.25 | 49.78 | 49.5 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
158.3 | 49.81 | 49.53 | 1 | 1 | 10 | 49.81 | 0.905 | 0.905 | 9.05 | 9.525 | 9.525 | 0 | 12 | 1 | 1 | 9.525 | 10 | 0 | 0
158.35 | 49.83 | 49.55 | 1 | 1 | 10 | 49.83 | 0.715 | 0.715 | 7.15 | 8.575 | 8.575 | 0 | 12 | 1 | 1 | 8.575 | 10 | 0 | 0
158.4 | 49.86 | 49.58 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
158.45 | 49.88 | 49.6 | 1 | 1 | 10 | 49.88 | 0.24 | 0.24 | 2.4 | 6.2 | 6.2 | 0 | 12 | 1 | 1 | 6.2 | 10 | 0 | 0
158.5 | 49.91 | 49.63 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
158.55 | 49.94 | 49.65 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
158.6 | 49.96 | 49.68 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
158.65 | 49.99 | 49.71 | 1 | 1 | 10 | 49.99 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
158.7 | 50.01 | 49.73 | 1 | 1 | 10 | 50.01 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
158.75 | 50.04 | 49.76 | 1 | 1 | 10 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 4.9265 | 4.9265 | 0 | 12 | 1 | 1 | 4.9265 | 10 | 0 | 0
158.8 | 50.06 | 49.78 | 1 | 1 | 10 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 4.8676 | 4.8676 | 0 | 12 | 1 | 1 | 4.8676 | 10 | 0 | 0
158.85 | 50.09 | 49.81 | 0.905 | 0.905 | 9.05 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 4.3044 | 4.3044 | 0 | 12 | 1 | 1 | 4.3044 | 10 | 0 | 0
158.9 | 50.12 | 49.83 | 0.715 | 0.805 | 8.05 | 50.12 | -0.24 | -0.24 | -2.4 | 2.825 | 2.825 | 0 | 12 | 1 | 1 | 2.825 | 10 | 0 | 0
158.95 | 50.14 | 49.86 | 0.43 | 0.705 | 7.05 | 50.14 | -0.43 | -0.43 | -4.3 | 1.375 | 1.375 | 0 | 12 | 1 | 1 | 1.375 | 10 | 0 | 0
159 | 50.17 | 49.88 | 0.24 | 0.605 | 6.05 | 50.17 | -0.715 | -0.715 | -7.15 | -0.55 | -0.55 | 0 | 12 | 1 | 1 | -0.55 | 10 | 0 | 0
159.05 | 50.19 | 49.91 | 0.044118 | 0.505 | 5.05 | 50.19 | -0.905 | -0.905 | -9.05 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
159.1 | 50.22 | 49.94 | 0.026471 | 0.405 | 4.05 | 50.22 | -1 | -1 | -10 | -2.975 | -2.975 | 0 | 12 | 1 | 1 | -2.975 | 10 | 0 | 0
159.15 | 50.24 | 49.96 | 0.014706 | 0.305 | 3.05 | 50.24 | -1 | -1 | -10 | -3.475 | -3.475 | 0 | 12 | 1 | 1 | -3.475 | 10 | 0 | 0
159.2 | 50.27 | 49.99 | 0 | 0.205 | 2.05 | 50.27 | -1 | -1 | -10 | -3.975 | -3.975 | 0 | 12 | 1 | 1 | -3.975 | 10 | 0 | 0
159.25 | 50.29 | 50.01 | 0 | 0.105 | 1.05 | 50.29 | -1 | -1 | -10 | -4.475 | -4.475 | 0 | 12 | 1 | 1 | -4.475 | 10 | 0 | 0
159.3 | 50.32 | 50.04 | -0.014706 | 0.005 | 0.05 | 50.32 | -1 | -1 | -10 | -4.975 | -4.975 | 0 | 12 | 1 | 1 | -4.975 | 10 | 0 | 0
159.35 | 50.35 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.35 | -1 | -1 | -10 | -5.1324 | -5.1324 | 0 | 12 | 1 | 1 | -5.1324 | 10 | 0 | 0
159.4 | 50.37 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 50.37 | -1 | -1 | -10 | -5.2206 | -5.2206 | 0 | 12 | 1 | 1 | -5.2206 | 10 | 0 | 0
159.45 | 50.4 | 50.12 | -0.24 | -0.14412 | -1.4412 | 50.4 | -1 | -1 | -10 | -5.7206 | -5.7206 | 0 | 12 | 1 | 1 | -5.7206 | 10 | 0 | 0
159.5 | 50.42 | 50.14 | -0.43 | -0.24412 | -2.4412 | 50.42 | -1 | -1 | -10 | -6.2206 | -6.2206 | 0 | 12 | 1 | 1 | -6.2206 | 10 | 0 | 0
159.55 | 50.45 | 50.17 | -0.715 | -0.34412 | -3.4412 | 50.45 | -1 | -1 | -10 | -6.7206 | -6.7206 | 0 | 12 | 1 | 1 | -6.7206 | 10 | 0 | 0
159.6 | 50.47 | 50.19 | -0.905 | -0.44412 | -4.4412 | 50.47 | -1 | -1 | -10 | -7.2206 | -7.2206 | 0 | 12 | 1 | 1 | -7.2206 | 10 | 0 | 0
159.65 | 50.5 | 50.22 | -1 | -0.54412 | -5.4412 | 50.5 | -1 | -1 | -10 | -7.7206 | -7.7206 | 0 | 12 | 1 | 1 | -7.7206 | 10 | 0 | 0
159.7 | 50.5 | 50.24 | -1 | -0.64412 | -6.4412 | 50.5 | -1 | -1 | -10 | -8.2206 | -8.2206 | 0 | 12 | 1 | 1 | -8.2206 | 10 | 0 | 0
159.75 | 50.47 | 50.27 | -1 | -0.74412 | -7.4412 | 50.5 | -1 | -1 | -10 | -8.7206 | -8.7206 | 0 | 12 | 1 | 1 | -8.7206 | 10 | 0 | 0
159.8 | 50.45 | 50.29 | -1 | -0.84412 | -8.4412 | 50.5 | -1 | -1 | -10 | -9.2206 | -9.2206 | 0 | 12 | 1 | 1 | -9.2206 | 10 | 0 | 0
159.85 | 50.42 | 50.32 | -1 | -0.94412 | -9.4412 | 50.5 | -1 | -1 | -10 | -9.7206 | -9.7206 | 0 | 12 | 1 | 1 | -9.7206 | 10 | 0 | 0
159.9 | 50.39 | 50.35 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
159.95 | 50.37 | 50.37 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
160 | 50.34 | 50.34 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
160.05 | 50.32 | 50.32 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
160.1 | 50.29 | 50.29 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
160.15 | 50.26 | 50.26 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
160.2 | 50.24 | 50.24 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
160.25 | 50.21 | 50.21 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
160.3 | 50.18 | 50.18 | -0.81 | -0.81 | -8.1 | 50.47 | -1 | -1 | -10 | -9.05 | -9.05 | 0 | 12 | 1 | 1 | -9.05 | 10 | 0 | 0
160.35 | 50.16 | 50.16 | -0.62 | -0.62 | -6.2 | 50.45 | -1 | -1 | -10 | -8.1 | -8.1 | 0 | 12 | 1 | 1 | -8.1 | 10 | 0 | 0
160.4 | 50.13 | 50.13 | -0.335 | -0.335 | -3.35 | 50.42 | -1 | -1 | -10 | -6.675 | -6.675 | 0 | 12 | 1 | 1 | -6.675 | 10 | 0 | 0
160.45 | 50.11 | 50.11 | -0.145 | -0.145 | -1.45 | 50.39 | -1 | -1 | -10 | -5.725 | -5.725 | 0 | 12 | 1 | 1 | -5.725 | 10 | 0 | 0
160.5 | 50.08 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 50.37 | -1 | -1 | -10 | -5.1912 | -5.1912 | 0 | 12 | 1 | 1 | -5.1912 | 10 | 0 | 0
160.55 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.34 | -1 | -1 | -10 | -5.1029 | -5.1029 | 0 | 12 | 1 | 1 | -5.1029 | 10 | 0 | 0
160.6 | 50.03 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 50.32 | -1 | -1 | -10 | -5.0441 | -5.0441 | 0 | 12 | 1 | 1 | -5.0441 | 10 | 0 | 0
160.65 | 50 | 50 | 0 | 0 | 0 | 50.29 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
160.7 | 50 | 50 | 0 | 0 | 0 | 50.26 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
160.75 | 50 | 50 | 0 | 0 | 0 | 50.24 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
160.8 | 50 | 50 | 0 | 0 | 0 | 50.21 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
160.85 | 50 | 50 | 0 | 0 | 0 | 50.18 | -0.81 | -0.9 | -9 | -4.5 | -4.5 | 0 | 12 | 1 | 1 | -4.5 | 10 | 0 | 0
160.9 | 50 | 50 | 0 | 0 | 0 | 50.16 | -0.62 | -0.8 | -8 | -4 | -4 | 0 | 12 | 1 | 1 | -4 | 10 | 0 | 0
160.95 | 50 | 50 | 0 | 0 | 0 | 50.13 | -0.335 | -0.7 | -7 | -3.5 | -3.5 | 0 | 12 | 1 | 1 | -3.5 | 10 | 0 | 0
161 | 50.01 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.6 | -6 | -3 | -3 | 0 | 12 | 1 | 1 | -3 | 10 | 0 | 0
161.05 | 50.01 | 50 | 0 | 0 | 0 | 50.08 | -0.038235 | -0.5 | -5 | -2.5 | -2.5 | 0 | 12 | 1 | 1 | -2.5 | 10 | 0 | 0
161.1 | 49.99 | 49.99 | 0 | 0 | 0 | 50.05 | -0.020588 | -0.4 | -4 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
161.15 | 49.99 | 49.99 | 0 | 0 | 0 | 50.03 | -0.0088235 | -0.3 | -3 | -1.5 | -1.5 | 0 | 12 | 1 | 1 | -1.5 | 10 | 0 | 0
161.2 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | -0.2 | -2 | -0.83824 | -0.83824 | 0 | 12 | 1 | 1 | -0.83824 | 10 | 0 | 0
161.25 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | -0.1 | -1 | -0.33824 | -0.33824 | 0 | 12 | 1 | 1 | -0.33824 | 10 | 0 | 0
161.3 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
161.35 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
161.4 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
161.45 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
161.5 | 49.89 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
161.55 | 49.89 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
161.6 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50.01 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
161.65 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
161.7 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
161.75 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 2.7868 | 2.7868 | 0 | 12 | 1 | 1 | 2.7868 | 10 | 0 | 0
161.8 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 2.7868 | 2.7868 | 0 | 12 | 1 | 1 | 2.7868 | 10 | 0 | 0
161.85 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 2.8456 | 2.8456 | 0 | 12 | 1 | 1 | 2.8456 | 10 | 0 | 0
161.9 | 49.94 | 49.85 | 0.525 | 0.525 | 5.25 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 2.7574 | 2.7574 | 0 | 12 | 1 | 1 | 2.7574 | 10 | 0 | 0
161.95 | 49.94 | 49.85 | 0.525 | 0.525 | 5.25 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 2.7574 | 2.7574 | 0 | 12 | 1 | 1 | 2.7574 | 10 | 0 | 0
162 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
162.05 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
162.1 | 49.93 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
162.15 | 49.93 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
162.2 | 49.96 | 49.85 | 0.525 | 0.525 | 5.25 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 2.6985 | 2.6985 | 0 | 12 | 1 | 1 | 2.6985 | 10 | 0 | 0
162.25 | 49.96 | 49.85 | 0.525 | 0.525 | 5.25 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 2.6985 | 2.6985 | 0 | 12 | 1 | 1 | 2.6985 | 10 | 0 | 0
162.3 | 49.99 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
162.35 | 49.99 | 49.91 | 0.044118 | 0.425 | 4.25 | 49.99 | 0 | 0 | 0 | 2.125 | 2.125 | 0 | 12 | 1 | 1 | 2.125 | 10 | 0 | 0
162.4 | 49.99 | 49.91 | 0.044118 | 0.325 | 3.25 | 49.99 | 0 | 0 | 0 | 1.625 | 1.625 | 0 | 12 | 1 | 1 | 1.625 | 10 | 0 | 0
162.45 | 49.99 | 49.93 | 0.032353 | 0.225 | 2.25 | 49.99 | 0 | 0 | 0 | 1.125 | 1.125 | 0 | 12 | 1 | 1 | 1.125 | 10 | 0 | 0
162.5 | 49.96 | 49.93 | 0.032353 | 0.125 | 1.25 | 49.99 | 0 | 0 | 0 | 0.625 | 0.625 | 0 | 12 | 1 | 1 | 0.625 | 10 | 0 | 0
162.55 | 49.96 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 49.99 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
162.6 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
162.65 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
162.7 | 50.05 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.058824 | 0.058824 | 0 | 12 | 1 | 1 | 0.058824 | 10 | 0 | 0
162.75 | 50.05 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
162.8 | 49.97 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
162.85 | 49.97 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
162.9 | 49.92 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
162.95 | 49.92 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
163 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
163.05 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
163.1 | 49.94 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
163.15 | 49.94 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
163.2 | 50.01 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
163.25 | 50.01 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
163.3 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
163.35 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
163.4 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
163.45 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
163.5 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
163.55 | 49.95 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
163.6 | 49.97 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
163.65 | 49.97 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
163.7 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
163.75 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
163.8 | 49.87 | 49.87 | 0.335 | 0.335 | 3.35 | 50.01 | 0 | 0 | 0 | 1.675 | 1.675 | 0 | 12 | 1 | 1 | 1.675 | 10 | 0 | 0
163.85 | 49.87 | 49.87 | 0.335 | 0.335 | 3.35 | 49.99 | 0 | 0 | 0 | 1.675 | 1.675 | 0 | 12 | 1 | 1 | 1.675 | 10 | 0 | 0
163.9 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
163.95 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 2.6691 | 2.6691 | 0 | 12 | 1 | 1 | 2.6691 | 10 | 0 | 0
164 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
164.05 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
164.1 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
164.15 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
164.2 | 49.84 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
164.25 | 49.84 | 49.79 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
164.3 | 49.89 | 49.79 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
164.35 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.12647 | 1.2647 | 5.6324 | 5.6324 | 0 | 12 | 1 | 1 | 5.6324 | 10 | 0 | 0
164.4 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.145 | 1.45 | 5.725 | 5.725 | 0 | 12 | 1 | 1 | 5.725 | 10 | 0 | 0
164.45 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.145 | 1.45 | 5.725 | 5.725 | 0 | 12 | 1 | 1 | 5.725 | 10 | 0 | 0
164.5 | 49.96 | 49.79 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
164.55 | 49.96 | 49.79 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
164.6 | 50.02 | 49.79 | 1 | 1 | 10 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 4.9853 | 4.9853 | 0 | 12 | 1 | 1 | 4.9853 | 10 | 0 | 0
164.65 | 50.02 | 49.79 | 1 | 1 | 10 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 4.9853 | 4.9853 | 0 | 12 | 1 | 1 | 4.9853 | 10 | 0 | 0
164.7 | 50.03 | 49.79 | 1 | 1 | 10 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.9559 | 4.9559 | 0 | 12 | 1 | 1 | 4.9559 | 10 | 0 | 0
164.75 | 50.03 | 49.84 | 0.62 | 0.9 | 9 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.4559 | 4.4559 | 0 | 12 | 1 | 1 | 4.4559 | 10 | 0 | 0
164.8 | 50.02 | 49.84 | 0.62 | 0.8 | 8 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 3.9559 | 3.9559 | 0 | 12 | 1 | 1 | 3.9559 | 10 | 0 | 0
164.85 | 50.02 | 49.89 | 0.145 | 0.7 | 7 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 3.4559 | 3.4559 | 0 | 12 | 1 | 1 | 3.4559 | 10 | 0 | 0
164.9 | 50.08 | 49.89 | 0.145 | 0.6 | 6 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 2.8088 | 2.8088 | 0 | 12 | 1 | 1 | 2.8088 | 10 | 0 | 0
164.95 | 50.08 | 49.89 | 0.145 | 0.5 | 5 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 2.3088 | 2.3088 | 0 | 12 | 1 | 1 | 2.3088 | 10 | 0 | 0
165 | 50.01 | 49.89 | 0.145 | 0.4 | 4 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 1.8088 | 1.8088 | 0 | 12 | 1 | 1 | 1.8088 | 10 | 0 | 0
165.05 | 50.01 | 49.96 | 0.014706 | 0.3 | 3 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 1.3088 | 1.3088 | 0 | 12 | 1 | 1 | 1.3088 | 10 | 0 | 0
165.1 | 49.94 | 49.94 | 0.026471 | 0.2 | 2 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.80882 | 0.80882 | 0 | 12 | 1 | 1 | 0.80882 | 10 | 0 | 0
165.15 | 49.94 | 49.94 | 0.026471 | 0.1 | 1 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.30882 | 0.30882 | 0 | 12 | 1 | 1 | 0.30882 | 10 | 0 | 0
165.2 | 50 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
165.25 | 50 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
165.3 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
165.35 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
165.4 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
165.45 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
165.5 | 49.92 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
165.55 | 49.92 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
165.6 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50.01 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
165.65 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
165.7 | 49.92 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
165.75 | 49.92 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
165.8 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
165.85 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
165.9 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
165.95 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
166 | 49.87 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
166.05 | 49.87 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
166.1 | 49.8 | 49.8 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
166.15 | 49.8 | 49.8 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
166.2 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
166.25 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
166.3 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
166.35 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
166.4 | 49.72 | 49.72 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
166.45 | 49.72 | 49.72 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
166.5 | 49.67 | 49.67 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
166.55 | 49.67 | 49.67 | 1 | 1 | 10 | 49.87 | 0.335 | 0.14412 | 1.4412 | 5.7206 | 5.7206 | 0 | 12 | 1 | 1 | 5.7206 | 10 | 0 | 0
166.6 | 49.65 | 49.65 | 1 | 1 | 10 | 49.87 | 0.335 | 0.24412 | 2.4412 | 6.2206 | 6.2206 | 0 | 12 | 1 | 1 | 6.2206 | 10 | 0 | 0
166.65 | 49.65 | 49.65 | 1 | 1 | 10 | 49.8 | 1 | 0.34412 | 3.4412 | 6.7206 | 6.7206 | 0 | 12 | 1 | 1 | 6.7206 | 10 | 0 | 0
166.7 | 49.59 | 49.59 | 1 | 1 | 10 | 49.8 | 1 | 0.44412 | 4.4412 | 7.2206 | 7.2206 | 0 | 12 | 1 | 1 | 7.2206 | 10 | 0 | 0
166.75 | 49.59 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.54412 | 5.4412 | 7.7206 | 7.7206 | 0 | 12 | 1 | 1 | 7.7206 | 10 | 0 | 0
166.8 | 49.66 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.64412 | 6.4412 | 8.2206 | 8.2206 | 0 | 12 | 1 | 1 | 8.2206 | 10 | 0 | 0
166.85 | 49.66 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.74412 | 7.4412 | 8.7206 | 8.7206 | 0 | 12 | 1 | 1 | 8.7206 | 10 | 0 | 0
166.9 | 49.63 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.84412 | 8.4412 | 9.2206 | 9.2206 | 0 | 12 | 1 | 1 | 9.2206 | 10 | 0 | 0
166.95 | 49.63 | 49.59 | 1 | 1 | 10 | 49.72 | 1 | 0.94412 | 9.4412 | 9.7206 | 9.7206 | 0 | 12 | 1 | 1 | 9.7206 | 10 | 0 | 0
167 | 49.61 | 49.59 | 1 | 1 | 10 | 49.72 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
167.05 | 49.61 | 49.59 | 1 | 1 | 10 | 49.67 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
167.1 | 49.54 | 49.54 | 1 | 1 | 10 | 49.67 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
167.15 | 49.54 | 49.54 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
167.2 | 49.46 | 49.46 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
167.25 | 49.46 | 49.46 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
167.3 | 49.45 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
167.35 | 49.45 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
167.4 | 49.51 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
167.45 | 49.51 | 49.45 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
167.5 | 49.5 | 49.45 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
167.55 | 49.5 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
167.6 | 49.54 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
167.65 | 49.54 | 49.45 | 1 | 1 | 10 | 49.54 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
167.7 | 49.59 | 49.45 | 1 | 1 | 10 | 49.59 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
167.75 | 49.59 | 49.45 | 1 | 1 | 10 | 49.59 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
167.8 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
167.85 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
167.9 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
167.95 | 49.61 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
168 | 49.53 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
168.05 | 49.53 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
168.1 | 49.54 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
168.15 | 49.54 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
168.2 | 49.61 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
168.25 | 49.61 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
168.3 | 49.66 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
168.35 | 49.66 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
168.4 | 49.64 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
168.45 | 49.64 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
168.5 | 49.69 | 49.53 | 1 | 1 | 10 | 49.69 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
168.55 | 49.69 | 49.53 | 1 | 1 | 10 | 49.69 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
168.6 | 49.74 | 49.53 | 1 | 1 | 10 | 49.74 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
168.65 | 49.74 | 49.54 | 1 | 1 | 10 | 49.74 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
168.7 | 49.78 | 49.54 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
168.75 | 49.78 | 49.61 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
168.8 | 49.82 | 49.61 | 1 | 1 | 10 | 49.82 | 0.81 | 0.81 | 8.1 | 9.05 | 9.05 | 0 | 12 | 1 | 1 | 9.05 | 10 | 0 | 0
168.85 | 49.82 | 49.64 | 1 | 1 | 10 | 49.82 | 0.81 | 0.81 | 8.1 | 9.05 | 9.05 | 0 | 12 | 1 | 1 | 9.05 | 10 | 0 | 0
168.9 | 49.86 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
168.95 | 49.86 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
169 | 49.84 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
169.05 | 49.84 | 49.69 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
169.1 | 49.91 | 49.69 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
169.15 | 49.91 | 49.74 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
169.2 | 49.97 | 49.74 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
169.25 | 49.97 | 49.78 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
169.3 | 50.03 | 49.78 | 1 | 1 | 10 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.9559 | 4.9559 | 0 | 12 | 1 | 1 | 4.9559 | 10 | 0 | 0
169.35 | 50.03 | 49.82 | 0.81 | 0.9 | 9 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.4559 | 4.4559 | 0 | 12 | 1 | 1 | 4.4559 | 10 | 0 | 0
169.4 | 50.05 | 49.82 | 0.81 | 0.81 | 8.1 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 3.9471 | 3.9471 | 0 | 12 | 1 | 1 | 3.9471 | 10 | 0 | 0
169.45 | 50.05 | 49.84 | 0.62 | 0.71 | 7.1 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 3.4471 | 3.4471 | 0 | 12 | 1 | 1 | 3.4471 | 10 | 0 | 0
169.5 | 50.01 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
169.55 | 50.01 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
169.6 | 49.95 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
169.65 | 49.95 | 49.91 | 0.044118 | 0.52 | 5.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.4971 | 2.4971 | 0 | 12 | 1 | 1 | 2.4971 | 10 | 0 | 0
169.7 | 49.99 | 49.91 | 0.044118 | 0.42 | 4.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 1.9971 | 1.9971 | 0 | 12 | 1 | 1 | 1.9971 | 10 | 0 | 0
169.75 | 49.99 | 49.95 | 0.020588 | 0.32 | 3.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 1.4971 | 1.4971 | 0 | 12 | 1 | 1 | 1.4971 | 10 | 0 | 0
169.8 | 49.92 | 49.92 | 0.038235 | 0.22 | 2.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.99706 | 0.99706 | 0 | 12 | 1 | 1 | 0.99706 | 10 | 0 | 0
169.85 | 49.92 | 49.92 | 0.038235 | 0.12 | 1.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.49706 | 0.49706 | 0 | 12 | 1 | 1 | 0.49706 | 10 | 0 | 0
169.9 | 49.97 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
169.95 | 49.97 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
170 | 50.02 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
170.05 | 50.02 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.17647 | 0.17647 | 0 | 12 | 1 | 1 | 0.17647 | 10 | 0 | 0
170.1 | 50.07 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
170.15 | 50.07 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
170.2 | 50.06 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
170.25 | 50.06 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
170.3 | 50.13 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
170.35 | 50.13 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
170.4 | 50.09 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
170.45 | 50.09 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6309 | -1.6309 | 0 | 12 | 1 | 1 | -1.6309 | 10 | 0 | 0
170.5 | 50.07 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6309 | -1.6309 | 0 | 12 | 1 | 1 | -1.6309 | 10 | 0 | 0
170.55 | 50.07 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6897 | -1.6897 | 0 | 12 | 1 | 1 | -1.6897 | 10 | 0 | 0
170.6 | 50.07 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6897 | -1.6897 | 0 | 12 | 1 | 1 | -1.6897 | 10 | 0 | 0
170.65 | 50.07 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.13 | -0.335 | -0.335 | -3.35 | -1.8074 | -1.8074 | 0 | 12 | 1 | 1 | -1.8074 | 10 | 0 | 0
170.7 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.13 | -0.335 | -0.335 | -3.35 | -1.7779 | -1.7779 | 0 | 12 | 1 | 1 | -1.7779 | 10 | 0 | 0
170.75 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.13 | -0.335 | -0.335 | -3.35 | -1.7779 | -1.7779 | 0 | 12 | 1 | 1 | -1.7779 | 10 | 0 | 0
170.8 | 50.01 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
170.85 | 50.01 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
170.9 | 50.07 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
170.95 | 50.07 | 50.01 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.235 | -2.35 | -1.175 | -1.175 | 0 | 12 | 1 | 1 | -1.175 | 10 | 0 | 0
171 | 50.05 | 50.01 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.135 | -1.35 | -0.675 | -0.675 | 0 | 12 | 1 | 1 | -0.675 | 10 | 0 | 0
171.05 | 50.05 | 50.01 | 0 | 0 | 0 | 50.07 | -0.032353 | -0.035 | -0.35 | -0.175 | -0.175 | 0 | 12 | 1 | 1 | -0.175 | 10 | 0 | 0
171.1 | 50.1 | 50.01 | 0 | 0 | 0 | 50.1 | -0.05 | -0.05 | -0.5 | -0.25 | -0.25 | 0 | 12 | 1 | 1 | -0.25 | 10 | 0 | 0
171.15 | 50.1 | 50.01 | 0 | 0 | 0 | 50.1 | -0.05 | -0.05 | -0.5 | -0.25 | -0.25 | 0 | 12 | 1 | 1 | -0.25 | 10 | 0 | 0
171.2 | 50.11 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
171.25 | 50.11 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
171.3 | 50.06 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
171.35 | 50.06 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
171.4 | 50.04 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
171.45 | 50.04 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
171.5 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
171.55 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
171.6 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
171.65 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
171.7 | 50.11 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
171.75 | 50.11 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
171.8 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
171.85 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
171.9 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
171.95 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
172 | 50.02 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.11 | -0.145 | -0.145 | -1.45 | -0.73971 | -0.73971 | 0 | 12 | 1 | 1 | -0.73971 | 10 | 0 | 0
172.05 | 50.02 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.11 | -0.145 | -0.145 | -1.45 | -0.73971 | -0.73971 | 0 | 12 | 1 | 1 | -0.73971 | 10 | 0 | 0
172.1 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
172.15 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
172.2 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
172.25 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
172.3 | 50.01 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
172.35 | 50.01 | 50 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.045 | -0.45 | -0.225 | -0.225 | 0 | 12 | 1 | 1 | -0.225 | 10 | 0 | 0
172.4 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
172.45 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
172.5 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
172.55 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
172.6 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.14706 | 0.14706 | 0 | 12 | 1 | 1 | 0.14706 | 10 | 0 | 0
172.65 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
172.7 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
172.75 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
172.8 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
172.85 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
172.9 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
172.95 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
173 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
173.05 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
173.1 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
173.15 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
173.2 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
173.25 | 50 | 50 | 0 | 0 | 0 | 50.01 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
173.3 | 49.5 | 49.5 | 1 | 1 | 10 | 50.01 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
173.35 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
173.4 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
173.45 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
173.5 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
173.55 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
173.6 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
173.65 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
173.7 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
173.75 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
173.8 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
173.85 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.1 | 1 | 5.5 | 5.5 | 0 | 12 | 1 | 1 | 5.5 | 10 | 0 | 0
173.9 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.2 | 2 | 6 | 6 | 0 | 12 | 1 | 1 | 6 | 10 | 0 | 0
173.95 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.3 | 3 | 6.5 | 6.5 | 0 | 12 | 1 | 1 | 6.5 | 10 | 0 | 0
174 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.4 | 4 | 7 | 7 | 0 | 12 | 1 | 1 | 7 | 10 | 0 | 0
174.05 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.5 | 5 | 7.5 | 7.5 | 0 | 12 | 1 | 1 | 7.5 | 10 | 0 | 0
174.1 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.6 | 6 | 8 | 8 | 0 | 12 | 1 | 1 | 8 | 10 | 0 | 0
174.15 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.7 | 7 | 8.5 | 8.5 | 0 | 12 | 1 | 1 | 8.5 | 10 | 0 | 0
174.2 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.8 | 8 | 9 | 9 | 0 | 12 | 1 | 1 | 9 | 10 | 0 | 0
174.25 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.9 | 9 | 9.5 | 9.5 | 0 | 12 | 1 | 1 | 9.5 | 10 | 0 | 0
174.3 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
174.35 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
174.4 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
174.45 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
174.5 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
174.55 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
174.6 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
174.65 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
174.7 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
174.75 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
174.8 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
174.85 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
174.9 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
174.95 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
175 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
175.05 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
175.1 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
175.15 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
175.2 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
175.25 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
175.3 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
175.35 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
175.4 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
175.45 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
175.5 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
175.55 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
175.6 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
175.65 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
175.7 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
175.75 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
175.8 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
175.85 | 50.5 | 50.5 | -1 | 0.9 | 9 | 50.5 | -1 | -1 | -10 | -0.5 | -0.5 | 0 | 12 | 1 | 1 | -0.5 | 10 | 0 | 0
175.9 | 50.5 | 50.5 | -1 | 0.8 | 8 | 50.5 | -1 | -1 | -10 | -1 | -1 | 0 | 12 | 1 | 1 | -1 | 10 | 0 | 0
175.95 | 50.5 | 50.5 | -1 | 0.7 | 7 | 50.5 | -1 | -1 | -10 | -1.5 | -1.5 | 0 | 12 | 1 | 1 | -1.5 | 10 | 0 | 0
176 | 50.5 | 50.5 | -1 | 0.6 | 6 | 50.5 | -1 | -1 | -10 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
176.05 | 50.5 | 50.5 | -1 | 0.5 | 5 | 50.5 | -1 | -1 | -10 | -2.5 | -2.5 | 0 | 12 | 1 | 1 | -2.5 | 10 | 0 | 0
176.1 | 50.5 | 50.5 | -1 | 0.4 | 4 | 50.5 | -1 | -1 | -10 | -3 | -3 | 0 | 12 | 1 | 1 | -3 | 10 | 0 | 0
176.15 | 50.5 | 50.5 | -1 | 0.3 | 3 | 50.5 | -1 | -1 | -10 | -3.5 | -3.5 | 0 | 12 | 1 | 1 | -3.5 | 10 | 0 | 0
176.2 | 50.5 | 50.5 | -1 | 0.2 | 2 | 50.5 | -1 | -1 | -10 | -4 | -4 | 0 | 12 | 1 | 1 | -4 | 10 | 0 | 0
176.25 | 50.5 | 50.5 | -1 | 0.1 | 1 | 50.5 | -1 | -1 | -10 | -4.5 | -4.5 | 0 | 12 | 1 | 1 | -4.5 | 10 | 0 | 0
176.3 | 50.5 | 50.5 | -1 | 0 | 0 | 50.5 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
176.35 | 50.5 | 50.5 | -1 | -0.1 | -1 | 50.5 | -1 | -1 | -10 | -5.5 | -5.5 | 0 | 12 | 1 | 1 | -5.5 | 10 | 0 | 0
176.4 | 50.5 | 50.5 | -1 | -0.2 | -2 | 50.5 | -1 | -1 | -10 | -6 | -6 | 0 | 12 | 1 | 1 | -6 | 10 | 0 | 0
176.45 | 50.5 | 50.5 | -1 | -0.3 | -3 | 50.5 | -1 | -1 | -10 | -6.5 | -6.5 | 0 | 12 | 1 | 1 | -6.5 | 10 | 0 | 0
176.5 | 50.5 | 50.5 | -1 | -0.4 | -4 | 50.5 | -1 | -1 | -10 | -7 | -7 | 0 | 12 | 1 | 1 | -7 | 10 | 0 | 0
176.55 | 50.5 | 50.5 | -1 | -0.5 | -5 | 50.5 | -1 | -1 | -10 | -7.5 | -7.5 | 0 | 12 | 1 | 1 | -7.5 | 10 | 0 | 0
176.6 | 50.5 | 50.5 | -1 | -0.6 | -6 | 50.5 | -1 | -1 | -10 | -8 | -8 | 0 | 12 | 1 | 1 | -8 | 10 | 0 | 0
176.65 | 50.5 | 50.5 | -1 | -0.7 | -7 | 50.5 | -1 | -1 | -10 | -8.5 | -8.5 | 0 | 12 | 1 | 1 | -8.5 | 10 | 0 | 0
176.7 | 50.5 | 50.5 | -1 | -0.8 | -8 | 50.5 | -1 | -1 | -10 | -9 | -9 | 0 | 12 | 1 | 1 | -9 | 10 | 0 | 0
176.75 | 50.5 | 50.5 | -1 | -0.9 | -9 | 50.5 | -1 | -1 | -10 | -9.5 | -9.5 | 0 | 12 | 1 | 1 | -9.5 | 10 | 0 | 0
176.8 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
176.85 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
176.9 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
176.95 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
177 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
177.05 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
177.1 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
177.15 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
177.2 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
177.25 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
177.3 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
177.35 | 50.47 | 50.47 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
177.4 | 50.45 | 50.45 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
177.45 | 50.42 | 50.42 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
177.5 | 50.4 | 50.4 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
177.55 | 50.37 | 50.37 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
177.6 | 50.35 | 50.35 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
177.65 | 50.32 | 50.32 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
177.7 | 50.29 | 50.29 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
177.75 | 50.27 | 50.27 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
177.8 | 50.24 | 50.24 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
177.85 | 50.22 | 50.22 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
177.9 | 50.19 | 50.19 | -0.905 | -0.905 | -9.05 | 50.47 | -1 | -1 | -10 | -9.525 | -9.525 | 0 | 12 | 1 | 1 | -9.525 | 10 | 0 | 0
177.95 | 50.17 | 50.17 | -0.715 | -0.715 | -7.15 | 50.45 | -1 | -1 | -10 | -8.575 | -8.575 | 0 | 12 | 1 | 1 | -8.575 | 10 | 0 | 0
178 | 50.14 | 50.14 | -0.43 | -0.43 | -4.3 | 50.42 | -1 | -1 | -10 | -7.15 | -7.15 | 0 | 12 | 1 | 1 | -7.15 | 10 | 0 | 0
178.05 | 50.12 | 50.12 | -0.24 | -0.24 | -2.4 | 50.4 | -1 | -1 | -10 | -6.2 | -6.2 | 0 | 12 | 1 | 1 | -6.2 | 10 | 0 | 0
178.1 | 50.09 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 50.37 | -1 | -1 | -10 | -5.2206 | -5.2206 | 0 | 12 | 1 | 1 | -5.2206 | 10 | 0 | 0
178.15 | 50.06 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.35 | -1 | -1 | -10 | -5.1324 | -5.1324 | 0 | 12 | 1 | 1 | -5.1324 | 10 | 0 | 0
178.2 | 50.04 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.32 | -1 | -1 | -10 | -5.0735 | -5.0735 | 0 | 12 | 1 | 1 | -5.0735 | 10 | 0 | 0
178.25 | 50.01 | 50.01 | 0 | 0 | 0 | 50.29 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
178.3 | 49.99 | 49.99 | 0 | 0 | 0 | 50.27 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
178.35 | 49.96 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.24 | -1 | -1 | -10 | -4.9265 | -4.9265 | 0 | 12 | 1 | 1 | -4.9265 | 10 | 0 | 0
178.4 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.22 | -1 | -1 | -10 | -4.8676 | -4.8676 | 0 | 12 | 1 | 1 | -4.8676 | 10 | 0 | 0
178.45 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.19 | -0.905 | -0.905 | -9.05 | -4.3044 | -4.3044 | 0 | 12 | 1 | 1 | -4.3044 | 10 | 0 | 0
178.5 | 49.88 | 49.88 | 0.24 | 0.24 | 2.4 | 50.17 | -0.715 | -0.805 | -8.05 | -2.825 | -2.825 | 0 | 12 | 1 | 1 | -2.825 | 10 | 0 | 0
178.55 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.14 | -0.43 | -0.705 | -7.05 | -1.375 | -1.375 | 0 | 12 | 1 | 1 | -1.375 | 10 | 0 | 0
178.6 | 49.83 | 49.83 | 0.715 | 0.715 | 7.15 | 50.12 | -0.24 | -0.605 | -6.05 | 0.55 | 0.55 | 0 | 12 | 1 | 1 | 0.55 | 10 | 0 | 0
178.65 | 49.81 | 49.81 | 0.905 | 0.905 | 9.05 | 50.09 | -0.044118 | -0.505 | -5.05 | 2 | 2 | 0 | 12 | 1 | 1 | 2 | 10 | 0 | 0
178.7 | 49.78 | 49.78 | 1 | 1 | 10 | 50.06 | -0.026471 | -0.405 | -4.05 | 2.975 | 2.975 | 0 | 12 | 1 | 1 | 2.975 | 10 | 0 | 0
178.75 | 49.76 | 49.76 | 1 | 1 | 10 | 50.04 | -0.014706 | -0.305 | -3.05 | 3.475 | 3.475 | 0 | 12 | 1 | 1 | 3.475 | 10 | 0 | 0
178.8 | 49.73 | 49.73 | 1 | 1 | 10 | 50.01 | 0 | -0.205 | -2.05 | 3.975 | 3.975 | 0 | 12 | 1 | 1 | 3.975 | 10 | 0 | 0
178.85 | 49.71 | 49.71 | 1 | 1 | 10 | 49.99 | 0 | -0.105 | -1.05 | 4.475 | 4.475 | 0 | 12 | 1 | 1 | 4.475 | 10 | 0 | 0
178.9 | 49.68 | 49.68 | 1 | 1 | 10 | 49.96 | 0.014706 | -0.005 | -0.05 | 4.975 | 4.975 | 0 | 12 | 1 | 1 | 4.975 | 10 | 0 | 0
178.95 | 49.65 | 49.65 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
179 | 49.63 | 49.63 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
179.05 | 49.6 | 49.6 | 1 | 1 | 10 | 49.88 | 0.24 | 0.14412 | 1.4412 | 5.7206 | 5.7206 | 0 | 12 | 1 | 1 | 5.7206 | 10 | 0 | 0
179.1 | 49.58 | 49.58 | 1 | 1 | 10 | 49.86 | 0.43 | 0.24412 | 2.4412 | 6.2206 | 6.2206 | 0 | 12 | 1 | 1 | 6.2206 | 10 | 0 | 0
179.15 | 49.55 | 49.55 | 1 | 1 | 10 | 49.83 | 0.715 | 0.34412 | 3.4412 | 6.7206 | 6.7206 | 0 | 12 | 1 | 1 | 6.7206 | 10 | 0 | 0
179.2 | 49.53 | 49.53 | 1 | 1 | 10 | 49.81 | 0.905 | 0.44412 | 4.4412 | 7.2206 | 7.2206 | 0 | 12 | 1 | 1 | 7.2206 | 10 | 0 | 0
179.25 | 49.5 | 49.5 | 1 | 1 | 10 | 49.78 | 1 | 0.54412 | 5.4412 | 7.7206 | 7.7206 | 0 | 12 | 1 | 1 | 7.7206 | 10 | 0 | 0
179.3 | 49.5 | 49.5 | 1 | 1 | 10 | 49.76 | 1 | 0.64412 | 6.4412 | 8.2206 | 8.2206 | 0 | 12 | 1 | 1 | 8.2206 | 10 | 0 | 0
179.35 | 49.53 | 49.5 | 1 | 1 | 10 | 49.73 | 1 | 0.74412 | 7.4412 | 8.7206 | 8.7206 | 0 | 12 | 1 | 1 | 8.7206 | 10 | 0 | 0
179.4 | 49.55 | 49.5 | 1 | 1 | 10 | 49.71 | 1 | 0.84412 | 8.4412 | 9.2206 | 9.2206 | 0 | 12 | 1 | 1 | 9.2206 | 10 | 0 | 0
179.45 | 49.58 | 49.5 | 1 | 1 | 10 | 49.68 | 1 | 0.94412 | 9.4412 | 9.7206 | 9.7206 | 0 | 12 | 1 | 1 | 9.7206 | 10 | 0 | 0
179.5 | 49.6 | 49.5 | 1 | 1 | 10 | 49.65 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
179.55 | 49.63 | 49.5 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
179.6 | 49.65 | 49.5 | 1 | 1 | 10 | 49.65 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
179.65 | 49.68 | 49.5 | 1 | 1 | 10 | 49.68 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
179.7 | 49.71 | 49.5 | 1 | 1 | 10 | 49.71 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
179.75 | 49.73 | 49.5 | 1 | 1 | 10 | 49.73 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
179.8 | 49.76 | 49.5 | 1 | 1 | 10 | 49.76 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
179.85 | 49.78 | 49.5 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
179.9 | 49.81 | 49.53 | 1 | 1 | 10 | 49.81 | 0.905 | 0.905 | 9.05 | 9.525 | 9.525 | 0 | 12 | 1 | 1 | 9.525 | 10 | 0 | 0
179.95 | 49.83 | 49.55 | 1 | 1 | 10 | 49.83 | 0.715 | 0.715 | 7.15 | 8.575 | 8.575 | 0 | 12 | 1 | 1 | 8.575 | 10 | 0 | 0
180 | 49.86 | 49.58 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
180.05 | 49.88 | 49.6 | 1 | 1 | 10 | 49.88 | 0.24 | 0.24 | 2.4 | 6.2 | 6.2 | 0 | 12 | 1 | 1 | 6.2 | 10 | 0 | 0
180.1 | 49.91 | 49.63 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
180.15 | 49.94 | 49.65 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
180.2 | 49.96 | 49.68 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
180.25 | 49.99 | 49.71 | 1 | 1 | 10 | 49.99 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
180.3 | 50.01 | 49.73 | 1 | 1 | 10 | 50.01 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
180.35 | 50.04 | 49.76 | 1 | 1 | 10 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 4.9265 | 4.9265 | 0 | 12 | 1 | 1 | 4.9265 | 10 | 0 | 0
180.4 | 50.06 | 49.78 | 1 | 1 | 10 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 4.8676 | 4.8676 | 0 | 12 | 1 | 1 | 4.8676 | 10 | 0 | 0
180.45 | 50.09 | 49.81 | 0.905 | 0.905 | 9.05 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 4.3044 | 4.3044 | 0 | 12 | 1 | 1 | 4.3044 | 10 | 0 | 0
180.5 | 50.12 | 49.83 | 0.715 | 0.805 | 8.05 | 50.12 | -0.24 | -0.24 | -2.4 | 2.825 | 2.825 | 0 | 12 | 1 | 1 | 2.825 | 10 | 0 | 0
180.55 | 50.14 | 49.86 | 0.43 | 0.705 | 7.05 | 50.14 | -0.43 | -0.43 | -4.3 | 1.375 | 1.375 | 0 | 12 | 1 | 1 | 1.375 | 10 | 0 | 0
180.6 | 50.17 | 49.88 | 0.24 | 0.605 | 6.05 | 50.17 | -0.715 | -0.715 | -7.15 | -0.55 | -0.55 | 0 | 12 | 1 | 1 | -0.55 | 10 | 0 | 0
180.65 | 50.19 | 49.91 | 0.044118 | 0.505 | 5.05 | 50.19 | -0.905 | -0.905 | -9.05 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
180.7 | 50.22 | 49.94 | 0.026471 | 0.405 | 4.05 | 50.22 | -1 | -1 | -10 | -2.975 | -2.975 | 0 | 12 | 1 | 1 | -2.975 | 10 | 0 | 0
180.75 | 50.24 | 49.96 | 0.014706 | 0.305 | 3.05 | 50.24 | -1 | -1 | -10 | -3.475 | -3.475 | 0 | 12 | 1 | 1 | -3.475 | 10 | 0 | 0
180.8 | 50.27 | 49.99 | 0 | 0.205 | 2.05 | 50.27 | -1 | -1 | -10 | -3.975 | -3.975 | 0 | 12 | 1 | 1 | -3.975 | 10 | 0 | 0
180.85 | 50.29 | 50.01 | 0 | 0.105 | 1.05 | 50.29 | -1 | -1 | -10 | -4.475 | -4.475 | 0 | 12 | 1 | 1 | -4.475 | 10 | 0 | 0
180.9 | 50.32 | 50.04 | -0.014706 | 0.005 | 0.05 | 50.32 | -1 | -1 | -10 | -4.975 | -4.975 | 0 | 12 | 1 | 1 | -4.975 | 10 | 0 | 0
180.95 | 50.35 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.35 | -1 | -1 | -10 | -5.1324 | -5.1324 | 0 | 12 | 1 | 1 | -5.1324 | 10 | 0 | 0
181 | 50.37 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 50.37 | -1 | -1 | -10 | -5.2206 | -5.2206 | 0 | 12 | 1 | 1 | -5.2206 | 10 | 0 | 0
181.05 | 50.4 | 50.12 | -0.24 | -0.14412 | -1.4412 | 50.4 | -1 | -1 | -10 | -5.7206 | -5.7206 | 0 | 12 | 1 | 1 | -5.7206 | 10 | 0 | 0
181.1 | 50.42 | 50.14 | -0.43 | -0.24412 | -2.4412 | 50.42 | -1 | -1 | -10 | -6.2206 | -6.2206 | 0 | 12 | 1 | 1 | -6.2206 | 10 | 0 | 0
181.15 | 50.45 | 50.17 | -0.715 | -0.34412 | -3.4412 | 50.45 | -1 | -1 | -10 | -6.7206 | -6.7206 | 0 | 12 | 1 | 1 | -6.7206 | 10 | 0 | 0
181.2 | 50.47 | 50.19 | -0.905 | -0.44412 | -4.4412 | 50.47 | -1 | -1 | -10 | -7.2206 | -7.2206 | 0 | 12 | 1 | 1 | -7.2206 | 10 | 0 | 0
181.25 | 50.5 | 50.22 | -1 | -0.54412 | -5.4412 | 50.5 | -1 | -1 | -10 | -7.7206 | -7.7206 | 0 | 12 | 1 | 1 | -7.7206 | 10 | 0 | 0
181.3 | 50.5 | 50.24 | -1 | -0.64412 | -6.4412 | 50.5 | -1 | -1 | -10 | -8.2206 | -8.2206 | 0 | 12 | 1 | 1 | -8.2206 | 10 | 0 | 0
181.35 | 50.47 | 50.27 | -1 | -0.74412 | -7.4412 | 50.5 | -1 | -1 | -10 | -8.7206 | -8.7206 | 0 | 12 | 1 | 1 | -8.7206 | 10 | 0 | 0
181.4 | 50.45 | 50.29 | -1 | -0.84412 | -8.4412 | 50.5 | -1 | -1 | -10 | -9.2206 | -9.2206 | 0 | 12 | 1 | 1 | -9.2206 | 10 | 0 | 0
181.45 | 50.42 | 50.32 | -1 | -0.94412 | -9.4412 | 50.5 | -1 | -1 | -10 | -9.7206 | -9.7206 | 0 | 12 | 1 | 1 | -9.7206 | 10 | 0 | 0
181.5 | 50.39 | 50.35 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
181.55 | 50.37 | 50.37 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
181.6 | 50.34 | 50.34 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
181.65 | 50.32 | 50.32 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
181.7 | 50.29 | 50.29 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
181.75 | 50.26 | 50.26 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
181.8 | 50.24 | 50.24 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
181.85 | 50.21 | 50.21 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
181.9 | 50.18 | 50.18 | -0.81 | -0.81 | -8.1 | 50.47 | -1 | -1 | -10 | -9.05 | -9.05 | 0 | 12 | 1 | 1 | -9.05 | 10 | 0 | 0
181.95 | 50.16 | 50.16 | -0.62 | -0.62 | -6.2 | 50.45 | -1 | -1 | -10 | -8.1 | -8.1 | 0 | 12 | 1 | 1 | -8.1 | 10 | 0 | 0
182 | 50.13 | 50.13 | -0.335 | -0.335 | -3.35 | 50.42 | -1 | -1 | -10 | -6.675 | -6.675 | 0 | 12 | 1 | 1 | -6.675 | 10 | 0 | 0
182.05 | 50.11 | 50.11 | -0.145 | -0.145 | -1.45 | 50.39 | -1 | -1 | -10 | -5.725 | -5.725 | 0 | 12 | 1 | 1 | -5.725 | 10 | 0 | 0
182.1 | 50.08 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 50.37 | -1 | -1 | -10 | -5.1912 | -5.1912 | 0 | 12 | 1 | 1 | -5.1912 | 10 | 0 | 0
182.15 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.34 | -1 | -1 | -10 | -5.1029 | -5.1029 | 0 | 12 | 1 | 1 | -5.1029 | 10 | 0 | 0
182.2 | 50.03 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 50.32 | -1 | -1 | -10 | -5.0441 | -5.0441 | 0 | 12 | 1 | 1 | -5.0441 | 10 | 0 | 0
182.25 | 50 | 50 | 0 | 0 | 0 | 50.29 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
182.3 | 50 | 50 | 0 | 0 | 0 | 50.26 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
182.35 | 50 | 50 | 0 | 0 | 0 | 50.24 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
182.4 | 50 | 50 | 0 | 0 | 0 | 50.21 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
182.45 | 50 | 50 | 0 | 0 | 0 | 50.18 | -0.81 | -0.9 | -9 | -4.5 | -4.5 | 0 | 12 | 1 | 1 | -4.5 | 10 | 0 | 0
182.5 | 50 | 50 | 0 | 0 | 0 | 50.16 | -0.62 | -0.8 | -8 | -4 | -4 | 0 | 12 | 1 | 1 | -4 | 10 | 0 | 0
182.55 | 50 | 50 | 0 | 0 | 0 | 50.13 | -0.335 | -0.7 | -7 | -3.5 | -3.5 | 0 | 12 | 1 | 1 | -3.5 | 10 | 0 | 0
182.6 | 50.01 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.6 | -6 | -3 | -3 | 0 | 12 | 1 | 1 | -3 | 10 | 0 | 0
182.65 | 50.01 | 50 | 0 | 0 | 0 | 50.08 | -0.038235 | -0.5 | -5 | -2.5 | -2.5 | 0 | 12 | 1 | 1 | -2.5 | 10 | 0 | 0
182.7 | 49.99 | 49.99 | 0 | 0 | 0 | 50.05 | -0.020588 | -0.4 | -4 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
182.75 | 49.99 | 49.99 | 0 | 0 | 0 | 50.03 | -0.0088235 | -0.3 | -3 | -1.5 | -1.5 | 0 | 12 | 1 | 1 | -1.5 | 10 | 0 | 0
182.8 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | -0.2 | -2 | -0.83824 | -0.83824 | 0 | 12 | 1 | 1 | -0.83824 | 10 | 0 | 0
182.85 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | -0.1 | -1 | -0.33824 | -0.33824 | 0 | 12 | 1 | 1 | -0.33824 | 10 | 0 | 0
182.9 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
182.95 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
183 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
183.05 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
183.1 | 49.89 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
183.15 | 49.89 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
183.2 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50.01 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
183.25 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
183.3 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
183.35 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 2.7868 | 2.7868 | 0 | 12 | 1 | 1 | 2.7868 | 10 | 0 | 0
183.4 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 2.7868 | 2.7868 | 0 | 12 | 1 | 1 | 2.7868 | 10 | 0 | 0
183.45 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 2.8456 | 2.8456 | 0 | 12 | 1 | 1 | 2.8456 | 10 | 0 | 0
183.5 | 49.94 | 49.85 | 0.525 | 0.525 | 5.25 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 2.7574 | 2.7574 | 0 | 12 | 1 | 1 | 2.7574 | 10 | 0 | 0
183.55 | 49.94 | 49.85 | 0.525 | 0.525 | 5.25 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 2.7574 | 2.7574 | 0 | 12 | 1 | 1 | 2.7574 | 10 | 0 | 0
183.6 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
183.65 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
183.7 | 49.93 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
183.75 | 49.93 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
183.8 | 49.96 | 49.85 | 0.525 | 0.525 | 5.25 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 2.6985 | 2.6985 | 0 | 12 | 1 | 1 | 2.6985 | 10 | 0 | 0
183.85 | 49.96 | 49.85 | 0.525 | 0.525 | 5.25 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 2.6985 | 2.6985 | 0 | 12 | 1 | 1 | 2.6985 | 10 | 0 | 0
183.9 | 49.99 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
183.95 | 49.99 | 49.91 | 0.044118 | 0.425 | 4.25 | 49.99 | 0 | 0 | 0 | 2.125 | 2.125 | 0 | 12 | 1 | 1 | 2.125 | 10 | 0 | 0
184 | 49.99 | 49.91 | 0.044118 | 0.325 | 3.25 | 49.99 | 0 | 0 | 0 | 1.625 | 1.625 | 0 | 12 | 1 | 1 | 1.625 | 10 | 0 | 0
184.05 | 49.99 | 49.93 | 0.032353 | 0.225 | 2.25 | 49.99 | 0 | 0 | 0 | 1.125 | 1.125 | 0 | 12 | 1 | 1 | 1.125 | 10 | 0 | 0
184.1 | 49.96 | 49.93 | 0.032353 | 0.125 | 1.25 | 49.99 | 0 | 0 | 0 | 0.625 | 0.625 | 0 | 12 | 1 | 1 | 0.625 | 10 | 0 | 0
184.15 | 49.96 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 49.99 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
184.2 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
184.25 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
184.3 | 50.05 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.058824 | 0.058824 | 0 | 12 | 1 | 1 | 0.058824 | 10 | 0 | 0
184.35 | 50.05 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
184.4 | 49.97 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
184.45 | 49.97 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
184.5 | 49.92 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
184.55 | 49.92 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
184.6 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
184.65 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
184.7 | 49.94 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
184.75 | 49.94 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
184.8 | 50.01 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
184.85 | 50.01 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
184.9 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
184.95 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
185 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
185.05 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
185.1 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
185.15 | 49.95 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
185.2 | 49.97 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
185.25 | 49.97 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
185.3 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
185.35 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
185.4 | 49.87 | 49.87 | 0.335 | 0.335 | 3.35 | 50.01 | 0 | 0 | 0 | 1.675 | 1.675 | 0 | 12 | 1 | 1 | 1.675 | 10 | 0 | 0
185.45 | 49.87 | 49.87 | 0.335 | 0.335 | 3.35 | 49.99 | 0 | 0 | 0 | 1.675 | 1.675 | 0 | 12 | 1 | 1 | 1.675 | 10 | 0 | 0
185.5 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
185.55 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 2.6691 | 2.6691 | 0 | 12 | 1 | 1 | 2.6691 | 10 | 0 | 0
185.6 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
185.65 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
185.7 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
185.75 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
185.8 | 49.84 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
185.85 | 49.84 | 49.79 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
185.9 | 49.89 | 49.79 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
185.95 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.12647 | 1.2647 | 5.6324 | 5.6324 | 0 | 12 | 1 | 1 | 5.6324 | 10 | 0 | 0
186 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.145 | 1.45 | 5.725 | 5.725 | 0 | 12 | 1 | 1 | 5.725 | 10 | 0 | 0
186.05 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.145 | 1.45 | 5.725 | 5.725 | 0 | 12 | 1 | 1 | 5.725 | 10 | 0 | 0
186.1 | 49.96 | 49.79 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
186.15 | 49.96 | 49.79 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
186.2 | 50.02 | 49.79 | 1 | 1 | 10 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 4.9853 | 4.9853 | 0 | 12 | 1 | 1 | 4.9853 | 10 | 0 | 0
186.25 | 50.02 | 49.79 | 1 | 1 | 10 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 4.9853 | 4.9853 | 0 | 12 | 1 | 1 | 4.9853 | 10 | 0 | 0
186.3 | 50.03 | 49.79 | 1 | 1 | 10 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.9559 | 4.9559 | 0 | 12 | 1 | 1 | 4.9559 | 10 | 0 | 0
186.35 | 50.03 | 49.84 | 0.62 | 0.9 | 9 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.4559 | 4.4559 | 0 | 12 | 1 | 1 | 4.4559 | 10 | 0 | 0
186.4 | 50.02 | 49.84 | 0.62 | 0.8 | 8 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 3.9559 | 3.9559 | 0 | 12 | 1 | 1 | 3.9559 | 10 | 0 | 0
186.45 | 50.02 | 49.89 | 0.145 | 0.7 | 7 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 3.4559 | 3.4559 | 0 | 12 | 1 | 1 | 3.4559 | 10 | 0 | 0
186.5 | 50.08 | 49.89 | 0.145 | 0.6 | 6 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 2.8088 | 2.8088 | 0 | 12 | 1 | 1 | 2.8088 | 10 | 0 | 0
186.55 | 50.08 | 49.89 | 0.145 | 0.5 | 5 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 2.3088 | 2.3088 | 0 | 12 | 1 | 1 | 2.3088 | 10 | 0 | 0
186.6 | 50.01 | 49.89 | 0.145 | 0.4 | 4 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 1.8088 | 1.8088 | 0 | 12 | 1 | 1 | 1.8088 | 10 | 0 | 0
186.65 | 50.01 | 49.96 | 0.014706 | 0.3 | 3 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 1.3088 | 1.3088 | 0 | 12 | 1 | 1 | 1.3088 | 10 | 0 | 0
186.7 | 49.94 | 49.94 | 0.026471 | 0.2 | 2 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.80882 | 0.80882 | 0 | 12 | 1 | 1 | 0.80882 | 10 | 0 | 0
186.75 | 49.94 | 49.94 | 0.026471 | 0.1 | 1 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.30882 | 0.30882 | 0 | 12 | 1 | 1 | 0.30882 | 10 | 0 | 0
186.8 | 50 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
186.85 | 50 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
186.9 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
186.95 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
187 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
187.05 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
187.1 | 49.92 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
187.15 | 49.92 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
187.2 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50.01 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
187.25 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
187.3 | 49.92 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
187.35 | 49.92 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
187.4 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
187.45 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
187.5 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
187.55 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
187.6 | 49.87 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
187.65 | 49.87 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
187.7 | 49.8 | 49.8 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
187.75 | 49.8 | 49.8 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
187.8 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
187.85 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
187.9 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
187.95 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
188 | 49.72 | 49.72 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
188.05 | 49.72 | 49.72 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
188.1 | 49.67 | 49.67 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
188.15 | 49.67 | 49.67 | 1 | 1 | 10 | 49.87 | 0.335 | 0.14412 | 1.4412 | 5.7206 | 5.7206 | 0 | 12 | 1 | 1 | 5.7206 | 10 | 0 | 0
188.2 | 49.65 | 49.65 | 1 | 1 | 10 | 49.87 | 0.335 | 0.24412 | 2.4412 | 6.2206 | 6.2206 | 0 | 12 | 1 | 1 | 6.2206 | 10 | 0 | 0
188.25 | 49.65 | 49.65 | 1 | 1 | 10 | 49.8 | 1 | 0.34412 | 3.4412 | 6.7206 | 6.7206 | 0 | 12 | 1 | 1 | 6.7206 | 10 | 0 | 0
188.3 | 49.59 | 49.59 | 1 | 1 | 10 | 49.8 | 1 | 0.44412 | 4.4412 | 7.2206 | 7.2206 | 0 | 12 | 1 | 1 | 7.2206 | 10 | 0 | 0
188.35 | 49.59 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.54412 | 5.4412 | 7.7206 | 7.7206 | 0 | 12 | 1 | 1 | 7.7206 | 10 | 0 | 0
188.4 | 49.66 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.64412 | 6.4412 | 8.2206 | 8.2206 | 0 | 12 | 1 | 1 | 8.2206 | 10 | 0 | 0
188.45 | 49.66 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.74412 | 7.4412 | 8.7206 | 8.7206 | 0 | 12 | 1 | 1 | 8.7206 | 10 | 0 | 0
188.5 | 49.63 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.84412 | 8.4412 | 9.2206 | 9.2206 | 0 | 12 | 1 | 1 | 9.2206 | 10 | 0 | 0
188.55 | 49.63 | 49.59 | 1 | 1 | 10 | 49.72 | 1 | 0.94412 | 9.4412 | 9.7206 | 9.7206 | 0 | 12 | 1 | 1 | 9.7206 | 10 | 0 | 0
188.6 | 49.61 | 49.59 | 1 | 1 | 10 | 49.72 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
188.65 | 49.61 | 49.59 | 1 | 1 | 10 | 49.67 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
188.7 | 49.54 | 49.54 | 1 | 1 | 10 | 49.67 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
188.75 | 49.54 | 49.54 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
188.8 | 49.46 | 49.46 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
188.85 | 49.46 | 49.46 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
188.9 | 49.45 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
188.95 | 49.45 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
189 | 49.51 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
189.05 | 49.51 | 49.45 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
189.1 | 49.5 | 49.45 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
189.15 | 49.5 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
189.2 | 49.54 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
189.25 | 49.54 | 49.45 | 1 | 1 | 10 | 49.54 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
189.3 | 49.59 | 49.45 | 1 | 1 | 10 | 49.59 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
189.35 | 49.59 | 49.45 | 1 | 1 | 10 | 49.59 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
189.4 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
189.45 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
189.5 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
189.55 | 49.61 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
189.6 | 49.53 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
189.65 | 49.53 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
189.7 | 49.54 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
189.75 | 49.54 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
189.8 | 49.61 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
189.85 | 49.61 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
189.9 | 49.66 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
189.95 | 49.66 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
190 | 49.64 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
190.05 | 49.64 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
190.1 | 49.69 | 49.53 | 1 | 1 | 10 | 49.69 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
190.15 | 49.69 | 49.53 | 1 | 1 | 10 | 49.69 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
190.2 | 49.74 | 49.53 | 1 | 1 | 10 | 49.74 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
190.25 | 49.74 | 49.54 | 1 | 1 | 10 | 49.74 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
190.3 | 49.78 | 49.54 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
190.35 | 49.78 | 49.61 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
190.4 | 49.82 | 49.61 | 1 | 1 | 10 | 49.82 | 0.81 | 0.81 | 8.1 | 9.05 | 9.05 | 0 | 12 | 1 | 1 | 9.05 | 10 | 0 | 0
190.45 | 49.82 | 49.64 | 1 | 1 | 10 | 49.82 | 0.81 | 0.81 | 8.1 | 9.05 | 9.05 | 0 | 12 | 1 | 1 | 9.05 | 10 | 0 | 0
190.5 | 49.86 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
190.55 | 49.86 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
190.6 | 49.84 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
190.65 | 49.84 | 49.69 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
190.7 | 49.91 | 49.69 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
190.75 | 49.91 | 49.74 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
190.8 | 49.97 | 49.74 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
190.85 | 49.97 | 49.78 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
190.9 | 50.03 | 49.78 | 1 | 1 | 10 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.9559 | 4.9559 | 0 | 12 | 1 | 1 | 4.9559 | 10 | 0 | 0
190.95 | 50.03 | 49.82 | 0.81 | 0.9 | 9 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.4559 | 4.4559 | 0 | 12 | 1 | 1 | 4.4559 | 10 | 0 | 0
191 | 50.05 | 49.82 | 0.81 | 0.81 | 8.1 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 3.9471 | 3.9471 | 0 | 12 | 1 | 1 | 3.9471 | 10 | 0 | 0
191.05 | 50.05 | 49.84 | 0.62 | 0.71 | 7.1 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 3.4471 | 3.4471 | 0 | 12 | 1 | 1 | 3.4471 | 10 | 0 | 0
191.1 | 50.01 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
191.15 | 50.01 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
191.2 | 49.95 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
191.25 | 49.95 | 49.91 | 0.044118 | 0.52 | 5.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.4971 | 2.4971 | 0 | 12 | 1 | 1 | 2.4971 | 10 | 0 | 0
191.3 | 49.99 | 49.91 | 0.044118 | 0.42 | 4.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 1.9971 | 1.9971 | 0 | 12 | 1 | 1 | 1.9971 | 10 | 0 | 0
191.35 | 49.99 | 49.95 | 0.020588 | 0.32 | 3.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 1.4971 | 1.4971 | 0 | 12 | 1 | 1 | 1.4971 | 10 | 0 | 0
191.4 | 49.92 | 49.92 | 0.038235 | 0.22 | 2.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.99706 | 0.99706 | 0 | 12 | 1 | 1 | 0.99706 | 10 | 0 | 0
191.45 | 49.92 | 49.92 | 0.038235 | 0.12 | 1.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.49706 | 0.49706 | 0 | 12 | 1 | 1 | 0.49706 | 10 | 0 | 0
191.5 | 49.97 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
191.55 | 49.97 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
191.6 | 50.02 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
191.65 | 50.02 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.17647 | 0.17647 | 0 | 12 | 1 | 1 | 0.17647 | 10 | 0 | 0
191.7 | 50.07 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
191.75 | 50.07 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
191.8 | 50.06 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
191.85 | 50.06 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
191.9 | 50.13 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
191.95 | 50.13 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
192 | 50.09 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
192.05 | 50.09 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6309 | -1.6309 | 0 | 12 | 1 | 1 | -1.6309 | 10 | 0 | 0
192.1 | 50.07 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6309 | -1.6309 | 0 | 12 | 1 | 1 | -1.6309 | 10 | 0 | 0
192.15 | 50.07 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6897 | -1.6897 | 0 | 12 | 1 | 1 | -1.6897 | 10 | 0 | 0
192.2 | 50.07 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6897 | -1.6897 | 0 | 12 | 1 | 1 | -1.6897 | 10 | 0 | 0
192.25 | 50.07 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.13 | -0.335 | -0.335 | -3.35 | -1.8074 | -1.8074 | 0 | 12 | 1 | 1 | -1.8074 | 10 | 0 | 0
192.3 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.13 | -0.335 | -0.335 | -3.35 | -1.7779 | -1.7779 | 0 | 12 | 1 | 1 | -1.7779 | 10 | 0 | 0
192.35 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.13 | -0.335 | -0.335 | -3.35 | -1.7779 | -1.7779 | 0 | 12 | 1 | 1 | -1.7779 | 10 | 0 | 0
192.4 | 50.01 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
192.45 | 50.01 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
192.5 | 50.07 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
192.55 | 50.07 | 50.01 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.235 | -2.35 | -1.175 | -1.175 | 0 | 12 | 1 | 1 | -1.175 | 10 | 0 | 0
192.6 | 50.05 | 50.01 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.135 | -1.35 | -0.675 | -0.675 | 0 | 12 | 1 | 1 | -0.675 | 10 | 0 | 0
192.65 | 50.05 | 50.01 | 0 | 0 | 0 | 50.07 | -0.032353 | -0.035 | -0.35 | -0.175 | -0.175 | 0 | 12 | 1 | 1 | -0.175 | 10 | 0 | 0
192.7 | 50.1 | 50.01 | 0 | 0 | 0 | 50.1 | -0.05 | -0.05 | -0.5 | -0.25 | -0.25 | 0 | 12 | 1 | 1 | -0.25 | 10 | 0 | 0
192.75 | 50.1 | 50.01 | 0 | 0 | 0 | 50.1 | -0.05 | -0.05 | -0.5 | -0.25 | -0.25 | 0 | 12 | 1 | 1 | -0.25 | 10 | 0 | 0
192.8 | 50.11 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
192.85 | 50.11 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
192.9 | 50.06 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
192.95 | 50.06 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
193 | 50.04 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
193.05 | 50.04 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
193.1 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
193.15 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
193.2 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
193.25 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
193.3 | 50.11 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
193.35 | 50.11 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
193.4 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
193.45 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
193.5 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
193.55 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
193.6 | 50.02 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.11 | -0.145 | -0.145 | -1.45 | -0.73971 | -0.73971 | 0 | 12 | 1 | 1 | -0.73971 | 10 | 0 | 0
193.65 | 50.02 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.11 | -0.145 | -0.145 | -1.45 | -0.73971 | -0.73971 | 0 | 12 | 1 | 1 | -0.73971 | 10 | 0 | 0
193.7 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
193.75 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
193.8 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
193.85 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
193.9 | 50.01 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
193.95 | 50.01 | 50 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.045 | -0.45 | -0.225 | -0.225 | 0 | 12 | 1 | 1 | -0.225 | 10 | 0 | 0
194 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
194.05 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
194.1 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
194.15 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
194.2 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.14706 | 0.14706 | 0 | 12 | 1 | 1 | 0.14706 | 10 | 0 | 0
194.25 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
194.3 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
194.35 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
194.4 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
194.45 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
194.5 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
194.55 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
194.6 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
194.65 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
194.7 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
194.75 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
194.8 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
194.85 | 50 | 50 | 0 | 0 | 0 | 50.01 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
194.9 | 49.5 | 49.5 | 1 | 1 | 10 | 50.01 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
194.95 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
195 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
195.05 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
195.1 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
195.15 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
195.2 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
195.25 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
195.3 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
195.35 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
195.4 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
195.45 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.1 | 1 | 5.5 | 5.5 | 0 | 12 | 1 | 1 | 5.5 | 10 | 0 | 0
195.5 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.2 | 2 | 6 | 6 | 0 | 12 | 1 | 1 | 6 | 10 | 0 | 0
195.55 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.3 | 3 | 6.5 | 6.5 | 0 | 12 | 1 | 1 | 6.5 | 10 | 0 | 0
195.6 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.4 | 4 | 7 | 7 | 0 | 12 | 1 | 1 | 7 | 10 | 0 | 0
195.65 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.5 | 5 | 7.5 | 7.5 | 0 | 12 | 1 | 1 | 7.5 | 10 | 0 | 0
195.7 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.6 | 6 | 8 | 8 | 0 | 12 | 1 | 1 | 8 | 10 | 0 | 0
195.75 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.7 | 7 | 8.5 | 8.5 | 0 | 12 | 1 | 1 | 8.5 | 10 | 0 | 0
195.8 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.8 | 8 | 9 | 9 | 0 | 12 | 1 | 1 | 9 | 10 | 0 | 0
195.85 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.9 | 9 | 9.5 | 9.5 | 0 | 12 | 1 | 1 | 9.5 | 10 | 0 | 0
195.9 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
195.95 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
196 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
196.05 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
196.1 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
196.15 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
196.2 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
196.25 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
196.3 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
196.35 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
196.4 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
196.45 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
196.5 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
196.55 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
196.6 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
196.65 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
196.7 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
196.75 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
196.8 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
196.85 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
196.9 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
196.95 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
197 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
197.05 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
197.1 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
197.15 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
197.2 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
197.25 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
197.3 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
197.35 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
197.4 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
197.45 | 50.5 | 50.5 | -1 | 0.9 | 9 | 50.5 | -1 | -1 | -10 | -0.5 | -0.5 | 0 | 12 | 1 | 1 | -0.5 | 10 | 0 | 0
197.5 | 50.5 | 50.5 | -1 | 0.8 | 8 | 50.5 | -1 | -1 | -10 | -1 | -1 | 0 | 12 | 1 | 1 | -1 | 10 | 0 | 0
197.55 | 50.5 | 50.5 | -1 | 0.7 | 7 | 50.5 | -1 | -1 | -10 | -1.5 | -1.5 | 0 | 12 | 1 | 1 | -1.5 | 10 | 0 | 0
197.6 | 50.5 | 50.5 | -1 | 0.6 | 6 | 50.5 | -1 | -1 | -10 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
197.65 | 50.5 | 50.5 | -1 | 0.5 | 5 | 50.5 | -1 | -1 | -10 | -2.5 | -2.5 | 0 | 12 | 1 | 1 | -2.5 | 10 | 0 | 0
197.7 | 50.5 | 50.5 | -1 | 0.4 | 4 | 50.5 | -1 | -1 | -10 | -3 | -3 | 0 | 12 | 1 | 1 | -3 | 10 | 0 | 0
197.75 | 50.5 | 50.5 | -1 | 0.3 | 3 | 50.5 | -1 | -1 | -10 | -3.5 | -3.5 | 0 | 12 | 1 | 1 | -3.5 | 10 | 0 | 0
197.8 | 50.5 | 50.5 | -1 | 0.2 | 2 | 50.5 | -1 | -1 | -10 | -4 | -4 | 0 | 12 | 1 | 1 | -4 | 10 | 0 | 0
197.85 | 50.5 | 50.5 | -1 | 0.1 | 1 | 50.5 | -1 | -1 | -10 | -4.5 | -4.5 | 0 | 12 | 1 | 1 | -4.5 | 10 | 0 | 0
197.9 | 50.5 | 50.5 | -1 | 0 | 0 | 50.5 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
197.95 | 50.5 | 50.5 | -1 | -0.1 | -1 | 50.5 | -1 | -1 | -10 | -5.5 | -5.5 | 0 | 12 | 1 | 1 | -5.5 | 10 | 0 | 0
198 | 50.5 | 50.5 | -1 | -0.2 | -2 | 50.5 | -1 | -1 | -10 | -6 | -6 | 0 | 12 | 1 | 1 | -6 | 10 | 0 | 0
198.05 | 50.5 | 50.5 | -1 | -0.3 | -3 | 50.5 | -1 | -1 | -10 | -6.5 | -6.5 | 0 | 12 | 1 | 1 | -6.5 | 10 | 0 | 0
198.1 | 50.5 | 50.5 | -1 | -0.4 | -4 | 50.5 | -1 | -1 | -10 | -7 | -7 | 0 | 12 | 1 | 1 | -7 | 10 | 0 | 0
198.15 | 50.5 | 50.5 | -1 | -0.5 | -5 | 50.5 | -1 | -1 | -10 | -7.5 | -7.5 | 0 | 12 | 1 | 1 | -7.5 | 10 | 0 | 0
198.2 | 50.5 | 50.5 | -1 | -0.6 | -6 | 50.5 | -1 | -1 | -10 | -8 | -8 | 0 | 12 | 1 | 1 | -8 | 10 | 0 | 0
198.25 | 50.5 | 50.5 | -1 | -0.7 | -7 | 50.5 | -1 | -1 | -10 | -8.5 | -8.5 | 0 | 12 | 1 | 1 | -8.5 | 10 | 0 | 0
198.3 | 50.5 | 50.5 | -1 | -0.8 | -8 | 50.5 | -1 | -1 | -10 | -9 | -9 | 0 | 12 | 1 | 1 | -9 | 10 | 0 | 0
198.35 | 50.5 | 50.5 | -1 | -0.9 | -9 | 50.5 | -1 | -1 | -10 | -9.5 | -9.5 | 0 | 12 | 1 | 1 | -9.5 | 10 | 0 | 0
198.4 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
198.45 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
198.5 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
198.55 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
198.6 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
198.65 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
198.7 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
198.75 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
198.8 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
198.85 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
198.9 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
198.95 | 50.47 | 50.47 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
199 | 50.45 | 50.45 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
199.05 | 50.42 | 50.42 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
199.1 | 50.4 | 50.4 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
199.15 | 50.37 | 50.37 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
199.2 | 50.35 | 50.35 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
199.25 | 50.32 | 50.32 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
199.3 | 50.29 | 50.29 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
199.35 | 50.27 | 50.27 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
199.4 | 50.24 | 50.24 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
199.45 | 50.22 | 50.22 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
199.5 | 50.19 | 50.19 | -0.905 | -0.905 | -9.05 | 50.47 | -1 | -1 | -10 | -9.525 | -9.525 | 0 | 12 | 1 | 1 | -9.525 | 10 | 0 | 0
199.55 | 50.17 | 50.17 | -0.715 | -0.715 | -7.15 | 50.45 | -1 | -1 | -10 | -8.575 | -8.575 | 0 | 12 | 1 | 1 | -8.575 | 10 | 0 | 0
199.6 | 50.14 | 50.14 | -0.43 | -0.43 | -4.3 | 50.42 | -1 | -1 | -10 | -7.15 | -7.15 | 0 | 12 | 1 | 1 | -7.15 | 10 | 0 | 0
199.65 | 50.12 | 50.12 | -0.24 | -0.24 | -2.4 | 50.4 | -1 | -1 | -10 | -6.2 | -6.2 | 0 | 12 | 1 | 1 | -6.2 | 10 | 0 | 0
199.7 | 50.09 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 50.37 | -1 | -1 | -10 | -5.2206 | -5.2206 | 0 | 12 | 1 | 1 | -5.2206 | 10 | 0 | 0
199.75 | 50.06 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.35 | -1 | -1 | -10 | -5.1324 | -5.1324 | 0 | 12 | 1 | 1 | -5.1324 | 10 | 0 | 0
199.8 | 50.04 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.32 | -1 | -1 | -10 | -5.0735 | -5.0735 | 0 | 12 | 1 | 1 | -5.0735 | 10 | 0 | 0
199.85 | 50.01 | 50.01 | 0 | 0 | 0 | 50.29 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
199.9 | 49.99 | 49.99 | 0 | 0 | 0 | 50.27 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
199.95 | 49.96 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.24 | -1 | -1 | -10 | -4.9265 | -4.9265 | 0 | 12 | 1 | 1 | -4.9265 | 10 | 0 | 0
200 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.22 | -1 | -1 | -10 | -4.8676 | -4.8676 | 0 | 12 | 1 | 1 | -4.8676 | 10 | 0 | 0
200.05 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.19 | -0.905 | -0.905 | -9.05 | -4.3044 | -4.3044 | 0 | 12 | 1 | 1 | -4.3044 | 10 | 0 | 0
200.1 | 49.88 | 49.88 | 0.24 | 0.24 | 2.4 | 50.17 | -0.715 | -0.805 | -8.05 | -2.825 | -2.825 | 0 | 12 | 1 | 1 | -2.825 | 10 | 0 | 0
200.15 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.14 | -0.43 | -0.705 | -7.05 | -1.375 | -1.375 | 0 | 12 | 1 | 1 | -1.375 | 10 | 0 | 0
200.2 | 49.83 | 49.83 | 0.715 | 0.715 | 7.15 | 50.12 | -0.24 | -0.605 | -6.05 | 0.55 | 0.55 | 0 | 12 | 1 | 1 | 0.55 | 10 | 0 | 0
200.25 | 49.81 | 49.81 | 0.905 | 0.905 | 9.05 | 50.09 | -0.044118 | -0.505 | -5.05 | 2 | 2 | 0 | 12 | 1 | 1 | 2 | 10 | 0 | 0
200.3 | 49.78 | 49.78 | 1 | 1 | 10 | 50.06 | -0.026471 | -0.405 | -4.05 | 2.975 | 2.975 | 0 | 12 | 1 | 1 | 2.975 | 10 | 0 | 0
200.35 | 49.76 | 49.76 | 1 | 1 | 10 | 50.04 | -0.014706 | -0.305 | -3.05 | 3.475 | 3.475 | 0 | 12 | 1 | 1 | 3.475 | 10 | 0 | 0
200.4 | 49.73 | 49.73 | 1 | 1 | 10 | 50.01 | 0 | -0.205 | -2.05 | 3.975 | 3.975 | 0 | 12 | 1 | 1 | 3.975 | 10 | 0 | 0
200.45 | 49.71 | 49.71 | 1 | 1 | 10 | 49.99 | 0 | -0.105 | -1.05 | 4.475 | 4.475 | 0 | 12 | 1 | 1 | 4.475 | 10 | 0 | 0
200.5 | 49.68 | 49.68 | 1 | 1 | 10 | 49.96 | 0.014706 | -0.005 | -0.05 | 4.975 | 4.975 | 0 | 12 | 1 | 1 | 4.975 | 10 | 0 | 0
200.55 | 49.65 | 49.65 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
200.6 | 49.63 | 49.63 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
200.65 | 49.6 | 49.6 | 1 | 1 | 10 | 49.88 | 0.24 | 0.14412 | 1.4412 | 5.7206 | 5.7206 | 0 | 12 | 1 | 1 | 5.7206 | 10 | 0 | 0
200.7 | 49.58 | 49.58 | 1 | 1 | 10 | 49.86 | 0.43 | 0.24412 | 2.4412 | 6.2206 | 6.2206 | 0 | 12 | 1 | 1 | 6.2206 | 10 | 0 | 0
200.75 | 49.55 | 49.55 | 1 | 1 | 10 | 49.83 | 0.715 | 0.34412 | 3.4412 | 6.7206 | 6.7206 | 0 | 12 | 1 | 1 | 6.7206 | 10 | 0 | 0
200.8 | 49.53 | 49.53 | 1 | 1 | 10 | 49.81 | 0.905 | 0.44412 | 4.4412 | 7.2206 | 7.2206 | 0 | 12 | 1 | 1 | 7.2206 | 10 | 0 | 0
200.85 | 49.5 | 49.5 | 1 | 1 | 10 | 49.78 | 1 | 0.54412 | 5.4412 | 7.7206 | 7.7206 | 0 | 12 | 1 | 1 | 7.7206 | 10 | 0 | 0
200.9 | 49.5 | 49.5 | 1 | 1 | 10 | 49.76 | 1 | 0.64412 | 6.4412 | 8.2206 | 8.2206 | 0 | 12 | 1 | 1 | 8.2206 | 10 | 0 | 0
200.95 | 49.53 | 49.5 | 1 | 1 | 10 | 49.73 | 1 | 0.74412 | 7.4412 | 8.7206 | 8.7206 | 0 | 12 | 1 | 1 | 8.7206 | 10 | 0 | 0
201 | 49.55 | 49.5 | 1 | 1 | 10 | 49.71 | 1 | 0.84412 | 8.4412 | 9.2206 | 9.2206 | 0 | 12 | 1 | 1 | 9.2206 | 10 | 0 | 0
201.05 | 49.58 | 49.5 | 1 | 1 | 10 | 49.68 | 1 | 0.94412 | 9.4412 | 9.7206 | 9.7206 | 0 | 12 | 1 | 1 | 9.7206 | 10 | 0 | 0
201.1 | 49.6 | 49.5 | 1 | 1 | 10 | 49.65 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
201.15 | 49.63 | 49.5 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
201.2 | 49.65 | 49.5 | 1 | 1 | 10 | 49.65 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
201.25 | 49.68 | 49.5 | 1 | 1 | 10 | 49.68 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
201.3 | 49.71 | 49.5 | 1 | 1 | 10 | 49.71 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
201.35 | 49.73 | 49.5 | 1 | 1 | 10 | 49.73 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
201.4 | 49.76 | 49.5 | 1 | 1 | 10 | 49.76 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
201.45 | 49.78 | 49.5 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
201.5 | 49.81 | 49.53 | 1 | 1 | 10 | 49.81 | 0.905 | 0.905 | 9.05 | 9.525 | 9.525 | 0 | 12 | 1 | 1 | 9.525 | 10 | 0 | 0
201.55 | 49.83 | 49.55 | 1 | 1 | 10 | 49.83 | 0.715 | 0.715 | 7.15 | 8.575 | 8.575 | 0 | 12 | 1 | 1 | 8.575 | 10 | 0 | 0
201.6 | 49.86 | 49.58 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
201.65 | 49.88 | 49.6 | 1 | 1 | 10 | 49.88 | 0.24 | 0.24 | 2.4 | 6.2 | 6.2 | 0 | 12 | 1 | 1 | 6.2 | 10 | 0 | 0
201.7 | 49.91 | 49.63 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
201.75 | 49.94 | 49.65 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
201.8 | 49.96 | 49.68 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
201.85 | 49.99 | 49.71 | 1 | 1 | 10 | 49.99 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
201.9 | 50.01 | 49.73 | 1 | 1 | 10 | 50.01 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
201.95 | 50.04 | 49.76 | 1 | 1 | 10 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 4.9265 | 4.9265 | 0 | 12 | 1 | 1 | 4.9265 | 10 | 0 | 0
202 | 50.06 | 49.78 | 1 | 1 | 10 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 4.8676 | 4.8676 | 0 | 12 | 1 | 1 | 4.8676 | 10 | 0 | 0
202.05 | 50.09 | 49.81 | 0.905 | 0.905 | 9.05 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 4.3044 | 4.3044 | 0 | 12 | 1 | 1 | 4.3044 | 10 | 0 | 0
202.1 | 50.12 | 49.83 | 0.715 | 0.805 | 8.05 | 50.12 | -0.24 | -0.24 | -2.4 | 2.825 | 2.825 | 0 | 12 | 1 | 1 | 2.825 | 10 | 0 | 0
202.15 | 50.14 | 49.86 | 0.43 | 0.705 | 7.05 | 50.14 | -0.43 | -0.43 | -4.3 | 1.375 | 1.375 | 0 | 12 | 1 | 1 | 1.375 | 10 | 0 | 0
202.2 | 50.17 | 49.88 | 0.24 | 0.605 | 6.05 | 50.17 | -0.715 | -0.715 | -7.15 | -0.55 | -0.55 | 0 | 12 | 1 | 1 | -0.55 | 10 | 0 | 0
202.25 | 50.19 | 49.91 | 0.044118 | 0.505 | 5.05 | 50.19 | -0.905 | -0.905 | -9.05 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
202.3 | 50.22 | 49.94 | 0.026471 | 0.405 | 4.05 | 50.22 | -1 | -1 | -10 | -2.975 | -2.975 | 0 | 12 | 1 | 1 | -2.975 | 10 | 0 | 0
202.35 | 50.24 | 49.96 | 0.014706 | 0.305 | 3.05 | 50.24 | -1 | -1 | -10 | -3.475 | -3.475 | 0 | 12 | 1 | 1 | -3.475 | 10 | 0 | 0
202.4 | 50.27 | 49.99 | 0 | 0.205 | 2.05 | 50.27 | -1 | -1 | -10 | -3.975 | -3.975 | 0 | 12 | 1 | 1 | -3.975 | 10 | 0 | 0
202.45 | 50.29 | 50.01 | 0 | 0.105 | 1.05 | 50.29 | -1 | -1 | -10 | -4.475 | -4.475 | 0 | 12 | 1 | 1 | -4.475 | 10 | 0 | 0
202.5 | 50.32 | 50.04 | -0.014706 | 0.005 | 0.05 | 50.32 | -1 | -1 | -10 | -4.975 | -4.975 | 0 | 12 | 1 | 1 | -4.975 | 10 | 0 | 0
202.55 | 50.35 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.35 | -1 | -1 | -10 | -5.1324 | -5.1324 | 0 | 12 | 1 | 1 | -5.1324 | 10 | 0 | 0
202.6 | 50.37 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 50.37 | -1 | -1 | -10 | -5.2206 | -5.2206 | 0 | 12 | 1 | 1 | -5.2206 | 10 | 0 | 0
202.65 | 50.4 | 50.12 | -0.24 | -0.14412 | -1.4412 | 50.4 | -1 | -1 | -10 | -5.7206 | -5.7206 | 0 | 12 | 1 | 1 | -5.7206 | 10 | 0 | 0
202.7 | 50.42 | 50.14 | -0.43 | -0.24412 | -2.4412 | 50.42 | -1 | -1 | -10 | -6.2206 | -6.2206 | 0 | 12 | 1 | 1 | -6.2206 | 10 | 0 | 0
202.75 | 50.45 | 50.17 | -0.715 | -0.34412 | -3.4412 | 50.45 | -1 | -1 | -10 | -6.7206 | -6.7206 | 0 | 12 | 1 | 1 | -6.7206 | 10 | 0 | 0
202.8 | 50.47 | 50.19 | -0.905 | -0.44412 | -4.4412 | 50.47 | -1 | -1 | -10 | -7.2206 | -7.2206 | 0 | 12 | 1 | 1 | -7.2206 | 10 | 0 | 0
202.85 | 50.5 | 50.22 | -1 | -0.54412 | -5.4412 | 50.5 | -1 | -1 | -10 | -7.7206 | -7.7206 | 0 | 12 | 1 | 1 | -7.7206 | 10 | 0 | 0
202.9 | 50.5 | 50.24 | -1 | -0.64412 | -6.4412 | 50.5 | -1 | -1 | -10 | -8.2206 | -8.2206 | 0 | 12 | 1 | 1 | -8.2206 | 10 | 0 | 0
202.95 | 50.47 | 50.27 | -1 | -0.74412 | -7.4412 | 50.5 | -1 | -1 | -10 | -8.7206 | -8.7206 | 0 | 12 | 1 | 1 | -8.7206 | 10 | 0 | 0
203 | 50.45 | 50.29 | -1 | -0.84412 | -8.4412 | 50.5 | -1 | -1 | -10 | -9.2206 | -9.2206 | 0 | 12 | 1 | 1 | -9.2206 | 10 | 0 | 0
203.05 | 50.42 | 50.32 | -1 | -0.94412 | -9.4412 | 50.5 | -1 | -1 | -10 | -9.7206 | -9.7206 | 0 | 12 | 1 | 1 | -9.7206 | 10 | 0 | 0
203.1 | 50.39 | 50.35 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
203.15 | 50.37 | 50.37 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
203.2 | 50.34 | 50.34 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
203.25 | 50.32 | 50.32 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
203.3 | 50.29 | 50.29 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
203.35 | 50.26 | 50.26 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
203.4 | 50.24 | 50.24 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
203.45 | 50.21 | 50.21 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
203.5 | 50.18 | 50.18 | -0.81 | -0.81 | -8.1 | 50.47 | -1 | -1 | -10 | -9.05 | -9.05 | 0 | 12 | 1 | 1 | -9.05 | 10 | 0 | 0
203.55 | 50.16 | 50.16 | -0.62 | -0.62 | -6.2 | 50.45 | -1 | -1 | -10 | -8.1 | -8.1 | 0 | 12 | 1 | 1 | -8.1 | 10 | 0 | 0
203.6 | 50.13 | 50.13 | -0.335 | -0.335 | -3.35 | 50.42 | -1 | -1 | -10 | -6.675 | -6.675 | 0 | 12 | 1 | 1 | -6.675 | 10 | 0 | 0
203.65 | 50.11 | 50.11 | -0.145 | -0.145 | -1.45 | 50.39 | -1 | -1 | -10 | -5.725 | -5.725 | 0 | 12 | 1 | 1 | -5.725 | 10 | 0 | 0
203.7 | 50.08 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 50.37 | -1 | -1 | -10 | -5.1912 | -5.1912 | 0 | 12 | 1 | 1 | -5.1912 | 10 | 0 | 0
203.75 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.34 | -1 | -1 | -10 | -5.1029 | -5.1029 | 0 | 12 | 1 | 1 | -5.1029 | 10 | 0 | 0
203.8 | 50.03 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 50.32 | -1 | -1 | -10 | -5.0441 | -5.0441 | 0 | 12 | 1 | 1 | -5.0441 | 10 | 0 | 0
203.85 | 50 | 50 | 0 | 0 | 0 | 50.29 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
203.9 | 50 | 50 | 0 | 0 | 0 | 50.26 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
203.95 | 50 | 50 | 0 | 0 | 0 | 50.24 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
204 | 50 | 50 | 0 | 0 | 0 | 50.21 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
204.05 | 50 | 50 | 0 | 0 | 0 | 50.18 | -0.81 | -0.9 | -9 | -4.5 | -4.5 | 0 | 12 | 1 | 1 | -4.5 | 10 | 0 | 0
204.1 | 50 | 50 | 0 | 0 | 0 | 50.16 | -0.62 | -0.8 | -8 | -4 | -4 | 0 | 12 | 1 | 1 | -4 | 10 | 0 | 0
204.15 | 50 | 50 | 0 | 0 | 0 | 50.13 | -0.335 | -0.7 | -7 | -3.5 | -3.5 | 0 | 12 | 1 | 1 | -3.5 | 10 | 0 | 0
204.2 | 50.01 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.6 | -6 | -3 | -3 | 0 | 12 | 1 | 1 | -3 | 10 | 0 | 0
204.25 | 50.01 | 50 | 0 | 0 | 0 | 50.08 | -0.038235 | -0.5 | -5 | -2.5 | -2.5 | 0 | 12 | 1 | 1 | -2.5 | 10 | 0 | 0
204.3 | 49.99 | 49.99 | 0 | 0 | 0 | 50.05 | -0.020588 | -0.4 | -4 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
204.35 | 49.99 | 49.99 | 0 | 0 | 0 | 50.03 | -0.0088235 | -0.3 | -3 | -1.5 | -1.5 | 0 | 12 | 1 | 1 | -1.5 | 10 | 0 | 0
204.4 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | -0.2 | -2 | -0.83824 | -0.83824 | 0 | 12 | 1 | 1 | -0.83824 | 10 | 0 | 0
204.45 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | -0.1 | -1 | -0.33824 | -0.33824 | 0 | 12 | 1 | 1 | -0.33824 | 10 | 0 | 0
204.5 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
204.55 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
204.6 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
204.65 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
204.7 | 49.89 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
204.75 | 49.89 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
204.8 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50.01 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
204.85 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
204.9 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
204.95 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 2.7868 | 2.7868 | 0 | 12 | 1 | 1 | 2.7868 | 10 | 0 | 0
205 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 2.7868 | 2.7868 | 0 | 12 | 1 | 1 | 2.7868 | 10 | 0 | 0
205.05 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 2.8456 | 2.8456 | 0 | 12 | 1 | 1 | 2.8456 | 10 | 0 | 0
205.1 | 49.94 | 49.85 | 0.525 | 0.525 | 5.25 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 2.7574 | 2.7574 | 0 | 12 | 1 | 1 | 2.7574 | 10 | 0 | 0
205.15 | 49.94 | 49.85 | 0.525 | 0.525 | 5.25 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 2.7574 | 2.7574 | 0 | 12 | 1 | 1 | 2.7574 | 10 | 0 | 0
205.2 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
205.25 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
205.3 | 49.93 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
205.35 | 49.93 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
205.4 | 49.96 | 49.85 | 0.525 | 0.525 | 5.25 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 2.6985 | 2.6985 | 0 | 12 | 1 | 1 | 2.6985 | 10 | 0 | 0
205.45 | 49.96 | 49.85 | 0.525 | 0.525 | 5.25 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 2.6985 | 2.6985 | 0 | 12 | 1 | 1 | 2.6985 | 10 | 0 | 0
205.5 | 49.99 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
205.55 | 49.99 | 49.91 | 0.044118 | 0.425 | 4.25 | 49.99 | 0 | 0 | 0 | 2.125 | 2.125 | 0 | 12 | 1 | 1 | 2.125 | 10 | 0 | 0
205.6 | 49.99 | 49.91 | 0.044118 | 0.325 | 3.25 | 49.99 | 0 | 0 | 0 | 1.625 | 1.625 | 0 | 12 | 1 | 1 | 1.625 | 10 | 0 | 0
205.65 | 49.99 | 49.93 | 0.032353 | 0.225 | 2.25 | 49.99 | 0 | 0 | 0 | 1.125 | 1.125 | 0 | 12 | 1 | 1 | 1.125 | 10 | 0 | 0
205.7 | 49.96 | 49.93 | 0.032353 | 0.125 | 1.25 | 49.99 | 0 | 0 | 0 | 0.625 | 0.625 | 0 | 12 | 1 | 1 | 0.625 | 10 | 0 | 0
205.75 | 49.96 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 49.99 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
205.8 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
205.85 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
205.9 | 50.05 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.058824 | 0.058824 | 0 | 12 | 1 | 1 | 0.058824 | 10 | 0 | 0
205.95 | 50.05 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
206 | 49.97 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
206.05 | 49.97 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
206.1 | 49.92 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
206.15 | 49.92 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
206.2 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
206.25 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
206.3 | 49.94 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
206.35 | 49.94 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
206.4 | 50.01 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
206.45 | 50.01 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
206.5 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
206.55 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
206.6 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
206.65 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
206.7 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
206.75 | 49.95 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
206.8 | 49.97 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
206.85 | 49.97 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
206.9 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
206.95 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
207 | 49.87 | 49.87 | 0.335 | 0.335 | 3.35 | 50.01 | 0 | 0 | 0 | 1.675 | 1.675 | 0 | 12 | 1 | 1 | 1.675 | 10 | 0 | 0
207.05 | 49.87 | 49.87 | 0.335 | 0.335 | 3.35 | 49.99 | 0 | 0 | 0 | 1.675 | 1.675 | 0 | 12 | 1 | 1 | 1.675 | 10 | 0 | 0
207.1 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
207.15 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 2.6691 | 2.6691 | 0 | 12 | 1 | 1 | 2.6691 | 10 | 0 | 0
207.2 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
207.25 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
207.3 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
207.35 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
207.4 | 49.84 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
207.45 | 49.84 | 49.79 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
207.5 | 49.89 | 49.79 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
207.55 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.12647 | 1.2647 | 5.6324 | 5.6324 | 0 | 12 | 1 | 1 | 5.6324 | 10 | 0 | 0
207.6 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.145 | 1.45 | 5.725 | 5.725 | 0 | 12 | 1 | 1 | 5.725 | 10 | 0 | 0
207.65 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.145 | 1.45 | 5.725 | 5.725 | 0 | 12 | 1 | 1 | 5.725 | 10 | 0 | 0
207.7 | 49.96 | 49.79 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
207.75 | 49.96 | 49.79 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
207.8 | 50.02 | 49.79 | 1 | 1 | 10 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 4.9853 | 4.9853 | 0 | 12 | 1 | 1 | 4.9853 | 10 | 0 | 0
207.85 | 50.02 | 49.79 | 1 | 1 | 10 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 4.9853 | 4.9853 | 0 | 12 | 1 | 1 | 4.9853 | 10 | 0 | 0
207.9 | 50.03 | 49.79 | 1 | 1 | 10 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.9559 | 4.9559 | 0 | 12 | 1 | 1 | 4.9559 | 10 | 0 | 0
207.95 | 50.03 | 49.84 | 0.62 | 0.9 | 9 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.4559 | 4.4559 | 0 | 12 | 1 | 1 | 4.4559 | 10 | 0 | 0
208 | 50.02 | 49.84 | 0.62 | 0.8 | 8 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 3.9559 | 3.9559 | 0 | 12 | 1 | 1 | 3.9559 | 10 | 0 | 0
208.05 | 50.02 | 49.89 | 0.145 | 0.7 | 7 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 3.4559 | 3.4559 | 0 | 12 | 1 | 1 | 3.4559 | 10 | 0 | 0
208.1 | 50.08 | 49.89 | 0.145 | 0.6 | 6 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 2.8088 | 2.8088 | 0 | 12 | 1 | 1 | 2.8088 | 10 | 0 | 0
208.15 | 50.08 | 49.89 | 0.145 | 0.5 | 5 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 2.3088 | 2.3088 | 0 | 12 | 1 | 1 | 2.3088 | 10 | 0 | 0
208.2 | 50.01 | 49.89 | 0.145 | 0.4 | 4 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 1.8088 | 1.8088 | 0 | 12 | 1 | 1 | 1.8088 | 10 | 0 | 0
208.25 | 50.01 | 49.96 | 0.014706 | 0.3 | 3 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 1.3088 | 1.3088 | 0 | 12 | 1 | 1 | 1.3088 | 10 | 0 | 0
208.3 | 49.94 | 49.94 | 0.026471 | 0.2 | 2 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.80882 | 0.80882 | 0 | 12 | 1 | 1 | 0.80882 | 10 | 0 | 0
208.35 | 49.94 | 49.94 | 0.026471 | 0.1 | 1 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.30882 | 0.30882 | 0 | 12 | 1 | 1 | 0.30882 | 10 | 0 | 0
208.4 | 50 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
208.45 | 50 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
208.5 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
208.55 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
208.6 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
208.65 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
208.7 | 49.92 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
208.75 | 49.92 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
208.8 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50.01 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
208.85 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
208.9 | 49.92 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
208.95 | 49.92 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
209 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
209.05 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
209.1 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
209.15 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
209.2 | 49.87 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
209.25 | 49.87 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
209.3 | 49.8 | 49.8 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
209.35 | 49.8 | 49.8 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
209.4 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
209.45 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
209.5 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
209.55 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
209.6 | 49.72 | 49.72 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
209.65 | 49.72 | 49.72 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
209.7 | 49.67 | 49.67 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
209.75 | 49.67 | 49.67 | 1 | 1 | 10 | 49.87 | 0.335 | 0.14412 | 1.4412 | 5.7206 | 5.7206 | 0 | 12 | 1 | 1 | 5.7206 | 10 | 0 | 0
209.8 | 49.65 | 49.65 | 1 | 1 | 10 | 49.87 | 0.335 | 0.24412 | 2.4412 | 6.2206 | 6.2206 | 0 | 12 | 1 | 1 | 6.2206 | 10 | 0 | 0
209.85 | 49.65 | 49.65 | 1 | 1 | 10 | 49.8 | 1 | 0.34412 | 3.4412 | 6.7206 | 6.7206 | 0 | 12 | 1 | 1 | 6.7206 | 10 | 0 | 0
209.9 | 49.59 | 49.59 | 1 | 1 | 10 | 49.8 | 1 | 0.44412 | 4.4412 | 7.2206 | 7.2206 | 0 | 12 | 1 | 1 | 7.2206 | 10 | 0 | 0
209.95 | 49.59 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.54412 | 5.4412 | 7.7206 | 7.7206 | 0 | 12 | 1 | 1 | 7.7206 | 10 | 0 | 0
210 | 49.66 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.64412 | 6.4412 | 8.2206 | 8.2206 | 0 | 12 | 1 | 1 | 8.2206 | 10 | 0 | 0
210.05 | 49.66 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.74412 | 7.4412 | 8.7206 | 8.7206 | 0 | 12 | 1 | 1 | 8.7206 | 10 | 0 | 0
210.1 | 49.63 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.84412 | 8.4412 | 9.2206 | 9.2206 | 0 | 12 | 1 | 1 | 9.2206 | 10 | 0 | 0
210.15 | 49.63 | 49.59 | 1 | 1 | 10 | 49.72 | 1 | 0.94412 | 9.4412 | 9.7206 | 9.7206 | 0 | 12 | 1 | 1 | 9.7206 | 10 | 0 | 0
210.2 | 49.61 | 49.59 | 1 | 1 | 10 | 49.72 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
210.25 | 49.61 | 49.59 | 1 | 1 | 10 | 49.67 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
210.3 | 49.54 | 49.54 | 1 | 1 | 10 | 49.67 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
210.35 | 49.54 | 49.54 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
210.4 | 49.46 | 49.46 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
210.45 | 49.46 | 49.46 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
210.5 | 49.45 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
210.55 | 49.45 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
210.6 | 49.51 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
210.65 | 49.51 | 49.45 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
210.7 | 49.5 | 49.45 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
210.75 | 49.5 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
210.8 | 49.54 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
210.85 | 49.54 | 49.45 | 1 | 1 | 10 | 49.54 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
210.9 | 49.59 | 49.45 | 1 | 1 | 10 | 49.59 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
210.95 | 49.59 | 49.45 | 1 | 1 | 10 | 49.59 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
211 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
211.05 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
211.1 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
211.15 | 49.61 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
211.2 | 49.53 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
211.25 | 49.53 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
211.3 | 49.54 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
211.35 | 49.54 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
211.4 | 49.61 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
211.45 | 49.61 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
211.5 | 49.66 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
211.55 | 49.66 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
211.6 | 49.64 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
211.65 | 49.64 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
211.7 | 49.69 | 49.53 | 1 | 1 | 10 | 49.69 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
211.75 | 49.69 | 49.53 | 1 | 1 | 10 | 49.69 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
211.8 | 49.74 | 49.53 | 1 | 1 | 10 | 49.74 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
211.85 | 49.74 | 49.54 | 1 | 1 | 10 | 49.74 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
211.9 | 49.78 | 49.54 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
211.95 | 49.78 | 49.61 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
212 | 49.82 | 49.61 | 1 | 1 | 10 | 49.82 | 0.81 | 0.81 | 8.1 | 9.05 | 9.05 | 0 | 12 | 1 | 1 | 9.05 | 10 | 0 | 0
212.05 | 49.82 | 49.64 | 1 | 1 | 10 | 49.82 | 0.81 | 0.81 | 8.1 | 9.05 | 9.05 | 0 | 12 | 1 | 1 | 9.05 | 10 | 0 | 0
212.1 | 49.86 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
212.15 | 49.86 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
212.2 | 49.84 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
212.25 | 49.84 | 49.69 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
212.3 | 49.91 | 49.69 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
212.35 | 49.91 | 49.74 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
212.4 | 49.97 | 49.74 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
212.45 | 49.97 | 49.78 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
212.5 | 50.03 | 49.78 | 1 | 1 | 10 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.9559 | 4.9559 | 0 | 12 | 1 | 1 | 4.9559 | 10 | 0 | 0
212.55 | 50.03 | 49.82 | 0.81 | 0.9 | 9 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.4559 | 4.4559 | 0 | 12 | 1 | 1 | 4.4559 | 10 | 0 | 0
212.6 | 50.05 | 49.82 | 0.81 | 0.81 | 8.1 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 3.9471 | 3.9471 | 0 | 12 | 1 | 1 | 3.9471 | 10 | 0 | 0
212.65 | 50.05 | 49.84 | 0.62 | 0.71 | 7.1 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 3.4471 | 3.4471 | 0 | 12 | 1 | 1 | 3.4471 | 10 | 0 | 0
212.7 | 50.01 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
212.75 | 50.01 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
212.8 | 49.95 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
212.85 | 49.95 | 49.91 | 0.044118 | 0.52 | 5.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.4971 | 2.4971 | 0 | 12 | 1 | 1 | 2.4971 | 10 | 0 | 0
212.9 | 49.99 | 49.91 | 0.044118 | 0.42 | 4.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 1.9971 | 1.9971 | 0 | 12 | 1 | 1 | 1.9971 | 10 | 0 | 0
212.95 | 49.99 | 49.95 | 0.020588 | 0.32 | 3.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 1.4971 | 1.4971 | 0 | 12 | 1 | 1 | 1.4971 | 10 | 0 | 0
213 | 49.92 | 49.92 | 0.038235 | 0.22 | 2.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.99706 | 0.99706 | 0 | 12 | 1 | 1 | 0.99706 | 10 | 0 | 0
213.05 | 49.92 | 49.92 | 0.038235 | 0.12 | 1.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.49706 | 0.49706 | 0 | 12 | 1 | 1 | 0.49706 | 10 | 0 | 0
213.1 | 49.97 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
213.15 | 49.97 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
213.2 | 50.02 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
213.25 | 50.02 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.17647 | 0.17647 | 0 | 12 | 1 | 1 | 0.17647 | 10 | 0 | 0
213.3 | 50.07 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
213.35 | 50.07 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
213.4 | 50.06 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
213.45 | 50.06 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
213.5 | 50.13 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
213.55 | 50.13 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
213.6 | 50.09 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
213.65 | 50.09 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6309 | -1.6309 | 0 | 12 | 1 | 1 | -1.6309 | 10 | 0 | 0
213.7 | 50.07 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6309 | -1.6309 | 0 | 12 | 1 | 1 | -1.6309 | 10 | 0 | 0
213.75 | 50.07 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6897 | -1.6897 | 0 | 12 | 1 | 1 | -1.6897 | 10 | 0 | 0
213.8 | 50.07 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6897 | -1.6897 | 0 | 12 | 1 | 1 | -1.6897 | 10 | 0 | 0
213.85 | 50.07 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.13 | -0.335 | -0.335 | -3.35 | -1.8074 | -1.8074 | 0 | 12 | 1 | 1 | -1.8074 | 10 | 0 | 0
213.9 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.13 | -0.335 | -0.335 | -3.35 | -1.7779 | -1.7779 | 0 | 12 | 1 | 1 | -1.7779 | 10 | 0 | 0
213.95 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.13 | -0.335 | -0.335 | -3.35 | -1.7779 | -1.7779 | 0 | 12 | 1 | 1 | -1.7779 | 10 | 0 | 0
214 | 50.01 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
214.05 | 50.01 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
214.1 | 50.07 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
214.15 | 50.07 | 50.01 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.235 | -2.35 | -1.175 | -1.175 | 0 | 12 | 1 | 1 | -1.175 | 10 | 0 | 0
214.2 | 50.05 | 50.01 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.135 | -1.35 | -0.675 | -0.675 | 0 | 12 | 1 | 1 | -0.675 | 10 | 0 | 0
214.25 | 50.05 | 50.01 | 0 | 0 | 0 | 50.07 | -0.032353 | -0.035 | -0.35 | -0.175 | -0.175 | 0 | 12 | 1 | 1 | -0.175 | 10 | 0 | 0
214.3 | 50.1 | 50.01 | 0 | 0 | 0 | 50.1 | -0.05 | -0.05 | -0.5 | -0.25 | -0.25 | 0 | 12 | 1 | 1 | -0.25 | 10 | 0 | 0
214.35 | 50.1 | 50.01 | 0 | 0 | 0 | 50.1 | -0.05 | -0.05 | -0.5 | -0.25 | -0.25 | 0 | 12 | 1 | 1 | -0.25 | 10 | 0 | 0
214.4 | 50.11 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
214.45 | 50.11 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
214.5 | 50.06 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
214.55 | 50.06 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
214.6 | 50.04 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
214.65 | 50.04 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
214.7 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
214.75 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
214.8 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
214.85 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
214.9 | 50.11 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
214.95 | 50.11 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
215 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
215.05 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
215.1 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
215.15 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
215.2 | 50.02 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.11 | -0.145 | -0.145 | -1.45 | -0.73971 | -0.73971 | 0 | 12 | 1 | 1 | -0.73971 | 10 | 0 | 0
215.25 | 50.02 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.11 | -0.145 | -0.145 | -1.45 | -0.73971 | -0.73971 | 0 | 12 | 1 | 1 | -0.73971 | 10 | 0 | 0
215.3 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
215.35 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
215.4 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
215.45 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
215.5 | 50.01 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
215.55 | 50.01 | 50 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.045 | -0.45 | -0.225 | -0.225 | 0 | 12 | 1 | 1 | -0.225 | 10 | 0 | 0
215.6 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
215.65 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
215.7 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
215.75 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
215.8 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.14706 | 0.14706 | 0 | 12 | 1 | 1 | 0.14706 | 10 | 0 | 0
215.85 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
215.9 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
215.95 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
216 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
216.05 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
216.1 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
216.15 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
216.2 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
216.25 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
216.3 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
216.35 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
216.4 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
216.45 | 50 | 50 | 0 | 0 | 0 | 50.01 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
216.5 | 49.5 | 49.5 | 1 | 1 | 10 | 50.01 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
216.55 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
216.6 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
216.65 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
216.7 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
216.75 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
216.8 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
216.85 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
216.9 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
216.95 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
217 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
217.05 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.1 | 1 | 5.5 | 5.5 | 0 | 12 | 1 | 1 | 5.5 | 10 | 0 | 0
217.1 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.2 | 2 | 6 | 6 | 0 | 12 | 1 | 1 | 6 | 10 | 0 | 0
217.15 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.3 | 3 | 6.5 | 6.5 | 0 | 12 | 1 | 1 | 6.5 | 10 | 0 | 0
217.2 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.4 | 4 | 7 | 7 | 0 | 12 | 1 | 1 | 7 | 10 | 0 | 0
217.25 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.5 | 5 | 7.5 | 7.5 | 0 | 12 | 1 | 1 | 7.5 | 10 | 0 | 0
217.3 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.6 | 6 | 8 | 8 | 0 | 12 | 1 | 1 | 8 | 10 | 0 | 0
217.35 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.7 | 7 | 8.5 | 8.5 | 0 | 12 | 1 | 1 | 8.5 | 10 | 0 | 0
217.4 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.8 | 8 | 9 | 9 | 0 | 12 | 1 | 1 | 9 | 10 | 0 | 0
217.45 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.9 | 9 | 9.5 | 9.5 | 0 | 12 | 1 | 1 | 9.5 | 10 | 0 | 0
217.5 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
217.55 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
217.6 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
217.65 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
217.7 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
217.75 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
217.8 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
217.85 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
217.9 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
217.95 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
218 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
218.05 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
218.1 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
218.15 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
218.2 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
218.25 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
218.3 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
218.35 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
218.4 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
218.45 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
218.5 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
218.55 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
218.6 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
218.65 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
218.7 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
218.75 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
218.8 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
218.85 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
218.9 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
218.95 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
219 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
219.05 | 50.5 | 50.5 | -1 | 0.9 | 9 | 50.5 | -1 | -1 | -10 | -0.5 | -0.5 | 0 | 12 | 1 | 1 | -0.5 | 10 | 0 | 0
219.1 | 50.5 | 50.5 | -1 | 0.8 | 8 | 50.5 | -1 | -1 | -10 | -1 | -1 | 0 | 12 | 1 | 1 | -1 | 10 | 0 | 0
219.15 | 50.5 | 50.5 | -1 | 0.7 | 7 | 50.5 | -1 | -1 | -10 | -1.5 | -1.5 | 0 | 12 | 1 | 1 | -1.5 | 10 | 0 | 0
219.2 | 50.5 | 50.5 | -1 | 0.6 | 6 | 50.5 | -1 | -1 | -10 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
219.25 | 50.5 | 50.5 | -1 | 0.5 | 5 | 50.5 | -1 | -1 | -10 | -2.5 | -2.5 | 0 | 12 | 1 | 1 | -2.5 | 10 | 0 | 0
219.3 | 50.5 | 50.5 | -1 | 0.4 | 4 | 50.5 | -1 | -1 | -10 | -3 | -3 | 0 | 12 | 1 | 1 | -3 | 10 | 0 | 0
219.35 | 50.5 | 50.5 | -1 | 0.3 | 3 | 50.5 | -1 | -1 | -10 | -3.5 | -3.5 | 0 | 12 | 1 | 1 | -3.5 | 10 | 0 | 0
219.4 | 50.5 | 50.5 | -1 | 0.2 | 2 | 50.5 | -1 | -1 | -10 | -4 | -4 | 0 | 12 | 1 | 1 | -4 | 10 | 0 | 0
219.45 | 50.5 | 50.5 | -1 | 0.1 | 1 | 50.5 | -1 | -1 | -10 | -4.5 | -4.5 | 0 | 12 | 1 | 1 | -4.5 | 10 | 0 | 0
219.5 | 50.5 | 50.5 | -1 | 0 | 0 | 50.5 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
219.55 | 50.5 | 50.5 | -1 | -0.1 | -1 | 50.5 | -1 | -1 | -10 | -5.5 | -5.5 | 0 | 12 | 1 | 1 | -5.5 | 10 | 0 | 0
219.6 | 50.5 | 50.5 | -1 | -0.2 | -2 | 50.5 | -1 | -1 | -10 | -6 | -6 | 0 | 12 | 1 | 1 | -6 | 10 | 0 | 0
219.65 | 50.5 | 50.5 | -1 | -0.3 | -3 | 50.5 | -1 | -1 | -10 | -6.5 | -6.5 | 0 | 12 | 1 | 1 | -6.5 | 10 | 0 | 0
219.7 | 50.5 | 50.5 | -1 | -0.4 | -4 | 50.5 | -1 | -1 | -10 | -7 | -7 | 0 | 12 | 1 | 1 | -7 | 10 | 0 | 0
219.75 | 50.5 | 50.5 | -1 | -0.5 | -5 | 50.5 | -1 | -1 | -10 | -7.5 | -7.5 | 0 | 12 | 1 | 1 | -7.5 | 10 | 0 | 0
219.8 | 50.5 | 50.5 | -1 | -0.6 | -6 | 50.5 | -1 | -1 | -10 | -8 | -8 | 0 | 12 | 1 | 1 | -8 | 10 | 0 | 0
219.85 | 50.5 | 50.5 | -1 | -0.7 | -7 | 50.5 | -1 | -1 | -10 | -8.5 | -8.5 | 0 | 12 | 1 | 1 | -8.5 | 10 | 0 | 0
219.9 | 50.5 | 50.5 | -1 | -0.8 | -8 | 50.5 | -1 | -1 | -10 | -9 | -9 | 0 | 12 | 1 | 1 | -9 | 10 | 0 | 0
219.95 | 50.5 | 50.5 | -1 | -0.9 | -9 | 50.5 | -1 | -1 | -10 | -9.5 | -9.5 | 0 | 12 | 1 | 1 | -9.5 | 10 | 0 | 0
220 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
220.05 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
220.1 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
220.15 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
220.2 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
220.25 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
220.3 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
220.35 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
220.4 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
220.45 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
220.5 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
220.55 | 50.47 | 50.47 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
220.6 | 50.45 | 50.45 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
220.65 | 50.42 | 50.42 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
220.7 | 50.4 | 50.4 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
220.75 | 50.37 | 50.37 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
220.8 | 50.35 | 50.35 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
220.85 | 50.32 | 50.32 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
220.9 | 50.29 | 50.29 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
220.95 | 50.27 | 50.27 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
221 | 50.24 | 50.24 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
221.05 | 50.22 | 50.22 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
221.1 | 50.19 | 50.19 | -0.905 | -0.905 | -9.05 | 50.47 | -1 | -1 | -10 | -9.525 | -9.525 | 0 | 12 | 1 | 1 | -9.525 | 10 | 0 | 0
221.15 | 50.17 | 50.17 | -0.715 | -0.715 | -7.15 | 50.45 | -1 | -1 | -10 | -8.575 | -8.575 | 0 | 12 | 1 | 1 | -8.575 | 10 | 0 | 0
221.2 | 50.14 | 50.14 | -0.43 | -0.43 | -4.3 | 50.42 | -1 | -1 | -10 | -7.15 | -7.15 | 0 | 12 | 1 | 1 | -7.15 | 10 | 0 | 0
221.25 | 50.12 | 50.12 | -0.24 | -0.24 | -2.4 | 50.4 | -1 | -1 | -10 | -6.2 | -6.2 | 0 | 12 | 1 | 1 | -6.2 | 10 | 0 | 0
221.3 | 50.09 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 50.37 | -1 | -1 | -10 | -5.2206 | -5.2206 | 0 | 12 | 1 | 1 | -5.2206 | 10 | 0 | 0
221.35 | 50.06 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.35 | -1 | -1 | -10 | -5.1324 | -5.1324 | 0 | 12 | 1 | 1 | -5.1324 | 10 | 0 | 0
221.4 | 50.04 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.32 | -1 | -1 | -10 | -5.0735 | -5.0735 | 0 | 12 | 1 | 1 | -5.0735 | 10 | 0 | 0
221.45 | 50.01 | 50.01 | 0 | 0 | 0 | 50.29 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
221.5 | 49.99 | 49.99 | 0 | 0 | 0 | 50.27 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
221.55 | 49.96 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.24 | -1 | -1 | -10 | -4.9265 | -4.9265 | 0 | 12 | 1 | 1 | -4.9265 | 10 | 0 | 0
221.6 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.22 | -1 | -1 | -10 | -4.8676 | -4.8676 | 0 | 12 | 1 | 1 | -4.8676 | 10 | 0 | 0
221.65 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.19 | -0.905 | -0.905 | -9.05 | -4.3044 | -4.3044 | 0 | 12 | 1 | 1 | -4.3044 | 10 | 0 | 0
221.7 | 49.88 | 49.88 | 0.24 | 0.24 | 2.4 | 50.17 | -0.715 | -0.805 | -8.05 | -2.825 | -2.825 | 0 | 12 | 1 | 1 | -2.825 | 10 | 0 | 0
221.75 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.14 | -0.43 | -0.705 | -7.05 | -1.375 | -1.375 | 0 | 12 | 1 | 1 | -1.375 | 10 | 0 | 0
221.8 | 49.83 | 49.83 | 0.715 | 0.715 | 7.15 | 50.12 | -0.24 | -0.605 | -6.05 | 0.55 | 0.55 | 0 | 12 | 1 | 1 | 0.55 | 10 | 0 | 0
221.85 | 49.81 | 49.81 | 0.905 | 0.905 | 9.05 | 50.09 | -0.044118 | -0.505 | -5.05 | 2 | 2 | 0 | 12 | 1 | 1 | 2 | 10 | 0 | 0
221.9 | 49.78 | 49.78 | 1 | 1 | 10 | 50.06 | -0.026471 | -0.405 | -4.05 | 2.975 | 2.975 | 0 | 12 | 1 | 1 | 2.975 | 10 | 0 | 0
221.95 | 49.76 | 49.76 | 1 | 1 | 10 | 50.04 | -0.014706 | -0.305 | -3.05 | 3.475 | 3.475 | 0 | 12 | 1 | 1 | 3.475 | 10 | 0 | 0
222 | 49.73 | 49.73 | 1 | 1 | 10 | 50.01 | 0 | -0.205 | -2.05 | 3.975 | 3.975 | 0 | 12 | 1 | 1 | 3.975 | 10 | 0 | 0
222.05 | 49.71 | 49.71 | 1 | 1 | 10 | 49.99 | 0 | -0.105 | -1.05 | 4.475 | 4.475 | 0 | 12 | 1 | 1 | 4.475 | 10 | 0 | 0
222.1 | 49.68 | 49.68 | 1 | 1 | 10 | 49.96 | 0.014706 | -0.005 | -0.05 | 4.975 | 4.975 | 0 | 12 | 1 | 1 | 4.975 | 10 | 0 | 0
222.15 | 49.65 | 49.65 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
222.2 | 49.63 | 49.63 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
222.25 | 49.6 | 49.6 | 1 | 1 | 10 | 49.88 | 0.24 | 0.14412 | 1.4412 | 5.7206 | 5.7206 | 0 | 12 | 1 | 1 | 5.7206 | 10 | 0 | 0
222.3 | 49.58 | 49.58 | 1 | 1 | 10 | 49.86 | 0.43 | 0.24412 | 2.4412 | 6.2206 | 6.2206 | 0 | 12 | 1 | 1 | 6.2206 | 10 | 0 | 0
222.35 | 49.55 | 49.55 | 1 | 1 | 10 | 49.83 | 0.715 | 0.34412 | 3.4412 | 6.7206 | 6.7206 | 0 | 12 | 1 | 1 | 6.7206 | 10 | 0 | 0
222.4 | 49.53 | 49.53 | 1 | 1 | 10 | 49.81 | 0.905 | 0.44412 | 4.4412 | 7.2206 | 7.2206 | 0 | 12 | 1 | 1 | 7.2206 | 10 | 0 | 0
222.45 | 49.5 | 49.5 | 1 | 1 | 10 | 49.78 | 1 | 0.54412 | 5.4412 | 7.7206 | 7.7206 | 0 | 12 | 1 | 1 | 7.7206 | 10 | 0 | 0
222.5 | 49.5 | 49.5 | 1 | 1 | 10 | 49.76 | 1 | 0.64412 | 6.4412 | 8.2206 | 8.2206 | 0 | 12 | 1 | 1 | 8.2206 | 10 | 0 | 0
222.55 | 49.53 | 49.5 | 1 | 1 | 10 | 49.73 | 1 | 0.74412 | 7.4412 | 8.7206 | 8.7206 | 0 | 12 | 1 | 1 | 8.7206 | 10 | 0 | 0
222.6 | 49.55 | 49.5 | 1 | 1 | 10 | 49.71 | 1 | 0.84412 | 8.4412 | 9.2206 | 9.2206 | 0 | 12 | 1 | 1 | 9.2206 | 10 | 0 | 0
222.65 | 49.58 | 49.5 | 1 | 1 | 10 | 49.68 | 1 | 0.94412 | 9.4412 | 9.7206 | 9.7206 | 0 | 12 | 1 | 1 | 9.7206 | 10 | 0 | 0
222.7 | 49.6 | 49.5 | 1 | 1 | 10 | 49.65 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
222.75 | 49.63 | 49.5 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
222.8 | 49.65 | 49.5 | 1 | 1 | 10 | 49.65 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
222.85 | 49.68 | 49.5 | 1 | 1 | 10 | 49.68 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
222.9 | 49.71 | 49.5 | 1 | 1 | 10 | 49.71 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
222.95 | 49.73 | 49.5 | 1 | 1 | 10 | 49.73 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
223 | 49.76 | 49.5 | 1 | 1 | 10 | 49.76 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
223.05 | 49.78 | 49.5 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
223.1 | 49.81 | 49.53 | 1 | 1 | 10 | 49.81 | 0.905 | 0.905 | 9.05 | 9.525 | 9.525 | 0 | 12 | 1 | 1 | 9.525 | 10 | 0 | 0
223.15 | 49.83 | 49.55 | 1 | 1 | 10 | 49.83 | 0.715 | 0.715 | 7.15 | 8.575 | 8.575 | 0 | 12 | 1 | 1 | 8.575 | 10 | 0 | 0
223.2 | 49.86 | 49.58 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
223.25 | 49.88 | 49.6 | 1 | 1 | 10 | 49.88 | 0.24 | 0.24 | 2.4 | 6.2 | 6.2 | 0 | 12 | 1 | 1 | 6.2 | 10 | 0 | 0
223.3 | 49.91 | 49.63 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
223.35 | 49.94 | 49.65 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
223.4 | 49.96 | 49.68 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
223.45 | 49.99 | 49.71 | 1 | 1 | 10 | 49.99 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
223.5 | 50.01 | 49.73 | 1 | 1 | 10 | 50.01 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
223.55 | 50.04 | 49.76 | 1 | 1 | 10 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 4.9265 | 4.9265 | 0 | 12 | 1 | 1 | 4.9265 | 10 | 0 | 0
223.6 | 50.06 | 49.78 | 1 | 1 | 10 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 4.8676 | 4.8676 | 0 | 12 | 1 | 1 | 4.8676 | 10 | 0 | 0
223.65 | 50.09 | 49.81 | 0.905 | 0.905 | 9.05 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 4.3044 | 4.3044 | 0 | 12 | 1 | 1 | 4.3044 | 10 | 0 | 0
223.7 | 50.12 | 49.83 | 0.715 | 0.805 | 8.05 | 50.12 | -0.24 | -0.24 | -2.4 | 2.825 | 2.825 | 0 | 12 | 1 | 1 | 2.825 | 10 | 0 | 0
223.75 | 50.14 | 49.86 | 0.43 | 0.705 | 7.05 | 50.14 | -0.43 | -0.43 | -4.3 | 1.375 | 1.375 | 0 | 12 | 1 | 1 | 1.375 | 10 | 0 | 0
223.8 | 50.17 | 49.88 | 0.24 | 0.605 | 6.05 | 50.17 | -0.715 | -0.715 | -7.15 | -0.55 | -0.55 | 0 | 12 | 1 | 1 | -0.55 | 10 | 0 | 0
223.85 | 50.19 | 49.91 | 0.044118 | 0.505 | 5.05 | 50.19 | -0.905 | -0.905 | -9.05 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
223.9 | 50.22 | 49.94 | 0.026471 | 0.405 | 4.05 | 50.22 | -1 | -1 | -10 | -2.975 | -2.975 | 0 | 12 | 1 | 1 | -2.975 | 10 | 0 | 0
223.95 | 50.24 | 49.96 | 0.014706 | 0.305 | 3.05 | 50.24 | -1 | -1 | -10 | -3.475 | -3.475 | 0 | 12 | 1 | 1 | -3.475 | 10 | 0 | 0
224 | 50.27 | 49.99 | 0 | 0.205 | 2.05 | 50.27 | -1 | -1 | -10 | -3.975 | -3.975 | 0 | 12 | 1 | 1 | -3.975 | 10 | 0 | 0
224.05 | 50.29 | 50.01 | 0 | 0.105 | 1.05 | 50.29 | -1 | -1 | -10 | -4.475 | -4.475 | 0 | 12 | 1 | 1 | -4.475 | 10 | 0 | 0
224.1 | 50.32 | 50.04 | -0.014706 | 0.005 | 0.05 | 50.32 | -1 | -1 | -10 | -4.975 | -4.975 | 0 | 12 | 1 | 1 | -4.975 | 10 | 0 | 0
224.15 | 50.35 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.35 | -1 | -1 | -10 | -5.1324 | -5.1324 | 0 | 12 | 1 | 1 | -5.1324 | 10 | 0 | 0
224.2 | 50.37 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 50.37 | -1 | -1 | -10 | -5.2206 | -5.2206 | 0 | 12 | 1 | 1 | -5.2206 | 10 | 0 | 0
224.25 | 50.4 | 50.12 | -0.24 | -0.14412 | -1.4412 | 50.4 | -1 | -1 | -10 | -5.7206 | -5.7206 | 0 | 12 | 1 | 1 | -5.7206 | 10 | 0 | 0
224.3 | 50.42 | 50.14 | -0.43 | -0.24412 | -2.4412 | 50.42 | -1 | -1 | -10 | -6.2206 | -6.2206 | 0 | 12 | 1 | 1 | -6.2206 | 10 | 0 | 0
224.35 | 50.45 | 50.17 | -0.715 | -0.34412 | -3.4412 | 50.45 | -1 | -1 | -10 | -6.7206 | -6.7206 | 0 | 12 | 1 | 1 | -6.7206 | 10 | 0 | 0
224.4 | 50.47 | 50.19 | -0.905 | -0.44412 | -4.4412 | 50.47 | -1 | -1 | -10 | -7.2206 | -7.2206 | 0 | 12 | 1 | 1 | -7.2206 | 10 | 0 | 0
224.45 | 50.5 | 50.22 | -1 | -0.54412 | -5.4412 | 50.5 | -1 | -1 | -10 | -7.7206 | -7.7206 | 0 | 12 | 1 | 1 | -7.7206 | 10 | 0 | 0
224.5 | 50.5 | 50.24 | -1 | -0.64412 | -6.4412 | 50.5 | -1 | -1 | -10 | -8.2206 | -8.2206 | 0 | 12 | 1 | 1 | -8.2206 | 10 | 0 | 0
224.55 | 50.47 | 50.27 | -1 | -0.74412 | -7.4412 | 50.5 | -1 | -1 | -10 | -8.7206 | -8.7206 | 0 | 12 | 1 | 1 | -8.7206 | 10 | 0 | 0
224.6 | 50.45 | 50.29 | -1 | -0.84412 | -8.4412 | 50.5 | -1 | -1 | -10 | -9.2206 | -9.2206 | 0 | 12 | 1 | 1 | -9.2206 | 10 | 0 | 0
224.65 | 50.42 | 50.32 | -1 | -0.94412 | -9.4412 | 50.5 | -1 | -1 | -10 | -9.7206 | -9.7206 | 0 | 12 | 1 | 1 | -9.7206 | 10 | 0 | 0
224.7 | 50.39 | 50.35 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
224.75 | 50.37 | 50.37 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
224.8 | 50.34 | 50.34 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
224.85 | 50.32 | 50.32 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
224.9 | 50.29 | 50.29 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
224.95 | 50.26 | 50.26 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
225 | 50.24 | 50.24 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
225.05 | 50.21 | 50.21 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
225.1 | 50.18 | 50.18 | -0.81 | -0.81 | -8.1 | 50.47 | -1 | -1 | -10 | -9.05 | -9.05 | 0 | 12 | 1 | 1 | -9.05 | 10 | 0 | 0
225.15 | 50.16 | 50.16 | -0.62 | -0.62 | -6.2 | 50.45 | -1 | -1 | -10 | -8.1 | -8.1 | 0 | 12 | 1 | 1 | -8.1 | 10 | 0 | 0
225.2 | 50.13 | 50.13 | -0.335 | -0.335 | -3.35 | 50.42 | -1 | -1 | -10 | -6.675 | -6.675 | 0 | 12 | 1 | 1 | -6.675 | 10 | 0 | 0
225.25 | 50.11 | 50.11 | -0.145 | -0.145 | -1.45 | 50.39 | -1 | -1 | -10 | -5.725 | -5.725 | 0 | 12 | 1 | 1 | -5.725 | 10 | 0 | 0
225.3 | 50.08 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 50.37 | -1 | -1 | -10 | -5.1912 | -5.1912 | 0 | 12 | 1 | 1 | -5.1912 | 10 | 0 | 0
225.35 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.34 | -1 | -1 | -10 | -5.1029 | -5.1029 | 0 | 12 | 1 | 1 | -5.1029 | 10 | 0 | 0
225.4 | 50.03 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 50.32 | -1 | -1 | -10 | -5.0441 | -5.0441 | 0 | 12 | 1 | 1 | -5.0441 | 10 | 0 | 0
225.45 | 50 | 50 | 0 | 0 | 0 | 50.29 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
225.5 | 50 | 50 | 0 | 0 | 0 | 50.26 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
225.55 | 50 | 50 | 0 | 0 | 0 | 50.24 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
225.6 | 50 | 50 | 0 | 0 | 0 | 50.21 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
225.65 | 50 | 50 | 0 | 0 | 0 | 50.18 | -0.81 | -0.9 | -9 | -4.5 | -4.5 | 0 | 12 | 1 | 1 | -4.5 | 10 | 0 | 0
225.7 | 50 | 50 | 0 | 0 | 0 | 50.16 | -0.62 | -0.8 | -8 | -4 | -4 | 0 | 12 | 1 | 1 | -4 | 10 | 0 | 0
225.75 | 50 | 50 | 0 | 0 | 0 | 50.13 | -0.335 | -0.7 | -7 | -3.5 | -3.5 | 0 | 12 | 1 | 1 | -3.5 | 10 | 0 | 0
225.8 | 50.01 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.6 | -6 | -3 | -3 | 0 | 12 | 1 | 1 | -3 | 10 | 0 | 0
225.85 | 50.01 | 50 | 0 | 0 | 0 | 50.08 | -0.038235 | -0.5 | -5 | -2.5 | -2.5 | 0 | 12 | 1 | 1 | -2.5 | 10 | 0 | 0
225.9 | 49.99 | 49.99 | 0 | 0 | 0 | 50.05 | -0.020588 | -0.4 | -4 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
225.95 | 49.99 | 49.99 | 0 | 0 | 0 | 50.03 | -0.0088235 | -0.3 | -3 | -1.5 | -1.5 | 0 | 12 | 1 | 1 | -1.5 | 10 | 0 | 0
226 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | -0.2 | -2 | -0.83824 | -0.83824 | 0 | 12 | 1 | 1 | -0.83824 | 10 | 0 | 0
226.05 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | -0.1 | -1 | -0.33824 | -0.33824 | 0 | 12 | 1 | 1 | -0.33824 | 10 | 0 | 0
226.1 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
226.15 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
226.2 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
226.25 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
226.3 | 49.89 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
226.35 | 49.89 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
226.4 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50.01 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
226.45 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
226.5 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
226.55 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 2.7868 | 2.7868 | 0 | 12 | 1 | 1 | 2.7868 | 10 | 0 | 0
226.6 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 2.7868 | 2.7868 | 0 | 12 | 1 | 1 | 2.7868 | 10 | 0 | 0
226.65 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 2.8456 | 2.8456 | 0 | 12 | 1 | 1 | 2.8456 | 10 | 0 | 0
226.7 | 49.94 | 49.85 | 0.525 | 0.525 | 5.25 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 2.7574 | 2.7574 | 0 | 12 | 1 | 1 | 2.7574 | 10 | 0 | 0
226.75 | 49.94 | 49.85 | 0.525 | 0.525 | 5.25 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 2.7574 | 2.7574 | 0 | 12 | 1 | 1 | 2.7574 | 10 | 0 | 0
226.8 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
226.85 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
226.9 | 49.93 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
226.95 | 49.93 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
227 | 49.96 | 49.85 | 0.525 | 0.525 | 5.25 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 2.6985 | 2.6985 | 0 | 12 | 1 | 1 | 2.6985 | 10 | 0 | 0
227.05 | 49.96 | 49.85 | 0.525 | 0.525 | 5.25 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 2.6985 | 2.6985 | 0 | 12 | 1 | 1 | 2.6985 | 10 | 0 | 0
227.1 | 49.99 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
227.15 | 49.99 | 49.91 | 0.044118 | 0.425 | 4.25 | 49.99 | 0 | 0 | 0 | 2.125 | 2.125 | 0 | 12 | 1 | 1 | 2.125 | 10 | 0 | 0
227.2 | 49.99 | 49.91 | 0.044118 | 0.325 | 3.25 | 49.99 | 0 | 0 | 0 | 1.625 | 1.625 | 0 | 12 | 1 | 1 | 1.625 | 10 | 0 | 0
227.25 | 49.99 | 49.93 | 0.032353 | 0.225 | 2.25 | 49.99 | 0 | 0 | 0 | 1.125 | 1.125 | 0 | 12 | 1 | 1 | 1.125 | 10 | 0 | 0
227.3 | 49.96 | 49.93 | 0.032353 | 0.125 | 1.25 | 49.99 | 0 | 0 | 0 | 0.625 | 0.625 | 0 | 12 | 1 | 1 | 0.625 | 10 | 0 | 0
227.35 | 49.96 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 49.99 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
227.4 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
227.45 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
227.5 | 50.05 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.058824 | 0.058824 | 0 | 12 | 1 | 1 | 0.058824 | 10 | 0 | 0
227.55 | 50.05 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
227.6 | 49.97 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
227.65 | 49.97 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
227.7 | 49.92 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
227.75 | 49.92 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
227.8 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
227.85 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
227.9 | 49.94 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
227.95 | 49.94 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
228 | 50.01 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
228.05 | 50.01 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
228.1 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
228.15 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
228.2 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
228.25 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
228.3 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
228.35 | 49.95 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
228.4 | 49.97 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
228.45 | 49.97 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
228.5 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
228.55 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
228.6 | 49.87 | 49.87 | 0.335 | 0.335 | 3.35 | 50.01 | 0 | 0 | 0 | 1.675 | 1.675 | 0 | 12 | 1 | 1 | 1.675 | 10 | 0 | 0
228.65 | 49.87 | 49.87 | 0.335 | 0.335 | 3.35 | 49.99 | 0 | 0 | 0 | 1.675 | 1.675 | 0 | 12 | 1 | 1 | 1.675 | 10 | 0 | 0
228.7 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
228.75 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 2.6691 | 2.6691 | 0 | 12 | 1 | 1 | 2.6691 | 10 | 0 | 0
228.8 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
228.85 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
228.9 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
228.95 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
229 | 49.84 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
229.05 | 49.84 | 49.79 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
229.1 | 49.89 | 49.79 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
229.15 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.12647 | 1.2647 | 5.6324 | 5.6324 | 0 | 12 | 1 | 1 | 5.6324 | 10 | 0 | 0
229.2 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.145 | 1.45 | 5.725 | 5.725 | 0 | 12 | 1 | 1 | 5.725 | 10 | 0 | 0
229.25 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.145 | 1.45 | 5.725 | 5.725 | 0 | 12 | 1 | 1 | 5.725 | 10 | 0 | 0
229.3 | 49.96 | 49.79 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
229.35 | 49.96 | 49.79 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
229.4 | 50.02 | 49.79 | 1 | 1 | 10 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 4.9853 | 4.9853 | 0 | 12 | 1 | 1 | 4.9853 | 10 | 0 | 0
229.45 | 50.02 | 49.79 | 1 | 1 | 10 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 4.9853 | 4.9853 | 0 | 12 | 1 | 1 | 4.9853 | 10 | 0 | 0
229.5 | 50.03 | 49.79 | 1 | 1 | 10 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.9559 | 4.9559 | 0 | 12 | 1 | 1 | 4.9559 | 10 | 0 | 0
229.55 | 50.03 | 49.84 | 0.62 | 0.9 | 9 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.4559 | 4.4559 | 0 | 12 | 1 | 1 | 4.4559 | 10 | 0 | 0
229.6 | 50.02 | 49.84 | 0.62 | 0.8 | 8 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 3.9559 | 3.9559 | 0 | 12 | 1 | 1 | 3.9559 | 10 | 0 | 0
229.65 | 50.02 | 49.89 | 0.145 | 0.7 | 7 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 3.4559 | 3.4559 | 0 | 12 | 1 | 1 | 3.4559 | 10 | 0 | 0
229.7 | 50.08 | 49.89 | 0.145 | 0.6 | 6 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 2.8088 | 2.8088 | 0 | 12 | 1 | 1 | 2.8088 | 10 | 0 | 0
229.75 | 50.08 | 49.89 | 0.145 | 0.5 | 5 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 2.3088 | 2.3088 | 0 | 12 | 1 | 1 | 2.3088 | 10 | 0 | 0
229.8 | 50.01 | 49.89 | 0.145 | 0.4 | 4 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 1.8088 | 1.8088 | 0 | 12 | 1 | 1 | 1.8088 | 10 | 0 | 0
229.85 | 50.01 | 49.96 | 0.014706 | 0.3 | 3 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 1.3088 | 1.3088 | 0 | 12 | 1 | 1 | 1.3088 | 10 | 0 | 0
229.9 | 49.94 | 49.94 | 0.026471 | 0.2 | 2 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.80882 | 0.80882 | 0 | 12 | 1 | 1 | 0.80882 | 10 | 0 | 0
229.95 | 49.94 | 49.94 | 0.026471 | 0.1 | 1 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.30882 | 0.30882 | 0 | 12 | 1 | 1 | 0.30882 | 10 | 0 | 0
230 | 50 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
230.05 | 50 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
230.1 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
230.15 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
230.2 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
230.25 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
230.3 | 49.92 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
230.35 | 49.92 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
230.4 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50.01 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
230.45 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
230.5 | 49.92 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
230.55 | 49.92 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
230.6 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
230.65 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
230.7 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
230.75 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
230.8 | 49.87 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
230.85 | 49.87 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
230.9 | 49.8 | 49.8 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
230.95 | 49.8 | 49.8 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
231 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
231.05 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
231.1 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
231.15 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
231.2 | 49.72 | 49.72 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
231.25 | 49.72 | 49.72 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
231.3 | 49.67 | 49.67 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
231.35 | 49.67 | 49.67 | 1 | 1 | 10 | 49.87 | 0.335 | 0.14412 | 1.4412 | 5.7206 | 5.7206 | 0 | 12 | 1 | 1 | 5.7206 | 10 | 0 | 0
231.4 | 49.65 | 49.65 | 1 | 1 | 10 | 49.87 | 0.335 | 0.24412 | 2.4412 | 6.2206 | 6.2206 | 0 | 12 | 1 | 1 | 6.2206 | 10 | 0 | 0
231.45 | 49.65 | 49.65 | 1 | 1 | 10 | 49.8 | 1 | 0.34412 | 3.4412 | 6.7206 | 6.7206 | 0 | 12 | 1 | 1 | 6.7206 | 10 | 0 | 0
231.5 | 49.59 | 49.59 | 1 | 1 | 10 | 49.8 | 1 | 0.44412 | 4.4412 | 7.2206 | 7.2206 | 0 | 12 | 1 | 1 | 7.2206 | 10 | 0 | 0
231.55 | 49.59 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.54412 | 5.4412 | 7.7206 | 7.7206 | 0 | 12 | 1 | 1 | 7.7206 | 10 | 0 | 0
231.6 | 49.66 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.64412 | 6.4412 | 8.2206 | 8.2206 | 0 | 12 | 1 | 1 | 8.2206 | 10 | 0 | 0
231.65 | 49.66 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.74412 | 7.4412 | 8.7206 | 8.7206 | 0 | 12 | 1 | 1 | 8.7206 | 10 | 0 | 0
231.7 | 49.63 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.84412 | 8.4412 | 9.2206 | 9.2206 | 0 | 12 | 1 | 1 | 9.2206 | 10 | 0 | 0
231.75 | 49.63 | 49.59 | 1 | 1 | 10 | 49.72 | 1 | 0.94412 | 9.4412 | 9.7206 | 9.7206 | 0 | 12 | 1 | 1 | 9.7206 | 10 | 0 | 0
231.8 | 49.61 | 49.59 | 1 | 1 | 10 | 49.72 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
231.85 | 49.61 | 49.59 | 1 | 1 | 10 | 49.67 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
231.9 | 49.54 | 49.54 | 1 | 1 | 10 | 49.67 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
231.95 | 49.54 | 49.54 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
232 | 49.46 | 49.46 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
232.05 | 49.46 | 49.46 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
232.1 | 49.45 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
232.15 | 49.45 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
232.2 | 49.51 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
232.25 | 49.51 | 49.45 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
232.3 | 49.5 | 49.45 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
232.35 | 49.5 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
232.4 | 49.54 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
232.45 | 49.54 | 49.45 | 1 | 1 | 10 | 49.54 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
232.5 | 49.59 | 49.45 | 1 | 1 | 10 | 49.59 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
232.55 | 49.59 | 49.45 | 1 | 1 | 10 | 49.59 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
232.6 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
232.65 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
232.7 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
232.75 | 49.61 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
232.8 | 49.53 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
232.85 | 49.53 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
232.9 | 49.54 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
232.95 | 49.54 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
233 | 49.61 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
233.05 | 49.61 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
233.1 | 49.66 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
233.15 | 49.66 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
233.2 | 49.64 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
233.25 | 49.64 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
233.3 | 49.69 | 49.53 | 1 | 1 | 10 | 49.69 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
233.35 | 49.69 | 49.53 | 1 | 1 | 10 | 49.69 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
233.4 | 49.74 | 49.53 | 1 | 1 | 10 | 49.74 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
233.45 | 49.74 | 49.54 | 1 | 1 | 10 | 49.74 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
233.5 | 49.78 | 49.54 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
233.55 | 49.78 | 49.61 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
233.6 | 49.82 | 49.61 | 1 | 1 | 10 | 49.82 | 0.81 | 0.81 | 8.1 | 9.05 | 9.05 | 0 | 12 | 1 | 1 | 9.05 | 10 | 0 | 0
233.65 | 49.82 | 49.64 | 1 | 1 | 10 | 49.82 | 0.81 | 0.81 | 8.1 | 9.05 | 9.05 | 0 | 12 | 1 | 1 | 9.05 | 10 | 0 | 0
233.7 | 49.86 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
233.75 | 49.86 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
233.8 | 49.84 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
233.85 | 49.84 | 49.69 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
233.9 | 49.91 | 49.69 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
233.95 | 49.91 | 49.74 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
234 | 49.97 | 49.74 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
234.05 | 49.97 | 49.78 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
234.1 | 50.03 | 49.78 | 1 | 1 | 10 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.9559 | 4.9559 | 0 | 12 | 1 | 1 | 4.9559 | 10 | 0 | 0
234.15 | 50.03 | 49.82 | 0.81 | 0.9 | 9 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.4559 | 4.4559 | 0 | 12 | 1 | 1 | 4.4559 | 10 | 0 | 0
234.2 | 50.05 | 49.82 | 0.81 | 0.81 | 8.1 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 3.9471 | 3.9471 | 0 | 12 | 1 | 1 | 3.9471 | 10 | 0 | 0
234.25 | 50.05 | 49.84 | 0.62 | 0.71 | 7.1 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 3.4471 | 3.4471 | 0 | 12 | 1 | 1 | 3.4471 | 10 | 0 | 0
234.3 | 50.01 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
234.35 | 50.01 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
234.4 | 49.95 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
234.45 | 49.95 | 49.91 | 0.044118 | 0.52 | 5.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.4971 | 2.4971 | 0 | 12 | 1 | 1 | 2.4971 | 10 | 0 | 0
234.5 | 49.99 | 49.91 | 0.044118 | 0.42 | 4.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 1.9971 | 1.9971 | 0 | 12 | 1 | 1 | 1.9971 | 10 | 0 | 0
234.55 | 49.99 | 49.95 | 0.020588 | 0.32 | 3.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 1.4971 | 1.4971 | 0 | 12 | 1 | 1 | 1.4971 | 10 | 0 | 0
234.6 | 49.92 | 49.92 | 0.038235 | 0.22 | 2.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.99706 | 0.99706 | 0 | 12 | 1 | 1 | 0.99706 | 10 | 0 | 0
234.65 | 49.92 | 49.92 | 0.038235 | 0.12 | 1.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.49706 | 0.49706 | 0 | 12 | 1 | 1 | 0.49706 | 10 | 0 | 0
234.7 | 49.97 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
234.75 | 49.97 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
234.8 | 50.02 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
234.85 | 50.02 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.17647 | 0.17647 | 0 | 12 | 1 | 1 | 0.17647 | 10 | 0 | 0
234.9 | 50.07 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
234.95 | 50.07 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
235 | 50.06 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
235.05 | 50.06 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
235.1 | 50.13 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
235.15 | 50.13 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
235.2 | 50.09 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
235.25 | 50.09 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6309 | -1.6309 | 0 | 12 | 1 | 1 | -1.6309 | 10 | 0 | 0
235.3 | 50.07 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6309 | -1.6309 | 0 | 12 | 1 | 1 | -1.6309 | 10 | 0 | 0
235.35 | 50.07 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6897 | -1.6897 | 0 | 12 | 1 | 1 | -1.6897 | 10 | 0 | 0
235.4 | 50.07 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6897 | -1.6897 | 0 | 12 | 1 | 1 | -1.6897 | 10 | 0 | 0
235.45 | 50.07 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.13 | -0.335 | -0.335 | -3.35 | -1.8074 | -1.8074 | 0 | 12 | 1 | 1 | -1.8074 | 10 | 0 | 0
235.5 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.13 | -0.335 | -0.335 | -3.35 | -1.7779 | -1.7779 | 0 | 12 | 1 | 1 | -1.7779 | 10 | 0 | 0
235.55 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.13 | -0.335 | -0.335 | -3.35 | -1.7779 | -1.7779 | 0 | 12 | 1 | 1 | -1.7779 | 10 | 0 | 0
235.6 | 50.01 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
235.65 | 50.01 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
235.7 | 50.07 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
235.75 | 50.07 | 50.01 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.235 | -2.35 | -1.175 | -1.175 | 0 | 12 | 1 | 1 | -1.175 | 10 | 0 | 0
235.8 | 50.05 | 50.01 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.135 | -1.35 | -0.675 | -0.675 | 0 | 12 | 1 | 1 | -0.675 | 10 | 0 | 0
235.85 | 50.05 | 50.01 | 0 | 0 | 0 | 50.07 | -0.032353 | -0.035 | -0.35 | -0.175 | -0.175 | 0 | 12 | 1 | 1 | -0.175 | 10 | 0 | 0
235.9 | 50.1 | 50.01 | 0 | 0 | 0 | 50.1 | -0.05 | -0.05 | -0.5 | -0.25 | -0.25 | 0 | 12 | 1 | 1 | -0.25 | 10 | 0 | 0
235.95 | 50.1 | 50.01 | 0 | 0 | 0 | 50.1 | -0.05 | -0.05 | -0.5 | -0.25 | -0.25 | 0 | 12 | 1 | 1 | -0.25 | 10 | 0 | 0
236 | 50.11 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
236.05 | 50.11 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
236.1 | 50.06 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
236.15 | 50.06 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
236.2 | 50.04 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
236.25 | 50.04 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
236.3 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
236.35 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
236.4 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
236.45 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
236.5 | 50.11 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
236.55 | 50.11 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
236.6 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
236.65 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
236.7 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
236.75 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
236.8 | 50.02 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.11 | -0.145 | -0.145 | -1.45 | -0.73971 | -0.73971 | 0 | 12 | 1 | 1 | -0.73971 | 10 | 0 | 0
236.85 | 50.02 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.11 | -0.145 | -0.145 | -1.45 | -0.73971 | -0.73971 | 0 | 12 | 1 | 1 | -0.73971 | 10 | 0 | 0
236.9 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
236.95 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
237 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
237.05 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
237.1 | 50.01 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
237.15 | 50.01 | 50 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.045 | -0.45 | -0.225 | -0.225 | 0 | 12 | 1 | 1 | -0.225 | 10 | 0 | 0
237.2 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
237.25 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
237.3 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
237.35 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
237.4 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.14706 | 0.14706 | 0 | 12 | 1 | 1 | 0.14706 | 10 | 0 | 0
237.45 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
237.5 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
237.55 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
237.6 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
237.65 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
237.7 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
237.75 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
237.8 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
237.85 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
237.9 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
237.95 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
238 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
238.05 | 50 | 50 | 0 | 0 | 0 | 50.01 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
238.1 | 49.5 | 49.5 | 1 | 1 | 10 | 50.01 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
238.15 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
238.2 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
238.25 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
238.3 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
238.35 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
238.4 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
238.45 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
238.5 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
238.55 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
238.6 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
238.65 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.1 | 1 | 5.5 | 5.5 | 0 | 12 | 1 | 1 | 5.5 | 10 | 0 | 0
238.7 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.2 | 2 | 6 | 6 | 0 | 12 | 1 | 1 | 6 | 10 | 0 | 0
238.75 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.3 | 3 | 6.5 | 6.5 | 0 | 12 | 1 | 1 | 6.5 | 10 | 0 | 0
238.8 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.4 | 4 | 7 | 7 | 0 | 12 | 1 | 1 | 7 | 10 | 0 | 0
238.85 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.5 | 5 | 7.5 | 7.5 | 0 | 12 | 1 | 1 | 7.5 | 10 | 0 | 0
238.9 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.6 | 6 | 8 | 8 | 0 | 12 | 1 | 1 | 8 | 10 | 0 | 0
238.95 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.7 | 7 | 8.5 | 8.5 | 0 | 12 | 1 | 1 | 8.5 | 10 | 0 | 0
239 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.8 | 8 | 9 | 9 | 0 | 12 | 1 | 1 | 9 | 10 | 0 | 0
239.05 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.9 | 9 | 9.5 | 9.5 | 0 | 12 | 1 | 1 | 9.5 | 10 | 0 | 0
239.1 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
239.15 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
239.2 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
239.25 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
239.3 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
239.35 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
239.4 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
239.45 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
239.5 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
239.55 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
239.6 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
239.65 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
239.7 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
239.75 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
239.8 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
239.85 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
239.9 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
239.95 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
240 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
240.05 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
240.1 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
240.15 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
240.2 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
240.25 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
240.3 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
240.35 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
240.4 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
240.45 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
240.5 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
240.55 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
240.6 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
240.65 | 50.5 | 50.5 | -1 | 0.9 | 9 | 50.5 | -1 | -1 | -10 | -0.5 | -0.5 | 0 | 12 | 1 | 1 | -0.5 | 10 | 0 | 0
240.7 | 50.5 | 50.5 | -1 | 0.8 | 8 | 50.5 | -1 | -1 | -10 | -1 | -1 | 0 | 12 | 1 | 1 | -1 | 10 | 0 | 0
240.75 | 50.5 | 50.5 | -1 | 0.7 | 7 | 50.5 | -1 | -1 | -10 | -1.5 | -1.5 | 0 | 12 | 1 | 1 | -1.5 | 10 | 0 | 0
240.8 | 50.5 | 50.5 | -1 | 0.6 | 6 | 50.5 | -1 | -1 | -10 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
240.85 | 50.5 | 50.5 | -1 | 0.5 | 5 | 50.5 | -1 | -1 | -10 | -2.5 | -2.5 | 0 | 12 | 1 | 1 | -2.5 | 10 | 0 | 0
240.9 | 50.5 | 50.5 | -1 | 0.4 | 4 | 50.5 | -1 | -1 | -10 | -3 | -3 | 0 | 12 | 1 | 1 | -3 | 10 | 0 | 0
240.95 | 50.5 | 50.5 | -1 | 0.3 | 3 | 50.5 | -1 | -1 | -10 | -3.5 | -3.5 | 0 | 12 | 1 | 1 | -3.5 | 10 | 0 | 0
241 | 50.5 | 50.5 | -1 | 0.2 | 2 | 50.5 | -1 | -1 | -10 | -4 | -4 | 0 | 12 | 1 | 1 | -4 | 10 | 0 | 0
241.05 | 50.5 | 50.5 | -1 | 0.1 | 1 | 50.5 | -1 | -1 | -10 | -4.5 | -4.5 | 0 | 12 | 1 | 1 | -4.5 | 10 | 0 | 0
241.1 | 50.5 | 50.5 | -1 | 0 | 0 | 50.5 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
241.15 | 50.5 | 50.5 | -1 | -0.1 | -1 | 50.5 | -1 | -1 | -10 | -5.5 | -5.5 | 0 | 12 | 1 | 1 | -5.5 | 10 | 0 | 0
241.2 | 50.5 | 50.5 | -1 | -0.2 | -2 | 50.5 | -1 | -1 | -10 | -6 | -6 | 0 | 12 | 1 | 1 | -6 | 10 | 0 | 0
241.25 | 50.5 | 50.5 | -1 | -0.3 | -3 | 50.5 | -1 | -1 | -10 | -6.5 | -6.5 | 0 | 12 | 1 | 1 | -6.5 | 10 | 0 | 0
241.3 | 50.5 | 50.5 | -1 | -0.4 | -4 | 50.5 | -1 | -1 | -10 | -7 | -7 | 0 | 12 | 1 | 1 | -7 | 10 | 0 | 0
241.35 | 50.5 | 50.5 | -1 | -0.5 | -5 | 50.5 | -1 | -1 | -10 | -7.5 | -7.5 | 0 | 12 | 1 | 1 | -7.5 | 10 | 0 | 0
241.4 | 50.5 | 50.5 | -1 | -0.6 | -6 | 50.5 | -1 | -1 | -10 | -8 | -8 | 0 | 12 | 1 | 1 | -8 | 10 | 0 | 0
241.45 | 50.5 | 50.5 | -1 | -0.7 | -7 | 50.5 | -1 | -1 | -10 | -8.5 | -8.5 | 0 | 12 | 1 | 1 | -8.5 | 10 | 0 | 0
241.5 | 50.5 | 50.5 | -1 | -0.8 | -8 | 50.5 | -1 | -1 | -10 | -9 | -9 | 0 | 12 | 1 | 1 | -9 | 10 | 0 | 0
241.55 | 50.5 | 50.5 | -1 | -0.9 | -9 | 50.5 | -1 | -1 | -10 | -9.5 | -9.5 | 0 | 12 | 1 | 1 | -9.5 | 10 | 0 | 0
241.6 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
241.65 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
241.7 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
241.75 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
241.8 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
241.85 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
241.9 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
241.95 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
242 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
242.05 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
242.1 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
242.15 | 50.47 | 50.47 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
242.2 | 50.45 | 50.45 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
242.25 | 50.42 | 50.42 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
242.3 | 50.4 | 50.4 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
242.35 | 50.37 | 50.37 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
242.4 | 50.35 | 50.35 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
242.45 | 50.32 | 50.32 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
242.5 | 50.29 | 50.29 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
242.55 | 50.27 | 50.27 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
242.6 | 50.24 | 50.24 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
242.65 | 50.22 | 50.22 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
242.7 | 50.19 | 50.19 | -0.905 | -0.905 | -9.05 | 50.47 | -1 | -1 | -10 | -9.525 | -9.525 | 0 | 12 | 1 | 1 | -9.525 | 10 | 0 | 0
242.75 | 50.17 | 50.17 | -0.715 | -0.715 | -7.15 | 50.45 | -1 | -1 | -10 | -8.575 | -8.575 | 0 | 12 | 1 | 1 | -8.575 | 10 | 0 | 0
242.8 | 50.14 | 50.14 | -0.43 | -0.43 | -4.3 | 50.42 | -1 | -1 | -10 | -7.15 | -7.15 | 0 | 12 | 1 | 1 | -7.15 | 10 | 0 | 0
242.85 | 50.12 | 50.12 | -0.24 | -0.24 | -2.4 | 50.4 | -1 | -1 | -10 | -6.2 | -6.2 | 0 | 12 | 1 | 1 | -6.2 | 10 | 0 | 0
242.9 | 50.09 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 50.37 | -1 | -1 | -10 | -5.2206 | -5.2206 | 0 | 12 | 1 | 1 | -5.2206 | 10 | 0 | 0
242.95 | 50.06 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.35 | -1 | -1 | -10 | -5.1324 | -5.1324 | 0 | 12 | 1 | 1 | -5.1324 | 10 | 0 | 0
243 | 50.04 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.32 | -1 | -1 | -10 | -5.0735 | -5.0735 | 0 | 12 | 1 | 1 | -5.0735 | 10 | 0 | 0
243.05 | 50.01 | 50.01 | 0 | 0 | 0 | 50.29 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
243.1 | 49.99 | 49.99 | 0 | 0 | 0 | 50.27 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
243.15 | 49.96 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.24 | -1 | -1 | -10 | -4.9265 | -4.9265 | 0 | 12 | 1 | 1 | -4.9265 | 10 | 0 | 0
243.2 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.22 | -1 | -1 | -10 | -4.8676 | -4.8676 | 0 | 12 | 1 | 1 | -4.8676 | 10 | 0 | 0
243.25 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.19 | -0.905 | -0.905 | -9.05 | -4.3044 | -4.3044 | 0 | 12 | 1 | 1 | -4.3044 | 10 | 0 | 0
243.3 | 49.88 | 49.88 | 0.24 | 0.24 | 2.4 | 50.17 | -0.715 | -0.805 | -8.05 | -2.825 | -2.825 | 0 | 12 | 1 | 1 | -2.825 | 10 | 0 | 0
243.35 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.14 | -0.43 | -0.705 | -7.05 | -1.375 | -1.375 | 0 | 12 | 1 | 1 | -1.375 | 10 | 0 | 0
243.4 | 49.83 | 49.83 | 0.715 | 0.715 | 7.15 | 50.12 | -0.24 | -0.605 | -6.05 | 0.55 | 0.55 | 0 | 12 | 1 | 1 | 0.55 | 10 | 0 | 0
243.45 | 49.81 | 49.81 | 0.905 | 0.905 | 9.05 | 50.09 | -0.044118 | -0.505 | -5.05 | 2 | 2 | 0 | 12 | 1 | 1 | 2 | 10 | 0 | 0
243.5 | 49.78 | 49.78 | 1 | 1 | 10 | 50.06 | -0.026471 | -0.405 | -4.05 | 2.975 | 2.975 | 0 | 12 | 1 | 1 | 2.975 | 10 | 0 | 0
243.55 | 49.76 | 49.76 | 1 | 1 | 10 | 50.04 | -0.014706 | -0.305 | -3.05 | 3.475 | 3.475 | 0 | 12 | 1 | 1 | 3.475 | 10 | 0 | 0
243.6 | 49.73 | 49.73 | 1 | 1 | 10 | 50.01 | 0 | -0.205 | -2.05 | 3.975 | 3.975 | 0 | 12 | 1 | 1 | 3.975 | 10 | 0 | 0
243.65 | 49.71 | 49.71 | 1 | 1 | 10 | 49.99 | 0 | -0.105 | -1.05 | 4.475 | 4.475 | 0 | 12 | 1 | 1 | 4.475 | 10 | 0 | 0
243.7 | 49.68 | 49.68 | 1 | 1 | 10 | 49.96 | 0.014706 | -0.005 | -0.05 | 4.975 | 4.975 | 0 | 12 | 1 | 1 | 4.975 | 10 | 0 | 0
243.75 | 49.65 | 49.65 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
243.8 | 49.63 | 49.63 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
243.85 | 49.6 | 49.6 | 1 | 1 | 10 | 49.88 | 0.24 | 0.14412 | 1.4412 | 5.7206 | 5.7206 | 0 | 12 | 1 | 1 | 5.7206 | 10 | 0 | 0
243.9 | 49.58 | 49.58 | 1 | 1 | 10 | 49.86 | 0.43 | 0.24412 | 2.4412 | 6.2206 | 6.2206 | 0 | 12 | 1 | 1 | 6.2206 | 10 | 0 | 0
243.95 | 49.55 | 49.55 | 1 | 1 | 10 | 49.83 | 0.715 | 0.34412 | 3.4412 | 6.7206 | 6.7206 | 0 | 12 | 1 | 1 | 6.7206 | 10 | 0 | 0
244 | 49.53 | 49.53 | 1 | 1 | 10 | 49.81 | 0.905 | 0.44412 | 4.4412 | 7.2206 | 7.2206 | 0 | 12 | 1 | 1 | 7.2206 | 10 | 0 | 0
244.05 | 49.5 | 49.5 | 1 | 1 | 10 | 49.78 | 1 | 0.54412 | 5.4412 | 7.7206 | 7.7206 | 0 | 12 | 1 | 1 | 7.7206 | 10 | 0 | 0
244.1 | 49.5 | 49.5 | 1 | 1 | 10 | 49.76 | 1 | 0.64412 | 6.4412 | 8.2206 | 8.2206 | 0 | 12 | 1 | 1 | 8.2206 | 10 | 0 | 0
244.15 | 49.53 | 49.5 | 1 | 1 | 10 | 49.73 | 1 | 0.74412 | 7.4412 | 8.7206 | 8.7206 | 0 | 12 | 1 | 1 | 8.7206 | 10 | 0 | 0
244.2 | 49.55 | 49.5 | 1 | 1 | 10 | 49.71 | 1 | 0.84412 | 8.4412 | 9.2206 | 9.2206 | 0 | 12 | 1 | 1 | 9.2206 | 10 | 0 | 0
244.25 | 49.58 | 49.5 | 1 | 1 | 10 | 49.68 | 1 | 0.94412 | 9.4412 | 9.7206 | 9.7206 | 0 | 12 | 1 | 1 | 9.7206 | 10 | 0 | 0
244.3 | 49.6 | 49.5 | 1 | 1 | 10 | 49.65 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
244.35 | 49.63 | 49.5 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
244.4 | 49.65 | 49.5 | 1 | 1 | 10 | 49.65 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
244.45 | 49.68 | 49.5 | 1 | 1 | 10 | 49.68 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
244.5 | 49.71 | 49.5 | 1 | 1 | 10 | 49.71 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
244.55 | 49.73 | 49.5 | 1 | 1 | 10 | 49.73 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
244.6 | 49.76 | 49.5 | 1 | 1 | 10 | 49.76 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
244.65 | 49.78 | 49.5 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
244.7 | 49.81 | 49.53 | 1 | 1 | 10 | 49.81 | 0.905 | 0.905 | 9.05 | 9.525 | 9.525 | 0 | 12 | 1 | 1 | 9.525 | 10 | 0 | 0
244.75 | 49.83 | 49.55 | 1 | 1 | 10 | 49.83 | 0.715 | 0.715 | 7.15 | 8.575 | 8.575 | 0 | 12 | 1 | 1 | 8.575 | 10 | 0 | 0
244.8 | 49.86 | 49.58 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
244.85 | 49.88 | 49.6 | 1 | 1 | 10 | 49.88 | 0.24 | 0.24 | 2.4 | 6.2 | 6.2 | 0 | 12 | 1 | 1 | 6.2 | 10 | 0 | 0
244.9 | 49.91 | 49.63 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
244.95 | 49.94 | 49.65 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
245 | 49.96 | 49.68 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
245.05 | 49.99 | 49.71 | 1 | 1 | 10 | 49.99 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
245.1 | 50.01 | 49.73 | 1 | 1 | 10 | 50.01 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
245.15 | 50.04 | 49.76 | 1 | 1 | 10 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 4.9265 | 4.9265 | 0 | 12 | 1 | 1 | 4.9265 | 10 | 0 | 0
245.2 | 50.06 | 49.78 | 1 | 1 | 10 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 4.8676 | 4.8676 | 0 | 12 | 1 | 1 | 4.8676 | 10 | 0 | 0
245.25 | 50.09 | 49.81 | 0.905 | 0.905 | 9.05 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 4.3044 | 4.3044 | 0 | 12 | 1 | 1 | 4.3044 | 10 | 0 | 0
245.3 | 50.12 | 49.83 | 0.715 | 0.805 | 8.05 | 50.12 | -0.24 | -0.24 | -2.4 | 2.825 | 2.825 | 0 | 12 | 1 | 1 | 2.825 | 10 | 0 | 0
245.35 | 50.14 | 49.86 | 0.43 | 0.705 | 7.05 | 50.14 | -0.43 | -0.43 | -4.3 | 1.375 | 1.375 | 0 | 12 | 1 | 1 | 1.375 | 10 | 0 | 0
245.4 | 50.17 | 49.88 | 0.24 | 0.605 | 6.05 | 50.17 | -0.715 | -0.715 | -7.15 | -0.55 | -0.55 | 0 | 12 | 1 | 1 | -0.55 | 10 | 0 | 0
245.45 | 50.19 | 49.91 | 0.044118 | 0.505 | 5.05 | 50.19 | -0.905 | -0.905 | -9.05 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
245.5 | 50.22 | 49.94 | 0.026471 | 0.405 | 4.05 | 50.22 | -1 | -1 | -10 | -2.975 | -2.975 | 0 | 12 | 1 | 1 | -2.975 | 10 | 0 | 0
245.55 | 50.24 | 49.96 | 0.014706 | 0.305 | 3.05 | 50.24 | -1 | -1 | -10 | -3.475 | -3.475 | 0 | 12 | 1 | 1 | -3.475 | 10 | 0 | 0
245.6 | 50.27 | 49.99 | 0 | 0.205 | 2.05 | 50.27 | -1 | -1 | -10 | -3.975 | -3.975 | 0 | 12 | 1 | 1 | -3.975 | 10 | 0 | 0
245.65 | 50.29 | 50.01 | 0 | 0.105 | 1.05 | 50.29 | -1 | -1 | -10 | -4.475 | -4.475 | 0 | 12 | 1 | 1 | -4.475 | 10 | 0 | 0
245.7 | 50.32 | 50.04 | -0.014706 | 0.005 | 0.05 | 50.32 | -1 | -1 | -10 | -4.975 | -4.975 | 0 | 12 | 1 | 1 | -4.975 | 10 | 0 | 0
245.75 | 50.35 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.35 | -1 | -1 | -10 | -5.1324 | -5.1324 | 0 | 12 | 1 | 1 | -5.1324 | 10 | 0 | 0
245.8 | 50.37 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 50.37 | -1 | -1 | -10 | -5.2206 | -5.2206 | 0 | 12 | 1 | 1 | -5.2206 | 10 | 0 | 0
245.85 | 50.4 | 50.12 | -0.24 | -0.14412 | -1.4412 | 50.4 | -1 | -1 | -10 | -5.7206 | -5.7206 | 0 | 12 | 1 | 1 | -5.7206 | 10 | 0 | 0
245.9 | 50.42 | 50.14 | -0.43 | -0.24412 | -2.4412 | 50.42 | -1 | -1 | -10 | -6.2206 | -6.2206 | 0 | 12 | 1 | 1 | -6.2206 | 10 | 0 | 0
245.95 | 50.45 | 50.17 | -0.715 | -0.34412 | -3.4412 | 50.45 | -1 | -1 | -10 | -6.7206 | -6.7206 | 0 | 12 | 1 | 1 | -6.7206 | 10 | 0 | 0
246 | 50.47 | 50.19 | -0.905 | -0.44412 | -4.4412 | 50.47 | -1 | -1 | -10 | -7.2206 | -7.2206 | 0 | 12 | 1 | 1 | -7.2206 | 10 | 0 | 0
246.05 | 50.5 | 50.22 | -1 | -0.54412 | -5.4412 | 50.5 | -1 | -1 | -10 | -7.7206 | -7.7206 | 0 | 12 | 1 | 1 | -7.7206 | 10 | 0 | 0
246.1 | 50.5 | 50.24 | -1 | -0.64412 | -6.4412 | 50.5 | -1 | -1 | -10 | -8.2206 | -8.2206 | 0 | 12 | 1 | 1 | -8.2206 | 10 | 0 | 0
246.15 | 50.47 | 50.27 | -1 | -0.74412 | -7.4412 | 50.5 | -1 | -1 | -10 | -8.7206 | -8.7206 | 0 | 12 | 1 | 1 | -8.7206 | 10 | 0 | 0
246.2 | 50.45 | 50.29 | -1 | -0.84412 | -8.4412 | 50.5 | -1 | -1 | -10 | -9.2206 | -9.2206 | 0 | 12 | 1 | 1 | -9.2206 | 10 | 0 | 0
246.25 | 50.42 | 50.32 | -1 | -0.94412 | -9.4412 | 50.5 | -1 | -1 | -10 | -9.7206 | -9.7206 | 0 | 12 | 1 | 1 | -9.7206 | 10 | 0 | 0
246.3 | 50.39 | 50.35 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
246.35 | 50.37 | 50.37 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
246.4 | 50.34 | 50.34 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
246.45 | 50.32 | 50.32 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
246.5 | 50.29 | 50.29 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
246.55 | 50.26 | 50.26 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
246.6 | 50.24 | 50.24 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
246.65 | 50.21 | 50.21 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
246.7 | 50.18 | 50.18 | -0.81 | -0.81 | -8.1 | 50.47 | -1 | -1 | -10 | -9.05 | -9.05 | 0 | 12 | 1 | 1 | -9.05 | 10 | 0 | 0
246.75 | 50.16 | 50.16 | -0.62 | -0.62 | -6.2 | 50.45 | -1 | -1 | -10 | -8.1 | -8.1 | 0 | 12 | 1 | 1 | -8.1 | 10 | 0 | 0
246.8 | 50.13 | 50.13 | -0.335 | -0.335 | -3.35 | 50.42 | -1 | -1 | -10 | -6.675 | -6.675 | 0 | 12 | 1 | 1 | -6.675 | 10 | 0 | 0
246.85 | 50.11 | 50.11 | -0.145 | -0.145 | -1.45 | 50.39 | -1 | -1 | -10 | -5.725 | -5.725 | 0 | 12 | 1 | 1 | -5.725 | 10 | 0 | 0
246.9 | 50.08 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 50.37 | -1 | -1 | -10 | -5.1912 | -5.1912 | 0 | 12 | 1 | 1 | -5.1912 | 10 | 0 | 0
246.95 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.34 | -1 | -1 | -10 | -5.1029 | -5.1029 | 0 | 12 | 1 | 1 | -5.1029 | 10 | 0 | 0
247 | 50.03 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 50.32 | -1 | -1 | -10 | -5.0441 | -5.0441 | 0 | 12 | 1 | 1 | -5.0441 | 10 | 0 | 0
247.05 | 50 | 50 | 0 | 0 | 0 | 50.29 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
247.1 | 50 | 50 | 0 | 0 | 0 | 50.26 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
247.15 | 50 | 50 | 0 | 0 | 0 | 50.24 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
247.2 | 50 | 50 | 0 | 0 | 0 | 50.21 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
247.25 | 50 | 50 | 0 | 0 | 0 | 50.18 | -0.81 | -0.9 | -9 | -4.5 | -4.5 | 0 | 12 | 1 | 1 | -4.5 | 10 | 0 | 0
247.3 | 50 | 50 | 0 | 0 | 0 | 50.16 | -0.62 | -0.8 | -8 | -4 | -4 | 0 | 12 | 1 | 1 | -4 | 10 | 0 | 0
247.35 | 50 | 50 | 0 | 0 | 0 | 50.13 | -0.335 | -0.7 | -7 | -3.5 | -3.5 | 0 | 12 | 1 | 1 | -3.5 | 10 | 0 | 0
247.4 | 50.01 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.6 | -6 | -3 | -3 | 0 | 12 | 1 | 1 | -3 | 10 | 0 | 0
247.45 | 50.01 | 50 | 0 | 0 | 0 | 50.08 | -0.038235 | -0.5 | -5 | -2.5 | -2.5 | 0 | 12 | 1 | 1 | -2.5 | 10 | 0 | 0
247.5 | 49.99 | 49.99 | 0 | 0 | 0 | 50.05 | -0.020588 | -0.4 | -4 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
247.55 | 49.99 | 49.99 | 0 | 0 | 0 | 50.03 | -0.0088235 | -0.3 | -3 | -1.5 | -1.5 | 0 | 12 | 1 | 1 | -1.5 | 10 | 0 | 0
247.6 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | -0.2 | -2 | -0.83824 | -0.83824 | 0 | 12 | 1 | 1 | -0.83824 | 10 | 0 | 0
247.65 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | -0.1 | -1 | -0.33824 | -0.33824 | 0 | 12 | 1 | 1 | -0.33824 | 10 | 0 | 0
247.7 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
247.75 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
247.8 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
247.85 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
247.9 | 49.89 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
247.95 | 49.89 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
248 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50.01 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
248.05 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
248.1 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
248.15 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 2.7868 | 2.7868 | 0 | 12 | 1 | 1 | 2.7868 | 10 | 0 | 0
248.2 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 2.7868 | 2.7868 | 0 | 12 | 1 | 1 | 2.7868 | 10 | 0 | 0
248.25 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 2.8456 | 2.8456 | 0 | 12 | 1 | 1 | 2.8456 | 10 | 0 | 0
248.3 | 49.94 | 49.85 | 0.525 | 0.525 | 5.25 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 2.7574 | 2.7574 | 0 | 12 | 1 | 1 | 2.7574 | 10 | 0 | 0
248.35 | 49.94 | 49.85 | 0.525 | 0.525 | 5.25 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 2.7574 | 2.7574 | 0 | 12 | 1 | 1 | 2.7574 | 10 | 0 | 0
248.4 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
248.45 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
248.5 | 49.93 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
248.55 | 49.93 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
248.6 | 49.96 | 49.85 | 0.525 | 0.525 | 5.25 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 2.6985 | 2.6985 | 0 | 12 | 1 | 1 | 2.6985 | 10 | 0 | 0
248.65 | 49.96 | 49.85 | 0.525 | 0.525 | 5.25 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 2.6985 | 2.6985 | 0 | 12 | 1 | 1 | 2.6985 | 10 | 0 | 0
248.7 | 49.99 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
248.75 | 49.99 | 49.91 | 0.044118 | 0.425 | 4.25 | 49.99 | 0 | 0 | 0 | 2.125 | 2.125 | 0 | 12 | 1 | 1 | 2.125 | 10 | 0 | 0
248.8 | 49.99 | 49.91 | 0.044118 | 0.325 | 3.25 | 49.99 | 0 | 0 | 0 | 1.625 | 1.625 | 0 | 12 | 1 | 1 | 1.625 | 10 | 0 | 0
248.85 | 49.99 | 49.93 | 0.032353 | 0.225 | 2.25 | 49.99 | 0 | 0 | 0 | 1.125 | 1.125 | 0 | 12 | 1 | 1 | 1.125 | 10 | 0 | 0
248.9 | 49.96 | 49.93 | 0.032353 | 0.125 | 1.25 | 49.99 | 0 | 0 | 0 | 0.625 | 0.625 | 0 | 12 | 1 | 1 | 0.625 | 10 | 0 | 0
248.95 | 49.96 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 49.99 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
249 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
249.05 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
249.1 | 50.05 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.058824 | 0.058824 | 0 | 12 | 1 | 1 | 0.058824 | 10 | 0 | 0
249.15 | 50.05 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
249.2 | 49.97 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
249.25 | 49.97 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
249.3 | 49.92 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
249.35 | 49.92 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
249.4 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
249.45 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
249.5 | 49.94 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
249.55 | 49.94 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
249.6 | 50.01 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
249.65 | 50.01 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
249.7 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
249.75 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
249.8 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
249.85 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
249.9 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
249.95 | 49.95 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
250 | 49.97 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
250.05 | 49.97 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
250.1 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
250.15 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
250.2 | 49.87 | 49.87 | 0.335 | 0.335 | 3.35 | 50.01 | 0 | 0 | 0 | 1.675 | 1.675 | 0 | 12 | 1 | 1 | 1.675 | 10 | 0 | 0
250.25 | 49.87 | 49.87 | 0.335 | 0.335 | 3.35 | 49.99 | 0 | 0 | 0 | 1.675 | 1.675 | 0 | 12 | 1 | 1 | 1.675 | 10 | 0 | 0
250.3 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
250.35 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 2.6691 | 2.6691 | 0 | 12 | 1 | 1 | 2.6691 | 10 | 0 | 0
250.4 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
250.45 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
250.5 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
250.55 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
250.6 | 49.84 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
250.65 | 49.84 | 49.79 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
250.7 | 49.89 | 49.79 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
250.75 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.12647 | 1.2647 | 5.6324 | 5.6324 | 0 | 12 | 1 | 1 | 5.6324 | 10 | 0 | 0
250.8 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.145 | 1.45 | 5.725 | 5.725 | 0 | 12 | 1 | 1 | 5.725 | 10 | 0 | 0
250.85 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.145 | 1.45 | 5.725 | 5.725 | 0 | 12 | 1 | 1 | 5.725 | 10 | 0 | 0
250.9 | 49.96 | 49.79 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
250.95 | 49.96 | 49.79 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
251 | 50.02 | 49.79 | 1 | 1 | 10 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 4.9853 | 4.9853 | 0 | 12 | 1 | 1 | 4.9853 | 10 | 0 | 0
251.05 | 50.02 | 49.79 | 1 | 1 | 10 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 4.9853 | 4.9853 | 0 | 12 | 1 | 1 | 4.9853 | 10 | 0 | 0
251.1 | 50.03 | 49.79 | 1 | 1 | 10 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.9559 | 4.9559 | 0 | 12 | 1 | 1 | 4.9559 | 10 | 0 | 0
251.15 | 50.03 | 49.84 | 0.62 | 0.9 | 9 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.4559 | 4.4559 | 0 | 12 | 1 | 1 | 4.4559 | 10 | 0 | 0
251.2 | 50.02 | 49.84 | 0.62 | 0.8 | 8 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 3.9559 | 3.9559 | 0 | 12 | 1 | 1 | 3.9559 | 10 | 0 | 0
251.25 | 50.02 | 49.89 | 0.145 | 0.7 | 7 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 3.4559 | 3.4559 | 0 | 12 | 1 | 1 | 3.4559 | 10 | 0 | 0
251.3 | 50.08 | 49.89 | 0.145 | 0.6 | 6 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 2.8088 | 2.8088 | 0 | 12 | 1 | 1 | 2.8088 | 10 | 0 | 0
251.35 | 50.08 | 49.89 | 0.145 | 0.5 | 5 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 2.3088 | 2.3088 | 0 | 12 | 1 | 1 | 2.3088 | 10 | 0 | 0
251.4 | 50.01 | 49.89 | 0.145 | 0.4 | 4 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 1.8088 | 1.8088 | 0 | 12 | 1 | 1 | 1.8088 | 10 | 0 | 0
251.45 | 50.01 | 49.96 | 0.014706 | 0.3 | 3 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 1.3088 | 1.3088 | 0 | 12 | 1 | 1 | 1.3088 | 10 | 0 | 0
251.5 | 49.94 | 49.94 | 0.026471 | 0.2 | 2 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.80882 | 0.80882 | 0 | 12 | 1 | 1 | 0.80882 | 10 | 0 | 0
251.55 | 49.94 | 49.94 | 0.026471 | 0.1 | 1 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.30882 | 0.30882 | 0 | 12 | 1 | 1 | 0.30882 | 10 | 0 | 0
251.6 | 50 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
251.65 | 50 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
251.7 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
251.75 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
251.8 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
251.85 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
251.9 | 49.92 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
251.95 | 49.92 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
252 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50.01 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
252.05 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
252.1 | 49.92 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
252.15 | 49.92 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
252.2 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
252.25 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
252.3 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
252.35 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
252.4 | 49.87 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
252.45 | 49.87 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
252.5 | 49.8 | 49.8 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
252.55 | 49.8 | 49.8 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
252.6 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
252.65 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
252.7 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
252.75 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
252.8 | 49.72 | 49.72 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
252.85 | 49.72 | 49.72 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
252.9 | 49.67 | 49.67 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
252.95 | 49.67 | 49.67 | 1 | 1 | 10 | 49.87 | 0.335 | 0.14412 | 1.4412 | 5.7206 | 5.7206 | 0 | 12 | 1 | 1 | 5.7206 | 10 | 0 | 0
253 | 49.65 | 49.65 | 1 | 1 | 10 | 49.87 | 0.335 | 0.24412 | 2.4412 | 6.2206 | 6.2206 | 0 | 12 | 1 | 1 | 6.2206 | 10 | 0 | 0
253.05 | 49.65 | 49.65 | 1 | 1 | 10 | 49.8 | 1 | 0.34412 | 3.4412 | 6.7206 | 6.7206 | 0 | 12 | 1 | 1 | 6.7206 | 10 | 0 | 0
253.1 | 49.59 | 49.59 | 1 | 1 | 10 | 49.8 | 1 | 0.44412 | 4.4412 | 7.2206 | 7.2206 | 0 | 12 | 1 | 1 | 7.2206 | 10 | 0 | 0
253.15 | 49.59 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.54412 | 5.4412 | 7.7206 | 7.7206 | 0 | 12 | 1 | 1 | 7.7206 | 10 | 0 | 0
253.2 | 49.66 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.64412 | 6.4412 | 8.2206 | 8.2206 | 0 | 12 | 1 | 1 | 8.2206 | 10 | 0 | 0
253.25 | 49.66 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.74412 | 7.4412 | 8.7206 | 8.7206 | 0 | 12 | 1 | 1 | 8.7206 | 10 | 0 | 0
253.3 | 49.63 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.84412 | 8.4412 | 9.2206 | 9.2206 | 0 | 12 | 1 | 1 | 9.2206 | 10 | 0 | 0
253.35 | 49.63 | 49.59 | 1 | 1 | 10 | 49.72 | 1 | 0.94412 | 9.4412 | 9.7206 | 9.7206 | 0 | 12 | 1 | 1 | 9.7206 | 10 | 0 | 0
253.4 | 49.61 | 49.59 | 1 | 1 | 10 | 49.72 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
253.45 | 49.61 | 49.59 | 1 | 1 | 10 | 49.67 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
253.5 | 49.54 | 49.54 | 1 | 1 | 10 | 49.67 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
253.55 | 49.54 | 49.54 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
253.6 | 49.46 | 49.46 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
253.65 | 49.46 | 49.46 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
253.7 | 49.45 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
253.75 | 49.45 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
253.8 | 49.51 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
253.85 | 49.51 | 49.45 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
253.9 | 49.5 | 49.45 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
253.95 | 49.5 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
254 | 49.54 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
254.05 | 49.54 | 49.45 | 1 | 1 | 10 | 49.54 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
254.1 | 49.59 | 49.45 | 1 | 1 | 10 | 49.59 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
254.15 | 49.59 | 49.45 | 1 | 1 | 10 | 49.59 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
254.2 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
254.25 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
254.3 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
254.35 | 49.61 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
254.4 | 49.53 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
254.45 | 49.53 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
254.5 | 49.54 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
254.55 | 49.54 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
254.6 | 49.61 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
254.65 | 49.61 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
254.7 | 49.66 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
254.75 | 49.66 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
254.8 | 49.64 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
254.85 | 49.64 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
254.9 | 49.69 | 49.53 | 1 | 1 | 10 | 49.69 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
254.95 | 49.69 | 49.53 | 1 | 1 | 10 | 49.69 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
255 | 49.74 | 49.53 | 1 | 1 | 10 | 49.74 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
255.05 | 49.74 | 49.54 | 1 | 1 | 10 | 49.74 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
255.1 | 49.78 | 49.54 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
255.15 | 49.78 | 49.61 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
255.2 | 49.82 | 49.61 | 1 | 1 | 10 | 49.82 | 0.81 | 0.81 | 8.1 | 9.05 | 9.05 | 0 | 12 | 1 | 1 | 9.05 | 10 | 0 | 0
255.25 | 49.82 | 49.64 | 1 | 1 | 10 | 49.82 | 0.81 | 0.81 | 8.1 | 9.05 | 9.05 | 0 | 12 | 1 | 1 | 9.05 | 10 | 0 | 0
255.3 | 49.86 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
255.35 | 49.86 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
255.4 | 49.84 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
255.45 | 49.84 | 49.69 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
255.5 | 49.91 | 49.69 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
255.55 | 49.91 | 49.74 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
255.6 | 49.97 | 49.74 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
255.65 | 49.97 | 49.78 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
255.7 | 50.03 | 49.78 | 1 | 1 | 10 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.9559 | 4.9559 | 0 | 12 | 1 | 1 | 4.9559 | 10 | 0 | 0
255.75 | 50.03 | 49.82 | 0.81 | 0.9 | 9 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.4559 | 4.4559 | 0 | 12 | 1 | 1 | 4.4559 | 10 | 0 | 0
255.8 | 50.05 | 49.82 | 0.81 | 0.81 | 8.1 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 3.9471 | 3.9471 | 0 | 12 | 1 | 1 | 3.9471 | 10 | 0 | 0
255.85 | 50.05 | 49.84 | 0.62 | 0.71 | 7.1 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 3.4471 | 3.4471 | 0 | 12 | 1 | 1 | 3.4471 | 10 | 0 | 0
255.9 | 50.01 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
255.95 | 50.01 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
256 | 49.95 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
256.05 | 49.95 | 49.91 | 0.044118 | 0.52 | 5.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.4971 | 2.4971 | 0 | 12 | 1 | 1 | 2.4971 | 10 | 0 | 0
256.1 | 49.99 | 49.91 | 0.044118 | 0.42 | 4.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 1.9971 | 1.9971 | 0 | 12 | 1 | 1 | 1.9971 | 10 | 0 | 0
256.15 | 49.99 | 49.95 | 0.020588 | 0.32 | 3.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 1.4971 | 1.4971 | 0 | 12 | 1 | 1 | 1.4971 | 10 | 0 | 0
256.2 | 49.92 | 49.92 | 0.038235 | 0.22 | 2.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.99706 | 0.99706 | 0 | 12 | 1 | 1 | 0.99706 | 10 | 0 | 0
256.25 | 49.92 | 49.92 | 0.038235 | 0.12 | 1.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.49706 | 0.49706 | 0 | 12 | 1 | 1 | 0.49706 | 10 | 0 | 0
256.3 | 49.97 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
256.35 | 49.97 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
256.4 | 50.02 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
256.45 | 50.02 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.17647 | 0.17647 | 0 | 12 | 1 | 1 | 0.17647 | 10 | 0 | 0
256.5 | 50.07 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
256.55 | 50.07 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
256.6 | 50.06 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
256.65 | 50.06 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
256.7 | 50.13 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
256.75 | 50.13 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
256.8 | 50.09 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
256.85 | 50.09 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6309 | -1.6309 | 0 | 12 | 1 | 1 | -1.6309 | 10 | 0 | 0
256.9 | 50.07 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6309 | -1.6309 | 0 | 12 | 1 | 1 | -1.6309 | 10 | 0 | 0
256.95 | 50.07 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6897 | -1.6897 | 0 | 12 | 1 | 1 | -1.6897 | 10 | 0 | 0
257 | 50.07 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6897 | -1.6897 | 0 | 12 | 1 | 1 | -1.6897 | 10 | 0 | 0
257.05 | 50.07 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.13 | -0.335 | -0.335 | -3.35 | -1.8074 | -1.8074 | 0 | 12 | 1 | 1 | -1.8074 | 10 | 0 | 0
257.1 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.13 | -0.335 | -0.335 | -3.35 | -1.7779 | -1.7779 | 0 | 12 | 1 | 1 | -1.7779 | 10 | 0 | 0
257.15 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.13 | -0.335 | -0.335 | -3.35 | -1.7779 | -1.7779 | 0 | 12 | 1 | 1 | -1.7779 | 10 | 0 | 0
257.2 | 50.01 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
257.25 | 50.01 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
257.3 | 50.07 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
257.35 | 50.07 | 50.01 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.235 | -2.35 | -1.175 | -1.175 | 0 | 12 | 1 | 1 | -1.175 | 10 | 0 | 0
257.4 | 50.05 | 50.01 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.135 | -1.35 | -0.675 | -0.675 | 0 | 12 | 1 | 1 | -0.675 | 10 | 0 | 0
257.45 | 50.05 | 50.01 | 0 | 0 | 0 | 50.07 | -0.032353 | -0.035 | -0.35 | -0.175 | -0.175 | 0 | 12 | 1 | 1 | -0.175 | 10 | 0 | 0
257.5 | 50.1 | 50.01 | 0 | 0 | 0 | 50.1 | -0.05 | -0.05 | -0.5 | -0.25 | -0.25 | 0 | 12 | 1 | 1 | -0.25 | 10 | 0 | 0
257.55 | 50.1 | 50.01 | 0 | 0 | 0 | 50.1 | -0.05 | -0.05 | -0.5 | -0.25 | -0.25 | 0 | 12 | 1 | 1 | -0.25 | 10 | 0 | 0
257.6 | 50.11 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
257.65 | 50.11 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
257.7 | 50.06 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
257.75 | 50.06 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
257.8 | 50.04 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
257.85 | 50.04 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
257.9 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
257.95 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
258 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
258.05 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
258.1 | 50.11 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
258.15 | 50.11 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
258.2 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
258.25 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
258.3 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
258.35 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
258.4 | 50.02 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.11 | -0.145 | -0.145 | -1.45 | -0.73971 | -0.73971 | 0 | 12 | 1 | 1 | -0.73971 | 10 | 0 | 0
258.45 | 50.02 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.11 | -0.145 | -0.145 | -1.45 | -0.73971 | -0.73971 | 0 | 12 | 1 | 1 | -0.73971 | 10 | 0 | 0
258.5 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
258.55 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
258.6 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
258.65 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
258.7 | 50.01 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
258.75 | 50.01 | 50 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.045 | -0.45 | -0.225 | -0.225 | 0 | 12 | 1 | 1 | -0.225 | 10 | 0 | 0
258.8 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
258.85 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
258.9 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
258.95 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
259 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.14706 | 0.14706 | 0 | 12 | 1 | 1 | 0.14706 | 10 | 0 | 0
259.05 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
259.1 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
259.15 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
259.2 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
259.25 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
259.3 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
259.35 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
259.4 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
259.45 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
259.5 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
259.55 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
259.6 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
259.65 | 50 | 50 | 0 | 0 | 0 | 50.01 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
259.7 | 49.5 | 49.5 | 1 | 1 | 10 | 50.01 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
259.75 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
259.8 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
259.85 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
259.9 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
259.95 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
260 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
260.05 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
260.1 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
260.15 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
260.2 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
260.25 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.1 | 1 | 5.5 | 5.5 | 0 | 12 | 1 | 1 | 5.5 | 10 | 0 | 0
260.3 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.2 | 2 | 6 | 6 | 0 | 12 | 1 | 1 | 6 | 10 | 0 | 0
260.35 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.3 | 3 | 6.5 | 6.5 | 0 | 12 | 1 | 1 | 6.5 | 10 | 0 | 0
260.4 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.4 | 4 | 7 | 7 | 0 | 12 | 1 | 1 | 7 | 10 | 0 | 0
260.45 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.5 | 5 | 7.5 | 7.5 | 0 | 12 | 1 | 1 | 7.5 | 10 | 0 | 0
260.5 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.6 | 6 | 8 | 8 | 0 | 12 | 1 | 1 | 8 | 10 | 0 | 0
260.55 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.7 | 7 | 8.5 | 8.5 | 0 | 12 | 1 | 1 | 8.5 | 10 | 0 | 0
260.6 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.8 | 8 | 9 | 9 | 0 | 12 | 1 | 1 | 9 | 10 | 0 | 0
260.65 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.9 | 9 | 9.5 | 9.5 | 0 | 12 | 1 | 1 | 9.5 | 10 | 0 | 0
260.7 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
260.75 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
260.8 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
260.85 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
260.9 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
260.95 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
261 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
261.05 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
261.1 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
261.15 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
261.2 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
261.25 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
261.3 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
261.35 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
261.4 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
261.45 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
261.5 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
261.55 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
261.6 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
261.65 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
261.7 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
261.75 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
261.8 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
261.85 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
261.9 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
261.95 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
262 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
262.05 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
262.1 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
262.15 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
262.2 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
262.25 | 50.5 | 50.5 | -1 | 0.9 | 9 | 50.5 | -1 | -1 | -10 | -0.5 | -0.5 | 0 | 12 | 1 | 1 | -0.5 | 10 | 0 | 0
262.3 | 50.5 | 50.5 | -1 | 0.8 | 8 | 50.5 | -1 | -1 | -10 | -1 | -1 | 0 | 12 | 1 | 1 | -1 | 10 | 0 | 0
262.35 | 50.5 | 50.5 | -1 | 0.7 | 7 | 50.5 | -1 | -1 | -10 | -1.5 | -1.5 | 0 | 12 | 1 | 1 | -1.5 | 10 | 0 | 0
262.4 | 50.5 | 50.5 | -1 | 0.6 | 6 | 50.5 | -1 | -1 | -10 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
262.45 | 50.5 | 50.5 | -1 | 0.5 | 5 | 50.5 | -1 | -1 | -10 | -2.5 | -2.5 | 0 | 12 | 1 | 1 | -2.5 | 10 | 0 | 0
262.5 | 50.5 | 50.5 | -1 | 0.4 | 4 | 50.5 | -1 | -1 | -10 | -3 | -3 | 0 | 12 | 1 | 1 | -3 | 10 | 0 | 0
262.55 | 50.5 | 50.5 | -1 | 0.3 | 3 | 50.5 | -1 | -1 | -10 | -3.5 | -3.5 | 0 | 12 | 1 | 1 | -3.5 | 10 | 0 | 0
262.6 | 50.5 | 50.5 | -1 | 0.2 | 2 | 50.5 | -1 | -1 | -10 | -4 | -4 | 0 | 12 | 1 | 1 | -4 | 10 | 0 | 0
262.65 | 50.5 | 50.5 | -1 | 0.1 | 1 | 50.5 | -1 | -1 | -10 | -4.5 | -4.5 | 0 | 12 | 1 | 1 | -4.5 | 10 | 0 | 0
262.7 | 50.5 | 50.5 | -1 | 0 | 0 | 50.5 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
262.75 | 50.5 | 50.5 | -1 | -0.1 | -1 | 50.5 | -1 | -1 | -10 | -5.5 | -5.5 | 0 | 12 | 1 | 1 | -5.5 | 10 | 0 | 0
262.8 | 50.5 | 50.5 | -1 | -0.2 | -2 | 50.5 | -1 | -1 | -10 | -6 | -6 | 0 | 12 | 1 | 1 | -6 | 10 | 0 | 0
262.85 | 50.5 | 50.5 | -1 | -0.3 | -3 | 50.5 | -1 | -1 | -10 | -6.5 | -6.5 | 0 | 12 | 1 | 1 | -6.5 | 10 | 0 | 0
262.9 | 50.5 | 50.5 | -1 | -0.4 | -4 | 50.5 | -1 | -1 | -10 | -7 | -7 | 0 | 12 | 1 | 1 | -7 | 10 | 0 | 0
262.95 | 50.5 | 50.5 | -1 | -0.5 | -5 | 50.5 | -1 | -1 | -10 | -7.5 | -7.5 | 0 | 12 | 1 | 1 | -7.5 | 10 | 0 | 0
263 | 50.5 | 50.5 | -1 | -0.6 | -6 | 50.5 | -1 | -1 | -10 | -8 | -8 | 0 | 12 | 1 | 1 | -8 | 10 | 0 | 0
263.05 | 50.5 | 50.5 | -1 | -0.7 | -7 | 50.5 | -1 | -1 | -10 | -8.5 | -8.5 | 0 | 12 | 1 | 1 | -8.5 | 10 | 0 | 0
263.1 | 50.5 | 50.5 | -1 | -0.8 | -8 | 50.5 | -1 | -1 | -10 | -9 | -9 | 0 | 12 | 1 | 1 | -9 | 10 | 0 | 0
263.15 | 50.5 | 50.5 | -1 | -0.9 | -9 | 50.5 | -1 | -1 | -10 | -9.5 | -9.5 | 0 | 12 | 1 | 1 | -9.5 | 10 | 0 | 0
263.2 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
263.25 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
263.3 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
263.35 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
263.4 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
263.45 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
263.5 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
263.55 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
263.6 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
263.65 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
263.7 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
263.75 | 50.47 | 50.47 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
263.8 | 50.45 | 50.45 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
263.85 | 50.42 | 50.42 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
263.9 | 50.4 | 50.4 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
263.95 | 50.37 | 50.37 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
264 | 50.35 | 50.35 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
264.05 | 50.32 | 50.32 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
264.1 | 50.29 | 50.29 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
264.15 | 50.27 | 50.27 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
264.2 | 50.24 | 50.24 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
264.25 | 50.22 | 50.22 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
264.3 | 50.19 | 50.19 | -0.905 | -0.905 | -9.05 | 50.47 | -1 | -1 | -10 | -9.525 | -9.525 | 0 | 12 | 1 | 1 | -9.525 | 10 | 0 | 0
264.35 | 50.17 | 50.17 | -0.715 | -0.715 | -7.15 | 50.45 | -1 | -1 | -10 | -8.575 | -8.575 | 0 | 12 | 1 | 1 | -8.575 | 10 | 0 | 0
264.4 | 50.14 | 50.14 | -0.43 | -0.43 | -4.3 | 50.42 | -1 | -1 | -10 | -7.15 | -7.15 | 0 | 12 | 1 | 1 | -7.15 | 10 | 0 | 0
264.45 | 50.12 | 50.12 | -0.24 | -0.24 | -2.4 | 50.4 | -1 | -1 | -10 | -6.2 | -6.2 | 0 | 12 | 1 | 1 | -6.2 | 10 | 0 | 0
264.5 | 50.09 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 50.37 | -1 | -1 | -10 | -5.2206 | -5.2206 | 0 | 12 | 1 | 1 | -5.2206 | 10 | 0 | 0
264.55 | 50.06 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.35 | -1 | -1 | -10 | -5.1324 | -5.1324 | 0 | 12 | 1 | 1 | -5.1324 | 10 | 0 | 0
264.6 | 50.04 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.32 | -1 | -1 | -10 | -5.0735 | -5.0735 | 0 | 12 | 1 | 1 | -5.0735 | 10 | 0 | 0
264.65 | 50.01 | 50.01 | 0 | 0 | 0 | 50.29 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
264.7 | 49.99 | 49.99 | 0 | 0 | 0 | 50.27 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
264.75 | 49.96 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.24 | -1 | -1 | -10 | -4.9265 | -4.9265 | 0 | 12 | 1 | 1 | -4.9265 | 10 | 0 | 0
264.8 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.22 | -1 | -1 | -10 | -4.8676 | -4.8676 | 0 | 12 | 1 | 1 | -4.8676 | 10 | 0 | 0
264.85 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.19 | -0.905 | -0.905 | -9.05 | -4.3044 | -4.3044 | 0 | 12 | 1 | 1 | -4.3044 | 10 | 0 | 0
264.9 | 49.88 | 49.88 | 0.24 | 0.24 | 2.4 | 50.17 | -0.715 | -0.805 | -8.05 | -2.825 | -2.825 | 0 | 12 | 1 | 1 | -2.825 | 10 | 0 | 0
264.95 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.14 | -0.43 | -0.705 | -7.05 | -1.375 | -1.375 | 0 | 12 | 1 | 1 | -1.375 | 10 | 0 | 0
265 | 49.83 | 49.83 | 0.715 | 0.715 | 7.15 | 50.12 | -0.24 | -0.605 | -6.05 | 0.55 | 0.55 | 0 | 12 | 1 | 1 | 0.55 | 10 | 0 | 0
265.05 | 49.81 | 49.81 | 0.905 | 0.905 | 9.05 | 50.09 | -0.044118 | -0.505 | -5.05 | 2 | 2 | 0 | 12 | 1 | 1 | 2 | 10 | 0 | 0
265.1 | 49.78 | 49.78 | 1 | 1 | 10 | 50.06 | -0.026471 | -0.405 | -4.05 | 2.975 | 2.975 | 0 | 12 | 1 | 1 | 2.975 | 10 | 0 | 0
265.15 | 49.76 | 49.76 | 1 | 1 | 10 | 50.04 | -0.014706 | -0.305 | -3.05 | 3.475 | 3.475 | 0 | 12 | 1 | 1 | 3.475 | 10 | 0 | 0
265.2 | 49.73 | 49.73 | 1 | 1 | 10 | 50.01 | 0 | -0.205 | -2.05 | 3.975 | 3.975 | 0 | 12 | 1 | 1 | 3.975 | 10 | 0 | 0
265.25 | 49.71 | 49.71 | 1 | 1 | 10 | 49.99 | 0 | -0.105 | -1.05 | 4.475 | 4.475 | 0 | 12 | 1 | 1 | 4.475 | 10 | 0 | 0
265.3 | 49.68 | 49.68 | 1 | 1 | 10 | 49.96 | 0.014706 | -0.005 | -0.05 | 4.975 | 4.975 | 0 | 12 | 1 | 1 | 4.975 | 10 | 0 | 0
265.35 | 49.65 | 49.65 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
265.4 | 49.63 | 49.63 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
265.45 | 49.6 | 49.6 | 1 | 1 | 10 | 49.88 | 0.24 | 0.14412 | 1.4412 | 5.7206 | 5.7206 | 0 | 12 | 1 | 1 | 5.7206 | 10 | 0 | 0
265.5 | 49.58 | 49.58 | 1 | 1 | 10 | 49.86 | 0.43 | 0.24412 | 2.4412 | 6.2206 | 6.2206 | 0 | 12 | 1 | 1 | 6.2206 | 10 | 0 | 0
265.55 | 49.55 | 49.55 | 1 | 1 | 10 | 49.83 | 0.715 | 0.34412 | 3.4412 | 6.7206 | 6.7206 | 0 | 12 | 1 | 1 | 6.7206 | 10 | 0 | 0
265.6 | 49.53 | 49.53 | 1 | 1 | 10 | 49.81 | 0.905 | 0.44412 | 4.4412 | 7.2206 | 7.2206 | 0 | 12 | 1 | 1 | 7.2206 | 10 | 0 | 0
265.65 | 49.5 | 49.5 | 1 | 1 | 10 | 49.78 | 1 | 0.54412 | 5.4412 | 7.7206 | 7.7206 | 0 | 12 | 1 | 1 | 7.7206 | 10 | 0 | 0
265.7 | 49.5 | 49.5 | 1 | 1 | 10 | 49.76 | 1 | 0.64412 | 6.4412 | 8.2206 | 8.2206 | 0 | 12 | 1 | 1 | 8.2206 | 10 | 0 | 0
265.75 | 49.53 | 49.5 | 1 | 1 | 10 | 49.73 | 1 | 0.74412 | 7.4412 | 8.7206 | 8.7206 | 0 | 12 | 1 | 1 | 8.7206 | 10 | 0 | 0
265.8 | 49.55 | 49.5 | 1 | 1 | 10 | 49.71 | 1 | 0.84412 | 8.4412 | 9.2206 | 9.2206 | 0 | 12 | 1 | 1 | 9.2206 | 10 | 0 | 0
265.85 | 49.58 | 49.5 | 1 | 1 | 10 | 49.68 | 1 | 0.94412 | 9.4412 | 9.7206 | 9.7206 | 0 | 12 | 1 | 1 | 9.7206 | 10 | 0 | 0
265.9 | 49.6 | 49.5 | 1 | 1 | 10 | 49.65 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
265.95 | 49.63 | 49.5 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
266 | 49.65 | 49.5 | 1 | 1 | 10 | 49.65 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
266.05 | 49.68 | 49.5 | 1 | 1 | 10 | 49.68 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
266.1 | 49.71 | 49.5 | 1 | 1 | 10 | 49.71 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
266.15 | 49.73 | 49.5 | 1 | 1 | 10 | 49.73 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
266.2 | 49.76 | 49.5 | 1 | 1 | 10 | 49.76 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
266.25 | 49.78 | 49.5 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
266.3 | 49.81 | 49.53 | 1 | 1 | 10 | 49.81 | 0.905 | 0.905 | 9.05 | 9.525 | 9.525 | 0 | 12 | 1 | 1 | 9.525 | 10 | 0 | 0
266.35 | 49.83 | 49.55 | 1 | 1 | 10 | 49.83 | 0.715 | 0.715 | 7.15 | 8.575 | 8.575 | 0 | 12 | 1 | 1 | 8.575 | 10 | 0 | 0
266.4 | 49.86 | 49.58 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
266.45 | 49.88 | 49.6 | 1 | 1 | 10 | 49.88 | 0.24 | 0.24 | 2.4 | 6.2 | 6.2 | 0 | 12 | 1 | 1 | 6.2 | 10 | 0 | 0
266.5 | 49.91 | 49.63 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
266.55 | 49.94 | 49.65 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
266.6 | 49.96 | 49.68 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
266.65 | 49.99 | 49.71 | 1 | 1 | 10 | 49.99 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
266.7 | 50.01 | 49.73 | 1 | 1 | 10 | 50.01 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
266.75 | 50.04 | 49.76 | 1 | 1 | 10 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 4.9265 | 4.9265 | 0 | 12 | 1 | 1 | 4.9265 | 10 | 0 | 0
266.8 | 50.06 | 49.78 | 1 | 1 | 10 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 4.8676 | 4.8676 | 0 | 12 | 1 | 1 | 4.8676 | 10 | 0 | 0
266.85 | 50.09 | 49.81 | 0.905 | 0.905 | 9.05 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 4.3044 | 4.3044 | 0 | 12 | 1 | 1 | 4.3044 | 10 | 0 | 0
266.9 | 50.12 | 49.83 | 0.715 | 0.805 | 8.05 | 50.12 | -0.24 | -0.24 | -2.4 | 2.825 | 2.825 | 0 | 12 | 1 | 1 | 2.825 | 10 | 0 | 0
266.95 | 50.14 | 49.86 | 0.43 | 0.705 | 7.05 | 50.14 | -0.43 | -0.43 | -4.3 | 1.375 | 1.375 | 0 | 12 | 1 | 1 | 1.375 | 10 | 0 | 0
267 | 50.17 | 49.88 | 0.24 | 0.605 | 6.05 | 50.17 | -0.715 | -0.715 | -7.15 | -0.55 | -0.55 | 0 | 12 | 1 | 1 | -0.55 | 10 | 0 | 0
267.05 | 50.19 | 49.91 | 0.044118 | 0.505 | 5.05 | 50.19 | -0.905 | -0.905 | -9.05 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
267.1 | 50.22 | 49.94 | 0.026471 | 0.405 | 4.05 | 50.22 | -1 | -1 | -10 | -2.975 | -2.975 | 0 | 12 | 1 | 1 | -2.975 | 10 | 0 | 0
267.15 | 50.24 | 49.96 | 0.014706 | 0.305 | 3.05 | 50.24 | -1 | -1 | -10 | -3.475 | -3.475 | 0 | 12 | 1 | 1 | -3.475 | 10 | 0 | 0
267.2 | 50.27 | 49.99 | 0 | 0.205 | 2.05 | 50.27 | -1 | -1 | -10 | -3.975 | -3.975 | 0 | 12 | 1 | 1 | -3.975 | 10 | 0 | 0
267.25 | 50.29 | 50.01 | 0 | 0.105 | 1.05 | 50.29 | -1 | -1 | -10 | -4.475 | -4.475 | 0 | 12 | 1 | 1 | -4.475 | 10 | 0 | 0
267.3 | 50.32 | 50.04 | -0.014706 | 0.005 | 0.05 | 50.32 | -1 | -1 | -10 | -4.975 | -4.975 | 0 | 12 | 1 | 1 | -4.975 | 10 | 0 | 0
267.35 | 50.35 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.35 | -1 | -1 | -10 | -5.1324 | -5.1324 | 0 | 12 | 1 | 1 | -5.1324 | 10 | 0 | 0
267.4 | 50.37 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 50.37 | -1 | -1 | -10 | -5.2206 | -5.2206 | 0 | 12 | 1 | 1 | -5.2206 | 10 | 0 | 0
267.45 | 50.4 | 50.12 | -0.24 | -0.14412 | -1.4412 | 50.4 | -1 | -1 | -10 | -5.7206 | -5.7206 | 0 | 12 | 1 | 1 | -5.7206 | 10 | 0 | 0
267.5 | 50.42 | 50.14 | -0.43 | -0.24412 | -2.4412 | 50.42 | -1 | -1 | -10 | -6.2206 | -6.2206 | 0 | 12 | 1 | 1 | -6.2206 | 10 | 0 | 0
267.55 | 50.45 | 50.17 | -0.715 | -0.34412 | -3.4412 | 50.45 | -1 | -1 | -10 | -6.7206 | -6.7206 | 0 | 12 | 1 | 1 | -6.7206 | 10 | 0 | 0
267.6 | 50.47 | 50.19 | -0.905 | -0.44412 | -4.4412 | 50.47 | -1 | -1 | -10 | -7.2206 | -7.2206 | 0 | 12 | 1 | 1 | -7.2206 | 10 | 0 | 0
267.65 | 50.5 | 50.22 | -1 | -0.54412 | -5.4412 | 50.5 | -1 | -1 | -10 | -7.7206 | -7.7206 | 0 | 12 | 1 | 1 | -7.7206 | 10 | 0 | 0
267.7 | 50.5 | 50.24 | -1 | -0.64412 | -6.4412 | 50.5 | -1 | -1 | -10 | -8.2206 | -8.2206 | 0 | 12 | 1 | 1 | -8.2206 | 10 | 0 | 0
267.75 | 50.47 | 50.27 | -1 | -0.74412 | -7.4412 | 50.5 | -1 | -1 | -10 | -8.7206 | -8.7206 | 0 | 12 | 1 | 1 | -8.7206 | 10 | 0 | 0
267.8 | 50.45 | 50.29 | -1 | -0.84412 | -8.4412 | 50.5 | -1 | -1 | -10 | -9.2206 | -9.2206 | 0 | 12 | 1 | 1 | -9.2206 | 10 | 0 | 0
267.85 | 50.42 | 50.32 | -1 | -0.94412 | -9.4412 | 50.5 | -1 | -1 | -10 | -9.7206 | -9.7206 | 0 | 12 | 1 | 1 | -9.7206 | 10 | 0 | 0
267.9 | 50.39 | 50.35 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
267.95 | 50.37 | 50.37 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
268 | 50.34 | 50.34 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
268.05 | 50.32 | 50.32 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
268.1 | 50.29 | 50.29 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
268.15 | 50.26 | 50.26 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
268.2 | 50.24 | 50.24 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
268.25 | 50.21 | 50.21 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
268.3 | 50.18 | 50.18 | -0.81 | -0.81 | -8.1 | 50.47 | -1 | -1 | -10 | -9.05 | -9.05 | 0 | 12 | 1 | 1 | -9.05 | 10 | 0 | 0
268.35 | 50.16 | 50.16 | -0.62 | -0.62 | -6.2 | 50.45 | -1 | -1 | -10 | -8.1 | -8.1 | 0 | 12 | 1 | 1 | -8.1 | 10 | 0 | 0
268.4 | 50.13 | 50.13 | -0.335 | -0.335 | -3.35 | 50.42 | -1 | -1 | -10 | -6.675 | -6.675 | 0 | 12 | 1 | 1 | -6.675 | 10 | 0 | 0
268.45 | 50.11 | 50.11 | -0.145 | -0.145 | -1.45 | 50.39 | -1 | -1 | -10 | -5.725 | -5.725 | 0 | 12 | 1 | 1 | -5.725 | 10 | 0 | 0
268.5 | 50.08 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 50.37 | -1 | -1 | -10 | -5.1912 | -5.1912 | 0 | 12 | 1 | 1 | -5.1912 | 10 | 0 | 0
268.55 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.34 | -1 | -1 | -10 | -5.1029 | -5.1029 | 0 | 12 | 1 | 1 | -5.1029 | 10 | 0 | 0
268.6 | 50.03 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 50.32 | -1 | -1 | -10 | -5.0441 | -5.0441 | 0 | 12 | 1 | 1 | -5.0441 | 10 | 0 | 0
268.65 | 50 | 50 | 0 | 0 | 0 | 50.29 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
268.7 | 50 | 50 | 0 | 0 | 0 | 50.26 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
268.75 | 50 | 50 | 0 | 0 | 0 | 50.24 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
268.8 | 50 | 50 | 0 | 0 | 0 | 50.21 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
268.85 | 50 | 50 | 0 | 0 | 0 | 50.18 | -0.81 | -0.9 | -9 | -4.5 | -4.5 | 0 | 12 | 1 | 1 | -4.5 | 10 | 0 | 0
268.9 | 50 | 50 | 0 | 0 | 0 | 50.16 | -0.62 | -0.8 | -8 | -4 | -4 | 0 | 12 | 1 | 1 | -4 | 10 | 0 | 0
268.95 | 50 | 50 | 0 | 0 | 0 | 50.13 | -0.335 | -0.7 | -7 | -3.5 | -3.5 | 0 | 12 | 1 | 1 | -3.5 | 10 | 0 | 0
269 | 50.01 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.6 | -6 | -3 | -3 | 0 | 12 | 1 | 1 | -3 | 10 | 0 | 0
269.05 | 50.01 | 50 | 0 | 0 | 0 | 50.08 | -0.038235 | -0.5 | -5 | -2.5 | -2.5 | 0 | 12 | 1 | 1 | -2.5 | 10 | 0 | 0
269.1 | 49.99 | 49.99 | 0 | 0 | 0 | 50.05 | -0.020588 | -0.4 | -4 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
269.15 | 49.99 | 49.99 | 0 | 0 | 0 | 50.03 | -0.0088235 | -0.3 | -3 | -1.5 | -1.5 | 0 | 12 | 1 | 1 | -1.5 | 10 | 0 | 0
269.2 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | -0.2 | -2 | -0.83824 | -0.83824 | 0 | 12 | 1 | 1 | -0.83824 | 10 | 0 | 0
269.25 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | -0.1 | -1 | -0.33824 | -0.33824 | 0 | 12 | 1 | 1 | -0.33824 | 10 | 0 | 0
269.3 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
269.35 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
269.4 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
269.45 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
269.5 | 49.89 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
269.55 | 49.89 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
269.6 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50.01 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
269.65 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
269.7 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
269.75 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 2.7868 | 2.7868 | 0 | 12 | 1 | 1 | 2.7868 | 10 | 0 | 0
269.8 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 2.7868 | 2.7868 | 0 | 12 | 1 | 1 | 2.7868 | 10 | 0 | 0
269.85 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 2.8456 | 2.8456 | 0 | 12 | 1 | 1 | 2.8456 | 10 | 0 | 0
269.9 | 49.94 | 49.85 | 0.525 | 0.525 | 5.25 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 2.7574 | 2.7574 | 0 | 12 | 1 | 1 | 2.7574 | 10 | 0 | 0
269.95 | 49.94 | 49.85 | 0.525 | 0.525 | 5.25 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 2.7574 | 2.7574 | 0 | 12 | 1 | 1 | 2.7574 | 10 | 0 | 0
270 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
270.05 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
270.1 | 49.93 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
270.15 | 49.93 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
270.2 | 49.96 | 49.85 | 0.525 | 0.525 | 5.25 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 2.6985 | 2.6985 | 0 | 12 | 1 | 1 | 2.6985 | 10 | 0 | 0
270.25 | 49.96 | 49.85 | 0.525 | 0.525 | 5.25 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 2.6985 | 2.6985 | 0 | 12 | 1 | 1 | 2.6985 | 10 | 0 | 0
270.3 | 49.99 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
270.35 | 49.99 | 49.91 | 0.044118 | 0.425 | 4.25 | 49.99 | 0 | 0 | 0 | 2.125 | 2.125 | 0 | 12 | 1 | 1 | 2.125 | 10 | 0 | 0
270.4 | 49.99 | 49.91 | 0.044118 | 0.325 | 3.25 | 49.99 | 0 | 0 | 0 | 1.625 | 1.625 | 0 | 12 | 1 | 1 | 1.625 | 10 | 0 | 0
270.45 | 49.99 | 49.93 | 0.032353 | 0.225 | 2.25 | 49.99 | 0 | 0 | 0 | 1.125 | 1.125 | 0 | 12 | 1 | 1 | 1.125 | 10 | 0 | 0
270.5 | 49.96 | 49.93 | 0.032353 | 0.125 | 1.25 | 49.99 | 0 | 0 | 0 | 0.625 | 0.625 | 0 | 12 | 1 | 1 | 0.625 | 10 | 0 | 0
270.55 | 49.96 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 49.99 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
270.6 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
270.65 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
270.7 | 50.05 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.058824 | 0.058824 | 0 | 12 | 1 | 1 | 0.058824 | 10 | 0 | 0
270.75 | 50.05 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
270.8 | 49.97 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
270.85 | 49.97 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
270.9 | 49.92 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
270.95 | 49.92 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
271 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
271.05 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
271.1 | 49.94 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
271.15 | 49.94 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
271.2 | 50.01 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
271.25 | 50.01 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
271.3 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
271.35 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
271.4 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
271.45 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
271.5 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
271.55 | 49.95 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
271.6 | 49.97 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
271.65 | 49.97 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
271.7 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
271.75 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
271.8 | 49.87 | 49.87 | 0.335 | 0.335 | 3.35 | 50.01 | 0 | 0 | 0 | 1.675 | 1.675 | 0 | 12 | 1 | 1 | 1.675 | 10 | 0 | 0
271.85 | 49.87 | 49.87 | 0.335 | 0.335 | 3.35 | 49.99 | 0 | 0 | 0 | 1.675 | 1.675 | 0 | 12 | 1 | 1 | 1.675 | 10 | 0 | 0
271.9 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
271.95 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 2.6691 | 2.6691 | 0 | 12 | 1 | 1 | 2.6691 | 10 | 0 | 0
272 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
272.05 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
272.1 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
272.15 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
272.2 | 49.84 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
272.25 | 49.84 | 49.79 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
272.3 | 49.89 | 49.79 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
272.35 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.12647 | 1.2647 | 5.6324 | 5.6324 | 0 | 12 | 1 | 1 | 5.6324 | 10 | 0 | 0
272.4 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.145 | 1.45 | 5.725 | 5.725 | 0 | 12 | 1 | 1 | 5.725 | 10 | 0 | 0
272.45 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.145 | 1.45 | 5.725 | 5.725 | 0 | 12 | 1 | 1 | 5.725 | 10 | 0 | 0
272.5 | 49.96 | 49.79 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
272.55 | 49.96 | 49.79 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
272.6 | 50.02 | 49.79 | 1 | 1 | 10 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 4.9853 | 4.9853 | 0 | 12 | 1 | 1 | 4.9853 | 10 | 0 | 0
272.65 | 50.02 | 49.79 | 1 | 1 | 10 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 4.9853 | 4.9853 | 0 | 12 | 1 | 1 | 4.9853 | 10 | 0 | 0
272.7 | 50.03 | 49.79 | 1 | 1 | 10 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.9559 | 4.9559 | 0 | 12 | 1 | 1 | 4.9559 | 10 | 0 | 0
272.75 | 50.03 | 49.84 | 0.62 | 0.9 | 9 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.4559 | 4.4559 | 0 | 12 | 1 | 1 | 4.4559 | 10 | 0 | 0
272.8 | 50.02 | 49.84 | 0.62 | 0.8 | 8 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 3.9559 | 3.9559 | 0 | 12 | 1 | 1 | 3.9559 | 10 | 0 | 0
272.85 | 50.02 | 49.89 | 0.145 | 0.7 | 7 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 3.4559 | 3.4559 | 0 | 12 | 1 | 1 | 3.4559 | 10 | 0 | 0
272.9 | 50.08 | 49.89 | 0.145 | 0.6 | 6 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 2.8088 | 2.8088 | 0 | 12 | 1 | 1 | 2.8088 | 10 | 0 | 0
272.95 | 50.08 | 49.89 | 0.145 | 0.5 | 5 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 2.3088 | 2.3088 | 0 | 12 | 1 | 1 | 2.3088 | 10 | 0 | 0
273 | 50.01 | 49.89 | 0.145 | 0.4 | 4 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 1.8088 | 1.8088 | 0 | 12 | 1 | 1 | 1.8088 | 10 | 0 | 0
273.05 | 50.01 | 49.96 | 0.014706 | 0.3 | 3 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 1.3088 | 1.3088 | 0 | 12 | 1 | 1 | 1.3088 | 10 | 0 | 0
273.1 | 49.94 | 49.94 | 0.026471 | 0.2 | 2 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.80882 | 0.80882 | 0 | 12 | 1 | 1 | 0.80882 | 10 | 0 | 0
273.15 | 49.94 | 49.94 | 0.026471 | 0.1 | 1 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.30882 | 0.30882 | 0 | 12 | 1 | 1 | 0.30882 | 10 | 0 | 0
273.2 | 50 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
273.25 | 50 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
273.3 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
273.35 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
273.4 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
273.45 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
273.5 | 49.92 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
273.55 | 49.92 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
273.6 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50.01 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
273.65 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
273.7 | 49.92 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
273.75 | 49.92 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
273.8 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
273.85 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
273.9 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
273.95 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
274 | 49.87 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
274.05 | 49.87 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
274.1 | 49.8 | 49.8 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
274.15 | 49.8 | 49.8 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
274.2 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
274.25 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
274.3 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
274.35 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
274.4 | 49.72 | 49.72 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
274.45 | 49.72 | 49.72 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
274.5 | 49.67 | 49.67 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
274.55 | 49.67 | 49.67 | 1 | 1 | 10 | 49.87 | 0.335 | 0.14412 | 1.4412 | 5.7206 | 5.7206 | 0 | 12 | 1 | 1 | 5.7206 | 10 | 0 | 0
274.6 | 49.65 | 49.65 | 1 | 1 | 10 | 49.87 | 0.335 | 0.24412 | 2.4412 | 6.2206 | 6.2206 | 0 | 12 | 1 | 1 | 6.2206 | 10 | 0 | 0
274.65 | 49.65 | 49.65 | 1 | 1 | 10 | 49.8 | 1 | 0.34412 | 3.4412 | 6.7206 | 6.7206 | 0 | 12 | 1 | 1 | 6.7206 | 10 | 0 | 0
274.7 | 49.59 | 49.59 | 1 | 1 | 10 | 49.8 | 1 | 0.44412 | 4.4412 | 7.2206 | 7.2206 | 0 | 12 | 1 | 1 | 7.2206 | 10 | 0 | 0
274.75 | 49.59 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.54412 | 5.4412 | 7.7206 | 7.7206 | 0 | 12 | 1 | 1 | 7.7206 | 10 | 0 | 0
274.8 | 49.66 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.64412 | 6.4412 | 8.2206 | 8.2206 | 0 | 12 | 1 | 1 | 8.2206 | 10 | 0 | 0
274.85 | 49.66 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.74412 | 7.4412 | 8.7206 | 8.7206 | 0 | 12 | 1 | 1 | 8.7206 | 10 | 0 | 0
274.9 | 49.63 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.84412 | 8.4412 | 9.2206 | 9.2206 | 0 | 12 | 1 | 1 | 9.2206 | 10 | 0 | 0
274.95 | 49.63 | 49.59 | 1 | 1 | 10 | 49.72 | 1 | 0.94412 | 9.4412 | 9.7206 | 9.7206 | 0 | 12 | 1 | 1 | 9.7206 | 10 | 0 | 0
275 | 49.61 | 49.59 | 1 | 1 | 10 | 49.72 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
275.05 | 49.61 | 49.59 | 1 | 1 | 10 | 49.67 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
275.1 | 49.54 | 49.54 | 1 | 1 | 10 | 49.67 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
275.15 | 49.54 | 49.54 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
275.2 | 49.46 | 49.46 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
275.25 | 49.46 | 49.46 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
275.3 | 49.45 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
275.35 | 49.45 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
275.4 | 49.51 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
275.45 | 49.51 | 49.45 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
275.5 | 49.5 | 49.45 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
275.55 | 49.5 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
275.6 | 49.54 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
275.65 | 49.54 | 49.45 | 1 | 1 | 10 | 49.54 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
275.7 | 49.59 | 49.45 | 1 | 1 | 10 | 49.59 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
275.75 | 49.59 | 49.45 | 1 | 1 | 10 | 49.59 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
275.8 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
275.85 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
275.9 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
275.95 | 49.61 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
276 | 49.53 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
276.05 | 49.53 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
276.1 | 49.54 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
276.15 | 49.54 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
276.2 | 49.61 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
276.25 | 49.61 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
276.3 | 49.66 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
276.35 | 49.66 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
276.4 | 49.64 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
276.45 | 49.64 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
276.5 | 49.69 | 49.53 | 1 | 1 | 10 | 49.69 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
276.55 | 49.69 | 49.53 | 1 | 1 | 10 | 49.69 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
276.6 | 49.74 | 49.53 | 1 | 1 | 10 | 49.74 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
276.65 | 49.74 | 49.54 | 1 | 1 | 10 | 49.74 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
276.7 | 49.78 | 49.54 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
276.75 | 49.78 | 49.61 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
276.8 | 49.82 | 49.61 | 1 | 1 | 10 | 49.82 | 0.81 | 0.81 | 8.1 | 9.05 | 9.05 | 0 | 12 | 1 | 1 | 9.05 | 10 | 0 | 0
276.85 | 49.82 | 49.64 | 1 | 1 | 10 | 49.82 | 0.81 | 0.81 | 8.1 | 9.05 | 9.05 | 0 | 12 | 1 | 1 | 9.05 | 10 | 0 | 0
276.9 | 49.86 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
276.95 | 49.86 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
277 | 49.84 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
277.05 | 49.84 | 49.69 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
277.1 | 49.91 | 49.69 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
277.15 | 49.91 | 49.74 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
277.2 | 49.97 | 49.74 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
277.25 | 49.97 | 49.78 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
277.3 | 50.03 | 49.78 | 1 | 1 | 10 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.9559 | 4.9559 | 0 | 12 | 1 | 1 | 4.9559 | 10 | 0 | 0
277.35 | 50.03 | 49.82 | 0.81 | 0.9 | 9 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.4559 | 4.4559 | 0 | 12 | 1 | 1 | 4.4559 | 10 | 0 | 0
277.4 | 50.05 | 49.82 | 0.81 | 0.81 | 8.1 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 3.9471 | 3.9471 | 0 | 12 | 1 | 1 | 3.9471 | 10 | 0 | 0
277.45 | 50.05 | 49.84 | 0.62 | 0.71 | 7.1 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 3.4471 | 3.4471 | 0 | 12 | 1 | 1 | 3.4471 | 10 | 0 | 0
277.5 | 50.01 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
277.55 | 50.01 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
277.6 | 49.95 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
277.65 | 49.95 | 49.91 | 0.044118 | 0.52 | 5.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.4971 | 2.4971 | 0 | 12 | 1 | 1 | 2.4971 | 10 | 0 | 0
277.7 | 49.99 | 49.91 | 0.044118 | 0.42 | 4.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 1.9971 | 1.9971 | 0 | 12 | 1 | 1 | 1.9971 | 10 | 0 | 0
277.75 | 49.99 | 49.95 | 0.020588 | 0.32 | 3.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 1.4971 | 1.4971 | 0 | 12 | 1 | 1 | 1.4971 | 10 | 0 | 0
277.8 | 49.92 | 49.92 | 0.038235 | 0.22 | 2.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.99706 | 0.99706 | 0 | 12 | 1 | 1 | 0.99706 | 10 | 0 | 0
277.85 | 49.92 | 49.92 | 0.038235 | 0.12 | 1.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.49706 | 0.49706 | 0 | 12 | 1 | 1 | 0.49706 | 10 | 0 | 0
277.9 | 49.97 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
277.95 | 49.97 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
278 | 50.02 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
278.05 | 50.02 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.17647 | 0.17647 | 0 | 12 | 1 | 1 | 0.17647 | 10 | 0 | 0
278.1 | 50.07 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
278.15 | 50.07 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
278.2 | 50.06 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
278.25 | 50.06 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
278.3 | 50.13 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
278.35 | 50.13 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
278.4 | 50.09 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
278.45 | 50.09 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6309 | -1.6309 | 0 | 12 | 1 | 1 | -1.6309 | 10 | 0 | 0
278.5 | 50.07 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6309 | -1.6309 | 0 | 12 | 1 | 1 | -1.6309 | 10 | 0 | 0
278.55 | 50.07 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6897 | -1.6897 | 0 | 12 | 1 | 1 | -1.6897 | 10 | 0 | 0
278.6 | 50.07 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6897 | -1.6897 | 0 | 12 | 1 | 1 | -1.6897 | 10 | 0 | 0
278.65 | 50.07 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.13 | -0.335 | -0.335 | -3.35 | -1.8074 | -1.8074 | 0 | 12 | 1 | 1 | -1.8074 | 10 | 0 | 0
278.7 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.13 | -0.335 | -0.335 | -3.35 | -1.7779 | -1.7779 | 0 | 12 | 1 | 1 | -1.7779 | 10 | 0 | 0
278.75 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.13 | -0.335 | -0.335 | -3.35 | -1.7779 | -1.7779 | 0 | 12 | 1 | 1 | -1.7779 | 10 | 0 | 0
278.8 | 50.01 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
278.85 | 50.01 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
278.9 | 50.07 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
278.95 | 50.07 | 50.01 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.235 | -2.35 | -1.175 | -1.175 | 0 | 12 | 1 | 1 | -1.175 | 10 | 0 | 0
279 | 50.05 | 50.01 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.135 | -1.35 | -0.675 | -0.675 | 0 | 12 | 1 | 1 | -0.675 | 10 | 0 | 0
279.05 | 50.05 | 50.01 | 0 | 0 | 0 | 50.07 | -0.032353 | -0.035 | -0.35 | -0.175 | -0.175 | 0 | 12 | 1 | 1 | -0.175 | 10 | 0 | 0
279.1 | 50.1 | 50.01 | 0 | 0 | 0 | 50.1 | -0.05 | -0.05 | -0.5 | -0.25 | -0.25 | 0 | 12 | 1 | 1 | -0.25 | 10 | 0 | 0
279.15 | 50.1 | 50.01 | 0 | 0 | 0 | 50.1 | -0.05 | -0.05 | -0.5 | -0.25 | -0.25 | 0 | 12 | 1 | 1 | -0.25 | 10 | 0 | 0
279.2 | 50.11 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
279.25 | 50.11 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
279.3 | 50.06 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
279.35 | 50.06 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
279.4 | 50.04 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
279.45 | 50.04 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
279.5 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
279.55 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
279.6 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
279.65 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
279.7 | 50.11 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
279.75 | 50.11 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
279.8 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
279.85 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
279.9 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
279.95 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
280 | 50.02 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.11 | -0.145 | -0.145 | -1.45 | -0.73971 | -0.73971 | 0 | 12 | 1 | 1 | -0.73971 | 10 | 0 | 0
280.05 | 50.02 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.11 | -0.145 | -0.145 | -1.45 | -0.73971 | -0.73971 | 0 | 12 | 1 | 1 | -0.73971 | 10 | 0 | 0
280.1 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
280.15 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
280.2 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
280.25 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
280.3 | 50.01 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
280.35 | 50.01 | 50 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.045 | -0.45 | -0.225 | -0.225 | 0 | 12 | 1 | 1 | -0.225 | 10 | 0 | 0
280.4 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
280.45 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
280.5 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
280.55 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
280.6 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.14706 | 0.14706 | 0 | 12 | 1 | 1 | 0.14706 | 10 | 0 | 0
280.65 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
280.7 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
280.75 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
280.8 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
280.85 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
280.9 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
280.95 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
281 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
281.05 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
281.1 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
281.15 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
281.2 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
281.25 | 50 | 50 | 0 | 0 | 0 | 50.01 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
281.3 | 49.5 | 49.5 | 1 | 1 | 10 | 50.01 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
281.35 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
281.4 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
281.45 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
281.5 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
281.55 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
281.6 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
281.65 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
281.7 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
281.75 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
281.8 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
281.85 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.1 | 1 | 5.5 | 5.5 | 0 | 12 | 1 | 1 | 5.5 | 10 | 0 | 0
281.9 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.2 | 2 | 6 | 6 | 0 | 12 | 1 | 1 | 6 | 10 | 0 | 0
281.95 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.3 | 3 | 6.5 | 6.5 | 0 | 12 | 1 | 1 | 6.5 | 10 | 0 | 0
282 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.4 | 4 | 7 | 7 | 0 | 12 | 1 | 1 | 7 | 10 | 0 | 0
282.05 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.5 | 5 | 7.5 | 7.5 | 0 | 12 | 1 | 1 | 7.5 | 10 | 0 | 0
282.1 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.6 | 6 | 8 | 8 | 0 | 12 | 1 | 1 | 8 | 10 | 0 | 0
282.15 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.7 | 7 | 8.5 | 8.5 | 0 | 12 | 1 | 1 | 8.5 | 10 | 0 | 0
282.2 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.8 | 8 | 9 | 9 | 0 | 12 | 1 | 1 | 9 | 10 | 0 | 0
282.25 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.9 | 9 | 9.5 | 9.5 | 0 | 12 | 1 | 1 | 9.5 | 10 | 0 | 0
282.3 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
282.35 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
282.4 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
282.45 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
282.5 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
282.55 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
282.6 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
282.65 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
282.7 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
282.75 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
282.8 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
282.85 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
282.9 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
282.95 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
283 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
283.05 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
283.1 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
283.15 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
283.2 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
283.25 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
283.3 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
283.35 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
283.4 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
283.45 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
283.5 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
283.55 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
283.6 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
283.65 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
283.7 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
283.75 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
283.8 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
283.85 | 50.5 | 50.5 | -1 | 0.9 | 9 | 50.5 | -1 | -1 | -10 | -0.5 | -0.5 | 0 | 12 | 1 | 1 | -0.5 | 10 | 0 | 0
283.9 | 50.5 | 50.5 | -1 | 0.8 | 8 | 50.5 | -1 | -1 | -10 | -1 | -1 | 0 | 12 | 1 | 1 | -1 | 10 | 0 | 0
283.95 | 50.5 | 50.5 | -1 | 0.7 | 7 | 50.5 | -1 | -1 | -10 | -1.5 | -1.5 | 0 | 12 | 1 | 1 | -1.5 | 10 | 0 | 0
284 | 50.5 | 50.5 | -1 | 0.6 | 6 | 50.5 | -1 | -1 | -10 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
284.05 | 50.5 | 50.5 | -1 | 0.5 | 5 | 50.5 | -1 | -1 | -10 | -2.5 | -2.5 | 0 | 12 | 1 | 1 | -2.5 | 10 | 0 | 0
284.1 | 50.5 | 50.5 | -1 | 0.4 | 4 | 50.5 | -1 | -1 | -10 | -3 | -3 | 0 | 12 | 1 | 1 | -3 | 10 | 0 | 0
284.15 | 50.5 | 50.5 | -1 | 0.3 | 3 | 50.5 | -1 | -1 | -10 | -3.5 | -3.5 | 0 | 12 | 1 | 1 | -3.5 | 10 | 0 | 0
284.2 | 50.5 | 50.5 | -1 | 0.2 | 2 | 50.5 | -1 | -1 | -10 | -4 | -4 | 0 | 12 | 1 | 1 | -4 | 10 | 0 | 0
284.25 | 50.5 | 50.5 | -1 | 0.1 | 1 | 50.5 | -1 | -1 | -10 | -4.5 | -4.5 | 0 | 12 | 1 | 1 | -4.5 | 10 | 0 | 0
284.3 | 50.5 | 50.5 | -1 | 0 | 0 | 50.5 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
284.35 | 50.5 | 50.5 | -1 | -0.1 | -1 | 50.5 | -1 | -1 | -10 | -5.5 | -5.5 | 0 | 12 | 1 | 1 | -5.5 | 10 | 0 | 0
284.4 | 50.5 | 50.5 | -1 | -0.2 | -2 | 50.5 | -1 | -1 | -10 | -6 | -6 | 0 | 12 | 1 | 1 | -6 | 10 | 0 | 0
284.45 | 50.5 | 50.5 | -1 | -0.3 | -3 | 50.5 | -1 | -1 | -10 | -6.5 | -6.5 | 0 | 12 | 1 | 1 | -6.5 | 10 | 0 | 0
284.5 | 50.5 | 50.5 | -1 | -0.4 | -4 | 50.5 | -1 | -1 | -10 | -7 | -7 | 0 | 12 | 1 | 1 | -7 | 10 | 0 | 0
284.55 | 50.5 | 50.5 | -1 | -0.5 | -5 | 50.5 | -1 | -1 | -10 | -7.5 | -7.5 | 0 | 12 | 1 | 1 | -7.5 | 10 | 0 | 0
284.6 | 50.5 | 50.5 | -1 | -0.6 | -6 | 50.5 | -1 | -1 | -10 | -8 | -8 | 0 | 12 | 1 | 1 | -8 | 10 | 0 | 0
284.65 | 50.5 | 50.5 | -1 | -0.7 | -7 | 50.5 | -1 | -1 | -10 | -8.5 | -8.5 | 0 | 12 | 1 | 1 | -8.5 | 10 | 0 | 0
284.7 | 50.5 | 50.5 | -1 | -0.8 | -8 | 50.5 | -1 | -1 | -10 | -9 | -9 | 0 | 12 | 1 | 1 | -9 | 10 | 0 | 0
284.75 | 50.5 | 50.5 | -1 | -0.9 | -9 | 50.5 | -1 | -1 | -10 | -9.5 | -9.5 | 0 | 12 | 1 | 1 | -9.5 | 10 | 0 | 0
284.8 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
284.85 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
284.9 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
284.95 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
285 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
285.05 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
285.1 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
285.15 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
285.2 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
285.25 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
285.3 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
285.35 | 50.47 | 50.47 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
285.4 | 50.45 | 50.45 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
285.45 | 50.42 | 50.42 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
285.5 | 50.4 | 50.4 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
285.55 | 50.37 | 50.37 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
285.6 | 50.35 | 50.35 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
285.65 | 50.32 | 50.32 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
285.7 | 50.29 | 50.29 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
285.75 | 50.27 | 50.27 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
285.8 | 50.24 | 50.24 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
285.85 | 50.22 | 50.22 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
285.9 | 50.19 | 50.19 | -0.905 | -0.905 | -9.05 | 50.47 | -1 | -1 | -10 | -9.525 | -9.525 | 0 | 12 | 1 | 1 | -9.525 | 10 | 0 | 0
285.95 | 50.17 | 50.17 | -0.715 | -0.715 | -7.15 | 50.45 | -1 | -1 | -10 | -8.575 | -8.575 | 0 | 12 | 1 | 1 | -8.575 | 10 | 0 | 0
286 | 50.14 | 50.14 | -0.43 | -0.43 | -4.3 | 50.42 | -1 | -1 | -10 | -7.15 | -7.15 | 0 | 12 | 1 | 1 | -7.15 | 10 | 0 | 0
286.05 | 50.12 | 50.12 | -0.24 | -0.24 | -2.4 | 50.4 | -1 | -1 | -10 | -6.2 | -6.2 | 0 | 12 | 1 | 1 | -6.2 | 10 | 0 | 0
286.1 | 50.09 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 50.37 | -1 | -1 | -10 | -5.2206 | -5.2206 | 0 | 12 | 1 | 1 | -5.2206 | 10 | 0 | 0
286.15 | 50.06 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.35 | -1 | -1 | -10 | -5.1324 | -5.1324 | 0 | 12 | 1 | 1 | -5.1324 | 10 | 0 | 0
286.2 | 50.04 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.32 | -1 | -1 | -10 | -5.0735 | -5.0735 | 0 | 12 | 1 | 1 | -5.0735 | 10 | 0 | 0
286.25 | 50.01 | 50.01 | 0 | 0 | 0 | 50.29 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
286.3 | 49.99 | 49.99 | 0 | 0 | 0 | 50.27 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
286.35 | 49.96 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.24 | -1 | -1 | -10 | -4.9265 | -4.9265 | 0 | 12 | 1 | 1 | -4.9265 | 10 | 0 | 0
286.4 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.22 | -1 | -1 | -10 | -4.8676 | -4.8676 | 0 | 12 | 1 | 1 | -4.8676 | 10 | 0 | 0
286.45 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.19 | -0.905 | -0.905 | -9.05 | -4.3044 | -4.3044 | 0 | 12 | 1 | 1 | -4.3044 | 10 | 0 | 0
286.5 | 49.88 | 49.88 | 0.24 | 0.24 | 2.4 | 50.17 | -0.715 | -0.805 | -8.05 | -2.825 | -2.825 | 0 | 12 | 1 | 1 | -2.825 | 10 | 0 | 0
286.55 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.14 | -0.43 | -0.705 | -7.05 | -1.375 | -1.375 | 0 | 12 | 1 | 1 | -1.375 | 10 | 0 | 0
286.6 | 49.83 | 49.83 | 0.715 | 0.715 | 7.15 | 50.12 | -0.24 | -0.605 | -6.05 | 0.55 | 0.55 | 0 | 12 | 1 | 1 | 0.55 | 10 | 0 | 0
286.65 | 49.81 | 49.81 | 0.905 | 0.905 | 9.05 | 50.09 | -0.044118 | -0.505 | -5.05 | 2 | 2 | 0 | 12 | 1 | 1 | 2 | 10 | 0 | 0
286.7 | 49.78 | 49.78 | 1 | 1 | 10 | 50.06 | -0.026471 | -0.405 | -4.05 | 2.975 | 2.975 | 0 | 12 | 1 | 1 | 2.975 | 10 | 0 | 0
286.75 | 49.76 | 49.76 | 1 | 1 | 10 | 50.04 | -0.014706 | -0.305 | -3.05 | 3.475 | 3.475 | 0 | 12 | 1 | 1 | 3.475 | 10 | 0 | 0
286.8 | 49.73 | 49.73 | 1 | 1 | 10 | 50.01 | 0 | -0.205 | -2.05 | 3.975 | 3.975 | 0 | 12 | 1 | 1 | 3.975 | 10 | 0 | 0
286.85 | 49.71 | 49.71 | 1 | 1 | 10 | 49.99 | 0 | -0.105 | -1.05 | 4.475 | 4.475 | 0 | 12 | 1 | 1 | 4.475 | 10 | 0 | 0
286.9 | 49.68 | 49.68 | 1 | 1 | 10 | 49.96 | 0.014706 | -0.005 | -0.05 | 4.975 | 4.975 | 0 | 12 | 1 | 1 | 4.975 | 10 | 0 | 0
286.95 | 49.65 | 49.65 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
287 | 49.63 | 49.63 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
287.05 | 49.6 | 49.6 | 1 | 1 | 10 | 49.88 | 0.24 | 0.14412 | 1.4412 | 5.7206 | 5.7206 | 0 | 12 | 1 | 1 | 5.7206 | 10 | 0 | 0
287.1 | 49.58 | 49.58 | 1 | 1 | 10 | 49.86 | 0.43 | 0.24412 | 2.4412 | 6.2206 | 6.2206 | 0 | 12 | 1 | 1 | 6.2206 | 10 | 0 | 0
287.15 | 49.55 | 49.55 | 1 | 1 | 10 | 49.83 | 0.715 | 0.34412 | 3.4412 | 6.7206 | 6.7206 | 0 | 12 | 1 | 1 | 6.7206 | 10 | 0 | 0
287.2 | 49.53 | 49.53 | 1 | 1 | 10 | 49.81 | 0.905 | 0.44412 | 4.4412 | 7.2206 | 7.2206 | 0 | 12 | 1 | 1 | 7.2206 | 10 | 0 | 0
287.25 | 49.5 | 49.5 | 1 | 1 | 10 | 49.78 | 1 | 0.54412 | 5.4412 | 7.7206 | 7.7206 | 0 | 12 | 1 | 1 | 7.7206 | 10 | 0 | 0
287.3 | 49.5 | 49.5 | 1 | 1 | 10 | 49.76 | 1 | 0.64412 | 6.4412 | 8.2206 | 8.2206 | 0 | 12 | 1 | 1 | 8.2206 | 10 | 0 | 0
287.35 | 49.53 | 49.5 | 1 | 1 | 10 | 49.73 | 1 | 0.74412 | 7.4412 | 8.7206 | 8.7206 | 0 | 12 | 1 | 1 | 8.7206 | 10 | 0 | 0
287.4 | 49.55 | 49.5 | 1 | 1 | 10 | 49.71 | 1 | 0.84412 | 8.4412 | 9.2206 | 9.2206 | 0 | 12 | 1 | 1 | 9.2206 | 10 | 0 | 0
287.45 | 49.58 | 49.5 | 1 | 1 | 10 | 49.68 | 1 | 0.94412 | 9.4412 | 9.7206 | 9.7206 | 0 | 12 | 1 | 1 | 9.7206 | 10 | 0 | 0
287.5 | 49.6 | 49.5 | 1 | 1 | 10 | 49.65 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
287.55 | 49.63 | 49.5 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
287.6 | 49.65 | 49.5 | 1 | 1 | 10 | 49.65 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
287.65 | 49.68 | 49.5 | 1 | 1 | 10 | 49.68 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
287.7 | 49.71 | 49.5 | 1 | 1 | 10 | 49.71 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
287.75 | 49.73 | 49.5 | 1 | 1 | 10 | 49.73 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
287.8 | 49.76 | 49.5 | 1 | 1 | 10 | 49.76 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
287.85 | 49.78 | 49.5 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
287.9 | 49.81 | 49.53 | 1 | 1 | 10 | 49.81 | 0.905 | 0.905 | 9.05 | 9.525 | 9.525 | 0 | 12 | 1 | 1 | 9.525 | 10 | 0 | 0
287.95 | 49.83 | 49.55 | 1 | 1 | 10 | 49.83 | 0.715 | 0.715 | 7.15 | 8.575 | 8.575 | 0 | 12 | 1 | 1 | 8.575 | 10 | 0 | 0
288 | 49.86 | 49.58 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
288.05 | 49.88 | 49.6 | 1 | 1 | 10 | 49.88 | 0.24 | 0.24 | 2.4 | 6.2 | 6.2 | 0 | 12 | 1 | 1 | 6.2 | 10 | 0 | 0
288.1 | 49.91 | 49.63 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
288.15 | 49.94 | 49.65 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
288.2 | 49.96 | 49.68 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
288.25 | 49.99 | 49.71 | 1 | 1 | 10 | 49.99 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
288.3 | 50.01 | 49.73 | 1 | 1 | 10 | 50.01 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
288.35 | 50.04 | 49.76 | 1 | 1 | 10 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 4.9265 | 4.9265 | 0 | 12 | 1 | 1 | 4.9265 | 10 | 0 | 0
288.4 | 50.06 | 49.78 | 1 | 1 | 10 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 4.8676 | 4.8676 | 0 | 12 | 1 | 1 | 4.8676 | 10 | 0 | 0
288.45 | 50.09 | 49.81 | 0.905 | 0.905 | 9.05 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 4.3044 | 4.3044 | 0 | 12 | 1 | 1 | 4.3044 | 10 | 0 | 0
288.5 | 50.12 | 49.83 | 0.715 | 0.805 | 8.05 | 50.12 | -0.24 | -0.24 | -2.4 | 2.825 | 2.825 | 0 | 12 | 1 | 1 | 2.825 | 10 | 0 | 0
288.55 | 50.14 | 49.86 | 0.43 | 0.705 | 7.05 | 50.14 | -0.43 | -0.43 | -4.3 | 1.375 | 1.375 | 0 | 12 | 1 | 1 | 1.375 | 10 | 0 | 0
288.6 | 50.17 | 49.88 | 0.24 | 0.605 | 6.05 | 50.17 | -0.715 | -0.715 | -7.15 | -0.55 | -0.55 | 0 | 12 | 1 | 1 | -0.55 | 10 | 0 | 0
288.65 | 50.19 | 49.91 | 0.044118 | 0.505 | 5.05 | 50.19 | -0.905 | -0.905 | -9.05 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
288.7 | 50.22 | 49.94 | 0.026471 | 0.405 | 4.05 | 50.22 | -1 | -1 | -10 | -2.975 | -2.975 | 0 | 12 | 1 | 1 | -2.975 | 10 | 0 | 0
288.75 | 50.24 | 49.96 | 0.014706 | 0.305 | 3.05 | 50.24 | -1 | -1 | -10 | -3.475 | -3.475 | 0 | 12 | 1 | 1 | -3.475 | 10 | 0 | 0
288.8 | 50.27 | 49.99 | 0 | 0.205 | 2.05 | 50.27 | -1 | -1 | -10 | -3.975 | -3.975 | 0 | 12 | 1 | 1 | -3.975 | 10 | 0 | 0
288.85 | 50.29 | 50.01 | 0 | 0.105 | 1.05 | 50.29 | -1 | -1 | -10 | -4.475 | -4.475 | 0 | 12 | 1 | 1 | -4.475 | 10 | 0 | 0
288.9 | 50.32 | 50.04 | -0.014706 | 0.005 | 0.05 | 50.32 | -1 | -1 | -10 | -4.975 | -4.975 | 0 | 12 | 1 | 1 | -4.975 | 10 | 0 | 0
288.95 | 50.35 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.35 | -1 | -1 | -10 | -5.1324 | -5.1324 | 0 | 12 | 1 | 1 | -5.1324 | 10 | 0 | 0
289 | 50.37 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 50.37 | -1 | -1 | -10 | -5.2206 | -5.2206 | 0 | 12 | 1 | 1 | -5.2206 | 10 | 0 | 0
289.05 | 50.4 | 50.12 | -0.24 | -0.14412 | -1.4412 | 50.4 | -1 | -1 | -10 | -5.7206 | -5.7206 | 0 | 12 | 1 | 1 | -5.7206 | 10 | 0 | 0
289.1 | 50.42 | 50.14 | -0.43 | -0.24412 | -2.4412 | 50.42 | -1 | -1 | -10 | -6.2206 | -6.2206 | 0 | 12 | 1 | 1 | -6.2206 | 10 | 0 | 0
289.15 | 50.45 | 50.17 | -0.715 | -0.34412 | -3.4412 | 50.45 | -1 | -1 | -10 | -6.7206 | -6.7206 | 0 | 12 | 1 | 1 | -6.7206 | 10 | 0 | 0
289.2 | 50.47 | 50.19 | -0.905 | -0.44412 | -4.4412 | 50.47 | -1 | -1 | -10 | -7.2206 | -7.2206 | 0 | 12 | 1 | 1 | -7.2206 | 10 | 0 | 0
289.25 | 50.5 | 50.22 | -1 | -0.54412 | -5.4412 | 50.5 | -1 | -1 | -10 | -7.7206 | -7.7206 | 0 | 12 | 1 | 1 | -7.7206 | 10 | 0 | 0
289.3 | 50.5 | 50.24 | -1 | -0.64412 | -6.4412 | 50.5 | -1 | -1 | -10 | -8.2206 | -8.2206 | 0 | 12 | 1 | 1 | -8.2206 | 10 | 0 | 0
289.35 | 50.47 | 50.27 | -1 | -0.74412 | -7.4412 | 50.5 | -1 | -1 | -10 | -8.7206 | -8.7206 | 0 | 12 | 1 | 1 | -8.7206 | 10 | 0 | 0
289.4 | 50.45 | 50.29 | -1 | -0.84412 | -8.4412 | 50.5 | -1 | -1 | -10 | -9.2206 | -9.2206 | 0 | 12 | 1 | 1 | -9.2206 | 10 | 0 | 0
289.45 | 50.42 | 50.32 | -1 | -0.94412 | -9.4412 | 50.5 | -1 | -1 | -10 | -9.7206 | -9.7206 | 0 | 12 | 1 | 1 | -9.7206 | 10 | 0 | 0
289.5 | 50.39 | 50.35 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
289.55 | 50.37 | 50.37 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
289.6 | 50.34 | 50.34 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
289.65 | 50.32 | 50.32 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
289.7 | 50.29 | 50.29 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
289.75 | 50.26 | 50.26 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
289.8 | 50.24 | 50.24 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
289.85 | 50.21 | 50.21 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
289.9 | 50.18 | 50.18 | -0.81 | -0.81 | -8.1 | 50.47 | -1 | -1 | -10 | -9.05 | -9.05 | 0 | 12 | 1 | 1 | -9.05 | 10 | 0 | 0
289.95 | 50.16 | 50.16 | -0.62 | -0.62 | -6.2 | 50.45 | -1 | -1 | -10 | -8.1 | -8.1 | 0 | 12 | 1 | 1 | -8.1 | 10 | 0 | 0
290 | 50.13 | 50.13 | -0.335 | -0.335 | -3.35 | 50.42 | -1 | -1 | -10 | -6.675 | -6.675 | 0 | 12 | 1 | 1 | -6.675 | 10 | 0 | 0
290.05 | 50.11 | 50.11 | -0.145 | -0.145 | -1.45 | 50.39 | -1 | -1 | -10 | -5.725 | -5.725 | 0 | 12 | 1 | 1 | -5.725 | 10 | 0 | 0
290.1 | 50.08 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 50.37 | -1 | -1 | -10 | -5.1912 | -5.1912 | 0 | 12 | 1 | 1 | -5.1912 | 10 | 0 | 0
290.15 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.34 | -1 | -1 | -10 | -5.1029 | -5.1029 | 0 | 12 | 1 | 1 | -5.1029 | 10 | 0 | 0
290.2 | 50.03 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 50.32 | -1 | -1 | -10 | -5.0441 | -5.0441 | 0 | 12 | 1 | 1 | -5.0441 | 10 | 0 | 0
290.25 | 50 | 50 | 0 | 0 | 0 | 50.29 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
290.3 | 50 | 50 | 0 | 0 | 0 | 50.26 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
290.35 | 50 | 50 | 0 | 0 | 0 | 50.24 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
290.4 | 50 | 50 | 0 | 0 | 0 | 50.21 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
290.45 | 50 | 50 | 0 | 0 | 0 | 50.18 | -0.81 | -0.9 | -9 | -4.5 | -4.5 | 0 | 12 | 1 | 1 | -4.5 | 10 | 0 | 0
290.5 | 50 | 50 | 0 | 0 | 0 | 50.16 | -0.62 | -0.8 | -8 | -4 | -4 | 0 | 12 | 1 | 1 | -4 | 10 | 0 | 0
290.55 | 50 | 50 | 0 | 0 | 0 | 50.13 | -0.335 | -0.7 | -7 | -3.5 | -3.5 | 0 | 12 | 1 | 1 | -3.5 | 10 | 0 | 0
290.6 | 50.01 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.6 | -6 | -3 | -3 | 0 | 12 | 1 | 1 | -3 | 10 | 0 | 0
290.65 | 50.01 | 50 | 0 | 0 | 0 | 50.08 | -0.038235 | -0.5 | -5 | -2.5 | -2.5 | 0 | 12 | 1 | 1 | -2.5 | 10 | 0 | 0
290.7 | 49.99 | 49.99 | 0 | 0 | 0 | 50.05 | -0.020588 | -0.4 | -4 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
290.75 | 49.99 | 49.99 | 0 | 0 | 0 | 50.03 | -0.0088235 | -0.3 | -3 | -1.5 | -1.5 | 0 | 12 | 1 | 1 | -1.5 | 10 | 0 | 0
290.8 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | -0.2 | -2 | -0.83824 | -0.83824 | 0 | 12 | 1 | 1 | -0.83824 | 10 | 0 | 0
290.85 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | -0.1 | -1 | -0.33824 | -0.33824 | 0 | 12 | 1 | 1 | -0.33824 | 10 | 0 | 0
290.9 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
290.95 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
291 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
291.05 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
291.1 | 49.89 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
291.15 | 49.89 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
291.2 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50.01 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
291.25 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
291.3 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
291.35 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 2.7868 | 2.7868 | 0 | 12 | 1 | 1 | 2.7868 | 10 | 0 | 0
291.4 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 2.7868 | 2.7868 | 0 | 12 | 1 | 1 | 2.7868 | 10 | 0 | 0
291.45 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 2.8456 | 2.8456 | 0 | 12 | 1 | 1 | 2.8456 | 10 | 0 | 0
291.5 | 49.94 | 49.85 | 0.525 | 0.525 | 5.25 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 2.7574 | 2.7574 | 0 | 12 | 1 | 1 | 2.7574 | 10 | 0 | 0
291.55 | 49.94 | 49.85 | 0.525 | 0.525 | 5.25 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 2.7574 | 2.7574 | 0 | 12 | 1 | 1 | 2.7574 | 10 | 0 | 0
291.6 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
291.65 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
291.7 | 49.93 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
291.75 | 49.93 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
291.8 | 49.96 | 49.85 | 0.525 | 0.525 | 5.25 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 2.6985 | 2.6985 | 0 | 12 | 1 | 1 | 2.6985 | 10 | 0 | 0
291.85 | 49.96 | 49.85 | 0.525 | 0.525 | 5.25 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 2.6985 | 2.6985 | 0 | 12 | 1 | 1 | 2.6985 | 10 | 0 | 0
291.9 | 49.99 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
291.95 | 49.99 | 49.91 | 0.044118 | 0.425 | 4.25 | 49.99 | 0 | 0 | 0 | 2.125 | 2.125 | 0 | 12 | 1 | 1 | 2.125 | 10 | 0 | 0
292 | 49.99 | 49.91 | 0.044118 | 0.325 | 3.25 | 49.99 | 0 | 0 | 0 | 1.625 | 1.625 | 0 | 12 | 1 | 1 | 1.625 | 10 | 0 | 0
292.05 | 49.99 | 49.93 | 0.032353 | 0.225 | 2.25 | 49.99 | 0 | 0 | 0 | 1.125 | 1.125 | 0 | 12 | 1 | 1 | 1.125 | 10 | 0 | 0
292.1 | 49.96 | 49.93 | 0.032353 | 0.125 | 1.25 | 49.99 | 0 | 0 | 0 | 0.625 | 0.625 | 0 | 12 | 1 | 1 | 0.625 | 10 | 0 | 0
292.15 | 49.96 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 49.99 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
292.2 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
292.25 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
292.3 | 50.05 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.058824 | 0.058824 | 0 | 12 | 1 | 1 | 0.058824 | 10 | 0 | 0
292.35 | 50.05 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
292.4 | 49.97 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
292.45 | 49.97 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
292.5 | 49.92 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
292.55 | 49.92 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
292.6 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
292.65 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
292.7 | 49.94 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
292.75 | 49.94 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
292.8 | 50.01 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
292.85 | 50.01 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
292.9 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
292.95 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
293 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
293.05 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
293.1 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
293.15 | 49.95 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
293.2 | 49.97 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
293.25 | 49.97 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
293.3 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
293.35 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
293.4 | 49.87 | 49.87 | 0.335 | 0.335 | 3.35 | 50.01 | 0 | 0 | 0 | 1.675 | 1.675 | 0 | 12 | 1 | 1 | 1.675 | 10 | 0 | 0
293.45 | 49.87 | 49.87 | 0.335 | 0.335 | 3.35 | 49.99 | 0 | 0 | 0 | 1.675 | 1.675 | 0 | 12 | 1 | 1 | 1.675 | 10 | 0 | 0
293.5 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
293.55 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 2.6691 | 2.6691 | 0 | 12 | 1 | 1 | 2.6691 | 10 | 0 | 0
293.6 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
293.65 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
293.7 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
293.75 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
293.8 | 49.84 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
293.85 | 49.84 | 49.79 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
293.9 | 49.89 | 49.79 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
293.95 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.12647 | 1.2647 | 5.6324 | 5.6324 | 0 | 12 | 1 | 1 | 5.6324 | 10 | 0 | 0
294 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.145 | 1.45 | 5.725 | 5.725 | 0 | 12 | 1 | 1 | 5.725 | 10 | 0 | 0
294.05 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.145 | 1.45 | 5.725 | 5.725 | 0 | 12 | 1 | 1 | 5.725 | 10 | 0 | 0
294.1 | 49.96 | 49.79 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
294.15 | 49.96 | 49.79 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
294.2 | 50.02 | 49.79 | 1 | 1 | 10 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 4.9853 | 4.9853 | 0 | 12 | 1 | 1 | 4.9853 | 10 | 0 | 0
294.25 | 50.02 | 49.79 | 1 | 1 | 10 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 4.9853 | 4.9853 | 0 | 12 | 1 | 1 | 4.9853 | 10 | 0 | 0
294.3 | 50.03 | 49.79 | 1 | 1 | 10 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.9559 | 4.9559 | 0 | 12 | 1 | 1 | 4.9559 | 10 | 0 | 0
294.35 | 50.03 | 49.84 | 0.62 | 0.9 | 9 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.4559 | 4.4559 | 0 | 12 | 1 | 1 | 4.4559 | 10 | 0 | 0
294.4 | 50.02 | 49.84 | 0.62 | 0.8 | 8 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 3.9559 | 3.9559 | 0 | 12 | 1 | 1 | 3.9559 | 10 | 0 | 0
294.45 | 50.02 | 49.89 | 0.145 | 0.7 | 7 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 3.4559 | 3.4559 | 0 | 12 | 1 | 1 | 3.4559 | 10 | 0 | 0
294.5 | 50.08 | 49.89 | 0.145 | 0.6 | 6 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 2.8088 | 2.8088 | 0 | 12 | 1 | 1 | 2.8088 | 10 | 0 | 0
294.55 | 50.08 | 49.89 | 0.145 | 0.5 | 5 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 2.3088 | 2.3088 | 0 | 12 | 1 | 1 | 2.3088 | 10 | 0 | 0
294.6 | 50.01 | 49.89 | 0.145 | 0.4 | 4 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 1.8088 | 1.8088 | 0 | 12 | 1 | 1 | 1.8088 | 10 | 0 | 0
294.65 | 50.01 | 49.96 | 0.014706 | 0.3 | 3 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 1.3088 | 1.3088 | 0 | 12 | 1 | 1 | 1.3088 | 10 | 0 | 0
294.7 | 49.94 | 49.94 | 0.026471 | 0.2 | 2 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.80882 | 0.80882 | 0 | 12 | 1 | 1 | 0.80882 | 10 | 0 | 0
294.75 | 49.94 | 49.94 | 0.026471 | 0.1 | 1 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.30882 | 0.30882 | 0 | 12 | 1 | 1 | 0.30882 | 10 | 0 | 0
294.8 | 50 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
294.85 | 50 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
294.9 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
294.95 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
295 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
295.05 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
295.1 | 49.92 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
295.15 | 49.92 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
295.2 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50.01 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
295.25 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
295.3 | 49.92 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
295.35 | 49.92 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
295.4 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
295.45 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
295.5 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
295.55 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
295.6 | 49.87 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
295.65 | 49.87 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
295.7 | 49.8 | 49.8 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
295.75 | 49.8 | 49.8 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
295.8 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
295.85 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
295.9 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
295.95 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
296 | 49.72 | 49.72 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
296.05 | 49.72 | 49.72 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
296.1 | 49.67 | 49.67 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
296.15 | 49.67 | 49.67 | 1 | 1 | 10 | 49.87 | 0.335 | 0.14412 | 1.4412 | 5.7206 | 5.7206 | 0 | 12 | 1 | 1 | 5.7206 | 10 | 0 | 0
296.2 | 49.65 | 49.65 | 1 | 1 | 10 | 49.87 | 0.335 | 0.24412 | 2.4412 | 6.2206 | 6.2206 | 0 | 12 | 1 | 1 | 6.2206 | 10 | 0 | 0
296.25 | 49.65 | 49.65 | 1 | 1 | 10 | 49.8 | 1 | 0.34412 | 3.4412 | 6.7206 | 6.7206 | 0 | 12 | 1 | 1 | 6.7206 | 10 | 0 | 0
296.3 | 49.59 | 49.59 | 1 | 1 | 10 | 49.8 | 1 | 0.44412 | 4.4412 | 7.2206 | 7.2206 | 0 | 12 | 1 | 1 | 7.2206 | 10 | 0 | 0
296.35 | 49.59 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.54412 | 5.4412 | 7.7206 | 7.7206 | 0 | 12 | 1 | 1 | 7.7206 | 10 | 0 | 0
296.4 | 49.66 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.64412 | 6.4412 | 8.2206 | 8.2206 | 0 | 12 | 1 | 1 | 8.2206 | 10 | 0 | 0
296.45 | 49.66 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.74412 | 7.4412 | 8.7206 | 8.7206 | 0 | 12 | 1 | 1 | 8.7206 | 10 | 0 | 0
296.5 | 49.63 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.84412 | 8.4412 | 9.2206 | 9.2206 | 0 | 12 | 1 | 1 | 9.2206 | 10 | 0 | 0
296.55 | 49.63 | 49.59 | 1 | 1 | 10 | 49.72 | 1 | 0.94412 | 9.4412 | 9.7206 | 9.7206 | 0 | 12 | 1 | 1 | 9.7206 | 10 | 0 | 0
296.6 | 49.61 | 49.59 | 1 | 1 | 10 | 49.72 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
296.65 | 49.61 | 49.59 | 1 | 1 | 10 | 49.67 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
296.7 | 49.54 | 49.54 | 1 | 1 | 10 | 49.67 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
296.75 | 49.54 | 49.54 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
296.8 | 49.46 | 49.46 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
296.85 | 49.46 | 49.46 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
296.9 | 49.45 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
296.95 | 49.45 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
297 | 49.51 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
297.05 | 49.51 | 49.45 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
297.1 | 49.5 | 49.45 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
297.15 | 49.5 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
297.2 | 49.54 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
297.25 | 49.54 | 49.45 | 1 | 1 | 10 | 49.54 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
297.3 | 49.59 | 49.45 | 1 | 1 | 10 | 49.59 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
297.35 | 49.59 | 49.45 | 1 | 1 | 10 | 49.59 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
297.4 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
297.45 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
297.5 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
297.55 | 49.61 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
297.6 | 49.53 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
297.65 | 49.53 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
297.7 | 49.54 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
297.75 | 49.54 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
297.8 | 49.61 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
297.85 | 49.61 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
297.9 | 49.66 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
297.95 | 49.66 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
298 | 49.64 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
298.05 | 49.64 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
298.1 | 49.69 | 49.53 | 1 | 1 | 10 | 49.69 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
298.15 | 49.69 | 49.53 | 1 | 1 | 10 | 49.69 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
298.2 | 49.74 | 49.53 | 1 | 1 | 10 | 49.74 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
298.25 | 49.74 | 49.54 | 1 | 1 | 10 | 49.74 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
298.3 | 49.78 | 49.54 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
298.35 | 49.78 | 49.61 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
298.4 | 49.82 | 49.61 | 1 | 1 | 10 | 49.82 | 0.81 | 0.81 | 8.1 | 9.05 | 9.05 | 0 | 12 | 1 | 1 | 9.05 | 10 | 0 | 0
298.45 | 49.82 | 49.64 | 1 | 1 | 10 | 49.82 | 0.81 | 0.81 | 8.1 | 9.05 | 9.05 | 0 | 12 | 1 | 1 | 9.05 | 10 | 0 | 0
298.5 | 49.86 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
298.55 | 49.86 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
298.6 | 49.84 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
298.65 | 49.84 | 49.69 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
298.7 | 49.91 | 49.69 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
298.75 | 49.91 | 49.74 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
298.8 | 49.97 | 49.74 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
298.85 | 49.97 | 49.78 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
298.9 | 50.03 | 49.78 | 1 | 1 | 10 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.9559 | 4.9559 | 0 | 12 | 1 | 1 | 4.9559 | 10 | 0 | 0
298.95 | 50.03 | 49.82 | 0.81 | 0.9 | 9 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.4559 | 4.4559 | 0 | 12 | 1 | 1 | 4.4559 | 10 | 0 | 0
299 | 50.05 | 49.82 | 0.81 | 0.81 | 8.1 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 3.9471 | 3.9471 | 0 | 12 | 1 | 1 | 3.9471 | 10 | 0 | 0
299.05 | 50.05 | 49.84 | 0.62 | 0.71 | 7.1 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 3.4471 | 3.4471 | 0 | 12 | 1 | 1 | 3.4471 | 10 | 0 | 0
299.1 | 50.01 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
299.15 | 50.01 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
299.2 | 49.95 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
299.25 | 49.95 | 49.91 | 0.044118 | 0.52 | 5.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.4971 | 2.4971 | 0 | 12 | 1 | 1 | 2.4971 | 10 | 0 | 0
299.3 | 49.99 | 49.91 | 0.044118 | 0.42 | 4.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 1.9971 | 1.9971 | 0 | 12 | 1 | 1 | 1.9971 | 10 | 0 | 0
299.35 | 49.99 | 49.95 | 0.020588 | 0.32 | 3.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 1.4971 | 1.4971 | 0 | 12 | 1 | 1 | 1.4971 | 10 | 0 | 0
299.4 | 49.92 | 49.92 | 0.038235 | 0.22 | 2.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.99706 | 0.99706 | 0 | 12 | 1 | 1 | 0.99706 | 10 | 0 | 0
299.45 | 49.92 | 49.92 | 0.038235 | 0.12 | 1.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.49706 | 0.49706 | 0 | 12 | 1 | 1 | 0.49706 | 10 | 0 | 0
299.5 | 49.97 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
299.55 | 49.97 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
299.6 | 50.02 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
299.65 | 50.02 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.17647 | 0.17647 | 0 | 12 | 1 | 1 | 0.17647 | 10 | 0 | 0
299.7 | 50.07 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
299.75 | 50.07 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
299.8 | 50.06 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
299.85 | 50.06 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
299.9 | 50.13 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
299.95 | 50.13 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
300 | 50.09 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
300.05 | 50.09 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6309 | -1.6309 | 0 | 12 | 1 | 1 | -1.6309 | 10 | 0 | 0
300.1 | 50.07 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6309 | -1.6309 | 0 | 12 | 1 | 1 | -1.6309 | 10 | 0 | 0
300.15 | 50.07 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6897 | -1.6897 | 0 | 12 | 1 | 1 | -1.6897 | 10 | 0 | 0
300.2 | 50.07 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6897 | -1.6897 | 0 | 12 | 1 | 1 | -1.6897 | 10 | 0 | 0
300.25 | 50.07 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.13 | -0.335 | -0.335 | -3.35 | -1.8074 | -1.8074 | 0 | 12 | 1 | 1 | -1.8074 | 10 | 0 | 0
300.3 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.13 | -0.335 | -0.335 | -3.35 | -1.7779 | -1.7779 | 0 | 12 | 1 | 1 | -1.7779 | 10 | 0 | 0
300.35 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.13 | -0.335 | -0.335 | -3.35 | -1.7779 | -1.7779 | 0 | 12 | 1 | 1 | -1.7779 | 10 | 0 | 0
300.4 | 50.01 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
300.45 | 50.01 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
300.5 | 50.07 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
300.55 | 50.07 | 50.01 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.235 | -2.35 | -1.175 | -1.175 | 0 | 12 | 1 | 1 | -1.175 | 10 | 0 | 0
300.6 | 50.05 | 50.01 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.135 | -1.35 | -0.675 | -0.675 | 0 | 12 | 1 | 1 | -0.675 | 10 | 0 | 0
300.65 | 50.05 | 50.01 | 0 | 0 | 0 | 50.07 | -0.032353 | -0.035 | -0.35 | -0.175 | -0.175 | 0 | 12 | 1 | 1 | -0.175 | 10 | 0 | 0
300.7 | 50.1 | 50.01 | 0 | 0 | 0 | 50.1 | -0.05 | -0.05 | -0.5 | -0.25 | -0.25 | 0 | 12 | 1 | 1 | -0.25 | 10 | 0 | 0
300.75 | 50.1 | 50.01 | 0 | 0 | 0 | 50.1 | -0.05 | -0.05 | -0.5 | -0.25 | -0.25 | 0 | 12 | 1 | 1 | -0.25 | 10 | 0 | 0
300.8 | 50.11 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
300.85 | 50.11 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
300.9 | 50.06 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
300.95 | 50.06 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
301 | 50.04 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
301.05 | 50.04 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
301.1 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
301.15 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
301.2 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
301.25 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
301.3 | 50.11 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
301.35 | 50.11 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
301.4 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
301.45 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
301.5 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
301.55 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
301.6 | 50.02 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.11 | -0.145 | -0.145 | -1.45 | -0.73971 | -0.73971 | 0 | 12 | 1 | 1 | -0.73971 | 10 | 0 | 0
301.65 | 50.02 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.11 | -0.145 | -0.145 | -1.45 | -0.73971 | -0.73971 | 0 | 12 | 1 | 1 | -0.73971 | 10 | 0 | 0
301.7 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
301.75 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
301.8 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
301.85 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
301.9 | 50.01 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
301.95 | 50.01 | 50 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.045 | -0.45 | -0.225 | -0.225 | 0 | 12 | 1 | 1 | -0.225 | 10 | 0 | 0
302 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
302.05 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
302.1 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
302.15 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
302.2 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.14706 | 0.14706 | 0 | 12 | 1 | 1 | 0.14706 | 10 | 0 | 0
302.25 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
302.3 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
302.35 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
302.4 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
302.45 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
302.5 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
302.55 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
302.6 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
302.65 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
302.7 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
302.75 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
302.8 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
302.85 | 50 | 50 | 0 | 0 | 0 | 50.01 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
302.9 | 49.5 | 49.5 | 1 | 1 | 10 | 50.01 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
302.95 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
303 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
303.05 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
303.1 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
303.15 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
303.2 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
303.25 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
303.3 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
303.35 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
303.4 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
303.45 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.1 | 1 | 5.5 | 5.5 | 0 | 12 | 1 | 1 | 5.5 | 10 | 0 | 0
303.5 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.2 | 2 | 6 | 6 | 0 | 12 | 1 | 1 | 6 | 10 | 0 | 0
303.55 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.3 | 3 | 6.5 | 6.5 | 0 | 12 | 1 | 1 | 6.5 | 10 | 0 | 0
303.6 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.4 | 4 | 7 | 7 | 0 | 12 | 1 | 1 | 7 | 10 | 0 | 0
303.65 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.5 | 5 | 7.5 | 7.5 | 0 | 12 | 1 | 1 | 7.5 | 10 | 0 | 0
303.7 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.6 | 6 | 8 | 8 | 0 | 12 | 1 | 1 | 8 | 10 | 0 | 0
303.75 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.7 | 7 | 8.5 | 8.5 | 0 | 12 | 1 | 1 | 8.5 | 10 | 0 | 0
303.8 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.8 | 8 | 9 | 9 | 0 | 12 | 1 | 1 | 9 | 10 | 0 | 0
303.85 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.9 | 9 | 9.5 | 9.5 | 0 | 12 | 1 | 1 | 9.5 | 10 | 0 | 0
303.9 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
303.95 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
304 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
304.05 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
304.1 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
304.15 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
304.2 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
304.25 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
304.3 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
304.35 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
304.4 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
304.45 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
304.5 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
304.55 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
304.6 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
304.65 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
304.7 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
304.75 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
304.8 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
304.85 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
304.9 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
304.95 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
305 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
305.05 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
305.1 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
305.15 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
305.2 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
305.25 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
305.3 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
305.35 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
305.4 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
305.45 | 50.5 | 50.5 | -1 | 0.9 | 9 | 50.5 | -1 | -1 | -10 | -0.5 | -0.5 | 0 | 12 | 1 | 1 | -0.5 | 10 | 0 | 0
305.5 | 50.5 | 50.5 | -1 | 0.8 | 8 | 50.5 | -1 | -1 | -10 | -1 | -1 | 0 | 12 | 1 | 1 | -1 | 10 | 0 | 0
305.55 | 50.5 | 50.5 | -1 | 0.7 | 7 | 50.5 | -1 | -1 | -10 | -1.5 | -1.5 | 0 | 12 | 1 | 1 | -1.5 | 10 | 0 | 0
305.6 | 50.5 | 50.5 | -1 | 0.6 | 6 | 50.5 | -1 | -1 | -10 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
305.65 | 50.5 | 50.5 | -1 | 0.5 | 5 | 50.5 | -1 | -1 | -10 | -2.5 | -2.5 | 0 | 12 | 1 | 1 | -2.5 | 10 | 0 | 0
305.7 | 50.5 | 50.5 | -1 | 0.4 | 4 | 50.5 | -1 | -1 | -10 | -3 | -3 | 0 | 12 | 1 | 1 | -3 | 10 | 0 | 0
305.75 | 50.5 | 50.5 | -1 | 0.3 | 3 | 50.5 | -1 | -1 | -10 | -3.5 | -3.5 | 0 | 12 | 1 | 1 | -3.5 | 10 | 0 | 0
305.8 | 50.5 | 50.5 | -1 | 0.2 | 2 | 50.5 | -1 | -1 | -10 | -4 | -4 | 0 | 12 | 1 | 1 | -4 | 10 | 0 | 0
305.85 | 50.5 | 50.5 | -1 | 0.1 | 1 | 50.5 | -1 | -1 | -10 | -4.5 | -4.5 | 0 | 12 | 1 | 1 | -4.5 | 10 | 0 | 0
305.9 | 50.5 | 50.5 | -1 | 0 | 0 | 50.5 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
305.95 | 50.5 | 50.5 | -1 | -0.1 | -1 | 50.5 | -1 | -1 | -10 | -5.5 | -5.5 | 0 | 12 | 1 | 1 | -5.5 | 10 | 0 | 0
306 | 50.5 | 50.5 | -1 | -0.2 | -2 | 50.5 | -1 | -1 | -10 | -6 | -6 | 0 | 12 | 1 | 1 | -6 | 10 | 0 | 0
306.05 | 50.5 | 50.5 | -1 | -0.3 | -3 | 50.5 | -1 | -1 | -10 | -6.5 | -6.5 | 0 | 12 | 1 | 1 | -6.5 | 10 | 0 | 0
306.1 | 50.5 | 50.5 | -1 | -0.4 | -4 | 50.5 | -1 | -1 | -10 | -7 | -7 | 0 | 12 | 1 | 1 | -7 | 10 | 0 | 0
306.15 | 50.5 | 50.5 | -1 | -0.5 | -5 | 50.5 | -1 | -1 | -10 | -7.5 | -7.5 | 0 | 12 | 1 | 1 | -7.5 | 10 | 0 | 0
306.2 | 50.5 | 50.5 | -1 | -0.6 | -6 | 50.5 | -1 | -1 | -10 | -8 | -8 | 0 | 12 | 1 | 1 | -8 | 10 | 0 | 0
306.25 | 50.5 | 50.5 | -1 | -0.7 | -7 | 50.5 | -1 | -1 | -10 | -8.5 | -8.5 | 0 | 12 | 1 | 1 | -8.5 | 10 | 0 | 0
306.3 | 50.5 | 50.5 | -1 | -0.8 | -8 | 50.5 | -1 | -1 | -10 | -9 | -9 | 0 | 12 | 1 | 1 | -9 | 10 | 0 | 0
306.35 | 50.5 | 50.5 | -1 | -0.9 | -9 | 50.5 | -1 | -1 | -10 | -9.5 | -9.5 | 0 | 12 | 1 | 1 | -9.5 | 10 | 0 | 0
306.4 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
306.45 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
306.5 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
306.55 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
306.6 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
306.65 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
306.7 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
306.75 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
306.8 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
306.85 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
306.9 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
306.95 | 50.47 | 50.47 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
307 | 50.45 | 50.45 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
307.05 | 50.42 | 50.42 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
307.1 | 50.4 | 50.4 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
307.15 | 50.37 | 50.37 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
307.2 | 50.35 | 50.35 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
307.25 | 50.32 | 50.32 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
307.3 | 50.29 | 50.29 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
307.35 | 50.27 | 50.27 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
307.4 | 50.24 | 50.24 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
307.45 | 50.22 | 50.22 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
307.5 | 50.19 | 50.19 | -0.905 | -0.905 | -9.05 | 50.47 | -1 | -1 | -10 | -9.525 | -9.525 | 0 | 12 | 1 | 1 | -9.525 | 10 | 0 | 0
307.55 | 50.17 | 50.17 | -0.715 | -0.715 | -7.15 | 50.45 | -1 | -1 | -10 | -8.575 | -8.575 | 0 | 12 | 1 | 1 | -8.575 | 10 | 0 | 0
307.6 | 50.14 | 50.14 | -0.43 | -0.43 | -4.3 | 50.42 | -1 | -1 | -10 | -7.15 | -7.15 | 0 | 12 | 1 | 1 | -7.15 | 10 | 0 | 0
307.65 | 50.12 | 50.12 | -0.24 | -0.24 | -2.4 | 50.4 | -1 | -1 | -10 | -6.2 | -6.2 | 0 | 12 | 1 | 1 | -6.2 | 10 | 0 | 0
307.7 | 50.09 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 50.37 | -1 | -1 | -10 | -5.2206 | -5.2206 | 0 | 12 | 1 | 1 | -5.2206 | 10 | 0 | 0
307.75 | 50.06 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.35 | -1 | -1 | -10 | -5.1324 | -5.1324 | 0 | 12 | 1 | 1 | -5.1324 | 10 | 0 | 0
307.8 | 50.04 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.32 | -1 | -1 | -10 | -5.0735 | -5.0735 | 0 | 12 | 1 | 1 | -5.0735 | 10 | 0 | 0
307.85 | 50.01 | 50.01 | 0 | 0 | 0 | 50.29 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
307.9 | 49.99 | 49.99 | 0 | 0 | 0 | 50.27 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
307.95 | 49.96 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.24 | -1 | -1 | -10 | -4.9265 | -4.9265 | 0 | 12 | 1 | 1 | -4.9265 | 10 | 0 | 0
308 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.22 | -1 | -1 | -10 | -4.8676 | -4.8676 | 0 | 12 | 1 | 1 | -4.8676 | 10 | 0 | 0
308.05 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.19 | -0.905 | -0.905 | -9.05 | -4.3044 | -4.3044 | 0 | 12 | 1 | 1 | -4.3044 | 10 | 0 | 0
308.1 | 49.88 | 49.88 | 0.24 | 0.24 | 2.4 | 50.17 | -0.715 | -0.805 | -8.05 | -2.825 | -2.825 | 0 | 12 | 1 | 1 | -2.825 | 10 | 0 | 0
308.15 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.14 | -0.43 | -0.705 | -7.05 | -1.375 | -1.375 | 0 | 12 | 1 | 1 | -1.375 | 10 | 0 | 0
308.2 | 49.83 | 49.83 | 0.715 | 0.715 | 7.15 | 50.12 | -0.24 | -0.605 | -6.05 | 0.55 | 0.55 | 0 | 12 | 1 | 1 | 0.55 | 10 | 0 | 0
308.25 | 49.81 | 49.81 | 0.905 | 0.905 | 9.05 | 50.09 | -0.044118 | -0.505 | -5.05 | 2 | 2 | 0 | 12 | 1 | 1 | 2 | 10 | 0 | 0
308.3 | 49.78 | 49.78 | 1 | 1 | 10 | 50.06 | -0.026471 | -0.405 | -4.05 | 2.975 | 2.975 | 0 | 12 | 1 | 1 | 2.975 | 10 | 0 | 0
308.35 | 49.76 | 49.76 | 1 | 1 | 10 | 50.04 | -0.014706 | -0.305 | -3.05 | 3.475 | 3.475 | 0 | 12 | 1 | 1 | 3.475 | 10 | 0 | 0
308.4 | 49.73 | 49.73 | 1 | 1 | 10 | 50.01 | 0 | -0.205 | -2.05 | 3.975 | 3.975 | 0 | 12 | 1 | 1 | 3.975 | 10 | 0 | 0
308.45 | 49.71 | 49.71 | 1 | 1 | 10 | 49.99 | 0 | -0.105 | -1.05 | 4.475 | 4.475 | 0 | 12 | 1 | 1 | 4.475 | 10 | 0 | 0
308.5 | 49.68 | 49.68 | 1 | 1 | 10 | 49.96 | 0.014706 | -0.005 | -0.05 | 4.975 | 4.975 | 0 | 12 | 1 | 1 | 4.975 | 10 | 0 | 0
308.55 | 49.65 | 49.65 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
308.6 | 49.63 | 49.63 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
308.65 | 49.6 | 49.6 | 1 | 1 | 10 | 49.88 | 0.24 | 0.14412 | 1.4412 | 5.7206 | 5.7206 | 0 | 12 | 1 | 1 | 5.7206 | 10 | 0 | 0
308.7 | 49.58 | 49.58 | 1 | 1 | 10 | 49.86 | 0.43 | 0.24412 | 2.4412 | 6.2206 | 6.2206 | 0 | 12 | 1 | 1 | 6.2206 | 10 | 0 | 0
308.75 | 49.55 | 49.55 | 1 | 1 | 10 | 49.83 | 0.715 | 0.34412 | 3.4412 | 6.7206 | 6.7206 | 0 | 12 | 1 | 1 | 6.7206 | 10 | 0 | 0
308.8 | 49.53 | 49.53 | 1 | 1 | 10 | 49.81 | 0.905 | 0.44412 | 4.4412 | 7.2206 | 7.2206 | 0 | 12 | 1 | 1 | 7.2206 | 10 | 0 | 0
308.85 | 49.5 | 49.5 | 1 | 1 | 10 | 49.78 | 1 | 0.54412 | 5.4412 | 7.7206 | 7.7206 | 0 | 12 | 1 | 1 | 7.7206 | 10 | 0 | 0
308.9 | 49.5 | 49.5 | 1 | 1 | 10 | 49.76 | 1 | 0.64412 | 6.4412 | 8.2206 | 8.2206 | 0 | 12 | 1 | 1 | 8.2206 | 10 | 0 | 0
308.95 | 49.53 | 49.5 | 1 | 1 | 10 | 49.73 | 1 | 0.74412 | 7.4412 | 8.7206 | 8.7206 | 0 | 12 | 1 | 1 | 8.7206 | 10 | 0 | 0
309 | 49.55 | 49.5 | 1 | 1 | 10 | 49.71 | 1 | 0.84412 | 8.4412 | 9.2206 | 9.2206 | 0 | 12 | 1 | 1 | 9.2206 | 10 | 0 | 0
309.05 | 49.58 | 49.5 | 1 | 1 | 10 | 49.68 | 1 | 0.94412 | 9.4412 | 9.7206 | 9.7206 | 0 | 12 | 1 | 1 | 9.7206 | 10 | 0 | 0
309.1 | 49.6 | 49.5 | 1 | 1 | 10 | 49.65 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
309.15 | 49.63 | 49.5 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
309.2 | 49.65 | 49.5 | 1 | 1 | 10 | 49.65 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
309.25 | 49.68 | 49.5 | 1 | 1 | 10 | 49.68 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
309.3 | 49.71 | 49.5 | 1 | 1 | 10 | 49.71 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
309.35 | 49.73 | 49.5 | 1 | 1 | 10 | 49.73 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
309.4 | 49.76 | 49.5 | 1 | 1 | 10 | 49.76 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
309.45 | 49.78 | 49.5 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
309.5 | 49.81 | 49.53 | 1 | 1 | 10 | 49.81 | 0.905 | 0.905 | 9.05 | 9.525 | 9.525 | 0 | 12 | 1 | 1 | 9.525 | 10 | 0 | 0
309.55 | 49.83 | 49.55 | 1 | 1 | 10 | 49.83 | 0.715 | 0.715 | 7.15 | 8.575 | 8.575 | 0 | 12 | 1 | 1 | 8.575 | 10 | 0 | 0
309.6 | 49.86 | 49.58 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
309.65 | 49.88 | 49.6 | 1 | 1 | 10 | 49.88 | 0.24 | 0.24 | 2.4 | 6.2 | 6.2 | 0 | 12 | 1 | 1 | 6.2 | 10 | 0 | 0
309.7 | 49.91 | 49.63 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
309.75 | 49.94 | 49.65 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
309.8 | 49.96 | 49.68 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
309.85 | 49.99 | 49.71 | 1 | 1 | 10 | 49.99 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
309.9 | 50.01 | 49.73 | 1 | 1 | 10 | 50.01 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
309.95 | 50.04 | 49.76 | 1 | 1 | 10 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 4.9265 | 4.9265 | 0 | 12 | 1 | 1 | 4.9265 | 10 | 0 | 0
310 | 50.06 | 49.78 | 1 | 1 | 10 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 4.8676 | 4.8676 | 0 | 12 | 1 | 1 | 4.8676 | 10 | 0 | 0
310.05 | 50.09 | 49.81 | 0.905 | 0.905 | 9.05 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 4.3044 | 4.3044 | 0 | 12 | 1 | 1 | 4.3044 | 10 | 0 | 0
310.1 | 50.12 | 49.83 | 0.715 | 0.805 | 8.05 | 50.12 | -0.24 | -0.24 | -2.4 | 2.825 | 2.825 | 0 | 12 | 1 | 1 | 2.825 | 10 | 0 | 0
310.15 | 50.14 | 49.86 | 0.43 | 0.705 | 7.05 | 50.14 | -0.43 | -0.43 | -4.3 | 1.375 | 1.375 | 0 | 12 | 1 | 1 | 1.375 | 10 | 0 | 0
310.2 | 50.17 | 49.88 | 0.24 | 0.605 | 6.05 | 50.17 | -0.715 | -0.715 | -7.15 | -0.55 | -0.55 | 0 | 12 | 1 | 1 | -0.55 | 10 | 0 | 0
310.25 | 50.19 | 49.91 | 0.044118 | 0.505 | 5.05 | 50.19 | -0.905 | -0.905 | -9.05 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
310.3 | 50.22 | 49.94 | 0.026471 | 0.405 | 4.05 | 50.22 | -1 | -1 | -10 | -2.975 | -2.975 | 0 | 12 | 1 | 1 | -2.975 | 10 | 0 | 0
310.35 | 50.24 | 49.96 | 0.014706 | 0.305 | 3.05 | 50.24 | -1 | -1 | -10 | -3.475 | -3.475 | 0 | 12 | 1 | 1 | -3.475 | 10 | 0 | 0
310.4 | 50.27 | 49.99 | 0 | 0.205 | 2.05 | 50.27 | -1 | -1 | -10 | -3.975 | -3.975 | 0 | 12 | 1 | 1 | -3.975 | 10 | 0 | 0
310.45 | 50.29 | 50.01 | 0 | 0.105 | 1.05 | 50.29 | -1 | -1 | -10 | -4.475 | -4.475 | 0 | 12 | 1 | 1 | -4.475 | 10 | 0 | 0
310.5 | 50.32 | 50.04 | -0.014706 | 0.005 | 0.05 | 50.32 | -1 | -1 | -10 | -4.975 | -4.975 | 0 | 12 | 1 | 1 | -4.975 | 10 | 0 | 0
310.55 | 50.35 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.35 | -1 | -1 | -10 | -5.1324 | -5.1324 | 0 | 12 | 1 | 1 | -5.1324 | 10 | 0 | 0
310.6 | 50.37 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 50.37 | -1 | -1 | -10 | -5.2206 | -5.2206 | 0 | 12 | 1 | 1 | -5.2206 | 10 | 0 | 0
310.65 | 50.4 | 50.12 | -0.24 | -0.14412 | -1.4412 | 50.4 | -1 | -1 | -10 | -5.7206 | -5.7206 | 0 | 12 | 1 | 1 | -5.7206 | 10 | 0 | 0
310.7 | 50.42 | 50.14 | -0.43 | -0.24412 | -2.4412 | 50.42 | -1 | -1 | -10 | -6.2206 | -6.2206 | 0 | 12 | 1 | 1 | -6.2206 | 10 | 0 | 0
310.75 | 50.45 | 50.17 | -0.715 | -0.34412 | -3.4412 | 50.45 | -1 | -1 | -10 | -6.7206 | -6.7206 | 0 | 12 | 1 | 1 | -6.7206 | 10 | 0 | 0
310.8 | 50.47 | 50.19 | -0.905 | -0.44412 | -4.4412 | 50.47 | -1 | -1 | -10 | -7.2206 | -7.2206 | 0 | 12 | 1 | 1 | -7.2206 | 10 | 0 | 0
310.85 | 50.5 | 50.22 | -1 | -0.54412 | -5.4412 | 50.5 | -1 | -1 | -10 | -7.7206 | -7.7206 | 0 | 12 | 1 | 1 | -7.7206 | 10 | 0 | 0
310.9 | 50.5 | 50.24 | -1 | -0.64412 | -6.4412 | 50.5 | -1 | -1 | -10 | -8.2206 | -8.2206 | 0 | 12 | 1 | 1 | -8.2206 | 10 | 0 | 0
310.95 | 50.47 | 50.27 | -1 | -0.74412 | -7.4412 | 50.5 | -1 | -1 | -10 | -8.7206 | -8.7206 | 0 | 12 | 1 | 1 | -8.7206 | 10 | 0 | 0
311 | 50.45 | 50.29 | -1 | -0.84412 | -8.4412 | 50.5 | -1 | -1 | -10 | -9.2206 | -9.2206 | 0 | 12 | 1 | 1 | -9.2206 | 10 | 0 | 0
311.05 | 50.42 | 50.32 | -1 | -0.94412 | -9.4412 | 50.5 | -1 | -1 | -10 | -9.7206 | -9.7206 | 0 | 12 | 1 | 1 | -9.7206 | 10 | 0 | 0
311.1 | 50.39 | 50.35 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
311.15 | 50.37 | 50.37 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
311.2 | 50.34 | 50.34 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
311.25 | 50.32 | 50.32 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
311.3 | 50.29 | 50.29 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
311.35 | 50.26 | 50.26 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
311.4 | 50.24 | 50.24 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
311.45 | 50.21 | 50.21 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
311.5 | 50.18 | 50.18 | -0.81 | -0.81 | -8.1 | 50.47 | -1 | -1 | -10 | -9.05 | -9.05 | 0 | 12 | 1 | 1 | -9.05 | 10 | 0 | 0
311.55 | 50.16 | 50.16 | -0.62 | -0.62 | -6.2 | 50.45 | -1 | -1 | -10 | -8.1 | -8.1 | 0 | 12 | 1 | 1 | -8.1 | 10 | 0 | 0
311.6 | 50.13 | 50.13 | -0.335 | -0.335 | -3.35 | 50.42 | -1 | -1 | -10 | -6.675 | -6.675 | 0 | 12 | 1 | 1 | -6.675 | 10 | 0 | 0
311.65 | 50.11 | 50.11 | -0.145 | -0.145 | -1.45 | 50.39 | -1 | -1 | -10 | -5.725 | -5.725 | 0 | 12 | 1 | 1 | -5.725 | 10 | 0 | 0
311.7 | 50.08 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 50.37 | -1 | -1 | -10 | -5.1912 | -5.1912 | 0 | 12 | 1 | 1 | -5.1912 | 10 | 0 | 0
311.75 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.34 | -1 | -1 | -10 | -5.1029 | -5.1029 | 0 | 12 | 1 | 1 | -5.1029 | 10 | 0 | 0
311.8 | 50.03 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 50.32 | -1 | -1 | -10 | -5.0441 | -5.0441 | 0 | 12 | 1 | 1 | -5.0441 | 10 | 0 | 0
311.85 | 50 | 50 | 0 | 0 | 0 | 50.29 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
311.9 | 50 | 50 | 0 | 0 | 0 | 50.26 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
311.95 | 50 | 50 | 0 | 0 | 0 | 50.24 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
312 | 50 | 50 | 0 | 0 | 0 | 50.21 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
312.05 | 50 | 50 | 0 | 0 | 0 | 50.18 | -0.81 | -0.9 | -9 | -4.5 | -4.5 | 0 | 12 | 1 | 1 | -4.5 | 10 | 0 | 0
312.1 | 50 | 50 | 0 | 0 | 0 | 50.16 | -0.62 | -0.8 | -8 | -4 | -4 | 0 | 12 | 1 | 1 | -4 | 10 | 0 | 0
312.15 | 50 | 50 | 0 | 0 | 0 | 50.13 | -0.335 | -0.7 | -7 | -3.5 | -3.5 | 0 | 12 | 1 | 1 | -3.5 | 10 | 0 | 0
312.2 | 50.01 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.6 | -6 | -3 | -3 | 0 | 12 | 1 | 1 | -3 | 10 | 0 | 0
312.25 | 50.01 | 50 | 0 | 0 | 0 | 50.08 | -0.038235 | -0.5 | -5 | -2.5 | -2.5 | 0 | 12 | 1 | 1 | -2.5 | 10 | 0 | 0
312.3 | 49.99 | 49.99 | 0 | 0 | 0 | 50.05 | -0.020588 | -0.4 | -4 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
312.35 | 49.99 | 49.99 | 0 | 0 | 0 | 50.03 | -0.0088235 | -0.3 | -3 | -1.5 | -1.5 | 0 | 12 | 1 | 1 | -1.5 | 10 | 0 | 0
312.4 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | -0.2 | -2 | -0.83824 | -0.83824 | 0 | 12 | 1 | 1 | -0.83824 | 10 | 0 | 0
312.45 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | -0.1 | -1 | -0.33824 | -0.33824 | 0 | 12 | 1 | 1 | -0.33824 | 10 | 0 | 0
312.5 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
312.55 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
312.6 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
312.65 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
312.7 | 49.89 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
312.75 | 49.89 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
312.8 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50.01 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
312.85 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
312.9 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
312.95 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 2.7868 | 2.7868 | 0 | 12 | 1 | 1 | 2.7868 | 10 | 0 | 0
313 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 2.7868 | 2.7868 | 0 | 12 | 1 | 1 | 2.7868 | 10 | 0 | 0
313.05 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 2.8456 | 2.8456 | 0 | 12 | 1 | 1 | 2.8456 | 10 | 0 | 0
313.1 | 49.94 | 49.85 | 0.525 | 0.525 | 5.25 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 2.7574 | 2.7574 | 0 | 12 | 1 | 1 | 2.7574 | 10 | 0 | 0
313.15 | 49.94 | 49.85 | 0.525 | 0.525 | 5.25 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 2.7574 | 2.7574 | 0 | 12 | 1 | 1 | 2.7574 | 10 | 0 | 0
313.2 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
313.25 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
313.3 | 49.93 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
313.35 | 49.93 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
313.4 | 49.96 | 49.85 | 0.525 | 0.525 | 5.25 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 2.6985 | 2.6985 | 0 | 12 | 1 | 1 | 2.6985 | 10 | 0 | 0
313.45 | 49.96 | 49.85 | 0.525 | 0.525 | 5.25 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 2.6985 | 2.6985 | 0 | 12 | 1 | 1 | 2.6985 | 10 | 0 | 0
313.5 | 49.99 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
313.55 | 49.99 | 49.91 | 0.044118 | 0.425 | 4.25 | 49.99 | 0 | 0 | 0 | 2.125 | 2.125 | 0 | 12 | 1 | 1 | 2.125 | 10 | 0 | 0
313.6 | 49.99 | 49.91 | 0.044118 | 0.325 | 3.25 | 49.99 | 0 | 0 | 0 | 1.625 | 1.625 | 0 | 12 | 1 | 1 | 1.625 | 10 | 0 | 0
313.65 | 49.99 | 49.93 | 0.032353 | 0.225 | 2.25 | 49.99 | 0 | 0 | 0 | 1.125 | 1.125 | 0 | 12 | 1 | 1 | 1.125 | 10 | 0 | 0
313.7 | 49.96 | 49.93 | 0.032353 | 0.125 | 1.25 | 49.99 | 0 | 0 | 0 | 0.625 | 0.625 | 0 | 12 | 1 | 1 | 0.625 | 10 | 0 | 0
313.75 | 49.96 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 49.99 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
313.8 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
313.85 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
313.9 | 50.05 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.058824 | 0.058824 | 0 | 12 | 1 | 1 | 0.058824 | 10 | 0 | 0
313.95 | 50.05 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
314 | 49.97 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
314.05 | 49.97 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
314.1 | 49.92 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
314.15 | 49.92 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
314.2 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
314.25 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
314.3 | 49.94 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
314.35 | 49.94 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
314.4 | 50.01 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
314.45 | 50.01 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
314.5 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
314.55 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
314.6 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
314.65 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
314.7 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
314.75 | 49.95 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
314.8 | 49.97 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
314.85 | 49.97 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
314.9 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
314.95 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
315 | 49.87 | 49.87 | 0.335 | 0.335 | 3.35 | 50.01 | 0 | 0 | 0 | 1.675 | 1.675 | 0 | 12 | 1 | 1 | 1.675 | 10 | 0 | 0
315.05 | 49.87 | 49.87 | 0.335 | 0.335 | 3.35 | 49.99 | 0 | 0 | 0 | 1.675 | 1.675 | 0 | 12 | 1 | 1 | 1.675 | 10 | 0 | 0
315.1 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
315.15 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 2.6691 | 2.6691 | 0 | 12 | 1 | 1 | 2.6691 | 10 | 0 | 0
315.2 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
315.25 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
315.3 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
315.35 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
315.4 | 49.84 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
315.45 | 49.84 | 49.79 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
315.5 | 49.89 | 49.79 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
315.55 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.12647 | 1.2647 | 5.6324 | 5.6324 | 0 | 12 | 1 | 1 | 5.6324 | 10 | 0 | 0
315.6 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.145 | 1.45 | 5.725 | 5.725 | 0 | 12 | 1 | 1 | 5.725 | 10 | 0 | 0
315.65 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.145 | 1.45 | 5.725 | 5.725 | 0 | 12 | 1 | 1 | 5.725 | 10 | 0 | 0
315.7 | 49.96 | 49.79 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
315.75 | 49.96 | 49.79 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
315.8 | 50.02 | 49.79 | 1 | 1 | 10 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 4.9853 | 4.9853 | 0 | 12 | 1 | 1 | 4.9853 | 10 | 0 | 0
315.85 | 50.02 | 49.79 | 1 | 1 | 10 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 4.9853 | 4.9853 | 0 | 12 | 1 | 1 | 4.9853 | 10 | 0 | 0
315.9 | 50.03 | 49.79 | 1 | 1 | 10 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.9559 | 4.9559 | 0 | 12 | 1 | 1 | 4.9559 | 10 | 0 | 0
315.95 | 50.03 | 49.84 | 0.62 | 0.9 | 9 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.4559 | 4.4559 | 0 | 12 | 1 | 1 | 4.4559 | 10 | 0 | 0
316 | 50.02 | 49.84 | 0.62 | 0.8 | 8 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 3.9559 | 3.9559 | 0 | 12 | 1 | 1 | 3.9559 | 10 | 0 | 0
316.05 | 50.02 | 49.89 | 0.145 | 0.7 | 7 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 3.4559 | 3.4559 | 0 | 12 | 1 | 1 | 3.4559 | 10 | 0 | 0
316.1 | 50.08 | 49.89 | 0.145 | 0.6 | 6 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 2.8088 | 2.8088 | 0 | 12 | 1 | 1 | 2.8088 | 10 | 0 | 0
316.15 | 50.08 | 49.89 | 0.145 | 0.5 | 5 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 2.3088 | 2.3088 | 0 | 12 | 1 | 1 | 2.3088 | 10 | 0 | 0
316.2 | 50.01 | 49.89 | 0.145 | 0.4 | 4 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 1.8088 | 1.8088 | 0 | 12 | 1 | 1 | 1.8088 | 10 | 0 | 0
316.25 | 50.01 | 49.96 | 0.014706 | 0.3 | 3 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 1.3088 | 1.3088 | 0 | 12 | 1 | 1 | 1.3088 | 10 | 0 | 0
316.3 | 49.94 | 49.94 | 0.026471 | 0.2 | 2 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.80882 | 0.80882 | 0 | 12 | 1 | 1 | 0.80882 | 10 | 0 | 0
316.35 | 49.94 | 49.94 | 0.026471 | 0.1 | 1 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.30882 | 0.30882 | 0 | 12 | 1 | 1 | 0.30882 | 10 | 0 | 0
316.4 | 50 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
316.45 | 50 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
316.5 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
316.55 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
316.6 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
316.65 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
316.7 | 49.92 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
316.75 | 49.92 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
316.8 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50.01 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
316.85 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
316.9 | 49.92 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
316.95 | 49.92 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
317 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
317.05 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
317.1 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
317.15 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
317.2 | 49.87 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
317.25 | 49.87 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
317.3 | 49.8 | 49.8 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
317.35 | 49.8 | 49.8 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
317.4 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
317.45 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
317.5 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
317.55 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
317.6 | 49.72 | 49.72 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
317.65 | 49.72 | 49.72 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
317.7 | 49.67 | 49.67 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
317.75 | 49.67 | 49.67 | 1 | 1 | 10 | 49.87 | 0.335 | 0.14412 | 1.4412 | 5.7206 | 5.7206 | 0 | 12 | 1 | 1 | 5.7206 | 10 | 0 | 0
317.8 | 49.65 | 49.65 | 1 | 1 | 10 | 49.87 | 0.335 | 0.24412 | 2.4412 | 6.2206 | 6.2206 | 0 | 12 | 1 | 1 | 6.2206 | 10 | 0 | 0
317.85 | 49.65 | 49.65 | 1 | 1 | 10 | 49.8 | 1 | 0.34412 | 3.4412 | 6.7206 | 6.7206 | 0 | 12 | 1 | 1 | 6.7206 | 10 | 0 | 0
317.9 | 49.59 | 49.59 | 1 | 1 | 10 | 49.8 | 1 | 0.44412 | 4.4412 | 7.2206 | 7.2206 | 0 | 12 | 1 | 1 | 7.2206 | 10 | 0 | 0
317.95 | 49.59 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.54412 | 5.4412 | 7.7206 | 7.7206 | 0 | 12 | 1 | 1 | 7.7206 | 10 | 0 | 0
318 | 49.66 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.64412 | 6.4412 | 8.2206 | 8.2206 | 0 | 12 | 1 | 1 | 8.2206 | 10 | 0 | 0
318.05 | 49.66 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.74412 | 7.4412 | 8.7206 | 8.7206 | 0 | 12 | 1 | 1 | 8.7206 | 10 | 0 | 0
318.1 | 49.63 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.84412 | 8.4412 | 9.2206 | 9.2206 | 0 | 12 | 1 | 1 | 9.2206 | 10 | 0 | 0
318.15 | 49.63 | 49.59 | 1 | 1 | 10 | 49.72 | 1 | 0.94412 | 9.4412 | 9.7206 | 9.7206 | 0 | 12 | 1 | 1 | 9.7206 | 10 | 0 | 0
318.2 | 49.61 | 49.59 | 1 | 1 | 10 | 49.72 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
318.25 | 49.61 | 49.59 | 1 | 1 | 10 | 49.67 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
318.3 | 49.54 | 49.54 | 1 | 1 | 10 | 49.67 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
318.35 | 49.54 | 49.54 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
318.4 | 49.46 | 49.46 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
318.45 | 49.46 | 49.46 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
318.5 | 49.45 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
318.55 | 49.45 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
318.6 | 49.51 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
318.65 | 49.51 | 49.45 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
318.7 | 49.5 | 49.45 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
318.75 | 49.5 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
318.8 | 49.54 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
318.85 | 49.54 | 49.45 | 1 | 1 | 10 | 49.54 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
318.9 | 49.59 | 49.45 | 1 | 1 | 10 | 49.59 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
318.95 | 49.59 | 49.45 | 1 | 1 | 10 | 49.59 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
319 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
319.05 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
319.1 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
319.15 | 49.61 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
319.2 | 49.53 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
319.25 | 49.53 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
319.3 | 49.54 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
319.35 | 49.54 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
319.4 | 49.61 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
319.45 | 49.61 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
319.5 | 49.66 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
319.55 | 49.66 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
319.6 | 49.64 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
319.65 | 49.64 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
319.7 | 49.69 | 49.53 | 1 | 1 | 10 | 49.69 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
319.75 | 49.69 | 49.53 | 1 | 1 | 10 | 49.69 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
319.8 | 49.74 | 49.53 | 1 | 1 | 10 | 49.74 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
319.85 | 49.74 | 49.54 | 1 | 1 | 10 | 49.74 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
319.9 | 49.78 | 49.54 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
319.95 | 49.78 | 49.61 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
320 | 49.82 | 49.61 | 1 | 1 | 10 | 49.82 | 0.81 | 0.81 | 8.1 | 9.05 | 9.05 | 0 | 12 | 1 | 1 | 9.05 | 10 | 0 | 0
320.05 | 49.82 | 49.64 | 1 | 1 | 10 | 49.82 | 0.81 | 0.81 | 8.1 | 9.05 | 9.05 | 0 | 12 | 1 | 1 | 9.05 | 10 | 0 | 0
320.1 | 49.86 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
320.15 | 49.86 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
320.2 | 49.84 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
320.25 | 49.84 | 49.69 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
320.3 | 49.91 | 49.69 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
320.35 | 49.91 | 49.74 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
320.4 | 49.97 | 49.74 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
320.45 | 49.97 | 49.78 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
320.5 | 50.03 | 49.78 | 1 | 1 | 10 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.9559 | 4.9559 | 0 | 12 | 1 | 1 | 4.9559 | 10 | 0 | 0
320.55 | 50.03 | 49.82 | 0.81 | 0.9 | 9 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.4559 | 4.4559 | 0 | 12 | 1 | 1 | 4.4559 | 10 | 0 | 0
320.6 | 50.05 | 49.82 | 0.81 | 0.81 | 8.1 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 3.9471 | 3.9471 | 0 | 12 | 1 | 1 | 3.9471 | 10 | 0 | 0
320.65 | 50.05 | 49.84 | 0.62 | 0.71 | 7.1 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 3.4471 | 3.4471 | 0 | 12 | 1 | 1 | 3.4471 | 10 | 0 | 0
320.7 | 50.01 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
320.75 | 50.01 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
320.8 | 49.95 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
320.85 | 49.95 | 49.91 | 0.044118 | 0.52 | 5.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.4971 | 2.4971 | 0 | 12 | 1 | 1 | 2.4971 | 10 | 0 | 0
320.9 | 49.99 | 49.91 | 0.044118 | 0.42 | 4.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 1.9971 | 1.9971 | 0 | 12 | 1 | 1 | 1.9971 | 10 | 0 | 0
320.95 | 49.99 | 49.95 | 0.020588 | 0.32 | 3.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 1.4971 | 1.4971 | 0 | 12 | 1 | 1 | 1.4971 | 10 | 0 | 0
321 | 49.92 | 49.92 | 0.038235 | 0.22 | 2.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.99706 | 0.99706 | 0 | 12 | 1 | 1 | 0.99706 | 10 | 0 | 0
321.05 | 49.92 | 49.92 | 0.038235 | 0.12 | 1.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.49706 | 0.49706 | 0 | 12 | 1 | 1 | 0.49706 | 10 | 0 | 0
321.1 | 49.97 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
321.15 | 49.97 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
321.2 | 50.02 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
321.25 | 50.02 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.17647 | 0.17647 | 0 | 12 | 1 | 1 | 0.17647 | 10 | 0 | 0
321.3 | 50.07 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
321.35 | 50.07 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
321.4 | 50.06 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
321.45 | 50.06 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
321.5 | 50.13 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
321.55 | 50.13 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
321.6 | 50.09 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
321.65 | 50.09 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6309 | -1.6309 | 0 | 12 | 1 | 1 | -1.6309 | 10 | 0 | 0
321.7 | 50.07 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6309 | -1.6309 | 0 | 12 | 1 | 1 | -1.6309 | 10 | 0 | 0
321.75 | 50.07 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6897 | -1.6897 | 0 | 12 | 1 | 1 | -1.6897 | 10 | 0 | 0
321.8 | 50.07 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6897 | -1.6897 | 0 | 12 | 1 | 1 | -1.6897 | 10 | 0 | 0
321.85 | 50.07 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.13 | -0.335 | -0.335 | -3.35 | -1.8074 | -1.8074 | 0 | 12 | 1 | 1 | -1.8074 | 10 | 0 | 0
321.9 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.13 | -0.335 | -0.335 | -3.35 | -1.7779 | -1.7779 | 0 | 12 | 1 | 1 | -1.7779 | 10 | 0 | 0
321.95 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.13 | -0.335 | -0.335 | -3.35 | -1.7779 | -1.7779 | 0 | 12 | 1 | 1 | -1.7779 | 10 | 0 | 0
322 | 50.01 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
322.05 | 50.01 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
322.1 | 50.07 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
322.15 | 50.07 | 50.01 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.235 | -2.35 | -1.175 | -1.175 | 0 | 12 | 1 | 1 | -1.175 | 10 | 0 | 0
322.2 | 50.05 | 50.01 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.135 | -1.35 | -0.675 | -0.675 | 0 | 12 | 1 | 1 | -0.675 | 10 | 0 | 0
322.25 | 50.05 | 50.01 | 0 | 0 | 0 | 50.07 | -0.032353 | -0.035 | -0.35 | -0.175 | -0.175 | 0 | 12 | 1 | 1 | -0.175 | 10 | 0 | 0
322.3 | 50.1 | 50.01 | 0 | 0 | 0 | 50.1 | -0.05 | -0.05 | -0.5 | -0.25 | -0.25 | 0 | 12 | 1 | 1 | -0.25 | 10 | 0 | 0
322.35 | 50.1 | 50.01 | 0 | 0 | 0 | 50.1 | -0.05 | -0.05 | -0.5 | -0.25 | -0.25 | 0 | 12 | 1 | 1 | -0.25 | 10 | 0 | 0
322.4 | 50.11 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
322.45 | 50.11 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
322.5 | 50.06 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
322.55 | 50.06 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
322.6 | 50.04 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
322.65 | 50.04 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
322.7 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
322.75 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
322.8 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
322.85 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
322.9 | 50.11 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
322.95 | 50.11 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
323 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
323.05 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
323.1 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
323.15 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
323.2 | 50.02 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.11 | -0.145 | -0.145 | -1.45 | -0.73971 | -0.73971 | 0 | 12 | 1 | 1 | -0.73971 | 10 | 0 | 0
323.25 | 50.02 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.11 | -0.145 | -0.145 | -1.45 | -0.73971 | -0.73971 | 0 | 12 | 1 | 1 | -0.73971 | 10 | 0 | 0
323.3 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
323.35 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
323.4 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
323.45 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
323.5 | 50.01 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
323.55 | 50.01 | 50 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.045 | -0.45 | -0.225 | -0.225 | 0 | 12 | 1 | 1 | -0.225 | 10 | 0 | 0
323.6 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
323.65 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
323.7 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
323.75 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
323.8 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.14706 | 0.14706 | 0 | 12 | 1 | 1 | 0.14706 | 10 | 0 | 0
323.85 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
323.9 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
323.95 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
324 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
324.05 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
324.1 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
324.15 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
324.2 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
324.25 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
324.3 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
324.35 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
324.4 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
324.45 | 50 | 50 | 0 | 0 | 0 | 50.01 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
324.5 | 49.5 | 49.5 | 1 | 1 | 10 | 50.01 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
324.55 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
324.6 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
324.65 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
324.7 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
324.75 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
324.8 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
324.85 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
324.9 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
324.95 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
325 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
325.05 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.1 | 1 | 5.5 | 5.5 | 0 | 12 | 1 | 1 | 5.5 | 10 | 0 | 0
325.1 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.2 | 2 | 6 | 6 | 0 | 12 | 1 | 1 | 6 | 10 | 0 | 0
325.15 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.3 | 3 | 6.5 | 6.5 | 0 | 12 | 1 | 1 | 6.5 | 10 | 0 | 0
325.2 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.4 | 4 | 7 | 7 | 0 | 12 | 1 | 1 | 7 | 10 | 0 | 0
325.25 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.5 | 5 | 7.5 | 7.5 | 0 | 12 | 1 | 1 | 7.5 | 10 | 0 | 0
325.3 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.6 | 6 | 8 | 8 | 0 | 12 | 1 | 1 | 8 | 10 | 0 | 0
325.35 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.7 | 7 | 8.5 | 8.5 | 0 | 12 | 1 | 1 | 8.5 | 10 | 0 | 0
325.4 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.8 | 8 | 9 | 9 | 0 | 12 | 1 | 1 | 9 | 10 | 0 | 0
325.45 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.9 | 9 | 9.5 | 9.5 | 0 | 12 | 1 | 1 | 9.5 | 10 | 0 | 0
325.5 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
325.55 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
325.6 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
325.65 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
325.7 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
325.75 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
325.8 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
325.85 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
325.9 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
325.95 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
326 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
326.05 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
326.1 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
326.15 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
326.2 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
326.25 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
326.3 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
326.35 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
326.4 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
326.45 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
326.5 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
326.55 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
326.6 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
326.65 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
326.7 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
326.75 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
326.8 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
326.85 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
326.9 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
326.95 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
327 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
327.05 | 50.5 | 50.5 | -1 | 0.9 | 9 | 50.5 | -1 | -1 | -10 | -0.5 | -0.5 | 0 | 12 | 1 | 1 | -0.5 | 10 | 0 | 0
327.1 | 50.5 | 50.5 | -1 | 0.8 | 8 | 50.5 | -1 | -1 | -10 | -1 | -1 | 0 | 12 | 1 | 1 | -1 | 10 | 0 | 0
327.15 | 50.5 | 50.5 | -1 | 0.7 | 7 | 50.5 | -1 | -1 | -10 | -1.5 | -1.5 | 0 | 12 | 1 | 1 | -1.5 | 10 | 0 | 0
327.2 | 50.5 | 50.5 | -1 | 0.6 | 6 | 50.5 | -1 | -1 | -10 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
327.25 | 50.5 | 50.5 | -1 | 0.5 | 5 | 50.5 | -1 | -1 | -10 | -2.5 | -2.5 | 0 | 12 | 1 | 1 | -2.5 | 10 | 0 | 0
327.3 | 50.5 | 50.5 | -1 | 0.4 | 4 | 50.5 | -1 | -1 | -10 | -3 | -3 | 0 | 12 | 1 | 1 | -3 | 10 | 0 | 0
327.35 | 50.5 | 50.5 | -1 | 0.3 | 3 | 50.5 | -1 | -1 | -10 | -3.5 | -3.5 | 0 | 12 | 1 | 1 | -3.5 | 10 | 0 | 0
327.4 | 50.5 | 50.5 | -1 | 0.2 | 2 | 50.5 | -1 | -1 | -10 | -4 | -4 | 0 | 12 | 1 | 1 | -4 | 10 | 0 | 0
327.45 | 50.5 | 50.5 | -1 | 0.1 | 1 | 50.5 | -1 | -1 | -10 | -4.5 | -4.5 | 0 | 12 | 1 | 1 | -4.5 | 10 | 0 | 0
327.5 | 50.5 | 50.5 | -1 | 0 | 0 | 50.5 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
327.55 | 50.5 | 50.5 | -1 | -0.1 | -1 | 50.5 | -1 | -1 | -10 | -5.5 | -5.5 | 0 | 12 | 1 | 1 | -5.5 | 10 | 0 | 0
327.6 | 50.5 | 50.5 | -1 | -0.2 | -2 | 50.5 | -1 | -1 | -10 | -6 | -6 | 0 | 12 | 1 | 1 | -6 | 10 | 0 | 0
327.65 | 50.5 | 50.5 | -1 | -0.3 | -3 | 50.5 | -1 | -1 | -10 | -6.5 | -6.5 | 0 | 12 | 1 | 1 | -6.5 | 10 | 0 | 0
327.7 | 50.5 | 50.5 | -1 | -0.4 | -4 | 50.5 | -1 | -1 | -10 | -7 | -7 | 0 | 12 | 1 | 1 | -7 | 10 | 0 | 0
327.75 | 50.5 | 50.5 | -1 | -0.5 | -5 | 50.5 | -1 | -1 | -10 | -7.5 | -7.5 | 0 | 12 | 1 | 1 | -7.5 | 10 | 0 | 0
327.8 | 50.5 | 50.5 | -1 | -0.6 | -6 | 50.5 | -1 | -1 | -10 | -8 | -8 | 0 | 12 | 1 | 1 | -8 | 10 | 0 | 0
327.85 | 50.5 | 50.5 | -1 | -0.7 | -7 | 50.5 | -1 | -1 | -10 | -8.5 | -8.5 | 0 | 12 | 1 | 1 | -8.5 | 10 | 0 | 0
327.9 | 50.5 | 50.5 | -1 | -0.8 | -8 | 50.5 | -1 | -1 | -10 | -9 | -9 | 0 | 12 | 1 | 1 | -9 | 10 | 0 | 0
327.95 | 50.5 | 50.5 | -1 | -0.9 | -9 | 50.5 | -1 | -1 | -10 | -9.5 | -9.5 | 0 | 12 | 1 | 1 | -9.5 | 10 | 0 | 0
328 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
328.05 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
328.1 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
328.15 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
328.2 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
328.25 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
328.3 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
328.35 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
328.4 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
328.45 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
328.5 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
328.55 | 50.47 | 50.47 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
328.6 | 50.45 | 50.45 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
328.65 | 50.42 | 50.42 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
328.7 | 50.4 | 50.4 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
328.75 | 50.37 | 50.37 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
328.8 | 50.35 | 50.35 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
328.85 | 50.32 | 50.32 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
328.9 | 50.29 | 50.29 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
328.95 | 50.27 | 50.27 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
329 | 50.24 | 50.24 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
329.05 | 50.22 | 50.22 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
329.1 | 50.19 | 50.19 | -0.905 | -0.905 | -9.05 | 50.47 | -1 | -1 | -10 | -9.525 | -9.525 | 0 | 12 | 1 | 1 | -9.525 | 10 | 0 | 0
329.15 | 50.17 | 50.17 | -0.715 | -0.715 | -7.15 | 50.45 | -1 | -1 | -10 | -8.575 | -8.575 | 0 | 12 | 1 | 1 | -8.575 | 10 | 0 | 0
329.2 | 50.14 | 50.14 | -0.43 | -0.43 | -4.3 | 50.42 | -1 | -1 | -10 | -7.15 | -7.15 | 0 | 12 | 1 | 1 | -7.15 | 10 | 0 | 0
329.25 | 50.12 | 50.12 | -0.24 | -0.24 | -2.4 | 50.4 | -1 | -1 | -10 | -6.2 | -6.2 | 0 | 12 | 1 | 1 | -6.2 | 10 | 0 | 0
329.3 | 50.09 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 50.37 | -1 | -1 | -10 | -5.2206 | -5.2206 | 0 | 12 | 1 | 1 | -5.2206 | 10 | 0 | 0
329.35 | 50.06 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.35 | -1 | -1 | -10 | -5.1324 | -5.1324 | 0 | 12 | 1 | 1 | -5.1324 | 10 | 0 | 0
329.4 | 50.04 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.32 | -1 | -1 | -10 | -5.0735 | -5.0735 | 0 | 12 | 1 | 1 | -5.0735 | 10 | 0 | 0
329.45 | 50.01 | 50.01 | 0 | 0 | 0 | 50.29 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
329.5 | 49.99 | 49.99 | 0 | 0 | 0 | 50.27 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
329.55 | 49.96 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.24 | -1 | -1 | -10 | -4.9265 | -4.9265 | 0 | 12 | 1 | 1 | -4.9265 | 10 | 0 | 0
329.6 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.22 | -1 | -1 | -10 | -4.8676 | -4.8676 | 0 | 12 | 1 | 1 | -4.8676 | 10 | 0 | 0
329.65 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.19 | -0.905 | -0.905 | -9.05 | -4.3044 | -4.3044 | 0 | 12 | 1 | 1 | -4.3044 | 10 | 0 | 0
329.7 | 49.88 | 49.88 | 0.24 | 0.24 | 2.4 | 50.17 | -0.715 | -0.805 | -8.05 | -2.825 | -2.825 | 0 | 12 | 1 | 1 | -2.825 | 10 | 0 | 0
329.75 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.14 | -0.43 | -0.705 | -7.05 | -1.375 | -1.375 | 0 | 12 | 1 | 1 | -1.375 | 10 | 0 | 0
329.8 | 49.83 | 49.83 | 0.715 | 0.715 | 7.15 | 50.12 | -0.24 | -0.605 | -6.05 | 0.55 | 0.55 | 0 | 12 | 1 | 1 | 0.55 | 10 | 0 | 0
329.85 | 49.81 | 49.81 | 0.905 | 0.905 | 9.05 | 50.09 | -0.044118 | -0.505 | -5.05 | 2 | 2 | 0 | 12 | 1 | 1 | 2 | 10 | 0 | 0
329.9 | 49.78 | 49.78 | 1 | 1 | 10 | 50.06 | -0.026471 | -0.405 | -4.05 | 2.975 | 2.975 | 0 | 12 | 1 | 1 | 2.975 | 10 | 0 | 0
329.95 | 49.76 | 49.76 | 1 | 1 | 10 | 50.04 | -0.014706 | -0.305 | -3.05 | 3.475 | 3.475 | 0 | 12 | 1 | 1 | 3.475 | 10 | 0 | 0
330 | 49.73 | 49.73 | 1 | 1 | 10 | 50.01 | 0 | -0.205 | -2.05 | 3.975 | 3.975 | 0 | 12 | 1 | 1 | 3.975 | 10 | 0 | 0
330.05 | 49.71 | 49.71 | 1 | 1 | 10 | 49.99 | 0 | -0.105 | -1.05 | 4.475 | 4.475 | 0 | 12 | 1 | 1 | 4.475 | 10 | 0 | 0
330.1 | 49.68 | 49.68 | 1 | 1 | 10 | 49.96 | 0.014706 | -0.005 | -0.05 | 4.975 | 4.975 | 0 | 12 | 1 | 1 | 4.975 | 10 | 0 | 0
330.15 | 49.65 | 49.65 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
330.2 | 49.63 | 49.63 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
330.25 | 49.6 | 49.6 | 1 | 1 | 10 | 49.88 | 0.24 | 0.14412 | 1.4412 | 5.7206 | 5.7206 | 0 | 12 | 1 | 1 | 5.7206 | 10 | 0 | 0
330.3 | 49.58 | 49.58 | 1 | 1 | 10 | 49.86 | 0.43 | 0.24412 | 2.4412 | 6.2206 | 6.2206 | 0 | 12 | 1 | 1 | 6.2206 | 10 | 0 | 0
330.35 | 49.55 | 49.55 | 1 | 1 | 10 | 49.83 | 0.715 | 0.34412 | 3.4412 | 6.7206 | 6.7206 | 0 | 12 | 1 | 1 | 6.7206 | 10 | 0 | 0
330.4 | 49.53 | 49.53 | 1 | 1 | 10 | 49.81 | 0.905 | 0.44412 | 4.4412 | 7.2206 | 7.2206 | 0 | 12 | 1 | 1 | 7.2206 | 10 | 0 | 0
330.45 | 49.5 | 49.5 | 1 | 1 | 10 | 49.78 | 1 | 0.54412 | 5.4412 | 7.7206 | 7.7206 | 0 | 12 | 1 | 1 | 7.7206 | 10 | 0 | 0
330.5 | 49.5 | 49.5 | 1 | 1 | 10 | 49.76 | 1 | 0.64412 | 6.4412 | 8.2206 | 8.2206 | 0 | 12 | 1 | 1 | 8.2206 | 10 | 0 | 0
330.55 | 49.53 | 49.5 | 1 | 1 | 10 | 49.73 | 1 | 0.74412 | 7.4412 | 8.7206 | 8.7206 | 0 | 12 | 1 | 1 | 8.7206 | 10 | 0 | 0
330.6 | 49.55 | 49.5 | 1 | 1 | 10 | 49.71 | 1 | 0.84412 | 8.4412 | 9.2206 | 9.2206 | 0 | 12 | 1 | 1 | 9.2206 | 10 | 0 | 0
330.65 | 49.58 | 49.5 | 1 | 1 | 10 | 49.68 | 1 | 0.94412 | 9.4412 | 9.7206 | 9.7206 | 0 | 12 | 1 | 1 | 9.7206 | 10 | 0 | 0
330.7 | 49.6 | 49.5 | 1 | 1 | 10 | 49.65 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
330.75 | 49.63 | 49.5 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
330.8 | 49.65 | 49.5 | 1 | 1 | 10 | 49.65 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
330.85 | 49.68 | 49.5 | 1 | 1 | 10 | 49.68 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
330.9 | 49.71 | 49.5 | 1 | 1 | 10 | 49.71 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
330.95 | 49.73 | 49.5 | 1 | 1 | 10 | 49.73 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
331 | 49.76 | 49.5 | 1 | 1 | 10 | 49.76 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
331.05 | 49.78 | 49.5 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
331.1 | 49.81 | 49.53 | 1 | 1 | 10 | 49.81 | 0.905 | 0.905 | 9.05 | 9.525 | 9.525 | 0 | 12 | 1 | 1 | 9.525 | 10 | 0 | 0
331.15 | 49.83 | 49.55 | 1 | 1 | 10 | 49.83 | 0.715 | 0.715 | 7.15 | 8.575 | 8.575 | 0 | 12 | 1 | 1 | 8.575 | 10 | 0 | 0
331.2 | 49.86 | 49.58 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
331.25 | 49.88 | 49.6 | 1 | 1 | 10 | 49.88 | 0.24 | 0.24 | 2.4 | 6.2 | 6.2 | 0 | 12 | 1 | 1 | 6.2 | 10 | 0 | 0
331.3 | 49.91 | 49.63 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
331.35 | 49.94 | 49.65 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
331.4 | 49.96 | 49.68 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
331.45 | 49.99 | 49.71 | 1 | 1 | 10 | 49.99 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
331.5 | 50.01 | 49.73 | 1 | 1 | 10 | 50.01 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
331.55 | 50.04 | 49.76 | 1 | 1 | 10 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 4.9265 | 4.9265 | 0 | 12 | 1 | 1 | 4.9265 | 10 | 0 | 0
331.6 | 50.06 | 49.78 | 1 | 1 | 10 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 4.8676 | 4.8676 | 0 | 12 | 1 | 1 | 4.8676 | 10 | 0 | 0
331.65 | 50.09 | 49.81 | 0.905 | 0.905 | 9.05 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 4.3044 | 4.3044 | 0 | 12 | 1 | 1 | 4.3044 | 10 | 0 | 0
331.7 | 50.12 | 49.83 | 0.715 | 0.805 | 8.05 | 50.12 | -0.24 | -0.24 | -2.4 | 2.825 | 2.825 | 0 | 12 | 1 | 1 | 2.825 | 10 | 0 | 0
331.75 | 50.14 | 49.86 | 0.43 | 0.705 | 7.05 | 50.14 | -0.43 | -0.43 | -4.3 | 1.375 | 1.375 | 0 | 12 | 1 | 1 | 1.375 | 10 | 0 | 0
331.8 | 50.17 | 49.88 | 0.24 | 0.605 | 6.05 | 50.17 | -0.715 | -0.715 | -7.15 | -0.55 | -0.55 | 0 | 12 | 1 | 1 | -0.55 | 10 | 0 | 0
331.85 | 50.19 | 49.91 | 0.044118 | 0.505 | 5.05 | 50.19 | -0.905 | -0.905 | -9.05 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
331.9 | 50.22 | 49.94 | 0.026471 | 0.405 | 4.05 | 50.22 | -1 | -1 | -10 | -2.975 | -2.975 | 0 | 12 | 1 | 1 | -2.975 | 10 | 0 | 0
331.95 | 50.24 | 49.96 | 0.014706 | 0.305 | 3.05 | 50.24 | -1 | -1 | -10 | -3.475 | -3.475 | 0 | 12 | 1 | 1 | -3.475 | 10 | 0 | 0
332 | 50.27 | 49.99 | 0 | 0.205 | 2.05 | 50.27 | -1 | -1 | -10 | -3.975 | -3.975 | 0 | 12 | 1 | 1 | -3.975 | 10 | 0 | 0
332.05 | 50.29 | 50.01 | 0 | 0.105 | 1.05 | 50.29 | -1 | -1 | -10 | -4.475 | -4.475 | 0 | 12 | 1 | 1 | -4.475 | 10 | 0 | 0
332.1 | 50.32 | 50.04 | -0.014706 | 0.005 | 0.05 | 50.32 | -1 | -1 | -10 | -4.975 | -4.975 | 0 | 12 | 1 | 1 | -4.975 | 10 | 0 | 0
332.15 | 50.35 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.35 | -1 | -1 | -10 | -5.1324 | -5.1324 | 0 | 12 | 1 | 1 | -5.1324 | 10 | 0 | 0
332.2 | 50.37 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 50.37 | -1 | -1 | -10 | -5.2206 | -5.2206 | 0 | 12 | 1 | 1 | -5.2206 | 10 | 0 | 0
332.25 | 50.4 | 50.12 | -0.24 | -0.14412 | -1.4412 | 50.4 | -1 | -1 | -10 | -5.7206 | -5.7206 | 0 | 12 | 1 | 1 | -5.7206 | 10 | 0 | 0
332.3 | 50.42 | 50.14 | -0.43 | -0.24412 | -2.4412 | 50.42 | -1 | -1 | -10 | -6.2206 | -6.2206 | 0 | 12 | 1 | 1 | -6.2206 | 10 | 0 | 0
332.35 | 50.45 | 50.17 | -0.715 | -0.34412 | -3.4412 | 50.45 | -1 | -1 | -10 | -6.7206 | -6.7206 | 0 | 12 | 1 | 1 | -6.7206 | 10 | 0 | 0
332.4 | 50.47 | 50.19 | -0.905 | -0.44412 | -4.4412 | 50.47 | -1 | -1 | -10 | -7.2206 | -7.2206 | 0 | 12 | 1 | 1 | -7.2206 | 10 | 0 | 0
332.45 | 50.5 | 50.22 | -1 | -0.54412 | -5.4412 | 50.5 | -1 | -1 | -10 | -7.7206 | -7.7206 | 0 | 12 | 1 | 1 | -7.7206 | 10 | 0 | 0
332.5 | 50.5 | 50.24 | -1 | -0.64412 | -6.4412 | 50.5 | -1 | -1 | -10 | -8.2206 | -8.2206 | 0 | 12 | 1 | 1 | -8.2206 | 10 | 0 | 0
332.55 | 50.47 | 50.27 | -1 | -0.74412 | -7.4412 | 50.5 | -1 | -1 | -10 | -8.7206 | -8.7206 | 0 | 12 | 1 | 1 | -8.7206 | 10 | 0 | 0
332.6 | 50.45 | 50.29 | -1 | -0.84412 | -8.4412 | 50.5 | -1 | -1 | -10 | -9.2206 | -9.2206 | 0 | 12 | 1 | 1 | -9.2206 | 10 | 0 | 0
332.65 | 50.42 | 50.32 | -1 | -0.94412 | -9.4412 | 50.5 | -1 | -1 | -10 | -9.7206 | -9.7206 | 0 | 12 | 1 | 1 | -9.7206 | 10 | 0 | 0
332.7 | 50.39 | 50.35 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
332.75 | 50.37 | 50.37 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
332.8 | 50.34 | 50.34 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
332.85 | 50.32 | 50.32 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
332.9 | 50.29 | 50.29 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
332.95 | 50.26 | 50.26 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
333 | 50.24 | 50.24 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
333.05 | 50.21 | 50.21 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
333.1 | 50.18 | 50.18 | -0.81 | -0.81 | -8.1 | 50.47 | -1 | -1 | -10 | -9.05 | -9.05 | 0 | 12 | 1 | 1 | -9.05 | 10 | 0 | 0
333.15 | 50.16 | 50.16 | -0.62 | -0.62 | -6.2 | 50.45 | -1 | -1 | -10 | -8.1 | -8.1 | 0 | 12 | 1 | 1 | -8.1 | 10 | 0 | 0
333.2 | 50.13 | 50.13 | -0.335 | -0.335 | -3.35 | 50.42 | -1 | -1 | -10 | -6.675 | -6.675 | 0 | 12 | 1 | 1 | -6.675 | 10 | 0 | 0
333.25 | 50.11 | 50.11 | -0.145 | -0.145 | -1.45 | 50.39 | -1 | -1 | -10 | -5.725 | -5.725 | 0 | 12 | 1 | 1 | -5.725 | 10 | 0 | 0
333.3 | 50.08 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 50.37 | -1 | -1 | -10 | -5.1912 | -5.1912 | 0 | 12 | 1 | 1 | -5.1912 | 10 | 0 | 0
333.35 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.34 | -1 | -1 | -10 | -5.1029 | -5.1029 | 0 | 12 | 1 | 1 | -5.1029 | 10 | 0 | 0
333.4 | 50.03 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 50.32 | -1 | -1 | -10 | -5.0441 | -5.0441 | 0 | 12 | 1 | 1 | -5.0441 | 10 | 0 | 0
333.45 | 50 | 50 | 0 | 0 | 0 | 50.29 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
333.5 | 50 | 50 | 0 | 0 | 0 | 50.26 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
333.55 | 50 | 50 | 0 | 0 | 0 | 50.24 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
333.6 | 50 | 50 | 0 | 0 | 0 | 50.21 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
333.65 | 50 | 50 | 0 | 0 | 0 | 50.18 | -0.81 | -0.9 | -9 | -4.5 | -4.5 | 0 | 12 | 1 | 1 | -4.5 | 10 | 0 | 0
333.7 | 50 | 50 | 0 | 0 | 0 | 50.16 | -0.62 | -0.8 | -8 | -4 | -4 | 0 | 12 | 1 | 1 | -4 | 10 | 0 | 0
333.75 | 50 | 50 | 0 | 0 | 0 | 50.13 | -0.335 | -0.7 | -7 | -3.5 | -3.5 | 0 | 12 | 1 | 1 | -3.5 | 10 | 0 | 0
333.8 | 50.01 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.6 | -6 | -3 | -3 | 0 | 12 | 1 | 1 | -3 | 10 | 0 | 0
333.85 | 50.01 | 50 | 0 | 0 | 0 | 50.08 | -0.038235 | -0.5 | -5 | -2.5 | -2.5 | 0 | 12 | 1 | 1 | -2.5 | 10 | 0 | 0
333.9 | 49.99 | 49.99 | 0 | 0 | 0 | 50.05 | -0.020588 | -0.4 | -4 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
333.95 | 49.99 | 49.99 | 0 | 0 | 0 | 50.03 | -0.0088235 | -0.3 | -3 | -1.5 | -1.5 | 0 | 12 | 1 | 1 | -1.5 | 10 | 0 | 0
334 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | -0.2 | -2 | -0.83824 | -0.83824 | 0 | 12 | 1 | 1 | -0.83824 | 10 | 0 | 0
334.05 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | -0.1 | -1 | -0.33824 | -0.33824 | 0 | 12 | 1 | 1 | -0.33824 | 10 | 0 | 0
334.1 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
334.15 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
334.2 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
334.25 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
334.3 | 49.89 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
334.35 | 49.89 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
334.4 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50.01 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
334.45 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
334.5 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
334.55 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 2.7868 | 2.7868 | 0 | 12 | 1 | 1 | 2.7868 | 10 | 0 | 0
334.6 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 2.7868 | 2.7868 | 0 | 12 | 1 | 1 | 2.7868 | 10 | 0 | 0
334.65 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 2.8456 | 2.8456 | 0 | 12 | 1 | 1 | 2.8456 | 10 | 0 | 0
334.7 | 49.94 | 49.85 | 0.525 | 0.525 | 5.25 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 2.7574 | 2.7574 | 0 | 12 | 1 | 1 | 2.7574 | 10 | 0 | 0
334.75 | 49.94 | 49.85 | 0.525 | 0.525 | 5.25 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 2.7574 | 2.7574 | 0 | 12 | 1 | 1 | 2.7574 | 10 | 0 | 0
334.8 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
334.85 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
334.9 | 49.93 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
334.95 | 49.93 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
335 | 49.96 | 49.85 | 0.525 | 0.525 | 5.25 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 2.6985 | 2.6985 | 0 | 12 | 1 | 1 | 2.6985 | 10 | 0 | 0
335.05 | 49.96 | 49.85 | 0.525 | 0.525 | 5.25 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 2.6985 | 2.6985 | 0 | 12 | 1 | 1 | 2.6985 | 10 | 0 | 0
335.1 | 49.99 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
335.15 | 49.99 | 49.91 | 0.044118 | 0.425 | 4.25 | 49.99 | 0 | 0 | 0 | 2.125 | 2.125 | 0 | 12 | 1 | 1 | 2.125 | 10 | 0 | 0
335.2 | 49.99 | 49.91 | 0.044118 | 0.325 | 3.25 | 49.99 | 0 | 0 | 0 | 1.625 | 1.625 | 0 | 12 | 1 | 1 | 1.625 | 10 | 0 | 0
335.25 | 49.99 | 49.93 | 0.032353 | 0.225 | 2.25 | 49.99 | 0 | 0 | 0 | 1.125 | 1.125 | 0 | 12 | 1 | 1 | 1.125 | 10 | 0 | 0
335.3 | 49.96 | 49.93 | 0.032353 | 0.125 | 1.25 | 49.99 | 0 | 0 | 0 | 0.625 | 0.625 | 0 | 12 | 1 | 1 | 0.625 | 10 | 0 | 0
335.35 | 49.96 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 49.99 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
335.4 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
335.45 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
335.5 | 50.05 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.058824 | 0.058824 | 0 | 12 | 1 | 1 | 0.058824 | 10 | 0 | 0
335.55 | 50.05 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
335.6 | 49.97 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
335.65 | 49.97 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
335.7 | 49.92 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
335.75 | 49.92 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
335.8 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
335.85 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
335.9 | 49.94 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
335.95 | 49.94 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
336 | 50.01 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
336.05 | 50.01 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
336.1 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
336.15 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
336.2 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
336.25 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
336.3 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
336.35 | 49.95 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
336.4 | 49.97 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
336.45 | 49.97 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
336.5 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
336.55 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
336.6 | 49.87 | 49.87 | 0.335 | 0.335 | 3.35 | 50.01 | 0 | 0 | 0 | 1.675 | 1.675 | 0 | 12 | 1 | 1 | 1.675 | 10 | 0 | 0
336.65 | 49.87 | 49.87 | 0.335 | 0.335 | 3.35 | 49.99 | 0 | 0 | 0 | 1.675 | 1.675 | 0 | 12 | 1 | 1 | 1.675 | 10 | 0 | 0
336.7 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
336.75 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 2.6691 | 2.6691 | 0 | 12 | 1 | 1 | 2.6691 | 10 | 0 | 0
336.8 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
336.85 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
336.9 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
336.95 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
337 | 49.84 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
337.05 | 49.84 | 49.79 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
337.1 | 49.89 | 49.79 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
337.15 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.12647 | 1.2647 | 5.6324 | 5.6324 | 0 | 12 | 1 | 1 | 5.6324 | 10 | 0 | 0
337.2 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.145 | 1.45 | 5.725 | 5.725 | 0 | 12 | 1 | 1 | 5.725 | 10 | 0 | 0
337.25 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.145 | 1.45 | 5.725 | 5.725 | 0 | 12 | 1 | 1 | 5.725 | 10 | 0 | 0
337.3 | 49.96 | 49.79 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
337.35 | 49.96 | 49.79 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
337.4 | 50.02 | 49.79 | 1 | 1 | 10 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 4.9853 | 4.9853 | 0 | 12 | 1 | 1 | 4.9853 | 10 | 0 | 0
337.45 | 50.02 | 49.79 | 1 | 1 | 10 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 4.9853 | 4.9853 | 0 | 12 | 1 | 1 | 4.9853 | 10 | 0 | 0
337.5 | 50.03 | 49.79 | 1 | 1 | 10 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.9559 | 4.9559 | 0 | 12 | 1 | 1 | 4.9559 | 10 | 0 | 0
337.55 | 50.03 | 49.84 | 0.62 | 0.9 | 9 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.4559 | 4.4559 | 0 | 12 | 1 | 1 | 4.4559 | 10 | 0 | 0
337.6 | 50.02 | 49.84 | 0.62 | 0.8 | 8 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 3.9559 | 3.9559 | 0 | 12 | 1 | 1 | 3.9559 | 10 | 0 | 0
337.65 | 50.02 | 49.89 | 0.145 | 0.7 | 7 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 3.4559 | 3.4559 | 0 | 12 | 1 | 1 | 3.4559 | 10 | 0 | 0
337.7 | 50.08 | 49.89 | 0.145 | 0.6 | 6 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 2.8088 | 2.8088 | 0 | 12 | 1 | 1 | 2.8088 | 10 | 0 | 0
337.75 | 50.08 | 49.89 | 0.145 | 0.5 | 5 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 2.3088 | 2.3088 | 0 | 12 | 1 | 1 | 2.3088 | 10 | 0 | 0
337.8 | 50.01 | 49.89 | 0.145 | 0.4 | 4 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 1.8088 | 1.8088 | 0 | 12 | 1 | 1 | 1.8088 | 10 | 0 | 0
337.85 | 50.01 | 49.96 | 0.014706 | 0.3 | 3 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 1.3088 | 1.3088 | 0 | 12 | 1 | 1 | 1.3088 | 10 | 0 | 0
337.9 | 49.94 | 49.94 | 0.026471 | 0.2 | 2 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.80882 | 0.80882 | 0 | 12 | 1 | 1 | 0.80882 | 10 | 0 | 0
337.95 | 49.94 | 49.94 | 0.026471 | 0.1 | 1 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.30882 | 0.30882 | 0 | 12 | 1 | 1 | 0.30882 | 10 | 0 | 0
338 | 50 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
338.05 | 50 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
338.1 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
338.15 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
338.2 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
338.25 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
338.3 | 49.92 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
338.35 | 49.92 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
338.4 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50.01 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
338.45 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
338.5 | 49.92 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
338.55 | 49.92 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
338.6 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
338.65 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
338.7 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
338.75 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
338.8 | 49.87 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
338.85 | 49.87 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
338.9 | 49.8 | 49.8 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
338.95 | 49.8 | 49.8 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
339 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
339.05 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
339.1 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
339.15 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
339.2 | 49.72 | 49.72 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
339.25 | 49.72 | 49.72 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
339.3 | 49.67 | 49.67 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
339.35 | 49.67 | 49.67 | 1 | 1 | 10 | 49.87 | 0.335 | 0.14412 | 1.4412 | 5.7206 | 5.7206 | 0 | 12 | 1 | 1 | 5.7206 | 10 | 0 | 0
339.4 | 49.65 | 49.65 | 1 | 1 | 10 | 49.87 | 0.335 | 0.24412 | 2.4412 | 6.2206 | 6.2206 | 0 | 12 | 1 | 1 | 6.2206 | 10 | 0 | 0
339.45 | 49.65 | 49.65 | 1 | 1 | 10 | 49.8 | 1 | 0.34412 | 3.4412 | 6.7206 | 6.7206 | 0 | 12 | 1 | 1 | 6.7206 | 10 | 0 | 0
339.5 | 49.59 | 49.59 | 1 | 1 | 10 | 49.8 | 1 | 0.44412 | 4.4412 | 7.2206 | 7.2206 | 0 | 12 | 1 | 1 | 7.2206 | 10 | 0 | 0
339.55 | 49.59 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.54412 | 5.4412 | 7.7206 | 7.7206 | 0 | 12 | 1 | 1 | 7.7206 | 10 | 0 | 0
339.6 | 49.66 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.64412 | 6.4412 | 8.2206 | 8.2206 | 0 | 12 | 1 | 1 | 8.2206 | 10 | 0 | 0
339.65 | 49.66 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.74412 | 7.4412 | 8.7206 | 8.7206 | 0 | 12 | 1 | 1 | 8.7206 | 10 | 0 | 0
339.7 | 49.63 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.84412 | 8.4412 | 9.2206 | 9.2206 | 0 | 12 | 1 | 1 | 9.2206 | 10 | 0 | 0
339.75 | 49.63 | 49.59 | 1 | 1 | 10 | 49.72 | 1 | 0.94412 | 9.4412 | 9.7206 | 9.7206 | 0 | 12 | 1 | 1 | 9.7206 | 10 | 0 | 0
339.8 | 49.61 | 49.59 | 1 | 1 | 10 | 49.72 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
339.85 | 49.61 | 49.59 | 1 | 1 | 10 | 49.67 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
339.9 | 49.54 | 49.54 | 1 | 1 | 10 | 49.67 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
339.95 | 49.54 | 49.54 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
340 | 49.46 | 49.46 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
340.05 | 49.46 | 49.46 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
340.1 | 49.45 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
340.15 | 49.45 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
340.2 | 49.51 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
340.25 | 49.51 | 49.45 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
340.3 | 49.5 | 49.45 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
340.35 | 49.5 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
340.4 | 49.54 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
340.45 | 49.54 | 49.45 | 1 | 1 | 10 | 49.54 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
340.5 | 49.59 | 49.45 | 1 | 1 | 10 | 49.59 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
340.55 | 49.59 | 49.45 | 1 | 1 | 10 | 49.59 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
340.6 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
340.65 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
340.7 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
340.75 | 49.61 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
340.8 | 49.53 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
340.85 | 49.53 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
340.9 | 49.54 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
340.95 | 49.54 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
341 | 49.61 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
341.05 | 49.61 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
341.1 | 49.66 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
341.15 | 49.66 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
341.2 | 49.64 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
341.25 | 49.64 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
341.3 | 49.69 | 49.53 | 1 | 1 | 10 | 49.69 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
341.35 | 49.69 | 49.53 | 1 | 1 | 10 | 49.69 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
341.4 | 49.74 | 49.53 | 1 | 1 | 10 | 49.74 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
341.45 | 49.74 | 49.54 | 1 | 1 | 10 | 49.74 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
341.5 | 49.78 | 49.54 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
341.55 | 49.78 | 49.61 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
341.6 | 49.82 | 49.61 | 1 | 1 | 10 | 49.82 | 0.81 | 0.81 | 8.1 | 9.05 | 9.05 | 0 | 12 | 1 | 1 | 9.05 | 10 | 0 | 0
341.65 | 49.82 | 49.64 | 1 | 1 | 10 | 49.82 | 0.81 | 0.81 | 8.1 | 9.05 | 9.05 | 0 | 12 | 1 | 1 | 9.05 | 10 | 0 | 0
341.7 | 49.86 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
341.75 | 49.86 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
341.8 | 49.84 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
341.85 | 49.84 | 49.69 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
341.9 | 49.91 | 49.69 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
341.95 | 49.91 | 49.74 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
342 | 49.97 | 49.74 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
342.05 | 49.97 | 49.78 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
342.1 | 50.03 | 49.78 | 1 | 1 | 10 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.9559 | 4.9559 | 0 | 12 | 1 | 1 | 4.9559 | 10 | 0 | 0
342.15 | 50.03 | 49.82 | 0.81 | 0.9 | 9 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.4559 | 4.4559 | 0 | 12 | 1 | 1 | 4.4559 | 10 | 0 | 0
342.2 | 50.05 | 49.82 | 0.81 | 0.81 | 8.1 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 3.9471 | 3.9471 | 0 | 12 | 1 | 1 | 3.9471 | 10 | 0 | 0
342.25 | 50.05 | 49.84 | 0.62 | 0.71 | 7.1 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 3.4471 | 3.4471 | 0 | 12 | 1 | 1 | 3.4471 | 10 | 0 | 0
342.3 | 50.01 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
342.35 | 50.01 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
342.4 | 49.95 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
342.45 | 49.95 | 49.91 | 0.044118 | 0.52 | 5.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.4971 | 2.4971 | 0 | 12 | 1 | 1 | 2.4971 | 10 | 0 | 0
342.5 | 49.99 | 49.91 | 0.044118 | 0.42 | 4.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 1.9971 | 1.9971 | 0 | 12 | 1 | 1 | 1.9971 | 10 | 0 | 0
342.55 | 49.99 | 49.95 | 0.020588 | 0.32 | 3.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 1.4971 | 1.4971 | 0 | 12 | 1 | 1 | 1.4971 | 10 | 0 | 0
342.6 | 49.92 | 49.92 | 0.038235 | 0.22 | 2.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.99706 | 0.99706 | 0 | 12 | 1 | 1 | 0.99706 | 10 | 0 | 0
342.65 | 49.92 | 49.92 | 0.038235 | 0.12 | 1.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.49706 | 0.49706 | 0 | 12 | 1 | 1 | 0.49706 | 10 | 0 | 0
342.7 | 49.97 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
342.75 | 49.97 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
342.8 | 50.02 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
342.85 | 50.02 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.17647 | 0.17647 | 0 | 12 | 1 | 1 | 0.17647 | 10 | 0 | 0
342.9 | 50.07 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
342.95 | 50.07 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
343 | 50.06 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
343.05 | 50.06 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
343.1 | 50.13 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
343.15 | 50.13 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
343.2 | 50.09 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
343.25 | 50.09 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6309 | -1.6309 | 0 | 12 | 1 | 1 | -1.6309 | 10 | 0 | 0
343.3 | 50.07 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6309 | -1.6309 | 0 | 12 | 1 | 1 | -1.6309 | 10 | 0 | 0
343.35 | 50.07 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6897 | -1.6897 | 0 | 12 | 1 | 1 | -1.6897 | 10 | 0 | 0
343.4 | 50.07 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6897 | -1.6897 | 0 | 12 | 1 | 1 | -1.6897 | 10 | 0 | 0
343.45 | 50.07 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.13 | -0.335 | -0.335 | -3.35 | -1.8074 | -1.8074 | 0 | 12 | 1 | 1 | -1.8074 | 10 | 0 | 0
343.5 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.13 | -0.335 | -0.335 | -3.35 | -1.7779 | -1.7779 | 0 | 12 | 1 | 1 | -1.7779 | 10 | 0 | 0
343.55 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.13 | -0.335 | -0.335 | -3.35 | -1.7779 | -1.7779 | 0 | 12 | 1 | 1 | -1.7779 | 10 | 0 | 0
343.6 | 50.01 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
343.65 | 50.01 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
343.7 | 50.07 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
343.75 | 50.07 | 50.01 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.235 | -2.35 | -1.175 | -1.175 | 0 | 12 | 1 | 1 | -1.175 | 10 | 0 | 0
343.8 | 50.05 | 50.01 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.135 | -1.35 | -0.675 | -0.675 | 0 | 12 | 1 | 1 | -0.675 | 10 | 0 | 0
343.85 | 50.05 | 50.01 | 0 | 0 | 0 | 50.07 | -0.032353 | -0.035 | -0.35 | -0.175 | -0.175 | 0 | 12 | 1 | 1 | -0.175 | 10 | 0 | 0
343.9 | 50.1 | 50.01 | 0 | 0 | 0 | 50.1 | -0.05 | -0.05 | -0.5 | -0.25 | -0.25 | 0 | 12 | 1 | 1 | -0.25 | 10 | 0 | 0
343.95 | 50.1 | 50.01 | 0 | 0 | 0 | 50.1 | -0.05 | -0.05 | -0.5 | -0.25 | -0.25 | 0 | 12 | 1 | 1 | -0.25 | 10 | 0 | 0
344 | 50.11 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
344.05 | 50.11 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
344.1 | 50.06 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
344.15 | 50.06 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
344.2 | 50.04 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
344.25 | 50.04 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
344.3 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
344.35 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
344.4 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
344.45 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
344.5 | 50.11 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
344.55 | 50.11 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
344.6 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
344.65 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
344.7 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
344.75 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
344.8 | 50.02 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.11 | -0.145 | -0.145 | -1.45 | -0.73971 | -0.73971 | 0 | 12 | 1 | 1 | -0.73971 | 10 | 0 | 0
344.85 | 50.02 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.11 | -0.145 | -0.145 | -1.45 | -0.73971 | -0.73971 | 0 | 12 | 1 | 1 | -0.73971 | 10 | 0 | 0
344.9 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
344.95 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
345 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
345.05 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
345.1 | 50.01 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
345.15 | 50.01 | 50 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.045 | -0.45 | -0.225 | -0.225 | 0 | 12 | 1 | 1 | -0.225 | 10 | 0 | 0
345.2 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
345.25 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
345.3 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
345.35 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
345.4 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.14706 | 0.14706 | 0 | 12 | 1 | 1 | 0.14706 | 10 | 0 | 0
345.45 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
345.5 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
345.55 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
345.6 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
345.65 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
345.7 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
345.75 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
345.8 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
345.85 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
345.9 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
345.95 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
346 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
346.05 | 50 | 50 | 0 | 0 | 0 | 50.01 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
346.1 | 49.5 | 49.5 | 1 | 1 | 10 | 50.01 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
346.15 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
346.2 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
346.25 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
346.3 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
346.35 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
346.4 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
346.45 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
346.5 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
346.55 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
346.6 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
346.65 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.1 | 1 | 5.5 | 5.5 | 0 | 12 | 1 | 1 | 5.5 | 10 | 0 | 0
346.7 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.2 | 2 | 6 | 6 | 0 | 12 | 1 | 1 | 6 | 10 | 0 | 0
346.75 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.3 | 3 | 6.5 | 6.5 | 0 | 12 | 1 | 1 | 6.5 | 10 | 0 | 0
346.8 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.4 | 4 | 7 | 7 | 0 | 12 | 1 | 1 | 7 | 10 | 0 | 0
346.85 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.5 | 5 | 7.5 | 7.5 | 0 | 12 | 1 | 1 | 7.5 | 10 | 0 | 0
346.9 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.6 | 6 | 8 | 8 | 0 | 12 | 1 | 1 | 8 | 10 | 0 | 0
346.95 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.7 | 7 | 8.5 | 8.5 | 0 | 12 | 1 | 1 | 8.5 | 10 | 0 | 0
347 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.8 | 8 | 9 | 9 | 0 | 12 | 1 | 1 | 9 | 10 | 0 | 0
347.05 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.9 | 9 | 9.5 | 9.5 | 0 | 12 | 1 | 1 | 9.5 | 10 | 0 | 0
347.1 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
347.15 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
347.2 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
347.25 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
347.3 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
347.35 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
347.4 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
347.45 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
347.5 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
347.55 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
347.6 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
347.65 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
347.7 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
347.75 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
347.8 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
347.85 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
347.9 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
347.95 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
348 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
348.05 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
348.1 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
348.15 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
348.2 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
348.25 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
348.3 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
348.35 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
348.4 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
348.45 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
348.5 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
348.55 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
348.6 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
348.65 | 50.5 | 50.5 | -1 | 0.9 | 9 | 50.5 | -1 | -1 | -10 | -0.5 | -0.5 | 0 | 12 | 1 | 1 | -0.5 | 10 | 0 | 0
348.7 | 50.5 | 50.5 | -1 | 0.8 | 8 | 50.5 | -1 | -1 | -10 | -1 | -1 | 0 | 12 | 1 | 1 | -1 | 10 | 0 | 0
348.75 | 50.5 | 50.5 | -1 | 0.7 | 7 | 50.5 | -1 | -1 | -10 | -1.5 | -1.5 | 0 | 12 | 1 | 1 | -1.5 | 10 | 0 | 0
348.8 | 50.5 | 50.5 | -1 | 0.6 | 6 | 50.5 | -1 | -1 | -10 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
348.85 | 50.5 | 50.5 | -1 | 0.5 | 5 | 50.5 | -1 | -1 | -10 | -2.5 | -2.5 | 0 | 12 | 1 | 1 | -2.5 | 10 | 0 | 0
348.9 | 50.5 | 50.5 | -1 | 0.4 | 4 | 50.5 | -1 | -1 | -10 | -3 | -3 | 0 | 12 | 1 | 1 | -3 | 10 | 0 | 0
348.95 | 50.5 | 50.5 | -1 | 0.3 | 3 | 50.5 | -1 | -1 | -10 | -3.5 | -3.5 | 0 | 12 | 1 | 1 | -3.5 | 10 | 0 | 0
349 | 50.5 | 50.5 | -1 | 0.2 | 2 | 50.5 | -1 | -1 | -10 | -4 | -4 | 0 | 12 | 1 | 1 | -4 | 10 | 0 | 0
349.05 | 50.5 | 50.5 | -1 | 0.1 | 1 | 50.5 | -1 | -1 | -10 | -4.5 | -4.5 | 0 | 12 | 1 | 1 | -4.5 | 10 | 0 | 0
349.1 | 50.5 | 50.5 | -1 | 0 | 0 | 50.5 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
349.15 | 50.5 | 50.5 | -1 | -0.1 | -1 | 50.5 | -1 | -1 | -10 | -5.5 | -5.5 | 0 | 12 | 1 | 1 | -5.5 | 10 | 0 | 0
349.2 | 50.5 | 50.5 | -1 | -0.2 | -2 | 50.5 | -1 | -1 | -10 | -6 | -6 | 0 | 12 | 1 | 1 | -6 | 10 | 0 | 0
349.25 | 50.5 | 50.5 | -1 | -0.3 | -3 | 50.5 | -1 | -1 | -10 | -6.5 | -6.5 | 0 | 12 | 1 | 1 | -6.5 | 10 | 0 | 0
349.3 | 50.5 | 50.5 | -1 | -0.4 | -4 | 50.5 | -1 | -1 | -10 | -7 | -7 | 0 | 12 | 1 | 1 | -7 | 10 | 0 | 0
349.35 | 50.5 | 50.5 | -1 | -0.5 | -5 | 50.5 | -1 | -1 | -10 | -7.5 | -7.5 | 0 | 12 | 1 | 1 | -7.5 | 10 | 0 | 0
349.4 | 50.5 | 50.5 | -1 | -0.6 | -6 | 50.5 | -1 | -1 | -10 | -8 | -8 | 0 | 12 | 1 | 1 | -8 | 10 | 0 | 0
349.45 | 50.5 | 50.5 | -1 | -0.7 | -7 | 50.5 | -1 | -1 | -10 | -8.5 | -8.5 | 0 | 12 | 1 | 1 | -8.5 | 10 | 0 | 0
349.5 | 50.5 | 50.5 | -1 | -0.8 | -8 | 50.5 | -1 | -1 | -10 | -9 | -9 | 0 | 12 | 1 | 1 | -9 | 10 | 0 | 0
349.55 | 50.5 | 50.5 | -1 | -0.9 | -9 | 50.5 | -1 | -1 | -10 | -9.5 | -9.5 | 0 | 12 | 1 | 1 | -9.5 | 10 | 0 | 0
349.6 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
349.65 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
349.7 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
349.75 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
349.8 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
349.85 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
349.9 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
349.95 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
350 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
350.05 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
350.1 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
350.15 | 50.47 | 50.47 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
350.2 | 50.45 | 50.45 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
350.25 | 50.42 | 50.42 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
350.3 | 50.4 | 50.4 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
350.35 | 50.37 | 50.37 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
350.4 | 50.35 | 50.35 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
350.45 | 50.32 | 50.32 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
350.5 | 50.29 | 50.29 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
350.55 | 50.27 | 50.27 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
350.6 | 50.24 | 50.24 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
350.65 | 50.22 | 50.22 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
350.7 | 50.19 | 50.19 | -0.905 | -0.905 | -9.05 | 50.47 | -1 | -1 | -10 | -9.525 | -9.525 | 0 | 12 | 1 | 1 | -9.525 | 10 | 0 | 0
350.75 | 50.17 | 50.17 | -0.715 | -0.715 | -7.15 | 50.45 | -1 | -1 | -10 | -8.575 | -8.575 | 0 | 12 | 1 | 1 | -8.575 | 10 | 0 | 0
350.8 | 50.14 | 50.14 | -0.43 | -0.43 | -4.3 | 50.42 | -1 | -1 | -10 | -7.15 | -7.15 | 0 | 12 | 1 | 1 | -7.15 | 10 | 0 | 0
350.85 | 50.12 | 50.12 | -0.24 | -0.24 | -2.4 | 50.4 | -1 | -1 | -10 | -6.2 | -6.2 | 0 | 12 | 1 | 1 | -6.2 | 10 | 0 | 0
350.9 | 50.09 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 50.37 | -1 | -1 | -10 | -5.2206 | -5.2206 | 0 | 12 | 1 | 1 | -5.2206 | 10 | 0 | 0
350.95 | 50.06 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.35 | -1 | -1 | -10 | -5.1324 | -5.1324 | 0 | 12 | 1 | 1 | -5.1324 | 10 | 0 | 0
351 | 50.04 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.32 | -1 | -1 | -10 | -5.0735 | -5.0735 | 0 | 12 | 1 | 1 | -5.0735 | 10 | 0 | 0
351.05 | 50.01 | 50.01 | 0 | 0 | 0 | 50.29 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
351.1 | 49.99 | 49.99 | 0 | 0 | 0 | 50.27 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
351.15 | 49.96 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.24 | -1 | -1 | -10 | -4.9265 | -4.9265 | 0 | 12 | 1 | 1 | -4.9265 | 10 | 0 | 0
351.2 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.22 | -1 | -1 | -10 | -4.8676 | -4.8676 | 0 | 12 | 1 | 1 | -4.8676 | 10 | 0 | 0
351.25 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.19 | -0.905 | -0.905 | -9.05 | -4.3044 | -4.3044 | 0 | 12 | 1 | 1 | -4.3044 | 10 | 0 | 0
351.3 | 49.88 | 49.88 | 0.24 | 0.24 | 2.4 | 50.17 | -0.715 | -0.805 | -8.05 | -2.825 | -2.825 | 0 | 12 | 1 | 1 | -2.825 | 10 | 0 | 0
351.35 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.14 | -0.43 | -0.705 | -7.05 | -1.375 | -1.375 | 0 | 12 | 1 | 1 | -1.375 | 10 | 0 | 0
351.4 | 49.83 | 49.83 | 0.715 | 0.715 | 7.15 | 50.12 | -0.24 | -0.605 | -6.05 | 0.55 | 0.55 | 0 | 12 | 1 | 1 | 0.55 | 10 | 0 | 0
351.45 | 49.81 | 49.81 | 0.905 | 0.905 | 9.05 | 50.09 | -0.044118 | -0.505 | -5.05 | 2 | 2 | 0 | 12 | 1 | 1 | 2 | 10 | 0 | 0
351.5 | 49.78 | 49.78 | 1 | 1 | 10 | 50.06 | -0.026471 | -0.405 | -4.05 | 2.975 | 2.975 | 0 | 12 | 1 | 1 | 2.975 | 10 | 0 | 0
351.55 | 49.76 | 49.76 | 1 | 1 | 10 | 50.04 | -0.014706 | -0.305 | -3.05 | 3.475 | 3.475 | 0 | 12 | 1 | 1 | 3.475 | 10 | 0 | 0
351.6 | 49.73 | 49.73 | 1 | 1 | 10 | 50.01 | 0 | -0.205 | -2.05 | 3.975 | 3.975 | 0 | 12 | 1 | 1 | 3.975 | 10 | 0 | 0
351.65 | 49.71 | 49.71 | 1 | 1 | 10 | 49.99 | 0 | -0.105 | -1.05 | 4.475 | 4.475 | 0 | 12 | 1 | 1 | 4.475 | 10 | 0 | 0
351.7 | 49.68 | 49.68 | 1 | 1 | 10 | 49.96 | 0.014706 | -0.005 | -0.05 | 4.975 | 4.975 | 0 | 12 | 1 | 1 | 4.975 | 10 | 0 | 0
351.75 | 49.65 | 49.65 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
351.8 | 49.63 | 49.63 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
351.85 | 49.6 | 49.6 | 1 | 1 | 10 | 49.88 | 0.24 | 0.14412 | 1.4412 | 5.7206 | 5.7206 | 0 | 12 | 1 | 1 | 5.7206 | 10 | 0 | 0
351.9 | 49.58 | 49.58 | 1 | 1 | 10 | 49.86 | 0.43 | 0.24412 | 2.4412 | 6.2206 | 6.2206 | 0 | 12 | 1 | 1 | 6.2206 | 10 | 0 | 0
351.95 | 49.55 | 49.55 | 1 | 1 | 10 | 49.83 | 0.715 | 0.34412 | 3.4412 | 6.7206 | 6.7206 | 0 | 12 | 1 | 1 | 6.7206 | 10 | 0 | 0
352 | 49.53 | 49.53 | 1 | 1 | 10 | 49.81 | 0.905 | 0.44412 | 4.4412 | 7.2206 | 7.2206 | 0 | 12 | 1 | 1 | 7.2206 | 10 | 0 | 0
352.05 | 49.5 | 49.5 | 1 | 1 | 10 | 49.78 | 1 | 0.54412 | 5.4412 | 7.7206 | 7.7206 | 0 | 12 | 1 | 1 | 7.7206 | 10 | 0 | 0
352.1 | 49.5 | 49.5 | 1 | 1 | 10 | 49.76 | 1 | 0.64412 | 6.4412 | 8.2206 | 8.2206 | 0 | 12 | 1 | 1 | 8.2206 | 10 | 0 | 0
352.15 | 49.53 | 49.5 | 1 | 1 | 10 | 49.73 | 1 | 0.74412 | 7.4412 | 8.7206 | 8.7206 | 0 | 12 | 1 | 1 | 8.7206 | 10 | 0 | 0
352.2 | 49.55 | 49.5 | 1 | 1 | 10 | 49.71 | 1 | 0.84412 | 8.4412 | 9.2206 | 9.2206 | 0 | 12 | 1 | 1 | 9.2206 | 10 | 0 | 0
352.25 | 49.58 | 49.5 | 1 | 1 | 10 | 49.68 | 1 | 0.94412 | 9.4412 | 9.7206 | 9.7206 | 0 | 12 | 1 | 1 | 9.7206 | 10 | 0 | 0
352.3 | 49.6 | 49.5 | 1 | 1 | 10 | 49.65 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
352.35 | 49.63 | 49.5 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
352.4 | 49.65 | 49.5 | 1 | 1 | 10 | 49.65 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
352.45 | 49.68 | 49.5 | 1 | 1 | 10 | 49.68 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
352.5 | 49.71 | 49.5 | 1 | 1 | 10 | 49.71 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
352.55 | 49.73 | 49.5 | 1 | 1 | 10 | 49.73 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
352.6 | 49.76 | 49.5 | 1 | 1 | 10 | 49.76 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
352.65 | 49.78 | 49.5 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
352.7 | 49.81 | 49.53 | 1 | 1 | 10 | 49.81 | 0.905 | 0.905 | 9.05 | 9.525 | 9.525 | 0 | 12 | 1 | 1 | 9.525 | 10 | 0 | 0
352.75 | 49.83 | 49.55 | 1 | 1 | 10 | 49.83 | 0.715 | 0.715 | 7.15 | 8.575 | 8.575 | 0 | 12 | 1 | 1 | 8.575 | 10 | 0 | 0
352.8 | 49.86 | 49.58 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
352.85 | 49.88 | 49.6 | 1 | 1 | 10 | 49.88 | 0.24 | 0.24 | 2.4 | 6.2 | 6.2 | 0 | 12 | 1 | 1 | 6.2 | 10 | 0 | 0
352.9 | 49.91 | 49.63 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
352.95 | 49.94 | 49.65 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
353 | 49.96 | 49.68 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
353.05 | 49.99 | 49.71 | 1 | 1 | 10 | 49.99 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
353.1 | 50.01 | 49.73 | 1 | 1 | 10 | 50.01 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
353.15 | 50.04 | 49.76 | 1 | 1 | 10 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 4.9265 | 4.9265 | 0 | 12 | 1 | 1 | 4.9265 | 10 | 0 | 0
353.2 | 50.06 | 49.78 | 1 | 1 | 10 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 4.8676 | 4.8676 | 0 | 12 | 1 | 1 | 4.8676 | 10 | 0 | 0
353.25 | 50.09 | 49.81 | 0.905 | 0.905 | 9.05 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 4.3044 | 4.3044 | 0 | 12 | 1 | 1 | 4.3044 | 10 | 0 | 0
353.3 | 50.12 | 49.83 | 0.715 | 0.805 | 8.05 | 50.12 | -0.24 | -0.24 | -2.4 | 2.825 | 2.825 | 0 | 12 | 1 | 1 | 2.825 | 10 | 0 | 0
353.35 | 50.14 | 49.86 | 0.43 | 0.705 | 7.05 | 50.14 | -0.43 | -0.43 | -4.3 | 1.375 | 1.375 | 0 | 12 | 1 | 1 | 1.375 | 10 | 0 | 0
353.4 | 50.17 | 49.88 | 0.24 | 0.605 | 6.05 | 50.17 | -0.715 | -0.715 | -7.15 | -0.55 | -0.55 | 0 | 12 | 1 | 1 | -0.55 | 10 | 0 | 0
353.45 | 50.19 | 49.91 | 0.044118 | 0.505 | 5.05 | 50.19 | -0.905 | -0.905 | -9.05 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
353.5 | 50.22 | 49.94 | 0.026471 | 0.405 | 4.05 | 50.22 | -1 | -1 | -10 | -2.975 | -2.975 | 0 | 12 | 1 | 1 | -2.975 | 10 | 0 | 0
353.55 | 50.24 | 49.96 | 0.014706 | 0.305 | 3.05 | 50.24 | -1 | -1 | -10 | -3.475 | -3.475 | 0 | 12 | 1 | 1 | -3.475 | 10 | 0 | 0
353.6 | 50.27 | 49.99 | 0 | 0.205 | 2.05 | 50.27 | -1 | -1 | -10 | -3.975 | -3.975 | 0 | 12 | 1 | 1 | -3.975 | 10 | 0 | 0
353.65 | 50.29 | 50.01 | 0 | 0.105 | 1.05 | 50.29 | -1 | -1 | -10 | -4.475 | -4.475 | 0 | 12 | 1 | 1 | -4.475 | 10 | 0 | 0
353.7 | 50.32 | 50.04 | -0.014706 | 0.005 | 0.05 | 50.32 | -1 | -1 | -10 | -4.975 | -4.975 | 0 | 12 | 1 | 1 | -4.975 | 10 | 0 | 0
353.75 | 50.35 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.35 | -1 | -1 | -10 | -5.1324 | -5.1324 | 0 | 12 | 1 | 1 | -5.1324 | 10 | 0 | 0
353.8 | 50.37 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 50.37 | -1 | -1 | -10 | -5.2206 | -5.2206 | 0 | 12 | 1 | 1 | -5.2206 | 10 | 0 | 0
353.85 | 50.4 | 50.12 | -0.24 | -0.14412 | -1.4412 | 50.4 | -1 | -1 | -10 | -5.7206 | -5.7206 | 0 | 12 | 1 | 1 | -5.7206 | 10 | 0 | 0
353.9 | 50.42 | 50.14 | -0.43 | -0.24412 | -2.4412 | 50.42 | -1 | -1 | -10 | -6.2206 | -6.2206 | 0 | 12 | 1 | 1 | -6.2206 | 10 | 0 | 0
353.95 | 50.45 | 50.17 | -0.715 | -0.34412 | -3.4412 | 50.45 | -1 | -1 | -10 | -6.7206 | -6.7206 | 0 | 12 | 1 | 1 | -6.7206 | 10 | 0 | 0
354 | 50.47 | 50.19 | -0.905 | -0.44412 | -4.4412 | 50.47 | -1 | -1 | -10 | -7.2206 | -7.2206 | 0 | 12 | 1 | 1 | -7.2206 | 10 | 0 | 0
354.05 | 50.5 | 50.22 | -1 | -0.54412 | -5.4412 | 50.5 | -1 | -1 | -10 | -7.7206 | -7.7206 | 0 | 12 | 1 | 1 | -7.7206 | 10 | 0 | 0
354.1 | 50.5 | 50.24 | -1 | -0.64412 | -6.4412 | 50.5 | -1 | -1 | -10 | -8.2206 | -8.2206 | 0 | 12 | 1 | 1 | -8.2206 | 10 | 0 | 0
354.15 | 50.47 | 50.27 | -1 | -0.74412 | -7.4412 | 50.5 | -1 | -1 | -10 | -8.7206 | -8.7206 | 0 | 12 | 1 | 1 | -8.7206 | 10 | 0 | 0
354.2 | 50.45 | 50.29 | -1 | -0.84412 | -8.4412 | 50.5 | -1 | -1 | -10 | -9.2206 | -9.2206 | 0 | 12 | 1 | 1 | -9.2206 | 10 | 0 | 0
354.25 | 50.42 | 50.32 | -1 | -0.94412 | -9.4412 | 50.5 | -1 | -1 | -10 | -9.7206 | -9.7206 | 0 | 12 | 1 | 1 | -9.7206 | 10 | 0 | 0
354.3 | 50.39 | 50.35 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
354.35 | 50.37 | 50.37 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
354.4 | 50.34 | 50.34 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
354.45 | 50.32 | 50.32 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
354.5 | 50.29 | 50.29 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
354.55 | 50.26 | 50.26 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
354.6 | 50.24 | 50.24 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
354.65 | 50.21 | 50.21 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
354.7 | 50.18 | 50.18 | -0.81 | -0.81 | -8.1 | 50.47 | -1 | -1 | -10 | -9.05 | -9.05 | 0 | 12 | 1 | 1 | -9.05 | 10 | 0 | 0
354.75 | 50.16 | 50.16 | -0.62 | -0.62 | -6.2 | 50.45 | -1 | -1 | -10 | -8.1 | -8.1 | 0 | 12 | 1 | 1 | -8.1 | 10 | 0 | 0
354.8 | 50.13 | 50.13 | -0.335 | -0.335 | -3.35 | 50.42 | -1 | -1 | -10 | -6.675 | -6.675 | 0 | 12 | 1 | 1 | -6.675 | 10 | 0 | 0
354.85 | 50.11 | 50.11 | -0.145 | -0.145 | -1.45 | 50.39 | -1 | -1 | -10 | -5.725 | -5.725 | 0 | 12 | 1 | 1 | -5.725 | 10 | 0 | 0
354.9 | 50.08 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 50.37 | -1 | -1 | -10 | -5.1912 | -5.1912 | 0 | 12 | 1 | 1 | -5.1912 | 10 | 0 | 0
354.95 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.34 | -1 | -1 | -10 | -5.1029 | -5.1029 | 0 | 12 | 1 | 1 | -5.1029 | 10 | 0 | 0
355 | 50.03 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 50.32 | -1 | -1 | -10 | -5.0441 | -5.0441 | 0 | 12 | 1 | 1 | -5.0441 | 10 | 0 | 0
355.05 | 50 | 50 | 0 | 0 | 0 | 50.29 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
355.1 | 50 | 50 | 0 | 0 | 0 | 50.26 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
355.15 | 50 | 50 | 0 | 0 | 0 | 50.24 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
355.2 | 50 | 50 | 0 | 0 | 0 | 50.21 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
355.25 | 50 | 50 | 0 | 0 | 0 | 50.18 | -0.81 | -0.9 | -9 | -4.5 | -4.5 | 0 | 12 | 1 | 1 | -4.5 | 10 | 0 | 0
355.3 | 50 | 50 | 0 | 0 | 0 | 50.16 | -0.62 | -0.8 | -8 | -4 | -4 | 0 | 12 | 1 | 1 | -4 | 10 | 0 | 0
355.35 | 50 | 50 | 0 | 0 | 0 | 50.13 | -0.335 | -0.7 | -7 | -3.5 | -3.5 | 0 | 12 | 1 | 1 | -3.5 | 10 | 0 | 0
355.4 | 50.01 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.6 | -6 | -3 | -3 | 0 | 12 | 1 | 1 | -3 | 10 | 0 | 0
355.45 | 50.01 | 50 | 0 | 0 | 0 | 50.08 | -0.038235 | -0.5 | -5 | -2.5 | -2.5 | 0 | 12 | 1 | 1 | -2.5 | 10 | 0 | 0
355.5 | 49.99 | 49.99 | 0 | 0 | 0 | 50.05 | -0.020588 | -0.4 | -4 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
355.55 | 49.99 | 49.99 | 0 | 0 | 0 | 50.03 | -0.0088235 | -0.3 | -3 | -1.5 | -1.5 | 0 | 12 | 1 | 1 | -1.5 | 10 | 0 | 0
355.6 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | -0.2 | -2 | -0.83824 | -0.83824 | 0 | 12 | 1 | 1 | -0.83824 | 10 | 0 | 0
355.65 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | -0.1 | -1 | -0.33824 | -0.33824 | 0 | 12 | 1 | 1 | -0.33824 | 10 | 0 | 0
355.7 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
355.75 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
355.8 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
355.85 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
355.9 | 49.89 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
355.95 | 49.89 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
356 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50.01 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
356.05 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
356.1 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
356.15 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 2.7868 | 2.7868 | 0 | 12 | 1 | 1 | 2.7868 | 10 | 0 | 0
356.2 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 2.7868 | 2.7868 | 0 | 12 | 1 | 1 | 2.7868 | 10 | 0 | 0
356.25 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 2.8456 | 2.8456 | 0 | 12 | 1 | 1 | 2.8456 | 10 | 0 | 0
356.3 | 49.94 | 49.85 | 0.525 | 0.525 | 5.25 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 2.7574 | 2.7574 | 0 | 12 | 1 | 1 | 2.7574 | 10 | 0 | 0
356.35 | 49.94 | 49.85 | 0.525 | 0.525 | 5.25 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 2.7574 | 2.7574 | 0 | 12 | 1 | 1 | 2.7574 | 10 | 0 | 0
356.4 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
356.45 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
356.5 | 49.93 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
356.55 | 49.93 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
356.6 | 49.96 | 49.85 | 0.525 | 0.525 | 5.25 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 2.6985 | 2.6985 | 0 | 12 | 1 | 1 | 2.6985 | 10 | 0 | 0
356.65 | 49.96 | 49.85 | 0.525 | 0.525 | 5.25 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 2.6985 | 2.6985 | 0 | 12 | 1 | 1 | 2.6985 | 10 | 0 | 0
356.7 | 49.99 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
356.75 | 49.99 | 49.91 | 0.044118 | 0.425 | 4.25 | 49.99 | 0 | 0 | 0 | 2.125 | 2.125 | 0 | 12 | 1 | 1 | 2.125 | 10 | 0 | 0
356.8 | 49.99 | 49.91 | 0.044118 | 0.325 | 3.25 | 49.99 | 0 | 0 | 0 | 1.625 | 1.625 | 0 | 12 | 1 | 1 | 1.625 | 10 | 0 | 0
356.85 | 49.99 | 49.93 | 0.032353 | 0.225 | 2.25 | 49.99 | 0 | 0 | 0 | 1.125 | 1.125 | 0 | 12 | 1 | 1 | 1.125 | 10 | 0 | 0
356.9 | 49.96 | 49.93 | 0.032353 | 0.125 | 1.25 | 49.99 | 0 | 0 | 0 | 0.625 | 0.625 | 0 | 12 | 1 | 1 | 0.625 | 10 | 0 | 0
356.95 | 49.96 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 49.99 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
357 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
357.05 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
357.1 | 50.05 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.058824 | 0.058824 | 0 | 12 | 1 | 1 | 0.058824 | 10 | 0 | 0
357.15 | 50.05 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
357.2 | 49.97 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
357.25 | 49.97 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
357.3 | 49.92 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
357.35 | 49.92 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
357.4 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
357.45 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
357.5 | 49.94 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
357.55 | 49.94 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
357.6 | 50.01 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
357.65 | 50.01 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
357.7 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
357.75 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
357.8 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
357.85 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
357.9 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
357.95 | 49.95 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
358 | 49.97 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
358.05 | 49.97 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
358.1 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
358.15 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
358.2 | 49.87 | 49.87 | 0.335 | 0.335 | 3.35 | 50.01 | 0 | 0 | 0 | 1.675 | 1.675 | 0 | 12 | 1 | 1 | 1.675 | 10 | 0 | 0
358.25 | 49.87 | 49.87 | 0.335 | 0.335 | 3.35 | 49.99 | 0 | 0 | 0 | 1.675 | 1.675 | 0 | 12 | 1 | 1 | 1.675 | 10 | 0 | 0
358.3 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
358.35 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 2.6691 | 2.6691 | 0 | 12 | 1 | 1 | 2.6691 | 10 | 0 | 0
358.4 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
358.45 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
358.5 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
358.55 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
358.6 | 49.84 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
358.65 | 49.84 | 49.79 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
358.7 | 49.89 | 49.79 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
358.75 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.12647 | 1.2647 | 5.6324 | 5.6324 | 0 | 12 | 1 | 1 | 5.6324 | 10 | 0 | 0
358.8 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.145 | 1.45 | 5.725 | 5.725 | 0 | 12 | 1 | 1 | 5.725 | 10 | 0 | 0
358.85 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.145 | 1.45 | 5.725 | 5.725 | 0 | 12 | 1 | 1 | 5.725 | 10 | 0 | 0
358.9 | 49.96 | 49.79 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
358.95 | 49.96 | 49.79 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
359 | 50.02 | 49.79 | 1 | 1 | 10 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 4.9853 | 4.9853 | 0 | 12 | 1 | 1 | 4.9853 | 10 | 0 | 0
359.05 | 50.02 | 49.79 | 1 | 1 | 10 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 4.9853 | 4.9853 | 0 | 12 | 1 | 1 | 4.9853 | 10 | 0 | 0
359.1 | 50.03 | 49.79 | 1 | 1 | 10 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.9559 | 4.9559 | 0 | 12 | 1 | 1 | 4.9559 | 10 | 0 | 0
359.15 | 50.03 | 49.84 | 0.62 | 0.9 | 9 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.4559 | 4.4559 | 0 | 12 | 1 | 1 | 4.4559 | 10 | 0 | 0
359.2 | 50.02 | 49.84 | 0.62 | 0.8 | 8 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 3.9559 | 3.9559 | 0 | 12 | 1 | 1 | 3.9559 | 10 | 0 | 0
359.25 | 50.02 | 49.89 | 0.145 | 0.7 | 7 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 3.4559 | 3.4559 | 0 | 12 | 1 | 1 | 3.4559 | 10 | 0 | 0
359.3 | 50.08 | 49.89 | 0.145 | 0.6 | 6 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 2.8088 | 2.8088 | 0 | 12 | 1 | 1 | 2.8088 | 10 | 0 | 0
359.35 | 50.08 | 49.89 | 0.145 | 0.5 | 5 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 2.3088 | 2.3088 | 0 | 12 | 1 | 1 | 2.3088 | 10 | 0 | 0
359.4 | 50.01 | 49.89 | 0.145 | 0.4 | 4 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 1.8088 | 1.8088 | 0 | 12 | 1 | 1 | 1.8088 | 10 | 0 | 0
359.45 | 50.01 | 49.96 | 0.014706 | 0.3 | 3 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 1.3088 | 1.3088 | 0 | 12 | 1 | 1 | 1.3088 | 10 | 0 | 0
359.5 | 49.94 | 49.94 | 0.026471 | 0.2 | 2 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.80882 | 0.80882 | 0 | 12 | 1 | 1 | 0.80882 | 10 | 0 | 0
359.55 | 49.94 | 49.94 | 0.026471 | 0.1 | 1 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.30882 | 0.30882 | 0 | 12 | 1 | 1 | 0.30882 | 10 | 0 | 0
359.6 | 50 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
359.65 | 50 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
359.7 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
359.75 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
359.8 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
359.85 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
359.9 | 49.92 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
359.95 | 49.92 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
360 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50.01 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
360.05 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
360.1 | 49.92 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
360.15 | 49.92 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
360.2 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
360.25 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
360.3 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
360.35 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
360.4 | 49.87 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
360.45 | 49.87 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
360.5 | 49.8 | 49.8 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
360.55 | 49.8 | 49.8 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
360.6 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
360.65 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
360.7 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
360.75 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
360.8 | 49.72 | 49.72 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
360.85 | 49.72 | 49.72 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
360.9 | 49.67 | 49.67 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
360.95 | 49.67 | 49.67 | 1 | 1 | 10 | 49.87 | 0.335 | 0.14412 | 1.4412 | 5.7206 | 5.7206 | 0 | 12 | 1 | 1 | 5.7206 | 10 | 0 | 0
361 | 49.65 | 49.65 | 1 | 1 | 10 | 49.87 | 0.335 | 0.24412 | 2.4412 | 6.2206 | 6.2206 | 0 | 12 | 1 | 1 | 6.2206 | 10 | 0 | 0
361.05 | 49.65 | 49.65 | 1 | 1 | 10 | 49.8 | 1 | 0.34412 | 3.4412 | 6.7206 | 6.7206 | 0 | 12 | 1 | 1 | 6.7206 | 10 | 0 | 0
361.1 | 49.59 | 49.59 | 1 | 1 | 10 | 49.8 | 1 | 0.44412 | 4.4412 | 7.2206 | 7.2206 | 0 | 12 | 1 | 1 | 7.2206 | 10 | 0 | 0
361.15 | 49.59 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.54412 | 5.4412 | 7.7206 | 7.7206 | 0 | 12 | 1 | 1 | 7.7206 | 10 | 0 | 0
361.2 | 49.66 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.64412 | 6.4412 | 8.2206 | 8.2206 | 0 | 12 | 1 | 1 | 8.2206 | 10 | 0 | 0
361.25 | 49.66 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.74412 | 7.4412 | 8.7206 | 8.7206 | 0 | 12 | 1 | 1 | 8.7206 | 10 | 0 | 0
361.3 | 49.63 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.84412 | 8.4412 | 9.2206 | 9.2206 | 0 | 12 | 1 | 1 | 9.2206 | 10 | 0 | 0
361.35 | 49.63 | 49.59 | 1 | 1 | 10 | 49.72 | 1 | 0.94412 | 9.4412 | 9.7206 | 9.7206 | 0 | 12 | 1 | 1 | 9.7206 | 10 | 0 | 0
361.4 | 49.61 | 49.59 | 1 | 1 | 10 | 49.72 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
361.45 | 49.61 | 49.59 | 1 | 1 | 10 | 49.67 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
361.5 | 49.54 | 49.54 | 1 | 1 | 10 | 49.67 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
361.55 | 49.54 | 49.54 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
361.6 | 49.46 | 49.46 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
361.65 | 49.46 | 49.46 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
361.7 | 49.45 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
361.75 | 49.45 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
361.8 | 49.51 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
361.85 | 49.51 | 49.45 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
361.9 | 49.5 | 49.45 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
361.95 | 49.5 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
362 | 49.54 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
362.05 | 49.54 | 49.45 | 1 | 1 | 10 | 49.54 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
362.1 | 49.59 | 49.45 | 1 | 1 | 10 | 49.59 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
362.15 | 49.59 | 49.45 | 1 | 1 | 10 | 49.59 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
362.2 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
362.25 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
362.3 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
362.35 | 49.61 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
362.4 | 49.53 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
362.45 | 49.53 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
362.5 | 49.54 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
362.55 | 49.54 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
362.6 | 49.61 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
362.65 | 49.61 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
362.7 | 49.66 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
362.75 | 49.66 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
362.8 | 49.64 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
362.85 | 49.64 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
362.9 | 49.69 | 49.53 | 1 | 1 | 10 | 49.69 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
362.95 | 49.69 | 49.53 | 1 | 1 | 10 | 49.69 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
363 | 49.74 | 49.53 | 1 | 1 | 10 | 49.74 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
363.05 | 49.74 | 49.54 | 1 | 1 | 10 | 49.74 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
363.1 | 49.78 | 49.54 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
363.15 | 49.78 | 49.61 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
363.2 | 49.82 | 49.61 | 1 | 1 | 10 | 49.82 | 0.81 | 0.81 | 8.1 | 9.05 | 9.05 | 0 | 12 | 1 | 1 | 9.05 | 10 | 0 | 0
363.25 | 49.82 | 49.64 | 1 | 1 | 10 | 49.82 | 0.81 | 0.81 | 8.1 | 9.05 | 9.05 | 0 | 12 | 1 | 1 | 9.05 | 10 | 0 | 0
363.3 | 49.86 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
363.35 | 49.86 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
363.4 | 49.84 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
363.45 | 49.84 | 49.69 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
363.5 | 49.91 | 49.69 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
363.55 | 49.91 | 49.74 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
363.6 | 49.97 | 49.74 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
363.65 | 49.97 | 49.78 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
363.7 | 50.03 | 49.78 | 1 | 1 | 10 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.9559 | 4.9559 | 0 | 12 | 1 | 1 | 4.9559 | 10 | 0 | 0
363.75 | 50.03 | 49.82 | 0.81 | 0.9 | 9 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.4559 | 4.4559 | 0 | 12 | 1 | 1 | 4.4559 | 10 | 0 | 0
363.8 | 50.05 | 49.82 | 0.81 | 0.81 | 8.1 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 3.9471 | 3.9471 | 0 | 12 | 1 | 1 | 3.9471 | 10 | 0 | 0
363.85 | 50.05 | 49.84 | 0.62 | 0.71 | 7.1 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 3.4471 | 3.4471 | 0 | 12 | 1 | 1 | 3.4471 | 10 | 0 | 0
363.9 | 50.01 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
363.95 | 50.01 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
364 | 49.95 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
364.05 | 49.95 | 49.91 | 0.044118 | 0.52 | 5.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.4971 | 2.4971 | 0 | 12 | 1 | 1 | 2.4971 | 10 | 0 | 0
364.1 | 49.99 | 49.91 | 0.044118 | 0.42 | 4.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 1.9971 | 1.9971 | 0 | 12 | 1 | 1 | 1.9971 | 10 | 0 | 0
364.15 | 49.99 | 49.95 | 0.020588 | 0.32 | 3.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 1.4971 | 1.4971 | 0 | 12 | 1 | 1 | 1.4971 | 10 | 0 | 0
364.2 | 49.92 | 49.92 | 0.038235 | 0.22 | 2.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.99706 | 0.99706 | 0 | 12 | 1 | 1 | 0.99706 | 10 | 0 | 0
364.25 | 49.92 | 49.92 | 0.038235 | 0.12 | 1.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.49706 | 0.49706 | 0 | 12 | 1 | 1 | 0.49706 | 10 | 0 | 0
364.3 | 49.97 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
364.35 | 49.97 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
364.4 | 50.02 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
364.45 | 50.02 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.17647 | 0.17647 | 0 | 12 | 1 | 1 | 0.17647 | 10 | 0 | 0
364.5 | 50.07 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
364.55 | 50.07 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
364.6 | 50.06 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
364.65 | 50.06 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
364.7 | 50.13 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
364.75 | 50.13 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
364.8 | 50.09 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
364.85 | 50.09 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6309 | -1.6309 | 0 | 12 | 1 | 1 | -1.6309 | 10 | 0 | 0
364.9 | 50.07 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6309 | -1.6309 | 0 | 12 | 1 | 1 | -1.6309 | 10 | 0 | 0
364.95 | 50.07 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6897 | -1.6897 | 0 | 12 | 1 | 1 | -1.6897 | 10 | 0 | 0
365 | 50.07 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6897 | -1.6897 | 0 | 12 | 1 | 1 | -1.6897 | 10 | 0 | 0
365.05 | 50.07 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.13 | -0.335 | -0.335 | -3.35 | -1.8074 | -1.8074 | 0 | 12 | 1 | 1 | -1.8074 | 10 | 0 | 0
365.1 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.13 | -0.335 | -0.335 | -3.35 | -1.7779 | -1.7779 | 0 | 12 | 1 | 1 | -1.7779 | 10 | 0 | 0
365.15 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.13 | -0.335 | -0.335 | -3.35 | -1.7779 | -1.7779 | 0 | 12 | 1 | 1 | -1.7779 | 10 | 0 | 0
365.2 | 50.01 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
365.25 | 50.01 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
365.3 | 50.07 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
365.35 | 50.07 | 50.01 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.235 | -2.35 | -1.175 | -1.175 | 0 | 12 | 1 | 1 | -1.175 | 10 | 0 | 0
365.4 | 50.05 | 50.01 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.135 | -1.35 | -0.675 | -0.675 | 0 | 12 | 1 | 1 | -0.675 | 10 | 0 | 0
365.45 | 50.05 | 50.01 | 0 | 0 | 0 | 50.07 | -0.032353 | -0.035 | -0.35 | -0.175 | -0.175 | 0 | 12 | 1 | 1 | -0.175 | 10 | 0 | 0
365.5 | 50.1 | 50.01 | 0 | 0 | 0 | 50.1 | -0.05 | -0.05 | -0.5 | -0.25 | -0.25 | 0 | 12 | 1 | 1 | -0.25 | 10 | 0 | 0
365.55 | 50.1 | 50.01 | 0 | 0 | 0 | 50.1 | -0.05 | -0.05 | -0.5 | -0.25 | -0.25 | 0 | 12 | 1 | 1 | -0.25 | 10 | 0 | 0
365.6 | 50.11 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
365.65 | 50.11 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
365.7 | 50.06 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
365.75 | 50.06 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
365.8 | 50.04 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
365.85 | 50.04 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
365.9 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
365.95 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
366 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
366.05 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
366.1 | 50.11 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
366.15 | 50.11 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
366.2 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
366.25 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
366.3 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
366.35 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
366.4 | 50.02 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.11 | -0.145 | -0.145 | -1.45 | -0.73971 | -0.73971 | 0 | 12 | 1 | 1 | -0.73971 | 10 | 0 | 0
366.45 | 50.02 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.11 | -0.145 | -0.145 | -1.45 | -0.73971 | -0.73971 | 0 | 12 | 1 | 1 | -0.73971 | 10 | 0 | 0
366.5 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
366.55 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
366.6 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
366.65 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
366.7 | 50.01 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
366.75 | 50.01 | 50 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.045 | -0.45 | -0.225 | -0.225 | 0 | 12 | 1 | 1 | -0.225 | 10 | 0 | 0
366.8 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
366.85 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
366.9 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
366.95 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
367 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.14706 | 0.14706 | 0 | 12 | 1 | 1 | 0.14706 | 10 | 0 | 0
367.05 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
367.1 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
367.15 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
367.2 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
367.25 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
367.3 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
367.35 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
367.4 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
367.45 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
367.5 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
367.55 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
367.6 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
367.65 | 50 | 50 | 0 | 0 | 0 | 50.01 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
367.7 | 49.5 | 49.5 | 1 | 1 | 10 | 50.01 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
367.75 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
367.8 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
367.85 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
367.9 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
367.95 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
368 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
368.05 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
368.1 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
368.15 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
368.2 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
368.25 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.1 | 1 | 5.5 | 5.5 | 0 | 12 | 1 | 1 | 5.5 | 10 | 0 | 0
368.3 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.2 | 2 | 6 | 6 | 0 | 12 | 1 | 1 | 6 | 10 | 0 | 0
368.35 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.3 | 3 | 6.5 | 6.5 | 0 | 12 | 1 | 1 | 6.5 | 10 | 0 | 0
368.4 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.4 | 4 | 7 | 7 | 0 | 12 | 1 | 1 | 7 | 10 | 0 | 0
368.45 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.5 | 5 | 7.5 | 7.5 | 0 | 12 | 1 | 1 | 7.5 | 10 | 0 | 0
368.5 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.6 | 6 | 8 | 8 | 0 | 12 | 1 | 1 | 8 | 10 | 0 | 0
368.55 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.7 | 7 | 8.5 | 8.5 | 0 | 12 | 1 | 1 | 8.5 | 10 | 0 | 0
368.6 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.8 | 8 | 9 | 9 | 0 | 12 | 1 | 1 | 9 | 10 | 0 | 0
368.65 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.9 | 9 | 9.5 | 9.5 | 0 | 12 | 1 | 1 | 9.5 | 10 | 0 | 0
368.7 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
368.75 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
368.8 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
368.85 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
368.9 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
368.95 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
369 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
369.05 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
369.1 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
369.15 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
369.2 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
369.25 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
369.3 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
369.35 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
369.4 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
369.45 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
369.5 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
369.55 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
369.6 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
369.65 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
369.7 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
369.75 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
369.8 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
369.85 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
369.9 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
369.95 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
370 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
370.05 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
370.1 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
370.15 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
370.2 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
370.25 | 50.5 | 50.5 | -1 | 0.9 | 9 | 50.5 | -1 | -1 | -10 | -0.5 | -0.5 | 0 | 12 | 1 | 1 | -0.5 | 10 | 0 | 0
370.3 | 50.5 | 50.5 | -1 | 0.8 | 8 | 50.5 | -1 | -1 | -10 | -1 | -1 | 0 | 12 | 1 | 1 | -1 | 10 | 0 | 0
370.35 | 50.5 | 50.5 | -1 | 0.7 | 7 | 50.5 | -1 | -1 | -10 | -1.5 | -1.5 | 0 | 12 | 1 | 1 | -1.5 | 10 | 0 | 0
370.4 | 50.5 | 50.5 | -1 | 0.6 | 6 | 50.5 | -1 | -1 | -10 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
370.45 | 50.5 | 50.5 | -1 | 0.5 | 5 | 50.5 | -1 | -1 | -10 | -2.5 | -2.5 | 0 | 12 | 1 | 1 | -2.5 | 10 | 0 | 0
370.5 | 50.5 | 50.5 | -1 | 0.4 | 4 | 50.5 | -1 | -1 | -10 | -3 | -3 | 0 | 12 | 1 | 1 | -3 | 10 | 0 | 0
370.55 | 50.5 | 50.5 | -1 | 0.3 | 3 | 50.5 | -1 | -1 | -10 | -3.5 | -3.5 | 0 | 12 | 1 | 1 | -3.5 | 10 | 0 | 0
370.6 | 50.5 | 50.5 | -1 | 0.2 | 2 | 50.5 | -1 | -1 | -10 | -4 | -4 | 0 | 12 | 1 | 1 | -4 | 10 | 0 | 0
370.65 | 50.5 | 50.5 | -1 | 0.1 | 1 | 50.5 | -1 | -1 | -10 | -4.5 | -4.5 | 0 | 12 | 1 | 1 | -4.5 | 10 | 0 | 0
370.7 | 50.5 | 50.5 | -1 | 0 | 0 | 50.5 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
370.75 | 50.5 | 50.5 | -1 | -0.1 | -1 | 50.5 | -1 | -1 | -10 | -5.5 | -5.5 | 0 | 12 | 1 | 1 | -5.5 | 10 | 0 | 0
370.8 | 50.5 | 50.5 | -1 | -0.2 | -2 | 50.5 | -1 | -1 | -10 | -6 | -6 | 0 | 12 | 1 | 1 | -6 | 10 | 0 | 0
370.85 | 50.5 | 50.5 | -1 | -0.3 | -3 | 50.5 | -1 | -1 | -10 | -6.5 | -6.5 | 0 | 12 | 1 | 1 | -6.5 | 10 | 0 | 0
370.9 | 50.5 | 50.5 | -1 | -0.4 | -4 | 50.5 | -1 | -1 | -10 | -7 | -7 | 0 | 12 | 1 | 1 | -7 | 10 | 0 | 0
370.95 | 50.5 | 50.5 | -1 | -0.5 | -5 | 50.5 | -1 | -1 | -10 | -7.5 | -7.5 | 0 | 12 | 1 | 1 | -7.5 | 10 | 0 | 0
371 | 50.5 | 50.5 | -1 | -0.6 | -6 | 50.5 | -1 | -1 | -10 | -8 | -8 | 0 | 12 | 1 | 1 | -8 | 10 | 0 | 0
371.05 | 50.5 | 50.5 | -1 | -0.7 | -7 | 50.5 | -1 | -1 | -10 | -8.5 | -8.5 | 0 | 12 | 1 | 1 | -8.5 | 10 | 0 | 0
371.1 | 50.5 | 50.5 | -1 | -0.8 | -8 | 50.5 | -1 | -1 | -10 | -9 | -9 | 0 | 12 | 1 | 1 | -9 | 10 | 0 | 0
371.15 | 50.5 | 50.5 | -1 | -0.9 | -9 | 50.5 | -1 | -1 | -10 | -9.5 | -9.5 | 0 | 12 | 1 | 1 | -9.5 | 10 | 0 | 0
371.2 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
371.25 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
371.3 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
371.35 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
371.4 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
371.45 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
371.5 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
371.55 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
371.6 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
371.65 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
371.7 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
371.75 | 50.47 | 50.47 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
371.8 | 50.45 | 50.45 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
371.85 | 50.42 | 50.42 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
371.9 | 50.4 | 50.4 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
371.95 | 50.37 | 50.37 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
372 | 50.35 | 50.35 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
372.05 | 50.32 | 50.32 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
372.1 | 50.29 | 50.29 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
372.15 | 50.27 | 50.27 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
372.2 | 50.24 | 50.24 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
372.25 | 50.22 | 50.22 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
372.3 | 50.19 | 50.19 | -0.905 | -0.905 | -9.05 | 50.47 | -1 | -1 | -10 | -9.525 | -9.525 | 0 | 12 | 1 | 1 | -9.525 | 10 | 0 | 0
372.35 | 50.17 | 50.17 | -0.715 | -0.715 | -7.15 | 50.45 | -1 | -1 | -10 | -8.575 | -8.575 | 0 | 12 | 1 | 1 | -8.575 | 10 | 0 | 0
372.4 | 50.14 | 50.14 | -0.43 | -0.43 | -4.3 | 50.42 | -1 | -1 | -10 | -7.15 | -7.15 | 0 | 12 | 1 | 1 | -7.15 | 10 | 0 | 0
372.45 | 50.12 | 50.12 | -0.24 | -0.24 | -2.4 | 50.4 | -1 | -1 | -10 | -6.2 | -6.2 | 0 | 12 | 1 | 1 | -6.2 | 10 | 0 | 0
372.5 | 50.09 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 50.37 | -1 | -1 | -10 | -5.2206 | -5.2206 | 0 | 12 | 1 | 1 | -5.2206 | 10 | 0 | 0
372.55 | 50.06 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.35 | -1 | -1 | -10 | -5.1324 | -5.1324 | 0 | 12 | 1 | 1 | -5.1324 | 10 | 0 | 0
372.6 | 50.04 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.32 | -1 | -1 | -10 | -5.0735 | -5.0735 | 0 | 12 | 1 | 1 | -5.0735 | 10 | 0 | 0
372.65 | 50.01 | 50.01 | 0 | 0 | 0 | 50.29 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
372.7 | 49.99 | 49.99 | 0 | 0 | 0 | 50.27 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
372.75 | 49.96 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.24 | -1 | -1 | -10 | -4.9265 | -4.9265 | 0 | 12 | 1 | 1 | -4.9265 | 10 | 0 | 0
372.8 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.22 | -1 | -1 | -10 | -4.8676 | -4.8676 | 0 | 12 | 1 | 1 | -4.8676 | 10 | 0 | 0
372.85 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.19 | -0.905 | -0.905 | -9.05 | -4.3044 | -4.3044 | 0 | 12 | 1 | 1 | -4.3044 | 10 | 0 | 0
372.9 | 49.88 | 49.88 | 0.24 | 0.24 | 2.4 | 50.17 | -0.715 | -0.805 | -8.05 | -2.825 | -2.825 | 0 | 12 | 1 | 1 | -2.825 | 10 | 0 | 0
372.95 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.14 | -0.43 | -0.705 | -7.05 | -1.375 | -1.375 | 0 | 12 | 1 | 1 | -1.375 | 10 | 0 | 0
373 | 49.83 | 49.83 | 0.715 | 0.715 | 7.15 | 50.12 | -0.24 | -0.605 | -6.05 | 0.55 | 0.55 | 0 | 12 | 1 | 1 | 0.55 | 10 | 0 | 0
373.05 | 49.81 | 49.81 | 0.905 | 0.905 | 9.05 | 50.09 | -0.044118 | -0.505 | -5.05 | 2 | 2 | 0 | 12 | 1 | 1 | 2 | 10 | 0 | 0
373.1 | 49.78 | 49.78 | 1 | 1 | 10 | 50.06 | -0.026471 | -0.405 | -4.05 | 2.975 | 2.975 | 0 | 12 | 1 | 1 | 2.975 | 10 | 0 | 0
373.15 | 49.76 | 49.76 | 1 | 1 | 10 | 50.04 | -0.014706 | -0.305 | -3.05 | 3.475 | 3.475 | 0 | 12 | 1 | 1 | 3.475 | 10 | 0 | 0
373.2 | 49.73 | 49.73 | 1 | 1 | 10 | 50.01 | 0 | -0.205 | -2.05 | 3.975 | 3.975 | 0 | 12 | 1 | 1 | 3.975 | 10 | 0 | 0
373.25 | 49.71 | 49.71 | 1 | 1 | 10 | 49.99 | 0 | -0.105 | -1.05 | 4.475 | 4.475 | 0 | 12 | 1 | 1 | 4.475 | 10 | 0 | 0
373.3 | 49.68 | 49.68 | 1 | 1 | 10 | 49.96 | 0.014706 | -0.005 | -0.05 | 4.975 | 4.975 | 0 | 12 | 1 | 1 | 4.975 | 10 | 0 | 0
373.35 | 49.65 | 49.65 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
373.4 | 49.63 | 49.63 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
373.45 | 49.6 | 49.6 | 1 | 1 | 10 | 49.88 | 0.24 | 0.14412 | 1.4412 | 5.7206 | 5.7206 | 0 | 12 | 1 | 1 | 5.7206 | 10 | 0 | 0
373.5 | 49.58 | 49.58 | 1 | 1 | 10 | 49.86 | 0.43 | 0.24412 | 2.4412 | 6.2206 | 6.2206 | 0 | 12 | 1 | 1 | 6.2206 | 10 | 0 | 0
373.55 | 49.55 | 49.55 | 1 | 1 | 10 | 49.83 | 0.715 | 0.34412 | 3.4412 | 6.7206 | 6.7206 | 0 | 12 | 1 | 1 | 6.7206 | 10 | 0 | 0
373.6 | 49.53 | 49.53 | 1 | 1 | 10 | 49.81 | 0.905 | 0.44412 | 4.4412 | 7.2206 | 7.2206 | 0 | 12 | 1 | 1 | 7.2206 | 10 | 0 | 0
373.65 | 49.5 | 49.5 | 1 | 1 | 10 | 49.78 | 1 | 0.54412 | 5.4412 | 7.7206 | 7.7206 | 0 | 12 | 1 | 1 | 7.7206 | 10 | 0 | 0
373.7 | 49.5 | 49.5 | 1 | 1 | 10 | 49.76 | 1 | 0.64412 | 6.4412 | 8.2206 | 8.2206 | 0 | 12 | 1 | 1 | 8.2206 | 10 | 0 | 0
373.75 | 49.53 | 49.5 | 1 | 1 | 10 | 49.73 | 1 | 0.74412 | 7.4412 | 8.7206 | 8.7206 | 0 | 12 | 1 | 1 | 8.7206 | 10 | 0 | 0
373.8 | 49.55 | 49.5 | 1 | 1 | 10 | 49.71 | 1 | 0.84412 | 8.4412 | 9.2206 | 9.2206 | 0 | 12 | 1 | 1 | 9.2206 | 10 | 0 | 0
373.85 | 49.58 | 49.5 | 1 | 1 | 10 | 49.68 | 1 | 0.94412 | 9.4412 | 9.7206 | 9.7206 | 0 | 12 | 1 | 1 | 9.7206 | 10 | 0 | 0
373.9 | 49.6 | 49.5 | 1 | 1 | 10 | 49.65 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
373.95 | 49.63 | 49.5 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
374 | 49.65 | 49.5 | 1 | 1 | 10 | 49.65 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
374.05 | 49.68 | 49.5 | 1 | 1 | 10 | 49.68 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
374.1 | 49.71 | 49.5 | 1 | 1 | 10 | 49.71 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
374.15 | 49.73 | 49.5 | 1 | 1 | 10 | 49.73 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
374.2 | 49.76 | 49.5 | 1 | 1 | 10 | 49.76 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
374.25 | 49.78 | 49.5 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
374.3 | 49.81 | 49.53 | 1 | 1 | 10 | 49.81 | 0.905 | 0.905 | 9.05 | 9.525 | 9.525 | 0 | 12 | 1 | 1 | 9.525 | 10 | 0 | 0
374.35 | 49.83 | 49.55 | 1 | 1 | 10 | 49.83 | 0.715 | 0.715 | 7.15 | 8.575 | 8.575 | 0 | 12 | 1 | 1 | 8.575 | 10 | 0 | 0
374.4 | 49.86 | 49.58 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
374.45 | 49.88 | 49.6 | 1 | 1 | 10 | 49.88 | 0.24 | 0.24 | 2.4 | 6.2 | 6.2 | 0 | 12 | 1 | 1 | 6.2 | 10 | 0 | 0
374.5 | 49.91 | 49.63 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
374.55 | 49.94 | 49.65 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
374.6 | 49.96 | 49.68 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
374.65 | 49.99 | 49.71 | 1 | 1 | 10 | 49.99 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
374.7 | 50.01 | 49.73 | 1 | 1 | 10 | 50.01 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
374.75 | 50.04 | 49.76 | 1 | 1 | 10 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 4.9265 | 4.9265 | 0 | 12 | 1 | 1 | 4.9265 | 10 | 0 | 0
374.8 | 50.06 | 49.78 | 1 | 1 | 10 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 4.8676 | 4.8676 | 0 | 12 | 1 | 1 | 4.8676 | 10 | 0 | 0
374.85 | 50.09 | 49.81 | 0.905 | 0.905 | 9.05 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 4.3044 | 4.3044 | 0 | 12 | 1 | 1 | 4.3044 | 10 | 0 | 0
374.9 | 50.12 | 49.83 | 0.715 | 0.805 | 8.05 | 50.12 | -0.24 | -0.24 | -2.4 | 2.825 | 2.825 | 0 | 12 | 1 | 1 | 2.825 | 10 | 0 | 0
374.95 | 50.14 | 49.86 | 0.43 | 0.705 | 7.05 | 50.14 | -0.43 | -0.43 | -4.3 | 1.375 | 1.375 | 0 | 12 | 1 | 1 | 1.375 | 10 | 0 | 0
375 | 50.17 | 49.88 | 0.24 | 0.605 | 6.05 | 50.17 | -0.715 | -0.715 | -7.15 | -0.55 | -0.55 | 0 | 12 | 1 | 1 | -0.55 | 10 | 0 | 0
375.05 | 50.19 | 49.91 | 0.044118 | 0.505 | 5.05 | 50.19 | -0.905 | -0.905 | -9.05 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
375.1 | 50.22 | 49.94 | 0.026471 | 0.405 | 4.05 | 50.22 | -1 | -1 | -10 | -2.975 | -2.975 | 0 | 12 | 1 | 1 | -2.975 | 10 | 0 | 0
375.15 | 50.24 | 49.96 | 0.014706 | 0.305 | 3.05 | 50.24 | -1 | -1 | -10 | -3.475 | -3.475 | 0 | 12 | 1 | 1 | -3.475 | 10 | 0 | 0
375.2 | 50.27 | 49.99 | 0 | 0.205 | 2.05 | 50.27 | -1 | -1 | -10 | -3.975 | -3.975 | 0 | 12 | 1 | 1 | -3.975 | 10 | 0 | 0
375.25 | 50.29 | 50.01 | 0 | 0.105 | 1.05 | 50.29 | -1 | -1 | -10 | -4.475 | -4.475 | 0 | 12 | 1 | 1 | -4.475 | 10 | 0 | 0
375.3 | 50.32 | 50.04 | -0.014706 | 0.005 | 0.05 | 50.32 | -1 | -1 | -10 | -4.975 | -4.975 | 0 | 12 | 1 | 1 | -4.975 | 10 | 0 | 0
375.35 | 50.35 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.35 | -1 | -1 | -10 | -5.1324 | -5.1324 | 0 | 12 | 1 | 1 | -5.1324 | 10 | 0 | 0
375.4 | 50.37 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 50.37 | -1 | -1 | -10 | -5.2206 | -5.2206 | 0 | 12 | 1 | 1 | -5.2206 | 10 | 0 | 0
375.45 | 50.4 | 50.12 | -0.24 | -0.14412 | -1.4412 | 50.4 | -1 | -1 | -10 | -5.7206 | -5.7206 | 0 | 12 | 1 | 1 | -5.7206 | 10 | 0 | 0
375.5 | 50.42 | 50.14 | -0.43 | -0.24412 | -2.4412 | 50.42 | -1 | -1 | -10 | -6.2206 | -6.2206 | 0 | 12 | 1 | 1 | -6.2206 | 10 | 0 | 0
375.55 | 50.45 | 50.17 | -0.715 | -0.34412 | -3.4412 | 50.45 | -1 | -1 | -10 | -6.7206 | -6.7206 | 0 | 12 | 1 | 1 | -6.7206 | 10 | 0 | 0
375.6 | 50.47 | 50.19 | -0.905 | -0.44412 | -4.4412 | 50.47 | -1 | -1 | -10 | -7.2206 | -7.2206 | 0 | 12 | 1 | 1 | -7.2206 | 10 | 0 | 0
375.65 | 50.5 | 50.22 | -1 | -0.54412 | -5.4412 | 50.5 | -1 | -1 | -10 | -7.7206 | -7.7206 | 0 | 12 | 1 | 1 | -7.7206 | 10 | 0 | 0
375.7 | 50.5 | 50.24 | -1 | -0.64412 | -6.4412 | 50.5 | -1 | -1 | -10 | -8.2206 | -8.2206 | 0 | 12 | 1 | 1 | -8.2206 | 10 | 0 | 0
375.75 | 50.47 | 50.27 | -1 | -0.74412 | -7.4412 | 50.5 | -1 | -1 | -10 | -8.7206 | -8.7206 | 0 | 12 | 1 | 1 | -8.7206 | 10 | 0 | 0
375.8 | 50.45 | 50.29 | -1 | -0.84412 | -8.4412 | 50.5 | -1 | -1 | -10 | -9.2206 | -9.2206 | 0 | 12 | 1 | 1 | -9.2206 | 10 | 0 | 0
375.85 | 50.42 | 50.32 | -1 | -0.94412 | -9.4412 | 50.5 | -1 | -1 | -10 | -9.7206 | -9.7206 | 0 | 12 | 1 | 1 | -9.7206 | 10 | 0 | 0
375.9 | 50.39 | 50.35 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
375.95 | 50.37 | 50.37 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
376 | 50.34 | 50.34 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
376.05 | 50.32 | 50.32 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
376.1 | 50.29 | 50.29 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
376.15 | 50.26 | 50.26 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
376.2 | 50.24 | 50.24 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
376.25 | 50.21 | 50.21 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
376.3 | 50.18 | 50.18 | -0.81 | -0.81 | -8.1 | 50.47 | -1 | -1 | -10 | -9.05 | -9.05 | 0 | 12 | 1 | 1 | -9.05 | 10 | 0 | 0
376.35 | 50.16 | 50.16 | -0.62 | -0.62 | -6.2 | 50.45 | -1 | -1 | -10 | -8.1 | -8.1 | 0 | 12 | 1 | 1 | -8.1 | 10 | 0 | 0
376.4 | 50.13 | 50.13 | -0.335 | -0.335 | -3.35 | 50.42 | -1 | -1 | -10 | -6.675 | -6.675 | 0 | 12 | 1 | 1 | -6.675 | 10 | 0 | 0
376.45 | 50.11 | 50.11 | -0.145 | -0.145 | -1.45 | 50.39 | -1 | -1 | -10 | -5.725 | -5.725 | 0 | 12 | 1 | 1 | -5.725 | 10 | 0 | 0
376.5 | 50.08 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 50.37 | -1 | -1 | -10 | -5.1912 | -5.1912 | 0 | 12 | 1 | 1 | -5.1912 | 10 | 0 | 0
376.55 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.34 | -1 | -1 | -10 | -5.1029 | -5.1029 | 0 | 12 | 1 | 1 | -5.1029 | 10 | 0 | 0
376.6 | 50.03 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 50.32 | -1 | -1 | -10 | -5.0441 | -5.0441 | 0 | 12 | 1 | 1 | -5.0441 | 10 | 0 | 0
376.65 | 50 | 50 | 0 | 0 | 0 | 50.29 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
376.7 | 50 | 50 | 0 | 0 | 0 | 50.26 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
376.75 | 50 | 50 | 0 | 0 | 0 | 50.24 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
376.8 | 50 | 50 | 0 | 0 | 0 | 50.21 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
376.85 | 50 | 50 | 0 | 0 | 0 | 50.18 | -0.81 | -0.9 | -9 | -4.5 | -4.5 | 0 | 12 | 1 | 1 | -4.5 | 10 | 0 | 0
376.9 | 50 | 50 | 0 | 0 | 0 | 50.16 | -0.62 | -0.8 | -8 | -4 | -4 | 0 | 12 | 1 | 1 | -4 | 10 | 0 | 0
376.95 | 50 | 50 | 0 | 0 | 0 | 50.13 | -0.335 | -0.7 | -7 | -3.5 | -3.5 | 0 | 12 | 1 | 1 | -3.5 | 10 | 0 | 0
377 | 50.01 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.6 | -6 | -3 | -3 | 0 | 12 | 1 | 1 | -3 | 10 | 0 | 0
377.05 | 50.01 | 50 | 0 | 0 | 0 | 50.08 | -0.038235 | -0.5 | -5 | -2.5 | -2.5 | 0 | 12 | 1 | 1 | -2.5 | 10 | 0 | 0
377.1 | 49.99 | 49.99 | 0 | 0 | 0 | 50.05 | -0.020588 | -0.4 | -4 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
377.15 | 49.99 | 49.99 | 0 | 0 | 0 | 50.03 | -0.0088235 | -0.3 | -3 | -1.5 | -1.5 | 0 | 12 | 1 | 1 | -1.5 | 10 | 0 | 0
377.2 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | -0.2 | -2 | -0.83824 | -0.83824 | 0 | 12 | 1 | 1 | -0.83824 | 10 | 0 | 0
377.25 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | -0.1 | -1 | -0.33824 | -0.33824 | 0 | 12 | 1 | 1 | -0.33824 | 10 | 0 | 0
377.3 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
377.35 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
377.4 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
377.45 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
377.5 | 49.89 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
377.55 | 49.89 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
377.6 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50.01 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
377.65 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
377.7 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
377.75 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 2.7868 | 2.7868 | 0 | 12 | 1 | 1 | 2.7868 | 10 | 0 | 0
377.8 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 2.7868 | 2.7868 | 0 | 12 | 1 | 1 | 2.7868 | 10 | 0 | 0
377.85 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 2.8456 | 2.8456 | 0 | 12 | 1 | 1 | 2.8456 | 10 | 0 | 0
377.9 | 49.94 | 49.85 | 0.525 | 0.525 | 5.25 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 2.7574 | 2.7574 | 0 | 12 | 1 | 1 | 2.7574 | 10 | 0 | 0
377.95 | 49.94 | 49.85 | 0.525 | 0.525 | 5.25 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 2.7574 | 2.7574 | 0 | 12 | 1 | 1 | 2.7574 | 10 | 0 | 0
378 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
378.05 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
378.1 | 49.93 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
378.15 | 49.93 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
378.2 | 49.96 | 49.85 | 0.525 | 0.525 | 5.25 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 2.6985 | 2.6985 | 0 | 12 | 1 | 1 | 2.6985 | 10 | 0 | 0
378.25 | 49.96 | 49.85 | 0.525 | 0.525 | 5.25 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 2.6985 | 2.6985 | 0 | 12 | 1 | 1 | 2.6985 | 10 | 0 | 0
378.3 | 49.99 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
378.35 | 49.99 | 49.91 | 0.044118 | 0.425 | 4.25 | 49.99 | 0 | 0 | 0 | 2.125 | 2.125 | 0 | 12 | 1 | 1 | 2.125 | 10 | 0 | 0
378.4 | 49.99 | 49.91 | 0.044118 | 0.325 | 3.25 | 49.99 | 0 | 0 | 0 | 1.625 | 1.625 | 0 | 12 | 1 | 1 | 1.625 | 10 | 0 | 0
378.45 | 49.99 | 49.93 | 0.032353 | 0.225 | 2.25 | 49.99 | 0 | 0 | 0 | 1.125 | 1.125 | 0 | 12 | 1 | 1 | 1.125 | 10 | 0 | 0
378.5 | 49.96 | 49.93 | 0.032353 | 0.125 | 1.25 | 49.99 | 0 | 0 | 0 | 0.625 | 0.625 | 0 | 12 | 1 | 1 | 0.625 | 10 | 0 | 0
378.55 | 49.96 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 49.99 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
378.6 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
378.65 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
378.7 | 50.05 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.058824 | 0.058824 | 0 | 12 | 1 | 1 | 0.058824 | 10 | 0 | 0
378.75 | 50.05 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
378.8 | 49.97 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
378.85 | 49.97 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
378.9 | 49.92 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
378.95 | 49.92 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
379 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
379.05 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
379.1 | 49.94 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
379.15 | 49.94 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
379.2 | 50.01 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
379.25 | 50.01 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
379.3 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
379.35 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
379.4 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
379.45 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
379.5 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
379.55 | 49.95 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
379.6 | 49.97 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
379.65 | 49.97 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
379.7 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
379.75 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
379.8 | 49.87 | 49.87 | 0.335 | 0.335 | 3.35 | 50.01 | 0 | 0 | 0 | 1.675 | 1.675 | 0 | 12 | 1 | 1 | 1.675 | 10 | 0 | 0
379.85 | 49.87 | 49.87 | 0.335 | 0.335 | 3.35 | 49.99 | 0 | 0 | 0 | 1.675 | 1.675 | 0 | 12 | 1 | 1 | 1.675 | 10 | 0 | 0
379.9 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
379.95 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 2.6691 | 2.6691 | 0 | 12 | 1 | 1 | 2.6691 | 10 | 0 | 0
380 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
380.05 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
380.1 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
380.15 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
380.2 | 49.84 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
380.25 | 49.84 | 49.79 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
380.3 | 49.89 | 49.79 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
380.35 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.12647 | 1.2647 | 5.6324 | 5.6324 | 0 | 12 | 1 | 1 | 5.6324 | 10 | 0 | 0
380.4 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.145 | 1.45 | 5.725 | 5.725 | 0 | 12 | 1 | 1 | 5.725 | 10 | 0 | 0
380.45 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.145 | 1.45 | 5.725 | 5.725 | 0 | 12 | 1 | 1 | 5.725 | 10 | 0 | 0
380.5 | 49.96 | 49.79 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
380.55 | 49.96 | 49.79 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
380.6 | 50.02 | 49.79 | 1 | 1 | 10 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 4.9853 | 4.9853 | 0 | 12 | 1 | 1 | 4.9853 | 10 | 0 | 0
380.65 | 50.02 | 49.79 | 1 | 1 | 10 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 4.9853 | 4.9853 | 0 | 12 | 1 | 1 | 4.9853 | 10 | 0 | 0
380.7 | 50.03 | 49.79 | 1 | 1 | 10 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.9559 | 4.9559 | 0 | 12 | 1 | 1 | 4.9559 | 10 | 0 | 0
380.75 | 50.03 | 49.84 | 0.62 | 0.9 | 9 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.4559 | 4.4559 | 0 | 12 | 1 | 1 | 4.4559 | 10 | 0 | 0
380.8 | 50.02 | 49.84 | 0.62 | 0.8 | 8 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 3.9559 | 3.9559 | 0 | 12 | 1 | 1 | 3.9559 | 10 | 0 | 0
380.85 | 50.02 | 49.89 | 0.145 | 0.7 | 7 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 3.4559 | 3.4559 | 0 | 12 | 1 | 1 | 3.4559 | 10 | 0 | 0
380.9 | 50.08 | 49.89 | 0.145 | 0.6 | 6 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 2.8088 | 2.8088 | 0 | 12 | 1 | 1 | 2.8088 | 10 | 0 | 0
380.95 | 50.08 | 49.89 | 0.145 | 0.5 | 5 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 2.3088 | 2.3088 | 0 | 12 | 1 | 1 | 2.3088 | 10 | 0 | 0
381 | 50.01 | 49.89 | 0.145 | 0.4 | 4 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 1.8088 | 1.8088 | 0 | 12 | 1 | 1 | 1.8088 | 10 | 0 | 0
381.05 | 50.01 | 49.96 | 0.014706 | 0.3 | 3 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 1.3088 | 1.3088 | 0 | 12 | 1 | 1 | 1.3088 | 10 | 0 | 0
381.1 | 49.94 | 49.94 | 0.026471 | 0.2 | 2 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.80882 | 0.80882 | 0 | 12 | 1 | 1 | 0.80882 | 10 | 0 | 0
381.15 | 49.94 | 49.94 | 0.026471 | 0.1 | 1 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.30882 | 0.30882 | 0 | 12 | 1 | 1 | 0.30882 | 10 | 0 | 0
381.2 | 50 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
381.25 | 50 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
381.3 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
381.35 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
381.4 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
381.45 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
381.5 | 49.92 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
381.55 | 49.92 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
381.6 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50.01 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
381.65 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
381.7 | 49.92 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
381.75 | 49.92 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
381.8 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
381.85 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
381.9 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
381.95 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
382 | 49.87 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
382.05 | 49.87 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
382.1 | 49.8 | 49.8 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
382.15 | 49.8 | 49.8 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
382.2 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
382.25 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
382.3 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
382.35 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
382.4 | 49.72 | 49.72 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
382.45 | 49.72 | 49.72 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
382.5 | 49.67 | 49.67 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
382.55 | 49.67 | 49.67 | 1 | 1 | 10 | 49.87 | 0.335 | 0.14412 | 1.4412 | 5.7206 | 5.7206 | 0 | 12 | 1 | 1 | 5.7206 | 10 | 0 | 0
382.6 | 49.65 | 49.65 | 1 | 1 | 10 | 49.87 | 0.335 | 0.24412 | 2.4412 | 6.2206 | 6.2206 | 0 | 12 | 1 | 1 | 6.2206 | 10 | 0 | 0
382.65 | 49.65 | 49.65 | 1 | 1 | 10 | 49.8 | 1 | 0.34412 | 3.4412 | 6.7206 | 6.7206 | 0 | 12 | 1 | 1 | 6.7206 | 10 | 0 | 0
382.7 | 49.59 | 49.59 | 1 | 1 | 10 | 49.8 | 1 | 0.44412 | 4.4412 | 7.2206 | 7.2206 | 0 | 12 | 1 | 1 | 7.2206 | 10 | 0 | 0
382.75 | 49.59 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.54412 | 5.4412 | 7.7206 | 7.7206 | 0 | 12 | 1 | 1 | 7.7206 | 10 | 0 | 0
382.8 | 49.66 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.64412 | 6.4412 | 8.2206 | 8.2206 | 0 | 12 | 1 | 1 | 8.2206 | 10 | 0 | 0
382.85 | 49.66 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.74412 | 7.4412 | 8.7206 | 8.7206 | 0 | 12 | 1 | 1 | 8.7206 | 10 | 0 | 0
382.9 | 49.63 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.84412 | 8.4412 | 9.2206 | 9.2206 | 0 | 12 | 1 | 1 | 9.2206 | 10 | 0 | 0
382.95 | 49.63 | 49.59 | 1 | 1 | 10 | 49.72 | 1 | 0.94412 | 9.4412 | 9.7206 | 9.7206 | 0 | 12 | 1 | 1 | 9.7206 | 10 | 0 | 0
383 | 49.61 | 49.59 | 1 | 1 | 10 | 49.72 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
383.05 | 49.61 | 49.59 | 1 | 1 | 10 | 49.67 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
383.1 | 49.54 | 49.54 | 1 | 1 | 10 | 49.67 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
383.15 | 49.54 | 49.54 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
383.2 | 49.46 | 49.46 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
383.25 | 49.46 | 49.46 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
383.3 | 49.45 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
383.35 | 49.45 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
383.4 | 49.51 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
383.45 | 49.51 | 49.45 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
383.5 | 49.5 | 49.45 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
383.55 | 49.5 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
383.6 | 49.54 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
383.65 | 49.54 | 49.45 | 1 | 1 | 10 | 49.54 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
383.7 | 49.59 | 49.45 | 1 | 1 | 10 | 49.59 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
383.75 | 49.59 | 49.45 | 1 | 1 | 10 | 49.59 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
383.8 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
383.85 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
383.9 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
383.95 | 49.61 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
384 | 49.53 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
384.05 | 49.53 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
384.1 | 49.54 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
384.15 | 49.54 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
384.2 | 49.61 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
384.25 | 49.61 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
384.3 | 49.66 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
384.35 | 49.66 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
384.4 | 49.64 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
384.45 | 49.64 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
384.5 | 49.69 | 49.53 | 1 | 1 | 10 | 49.69 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
384.55 | 49.69 | 49.53 | 1 | 1 | 10 | 49.69 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
384.6 | 49.74 | 49.53 | 1 | 1 | 10 | 49.74 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
384.65 | 49.74 | 49.54 | 1 | 1 | 10 | 49.74 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
384.7 | 49.78 | 49.54 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
384.75 | 49.78 | 49.61 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
384.8 | 49.82 | 49.61 | 1 | 1 | 10 | 49.82 | 0.81 | 0.81 | 8.1 | 9.05 | 9.05 | 0 | 12 | 1 | 1 | 9.05 | 10 | 0 | 0
384.85 | 49.82 | 49.64 | 1 | 1 | 10 | 49.82 | 0.81 | 0.81 | 8.1 | 9.05 | 9.05 | 0 | 12 | 1 | 1 | 9.05 | 10 | 0 | 0
384.9 | 49.86 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
384.95 | 49.86 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
385 | 49.84 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
385.05 | 49.84 | 49.69 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
385.1 | 49.91 | 49.69 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
385.15 | 49.91 | 49.74 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
385.2 | 49.97 | 49.74 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
385.25 | 49.97 | 49.78 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
385.3 | 50.03 | 49.78 | 1 | 1 | 10 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.9559 | 4.9559 | 0 | 12 | 1 | 1 | 4.9559 | 10 | 0 | 0
385.35 | 50.03 | 49.82 | 0.81 | 0.9 | 9 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.4559 | 4.4559 | 0 | 12 | 1 | 1 | 4.4559 | 10 | 0 | 0
385.4 | 50.05 | 49.82 | 0.81 | 0.81 | 8.1 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 3.9471 | 3.9471 | 0 | 12 | 1 | 1 | 3.9471 | 10 | 0 | 0
385.45 | 50.05 | 49.84 | 0.62 | 0.71 | 7.1 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 3.4471 | 3.4471 | 0 | 12 | 1 | 1 | 3.4471 | 10 | 0 | 0
385.5 | 50.01 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
385.55 | 50.01 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
385.6 | 49.95 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
385.65 | 49.95 | 49.91 | 0.044118 | 0.52 | 5.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.4971 | 2.4971 | 0 | 12 | 1 | 1 | 2.4971 | 10 | 0 | 0
385.7 | 49.99 | 49.91 | 0.044118 | 0.42 | 4.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 1.9971 | 1.9971 | 0 | 12 | 1 | 1 | 1.9971 | 10 | 0 | 0
385.75 | 49.99 | 49.95 | 0.020588 | 0.32 | 3.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 1.4971 | 1.4971 | 0 | 12 | 1 | 1 | 1.4971 | 10 | 0 | 0
385.8 | 49.92 | 49.92 | 0.038235 | 0.22 | 2.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.99706 | 0.99706 | 0 | 12 | 1 | 1 | 0.99706 | 10 | 0 | 0
385.85 | 49.92 | 49.92 | 0.038235 | 0.12 | 1.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.49706 | 0.49706 | 0 | 12 | 1 | 1 | 0.49706 | 10 | 0 | 0
385.9 | 49.97 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
385.95 | 49.97 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
386 | 50.02 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
386.05 | 50.02 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.17647 | 0.17647 | 0 | 12 | 1 | 1 | 0.17647 | 10 | 0 | 0
386.1 | 50.07 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
386.15 | 50.07 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
386.2 | 50.06 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
386.25 | 50.06 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
386.3 | 50.13 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
386.35 | 50.13 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
386.4 | 50.09 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
386.45 | 50.09 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6309 | -1.6309 | 0 | 12 | 1 | 1 | -1.6309 | 10 | 0 | 0
386.5 | 50.07 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6309 | -1.6309 | 0 | 12 | 1 | 1 | -1.6309 | 10 | 0 | 0
386.55 | 50.07 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6897 | -1.6897 | 0 | 12 | 1 | 1 | -1.6897 | 10 | 0 | 0
386.6 | 50.07 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6897 | -1.6897 | 0 | 12 | 1 | 1 | -1.6897 | 10 | 0 | 0
386.65 | 50.07 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.13 | -0.335 | -0.335 | -3.35 | -1.8074 | -1.8074 | 0 | 12 | 1 | 1 | -1.8074 | 10 | 0 | 0
386.7 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.13 | -0.335 | -0.335 | -3.35 | -1.7779 | -1.7779 | 0 | 12 | 1 | 1 | -1.7779 | 10 | 0 | 0
386.75 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.13 | -0.335 | -0.335 | -3.35 | -1.7779 | -1.7779 | 0 | 12 | 1 | 1 | -1.7779 | 10 | 0 | 0
386.8 | 50.01 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
386.85 | 50.01 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
386.9 | 50.07 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
386.95 | 50.07 | 50.01 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.235 | -2.35 | -1.175 | -1.175 | 0 | 12 | 1 | 1 | -1.175 | 10 | 0 | 0
387 | 50.05 | 50.01 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.135 | -1.35 | -0.675 | -0.675 | 0 | 12 | 1 | 1 | -0.675 | 10 | 0 | 0
387.05 | 50.05 | 50.01 | 0 | 0 | 0 | 50.07 | -0.032353 | -0.035 | -0.35 | -0.175 | -0.175 | 0 | 12 | 1 | 1 | -0.175 | 10 | 0 | 0
387.1 | 50.1 | 50.01 | 0 | 0 | 0 | 50.1 | -0.05 | -0.05 | -0.5 | -0.25 | -0.25 | 0 | 12 | 1 | 1 | -0.25 | 10 | 0 | 0
387.15 | 50.1 | 50.01 | 0 | 0 | 0 | 50.1 | -0.05 | -0.05 | -0.5 | -0.25 | -0.25 | 0 | 12 | 1 | 1 | -0.25 | 10 | 0 | 0
387.2 | 50.11 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
387.25 | 50.11 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
387.3 | 50.06 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
387.35 | 50.06 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
387.4 | 50.04 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
387.45 | 50.04 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
387.5 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
387.55 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
387.6 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
387.65 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
387.7 | 50.11 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
387.75 | 50.11 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
387.8 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
387.85 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
387.9 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
387.95 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
388 | 50.02 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.11 | -0.145 | -0.145 | -1.45 | -0.73971 | -0.73971 | 0 | 12 | 1 | 1 | -0.73971 | 10 | 0 | 0
388.05 | 50.02 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.11 | -0.145 | -0.145 | -1.45 | -0.73971 | -0.73971 | 0 | 12 | 1 | 1 | -0.73971 | 10 | 0 | 0
388.1 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
388.15 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
388.2 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
388.25 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
388.3 | 50.01 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
388.35 | 50.01 | 50 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.045 | -0.45 | -0.225 | -0.225 | 0 | 12 | 1 | 1 | -0.225 | 10 | 0 | 0
388.4 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
388.45 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
388.5 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
388.55 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
388.6 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.14706 | 0.14706 | 0 | 12 | 1 | 1 | 0.14706 | 10 | 0 | 0
388.65 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
388.7 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
388.75 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
388.8 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
388.85 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
388.9 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
388.95 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
389 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
389.05 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
389.1 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
389.15 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
389.2 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
389.25 | 50 | 50 | 0 | 0 | 0 | 50.01 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
389.3 | 49.5 | 49.5 | 1 | 1 | 10 | 50.01 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
389.35 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
389.4 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
389.45 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
389.5 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
389.55 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
389.6 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
389.65 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
389.7 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
389.75 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
389.8 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
389.85 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.1 | 1 | 5.5 | 5.5 | 0 | 12 | 1 | 1 | 5.5 | 10 | 0 | 0
389.9 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.2 | 2 | 6 | 6 | 0 | 12 | 1 | 1 | 6 | 10 | 0 | 0
389.95 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.3 | 3 | 6.5 | 6.5 | 0 | 12 | 1 | 1 | 6.5 | 10 | 0 | 0
390 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.4 | 4 | 7 | 7 | 0 | 12 | 1 | 1 | 7 | 10 | 0 | 0
390.05 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.5 | 5 | 7.5 | 7.5 | 0 | 12 | 1 | 1 | 7.5 | 10 | 0 | 0
390.1 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.6 | 6 | 8 | 8 | 0 | 12 | 1 | 1 | 8 | 10 | 0 | 0
390.15 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.7 | 7 | 8.5 | 8.5 | 0 | 12 | 1 | 1 | 8.5 | 10 | 0 | 0
390.2 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.8 | 8 | 9 | 9 | 0 | 12 | 1 | 1 | 9 | 10 | 0 | 0
390.25 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.9 | 9 | 9.5 | 9.5 | 0 | 12 | 1 | 1 | 9.5 | 10 | 0 | 0
390.3 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
390.35 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
390.4 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
390.45 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
390.5 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
390.55 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
390.6 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
390.65 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
390.7 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
390.75 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
390.8 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
390.85 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
390.9 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
390.95 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
391 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
391.05 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
391.1 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
391.15 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
391.2 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
391.25 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
391.3 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
391.35 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
391.4 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
391.45 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
391.5 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
391.55 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
391.6 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
391.65 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
391.7 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
391.75 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
391.8 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
391.85 | 50.5 | 50.5 | -1 | 0.9 | 9 | 50.5 | -1 | -1 | -10 | -0.5 | -0.5 | 0 | 12 | 1 | 1 | -0.5 | 10 | 0 | 0
391.9 | 50.5 | 50.5 | -1 | 0.8 | 8 | 50.5 | -1 | -1 | -10 | -1 | -1 | 0 | 12 | 1 | 1 | -1 | 10 | 0 | 0
391.95 | 50.5 | 50.5 | -1 | 0.7 | 7 | 50.5 | -1 | -1 | -10 | -1.5 | -1.5 | 0 | 12 | 1 | 1 | -1.5 | 10 | 0 | 0
392 | 50.5 | 50.5 | -1 | 0.6 | 6 | 50.5 | -1 | -1 | -10 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
392.05 | 50.5 | 50.5 | -1 | 0.5 | 5 | 50.5 | -1 | -1 | -10 | -2.5 | -2.5 | 0 | 12 | 1 | 1 | -2.5 | 10 | 0 | 0
392.1 | 50.5 | 50.5 | -1 | 0.4 | 4 | 50.5 | -1 | -1 | -10 | -3 | -3 | 0 | 12 | 1 | 1 | -3 | 10 | 0 | 0
392.15 | 50.5 | 50.5 | -1 | 0.3 | 3 | 50.5 | -1 | -1 | -10 | -3.5 | -3.5 | 0 | 12 | 1 | 1 | -3.5 | 10 | 0 | 0
392.2 | 50.5 | 50.5 | -1 | 0.2 | 2 | 50.5 | -1 | -1 | -10 | -4 | -4 | 0 | 12 | 1 | 1 | -4 | 10 | 0 | 0
392.25 | 50.5 | 50.5 | -1 | 0.1 | 1 | 50.5 | -1 | -1 | -10 | -4.5 | -4.5 | 0 | 12 | 1 | 1 | -4.5 | 10 | 0 | 0
392.3 | 50.5 | 50.5 | -1 | 0 | 0 | 50.5 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
392.35 | 50.5 | 50.5 | -1 | -0.1 | -1 | 50.5 | -1 | -1 | -10 | -5.5 | -5.5 | 0 | 12 | 1 | 1 | -5.5 | 10 | 0 | 0
392.4 | 50.5 | 50.5 | -1 | -0.2 | -2 | 50.5 | -1 | -1 | -10 | -6 | -6 | 0 | 12 | 1 | 1 | -6 | 10 | 0 | 0
392.45 | 50.5 | 50.5 | -1 | -0.3 | -3 | 50.5 | -1 | -1 | -10 | -6.5 | -6.5 | 0 | 12 | 1 | 1 | -6.5 | 10 | 0 | 0
392.5 | 50.5 | 50.5 | -1 | -0.4 | -4 | 50.5 | -1 | -1 | -10 | -7 | -7 | 0 | 12 | 1 | 1 | -7 | 10 | 0 | 0
392.55 | 50.5 | 50.5 | -1 | -0.5 | -5 | 50.5 | -1 | -1 | -10 | -7.5 | -7.5 | 0 | 12 | 1 | 1 | -7.5 | 10 | 0 | 0
392.6 | 50.5 | 50.5 | -1 | -0.6 | -6 | 50.5 | -1 | -1 | -10 | -8 | -8 | 0 | 12 | 1 | 1 | -8 | 10 | 0 | 0
392.65 | 50.5 | 50.5 | -1 | -0.7 | -7 | 50.5 | -1 | -1 | -10 | -8.5 | -8.5 | 0 | 12 | 1 | 1 | -8.5 | 10 | 0 | 0
392.7 | 50.5 | 50.5 | -1 | -0.8 | -8 | 50.5 | -1 | -1 | -10 | -9 | -9 | 0 | 12 | 1 | 1 | -9 | 10 | 0 | 0
392.75 | 50.5 | 50.5 | -1 | -0.9 | -9 | 50.5 | -1 | -1 | -10 | -9.5 | -9.5 | 0 | 12 | 1 | 1 | -9.5 | 10 | 0 | 0
392.8 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
392.85 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
392.9 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
392.95 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
393 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
393.05 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
393.1 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
393.15 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
393.2 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
393.25 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
393.3 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
393.35 | 50.47 | 50.47 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
393.4 | 50.45 | 50.45 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
393.45 | 50.42 | 50.42 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
393.5 | 50.4 | 50.4 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
393.55 | 50.37 | 50.37 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
393.6 | 50.35 | 50.35 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
393.65 | 50.32 | 50.32 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
393.7 | 50.29 | 50.29 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
393.75 | 50.27 | 50.27 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
393.8 | 50.24 | 50.24 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
393.85 | 50.22 | 50.22 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
393.9 | 50.19 | 50.19 | -0.905 | -0.905 | -9.05 | 50.47 | -1 | -1 | -10 | -9.525 | -9.525 | 0 | 12 | 1 | 1 | -9.525 | 10 | 0 | 0
393.95 | 50.17 | 50.17 | -0.715 | -0.715 | -7.15 | 50.45 | -1 | -1 | -10 | -8.575 | -8.575 | 0 | 12 | 1 | 1 | -8.575 | 10 | 0 | 0
394 | 50.14 | 50.14 | -0.43 | -0.43 | -4.3 | 50.42 | -1 | -1 | -10 | -7.15 | -7.15 | 0 | 12 | 1 | 1 | -7.15 | 10 | 0 | 0
394.05 | 50.12 | 50.12 | -0.24 | -0.24 | -2.4 | 50.4 | -1 | -1 | -10 | -6.2 | -6.2 | 0 | 12 | 1 | 1 | -6.2 | 10 | 0 | 0
394.1 | 50.09 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 50.37 | -1 | -1 | -10 | -5.2206 | -5.2206 | 0 | 12 | 1 | 1 | -5.2206 | 10 | 0 | 0
394.15 | 50.06 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.35 | -1 | -1 | -10 | -5.1324 | -5.1324 | 0 | 12 | 1 | 1 | -5.1324 | 10 | 0 | 0
394.2 | 50.04 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.32 | -1 | -1 | -10 | -5.0735 | -5.0735 | 0 | 12 | 1 | 1 | -5.0735 | 10 | 0 | 0
394.25 | 50.01 | 50.01 | 0 | 0 | 0 | 50.29 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
394.3 | 49.99 | 49.99 | 0 | 0 | 0 | 50.27 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
394.35 | 49.96 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.24 | -1 | -1 | -10 | -4.9265 | -4.9265 | 0 | 12 | 1 | 1 | -4.9265 | 10 | 0 | 0
394.4 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.22 | -1 | -1 | -10 | -4.8676 | -4.8676 | 0 | 12 | 1 | 1 | -4.8676 | 10 | 0 | 0
394.45 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.19 | -0.905 | -0.905 | -9.05 | -4.3044 | -4.3044 | 0 | 12 | 1 | 1 | -4.3044 | 10 | 0 | 0
394.5 | 49.88 | 49.88 | 0.24 | 0.24 | 2.4 | 50.17 | -0.715 | -0.805 | -8.05 | -2.825 | -2.825 | 0 | 12 | 1 | 1 | -2.825 | 10 | 0 | 0
394.55 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.14 | -0.43 | -0.705 | -7.05 | -1.375 | -1.375 | 0 | 12 | 1 | 1 | -1.375 | 10 | 0 | 0
394.6 | 49.83 | 49.83 | 0.715 | 0.715 | 7.15 | 50.12 | -0.24 | -0.605 | -6.05 | 0.55 | 0.55 | 0 | 12 | 1 | 1 | 0.55 | 10 | 0 | 0
394.65 | 49.81 | 49.81 | 0.905 | 0.905 | 9.05 | 50.09 | -0.044118 | -0.505 | -5.05 | 2 | 2 | 0 | 12 | 1 | 1 | 2 | 10 | 0 | 0
394.7 | 49.78 | 49.78 | 1 | 1 | 10 | 50.06 | -0.026471 | -0.405 | -4.05 | 2.975 | 2.975 | 0 | 12 | 1 | 1 | 2.975 | 10 | 0 | 0
394.75 | 49.76 | 49.76 | 1 | 1 | 10 | 50.04 | -0.014706 | -0.305 | -3.05 | 3.475 | 3.475 | 0 | 12 | 1 | 1 | 3.475 | 10 | 0 | 0
394.8 | 49.73 | 49.73 | 1 | 1 | 10 | 50.01 | 0 | -0.205 | -2.05 | 3.975 | 3.975 | 0 | 12 | 1 | 1 | 3.975 | 10 | 0 | 0
394.85 | 49.71 | 49.71 | 1 | 1 | 10 | 49.99 | 0 | -0.105 | -1.05 | 4.475 | 4.475 | 0 | 12 | 1 | 1 | 4.475 | 10 | 0 | 0
394.9 | 49.68 | 49.68 | 1 | 1 | 10 | 49.96 | 0.014706 | -0.005 | -0.05 | 4.975 | 4.975 | 0 | 12 | 1 | 1 | 4.975 | 10 | 0 | 0
394.95 | 49.65 | 49.65 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
395 | 49.63 | 49.63 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
395.05 | 49.6 | 49.6 | 1 | 1 | 10 | 49.88 | 0.24 | 0.14412 | 1.4412 | 5.7206 | 5.7206 | 0 | 12 | 1 | 1 | 5.7206 | 10 | 0 | 0
395.1 | 49.58 | 49.58 | 1 | 1 | 10 | 49.86 | 0.43 | 0.24412 | 2.4412 | 6.2206 | 6.2206 | 0 | 12 | 1 | 1 | 6.2206 | 10 | 0 | 0
395.15 | 49.55 | 49.55 | 1 | 1 | 10 | 49.83 | 0.715 | 0.34412 | 3.4412 | 6.7206 | 6.7206 | 0 | 12 | 1 | 1 | 6.7206 | 10 | 0 | 0
395.2 | 49.53 | 49.53 | 1 | 1 | 10 | 49.81 | 0.905 | 0.44412 | 4.4412 | 7.2206 | 7.2206 | 0 | 12 | 1 | 1 | 7.2206 | 10 | 0 | 0
395.25 | 49.5 | 49.5 | 1 | 1 | 10 | 49.78 | 1 | 0.54412 | 5.4412 | 7.7206 | 7.7206 | 0 | 12 | 1 | 1 | 7.7206 | 10 | 0 | 0
395.3 | 49.5 | 49.5 | 1 | 1 | 10 | 49.76 | 1 | 0.64412 | 6.4412 | 8.2206 | 8.2206 | 0 | 12 | 1 | 1 | 8.2206 | 10 | 0 | 0
395.35 | 49.53 | 49.5 | 1 | 1 | 10 | 49.73 | 1 | 0.74412 | 7.4412 | 8.7206 | 8.7206 | 0 | 12 | 1 | 1 | 8.7206 | 10 | 0 | 0
395.4 | 49.55 | 49.5 | 1 | 1 | 10 | 49.71 | 1 | 0.84412 | 8.4412 | 9.2206 | 9.2206 | 0 | 12 | 1 | 1 | 9.2206 | 10 | 0 | 0
395.45 | 49.58 | 49.5 | 1 | 1 | 10 | 49.68 | 1 | 0.94412 | 9.4412 | 9.7206 | 9.7206 | 0 | 12 | 1 | 1 | 9.7206 | 10 | 0 | 0
395.5 | 49.6 | 49.5 | 1 | 1 | 10 | 49.65 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
395.55 | 49.63 | 49.5 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
395.6 | 49.65 | 49.5 | 1 | 1 | 10 | 49.65 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
395.65 | 49.68 | 49.5 | 1 | 1 | 10 | 49.68 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
395.7 | 49.71 | 49.5 | 1 | 1 | 10 | 49.71 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
395.75 | 49.73 | 49.5 | 1 | 1 | 10 | 49.73 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
395.8 | 49.76 | 49.5 | 1 | 1 | 10 | 49.76 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
395.85 | 49.78 | 49.5 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
395.9 | 49.81 | 49.53 | 1 | 1 | 10 | 49.81 | 0.905 | 0.905 | 9.05 | 9.525 | 9.525 | 0 | 12 | 1 | 1 | 9.525 | 10 | 0 | 0
395.95 | 49.83 | 49.55 | 1 | 1 | 10 | 49.83 | 0.715 | 0.715 | 7.15 | 8.575 | 8.575 | 0 | 12 | 1 | 1 | 8.575 | 10 | 0 | 0
396 | 49.86 | 49.58 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
396.05 | 49.88 | 49.6 | 1 | 1 | 10 | 49.88 | 0.24 | 0.24 | 2.4 | 6.2 | 6.2 | 0 | 12 | 1 | 1 | 6.2 | 10 | 0 | 0
396.1 | 49.91 | 49.63 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
396.15 | 49.94 | 49.65 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
396.2 | 49.96 | 49.68 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
396.25 | 49.99 | 49.71 | 1 | 1 | 10 | 49.99 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
396.3 | 50.01 | 49.73 | 1 | 1 | 10 | 50.01 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
396.35 | 50.04 | 49.76 | 1 | 1 | 10 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 4.9265 | 4.9265 | 0 | 12 | 1 | 1 | 4.9265 | 10 | 0 | 0
396.4 | 50.06 | 49.78 | 1 | 1 | 10 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 4.8676 | 4.8676 | 0 | 12 | 1 | 1 | 4.8676 | 10 | 0 | 0
396.45 | 50.09 | 49.81 | 0.905 | 0.905 | 9.05 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 4.3044 | 4.3044 | 0 | 12 | 1 | 1 | 4.3044 | 10 | 0 | 0
396.5 | 50.12 | 49.83 | 0.715 | 0.805 | 8.05 | 50.12 | -0.24 | -0.24 | -2.4 | 2.825 | 2.825 | 0 | 12 | 1 | 1 | 2.825 | 10 | 0 | 0
396.55 | 50.14 | 49.86 | 0.43 | 0.705 | 7.05 | 50.14 | -0.43 | -0.43 | -4.3 | 1.375 | 1.375 | 0 | 12 | 1 | 1 | 1.375 | 10 | 0 | 0
396.6 | 50.17 | 49.88 | 0.24 | 0.605 | 6.05 | 50.17 | -0.715 | -0.715 | -7.15 | -0.55 | -0.55 | 0 | 12 | 1 | 1 | -0.55 | 10 | 0 | 0
396.65 | 50.19 | 49.91 | 0.044118 | 0.505 | 5.05 | 50.19 | -0.905 | -0.905 | -9.05 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
396.7 | 50.22 | 49.94 | 0.026471 | 0.405 | 4.05 | 50.22 | -1 | -1 | -10 | -2.975 | -2.975 | 0 | 12 | 1 | 1 | -2.975 | 10 | 0 | 0
396.75 | 50.24 | 49.96 | 0.014706 | 0.305 | 3.05 | 50.24 | -1 | -1 | -10 | -3.475 | -3.475 | 0 | 12 | 1 | 1 | -3.475 | 10 | 0 | 0
396.8 | 50.27 | 49.99 | 0 | 0.205 | 2.05 | 50.27 | -1 | -1 | -10 | -3.975 | -3.975 | 0 | 12 | 1 | 1 | -3.975 | 10 | 0 | 0
396.85 | 50.29 | 50.01 | 0 | 0.105 | 1.05 | 50.29 | -1 | -1 | -10 | -4.475 | -4.475 | 0 | 12 | 1 | 1 | -4.475 | 10 | 0 | 0
396.9 | 50.32 | 50.04 | -0.014706 | 0.005 | 0.05 | 50.32 | -1 | -1 | -10 | -4.975 | -4.975 | 0 | 12 | 1 | 1 | -4.975 | 10 | 0 | 0
396.95 | 50.35 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.35 | -1 | -1 | -10 | -5.1324 | -5.1324 | 0 | 12 | 1 | 1 | -5.1324 | 10 | 0 | 0
397 | 50.37 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 50.37 | -1 | -1 | -10 | -5.2206 | -5.2206 | 0 | 12 | 1 | 1 | -5.2206 | 10 | 0 | 0
397.05 | 50.4 | 50.12 | -0.24 | -0.14412 | -1.4412 | 50.4 | -1 | -1 | -10 | -5.7206 | -5.7206 | 0 | 12 | 1 | 1 | -5.7206 | 10 | 0 | 0
397.1 | 50.42 | 50.14 | -0.43 | -0.24412 | -2.4412 | 50.42 | -1 | -1 | -10 | -6.2206 | -6.2206 | 0 | 12 | 1 | 1 | -6.2206 | 10 | 0 | 0
397.15 | 50.45 | 50.17 | -0.715 | -0.34412 | -3.4412 | 50.45 | -1 | -1 | -10 | -6.7206 | -6.7206 | 0 | 12 | 1 | 1 | -6.7206 | 10 | 0 | 0
397.2 | 50.47 | 50.19 | -0.905 | -0.44412 | -4.4412 | 50.47 | -1 | -1 | -10 | -7.2206 | -7.2206 | 0 | 12 | 1 | 1 | -7.2206 | 10 | 0 | 0
397.25 | 50.5 | 50.22 | -1 | -0.54412 | -5.4412 | 50.5 | -1 | -1 | -10 | -7.7206 | -7.7206 | 0 | 12 | 1 | 1 | -7.7206 | 10 | 0 | 0
397.3 | 50.5 | 50.24 | -1 | -0.64412 | -6.4412 | 50.5 | -1 | -1 | -10 | -8.2206 | -8.2206 | 0 | 12 | 1 | 1 | -8.2206 | 10 | 0 | 0
397.35 | 50.47 | 50.27 | -1 | -0.74412 | -7.4412 | 50.5 | -1 | -1 | -10 | -8.7206 | -8.7206 | 0 | 12 | 1 | 1 | -8.7206 | 10 | 0 | 0
397.4 | 50.45 | 50.29 | -1 | -0.84412 | -8.4412 | 50.5 | -1 | -1 | -10 | -9.2206 | -9.2206 | 0 | 12 | 1 | 1 | -9.2206 | 10 | 0 | 0
397.45 | 50.42 | 50.32 | -1 | -0.94412 | -9.4412 | 50.5 | -1 | -1 | -10 | -9.7206 | -9.7206 | 0 | 12 | 1 | 1 | -9.7206 | 10 | 0 | 0
397.5 | 50.39 | 50.35 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
397.55 | 50.37 | 50.37 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
397.6 | 50.34 | 50.34 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
397.65 | 50.32 | 50.32 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
397.7 | 50.29 | 50.29 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
397.75 | 50.26 | 50.26 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
397.8 | 50.24 | 50.24 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
397.85 | 50.21 | 50.21 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
397.9 | 50.18 | 50.18 | -0.81 | -0.81 | -8.1 | 50.47 | -1 | -1 | -10 | -9.05 | -9.05 | 0 | 12 | 1 | 1 | -9.05 | 10 | 0 | 0
397.95 | 50.16 | 50.16 | -0.62 | -0.62 | -6.2 | 50.45 | -1 | -1 | -10 | -8.1 | -8.1 | 0 | 12 | 1 | 1 | -8.1 | 10 | 0 | 0
398 | 50.13 | 50.13 | -0.335 | -0.335 | -3.35 | 50.42 | -1 | -1 | -10 | -6.675 | -6.675 | 0 | 12 | 1 | 1 | -6.675 | 10 | 0 | 0
398.05 | 50.11 | 50.11 | -0.145 | -0.145 | -1.45 | 50.39 | -1 | -1 | -10 | -5.725 | -5.725 | 0 | 12 | 1 | 1 | -5.725 | 10 | 0 | 0
398.1 | 50.08 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 50.37 | -1 | -1 | -10 | -5.1912 | -5.1912 | 0 | 12 | 1 | 1 | -5.1912 | 10 | 0 | 0
398.15 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.34 | -1 | -1 | -10 | -5.1029 | -5.1029 | 0 | 12 | 1 | 1 | -5.1029 | 10 | 0 | 0
398.2 | 50.03 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 50.32 | -1 | -1 | -10 | -5.0441 | -5.0441 | 0 | 12 | 1 | 1 | -5.0441 | 10 | 0 | 0
398.25 | 50 | 50 | 0 | 0 | 0 | 50.29 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
398.3 | 50 | 50 | 0 | 0 | 0 | 50.26 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
398.35 | 50 | 50 | 0 | 0 | 0 | 50.24 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
398.4 | 50 | 50 | 0 | 0 | 0 | 50.21 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
398.45 | 50 | 50 | 0 | 0 | 0 | 50.18 | -0.81 | -0.9 | -9 | -4.5 | -4.5 | 0 | 12 | 1 | 1 | -4.5 | 10 | 0 | 0
398.5 | 50 | 50 | 0 | 0 | 0 | 50.16 | -0.62 | -0.8 | -8 | -4 | -4 | 0 | 12 | 1 | 1 | -4 | 10 | 0 | 0
398.55 | 50 | 50 | 0 | 0 | 0 | 50.13 | -0.335 | -0.7 | -7 | -3.5 | -3.5 | 0 | 12 | 1 | 1 | -3.5 | 10 | 0 | 0
398.6 | 50.01 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.6 | -6 | -3 | -3 | 0 | 12 | 1 | 1 | -3 | 10 | 0 | 0
398.65 | 50.01 | 50 | 0 | 0 | 0 | 50.08 | -0.038235 | -0.5 | -5 | -2.5 | -2.5 | 0 | 12 | 1 | 1 | -2.5 | 10 | 0 | 0
398.7 | 49.99 | 49.99 | 0 | 0 | 0 | 50.05 | -0.020588 | -0.4 | -4 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
398.75 | 49.99 | 49.99 | 0 | 0 | 0 | 50.03 | -0.0088235 | -0.3 | -3 | -1.5 | -1.5 | 0 | 12 | 1 | 1 | -1.5 | 10 | 0 | 0
398.8 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | -0.2 | -2 | -0.83824 | -0.83824 | 0 | 12 | 1 | 1 | -0.83824 | 10 | 0 | 0
398.85 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | -0.1 | -1 | -0.33824 | -0.33824 | 0 | 12 | 1 | 1 | -0.33824 | 10 | 0 | 0
398.9 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
398.95 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
399 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
399.05 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
399.1 | 49.89 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
399.15 | 49.89 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
399.2 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50.01 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
399.25 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
399.3 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
399.35 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 2.7868 | 2.7868 | 0 | 12 | 1 | 1 | 2.7868 | 10 | 0 | 0
399.4 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 2.7868 | 2.7868 | 0 | 12 | 1 | 1 | 2.7868 | 10 | 0 | 0
399.45 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 2.8456 | 2.8456 | 0 | 12 | 1 | 1 | 2.8456 | 10 | 0 | 0
399.5 | 49.94 | 49.85 | 0.525 | 0.525 | 5.25 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 2.7574 | 2.7574 | 0 | 12 | 1 | 1 | 2.7574 | 10 | 0 | 0
399.55 | 49.94 | 49.85 | 0.525 | 0.525 | 5.25 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 2.7574 | 2.7574 | 0 | 12 | 1 | 1 | 2.7574 | 10 | 0 | 0
399.6 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
399.65 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
399.7 | 49.93 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
399.75 | 49.93 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
399.8 | 49.96 | 49.85 | 0.525 | 0.525 | 5.25 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 2.6985 | 2.6985 | 0 | 12 | 1 | 1 | 2.6985 | 10 | 0 | 0
399.85 | 49.96 | 49.85 | 0.525 | 0.525 | 5.25 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 2.6985 | 2.6985 | 0 | 12 | 1 | 1 | 2.6985 | 10 | 0 | 0
399.9 | 49.99 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
399.95 | 49.99 | 49.91 | 0.044118 | 0.425 | 4.25 | 49.99 | 0 | 0 | 0 | 2.125 | 2.125 | 0 | 12 | 1 | 1 | 2.125 | 10 | 0 | 0
400 | 49.99 | 49.91 | 0.044118 | 0.325 | 3.25 | 49.99 | 0 | 0 | 0 | 1.625 | 1.625 | 0 | 12 | 1 | 1 | 1.625 | 10 | 0 | 0
400.05 | 49.99 | 49.93 | 0.032353 | 0.225 | 2.25 | 49.99 | 0 | 0 | 0 | 1.125 | 1.125 | 0 | 12 | 1 | 1 | 1.125 | 10 | 0 | 0
400.1 | 49.96 | 49.93 | 0.032353 | 0.125 | 1.25 | 49.99 | 0 | 0 | 0 | 0.625 | 0.625 | 0 | 12 | 1 | 1 | 0.625 | 10 | 0 | 0
400.15 | 49.96 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 49.99 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
400.2 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
400.25 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
400.3 | 50.05 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.058824 | 0.058824 | 0 | 12 | 1 | 1 | 0.058824 | 10 | 0 | 0
400.35 | 50.05 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
400.4 | 49.97 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
400.45 | 49.97 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
400.5 | 49.92 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
400.55 | 49.92 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
400.6 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
400.65 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
400.7 | 49.94 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
400.75 | 49.94 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
400.8 | 50.01 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
400.85 | 50.01 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
400.9 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
400.95 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
401 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
401.05 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
401.1 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
401.15 | 49.95 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
401.2 | 49.97 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
401.25 | 49.97 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
401.3 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
401.35 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
401.4 | 49.87 | 49.87 | 0.335 | 0.335 | 3.35 | 50.01 | 0 | 0 | 0 | 1.675 | 1.675 | 0 | 12 | 1 | 1 | 1.675 | 10 | 0 | 0
401.45 | 49.87 | 49.87 | 0.335 | 0.335 | 3.35 | 49.99 | 0 | 0 | 0 | 1.675 | 1.675 | 0 | 12 | 1 | 1 | 1.675 | 10 | 0 | 0
401.5 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
401.55 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 2.6691 | 2.6691 | 0 | 12 | 1 | 1 | 2.6691 | 10 | 0 | 0
401.6 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
401.65 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
401.7 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
401.75 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
401.8 | 49.84 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
401.85 | 49.84 | 49.79 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
401.9 | 49.89 | 49.79 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
401.95 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.12647 | 1.2647 | 5.6324 | 5.6324 | 0 | 12 | 1 | 1 | 5.6324 | 10 | 0 | 0
402 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.145 | 1.45 | 5.725 | 5.725 | 0 | 12 | 1 | 1 | 5.725 | 10 | 0 | 0
402.05 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.145 | 1.45 | 5.725 | 5.725 | 0 | 12 | 1 | 1 | 5.725 | 10 | 0 | 0
402.1 | 49.96 | 49.79 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
402.15 | 49.96 | 49.79 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
402.2 | 50.02 | 49.79 | 1 | 1 | 10 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 4.9853 | 4.9853 | 0 | 12 | 1 | 1 | 4.9853 | 10 | 0 | 0
402.25 | 50.02 | 49.79 | 1 | 1 | 10 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 4.9853 | 4.9853 | 0 | 12 | 1 | 1 | 4.9853 | 10 | 0 | 0
402.3 | 50.03 | 49.79 | 1 | 1 | 10 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.9559 | 4.9559 | 0 | 12 | 1 | 1 | 4.9559 | 10 | 0 | 0
402.35 | 50.03 | 49.84 | 0.62 | 0.9 | 9 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.4559 | 4.4559 | 0 | 12 | 1 | 1 | 4.4559 | 10 | 0 | 0
402.4 | 50.02 | 49.84 | 0.62 | 0.8 | 8 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 3.9559 | 3.9559 | 0 | 12 | 1 | 1 | 3.9559 | 10 | 0 | 0
402.45 | 50.02 | 49.89 | 0.145 | 0.7 | 7 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 3.4559 | 3.4559 | 0 | 12 | 1 | 1 | 3.4559 | 10 | 0 | 0
402.5 | 50.08 | 49.89 | 0.145 | 0.6 | 6 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 2.8088 | 2.8088 | 0 | 12 | 1 | 1 | 2.8088 | 10 | 0 | 0
402.55 | 50.08 | 49.89 | 0.145 | 0.5 | 5 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 2.3088 | 2.3088 | 0 | 12 | 1 | 1 | 2.3088 | 10 | 0 | 0
402.6 | 50.01 | 49.89 | 0.145 | 0.4 | 4 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 1.8088 | 1.8088 | 0 | 12 | 1 | 1 | 1.8088 | 10 | 0 | 0
402.65 | 50.01 | 49.96 | 0.014706 | 0.3 | 3 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 1.3088 | 1.3088 | 0 | 12 | 1 | 1 | 1.3088 | 10 | 0 | 0
402.7 | 49.94 | 49.94 | 0.026471 | 0.2 | 2 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.80882 | 0.80882 | 0 | 12 | 1 | 1 | 0.80882 | 10 | 0 | 0
402.75 | 49.94 | 49.94 | 0.026471 | 0.1 | 1 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.30882 | 0.30882 | 0 | 12 | 1 | 1 | 0.30882 | 10 | 0 | 0
402.8 | 50 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
402.85 | 50 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
402.9 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
402.95 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
403 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
403.05 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
403.1 | 49.92 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
403.15 | 49.92 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
403.2 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50.01 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
403.25 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
403.3 | 49.92 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
403.35 | 49.92 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
403.4 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
403.45 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
403.5 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
403.55 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
403.6 | 49.87 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
403.65 | 49.87 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
403.7 | 49.8 | 49.8 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
403.75 | 49.8 | 49.8 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
403.8 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
403.85 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
403.9 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
403.95 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
404 | 49.72 | 49.72 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
404.05 | 49.72 | 49.72 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
404.1 | 49.67 | 49.67 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
404.15 | 49.67 | 49.67 | 1 | 1 | 10 | 49.87 | 0.335 | 0.14412 | 1.4412 | 5.7206 | 5.7206 | 0 | 12 | 1 | 1 | 5.7206 | 10 | 0 | 0
404.2 | 49.65 | 49.65 | 1 | 1 | 10 | 49.87 | 0.335 | 0.24412 | 2.4412 | 6.2206 | 6.2206 | 0 | 12 | 1 | 1 | 6.2206 | 10 | 0 | 0
404.25 | 49.65 | 49.65 | 1 | 1 | 10 | 49.8 | 1 | 0.34412 | 3.4412 | 6.7206 | 6.7206 | 0 | 12 | 1 | 1 | 6.7206 | 10 | 0 | 0
404.3 | 49.59 | 49.59 | 1 | 1 | 10 | 49.8 | 1 | 0.44412 | 4.4412 | 7.2206 | 7.2206 | 0 | 12 | 1 | 1 | 7.2206 | 10 | 0 | 0
404.35 | 49.59 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.54412 | 5.4412 | 7.7206 | 7.7206 | 0 | 12 | 1 | 1 | 7.7206 | 10 | 0 | 0
404.4 | 49.66 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.64412 | 6.4412 | 8.2206 | 8.2206 | 0 | 12 | 1 | 1 | 8.2206 | 10 | 0 | 0
404.45 | 49.66 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.74412 | 7.4412 | 8.7206 | 8.7206 | 0 | 12 | 1 | 1 | 8.7206 | 10 | 0 | 0
404.5 | 49.63 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.84412 | 8.4412 | 9.2206 | 9.2206 | 0 | 12 | 1 | 1 | 9.2206 | 10 | 0 | 0
404.55 | 49.63 | 49.59 | 1 | 1 | 10 | 49.72 | 1 | 0.94412 | 9.4412 | 9.7206 | 9.7206 | 0 | 12 | 1 | 1 | 9.7206 | 10 | 0 | 0
404.6 | 49.61 | 49.59 | 1 | 1 | 10 | 49.72 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
404.65 | 49.61 | 49.59 | 1 | 1 | 10 | 49.67 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
404.7 | 49.54 | 49.54 | 1 | 1 | 10 | 49.67 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
404.75 | 49.54 | 49.54 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
404.8 | 49.46 | 49.46 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
404.85 | 49.46 | 49.46 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
404.9 | 49.45 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
404.95 | 49.45 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
405 | 49.51 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
405.05 | 49.51 | 49.45 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
405.1 | 49.5 | 49.45 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
405.15 | 49.5 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
405.2 | 49.54 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
405.25 | 49.54 | 49.45 | 1 | 1 | 10 | 49.54 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
405.3 | 49.59 | 49.45 | 1 | 1 | 10 | 49.59 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
405.35 | 49.59 | 49.45 | 1 | 1 | 10 | 49.59 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
405.4 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
405.45 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
405.5 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
405.55 | 49.61 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
405.6 | 49.53 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
405.65 | 49.53 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
405.7 | 49.54 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
405.75 | 49.54 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
405.8 | 49.61 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
405.85 | 49.61 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
405.9 | 49.66 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
405.95 | 49.66 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
406 | 49.64 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
406.05 | 49.64 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
406.1 | 49.69 | 49.53 | 1 | 1 | 10 | 49.69 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
406.15 | 49.69 | 49.53 | 1 | 1 | 10 | 49.69 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
406.2 | 49.74 | 49.53 | 1 | 1 | 10 | 49.74 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
406.25 | 49.74 | 49.54 | 1 | 1 | 10 | 49.74 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
406.3 | 49.78 | 49.54 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
406.35 | 49.78 | 49.61 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
406.4 | 49.82 | 49.61 | 1 | 1 | 10 | 49.82 | 0.81 | 0.81 | 8.1 | 9.05 | 9.05 | 0 | 12 | 1 | 1 | 9.05 | 10 | 0 | 0
406.45 | 49.82 | 49.64 | 1 | 1 | 10 | 49.82 | 0.81 | 0.81 | 8.1 | 9.05 | 9.05 | 0 | 12 | 1 | 1 | 9.05 | 10 | 0 | 0
406.5 | 49.86 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
406.55 | 49.86 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
406.6 | 49.84 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
406.65 | 49.84 | 49.69 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
406.7 | 49.91 | 49.69 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
406.75 | 49.91 | 49.74 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
406.8 | 49.97 | 49.74 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
406.85 | 49.97 | 49.78 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
406.9 | 50.03 | 49.78 | 1 | 1 | 10 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.9559 | 4.9559 | 0 | 12 | 1 | 1 | 4.9559 | 10 | 0 | 0
406.95 | 50.03 | 49.82 | 0.81 | 0.9 | 9 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.4559 | 4.4559 | 0 | 12 | 1 | 1 | 4.4559 | 10 | 0 | 0
407 | 50.05 | 49.82 | 0.81 | 0.81 | 8.1 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 3.9471 | 3.9471 | 0 | 12 | 1 | 1 | 3.9471 | 10 | 0 | 0
407.05 | 50.05 | 49.84 | 0.62 | 0.71 | 7.1 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 3.4471 | 3.4471 | 0 | 12 | 1 | 1 | 3.4471 | 10 | 0 | 0
407.1 | 50.01 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
407.15 | 50.01 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
407.2 | 49.95 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
407.25 | 49.95 | 49.91 | 0.044118 | 0.52 | 5.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.4971 | 2.4971 | 0 | 12 | 1 | 1 | 2.4971 | 10 | 0 | 0
407.3 | 49.99 | 49.91 | 0.044118 | 0.42 | 4.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 1.9971 | 1.9971 | 0 | 12 | 1 | 1 | 1.9971 | 10 | 0 | 0
407.35 | 49.99 | 49.95 | 0.020588 | 0.32 | 3.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 1.4971 | 1.4971 | 0 | 12 | 1 | 1 | 1.4971 | 10 | 0 | 0
407.4 | 49.92 | 49.92 | 0.038235 | 0.22 | 2.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.99706 | 0.99706 | 0 | 12 | 1 | 1 | 0.99706 | 10 | 0 | 0
407.45 | 49.92 | 49.92 | 0.038235 | 0.12 | 1.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.49706 | 0.49706 | 0 | 12 | 1 | 1 | 0.49706 | 10 | 0 | 0
407.5 | 49.97 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
407.55 | 49.97 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
407.6 | 50.02 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
407.65 | 50.02 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.17647 | 0.17647 | 0 | 12 | 1 | 1 | 0.17647 | 10 | 0 | 0
407.7 | 50.07 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
407.75 | 50.07 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
407.8 | 50.06 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
407.85 | 50.06 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
407.9 | 50.13 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
407.95 | 50.13 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
408 | 50.09 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
408.05 | 50.09 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6309 | -1.6309 | 0 | 12 | 1 | 1 | -1.6309 | 10 | 0 | 0
408.1 | 50.07 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6309 | -1.6309 | 0 | 12 | 1 | 1 | -1.6309 | 10 | 0 | 0
408.15 | 50.07 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6897 | -1.6897 | 0 | 12 | 1 | 1 | -1.6897 | 10 | 0 | 0
408.2 | 50.07 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6897 | -1.6897 | 0 | 12 | 1 | 1 | -1.6897 | 10 | 0 | 0
408.25 | 50.07 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.13 | -0.335 | -0.335 | -3.35 | -1.8074 | -1.8074 | 0 | 12 | 1 | 1 | -1.8074 | 10 | 0 | 0
408.3 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.13 | -0.335 | -0.335 | -3.35 | -1.7779 | -1.7779 | 0 | 12 | 1 | 1 | -1.7779 | 10 | 0 | 0
408.35 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.13 | -0.335 | -0.335 | -3.35 | -1.7779 | -1.7779 | 0 | 12 | 1 | 1 | -1.7779 | 10 | 0 | 0
408.4 | 50.01 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
408.45 | 50.01 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
408.5 | 50.07 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
408.55 | 50.07 | 50.01 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.235 | -2.35 | -1.175 | -1.175 | 0 | 12 | 1 | 1 | -1.175 | 10 | 0 | 0
408.6 | 50.05 | 50.01 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.135 | -1.35 | -0.675 | -0.675 | 0 | 12 | 1 | 1 | -0.675 | 10 | 0 | 0
408.65 | 50.05 | 50.01 | 0 | 0 | 0 | 50.07 | -0.032353 | -0.035 | -0.35 | -0.175 | -0.175 | 0 | 12 | 1 | 1 | -0.175 | 10 | 0 | 0
408.7 | 50.1 | 50.01 | 0 | 0 | 0 | 50.1 | -0.05 | -0.05 | -0.5 | -0.25 | -0.25 | 0 | 12 | 1 | 1 | -0.25 | 10 | 0 | 0
408.75 | 50.1 | 50.01 | 0 | 0 | 0 | 50.1 | -0.05 | -0.05 | -0.5 | -0.25 | -0.25 | 0 | 12 | 1 | 1 | -0.25 | 10 | 0 | 0
408.8 | 50.11 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
408.85 | 50.11 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
408.9 | 50.06 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
408.95 | 50.06 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
409 | 50.04 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
409.05 | 50.04 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
409.1 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
409.15 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
409.2 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
409.25 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
409.3 | 50.11 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
409.35 | 50.11 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
409.4 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
409.45 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
409.5 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
409.55 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
409.6 | 50.02 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.11 | -0.145 | -0.145 | -1.45 | -0.73971 | -0.73971 | 0 | 12 | 1 | 1 | -0.73971 | 10 | 0 | 0
409.65 | 50.02 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.11 | -0.145 | -0.145 | -1.45 | -0.73971 | -0.73971 | 0 | 12 | 1 | 1 | -0.73971 | 10 | 0 | 0
409.7 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
409.75 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
409.8 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
409.85 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
409.9 | 50.01 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
409.95 | 50.01 | 50 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.045 | -0.45 | -0.225 | -0.225 | 0 | 12 | 1 | 1 | -0.225 | 10 | 0 | 0
410 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
410.05 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
410.1 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
410.15 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
410.2 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.14706 | 0.14706 | 0 | 12 | 1 | 1 | 0.14706 | 10 | 0 | 0
410.25 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
410.3 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
410.35 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
410.4 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
410.45 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
410.5 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
410.55 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
410.6 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
410.65 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
410.7 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
410.75 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
410.8 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
410.85 | 50 | 50 | 0 | 0 | 0 | 50.01 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
410.9 | 49.5 | 49.5 | 1 | 1 | 10 | 50.01 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
410.95 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
411 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
411.05 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
411.1 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
411.15 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
411.2 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
411.25 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
411.3 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
411.35 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
411.4 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
411.45 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.1 | 1 | 5.5 | 5.5 | 0 | 12 | 1 | 1 | 5.5 | 10 | 0 | 0
411.5 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.2 | 2 | 6 | 6 | 0 | 12 | 1 | 1 | 6 | 10 | 0 | 0
411.55 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.3 | 3 | 6.5 | 6.5 | 0 | 12 | 1 | 1 | 6.5 | 10 | 0 | 0
411.6 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.4 | 4 | 7 | 7 | 0 | 12 | 1 | 1 | 7 | 10 | 0 | 0
411.65 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.5 | 5 | 7.5 | 7.5 | 0 | 12 | 1 | 1 | 7.5 | 10 | 0 | 0
411.7 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.6 | 6 | 8 | 8 | 0 | 12 | 1 | 1 | 8 | 10 | 0 | 0
411.75 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.7 | 7 | 8.5 | 8.5 | 0 | 12 | 1 | 1 | 8.5 | 10 | 0 | 0
411.8 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.8 | 8 | 9 | 9 | 0 | 12 | 1 | 1 | 9 | 10 | 0 | 0
411.85 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.9 | 9 | 9.5 | 9.5 | 0 | 12 | 1 | 1 | 9.5 | 10 | 0 | 0
411.9 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
411.95 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
412 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
412.05 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
412.1 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
412.15 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
412.2 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
412.25 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
412.3 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
412.35 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
412.4 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
412.45 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
412.5 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
412.55 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
412.6 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
412.65 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
412.7 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
412.75 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
412.8 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
412.85 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
412.9 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
412.95 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
413 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
413.05 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
413.1 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
413.15 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
413.2 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
413.25 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
413.3 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
413.35 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
413.4 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
413.45 | 50.5 | 50.5 | -1 | 0.9 | 9 | 50.5 | -1 | -1 | -10 | -0.5 | -0.5 | 0 | 12 | 1 | 1 | -0.5 | 10 | 0 | 0
413.5 | 50.5 | 50.5 | -1 | 0.8 | 8 | 50.5 | -1 | -1 | -10 | -1 | -1 | 0 | 12 | 1 | 1 | -1 | 10 | 0 | 0
413.55 | 50.5 | 50.5 | -1 | 0.7 | 7 | 50.5 | -1 | -1 | -10 | -1.5 | -1.5 | 0 | 12 | 1 | 1 | -1.5 | 10 | 0 | 0
413.6 | 50.5 | 50.5 | -1 | 0.6 | 6 | 50.5 | -1 | -1 | -10 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
413.65 | 50.5 | 50.5 | -1 | 0.5 | 5 | 50.5 | -1 | -1 | -10 | -2.5 | -2.5 | 0 | 12 | 1 | 1 | -2.5 | 10 | 0 | 0
413.7 | 50.5 | 50.5 | -1 | 0.4 | 4 | 50.5 | -1 | -1 | -10 | -3 | -3 | 0 | 12 | 1 | 1 | -3 | 10 | 0 | 0
413.75 | 50.5 | 50.5 | -1 | 0.3 | 3 | 50.5 | -1 | -1 | -10 | -3.5 | -3.5 | 0 | 12 | 1 | 1 | -3.5 | 10 | 0 | 0
413.8 | 50.5 | 50.5 | -1 | 0.2 | 2 | 50.5 | -1 | -1 | -10 | -4 | -4 | 0 | 12 | 1 | 1 | -4 | 10 | 0 | 0
413.85 | 50.5 | 50.5 | -1 | 0.1 | 1 | 50.5 | -1 | -1 | -10 | -4.5 | -4.5 | 0 | 12 | 1 | 1 | -4.5 | 10 | 0 | 0
413.9 | 50.5 | 50.5 | -1 | 0 | 0 | 50.5 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
413.95 | 50.5 | 50.5 | -1 | -0.1 | -1 | 50.5 | -1 | -1 | -10 | -5.5 | -5.5 | 0 | 12 | 1 | 1 | -5.5 | 10 | 0 | 0
414 | 50.5 | 50.5 | -1 | -0.2 | -2 | 50.5 | -1 | -1 | -10 | -6 | -6 | 0 | 12 | 1 | 1 | -6 | 10 | 0 | 0
414.05 | 50.5 | 50.5 | -1 | -0.3 | -3 | 50.5 | -1 | -1 | -10 | -6.5 | -6.5 | 0 | 12 | 1 | 1 | -6.5 | 10 | 0 | 0
414.1 | 50.5 | 50.5 | -1 | -0.4 | -4 | 50.5 | -1 | -1 | -10 | -7 | -7 | 0 | 12 | 1 | 1 | -7 | 10 | 0 | 0
414.15 | 50.5 | 50.5 | -1 | -0.5 | -5 | 50.5 | -1 | -1 | -10 | -7.5 | -7.5 | 0 | 12 | 1 | 1 | -7.5 | 10 | 0 | 0
414.2 | 50.5 | 50.5 | -1 | -0.6 | -6 | 50.5 | -1 | -1 | -10 | -8 | -8 | 0 | 12 | 1 | 1 | -8 | 10 | 0 | 0
414.25 | 50.5 | 50.5 | -1 | -0.7 | -7 | 50.5 | -1 | -1 | -10 | -8.5 | -8.5 | 0 | 12 | 1 | 1 | -8.5 | 10 | 0 | 0
414.3 | 50.5 | 50.5 | -1 | -0.8 | -8 | 50.5 | -1 | -1 | -10 | -9 | -9 | 0 | 12 | 1 | 1 | -9 | 10 | 0 | 0
414.35 | 50.5 | 50.5 | -1 | -0.9 | -9 | 50.5 | -1 | -1 | -10 | -9.5 | -9.5 | 0 | 12 | 1 | 1 | -9.5 | 10 | 0 | 0
414.4 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
414.45 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
414.5 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
414.55 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
414.6 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
414.65 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
414.7 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
414.75 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
414.8 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
414.85 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
414.9 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
414.95 | 50.47 | 50.47 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
415 | 50.45 | 50.45 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
415.05 | 50.42 | 50.42 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
415.1 | 50.4 | 50.4 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
415.15 | 50.37 | 50.37 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
415.2 | 50.35 | 50.35 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
415.25 | 50.32 | 50.32 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
415.3 | 50.29 | 50.29 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
415.35 | 50.27 | 50.27 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
415.4 | 50.24 | 50.24 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
415.45 | 50.22 | 50.22 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
415.5 | 50.19 | 50.19 | -0.905 | -0.905 | -9.05 | 50.47 | -1 | -1 | -10 | -9.525 | -9.525 | 0 | 12 | 1 | 1 | -9.525 | 10 | 0 | 0
415.55 | 50.17 | 50.17 | -0.715 | -0.715 | -7.15 | 50.45 | -1 | -1 | -10 | -8.575 | -8.575 | 0 | 12 | 1 | 1 | -8.575 | 10 | 0 | 0
415.6 | 50.14 | 50.14 | -0.43 | -0.43 | -4.3 | 50.42 | -1 | -1 | -10 | -7.15 | -7.15 | 0 | 12 | 1 | 1 | -7.15 | 10 | 0 | 0
415.65 | 50.12 | 50.12 | -0.24 | -0.24 | -2.4 | 50.4 | -1 | -1 | -10 | -6.2 | -6.2 | 0 | 12 | 1 | 1 | -6.2 | 10 | 0 | 0
415.7 | 50.09 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 50.37 | -1 | -1 | -10 | -5.2206 | -5.2206 | 0 | 12 | 1 | 1 | -5.2206 | 10 | 0 | 0
415.75 | 50.06 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.35 | -1 | -1 | -10 | -5.1324 | -5.1324 | 0 | 12 | 1 | 1 | -5.1324 | 10 | 0 | 0
415.8 | 50.04 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.32 | -1 | -1 | -10 | -5.0735 | -5.0735 | 0 | 12 | 1 | 1 | -5.0735 | 10 | 0 | 0
415.85 | 50.01 | 50.01 | 0 | 0 | 0 | 50.29 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
415.9 | 49.99 | 49.99 | 0 | 0 | 0 | 50.27 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
415.95 | 49.96 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.24 | -1 | -1 | -10 | -4.9265 | -4.9265 | 0 | 12 | 1 | 1 | -4.9265 | 10 | 0 | 0
416 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.22 | -1 | -1 | -10 | -4.8676 | -4.8676 | 0 | 12 | 1 | 1 | -4.8676 | 10 | 0 | 0
416.05 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.19 | -0.905 | -0.905 | -9.05 | -4.3044 | -4.3044 | 0 | 12 | 1 | 1 | -4.3044 | 10 | 0 | 0
416.1 | 49.88 | 49.88 | 0.24 | 0.24 | 2.4 | 50.17 | -0.715 | -0.805 | -8.05 | -2.825 | -2.825 | 0 | 12 | 1 | 1 | -2.825 | 10 | 0 | 0
416.15 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.14 | -0.43 | -0.705 | -7.05 | -1.375 | -1.375 | 0 | 12 | 1 | 1 | -1.375 | 10 | 0 | 0
416.2 | 49.83 | 49.83 | 0.715 | 0.715 | 7.15 | 50.12 | -0.24 | -0.605 | -6.05 | 0.55 | 0.55 | 0 | 12 | 1 | 1 | 0.55 | 10 | 0 | 0
416.25 | 49.81 | 49.81 | 0.905 | 0.905 | 9.05 | 50.09 | -0.044118 | -0.505 | -5.05 | 2 | 2 | 0 | 12 | 1 | 1 | 2 | 10 | 0 | 0
416.3 | 49.78 | 49.78 | 1 | 1 | 10 | 50.06 | -0.026471 | -0.405 | -4.05 | 2.975 | 2.975 | 0 | 12 | 1 | 1 | 2.975 | 10 | 0 | 0
416.35 | 49.76 | 49.76 | 1 | 1 | 10 | 50.04 | -0.014706 | -0.305 | -3.05 | 3.475 | 3.475 | 0 | 12 | 1 | 1 | 3.475 | 10 | 0 | 0
416.4 | 49.73 | 49.73 | 1 | 1 | 10 | 50.01 | 0 | -0.205 | -2.05 | 3.975 | 3.975 | 0 | 12 | 1 | 1 | 3.975 | 10 | 0 | 0
416.45 | 49.71 | 49.71 | 1 | 1 | 10 | 49.99 | 0 | -0.105 | -1.05 | 4.475 | 4.475 | 0 | 12 | 1 | 1 | 4.475 | 10 | 0 | 0
416.5 | 49.68 | 49.68 | 1 | 1 | 10 | 49.96 | 0.014706 | -0.005 | -0.05 | 4.975 | 4.975 | 0 | 12 | 1 | 1 | 4.975 | 10 | 0 | 0
416.55 | 49.65 | 49.65 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
416.6 | 49.63 | 49.63 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
416.65 | 49.6 | 49.6 | 1 | 1 | 10 | 49.88 | 0.24 | 0.14412 | 1.4412 | 5.7206 | 5.7206 | 0 | 12 | 1 | 1 | 5.7206 | 10 | 0 | 0
416.7 | 49.58 | 49.58 | 1 | 1 | 10 | 49.86 | 0.43 | 0.24412 | 2.4412 | 6.2206 | 6.2206 | 0 | 12 | 1 | 1 | 6.2206 | 10 | 0 | 0
416.75 | 49.55 | 49.55 | 1 | 1 | 10 | 49.83 | 0.715 | 0.34412 | 3.4412 | 6.7206 | 6.7206 | 0 | 12 | 1 | 1 | 6.7206 | 10 | 0 | 0
416.8 | 49.53 | 49.53 | 1 | 1 | 10 | 49.81 | 0.905 | 0.44412 | 4.4412 | 7.2206 | 7.2206 | 0 | 12 | 1 | 1 | 7.2206 | 10 | 0 | 0
416.85 | 49.5 | 49.5 | 1 | 1 | 10 | 49.78 | 1 | 0.54412 | 5.4412 | 7.7206 | 7.7206 | 0 | 12 | 1 | 1 | 7.7206 | 10 | 0 | 0
416.9 | 49.5 | 49.5 | 1 | 1 | 10 | 49.76 | 1 | 0.64412 | 6.4412 | 8.2206 | 8.2206 | 0 | 12 | 1 | 1 | 8.2206 | 10 | 0 | 0
416.95 | 49.53 | 49.5 | 1 | 1 | 10 | 49.73 | 1 | 0.74412 | 7.4412 | 8.7206 | 8.7206 | 0 | 12 | 1 | 1 | 8.7206 | 10 | 0 | 0
417 | 49.55 | 49.5 | 1 | 1 | 10 | 49.71 | 1 | 0.84412 | 8.4412 | 9.2206 | 9.2206 | 0 | 12 | 1 | 1 | 9.2206 | 10 | 0 | 0
417.05 | 49.58 | 49.5 | 1 | 1 | 10 | 49.68 | 1 | 0.94412 | 9.4412 | 9.7206 | 9.7206 | 0 | 12 | 1 | 1 | 9.7206 | 10 | 0 | 0
417.1 | 49.6 | 49.5 | 1 | 1 | 10 | 49.65 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
417.15 | 49.63 | 49.5 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
417.2 | 49.65 | 49.5 | 1 | 1 | 10 | 49.65 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
417.25 | 49.68 | 49.5 | 1 | 1 | 10 | 49.68 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
417.3 | 49.71 | 49.5 | 1 | 1 | 10 | 49.71 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
417.35 | 49.73 | 49.5 | 1 | 1 | 10 | 49.73 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
417.4 | 49.76 | 49.5 | 1 | 1 | 10 | 49.76 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
417.45 | 49.78 | 49.5 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
417.5 | 49.81 | 49.53 | 1 | 1 | 10 | 49.81 | 0.905 | 0.905 | 9.05 | 9.525 | 9.525 | 0 | 12 | 1 | 1 | 9.525 | 10 | 0 | 0
417.55 | 49.83 | 49.55 | 1 | 1 | 10 | 49.83 | 0.715 | 0.715 | 7.15 | 8.575 | 8.575 | 0 | 12 | 1 | 1 | 8.575 | 10 | 0 | 0
417.6 | 49.86 | 49.58 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
417.65 | 49.88 | 49.6 | 1 | 1 | 10 | 49.88 | 0.24 | 0.24 | 2.4 | 6.2 | 6.2 | 0 | 12 | 1 | 1 | 6.2 | 10 | 0 | 0
417.7 | 49.91 | 49.63 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
417.75 | 49.94 | 49.65 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
417.8 | 49.96 | 49.68 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
417.85 | 49.99 | 49.71 | 1 | 1 | 10 | 49.99 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
417.9 | 50.01 | 49.73 | 1 | 1 | 10 | 50.01 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
417.95 | 50.04 | 49.76 | 1 | 1 | 10 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 4.9265 | 4.9265 | 0 | 12 | 1 | 1 | 4.9265 | 10 | 0 | 0
418 | 50.06 | 49.78 | 1 | 1 | 10 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 4.8676 | 4.8676 | 0 | 12 | 1 | 1 | 4.8676 | 10 | 0 | 0
418.05 | 50.09 | 49.81 | 0.905 | 0.905 | 9.05 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 4.3044 | 4.3044 | 0 | 12 | 1 | 1 | 4.3044 | 10 | 0 | 0
418.1 | 50.12 | 49.83 | 0.715 | 0.805 | 8.05 | 50.12 | -0.24 | -0.24 | -2.4 | 2.825 | 2.825 | 0 | 12 | 1 | 1 | 2.825 | 10 | 0 | 0
418.15 | 50.14 | 49.86 | 0.43 | 0.705 | 7.05 | 50.14 | -0.43 | -0.43 | -4.3 | 1.375 | 1.375 | 0 | 12 | 1 | 1 | 1.375 | 10 | 0 | 0
418.2 | 50.17 | 49.88 | 0.24 | 0.605 | 6.05 | 50.17 | -0.715 | -0.715 | -7.15 | -0.55 | -0.55 | 0 | 12 | 1 | 1 | -0.55 | 10 | 0 | 0
418.25 | 50.19 | 49.91 | 0.044118 | 0.505 | 5.05 | 50.19 | -0.905 | -0.905 | -9.05 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
418.3 | 50.22 | 49.94 | 0.026471 | 0.405 | 4.05 | 50.22 | -1 | -1 | -10 | -2.975 | -2.975 | 0 | 12 | 1 | 1 | -2.975 | 10 | 0 | 0
418.35 | 50.24 | 49.96 | 0.014706 | 0.305 | 3.05 | 50.24 | -1 | -1 | -10 | -3.475 | -3.475 | 0 | 12 | 1 | 1 | -3.475 | 10 | 0 | 0
418.4 | 50.27 | 49.99 | 0 | 0.205 | 2.05 | 50.27 | -1 | -1 | -10 | -3.975 | -3.975 | 0 | 12 | 1 | 1 | -3.975 | 10 | 0 | 0
418.45 | 50.29 | 50.01 | 0 | 0.105 | 1.05 | 50.29 | -1 | -1 | -10 | -4.475 | -4.475 | 0 | 12 | 1 | 1 | -4.475 | 10 | 0 | 0
418.5 | 50.32 | 50.04 | -0.014706 | 0.005 | 0.05 | 50.32 | -1 | -1 | -10 | -4.975 | -4.975 | 0 | 12 | 1 | 1 | -4.975 | 10 | 0 | 0
418.55 | 50.35 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.35 | -1 | -1 | -10 | -5.1324 | -5.1324 | 0 | 12 | 1 | 1 | -5.1324 | 10 | 0 | 0
418.6 | 50.37 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 50.37 | -1 | -1 | -10 | -5.2206 | -5.2206 | 0 | 12 | 1 | 1 | -5.2206 | 10 | 0 | 0
418.65 | 50.4 | 50.12 | -0.24 | -0.14412 | -1.4412 | 50.4 | -1 | -1 | -10 | -5.7206 | -5.7206 | 0 | 12 | 1 | 1 | -5.7206 | 10 | 0 | 0
418.7 | 50.42 | 50.14 | -0.43 | -0.24412 | -2.4412 | 50.42 | -1 | -1 | -10 | -6.2206 | -6.2206 | 0 | 12 | 1 | 1 | -6.2206 | 10 | 0 | 0
418.75 | 50.45 | 50.17 | -0.715 | -0.34412 | -3.4412 | 50.45 | -1 | -1 | -10 | -6.7206 | -6.7206 | 0 | 12 | 1 | 1 | -6.7206 | 10 | 0 | 0
418.8 | 50.47 | 50.19 | -0.905 | -0.44412 | -4.4412 | 50.47 | -1 | -1 | -10 | -7.2206 | -7.2206 | 0 | 12 | 1 | 1 | -7.2206 | 10 | 0 | 0
418.85 | 50.5 | 50.22 | -1 | -0.54412 | -5.4412 | 50.5 | -1 | -1 | -10 | -7.7206 | -7.7206 | 0 | 12 | 1 | 1 | -7.7206 | 10 | 0 | 0
418.9 | 50.5 | 50.24 | -1 | -0.64412 | -6.4412 | 50.5 | -1 | -1 | -10 | -8.2206 | -8.2206 | 0 | 12 | 1 | 1 | -8.2206 | 10 | 0 | 0
418.95 | 50.47 | 50.27 | -1 | -0.74412 | -7.4412 | 50.5 | -1 | -1 | -10 | -8.7206 | -8.7206 | 0 | 12 | 1 | 1 | -8.7206 | 10 | 0 | 0
419 | 50.45 | 50.29 | -1 | -0.84412 | -8.4412 | 50.5 | -1 | -1 | -10 | -9.2206 | -9.2206 | 0 | 12 | 1 | 1 | -9.2206 | 10 | 0 | 0
419.05 | 50.42 | 50.32 | -1 | -0.94412 | -9.4412 | 50.5 | -1 | -1 | -10 | -9.7206 | -9.7206 | 0 | 12 | 1 | 1 | -9.7206 | 10 | 0 | 0
419.1 | 50.39 | 50.35 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
419.15 | 50.37 | 50.37 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
419.2 | 50.34 | 50.34 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
419.25 | 50.32 | 50.32 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
419.3 | 50.29 | 50.29 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
419.35 | 50.26 | 50.26 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
419.4 | 50.24 | 50.24 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
419.45 | 50.21 | 50.21 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
419.5 | 50.18 | 50.18 | -0.81 | -0.81 | -8.1 | 50.47 | -1 | -1 | -10 | -9.05 | -9.05 | 0 | 12 | 1 | 1 | -9.05 | 10 | 0 | 0
419.55 | 50.16 | 50.16 | -0.62 | -0.62 | -6.2 | 50.45 | -1 | -1 | -10 | -8.1 | -8.1 | 0 | 12 | 1 | 1 | -8.1 | 10 | 0 | 0
419.6 | 50.13 | 50.13 | -0.335 | -0.335 | -3.35 | 50.42 | -1 | -1 | -10 | -6.675 | -6.675 | 0 | 12 | 1 | 1 | -6.675 | 10 | 0 | 0
419.65 | 50.11 | 50.11 | -0.145 | -0.145 | -1.45 | 50.39 | -1 | -1 | -10 | -5.725 | -5.725 | 0 | 12 | 1 | 1 | -5.725 | 10 | 0 | 0
419.7 | 50.08 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 50.37 | -1 | -1 | -10 | -5.1912 | -5.1912 | 0 | 12 | 1 | 1 | -5.1912 | 10 | 0 | 0
419.75 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.34 | -1 | -1 | -10 | -5.1029 | -5.1029 | 0 | 12 | 1 | 1 | -5.1029 | 10 | 0 | 0
419.8 | 50.03 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 50.32 | -1 | -1 | -10 | -5.0441 | -5.0441 | 0 | 12 | 1 | 1 | -5.0441 | 10 | 0 | 0
419.85 | 50 | 50 | 0 | 0 | 0 | 50.29 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
419.9 | 50 | 50 | 0 | 0 | 0 | 50.26 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
419.95 | 50 | 50 | 0 | 0 | 0 | 50.24 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
420 | 50 | 50 | 0 | 0 | 0 | 50.21 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
420.05 | 50 | 50 | 0 | 0 | 0 | 50.18 | -0.81 | -0.9 | -9 | -4.5 | -4.5 | 0 | 12 | 1 | 1 | -4.5 | 10 | 0 | 0
420.1 | 50 | 50 | 0 | 0 | 0 | 50.16 | -0.62 | -0.8 | -8 | -4 | -4 | 0 | 12 | 1 | 1 | -4 | 10 | 0 | 0
420.15 | 50 | 50 | 0 | 0 | 0 | 50.13 | -0.335 | -0.7 | -7 | -3.5 | -3.5 | 0 | 12 | 1 | 1 | -3.5 | 10 | 0 | 0
420.2 | 50.01 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.6 | -6 | -3 | -3 | 0 | 12 | 1 | 1 | -3 | 10 | 0 | 0
420.25 | 50.01 | 50 | 0 | 0 | 0 | 50.08 | -0.038235 | -0.5 | -5 | -2.5 | -2.5 | 0 | 12 | 1 | 1 | -2.5 | 10 | 0 | 0
420.3 | 49.99 | 49.99 | 0 | 0 | 0 | 50.05 | -0.020588 | -0.4 | -4 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
420.35 | 49.99 | 49.99 | 0 | 0 | 0 | 50.03 | -0.0088235 | -0.3 | -3 | -1.5 | -1.5 | 0 | 12 | 1 | 1 | -1.5 | 10 | 0 | 0
420.4 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | -0.2 | -2 | -0.83824 | -0.83824 | 0 | 12 | 1 | 1 | -0.83824 | 10 | 0 | 0
420.45 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | -0.1 | -1 | -0.33824 | -0.33824 | 0 | 12 | 1 | 1 | -0.33824 | 10 | 0 | 0
420.5 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
420.55 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
420.6 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
420.65 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
420.7 | 49.89 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
420.75 | 49.89 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
420.8 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50.01 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
420.85 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
420.9 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
420.95 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 2.7868 | 2.7868 | 0 | 12 | 1 | 1 | 2.7868 | 10 | 0 | 0
421 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 2.7868 | 2.7868 | 0 | 12 | 1 | 1 | 2.7868 | 10 | 0 | 0
421.05 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 2.8456 | 2.8456 | 0 | 12 | 1 | 1 | 2.8456 | 10 | 0 | 0
421.1 | 49.94 | 49.85 | 0.525 | 0.525 | 5.25 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 2.7574 | 2.7574 | 0 | 12 | 1 | 1 | 2.7574 | 10 | 0 | 0
421.15 | 49.94 | 49.85 | 0.525 | 0.525 | 5.25 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 2.7574 | 2.7574 | 0 | 12 | 1 | 1 | 2.7574 | 10 | 0 | 0
421.2 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
421.25 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
421.3 | 49.93 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
421.35 | 49.93 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
421.4 | 49.96 | 49.85 | 0.525 | 0.525 | 5.25 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 2.6985 | 2.6985 | 0 | 12 | 1 | 1 | 2.6985 | 10 | 0 | 0
421.45 | 49.96 | 49.85 | 0.525 | 0.525 | 5.25 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 2.6985 | 2.6985 | 0 | 12 | 1 | 1 | 2.6985 | 10 | 0 | 0
421.5 | 49.99 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
421.55 | 49.99 | 49.91 | 0.044118 | 0.425 | 4.25 | 49.99 | 0 | 0 | 0 | 2.125 | 2.125 | 0 | 12 | 1 | 1 | 2.125 | 10 | 0 | 0
421.6 | 49.99 | 49.91 | 0.044118 | 0.325 | 3.25 | 49.99 | 0 | 0 | 0 | 1.625 | 1.625 | 0 | 12 | 1 | 1 | 1.625 | 10 | 0 | 0
421.65 | 49.99 | 49.93 | 0.032353 | 0.225 | 2.25 | 49.99 | 0 | 0 | 0 | 1.125 | 1.125 | 0 | 12 | 1 | 1 | 1.125 | 10 | 0 | 0
421.7 | 49.96 | 49.93 | 0.032353 | 0.125 | 1.25 | 49.99 | 0 | 0 | 0 | 0.625 | 0.625 | 0 | 12 | 1 | 1 | 0.625 | 10 | 0 | 0
421.75 | 49.96 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 49.99 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
421.8 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
421.85 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
421.9 | 50.05 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.058824 | 0.058824 | 0 | 12 | 1 | 1 | 0.058824 | 10 | 0 | 0
421.95 | 50.05 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
422 | 49.97 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
422.05 | 49.97 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
422.1 | 49.92 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
422.15 | 49.92 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
422.2 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
422.25 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
422.3 | 49.94 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
422.35 | 49.94 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
422.4 | 50.01 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
422.45 | 50.01 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
422.5 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
422.55 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
422.6 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
422.65 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
422.7 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
422.75 | 49.95 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
422.8 | 49.97 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
422.85 | 49.97 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
422.9 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
422.95 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
423 | 49.87 | 49.87 | 0.335 | 0.335 | 3.35 | 50.01 | 0 | 0 | 0 | 1.675 | 1.675 | 0 | 12 | 1 | 1 | 1.675 | 10 | 0 | 0
423.05 | 49.87 | 49.87 | 0.335 | 0.335 | 3.35 | 49.99 | 0 | 0 | 0 | 1.675 | 1.675 | 0 | 12 | 1 | 1 | 1.675 | 10 | 0 | 0
423.1 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
423.15 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 2.6691 | 2.6691 | 0 | 12 | 1 | 1 | 2.6691 | 10 | 0 | 0
423.2 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
423.25 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
423.3 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
423.35 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
423.4 | 49.84 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
423.45 | 49.84 | 49.79 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
423.5 | 49.89 | 49.79 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
423.55 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.12647 | 1.2647 | 5.6324 | 5.6324 | 0 | 12 | 1 | 1 | 5.6324 | 10 | 0 | 0
423.6 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.145 | 1.45 | 5.725 | 5.725 | 0 | 12 | 1 | 1 | 5.725 | 10 | 0 | 0
423.65 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.145 | 1.45 | 5.725 | 5.725 | 0 | 12 | 1 | 1 | 5.725 | 10 | 0 | 0
423.7 | 49.96 | 49.79 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
423.75 | 49.96 | 49.79 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
423.8 | 50.02 | 49.79 | 1 | 1 | 10 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 4.9853 | 4.9853 | 0 | 12 | 1 | 1 | 4.9853 | 10 | 0 | 0
423.85 | 50.02 | 49.79 | 1 | 1 | 10 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 4.9853 | 4.9853 | 0 | 12 | 1 | 1 | 4.9853 | 10 | 0 | 0
423.9 | 50.03 | 49.79 | 1 | 1 | 10 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.9559 | 4.9559 | 0 | 12 | 1 | 1 | 4.9559 | 10 | 0 | 0
423.95 | 50.03 | 49.84 | 0.62 | 0.9 | 9 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.4559 | 4.4559 | 0 | 12 | 1 | 1 | 4.4559 | 10 | 0 | 0
424 | 50.02 | 49.84 | 0.62 | 0.8 | 8 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 3.9559 | 3.9559 | 0 | 12 | 1 | 1 | 3.9559 | 10 | 0 | 0
424.05 | 50.02 | 49.89 | 0.145 | 0.7 | 7 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 3.4559 | 3.4559 | 0 | 12 | 1 | 1 | 3.4559 | 10 | 0 | 0
424.1 | 50.08 | 49.89 | 0.145 | 0.6 | 6 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 2.8088 | 2.8088 | 0 | 12 | 1 | 1 | 2.8088 | 10 | 0 | 0
424.15 | 50.08 | 49.89 | 0.145 | 0.5 | 5 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 2.3088 | 2.3088 | 0 | 12 | 1 | 1 | 2.3088 | 10 | 0 | 0
424.2 | 50.01 | 49.89 | 0.145 | 0.4 | 4 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 1.8088 | 1.8088 | 0 | 12 | 1 | 1 | 1.8088 | 10 | 0 | 0
424.25 | 50.01 | 49.96 | 0.014706 | 0.3 | 3 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 1.3088 | 1.3088 | 0 | 12 | 1 | 1 | 1.3088 | 10 | 0 | 0
424.3 | 49.94 | 49.94 | 0.026471 | 0.2 | 2 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.80882 | 0.80882 | 0 | 12 | 1 | 1 | 0.80882 | 10 | 0 | 0
424.35 | 49.94 | 49.94 | 0.026471 | 0.1 | 1 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.30882 | 0.30882 | 0 | 12 | 1 | 1 | 0.30882 | 10 | 0 | 0
424.4 | 50 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
424.45 | 50 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
424.5 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
424.55 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
424.6 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
424.65 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
424.7 | 49.92 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
424.75 | 49.92 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
424.8 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50.01 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
424.85 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
424.9 | 49.92 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
424.95 | 49.92 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
425 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
425.05 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
425.1 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
425.15 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
425.2 | 49.87 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
425.25 | 49.87 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
425.3 | 49.8 | 49.8 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
425.35 | 49.8 | 49.8 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
425.4 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
425.45 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
425.5 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
425.55 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
425.6 | 49.72 | 49.72 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
425.65 | 49.72 | 49.72 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
425.7 | 49.67 | 49.67 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
425.75 | 49.67 | 49.67 | 1 | 1 | 10 | 49.87 | 0.335 | 0.14412 | 1.4412 | 5.7206 | 5.7206 | 0 | 12 | 1 | 1 | 5.7206 | 10 | 0 | 0
425.8 | 49.65 | 49.65 | 1 | 1 | 10 | 49.87 | 0.335 | 0.24412 | 2.4412 | 6.2206 | 6.2206 | 0 | 12 | 1 | 1 | 6.2206 | 10 | 0 | 0
425.85 | 49.65 | 49.65 | 1 | 1 | 10 | 49.8 | 1 | 0.34412 | 3.4412 | 6.7206 | 6.7206 | 0 | 12 | 1 | 1 | 6.7206 | 10 | 0 | 0
425.9 | 49.59 | 49.59 | 1 | 1 | 10 | 49.8 | 1 | 0.44412 | 4.4412 | 7.2206 | 7.2206 | 0 | 12 | 1 | 1 | 7.2206 | 10 | 0 | 0
425.95 | 49.59 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.54412 | 5.4412 | 7.7206 | 7.7206 | 0 | 12 | 1 | 1 | 7.7206 | 10 | 0 | 0
426 | 49.66 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.64412 | 6.4412 | 8.2206 | 8.2206 | 0 | 12 | 1 | 1 | 8.2206 | 10 | 0 | 0
426.05 | 49.66 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.74412 | 7.4412 | 8.7206 | 8.7206 | 0 | 12 | 1 | 1 | 8.7206 | 10 | 0 | 0
426.1 | 49.63 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.84412 | 8.4412 | 9.2206 | 9.2206 | 0 | 12 | 1 | 1 | 9.2206 | 10 | 0 | 0
426.15 | 49.63 | 49.59 | 1 | 1 | 10 | 49.72 | 1 | 0.94412 | 9.4412 | 9.7206 | 9.7206 | 0 | 12 | 1 | 1 | 9.7206 | 10 | 0 | 0
426.2 | 49.61 | 49.59 | 1 | 1 | 10 | 49.72 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
426.25 | 49.61 | 49.59 | 1 | 1 | 10 | 49.67 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
426.3 | 49.54 | 49.54 | 1 | 1 | 10 | 49.67 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
426.35 | 49.54 | 49.54 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
426.4 | 49.46 | 49.46 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
426.45 | 49.46 | 49.46 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
426.5 | 49.45 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
426.55 | 49.45 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
426.6 | 49.51 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
426.65 | 49.51 | 49.45 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
426.7 | 49.5 | 49.45 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
426.75 | 49.5 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
426.8 | 49.54 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
426.85 | 49.54 | 49.45 | 1 | 1 | 10 | 49.54 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
426.9 | 49.59 | 49.45 | 1 | 1 | 10 | 49.59 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
426.95 | 49.59 | 49.45 | 1 | 1 | 10 | 49.59 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
427 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
427.05 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
427.1 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
427.15 | 49.61 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
427.2 | 49.53 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
427.25 | 49.53 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
427.3 | 49.54 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
427.35 | 49.54 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
427.4 | 49.61 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
427.45 | 49.61 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
427.5 | 49.66 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
427.55 | 49.66 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
427.6 | 49.64 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
427.65 | 49.64 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
427.7 | 49.69 | 49.53 | 1 | 1 | 10 | 49.69 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
427.75 | 49.69 | 49.53 | 1 | 1 | 10 | 49.69 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
427.8 | 49.74 | 49.53 | 1 | 1 | 10 | 49.74 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
427.85 | 49.74 | 49.54 | 1 | 1 | 10 | 49.74 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
427.9 | 49.78 | 49.54 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
427.95 | 49.78 | 49.61 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
428 | 49.82 | 49.61 | 1 | 1 | 10 | 49.82 | 0.81 | 0.81 | 8.1 | 9.05 | 9.05 | 0 | 12 | 1 | 1 | 9.05 | 10 | 0 | 0
428.05 | 49.82 | 49.64 | 1 | 1 | 10 | 49.82 | 0.81 | 0.81 | 8.1 | 9.05 | 9.05 | 0 | 12 | 1 | 1 | 9.05 | 10 | 0 | 0
428.1 | 49.86 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
428.15 | 49.86 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
428.2 | 49.84 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
428.25 | 49.84 | 49.69 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
428.3 | 49.91 | 49.69 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
428.35 | 49.91 | 49.74 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
428.4 | 49.97 | 49.74 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
428.45 | 49.97 | 49.78 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
428.5 | 50.03 | 49.78 | 1 | 1 | 10 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.9559 | 4.9559 | 0 | 12 | 1 | 1 | 4.9559 | 10 | 0 | 0
428.55 | 50.03 | 49.82 | 0.81 | 0.9 | 9 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.4559 | 4.4559 | 0 | 12 | 1 | 1 | 4.4559 | 10 | 0 | 0
428.6 | 50.05 | 49.82 | 0.81 | 0.81 | 8.1 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 3.9471 | 3.9471 | 0 | 12 | 1 | 1 | 3.9471 | 10 | 0 | 0
428.65 | 50.05 | 49.84 | 0.62 | 0.71 | 7.1 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 3.4471 | 3.4471 | 0 | 12 | 1 | 1 | 3.4471 | 10 | 0 | 0
428.7 | 50.01 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
428.75 | 50.01 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
428.8 | 49.95 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
428.85 | 49.95 | 49.91 | 0.044118 | 0.52 | 5.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.4971 | 2.4971 | 0 | 12 | 1 | 1 | 2.4971 | 10 | 0 | 0
428.9 | 49.99 | 49.91 | 0.044118 | 0.42 | 4.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 1.9971 | 1.9971 | 0 | 12 | 1 | 1 | 1.9971 | 10 | 0 | 0
428.95 | 49.99 | 49.95 | 0.020588 | 0.32 | 3.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 1.4971 | 1.4971 | 0 | 12 | 1 | 1 | 1.4971 | 10 | 0 | 0
429 | 49.92 | 49.92 | 0.038235 | 0.22 | 2.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.99706 | 0.99706 | 0 | 12 | 1 | 1 | 0.99706 | 10 | 0 | 0
429.05 | 49.92 | 49.92 | 0.038235 | 0.12 | 1.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.49706 | 0.49706 | 0 | 12 | 1 | 1 | 0.49706 | 10 | 0 | 0
429.1 | 49.97 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
429.15 | 49.97 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
429.2 | 50.02 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
429.25 | 50.02 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.17647 | 0.17647 | 0 | 12 | 1 | 1 | 0.17647 | 10 | 0 | 0
429.3 | 50.07 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
429.35 | 50.07 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
429.4 | 50.06 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
429.45 | 50.06 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
429.5 | 50.13 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
429.55 | 50.13 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
429.6 | 50.09 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
429.65 | 50.09 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6309 | -1.6309 | 0 | 12 | 1 | 1 | -1.6309 | 10 | 0 | 0
429.7 | 50.07 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6309 | -1.6309 | 0 | 12 | 1 | 1 | -1.6309 | 10 | 0 | 0
429.75 | 50.07 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6897 | -1.6897 | 0 | 12 | 1 | 1 | -1.6897 | 10 | 0 | 0
429.8 | 50.07 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6897 | -1.6897 | 0 | 12 | 1 | 1 | -1.6897 | 10 | 0 | 0
429.85 | 50.07 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.13 | -0.335 | -0.335 | -3.35 | -1.8074 | -1.8074 | 0 | 12 | 1 | 1 | -1.8074 | 10 | 0 | 0
429.9 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.13 | -0.335 | -0.335 | -3.35 | -1.7779 | -1.7779 | 0 | 12 | 1 | 1 | -1.7779 | 10 | 0 | 0
429.95 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.13 | -0.335 | -0.335 | -3.35 | -1.7779 | -1.7779 | 0 | 12 | 1 | 1 | -1.7779 | 10 | 0 | 0
430 | 50.01 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
430.05 | 50.01 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
430.1 | 50.07 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
430.15 | 50.07 | 50.01 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.235 | -2.35 | -1.175 | -1.175 | 0 | 12 | 1 | 1 | -1.175 | 10 | 0 | 0
430.2 | 50.05 | 50.01 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.135 | -1.35 | -0.675 | -0.675 | 0 | 12 | 1 | 1 | -0.675 | 10 | 0 | 0
430.25 | 50.05 | 50.01 | 0 | 0 | 0 | 50.07 | -0.032353 | -0.035 | -0.35 | -0.175 | -0.175 | 0 | 12 | 1 | 1 | -0.175 | 10 | 0 | 0
430.3 | 50.1 | 50.01 | 0 | 0 | 0 | 50.1 | -0.05 | -0.05 | -0.5 | -0.25 | -0.25 | 0 | 12 | 1 | 1 | -0.25 | 10 | 0 | 0
430.35 | 50.1 | 50.01 | 0 | 0 | 0 | 50.1 | -0.05 | -0.05 | -0.5 | -0.25 | -0.25 | 0 | 12 | 1 | 1 | -0.25 | 10 | 0 | 0
430.4 | 50.11 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
430.45 | 50.11 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
430.5 | 50.06 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
430.55 | 50.06 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
430.6 | 50.04 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
430.65 | 50.04 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
430.7 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
430.75 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
430.8 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
430.85 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
430.9 | 50.11 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
430.95 | 50.11 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
431 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
431.05 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
431.1 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
431.15 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
431.2 | 50.02 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.11 | -0.145 | -0.145 | -1.45 | -0.73971 | -0.73971 | 0 | 12 | 1 | 1 | -0.73971 | 10 | 0 | 0
431.25 | 50.02 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.11 | -0.145 | -0.145 | -1.45 | -0.73971 | -0.73971 | 0 | 12 | 1 | 1 | -0.73971 | 10 | 0 | 0
431.3 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
431.35 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
431.4 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
431.45 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
431.5 | 50.01 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
431.55 | 50.01 | 50 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.045 | -0.45 | -0.225 | -0.225 | 0 | 12 | 1 | 1 | -0.225 | 10 | 0 | 0
431.6 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
431.65 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
431.7 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
431.75 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
431.8 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.14706 | 0.14706 | 0 | 12 | 1 | 1 | 0.14706 | 10 | 0 | 0
431.85 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
431.9 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
431.95 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
432 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
432.05 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
432.1 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
432.15 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
432.2 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
432.25 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
432.3 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
432.35 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
432.4 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
432.45 | 50 | 50 | 0 | 0 | 0 | 50.01 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
432.5 | 49.5 | 49.5 | 1 | 1 | 10 | 50.01 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
432.55 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
432.6 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
432.65 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
432.7 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
432.75 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
432.8 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
432.85 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
432.9 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
432.95 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
433 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
433.05 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.1 | 1 | 5.5 | 5.5 | 0 | 12 | 1 | 1 | 5.5 | 10 | 0 | 0
433.1 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.2 | 2 | 6 | 6 | 0 | 12 | 1 | 1 | 6 | 10 | 0 | 0
433.15 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.3 | 3 | 6.5 | 6.5 | 0 | 12 | 1 | 1 | 6.5 | 10 | 0 | 0
433.2 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.4 | 4 | 7 | 7 | 0 | 12 | 1 | 1 | 7 | 10 | 0 | 0
433.25 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.5 | 5 | 7.5 | 7.5 | 0 | 12 | 1 | 1 | 7.5 | 10 | 0 | 0
433.3 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.6 | 6 | 8 | 8 | 0 | 12 | 1 | 1 | 8 | 10 | 0 | 0
433.35 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.7 | 7 | 8.5 | 8.5 | 0 | 12 | 1 | 1 | 8.5 | 10 | 0 | 0
433.4 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.8 | 8 | 9 | 9 | 0 | 12 | 1 | 1 | 9 | 10 | 0 | 0
433.45 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.9 | 9 | 9.5 | 9.5 | 0 | 12 | 1 | 1 | 9.5 | 10 | 0 | 0
433.5 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
433.55 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
433.6 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
433.65 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
433.7 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
433.75 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
433.8 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
433.85 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
433.9 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
433.95 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
434 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
434.05 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
434.1 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
434.15 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
434.2 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
434.25 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
434.3 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
434.35 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
434.4 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
434.45 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
434.5 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
434.55 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
434.6 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
434.65 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
434.7 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
434.75 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
434.8 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
434.85 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
434.9 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
434.95 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
435 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
435.05 | 50.5 | 50.5 | -1 | 0.9 | 9 | 50.5 | -1 | -1 | -10 | -0.5 | -0.5 | 0 | 12 | 1 | 1 | -0.5 | 10 | 0 | 0
435.1 | 50.5 | 50.5 | -1 | 0.8 | 8 | 50.5 | -1 | -1 | -10 | -1 | -1 | 0 | 12 | 1 | 1 | -1 | 10 | 0 | 0
435.15 | 50.5 | 50.5 | -1 | 0.7 | 7 | 50.5 | -1 | -1 | -10 | -1.5 | -1.5 | 0 | 12 | 1 | 1 | -1.5 | 10 | 0 | 0
435.2 | 50.5 | 50.5 | -1 | 0.6 | 6 | 50.5 | -1 | -1 | -10 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
435.25 | 50.5 | 50.5 | -1 | 0.5 | 5 | 50.5 | -1 | -1 | -10 | -2.5 | -2.5 | 0 | 12 | 1 | 1 | -2.5 | 10 | 0 | 0
435.3 | 50.5 | 50.5 | -1 | 0.4 | 4 | 50.5 | -1 | -1 | -10 | -3 | -3 | 0 | 12 | 1 | 1 | -3 | 10 | 0 | 0
435.35 | 50.5 | 50.5 | -1 | 0.3 | 3 | 50.5 | -1 | -1 | -10 | -3.5 | -3.5 | 0 | 12 | 1 | 1 | -3.5 | 10 | 0 | 0
435.4 | 50.5 | 50.5 | -1 | 0.2 | 2 | 50.5 | -1 | -1 | -10 | -4 | -4 | 0 | 12 | 1 | 1 | -4 | 10 | 0 | 0
435.45 | 50.5 | 50.5 | -1 | 0.1 | 1 | 50.5 | -1 | -1 | -10 | -4.5 | -4.5 | 0 | 12 | 1 | 1 | -4.5 | 10 | 0 | 0
435.5 | 50.5 | 50.5 | -1 | 0 | 0 | 50.5 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
435.55 | 50.5 | 50.5 | -1 | -0.1 | -1 | 50.5 | -1 | -1 | -10 | -5.5 | -5.5 | 0 | 12 | 1 | 1 | -5.5 | 10 | 0 | 0
435.6 | 50.5 | 50.5 | -1 | -0.2 | -2 | 50.5 | -1 | -1 | -10 | -6 | -6 | 0 | 12 | 1 | 1 | -6 | 10 | 0 | 0
435.65 | 50.5 | 50.5 | -1 | -0.3 | -3 | 50.5 | -1 | -1 | -10 | -6.5 | -6.5 | 0 | 12 | 1 | 1 | -6.5 | 10 | 0 | 0
435.7 | 50.5 | 50.5 | -1 | -0.4 | -4 | 50.5 | -1 | -1 | -10 | -7 | -7 | 0 | 12 | 1 | 1 | -7 | 10 | 0 | 0
435.75 | 50.5 | 50.5 | -1 | -0.5 | -5 | 50.5 | -1 | -1 | -10 | -7.5 | -7.5 | 0 | 12 | 1 | 1 | -7.5 | 10 | 0 | 0
435.8 | 50.5 | 50.5 | -1 | -0.6 | -6 | 50.5 | -1 | -1 | -10 | -8 | -8 | 0 | 12 | 1 | 1 | -8 | 10 | 0 | 0
435.85 | 50.5 | 50.5 | -1 | -0.7 | -7 | 50.5 | -1 | -1 | -10 | -8.5 | -8.5 | 0 | 12 | 1 | 1 | -8.5 | 10 | 0 | 0
435.9 | 50.5 | 50.5 | -1 | -0.8 | -8 | 50.5 | -1 | -1 | -10 | -9 | -9 | 0 | 12 | 1 | 1 | -9 | 10 | 0 | 0
435.95 | 50.5 | 50.5 | -1 | -0.9 | -9 | 50.5 | -1 | -1 | -10 | -9.5 | -9.5 | 0 | 12 | 1 | 1 | -9.5 | 10 | 0 | 0
436 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
436.05 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
436.1 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
436.15 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
436.2 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
436.25 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
436.3 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
436.35 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
436.4 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
436.45 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
436.5 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
436.55 | 50.47 | 50.47 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
436.6 | 50.45 | 50.45 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
436.65 | 50.42 | 50.42 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
436.7 | 50.4 | 50.4 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
436.75 | 50.37 | 50.37 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
436.8 | 50.35 | 50.35 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
436.85 | 50.32 | 50.32 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
436.9 | 50.29 | 50.29 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
436.95 | 50.27 | 50.27 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
437 | 50.24 | 50.24 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
437.05 | 50.22 | 50.22 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
437.1 | 50.19 | 50.19 | -0.905 | -0.905 | -9.05 | 50.47 | -1 | -1 | -10 | -9.525 | -9.525 | 0 | 12 | 1 | 1 | -9.525 | 10 | 0 | 0
437.15 | 50.17 | 50.17 | -0.715 | -0.715 | -7.15 | 50.45 | -1 | -1 | -10 | -8.575 | -8.575 | 0 | 12 | 1 | 1 | -8.575 | 10 | 0 | 0
437.2 | 50.14 | 50.14 | -0.43 | -0.43 | -4.3 | 50.42 | -1 | -1 | -10 | -7.15 | -7.15 | 0 | 12 | 1 | 1 | -7.15 | 10 | 0 | 0
437.25 | 50.12 | 50.12 | -0.24 | -0.24 | -2.4 | 50.4 | -1 | -1 | -10 | -6.2 | -6.2 | 0 | 12 | 1 | 1 | -6.2 | 10 | 0 | 0
437.3 | 50.09 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 50.37 | -1 | -1 | -10 | -5.2206 | -5.2206 | 0 | 12 | 1 | 1 | -5.2206 | 10 | 0 | 0
437.35 | 50.06 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.35 | -1 | -1 | -10 | -5.1324 | -5.1324 | 0 | 12 | 1 | 1 | -5.1324 | 10 | 0 | 0
437.4 | 50.04 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.32 | -1 | -1 | -10 | -5.0735 | -5.0735 | 0 | 12 | 1 | 1 | -5.0735 | 10 | 0 | 0
437.45 | 50.01 | 50.01 | 0 | 0 | 0 | 50.29 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
437.5 | 49.99 | 49.99 | 0 | 0 | 0 | 50.27 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
437.55 | 49.96 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.24 | -1 | -1 | -10 | -4.9265 | -4.9265 | 0 | 12 | 1 | 1 | -4.9265 | 10 | 0 | 0
437.6 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.22 | -1 | -1 | -10 | -4.8676 | -4.8676 | 0 | 12 | 1 | 1 | -4.8676 | 10 | 0 | 0
437.65 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.19 | -0.905 | -0.905 | -9.05 | -4.3044 | -4.3044 | 0 | 12 | 1 | 1 | -4.3044 | 10 | 0 | 0
437.7 | 49.88 | 49.88 | 0.24 | 0.24 | 2.4 | 50.17 | -0.715 | -0.805 | -8.05 | -2.825 | -2.825 | 0 | 12 | 1 | 1 | -2.825 | 10 | 0 | 0
437.75 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.14 | -0.43 | -0.705 | -7.05 | -1.375 | -1.375 | 0 | 12 | 1 | 1 | -1.375 | 10 | 0 | 0
437.8 | 49.83 | 49.83 | 0.715 | 0.715 | 7.15 | 50.12 | -0.24 | -0.605 | -6.05 | 0.55 | 0.55 | 0 | 12 | 1 | 1 | 0.55 | 10 | 0 | 0
437.85 | 49.81 | 49.81 | 0.905 | 0.905 | 9.05 | 50.09 | -0.044118 | -0.505 | -5.05 | 2 | 2 | 0 | 12 | 1 | 1 | 2 | 10 | 0 | 0
437.9 | 49.78 | 49.78 | 1 | 1 | 10 | 50.06 | -0.026471 | -0.405 | -4.05 | 2.975 | 2.975 | 0 | 12 | 1 | 1 | 2.975 | 10 | 0 | 0
437.95 | 49.76 | 49.76 | 1 | 1 | 10 | 50.04 | -0.014706 | -0.305 | -3.05 | 3.475 | 3.475 | 0 | 12 | 1 | 1 | 3.475 | 10 | 0 | 0
438 | 49.73 | 49.73 | 1 | 1 | 10 | 50.01 | 0 | -0.205 | -2.05 | 3.975 | 3.975 | 0 | 12 | 1 | 1 | 3.975 | 10 | 0 | 0
438.05 | 49.71 | 49.71 | 1 | 1 | 10 | 49.99 | 0 | -0.105 | -1.05 | 4.475 | 4.475 | 0 | 12 | 1 | 1 | 4.475 | 10 | 0 | 0
438.1 | 49.68 | 49.68 | 1 | 1 | 10 | 49.96 | 0.014706 | -0.005 | -0.05 | 4.975 | 4.975 | 0 | 12 | 1 | 1 | 4.975 | 10 | 0 | 0
438.15 | 49.65 | 49.65 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
438.2 | 49.63 | 49.63 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
438.25 | 49.6 | 49.6 | 1 | 1 | 10 | 49.88 | 0.24 | 0.14412 | 1.4412 | 5.7206 | 5.7206 | 0 | 12 | 1 | 1 | 5.7206 | 10 | 0 | 0
438.3 | 49.58 | 49.58 | 1 | 1 | 10 | 49.86 | 0.43 | 0.24412 | 2.4412 | 6.2206 | 6.2206 | 0 | 12 | 1 | 1 | 6.2206 | 10 | 0 | 0
438.35 | 49.55 | 49.55 | 1 | 1 | 10 | 49.83 | 0.715 | 0.34412 | 3.4412 | 6.7206 | 6.7206 | 0 | 12 | 1 | 1 | 6.7206 | 10 | 0 | 0
438.4 | 49.53 | 49.53 | 1 | 1 | 10 | 49.81 | 0.905 | 0.44412 | 4.4412 | 7.2206 | 7.2206 | 0 | 12 | 1 | 1 | 7.2206 | 10 | 0 | 0
438.45 | 49.5 | 49.5 | 1 | 1 | 10 | 49.78 | 1 | 0.54412 | 5.4412 | 7.7206 | 7.7206 | 0 | 12 | 1 | 1 | 7.7206 | 10 | 0 | 0
438.5 | 49.5 | 49.5 | 1 | 1 | 10 | 49.76 | 1 | 0.64412 | 6.4412 | 8.2206 | 8.2206 | 0 | 12 | 1 | 1 | 8.2206 | 10 | 0 | 0
438.55 | 49.53 | 49.5 | 1 | 1 | 10 | 49.73 | 1 | 0.74412 | 7.4412 | 8.7206 | 8.7206 | 0 | 12 | 1 | 1 | 8.7206 | 10 | 0 | 0
438.6 | 49.55 | 49.5 | 1 | 1 | 10 | 49.71 | 1 | 0.84412 | 8.4412 | 9.2206 | 9.2206 | 0 | 12 | 1 | 1 | 9.2206 | 10 | 0 | 0
438.65 | 49.58 | 49.5 | 1 | 1 | 10 | 49.68 | 1 | 0.94412 | 9.4412 | 9.7206 | 9.7206 | 0 | 12 | 1 | 1 | 9.7206 | 10 | 0 | 0
438.7 | 49.6 | 49.5 | 1 | 1 | 10 | 49.65 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
438.75 | 49.63 | 49.5 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
438.8 | 49.65 | 49.5 | 1 | 1 | 10 | 49.65 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
438.85 | 49.68 | 49.5 | 1 | 1 | 10 | 49.68 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
438.9 | 49.71 | 49.5 | 1 | 1 | 10 | 49.71 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
438.95 | 49.73 | 49.5 | 1 | 1 | 10 | 49.73 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
439 | 49.76 | 49.5 | 1 | 1 | 10 | 49.76 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
439.05 | 49.78 | 49.5 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
439.1 | 49.81 | 49.53 | 1 | 1 | 10 | 49.81 | 0.905 | 0.905 | 9.05 | 9.525 | 9.525 | 0 | 12 | 1 | 1 | 9.525 | 10 | 0 | 0
439.15 | 49.83 | 49.55 | 1 | 1 | 10 | 49.83 | 0.715 | 0.715 | 7.15 | 8.575 | 8.575 | 0 | 12 | 1 | 1 | 8.575 | 10 | 0 | 0
439.2 | 49.86 | 49.58 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
439.25 | 49.88 | 49.6 | 1 | 1 | 10 | 49.88 | 0.24 | 0.24 | 2.4 | 6.2 | 6.2 | 0 | 12 | 1 | 1 | 6.2 | 10 | 0 | 0
439.3 | 49.91 | 49.63 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
439.35 | 49.94 | 49.65 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
439.4 | 49.96 | 49.68 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
439.45 | 49.99 | 49.71 | 1 | 1 | 10 | 49.99 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
439.5 | 50.01 | 49.73 | 1 | 1 | 10 | 50.01 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
439.55 | 50.04 | 49.76 | 1 | 1 | 10 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 4.9265 | 4.9265 | 0 | 12 | 1 | 1 | 4.9265 | 10 | 0 | 0
439.6 | 50.06 | 49.78 | 1 | 1 | 10 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 4.8676 | 4.8676 | 0 | 12 | 1 | 1 | 4.8676 | 10 | 0 | 0
439.65 | 50.09 | 49.81 | 0.905 | 0.905 | 9.05 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 4.3044 | 4.3044 | 0 | 12 | 1 | 1 | 4.3044 | 10 | 0 | 0
439.7 | 50.12 | 49.83 | 0.715 | 0.805 | 8.05 | 50.12 | -0.24 | -0.24 | -2.4 | 2.825 | 2.825 | 0 | 12 | 1 | 1 | 2.825 | 10 | 0 | 0
439.75 | 50.14 | 49.86 | 0.43 | 0.705 | 7.05 | 50.14 | -0.43 | -0.43 | -4.3 | 1.375 | 1.375 | 0 | 12 | 1 | 1 | 1.375 | 10 | 0 | 0
439.8 | 50.17 | 49.88 | 0.24 | 0.605 | 6.05 | 50.17 | -0.715 | -0.715 | -7.15 | -0.55 | -0.55 | 0 | 12 | 1 | 1 | -0.55 | 10 | 0 | 0
439.85 | 50.19 | 49.91 | 0.044118 | 0.505 | 5.05 | 50.19 | -0.905 | -0.905 | -9.05 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
439.9 | 50.22 | 49.94 | 0.026471 | 0.405 | 4.05 | 50.22 | -1 | -1 | -10 | -2.975 | -2.975 | 0 | 12 | 1 | 1 | -2.975 | 10 | 0 | 0
439.95 | 50.24 | 49.96 | 0.014706 | 0.305 | 3.05 | 50.24 | -1 | -1 | -10 | -3.475 | -3.475 | 0 | 12 | 1 | 1 | -3.475 | 10 | 0 | 0
440 | 50.27 | 49.99 | 0 | 0.205 | 2.05 | 50.27 | -1 | -1 | -10 | -3.975 | -3.975 | 0 | 12 | 1 | 1 | -3.975 | 10 | 0 | 0
440.05 | 50.29 | 50.01 | 0 | 0.105 | 1.05 | 50.29 | -1 | -1 | -10 | -4.475 | -4.475 | 0 | 12 | 1 | 1 | -4.475 | 10 | 0 | 0
440.1 | 50.32 | 50.04 | -0.014706 | 0.005 | 0.05 | 50.32 | -1 | -1 | -10 | -4.975 | -4.975 | 0 | 12 | 1 | 1 | -4.975 | 10 | 0 | 0
440.15 | 50.35 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.35 | -1 | -1 | -10 | -5.1324 | -5.1324 | 0 | 12 | 1 | 1 | -5.1324 | 10 | 0 | 0
440.2 | 50.37 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 50.37 | -1 | -1 | -10 | -5.2206 | -5.2206 | 0 | 12 | 1 | 1 | -5.2206 | 10 | 0 | 0
440.25 | 50.4 | 50.12 | -0.24 | -0.14412 | -1.4412 | 50.4 | -1 | -1 | -10 | -5.7206 | -5.7206 | 0 | 12 | 1 | 1 | -5.7206 | 10 | 0 | 0
440.3 | 50.42 | 50.14 | -0.43 | -0.24412 | -2.4412 | 50.42 | -1 | -1 | -10 | -6.2206 | -6.2206 | 0 | 12 | 1 | 1 | -6.2206 | 10 | 0 | 0
440.35 | 50.45 | 50.17 | -0.715 | -0.34412 | -3.4412 | 50.45 | -1 | -1 | -10 | -6.7206 | -6.7206 | 0 | 12 | 1 | 1 | -6.7206 | 10 | 0 | 0
440.4 | 50.47 | 50.19 | -0.905 | -0.44412 | -4.4412 | 50.47 | -1 | -1 | -10 | -7.2206 | -7.2206 | 0 | 12 | 1 | 1 | -7.2206 | 10 | 0 | 0
440.45 | 50.5 | 50.22 | -1 | -0.54412 | -5.4412 | 50.5 | -1 | -1 | -10 | -7.7206 | -7.7206 | 0 | 12 | 1 | 1 | -7.7206 | 10 | 0 | 0
440.5 | 50.5 | 50.24 | -1 | -0.64412 | -6.4412 | 50.5 | -1 | -1 | -10 | -8.2206 | -8.2206 | 0 | 12 | 1 | 1 | -8.2206 | 10 | 0 | 0
440.55 | 50.47 | 50.27 | -1 | -0.74412 | -7.4412 | 50.5 | -1 | -1 | -10 | -8.7206 | -8.7206 | 0 | 12 | 1 | 1 | -8.7206 | 10 | 0 | 0
440.6 | 50.45 | 50.29 | -1 | -0.84412 | -8.4412 | 50.5 | -1 | -1 | -10 | -9.2206 | -9.2206 | 0 | 12 | 1 | 1 | -9.2206 | 10 | 0 | 0
440.65 | 50.42 | 50.32 | -1 | -0.94412 | -9.4412 | 50.5 | -1 | -1 | -10 | -9.7206 | -9.7206 | 0 | 12 | 1 | 1 | -9.7206 | 10 | 0 | 0
440.7 | 50.39 | 50.35 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
440.75 | 50.37 | 50.37 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
440.8 | 50.34 | 50.34 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
440.85 | 50.32 | 50.32 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
440.9 | 50.29 | 50.29 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
440.95 | 50.26 | 50.26 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
441 | 50.24 | 50.24 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
441.05 | 50.21 | 50.21 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
441.1 | 50.18 | 50.18 | -0.81 | -0.81 | -8.1 | 50.47 | -1 | -1 | -10 | -9.05 | -9.05 | 0 | 12 | 1 | 1 | -9.05 | 10 | 0 | 0
441.15 | 50.16 | 50.16 | -0.62 | -0.62 | -6.2 | 50.45 | -1 | -1 | -10 | -8.1 | -8.1 | 0 | 12 | 1 | 1 | -8.1 | 10 | 0 | 0
441.2 | 50.13 | 50.13 | -0.335 | -0.335 | -3.35 | 50.42 | -1 | -1 | -10 | -6.675 | -6.675 | 0 | 12 | 1 | 1 | -6.675 | 10 | 0 | 0
441.25 | 50.11 | 50.11 | -0.145 | -0.145 | -1.45 | 50.39 | -1 | -1 | -10 | -5.725 | -5.725 | 0 | 12 | 1 | 1 | -5.725 | 10 | 0 | 0
441.3 | 50.08 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 50.37 | -1 | -1 | -10 | -5.1912 | -5.1912 | 0 | 12 | 1 | 1 | -5.1912 | 10 | 0 | 0
441.35 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.34 | -1 | -1 | -10 | -5.1029 | -5.1029 | 0 | 12 | 1 | 1 | -5.1029 | 10 | 0 | 0
441.4 | 50.03 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 50.32 | -1 | -1 | -10 | -5.0441 | -5.0441 | 0 | 12 | 1 | 1 | -5.0441 | 10 | 0 | 0
441.45 | 50 | 50 | 0 | 0 | 0 | 50.29 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
441.5 | 50 | 50 | 0 | 0 | 0 | 50.26 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
441.55 | 50 | 50 | 0 | 0 | 0 | 50.24 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
441.6 | 50 | 50 | 0 | 0 | 0 | 50.21 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
441.65 | 50 | 50 | 0 | 0 | 0 | 50.18 | -0.81 | -0.9 | -9 | -4.5 | -4.5 | 0 | 12 | 1 | 1 | -4.5 | 10 | 0 | 0
441.7 | 50 | 50 | 0 | 0 | 0 | 50.16 | -0.62 | -0.8 | -8 | -4 | -4 | 0 | 12 | 1 | 1 | -4 | 10 | 0 | 0
441.75 | 50 | 50 | 0 | 0 | 0 | 50.13 | -0.335 | -0.7 | -7 | -3.5 | -3.5 | 0 | 12 | 1 | 1 | -3.5 | 10 | 0 | 0
441.8 | 50.01 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.6 | -6 | -3 | -3 | 0 | 12 | 1 | 1 | -3 | 10 | 0 | 0
441.85 | 50.01 | 50 | 0 | 0 | 0 | 50.08 | -0.038235 | -0.5 | -5 | -2.5 | -2.5 | 0 | 12 | 1 | 1 | -2.5 | 10 | 0 | 0
441.9 | 49.99 | 49.99 | 0 | 0 | 0 | 50.05 | -0.020588 | -0.4 | -4 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
441.95 | 49.99 | 49.99 | 0 | 0 | 0 | 50.03 | -0.0088235 | -0.3 | -3 | -1.5 | -1.5 | 0 | 12 | 1 | 1 | -1.5 | 10 | 0 | 0
442 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | -0.2 | -2 | -0.83824 | -0.83824 | 0 | 12 | 1 | 1 | -0.83824 | 10 | 0 | 0
442.05 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | -0.1 | -1 | -0.33824 | -0.33824 | 0 | 12 | 1 | 1 | -0.33824 | 10 | 0 | 0
442.1 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
442.15 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
442.2 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
442.25 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
442.3 | 49.89 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
442.35 | 49.89 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
442.4 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50.01 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
442.45 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
442.5 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
442.55 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 2.7868 | 2.7868 | 0 | 12 | 1 | 1 | 2.7868 | 10 | 0 | 0
442.6 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 2.7868 | 2.7868 | 0 | 12 | 1 | 1 | 2.7868 | 10 | 0 | 0
442.65 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 2.8456 | 2.8456 | 0 | 12 | 1 | 1 | 2.8456 | 10 | 0 | 0
442.7 | 49.94 | 49.85 | 0.525 | 0.525 | 5.25 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 2.7574 | 2.7574 | 0 | 12 | 1 | 1 | 2.7574 | 10 | 0 | 0
442.75 | 49.94 | 49.85 | 0.525 | 0.525 | 5.25 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 2.7574 | 2.7574 | 0 | 12 | 1 | 1 | 2.7574 | 10 | 0 | 0
442.8 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
442.85 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
442.9 | 49.93 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
442.95 | 49.93 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
443 | 49.96 | 49.85 | 0.525 | 0.525 | 5.25 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 2.6985 | 2.6985 | 0 | 12 | 1 | 1 | 2.6985 | 10 | 0 | 0
443.05 | 49.96 | 49.85 | 0.525 | 0.525 | 5.25 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 2.6985 | 2.6985 | 0 | 12 | 1 | 1 | 2.6985 | 10 | 0 | 0
443.1 | 49.99 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
443.15 | 49.99 | 49.91 | 0.044118 | 0.425 | 4.25 | 49.99 | 0 | 0 | 0 | 2.125 | 2.125 | 0 | 12 | 1 | 1 | 2.125 | 10 | 0 | 0
443.2 | 49.99 | 49.91 | 0.044118 | 0.325 | 3.25 | 49.99 | 0 | 0 | 0 | 1.625 | 1.625 | 0 | 12 | 1 | 1 | 1.625 | 10 | 0 | 0
443.25 | 49.99 | 49.93 | 0.032353 | 0.225 | 2.25 | 49.99 | 0 | 0 | 0 | 1.125 | 1.125 | 0 | 12 | 1 | 1 | 1.125 | 10 | 0 | 0
443.3 | 49.96 | 49.93 | 0.032353 | 0.125 | 1.25 | 49.99 | 0 | 0 | 0 | 0.625 | 0.625 | 0 | 12 | 1 | 1 | 0.625 | 10 | 0 | 0
443.35 | 49.96 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 49.99 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
443.4 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
443.45 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
443.5 | 50.05 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.058824 | 0.058824 | 0 | 12 | 1 | 1 | 0.058824 | 10 | 0 | 0
443.55 | 50.05 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
443.6 | 49.97 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
443.65 | 49.97 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
443.7 | 49.92 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
443.75 | 49.92 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
443.8 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
443.85 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
443.9 | 49.94 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
443.95 | 49.94 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
444 | 50.01 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
444.05 | 50.01 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
444.1 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
444.15 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
444.2 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
444.25 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
444.3 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
444.35 | 49.95 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
444.4 | 49.97 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
444.45 | 49.97 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
444.5 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
444.55 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
444.6 | 49.87 | 49.87 | 0.335 | 0.335 | 3.35 | 50.01 | 0 | 0 | 0 | 1.675 | 1.675 | 0 | 12 | 1 | 1 | 1.675 | 10 | 0 | 0
444.65 | 49.87 | 49.87 | 0.335 | 0.335 | 3.35 | 49.99 | 0 | 0 | 0 | 1.675 | 1.675 | 0 | 12 | 1 | 1 | 1.675 | 10 | 0 | 0
444.7 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
444.75 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 2.6691 | 2.6691 | 0 | 12 | 1 | 1 | 2.6691 | 10 | 0 | 0
444.8 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
444.85 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
444.9 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
444.95 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
445 | 49.84 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
445.05 | 49.84 | 49.79 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
445.1 | 49.89 | 49.79 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
445.15 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.12647 | 1.2647 | 5.6324 | 5.6324 | 0 | 12 | 1 | 1 | 5.6324 | 10 | 0 | 0
445.2 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.145 | 1.45 | 5.725 | 5.725 | 0 | 12 | 1 | 1 | 5.725 | 10 | 0 | 0
445.25 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.145 | 1.45 | 5.725 | 5.725 | 0 | 12 | 1 | 1 | 5.725 | 10 | 0 | 0
445.3 | 49.96 | 49.79 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
445.35 | 49.96 | 49.79 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
445.4 | 50.02 | 49.79 | 1 | 1 | 10 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 4.9853 | 4.9853 | 0 | 12 | 1 | 1 | 4.9853 | 10 | 0 | 0
445.45 | 50.02 | 49.79 | 1 | 1 | 10 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 4.9853 | 4.9853 | 0 | 12 | 1 | 1 | 4.9853 | 10 | 0 | 0
445.5 | 50.03 | 49.79 | 1 | 1 | 10 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.9559 | 4.9559 | 0 | 12 | 1 | 1 | 4.9559 | 10 | 0 | 0
445.55 | 50.03 | 49.84 | 0.62 | 0.9 | 9 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.4559 | 4.4559 | 0 | 12 | 1 | 1 | 4.4559 | 10 | 0 | 0
445.6 | 50.02 | 49.84 | 0.62 | 0.8 | 8 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 3.9559 | 3.9559 | 0 | 12 | 1 | 1 | 3.9559 | 10 | 0 | 0
445.65 | 50.02 | 49.89 | 0.145 | 0.7 | 7 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 3.4559 | 3.4559 | 0 | 12 | 1 | 1 | 3.4559 | 10 | 0 | 0
445.7 | 50.08 | 49.89 | 0.145 | 0.6 | 6 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 2.8088 | 2.8088 | 0 | 12 | 1 | 1 | 2.8088 | 10 | 0 | 0
445.75 | 50.08 | 49.89 | 0.145 | 0.5 | 5 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 2.3088 | 2.3088 | 0 | 12 | 1 | 1 | 2.3088 | 10 | 0 | 0
445.8 | 50.01 | 49.89 | 0.145 | 0.4 | 4 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 1.8088 | 1.8088 | 0 | 12 | 1 | 1 | 1.8088 | 10 | 0 | 0
445.85 | 50.01 | 49.96 | 0.014706 | 0.3 | 3 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 1.3088 | 1.3088 | 0 | 12 | 1 | 1 | 1.3088 | 10 | 0 | 0
445.9 | 49.94 | 49.94 | 0.026471 | 0.2 | 2 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.80882 | 0.80882 | 0 | 12 | 1 | 1 | 0.80882 | 10 | 0 | 0
445.95 | 49.94 | 49.94 | 0.026471 | 0.1 | 1 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.30882 | 0.30882 | 0 | 12 | 1 | 1 | 0.30882 | 10 | 0 | 0
446 | 50 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
446.05 | 50 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
446.1 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
446.15 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
446.2 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
446.25 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
446.3 | 49.92 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
446.35 | 49.92 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
446.4 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50.01 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
446.45 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
446.5 | 49.92 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
446.55 | 49.92 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
446.6 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
446.65 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
446.7 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
446.75 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
446.8 | 49.87 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
446.85 | 49.87 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
446.9 | 49.8 | 49.8 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
446.95 | 49.8 | 49.8 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
447 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
447.05 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
447.1 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
447.15 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
447.2 | 49.72 | 49.72 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
447.25 | 49.72 | 49.72 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
447.3 | 49.67 | 49.67 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
447.35 | 49.67 | 49.67 | 1 | 1 | 10 | 49.87 | 0.335 | 0.14412 | 1.4412 | 5.7206 | 5.7206 | 0 | 12 | 1 | 1 | 5.7206 | 10 | 0 | 0
447.4 | 49.65 | 49.65 | 1 | 1 | 10 | 49.87 | 0.335 | 0.24412 | 2.4412 | 6.2206 | 6.2206 | 0 | 12 | 1 | 1 | 6.2206 | 10 | 0 | 0
447.45 | 49.65 | 49.65 | 1 | 1 | 10 | 49.8 | 1 | 0.34412 | 3.4412 | 6.7206 | 6.7206 | 0 | 12 | 1 | 1 | 6.7206 | 10 | 0 | 0
447.5 | 49.59 | 49.59 | 1 | 1 | 10 | 49.8 | 1 | 0.44412 | 4.4412 | 7.2206 | 7.2206 | 0 | 12 | 1 | 1 | 7.2206 | 10 | 0 | 0
447.55 | 49.59 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.54412 | 5.4412 | 7.7206 | 7.7206 | 0 | 12 | 1 | 1 | 7.7206 | 10 | 0 | 0
447.6 | 49.66 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.64412 | 6.4412 | 8.2206 | 8.2206 | 0 | 12 | 1 | 1 | 8.2206 | 10 | 0 | 0
447.65 | 49.66 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.74412 | 7.4412 | 8.7206 | 8.7206 | 0 | 12 | 1 | 1 | 8.7206 | 10 | 0 | 0
447.7 | 49.63 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.84412 | 8.4412 | 9.2206 | 9.2206 | 0 | 12 | 1 | 1 | 9.2206 | 10 | 0 | 0
447.75 | 49.63 | 49.59 | 1 | 1 | 10 | 49.72 | 1 | 0.94412 | 9.4412 | 9.7206 | 9.7206 | 0 | 12 | 1 | 1 | 9.7206 | 10 | 0 | 0
447.8 | 49.61 | 49.59 | 1 | 1 | 10 | 49.72 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
447.85 | 49.61 | 49.59 | 1 | 1 | 10 | 49.67 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
447.9 | 49.54 | 49.54 | 1 | 1 | 10 | 49.67 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
447.95 | 49.54 | 49.54 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
448 | 49.46 | 49.46 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
448.05 | 49.46 | 49.46 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
448.1 | 49.45 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
448.15 | 49.45 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
448.2 | 49.51 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
448.25 | 49.51 | 49.45 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
448.3 | 49.5 | 49.45 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
448.35 | 49.5 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
448.4 | 49.54 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
448.45 | 49.54 | 49.45 | 1 | 1 | 10 | 49.54 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
448.5 | 49.59 | 49.45 | 1 | 1 | 10 | 49.59 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
448.55 | 49.59 | 49.45 | 1 | 1 | 10 | 49.59 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
448.6 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
448.65 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
448.7 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
448.75 | 49.61 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
448.8 | 49.53 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
448.85 | 49.53 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
448.9 | 49.54 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
448.95 | 49.54 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
449 | 49.61 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
449.05 | 49.61 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
449.1 | 49.66 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
449.15 | 49.66 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
449.2 | 49.64 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
449.25 | 49.64 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
449.3 | 49.69 | 49.53 | 1 | 1 | 10 | 49.69 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
449.35 | 49.69 | 49.53 | 1 | 1 | 10 | 49.69 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
449.4 | 49.74 | 49.53 | 1 | 1 | 10 | 49.74 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
449.45 | 49.74 | 49.54 | 1 | 1 | 10 | 49.74 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
449.5 | 49.78 | 49.54 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
449.55 | 49.78 | 49.61 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
449.6 | 49.82 | 49.61 | 1 | 1 | 10 | 49.82 | 0.81 | 0.81 | 8.1 | 9.05 | 9.05 | 0 | 12 | 1 | 1 | 9.05 | 10 | 0 | 0
449.65 | 49.82 | 49.64 | 1 | 1 | 10 | 49.82 | 0.81 | 0.81 | 8.1 | 9.05 | 9.05 | 0 | 12 | 1 | 1 | 9.05 | 10 | 0 | 0
449.7 | 49.86 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
449.75 | 49.86 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
449.8 | 49.84 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
449.85 | 49.84 | 49.69 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
449.9 | 49.91 | 49.69 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
449.95 | 49.91 | 49.74 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
450 | 49.97 | 49.74 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
450.05 | 49.97 | 49.78 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
450.1 | 50.03 | 49.78 | 1 | 1 | 10 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.9559 | 4.9559 | 0 | 12 | 1 | 1 | 4.9559 | 10 | 0 | 0
450.15 | 50.03 | 49.82 | 0.81 | 0.9 | 9 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.4559 | 4.4559 | 0 | 12 | 1 | 1 | 4.4559 | 10 | 0 | 0
450.2 | 50.05 | 49.82 | 0.81 | 0.81 | 8.1 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 3.9471 | 3.9471 | 0 | 12 | 1 | 1 | 3.9471 | 10 | 0 | 0
450.25 | 50.05 | 49.84 | 0.62 | 0.71 | 7.1 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 3.4471 | 3.4471 | 0 | 12 | 1 | 1 | 3.4471 | 10 | 0 | 0
450.3 | 50.01 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
450.35 | 50.01 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
450.4 | 49.95 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
450.45 | 49.95 | 49.91 | 0.044118 | 0.52 | 5.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.4971 | 2.4971 | 0 | 12 | 1 | 1 | 2.4971 | 10 | 0 | 0
450.5 | 49.99 | 49.91 | 0.044118 | 0.42 | 4.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 1.9971 | 1.9971 | 0 | 12 | 1 | 1 | 1.9971 | 10 | 0 | 0
450.55 | 49.99 | 49.95 | 0.020588 | 0.32 | 3.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 1.4971 | 1.4971 | 0 | 12 | 1 | 1 | 1.4971 | 10 | 0 | 0
450.6 | 49.92 | 49.92 | 0.038235 | 0.22 | 2.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.99706 | 0.99706 | 0 | 12 | 1 | 1 | 0.99706 | 10 | 0 | 0
450.65 | 49.92 | 49.92 | 0.038235 | 0.12 | 1.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.49706 | 0.49706 | 0 | 12 | 1 | 1 | 0.49706 | 10 | 0 | 0
450.7 | 49.97 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
450.75 | 49.97 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
450.8 | 50.02 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
450.85 | 50.02 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.17647 | 0.17647 | 0 | 12 | 1 | 1 | 0.17647 | 10 | 0 | 0
450.9 | 50.07 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
450.95 | 50.07 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
451 | 50.06 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
451.05 | 50.06 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
451.1 | 50.13 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
451.15 | 50.13 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
451.2 | 50.09 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
451.25 | 50.09 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6309 | -1.6309 | 0 | 12 | 1 | 1 | -1.6309 | 10 | 0 | 0
451.3 | 50.07 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6309 | -1.6309 | 0 | 12 | 1 | 1 | -1.6309 | 10 | 0 | 0
451.35 | 50.07 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6897 | -1.6897 | 0 | 12 | 1 | 1 | -1.6897 | 10 | 0 | 0
451.4 | 50.07 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6897 | -1.6897 | 0 | 12 | 1 | 1 | -1.6897 | 10 | 0 | 0
451.45 | 50.07 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.13 | -0.335 | -0.335 | -3.35 | -1.8074 | -1.8074 | 0 | 12 | 1 | 1 | -1.8074 | 10 | 0 | 0
451.5 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.13 | -0.335 | -0.335 | -3.35 | -1.7779 | -1.7779 | 0 | 12 | 1 | 1 | -1.7779 | 10 | 0 | 0
451.55 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.13 | -0.335 | -0.335 | -3.35 | -1.7779 | -1.7779 | 0 | 12 | 1 | 1 | -1.7779 | 10 | 0 | 0
451.6 | 50.01 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
451.65 | 50.01 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
451.7 | 50.07 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
451.75 | 50.07 | 50.01 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.235 | -2.35 | -1.175 | -1.175 | 0 | 12 | 1 | 1 | -1.175 | 10 | 0 | 0
451.8 | 50.05 | 50.01 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.135 | -1.35 | -0.675 | -0.675 | 0 | 12 | 1 | 1 | -0.675 | 10 | 0 | 0
451.85 | 50.05 | 50.01 | 0 | 0 | 0 | 50.07 | -0.032353 | -0.035 | -0.35 | -0.175 | -0.175 | 0 | 12 | 1 | 1 | -0.175 | 10 | 0 | 0
451.9 | 50.1 | 50.01 | 0 | 0 | 0 | 50.1 | -0.05 | -0.05 | -0.5 | -0.25 | -0.25 | 0 | 12 | 1 | 1 | -0.25 | 10 | 0 | 0
451.95 | 50.1 | 50.01 | 0 | 0 | 0 | 50.1 | -0.05 | -0.05 | -0.5 | -0.25 | -0.25 | 0 | 12 | 1 | 1 | -0.25 | 10 | 0 | 0
452 | 50.11 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
452.05 | 50.11 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
452.1 | 50.06 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
452.15 | 50.06 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
452.2 | 50.04 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
452.25 | 50.04 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
452.3 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
452.35 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
452.4 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
452.45 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
452.5 | 50.11 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
452.55 | 50.11 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
452.6 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
452.65 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
452.7 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
452.75 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
452.8 | 50.02 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.11 | -0.145 | -0.145 | -1.45 | -0.73971 | -0.73971 | 0 | 12 | 1 | 1 | -0.73971 | 10 | 0 | 0
452.85 | 50.02 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.11 | -0.145 | -0.145 | -1.45 | -0.73971 | -0.73971 | 0 | 12 | 1 | 1 | -0.73971 | 10 | 0 | 0
452.9 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
452.95 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
453 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
453.05 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
453.1 | 50.01 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
453.15 | 50.01 | 50 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.045 | -0.45 | -0.225 | -0.225 | 0 | 12 | 1 | 1 | -0.225 | 10 | 0 | 0
453.2 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
453.25 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
453.3 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
453.35 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
453.4 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.14706 | 0.14706 | 0 | 12 | 1 | 1 | 0.14706 | 10 | 0 | 0
453.45 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
453.5 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
453.55 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
453.6 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
453.65 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
453.7 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
453.75 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
453.8 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
453.85 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
453.9 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
453.95 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
454 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
454.05 | 50 | 50 | 0 | 0 | 0 | 50.01 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
454.1 | 49.5 | 49.5 | 1 | 1 | 10 | 50.01 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
454.15 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
454.2 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
454.25 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
454.3 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
454.35 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
454.4 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
454.45 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
454.5 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
454.55 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
454.6 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
454.65 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.1 | 1 | 5.5 | 5.5 | 0 | 12 | 1 | 1 | 5.5 | 10 | 0 | 0
454.7 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.2 | 2 | 6 | 6 | 0 | 12 | 1 | 1 | 6 | 10 | 0 | 0
454.75 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.3 | 3 | 6.5 | 6.5 | 0 | 12 | 1 | 1 | 6.5 | 10 | 0 | 0
454.8 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.4 | 4 | 7 | 7 | 0 | 12 | 1 | 1 | 7 | 10 | 0 | 0
454.85 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.5 | 5 | 7.5 | 7.5 | 0 | 12 | 1 | 1 | 7.5 | 10 | 0 | 0
454.9 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.6 | 6 | 8 | 8 | 0 | 12 | 1 | 1 | 8 | 10 | 0 | 0
454.95 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.7 | 7 | 8.5 | 8.5 | 0 | 12 | 1 | 1 | 8.5 | 10 | 0 | 0
455 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.8 | 8 | 9 | 9 | 0 | 12 | 1 | 1 | 9 | 10 | 0 | 0
455.05 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.9 | 9 | 9.5 | 9.5 | 0 | 12 | 1 | 1 | 9.5 | 10 | 0 | 0
455.1 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
455.15 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
455.2 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
455.25 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
455.3 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
455.35 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
455.4 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
455.45 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
455.5 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
455.55 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
455.6 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
455.65 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
455.7 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
455.75 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
455.8 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
455.85 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
455.9 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
455.95 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
456 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
456.05 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
456.1 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
456.15 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
456.2 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
456.25 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
456.3 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
456.35 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
456.4 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
456.45 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
456.5 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
456.55 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
456.6 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
456.65 | 50.5 | 50.5 | -1 | 0.9 | 9 | 50.5 | -1 | -1 | -10 | -0.5 | -0.5 | 0 | 12 | 1 | 1 | -0.5 | 10 | 0 | 0
456.7 | 50.5 | 50.5 | -1 | 0.8 | 8 | 50.5 | -1 | -1 | -10 | -1 | -1 | 0 | 12 | 1 | 1 | -1 | 10 | 0 | 0
456.75 | 50.5 | 50.5 | -1 | 0.7 | 7 | 50.5 | -1 | -1 | -10 | -1.5 | -1.5 | 0 | 12 | 1 | 1 | -1.5 | 10 | 0 | 0
456.8 | 50.5 | 50.5 | -1 | 0.6 | 6 | 50.5 | -1 | -1 | -10 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
456.85 | 50.5 | 50.5 | -1 | 0.5 | 5 | 50.5 | -1 | -1 | -10 | -2.5 | -2.5 | 0 | 12 | 1 | 1 | -2.5 | 10 | 0 | 0
456.9 | 50.5 | 50.5 | -1 | 0.4 | 4 | 50.5 | -1 | -1 | -10 | -3 | -3 | 0 | 12 | 1 | 1 | -3 | 10 | 0 | 0
456.95 | 50.5 | 50.5 | -1 | 0.3 | 3 | 50.5 | -1 | -1 | -10 | -3.5 | -3.5 | 0 | 12 | 1 | 1 | -3.5 | 10 | 0 | 0
457 | 50.5 | 50.5 | -1 | 0.2 | 2 | 50.5 | -1 | -1 | -10 | -4 | -4 | 0 | 12 | 1 | 1 | -4 | 10 | 0 | 0
457.05 | 50.5 | 50.5 | -1 | 0.1 | 1 | 50.5 | -1 | -1 | -10 | -4.5 | -4.5 | 0 | 12 | 1 | 1 | -4.5 | 10 | 0 | 0
457.1 | 50.5 | 50.5 | -1 | 0 | 0 | 50.5 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
457.15 | 50.5 | 50.5 | -1 | -0.1 | -1 | 50.5 | -1 | -1 | -10 | -5.5 | -5.5 | 0 | 12 | 1 | 1 | -5.5 | 10 | 0 | 0
457.2 | 50.5 | 50.5 | -1 | -0.2 | -2 | 50.5 | -1 | -1 | -10 | -6 | -6 | 0 | 12 | 1 | 1 | -6 | 10 | 0 | 0
457.25 | 50.5 | 50.5 | -1 | -0.3 | -3 | 50.5 | -1 | -1 | -10 | -6.5 | -6.5 | 0 | 12 | 1 | 1 | -6.5 | 10 | 0 | 0
457.3 | 50.5 | 50.5 | -1 | -0.4 | -4 | 50.5 | -1 | -1 | -10 | -7 | -7 | 0 | 12 | 1 | 1 | -7 | 10 | 0 | 0
457.35 | 50.5 | 50.5 | -1 | -0.5 | -5 | 50.5 | -1 | -1 | -10 | -7.5 | -7.5 | 0 | 12 | 1 | 1 | -7.5 | 10 | 0 | 0
457.4 | 50.5 | 50.5 | -1 | -0.6 | -6 | 50.5 | -1 | -1 | -10 | -8 | -8 | 0 | 12 | 1 | 1 | -8 | 10 | 0 | 0
457.45 | 50.5 | 50.5 | -1 | -0.7 | -7 | 50.5 | -1 | -1 | -10 | -8.5 | -8.5 | 0 | 12 | 1 | 1 | -8.5 | 10 | 0 | 0
457.5 | 50.5 | 50.5 | -1 | -0.8 | -8 | 50.5 | -1 | -1 | -10 | -9 | -9 | 0 | 12 | 1 | 1 | -9 | 10 | 0 | 0
457.55 | 50.5 | 50.5 | -1 | -0.9 | -9 | 50.5 | -1 | -1 | -10 | -9.5 | -9.5 | 0 | 12 | 1 | 1 | -9.5 | 10 | 0 | 0
457.6 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
457.65 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
457.7 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
457.75 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
457.8 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
457.85 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
457.9 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
457.95 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
458 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
458.05 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
458.1 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
458.15 | 50.47 | 50.47 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
458.2 | 50.45 | 50.45 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
458.25 | 50.42 | 50.42 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
458.3 | 50.4 | 50.4 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
458.35 | 50.37 | 50.37 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
458.4 | 50.35 | 50.35 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
458.45 | 50.32 | 50.32 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
458.5 | 50.29 | 50.29 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
458.55 | 50.27 | 50.27 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
458.6 | 50.24 | 50.24 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
458.65 | 50.22 | 50.22 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
458.7 | 50.19 | 50.19 | -0.905 | -0.905 | -9.05 | 50.47 | -1 | -1 | -10 | -9.525 | -9.525 | 0 | 12 | 1 | 1 | -9.525 | 10 | 0 | 0
458.75 | 50.17 | 50.17 | -0.715 | -0.715 | -7.15 | 50.45 | -1 | -1 | -10 | -8.575 | -8.575 | 0 | 12 | 1 | 1 | -8.575 | 10 | 0 | 0
458.8 | 50.14 | 50.14 | -0.43 | -0.43 | -4.3 | 50.42 | -1 | -1 | -10 | -7.15 | -7.15 | 0 | 12 | 1 | 1 | -7.15 | 10 | 0 | 0
458.85 | 50.12 | 50.12 | -0.24 | -0.24 | -2.4 | 50.4 | -1 | -1 | -10 | -6.2 | -6.2 | 0 | 12 | 1 | 1 | -6.2 | 10 | 0 | 0
458.9 | 50.09 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 50.37 | -1 | -1 | -10 | -5.2206 | -5.2206 | 0 | 12 | 1 | 1 | -5.2206 | 10 | 0 | 0
458.95 | 50.06 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.35 | -1 | -1 | -10 | -5.1324 | -5.1324 | 0 | 12 | 1 | 1 | -5.1324 | 10 | 0 | 0
459 | 50.04 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.32 | -1 | -1 | -10 | -5.0735 | -5.0735 | 0 | 12 | 1 | 1 | -5.0735 | 10 | 0 | 0
459.05 | 50.01 | 50.01 | 0 | 0 | 0 | 50.29 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
459.1 | 49.99 | 49.99 | 0 | 0 | 0 | 50.27 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
459.15 | 49.96 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.24 | -1 | -1 | -10 | -4.9265 | -4.9265 | 0 | 12 | 1 | 1 | -4.9265 | 10 | 0 | 0
459.2 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.22 | -1 | -1 | -10 | -4.8676 | -4.8676 | 0 | 12 | 1 | 1 | -4.8676 | 10 | 0 | 0
459.25 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.19 | -0.905 | -0.905 | -9.05 | -4.3044 | -4.3044 | 0 | 12 | 1 | 1 | -4.3044 | 10 | 0 | 0
459.3 | 49.88 | 49.88 | 0.24 | 0.24 | 2.4 | 50.17 | -0.715 | -0.805 | -8.05 | -2.825 | -2.825 | 0 | 12 | 1 | 1 | -2.825 | 10 | 0 | 0
459.35 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.14 | -0.43 | -0.705 | -7.05 | -1.375 | -1.375 | 0 | 12 | 1 | 1 | -1.375 | 10 | 0 | 0
459.4 | 49.83 | 49.83 | 0.715 | 0.715 | 7.15 | 50.12 | -0.24 | -0.605 | -6.05 | 0.55 | 0.55 | 0 | 12 | 1 | 1 | 0.55 | 10 | 0 | 0
459.45 | 49.81 | 49.81 | 0.905 | 0.905 | 9.05 | 50.09 | -0.044118 | -0.505 | -5.05 | 2 | 2 | 0 | 12 | 1 | 1 | 2 | 10 | 0 | 0
459.5 | 49.78 | 49.78 | 1 | 1 | 10 | 50.06 | -0.026471 | -0.405 | -4.05 | 2.975 | 2.975 | 0 | 12 | 1 | 1 | 2.975 | 10 | 0 | 0
459.55 | 49.76 | 49.76 | 1 | 1 | 10 | 50.04 | -0.014706 | -0.305 | -3.05 | 3.475 | 3.475 | 0 | 12 | 1 | 1 | 3.475 | 10 | 0 | 0
459.6 | 49.73 | 49.73 | 1 | 1 | 10 | 50.01 | 0 | -0.205 | -2.05 | 3.975 | 3.975 | 0 | 12 | 1 | 1 | 3.975 | 10 | 0 | 0
459.65 | 49.71 | 49.71 | 1 | 1 | 10 | 49.99 | 0 | -0.105 | -1.05 | 4.475 | 4.475 | 0 | 12 | 1 | 1 | 4.475 | 10 | 0 | 0
459.7 | 49.68 | 49.68 | 1 | 1 | 10 | 49.96 | 0.014706 | -0.005 | -0.05 | 4.975 | 4.975 | 0 | 12 | 1 | 1 | 4.975 | 10 | 0 | 0
459.75 | 49.65 | 49.65 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
459.8 | 49.63 | 49.63 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
459.85 | 49.6 | 49.6 | 1 | 1 | 10 | 49.88 | 0.24 | 0.14412 | 1.4412 | 5.7206 | 5.7206 | 0 | 12 | 1 | 1 | 5.7206 | 10 | 0 | 0
459.9 | 49.58 | 49.58 | 1 | 1 | 10 | 49.86 | 0.43 | 0.24412 | 2.4412 | 6.2206 | 6.2206 | 0 | 12 | 1 | 1 | 6.2206 | 10 | 0 | 0
459.95 | 49.55 | 49.55 | 1 | 1 | 10 | 49.83 | 0.715 | 0.34412 | 3.4412 | 6.7206 | 6.7206 | 0 | 12 | 1 | 1 | 6.7206 | 10 | 0 | 0
460 | 49.53 | 49.53 | 1 | 1 | 10 | 49.81 | 0.905 | 0.44412 | 4.4412 | 7.2206 | 7.2206 | 0 | 12 | 1 | 1 | 7.2206 | 10 | 0 | 0
460.05 | 49.5 | 49.5 | 1 | 1 | 10 | 49.78 | 1 | 0.54412 | 5.4412 | 7.7206 | 7.7206 | 0 | 12 | 1 | 1 | 7.7206 | 10 | 0 | 0
460.1 | 49.5 | 49.5 | 1 | 1 | 10 | 49.76 | 1 | 0.64412 | 6.4412 | 8.2206 | 8.2206 | 0 | 12 | 1 | 1 | 8.2206 | 10 | 0 | 0
460.15 | 49.53 | 49.5 | 1 | 1 | 10 | 49.73 | 1 | 0.74412 | 7.4412 | 8.7206 | 8.7206 | 0 | 12 | 1 | 1 | 8.7206 | 10 | 0 | 0
460.2 | 49.55 | 49.5 | 1 | 1 | 10 | 49.71 | 1 | 0.84412 | 8.4412 | 9.2206 | 9.2206 | 0 | 12 | 1 | 1 | 9.2206 | 10 | 0 | 0
460.25 | 49.58 | 49.5 | 1 | 1 | 10 | 49.68 | 1 | 0.94412 | 9.4412 | 9.7206 | 9.7206 | 0 | 12 | 1 | 1 | 9.7206 | 10 | 0 | 0
460.3 | 49.6 | 49.5 | 1 | 1 | 10 | 49.65 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
460.35 | 49.63 | 49.5 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
460.4 | 49.65 | 49.5 | 1 | 1 | 10 | 49.65 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
460.45 | 49.68 | 49.5 | 1 | 1 | 10 | 49.68 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
460.5 | 49.71 | 49.5 | 1 | 1 | 10 | 49.71 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
460.55 | 49.73 | 49.5 | 1 | 1 | 10 | 49.73 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
460.6 | 49.76 | 49.5 | 1 | 1 | 10 | 49.76 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
460.65 | 49.78 | 49.5 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
460.7 | 49.81 | 49.53 | 1 | 1 | 10 | 49.81 | 0.905 | 0.905 | 9.05 | 9.525 | 9.525 | 0 | 12 | 1 | 1 | 9.525 | 10 | 0 | 0
460.75 | 49.83 | 49.55 | 1 | 1 | 10 | 49.83 | 0.715 | 0.715 | 7.15 | 8.575 | 8.575 | 0 | 12 | 1 | 1 | 8.575 | 10 | 0 | 0
460.8 | 49.86 | 49.58 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
460.85 | 49.88 | 49.6 | 1 | 1 | 10 | 49.88 | 0.24 | 0.24 | 2.4 | 6.2 | 6.2 | 0 | 12 | 1 | 1 | 6.2 | 10 | 0 | 0
460.9 | 49.91 | 49.63 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
460.95 | 49.94 | 49.65 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
461 | 49.96 | 49.68 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
461.05 | 49.99 | 49.71 | 1 | 1 | 10 | 49.99 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
461.1 | 50.01 | 49.73 | 1 | 1 | 10 | 50.01 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
461.15 | 50.04 | 49.76 | 1 | 1 | 10 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 4.9265 | 4.9265 | 0 | 12 | 1 | 1 | 4.9265 | 10 | 0 | 0
461.2 | 50.06 | 49.78 | 1 | 1 | 10 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 4.8676 | 4.8676 | 0 | 12 | 1 | 1 | 4.8676 | 10 | 0 | 0
461.25 | 50.09 | 49.81 | 0.905 | 0.905 | 9.05 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 4.3044 | 4.3044 | 0 | 12 | 1 | 1 | 4.3044 | 10 | 0 | 0
461.3 | 50.12 | 49.83 | 0.715 | 0.805 | 8.05 | 50.12 | -0.24 | -0.24 | -2.4 | 2.825 | 2.825 | 0 | 12 | 1 | 1 | 2.825 | 10 | 0 | 0
461.35 | 50.14 | 49.86 | 0.43 | 0.705 | 7.05 | 50.14 | -0.43 | -0.43 | -4.3 | 1.375 | 1.375 | 0 | 12 | 1 | 1 | 1.375 | 10 | 0 | 0
461.4 | 50.17 | 49.88 | 0.24 | 0.605 | 6.05 | 50.17 | -0.715 | -0.715 | -7.15 | -0.55 | -0.55 | 0 | 12 | 1 | 1 | -0.55 | 10 | 0 | 0
461.45 | 50.19 | 49.91 | 0.044118 | 0.505 | 5.05 | 50.19 | -0.905 | -0.905 | -9.05 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
461.5 | 50.22 | 49.94 | 0.026471 | 0.405 | 4.05 | 50.22 | -1 | -1 | -10 | -2.975 | -2.975 | 0 | 12 | 1 | 1 | -2.975 | 10 | 0 | 0
461.55 | 50.24 | 49.96 | 0.014706 | 0.305 | 3.05 | 50.24 | -1 | -1 | -10 | -3.475 | -3.475 | 0 | 12 | 1 | 1 | -3.475 | 10 | 0 | 0
461.6 | 50.27 | 49.99 | 0 | 0.205 | 2.05 | 50.27 | -1 | -1 | -10 | -3.975 | -3.975 | 0 | 12 | 1 | 1 | -3.975 | 10 | 0 | 0
461.65 | 50.29 | 50.01 | 0 | 0.105 | 1.05 | 50.29 | -1 | -1 | -10 | -4.475 | -4.475 | 0 | 12 | 1 | 1 | -4.475 | 10 | 0 | 0
461.7 | 50.32 | 50.04 | -0.014706 | 0.005 | 0.05 | 50.32 | -1 | -1 | -10 | -4.975 | -4.975 | 0 | 12 | 1 | 1 | -4.975 | 10 | 0 | 0
461.75 | 50.35 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.35 | -1 | -1 | -10 | -5.1324 | -5.1324 | 0 | 12 | 1 | 1 | -5.1324 | 10 | 0 | 0
461.8 | 50.37 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 50.37 | -1 | -1 | -10 | -5.2206 | -5.2206 | 0 | 12 | 1 | 1 | -5.2206 | 10 | 0 | 0
461.85 | 50.4 | 50.12 | -0.24 | -0.14412 | -1.4412 | 50.4 | -1 | -1 | -10 | -5.7206 | -5.7206 | 0 | 12 | 1 | 1 | -5.7206 | 10 | 0 | 0
461.9 | 50.42 | 50.14 | -0.43 | -0.24412 | -2.4412 | 50.42 | -1 | -1 | -10 | -6.2206 | -6.2206 | 0 | 12 | 1 | 1 | -6.2206 | 10 | 0 | 0
461.95 | 50.45 | 50.17 | -0.715 | -0.34412 | -3.4412 | 50.45 | -1 | -1 | -10 | -6.7206 | -6.7206 | 0 | 12 | 1 | 1 | -6.7206 | 10 | 0 | 0
462 | 50.47 | 50.19 | -0.905 | -0.44412 | -4.4412 | 50.47 | -1 | -1 | -10 | -7.2206 | -7.2206 | 0 | 12 | 1 | 1 | -7.2206 | 10 | 0 | 0
462.05 | 50.5 | 50.22 | -1 | -0.54412 | -5.4412 | 50.5 | -1 | -1 | -10 | -7.7206 | -7.7206 | 0 | 12 | 1 | 1 | -7.7206 | 10 | 0 | 0
462.1 | 50.5 | 50.24 | -1 | -0.64412 | -6.4412 | 50.5 | -1 | -1 | -10 | -8.2206 | -8.2206 | 0 | 12 | 1 | 1 | -8.2206 | 10 | 0 | 0
462.15 | 50.47 | 50.27 | -1 | -0.74412 | -7.4412 | 50.5 | -1 | -1 | -10 | -8.7206 | -8.7206 | 0 | 12 | 1 | 1 | -8.7206 | 10 | 0 | 0
462.2 | 50.45 | 50.29 | -1 | -0.84412 | -8.4412 | 50.5 | -1 | -1 | -10 | -9.2206 | -9.2206 | 0 | 12 | 1 | 1 | -9.2206 | 10 | 0 | 0
462.25 | 50.42 | 50.32 | -1 | -0.94412 | -9.4412 | 50.5 | -1 | -1 | -10 | -9.7206 | -9.7206 | 0 | 12 | 1 | 1 | -9.7206 | 10 | 0 | 0
462.3 | 50.39 | 50.35 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
462.35 | 50.37 | 50.37 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
462.4 | 50.34 | 50.34 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
462.45 | 50.32 | 50.32 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
462.5 | 50.29 | 50.29 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
462.55 | 50.26 | 50.26 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
462.6 | 50.24 | 50.24 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
462.65 | 50.21 | 50.21 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
462.7 | 50.18 | 50.18 | -0.81 | -0.81 | -8.1 | 50.47 | -1 | -1 | -10 | -9.05 | -9.05 | 0 | 12 | 1 | 1 | -9.05 | 10 | 0 | 0
462.75 | 50.16 | 50.16 | -0.62 | -0.62 | -6.2 | 50.45 | -1 | -1 | -10 | -8.1 | -8.1 | 0 | 12 | 1 | 1 | -8.1 | 10 | 0 | 0
462.8 | 50.13 | 50.13 | -0.335 | -0.335 | -3.35 | 50.42 | -1 | -1 | -10 | -6.675 | -6.675 | 0 | 12 | 1 | 1 | -6.675 | 10 | 0 | 0
462.85 | 50.11 | 50.11 | -0.145 | -0.145 | -1.45 | 50.39 | -1 | -1 | -10 | -5.725 | -5.725 | 0 | 12 | 1 | 1 | -5.725 | 10 | 0 | 0
462.9 | 50.08 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 50.37 | -1 | -1 | -10 | -5.1912 | -5.1912 | 0 | 12 | 1 | 1 | -5.1912 | 10 | 0 | 0
462.95 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.34 | -1 | -1 | -10 | -5.1029 | -5.1029 | 0 | 12 | 1 | 1 | -5.1029 | 10 | 0 | 0
463 | 50.03 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 50.32 | -1 | -1 | -10 | -5.0441 | -5.0441 | 0 | 12 | 1 | 1 | -5.0441 | 10 | 0 | 0
463.05 | 50 | 50 | 0 | 0 | 0 | 50.29 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
463.1 | 50 | 50 | 0 | 0 | 0 | 50.26 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
463.15 | 50 | 50 | 0 | 0 | 0 | 50.24 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
463.2 | 50 | 50 | 0 | 0 | 0 | 50.21 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
463.25 | 50 | 50 | 0 | 0 | 0 | 50.18 | -0.81 | -0.9 | -9 | -4.5 | -4.5 | 0 | 12 | 1 | 1 | -4.5 | 10 | 0 | 0
463.3 | 50 | 50 | 0 | 0 | 0 | 50.16 | -0.62 | -0.8 | -8 | -4 | -4 | 0 | 12 | 1 | 1 | -4 | 10 | 0 | 0
463.35 | 50 | 50 | 0 | 0 | 0 | 50.13 | -0.335 | -0.7 | -7 | -3.5 | -3.5 | 0 | 12 | 1 | 1 | -3.5 | 10 | 0 | 0
463.4 | 50.01 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.6 | -6 | -3 | -3 | 0 | 12 | 1 | 1 | -3 | 10 | 0 | 0
463.45 | 50.01 | 50 | 0 | 0 | 0 | 50.08 | -0.038235 | -0.5 | -5 | -2.5 | -2.5 | 0 | 12 | 1 | 1 | -2.5 | 10 | 0 | 0
463.5 | 49.99 | 49.99 | 0 | 0 | 0 | 50.05 | -0.020588 | -0.4 | -4 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
463.55 | 49.99 | 49.99 | 0 | 0 | 0 | 50.03 | -0.0088235 | -0.3 | -3 | -1.5 | -1.5 | 0 | 12 | 1 | 1 | -1.5 | 10 | 0 | 0
463.6 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | -0.2 | -2 | -0.83824 | -0.83824 | 0 | 12 | 1 | 1 | -0.83824 | 10 | 0 | 0
463.65 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | -0.1 | -1 | -0.33824 | -0.33824 | 0 | 12 | 1 | 1 | -0.33824 | 10 | 0 | 0
463.7 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
463.75 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
463.8 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
463.85 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
463.9 | 49.89 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
463.95 | 49.89 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
464 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50.01 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
464.05 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
464.1 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
464.15 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 2.7868 | 2.7868 | 0 | 12 | 1 | 1 | 2.7868 | 10 | 0 | 0
464.2 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 2.7868 | 2.7868 | 0 | 12 | 1 | 1 | 2.7868 | 10 | 0 | 0
464.25 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 2.8456 | 2.8456 | 0 | 12 | 1 | 1 | 2.8456 | 10 | 0 | 0
464.3 | 49.94 | 49.85 | 0.525 | 0.525 | 5.25 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 2.7574 | 2.7574 | 0 | 12 | 1 | 1 | 2.7574 | 10 | 0 | 0
464.35 | 49.94 | 49.85 | 0.525 | 0.525 | 5.25 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 2.7574 | 2.7574 | 0 | 12 | 1 | 1 | 2.7574 | 10 | 0 | 0
464.4 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
464.45 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
464.5 | 49.93 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
464.55 | 49.93 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
464.6 | 49.96 | 49.85 | 0.525 | 0.525 | 5.25 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 2.6985 | 2.6985 | 0 | 12 | 1 | 1 | 2.6985 | 10 | 0 | 0
464.65 | 49.96 | 49.85 | 0.525 | 0.525 | 5.25 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 2.6985 | 2.6985 | 0 | 12 | 1 | 1 | 2.6985 | 10 | 0 | 0
464.7 | 49.99 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
464.75 | 49.99 | 49.91 | 0.044118 | 0.425 | 4.25 | 49.99 | 0 | 0 | 0 | 2.125 | 2.125 | 0 | 12 | 1 | 1 | 2.125 | 10 | 0 | 0
464.8 | 49.99 | 49.91 | 0.044118 | 0.325 | 3.25 | 49.99 | 0 | 0 | 0 | 1.625 | 1.625 | 0 | 12 | 1 | 1 | 1.625 | 10 | 0 | 0
464.85 | 49.99 | 49.93 | 0.032353 | 0.225 | 2.25 | 49.99 | 0 | 0 | 0 | 1.125 | 1.125 | 0 | 12 | 1 | 1 | 1.125 | 10 | 0 | 0
464.9 | 49.96 | 49.93 | 0.032353 | 0.125 | 1.25 | 49.99 | 0 | 0 | 0 | 0.625 | 0.625 | 0 | 12 | 1 | 1 | 0.625 | 10 | 0 | 0
464.95 | 49.96 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 49.99 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
465 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
465.05 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
465.1 | 50.05 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.058824 | 0.058824 | 0 | 12 | 1 | 1 | 0.058824 | 10 | 0 | 0
465.15 | 50.05 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
465.2 | 49.97 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
465.25 | 49.97 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
465.3 | 49.92 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
465.35 | 49.92 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
465.4 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
465.45 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
465.5 | 49.94 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
465.55 | 49.94 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
465.6 | 50.01 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
465.65 | 50.01 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
465.7 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
465.75 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
465.8 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
465.85 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
465.9 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
465.95 | 49.95 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
466 | 49.97 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
466.05 | 49.97 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
466.1 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
466.15 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
466.2 | 49.87 | 49.87 | 0.335 | 0.335 | 3.35 | 50.01 | 0 | 0 | 0 | 1.675 | 1.675 | 0 | 12 | 1 | 1 | 1.675 | 10 | 0 | 0
466.25 | 49.87 | 49.87 | 0.335 | 0.335 | 3.35 | 49.99 | 0 | 0 | 0 | 1.675 | 1.675 | 0 | 12 | 1 | 1 | 1.675 | 10 | 0 | 0
466.3 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
466.35 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 2.6691 | 2.6691 | 0 | 12 | 1 | 1 | 2.6691 | 10 | 0 | 0
466.4 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
466.45 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
466.5 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
466.55 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
466.6 | 49.84 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
466.65 | 49.84 | 49.79 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
466.7 | 49.89 | 49.79 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
466.75 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.12647 | 1.2647 | 5.6324 | 5.6324 | 0 | 12 | 1 | 1 | 5.6324 | 10 | 0 | 0
466.8 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.145 | 1.45 | 5.725 | 5.725 | 0 | 12 | 1 | 1 | 5.725 | 10 | 0 | 0
466.85 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.145 | 1.45 | 5.725 | 5.725 | 0 | 12 | 1 | 1 | 5.725 | 10 | 0 | 0
466.9 | 49.96 | 49.79 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
466.95 | 49.96 | 49.79 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
467 | 50.02 | 49.79 | 1 | 1 | 10 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 4.9853 | 4.9853 | 0 | 12 | 1 | 1 | 4.9853 | 10 | 0 | 0
467.05 | 50.02 | 49.79 | 1 | 1 | 10 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 4.9853 | 4.9853 | 0 | 12 | 1 | 1 | 4.9853 | 10 | 0 | 0
467.1 | 50.03 | 49.79 | 1 | 1 | 10 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.9559 | 4.9559 | 0 | 12 | 1 | 1 | 4.9559 | 10 | 0 | 0
467.15 | 50.03 | 49.84 | 0.62 | 0.9 | 9 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.4559 | 4.4559 | 0 | 12 | 1 | 1 | 4.4559 | 10 | 0 | 0
467.2 | 50.02 | 49.84 | 0.62 | 0.8 | 8 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 3.9559 | 3.9559 | 0 | 12 | 1 | 1 | 3.9559 | 10 | 0 | 0
467.25 | 50.02 | 49.89 | 0.145 | 0.7 | 7 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 3.4559 | 3.4559 | 0 | 12 | 1 | 1 | 3.4559 | 10 | 0 | 0
467.3 | 50.08 | 49.89 | 0.145 | 0.6 | 6 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 2.8088 | 2.8088 | 0 | 12 | 1 | 1 | 2.8088 | 10 | 0 | 0
467.35 | 50.08 | 49.89 | 0.145 | 0.5 | 5 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 2.3088 | 2.3088 | 0 | 12 | 1 | 1 | 2.3088 | 10 | 0 | 0
467.4 | 50.01 | 49.89 | 0.145 | 0.4 | 4 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 1.8088 | 1.8088 | 0 | 12 | 1 | 1 | 1.8088 | 10 | 0 | 0
467.45 | 50.01 | 49.96 | 0.014706 | 0.3 | 3 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 1.3088 | 1.3088 | 0 | 12 | 1 | 1 | 1.3088 | 10 | 0 | 0
467.5 | 49.94 | 49.94 | 0.026471 | 0.2 | 2 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.80882 | 0.80882 | 0 | 12 | 1 | 1 | 0.80882 | 10 | 0 | 0
467.55 | 49.94 | 49.94 | 0.026471 | 0.1 | 1 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.30882 | 0.30882 | 0 | 12 | 1 | 1 | 0.30882 | 10 | 0 | 0
467.6 | 50 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
467.65 | 50 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
467.7 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
467.75 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
467.8 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
467.85 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
467.9 | 49.92 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
467.95 | 49.92 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
468 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50.01 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
468.05 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
468.1 | 49.92 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
468.15 | 49.92 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
468.2 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
468.25 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
468.3 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
468.35 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
468.4 | 49.87 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
468.45 | 49.87 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
468.5 | 49.8 | 49.8 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
468.55 | 49.8 | 49.8 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
468.6 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
468.65 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
468.7 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
468.75 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
468.8 | 49.72 | 49.72 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
468.85 | 49.72 | 49.72 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
468.9 | 49.67 | 49.67 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
468.95 | 49.67 | 49.67 | 1 | 1 | 10 | 49.87 | 0.335 | 0.14412 | 1.4412 | 5.7206 | 5.7206 | 0 | 12 | 1 | 1 | 5.7206 | 10 | 0 | 0
469 | 49.65 | 49.65 | 1 | 1 | 10 | 49.87 | 0.335 | 0.24412 | 2.4412 | 6.2206 | 6.2206 | 0 | 12 | 1 | 1 | 6.2206 | 10 | 0 | 0
469.05 | 49.65 | 49.65 | 1 | 1 | 10 | 49.8 | 1 | 0.34412 | 3.4412 | 6.7206 | 6.7206 | 0 | 12 | 1 | 1 | 6.7206 | 10 | 0 | 0
469.1 | 49.59 | 49.59 | 1 | 1 | 10 | 49.8 | 1 | 0.44412 | 4.4412 | 7.2206 | 7.2206 | 0 | 12 | 1 | 1 | 7.2206 | 10 | 0 | 0
469.15 | 49.59 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.54412 | 5.4412 | 7.7206 | 7.7206 | 0 | 12 | 1 | 1 | 7.7206 | 10 | 0 | 0
469.2 | 49.66 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.64412 | 6.4412 | 8.2206 | 8.2206 | 0 | 12 | 1 | 1 | 8.2206 | 10 | 0 | 0
469.25 | 49.66 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.74412 | 7.4412 | 8.7206 | 8.7206 | 0 | 12 | 1 | 1 | 8.7206 | 10 | 0 | 0
469.3 | 49.63 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.84412 | 8.4412 | 9.2206 | 9.2206 | 0 | 12 | 1 | 1 | 9.2206 | 10 | 0 | 0
469.35 | 49.63 | 49.59 | 1 | 1 | 10 | 49.72 | 1 | 0.94412 | 9.4412 | 9.7206 | 9.7206 | 0 | 12 | 1 | 1 | 9.7206 | 10 | 0 | 0
469.4 | 49.61 | 49.59 | 1 | 1 | 10 | 49.72 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
469.45 | 49.61 | 49.59 | 1 | 1 | 10 | 49.67 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
469.5 | 49.54 | 49.54 | 1 | 1 | 10 | 49.67 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
469.55 | 49.54 | 49.54 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
469.6 | 49.46 | 49.46 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
469.65 | 49.46 | 49.46 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
469.7 | 49.45 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
469.75 | 49.45 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
469.8 | 49.51 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
469.85 | 49.51 | 49.45 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
469.9 | 49.5 | 49.45 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
469.95 | 49.5 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
470 | 49.54 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
470.05 | 49.54 | 49.45 | 1 | 1 | 10 | 49.54 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
470.1 | 49.59 | 49.45 | 1 | 1 | 10 | 49.59 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
470.15 | 49.59 | 49.45 | 1 | 1 | 10 | 49.59 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
470.2 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
470.25 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
470.3 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
470.35 | 49.61 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
470.4 | 49.53 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
470.45 | 49.53 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
470.5 | 49.54 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
470.55 | 49.54 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
470.6 | 49.61 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
470.65 | 49.61 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
470.7 | 49.66 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
470.75 | 49.66 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
470.8 | 49.64 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
470.85 | 49.64 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
470.9 | 49.69 | 49.53 | 1 | 1 | 10 | 49.69 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
470.95 | 49.69 | 49.53 | 1 | 1 | 10 | 49.69 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
471 | 49.74 | 49.53 | 1 | 1 | 10 | 49.74 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
471.05 | 49.74 | 49.54 | 1 | 1 | 10 | 49.74 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
471.1 | 49.78 | 49.54 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
471.15 | 49.78 | 49.61 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
471.2 | 49.82 | 49.61 | 1 | 1 | 10 | 49.82 | 0.81 | 0.81 | 8.1 | 9.05 | 9.05 | 0 | 12 | 1 | 1 | 9.05 | 10 | 0 | 0
471.25 | 49.82 | 49.64 | 1 | 1 | 10 | 49.82 | 0.81 | 0.81 | 8.1 | 9.05 | 9.05 | 0 | 12 | 1 | 1 | 9.05 | 10 | 0 | 0
471.3 | 49.86 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
471.35 | 49.86 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
471.4 | 49.84 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
471.45 | 49.84 | 49.69 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
471.5 | 49.91 | 49.69 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
471.55 | 49.91 | 49.74 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
471.6 | 49.97 | 49.74 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
471.65 | 49.97 | 49.78 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
471.7 | 50.03 | 49.78 | 1 | 1 | 10 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.9559 | 4.9559 | 0 | 12 | 1 | 1 | 4.9559 | 10 | 0 | 0
471.75 | 50.03 | 49.82 | 0.81 | 0.9 | 9 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.4559 | 4.4559 | 0 | 12 | 1 | 1 | 4.4559 | 10 | 0 | 0
471.8 | 50.05 | 49.82 | 0.81 | 0.81 | 8.1 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 3.9471 | 3.9471 | 0 | 12 | 1 | 1 | 3.9471 | 10 | 0 | 0
471.85 | 50.05 | 49.84 | 0.62 | 0.71 | 7.1 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 3.4471 | 3.4471 | 0 | 12 | 1 | 1 | 3.4471 | 10 | 0 | 0
471.9 | 50.01 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
471.95 | 50.01 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
472 | 49.95 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
472.05 | 49.95 | 49.91 | 0.044118 | 0.52 | 5.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.4971 | 2.4971 | 0 | 12 | 1 | 1 | 2.4971 | 10 | 0 | 0
472.1 | 49.99 | 49.91 | 0.044118 | 0.42 | 4.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 1.9971 | 1.9971 | 0 | 12 | 1 | 1 | 1.9971 | 10 | 0 | 0
472.15 | 49.99 | 49.95 | 0.020588 | 0.32 | 3.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 1.4971 | 1.4971 | 0 | 12 | 1 | 1 | 1.4971 | 10 | 0 | 0
472.2 | 49.92 | 49.92 | 0.038235 | 0.22 | 2.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.99706 | 0.99706 | 0 | 12 | 1 | 1 | 0.99706 | 10 | 0 | 0
472.25 | 49.92 | 49.92 | 0.038235 | 0.12 | 1.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.49706 | 0.49706 | 0 | 12 | 1 | 1 | 0.49706 | 10 | 0 | 0
472.3 | 49.97 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
472.35 | 49.97 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
472.4 | 50.02 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
472.45 | 50.02 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.17647 | 0.17647 | 0 | 12 | 1 | 1 | 0.17647 | 10 | 0 | 0
472.5 | 50.07 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
472.55 | 50.07 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
472.6 | 50.06 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
472.65 | 50.06 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
472.7 | 50.13 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
472.75 | 50.13 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
472.8 | 50.09 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
472.85 | 50.09 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6309 | -1.6309 | 0 | 12 | 1 | 1 | -1.6309 | 10 | 0 | 0
472.9 | 50.07 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6309 | -1.6309 | 0 | 12 | 1 | 1 | -1.6309 | 10 | 0 | 0
472.95 | 50.07 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6897 | -1.6897 | 0 | 12 | 1 | 1 | -1.6897 | 10 | 0 | 0
473 | 50.07 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6897 | -1.6897 | 0 | 12 | 1 | 1 | -1.6897 | 10 | 0 | 0
473.05 | 50.07 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.13 | -0.335 | -0.335 | -3.35 | -1.8074 | -1.8074 | 0 | 12 | 1 | 1 | -1.8074 | 10 | 0 | 0
473.1 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.13 | -0.335 | -0.335 | -3.35 | -1.7779 | -1.7779 | 0 | 12 | 1 | 1 | -1.7779 | 10 | 0 | 0
473.15 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.13 | -0.335 | -0.335 | -3.35 | -1.7779 | -1.7779 | 0 | 12 | 1 | 1 | -1.7779 | 10 | 0 | 0
473.2 | 50.01 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
473.25 | 50.01 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
473.3 | 50.07 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
473.35 | 50.07 | 50.01 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.235 | -2.35 | -1.175 | -1.175 | 0 | 12 | 1 | 1 | -1.175 | 10 | 0 | 0
473.4 | 50.05 | 50.01 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.135 | -1.35 | -0.675 | -0.675 | 0 | 12 | 1 | 1 | -0.675 | 10 | 0 | 0
473.45 | 50.05 | 50.01 | 0 | 0 | 0 | 50.07 | -0.032353 | -0.035 | -0.35 | -0.175 | -0.175 | 0 | 12 | 1 | 1 | -0.175 | 10 | 0 | 0
473.5 | 50.1 | 50.01 | 0 | 0 | 0 | 50.1 | -0.05 | -0.05 | -0.5 | -0.25 | -0.25 | 0 | 12 | 1 | 1 | -0.25 | 10 | 0 | 0
473.55 | 50.1 | 50.01 | 0 | 0 | 0 | 50.1 | -0.05 | -0.05 | -0.5 | -0.25 | -0.25 | 0 | 12 | 1 | 1 | -0.25 | 10 | 0 | 0
473.6 | 50.11 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
473.65 | 50.11 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
473.7 | 50.06 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
473.75 | 50.06 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
473.8 | 50.04 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
473.85 | 50.04 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
473.9 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
473.95 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
474 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
474.05 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
474.1 | 50.11 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
474.15 | 50.11 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
474.2 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
474.25 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
474.3 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
474.35 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
474.4 | 50.02 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.11 | -0.145 | -0.145 | -1.45 | -0.73971 | -0.73971 | 0 | 12 | 1 | 1 | -0.73971 | 10 | 0 | 0
474.45 | 50.02 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.11 | -0.145 | -0.145 | -1.45 | -0.73971 | -0.73971 | 0 | 12 | 1 | 1 | -0.73971 | 10 | 0 | 0
474.5 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
474.55 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
474.6 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
474.65 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
474.7 | 50.01 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
474.75 | 50.01 | 50 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.045 | -0.45 | -0.225 | -0.225 | 0 | 12 | 1 | 1 | -0.225 | 10 | 0 | 0
474.8 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
474.85 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
474.9 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
474.95 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
475 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.14706 | 0.14706 | 0 | 12 | 1 | 1 | 0.14706 | 10 | 0 | 0
475.05 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
475.1 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
475.15 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
475.2 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
475.25 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
475.3 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
475.35 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
475.4 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
475.45 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
475.5 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
475.55 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
475.6 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
475.65 | 50 | 50 | 0 | 0 | 0 | 50.01 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
475.7 | 49.5 | 49.5 | 1 | 1 | 10 | 50.01 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
475.75 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
475.8 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
475.85 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
475.9 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
475.95 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
476 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
476.05 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
476.1 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
476.15 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
476.2 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
476.25 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.1 | 1 | 5.5 | 5.5 | 0 | 12 | 1 | 1 | 5.5 | 10 | 0 | 0
476.3 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.2 | 2 | 6 | 6 | 0 | 12 | 1 | 1 | 6 | 10 | 0 | 0
476.35 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.3 | 3 | 6.5 | 6.5 | 0 | 12 | 1 | 1 | 6.5 | 10 | 0 | 0
476.4 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.4 | 4 | 7 | 7 | 0 | 12 | 1 | 1 | 7 | 10 | 0 | 0
476.45 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.5 | 5 | 7.5 | 7.5 | 0 | 12 | 1 | 1 | 7.5 | 10 | 0 | 0
476.5 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.6 | 6 | 8 | 8 | 0 | 12 | 1 | 1 | 8 | 10 | 0 | 0
476.55 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.7 | 7 | 8.5 | 8.5 | 0 | 12 | 1 | 1 | 8.5 | 10 | 0 | 0
476.6 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.8 | 8 | 9 | 9 | 0 | 12 | 1 | 1 | 9 | 10 | 0 | 0
476.65 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.9 | 9 | 9.5 | 9.5 | 0 | 12 | 1 | 1 | 9.5 | 10 | 0 | 0
476.7 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
476.75 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
476.8 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
476.85 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
476.9 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
476.95 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
477 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
477.05 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
477.1 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
477.15 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
477.2 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
477.25 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
477.3 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
477.35 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
477.4 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
477.45 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
477.5 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
477.55 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
477.6 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
477.65 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
477.7 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
477.75 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
477.8 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
477.85 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
477.9 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
477.95 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
478 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
478.05 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
478.1 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
478.15 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
478.2 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
478.25 | 50.5 | 50.5 | -1 | 0.9 | 9 | 50.5 | -1 | -1 | -10 | -0.5 | -0.5 | 0 | 12 | 1 | 1 | -0.5 | 10 | 0 | 0
478.3 | 50.5 | 50.5 | -1 | 0.8 | 8 | 50.5 | -1 | -1 | -10 | -1 | -1 | 0 | 12 | 1 | 1 | -1 | 10 | 0 | 0
478.35 | 50.5 | 50.5 | -1 | 0.7 | 7 | 50.5 | -1 | -1 | -10 | -1.5 | -1.5 | 0 | 12 | 1 | 1 | -1.5 | 10 | 0 | 0
478.4 | 50.5 | 50.5 | -1 | 0.6 | 6 | 50.5 | -1 | -1 | -10 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
478.45 | 50.5 | 50.5 | -1 | 0.5 | 5 | 50.5 | -1 | -1 | -10 | -2.5 | -2.5 | 0 | 12 | 1 | 1 | -2.5 | 10 | 0 | 0
478.5 | 50.5 | 50.5 | -1 | 0.4 | 4 | 50.5 | -1 | -1 | -10 | -3 | -3 | 0 | 12 | 1 | 1 | -3 | 10 | 0 | 0
478.55 | 50.5 | 50.5 | -1 | 0.3 | 3 | 50.5 | -1 | -1 | -10 | -3.5 | -3.5 | 0 | 12 | 1 | 1 | -3.5 | 10 | 0 | 0
478.6 | 50.5 | 50.5 | -1 | 0.2 | 2 | 50.5 | -1 | -1 | -10 | -4 | -4 | 0 | 12 | 1 | 1 | -4 | 10 | 0 | 0
478.65 | 50.5 | 50.5 | -1 | 0.1 | 1 | 50.5 | -1 | -1 | -10 | -4.5 | -4.5 | 0 | 12 | 1 | 1 | -4.5 | 10 | 0 | 0
478.7 | 50.5 | 50.5 | -1 | 0 | 0 | 50.5 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
478.75 | 50.5 | 50.5 | -1 | -0.1 | -1 | 50.5 | -1 | -1 | -10 | -5.5 | -5.5 | 0 | 12 | 1 | 1 | -5.5 | 10 | 0 | 0
478.8 | 50.5 | 50.5 | -1 | -0.2 | -2 | 50.5 | -1 | -1 | -10 | -6 | -6 | 0 | 12 | 1 | 1 | -6 | 10 | 0 | 0
478.85 | 50.5 | 50.5 | -1 | -0.3 | -3 | 50.5 | -1 | -1 | -10 | -6.5 | -6.5 | 0 | 12 | 1 | 1 | -6.5 | 10 | 0 | 0
478.9 | 50.5 | 50.5 | -1 | -0.4 | -4 | 50.5 | -1 | -1 | -10 | -7 | -7 | 0 | 12 | 1 | 1 | -7 | 10 | 0 | 0
478.95 | 50.5 | 50.5 | -1 | -0.5 | -5 | 50.5 | -1 | -1 | -10 | -7.5 | -7.5 | 0 | 12 | 1 | 1 | -7.5 | 10 | 0 | 0
479 | 50.5 | 50.5 | -1 | -0.6 | -6 | 50.5 | -1 | -1 | -10 | -8 | -8 | 0 | 12 | 1 | 1 | -8 | 10 | 0 | 0
479.05 | 50.5 | 50.5 | -1 | -0.7 | -7 | 50.5 | -1 | -1 | -10 | -8.5 | -8.5 | 0 | 12 | 1 | 1 | -8.5 | 10 | 0 | 0
479.1 | 50.5 | 50.5 | -1 | -0.8 | -8 | 50.5 | -1 | -1 | -10 | -9 | -9 | 0 | 12 | 1 | 1 | -9 | 10 | 0 | 0
479.15 | 50.5 | 50.5 | -1 | -0.9 | -9 | 50.5 | -1 | -1 | -10 | -9.5 | -9.5 | 0 | 12 | 1 | 1 | -9.5 | 10 | 0 | 0
479.2 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
479.25 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
479.3 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
479.35 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
479.4 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
479.45 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
479.5 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
479.55 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
479.6 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
479.65 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
479.7 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
479.75 | 50.47 | 50.47 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
479.8 | 50.45 | 50.45 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
479.85 | 50.42 | 50.42 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
479.9 | 50.4 | 50.4 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
479.95 | 50.37 | 50.37 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
480 | 50.35 | 50.35 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
480.05 | 50.32 | 50.32 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
480.1 | 50.29 | 50.29 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
480.15 | 50.27 | 50.27 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
480.2 | 50.24 | 50.24 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
480.25 | 50.22 | 50.22 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
480.3 | 50.19 | 50.19 | -0.905 | -0.905 | -9.05 | 50.47 | -1 | -1 | -10 | -9.525 | -9.525 | 0 | 12 | 1 | 1 | -9.525 | 10 | 0 | 0
480.35 | 50.17 | 50.17 | -0.715 | -0.715 | -7.15 | 50.45 | -1 | -1 | -10 | -8.575 | -8.575 | 0 | 12 | 1 | 1 | -8.575 | 10 | 0 | 0
480.4 | 50.14 | 50.14 | -0.43 | -0.43 | -4.3 | 50.42 | -1 | -1 | -10 | -7.15 | -7.15 | 0 | 12 | 1 | 1 | -7.15 | 10 | 0 | 0
480.45 | 50.12 | 50.12 | -0.24 | -0.24 | -2.4 | 50.4 | -1 | -1 | -10 | -6.2 | -6.2 | 0 | 12 | 1 | 1 | -6.2 | 10 | 0 | 0
480.5 | 50.09 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 50.37 | -1 | -1 | -10 | -5.2206 | -5.2206 | 0 | 12 | 1 | 1 | -5.2206 | 10 | 0 | 0
480.55 | 50.06 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.35 | -1 | -1 | -10 | -5.1324 | -5.1324 | 0 | 12 | 1 | 1 | -5.1324 | 10 | 0 | 0
480.6 | 50.04 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.32 | -1 | -1 | -10 | -5.0735 | -5.0735 | 0 | 12 | 1 | 1 | -5.0735 | 10 | 0 | 0
480.65 | 50.01 | 50.01 | 0 | 0 | 0 | 50.29 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
480.7 | 49.99 | 49.99 | 0 | 0 | 0 | 50.27 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
480.75 | 49.96 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.24 | -1 | -1 | -10 | -4.9265 | -4.9265 | 0 | 12 | 1 | 1 | -4.9265 | 10 | 0 | 0
480.8 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.22 | -1 | -1 | -10 | -4.8676 | -4.8676 | 0 | 12 | 1 | 1 | -4.8676 | 10 | 0 | 0
480.85 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.19 | -0.905 | -0.905 | -9.05 | -4.3044 | -4.3044 | 0 | 12 | 1 | 1 | -4.3044 | 10 | 0 | 0
480.9 | 49.88 | 49.88 | 0.24 | 0.24 | 2.4 | 50.17 | -0.715 | -0.805 | -8.05 | -2.825 | -2.825 | 0 | 12 | 1 | 1 | -2.825 | 10 | 0 | 0
480.95 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.14 | -0.43 | -0.705 | -7.05 | -1.375 | -1.375 | 0 | 12 | 1 | 1 | -1.375 | 10 | 0 | 0
481 | 49.83 | 49.83 | 0.715 | 0.715 | 7.15 | 50.12 | -0.24 | -0.605 | -6.05 | 0.55 | 0.55 | 0 | 12 | 1 | 1 | 0.55 | 10 | 0 | 0
481.05 | 49.81 | 49.81 | 0.905 | 0.905 | 9.05 | 50.09 | -0.044118 | -0.505 | -5.05 | 2 | 2 | 0 | 12 | 1 | 1 | 2 | 10 | 0 | 0
481.1 | 49.78 | 49.78 | 1 | 1 | 10 | 50.06 | -0.026471 | -0.405 | -4.05 | 2.975 | 2.975 | 0 | 12 | 1 | 1 | 2.975 | 10 | 0 | 0
481.15 | 49.76 | 49.76 | 1 | 1 | 10 | 50.04 | -0.014706 | -0.305 | -3.05 | 3.475 | 3.475 | 0 | 12 | 1 | 1 | 3.475 | 10 | 0 | 0
481.2 | 49.73 | 49.73 | 1 | 1 | 10 | 50.01 | 0 | -0.205 | -2.05 | 3.975 | 3.975 | 0 | 12 | 1 | 1 | 3.975 | 10 | 0 | 0
481.25 | 49.71 | 49.71 | 1 | 1 | 10 | 49.99 | 0 | -0.105 | -1.05 | 4.475 | 4.475 | 0 | 12 | 1 | 1 | 4.475 | 10 | 0 | 0
481.3 | 49.68 | 49.68 | 1 | 1 | 10 | 49.96 | 0.014706 | -0.005 | -0.05 | 4.975 | 4.975 | 0 | 12 | 1 | 1 | 4.975 | 10 | 0 | 0
481.35 | 49.65 | 49.65 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
481.4 | 49.63 | 49.63 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
481.45 | 49.6 | 49.6 | 1 | 1 | 10 | 49.88 | 0.24 | 0.14412 | 1.4412 | 5.7206 | 5.7206 | 0 | 12 | 1 | 1 | 5.7206 | 10 | 0 | 0
481.5 | 49.58 | 49.58 | 1 | 1 | 10 | 49.86 | 0.43 | 0.24412 | 2.4412 | 6.2206 | 6.2206 | 0 | 12 | 1 | 1 | 6.2206 | 10 | 0 | 0
481.55 | 49.55 | 49.55 | 1 | 1 | 10 | 49.83 | 0.715 | 0.34412 | 3.4412 | 6.7206 | 6.7206 | 0 | 12 | 1 | 1 | 6.7206 | 10 | 0 | 0
481.6 | 49.53 | 49.53 | 1 | 1 | 10 | 49.81 | 0.905 | 0.44412 | 4.4412 | 7.2206 | 7.2206 | 0 | 12 | 1 | 1 | 7.2206 | 10 | 0 | 0
481.65 | 49.5 | 49.5 | 1 | 1 | 10 | 49.78 | 1 | 0.54412 | 5.4412 | 7.7206 | 7.7206 | 0 | 12 | 1 | 1 | 7.7206 | 10 | 0 | 0
481.7 | 49.5 | 49.5 | 1 | 1 | 10 | 49.76 | 1 | 0.64412 | 6.4412 | 8.2206 | 8.2206 | 0 | 12 | 1 | 1 | 8.2206 | 10 | 0 | 0
481.75 | 49.53 | 49.5 | 1 | 1 | 10 | 49.73 | 1 | 0.74412 | 7.4412 | 8.7206 | 8.7206 | 0 | 12 | 1 | 1 | 8.7206 | 10 | 0 | 0
481.8 | 49.55 | 49.5 | 1 | 1 | 10 | 49.71 | 1 | 0.84412 | 8.4412 | 9.2206 | 9.2206 | 0 | 12 | 1 | 1 | 9.2206 | 10 | 0 | 0
481.85 | 49.58 | 49.5 | 1 | 1 | 10 | 49.68 | 1 | 0.94412 | 9.4412 | 9.7206 | 9.7206 | 0 | 12 | 1 | 1 | 9.7206 | 10 | 0 | 0
481.9 | 49.6 | 49.5 | 1 | 1 | 10 | 49.65 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
481.95 | 49.63 | 49.5 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
482 | 49.65 | 49.5 | 1 | 1 | 10 | 49.65 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
482.05 | 49.68 | 49.5 | 1 | 1 | 10 | 49.68 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
482.1 | 49.71 | 49.5 | 1 | 1 | 10 | 49.71 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
482.15 | 49.73 | 49.5 | 1 | 1 | 10 | 49.73 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
482.2 | 49.76 | 49.5 | 1 | 1 | 10 | 49.76 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
482.25 | 49.78 | 49.5 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
482.3 | 49.81 | 49.53 | 1 | 1 | 10 | 49.81 | 0.905 | 0.905 | 9.05 | 9.525 | 9.525 | 0 | 12 | 1 | 1 | 9.525 | 10 | 0 | 0
482.35 | 49.83 | 49.55 | 1 | 1 | 10 | 49.83 | 0.715 | 0.715 | 7.15 | 8.575 | 8.575 | 0 | 12 | 1 | 1 | 8.575 | 10 | 0 | 0
482.4 | 49.86 | 49.58 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
482.45 | 49.88 | 49.6 | 1 | 1 | 10 | 49.88 | 0.24 | 0.24 | 2.4 | 6.2 | 6.2 | 0 | 12 | 1 | 1 | 6.2 | 10 | 0 | 0
482.5 | 49.91 | 49.63 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
482.55 | 49.94 | 49.65 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
482.6 | 49.96 | 49.68 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
482.65 | 49.99 | 49.71 | 1 | 1 | 10 | 49.99 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
482.7 | 50.01 | 49.73 | 1 | 1 | 10 | 50.01 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
482.75 | 50.04 | 49.76 | 1 | 1 | 10 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 4.9265 | 4.9265 | 0 | 12 | 1 | 1 | 4.9265 | 10 | 0 | 0
482.8 | 50.06 | 49.78 | 1 | 1 | 10 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 4.8676 | 4.8676 | 0 | 12 | 1 | 1 | 4.8676 | 10 | 0 | 0
482.85 | 50.09 | 49.81 | 0.905 | 0.905 | 9.05 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 4.3044 | 4.3044 | 0 | 12 | 1 | 1 | 4.3044 | 10 | 0 | 0
482.9 | 50.12 | 49.83 | 0.715 | 0.805 | 8.05 | 50.12 | -0.24 | -0.24 | -2.4 | 2.825 | 2.825 | 0 | 12 | 1 | 1 | 2.825 | 10 | 0 | 0
482.95 | 50.14 | 49.86 | 0.43 | 0.705 | 7.05 | 50.14 | -0.43 | -0.43 | -4.3 | 1.375 | 1.375 | 0 | 12 | 1 | 1 | 1.375 | 10 | 0 | 0
483 | 50.17 | 49.88 | 0.24 | 0.605 | 6.05 | 50.17 | -0.715 | -0.715 | -7.15 | -0.55 | -0.55 | 0 | 12 | 1 | 1 | -0.55 | 10 | 0 | 0
483.05 | 50.19 | 49.91 | 0.044118 | 0.505 | 5.05 | 50.19 | -0.905 | -0.905 | -9.05 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
483.1 | 50.22 | 49.94 | 0.026471 | 0.405 | 4.05 | 50.22 | -1 | -1 | -10 | -2.975 | -2.975 | 0 | 12 | 1 | 1 | -2.975 | 10 | 0 | 0
483.15 | 50.24 | 49.96 | 0.014706 | 0.305 | 3.05 | 50.24 | -1 | -1 | -10 | -3.475 | -3.475 | 0 | 12 | 1 | 1 | -3.475 | 10 | 0 | 0
483.2 | 50.27 | 49.99 | 0 | 0.205 | 2.05 | 50.27 | -1 | -1 | -10 | -3.975 | -3.975 | 0 | 12 | 1 | 1 | -3.975 | 10 | 0 | 0
483.25 | 50.29 | 50.01 | 0 | 0.105 | 1.05 | 50.29 | -1 | -1 | -10 | -4.475 | -4.475 | 0 | 12 | 1 | 1 | -4.475 | 10 | 0 | 0
483.3 | 50.32 | 50.04 | -0.014706 | 0.005 | 0.05 | 50.32 | -1 | -1 | -10 | -4.975 | -4.975 | 0 | 12 | 1 | 1 | -4.975 | 10 | 0 | 0
483.35 | 50.35 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.35 | -1 | -1 | -10 | -5.1324 | -5.1324 | 0 | 12 | 1 | 1 | -5.1324 | 10 | 0 | 0
483.4 | 50.37 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 50.37 | -1 | -1 | -10 | -5.2206 | -5.2206 | 0 | 12 | 1 | 1 | -5.2206 | 10 | 0 | 0
483.45 | 50.4 | 50.12 | -0.24 | -0.14412 | -1.4412 | 50.4 | -1 | -1 | -10 | -5.7206 | -5.7206 | 0 | 12 | 1 | 1 | -5.7206 | 10 | 0 | 0
483.5 | 50.42 | 50.14 | -0.43 | -0.24412 | -2.4412 | 50.42 | -1 | -1 | -10 | -6.2206 | -6.2206 | 0 | 12 | 1 | 1 | -6.2206 | 10 | 0 | 0
483.55 | 50.45 | 50.17 | -0.715 | -0.34412 | -3.4412 | 50.45 | -1 | -1 | -10 | -6.7206 | -6.7206 | 0 | 12 | 1 | 1 | -6.7206 | 10 | 0 | 0
483.6 | 50.47 | 50.19 | -0.905 | -0.44412 | -4.4412 | 50.47 | -1 | -1 | -10 | -7.2206 | -7.2206 | 0 | 12 | 1 | 1 | -7.2206 | 10 | 0 | 0
483.65 | 50.5 | 50.22 | -1 | -0.54412 | -5.4412 | 50.5 | -1 | -1 | -10 | -7.7206 | -7.7206 | 0 | 12 | 1 | 1 | -7.7206 | 10 | 0 | 0
483.7 | 50.5 | 50.24 | -1 | -0.64412 | -6.4412 | 50.5 | -1 | -1 | -10 | -8.2206 | -8.2206 | 0 | 12 | 1 | 1 | -8.2206 | 10 | 0 | 0
483.75 | 50.47 | 50.27 | -1 | -0.74412 | -7.4412 | 50.5 | -1 | -1 | -10 | -8.7206 | -8.7206 | 0 | 12 | 1 | 1 | -8.7206 | 10 | 0 | 0
483.8 | 50.45 | 50.29 | -1 | -0.84412 | -8.4412 | 50.5 | -1 | -1 | -10 | -9.2206 | -9.2206 | 0 | 12 | 1 | 1 | -9.2206 | 10 | 0 | 0
483.85 | 50.42 | 50.32 | -1 | -0.94412 | -9.4412 | 50.5 | -1 | -1 | -10 | -9.7206 | -9.7206 | 0 | 12 | 1 | 1 | -9.7206 | 10 | 0 | 0
483.9 | 50.39 | 50.35 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
483.95 | 50.37 | 50.37 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
484 | 50.34 | 50.34 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
484.05 | 50.32 | 50.32 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
484.1 | 50.29 | 50.29 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
484.15 | 50.26 | 50.26 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
484.2 | 50.24 | 50.24 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
484.25 | 50.21 | 50.21 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
484.3 | 50.18 | 50.18 | -0.81 | -0.81 | -8.1 | 50.47 | -1 | -1 | -10 | -9.05 | -9.05 | 0 | 12 | 1 | 1 | -9.05 | 10 | 0 | 0
484.35 | 50.16 | 50.16 | -0.62 | -0.62 | -6.2 | 50.45 | -1 | -1 | -10 | -8.1 | -8.1 | 0 | 12 | 1 | 1 | -8.1 | 10 | 0 | 0
484.4 | 50.13 | 50.13 | -0.335 | -0.335 | -3.35 | 50.42 | -1 | -1 | -10 | -6.675 | -6.675 | 0 | 12 | 1 | 1 | -6.675 | 10 | 0 | 0
484.45 | 50.11 | 50.11 | -0.145 | -0.145 | -1.45 | 50.39 | -1 | -1 | -10 | -5.725 | -5.725 | 0 | 12 | 1 | 1 | -5.725 | 10 | 0 | 0
484.5 | 50.08 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 50.37 | -1 | -1 | -10 | -5.1912 | -5.1912 | 0 | 12 | 1 | 1 | -5.1912 | 10 | 0 | 0
484.55 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.34 | -1 | -1 | -10 | -5.1029 | -5.1029 | 0 | 12 | 1 | 1 | -5.1029 | 10 | 0 | 0
484.6 | 50.03 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 50.32 | -1 | -1 | -10 | -5.0441 | -5.0441 | 0 | 12 | 1 | 1 | -5.0441 | 10 | 0 | 0
484.65 | 50 | 50 | 0 | 0 | 0 | 50.29 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
484.7 | 50 | 50 | 0 | 0 | 0 | 50.26 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
484.75 | 50 | 50 | 0 | 0 | 0 | 50.24 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
484.8 | 50 | 50 | 0 | 0 | 0 | 50.21 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
484.85 | 50 | 50 | 0 | 0 | 0 | 50.18 | -0.81 | -0.9 | -9 | -4.5 | -4.5 | 0 | 12 | 1 | 1 | -4.5 | 10 | 0 | 0
484.9 | 50 | 50 | 0 | 0 | 0 | 50.16 | -0.62 | -0.8 | -8 | -4 | -4 | 0 | 12 | 1 | 1 | -4 | 10 | 0 | 0
484.95 | 50 | 50 | 0 | 0 | 0 | 50.13 | -0.335 | -0.7 | -7 | -3.5 | -3.5 | 0 | 12 | 1 | 1 | -3.5 | 10 | 0 | 0
485 | 50.01 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.6 | -6 | -3 | -3 | 0 | 12 | 1 | 1 | -3 | 10 | 0 | 0
485.05 | 50.01 | 50 | 0 | 0 | 0 | 50.08 | -0.038235 | -0.5 | -5 | -2.5 | -2.5 | 0 | 12 | 1 | 1 | -2.5 | 10 | 0 | 0
485.1 | 49.99 | 49.99 | 0 | 0 | 0 | 50.05 | -0.020588 | -0.4 | -4 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
485.15 | 49.99 | 49.99 | 0 | 0 | 0 | 50.03 | -0.0088235 | -0.3 | -3 | -1.5 | -1.5 | 0 | 12 | 1 | 1 | -1.5 | 10 | 0 | 0
485.2 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | -0.2 | -2 | -0.83824 | -0.83824 | 0 | 12 | 1 | 1 | -0.83824 | 10 | 0 | 0
485.25 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | -0.1 | -1 | -0.33824 | -0.33824 | 0 | 12 | 1 | 1 | -0.33824 | 10 | 0 | 0
485.3 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
485.35 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
485.4 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
485.45 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
485.5 | 49.89 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
485.55 | 49.89 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
485.6 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50.01 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
485.65 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
485.7 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
485.75 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 2.7868 | 2.7868 | 0 | 12 | 1 | 1 | 2.7868 | 10 | 0 | 0
485.8 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 2.7868 | 2.7868 | 0 | 12 | 1 | 1 | 2.7868 | 10 | 0 | 0
485.85 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 2.8456 | 2.8456 | 0 | 12 | 1 | 1 | 2.8456 | 10 | 0 | 0
485.9 | 49.94 | 49.85 | 0.525 | 0.525 | 5.25 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 2.7574 | 2.7574 | 0 | 12 | 1 | 1 | 2.7574 | 10 | 0 | 0
485.95 | 49.94 | 49.85 | 0.525 | 0.525 | 5.25 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 2.7574 | 2.7574 | 0 | 12 | 1 | 1 | 2.7574 | 10 | 0 | 0
486 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
486.05 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
486.1 | 49.93 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
486.15 | 49.93 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
486.2 | 49.96 | 49.85 | 0.525 | 0.525 | 5.25 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 2.6985 | 2.6985 | 0 | 12 | 1 | 1 | 2.6985 | 10 | 0 | 0
486.25 | 49.96 | 49.85 | 0.525 | 0.525 | 5.25 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 2.6985 | 2.6985 | 0 | 12 | 1 | 1 | 2.6985 | 10 | 0 | 0
486.3 | 49.99 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
486.35 | 49.99 | 49.91 | 0.044118 | 0.425 | 4.25 | 49.99 | 0 | 0 | 0 | 2.125 | 2.125 | 0 | 12 | 1 | 1 | 2.125 | 10 | 0 | 0
486.4 | 49.99 | 49.91 | 0.044118 | 0.325 | 3.25 | 49.99 | 0 | 0 | 0 | 1.625 | 1.625 | 0 | 12 | 1 | 1 | 1.625 | 10 | 0 | 0
486.45 | 49.99 | 49.93 | 0.032353 | 0.225 | 2.25 | 49.99 | 0 | 0 | 0 | 1.125 | 1.125 | 0 | 12 | 1 | 1 | 1.125 | 10 | 0 | 0
486.5 | 49.96 | 49.93 | 0.032353 | 0.125 | 1.25 | 49.99 | 0 | 0 | 0 | 0.625 | 0.625 | 0 | 12 | 1 | 1 | 0.625 | 10 | 0 | 0
486.55 | 49.96 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 49.99 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
486.6 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
486.65 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
486.7 | 50.05 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.058824 | 0.058824 | 0 | 12 | 1 | 1 | 0.058824 | 10 | 0 | 0
486.75 | 50.05 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
486.8 | 49.97 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
486.85 | 49.97 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
486.9 | 49.92 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
486.95 | 49.92 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
487 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
487.05 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
487.1 | 49.94 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
487.15 | 49.94 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
487.2 | 50.01 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
487.25 | 50.01 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
487.3 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
487.35 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
487.4 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
487.45 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
487.5 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
487.55 | 49.95 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
487.6 | 49.97 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
487.65 | 49.97 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
487.7 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
487.75 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
487.8 | 49.87 | 49.87 | 0.335 | 0.335 | 3.35 | 50.01 | 0 | 0 | 0 | 1.675 | 1.675 | 0 | 12 | 1 | 1 | 1.675 | 10 | 0 | 0
487.85 | 49.87 | 49.87 | 0.335 | 0.335 | 3.35 | 49.99 | 0 | 0 | 0 | 1.675 | 1.675 | 0 | 12 | 1 | 1 | 1.675 | 10 | 0 | 0
487.9 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
487.95 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 2.6691 | 2.6691 | 0 | 12 | 1 | 1 | 2.6691 | 10 | 0 | 0
488 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
488.05 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
488.1 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
488.15 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
488.2 | 49.84 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
488.25 | 49.84 | 49.79 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
488.3 | 49.89 | 49.79 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
488.35 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.12647 | 1.2647 | 5.6324 | 5.6324 | 0 | 12 | 1 | 1 | 5.6324 | 10 | 0 | 0
488.4 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.145 | 1.45 | 5.725 | 5.725 | 0 | 12 | 1 | 1 | 5.725 | 10 | 0 | 0
488.45 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.145 | 1.45 | 5.725 | 5.725 | 0 | 12 | 1 | 1 | 5.725 | 10 | 0 | 0
488.5 | 49.96 | 49.79 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
488.55 | 49.96 | 49.79 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
488.6 | 50.02 | 49.79 | 1 | 1 | 10 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 4.9853 | 4.9853 | 0 | 12 | 1 | 1 | 4.9853 | 10 | 0 | 0
488.65 | 50.02 | 49.79 | 1 | 1 | 10 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 4.9853 | 4.9853 | 0 | 12 | 1 | 1 | 4.9853 | 10 | 0 | 0
488.7 | 50.03 | 49.79 | 1 | 1 | 10 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.9559 | 4.9559 | 0 | 12 | 1 | 1 | 4.9559 | 10 | 0 | 0
488.75 | 50.03 | 49.84 | 0.62 | 0.9 | 9 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.4559 | 4.4559 | 0 | 12 | 1 | 1 | 4.4559 | 10 | 0 | 0
488.8 | 50.02 | 49.84 | 0.62 | 0.8 | 8 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 3.9559 | 3.9559 | 0 | 12 | 1 | 1 | 3.9559 | 10 | 0 | 0
488.85 | 50.02 | 49.89 | 0.145 | 0.7 | 7 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 3.4559 | 3.4559 | 0 | 12 | 1 | 1 | 3.4559 | 10 | 0 | 0
488.9 | 50.08 | 49.89 | 0.145 | 0.6 | 6 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 2.8088 | 2.8088 | 0 | 12 | 1 | 1 | 2.8088 | 10 | 0 | 0
488.95 | 50.08 | 49.89 | 0.145 | 0.5 | 5 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 2.3088 | 2.3088 | 0 | 12 | 1 | 1 | 2.3088 | 10 | 0 | 0
489 | 50.01 | 49.89 | 0.145 | 0.4 | 4 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 1.8088 | 1.8088 | 0 | 12 | 1 | 1 | 1.8088 | 10 | 0 | 0
489.05 | 50.01 | 49.96 | 0.014706 | 0.3 | 3 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 1.3088 | 1.3088 | 0 | 12 | 1 | 1 | 1.3088 | 10 | 0 | 0
489.1 | 49.94 | 49.94 | 0.026471 | 0.2 | 2 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.80882 | 0.80882 | 0 | 12 | 1 | 1 | 0.80882 | 10 | 0 | 0
489.15 | 49.94 | 49.94 | 0.026471 | 0.1 | 1 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.30882 | 0.30882 | 0 | 12 | 1 | 1 | 0.30882 | 10 | 0 | 0
489.2 | 50 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
489.25 | 50 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
489.3 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
489.35 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
489.4 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
489.45 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
489.5 | 49.92 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
489.55 | 49.92 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
489.6 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50.01 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
489.65 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
489.7 | 49.92 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
489.75 | 49.92 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
489.8 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
489.85 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
489.9 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
489.95 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
490 | 49.87 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
490.05 | 49.87 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
490.1 | 49.8 | 49.8 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
490.15 | 49.8 | 49.8 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
490.2 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
490.25 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
490.3 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
490.35 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
490.4 | 49.72 | 49.72 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
490.45 | 49.72 | 49.72 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
490.5 | 49.67 | 49.67 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
490.55 | 49.67 | 49.67 | 1 | 1 | 10 | 49.87 | 0.335 | 0.14412 | 1.4412 | 5.7206 | 5.7206 | 0 | 12 | 1 | 1 | 5.7206 | 10 | 0 | 0
490.6 | 49.65 | 49.65 | 1 | 1 | 10 | 49.87 | 0.335 | 0.24412 | 2.4412 | 6.2206 | 6.2206 | 0 | 12 | 1 | 1 | 6.2206 | 10 | 0 | 0
490.65 | 49.65 | 49.65 | 1 | 1 | 10 | 49.8 | 1 | 0.34412 | 3.4412 | 6.7206 | 6.7206 | 0 | 12 | 1 | 1 | 6.7206 | 10 | 0 | 0
490.7 | 49.59 | 49.59 | 1 | 1 | 10 | 49.8 | 1 | 0.44412 | 4.4412 | 7.2206 | 7.2206 | 0 | 12 | 1 | 1 | 7.2206 | 10 | 0 | 0
490.75 | 49.59 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.54412 | 5.4412 | 7.7206 | 7.7206 | 0 | 12 | 1 | 1 | 7.7206 | 10 | 0 | 0
490.8 | 49.66 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.64412 | 6.4412 | 8.2206 | 8.2206 | 0 | 12 | 1 | 1 | 8.2206 | 10 | 0 | 0
490.85 | 49.66 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.74412 | 7.4412 | 8.7206 | 8.7206 | 0 | 12 | 1 | 1 | 8.7206 | 10 | 0 | 0
490.9 | 49.63 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.84412 | 8.4412 | 9.2206 | 9.2206 | 0 | 12 | 1 | 1 | 9.2206 | 10 | 0 | 0
490.95 | 49.63 | 49.59 | 1 | 1 | 10 | 49.72 | 1 | 0.94412 | 9.4412 | 9.7206 | 9.7206 | 0 | 12 | 1 | 1 | 9.7206 | 10 | 0 | 0
491 | 49.61 | 49.59 | 1 | 1 | 10 | 49.72 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
491.05 | 49.61 | 49.59 | 1 | 1 | 10 | 49.67 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
491.1 | 49.54 | 49.54 | 1 | 1 | 10 | 49.67 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
491.15 | 49.54 | 49.54 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
491.2 | 49.46 | 49.46 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
491.25 | 49.46 | 49.46 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
491.3 | 49.45 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
491.35 | 49.45 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
491.4 | 49.51 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
491.45 | 49.51 | 49.45 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
491.5 | 49.5 | 49.45 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
491.55 | 49.5 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
491.6 | 49.54 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
491.65 | 49.54 | 49.45 | 1 | 1 | 10 | 49.54 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
491.7 | 49.59 | 49.45 | 1 | 1 | 10 | 49.59 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
491.75 | 49.59 | 49.45 | 1 | 1 | 10 | 49.59 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
491.8 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
491.85 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
491.9 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
491.95 | 49.61 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
492 | 49.53 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
492.05 | 49.53 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
492.1 | 49.54 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
492.15 | 49.54 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
492.2 | 49.61 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
492.25 | 49.61 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
492.3 | 49.66 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
492.35 | 49.66 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
492.4 | 49.64 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
492.45 | 49.64 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
492.5 | 49.69 | 49.53 | 1 | 1 | 10 | 49.69 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
492.55 | 49.69 | 49.53 | 1 | 1 | 10 | 49.69 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
492.6 | 49.74 | 49.53 | 1 | 1 | 10 | 49.74 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
492.65 | 49.74 | 49.54 | 1 | 1 | 10 | 49.74 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
492.7 | 49.78 | 49.54 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
492.75 | 49.78 | 49.61 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
492.8 | 49.82 | 49.61 | 1 | 1 | 10 | 49.82 | 0.81 | 0.81 | 8.1 | 9.05 | 9.05 | 0 | 12 | 1 | 1 | 9.05 | 10 | 0 | 0
492.85 | 49.82 | 49.64 | 1 | 1 | 10 | 49.82 | 0.81 | 0.81 | 8.1 | 9.05 | 9.05 | 0 | 12 | 1 | 1 | 9.05 | 10 | 0 | 0
492.9 | 49.86 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
492.95 | 49.86 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
493 | 49.84 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
493.05 | 49.84 | 49.69 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
493.1 | 49.91 | 49.69 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
493.15 | 49.91 | 49.74 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
493.2 | 49.97 | 49.74 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
493.25 | 49.97 | 49.78 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
493.3 | 50.03 | 49.78 | 1 | 1 | 10 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.9559 | 4.9559 | 0 | 12 | 1 | 1 | 4.9559 | 10 | 0 | 0
493.35 | 50.03 | 49.82 | 0.81 | 0.9 | 9 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.4559 | 4.4559 | 0 | 12 | 1 | 1 | 4.4559 | 10 | 0 | 0
493.4 | 50.05 | 49.82 | 0.81 | 0.81 | 8.1 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 3.9471 | 3.9471 | 0 | 12 | 1 | 1 | 3.9471 | 10 | 0 | 0
493.45 | 50.05 | 49.84 | 0.62 | 0.71 | 7.1 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 3.4471 | 3.4471 | 0 | 12 | 1 | 1 | 3.4471 | 10 | 0 | 0
493.5 | 50.01 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
493.55 | 50.01 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
493.6 | 49.95 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
493.65 | 49.95 | 49.91 | 0.044118 | 0.52 | 5.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.4971 | 2.4971 | 0 | 12 | 1 | 1 | 2.4971 | 10 | 0 | 0
493.7 | 49.99 | 49.91 | 0.044118 | 0.42 | 4.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 1.9971 | 1.9971 | 0 | 12 | 1 | 1 | 1.9971 | 10 | 0 | 0
493.75 | 49.99 | 49.95 | 0.020588 | 0.32 | 3.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 1.4971 | 1.4971 | 0 | 12 | 1 | 1 | 1.4971 | 10 | 0 | 0
493.8 | 49.92 | 49.92 | 0.038235 | 0.22 | 2.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.99706 | 0.99706 | 0 | 12 | 1 | 1 | 0.99706 | 10 | 0 | 0
493.85 | 49.92 | 49.92 | 0.038235 | 0.12 | 1.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.49706 | 0.49706 | 0 | 12 | 1 | 1 | 0.49706 | 10 | 0 | 0
493.9 | 49.97 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
493.95 | 49.97 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
494 | 50.02 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
494.05 | 50.02 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.17647 | 0.17647 | 0 | 12 | 1 | 1 | 0.17647 | 10 | 0 | 0
494.1 | 50.07 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
494.15 | 50.07 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
494.2 | 50.06 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
494.25 | 50.06 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
494.3 | 50.13 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
494.35 | 50.13 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
494.4 | 50.09 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
494.45 | 50.09 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6309 | -1.6309 | 0 | 12 | 1 | 1 | -1.6309 | 10 | 0 | 0
494.5 | 50.07 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6309 | -1.6309 | 0 | 12 | 1 | 1 | -1.6309 | 10 | 0 | 0
494.55 | 50.07 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6897 | -1.6897 | 0 | 12 | 1 | 1 | -1.6897 | 10 | 0 | 0
494.6 | 50.07 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6897 | -1.6897 | 0 | 12 | 1 | 1 | -1.6897 | 10 | 0 | 0
494.65 | 50.07 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.13 | -0.335 | -0.335 | -3.35 | -1.8074 | -1.8074 | 0 | 12 | 1 | 1 | -1.8074 | 10 | 0 | 0
494.7 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.13 | -0.335 | -0.335 | -3.35 | -1.7779 | -1.7779 | 0 | 12 | 1 | 1 | -1.7779 | 10 | 0 | 0
494.75 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.13 | -0.335 | -0.335 | -3.35 | -1.7779 | -1.7779 | 0 | 12 | 1 | 1 | -1.7779 | 10 | 0 | 0
494.8 | 50.01 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
494.85 | 50.01 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
494.9 | 50.07 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
494.95 | 50.07 | 50.01 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.235 | -2.35 | -1.175 | -1.175 | 0 | 12 | 1 | 1 | -1.175 | 10 | 0 | 0
495 | 50.05 | 50.01 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.135 | -1.35 | -0.675 | -0.675 | 0 | 12 | 1 | 1 | -0.675 | 10 | 0 | 0
495.05 | 50.05 | 50.01 | 0 | 0 | 0 | 50.07 | -0.032353 | -0.035 | -0.35 | -0.175 | -0.175 | 0 | 12 | 1 | 1 | -0.175 | 10 | 0 | 0
495.1 | 50.1 | 50.01 | 0 | 0 | 0 | 50.1 | -0.05 | -0.05 | -0.5 | -0.25 | -0.25 | 0 | 12 | 1 | 1 | -0.25 | 10 | 0 | 0
495.15 | 50.1 | 50.01 | 0 | 0 | 0 | 50.1 | -0.05 | -0.05 | -0.5 | -0.25 | -0.25 | 0 | 12 | 1 | 1 | -0.25 | 10 | 0 | 0
495.2 | 50.11 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
495.25 | 50.11 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
495.3 | 50.06 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
495.35 | 50.06 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
495.4 | 50.04 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
495.45 | 50.04 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
495.5 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
495.55 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
495.6 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
495.65 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
495.7 | 50.11 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
495.75 | 50.11 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
495.8 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
495.85 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
495.9 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
495.95 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
496 | 50.02 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.11 | -0.145 | -0.145 | -1.45 | -0.73971 | -0.73971 | 0 | 12 | 1 | 1 | -0.73971 | 10 | 0 | 0
496.05 | 50.02 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.11 | -0.145 | -0.145 | -1.45 | -0.73971 | -0.73971 | 0 | 12 | 1 | 1 | -0.73971 | 10 | 0 | 0
496.1 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
496.15 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
496.2 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
496.25 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
496.3 | 50.01 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
496.35 | 50.01 | 50 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.045 | -0.45 | -0.225 | -0.225 | 0 | 12 | 1 | 1 | -0.225 | 10 | 0 | 0
496.4 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
496.45 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
496.5 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
496.55 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
496.6 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.14706 | 0.14706 | 0 | 12 | 1 | 1 | 0.14706 | 10 | 0 | 0
496.65 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
496.7 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
496.75 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
496.8 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
496.85 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
496.9 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
496.95 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
497 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
497.05 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
497.1 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
497.15 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
497.2 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
497.25 | 50 | 50 | 0 | 0 | 0 | 50.01 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
497.3 | 49.5 | 49.5 | 1 | 1 | 10 | 50.01 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
497.35 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
497.4 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
497.45 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
497.5 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
497.55 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
497.6 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
497.65 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
497.7 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
497.75 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
497.8 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
497.85 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.1 | 1 | 5.5 | 5.5 | 0 | 12 | 1 | 1 | 5.5 | 10 | 0 | 0
497.9 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.2 | 2 | 6 | 6 | 0 | 12 | 1 | 1 | 6 | 10 | 0 | 0
497.95 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.3 | 3 | 6.5 | 6.5 | 0 | 12 | 1 | 1 | 6.5 | 10 | 0 | 0
498 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.4 | 4 | 7 | 7 | 0 | 12 | 1 | 1 | 7 | 10 | 0 | 0
498.05 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.5 | 5 | 7.5 | 7.5 | 0 | 12 | 1 | 1 | 7.5 | 10 | 0 | 0
498.1 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.6 | 6 | 8 | 8 | 0 | 12 | 1 | 1 | 8 | 10 | 0 | 0
498.15 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.7 | 7 | 8.5 | 8.5 | 0 | 12 | 1 | 1 | 8.5 | 10 | 0 | 0
498.2 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.8 | 8 | 9 | 9 | 0 | 12 | 1 | 1 | 9 | 10 | 0 | 0
498.25 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.9 | 9 | 9.5 | 9.5 | 0 | 12 | 1 | 1 | 9.5 | 10 | 0 | 0
498.3 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
498.35 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
498.4 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
498.45 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
498.5 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
498.55 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
498.6 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
498.65 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
498.7 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
498.75 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
498.8 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
498.85 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
498.9 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
498.95 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
499 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
499.05 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
499.1 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
499.15 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
499.2 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
499.25 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
499.3 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
499.35 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
499.4 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
499.45 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
499.5 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
499.55 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
499.6 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
499.65 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
499.7 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
499.75 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
499.8 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
499.85 | 50.5 | 50.5 | -1 | 0.9 | 9 | 50.5 | -1 | -1 | -10 | -0.5 | -0.5 | 0 | 12 | 1 | 1 | -0.5 | 10 | 0 | 0
499.9 | 50.5 | 50.5 | -1 | 0.8 | 8 | 50.5 | -1 | -1 | -10 | -1 | -1 | 0 | 12 | 1 | 1 | -1 | 10 | 0 | 0
499.95 | 50.5 | 50.5 | -1 | 0.7 | 7 | 50.5 | -1 | -1 | -10 | -1.5 | -1.5 | 0 | 12 | 1 | 1 | -1.5 | 10 | 0 | 0
500 | 50.5 | 50.5 | -1 | 0.6 | 6 | 50.5 | -1 | -1 | -10 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
500.05 | 50.5 | 50.5 | -1 | 0.5 | 5 | 50.5 | -1 | -1 | -10 | -2.5 | -2.5 | 0 | 12 | 1 | 1 | -2.5 | 10 | 0 | 0
500.1 | 50.5 | 50.5 | -1 | 0.4 | 4 | 50.5 | -1 | -1 | -10 | -3 | -3 | 0 | 12 | 1 | 1 | -3 | 10 | 0 | 0
500.15 | 50.5 | 50.5 | -1 | 0.3 | 3 | 50.5 | -1 | -1 | -10 | -3.5 | -3.5 | 0 | 12 | 1 | 1 | -3.5 | 10 | 0 | 0
500.2 | 50.5 | 50.5 | -1 | 0.2 | 2 | 50.5 | -1 | -1 | -10 | -4 | -4 | 0 | 12 | 1 | 1 | -4 | 10 | 0 | 0
500.25 | 50.5 | 50.5 | -1 | 0.1 | 1 | 50.5 | -1 | -1 | -10 | -4.5 | -4.5 | 0 | 12 | 1 | 1 | -4.5 | 10 | 0 | 0
500.3 | 50.5 | 50.5 | -1 | 0 | 0 | 50.5 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
500.35 | 50.5 | 50.5 | -1 | -0.1 | -1 | 50.5 | -1 | -1 | -10 | -5.5 | -5.5 | 0 | 12 | 1 | 1 | -5.5 | 10 | 0 | 0
500.4 | 50.5 | 50.5 | -1 | -0.2 | -2 | 50.5 | -1 | -1 | -10 | -6 | -6 | 0 | 12 | 1 | 1 | -6 | 10 | 0 | 0
500.45 | 50.5 | 50.5 | -1 | -0.3 | -3 | 50.5 | -1 | -1 | -10 | -6.5 | -6.5 | 0 | 12 | 1 | 1 | -6.5 | 10 | 0 | 0
500.5 | 50.5 | 50.5 | -1 | -0.4 | -4 | 50.5 | -1 | -1 | -10 | -7 | -7 | 0 | 12 | 1 | 1 | -7 | 10 | 0 | 0
500.55 | 50.5 | 50.5 | -1 | -0.5 | -5 | 50.5 | -1 | -1 | -10 | -7.5 | -7.5 | 0 | 12 | 1 | 1 | -7.5 | 10 | 0 | 0
500.6 | 50.5 | 50.5 | -1 | -0.6 | -6 | 50.5 | -1 | -1 | -10 | -8 | -8 | 0 | 12 | 1 | 1 | -8 | 10 | 0 | 0
500.65 | 50.5 | 50.5 | -1 | -0.7 | -7 | 50.5 | -1 | -1 | -10 | -8.5 | -8.5 | 0 | 12 | 1 | 1 | -8.5 | 10 | 0 | 0
500.7 | 50.5 | 50.5 | -1 | -0.8 | -8 | 50.5 | -1 | -1 | -10 | -9 | -9 | 0 | 12 | 1 | 1 | -9 | 10 | 0 | 0
500.75 | 50.5 | 50.5 | -1 | -0.9 | -9 | 50.5 | -1 | -1 | -10 | -9.5 | -9.5 | 0 | 12 | 1 | 1 | -9.5 | 10 | 0 | 0
500.8 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
500.85 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
500.9 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
500.95 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
501 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
501.05 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
501.1 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
501.15 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
501.2 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
501.25 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
501.3 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
501.35 | 50.47 | 50.47 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
501.4 | 50.45 | 50.45 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
501.45 | 50.42 | 50.42 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
501.5 | 50.4 | 50.4 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
501.55 | 50.37 | 50.37 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
501.6 | 50.35 | 50.35 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
501.65 | 50.32 | 50.32 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
501.7 | 50.29 | 50.29 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
501.75 | 50.27 | 50.27 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
501.8 | 50.24 | 50.24 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
501.85 | 50.22 | 50.22 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
501.9 | 50.19 | 50.19 | -0.905 | -0.905 | -9.05 | 50.47 | -1 | -1 | -10 | -9.525 | -9.525 | 0 | 12 | 1 | 1 | -9.525 | 10 | 0 | 0
501.95 | 50.17 | 50.17 | -0.715 | -0.715 | -7.15 | 50.45 | -1 | -1 | -10 | -8.575 | -8.575 | 0 | 12 | 1 | 1 | -8.575 | 10 | 0 | 0
502 | 50.14 | 50.14 | -0.43 | -0.43 | -4.3 | 50.42 | -1 | -1 | -10 | -7.15 | -7.15 | 0 | 12 | 1 | 1 | -7.15 | 10 | 0 | 0
502.05 | 50.12 | 50.12 | -0.24 | -0.24 | -2.4 | 50.4 | -1 | -1 | -10 | -6.2 | -6.2 | 0 | 12 | 1 | 1 | -6.2 | 10 | 0 | 0
502.1 | 50.09 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 50.37 | -1 | -1 | -10 | -5.2206 | -5.2206 | 0 | 12 | 1 | 1 | -5.2206 | 10 | 0 | 0
502.15 | 50.06 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.35 | -1 | -1 | -10 | -5.1324 | -5.1324 | 0 | 12 | 1 | 1 | -5.1324 | 10 | 0 | 0
502.2 | 50.04 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.32 | -1 | -1 | -10 | -5.0735 | -5.0735 | 0 | 12 | 1 | 1 | -5.0735 | 10 | 0 | 0
502.25 | 50.01 | 50.01 | 0 | 0 | 0 | 50.29 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
502.3 | 49.99 | 49.99 | 0 | 0 | 0 | 50.27 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
502.35 | 49.96 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.24 | -1 | -1 | -10 | -4.9265 | -4.9265 | 0 | 12 | 1 | 1 | -4.9265 | 10 | 0 | 0
502.4 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.22 | -1 | -1 | -10 | -4.8676 | -4.8676 | 0 | 12 | 1 | 1 | -4.8676 | 10 | 0 | 0
502.45 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.19 | -0.905 | -0.905 | -9.05 | -4.3044 | -4.3044 | 0 | 12 | 1 | 1 | -4.3044 | 10 | 0 | 0
502.5 | 49.88 | 49.88 | 0.24 | 0.24 | 2.4 | 50.17 | -0.715 | -0.805 | -8.05 | -2.825 | -2.825 | 0 | 12 | 1 | 1 | -2.825 | 10 | 0 | 0
502.55 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.14 | -0.43 | -0.705 | -7.05 | -1.375 | -1.375 | 0 | 12 | 1 | 1 | -1.375 | 10 | 0 | 0
502.6 | 49.83 | 49.83 | 0.715 | 0.715 | 7.15 | 50.12 | -0.24 | -0.605 | -6.05 | 0.55 | 0.55 | 0 | 12 | 1 | 1 | 0.55 | 10 | 0 | 0
502.65 | 49.81 | 49.81 | 0.905 | 0.905 | 9.05 | 50.09 | -0.044118 | -0.505 | -5.05 | 2 | 2 | 0 | 12 | 1 | 1 | 2 | 10 | 0 | 0
502.7 | 49.78 | 49.78 | 1 | 1 | 10 | 50.06 | -0.026471 | -0.405 | -4.05 | 2.975 | 2.975 | 0 | 12 | 1 | 1 | 2.975 | 10 | 0 | 0
502.75 | 49.76 | 49.76 | 1 | 1 | 10 | 50.04 | -0.014706 | -0.305 | -3.05 | 3.475 | 3.475 | 0 | 12 | 1 | 1 | 3.475 | 10 | 0 | 0
502.8 | 49.73 | 49.73 | 1 | 1 | 10 | 50.01 | 0 | -0.205 | -2.05 | 3.975 | 3.975 | 0 | 12 | 1 | 1 | 3.975 | 10 | 0 | 0
502.85 | 49.71 | 49.71 | 1 | 1 | 10 | 49.99 | 0 | -0.105 | -1.05 | 4.475 | 4.475 | 0 | 12 | 1 | 1 | 4.475 | 10 | 0 | 0
502.9 | 49.68 | 49.68 | 1 | 1 | 10 | 49.96 | 0.014706 | -0.005 | -0.05 | 4.975 | 4.975 | 0 | 12 | 1 | 1 | 4.975 | 10 | 0 | 0
502.95 | 49.65 | 49.65 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
503 | 49.63 | 49.63 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
503.05 | 49.6 | 49.6 | 1 | 1 | 10 | 49.88 | 0.24 | 0.14412 | 1.4412 | 5.7206 | 5.7206 | 0 | 12 | 1 | 1 | 5.7206 | 10 | 0 | 0
503.1 | 49.58 | 49.58 | 1 | 1 | 10 | 49.86 | 0.43 | 0.24412 | 2.4412 | 6.2206 | 6.2206 | 0 | 12 | 1 | 1 | 6.2206 | 10 | 0 | 0
503.15 | 49.55 | 49.55 | 1 | 1 | 10 | 49.83 | 0.715 | 0.34412 | 3.4412 | 6.7206 | 6.7206 | 0 | 12 | 1 | 1 | 6.7206 | 10 | 0 | 0
503.2 | 49.53 | 49.53 | 1 | 1 | 10 | 49.81 | 0.905 | 0.44412 | 4.4412 | 7.2206 | 7.2206 | 0 | 12 | 1 | 1 | 7.2206 | 10 | 0 | 0
503.25 | 49.5 | 49.5 | 1 | 1 | 10 | 49.78 | 1 | 0.54412 | 5.4412 | 7.7206 | 7.7206 | 0 | 12 | 1 | 1 | 7.7206 | 10 | 0 | 0
503.3 | 49.5 | 49.5 | 1 | 1 | 10 | 49.76 | 1 | 0.64412 | 6.4412 | 8.2206 | 8.2206 | 0 | 12 | 1 | 1 | 8.2206 | 10 | 0 | 0
503.35 | 49.53 | 49.5 | 1 | 1 | 10 | 49.73 | 1 | 0.74412 | 7.4412 | 8.7206 | 8.7206 | 0 | 12 | 1 | 1 | 8.7206 | 10 | 0 | 0
503.4 | 49.55 | 49.5 | 1 | 1 | 10 | 49.71 | 1 | 0.84412 | 8.4412 | 9.2206 | 9.2206 | 0 | 12 | 1 | 1 | 9.2206 | 10 | 0 | 0
503.45 | 49.58 | 49.5 | 1 | 1 | 10 | 49.68 | 1 | 0.94412 | 9.4412 | 9.7206 | 9.7206 | 0 | 12 | 1 | 1 | 9.7206 | 10 | 0 | 0
503.5 | 49.6 | 49.5 | 1 | 1 | 10 | 49.65 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
503.55 | 49.63 | 49.5 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
503.6 | 49.65 | 49.5 | 1 | 1 | 10 | 49.65 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
503.65 | 49.68 | 49.5 | 1 | 1 | 10 | 49.68 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
503.7 | 49.71 | 49.5 | 1 | 1 | 10 | 49.71 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
503.75 | 49.73 | 49.5 | 1 | 1 | 10 | 49.73 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
503.8 | 49.76 | 49.5 | 1 | 1 | 10 | 49.76 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
503.85 | 49.78 | 49.5 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
503.9 | 49.81 | 49.53 | 1 | 1 | 10 | 49.81 | 0.905 | 0.905 | 9.05 | 9.525 | 9.525 | 0 | 12 | 1 | 1 | 9.525 | 10 | 0 | 0
503.95 | 49.83 | 49.55 | 1 | 1 | 10 | 49.83 | 0.715 | 0.715 | 7.15 | 8.575 | 8.575 | 0 | 12 | 1 | 1 | 8.575 | 10 | 0 | 0
504 | 49.86 | 49.58 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
504.05 | 49.88 | 49.6 | 1 | 1 | 10 | 49.88 | 0.24 | 0.24 | 2.4 | 6.2 | 6.2 | 0 | 12 | 1 | 1 | 6.2 | 10 | 0 | 0
504.1 | 49.91 | 49.63 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
504.15 | 49.94 | 49.65 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
504.2 | 49.96 | 49.68 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
504.25 | 49.99 | 49.71 | 1 | 1 | 10 | 49.99 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
504.3 | 50.01 | 49.73 | 1 | 1 | 10 | 50.01 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
504.35 | 50.04 | 49.76 | 1 | 1 | 10 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 4.9265 | 4.9265 | 0 | 12 | 1 | 1 | 4.9265 | 10 | 0 | 0
504.4 | 50.06 | 49.78 | 1 | 1 | 10 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 4.8676 | 4.8676 | 0 | 12 | 1 | 1 | 4.8676 | 10 | 0 | 0
504.45 | 50.09 | 49.81 | 0.905 | 0.905 | 9.05 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 4.3044 | 4.3044 | 0 | 12 | 1 | 1 | 4.3044 | 10 | 0 | 0
504.5 | 50.12 | 49.83 | 0.715 | 0.805 | 8.05 | 50.12 | -0.24 | -0.24 | -2.4 | 2.825 | 2.825 | 0 | 12 | 1 | 1 | 2.825 | 10 | 0 | 0
504.55 | 50.14 | 49.86 | 0.43 | 0.705 | 7.05 | 50.14 | -0.43 | -0.43 | -4.3 | 1.375 | 1.375 | 0 | 12 | 1 | 1 | 1.375 | 10 | 0 | 0
504.6 | 50.17 | 49.88 | 0.24 | 0.605 | 6.05 | 50.17 | -0.715 | -0.715 | -7.15 | -0.55 | -0.55 | 0 | 12 | 1 | 1 | -0.55 | 10 | 0 | 0
504.65 | 50.19 | 49.91 | 0.044118 | 0.505 | 5.05 | 50.19 | -0.905 | -0.905 | -9.05 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
504.7 | 50.22 | 49.94 | 0.026471 | 0.405 | 4.05 | 50.22 | -1 | -1 | -10 | -2.975 | -2.975 | 0 | 12 | 1 | 1 | -2.975 | 10 | 0 | 0
504.75 | 50.24 | 49.96 | 0.014706 | 0.305 | 3.05 | 50.24 | -1 | -1 | -10 | -3.475 | -3.475 | 0 | 12 | 1 | 1 | -3.475 | 10 | 0 | 0
504.8 | 50.27 | 49.99 | 0 | 0.205 | 2.05 | 50.27 | -1 | -1 | -10 | -3.975 | -3.975 | 0 | 12 | 1 | 1 | -3.975 | 10 | 0 | 0
504.85 | 50.29 | 50.01 | 0 | 0.105 | 1.05 | 50.29 | -1 | -1 | -10 | -4.475 | -4.475 | 0 | 12 | 1 | 1 | -4.475 | 10 | 0 | 0
504.9 | 50.32 | 50.04 | -0.014706 | 0.005 | 0.05 | 50.32 | -1 | -1 | -10 | -4.975 | -4.975 | 0 | 12 | 1 | 1 | -4.975 | 10 | 0 | 0
504.95 | 50.35 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.35 | -1 | -1 | -10 | -5.1324 | -5.1324 | 0 | 12 | 1 | 1 | -5.1324 | 10 | 0 | 0
505 | 50.37 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 50.37 | -1 | -1 | -10 | -5.2206 | -5.2206 | 0 | 12 | 1 | 1 | -5.2206 | 10 | 0 | 0
505.05 | 50.4 | 50.12 | -0.24 | -0.14412 | -1.4412 | 50.4 | -1 | -1 | -10 | -5.7206 | -5.7206 | 0 | 12 | 1 | 1 | -5.7206 | 10 | 0 | 0
505.1 | 50.42 | 50.14 | -0.43 | -0.24412 | -2.4412 | 50.42 | -1 | -1 | -10 | -6.2206 | -6.2206 | 0 | 12 | 1 | 1 | -6.2206 | 10 | 0 | 0
505.15 | 50.45 | 50.17 | -0.715 | -0.34412 | -3.4412 | 50.45 | -1 | -1 | -10 | -6.7206 | -6.7206 | 0 | 12 | 1 | 1 | -6.7206 | 10 | 0 | 0
505.2 | 50.47 | 50.19 | -0.905 | -0.44412 | -4.4412 | 50.47 | -1 | -1 | -10 | -7.2206 | -7.2206 | 0 | 12 | 1 | 1 | -7.2206 | 10 | 0 | 0
505.25 | 50.5 | 50.22 | -1 | -0.54412 | -5.4412 | 50.5 | -1 | -1 | -10 | -7.7206 | -7.7206 | 0 | 12 | 1 | 1 | -7.7206 | 10 | 0 | 0
505.3 | 50.5 | 50.24 | -1 | -0.64412 | -6.4412 | 50.5 | -1 | -1 | -10 | -8.2206 | -8.2206 | 0 | 12 | 1 | 1 | -8.2206 | 10 | 0 | 0
505.35 | 50.47 | 50.27 | -1 | -0.74412 | -7.4412 | 50.5 | -1 | -1 | -10 | -8.7206 | -8.7206 | 0 | 12 | 1 | 1 | -8.7206 | 10 | 0 | 0
505.4 | 50.45 | 50.29 | -1 | -0.84412 | -8.4412 | 50.5 | -1 | -1 | -10 | -9.2206 | -9.2206 | 0 | 12 | 1 | 1 | -9.2206 | 10 | 0 | 0
505.45 | 50.42 | 50.32 | -1 | -0.94412 | -9.4412 | 50.5 | -1 | -1 | -10 | -9.7206 | -9.7206 | 0 | 12 | 1 | 1 | -9.7206 | 10 | 0 | 0
505.5 | 50.39 | 50.35 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
505.55 | 50.37 | 50.37 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
505.6 | 50.34 | 50.34 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
505.65 | 50.32 | 50.32 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
505.7 | 50.29 | 50.29 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
505.75 | 50.26 | 50.26 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
505.8 | 50.24 | 50.24 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
505.85 | 50.21 | 50.21 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
505.9 | 50.18 | 50.18 | -0.81 | -0.81 | -8.1 | 50.47 | -1 | -1 | -10 | -9.05 | -9.05 | 0 | 12 | 1 | 1 | -9.05 | 10 | 0 | 0
505.95 | 50.16 | 50.16 | -0.62 | -0.62 | -6.2 | 50.45 | -1 | -1 | -10 | -8.1 | -8.1 | 0 | 12 | 1 | 1 | -8.1 | 10 | 0 | 0
506 | 50.13 | 50.13 | -0.335 | -0.335 | -3.35 | 50.42 | -1 | -1 | -10 | -6.675 | -6.675 | 0 | 12 | 1 | 1 | -6.675 | 10 | 0 | 0
506.05 | 50.11 | 50.11 | -0.145 | -0.145 | -1.45 | 50.39 | -1 | -1 | -10 | -5.725 | -5.725 | 0 | 12 | 1 | 1 | -5.725 | 10 | 0 | 0
506.1 | 50.08 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 50.37 | -1 | -1 | -10 | -5.1912 | -5.1912 | 0 | 12 | 1 | 1 | -5.1912 | 10 | 0 | 0
506.15 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.34 | -1 | -1 | -10 | -5.1029 | -5.1029 | 0 | 12 | 1 | 1 | -5.1029 | 10 | 0 | 0
506.2 | 50.03 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 50.32 | -1 | -1 | -10 | -5.0441 | -5.0441 | 0 | 12 | 1 | 1 | -5.0441 | 10 | 0 | 0
506.25 | 50 | 50 | 0 | 0 | 0 | 50.29 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
506.3 | 50 | 50 | 0 | 0 | 0 | 50.26 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
506.35 | 50 | 50 | 0 | 0 | 0 | 50.24 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
506.4 | 50 | 50 | 0 | 0 | 0 | 50.21 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
506.45 | 50 | 50 | 0 | 0 | 0 | 50.18 | -0.81 | -0.9 | -9 | -4.5 | -4.5 | 0 | 12 | 1 | 1 | -4.5 | 10 | 0 | 0
506.5 | 50 | 50 | 0 | 0 | 0 | 50.16 | -0.62 | -0.8 | -8 | -4 | -4 | 0 | 12 | 1 | 1 | -4 | 10 | 0 | 0
506.55 | 50 | 50 | 0 | 0 | 0 | 50.13 | -0.335 | -0.7 | -7 | -3.5 | -3.5 | 0 | 12 | 1 | 1 | -3.5 | 10 | 0 | 0
506.6 | 50.01 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.6 | -6 | -3 | -3 | 0 | 12 | 1 | 1 | -3 | 10 | 0 | 0
506.65 | 50.01 | 50 | 0 | 0 | 0 | 50.08 | -0.038235 | -0.5 | -5 | -2.5 | -2.5 | 0 | 12 | 1 | 1 | -2.5 | 10 | 0 | 0
506.7 | 49.99 | 49.99 | 0 | 0 | 0 | 50.05 | -0.020588 | -0.4 | -4 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
506.75 | 49.99 | 49.99 | 0 | 0 | 0 | 50.03 | -0.0088235 | -0.3 | -3 | -1.5 | -1.5 | 0 | 12 | 1 | 1 | -1.5 | 10 | 0 | 0
506.8 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | -0.2 | -2 | -0.83824 | -0.83824 | 0 | 12 | 1 | 1 | -0.83824 | 10 | 0 | 0
506.85 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | -0.1 | -1 | -0.33824 | -0.33824 | 0 | 12 | 1 | 1 | -0.33824 | 10 | 0 | 0
506.9 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
506.95 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
507 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
507.05 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
507.1 | 49.89 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
507.15 | 49.89 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
507.2 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50.01 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
507.25 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
507.3 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
507.35 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 2.7868 | 2.7868 | 0 | 12 | 1 | 1 | 2.7868 | 10 | 0 | 0
507.4 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 2.7868 | 2.7868 | 0 | 12 | 1 | 1 | 2.7868 | 10 | 0 | 0
507.45 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 2.8456 | 2.8456 | 0 | 12 | 1 | 1 | 2.8456 | 10 | 0 | 0
507.5 | 49.94 | 49.85 | 0.525 | 0.525 | 5.25 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 2.7574 | 2.7574 | 0 | 12 | 1 | 1 | 2.7574 | 10 | 0 | 0
507.55 | 49.94 | 49.85 | 0.525 | 0.525 | 5.25 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 2.7574 | 2.7574 | 0 | 12 | 1 | 1 | 2.7574 | 10 | 0 | 0
507.6 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
507.65 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
507.7 | 49.93 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
507.75 | 49.93 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
507.8 | 49.96 | 49.85 | 0.525 | 0.525 | 5.25 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 2.6985 | 2.6985 | 0 | 12 | 1 | 1 | 2.6985 | 10 | 0 | 0
507.85 | 49.96 | 49.85 | 0.525 | 0.525 | 5.25 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 2.6985 | 2.6985 | 0 | 12 | 1 | 1 | 2.6985 | 10 | 0 | 0
507.9 | 49.99 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
507.95 | 49.99 | 49.91 | 0.044118 | 0.425 | 4.25 | 49.99 | 0 | 0 | 0 | 2.125 | 2.125 | 0 | 12 | 1 | 1 | 2.125 | 10 | 0 | 0
508 | 49.99 | 49.91 | 0.044118 | 0.325 | 3.25 | 49.99 | 0 | 0 | 0 | 1.625 | 1.625 | 0 | 12 | 1 | 1 | 1.625 | 10 | 0 | 0
508.05 | 49.99 | 49.93 | 0.032353 | 0.225 | 2.25 | 49.99 | 0 | 0 | 0 | 1.125 | 1.125 | 0 | 12 | 1 | 1 | 1.125 | 10 | 0 | 0
508.1 | 49.96 | 49.93 | 0.032353 | 0.125 | 1.25 | 49.99 | 0 | 0 | 0 | 0.625 | 0.625 | 0 | 12 | 1 | 1 | 0.625 | 10 | 0 | 0
508.15 | 49.96 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 49.99 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
508.2 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
508.25 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
508.3 | 50.05 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.058824 | 0.058824 | 0 | 12 | 1 | 1 | 0.058824 | 10 | 0 | 0
508.35 | 50.05 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
508.4 | 49.97 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
508.45 | 49.97 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
508.5 | 49.92 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
508.55 | 49.92 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
508.6 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
508.65 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
508.7 | 49.94 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
508.75 | 49.94 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
508.8 | 50.01 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
508.85 | 50.01 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
508.9 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
508.95 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
509 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
509.05 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
509.1 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
509.15 | 49.95 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
509.2 | 49.97 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
509.25 | 49.97 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
509.3 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
509.35 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
509.4 | 49.87 | 49.87 | 0.335 | 0.335 | 3.35 | 50.01 | 0 | 0 | 0 | 1.675 | 1.675 | 0 | 12 | 1 | 1 | 1.675 | 10 | 0 | 0
509.45 | 49.87 | 49.87 | 0.335 | 0.335 | 3.35 | 49.99 | 0 | 0 | 0 | 1.675 | 1.675 | 0 | 12 | 1 | 1 | 1.675 | 10 | 0 | 0
509.5 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
509.55 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 2.6691 | 2.6691 | 0 | 12 | 1 | 1 | 2.6691 | 10 | 0 | 0
509.6 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
509.65 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
509.7 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
509.75 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
509.8 | 49.84 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
509.85 | 49.84 | 49.79 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
509.9 | 49.89 | 49.79 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
509.95 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.12647 | 1.2647 | 5.6324 | 5.6324 | 0 | 12 | 1 | 1 | 5.6324 | 10 | 0 | 0
510 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.145 | 1.45 | 5.725 | 5.725 | 0 | 12 | 1 | 1 | 5.725 | 10 | 0 | 0
510.05 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.145 | 1.45 | 5.725 | 5.725 | 0 | 12 | 1 | 1 | 5.725 | 10 | 0 | 0
510.1 | 49.96 | 49.79 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
510.15 | 49.96 | 49.79 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
510.2 | 50.02 | 49.79 | 1 | 1 | 10 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 4.9853 | 4.9853 | 0 | 12 | 1 | 1 | 4.9853 | 10 | 0 | 0
510.25 | 50.02 | 49.79 | 1 | 1 | 10 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 4.9853 | 4.9853 | 0 | 12 | 1 | 1 | 4.9853 | 10 | 0 | 0
510.3 | 50.03 | 49.79 | 1 | 1 | 10 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.9559 | 4.9559 | 0 | 12 | 1 | 1 | 4.9559 | 10 | 0 | 0
510.35 | 50.03 | 49.84 | 0.62 | 0.9 | 9 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.4559 | 4.4559 | 0 | 12 | 1 | 1 | 4.4559 | 10 | 0 | 0
510.4 | 50.02 | 49.84 | 0.62 | 0.8 | 8 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 3.9559 | 3.9559 | 0 | 12 | 1 | 1 | 3.9559 | 10 | 0 | 0
510.45 | 50.02 | 49.89 | 0.145 | 0.7 | 7 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 3.4559 | 3.4559 | 0 | 12 | 1 | 1 | 3.4559 | 10 | 0 | 0
510.5 | 50.08 | 49.89 | 0.145 | 0.6 | 6 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 2.8088 | 2.8088 | 0 | 12 | 1 | 1 | 2.8088 | 10 | 0 | 0
510.55 | 50.08 | 49.89 | 0.145 | 0.5 | 5 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 2.3088 | 2.3088 | 0 | 12 | 1 | 1 | 2.3088 | 10 | 0 | 0
510.6 | 50.01 | 49.89 | 0.145 | 0.4 | 4 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 1.8088 | 1.8088 | 0 | 12 | 1 | 1 | 1.8088 | 10 | 0 | 0
510.65 | 50.01 | 49.96 | 0.014706 | 0.3 | 3 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 1.3088 | 1.3088 | 0 | 12 | 1 | 1 | 1.3088 | 10 | 0 | 0
510.7 | 49.94 | 49.94 | 0.026471 | 0.2 | 2 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.80882 | 0.80882 | 0 | 12 | 1 | 1 | 0.80882 | 10 | 0 | 0
510.75 | 49.94 | 49.94 | 0.026471 | 0.1 | 1 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.30882 | 0.30882 | 0 | 12 | 1 | 1 | 0.30882 | 10 | 0 | 0
510.8 | 50 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
510.85 | 50 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
510.9 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
510.95 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
511 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
511.05 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
511.1 | 49.92 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
511.15 | 49.92 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
511.2 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50.01 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
511.25 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
511.3 | 49.92 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
511.35 | 49.92 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
511.4 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
511.45 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
511.5 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
511.55 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
511.6 | 49.87 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
511.65 | 49.87 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
511.7 | 49.8 | 49.8 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
511.75 | 49.8 | 49.8 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
511.8 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
511.85 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
511.9 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
511.95 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
512 | 49.72 | 49.72 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
512.05 | 49.72 | 49.72 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
512.1 | 49.67 | 49.67 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
512.15 | 49.67 | 49.67 | 1 | 1 | 10 | 49.87 | 0.335 | 0.14412 | 1.4412 | 5.7206 | 5.7206 | 0 | 12 | 1 | 1 | 5.7206 | 10 | 0 | 0
512.2 | 49.65 | 49.65 | 1 | 1 | 10 | 49.87 | 0.335 | 0.24412 | 2.4412 | 6.2206 | 6.2206 | 0 | 12 | 1 | 1 | 6.2206 | 10 | 0 | 0
512.25 | 49.65 | 49.65 | 1 | 1 | 10 | 49.8 | 1 | 0.34412 | 3.4412 | 6.7206 | 6.7206 | 0 | 12 | 1 | 1 | 6.7206 | 10 | 0 | 0
512.3 | 49.59 | 49.59 | 1 | 1 | 10 | 49.8 | 1 | 0.44412 | 4.4412 | 7.2206 | 7.2206 | 0 | 12 | 1 | 1 | 7.2206 | 10 | 0 | 0
512.35 | 49.59 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.54412 | 5.4412 | 7.7206 | 7.7206 | 0 | 12 | 1 | 1 | 7.7206 | 10 | 0 | 0
512.4 | 49.66 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.64412 | 6.4412 | 8.2206 | 8.2206 | 0 | 12 | 1 | 1 | 8.2206 | 10 | 0 | 0
512.45 | 49.66 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.74412 | 7.4412 | 8.7206 | 8.7206 | 0 | 12 | 1 | 1 | 8.7206 | 10 | 0 | 0
512.5 | 49.63 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.84412 | 8.4412 | 9.2206 | 9.2206 | 0 | 12 | 1 | 1 | 9.2206 | 10 | 0 | 0
512.55 | 49.63 | 49.59 | 1 | 1 | 10 | 49.72 | 1 | 0.94412 | 9.4412 | 9.7206 | 9.7206 | 0 | 12 | 1 | 1 | 9.7206 | 10 | 0 | 0
512.6 | 49.61 | 49.59 | 1 | 1 | 10 | 49.72 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
512.65 | 49.61 | 49.59 | 1 | 1 | 10 | 49.67 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
512.7 | 49.54 | 49.54 | 1 | 1 | 10 | 49.67 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
512.75 | 49.54 | 49.54 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
512.8 | 49.46 | 49.46 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
512.85 | 49.46 | 49.46 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
512.9 | 49.45 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
512.95 | 49.45 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
513 | 49.51 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
513.05 | 49.51 | 49.45 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
513.1 | 49.5 | 49.45 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
513.15 | 49.5 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
513.2 | 49.54 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
513.25 | 49.54 | 49.45 | 1 | 1 | 10 | 49.54 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
513.3 | 49.59 | 49.45 | 1 | 1 | 10 | 49.59 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
513.35 | 49.59 | 49.45 | 1 | 1 | 10 | 49.59 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
513.4 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
513.45 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
513.5 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
513.55 | 49.61 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
513.6 | 49.53 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
513.65 | 49.53 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
513.7 | 49.54 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
513.75 | 49.54 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
513.8 | 49.61 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
513.85 | 49.61 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
513.9 | 49.66 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
513.95 | 49.66 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
514 | 49.64 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
514.05 | 49.64 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
514.1 | 49.69 | 49.53 | 1 | 1 | 10 | 49.69 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
514.15 | 49.69 | 49.53 | 1 | 1 | 10 | 49.69 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
514.2 | 49.74 | 49.53 | 1 | 1 | 10 | 49.74 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
514.25 | 49.74 | 49.54 | 1 | 1 | 10 | 49.74 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
514.3 | 49.78 | 49.54 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
514.35 | 49.78 | 49.61 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
514.4 | 49.82 | 49.61 | 1 | 1 | 10 | 49.82 | 0.81 | 0.81 | 8.1 | 9.05 | 9.05 | 0 | 12 | 1 | 1 | 9.05 | 10 | 0 | 0
514.45 | 49.82 | 49.64 | 1 | 1 | 10 | 49.82 | 0.81 | 0.81 | 8.1 | 9.05 | 9.05 | 0 | 12 | 1 | 1 | 9.05 | 10 | 0 | 0
514.5 | 49.86 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
514.55 | 49.86 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
514.6 | 49.84 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
514.65 | 49.84 | 49.69 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
514.7 | 49.91 | 49.69 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
514.75 | 49.91 | 49.74 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
514.8 | 49.97 | 49.74 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
514.85 | 49.97 | 49.78 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
514.9 | 50.03 | 49.78 | 1 | 1 | 10 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.9559 | 4.9559 | 0 | 12 | 1 | 1 | 4.9559 | 10 | 0 | 0
514.95 | 50.03 | 49.82 | 0.81 | 0.9 | 9 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.4559 | 4.4559 | 0 | 12 | 1 | 1 | 4.4559 | 10 | 0 | 0
515 | 50.05 | 49.82 | 0.81 | 0.81 | 8.1 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 3.9471 | 3.9471 | 0 | 12 | 1 | 1 | 3.9471 | 10 | 0 | 0
515.05 | 50.05 | 49.84 | 0.62 | 0.71 | 7.1 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 3.4471 | 3.4471 | 0 | 12 | 1 | 1 | 3.4471 | 10 | 0 | 0
515.1 | 50.01 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
515.15 | 50.01 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
515.2 | 49.95 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
515.25 | 49.95 | 49.91 | 0.044118 | 0.52 | 5.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.4971 | 2.4971 | 0 | 12 | 1 | 1 | 2.4971 | 10 | 0 | 0
515.3 | 49.99 | 49.91 | 0.044118 | 0.42 | 4.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 1.9971 | 1.9971 | 0 | 12 | 1 | 1 | 1.9971 | 10 | 0 | 0
515.35 | 49.99 | 49.95 | 0.020588 | 0.32 | 3.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 1.4971 | 1.4971 | 0 | 12 | 1 | 1 | 1.4971 | 10 | 0 | 0
515.4 | 49.92 | 49.92 | 0.038235 | 0.22 | 2.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.99706 | 0.99706 | 0 | 12 | 1 | 1 | 0.99706 | 10 | 0 | 0
515.45 | 49.92 | 49.92 | 0.038235 | 0.12 | 1.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.49706 | 0.49706 | 0 | 12 | 1 | 1 | 0.49706 | 10 | 0 | 0
515.5 | 49.97 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
515.55 | 49.97 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
515.6 | 50.02 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
515.65 | 50.02 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.17647 | 0.17647 | 0 | 12 | 1 | 1 | 0.17647 | 10 | 0 | 0
515.7 | 50.07 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
515.75 | 50.07 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
515.8 | 50.06 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
515.85 | 50.06 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
515.9 | 50.13 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
515.95 | 50.13 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
516 | 50.09 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
516.05 | 50.09 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6309 | -1.6309 | 0 | 12 | 1 | 1 | -1.6309 | 10 | 0 | 0
516.1 | 50.07 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6309 | -1.6309 | 0 | 12 | 1 | 1 | -1.6309 | 10 | 0 | 0
516.15 | 50.07 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6897 | -1.6897 | 0 | 12 | 1 | 1 | -1.6897 | 10 | 0 | 0
516.2 | 50.07 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6897 | -1.6897 | 0 | 12 | 1 | 1 | -1.6897 | 10 | 0 | 0
516.25 | 50.07 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.13 | -0.335 | -0.335 | -3.35 | -1.8074 | -1.8074 | 0 | 12 | 1 | 1 | -1.8074 | 10 | 0 | 0
516.3 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.13 | -0.335 | -0.335 | -3.35 | -1.7779 | -1.7779 | 0 | 12 | 1 | 1 | -1.7779 | 10 | 0 | 0
516.35 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.13 | -0.335 | -0.335 | -3.35 | -1.7779 | -1.7779 | 0 | 12 | 1 | 1 | -1.7779 | 10 | 0 | 0
516.4 | 50.01 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
516.45 | 50.01 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
516.5 | 50.07 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
516.55 | 50.07 | 50.01 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.235 | -2.35 | -1.175 | -1.175 | 0 | 12 | 1 | 1 | -1.175 | 10 | 0 | 0
516.6 | 50.05 | 50.01 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.135 | -1.35 | -0.675 | -0.675 | 0 | 12 | 1 | 1 | -0.675 | 10 | 0 | 0
516.65 | 50.05 | 50.01 | 0 | 0 | 0 | 50.07 | -0.032353 | -0.035 | -0.35 | -0.175 | -0.175 | 0 | 12 | 1 | 1 | -0.175 | 10 | 0 | 0
516.7 | 50.1 | 50.01 | 0 | 0 | 0 | 50.1 | -0.05 | -0.05 | -0.5 | -0.25 | -0.25 | 0 | 12 | 1 | 1 | -0.25 | 10 | 0 | 0
516.75 | 50.1 | 50.01 | 0 | 0 | 0 | 50.1 | -0.05 | -0.05 | -0.5 | -0.25 | -0.25 | 0 | 12 | 1 | 1 | -0.25 | 10 | 0 | 0
516.8 | 50.11 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
516.85 | 50.11 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
516.9 | 50.06 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
516.95 | 50.06 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
517 | 50.04 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
517.05 | 50.04 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
517.1 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
517.15 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
517.2 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
517.25 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
517.3 | 50.11 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
517.35 | 50.11 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
517.4 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
517.45 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
517.5 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
517.55 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
517.6 | 50.02 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.11 | -0.145 | -0.145 | -1.45 | -0.73971 | -0.73971 | 0 | 12 | 1 | 1 | -0.73971 | 10 | 0 | 0
517.65 | 50.02 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.11 | -0.145 | -0.145 | -1.45 | -0.73971 | -0.73971 | 0 | 12 | 1 | 1 | -0.73971 | 10 | 0 | 0
517.7 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
517.75 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
517.8 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
517.85 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
517.9 | 50.01 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
517.95 | 50.01 | 50 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.045 | -0.45 | -0.225 | -0.225 | 0 | 12 | 1 | 1 | -0.225 | 10 | 0 | 0
518 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
518.05 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
518.1 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
518.15 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
518.2 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.14706 | 0.14706 | 0 | 12 | 1 | 1 | 0.14706 | 10 | 0 | 0
518.25 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
518.3 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
518.35 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
518.4 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
518.45 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
518.5 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
518.55 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
518.6 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
518.65 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
518.7 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
518.75 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
518.8 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
518.85 | 50 | 50 | 0 | 0 | 0 | 50.01 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
518.9 | 49.5 | 49.5 | 1 | 1 | 10 | 50.01 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
518.95 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
519 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
519.05 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
519.1 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
519.15 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
519.2 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
519.25 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
519.3 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
519.35 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
519.4 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
519.45 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.1 | 1 | 5.5 | 5.5 | 0 | 12 | 1 | 1 | 5.5 | 10 | 0 | 0
519.5 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.2 | 2 | 6 | 6 | 0 | 12 | 1 | 1 | 6 | 10 | 0 | 0
519.55 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.3 | 3 | 6.5 | 6.5 | 0 | 12 | 1 | 1 | 6.5 | 10 | 0 | 0
519.6 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.4 | 4 | 7 | 7 | 0 | 12 | 1 | 1 | 7 | 10 | 0 | 0
519.65 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.5 | 5 | 7.5 | 7.5 | 0 | 12 | 1 | 1 | 7.5 | 10 | 0 | 0
519.7 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.6 | 6 | 8 | 8 | 0 | 12 | 1 | 1 | 8 | 10 | 0 | 0
519.75 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.7 | 7 | 8.5 | 8.5 | 0 | 12 | 1 | 1 | 8.5 | 10 | 0 | 0
519.8 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.8 | 8 | 9 | 9 | 0 | 12 | 1 | 1 | 9 | 10 | 0 | 0
519.85 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.9 | 9 | 9.5 | 9.5 | 0 | 12 | 1 | 1 | 9.5 | 10 | 0 | 0
519.9 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
519.95 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
520 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
520.05 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
520.1 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
520.15 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
520.2 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
520.25 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
520.3 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
520.35 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
520.4 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
520.45 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
520.5 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
520.55 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
520.6 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
520.65 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
520.7 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
520.75 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
520.8 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
520.85 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
520.9 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
520.95 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
521 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
521.05 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
521.1 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
521.15 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
521.2 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
521.25 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
521.3 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
521.35 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
521.4 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
521.45 | 50.5 | 50.5 | -1 | 0.9 | 9 | 50.5 | -1 | -1 | -10 | -0.5 | -0.5 | 0 | 12 | 1 | 1 | -0.5 | 10 | 0 | 0
521.5 | 50.5 | 50.5 | -1 | 0.8 | 8 | 50.5 | -1 | -1 | -10 | -1 | -1 | 0 | 12 | 1 | 1 | -1 | 10 | 0 | 0
521.55 | 50.5 | 50.5 | -1 | 0.7 | 7 | 50.5 | -1 | -1 | -10 | -1.5 | -1.5 | 0 | 12 | 1 | 1 | -1.5 | 10 | 0 | 0
521.6 | 50.5 | 50.5 | -1 | 0.6 | 6 | 50.5 | -1 | -1 | -10 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
521.65 | 50.5 | 50.5 | -1 | 0.5 | 5 | 50.5 | -1 | -1 | -10 | -2.5 | -2.5 | 0 | 12 | 1 | 1 | -2.5 | 10 | 0 | 0
521.7 | 50.5 | 50.5 | -1 | 0.4 | 4 | 50.5 | -1 | -1 | -10 | -3 | -3 | 0 | 12 | 1 | 1 | -3 | 10 | 0 | 0
521.75 | 50.5 | 50.5 | -1 | 0.3 | 3 | 50.5 | -1 | -1 | -10 | -3.5 | -3.5 | 0 | 12 | 1 | 1 | -3.5 | 10 | 0 | 0
521.8 | 50.5 | 50.5 | -1 | 0.2 | 2 | 50.5 | -1 | -1 | -10 | -4 | -4 | 0 | 12 | 1 | 1 | -4 | 10 | 0 | 0
521.85 | 50.5 | 50.5 | -1 | 0.1 | 1 | 50.5 | -1 | -1 | -10 | -4.5 | -4.5 | 0 | 12 | 1 | 1 | -4.5 | 10 | 0 | 0
521.9 | 50.5 | 50.5 | -1 | 0 | 0 | 50.5 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
521.95 | 50.5 | 50.5 | -1 | -0.1 | -1 | 50.5 | -1 | -1 | -10 | -5.5 | -5.5 | 0 | 12 | 1 | 1 | -5.5 | 10 | 0 | 0
522 | 50.5 | 50.5 | -1 | -0.2 | -2 | 50.5 | -1 | -1 | -10 | -6 | -6 | 0 | 12 | 1 | 1 | -6 | 10 | 0 | 0
522.05 | 50.5 | 50.5 | -1 | -0.3 | -3 | 50.5 | -1 | -1 | -10 | -6.5 | -6.5 | 0 | 12 | 1 | 1 | -6.5 | 10 | 0 | 0
522.1 | 50.5 | 50.5 | -1 | -0.4 | -4 | 50.5 | -1 | -1 | -10 | -7 | -7 | 0 | 12 | 1 | 1 | -7 | 10 | 0 | 0
522.15 | 50.5 | 50.5 | -1 | -0.5 | -5 | 50.5 | -1 | -1 | -10 | -7.5 | -7.5 | 0 | 12 | 1 | 1 | -7.5 | 10 | 0 | 0
522.2 | 50.5 | 50.5 | -1 | -0.6 | -6 | 50.5 | -1 | -1 | -10 | -8 | -8 | 0 | 12 | 1 | 1 | -8 | 10 | 0 | 0
522.25 | 50.5 | 50.5 | -1 | -0.7 | -7 | 50.5 | -1 | -1 | -10 | -8.5 | -8.5 | 0 | 12 | 1 | 1 | -8.5 | 10 | 0 | 0
522.3 | 50.5 | 50.5 | -1 | -0.8 | -8 | 50.5 | -1 | -1 | -10 | -9 | -9 | 0 | 12 | 1 | 1 | -9 | 10 | 0 | 0
522.35 | 50.5 | 50.5 | -1 | -0.9 | -9 | 50.5 | -1 | -1 | -10 | -9.5 | -9.5 | 0 | 12 | 1 | 1 | -9.5 | 10 | 0 | 0
522.4 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
522.45 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
522.5 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
522.55 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
522.6 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
522.65 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
522.7 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
522.75 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
522.8 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
522.85 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
522.9 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
522.95 | 50.47 | 50.47 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
523 | 50.45 | 50.45 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
523.05 | 50.42 | 50.42 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
523.1 | 50.4 | 50.4 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
523.15 | 50.37 | 50.37 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
523.2 | 50.35 | 50.35 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
523.25 | 50.32 | 50.32 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
523.3 | 50.29 | 50.29 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
523.35 | 50.27 | 50.27 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
523.4 | 50.24 | 50.24 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
523.45 | 50.22 | 50.22 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
523.5 | 50.19 | 50.19 | -0.905 | -0.905 | -9.05 | 50.47 | -1 | -1 | -10 | -9.525 | -9.525 | 0 | 12 | 1 | 1 | -9.525 | 10 | 0 | 0
523.55 | 50.17 | 50.17 | -0.715 | -0.715 | -7.15 | 50.45 | -1 | -1 | -10 | -8.575 | -8.575 | 0 | 12 | 1 | 1 | -8.575 | 10 | 0 | 0
523.6 | 50.14 | 50.14 | -0.43 | -0.43 | -4.3 | 50.42 | -1 | -1 | -10 | -7.15 | -7.15 | 0 | 12 | 1 | 1 | -7.15 | 10 | 0 | 0
523.65 | 50.12 | 50.12 | -0.24 | -0.24 | -2.4 | 50.4 | -1 | -1 | -10 | -6.2 | -6.2 | 0 | 12 | 1 | 1 | -6.2 | 10 | 0 | 0
523.7 | 50.09 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 50.37 | -1 | -1 | -10 | -5.2206 | -5.2206 | 0 | 12 | 1 | 1 | -5.2206 | 10 | 0 | 0
523.75 | 50.06 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.35 | -1 | -1 | -10 | -5.1324 | -5.1324 | 0 | 12 | 1 | 1 | -5.1324 | 10 | 0 | 0
523.8 | 50.04 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.32 | -1 | -1 | -10 | -5.0735 | -5.0735 | 0 | 12 | 1 | 1 | -5.0735 | 10 | 0 | 0
523.85 | 50.01 | 50.01 | 0 | 0 | 0 | 50.29 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
523.9 | 49.99 | 49.99 | 0 | 0 | 0 | 50.27 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
523.95 | 49.96 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.24 | -1 | -1 | -10 | -4.9265 | -4.9265 | 0 | 12 | 1 | 1 | -4.9265 | 10 | 0 | 0
524 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.22 | -1 | -1 | -10 | -4.8676 | -4.8676 | 0 | 12 | 1 | 1 | -4.8676 | 10 | 0 | 0
524.05 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.19 | -0.905 | -0.905 | -9.05 | -4.3044 | -4.3044 | 0 | 12 | 1 | 1 | -4.3044 | 10 | 0 | 0
524.1 | 49.88 | 49.88 | 0.24 | 0.24 | 2.4 | 50.17 | -0.715 | -0.805 | -8.05 | -2.825 | -2.825 | 0 | 12 | 1 | 1 | -2.825 | 10 | 0 | 0
524.15 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.14 | -0.43 | -0.705 | -7.05 | -1.375 | -1.375 | 0 | 12 | 1 | 1 | -1.375 | 10 | 0 | 0
524.2 | 49.83 | 49.83 | 0.715 | 0.715 | 7.15 | 50.12 | -0.24 | -0.605 | -6.05 | 0.55 | 0.55 | 0 | 12 | 1 | 1 | 0.55 | 10 | 0 | 0
524.25 | 49.81 | 49.81 | 0.905 | 0.905 | 9.05 | 50.09 | -0.044118 | -0.505 | -5.05 | 2 | 2 | 0 | 12 | 1 | 1 | 2 | 10 | 0 | 0
524.3 | 49.78 | 49.78 | 1 | 1 | 10 | 50.06 | -0.026471 | -0.405 | -4.05 | 2.975 | 2.975 | 0 | 12 | 1 | 1 | 2.975 | 10 | 0 | 0
524.35 | 49.76 | 49.76 | 1 | 1 | 10 | 50.04 | -0.014706 | -0.305 | -3.05 | 3.475 | 3.475 | 0 | 12 | 1 | 1 | 3.475 | 10 | 0 | 0
524.4 | 49.73 | 49.73 | 1 | 1 | 10 | 50.01 | 0 | -0.205 | -2.05 | 3.975 | 3.975 | 0 | 12 | 1 | 1 | 3.975 | 10 | 0 | 0
524.45 | 49.71 | 49.71 | 1 | 1 | 10 | 49.99 | 0 | -0.105 | -1.05 | 4.475 | 4.475 | 0 | 12 | 1 | 1 | 4.475 | 10 | 0 | 0
524.5 | 49.68 | 49.68 | 1 | 1 | 10 | 49.96 | 0.014706 | -0.005 | -0.05 | 4.975 | 4.975 | 0 | 12 | 1 | 1 | 4.975 | 10 | 0 | 0
524.55 | 49.65 | 49.65 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
524.6 | 49.63 | 49.63 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
524.65 | 49.6 | 49.6 | 1 | 1 | 10 | 49.88 | 0.24 | 0.14412 | 1.4412 | 5.7206 | 5.7206 | 0 | 12 | 1 | 1 | 5.7206 | 10 | 0 | 0
524.7 | 49.58 | 49.58 | 1 | 1 | 10 | 49.86 | 0.43 | 0.24412 | 2.4412 | 6.2206 | 6.2206 | 0 | 12 | 1 | 1 | 6.2206 | 10 | 0 | 0
524.75 | 49.55 | 49.55 | 1 | 1 | 10 | 49.83 | 0.715 | 0.34412 | 3.4412 | 6.7206 | 6.7206 | 0 | 12 | 1 | 1 | 6.7206 | 10 | 0 | 0
524.8 | 49.53 | 49.53 | 1 | 1 | 10 | 49.81 | 0.905 | 0.44412 | 4.4412 | 7.2206 | 7.2206 | 0 | 12 | 1 | 1 | 7.2206 | 10 | 0 | 0
524.85 | 49.5 | 49.5 | 1 | 1 | 10 | 49.78 | 1 | 0.54412 | 5.4412 | 7.7206 | 7.7206 | 0 | 12 | 1 | 1 | 7.7206 | 10 | 0 | 0
524.9 | 49.5 | 49.5 | 1 | 1 | 10 | 49.76 | 1 | 0.64412 | 6.4412 | 8.2206 | 8.2206 | 0 | 12 | 1 | 1 | 8.2206 | 10 | 0 | 0
524.95 | 49.53 | 49.5 | 1 | 1 | 10 | 49.73 | 1 | 0.74412 | 7.4412 | 8.7206 | 8.7206 | 0 | 12 | 1 | 1 | 8.7206 | 10 | 0 | 0
525 | 49.55 | 49.5 | 1 | 1 | 10 | 49.71 | 1 | 0.84412 | 8.4412 | 9.2206 | 9.2206 | 0 | 12 | 1 | 1 | 9.2206 | 10 | 0 | 0
525.05 | 49.58 | 49.5 | 1 | 1 | 10 | 49.68 | 1 | 0.94412 | 9.4412 | 9.7206 | 9.7206 | 0 | 12 | 1 | 1 | 9.7206 | 10 | 0 | 0
525.1 | 49.6 | 49.5 | 1 | 1 | 10 | 49.65 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
525.15 | 49.63 | 49.5 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
525.2 | 49.65 | 49.5 | 1 | 1 | 10 | 49.65 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
525.25 | 49.68 | 49.5 | 1 | 1 | 10 | 49.68 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
525.3 | 49.71 | 49.5 | 1 | 1 | 10 | 49.71 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
525.35 | 49.73 | 49.5 | 1 | 1 | 10 | 49.73 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
525.4 | 49.76 | 49.5 | 1 | 1 | 10 | 49.76 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
525.45 | 49.78 | 49.5 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
525.5 | 49.81 | 49.53 | 1 | 1 | 10 | 49.81 | 0.905 | 0.905 | 9.05 | 9.525 | 9.525 | 0 | 12 | 1 | 1 | 9.525 | 10 | 0 | 0
525.55 | 49.83 | 49.55 | 1 | 1 | 10 | 49.83 | 0.715 | 0.715 | 7.15 | 8.575 | 8.575 | 0 | 12 | 1 | 1 | 8.575 | 10 | 0 | 0
525.6 | 49.86 | 49.58 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
525.65 | 49.88 | 49.6 | 1 | 1 | 10 | 49.88 | 0.24 | 0.24 | 2.4 | 6.2 | 6.2 | 0 | 12 | 1 | 1 | 6.2 | 10 | 0 | 0
525.7 | 49.91 | 49.63 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
525.75 | 49.94 | 49.65 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
525.8 | 49.96 | 49.68 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
525.85 | 49.99 | 49.71 | 1 | 1 | 10 | 49.99 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
525.9 | 50.01 | 49.73 | 1 | 1 | 10 | 50.01 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
525.95 | 50.04 | 49.76 | 1 | 1 | 10 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 4.9265 | 4.9265 | 0 | 12 | 1 | 1 | 4.9265 | 10 | 0 | 0
526 | 50.06 | 49.78 | 1 | 1 | 10 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 4.8676 | 4.8676 | 0 | 12 | 1 | 1 | 4.8676 | 10 | 0 | 0
526.05 | 50.09 | 49.81 | 0.905 | 0.905 | 9.05 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 4.3044 | 4.3044 | 0 | 12 | 1 | 1 | 4.3044 | 10 | 0 | 0
526.1 | 50.12 | 49.83 | 0.715 | 0.805 | 8.05 | 50.12 | -0.24 | -0.24 | -2.4 | 2.825 | 2.825 | 0 | 12 | 1 | 1 | 2.825 | 10 | 0 | 0
526.15 | 50.14 | 49.86 | 0.43 | 0.705 | 7.05 | 50.14 | -0.43 | -0.43 | -4.3 | 1.375 | 1.375 | 0 | 12 | 1 | 1 | 1.375 | 10 | 0 | 0
526.2 | 50.17 | 49.88 | 0.24 | 0.605 | 6.05 | 50.17 | -0.715 | -0.715 | -7.15 | -0.55 | -0.55 | 0 | 12 | 1 | 1 | -0.55 | 10 | 0 | 0
526.25 | 50.19 | 49.91 | 0.044118 | 0.505 | 5.05 | 50.19 | -0.905 | -0.905 | -9.05 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
526.3 | 50.22 | 49.94 | 0.026471 | 0.405 | 4.05 | 50.22 | -1 | -1 | -10 | -2.975 | -2.975 | 0 | 12 | 1 | 1 | -2.975 | 10 | 0 | 0
526.35 | 50.24 | 49.96 | 0.014706 | 0.305 | 3.05 | 50.24 | -1 | -1 | -10 | -3.475 | -3.475 | 0 | 12 | 1 | 1 | -3.475 | 10 | 0 | 0
526.4 | 50.27 | 49.99 | 0 | 0.205 | 2.05 | 50.27 | -1 | -1 | -10 | -3.975 | -3.975 | 0 | 12 | 1 | 1 | -3.975 | 10 | 0 | 0
526.45 | 50.29 | 50.01 | 0 | 0.105 | 1.05 | 50.29 | -1 | -1 | -10 | -4.475 | -4.475 | 0 | 12 | 1 | 1 | -4.475 | 10 | 0 | 0
526.5 | 50.32 | 50.04 | -0.014706 | 0.005 | 0.05 | 50.32 | -1 | -1 | -10 | -4.975 | -4.975 | 0 | 12 | 1 | 1 | -4.975 | 10 | 0 | 0
526.55 | 50.35 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.35 | -1 | -1 | -10 | -5.1324 | -5.1324 | 0 | 12 | 1 | 1 | -5.1324 | 10 | 0 | 0
526.6 | 50.37 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 50.37 | -1 | -1 | -10 | -5.2206 | -5.2206 | 0 | 12 | 1 | 1 | -5.2206 | 10 | 0 | 0
526.65 | 50.4 | 50.12 | -0.24 | -0.14412 | -1.4412 | 50.4 | -1 | -1 | -10 | -5.7206 | -5.7206 | 0 | 12 | 1 | 1 | -5.7206 | 10 | 0 | 0
526.7 | 50.42 | 50.14 | -0.43 | -0.24412 | -2.4412 | 50.42 | -1 | -1 | -10 | -6.2206 | -6.2206 | 0 | 12 | 1 | 1 | -6.2206 | 10 | 0 | 0
526.75 | 50.45 | 50.17 | -0.715 | -0.34412 | -3.4412 | 50.45 | -1 | -1 | -10 | -6.7206 | -6.7206 | 0 | 12 | 1 | 1 | -6.7206 | 10 | 0 | 0
526.8 | 50.47 | 50.19 | -0.905 | -0.44412 | -4.4412 | 50.47 | -1 | -1 | -10 | -7.2206 | -7.2206 | 0 | 12 | 1 | 1 | -7.2206 | 10 | 0 | 0
526.85 | 50.5 | 50.22 | -1 | -0.54412 | -5.4412 | 50.5 | -1 | -1 | -10 | -7.7206 | -7.7206 | 0 | 12 | 1 | 1 | -7.7206 | 10 | 0 | 0
526.9 | 50.5 | 50.24 | -1 | -0.64412 | -6.4412 | 50.5 | -1 | -1 | -10 | -8.2206 | -8.2206 | 0 | 12 | 1 | 1 | -8.2206 | 10 | 0 | 0
526.95 | 50.47 | 50.27 | -1 | -0.74412 | -7.4412 | 50.5 | -1 | -1 | -10 | -8.7206 | -8.7206 | 0 | 12 | 1 | 1 | -8.7206 | 10 | 0 | 0
527 | 50.45 | 50.29 | -1 | -0.84412 | -8.4412 | 50.5 | -1 | -1 | -10 | -9.2206 | -9.2206 | 0 | 12 | 1 | 1 | -9.2206 | 10 | 0 | 0
527.05 | 50.42 | 50.32 | -1 | -0.94412 | -9.4412 | 50.5 | -1 | -1 | -10 | -9.7206 | -9.7206 | 0 | 12 | 1 | 1 | -9.7206 | 10 | 0 | 0
527.1 | 50.39 | 50.35 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
527.15 | 50.37 | 50.37 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
527.2 | 50.34 | 50.34 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
527.25 | 50.32 | 50.32 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
527.3 | 50.29 | 50.29 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
527.35 | 50.26 | 50.26 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
527.4 | 50.24 | 50.24 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
527.45 | 50.21 | 50.21 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
527.5 | 50.18 | 50.18 | -0.81 | -0.81 | -8.1 | 50.47 | -1 | -1 | -10 | -9.05 | -9.05 | 0 | 12 | 1 | 1 | -9.05 | 10 | 0 | 0
527.55 | 50.16 | 50.16 | -0.62 | -0.62 | -6.2 | 50.45 | -1 | -1 | -10 | -8.1 | -8.1 | 0 | 12 | 1 | 1 | -8.1 | 10 | 0 | 0
527.6 | 50.13 | 50.13 | -0.335 | -0.335 | -3.35 | 50.42 | -1 | -1 | -10 | -6.675 | -6.675 | 0 | 12 | 1 | 1 | -6.675 | 10 | 0 | 0
527.65 | 50.11 | 50.11 | -0.145 | -0.145 | -1.45 | 50.39 | -1 | -1 | -10 | -5.725 | -5.725 | 0 | 12 | 1 | 1 | -5.725 | 10 | 0 | 0
527.7 | 50.08 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 50.37 | -1 | -1 | -10 | -5.1912 | -5.1912 | 0 | 12 | 1 | 1 | -5.1912 | 10 | 0 | 0
527.75 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.34 | -1 | -1 | -10 | -5.1029 | -5.1029 | 0 | 12 | 1 | 1 | -5.1029 | 10 | 0 | 0
527.8 | 50.03 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 50.32 | -1 | -1 | -10 | -5.0441 | -5.0441 | 0 | 12 | 1 | 1 | -5.0441 | 10 | 0 | 0
527.85 | 50 | 50 | 0 | 0 | 0 | 50.29 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
527.9 | 50 | 50 | 0 | 0 | 0 | 50.26 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
527.95 | 50 | 50 | 0 | 0 | 0 | 50.24 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
528 | 50 | 50 | 0 | 0 | 0 | 50.21 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
528.05 | 50 | 50 | 0 | 0 | 0 | 50.18 | -0.81 | -0.9 | -9 | -4.5 | -4.5 | 0 | 12 | 1 | 1 | -4.5 | 10 | 0 | 0
528.1 | 50 | 50 | 0 | 0 | 0 | 50.16 | -0.62 | -0.8 | -8 | -4 | -4 | 0 | 12 | 1 | 1 | -4 | 10 | 0 | 0
528.15 | 50 | 50 | 0 | 0 | 0 | 50.13 | -0.335 | -0.7 | -7 | -3.5 | -3.5 | 0 | 12 | 1 | 1 | -3.5 | 10 | 0 | 0
528.2 | 50.01 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.6 | -6 | -3 | -3 | 0 | 12 | 1 | 1 | -3 | 10 | 0 | 0
528.25 | 50.01 | 50 | 0 | 0 | 0 | 50.08 | -0.038235 | -0.5 | -5 | -2.5 | -2.5 | 0 | 12 | 1 | 1 | -2.5 | 10 | 0 | 0
528.3 | 49.99 | 49.99 | 0 | 0 | 0 | 50.05 | -0.020588 | -0.4 | -4 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
528.35 | 49.99 | 49.99 | 0 | 0 | 0 | 50.03 | -0.0088235 | -0.3 | -3 | -1.5 | -1.5 | 0 | 12 | 1 | 1 | -1.5 | 10 | 0 | 0
528.4 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | -0.2 | -2 | -0.83824 | -0.83824 | 0 | 12 | 1 | 1 | -0.83824 | 10 | 0 | 0
528.45 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | -0.1 | -1 | -0.33824 | -0.33824 | 0 | 12 | 1 | 1 | -0.33824 | 10 | 0 | 0
528.5 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
528.55 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
528.6 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
528.65 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
528.7 | 49.89 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
528.75 | 49.89 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
528.8 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50.01 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
528.85 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
528.9 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
528.95 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 2.7868 | 2.7868 | 0 | 12 | 1 | 1 | 2.7868 | 10 | 0 | 0
529 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 2.7868 | 2.7868 | 0 | 12 | 1 | 1 | 2.7868 | 10 | 0 | 0
529.05 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 2.8456 | 2.8456 | 0 | 12 | 1 | 1 | 2.8456 | 10 | 0 | 0
529.1 | 49.94 | 49.85 | 0.525 | 0.525 | 5.25 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 2.7574 | 2.7574 | 0 | 12 | 1 | 1 | 2.7574 | 10 | 0 | 0
529.15 | 49.94 | 49.85 | 0.525 | 0.525 | 5.25 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 2.7574 | 2.7574 | 0 | 12 | 1 | 1 | 2.7574 | 10 | 0 | 0
529.2 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
529.25 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
529.3 | 49.93 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
529.35 | 49.93 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
529.4 | 49.96 | 49.85 | 0.525 | 0.525 | 5.25 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 2.6985 | 2.6985 | 0 | 12 | 1 | 1 | 2.6985 | 10 | 0 | 0
529.45 | 49.96 | 49.85 | 0.525 | 0.525 | 5.25 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 2.6985 | 2.6985 | 0 | 12 | 1 | 1 | 2.6985 | 10 | 0 | 0
529.5 | 49.99 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
529.55 | 49.99 | 49.91 | 0.044118 | 0.425 | 4.25 | 49.99 | 0 | 0 | 0 | 2.125 | 2.125 | 0 | 12 | 1 | 1 | 2.125 | 10 | 0 | 0
529.6 | 49.99 | 49.91 | 0.044118 | 0.325 | 3.25 | 49.99 | 0 | 0 | 0 | 1.625 | 1.625 | 0 | 12 | 1 | 1 | 1.625 | 10 | 0 | 0
529.65 | 49.99 | 49.93 | 0.032353 | 0.225 | 2.25 | 49.99 | 0 | 0 | 0 | 1.125 | 1.125 | 0 | 12 | 1 | 1 | 1.125 | 10 | 0 | 0
529.7 | 49.96 | 49.93 | 0.032353 | 0.125 | 1.25 | 49.99 | 0 | 0 | 0 | 0.625 | 0.625 | 0 | 12 | 1 | 1 | 0.625 | 10 | 0 | 0
529.75 | 49.96 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 49.99 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
529.8 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
529.85 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
529.9 | 50.05 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.058824 | 0.058824 | 0 | 12 | 1 | 1 | 0.058824 | 10 | 0 | 0
529.95 | 50.05 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
530 | 49.97 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
530.05 | 49.97 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
530.1 | 49.92 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
530.15 | 49.92 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
530.2 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
530.25 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
530.3 | 49.94 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
530.35 | 49.94 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
530.4 | 50.01 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
530.45 | 50.01 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
530.5 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
530.55 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
530.6 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
530.65 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
530.7 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
530.75 | 49.95 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
530.8 | 49.97 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
530.85 | 49.97 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
530.9 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
530.95 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
531 | 49.87 | 49.87 | 0.335 | 0.335 | 3.35 | 50.01 | 0 | 0 | 0 | 1.675 | 1.675 | 0 | 12 | 1 | 1 | 1.675 | 10 | 0 | 0
531.05 | 49.87 | 49.87 | 0.335 | 0.335 | 3.35 | 49.99 | 0 | 0 | 0 | 1.675 | 1.675 | 0 | 12 | 1 | 1 | 1.675 | 10 | 0 | 0
531.1 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
531.15 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 2.6691 | 2.6691 | 0 | 12 | 1 | 1 | 2.6691 | 10 | 0 | 0
531.2 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
531.25 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
531.3 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
531.35 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
531.4 | 49.84 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
531.45 | 49.84 | 49.79 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
531.5 | 49.89 | 49.79 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
531.55 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.12647 | 1.2647 | 5.6324 | 5.6324 | 0 | 12 | 1 | 1 | 5.6324 | 10 | 0 | 0
531.6 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.145 | 1.45 | 5.725 | 5.725 | 0 | 12 | 1 | 1 | 5.725 | 10 | 0 | 0
531.65 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.145 | 1.45 | 5.725 | 5.725 | 0 | 12 | 1 | 1 | 5.725 | 10 | 0 | 0
531.7 | 49.96 | 49.79 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
531.75 | 49.96 | 49.79 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
531.8 | 50.02 | 49.79 | 1 | 1 | 10 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 4.9853 | 4.9853 | 0 | 12 | 1 | 1 | 4.9853 | 10 | 0 | 0
531.85 | 50.02 | 49.79 | 1 | 1 | 10 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 4.9853 | 4.9853 | 0 | 12 | 1 | 1 | 4.9853 | 10 | 0 | 0
531.9 | 50.03 | 49.79 | 1 | 1 | 10 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.9559 | 4.9559 | 0 | 12 | 1 | 1 | 4.9559 | 10 | 0 | 0
531.95 | 50.03 | 49.84 | 0.62 | 0.9 | 9 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.4559 | 4.4559 | 0 | 12 | 1 | 1 | 4.4559 | 10 | 0 | 0
532 | 50.02 | 49.84 | 0.62 | 0.8 | 8 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 3.9559 | 3.9559 | 0 | 12 | 1 | 1 | 3.9559 | 10 | 0 | 0
532.05 | 50.02 | 49.89 | 0.145 | 0.7 | 7 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 3.4559 | 3.4559 | 0 | 12 | 1 | 1 | 3.4559 | 10 | 0 | 0
532.1 | 50.08 | 49.89 | 0.145 | 0.6 | 6 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 2.8088 | 2.8088 | 0 | 12 | 1 | 1 | 2.8088 | 10 | 0 | 0
532.15 | 50.08 | 49.89 | 0.145 | 0.5 | 5 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 2.3088 | 2.3088 | 0 | 12 | 1 | 1 | 2.3088 | 10 | 0 | 0
532.2 | 50.01 | 49.89 | 0.145 | 0.4 | 4 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 1.8088 | 1.8088 | 0 | 12 | 1 | 1 | 1.8088 | 10 | 0 | 0
532.25 | 50.01 | 49.96 | 0.014706 | 0.3 | 3 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 1.3088 | 1.3088 | 0 | 12 | 1 | 1 | 1.3088 | 10 | 0 | 0
532.3 | 49.94 | 49.94 | 0.026471 | 0.2 | 2 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.80882 | 0.80882 | 0 | 12 | 1 | 1 | 0.80882 | 10 | 0 | 0
532.35 | 49.94 | 49.94 | 0.026471 | 0.1 | 1 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.30882 | 0.30882 | 0 | 12 | 1 | 1 | 0.30882 | 10 | 0 | 0
532.4 | 50 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
532.45 | 50 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
532.5 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
532.55 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
532.6 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
532.65 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
532.7 | 49.92 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
532.75 | 49.92 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
532.8 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50.01 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
532.85 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
532.9 | 49.92 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
532.95 | 49.92 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
533 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
533.05 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
533.1 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
533.15 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
533.2 | 49.87 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
533.25 | 49.87 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
533.3 | 49.8 | 49.8 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
533.35 | 49.8 | 49.8 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
533.4 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
533.45 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
533.5 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
533.55 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
533.6 | 49.72 | 49.72 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
533.65 | 49.72 | 49.72 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
533.7 | 49.67 | 49.67 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
533.75 | 49.67 | 49.67 | 1 | 1 | 10 | 49.87 | 0.335 | 0.14412 | 1.4412 | 5.7206 | 5.7206 | 0 | 12 | 1 | 1 | 5.7206 | 10 | 0 | 0
533.8 | 49.65 | 49.65 | 1 | 1 | 10 | 49.87 | 0.335 | 0.24412 | 2.4412 | 6.2206 | 6.2206 | 0 | 12 | 1 | 1 | 6.2206 | 10 | 0 | 0
533.85 | 49.65 | 49.65 | 1 | 1 | 10 | 49.8 | 1 | 0.34412 | 3.4412 | 6.7206 | 6.7206 | 0 | 12 | 1 | 1 | 6.7206 | 10 | 0 | 0
533.9 | 49.59 | 49.59 | 1 | 1 | 10 | 49.8 | 1 | 0.44412 | 4.4412 | 7.2206 | 7.2206 | 0 | 12 | 1 | 1 | 7.2206 | 10 | 0 | 0
533.95 | 49.59 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.54412 | 5.4412 | 7.7206 | 7.7206 | 0 | 12 | 1 | 1 | 7.7206 | 10 | 0 | 0
534 | 49.66 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.64412 | 6.4412 | 8.2206 | 8.2206 | 0 | 12 | 1 | 1 | 8.2206 | 10 | 0 | 0
534.05 | 49.66 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.74412 | 7.4412 | 8.7206 | 8.7206 | 0 | 12 | 1 | 1 | 8.7206 | 10 | 0 | 0
534.1 | 49.63 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.84412 | 8.4412 | 9.2206 | 9.2206 | 0 | 12 | 1 | 1 | 9.2206 | 10 | 0 | 0
534.15 | 49.63 | 49.59 | 1 | 1 | 10 | 49.72 | 1 | 0.94412 | 9.4412 | 9.7206 | 9.7206 | 0 | 12 | 1 | 1 | 9.7206 | 10 | 0 | 0
534.2 | 49.61 | 49.59 | 1 | 1 | 10 | 49.72 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
534.25 | 49.61 | 49.59 | 1 | 1 | 10 | 49.67 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
534.3 | 49.54 | 49.54 | 1 | 1 | 10 | 49.67 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
534.35 | 49.54 | 49.54 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
534.4 | 49.46 | 49.46 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
534.45 | 49.46 | 49.46 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
534.5 | 49.45 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
534.55 | 49.45 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
534.6 | 49.51 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
534.65 | 49.51 | 49.45 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
534.7 | 49.5 | 49.45 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
534.75 | 49.5 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
534.8 | 49.54 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
534.85 | 49.54 | 49.45 | 1 | 1 | 10 | 49.54 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
534.9 | 49.59 | 49.45 | 1 | 1 | 10 | 49.59 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
534.95 | 49.59 | 49.45 | 1 | 1 | 10 | 49.59 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
535 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
535.05 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
535.1 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
535.15 | 49.61 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
535.2 | 49.53 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
535.25 | 49.53 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
535.3 | 49.54 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
535.35 | 49.54 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
535.4 | 49.61 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
535.45 | 49.61 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
535.5 | 49.66 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
535.55 | 49.66 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
535.6 | 49.64 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
535.65 | 49.64 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
535.7 | 49.69 | 49.53 | 1 | 1 | 10 | 49.69 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
535.75 | 49.69 | 49.53 | 1 | 1 | 10 | 49.69 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
535.8 | 49.74 | 49.53 | 1 | 1 | 10 | 49.74 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
535.85 | 49.74 | 49.54 | 1 | 1 | 10 | 49.74 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
535.9 | 49.78 | 49.54 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
535.95 | 49.78 | 49.61 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
536 | 49.82 | 49.61 | 1 | 1 | 10 | 49.82 | 0.81 | 0.81 | 8.1 | 9.05 | 9.05 | 0 | 12 | 1 | 1 | 9.05 | 10 | 0 | 0
536.05 | 49.82 | 49.64 | 1 | 1 | 10 | 49.82 | 0.81 | 0.81 | 8.1 | 9.05 | 9.05 | 0 | 12 | 1 | 1 | 9.05 | 10 | 0 | 0
536.1 | 49.86 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
536.15 | 49.86 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
536.2 | 49.84 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
536.25 | 49.84 | 49.69 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
536.3 | 49.91 | 49.69 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
536.35 | 49.91 | 49.74 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
536.4 | 49.97 | 49.74 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
536.45 | 49.97 | 49.78 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
536.5 | 50.03 | 49.78 | 1 | 1 | 10 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.9559 | 4.9559 | 0 | 12 | 1 | 1 | 4.9559 | 10 | 0 | 0
536.55 | 50.03 | 49.82 | 0.81 | 0.9 | 9 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.4559 | 4.4559 | 0 | 12 | 1 | 1 | 4.4559 | 10 | 0 | 0
536.6 | 50.05 | 49.82 | 0.81 | 0.81 | 8.1 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 3.9471 | 3.9471 | 0 | 12 | 1 | 1 | 3.9471 | 10 | 0 | 0
536.65 | 50.05 | 49.84 | 0.62 | 0.71 | 7.1 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 3.4471 | 3.4471 | 0 | 12 | 1 | 1 | 3.4471 | 10 | 0 | 0
536.7 | 50.01 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
536.75 | 50.01 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
536.8 | 49.95 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
536.85 | 49.95 | 49.91 | 0.044118 | 0.52 | 5.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.4971 | 2.4971 | 0 | 12 | 1 | 1 | 2.4971 | 10 | 0 | 0
536.9 | 49.99 | 49.91 | 0.044118 | 0.42 | 4.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 1.9971 | 1.9971 | 0 | 12 | 1 | 1 | 1.9971 | 10 | 0 | 0
536.95 | 49.99 | 49.95 | 0.020588 | 0.32 | 3.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 1.4971 | 1.4971 | 0 | 12 | 1 | 1 | 1.4971 | 10 | 0 | 0
537 | 49.92 | 49.92 | 0.038235 | 0.22 | 2.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.99706 | 0.99706 | 0 | 12 | 1 | 1 | 0.99706 | 10 | 0 | 0
537.05 | 49.92 | 49.92 | 0.038235 | 0.12 | 1.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.49706 | 0.49706 | 0 | 12 | 1 | 1 | 0.49706 | 10 | 0 | 0
537.1 | 49.97 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
537.15 | 49.97 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
537.2 | 50.02 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
537.25 | 50.02 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.17647 | 0.17647 | 0 | 12 | 1 | 1 | 0.17647 | 10 | 0 | 0
537.3 | 50.07 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
537.35 | 50.07 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
537.4 | 50.06 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
537.45 | 50.06 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
537.5 | 50.13 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
537.55 | 50.13 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
537.6 | 50.09 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
537.65 | 50.09 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6309 | -1.6309 | 0 | 12 | 1 | 1 | -1.6309 | 10 | 0 | 0
537.7 | 50.07 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6309 | -1.6309 | 0 | 12 | 1 | 1 | -1.6309 | 10 | 0 | 0
537.75 | 50.07 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6897 | -1.6897 | 0 | 12 | 1 | 1 | -1.6897 | 10 | 0 | 0
537.8 | 50.07 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6897 | -1.6897 | 0 | 12 | 1 | 1 | -1.6897 | 10 | 0 | 0
537.85 | 50.07 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.13 | -0.335 | -0.335 | -3.35 | -1.8074 | -1.8074 | 0 | 12 | 1 | 1 | -1.8074 | 10 | 0 | 0
537.9 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.13 | -0.335 | -0.335 | -3.35 | -1.7779 | -1.7779 | 0 | 12 | 1 | 1 | -1.7779 | 10 | 0 | 0
537.95 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.13 | -0.335 | -0.335 | -3.35 | -1.7779 | -1.7779 | 0 | 12 | 1 | 1 | -1.7779 | 10 | 0 | 0
538 | 50.01 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
538.05 | 50.01 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
538.1 | 50.07 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
538.15 | 50.07 | 50.01 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.235 | -2.35 | -1.175 | -1.175 | 0 | 12 | 1 | 1 | -1.175 | 10 | 0 | 0
538.2 | 50.05 | 50.01 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.135 | -1.35 | -0.675 | -0.675 | 0 | 12 | 1 | 1 | -0.675 | 10 | 0 | 0
538.25 | 50.05 | 50.01 | 0 | 0 | 0 | 50.07 | -0.032353 | -0.035 | -0.35 | -0.175 | -0.175 | 0 | 12 | 1 | 1 | -0.175 | 10 | 0 | 0
538.3 | 50.1 | 50.01 | 0 | 0 | 0 | 50.1 | -0.05 | -0.05 | -0.5 | -0.25 | -0.25 | 0 | 12 | 1 | 1 | -0.25 | 10 | 0 | 0
538.35 | 50.1 | 50.01 | 0 | 0 | 0 | 50.1 | -0.05 | -0.05 | -0.5 | -0.25 | -0.25 | 0 | 12 | 1 | 1 | -0.25 | 10 | 0 | 0
538.4 | 50.11 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
538.45 | 50.11 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
538.5 | 50.06 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
538.55 | 50.06 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
538.6 | 50.04 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
538.65 | 50.04 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
538.7 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
538.75 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
538.8 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
538.85 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
538.9 | 50.11 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
538.95 | 50.11 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
539 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
539.05 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
539.1 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
539.15 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
539.2 | 50.02 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.11 | -0.145 | -0.145 | -1.45 | -0.73971 | -0.73971 | 0 | 12 | 1 | 1 | -0.73971 | 10 | 0 | 0
539.25 | 50.02 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.11 | -0.145 | -0.145 | -1.45 | -0.73971 | -0.73971 | 0 | 12 | 1 | 1 | -0.73971 | 10 | 0 | 0
539.3 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
539.35 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
539.4 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
539.45 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
539.5 | 50.01 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
539.55 | 50.01 | 50 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.045 | -0.45 | -0.225 | -0.225 | 0 | 12 | 1 | 1 | -0.225 | 10 | 0 | 0
539.6 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
539.65 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
539.7 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
539.75 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
539.8 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.14706 | 0.14706 | 0 | 12 | 1 | 1 | 0.14706 | 10 | 0 | 0
539.85 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
539.9 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
539.95 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
540 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
540.05 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
540.1 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
540.15 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
540.2 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
540.25 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
540.3 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
540.35 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
540.4 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
540.45 | 50 | 50 | 0 | 0 | 0 | 50.01 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
540.5 | 49.5 | 49.5 | 1 | 1 | 10 | 50.01 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
540.55 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
540.6 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
540.65 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
540.7 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
540.75 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
540.8 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
540.85 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
540.9 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
540.95 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
541 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
541.05 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.1 | 1 | 5.5 | 5.5 | 0 | 12 | 1 | 1 | 5.5 | 10 | 0 | 0
541.1 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.2 | 2 | 6 | 6 | 0 | 12 | 1 | 1 | 6 | 10 | 0 | 0
541.15 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.3 | 3 | 6.5 | 6.5 | 0 | 12 | 1 | 1 | 6.5 | 10 | 0 | 0
541.2 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.4 | 4 | 7 | 7 | 0 | 12 | 1 | 1 | 7 | 10 | 0 | 0
541.25 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.5 | 5 | 7.5 | 7.5 | 0 | 12 | 1 | 1 | 7.5 | 10 | 0 | 0
541.3 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.6 | 6 | 8 | 8 | 0 | 12 | 1 | 1 | 8 | 10 | 0 | 0
541.35 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.7 | 7 | 8.5 | 8.5 | 0 | 12 | 1 | 1 | 8.5 | 10 | 0 | 0
541.4 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.8 | 8 | 9 | 9 | 0 | 12 | 1 | 1 | 9 | 10 | 0 | 0
541.45 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.9 | 9 | 9.5 | 9.5 | 0 | 12 | 1 | 1 | 9.5 | 10 | 0 | 0
541.5 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
541.55 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
541.6 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
541.65 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
541.7 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
541.75 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
541.8 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
541.85 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
541.9 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
541.95 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
542 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
542.05 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
542.1 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
542.15 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
542.2 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
542.25 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
542.3 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
542.35 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
542.4 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
542.45 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
542.5 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
542.55 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
542.6 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
542.65 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
542.7 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
542.75 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
542.8 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
542.85 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
542.9 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
542.95 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
543 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
543.05 | 50.5 | 50.5 | -1 | 0.9 | 9 | 50.5 | -1 | -1 | -10 | -0.5 | -0.5 | 0 | 12 | 1 | 1 | -0.5 | 10 | 0 | 0
543.1 | 50.5 | 50.5 | -1 | 0.8 | 8 | 50.5 | -1 | -1 | -10 | -1 | -1 | 0 | 12 | 1 | 1 | -1 | 10 | 0 | 0
543.15 | 50.5 | 50.5 | -1 | 0.7 | 7 | 50.5 | -1 | -1 | -10 | -1.5 | -1.5 | 0 | 12 | 1 | 1 | -1.5 | 10 | 0 | 0
543.2 | 50.5 | 50.5 | -1 | 0.6 | 6 | 50.5 | -1 | -1 | -10 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
543.25 | 50.5 | 50.5 | -1 | 0.5 | 5 | 50.5 | -1 | -1 | -10 | -2.5 | -2.5 | 0 | 12 | 1 | 1 | -2.5 | 10 | 0 | 0
543.3 | 50.5 | 50.5 | -1 | 0.4 | 4 | 50.5 | -1 | -1 | -10 | -3 | -3 | 0 | 12 | 1 | 1 | -3 | 10 | 0 | 0
543.35 | 50.5 | 50.5 | -1 | 0.3 | 3 | 50.5 | -1 | -1 | -10 | -3.5 | -3.5 | 0 | 12 | 1 | 1 | -3.5 | 10 | 0 | 0
543.4 | 50.5 | 50.5 | -1 | 0.2 | 2 | 50.5 | -1 | -1 | -10 | -4 | -4 | 0 | 12 | 1 | 1 | -4 | 10 | 0 | 0
543.45 | 50.5 | 50.5 | -1 | 0.1 | 1 | 50.5 | -1 | -1 | -10 | -4.5 | -4.5 | 0 | 12 | 1 | 1 | -4.5 | 10 | 0 | 0
543.5 | 50.5 | 50.5 | -1 | 0 | 0 | 50.5 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
543.55 | 50.5 | 50.5 | -1 | -0.1 | -1 | 50.5 | -1 | -1 | -10 | -5.5 | -5.5 | 0 | 12 | 1 | 1 | -5.5 | 10 | 0 | 0
543.6 | 50.5 | 50.5 | -1 | -0.2 | -2 | 50.5 | -1 | -1 | -10 | -6 | -6 | 0 | 12 | 1 | 1 | -6 | 10 | 0 | 0
543.65 | 50.5 | 50.5 | -1 | -0.3 | -3 | 50.5 | -1 | -1 | -10 | -6.5 | -6.5 | 0 | 12 | 1 | 1 | -6.5 | 10 | 0 | 0
543.7 | 50.5 | 50.5 | -1 | -0.4 | -4 | 50.5 | -1 | -1 | -10 | -7 | -7 | 0 | 12 | 1 | 1 | -7 | 10 | 0 | 0
543.75 | 50.5 | 50.5 | -1 | -0.5 | -5 | 50.5 | -1 | -1 | -10 | -7.5 | -7.5 | 0 | 12 | 1 | 1 | -7.5 | 10 | 0 | 0
543.8 | 50.5 | 50.5 | -1 | -0.6 | -6 | 50.5 | -1 | -1 | -10 | -8 | -8 | 0 | 12 | 1 | 1 | -8 | 10 | 0 | 0
543.85 | 50.5 | 50.5 | -1 | -0.7 | -7 | 50.5 | -1 | -1 | -10 | -8.5 | -8.5 | 0 | 12 | 1 | 1 | -8.5 | 10 | 0 | 0
543.9 | 50.5 | 50.5 | -1 | -0.8 | -8 | 50.5 | -1 | -1 | -10 | -9 | -9 | 0 | 12 | 1 | 1 | -9 | 10 | 0 | 0
543.95 | 50.5 | 50.5 | -1 | -0.9 | -9 | 50.5 | -1 | -1 | -10 | -9.5 | -9.5 | 0 | 12 | 1 | 1 | -9.5 | 10 | 0 | 0
544 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
544.05 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
544.1 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
544.15 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
544.2 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
544.25 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
544.3 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
544.35 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
544.4 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
544.45 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
544.5 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
544.55 | 50.47 | 50.47 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
544.6 | 50.45 | 50.45 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
544.65 | 50.42 | 50.42 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
544.7 | 50.4 | 50.4 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
544.75 | 50.37 | 50.37 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
544.8 | 50.35 | 50.35 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
544.85 | 50.32 | 50.32 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
544.9 | 50.29 | 50.29 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
544.95 | 50.27 | 50.27 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
545 | 50.24 | 50.24 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
545.05 | 50.22 | 50.22 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
545.1 | 50.19 | 50.19 | -0.905 | -0.905 | -9.05 | 50.47 | -1 | -1 | -10 | -9.525 | -9.525 | 0 | 12 | 1 | 1 | -9.525 | 10 | 0 | 0
545.15 | 50.17 | 50.17 | -0.715 | -0.715 | -7.15 | 50.45 | -1 | -1 | -10 | -8.575 | -8.575 | 0 | 12 | 1 | 1 | -8.575 | 10 | 0 | 0
545.2 | 50.14 | 50.14 | -0.43 | -0.43 | -4.3 | 50.42 | -1 | -1 | -10 | -7.15 | -7.15 | 0 | 12 | 1 | 1 | -7.15 | 10 | 0 | 0
545.25 | 50.12 | 50.12 | -0.24 | -0.24 | -2.4 | 50.4 | -1 | -1 | -10 | -6.2 | -6.2 | 0 | 12 | 1 | 1 | -6.2 | 10 | 0 | 0
545.3 | 50.09 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 50.37 | -1 | -1 | -10 | -5.2206 | -5.2206 | 0 | 12 | 1 | 1 | -5.2206 | 10 | 0 | 0
545.35 | 50.06 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.35 | -1 | -1 | -10 | -5.1324 | -5.1324 | 0 | 12 | 1 | 1 | -5.1324 | 10 | 0 | 0
545.4 | 50.04 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.32 | -1 | -1 | -10 | -5.0735 | -5.0735 | 0 | 12 | 1 | 1 | -5.0735 | 10 | 0 | 0
545.45 | 50.01 | 50.01 | 0 | 0 | 0 | 50.29 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
545.5 | 49.99 | 49.99 | 0 | 0 | 0 | 50.27 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
545.55 | 49.96 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.24 | -1 | -1 | -10 | -4.9265 | -4.9265 | 0 | 12 | 1 | 1 | -4.9265 | 10 | 0 | 0
545.6 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.22 | -1 | -1 | -10 | -4.8676 | -4.8676 | 0 | 12 | 1 | 1 | -4.8676 | 10 | 0 | 0
545.65 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.19 | -0.905 | -0.905 | -9.05 | -4.3044 | -4.3044 | 0 | 12 | 1 | 1 | -4.3044 | 10 | 0 | 0
545.7 | 49.88 | 49.88 | 0.24 | 0.24 | 2.4 | 50.17 | -0.715 | -0.805 | -8.05 | -2.825 | -2.825 | 0 | 12 | 1 | 1 | -2.825 | 10 | 0 | 0
545.75 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.14 | -0.43 | -0.705 | -7.05 | -1.375 | -1.375 | 0 | 12 | 1 | 1 | -1.375 | 10 | 0 | 0
545.8 | 49.83 | 49.83 | 0.715 | 0.715 | 7.15 | 50.12 | -0.24 | -0.605 | -6.05 | 0.55 | 0.55 | 0 | 12 | 1 | 1 | 0.55 | 10 | 0 | 0
545.85 | 49.81 | 49.81 | 0.905 | 0.905 | 9.05 | 50.09 | -0.044118 | -0.505 | -5.05 | 2 | 2 | 0 | 12 | 1 | 1 | 2 | 10 | 0 | 0
545.9 | 49.78 | 49.78 | 1 | 1 | 10 | 50.06 | -0.026471 | -0.405 | -4.05 | 2.975 | 2.975 | 0 | 12 | 1 | 1 | 2.975 | 10 | 0 | 0
545.95 | 49.76 | 49.76 | 1 | 1 | 10 | 50.04 | -0.014706 | -0.305 | -3.05 | 3.475 | 3.475 | 0 | 12 | 1 | 1 | 3.475 | 10 | 0 | 0
546 | 49.73 | 49.73 | 1 | 1 | 10 | 50.01 | 0 | -0.205 | -2.05 | 3.975 | 3.975 | 0 | 12 | 1 | 1 | 3.975 | 10 | 0 | 0
546.05 | 49.71 | 49.71 | 1 | 1 | 10 | 49.99 | 0 | -0.105 | -1.05 | 4.475 | 4.475 | 0 | 12 | 1 | 1 | 4.475 | 10 | 0 | 0
546.1 | 49.68 | 49.68 | 1 | 1 | 10 | 49.96 | 0.014706 | -0.005 | -0.05 | 4.975 | 4.975 | 0 | 12 | 1 | 1 | 4.975 | 10 | 0 | 0
546.15 | 49.65 | 49.65 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
546.2 | 49.63 | 49.63 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
546.25 | 49.6 | 49.6 | 1 | 1 | 10 | 49.88 | 0.24 | 0.14412 | 1.4412 | 5.7206 | 5.7206 | 0 | 12 | 1 | 1 | 5.7206 | 10 | 0 | 0
546.3 | 49.58 | 49.58 | 1 | 1 | 10 | 49.86 | 0.43 | 0.24412 | 2.4412 | 6.2206 | 6.2206 | 0 | 12 | 1 | 1 | 6.2206 | 10 | 0 | 0
546.35 | 49.55 | 49.55 | 1 | 1 | 10 | 49.83 | 0.715 | 0.34412 | 3.4412 | 6.7206 | 6.7206 | 0 | 12 | 1 | 1 | 6.7206 | 10 | 0 | 0
546.4 | 49.53 | 49.53 | 1 | 1 | 10 | 49.81 | 0.905 | 0.44412 | 4.4412 | 7.2206 | 7.2206 | 0 | 12 | 1 | 1 | 7.2206 | 10 | 0 | 0
546.45 | 49.5 | 49.5 | 1 | 1 | 10 | 49.78 | 1 | 0.54412 | 5.4412 | 7.7206 | 7.7206 | 0 | 12 | 1 | 1 | 7.7206 | 10 | 0 | 0
546.5 | 49.5 | 49.5 | 1 | 1 | 10 | 49.76 | 1 | 0.64412 | 6.4412 | 8.2206 | 8.2206 | 0 | 12 | 1 | 1 | 8.2206 | 10 | 0 | 0
546.55 | 49.53 | 49.5 | 1 | 1 | 10 | 49.73 | 1 | 0.74412 | 7.4412 | 8.7206 | 8.7206 | 0 | 12 | 1 | 1 | 8.7206 | 10 | 0 | 0
546.6 | 49.55 | 49.5 | 1 | 1 | 10 | 49.71 | 1 | 0.84412 | 8.4412 | 9.2206 | 9.2206 | 0 | 12 | 1 | 1 | 9.2206 | 10 | 0 | 0
546.65 | 49.58 | 49.5 | 1 | 1 | 10 | 49.68 | 1 | 0.94412 | 9.4412 | 9.7206 | 9.7206 | 0 | 12 | 1 | 1 | 9.7206 | 10 | 0 | 0
546.7 | 49.6 | 49.5 | 1 | 1 | 10 | 49.65 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
546.75 | 49.63 | 49.5 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
546.8 | 49.65 | 49.5 | 1 | 1 | 10 | 49.65 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
546.85 | 49.68 | 49.5 | 1 | 1 | 10 | 49.68 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
546.9 | 49.71 | 49.5 | 1 | 1 | 10 | 49.71 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
546.95 | 49.73 | 49.5 | 1 | 1 | 10 | 49.73 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
547 | 49.76 | 49.5 | 1 | 1 | 10 | 49.76 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
547.05 | 49.78 | 49.5 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
547.1 | 49.81 | 49.53 | 1 | 1 | 10 | 49.81 | 0.905 | 0.905 | 9.05 | 9.525 | 9.525 | 0 | 12 | 1 | 1 | 9.525 | 10 | 0 | 0
547.15 | 49.83 | 49.55 | 1 | 1 | 10 | 49.83 | 0.715 | 0.715 | 7.15 | 8.575 | 8.575 | 0 | 12 | 1 | 1 | 8.575 | 10 | 0 | 0
547.2 | 49.86 | 49.58 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
547.25 | 49.88 | 49.6 | 1 | 1 | 10 | 49.88 | 0.24 | 0.24 | 2.4 | 6.2 | 6.2 | 0 | 12 | 1 | 1 | 6.2 | 10 | 0 | 0
547.3 | 49.91 | 49.63 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
547.35 | 49.94 | 49.65 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
547.4 | 49.96 | 49.68 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
547.45 | 49.99 | 49.71 | 1 | 1 | 10 | 49.99 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
547.5 | 50.01 | 49.73 | 1 | 1 | 10 | 50.01 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
547.55 | 50.04 | 49.76 | 1 | 1 | 10 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 4.9265 | 4.9265 | 0 | 12 | 1 | 1 | 4.9265 | 10 | 0 | 0
547.6 | 50.06 | 49.78 | 1 | 1 | 10 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 4.8676 | 4.8676 | 0 | 12 | 1 | 1 | 4.8676 | 10 | 0 | 0
547.65 | 50.09 | 49.81 | 0.905 | 0.905 | 9.05 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 4.3044 | 4.3044 | 0 | 12 | 1 | 1 | 4.3044 | 10 | 0 | 0
547.7 | 50.12 | 49.83 | 0.715 | 0.805 | 8.05 | 50.12 | -0.24 | -0.24 | -2.4 | 2.825 | 2.825 | 0 | 12 | 1 | 1 | 2.825 | 10 | 0 | 0
547.75 | 50.14 | 49.86 | 0.43 | 0.705 | 7.05 | 50.14 | -0.43 | -0.43 | -4.3 | 1.375 | 1.375 | 0 | 12 | 1 | 1 | 1.375 | 10 | 0 | 0
547.8 | 50.17 | 49.88 | 0.24 | 0.605 | 6.05 | 50.17 | -0.715 | -0.715 | -7.15 | -0.55 | -0.55 | 0 | 12 | 1 | 1 | -0.55 | 10 | 0 | 0
547.85 | 50.19 | 49.91 | 0.044118 | 0.505 | 5.05 | 50.19 | -0.905 | -0.905 | -9.05 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
547.9 | 50.22 | 49.94 | 0.026471 | 0.405 | 4.05 | 50.22 | -1 | -1 | -10 | -2.975 | -2.975 | 0 | 12 | 1 | 1 | -2.975 | 10 | 0 | 0
547.95 | 50.24 | 49.96 | 0.014706 | 0.305 | 3.05 | 50.24 | -1 | -1 | -10 | -3.475 | -3.475 | 0 | 12 | 1 | 1 | -3.475 | 10 | 0 | 0
548 | 50.27 | 49.99 | 0 | 0.205 | 2.05 | 50.27 | -1 | -1 | -10 | -3.975 | -3.975 | 0 | 12 | 1 | 1 | -3.975 | 10 | 0 | 0
548.05 | 50.29 | 50.01 | 0 | 0.105 | 1.05 | 50.29 | -1 | -1 | -10 | -4.475 | -4.475 | 0 | 12 | 1 | 1 | -4.475 | 10 | 0 | 0
548.1 | 50.32 | 50.04 | -0.014706 | 0.005 | 0.05 | 50.32 | -1 | -1 | -10 | -4.975 | -4.975 | 0 | 12 | 1 | 1 | -4.975 | 10 | 0 | 0
548.15 | 50.35 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.35 | -1 | -1 | -10 | -5.1324 | -5.1324 | 0 | 12 | 1 | 1 | -5.1324 | 10 | 0 | 0
548.2 | 50.37 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 50.37 | -1 | -1 | -10 | -5.2206 | -5.2206 | 0 | 12 | 1 | 1 | -5.2206 | 10 | 0 | 0
548.25 | 50.4 | 50.12 | -0.24 | -0.14412 | -1.4412 | 50.4 | -1 | -1 | -10 | -5.7206 | -5.7206 | 0 | 12 | 1 | 1 | -5.7206 | 10 | 0 | 0
548.3 | 50.42 | 50.14 | -0.43 | -0.24412 | -2.4412 | 50.42 | -1 | -1 | -10 | -6.2206 | -6.2206 | 0 | 12 | 1 | 1 | -6.2206 | 10 | 0 | 0
548.35 | 50.45 | 50.17 | -0.715 | -0.34412 | -3.4412 | 50.45 | -1 | -1 | -10 | -6.7206 | -6.7206 | 0 | 12 | 1 | 1 | -6.7206 | 10 | 0 | 0
548.4 | 50.47 | 50.19 | -0.905 | -0.44412 | -4.4412 | 50.47 | -1 | -1 | -10 | -7.2206 | -7.2206 | 0 | 12 | 1 | 1 | -7.2206 | 10 | 0 | 0
548.45 | 50.5 | 50.22 | -1 | -0.54412 | -5.4412 | 50.5 | -1 | -1 | -10 | -7.7206 | -7.7206 | 0 | 12 | 1 | 1 | -7.7206 | 10 | 0 | 0
548.5 | 50.5 | 50.24 | -1 | -0.64412 | -6.4412 | 50.5 | -1 | -1 | -10 | -8.2206 | -8.2206 | 0 | 12 | 1 | 1 | -8.2206 | 10 | 0 | 0
548.55 | 50.47 | 50.27 | -1 | -0.74412 | -7.4412 | 50.5 | -1 | -1 | -10 | -8.7206 | -8.7206 | 0 | 12 | 1 | 1 | -8.7206 | 10 | 0 | 0
548.6 | 50.45 | 50.29 | -1 | -0.84412 | -8.4412 | 50.5 | -1 | -1 | -10 | -9.2206 | -9.2206 | 0 | 12 | 1 | 1 | -9.2206 | 10 | 0 | 0
548.65 | 50.42 | 50.32 | -1 | -0.94412 | -9.4412 | 50.5 | -1 | -1 | -10 | -9.7206 | -9.7206 | 0 | 12 | 1 | 1 | -9.7206 | 10 | 0 | 0
548.7 | 50.39 | 50.35 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
548.75 | 50.37 | 50.37 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
548.8 | 50.34 | 50.34 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
548.85 | 50.32 | 50.32 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
548.9 | 50.29 | 50.29 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
548.95 | 50.26 | 50.26 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
549 | 50.24 | 50.24 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
549.05 | 50.21 | 50.21 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
549.1 | 50.18 | 50.18 | -0.81 | -0.81 | -8.1 | 50.47 | -1 | -1 | -10 | -9.05 | -9.05 | 0 | 12 | 1 | 1 | -9.05 | 10 | 0 | 0
549.15 | 50.16 | 50.16 | -0.62 | -0.62 | -6.2 | 50.45 | -1 | -1 | -10 | -8.1 | -8.1 | 0 | 12 | 1 | 1 | -8.1 | 10 | 0 | 0
549.2 | 50.13 | 50.13 | -0.335 | -0.335 | -3.35 | 50.42 | -1 | -1 | -10 | -6.675 | -6.675 | 0 | 12 | 1 | 1 | -6.675 | 10 | 0 | 0
549.25 | 50.11 | 50.11 | -0.145 | -0.145 | -1.45 | 50.39 | -1 | -1 | -10 | -5.725 | -5.725 | 0 | 12 | 1 | 1 | -5.725 | 10 | 0 | 0
549.3 | 50.08 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 50.37 | -1 | -1 | -10 | -5.1912 | -5.1912 | 0 | 12 | 1 | 1 | -5.1912 | 10 | 0 | 0
549.35 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.34 | -1 | -1 | -10 | -5.1029 | -5.1029 | 0 | 12 | 1 | 1 | -5.1029 | 10 | 0 | 0
549.4 | 50.03 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 50.32 | -1 | -1 | -10 | -5.0441 | -5.0441 | 0 | 12 | 1 | 1 | -5.0441 | 10 | 0 | 0
549.45 | 50 | 50 | 0 | 0 | 0 | 50.29 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
549.5 | 50 | 50 | 0 | 0 | 0 | 50.26 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
549.55 | 50 | 50 | 0 | 0 | 0 | 50.24 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
549.6 | 50 | 50 | 0 | 0 | 0 | 50.21 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
549.65 | 50 | 50 | 0 | 0 | 0 | 50.18 | -0.81 | -0.9 | -9 | -4.5 | -4.5 | 0 | 12 | 1 | 1 | -4.5 | 10 | 0 | 0
549.7 | 50 | 50 | 0 | 0 | 0 | 50.16 | -0.62 | -0.8 | -8 | -4 | -4 | 0 | 12 | 1 | 1 | -4 | 10 | 0 | 0
549.75 | 50 | 50 | 0 | 0 | 0 | 50.13 | -0.335 | -0.7 | -7 | -3.5 | -3.5 | 0 | 12 | 1 | 1 | -3.5 | 10 | 0 | 0
549.8 | 50.01 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.6 | -6 | -3 | -3 | 0 | 12 | 1 | 1 | -3 | 10 | 0 | 0
549.85 | 50.01 | 50 | 0 | 0 | 0 | 50.08 | -0.038235 | -0.5 | -5 | -2.5 | -2.5 | 0 | 12 | 1 | 1 | -2.5 | 10 | 0 | 0
549.9 | 49.99 | 49.99 | 0 | 0 | 0 | 50.05 | -0.020588 | -0.4 | -4 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
549.95 | 49.99 | 49.99 | 0 | 0 | 0 | 50.03 | -0.0088235 | -0.3 | -3 | -1.5 | -1.5 | 0 | 12 | 1 | 1 | -1.5 | 10 | 0 | 0
550 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | -0.2 | -2 | -0.83824 | -0.83824 | 0 | 12 | 1 | 1 | -0.83824 | 10 | 0 | 0
550.05 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | -0.1 | -1 | -0.33824 | -0.33824 | 0 | 12 | 1 | 1 | -0.33824 | 10 | 0 | 0
550.1 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
550.15 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
550.2 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
550.25 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
550.3 | 49.89 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
550.35 | 49.89 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
550.4 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50.01 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
550.45 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
550.5 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
550.55 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 2.7868 | 2.7868 | 0 | 12 | 1 | 1 | 2.7868 | 10 | 0 | 0
550.6 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 2.7868 | 2.7868 | 0 | 12 | 1 | 1 | 2.7868 | 10 | 0 | 0
550.65 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 2.8456 | 2.8456 | 0 | 12 | 1 | 1 | 2.8456 | 10 | 0 | 0
550.7 | 49.94 | 49.85 | 0.525 | 0.525 | 5.25 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 2.7574 | 2.7574 | 0 | 12 | 1 | 1 | 2.7574 | 10 | 0 | 0
550.75 | 49.94 | 49.85 | 0.525 | 0.525 | 5.25 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 2.7574 | 2.7574 | 0 | 12 | 1 | 1 | 2.7574 | 10 | 0 | 0
550.8 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
550.85 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
550.9 | 49.93 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
550.95 | 49.93 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
551 | 49.96 | 49.85 | 0.525 | 0.525 | 5.25 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 2.6985 | 2.6985 | 0 | 12 | 1 | 1 | 2.6985 | 10 | 0 | 0
551.05 | 49.96 | 49.85 | 0.525 | 0.525 | 5.25 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 2.6985 | 2.6985 | 0 | 12 | 1 | 1 | 2.6985 | 10 | 0 | 0
551.1 | 49.99 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
551.15 | 49.99 | 49.91 | 0.044118 | 0.425 | 4.25 | 49.99 | 0 | 0 | 0 | 2.125 | 2.125 | 0 | 12 | 1 | 1 | 2.125 | 10 | 0 | 0
551.2 | 49.99 | 49.91 | 0.044118 | 0.325 | 3.25 | 49.99 | 0 | 0 | 0 | 1.625 | 1.625 | 0 | 12 | 1 | 1 | 1.625 | 10 | 0 | 0
551.25 | 49.99 | 49.93 | 0.032353 | 0.225 | 2.25 | 49.99 | 0 | 0 | 0 | 1.125 | 1.125 | 0 | 12 | 1 | 1 | 1.125 | 10 | 0 | 0
551.3 | 49.96 | 49.93 | 0.032353 | 0.125 | 1.25 | 49.99 | 0 | 0 | 0 | 0.625 | 0.625 | 0 | 12 | 1 | 1 | 0.625 | 10 | 0 | 0
551.35 | 49.96 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 49.99 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
551.4 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
551.45 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
551.5 | 50.05 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.058824 | 0.058824 | 0 | 12 | 1 | 1 | 0.058824 | 10 | 0 | 0
551.55 | 50.05 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
551.6 | 49.97 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
551.65 | 49.97 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
551.7 | 49.92 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
551.75 | 49.92 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
551.8 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
551.85 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
551.9 | 49.94 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
551.95 | 49.94 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
552 | 50.01 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
552.05 | 50.01 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
552.1 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
552.15 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
552.2 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
552.25 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
552.3 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
552.35 | 49.95 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
552.4 | 49.97 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
552.45 | 49.97 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
552.5 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
552.55 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
552.6 | 49.87 | 49.87 | 0.335 | 0.335 | 3.35 | 50.01 | 0 | 0 | 0 | 1.675 | 1.675 | 0 | 12 | 1 | 1 | 1.675 | 10 | 0 | 0
552.65 | 49.87 | 49.87 | 0.335 | 0.335 | 3.35 | 49.99 | 0 | 0 | 0 | 1.675 | 1.675 | 0 | 12 | 1 | 1 | 1.675 | 10 | 0 | 0
552.7 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
552.75 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 2.6691 | 2.6691 | 0 | 12 | 1 | 1 | 2.6691 | 10 | 0 | 0
552.8 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
552.85 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
552.9 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
552.95 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
553 | 49.84 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
553.05 | 49.84 | 49.79 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
553.1 | 49.89 | 49.79 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
553.15 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.12647 | 1.2647 | 5.6324 | 5.6324 | 0 | 12 | 1 | 1 | 5.6324 | 10 | 0 | 0
553.2 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.145 | 1.45 | 5.725 | 5.725 | 0 | 12 | 1 | 1 | 5.725 | 10 | 0 | 0
553.25 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.145 | 1.45 | 5.725 | 5.725 | 0 | 12 | 1 | 1 | 5.725 | 10 | 0 | 0
553.3 | 49.96 | 49.79 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
553.35 | 49.96 | 49.79 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
553.4 | 50.02 | 49.79 | 1 | 1 | 10 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 4.9853 | 4.9853 | 0 | 12 | 1 | 1 | 4.9853 | 10 | 0 | 0
553.45 | 50.02 | 49.79 | 1 | 1 | 10 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 4.9853 | 4.9853 | 0 | 12 | 1 | 1 | 4.9853 | 10 | 0 | 0
553.5 | 50.03 | 49.79 | 1 | 1 | 10 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.9559 | 4.9559 | 0 | 12 | 1 | 1 | 4.9559 | 10 | 0 | 0
553.55 | 50.03 | 49.84 | 0.62 | 0.9 | 9 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.4559 | 4.4559 | 0 | 12 | 1 | 1 | 4.4559 | 10 | 0 | 0
553.6 | 50.02 | 49.84 | 0.62 | 0.8 | 8 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 3.9559 | 3.9559 | 0 | 12 | 1 | 1 | 3.9559 | 10 | 0 | 0
553.65 | 50.02 | 49.89 | 0.145 | 0.7 | 7 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 3.4559 | 3.4559 | 0 | 12 | 1 | 1 | 3.4559 | 10 | 0 | 0
553.7 | 50.08 | 49.89 | 0.145 | 0.6 | 6 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 2.8088 | 2.8088 | 0 | 12 | 1 | 1 | 2.8088 | 10 | 0 | 0
553.75 | 50.08 | 49.89 | 0.145 | 0.5 | 5 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 2.3088 | 2.3088 | 0 | 12 | 1 | 1 | 2.3088 | 10 | 0 | 0
553.8 | 50.01 | 49.89 | 0.145 | 0.4 | 4 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 1.8088 | 1.8088 | 0 | 12 | 1 | 1 | 1.8088 | 10 | 0 | 0
553.85 | 50.01 | 49.96 | 0.014706 | 0.3 | 3 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 1.3088 | 1.3088 | 0 | 12 | 1 | 1 | 1.3088 | 10 | 0 | 0
553.9 | 49.94 | 49.94 | 0.026471 | 0.2 | 2 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.80882 | 0.80882 | 0 | 12 | 1 | 1 | 0.80882 | 10 | 0 | 0
553.95 | 49.94 | 49.94 | 0.026471 | 0.1 | 1 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.30882 | 0.30882 | 0 | 12 | 1 | 1 | 0.30882 | 10 | 0 | 0
554 | 50 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
554.05 | 50 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
554.1 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
554.15 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
554.2 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
554.25 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
554.3 | 49.92 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
554.35 | 49.92 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
554.4 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50.01 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
554.45 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
554.5 | 49.92 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
554.55 | 49.92 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
554.6 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
554.65 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
554.7 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
554.75 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
554.8 | 49.87 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
554.85 | 49.87 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
554.9 | 49.8 | 49.8 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
554.95 | 49.8 | 49.8 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
555 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
555.05 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
555.1 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
555.15 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
555.2 | 49.72 | 49.72 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
555.25 | 49.72 | 49.72 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
555.3 | 49.67 | 49.67 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
555.35 | 49.67 | 49.67 | 1 | 1 | 10 | 49.87 | 0.335 | 0.14412 | 1.4412 | 5.7206 | 5.7206 | 0 | 12 | 1 | 1 | 5.7206 | 10 | 0 | 0
555.4 | 49.65 | 49.65 | 1 | 1 | 10 | 49.87 | 0.335 | 0.24412 | 2.4412 | 6.2206 | 6.2206 | 0 | 12 | 1 | 1 | 6.2206 | 10 | 0 | 0
555.45 | 49.65 | 49.65 | 1 | 1 | 10 | 49.8 | 1 | 0.34412 | 3.4412 | 6.7206 | 6.7206 | 0 | 12 | 1 | 1 | 6.7206 | 10 | 0 | 0
555.5 | 49.59 | 49.59 | 1 | 1 | 10 | 49.8 | 1 | 0.44412 | 4.4412 | 7.2206 | 7.2206 | 0 | 12 | 1 | 1 | 7.2206 | 10 | 0 | 0
555.55 | 49.59 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.54412 | 5.4412 | 7.7206 | 7.7206 | 0 | 12 | 1 | 1 | 7.7206 | 10 | 0 | 0
555.6 | 49.66 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.64412 | 6.4412 | 8.2206 | 8.2206 | 0 | 12 | 1 | 1 | 8.2206 | 10 | 0 | 0
555.65 | 49.66 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.74412 | 7.4412 | 8.7206 | 8.7206 | 0 | 12 | 1 | 1 | 8.7206 | 10 | 0 | 0
555.7 | 49.63 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.84412 | 8.4412 | 9.2206 | 9.2206 | 0 | 12 | 1 | 1 | 9.2206 | 10 | 0 | 0
555.75 | 49.63 | 49.59 | 1 | 1 | 10 | 49.72 | 1 | 0.94412 | 9.4412 | 9.7206 | 9.7206 | 0 | 12 | 1 | 1 | 9.7206 | 10 | 0 | 0
555.8 | 49.61 | 49.59 | 1 | 1 | 10 | 49.72 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
555.85 | 49.61 | 49.59 | 1 | 1 | 10 | 49.67 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
555.9 | 49.54 | 49.54 | 1 | 1 | 10 | 49.67 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
555.95 | 49.54 | 49.54 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
556 | 49.46 | 49.46 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
556.05 | 49.46 | 49.46 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
556.1 | 49.45 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
556.15 | 49.45 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
556.2 | 49.51 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
556.25 | 49.51 | 49.45 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
556.3 | 49.5 | 49.45 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
556.35 | 49.5 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
556.4 | 49.54 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
556.45 | 49.54 | 49.45 | 1 | 1 | 10 | 49.54 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
556.5 | 49.59 | 49.45 | 1 | 1 | 10 | 49.59 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
556.55 | 49.59 | 49.45 | 1 | 1 | 10 | 49.59 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
556.6 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
556.65 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
556.7 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
556.75 | 49.61 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
556.8 | 49.53 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
556.85 | 49.53 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
556.9 | 49.54 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
556.95 | 49.54 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
557 | 49.61 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
557.05 | 49.61 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
557.1 | 49.66 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
557.15 | 49.66 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
557.2 | 49.64 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
557.25 | 49.64 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
557.3 | 49.69 | 49.53 | 1 | 1 | 10 | 49.69 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
557.35 | 49.69 | 49.53 | 1 | 1 | 10 | 49.69 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
557.4 | 49.74 | 49.53 | 1 | 1 | 10 | 49.74 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
557.45 | 49.74 | 49.54 | 1 | 1 | 10 | 49.74 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
557.5 | 49.78 | 49.54 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
557.55 | 49.78 | 49.61 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
557.6 | 49.82 | 49.61 | 1 | 1 | 10 | 49.82 | 0.81 | 0.81 | 8.1 | 9.05 | 9.05 | 0 | 12 | 1 | 1 | 9.05 | 10 | 0 | 0
557.65 | 49.82 | 49.64 | 1 | 1 | 10 | 49.82 | 0.81 | 0.81 | 8.1 | 9.05 | 9.05 | 0 | 12 | 1 | 1 | 9.05 | 10 | 0 | 0
557.7 | 49.86 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
557.75 | 49.86 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
557.8 | 49.84 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
557.85 | 49.84 | 49.69 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
557.9 | 49.91 | 49.69 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
557.95 | 49.91 | 49.74 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
558 | 49.97 | 49.74 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
558.05 | 49.97 | 49.78 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
558.1 | 50.03 | 49.78 | 1 | 1 | 10 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.9559 | 4.9559 | 0 | 12 | 1 | 1 | 4.9559 | 10 | 0 | 0
558.15 | 50.03 | 49.82 | 0.81 | 0.9 | 9 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.4559 | 4.4559 | 0 | 12 | 1 | 1 | 4.4559 | 10 | 0 | 0
558.2 | 50.05 | 49.82 | 0.81 | 0.81 | 8.1 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 3.9471 | 3.9471 | 0 | 12 | 1 | 1 | 3.9471 | 10 | 0 | 0
558.25 | 50.05 | 49.84 | 0.62 | 0.71 | 7.1 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 3.4471 | 3.4471 | 0 | 12 | 1 | 1 | 3.4471 | 10 | 0 | 0
558.3 | 50.01 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
558.35 | 50.01 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
558.4 | 49.95 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
558.45 | 49.95 | 49.91 | 0.044118 | 0.52 | 5.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.4971 | 2.4971 | 0 | 12 | 1 | 1 | 2.4971 | 10 | 0 | 0
558.5 | 49.99 | 49.91 | 0.044118 | 0.42 | 4.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 1.9971 | 1.9971 | 0 | 12 | 1 | 1 | 1.9971 | 10 | 0 | 0
558.55 | 49.99 | 49.95 | 0.020588 | 0.32 | 3.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 1.4971 | 1.4971 | 0 | 12 | 1 | 1 | 1.4971 | 10 | 0 | 0
558.6 | 49.92 | 49.92 | 0.038235 | 0.22 | 2.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.99706 | 0.99706 | 0 | 12 | 1 | 1 | 0.99706 | 10 | 0 | 0
558.65 | 49.92 | 49.92 | 0.038235 | 0.12 | 1.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.49706 | 0.49706 | 0 | 12 | 1 | 1 | 0.49706 | 10 | 0 | 0
558.7 | 49.97 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
558.75 | 49.97 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
558.8 | 50.02 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
558.85 | 50.02 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.17647 | 0.17647 | 0 | 12 | 1 | 1 | 0.17647 | 10 | 0 | 0
558.9 | 50.07 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
558.95 | 50.07 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
559 | 50.06 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
559.05 | 50.06 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
559.1 | 50.13 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
559.15 | 50.13 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
559.2 | 50.09 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
559.25 | 50.09 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6309 | -1.6309 | 0 | 12 | 1 | 1 | -1.6309 | 10 | 0 | 0
559.3 | 50.07 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6309 | -1.6309 | 0 | 12 | 1 | 1 | -1.6309 | 10 | 0 | 0
559.35 | 50.07 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6897 | -1.6897 | 0 | 12 | 1 | 1 | -1.6897 | 10 | 0 | 0
559.4 | 50.07 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6897 | -1.6897 | 0 | 12 | 1 | 1 | -1.6897 | 10 | 0 | 0
559.45 | 50.07 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.13 | -0.335 | -0.335 | -3.35 | -1.8074 | -1.8074 | 0 | 12 | 1 | 1 | -1.8074 | 10 | 0 | 0
559.5 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.13 | -0.335 | -0.335 | -3.35 | -1.7779 | -1.7779 | 0 | 12 | 1 | 1 | -1.7779 | 10 | 0 | 0
559.55 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.13 | -0.335 | -0.335 | -3.35 | -1.7779 | -1.7779 | 0 | 12 | 1 | 1 | -1.7779 | 10 | 0 | 0
559.6 | 50.01 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
559.65 | 50.01 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
559.7 | 50.07 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
559.75 | 50.07 | 50.01 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.235 | -2.35 | -1.175 | -1.175 | 0 | 12 | 1 | 1 | -1.175 | 10 | 0 | 0
559.8 | 50.05 | 50.01 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.135 | -1.35 | -0.675 | -0.675 | 0 | 12 | 1 | 1 | -0.675 | 10 | 0 | 0
559.85 | 50.05 | 50.01 | 0 | 0 | 0 | 50.07 | -0.032353 | -0.035 | -0.35 | -0.175 | -0.175 | 0 | 12 | 1 | 1 | -0.175 | 10 | 0 | 0
559.9 | 50.1 | 50.01 | 0 | 0 | 0 | 50.1 | -0.05 | -0.05 | -0.5 | -0.25 | -0.25 | 0 | 12 | 1 | 1 | -0.25 | 10 | 0 | 0
559.95 | 50.1 | 50.01 | 0 | 0 | 0 | 50.1 | -0.05 | -0.05 | -0.5 | -0.25 | -0.25 | 0 | 12 | 1 | 1 | -0.25 | 10 | 0 | 0
560 | 50.11 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
560.05 | 50.11 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
560.1 | 50.06 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
560.15 | 50.06 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
560.2 | 50.04 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
560.25 | 50.04 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
560.3 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
560.35 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
560.4 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
560.45 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
560.5 | 50.11 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
560.55 | 50.11 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
560.6 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
560.65 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
560.7 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
560.75 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
560.8 | 50.02 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.11 | -0.145 | -0.145 | -1.45 | -0.73971 | -0.73971 | 0 | 12 | 1 | 1 | -0.73971 | 10 | 0 | 0
560.85 | 50.02 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.11 | -0.145 | -0.145 | -1.45 | -0.73971 | -0.73971 | 0 | 12 | 1 | 1 | -0.73971 | 10 | 0 | 0
560.9 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
560.95 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
561 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
561.05 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
561.1 | 50.01 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
561.15 | 50.01 | 50 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.045 | -0.45 | -0.225 | -0.225 | 0 | 12 | 1 | 1 | -0.225 | 10 | 0 | 0
561.2 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
561.25 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
561.3 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
561.35 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
561.4 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.14706 | 0.14706 | 0 | 12 | 1 | 1 | 0.14706 | 10 | 0 | 0
561.45 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
561.5 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
561.55 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
561.6 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
561.65 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
561.7 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
561.75 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
561.8 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
561.85 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
561.9 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
561.95 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
562 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
562.05 | 50 | 50 | 0 | 0 | 0 | 50.01 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
562.1 | 49.5 | 49.5 | 1 | 1 | 10 | 50.01 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
562.15 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
562.2 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
562.25 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
562.3 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
562.35 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
562.4 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
562.45 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
562.5 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
562.55 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
562.6 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
562.65 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.1 | 1 | 5.5 | 5.5 | 0 | 12 | 1 | 1 | 5.5 | 10 | 0 | 0
562.7 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.2 | 2 | 6 | 6 | 0 | 12 | 1 | 1 | 6 | 10 | 0 | 0
562.75 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.3 | 3 | 6.5 | 6.5 | 0 | 12 | 1 | 1 | 6.5 | 10 | 0 | 0
562.8 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.4 | 4 | 7 | 7 | 0 | 12 | 1 | 1 | 7 | 10 | 0 | 0
562.85 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.5 | 5 | 7.5 | 7.5 | 0 | 12 | 1 | 1 | 7.5 | 10 | 0 | 0
562.9 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.6 | 6 | 8 | 8 | 0 | 12 | 1 | 1 | 8 | 10 | 0 | 0
562.95 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.7 | 7 | 8.5 | 8.5 | 0 | 12 | 1 | 1 | 8.5 | 10 | 0 | 0
563 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.8 | 8 | 9 | 9 | 0 | 12 | 1 | 1 | 9 | 10 | 0 | 0
563.05 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.9 | 9 | 9.5 | 9.5 | 0 | 12 | 1 | 1 | 9.5 | 10 | 0 | 0
563.1 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
563.15 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
563.2 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
563.25 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
563.3 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
563.35 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
563.4 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
563.45 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
563.5 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
563.55 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
563.6 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
563.65 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
563.7 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
563.75 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
563.8 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
563.85 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
563.9 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
563.95 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
564 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
564.05 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
564.1 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
564.15 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
564.2 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
564.25 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
564.3 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
564.35 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
564.4 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
564.45 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
564.5 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
564.55 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
564.6 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
564.65 | 50.5 | 50.5 | -1 | 0.9 | 9 | 50.5 | -1 | -1 | -10 | -0.5 | -0.5 | 0 | 12 | 1 | 1 | -0.5 | 10 | 0 | 0
564.7 | 50.5 | 50.5 | -1 | 0.8 | 8 | 50.5 | -1 | -1 | -10 | -1 | -1 | 0 | 12 | 1 | 1 | -1 | 10 | 0 | 0
564.75 | 50.5 | 50.5 | -1 | 0.7 | 7 | 50.5 | -1 | -1 | -10 | -1.5 | -1.5 | 0 | 12 | 1 | 1 | -1.5 | 10 | 0 | 0
564.8 | 50.5 | 50.5 | -1 | 0.6 | 6 | 50.5 | -1 | -1 | -10 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
564.85 | 50.5 | 50.5 | -1 | 0.5 | 5 | 50.5 | -1 | -1 | -10 | -2.5 | -2.5 | 0 | 12 | 1 | 1 | -2.5 | 10 | 0 | 0
564.9 | 50.5 | 50.5 | -1 | 0.4 | 4 | 50.5 | -1 | -1 | -10 | -3 | -3 | 0 | 12 | 1 | 1 | -3 | 10 | 0 | 0
564.95 | 50.5 | 50.5 | -1 | 0.3 | 3 | 50.5 | -1 | -1 | -10 | -3.5 | -3.5 | 0 | 12 | 1 | 1 | -3.5 | 10 | 0 | 0
565 | 50.5 | 50.5 | -1 | 0.2 | 2 | 50.5 | -1 | -1 | -10 | -4 | -4 | 0 | 12 | 1 | 1 | -4 | 10 | 0 | 0
565.05 | 50.5 | 50.5 | -1 | 0.1 | 1 | 50.5 | -1 | -1 | -10 | -4.5 | -4.5 | 0 | 12 | 1 | 1 | -4.5 | 10 | 0 | 0
565.1 | 50.5 | 50.5 | -1 | 0 | 0 | 50.5 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
565.15 | 50.5 | 50.5 | -1 | -0.1 | -1 | 50.5 | -1 | -1 | -10 | -5.5 | -5.5 | 0 | 12 | 1 | 1 | -5.5 | 10 | 0 | 0
565.2 | 50.5 | 50.5 | -1 | -0.2 | -2 | 50.5 | -1 | -1 | -10 | -6 | -6 | 0 | 12 | 1 | 1 | -6 | 10 | 0 | 0
565.25 | 50.5 | 50.5 | -1 | -0.3 | -3 | 50.5 | -1 | -1 | -10 | -6.5 | -6.5 | 0 | 12 | 1 | 1 | -6.5 | 10 | 0 | 0
565.3 | 50.5 | 50.5 | -1 | -0.4 | -4 | 50.5 | -1 | -1 | -10 | -7 | -7 | 0 | 12 | 1 | 1 | -7 | 10 | 0 | 0
565.35 | 50.5 | 50.5 | -1 | -0.5 | -5 | 50.5 | -1 | -1 | -10 | -7.5 | -7.5 | 0 | 12 | 1 | 1 | -7.5 | 10 | 0 | 0
565.4 | 50.5 | 50.5 | -1 | -0.6 | -6 | 50.5 | -1 | -1 | -10 | -8 | -8 | 0 | 12 | 1 | 1 | -8 | 10 | 0 | 0
565.45 | 50.5 | 50.5 | -1 | -0.7 | -7 | 50.5 | -1 | -1 | -10 | -8.5 | -8.5 | 0 | 12 | 1 | 1 | -8.5 | 10 | 0 | 0
565.5 | 50.5 | 50.5 | -1 | -0.8 | -8 | 50.5 | -1 | -1 | -10 | -9 | -9 | 0 | 12 | 1 | 1 | -9 | 10 | 0 | 0
565.55 | 50.5 | 50.5 | -1 | -0.9 | -9 | 50.5 | -1 | -1 | -10 | -9.5 | -9.5 | 0 | 12 | 1 | 1 | -9.5 | 10 | 0 | 0
565.6 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
565.65 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
565.7 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
565.75 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
565.8 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
565.85 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
565.9 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
565.95 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
566 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
566.05 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
566.1 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
566.15 | 50.47 | 50.47 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
566.2 | 50.45 | 50.45 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
566.25 | 50.42 | 50.42 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
566.3 | 50.4 | 50.4 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
566.35 | 50.37 | 50.37 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
566.4 | 50.35 | 50.35 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
566.45 | 50.32 | 50.32 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
566.5 | 50.29 | 50.29 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
566.55 | 50.27 | 50.27 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
566.6 | 50.24 | 50.24 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
566.65 | 50.22 | 50.22 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
566.7 | 50.19 | 50.19 | -0.905 | -0.905 | -9.05 | 50.47 | -1 | -1 | -10 | -9.525 | -9.525 | 0 | 12 | 1 | 1 | -9.525 | 10 | 0 | 0
566.75 | 50.17 | 50.17 | -0.715 | -0.715 | -7.15 | 50.45 | -1 | -1 | -10 | -8.575 | -8.575 | 0 | 12 | 1 | 1 | -8.575 | 10 | 0 | 0
566.8 | 50.14 | 50.14 | -0.43 | -0.43 | -4.3 | 50.42 | -1 | -1 | -10 | -7.15 | -7.15 | 0 | 12 | 1 | 1 | -7.15 | 10 | 0 | 0
566.85 | 50.12 | 50.12 | -0.24 | -0.24 | -2.4 | 50.4 | -1 | -1 | -10 | -6.2 | -6.2 | 0 | 12 | 1 | 1 | -6.2 | 10 | 0 | 0
566.9 | 50.09 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 50.37 | -1 | -1 | -10 | -5.2206 | -5.2206 | 0 | 12 | 1 | 1 | -5.2206 | 10 | 0 | 0
566.95 | 50.06 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.35 | -1 | -1 | -10 | -5.1324 | -5.1324 | 0 | 12 | 1 | 1 | -5.1324 | 10 | 0 | 0
567 | 50.04 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.32 | -1 | -1 | -10 | -5.0735 | -5.0735 | 0 | 12 | 1 | 1 | -5.0735 | 10 | 0 | 0
567.05 | 50.01 | 50.01 | 0 | 0 | 0 | 50.29 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
567.1 | 49.99 | 49.99 | 0 | 0 | 0 | 50.27 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
567.15 | 49.96 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.24 | -1 | -1 | -10 | -4.9265 | -4.9265 | 0 | 12 | 1 | 1 | -4.9265 | 10 | 0 | 0
567.2 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.22 | -1 | -1 | -10 | -4.8676 | -4.8676 | 0 | 12 | 1 | 1 | -4.8676 | 10 | 0 | 0
567.25 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.19 | -0.905 | -0.905 | -9.05 | -4.3044 | -4.3044 | 0 | 12 | 1 | 1 | -4.3044 | 10 | 0 | 0
567.3 | 49.88 | 49.88 | 0.24 | 0.24 | 2.4 | 50.17 | -0.715 | -0.805 | -8.05 | -2.825 | -2.825 | 0 | 12 | 1 | 1 | -2.825 | 10 | 0 | 0
567.35 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.14 | -0.43 | -0.705 | -7.05 | -1.375 | -1.375 | 0 | 12 | 1 | 1 | -1.375 | 10 | 0 | 0
567.4 | 49.83 | 49.83 | 0.715 | 0.715 | 7.15 | 50.12 | -0.24 | -0.605 | -6.05 | 0.55 | 0.55 | 0 | 12 | 1 | 1 | 0.55 | 10 | 0 | 0
567.45 | 49.81 | 49.81 | 0.905 | 0.905 | 9.05 | 50.09 | -0.044118 | -0.505 | -5.05 | 2 | 2 | 0 | 12 | 1 | 1 | 2 | 10 | 0 | 0
567.5 | 49.78 | 49.78 | 1 | 1 | 10 | 50.06 | -0.026471 | -0.405 | -4.05 | 2.975 | 2.975 | 0 | 12 | 1 | 1 | 2.975 | 10 | 0 | 0
567.55 | 49.76 | 49.76 | 1 | 1 | 10 | 50.04 | -0.014706 | -0.305 | -3.05 | 3.475 | 3.475 | 0 | 12 | 1 | 1 | 3.475 | 10 | 0 | 0
567.6 | 49.73 | 49.73 | 1 | 1 | 10 | 50.01 | 0 | -0.205 | -2.05 | 3.975 | 3.975 | 0 | 12 | 1 | 1 | 3.975 | 10 | 0 | 0
567.65 | 49.71 | 49.71 | 1 | 1 | 10 | 49.99 | 0 | -0.105 | -1.05 | 4.475 | 4.475 | 0 | 12 | 1 | 1 | 4.475 | 10 | 0 | 0
567.7 | 49.68 | 49.68 | 1 | 1 | 10 | 49.96 | 0.014706 | -0.005 | -0.05 | 4.975 | 4.975 | 0 | 12 | 1 | 1 | 4.975 | 10 | 0 | 0
567.75 | 49.65 | 49.65 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
567.8 | 49.63 | 49.63 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
567.85 | 49.6 | 49.6 | 1 | 1 | 10 | 49.88 | 0.24 | 0.14412 | 1.4412 | 5.7206 | 5.7206 | 0 | 12 | 1 | 1 | 5.7206 | 10 | 0 | 0
567.9 | 49.58 | 49.58 | 1 | 1 | 10 | 49.86 | 0.43 | 0.24412 | 2.4412 | 6.2206 | 6.2206 | 0 | 12 | 1 | 1 | 6.2206 | 10 | 0 | 0
567.95 | 49.55 | 49.55 | 1 | 1 | 10 | 49.83 | 0.715 | 0.34412 | 3.4412 | 6.7206 | 6.7206 | 0 | 12 | 1 | 1 | 6.7206 | 10 | 0 | 0
568 | 49.53 | 49.53 | 1 | 1 | 10 | 49.81 | 0.905 | 0.44412 | 4.4412 | 7.2206 | 7.2206 | 0 | 12 | 1 | 1 | 7.2206 | 10 | 0 | 0
568.05 | 49.5 | 49.5 | 1 | 1 | 10 | 49.78 | 1 | 0.54412 | 5.4412 | 7.7206 | 7.7206 | 0 | 12 | 1 | 1 | 7.7206 | 10 | 0 | 0
568.1 | 49.5 | 49.5 | 1 | 1 | 10 | 49.76 | 1 | 0.64412 | 6.4412 | 8.2206 | 8.2206 | 0 | 12 | 1 | 1 | 8.2206 | 10 | 0 | 0
568.15 | 49.53 | 49.5 | 1 | 1 | 10 | 49.73 | 1 | 0.74412 | 7.4412 | 8.7206 | 8.7206 | 0 | 12 | 1 | 1 | 8.7206 | 10 | 0 | 0
568.2 | 49.55 | 49.5 | 1 | 1 | 10 | 49.71 | 1 | 0.84412 | 8.4412 | 9.2206 | 9.2206 | 0 | 12 | 1 | 1 | 9.2206 | 10 | 0 | 0
568.25 | 49.58 | 49.5 | 1 | 1 | 10 | 49.68 | 1 | 0.94412 | 9.4412 | 9.7206 | 9.7206 | 0 | 12 | 1 | 1 | 9.7206 | 10 | 0 | 0
568.3 | 49.6 | 49.5 | 1 | 1 | 10 | 49.65 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
568.35 | 49.63 | 49.5 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
568.4 | 49.65 | 49.5 | 1 | 1 | 10 | 49.65 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
568.45 | 49.68 | 49.5 | 1 | 1 | 10 | 49.68 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
568.5 | 49.71 | 49.5 | 1 | 1 | 10 | 49.71 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
568.55 | 49.73 | 49.5 | 1 | 1 | 10 | 49.73 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
568.6 | 49.76 | 49.5 | 1 | 1 | 10 | 49.76 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
568.65 | 49.78 | 49.5 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
568.7 | 49.81 | 49.53 | 1 | 1 | 10 | 49.81 | 0.905 | 0.905 | 9.05 | 9.525 | 9.525 | 0 | 12 | 1 | 1 | 9.525 | 10 | 0 | 0
568.75 | 49.83 | 49.55 | 1 | 1 | 10 | 49.83 | 0.715 | 0.715 | 7.15 | 8.575 | 8.575 | 0 | 12 | 1 | 1 | 8.575 | 10 | 0 | 0
568.8 | 49.86 | 49.58 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
568.85 | 49.88 | 49.6 | 1 | 1 | 10 | 49.88 | 0.24 | 0.24 | 2.4 | 6.2 | 6.2 | 0 | 12 | 1 | 1 | 6.2 | 10 | 0 | 0
568.9 | 49.91 | 49.63 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
568.95 | 49.94 | 49.65 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
569 | 49.96 | 49.68 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
569.05 | 49.99 | 49.71 | 1 | 1 | 10 | 49.99 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
569.1 | 50.01 | 49.73 | 1 | 1 | 10 | 50.01 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
569.15 | 50.04 | 49.76 | 1 | 1 | 10 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 4.9265 | 4.9265 | 0 | 12 | 1 | 1 | 4.9265 | 10 | 0 | 0
569.2 | 50.06 | 49.78 | 1 | 1 | 10 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 4.8676 | 4.8676 | 0 | 12 | 1 | 1 | 4.8676 | 10 | 0 | 0
569.25 | 50.09 | 49.81 | 0.905 | 0.905 | 9.05 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 4.3044 | 4.3044 | 0 | 12 | 1 | 1 | 4.3044 | 10 | 0 | 0
569.3 | 50.12 | 49.83 | 0.715 | 0.805 | 8.05 | 50.12 | -0.24 | -0.24 | -2.4 | 2.825 | 2.825 | 0 | 12 | 1 | 1 | 2.825 | 10 | 0 | 0
569.35 | 50.14 | 49.86 | 0.43 | 0.705 | 7.05 | 50.14 | -0.43 | -0.43 | -4.3 | 1.375 | 1.375 | 0 | 12 | 1 | 1 | 1.375 | 10 | 0 | 0
569.4 | 50.17 | 49.88 | 0.24 | 0.605 | 6.05 | 50.17 | -0.715 | -0.715 | -7.15 | -0.55 | -0.55 | 0 | 12 | 1 | 1 | -0.55 | 10 | 0 | 0
569.45 | 50.19 | 49.91 | 0.044118 | 0.505 | 5.05 | 50.19 | -0.905 | -0.905 | -9.05 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
569.5 | 50.22 | 49.94 | 0.026471 | 0.405 | 4.05 | 50.22 | -1 | -1 | -10 | -2.975 | -2.975 | 0 | 12 | 1 | 1 | -2.975 | 10 | 0 | 0
569.55 | 50.24 | 49.96 | 0.014706 | 0.305 | 3.05 | 50.24 | -1 | -1 | -10 | -3.475 | -3.475 | 0 | 12 | 1 | 1 | -3.475 | 10 | 0 | 0
569.6 | 50.27 | 49.99 | 0 | 0.205 | 2.05 | 50.27 | -1 | -1 | -10 | -3.975 | -3.975 | 0 | 12 | 1 | 1 | -3.975 | 10 | 0 | 0
569.65 | 50.29 | 50.01 | 0 | 0.105 | 1.05 | 50.29 | -1 | -1 | -10 | -4.475 | -4.475 | 0 | 12 | 1 | 1 | -4.475 | 10 | 0 | 0
569.7 | 50.32 | 50.04 | -0.014706 | 0.005 | 0.05 | 50.32 | -1 | -1 | -10 | -4.975 | -4.975 | 0 | 12 | 1 | 1 | -4.975 | 10 | 0 | 0
569.75 | 50.35 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.35 | -1 | -1 | -10 | -5.1324 | -5.1324 | 0 | 12 | 1 | 1 | -5.1324 | 10 | 0 | 0
569.8 | 50.37 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 50.37 | -1 | -1 | -10 | -5.2206 | -5.2206 | 0 | 12 | 1 | 1 | -5.2206 | 10 | 0 | 0
569.85 | 50.4 | 50.12 | -0.24 | -0.14412 | -1.4412 | 50.4 | -1 | -1 | -10 | -5.7206 | -5.7206 | 0 | 12 | 1 | 1 | -5.7206 | 10 | 0 | 0
569.9 | 50.42 | 50.14 | -0.43 | -0.24412 | -2.4412 | 50.42 | -1 | -1 | -10 | -6.2206 | -6.2206 | 0 | 12 | 1 | 1 | -6.2206 | 10 | 0 | 0
569.95 | 50.45 | 50.17 | -0.715 | -0.34412 | -3.4412 | 50.45 | -1 | -1 | -10 | -6.7206 | -6.7206 | 0 | 12 | 1 | 1 | -6.7206 | 10 | 0 | 0
570 | 50.47 | 50.19 | -0.905 | -0.44412 | -4.4412 | 50.47 | -1 | -1 | -10 | -7.2206 | -7.2206 | 0 | 12 | 1 | 1 | -7.2206 | 10 | 0 | 0
570.05 | 50.5 | 50.22 | -1 | -0.54412 | -5.4412 | 50.5 | -1 | -1 | -10 | -7.7206 | -7.7206 | 0 | 12 | 1 | 1 | -7.7206 | 10 | 0 | 0
570.1 | 50.5 | 50.24 | -1 | -0.64412 | -6.4412 | 50.5 | -1 | -1 | -10 | -8.2206 | -8.2206 | 0 | 12 | 1 | 1 | -8.2206 | 10 | 0 | 0
570.15 | 50.47 | 50.27 | -1 | -0.74412 | -7.4412 | 50.5 | -1 | -1 | -10 | -8.7206 | -8.7206 | 0 | 12 | 1 | 1 | -8.7206 | 10 | 0 | 0
570.2 | 50.45 | 50.29 | -1 | -0.84412 | -8.4412 | 50.5 | -1 | -1 | -10 | -9.2206 | -9.2206 | 0 | 12 | 1 | 1 | -9.2206 | 10 | 0 | 0
570.25 | 50.42 | 50.32 | -1 | -0.94412 | -9.4412 | 50.5 | -1 | -1 | -10 | -9.7206 | -9.7206 | 0 | 12 | 1 | 1 | -9.7206 | 10 | 0 | 0
570.3 | 50.39 | 50.35 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
570.35 | 50.37 | 50.37 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
570.4 | 50.34 | 50.34 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
570.45 | 50.32 | 50.32 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
570.5 | 50.29 | 50.29 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
570.55 | 50.26 | 50.26 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
570.6 | 50.24 | 50.24 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
570.65 | 50.21 | 50.21 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
570.7 | 50.18 | 50.18 | -0.81 | -0.81 | -8.1 | 50.47 | -1 | -1 | -10 | -9.05 | -9.05 | 0 | 12 | 1 | 1 | -9.05 | 10 | 0 | 0
570.75 | 50.16 | 50.16 | -0.62 | -0.62 | -6.2 | 50.45 | -1 | -1 | -10 | -8.1 | -8.1 | 0 | 12 | 1 | 1 | -8.1 | 10 | 0 | 0
570.8 | 50.13 | 50.13 | -0.335 | -0.335 | -3.35 | 50.42 | -1 | -1 | -10 | -6.675 | -6.675 | 0 | 12 | 1 | 1 | -6.675 | 10 | 0 | 0
570.85 | 50.11 | 50.11 | -0.145 | -0.145 | -1.45 | 50.39 | -1 | -1 | -10 | -5.725 | -5.725 | 0 | 12 | 1 | 1 | -5.725 | 10 | 0 | 0
570.9 | 50.08 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 50.37 | -1 | -1 | -10 | -5.1912 | -5.1912 | 0 | 12 | 1 | 1 | -5.1912 | 10 | 0 | 0
570.95 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.34 | -1 | -1 | -10 | -5.1029 | -5.1029 | 0 | 12 | 1 | 1 | -5.1029 | 10 | 0 | 0
571 | 50.03 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 50.32 | -1 | -1 | -10 | -5.0441 | -5.0441 | 0 | 12 | 1 | 1 | -5.0441 | 10 | 0 | 0
571.05 | 50 | 50 | 0 | 0 | 0 | 50.29 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
571.1 | 50 | 50 | 0 | 0 | 0 | 50.26 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
571.15 | 50 | 50 | 0 | 0 | 0 | 50.24 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
571.2 | 50 | 50 | 0 | 0 | 0 | 50.21 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
571.25 | 50 | 50 | 0 | 0 | 0 | 50.18 | -0.81 | -0.9 | -9 | -4.5 | -4.5 | 0 | 12 | 1 | 1 | -4.5 | 10 | 0 | 0
571.3 | 50 | 50 | 0 | 0 | 0 | 50.16 | -0.62 | -0.8 | -8 | -4 | -4 | 0 | 12 | 1 | 1 | -4 | 10 | 0 | 0
571.35 | 50 | 50 | 0 | 0 | 0 | 50.13 | -0.335 | -0.7 | -7 | -3.5 | -3.5 | 0 | 12 | 1 | 1 | -3.5 | 10 | 0 | 0
571.4 | 50.01 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.6 | -6 | -3 | -3 | 0 | 12 | 1 | 1 | -3 | 10 | 0 | 0
571.45 | 50.01 | 50 | 0 | 0 | 0 | 50.08 | -0.038235 | -0.5 | -5 | -2.5 | -2.5 | 0 | 12 | 1 | 1 | -2.5 | 10 | 0 | 0
571.5 | 49.99 | 49.99 | 0 | 0 | 0 | 50.05 | -0.020588 | -0.4 | -4 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
571.55 | 49.99 | 49.99 | 0 | 0 | 0 | 50.03 | -0.0088235 | -0.3 | -3 | -1.5 | -1.5 | 0 | 12 | 1 | 1 | -1.5 | 10 | 0 | 0
571.6 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | -0.2 | -2 | -0.83824 | -0.83824 | 0 | 12 | 1 | 1 | -0.83824 | 10 | 0 | 0
571.65 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | -0.1 | -1 | -0.33824 | -0.33824 | 0 | 12 | 1 | 1 | -0.33824 | 10 | 0 | 0
571.7 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
571.75 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
571.8 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
571.85 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
571.9 | 49.89 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
571.95 | 49.89 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
572 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50.01 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
572.05 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
572.1 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
572.15 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 2.7868 | 2.7868 | 0 | 12 | 1 | 1 | 2.7868 | 10 | 0 | 0
572.2 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 2.7868 | 2.7868 | 0 | 12 | 1 | 1 | 2.7868 | 10 | 0 | 0
572.25 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 2.8456 | 2.8456 | 0 | 12 | 1 | 1 | 2.8456 | 10 | 0 | 0
572.3 | 49.94 | 49.85 | 0.525 | 0.525 | 5.25 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 2.7574 | 2.7574 | 0 | 12 | 1 | 1 | 2.7574 | 10 | 0 | 0
572.35 | 49.94 | 49.85 | 0.525 | 0.525 | 5.25 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 2.7574 | 2.7574 | 0 | 12 | 1 | 1 | 2.7574 | 10 | 0 | 0
572.4 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
572.45 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
572.5 | 49.93 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
572.55 | 49.93 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
572.6 | 49.96 | 49.85 | 0.525 | 0.525 | 5.25 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 2.6985 | 2.6985 | 0 | 12 | 1 | 1 | 2.6985 | 10 | 0 | 0
572.65 | 49.96 | 49.85 | 0.525 | 0.525 | 5.25 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 2.6985 | 2.6985 | 0 | 12 | 1 | 1 | 2.6985 | 10 | 0 | 0
572.7 | 49.99 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
572.75 | 49.99 | 49.91 | 0.044118 | 0.425 | 4.25 | 49.99 | 0 | 0 | 0 | 2.125 | 2.125 | 0 | 12 | 1 | 1 | 2.125 | 10 | 0 | 0
572.8 | 49.99 | 49.91 | 0.044118 | 0.325 | 3.25 | 49.99 | 0 | 0 | 0 | 1.625 | 1.625 | 0 | 12 | 1 | 1 | 1.625 | 10 | 0 | 0
572.85 | 49.99 | 49.93 | 0.032353 | 0.225 | 2.25 | 49.99 | 0 | 0 | 0 | 1.125 | 1.125 | 0 | 12 | 1 | 1 | 1.125 | 10 | 0 | 0
572.9 | 49.96 | 49.93 | 0.032353 | 0.125 | 1.25 | 49.99 | 0 | 0 | 0 | 0.625 | 0.625 | 0 | 12 | 1 | 1 | 0.625 | 10 | 0 | 0
572.95 | 49.96 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 49.99 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
573 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
573.05 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
573.1 | 50.05 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.058824 | 0.058824 | 0 | 12 | 1 | 1 | 0.058824 | 10 | 0 | 0
573.15 | 50.05 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
573.2 | 49.97 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
573.25 | 49.97 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
573.3 | 49.92 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
573.35 | 49.92 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
573.4 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
573.45 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
573.5 | 49.94 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
573.55 | 49.94 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
573.6 | 50.01 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
573.65 | 50.01 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
573.7 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
573.75 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
573.8 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
573.85 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
573.9 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
573.95 | 49.95 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
574 | 49.97 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
574.05 | 49.97 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
574.1 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
574.15 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
574.2 | 49.87 | 49.87 | 0.335 | 0.335 | 3.35 | 50.01 | 0 | 0 | 0 | 1.675 | 1.675 | 0 | 12 | 1 | 1 | 1.675 | 10 | 0 | 0
574.25 | 49.87 | 49.87 | 0.335 | 0.335 | 3.35 | 49.99 | 0 | 0 | 0 | 1.675 | 1.675 | 0 | 12 | 1 | 1 | 1.675 | 10 | 0 | 0
574.3 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
574.35 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 2.6691 | 2.6691 | 0 | 12 | 1 | 1 | 2.6691 | 10 | 0 | 0
574.4 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
574.45 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
574.5 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
574.55 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
574.6 | 49.84 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
574.65 | 49.84 | 49.79 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
574.7 | 49.89 | 49.79 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
574.75 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.12647 | 1.2647 | 5.6324 | 5.6324 | 0 | 12 | 1 | 1 | 5.6324 | 10 | 0 | 0
574.8 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.145 | 1.45 | 5.725 | 5.725 | 0 | 12 | 1 | 1 | 5.725 | 10 | 0 | 0
574.85 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.145 | 1.45 | 5.725 | 5.725 | 0 | 12 | 1 | 1 | 5.725 | 10 | 0 | 0
574.9 | 49.96 | 49.79 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
574.95 | 49.96 | 49.79 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
575 | 50.02 | 49.79 | 1 | 1 | 10 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 4.9853 | 4.9853 | 0 | 12 | 1 | 1 | 4.9853 | 10 | 0 | 0
575.05 | 50.02 | 49.79 | 1 | 1 | 10 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 4.9853 | 4.9853 | 0 | 12 | 1 | 1 | 4.9853 | 10 | 0 | 0
575.1 | 50.03 | 49.79 | 1 | 1 | 10 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.9559 | 4.9559 | 0 | 12 | 1 | 1 | 4.9559 | 10 | 0 | 0
575.15 | 50.03 | 49.84 | 0.62 | 0.9 | 9 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.4559 | 4.4559 | 0 | 12 | 1 | 1 | 4.4559 | 10 | 0 | 0
575.2 | 50.02 | 49.84 | 0.62 | 0.8 | 8 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 3.9559 | 3.9559 | 0 | 12 | 1 | 1 | 3.9559 | 10 | 0 | 0
575.25 | 50.02 | 49.89 | 0.145 | 0.7 | 7 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 3.4559 | 3.4559 | 0 | 12 | 1 | 1 | 3.4559 | 10 | 0 | 0
575.3 | 50.08 | 49.89 | 0.145 | 0.6 | 6 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 2.8088 | 2.8088 | 0 | 12 | 1 | 1 | 2.8088 | 10 | 0 | 0
575.35 | 50.08 | 49.89 | 0.145 | 0.5 | 5 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 2.3088 | 2.3088 | 0 | 12 | 1 | 1 | 2.3088 | 10 | 0 | 0
575.4 | 50.01 | 49.89 | 0.145 | 0.4 | 4 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 1.8088 | 1.8088 | 0 | 12 | 1 | 1 | 1.8088 | 10 | 0 | 0
575.45 | 50.01 | 49.96 | 0.014706 | 0.3 | 3 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 1.3088 | 1.3088 | 0 | 12 | 1 | 1 | 1.3088 | 10 | 0 | 0
575.5 | 49.94 | 49.94 | 0.026471 | 0.2 | 2 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.80882 | 0.80882 | 0 | 12 | 1 | 1 | 0.80882 | 10 | 0 | 0
575.55 | 49.94 | 49.94 | 0.026471 | 0.1 | 1 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.30882 | 0.30882 | 0 | 12 | 1 | 1 | 0.30882 | 10 | 0 | 0
575.6 | 50 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
575.65 | 50 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
575.7 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
575.75 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
575.8 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
575.85 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
575.9 | 49.92 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
575.95 | 49.92 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
576 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50.01 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
576.05 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
576.1 | 49.92 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
576.15 | 49.92 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
576.2 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
576.25 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
576.3 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
576.35 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
576.4 | 49.87 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
576.45 | 49.87 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
576.5 | 49.8 | 49.8 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
576.55 | 49.8 | 49.8 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
576.6 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
576.65 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
576.7 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
576.75 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
576.8 | 49.72 | 49.72 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
576.85 | 49.72 | 49.72 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
576.9 | 49.67 | 49.67 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
576.95 | 49.67 | 49.67 | 1 | 1 | 10 | 49.87 | 0.335 | 0.14412 | 1.4412 | 5.7206 | 5.7206 | 0 | 12 | 1 | 1 | 5.7206 | 10 | 0 | 0
577 | 49.65 | 49.65 | 1 | 1 | 10 | 49.87 | 0.335 | 0.24412 | 2.4412 | 6.2206 | 6.2206 | 0 | 12 | 1 | 1 | 6.2206 | 10 | 0 | 0
577.05 | 49.65 | 49.65 | 1 | 1 | 10 | 49.8 | 1 | 0.34412 | 3.4412 | 6.7206 | 6.7206 | 0 | 12 | 1 | 1 | 6.7206 | 10 | 0 | 0
577.1 | 49.59 | 49.59 | 1 | 1 | 10 | 49.8 | 1 | 0.44412 | 4.4412 | 7.2206 | 7.2206 | 0 | 12 | 1 | 1 | 7.2206 | 10 | 0 | 0
577.15 | 49.59 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.54412 | 5.4412 | 7.7206 | 7.7206 | 0 | 12 | 1 | 1 | 7.7206 | 10 | 0 | 0
577.2 | 49.66 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.64412 | 6.4412 | 8.2206 | 8.2206 | 0 | 12 | 1 | 1 | 8.2206 | 10 | 0 | 0
577.25 | 49.66 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.74412 | 7.4412 | 8.7206 | 8.7206 | 0 | 12 | 1 | 1 | 8.7206 | 10 | 0 | 0
577.3 | 49.63 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.84412 | 8.4412 | 9.2206 | 9.2206 | 0 | 12 | 1 | 1 | 9.2206 | 10 | 0 | 0
577.35 | 49.63 | 49.59 | 1 | 1 | 10 | 49.72 | 1 | 0.94412 | 9.4412 | 9.7206 | 9.7206 | 0 | 12 | 1 | 1 | 9.7206 | 10 | 0 | 0
577.4 | 49.61 | 49.59 | 1 | 1 | 10 | 49.72 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
577.45 | 49.61 | 49.59 | 1 | 1 | 10 | 49.67 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
577.5 | 49.54 | 49.54 | 1 | 1 | 10 | 49.67 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
577.55 | 49.54 | 49.54 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
577.6 | 49.46 | 49.46 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
577.65 | 49.46 | 49.46 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
577.7 | 49.45 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
577.75 | 49.45 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
577.8 | 49.51 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
577.85 | 49.51 | 49.45 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
577.9 | 49.5 | 49.45 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
577.95 | 49.5 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
578 | 49.54 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
578.05 | 49.54 | 49.45 | 1 | 1 | 10 | 49.54 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
578.1 | 49.59 | 49.45 | 1 | 1 | 10 | 49.59 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
578.15 | 49.59 | 49.45 | 1 | 1 | 10 | 49.59 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
578.2 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
578.25 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
578.3 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
578.35 | 49.61 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
578.4 | 49.53 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
578.45 | 49.53 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
578.5 | 49.54 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
578.55 | 49.54 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
578.6 | 49.61 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
578.65 | 49.61 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
578.7 | 49.66 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
578.75 | 49.66 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
578.8 | 49.64 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
578.85 | 49.64 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
578.9 | 49.69 | 49.53 | 1 | 1 | 10 | 49.69 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
578.95 | 49.69 | 49.53 | 1 | 1 | 10 | 49.69 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
579 | 49.74 | 49.53 | 1 | 1 | 10 | 49.74 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
579.05 | 49.74 | 49.54 | 1 | 1 | 10 | 49.74 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
579.1 | 49.78 | 49.54 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
579.15 | 49.78 | 49.61 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
579.2 | 49.82 | 49.61 | 1 | 1 | 10 | 49.82 | 0.81 | 0.81 | 8.1 | 9.05 | 9.05 | 0 | 12 | 1 | 1 | 9.05 | 10 | 0 | 0
579.25 | 49.82 | 49.64 | 1 | 1 | 10 | 49.82 | 0.81 | 0.81 | 8.1 | 9.05 | 9.05 | 0 | 12 | 1 | 1 | 9.05 | 10 | 0 | 0
579.3 | 49.86 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
579.35 | 49.86 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
579.4 | 49.84 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
579.45 | 49.84 | 49.69 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
579.5 | 49.91 | 49.69 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
579.55 | 49.91 | 49.74 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
579.6 | 49.97 | 49.74 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
579.65 | 49.97 | 49.78 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
579.7 | 50.03 | 49.78 | 1 | 1 | 10 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.9559 | 4.9559 | 0 | 12 | 1 | 1 | 4.9559 | 10 | 0 | 0
579.75 | 50.03 | 49.82 | 0.81 | 0.9 | 9 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.4559 | 4.4559 | 0 | 12 | 1 | 1 | 4.4559 | 10 | 0 | 0
579.8 | 50.05 | 49.82 | 0.81 | 0.81 | 8.1 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 3.9471 | 3.9471 | 0 | 12 | 1 | 1 | 3.9471 | 10 | 0 | 0
579.85 | 50.05 | 49.84 | 0.62 | 0.71 | 7.1 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 3.4471 | 3.4471 | 0 | 12 | 1 | 1 | 3.4471 | 10 | 0 | 0
579.9 | 50.01 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
579.95 | 50.01 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
580 | 49.95 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
580.05 | 49.95 | 49.91 | 0.044118 | 0.52 | 5.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.4971 | 2.4971 | 0 | 12 | 1 | 1 | 2.4971 | 10 | 0 | 0
580.1 | 49.99 | 49.91 | 0.044118 | 0.42 | 4.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 1.9971 | 1.9971 | 0 | 12 | 1 | 1 | 1.9971 | 10 | 0 | 0
580.15 | 49.99 | 49.95 | 0.020588 | 0.32 | 3.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 1.4971 | 1.4971 | 0 | 12 | 1 | 1 | 1.4971 | 10 | 0 | 0
580.2 | 49.92 | 49.92 | 0.038235 | 0.22 | 2.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.99706 | 0.99706 | 0 | 12 | 1 | 1 | 0.99706 | 10 | 0 | 0
580.25 | 49.92 | 49.92 | 0.038235 | 0.12 | 1.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.49706 | 0.49706 | 0 | 12 | 1 | 1 | 0.49706 | 10 | 0 | 0
580.3 | 49.97 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
580.35 | 49.97 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
580.4 | 50.02 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
580.45 | 50.02 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.17647 | 0.17647 | 0 | 12 | 1 | 1 | 0.17647 | 10 | 0 | 0
580.5 | 50.07 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
580.55 | 50.07 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
580.6 | 50.06 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
580.65 | 50.06 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
580.7 | 50.13 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
580.75 | 50.13 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
580.8 | 50.09 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
580.85 | 50.09 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6309 | -1.6309 | 0 | 12 | 1 | 1 | -1.6309 | 10 | 0 | 0
580.9 | 50.07 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6309 | -1.6309 | 0 | 12 | 1 | 1 | -1.6309 | 10 | 0 | 0
580.95 | 50.07 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6897 | -1.6897 | 0 | 12 | 1 | 1 | -1.6897 | 10 | 0 | 0
581 | 50.07 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6897 | -1.6897 | 0 | 12 | 1 | 1 | -1.6897 | 10 | 0 | 0
581.05 | 50.07 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.13 | -0.335 | -0.335 | -3.35 | -1.8074 | -1.8074 | 0 | 12 | 1 | 1 | -1.8074 | 10 | 0 | 0
581.1 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.13 | -0.335 | -0.335 | -3.35 | -1.7779 | -1.7779 | 0 | 12 | 1 | 1 | -1.7779 | 10 | 0 | 0
581.15 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.13 | -0.335 | -0.335 | -3.35 | -1.7779 | -1.7779 | 0 | 12 | 1 | 1 | -1.7779 | 10 | 0 | 0
581.2 | 50.01 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
581.25 | 50.01 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
581.3 | 50.07 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
581.35 | 50.07 | 50.01 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.235 | -2.35 | -1.175 | -1.175 | 0 | 12 | 1 | 1 | -1.175 | 10 | 0 | 0
581.4 | 50.05 | 50.01 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.135 | -1.35 | -0.675 | -0.675 | 0 | 12 | 1 | 1 | -0.675 | 10 | 0 | 0
581.45 | 50.05 | 50.01 | 0 | 0 | 0 | 50.07 | -0.032353 | -0.035 | -0.35 | -0.175 | -0.175 | 0 | 12 | 1 | 1 | -0.175 | 10 | 0 | 0
581.5 | 50.1 | 50.01 | 0 | 0 | 0 | 50.1 | -0.05 | -0.05 | -0.5 | -0.25 | -0.25 | 0 | 12 | 1 | 1 | -0.25 | 10 | 0 | 0
581.55 | 50.1 | 50.01 | 0 | 0 | 0 | 50.1 | -0.05 | -0.05 | -0.5 | -0.25 | -0.25 | 0 | 12 | 1 | 1 | -0.25 | 10 | 0 | 0
581.6 | 50.11 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
581.65 | 50.11 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
581.7 | 50.06 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
581.75 | 50.06 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
581.8 | 50.04 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
581.85 | 50.04 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
581.9 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
581.95 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
582 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
582.05 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
582.1 | 50.11 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
582.15 | 50.11 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
582.2 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
582.25 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
582.3 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
582.35 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
582.4 | 50.02 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.11 | -0.145 | -0.145 | -1.45 | -0.73971 | -0.73971 | 0 | 12 | 1 | 1 | -0.73971 | 10 | 0 | 0
582.45 | 50.02 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.11 | -0.145 | -0.145 | -1.45 | -0.73971 | -0.73971 | 0 | 12 | 1 | 1 | -0.73971 | 10 | 0 | 0
582.5 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
582.55 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
582.6 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
582.65 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
582.7 | 50.01 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
582.75 | 50.01 | 50 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.045 | -0.45 | -0.225 | -0.225 | 0 | 12 | 1 | 1 | -0.225 | 10 | 0 | 0
582.8 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
582.85 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
582.9 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
582.95 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
583 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.14706 | 0.14706 | 0 | 12 | 1 | 1 | 0.14706 | 10 | 0 | 0
583.05 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
583.1 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
583.15 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
583.2 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
583.25 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
583.3 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
583.35 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
583.4 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
583.45 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
583.5 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
583.55 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
583.6 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
583.65 | 50 | 50 | 0 | 0 | 0 | 50.01 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
583.7 | 49.5 | 49.5 | 1 | 1 | 10 | 50.01 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
583.75 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
583.8 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
583.85 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
583.9 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
583.95 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
584 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
584.05 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
584.1 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
584.15 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
584.2 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
584.25 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.1 | 1 | 5.5 | 5.5 | 0 | 12 | 1 | 1 | 5.5 | 10 | 0 | 0
584.3 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.2 | 2 | 6 | 6 | 0 | 12 | 1 | 1 | 6 | 10 | 0 | 0
584.35 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.3 | 3 | 6.5 | 6.5 | 0 | 12 | 1 | 1 | 6.5 | 10 | 0 | 0
584.4 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.4 | 4 | 7 | 7 | 0 | 12 | 1 | 1 | 7 | 10 | 0 | 0
584.45 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.5 | 5 | 7.5 | 7.5 | 0 | 12 | 1 | 1 | 7.5 | 10 | 0 | 0
584.5 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.6 | 6 | 8 | 8 | 0 | 12 | 1 | 1 | 8 | 10 | 0 | 0
584.55 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.7 | 7 | 8.5 | 8.5 | 0 | 12 | 1 | 1 | 8.5 | 10 | 0 | 0
584.6 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.8 | 8 | 9 | 9 | 0 | 12 | 1 | 1 | 9 | 10 | 0 | 0
584.65 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.9 | 9 | 9.5 | 9.5 | 0 | 12 | 1 | 1 | 9.5 | 10 | 0 | 0
584.7 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
584.75 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
584.8 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
584.85 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
584.9 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
584.95 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
585 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
585.05 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
585.1 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
585.15 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
585.2 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
585.25 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
585.3 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
585.35 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
585.4 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
585.45 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
585.5 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
585.55 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
585.6 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
585.65 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
585.7 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
585.75 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
585.8 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
585.85 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
585.9 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
585.95 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
586 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
586.05 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
586.1 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
586.15 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
586.2 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
586.25 | 50.5 | 50.5 | -1 | 0.9 | 9 | 50.5 | -1 | -1 | -10 | -0.5 | -0.5 | 0 | 12 | 1 | 1 | -0.5 | 10 | 0 | 0
586.3 | 50.5 | 50.5 | -1 | 0.8 | 8 | 50.5 | -1 | -1 | -10 | -1 | -1 | 0 | 12 | 1 | 1 | -1 | 10 | 0 | 0
586.35 | 50.5 | 50.5 | -1 | 0.7 | 7 | 50.5 | -1 | -1 | -10 | -1.5 | -1.5 | 0 | 12 | 1 | 1 | -1.5 | 10 | 0 | 0
586.4 | 50.5 | 50.5 | -1 | 0.6 | 6 | 50.5 | -1 | -1 | -10 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
586.45 | 50.5 | 50.5 | -1 | 0.5 | 5 | 50.5 | -1 | -1 | -10 | -2.5 | -2.5 | 0 | 12 | 1 | 1 | -2.5 | 10 | 0 | 0
586.5 | 50.5 | 50.5 | -1 | 0.4 | 4 | 50.5 | -1 | -1 | -10 | -3 | -3 | 0 | 12 | 1 | 1 | -3 | 10 | 0 | 0
586.55 | 50.5 | 50.5 | -1 | 0.3 | 3 | 50.5 | -1 | -1 | -10 | -3.5 | -3.5 | 0 | 12 | 1 | 1 | -3.5 | 10 | 0 | 0
586.6 | 50.5 | 50.5 | -1 | 0.2 | 2 | 50.5 | -1 | -1 | -10 | -4 | -4 | 0 | 12 | 1 | 1 | -4 | 10 | 0 | 0
586.65 | 50.5 | 50.5 | -1 | 0.1 | 1 | 50.5 | -1 | -1 | -10 | -4.5 | -4.5 | 0 | 12 | 1 | 1 | -4.5 | 10 | 0 | 0
586.7 | 50.5 | 50.5 | -1 | 0 | 0 | 50.5 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
586.75 | 50.5 | 50.5 | -1 | -0.1 | -1 | 50.5 | -1 | -1 | -10 | -5.5 | -5.5 | 0 | 12 | 1 | 1 | -5.5 | 10 | 0 | 0
586.8 | 50.5 | 50.5 | -1 | -0.2 | -2 | 50.5 | -1 | -1 | -10 | -6 | -6 | 0 | 12 | 1 | 1 | -6 | 10 | 0 | 0
586.85 | 50.5 | 50.5 | -1 | -0.3 | -3 | 50.5 | -1 | -1 | -10 | -6.5 | -6.5 | 0 | 12 | 1 | 1 | -6.5 | 10 | 0 | 0
586.9 | 50.5 | 50.5 | -1 | -0.4 | -4 | 50.5 | -1 | -1 | -10 | -7 | -7 | 0 | 12 | 1 | 1 | -7 | 10 | 0 | 0
586.95 | 50.5 | 50.5 | -1 | -0.5 | -5 | 50.5 | -1 | -1 | -10 | -7.5 | -7.5 | 0 | 12 | 1 | 1 | -7.5 | 10 | 0 | 0
587 | 50.5 | 50.5 | -1 | -0.6 | -6 | 50.5 | -1 | -1 | -10 | -8 | -8 | 0 | 12 | 1 | 1 | -8 | 10 | 0 | 0
587.05 | 50.5 | 50.5 | -1 | -0.7 | -7 | 50.5 | -1 | -1 | -10 | -8.5 | -8.5 | 0 | 12 | 1 | 1 | -8.5 | 10 | 0 | 0
587.1 | 50.5 | 50.5 | -1 | -0.8 | -8 | 50.5 | -1 | -1 | -10 | -9 | -9 | 0 | 12 | 1 | 1 | -9 | 10 | 0 | 0
587.15 | 50.5 | 50.5 | -1 | -0.9 | -9 | 50.5 | -1 | -1 | -10 | -9.5 | -9.5 | 0 | 12 | 1 | 1 | -9.5 | 10 | 0 | 0
587.2 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
587.25 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
587.3 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
587.35 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
587.4 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
587.45 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
587.5 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
587.55 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
587.6 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
587.65 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
587.7 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
587.75 | 50.47 | 50.47 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
587.8 | 50.45 | 50.45 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
587.85 | 50.42 | 50.42 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
587.9 | 50.4 | 50.4 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
587.95 | 50.37 | 50.37 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
588 | 50.35 | 50.35 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
588.05 | 50.32 | 50.32 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
588.1 | 50.29 | 50.29 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
588.15 | 50.27 | 50.27 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
588.2 | 50.24 | 50.24 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
588.25 | 50.22 | 50.22 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
588.3 | 50.19 | 50.19 | -0.905 | -0.905 | -9.05 | 50.47 | -1 | -1 | -10 | -9.525 | -9.525 | 0 | 12 | 1 | 1 | -9.525 | 10 | 0 | 0
588.35 | 50.17 | 50.17 | -0.715 | -0.715 | -7.15 | 50.45 | -1 | -1 | -10 | -8.575 | -8.575 | 0 | 12 | 1 | 1 | -8.575 | 10 | 0 | 0
588.4 | 50.14 | 50.14 | -0.43 | -0.43 | -4.3 | 50.42 | -1 | -1 | -10 | -7.15 | -7.15 | 0 | 12 | 1 | 1 | -7.15 | 10 | 0 | 0
588.45 | 50.12 | 50.12 | -0.24 | -0.24 | -2.4 | 50.4 | -1 | -1 | -10 | -6.2 | -6.2 | 0 | 12 | 1 | 1 | -6.2 | 10 | 0 | 0
588.5 | 50.09 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 50.37 | -1 | -1 | -10 | -5.2206 | -5.2206 | 0 | 12 | 1 | 1 | -5.2206 | 10 | 0 | 0
588.55 | 50.06 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.35 | -1 | -1 | -10 | -5.1324 | -5.1324 | 0 | 12 | 1 | 1 | -5.1324 | 10 | 0 | 0
588.6 | 50.04 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.32 | -1 | -1 | -10 | -5.0735 | -5.0735 | 0 | 12 | 1 | 1 | -5.0735 | 10 | 0 | 0
588.65 | 50.01 | 50.01 | 0 | 0 | 0 | 50.29 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
588.7 | 49.99 | 49.99 | 0 | 0 | 0 | 50.27 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
588.75 | 49.96 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.24 | -1 | -1 | -10 | -4.9265 | -4.9265 | 0 | 12 | 1 | 1 | -4.9265 | 10 | 0 | 0
588.8 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.22 | -1 | -1 | -10 | -4.8676 | -4.8676 | 0 | 12 | 1 | 1 | -4.8676 | 10 | 0 | 0
588.85 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.19 | -0.905 | -0.905 | -9.05 | -4.3044 | -4.3044 | 0 | 12 | 1 | 1 | -4.3044 | 10 | 0 | 0
588.9 | 49.88 | 49.88 | 0.24 | 0.24 | 2.4 | 50.17 | -0.715 | -0.805 | -8.05 | -2.825 | -2.825 | 0 | 12 | 1 | 1 | -2.825 | 10 | 0 | 0
588.95 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.14 | -0.43 | -0.705 | -7.05 | -1.375 | -1.375 | 0 | 12 | 1 | 1 | -1.375 | 10 | 0 | 0
589 | 49.83 | 49.83 | 0.715 | 0.715 | 7.15 | 50.12 | -0.24 | -0.605 | -6.05 | 0.55 | 0.55 | 0 | 12 | 1 | 1 | 0.55 | 10 | 0 | 0
589.05 | 49.81 | 49.81 | 0.905 | 0.905 | 9.05 | 50.09 | -0.044118 | -0.505 | -5.05 | 2 | 2 | 0 | 12 | 1 | 1 | 2 | 10 | 0 | 0
589.1 | 49.78 | 49.78 | 1 | 1 | 10 | 50.06 | -0.026471 | -0.405 | -4.05 | 2.975 | 2.975 | 0 | 12 | 1 | 1 | 2.975 | 10 | 0 | 0
589.15 | 49.76 | 49.76 | 1 | 1 | 10 | 50.04 | -0.014706 | -0.305 | -3.05 | 3.475 | 3.475 | 0 | 12 | 1 | 1 | 3.475 | 10 | 0 | 0
589.2 | 49.73 | 49.73 | 1 | 1 | 10 | 50.01 | 0 | -0.205 | -2.05 | 3.975 | 3.975 | 0 | 12 | 1 | 1 | 3.975 | 10 | 0 | 0
589.25 | 49.71 | 49.71 | 1 | 1 | 10 | 49.99 | 0 | -0.105 | -1.05 | 4.475 | 4.475 | 0 | 12 | 1 | 1 | 4.475 | 10 | 0 | 0
589.3 | 49.68 | 49.68 | 1 | 1 | 10 | 49.96 | 0.014706 | -0.005 | -0.05 | 4.975 | 4.975 | 0 | 12 | 1 | 1 | 4.975 | 10 | 0 | 0
589.35 | 49.65 | 49.65 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
589.4 | 49.63 | 49.63 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
589.45 | 49.6 | 49.6 | 1 | 1 | 10 | 49.88 | 0.24 | 0.14412 | 1.4412 | 5.7206 | 5.7206 | 0 | 12 | 1 | 1 | 5.7206 | 10 | 0 | 0
589.5 | 49.58 | 49.58 | 1 | 1 | 10 | 49.86 | 0.43 | 0.24412 | 2.4412 | 6.2206 | 6.2206 | 0 | 12 | 1 | 1 | 6.2206 | 10 | 0 | 0
589.55 | 49.55 | 49.55 | 1 | 1 | 10 | 49.83 | 0.715 | 0.34412 | 3.4412 | 6.7206 | 6.7206 | 0 | 12 | 1 | 1 | 6.7206 | 10 | 0 | 0
589.6 | 49.53 | 49.53 | 1 | 1 | 10 | 49.81 | 0.905 | 0.44412 | 4.4412 | 7.2206 | 7.2206 | 0 | 12 | 1 | 1 | 7.2206 | 10 | 0 | 0
589.65 | 49.5 | 49.5 | 1 | 1 | 10 | 49.78 | 1 | 0.54412 | 5.4412 | 7.7206 | 7.7206 | 0 | 12 | 1 | 1 | 7.7206 | 10 | 0 | 0
589.7 | 49.5 | 49.5 | 1 | 1 | 10 | 49.76 | 1 | 0.64412 | 6.4412 | 8.2206 | 8.2206 | 0 | 12 | 1 | 1 | 8.2206 | 10 | 0 | 0
589.75 | 49.53 | 49.5 | 1 | 1 | 10 | 49.73 | 1 | 0.74412 | 7.4412 | 8.7206 | 8.7206 | 0 | 12 | 1 | 1 | 8.7206 | 10 | 0 | 0
589.8 | 49.55 | 49.5 | 1 | 1 | 10 | 49.71 | 1 | 0.84412 | 8.4412 | 9.2206 | 9.2206 | 0 | 12 | 1 | 1 | 9.2206 | 10 | 0 | 0
589.85 | 49.58 | 49.5 | 1 | 1 | 10 | 49.68 | 1 | 0.94412 | 9.4412 | 9.7206 | 9.7206 | 0 | 12 | 1 | 1 | 9.7206 | 10 | 0 | 0
589.9 | 49.6 | 49.5 | 1 | 1 | 10 | 49.65 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
589.95 | 49.63 | 49.5 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
590 | 49.65 | 49.5 | 1 | 1 | 10 | 49.65 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
590.05 | 49.68 | 49.5 | 1 | 1 | 10 | 49.68 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
590.1 | 49.71 | 49.5 | 1 | 1 | 10 | 49.71 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
590.15 | 49.73 | 49.5 | 1 | 1 | 10 | 49.73 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
590.2 | 49.76 | 49.5 | 1 | 1 | 10 | 49.76 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
590.25 | 49.78 | 49.5 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
590.3 | 49.81 | 49.53 | 1 | 1 | 10 | 49.81 | 0.905 | 0.905 | 9.05 | 9.525 | 9.525 | 0 | 12 | 1 | 1 | 9.525 | 10 | 0 | 0
590.35 | 49.83 | 49.55 | 1 | 1 | 10 | 49.83 | 0.715 | 0.715 | 7.15 | 8.575 | 8.575 | 0 | 12 | 1 | 1 | 8.575 | 10 | 0 | 0
590.4 | 49.86 | 49.58 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
590.45 | 49.88 | 49.6 | 1 | 1 | 10 | 49.88 | 0.24 | 0.24 | 2.4 | 6.2 | 6.2 | 0 | 12 | 1 | 1 | 6.2 | 10 | 0 | 0
590.5 | 49.91 | 49.63 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
590.55 | 49.94 | 49.65 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
590.6 | 49.96 | 49.68 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
590.65 | 49.99 | 49.71 | 1 | 1 | 10 | 49.99 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
590.7 | 50.01 | 49.73 | 1 | 1 | 10 | 50.01 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
590.75 | 50.04 | 49.76 | 1 | 1 | 10 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 4.9265 | 4.9265 | 0 | 12 | 1 | 1 | 4.9265 | 10 | 0 | 0
590.8 | 50.06 | 49.78 | 1 | 1 | 10 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 4.8676 | 4.8676 | 0 | 12 | 1 | 1 | 4.8676 | 10 | 0 | 0
590.85 | 50.09 | 49.81 | 0.905 | 0.905 | 9.05 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 4.3044 | 4.3044 | 0 | 12 | 1 | 1 | 4.3044 | 10 | 0 | 0
590.9 | 50.12 | 49.83 | 0.715 | 0.805 | 8.05 | 50.12 | -0.24 | -0.24 | -2.4 | 2.825 | 2.825 | 0 | 12 | 1 | 1 | 2.825 | 10 | 0 | 0
590.95 | 50.14 | 49.86 | 0.43 | 0.705 | 7.05 | 50.14 | -0.43 | -0.43 | -4.3 | 1.375 | 1.375 | 0 | 12 | 1 | 1 | 1.375 | 10 | 0 | 0
591 | 50.17 | 49.88 | 0.24 | 0.605 | 6.05 | 50.17 | -0.715 | -0.715 | -7.15 | -0.55 | -0.55 | 0 | 12 | 1 | 1 | -0.55 | 10 | 0 | 0
591.05 | 50.19 | 49.91 | 0.044118 | 0.505 | 5.05 | 50.19 | -0.905 | -0.905 | -9.05 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
591.1 | 50.22 | 49.94 | 0.026471 | 0.405 | 4.05 | 50.22 | -1 | -1 | -10 | -2.975 | -2.975 | 0 | 12 | 1 | 1 | -2.975 | 10 | 0 | 0
591.15 | 50.24 | 49.96 | 0.014706 | 0.305 | 3.05 | 50.24 | -1 | -1 | -10 | -3.475 | -3.475 | 0 | 12 | 1 | 1 | -3.475 | 10 | 0 | 0
591.2 | 50.27 | 49.99 | 0 | 0.205 | 2.05 | 50.27 | -1 | -1 | -10 | -3.975 | -3.975 | 0 | 12 | 1 | 1 | -3.975 | 10 | 0 | 0
591.25 | 50.29 | 50.01 | 0 | 0.105 | 1.05 | 50.29 | -1 | -1 | -10 | -4.475 | -4.475 | 0 | 12 | 1 | 1 | -4.475 | 10 | 0 | 0
591.3 | 50.32 | 50.04 | -0.014706 | 0.005 | 0.05 | 50.32 | -1 | -1 | -10 | -4.975 | -4.975 | 0 | 12 | 1 | 1 | -4.975 | 10 | 0 | 0
591.35 | 50.35 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.35 | -1 | -1 | -10 | -5.1324 | -5.1324 | 0 | 12 | 1 | 1 | -5.1324 | 10 | 0 | 0
591.4 | 50.37 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 50.37 | -1 | -1 | -10 | -5.2206 | -5.2206 | 0 | 12 | 1 | 1 | -5.2206 | 10 | 0 | 0
591.45 | 50.4 | 50.12 | -0.24 | -0.14412 | -1.4412 | 50.4 | -1 | -1 | -10 | -5.7206 | -5.7206 | 0 | 12 | 1 | 1 | -5.7206 | 10 | 0 | 0
591.5 | 50.42 | 50.14 | -0.43 | -0.24412 | -2.4412 | 50.42 | -1 | -1 | -10 | -6.2206 | -6.2206 | 0 | 12 | 1 | 1 | -6.2206 | 10 | 0 | 0
591.55 | 50.45 | 50.17 | -0.715 | -0.34412 | -3.4412 | 50.45 | -1 | -1 | -10 | -6.7206 | -6.7206 | 0 | 12 | 1 | 1 | -6.7206 | 10 | 0 | 0
591.6 | 50.47 | 50.19 | -0.905 | -0.44412 | -4.4412 | 50.47 | -1 | -1 | -10 | -7.2206 | -7.2206 | 0 | 12 | 1 | 1 | -7.2206 | 10 | 0 | 0
591.65 | 50.5 | 50.22 | -1 | -0.54412 | -5.4412 | 50.5 | -1 | -1 | -10 | -7.7206 | -7.7206 | 0 | 12 | 1 | 1 | -7.7206 | 10 | 0 | 0
591.7 | 50.5 | 50.24 | -1 | -0.64412 | -6.4412 | 50.5 | -1 | -1 | -10 | -8.2206 | -8.2206 | 0 | 12 | 1 | 1 | -8.2206 | 10 | 0 | 0
591.75 | 50.47 | 50.27 | -1 | -0.74412 | -7.4412 | 50.5 | -1 | -1 | -10 | -8.7206 | -8.7206 | 0 | 12 | 1 | 1 | -8.7206 | 10 | 0 | 0
591.8 | 50.45 | 50.29 | -1 | -0.84412 | -8.4412 | 50.5 | -1 | -1 | -10 | -9.2206 | -9.2206 | 0 | 12 | 1 | 1 | -9.2206 | 10 | 0 | 0
591.85 | 50.42 | 50.32 | -1 | -0.94412 | -9.4412 | 50.5 | -1 | -1 | -10 | -9.7206 | -9.7206 | 0 | 12 | 1 | 1 | -9.7206 | 10 | 0 | 0
591.9 | 50.39 | 50.35 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
591.95 | 50.37 | 50.37 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
592 | 50.34 | 50.34 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
592.05 | 50.32 | 50.32 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
592.1 | 50.29 | 50.29 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
592.15 | 50.26 | 50.26 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
592.2 | 50.24 | 50.24 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
592.25 | 50.21 | 50.21 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
592.3 | 50.18 | 50.18 | -0.81 | -0.81 | -8.1 | 50.47 | -1 | -1 | -10 | -9.05 | -9.05 | 0 | 12 | 1 | 1 | -9.05 | 10 | 0 | 0
592.35 | 50.16 | 50.16 | -0.62 | -0.62 | -6.2 | 50.45 | -1 | -1 | -10 | -8.1 | -8.1 | 0 | 12 | 1 | 1 | -8.1 | 10 | 0 | 0
592.4 | 50.13 | 50.13 | -0.335 | -0.335 | -3.35 | 50.42 | -1 | -1 | -10 | -6.675 | -6.675 | 0 | 12 | 1 | 1 | -6.675 | 10 | 0 | 0
592.45 | 50.11 | 50.11 | -0.145 | -0.145 | -1.45 | 50.39 | -1 | -1 | -10 | -5.725 | -5.725 | 0 | 12 | 1 | 1 | -5.725 | 10 | 0 | 0
592.5 | 50.08 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 50.37 | -1 | -1 | -10 | -5.1912 | -5.1912 | 0 | 12 | 1 | 1 | -5.1912 | 10 | 0 | 0
592.55 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.34 | -1 | -1 | -10 | -5.1029 | -5.1029 | 0 | 12 | 1 | 1 | -5.1029 | 10 | 0 | 0
592.6 | 50.03 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 50.32 | -1 | -1 | -10 | -5.0441 | -5.0441 | 0 | 12 | 1 | 1 | -5.0441 | 10 | 0 | 0
592.65 | 50 | 50 | 0 | 0 | 0 | 50.29 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
592.7 | 50 | 50 | 0 | 0 | 0 | 50.26 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
592.75 | 50 | 50 | 0 | 0 | 0 | 50.24 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
592.8 | 50 | 50 | 0 | 0 | 0 | 50.21 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
592.85 | 50 | 50 | 0 | 0 | 0 | 50.18 | -0.81 | -0.9 | -9 | -4.5 | -4.5 | 0 | 12 | 1 | 1 | -4.5 | 10 | 0 | 0
592.9 | 50 | 50 | 0 | 0 | 0 | 50.16 | -0.62 | -0.8 | -8 | -4 | -4 | 0 | 12 | 1 | 1 | -4 | 10 | 0 | 0
592.95 | 50 | 50 | 0 | 0 | 0 | 50.13 | -0.335 | -0.7 | -7 | -3.5 | -3.5 | 0 | 12 | 1 | 1 | -3.5 | 10 | 0 | 0
593 | 50.01 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.6 | -6 | -3 | -3 | 0 | 12 | 1 | 1 | -3 | 10 | 0 | 0
593.05 | 50.01 | 50 | 0 | 0 | 0 | 50.08 | -0.038235 | -0.5 | -5 | -2.5 | -2.5 | 0 | 12 | 1 | 1 | -2.5 | 10 | 0 | 0
593.1 | 49.99 | 49.99 | 0 | 0 | 0 | 50.05 | -0.020588 | -0.4 | -4 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
593.15 | 49.99 | 49.99 | 0 | 0 | 0 | 50.03 | -0.0088235 | -0.3 | -3 | -1.5 | -1.5 | 0 | 12 | 1 | 1 | -1.5 | 10 | 0 | 0
593.2 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | -0.2 | -2 | -0.83824 | -0.83824 | 0 | 12 | 1 | 1 | -0.83824 | 10 | 0 | 0
593.25 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | -0.1 | -1 | -0.33824 | -0.33824 | 0 | 12 | 1 | 1 | -0.33824 | 10 | 0 | 0
593.3 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
593.35 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
593.4 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
593.45 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
593.5 | 49.89 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
593.55 | 49.89 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
593.6 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50.01 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
593.65 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
593.7 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
593.75 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 2.7868 | 2.7868 | 0 | 12 | 1 | 1 | 2.7868 | 10 | 0 | 0
593.8 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 2.7868 | 2.7868 | 0 | 12 | 1 | 1 | 2.7868 | 10 | 0 | 0
593.85 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 2.8456 | 2.8456 | 0 | 12 | 1 | 1 | 2.8456 | 10 | 0 | 0
593.9 | 49.94 | 49.85 | 0.525 | 0.525 | 5.25 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 2.7574 | 2.7574 | 0 | 12 | 1 | 1 | 2.7574 | 10 | 0 | 0
593.95 | 49.94 | 49.85 | 0.525 | 0.525 | 5.25 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 2.7574 | 2.7574 | 0 | 12 | 1 | 1 | 2.7574 | 10 | 0 | 0
594 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
594.05 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
594.1 | 49.93 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
594.15 | 49.93 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
594.2 | 49.96 | 49.85 | 0.525 | 0.525 | 5.25 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 2.6985 | 2.6985 | 0 | 12 | 1 | 1 | 2.6985 | 10 | 0 | 0
594.25 | 49.96 | 49.85 | 0.525 | 0.525 | 5.25 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 2.6985 | 2.6985 | 0 | 12 | 1 | 1 | 2.6985 | 10 | 0 | 0
594.3 | 49.99 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
594.35 | 49.99 | 49.91 | 0.044118 | 0.425 | 4.25 | 49.99 | 0 | 0 | 0 | 2.125 | 2.125 | 0 | 12 | 1 | 1 | 2.125 | 10 | 0 | 0
594.4 | 49.99 | 49.91 | 0.044118 | 0.325 | 3.25 | 49.99 | 0 | 0 | 0 | 1.625 | 1.625 | 0 | 12 | 1 | 1 | 1.625 | 10 | 0 | 0
594.45 | 49.99 | 49.93 | 0.032353 | 0.225 | 2.25 | 49.99 | 0 | 0 | 0 | 1.125 | 1.125 | 0 | 12 | 1 | 1 | 1.125 | 10 | 0 | 0
594.5 | 49.96 | 49.93 | 0.032353 | 0.125 | 1.25 | 49.99 | 0 | 0 | 0 | 0.625 | 0.625 | 0 | 12 | 1 | 1 | 0.625 | 10 | 0 | 0
594.55 | 49.96 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 49.99 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
594.6 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
594.65 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
594.7 | 50.05 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.058824 | 0.058824 | 0 | 12 | 1 | 1 | 0.058824 | 10 | 0 | 0
594.75 | 50.05 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
594.8 | 49.97 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
594.85 | 49.97 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
594.9 | 49.92 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
594.95 | 49.92 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
595 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
595.05 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
595.1 | 49.94 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
595.15 | 49.94 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
595.2 | 50.01 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
595.25 | 50.01 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
595.3 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
595.35 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
595.4 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
595.45 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
595.5 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
595.55 | 49.95 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
595.6 | 49.97 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
595.65 | 49.97 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
595.7 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
595.75 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
595.8 | 49.87 | 49.87 | 0.335 | 0.335 | 3.35 | 50.01 | 0 | 0 | 0 | 1.675 | 1.675 | 0 | 12 | 1 | 1 | 1.675 | 10 | 0 | 0
595.85 | 49.87 | 49.87 | 0.335 | 0.335 | 3.35 | 49.99 | 0 | 0 | 0 | 1.675 | 1.675 | 0 | 12 | 1 | 1 | 1.675 | 10 | 0 | 0
595.9 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
595.95 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 2.6691 | 2.6691 | 0 | 12 | 1 | 1 | 2.6691 | 10 | 0 | 0
596 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
596.05 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
596.1 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
596.15 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
596.2 | 49.84 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
596.25 | 49.84 | 49.79 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
596.3 | 49.89 | 49.79 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
596.35 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.12647 | 1.2647 | 5.6324 | 5.6324 | 0 | 12 | 1 | 1 | 5.6324 | 10 | 0 | 0
596.4 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.145 | 1.45 | 5.725 | 5.725 | 0 | 12 | 1 | 1 | 5.725 | 10 | 0 | 0
596.45 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.145 | 1.45 | 5.725 | 5.725 | 0 | 12 | 1 | 1 | 5.725 | 10 | 0 | 0
596.5 | 49.96 | 49.79 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
596.55 | 49.96 | 49.79 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
596.6 | 50.02 | 49.79 | 1 | 1 | 10 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 4.9853 | 4.9853 | 0 | 12 | 1 | 1 | 4.9853 | 10 | 0 | 0
596.65 | 50.02 | 49.79 | 1 | 1 | 10 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 4.9853 | 4.9853 | 0 | 12 | 1 | 1 | 4.9853 | 10 | 0 | 0
596.7 | 50.03 | 49.79 | 1 | 1 | 10 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.9559 | 4.9559 | 0 | 12 | 1 | 1 | 4.9559 | 10 | 0 | 0
596.75 | 50.03 | 49.84 | 0.62 | 0.9 | 9 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.4559 | 4.4559 | 0 | 12 | 1 | 1 | 4.4559 | 10 | 0 | 0
596.8 | 50.02 | 49.84 | 0.62 | 0.8 | 8 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 3.9559 | 3.9559 | 0 | 12 | 1 | 1 | 3.9559 | 10 | 0 | 0
596.85 | 50.02 | 49.89 | 0.145 | 0.7 | 7 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 3.4559 | 3.4559 | 0 | 12 | 1 | 1 | 3.4559 | 10 | 0 | 0
596.9 | 50.08 | 49.89 | 0.145 | 0.6 | 6 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 2.8088 | 2.8088 | 0 | 12 | 1 | 1 | 2.8088 | 10 | 0 | 0
596.95 | 50.08 | 49.89 | 0.145 | 0.5 | 5 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 2.3088 | 2.3088 | 0 | 12 | 1 | 1 | 2.3088 | 10 | 0 | 0
597 | 50.01 | 49.89 | 0.145 | 0.4 | 4 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 1.8088 | 1.8088 | 0 | 12 | 1 | 1 | 1.8088 | 10 | 0 | 0
597.05 | 50.01 | 49.96 | 0.014706 | 0.3 | 3 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 1.3088 | 1.3088 | 0 | 12 | 1 | 1 | 1.3088 | 10 | 0 | 0
597.1 | 49.94 | 49.94 | 0.026471 | 0.2 | 2 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.80882 | 0.80882 | 0 | 12 | 1 | 1 | 0.80882 | 10 | 0 | 0
597.15 | 49.94 | 49.94 | 0.026471 | 0.1 | 1 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.30882 | 0.30882 | 0 | 12 | 1 | 1 | 0.30882 | 10 | 0 | 0
597.2 | 50 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
597.25 | 50 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
597.3 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
597.35 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
597.4 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
597.45 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
597.5 | 49.92 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
597.55 | 49.92 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
597.6 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50.01 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
597.65 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
597.7 | 49.92 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
597.75 | 49.92 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
597.8 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
597.85 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
597.9 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
597.95 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
598 | 49.87 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
598.05 | 49.87 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
598.1 | 49.8 | 49.8 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
598.15 | 49.8 | 49.8 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
598.2 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
598.25 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
598.3 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
598.35 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
598.4 | 49.72 | 49.72 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
598.45 | 49.72 | 49.72 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
598.5 | 49.67 | 49.67 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
598.55 | 49.67 | 49.67 | 1 | 1 | 10 | 49.87 | 0.335 | 0.14412 | 1.4412 | 5.7206 | 5.7206 | 0 | 12 | 1 | 1 | 5.7206 | 10 | 0 | 0
598.6 | 49.65 | 49.65 | 1 | 1 | 10 | 49.87 | 0.335 | 0.24412 | 2.4412 | 6.2206 | 6.2206 | 0 | 12 | 1 | 1 | 6.2206 | 10 | 0 | 0
598.65 | 49.65 | 49.65 | 1 | 1 | 10 | 49.8 | 1 | 0.34412 | 3.4412 | 6.7206 | 6.7206 | 0 | 12 | 1 | 1 | 6.7206 | 10 | 0 | 0
598.7 | 49.59 | 49.59 | 1 | 1 | 10 | 49.8 | 1 | 0.44412 | 4.4412 | 7.2206 | 7.2206 | 0 | 12 | 1 | 1 | 7.2206 | 10 | 0 | 0
598.75 | 49.59 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.54412 | 5.4412 | 7.7206 | 7.7206 | 0 | 12 | 1 | 1 | 7.7206 | 10 | 0 | 0
598.8 | 49.66 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.64412 | 6.4412 | 8.2206 | 8.2206 | 0 | 12 | 1 | 1 | 8.2206 | 10 | 0 | 0
598.85 | 49.66 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.74412 | 7.4412 | 8.7206 | 8.7206 | 0 | 12 | 1 | 1 | 8.7206 | 10 | 0 | 0
598.9 | 49.63 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.84412 | 8.4412 | 9.2206 | 9.2206 | 0 | 12 | 1 | 1 | 9.2206 | 10 | 0 | 0
598.95 | 49.63 | 49.59 | 1 | 1 | 10 | 49.72 | 1 | 0.94412 | 9.4412 | 9.7206 | 9.7206 | 0 | 12 | 1 | 1 | 9.7206 | 10 | 0 | 0
599 | 49.61 | 49.59 | 1 | 1 | 10 | 49.72 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
599.05 | 49.61 | 49.59 | 1 | 1 | 10 | 49.67 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
599.1 | 49.54 | 49.54 | 1 | 1 | 10 | 49.67 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
599.15 | 49.54 | 49.54 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
599.2 | 49.46 | 49.46 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
599.25 | 49.46 | 49.46 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
599.3 | 49.45 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
599.35 | 49.45 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
599.4 | 49.51 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
599.45 | 49.51 | 49.45 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
599.5 | 49.5 | 49.45 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
599.55 | 49.5 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
599.6 | 49.54 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
599.65 | 49.54 | 49.45 | 1 | 1 | 10 | 49.54 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
599.7 | 49.59 | 49.45 | 1 | 1 | 10 | 49.59 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
599.75 | 49.59 | 49.45 | 1 | 1 | 10 | 49.59 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
599.8 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
599.85 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
599.9 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
599.95 | 49.61 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
600 | 49.53 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
600.05 | 49.53 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
600.1 | 49.54 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
600.15 | 49.54 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
600.2 | 49.61 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
600.25 | 49.61 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
600.3 | 49.66 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
600.35 | 49.66 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
600.4 | 49.64 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
600.45 | 49.64 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
600.5 | 49.69 | 49.53 | 1 | 1 | 10 | 49.69 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
600.55 | 49.69 | 49.53 | 1 | 1 | 10 | 49.69 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
600.6 | 49.74 | 49.53 | 1 | 1 | 10 | 49.74 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
600.65 | 49.74 | 49.54 | 1 | 1 | 10 | 49.74 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
600.7 | 49.78 | 49.54 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
600.75 | 49.78 | 49.61 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
600.8 | 49.82 | 49.61 | 1 | 1 | 10 | 49.82 | 0.81 | 0.81 | 8.1 | 9.05 | 9.05 | 0 | 12 | 1 | 1 | 9.05 | 10 | 0 | 0
600.85 | 49.82 | 49.64 | 1 | 1 | 10 | 49.82 | 0.81 | 0.81 | 8.1 | 9.05 | 9.05 | 0 | 12 | 1 | 1 | 9.05 | 10 | 0 | 0
600.9 | 49.86 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
600.95 | 49.86 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
601 | 49.84 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
601.05 | 49.84 | 49.69 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
601.1 | 49.91 | 49.69 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
601.15 | 49.91 | 49.74 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
601.2 | 49.97 | 49.74 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
601.25 | 49.97 | 49.78 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
601.3 | 50.03 | 49.78 | 1 | 1 | 10 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.9559 | 4.9559 | 0 | 12 | 1 | 1 | 4.9559 | 10 | 0 | 0
601.35 | 50.03 | 49.82 | 0.81 | 0.9 | 9 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.4559 | 4.4559 | 0 | 12 | 1 | 1 | 4.4559 | 10 | 0 | 0
601.4 | 50.05 | 49.82 | 0.81 | 0.81 | 8.1 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 3.9471 | 3.9471 | 0 | 12 | 1 | 1 | 3.9471 | 10 | 0 | 0
601.45 | 50.05 | 49.84 | 0.62 | 0.71 | 7.1 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 3.4471 | 3.4471 | 0 | 12 | 1 | 1 | 3.4471 | 10 | 0 | 0
601.5 | 50.01 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
601.55 | 50.01 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
601.6 | 49.95 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
601.65 | 49.95 | 49.91 | 0.044118 | 0.52 | 5.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.4971 | 2.4971 | 0 | 12 | 1 | 1 | 2.4971 | 10 | 0 | 0
601.7 | 49.99 | 49.91 | 0.044118 | 0.42 | 4.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 1.9971 | 1.9971 | 0 | 12 | 1 | 1 | 1.9971 | 10 | 0 | 0
601.75 | 49.99 | 49.95 | 0.020588 | 0.32 | 3.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 1.4971 | 1.4971 | 0 | 12 | 1 | 1 | 1.4971 | 10 | 0 | 0
601.8 | 49.92 | 49.92 | 0.038235 | 0.22 | 2.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.99706 | 0.99706 | 0 | 12 | 1 | 1 | 0.99706 | 10 | 0 | 0
601.85 | 49.92 | 49.92 | 0.038235 | 0.12 | 1.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.49706 | 0.49706 | 0 | 12 | 1 | 1 | 0.49706 | 10 | 0 | 0
601.9 | 49.97 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
601.95 | 49.97 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
602 | 50.02 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
602.05 | 50.02 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.17647 | 0.17647 | 0 | 12 | 1 | 1 | 0.17647 | 10 | 0 | 0
602.1 | 50.07 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
602.15 | 50.07 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
602.2 | 50.06 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
602.25 | 50.06 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
602.3 | 50.13 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
602.35 | 50.13 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
602.4 | 50.09 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
602.45 | 50.09 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6309 | -1.6309 | 0 | 12 | 1 | 1 | -1.6309 | 10 | 0 | 0
602.5 | 50.07 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6309 | -1.6309 | 0 | 12 | 1 | 1 | -1.6309 | 10 | 0 | 0
602.55 | 50.07 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6897 | -1.6897 | 0 | 12 | 1 | 1 | -1.6897 | 10 | 0 | 0
602.6 | 50.07 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6897 | -1.6897 | 0 | 12 | 1 | 1 | -1.6897 | 10 | 0 | 0
602.65 | 50.07 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.13 | -0.335 | -0.335 | -3.35 | -1.8074 | -1.8074 | 0 | 12 | 1 | 1 | -1.8074 | 10 | 0 | 0
602.7 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.13 | -0.335 | -0.335 | -3.35 | -1.7779 | -1.7779 | 0 | 12 | 1 | 1 | -1.7779 | 10 | 0 | 0
602.75 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.13 | -0.335 | -0.335 | -3.35 | -1.7779 | -1.7779 | 0 | 12 | 1 | 1 | -1.7779 | 10 | 0 | 0
602.8 | 50.01 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
602.85 | 50.01 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
602.9 | 50.07 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
602.95 | 50.07 | 50.01 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.235 | -2.35 | -1.175 | -1.175 | 0 | 12 | 1 | 1 | -1.175 | 10 | 0 | 0
603 | 50.05 | 50.01 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.135 | -1.35 | -0.675 | -0.675 | 0 | 12 | 1 | 1 | -0.675 | 10 | 0 | 0
603.05 | 50.05 | 50.01 | 0 | 0 | 0 | 50.07 | -0.032353 | -0.035 | -0.35 | -0.175 | -0.175 | 0 | 12 | 1 | 1 | -0.175 | 10 | 0 | 0
603.1 | 50.1 | 50.01 | 0 | 0 | 0 | 50.1 | -0.05 | -0.05 | -0.5 | -0.25 | -0.25 | 0 | 12 | 1 | 1 | -0.25 | 10 | 0 | 0
603.15 | 50.1 | 50.01 | 0 | 0 | 0 | 50.1 | -0.05 | -0.05 | -0.5 | -0.25 | -0.25 | 0 | 12 | 1 | 1 | -0.25 | 10 | 0 | 0
603.2 | 50.11 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
603.25 | 50.11 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
603.3 | 50.06 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
603.35 | 50.06 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
603.4 | 50.04 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
603.45 | 50.04 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
603.5 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
603.55 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
603.6 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
603.65 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
603.7 | 50.11 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
603.75 | 50.11 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
603.8 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
603.85 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
603.9 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
603.95 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
604 | 50.02 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.11 | -0.145 | -0.145 | -1.45 | -0.73971 | -0.73971 | 0 | 12 | 1 | 1 | -0.73971 | 10 | 0 | 0
604.05 | 50.02 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.11 | -0.145 | -0.145 | -1.45 | -0.73971 | -0.73971 | 0 | 12 | 1 | 1 | -0.73971 | 10 | 0 | 0
604.1 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
604.15 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
604.2 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
604.25 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
604.3 | 50.01 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
604.35 | 50.01 | 50 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.045 | -0.45 | -0.225 | -0.225 | 0 | 12 | 1 | 1 | -0.225 | 10 | 0 | 0
604.4 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
604.45 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
604.5 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
604.55 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
604.6 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.14706 | 0.14706 | 0 | 12 | 1 | 1 | 0.14706 | 10 | 0 | 0
604.65 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
604.7 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
604.75 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
604.8 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
604.85 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
604.9 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
604.95 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
605 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
605.05 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
605.1 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
605.15 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
605.2 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
605.25 | 50 | 50 | 0 | 0 | 0 | 50.01 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
605.3 | 49.5 | 49.5 | 1 | 1 | 10 | 50.01 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
605.35 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
605.4 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
605.45 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
605.5 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
605.55 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
605.6 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
605.65 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
605.7 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
605.75 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
605.8 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
605.85 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.1 | 1 | 5.5 | 5.5 | 0 | 12 | 1 | 1 | 5.5 | 10 | 0 | 0
605.9 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.2 | 2 | 6 | 6 | 0 | 12 | 1 | 1 | 6 | 10 | 0 | 0
605.95 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.3 | 3 | 6.5 | 6.5 | 0 | 12 | 1 | 1 | 6.5 | 10 | 0 | 0
606 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.4 | 4 | 7 | 7 | 0 | 12 | 1 | 1 | 7 | 10 | 0 | 0
606.05 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.5 | 5 | 7.5 | 7.5 | 0 | 12 | 1 | 1 | 7.5 | 10 | 0 | 0
606.1 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.6 | 6 | 8 | 8 | 0 | 12 | 1 | 1 | 8 | 10 | 0 | 0
606.15 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.7 | 7 | 8.5 | 8.5 | 0 | 12 | 1 | 1 | 8.5 | 10 | 0 | 0
606.2 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.8 | 8 | 9 | 9 | 0 | 12 | 1 | 1 | 9 | 10 | 0 | 0
606.25 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.9 | 9 | 9.5 | 9.5 | 0 | 12 | 1 | 1 | 9.5 | 10 | 0 | 0
606.3 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
606.35 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
606.4 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
606.45 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
606.5 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
606.55 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
606.6 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
606.65 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
606.7 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
606.75 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
606.8 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
606.85 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
606.9 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
606.95 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
607 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
607.05 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
607.1 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
607.15 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
607.2 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
607.25 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
607.3 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
607.35 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
607.4 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
607.45 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
607.5 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
607.55 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
607.6 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
607.65 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
607.7 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
607.75 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
607.8 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
607.85 | 50.5 | 50.5 | -1 | 0.9 | 9 | 50.5 | -1 | -1 | -10 | -0.5 | -0.5 | 0 | 12 | 1 | 1 | -0.5 | 10 | 0 | 0
607.9 | 50.5 | 50.5 | -1 | 0.8 | 8 | 50.5 | -1 | -1 | -10 | -1 | -1 | 0 | 12 | 1 | 1 | -1 | 10 | 0 | 0
607.95 | 50.5 | 50.5 | -1 | 0.7 | 7 | 50.5 | -1 | -1 | -10 | -1.5 | -1.5 | 0 | 12 | 1 | 1 | -1.5 | 10 | 0 | 0
608 | 50.5 | 50.5 | -1 | 0.6 | 6 | 50.5 | -1 | -1 | -10 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
608.05 | 50.5 | 50.5 | -1 | 0.5 | 5 | 50.5 | -1 | -1 | -10 | -2.5 | -2.5 | 0 | 12 | 1 | 1 | -2.5 | 10 | 0 | 0
608.1 | 50.5 | 50.5 | -1 | 0.4 | 4 | 50.5 | -1 | -1 | -10 | -3 | -3 | 0 | 12 | 1 | 1 | -3 | 10 | 0 | 0
608.15 | 50.5 | 50.5 | -1 | 0.3 | 3 | 50.5 | -1 | -1 | -10 | -3.5 | -3.5 | 0 | 12 | 1 | 1 | -3.5 | 10 | 0 | 0
608.2 | 50.5 | 50.5 | -1 | 0.2 | 2 | 50.5 | -1 | -1 | -10 | -4 | -4 | 0 | 12 | 1 | 1 | -4 | 10 | 0 | 0
608.25 | 50.5 | 50.5 | -1 | 0.1 | 1 | 50.5 | -1 | -1 | -10 | -4.5 | -4.5 | 0 | 12 | 1 | 1 | -4.5 | 10 | 0 | 0
608.3 | 50.5 | 50.5 | -1 | 0 | 0 | 50.5 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
608.35 | 50.5 | 50.5 | -1 | -0.1 | -1 | 50.5 | -1 | -1 | -10 | -5.5 | -5.5 | 0 | 12 | 1 | 1 | -5.5 | 10 | 0 | 0
608.4 | 50.5 | 50.5 | -1 | -0.2 | -2 | 50.5 | -1 | -1 | -10 | -6 | -6 | 0 | 12 | 1 | 1 | -6 | 10 | 0 | 0
608.45 | 50.5 | 50.5 | -1 | -0.3 | -3 | 50.5 | -1 | -1 | -10 | -6.5 | -6.5 | 0 | 12 | 1 | 1 | -6.5 | 10 | 0 | 0
608.5 | 50.5 | 50.5 | -1 | -0.4 | -4 | 50.5 | -1 | -1 | -10 | -7 | -7 | 0 | 12 | 1 | 1 | -7 | 10 | 0 | 0
608.55 | 50.5 | 50.5 | -1 | -0.5 | -5 | 50.5 | -1 | -1 | -10 | -7.5 | -7.5 | 0 | 12 | 1 | 1 | -7.5 | 10 | 0 | 0
608.6 | 50.5 | 50.5 | -1 | -0.6 | -6 | 50.5 | -1 | -1 | -10 | -8 | -8 | 0 | 12 | 1 | 1 | -8 | 10 | 0 | 0
608.65 | 50.5 | 50.5 | -1 | -0.7 | -7 | 50.5 | -1 | -1 | -10 | -8.5 | -8.5 | 0 | 12 | 1 | 1 | -8.5 | 10 | 0 | 0
608.7 | 50.5 | 50.5 | -1 | -0.8 | -8 | 50.5 | -1 | -1 | -10 | -9 | -9 | 0 | 12 | 1 | 1 | -9 | 10 | 0 | 0
608.75 | 50.5 | 50.5 | -1 | -0.9 | -9 | 50.5 | -1 | -1 | -10 | -9.5 | -9.5 | 0 | 12 | 1 | 1 | -9.5 | 10 | 0 | 0
608.8 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
608.85 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
608.9 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
608.95 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
609 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
609.05 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
609.1 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
609.15 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
609.2 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
609.25 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
609.3 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
609.35 | 50.47 | 50.47 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
609.4 | 50.45 | 50.45 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
609.45 | 50.42 | 50.42 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
609.5 | 50.4 | 50.4 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
609.55 | 50.37 | 50.37 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
609.6 | 50.35 | 50.35 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
609.65 | 50.32 | 50.32 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
609.7 | 50.29 | 50.29 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
609.75 | 50.27 | 50.27 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
609.8 | 50.24 | 50.24 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
609.85 | 50.22 | 50.22 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
609.9 | 50.19 | 50.19 | -0.905 | -0.905 | -9.05 | 50.47 | -1 | -1 | -10 | -9.525 | -9.525 | 0 | 12 | 1 | 1 | -9.525 | 10 | 0 | 0
609.95 | 50.17 | 50.17 | -0.715 | -0.715 | -7.15 | 50.45 | -1 | -1 | -10 | -8.575 | -8.575 | 0 | 12 | 1 | 1 | -8.575 | 10 | 0 | 0
610 | 50.14 | 50.14 | -0.43 | -0.43 | -4.3 | 50.42 | -1 | -1 | -10 | -7.15 | -7.15 | 0 | 12 | 1 | 1 | -7.15 | 10 | 0 | 0
610.05 | 50.12 | 50.12 | -0.24 | -0.24 | -2.4 | 50.4 | -1 | -1 | -10 | -6.2 | -6.2 | 0 | 12 | 1 | 1 | -6.2 | 10 | 0 | 0
610.1 | 50.09 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 50.37 | -1 | -1 | -10 | -5.2206 | -5.2206 | 0 | 12 | 1 | 1 | -5.2206 | 10 | 0 | 0
610.15 | 50.06 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.35 | -1 | -1 | -10 | -5.1324 | -5.1324 | 0 | 12 | 1 | 1 | -5.1324 | 10 | 0 | 0
610.2 | 50.04 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.32 | -1 | -1 | -10 | -5.0735 | -5.0735 | 0 | 12 | 1 | 1 | -5.0735 | 10 | 0 | 0
610.25 | 50.01 | 50.01 | 0 | 0 | 0 | 50.29 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
610.3 | 49.99 | 49.99 | 0 | 0 | 0 | 50.27 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
610.35 | 49.96 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.24 | -1 | -1 | -10 | -4.9265 | -4.9265 | 0 | 12 | 1 | 1 | -4.9265 | 10 | 0 | 0
610.4 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.22 | -1 | -1 | -10 | -4.8676 | -4.8676 | 0 | 12 | 1 | 1 | -4.8676 | 10 | 0 | 0
610.45 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.19 | -0.905 | -0.905 | -9.05 | -4.3044 | -4.3044 | 0 | 12 | 1 | 1 | -4.3044 | 10 | 0 | 0
610.5 | 49.88 | 49.88 | 0.24 | 0.24 | 2.4 | 50.17 | -0.715 | -0.805 | -8.05 | -2.825 | -2.825 | 0 | 12 | 1 | 1 | -2.825 | 10 | 0 | 0
610.55 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.14 | -0.43 | -0.705 | -7.05 | -1.375 | -1.375 | 0 | 12 | 1 | 1 | -1.375 | 10 | 0 | 0
610.6 | 49.83 | 49.83 | 0.715 | 0.715 | 7.15 | 50.12 | -0.24 | -0.605 | -6.05 | 0.55 | 0.55 | 0 | 12 | 1 | 1 | 0.55 | 10 | 0 | 0
610.65 | 49.81 | 49.81 | 0.905 | 0.905 | 9.05 | 50.09 | -0.044118 | -0.505 | -5.05 | 2 | 2 | 0 | 12 | 1 | 1 | 2 | 10 | 0 | 0
610.7 | 49.78 | 49.78 | 1 | 1 | 10 | 50.06 | -0.026471 | -0.405 | -4.05 | 2.975 | 2.975 | 0 | 12 | 1 | 1 | 2.975 | 10 | 0 | 0
610.75 | 49.76 | 49.76 | 1 | 1 | 10 | 50.04 | -0.014706 | -0.305 | -3.05 | 3.475 | 3.475 | 0 | 12 | 1 | 1 | 3.475 | 10 | 0 | 0
610.8 | 49.73 | 49.73 | 1 | 1 | 10 | 50.01 | 0 | -0.205 | -2.05 | 3.975 | 3.975 | 0 | 12 | 1 | 1 | 3.975 | 10 | 0 | 0
610.85 | 49.71 | 49.71 | 1 | 1 | 10 | 49.99 | 0 | -0.105 | -1.05 | 4.475 | 4.475 | 0 | 12 | 1 | 1 | 4.475 | 10 | 0 | 0
610.9 | 49.68 | 49.68 | 1 | 1 | 10 | 49.96 | 0.014706 | -0.005 | -0.05 | 4.975 | 4.975 | 0 | 12 | 1 | 1 | 4.975 | 10 | 0 | 0
610.95 | 49.65 | 49.65 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
611 | 49.63 | 49.63 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
611.05 | 49.6 | 49.6 | 1 | 1 | 10 | 49.88 | 0.24 | 0.14412 | 1.4412 | 5.7206 | 5.7206 | 0 | 12 | 1 | 1 | 5.7206 | 10 | 0 | 0
611.1 | 49.58 | 49.58 | 1 | 1 | 10 | 49.86 | 0.43 | 0.24412 | 2.4412 | 6.2206 | 6.2206 | 0 | 12 | 1 | 1 | 6.2206 | 10 | 0 | 0
611.15 | 49.55 | 49.55 | 1 | 1 | 10 | 49.83 | 0.715 | 0.34412 | 3.4412 | 6.7206 | 6.7206 | 0 | 12 | 1 | 1 | 6.7206 | 10 | 0 | 0
611.2 | 49.53 | 49.53 | 1 | 1 | 10 | 49.81 | 0.905 | 0.44412 | 4.4412 | 7.2206 | 7.2206 | 0 | 12 | 1 | 1 | 7.2206 | 10 | 0 | 0
611.25 | 49.5 | 49.5 | 1 | 1 | 10 | 49.78 | 1 | 0.54412 | 5.4412 | 7.7206 | 7.7206 | 0 | 12 | 1 | 1 | 7.7206 | 10 | 0 | 0
611.3 | 49.5 | 49.5 | 1 | 1 | 10 | 49.76 | 1 | 0.64412 | 6.4412 | 8.2206 | 8.2206 | 0 | 12 | 1 | 1 | 8.2206 | 10 | 0 | 0
611.35 | 49.53 | 49.5 | 1 | 1 | 10 | 49.73 | 1 | 0.74412 | 7.4412 | 8.7206 | 8.7206 | 0 | 12 | 1 | 1 | 8.7206 | 10 | 0 | 0
611.4 | 49.55 | 49.5 | 1 | 1 | 10 | 49.71 | 1 | 0.84412 | 8.4412 | 9.2206 | 9.2206 | 0 | 12 | 1 | 1 | 9.2206 | 10 | 0 | 0
611.45 | 49.58 | 49.5 | 1 | 1 | 10 | 49.68 | 1 | 0.94412 | 9.4412 | 9.7206 | 9.7206 | 0 | 12 | 1 | 1 | 9.7206 | 10 | 0 | 0
611.5 | 49.6 | 49.5 | 1 | 1 | 10 | 49.65 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
611.55 | 49.63 | 49.5 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
611.6 | 49.65 | 49.5 | 1 | 1 | 10 | 49.65 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
611.65 | 49.68 | 49.5 | 1 | 1 | 10 | 49.68 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
611.7 | 49.71 | 49.5 | 1 | 1 | 10 | 49.71 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
611.75 | 49.73 | 49.5 | 1 | 1 | 10 | 49.73 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
611.8 | 49.76 | 49.5 | 1 | 1 | 10 | 49.76 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
611.85 | 49.78 | 49.5 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
611.9 | 49.81 | 49.53 | 1 | 1 | 10 | 49.81 | 0.905 | 0.905 | 9.05 | 9.525 | 9.525 | 0 | 12 | 1 | 1 | 9.525 | 10 | 0 | 0
611.95 | 49.83 | 49.55 | 1 | 1 | 10 | 49.83 | 0.715 | 0.715 | 7.15 | 8.575 | 8.575 | 0 | 12 | 1 | 1 | 8.575 | 10 | 0 | 0
612 | 49.86 | 49.58 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
612.05 | 49.88 | 49.6 | 1 | 1 | 10 | 49.88 | 0.24 | 0.24 | 2.4 | 6.2 | 6.2 | 0 | 12 | 1 | 1 | 6.2 | 10 | 0 | 0
612.1 | 49.91 | 49.63 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
612.15 | 49.94 | 49.65 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
612.2 | 49.96 | 49.68 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
612.25 | 49.99 | 49.71 | 1 | 1 | 10 | 49.99 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
612.3 | 50.01 | 49.73 | 1 | 1 | 10 | 50.01 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
612.35 | 50.04 | 49.76 | 1 | 1 | 10 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 4.9265 | 4.9265 | 0 | 12 | 1 | 1 | 4.9265 | 10 | 0 | 0
612.4 | 50.06 | 49.78 | 1 | 1 | 10 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 4.8676 | 4.8676 | 0 | 12 | 1 | 1 | 4.8676 | 10 | 0 | 0
612.45 | 50.09 | 49.81 | 0.905 | 0.905 | 9.05 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 4.3044 | 4.3044 | 0 | 12 | 1 | 1 | 4.3044 | 10 | 0 | 0
612.5 | 50.12 | 49.83 | 0.715 | 0.805 | 8.05 | 50.12 | -0.24 | -0.24 | -2.4 | 2.825 | 2.825 | 0 | 12 | 1 | 1 | 2.825 | 10 | 0 | 0
612.55 | 50.14 | 49.86 | 0.43 | 0.705 | 7.05 | 50.14 | -0.43 | -0.43 | -4.3 | 1.375 | 1.375 | 0 | 12 | 1 | 1 | 1.375 | 10 | 0 | 0
612.6 | 50.17 | 49.88 | 0.24 | 0.605 | 6.05 | 50.17 | -0.715 | -0.715 | -7.15 | -0.55 | -0.55 | 0 | 12 | 1 | 1 | -0.55 | 10 | 0 | 0
612.65 | 50.19 | 49.91 | 0.044118 | 0.505 | 5.05 | 50.19 | -0.905 | -0.905 | -9.05 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
612.7 | 50.22 | 49.94 | 0.026471 | 0.405 | 4.05 | 50.22 | -1 | -1 | -10 | -2.975 | -2.975 | 0 | 12 | 1 | 1 | -2.975 | 10 | 0 | 0
612.75 | 50.24 | 49.96 | 0.014706 | 0.305 | 3.05 | 50.24 | -1 | -1 | -10 | -3.475 | -3.475 | 0 | 12 | 1 | 1 | -3.475 | 10 | 0 | 0
612.8 | 50.27 | 49.99 | 0 | 0.205 | 2.05 | 50.27 | -1 | -1 | -10 | -3.975 | -3.975 | 0 | 12 | 1 | 1 | -3.975 | 10 | 0 | 0
612.85 | 50.29 | 50.01 | 0 | 0.105 | 1.05 | 50.29 | -1 | -1 | -10 | -4.475 | -4.475 | 0 | 12 | 1 | 1 | -4.475 | 10 | 0 | 0
612.9 | 50.32 | 50.04 | -0.014706 | 0.005 | 0.05 | 50.32 | -1 | -1 | -10 | -4.975 | -4.975 | 0 | 12 | 1 | 1 | -4.975 | 10 | 0 | 0
612.95 | 50.35 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.35 | -1 | -1 | -10 | -5.1324 | -5.1324 | 0 | 12 | 1 | 1 | -5.1324 | 10 | 0 | 0
613 | 50.37 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 50.37 | -1 | -1 | -10 | -5.2206 | -5.2206 | 0 | 12 | 1 | 1 | -5.2206 | 10 | 0 | 0
613.05 | 50.4 | 50.12 | -0.24 | -0.14412 | -1.4412 | 50.4 | -1 | -1 | -10 | -5.7206 | -5.7206 | 0 | 12 | 1 | 1 | -5.7206 | 10 | 0 | 0
613.1 | 50.42 | 50.14 | -0.43 | -0.24412 | -2.4412 | 50.42 | -1 | -1 | -10 | -6.2206 | -6.2206 | 0 | 12 | 1 | 1 | -6.2206 | 10 | 0 | 0
613.15 | 50.45 | 50.17 | -0.715 | -0.34412 | -3.4412 | 50.45 | -1 | -1 | -10 | -6.7206 | -6.7206 | 0 | 12 | 1 | 1 | -6.7206 | 10 | 0 | 0
613.2 | 50.47 | 50.19 | -0.905 | -0.44412 | -4.4412 | 50.47 | -1 | -1 | -10 | -7.2206 | -7.2206 | 0 | 12 | 1 | 1 | -7.2206 | 10 | 0 | 0
613.25 | 50.5 | 50.22 | -1 | -0.54412 | -5.4412 | 50.5 | -1 | -1 | -10 | -7.7206 | -7.7206 | 0 | 12 | 1 | 1 | -7.7206 | 10 | 0 | 0
613.3 | 50.5 | 50.24 | -1 | -0.64412 | -6.4412 | 50.5 | -1 | -1 | -10 | -8.2206 | -8.2206 | 0 | 12 | 1 | 1 | -8.2206 | 10 | 0 | 0
613.35 | 50.47 | 50.27 | -1 | -0.74412 | -7.4412 | 50.5 | -1 | -1 | -10 | -8.7206 | -8.7206 | 0 | 12 | 1 | 1 | -8.7206 | 10 | 0 | 0
613.4 | 50.45 | 50.29 | -1 | -0.84412 | -8.4412 | 50.5 | -1 | -1 | -10 | -9.2206 | -9.2206 | 0 | 12 | 1 | 1 | -9.2206 | 10 | 0 | 0
613.45 | 50.42 | 50.32 | -1 | -0.94412 | -9.4412 | 50.5 | -1 | -1 | -10 | -9.7206 | -9.7206 | 0 | 12 | 1 | 1 | -9.7206 | 10 | 0 | 0
613.5 | 50.39 | 50.35 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
613.55 | 50.37 | 50.37 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
613.6 | 50.34 | 50.34 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
613.65 | 50.32 | 50.32 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
613.7 | 50.29 | 50.29 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
613.75 | 50.26 | 50.26 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
613.8 | 50.24 | 50.24 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
613.85 | 50.21 | 50.21 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
613.9 | 50.18 | 50.18 | -0.81 | -0.81 | -8.1 | 50.47 | -1 | -1 | -10 | -9.05 | -9.05 | 0 | 12 | 1 | 1 | -9.05 | 10 | 0 | 0
613.95 | 50.16 | 50.16 | -0.62 | -0.62 | -6.2 | 50.45 | -1 | -1 | -10 | -8.1 | -8.1 | 0 | 12 | 1 | 1 | -8.1 | 10 | 0 | 0
614 | 50.13 | 50.13 | -0.335 | -0.335 | -3.35 | 50.42 | -1 | -1 | -10 | -6.675 | -6.675 | 0 | 12 | 1 | 1 | -6.675 | 10 | 0 | 0
614.05 | 50.11 | 50.11 | -0.145 | -0.145 | -1.45 | 50.39 | -1 | -1 | -10 | -5.725 | -5.725 | 0 | 12 | 1 | 1 | -5.725 | 10 | 0 | 0
614.1 | 50.08 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 50.37 | -1 | -1 | -10 | -5.1912 | -5.1912 | 0 | 12 | 1 | 1 | -5.1912 | 10 | 0 | 0
614.15 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.34 | -1 | -1 | -10 | -5.1029 | -5.1029 | 0 | 12 | 1 | 1 | -5.1029 | 10 | 0 | 0
614.2 | 50.03 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 50.32 | -1 | -1 | -10 | -5.0441 | -5.0441 | 0 | 12 | 1 | 1 | -5.0441 | 10 | 0 | 0
614.25 | 50 | 50 | 0 | 0 | 0 | 50.29 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
614.3 | 50 | 50 | 0 | 0 | 0 | 50.26 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
614.35 | 50 | 50 | 0 | 0 | 0 | 50.24 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
614.4 | 50 | 50 | 0 | 0 | 0 | 50.21 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
614.45 | 50 | 50 | 0 | 0 | 0 | 50.18 | -0.81 | -0.9 | -9 | -4.5 | -4.5 | 0 | 12 | 1 | 1 | -4.5 | 10 | 0 | 0
614.5 | 50 | 50 | 0 | 0 | 0 | 50.16 | -0.62 | -0.8 | -8 | -4 | -4 | 0 | 12 | 1 | 1 | -4 | 10 | 0 | 0
614.55 | 50 | 50 | 0 | 0 | 0 | 50.13 | -0.335 | -0.7 | -7 | -3.5 | -3.5 | 0 | 12 | 1 | 1 | -3.5 | 10 | 0 | 0
614.6 | 50.01 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.6 | -6 | -3 | -3 | 0 | 12 | 1 | 1 | -3 | 10 | 0 | 0
614.65 | 50.01 | 50 | 0 | 0 | 0 | 50.08 | -0.038235 | -0.5 | -5 | -2.5 | -2.5 | 0 | 12 | 1 | 1 | -2.5 | 10 | 0 | 0
614.7 | 49.99 | 49.99 | 0 | 0 | 0 | 50.05 | -0.020588 | -0.4 | -4 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
614.75 | 49.99 | 49.99 | 0 | 0 | 0 | 50.03 | -0.0088235 | -0.3 | -3 | -1.5 | -1.5 | 0 | 12 | 1 | 1 | -1.5 | 10 | 0 | 0
614.8 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | -0.2 | -2 | -0.83824 | -0.83824 | 0 | 12 | 1 | 1 | -0.83824 | 10 | 0 | 0
614.85 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | -0.1 | -1 | -0.33824 | -0.33824 | 0 | 12 | 1 | 1 | -0.33824 | 10 | 0 | 0
614.9 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
614.95 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
615 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
615.05 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
615.1 | 49.89 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
615.15 | 49.89 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
615.2 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50.01 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
615.25 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
615.3 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
615.35 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 2.7868 | 2.7868 | 0 | 12 | 1 | 1 | 2.7868 | 10 | 0 | 0
615.4 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 2.7868 | 2.7868 | 0 | 12 | 1 | 1 | 2.7868 | 10 | 0 | 0
615.45 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 2.8456 | 2.8456 | 0 | 12 | 1 | 1 | 2.8456 | 10 | 0 | 0
615.5 | 49.94 | 49.85 | 0.525 | 0.525 | 5.25 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 2.7574 | 2.7574 | 0 | 12 | 1 | 1 | 2.7574 | 10 | 0 | 0
615.55 | 49.94 | 49.85 | 0.525 | 0.525 | 5.25 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 2.7574 | 2.7574 | 0 | 12 | 1 | 1 | 2.7574 | 10 | 0 | 0
615.6 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
615.65 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
615.7 | 49.93 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
615.75 | 49.93 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
615.8 | 49.96 | 49.85 | 0.525 | 0.525 | 5.25 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 2.6985 | 2.6985 | 0 | 12 | 1 | 1 | 2.6985 | 10 | 0 | 0
615.85 | 49.96 | 49.85 | 0.525 | 0.525 | 5.25 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 2.6985 | 2.6985 | 0 | 12 | 1 | 1 | 2.6985 | 10 | 0 | 0
615.9 | 49.99 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
615.95 | 49.99 | 49.91 | 0.044118 | 0.425 | 4.25 | 49.99 | 0 | 0 | 0 | 2.125 | 2.125 | 0 | 12 | 1 | 1 | 2.125 | 10 | 0 | 0
616 | 49.99 | 49.91 | 0.044118 | 0.325 | 3.25 | 49.99 | 0 | 0 | 0 | 1.625 | 1.625 | 0 | 12 | 1 | 1 | 1.625 | 10 | 0 | 0
616.05 | 49.99 | 49.93 | 0.032353 | 0.225 | 2.25 | 49.99 | 0 | 0 | 0 | 1.125 | 1.125 | 0 | 12 | 1 | 1 | 1.125 | 10 | 0 | 0
616.1 | 49.96 | 49.93 | 0.032353 | 0.125 | 1.25 | 49.99 | 0 | 0 | 0 | 0.625 | 0.625 | 0 | 12 | 1 | 1 | 0.625 | 10 | 0 | 0
616.15 | 49.96 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 49.99 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
616.2 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
616.25 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
616.3 | 50.05 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.058824 | 0.058824 | 0 | 12 | 1 | 1 | 0.058824 | 10 | 0 | 0
616.35 | 50.05 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
616.4 | 49.97 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
616.45 | 49.97 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
616.5 | 49.92 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
616.55 | 49.92 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
616.6 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
616.65 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
616.7 | 49.94 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
616.75 | 49.94 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
616.8 | 50.01 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
616.85 | 50.01 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
616.9 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
616.95 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
617 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
617.05 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
617.1 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
617.15 | 49.95 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
617.2 | 49.97 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
617.25 | 49.97 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
617.3 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
617.35 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
617.4 | 49.87 | 49.87 | 0.335 | 0.335 | 3.35 | 50.01 | 0 | 0 | 0 | 1.675 | 1.675 | 0 | 12 | 1 | 1 | 1.675 | 10 | 0 | 0
617.45 | 49.87 | 49.87 | 0.335 | 0.335 | 3.35 | 49.99 | 0 | 0 | 0 | 1.675 | 1.675 | 0 | 12 | 1 | 1 | 1.675 | 10 | 0 | 0
617.5 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
617.55 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 2.6691 | 2.6691 | 0 | 12 | 1 | 1 | 2.6691 | 10 | 0 | 0
617.6 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
617.65 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
617.7 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
617.75 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
617.8 | 49.84 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
617.85 | 49.84 | 49.79 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
617.9 | 49.89 | 49.79 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
617.95 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.12647 | 1.2647 | 5.6324 | 5.6324 | 0 | 12 | 1 | 1 | 5.6324 | 10 | 0 | 0
618 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.145 | 1.45 | 5.725 | 5.725 | 0 | 12 | 1 | 1 | 5.725 | 10 | 0 | 0
618.05 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.145 | 1.45 | 5.725 | 5.725 | 0 | 12 | 1 | 1 | 5.725 | 10 | 0 | 0
618.1 | 49.96 | 49.79 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
618.15 | 49.96 | 49.79 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
618.2 | 50.02 | 49.79 | 1 | 1 | 10 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 4.9853 | 4.9853 | 0 | 12 | 1 | 1 | 4.9853 | 10 | 0 | 0
618.25 | 50.02 | 49.79 | 1 | 1 | 10 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 4.9853 | 4.9853 | 0 | 12 | 1 | 1 | 4.9853 | 10 | 0 | 0
618.3 | 50.03 | 49.79 | 1 | 1 | 10 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.9559 | 4.9559 | 0 | 12 | 1 | 1 | 4.9559 | 10 | 0 | 0
618.35 | 50.03 | 49.84 | 0.62 | 0.9 | 9 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.4559 | 4.4559 | 0 | 12 | 1 | 1 | 4.4559 | 10 | 0 | 0
618.4 | 50.02 | 49.84 | 0.62 | 0.8 | 8 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 3.9559 | 3.9559 | 0 | 12 | 1 | 1 | 3.9559 | 10 | 0 | 0
618.45 | 50.02 | 49.89 | 0.145 | 0.7 | 7 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 3.4559 | 3.4559 | 0 | 12 | 1 | 1 | 3.4559 | 10 | 0 | 0
618.5 | 50.08 | 49.89 | 0.145 | 0.6 | 6 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 2.8088 | 2.8088 | 0 | 12 | 1 | 1 | 2.8088 | 10 | 0 | 0
618.55 | 50.08 | 49.89 | 0.145 | 0.5 | 5 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 2.3088 | 2.3088 | 0 | 12 | 1 | 1 | 2.3088 | 10 | 0 | 0
618.6 | 50.01 | 49.89 | 0.145 | 0.4 | 4 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 1.8088 | 1.8088 | 0 | 12 | 1 | 1 | 1.8088 | 10 | 0 | 0
618.65 | 50.01 | 49.96 | 0.014706 | 0.3 | 3 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 1.3088 | 1.3088 | 0 | 12 | 1 | 1 | 1.3088 | 10 | 0 | 0
618.7 | 49.94 | 49.94 | 0.026471 | 0.2 | 2 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.80882 | 0.80882 | 0 | 12 | 1 | 1 | 0.80882 | 10 | 0 | 0
618.75 | 49.94 | 49.94 | 0.026471 | 0.1 | 1 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.30882 | 0.30882 | 0 | 12 | 1 | 1 | 0.30882 | 10 | 0 | 0
618.8 | 50 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
618.85 | 50 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
618.9 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
618.95 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
619 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
619.05 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
619.1 | 49.92 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
619.15 | 49.92 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
619.2 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50.01 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
619.25 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
619.3 | 49.92 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
619.35 | 49.92 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
619.4 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
619.45 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
619.5 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
619.55 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
619.6 | 49.87 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
619.65 | 49.87 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
619.7 | 49.8 | 49.8 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
619.75 | 49.8 | 49.8 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
619.8 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
619.85 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
619.9 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
619.95 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
620 | 49.72 | 49.72 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
620.05 | 49.72 | 49.72 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
620.1 | 49.67 | 49.67 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
620.15 | 49.67 | 49.67 | 1 | 1 | 10 | 49.87 | 0.335 | 0.14412 | 1.4412 | 5.7206 | 5.7206 | 0 | 12 | 1 | 1 | 5.7206 | 10 | 0 | 0
620.2 | 49.65 | 49.65 | 1 | 1 | 10 | 49.87 | 0.335 | 0.24412 | 2.4412 | 6.2206 | 6.2206 | 0 | 12 | 1 | 1 | 6.2206 | 10 | 0 | 0
620.25 | 49.65 | 49.65 | 1 | 1 | 10 | 49.8 | 1 | 0.34412 | 3.4412 | 6.7206 | 6.7206 | 0 | 12 | 1 | 1 | 6.7206 | 10 | 0 | 0
620.3 | 49.59 | 49.59 | 1 | 1 | 10 | 49.8 | 1 | 0.44412 | 4.4412 | 7.2206 | 7.2206 | 0 | 12 | 1 | 1 | 7.2206 | 10 | 0 | 0
620.35 | 49.59 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.54412 | 5.4412 | 7.7206 | 7.7206 | 0 | 12 | 1 | 1 | 7.7206 | 10 | 0 | 0
620.4 | 49.66 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.64412 | 6.4412 | 8.2206 | 8.2206 | 0 | 12 | 1 | 1 | 8.2206 | 10 | 0 | 0
620.45 | 49.66 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.74412 | 7.4412 | 8.7206 | 8.7206 | 0 | 12 | 1 | 1 | 8.7206 | 10 | 0 | 0
620.5 | 49.63 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.84412 | 8.4412 | 9.2206 | 9.2206 | 0 | 12 | 1 | 1 | 9.2206 | 10 | 0 | 0
620.55 | 49.63 | 49.59 | 1 | 1 | 10 | 49.72 | 1 | 0.94412 | 9.4412 | 9.7206 | 9.7206 | 0 | 12 | 1 | 1 | 9.7206 | 10 | 0 | 0
620.6 | 49.61 | 49.59 | 1 | 1 | 10 | 49.72 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
620.65 | 49.61 | 49.59 | 1 | 1 | 10 | 49.67 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
620.7 | 49.54 | 49.54 | 1 | 1 | 10 | 49.67 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
620.75 | 49.54 | 49.54 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
620.8 | 49.46 | 49.46 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
620.85 | 49.46 | 49.46 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
620.9 | 49.45 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
620.95 | 49.45 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
621 | 49.51 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
621.05 | 49.51 | 49.45 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
621.1 | 49.5 | 49.45 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
621.15 | 49.5 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
621.2 | 49.54 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
621.25 | 49.54 | 49.45 | 1 | 1 | 10 | 49.54 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
621.3 | 49.59 | 49.45 | 1 | 1 | 10 | 49.59 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
621.35 | 49.59 | 49.45 | 1 | 1 | 10 | 49.59 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
621.4 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
621.45 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
621.5 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
621.55 | 49.61 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
621.6 | 49.53 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
621.65 | 49.53 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
621.7 | 49.54 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
621.75 | 49.54 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
621.8 | 49.61 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
621.85 | 49.61 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
621.9 | 49.66 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
621.95 | 49.66 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
622 | 49.64 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
622.05 | 49.64 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
622.1 | 49.69 | 49.53 | 1 | 1 | 10 | 49.69 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
622.15 | 49.69 | 49.53 | 1 | 1 | 10 | 49.69 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
622.2 | 49.74 | 49.53 | 1 | 1 | 10 | 49.74 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
622.25 | 49.74 | 49.54 | 1 | 1 | 10 | 49.74 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
622.3 | 49.78 | 49.54 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
622.35 | 49.78 | 49.61 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
622.4 | 49.82 | 49.61 | 1 | 1 | 10 | 49.82 | 0.81 | 0.81 | 8.1 | 9.05 | 9.05 | 0 | 12 | 1 | 1 | 9.05 | 10 | 0 | 0
622.45 | 49.82 | 49.64 | 1 | 1 | 10 | 49.82 | 0.81 | 0.81 | 8.1 | 9.05 | 9.05 | 0 | 12 | 1 | 1 | 9.05 | 10 | 0 | 0
622.5 | 49.86 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
622.55 | 49.86 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
622.6 | 49.84 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
622.65 | 49.84 | 49.69 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
622.7 | 49.91 | 49.69 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
622.75 | 49.91 | 49.74 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
622.8 | 49.97 | 49.74 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
622.85 | 49.97 | 49.78 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
622.9 | 50.03 | 49.78 | 1 | 1 | 10 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.9559 | 4.9559 | 0 | 12 | 1 | 1 | 4.9559 | 10 | 0 | 0
622.95 | 50.03 | 49.82 | 0.81 | 0.9 | 9 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.4559 | 4.4559 | 0 | 12 | 1 | 1 | 4.4559 | 10 | 0 | 0
623 | 50.05 | 49.82 | 0.81 | 0.81 | 8.1 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 3.9471 | 3.9471 | 0 | 12 | 1 | 1 | 3.9471 | 10 | 0 | 0
623.05 | 50.05 | 49.84 | 0.62 | 0.71 | 7.1 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 3.4471 | 3.4471 | 0 | 12 | 1 | 1 | 3.4471 | 10 | 0 | 0
623.1 | 50.01 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
623.15 | 50.01 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
623.2 | 49.95 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
623.25 | 49.95 | 49.91 | 0.044118 | 0.52 | 5.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.4971 | 2.4971 | 0 | 12 | 1 | 1 | 2.4971 | 10 | 0 | 0
623.3 | 49.99 | 49.91 | 0.044118 | 0.42 | 4.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 1.9971 | 1.9971 | 0 | 12 | 1 | 1 | 1.9971 | 10 | 0 | 0
623.35 | 49.99 | 49.95 | 0.020588 | 0.32 | 3.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 1.4971 | 1.4971 | 0 | 12 | 1 | 1 | 1.4971 | 10 | 0 | 0
623.4 | 49.92 | 49.92 | 0.038235 | 0.22 | 2.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.99706 | 0.99706 | 0 | 12 | 1 | 1 | 0.99706 | 10 | 0 | 0
623.45 | 49.92 | 49.92 | 0.038235 | 0.12 | 1.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.49706 | 0.49706 | 0 | 12 | 1 | 1 | 0.49706 | 10 | 0 | 0
623.5 | 49.97 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
623.55 | 49.97 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
623.6 | 50.02 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
623.65 | 50.02 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.17647 | 0.17647 | 0 | 12 | 1 | 1 | 0.17647 | 10 | 0 | 0
623.7 | 50.07 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
623.75 | 50.07 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
623.8 | 50.06 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
623.85 | 50.06 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
623.9 | 50.13 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
623.95 | 50.13 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
624 | 50.09 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
624.05 | 50.09 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6309 | -1.6309 | 0 | 12 | 1 | 1 | -1.6309 | 10 | 0 | 0
624.1 | 50.07 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6309 | -1.6309 | 0 | 12 | 1 | 1 | -1.6309 | 10 | 0 | 0
624.15 | 50.07 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6897 | -1.6897 | 0 | 12 | 1 | 1 | -1.6897 | 10 | 0 | 0
624.2 | 50.07 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6897 | -1.6897 | 0 | 12 | 1 | 1 | -1.6897 | 10 | 0 | 0
624.25 | 50.07 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.13 | -0.335 | -0.335 | -3.35 | -1.8074 | -1.8074 | 0 | 12 | 1 | 1 | -1.8074 | 10 | 0 | 0
624.3 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.13 | -0.335 | -0.335 | -3.35 | -1.7779 | -1.7779 | 0 | 12 | 1 | 1 | -1.7779 | 10 | 0 | 0
624.35 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.13 | -0.335 | -0.335 | -3.35 | -1.7779 | -1.7779 | 0 | 12 | 1 | 1 | -1.7779 | 10 | 0 | 0
624.4 | 50.01 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
624.45 | 50.01 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
624.5 | 50.07 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
624.55 | 50.07 | 50.01 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.235 | -2.35 | -1.175 | -1.175 | 0 | 12 | 1 | 1 | -1.175 | 10 | 0 | 0
624.6 | 50.05 | 50.01 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.135 | -1.35 | -0.675 | -0.675 | 0 | 12 | 1 | 1 | -0.675 | 10 | 0 | 0
624.65 | 50.05 | 50.01 | 0 | 0 | 0 | 50.07 | -0.032353 | -0.035 | -0.35 | -0.175 | -0.175 | 0 | 12 | 1 | 1 | -0.175 | 10 | 0 | 0
624.7 | 50.1 | 50.01 | 0 | 0 | 0 | 50.1 | -0.05 | -0.05 | -0.5 | -0.25 | -0.25 | 0 | 12 | 1 | 1 | -0.25 | 10 | 0 | 0
624.75 | 50.1 | 50.01 | 0 | 0 | 0 | 50.1 | -0.05 | -0.05 | -0.5 | -0.25 | -0.25 | 0 | 12 | 1 | 1 | -0.25 | 10 | 0 | 0
624.8 | 50.11 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
624.85 | 50.11 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
624.9 | 50.06 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
624.95 | 50.06 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
625 | 50.04 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
625.05 | 50.04 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
625.1 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
625.15 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
625.2 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
625.25 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
625.3 | 50.11 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
625.35 | 50.11 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
625.4 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
625.45 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
625.5 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
625.55 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
625.6 | 50.02 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.11 | -0.145 | -0.145 | -1.45 | -0.73971 | -0.73971 | 0 | 12 | 1 | 1 | -0.73971 | 10 | 0 | 0
625.65 | 50.02 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.11 | -0.145 | -0.145 | -1.45 | -0.73971 | -0.73971 | 0 | 12 | 1 | 1 | -0.73971 | 10 | 0 | 0
625.7 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
625.75 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
625.8 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
625.85 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
625.9 | 50.01 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
625.95 | 50.01 | 50 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.045 | -0.45 | -0.225 | -0.225 | 0 | 12 | 1 | 1 | -0.225 | 10 | 0 | 0
626 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
626.05 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
626.1 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
626.15 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
626.2 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.14706 | 0.14706 | 0 | 12 | 1 | 1 | 0.14706 | 10 | 0 | 0
626.25 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
626.3 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
626.35 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
626.4 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
626.45 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
626.5 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
626.55 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
626.6 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
626.65 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
626.7 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
626.75 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
626.8 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
626.85 | 50 | 50 | 0 | 0 | 0 | 50.01 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
626.9 | 49.5 | 49.5 | 1 | 1 | 10 | 50.01 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
626.95 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
627 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
627.05 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
627.1 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
627.15 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
627.2 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
627.25 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
627.3 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
627.35 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
627.4 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
627.45 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.1 | 1 | 5.5 | 5.5 | 0 | 12 | 1 | 1 | 5.5 | 10 | 0 | 0
627.5 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.2 | 2 | 6 | 6 | 0 | 12 | 1 | 1 | 6 | 10 | 0 | 0
627.55 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.3 | 3 | 6.5 | 6.5 | 0 | 12 | 1 | 1 | 6.5 | 10 | 0 | 0
627.6 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.4 | 4 | 7 | 7 | 0 | 12 | 1 | 1 | 7 | 10 | 0 | 0
627.65 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.5 | 5 | 7.5 | 7.5 | 0 | 12 | 1 | 1 | 7.5 | 10 | 0 | 0
627.7 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.6 | 6 | 8 | 8 | 0 | 12 | 1 | 1 | 8 | 10 | 0 | 0
627.75 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.7 | 7 | 8.5 | 8.5 | 0 | 12 | 1 | 1 | 8.5 | 10 | 0 | 0
627.8 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.8 | 8 | 9 | 9 | 0 | 12 | 1 | 1 | 9 | 10 | 0 | 0
627.85 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.9 | 9 | 9.5 | 9.5 | 0 | 12 | 1 | 1 | 9.5 | 10 | 0 | 0
627.9 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
627.95 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
628 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
628.05 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
628.1 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
628.15 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
628.2 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
628.25 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
628.3 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
628.35 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
628.4 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
628.45 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
628.5 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
628.55 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
628.6 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
628.65 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
628.7 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
628.75 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
628.8 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
628.85 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
628.9 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
628.95 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
629 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
629.05 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
629.1 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
629.15 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
629.2 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
629.25 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
629.3 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
629.35 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
629.4 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
629.45 | 50.5 | 50.5 | -1 | 0.9 | 9 | 50.5 | -1 | -1 | -10 | -0.5 | -0.5 | 0 | 12 | 1 | 1 | -0.5 | 10 | 0 | 0
629.5 | 50.5 | 50.5 | -1 | 0.8 | 8 | 50.5 | -1 | -1 | -10 | -1 | -1 | 0 | 12 | 1 | 1 | -1 | 10 | 0 | 0
629.55 | 50.5 | 50.5 | -1 | 0.7 | 7 | 50.5 | -1 | -1 | -10 | -1.5 | -1.5 | 0 | 12 | 1 | 1 | -1.5 | 10 | 0 | 0
629.6 | 50.5 | 50.5 | -1 | 0.6 | 6 | 50.5 | -1 | -1 | -10 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
629.65 | 50.5 | 50.5 | -1 | 0.5 | 5 | 50.5 | -1 | -1 | -10 | -2.5 | -2.5 | 0 | 12 | 1 | 1 | -2.5 | 10 | 0 | 0
629.7 | 50.5 | 50.5 | -1 | 0.4 | 4 | 50.5 | -1 | -1 | -10 | -3 | -3 | 0 | 12 | 1 | 1 | -3 | 10 | 0 | 0
629.75 | 50.5 | 50.5 | -1 | 0.3 | 3 | 50.5 | -1 | -1 | -10 | -3.5 | -3.5 | 0 | 12 | 1 | 1 | -3.5 | 10 | 0 | 0
629.8 | 50.5 | 50.5 | -1 | 0.2 | 2 | 50.5 | -1 | -1 | -10 | -4 | -4 | 0 | 12 | 1 | 1 | -4 | 10 | 0 | 0
629.85 | 50.5 | 50.5 | -1 | 0.1 | 1 | 50.5 | -1 | -1 | -10 | -4.5 | -4.5 | 0 | 12 | 1 | 1 | -4.5 | 10 | 0 | 0
629.9 | 50.5 | 50.5 | -1 | 0 | 0 | 50.5 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
629.95 | 50.5 | 50.5 | -1 | -0.1 | -1 | 50.5 | -1 | -1 | -10 | -5.5 | -5.5 | 0 | 12 | 1 | 1 | -5.5 | 10 | 0 | 0
630 | 50.5 | 50.5 | -1 | -0.2 | -2 | 50.5 | -1 | -1 | -10 | -6 | -6 | 0 | 12 | 1 | 1 | -6 | 10 | 0 | 0
630.05 | 50.5 | 50.5 | -1 | -0.3 | -3 | 50.5 | -1 | -1 | -10 | -6.5 | -6.5 | 0 | 12 | 1 | 1 | -6.5 | 10 | 0 | 0
630.1 | 50.5 | 50.5 | -1 | -0.4 | -4 | 50.5 | -1 | -1 | -10 | -7 | -7 | 0 | 12 | 1 | 1 | -7 | 10 | 0 | 0
630.15 | 50.5 | 50.5 | -1 | -0.5 | -5 | 50.5 | -1 | -1 | -10 | -7.5 | -7.5 | 0 | 12 | 1 | 1 | -7.5 | 10 | 0 | 0
630.2 | 50.5 | 50.5 | -1 | -0.6 | -6 | 50.5 | -1 | -1 | -10 | -8 | -8 | 0 | 12 | 1 | 1 | -8 | 10 | 0 | 0
630.25 | 50.5 | 50.5 | -1 | -0.7 | -7 | 50.5 | -1 | -1 | -10 | -8.5 | -8.5 | 0 | 12 | 1 | 1 | -8.5 | 10 | 0 | 0
630.3 | 50.5 | 50.5 | -1 | -0.8 | -8 | 50.5 | -1 | -1 | -10 | -9 | -9 | 0 | 12 | 1 | 1 | -9 | 10 | 0 | 0
630.35 | 50.5 | 50.5 | -1 | -0.9 | -9 | 50.5 | -1 | -1 | -10 | -9.5 | -9.5 | 0 | 12 | 1 | 1 | -9.5 | 10 | 0 | 0
630.4 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
630.45 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
630.5 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
630.55 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
630.6 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
630.65 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
630.7 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
630.75 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
630.8 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
630.85 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
630.9 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
630.95 | 50.47 | 50.47 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
631 | 50.45 | 50.45 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
631.05 | 50.42 | 50.42 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
631.1 | 50.4 | 50.4 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
631.15 | 50.37 | 50.37 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
631.2 | 50.35 | 50.35 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
631.25 | 50.32 | 50.32 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
631.3 | 50.29 | 50.29 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
631.35 | 50.27 | 50.27 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
631.4 | 50.24 | 50.24 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
631.45 | 50.22 | 50.22 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
631.5 | 50.19 | 50.19 | -0.905 | -0.905 | -9.05 | 50.47 | -1 | -1 | -10 | -9.525 | -9.525 | 0 | 12 | 1 | 1 | -9.525 | 10 | 0 | 0
631.55 | 50.17 | 50.17 | -0.715 | -0.715 | -7.15 | 50.45 | -1 | -1 | -10 | -8.575 | -8.575 | 0 | 12 | 1 | 1 | -8.575 | 10 | 0 | 0
631.6 | 50.14 | 50.14 | -0.43 | -0.43 | -4.3 | 50.42 | -1 | -1 | -10 | -7.15 | -7.15 | 0 | 12 | 1 | 1 | -7.15 | 10 | 0 | 0
631.65 | 50.12 | 50.12 | -0.24 | -0.24 | -2.4 | 50.4 | -1 | -1 | -10 | -6.2 | -6.2 | 0 | 12 | 1 | 1 | -6.2 | 10 | 0 | 0
631.7 | 50.09 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 50.37 | -1 | -1 | -10 | -5.2206 | -5.2206 | 0 | 12 | 1 | 1 | -5.2206 | 10 | 0 | 0
631.75 | 50.06 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.35 | -1 | -1 | -10 | -5.1324 | -5.1324 | 0 | 12 | 1 | 1 | -5.1324 | 10 | 0 | 0
631.8 | 50.04 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.32 | -1 | -1 | -10 | -5.0735 | -5.0735 | 0 | 12 | 1 | 1 | -5.0735 | 10 | 0 | 0
631.85 | 50.01 | 50.01 | 0 | 0 | 0 | 50.29 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
631.9 | 49.99 | 49.99 | 0 | 0 | 0 | 50.27 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
631.95 | 49.96 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.24 | -1 | -1 | -10 | -4.9265 | -4.9265 | 0 | 12 | 1 | 1 | -4.9265 | 10 | 0 | 0
632 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.22 | -1 | -1 | -10 | -4.8676 | -4.8676 | 0 | 12 | 1 | 1 | -4.8676 | 10 | 0 | 0
632.05 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.19 | -0.905 | -0.905 | -9.05 | -4.3044 | -4.3044 | 0 | 12 | 1 | 1 | -4.3044 | 10 | 0 | 0
632.1 | 49.88 | 49.88 | 0.24 | 0.24 | 2.4 | 50.17 | -0.715 | -0.805 | -8.05 | -2.825 | -2.825 | 0 | 12 | 1 | 1 | -2.825 | 10 | 0 | 0
632.15 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.14 | -0.43 | -0.705 | -7.05 | -1.375 | -1.375 | 0 | 12 | 1 | 1 | -1.375 | 10 | 0 | 0
632.2 | 49.83 | 49.83 | 0.715 | 0.715 | 7.15 | 50.12 | -0.24 | -0.605 | -6.05 | 0.55 | 0.55 | 0 | 12 | 1 | 1 | 0.55 | 10 | 0 | 0
632.25 | 49.81 | 49.81 | 0.905 | 0.905 | 9.05 | 50.09 | -0.044118 | -0.505 | -5.05 | 2 | 2 | 0 | 12 | 1 | 1 | 2 | 10 | 0 | 0
632.3 | 49.78 | 49.78 | 1 | 1 | 10 | 50.06 | -0.026471 | -0.405 | -4.05 | 2.975 | 2.975 | 0 | 12 | 1 | 1 | 2.975 | 10 | 0 | 0
632.35 | 49.76 | 49.76 | 1 | 1 | 10 | 50.04 | -0.014706 | -0.305 | -3.05 | 3.475 | 3.475 | 0 | 12 | 1 | 1 | 3.475 | 10 | 0 | 0
632.4 | 49.73 | 49.73 | 1 | 1 | 10 | 50.01 | 0 | -0.205 | -2.05 | 3.975 | 3.975 | 0 | 12 | 1 | 1 | 3.975 | 10 | 0 | 0
632.45 | 49.71 | 49.71 | 1 | 1 | 10 | 49.99 | 0 | -0.105 | -1.05 | 4.475 | 4.475 | 0 | 12 | 1 | 1 | 4.475 | 10 | 0 | 0
632.5 | 49.68 | 49.68 | 1 | 1 | 10 | 49.96 | 0.014706 | -0.005 | -0.05 | 4.975 | 4.975 | 0 | 12 | 1 | 1 | 4.975 | 10 | 0 | 0
632.55 | 49.65 | 49.65 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
632.6 | 49.63 | 49.63 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
632.65 | 49.6 | 49.6 | 1 | 1 | 10 | 49.88 | 0.24 | 0.14412 | 1.4412 | 5.7206 | 5.7206 | 0 | 12 | 1 | 1 | 5.7206 | 10 | 0 | 0
632.7 | 49.58 | 49.58 | 1 | 1 | 10 | 49.86 | 0.43 | 0.24412 | 2.4412 | 6.2206 | 6.2206 | 0 | 12 | 1 | 1 | 6.2206 | 10 | 0 | 0
632.75 | 49.55 | 49.55 | 1 | 1 | 10 | 49.83 | 0.715 | 0.34412 | 3.4412 | 6.7206 | 6.7206 | 0 | 12 | 1 | 1 | 6.7206 | 10 | 0 | 0
632.8 | 49.53 | 49.53 | 1 | 1 | 10 | 49.81 | 0.905 | 0.44412 | 4.4412 | 7.2206 | 7.2206 | 0 | 12 | 1 | 1 | 7.2206 | 10 | 0 | 0
632.85 | 49.5 | 49.5 | 1 | 1 | 10 | 49.78 | 1 | 0.54412 | 5.4412 | 7.7206 | 7.7206 | 0 | 12 | 1 | 1 | 7.7206 | 10 | 0 | 0
632.9 | 49.5 | 49.5 | 1 | 1 | 10 | 49.76 | 1 | 0.64412 | 6.4412 | 8.2206 | 8.2206 | 0 | 12 | 1 | 1 | 8.2206 | 10 | 0 | 0
632.95 | 49.53 | 49.5 | 1 | 1 | 10 | 49.73 | 1 | 0.74412 | 7.4412 | 8.7206 | 8.7206 | 0 | 12 | 1 | 1 | 8.7206 | 10 | 0 | 0
633 | 49.55 | 49.5 | 1 | 1 | 10 | 49.71 | 1 | 0.84412 | 8.4412 | 9.2206 | 9.2206 | 0 | 12 | 1 | 1 | 9.2206 | 10 | 0 | 0
633.05 | 49.58 | 49.5 | 1 | 1 | 10 | 49.68 | 1 | 0.94412 | 9.4412 | 9.7206 | 9.7206 | 0 | 12 | 1 | 1 | 9.7206 | 10 | 0 | 0
633.1 | 49.6 | 49.5 | 1 | 1 | 10 | 49.65 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
633.15 | 49.63 | 49.5 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
633.2 | 49.65 | 49.5 | 1 | 1 | 10 | 49.65 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
633.25 | 49.68 | 49.5 | 1 | 1 | 10 | 49.68 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
633.3 | 49.71 | 49.5 | 1 | 1 | 10 | 49.71 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
633.35 | 49.73 | 49.5 | 1 | 1 | 10 | 49.73 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
633.4 | 49.76 | 49.5 | 1 | 1 | 10 | 49.76 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
633.45 | 49.78 | 49.5 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
633.5 | 49.81 | 49.53 | 1 | 1 | 10 | 49.81 | 0.905 | 0.905 | 9.05 | 9.525 | 9.525 | 0 | 12 | 1 | 1 | 9.525 | 10 | 0 | 0
633.55 | 49.83 | 49.55 | 1 | 1 | 10 | 49.83 | 0.715 | 0.715 | 7.15 | 8.575 | 8.575 | 0 | 12 | 1 | 1 | 8.575 | 10 | 0 | 0
633.6 | 49.86 | 49.58 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
633.65 | 49.88 | 49.6 | 1 | 1 | 10 | 49.88 | 0.24 | 0.24 | 2.4 | 6.2 | 6.2 | 0 | 12 | 1 | 1 | 6.2 | 10 | 0 | 0
633.7 | 49.91 | 49.63 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
633.75 | 49.94 | 49.65 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
633.8 | 49.96 | 49.68 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
633.85 | 49.99 | 49.71 | 1 | 1 | 10 | 49.99 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
633.9 | 50.01 | 49.73 | 1 | 1 | 10 | 50.01 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
633.95 | 50.04 | 49.76 | 1 | 1 | 10 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 4.9265 | 4.9265 | 0 | 12 | 1 | 1 | 4.9265 | 10 | 0 | 0
634 | 50.06 | 49.78 | 1 | 1 | 10 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 4.8676 | 4.8676 | 0 | 12 | 1 | 1 | 4.8676 | 10 | 0 | 0
634.05 | 50.09 | 49.81 | 0.905 | 0.905 | 9.05 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 4.3044 | 4.3044 | 0 | 12 | 1 | 1 | 4.3044 | 10 | 0 | 0
634.1 | 50.12 | 49.83 | 0.715 | 0.805 | 8.05 | 50.12 | -0.24 | -0.24 | -2.4 | 2.825 | 2.825 | 0 | 12 | 1 | 1 | 2.825 | 10 | 0 | 0
634.15 | 50.14 | 49.86 | 0.43 | 0.705 | 7.05 | 50.14 | -0.43 | -0.43 | -4.3 | 1.375 | 1.375 | 0 | 12 | 1 | 1 | 1.375 | 10 | 0 | 0
634.2 | 50.17 | 49.88 | 0.24 | 0.605 | 6.05 | 50.17 | -0.715 | -0.715 | -7.15 | -0.55 | -0.55 | 0 | 12 | 1 | 1 | -0.55 | 10 | 0 | 0
634.25 | 50.19 | 49.91 | 0.044118 | 0.505 | 5.05 | 50.19 | -0.905 | -0.905 | -9.05 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
634.3 | 50.22 | 49.94 | 0.026471 | 0.405 | 4.05 | 50.22 | -1 | -1 | -10 | -2.975 | -2.975 | 0 | 12 | 1 | 1 | -2.975 | 10 | 0 | 0
634.35 | 50.24 | 49.96 | 0.014706 | 0.305 | 3.05 | 50.24 | -1 | -1 | -10 | -3.475 | -3.475 | 0 | 12 | 1 | 1 | -3.475 | 10 | 0 | 0
634.4 | 50.27 | 49.99 | 0 | 0.205 | 2.05 | 50.27 | -1 | -1 | -10 | -3.975 | -3.975 | 0 | 12 | 1 | 1 | -3.975 | 10 | 0 | 0
634.45 | 50.29 | 50.01 | 0 | 0.105 | 1.05 | 50.29 | -1 | -1 | -10 | -4.475 | -4.475 | 0 | 12 | 1 | 1 | -4.475 | 10 | 0 | 0
634.5 | 50.32 | 50.04 | -0.014706 | 0.005 | 0.05 | 50.32 | -1 | -1 | -10 | -4.975 | -4.975 | 0 | 12 | 1 | 1 | -4.975 | 10 | 0 | 0
634.55 | 50.35 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.35 | -1 | -1 | -10 | -5.1324 | -5.1324 | 0 | 12 | 1 | 1 | -5.1324 | 10 | 0 | 0
634.6 | 50.37 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 50.37 | -1 | -1 | -10 | -5.2206 | -5.2206 | 0 | 12 | 1 | 1 | -5.2206 | 10 | 0 | 0
634.65 | 50.4 | 50.12 | -0.24 | -0.14412 | -1.4412 | 50.4 | -1 | -1 | -10 | -5.7206 | -5.7206 | 0 | 12 | 1 | 1 | -5.7206 | 10 | 0 | 0
634.7 | 50.42 | 50.14 | -0.43 | -0.24412 | -2.4412 | 50.42 | -1 | -1 | -10 | -6.2206 | -6.2206 | 0 | 12 | 1 | 1 | -6.2206 | 10 | 0 | 0
634.75 | 50.45 | 50.17 | -0.715 | -0.34412 | -3.4412 | 50.45 | -1 | -1 | -10 | -6.7206 | -6.7206 | 0 | 12 | 1 | 1 | -6.7206 | 10 | 0 | 0
634.8 | 50.47 | 50.19 | -0.905 | -0.44412 | -4.4412 | 50.47 | -1 | -1 | -10 | -7.2206 | -7.2206 | 0 | 12 | 1 | 1 | -7.2206 | 10 | 0 | 0
634.85 | 50.5 | 50.22 | -1 | -0.54412 | -5.4412 | 50.5 | -1 | -1 | -10 | -7.7206 | -7.7206 | 0 | 12 | 1 | 1 | -7.7206 | 10 | 0 | 0
634.9 | 50.5 | 50.24 | -1 | -0.64412 | -6.4412 | 50.5 | -1 | -1 | -10 | -8.2206 | -8.2206 | 0 | 12 | 1 | 1 | -8.2206 | 10 | 0 | 0
634.95 | 50.47 | 50.27 | -1 | -0.74412 | -7.4412 | 50.5 | -1 | -1 | -10 | -8.7206 | -8.7206 | 0 | 12 | 1 | 1 | -8.7206 | 10 | 0 | 0
635 | 50.45 | 50.29 | -1 | -0.84412 | -8.4412 | 50.5 | -1 | -1 | -10 | -9.2206 | -9.2206 | 0 | 12 | 1 | 1 | -9.2206 | 10 | 0 | 0
635.05 | 50.42 | 50.32 | -1 | -0.94412 | -9.4412 | 50.5 | -1 | -1 | -10 | -9.7206 | -9.7206 | 0 | 12 | 1 | 1 | -9.7206 | 10 | 0 | 0
635.1 | 50.39 | 50.35 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
635.15 | 50.37 | 50.37 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
635.2 | 50.34 | 50.34 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
635.25 | 50.32 | 50.32 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
635.3 | 50.29 | 50.29 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
635.35 | 50.26 | 50.26 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
635.4 | 50.24 | 50.24 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
635.45 | 50.21 | 50.21 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
635.5 | 50.18 | 50.18 | -0.81 | -0.81 | -8.1 | 50.47 | -1 | -1 | -10 | -9.05 | -9.05 | 0 | 12 | 1 | 1 | -9.05 | 10 | 0 | 0
635.55 | 50.16 | 50.16 | -0.62 | -0.62 | -6.2 | 50.45 | -1 | -1 | -10 | -8.1 | -8.1 | 0 | 12 | 1 | 1 | -8.1 | 10 | 0 | 0
635.6 | 50.13 | 50.13 | -0.335 | -0.335 | -3.35 | 50.42 | -1 | -1 | -10 | -6.675 | -6.675 | 0 | 12 | 1 | 1 | -6.675 | 10 | 0 | 0
635.65 | 50.11 | 50.11 | -0.145 | -0.145 | -1.45 | 50.39 | -1 | -1 | -10 | -5.725 | -5.725 | 0 | 12 | 1 | 1 | -5.725 | 10 | 0 | 0
635.7 | 50.08 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 50.37 | -1 | -1 | -10 | -5.1912 | -5.1912 | 0 | 12 | 1 | 1 | -5.1912 | 10 | 0 | 0
635.75 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.34 | -1 | -1 | -10 | -5.1029 | -5.1029 | 0 | 12 | 1 | 1 | -5.1029 | 10 | 0 | 0
635.8 | 50.03 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 50.32 | -1 | -1 | -10 | -5.0441 | -5.0441 | 0 | 12 | 1 | 1 | -5.0441 | 10 | 0 | 0
635.85 | 50 | 50 | 0 | 0 | 0 | 50.29 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
635.9 | 50 | 50 | 0 | 0 | 0 | 50.26 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
635.95 | 50 | 50 | 0 | 0 | 0 | 50.24 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
636 | 50 | 50 | 0 | 0 | 0 | 50.21 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
636.05 | 50 | 50 | 0 | 0 | 0 | 50.18 | -0.81 | -0.9 | -9 | -4.5 | -4.5 | 0 | 12 | 1 | 1 | -4.5 | 10 | 0 | 0
636.1 | 50 | 50 | 0 | 0 | 0 | 50.16 | -0.62 | -0.8 | -8 | -4 | -4 | 0 | 12 | 1 | 1 | -4 | 10 | 0 | 0
636.15 | 50 | 50 | 0 | 0 | 0 | 50.13 | -0.335 | -0.7 | -7 | -3.5 | -3.5 | 0 | 12 | 1 | 1 | -3.5 | 10 | 0 | 0
636.2 | 50.01 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.6 | -6 | -3 | -3 | 0 | 12 | 1 | 1 | -3 | 10 | 0 | 0
636.25 | 50.01 | 50 | 0 | 0 | 0 | 50.08 | -0.038235 | -0.5 | -5 | -2.5 | -2.5 | 0 | 12 | 1 | 1 | -2.5 | 10 | 0 | 0
636.3 | 49.99 | 49.99 | 0 | 0 | 0 | 50.05 | -0.020588 | -0.4 | -4 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
636.35 | 49.99 | 49.99 | 0 | 0 | 0 | 50.03 | -0.0088235 | -0.3 | -3 | -1.5 | -1.5 | 0 | 12 | 1 | 1 | -1.5 | 10 | 0 | 0
636.4 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | -0.2 | -2 | -0.83824 | -0.83824 | 0 | 12 | 1 | 1 | -0.83824 | 10 | 0 | 0
636.45 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | -0.1 | -1 | -0.33824 | -0.33824 | 0 | 12 | 1 | 1 | -0.33824 | 10 | 0 | 0
636.5 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
636.55 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
636.6 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
636.65 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
636.7 | 49.89 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
636.75 | 49.89 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
636.8 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50.01 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
636.85 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
636.9 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
636.95 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 2.7868 | 2.7868 | 0 | 12 | 1 | 1 | 2.7868 | 10 | 0 | 0
637 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 2.7868 | 2.7868 | 0 | 12 | 1 | 1 | 2.7868 | 10 | 0 | 0
637.05 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 2.8456 | 2.8456 | 0 | 12 | 1 | 1 | 2.8456 | 10 | 0 | 0
637.1 | 49.94 | 49.85 | 0.525 | 0.525 | 5.25 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 2.7574 | 2.7574 | 0 | 12 | 1 | 1 | 2.7574 | 10 | 0 | 0
637.15 | 49.94 | 49.85 | 0.525 | 0.525 | 5.25 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 2.7574 | 2.7574 | 0 | 12 | 1 | 1 | 2.7574 | 10 | 0 | 0
637.2 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
637.25 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
637.3 | 49.93 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
637.35 | 49.93 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
637.4 | 49.96 | 49.85 | 0.525 | 0.525 | 5.25 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 2.6985 | 2.6985 | 0 | 12 | 1 | 1 | 2.6985 | 10 | 0 | 0
637.45 | 49.96 | 49.85 | 0.525 | 0.525 | 5.25 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 2.6985 | 2.6985 | 0 | 12 | 1 | 1 | 2.6985 | 10 | 0 | 0
637.5 | 49.99 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
637.55 | 49.99 | 49.91 | 0.044118 | 0.425 | 4.25 | 49.99 | 0 | 0 | 0 | 2.125 | 2.125 | 0 | 12 | 1 | 1 | 2.125 | 10 | 0 | 0
637.6 | 49.99 | 49.91 | 0.044118 | 0.325 | 3.25 | 49.99 | 0 | 0 | 0 | 1.625 | 1.625 | 0 | 12 | 1 | 1 | 1.625 | 10 | 0 | 0
637.65 | 49.99 | 49.93 | 0.032353 | 0.225 | 2.25 | 49.99 | 0 | 0 | 0 | 1.125 | 1.125 | 0 | 12 | 1 | 1 | 1.125 | 10 | 0 | 0
637.7 | 49.96 | 49.93 | 0.032353 | 0.125 | 1.25 | 49.99 | 0 | 0 | 0 | 0.625 | 0.625 | 0 | 12 | 1 | 1 | 0.625 | 10 | 0 | 0
637.75 | 49.96 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 49.99 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
637.8 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
637.85 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
637.9 | 50.05 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.058824 | 0.058824 | 0 | 12 | 1 | 1 | 0.058824 | 10 | 0 | 0
637.95 | 50.05 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
638 | 49.97 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
638.05 | 49.97 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
638.1 | 49.92 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
638.15 | 49.92 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
638.2 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
638.25 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
638.3 | 49.94 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
638.35 | 49.94 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
638.4 | 50.01 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
638.45 | 50.01 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
638.5 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
638.55 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
638.6 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
638.65 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
638.7 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
638.75 | 49.95 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
638.8 | 49.97 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
638.85 | 49.97 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
638.9 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
638.95 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
639 | 49.87 | 49.87 | 0.335 | 0.335 | 3.35 | 50.01 | 0 | 0 | 0 | 1.675 | 1.675 | 0 | 12 | 1 | 1 | 1.675 | 10 | 0 | 0
639.05 | 49.87 | 49.87 | 0.335 | 0.335 | 3.35 | 49.99 | 0 | 0 | 0 | 1.675 | 1.675 | 0 | 12 | 1 | 1 | 1.675 | 10 | 0 | 0
639.1 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
639.15 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 2.6691 | 2.6691 | 0 | 12 | 1 | 1 | 2.6691 | 10 | 0 | 0
639.2 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
639.25 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
639.3 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
639.35 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
639.4 | 49.84 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
639.45 | 49.84 | 49.79 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
639.5 | 49.89 | 49.79 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
639.55 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.12647 | 1.2647 | 5.6324 | 5.6324 | 0 | 12 | 1 | 1 | 5.6324 | 10 | 0 | 0
639.6 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.145 | 1.45 | 5.725 | 5.725 | 0 | 12 | 1 | 1 | 5.725 | 10 | 0 | 0
639.65 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.145 | 1.45 | 5.725 | 5.725 | 0 | 12 | 1 | 1 | 5.725 | 10 | 0 | 0
639.7 | 49.96 | 49.79 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
639.75 | 49.96 | 49.79 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
639.8 | 50.02 | 49.79 | 1 | 1 | 10 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 4.9853 | 4.9853 | 0 | 12 | 1 | 1 | 4.9853 | 10 | 0 | 0
639.85 | 50.02 | 49.79 | 1 | 1 | 10 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 4.9853 | 4.9853 | 0 | 12 | 1 | 1 | 4.9853 | 10 | 0 | 0
639.9 | 50.03 | 49.79 | 1 | 1 | 10 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.9559 | 4.9559 | 0 | 12 | 1 | 1 | 4.9559 | 10 | 0 | 0
639.95 | 50.03 | 49.84 | 0.62 | 0.9 | 9 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.4559 | 4.4559 | 0 | 12 | 1 | 1 | 4.4559 | 10 | 0 | 0
640 | 50.02 | 49.84 | 0.62 | 0.8 | 8 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 3.9559 | 3.9559 | 0 | 12 | 1 | 1 | 3.9559 | 10 | 0 | 0
640.05 | 50.02 | 49.89 | 0.145 | 0.7 | 7 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 3.4559 | 3.4559 | 0 | 12 | 1 | 1 | 3.4559 | 10 | 0 | 0
640.1 | 50.08 | 49.89 | 0.145 | 0.6 | 6 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 2.8088 | 2.8088 | 0 | 12 | 1 | 1 | 2.8088 | 10 | 0 | 0
640.15 | 50.08 | 49.89 | 0.145 | 0.5 | 5 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 2.3088 | 2.3088 | 0 | 12 | 1 | 1 | 2.3088 | 10 | 0 | 0
640.2 | 50.01 | 49.89 | 0.145 | 0.4 | 4 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 1.8088 | 1.8088 | 0 | 12 | 1 | 1 | 1.8088 | 10 | 0 | 0
640.25 | 50.01 | 49.96 | 0.014706 | 0.3 | 3 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 1.3088 | 1.3088 | 0 | 12 | 1 | 1 | 1.3088 | 10 | 0 | 0
640.3 | 49.94 | 49.94 | 0.026471 | 0.2 | 2 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.80882 | 0.80882 | 0 | 12 | 1 | 1 | 0.80882 | 10 | 0 | 0
640.35 | 49.94 | 49.94 | 0.026471 | 0.1 | 1 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.30882 | 0.30882 | 0 | 12 | 1 | 1 | 0.30882 | 10 | 0 | 0
640.4 | 50 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
640.45 | 50 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
640.5 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
640.55 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
640.6 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
640.65 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
640.7 | 49.92 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
640.75 | 49.92 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
640.8 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50.01 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
640.85 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
640.9 | 49.92 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
640.95 | 49.92 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
641 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
641.05 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
641.1 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
641.15 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
641.2 | 49.87 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
641.25 | 49.87 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
641.3 | 49.8 | 49.8 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
641.35 | 49.8 | 49.8 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
641.4 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
641.45 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
641.5 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
641.55 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
641.6 | 49.72 | 49.72 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
641.65 | 49.72 | 49.72 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
641.7 | 49.67 | 49.67 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
641.75 | 49.67 | 49.67 | 1 | 1 | 10 | 49.87 | 0.335 | 0.14412 | 1.4412 | 5.7206 | 5.7206 | 0 | 12 | 1 | 1 | 5.7206 | 10 | 0 | 0
641.8 | 49.65 | 49.65 | 1 | 1 | 10 | 49.87 | 0.335 | 0.24412 | 2.4412 | 6.2206 | 6.2206 | 0 | 12 | 1 | 1 | 6.2206 | 10 | 0 | 0
641.85 | 49.65 | 49.65 | 1 | 1 | 10 | 49.8 | 1 | 0.34412 | 3.4412 | 6.7206 | 6.7206 | 0 | 12 | 1 | 1 | 6.7206 | 10 | 0 | 0
641.9 | 49.59 | 49.59 | 1 | 1 | 10 | 49.8 | 1 | 0.44412 | 4.4412 | 7.2206 | 7.2206 | 0 | 12 | 1 | 1 | 7.2206 | 10 | 0 | 0
641.95 | 49.59 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.54412 | 5.4412 | 7.7206 | 7.7206 | 0 | 12 | 1 | 1 | 7.7206 | 10 | 0 | 0
642 | 49.66 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.64412 | 6.4412 | 8.2206 | 8.2206 | 0 | 12 | 1 | 1 | 8.2206 | 10 | 0 | 0
642.05 | 49.66 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.74412 | 7.4412 | 8.7206 | 8.7206 | 0 | 12 | 1 | 1 | 8.7206 | 10 | 0 | 0
642.1 | 49.63 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.84412 | 8.4412 | 9.2206 | 9.2206 | 0 | 12 | 1 | 1 | 9.2206 | 10 | 0 | 0
642.15 | 49.63 | 49.59 | 1 | 1 | 10 | 49.72 | 1 | 0.94412 | 9.4412 | 9.7206 | 9.7206 | 0 | 12 | 1 | 1 | 9.7206 | 10 | 0 | 0
642.2 | 49.61 | 49.59 | 1 | 1 | 10 | 49.72 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
642.25 | 49.61 | 49.59 | 1 | 1 | 10 | 49.67 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
642.3 | 49.54 | 49.54 | 1 | 1 | 10 | 49.67 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
642.35 | 49.54 | 49.54 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
642.4 | 49.46 | 49.46 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
642.45 | 49.46 | 49.46 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
642.5 | 49.45 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
642.55 | 49.45 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
642.6 | 49.51 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
642.65 | 49.51 | 49.45 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
642.7 | 49.5 | 49.45 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
642.75 | 49.5 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
642.8 | 49.54 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
642.85 | 49.54 | 49.45 | 1 | 1 | 10 | 49.54 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
642.9 | 49.59 | 49.45 | 1 | 1 | 10 | 49.59 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
642.95 | 49.59 | 49.45 | 1 | 1 | 10 | 49.59 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
643 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
643.05 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
643.1 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
643.15 | 49.61 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
643.2 | 49.53 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
643.25 | 49.53 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
643.3 | 49.54 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
643.35 | 49.54 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
643.4 | 49.61 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
643.45 | 49.61 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
643.5 | 49.66 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
643.55 | 49.66 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
643.6 | 49.64 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
643.65 | 49.64 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
643.7 | 49.69 | 49.53 | 1 | 1 | 10 | 49.69 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
643.75 | 49.69 | 49.53 | 1 | 1 | 10 | 49.69 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
643.8 | 49.74 | 49.53 | 1 | 1 | 10 | 49.74 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
643.85 | 49.74 | 49.54 | 1 | 1 | 10 | 49.74 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
643.9 | 49.78 | 49.54 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
643.95 | 49.78 | 49.61 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
644 | 49.82 | 49.61 | 1 | 1 | 10 | 49.82 | 0.81 | 0.81 | 8.1 | 9.05 | 9.05 | 0 | 12 | 1 | 1 | 9.05 | 10 | 0 | 0
644.05 | 49.82 | 49.64 | 1 | 1 | 10 | 49.82 | 0.81 | 0.81 | 8.1 | 9.05 | 9.05 | 0 | 12 | 1 | 1 | 9.05 | 10 | 0 | 0
644.1 | 49.86 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
644.15 | 49.86 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
644.2 | 49.84 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
644.25 | 49.84 | 49.69 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
644.3 | 49.91 | 49.69 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
644.35 | 49.91 | 49.74 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
644.4 | 49.97 | 49.74 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
644.45 | 49.97 | 49.78 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
644.5 | 50.03 | 49.78 | 1 | 1 | 10 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.9559 | 4.9559 | 0 | 12 | 1 | 1 | 4.9559 | 10 | 0 | 0
644.55 | 50.03 | 49.82 | 0.81 | 0.9 | 9 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.4559 | 4.4559 | 0 | 12 | 1 | 1 | 4.4559 | 10 | 0 | 0
644.6 | 50.05 | 49.82 | 0.81 | 0.81 | 8.1 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 3.9471 | 3.9471 | 0 | 12 | 1 | 1 | 3.9471 | 10 | 0 | 0
644.65 | 50.05 | 49.84 | 0.62 | 0.71 | 7.1 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 3.4471 | 3.4471 | 0 | 12 | 1 | 1 | 3.4471 | 10 | 0 | 0
644.7 | 50.01 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
644.75 | 50.01 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
644.8 | 49.95 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
644.85 | 49.95 | 49.91 | 0.044118 | 0.52 | 5.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.4971 | 2.4971 | 0 | 12 | 1 | 1 | 2.4971 | 10 | 0 | 0
644.9 | 49.99 | 49.91 | 0.044118 | 0.42 | 4.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 1.9971 | 1.9971 | 0 | 12 | 1 | 1 | 1.9971 | 10 | 0 | 0
644.95 | 49.99 | 49.95 | 0.020588 | 0.32 | 3.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 1.4971 | 1.4971 | 0 | 12 | 1 | 1 | 1.4971 | 10 | 0 | 0
645 | 49.92 | 49.92 | 0.038235 | 0.22 | 2.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.99706 | 0.99706 | 0 | 12 | 1 | 1 | 0.99706 | 10 | 0 | 0
645.05 | 49.92 | 49.92 | 0.038235 | 0.12 | 1.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.49706 | 0.49706 | 0 | 12 | 1 | 1 | 0.49706 | 10 | 0 | 0
645.1 | 49.97 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
645.15 | 49.97 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
645.2 | 50.02 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
645.25 | 50.02 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.17647 | 0.17647 | 0 | 12 | 1 | 1 | 0.17647 | 10 | 0 | 0
645.3 | 50.07 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
645.35 | 50.07 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
645.4 | 50.06 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
645.45 | 50.06 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
645.5 | 50.13 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
645.55 | 50.13 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
645.6 | 50.09 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
645.65 | 50.09 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6309 | -1.6309 | 0 | 12 | 1 | 1 | -1.6309 | 10 | 0 | 0
645.7 | 50.07 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6309 | -1.6309 | 0 | 12 | 1 | 1 | -1.6309 | 10 | 0 | 0
645.75 | 50.07 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6897 | -1.6897 | 0 | 12 | 1 | 1 | -1.6897 | 10 | 0 | 0
645.8 | 50.07 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6897 | -1.6897 | 0 | 12 | 1 | 1 | -1.6897 | 10 | 0 | 0
645.85 | 50.07 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.13 | -0.335 | -0.335 | -3.35 | -1.8074 | -1.8074 | 0 | 12 | 1 | 1 | -1.8074 | 10 | 0 | 0
645.9 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.13 | -0.335 | -0.335 | -3.35 | -1.7779 | -1.7779 | 0 | 12 | 1 | 1 | -1.7779 | 10 | 0 | 0
645.95 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.13 | -0.335 | -0.335 | -3.35 | -1.7779 | -1.7779 | 0 | 12 | 1 | 1 | -1.7779 | 10 | 0 | 0
646 | 50.01 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
646.05 | 50.01 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
646.1 | 50.07 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
646.15 | 50.07 | 50.01 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.235 | -2.35 | -1.175 | -1.175 | 0 | 12 | 1 | 1 | -1.175 | 10 | 0 | 0
646.2 | 50.05 | 50.01 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.135 | -1.35 | -0.675 | -0.675 | 0 | 12 | 1 | 1 | -0.675 | 10 | 0 | 0
646.25 | 50.05 | 50.01 | 0 | 0 | 0 | 50.07 | -0.032353 | -0.035 | -0.35 | -0.175 | -0.175 | 0 | 12 | 1 | 1 | -0.175 | 10 | 0 | 0
646.3 | 50.1 | 50.01 | 0 | 0 | 0 | 50.1 | -0.05 | -0.05 | -0.5 | -0.25 | -0.25 | 0 | 12 | 1 | 1 | -0.25 | 10 | 0 | 0
646.35 | 50.1 | 50.01 | 0 | 0 | 0 | 50.1 | -0.05 | -0.05 | -0.5 | -0.25 | -0.25 | 0 | 12 | 1 | 1 | -0.25 | 10 | 0 | 0
646.4 | 50.11 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
646.45 | 50.11 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
646.5 | 50.06 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
646.55 | 50.06 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
646.6 | 50.04 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
646.65 | 50.04 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
646.7 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
646.75 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
646.8 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
646.85 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
646.9 | 50.11 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
646.95 | 50.11 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
647 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
647.05 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
647.1 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
647.15 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
647.2 | 50.02 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.11 | -0.145 | -0.145 | -1.45 | -0.73971 | -0.73971 | 0 | 12 | 1 | 1 | -0.73971 | 10 | 0 | 0
647.25 | 50.02 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.11 | -0.145 | -0.145 | -1.45 | -0.73971 | -0.73971 | 0 | 12 | 1 | 1 | -0.73971 | 10 | 0 | 0
647.3 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
647.35 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
647.4 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
647.45 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
647.5 | 50.01 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
647.55 | 50.01 | 50 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.045 | -0.45 | -0.225 | -0.225 | 0 | 12 | 1 | 1 | -0.225 | 10 | 0 | 0
647.6 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
647.65 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
647.7 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
647.75 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
647.8 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.14706 | 0.14706 | 0 | 12 | 1 | 1 | 0.14706 | 10 | 0 | 0
647.85 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
647.9 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
647.95 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
648 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
648.05 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
648.1 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
648.15 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
648.2 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
648.25 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
648.3 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
648.35 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
648.4 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
648.45 | 50 | 50 | 0 | 0 | 0 | 50.01 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
648.5 | 49.5 | 49.5 | 1 | 1 | 10 | 50.01 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
648.55 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
648.6 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
648.65 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
648.7 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
648.75 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
648.8 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
648.85 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
648.9 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
648.95 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
649 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
649.05 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.1 | 1 | 5.5 | 5.5 | 0 | 12 | 1 | 1 | 5.5 | 10 | 0 | 0
649.1 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.2 | 2 | 6 | 6 | 0 | 12 | 1 | 1 | 6 | 10 | 0 | 0
649.15 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.3 | 3 | 6.5 | 6.5 | 0 | 12 | 1 | 1 | 6.5 | 10 | 0 | 0
649.2 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.4 | 4 | 7 | 7 | 0 | 12 | 1 | 1 | 7 | 10 | 0 | 0
649.25 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.5 | 5 | 7.5 | 7.5 | 0 | 12 | 1 | 1 | 7.5 | 10 | 0 | 0
649.3 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.6 | 6 | 8 | 8 | 0 | 12 | 1 | 1 | 8 | 10 | 0 | 0
649.35 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.7 | 7 | 8.5 | 8.5 | 0 | 12 | 1 | 1 | 8.5 | 10 | 0 | 0
649.4 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.8 | 8 | 9 | 9 | 0 | 12 | 1 | 1 | 9 | 10 | 0 | 0
649.45 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.9 | 9 | 9.5 | 9.5 | 0 | 12 | 1 | 1 | 9.5 | 10 | 0 | 0
649.5 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
649.55 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
649.6 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
649.65 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
649.7 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
649.75 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
649.8 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
649.85 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
649.9 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
649.95 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
650 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
650.05 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
650.1 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
650.15 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
650.2 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
650.25 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
650.3 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
650.35 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
650.4 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
650.45 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
650.5 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
650.55 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
650.6 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
650.65 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
650.7 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
650.75 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
650.8 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
650.85 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
650.9 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
650.95 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
651 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
651.05 | 50.5 | 50.5 | -1 | 0.9 | 9 | 50.5 | -1 | -1 | -10 | -0.5 | -0.5 | 0 | 12 | 1 | 1 | -0.5 | 10 | 0 | 0
651.1 | 50.5 | 50.5 | -1 | 0.8 | 8 | 50.5 | -1 | -1 | -10 | -1 | -1 | 0 | 12 | 1 | 1 | -1 | 10 | 0 | 0
651.15 | 50.5 | 50.5 | -1 | 0.7 | 7 | 50.5 | -1 | -1 | -10 | -1.5 | -1.5 | 0 | 12 | 1 | 1 | -1.5 | 10 | 0 | 0
651.2 | 50.5 | 50.5 | -1 | 0.6 | 6 | 50.5 | -1 | -1 | -10 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
651.25 | 50.5 | 50.5 | -1 | 0.5 | 5 | 50.5 | -1 | -1 | -10 | -2.5 | -2.5 | 0 | 12 | 1 | 1 | -2.5 | 10 | 0 | 0
651.3 | 50.5 | 50.5 | -1 | 0.4 | 4 | 50.5 | -1 | -1 | -10 | -3 | -3 | 0 | 12 | 1 | 1 | -3 | 10 | 0 | 0
651.35 | 50.5 | 50.5 | -1 | 0.3 | 3 | 50.5 | -1 | -1 | -10 | -3.5 | -3.5 | 0 | 12 | 1 | 1 | -3.5 | 10 | 0 | 0
651.4 | 50.5 | 50.5 | -1 | 0.2 | 2 | 50.5 | -1 | -1 | -10 | -4 | -4 | 0 | 12 | 1 | 1 | -4 | 10 | 0 | 0
651.45 | 50.5 | 50.5 | -1 | 0.1 | 1 | 50.5 | -1 | -1 | -10 | -4.5 | -4.5 | 0 | 12 | 1 | 1 | -4.5 | 10 | 0 | 0
651.5 | 50.5 | 50.5 | -1 | 0 | 0 | 50.5 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
651.55 | 50.5 | 50.5 | -1 | -0.1 | -1 | 50.5 | -1 | -1 | -10 | -5.5 | -5.5 | 0 | 12 | 1 | 1 | -5.5 | 10 | 0 | 0
651.6 | 50.5 | 50.5 | -1 | -0.2 | -2 | 50.5 | -1 | -1 | -10 | -6 | -6 | 0 | 12 | 1 | 1 | -6 | 10 | 0 | 0
651.65 | 50.5 | 50.5 | -1 | -0.3 | -3 | 50.5 | -1 | -1 | -10 | -6.5 | -6.5 | 0 | 12 | 1 | 1 | -6.5 | 10 | 0 | 0
651.7 | 50.5 | 50.5 | -1 | -0.4 | -4 | 50.5 | -1 | -1 | -10 | -7 | -7 | 0 | 12 | 1 | 1 | -7 | 10 | 0 | 0
651.75 | 50.5 | 50.5 | -1 | -0.5 | -5 | 50.5 | -1 | -1 | -10 | -7.5 | -7.5 | 0 | 12 | 1 | 1 | -7.5 | 10 | 0 | 0
651.8 | 50.5 | 50.5 | -1 | -0.6 | -6 | 50.5 | -1 | -1 | -10 | -8 | -8 | 0 | 12 | 1 | 1 | -8 | 10 | 0 | 0
651.85 | 50.5 | 50.5 | -1 | -0.7 | -7 | 50.5 | -1 | -1 | -10 | -8.5 | -8.5 | 0 | 12 | 1 | 1 | -8.5 | 10 | 0 | 0
651.9 | 50.5 | 50.5 | -1 | -0.8 | -8 | 50.5 | -1 | -1 | -10 | -9 | -9 | 0 | 12 | 1 | 1 | -9 | 10 | 0 | 0
651.95 | 50.5 | 50.5 | -1 | -0.9 | -9 | 50.5 | -1 | -1 | -10 | -9.5 | -9.5 | 0 | 12 | 1 | 1 | -9.5 | 10 | 0 | 0
652 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
652.05 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
652.1 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
652.15 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
652.2 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
652.25 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
652.3 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
652.35 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
652.4 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
652.45 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
652.5 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
652.55 | 50.47 | 50.47 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
652.6 | 50.45 | 50.45 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
652.65 | 50.42 | 50.42 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
652.7 | 50.4 | 50.4 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
652.75 | 50.37 | 50.37 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
652.8 | 50.35 | 50.35 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
652.85 | 50.32 | 50.32 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
652.9 | 50.29 | 50.29 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
652.95 | 50.27 | 50.27 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
653 | 50.24 | 50.24 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
653.05 | 50.22 | 50.22 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
653.1 | 50.19 | 50.19 | -0.905 | -0.905 | -9.05 | 50.47 | -1 | -1 | -10 | -9.525 | -9.525 | 0 | 12 | 1 | 1 | -9.525 | 10 | 0 | 0
653.15 | 50.17 | 50.17 | -0.715 | -0.715 | -7.15 | 50.45 | -1 | -1 | -10 | -8.575 | -8.575 | 0 | 12 | 1 | 1 | -8.575 | 10 | 0 | 0
653.2 | 50.14 | 50.14 | -0.43 | -0.43 | -4.3 | 50.42 | -1 | -1 | -10 | -7.15 | -7.15 | 0 | 12 | 1 | 1 | -7.15 | 10 | 0 | 0
653.25 | 50.12 | 50.12 | -0.24 | -0.24 | -2.4 | 50.4 | -1 | -1 | -10 | -6.2 | -6.2 | 0 | 12 | 1 | 1 | -6.2 | 10 | 0 | 0
653.3 | 50.09 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 50.37 | -1 | -1 | -10 | -5.2206 | -5.2206 | 0 | 12 | 1 | 1 | -5.2206 | 10 | 0 | 0
653.35 | 50.06 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.35 | -1 | -1 | -10 | -5.1324 | -5.1324 | 0 | 12 | 1 | 1 | -5.1324 | 10 | 0 | 0
653.4 | 50.04 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.32 | -1 | -1 | -10 | -5.0735 | -5.0735 | 0 | 12 | 1 | 1 | -5.0735 | 10 | 0 | 0
653.45 | 50.01 | 50.01 | 0 | 0 | 0 | 50.29 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
653.5 | 49.99 | 49.99 | 0 | 0 | 0 | 50.27 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
653.55 | 49.96 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.24 | -1 | -1 | -10 | -4.9265 | -4.9265 | 0 | 12 | 1 | 1 | -4.9265 | 10 | 0 | 0
653.6 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.22 | -1 | -1 | -10 | -4.8676 | -4.8676 | 0 | 12 | 1 | 1 | -4.8676 | 10 | 0 | 0
653.65 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.19 | -0.905 | -0.905 | -9.05 | -4.3044 | -4.3044 | 0 | 12 | 1 | 1 | -4.3044 | 10 | 0 | 0
653.7 | 49.88 | 49.88 | 0.24 | 0.24 | 2.4 | 50.17 | -0.715 | -0.805 | -8.05 | -2.825 | -2.825 | 0 | 12 | 1 | 1 | -2.825 | 10 | 0 | 0
653.75 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.14 | -0.43 | -0.705 | -7.05 | -1.375 | -1.375 | 0 | 12 | 1 | 1 | -1.375 | 10 | 0 | 0
653.8 | 49.83 | 49.83 | 0.715 | 0.715 | 7.15 | 50.12 | -0.24 | -0.605 | -6.05 | 0.55 | 0.55 | 0 | 12 | 1 | 1 | 0.55 | 10 | 0 | 0
653.85 | 49.81 | 49.81 | 0.905 | 0.905 | 9.05 | 50.09 | -0.044118 | -0.505 | -5.05 | 2 | 2 | 0 | 12 | 1 | 1 | 2 | 10 | 0 | 0
653.9 | 49.78 | 49.78 | 1 | 1 | 10 | 50.06 | -0.026471 | -0.405 | -4.05 | 2.975 | 2.975 | 0 | 12 | 1 | 1 | 2.975 | 10 | 0 | 0
653.95 | 49.76 | 49.76 | 1 | 1 | 10 | 50.04 | -0.014706 | -0.305 | -3.05 | 3.475 | 3.475 | 0 | 12 | 1 | 1 | 3.475 | 10 | 0 | 0
654 | 49.73 | 49.73 | 1 | 1 | 10 | 50.01 | 0 | -0.205 | -2.05 | 3.975 | 3.975 | 0 | 12 | 1 | 1 | 3.975 | 10 | 0 | 0
654.05 | 49.71 | 49.71 | 1 | 1 | 10 | 49.99 | 0 | -0.105 | -1.05 | 4.475 | 4.475 | 0 | 12 | 1 | 1 | 4.475 | 10 | 0 | 0
654.1 | 49.68 | 49.68 | 1 | 1 | 10 | 49.96 | 0.014706 | -0.005 | -0.05 | 4.975 | 4.975 | 0 | 12 | 1 | 1 | 4.975 | 10 | 0 | 0
654.15 | 49.65 | 49.65 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
654.2 | 49.63 | 49.63 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
654.25 | 49.6 | 49.6 | 1 | 1 | 10 | 49.88 | 0.24 | 0.14412 | 1.4412 | 5.7206 | 5.7206 | 0 | 12 | 1 | 1 | 5.7206 | 10 | 0 | 0
654.3 | 49.58 | 49.58 | 1 | 1 | 10 | 49.86 | 0.43 | 0.24412 | 2.4412 | 6.2206 | 6.2206 | 0 | 12 | 1 | 1 | 6.2206 | 10 | 0 | 0
654.35 | 49.55 | 49.55 | 1 | 1 | 10 | 49.83 | 0.715 | 0.34412 | 3.4412 | 6.7206 | 6.7206 | 0 | 12 | 1 | 1 | 6.7206 | 10 | 0 | 0
654.4 | 49.53 | 49.53 | 1 | 1 | 10 | 49.81 | 0.905 | 0.44412 | 4.4412 | 7.2206 | 7.2206 | 0 | 12 | 1 | 1 | 7.2206 | 10 | 0 | 0
654.45 | 49.5 | 49.5 | 1 | 1 | 10 | 49.78 | 1 | 0.54412 | 5.4412 | 7.7206 | 7.7206 | 0 | 12 | 1 | 1 | 7.7206 | 10 | 0 | 0
654.5 | 49.5 | 49.5 | 1 | 1 | 10 | 49.76 | 1 | 0.64412 | 6.4412 | 8.2206 | 8.2206 | 0 | 12 | 1 | 1 | 8.2206 | 10 | 0 | 0
654.55 | 49.53 | 49.5 | 1 | 1 | 10 | 49.73 | 1 | 0.74412 | 7.4412 | 8.7206 | 8.7206 | 0 | 12 | 1 | 1 | 8.7206 | 10 | 0 | 0
654.6 | 49.55 | 49.5 | 1 | 1 | 10 | 49.71 | 1 | 0.84412 | 8.4412 | 9.2206 | 9.2206 | 0 | 12 | 1 | 1 | 9.2206 | 10 | 0 | 0
654.65 | 49.58 | 49.5 | 1 | 1 | 10 | 49.68 | 1 | 0.94412 | 9.4412 | 9.7206 | 9.7206 | 0 | 12 | 1 | 1 | 9.7206 | 10 | 0 | 0
654.7 | 49.6 | 49.5 | 1 | 1 | 10 | 49.65 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
654.75 | 49.63 | 49.5 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
654.8 | 49.65 | 49.5 | 1 | 1 | 10 | 49.65 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
654.85 | 49.68 | 49.5 | 1 | 1 | 10 | 49.68 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
654.9 | 49.71 | 49.5 | 1 | 1 | 10 | 49.71 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
654.95 | 49.73 | 49.5 | 1 | 1 | 10 | 49.73 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
655 | 49.76 | 49.5 | 1 | 1 | 10 | 49.76 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
655.05 | 49.78 | 49.5 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
655.1 | 49.81 | 49.53 | 1 | 1 | 10 | 49.81 | 0.905 | 0.905 | 9.05 | 9.525 | 9.525 | 0 | 12 | 1 | 1 | 9.525 | 10 | 0 | 0
655.15 | 49.83 | 49.55 | 1 | 1 | 10 | 49.83 | 0.715 | 0.715 | 7.15 | 8.575 | 8.575 | 0 | 12 | 1 | 1 | 8.575 | 10 | 0 | 0
655.2 | 49.86 | 49.58 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
655.25 | 49.88 | 49.6 | 1 | 1 | 10 | 49.88 | 0.24 | 0.24 | 2.4 | 6.2 | 6.2 | 0 | 12 | 1 | 1 | 6.2 | 10 | 0 | 0
655.3 | 49.91 | 49.63 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
655.35 | 49.94 | 49.65 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
655.4 | 49.96 | 49.68 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
655.45 | 49.99 | 49.71 | 1 | 1 | 10 | 49.99 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
655.5 | 50.01 | 49.73 | 1 | 1 | 10 | 50.01 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
655.55 | 50.04 | 49.76 | 1 | 1 | 10 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 4.9265 | 4.9265 | 0 | 12 | 1 | 1 | 4.9265 | 10 | 0 | 0
655.6 | 50.06 | 49.78 | 1 | 1 | 10 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 4.8676 | 4.8676 | 0 | 12 | 1 | 1 | 4.8676 | 10 | 0 | 0
655.65 | 50.09 | 49.81 | 0.905 | 0.905 | 9.05 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 4.3044 | 4.3044 | 0 | 12 | 1 | 1 | 4.3044 | 10 | 0 | 0
655.7 | 50.12 | 49.83 | 0.715 | 0.805 | 8.05 | 50.12 | -0.24 | -0.24 | -2.4 | 2.825 | 2.825 | 0 | 12 | 1 | 1 | 2.825 | 10 | 0 | 0
655.75 | 50.14 | 49.86 | 0.43 | 0.705 | 7.05 | 50.14 | -0.43 | -0.43 | -4.3 | 1.375 | 1.375 | 0 | 12 | 1 | 1 | 1.375 | 10 | 0 | 0
655.8 | 50.17 | 49.88 | 0.24 | 0.605 | 6.05 | 50.17 | -0.715 | -0.715 | -7.15 | -0.55 | -0.55 | 0 | 12 | 1 | 1 | -0.55 | 10 | 0 | 0
655.85 | 50.19 | 49.91 | 0.044118 | 0.505 | 5.05 | 50.19 | -0.905 | -0.905 | -9.05 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
655.9 | 50.22 | 49.94 | 0.026471 | 0.405 | 4.05 | 50.22 | -1 | -1 | -10 | -2.975 | -2.975 | 0 | 12 | 1 | 1 | -2.975 | 10 | 0 | 0
655.95 | 50.24 | 49.96 | 0.014706 | 0.305 | 3.05 | 50.24 | -1 | -1 | -10 | -3.475 | -3.475 | 0 | 12 | 1 | 1 | -3.475 | 10 | 0 | 0
656 | 50.27 | 49.99 | 0 | 0.205 | 2.05 | 50.27 | -1 | -1 | -10 | -3.975 | -3.975 | 0 | 12 | 1 | 1 | -3.975 | 10 | 0 | 0
656.05 | 50.29 | 50.01 | 0 | 0.105 | 1.05 | 50.29 | -1 | -1 | -10 | -4.475 | -4.475 | 0 | 12 | 1 | 1 | -4.475 | 10 | 0 | 0
656.1 | 50.32 | 50.04 | -0.014706 | 0.005 | 0.05 | 50.32 | -1 | -1 | -10 | -4.975 | -4.975 | 0 | 12 | 1 | 1 | -4.975 | 10 | 0 | 0
656.15 | 50.35 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.35 | -1 | -1 | -10 | -5.1324 | -5.1324 | 0 | 12 | 1 | 1 | -5.1324 | 10 | 0 | 0
656.2 | 50.37 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 50.37 | -1 | -1 | -10 | -5.2206 | -5.2206 | 0 | 12 | 1 | 1 | -5.2206 | 10 | 0 | 0
656.25 | 50.4 | 50.12 | -0.24 | -0.14412 | -1.4412 | 50.4 | -1 | -1 | -10 | -5.7206 | -5.7206 | 0 | 12 | 1 | 1 | -5.7206 | 10 | 0 | 0
656.3 | 50.42 | 50.14 | -0.43 | -0.24412 | -2.4412 | 50.42 | -1 | -1 | -10 | -6.2206 | -6.2206 | 0 | 12 | 1 | 1 | -6.2206 | 10 | 0 | 0
656.35 | 50.45 | 50.17 | -0.715 | -0.34412 | -3.4412 | 50.45 | -1 | -1 | -10 | -6.7206 | -6.7206 | 0 | 12 | 1 | 1 | -6.7206 | 10 | 0 | 0
656.4 | 50.47 | 50.19 | -0.905 | -0.44412 | -4.4412 | 50.47 | -1 | -1 | -10 | -7.2206 | -7.2206 | 0 | 12 | 1 | 1 | -7.2206 | 10 | 0 | 0
656.45 | 50.5 | 50.22 | -1 | -0.54412 | -5.4412 | 50.5 | -1 | -1 | -10 | -7.7206 | -7.7206 | 0 | 12 | 1 | 1 | -7.7206 | 10 | 0 | 0
656.5 | 50.5 | 50.24 | -1 | -0.64412 | -6.4412 | 50.5 | -1 | -1 | -10 | -8.2206 | -8.2206 | 0 | 12 | 1 | 1 | -8.2206 | 10 | 0 | 0
656.55 | 50.47 | 50.27 | -1 | -0.74412 | -7.4412 | 50.5 | -1 | -1 | -10 | -8.7206 | -8.7206 | 0 | 12 | 1 | 1 | -8.7206 | 10 | 0 | 0
656.6 | 50.45 | 50.29 | -1 | -0.84412 | -8.4412 | 50.5 | -1 | -1 | -10 | -9.2206 | -9.2206 | 0 | 12 | 1 | 1 | -9.2206 | 10 | 0 | 0
656.65 | 50.42 | 50.32 | -1 | -0.94412 | -9.4412 | 50.5 | -1 | -1 | -10 | -9.7206 | -9.7206 | 0 | 12 | 1 | 1 | -9.7206 | 10 | 0 | 0
656.7 | 50.39 | 50.35 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
656.75 | 50.37 | 50.37 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
656.8 | 50.34 | 50.34 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
656.85 | 50.32 | 50.32 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
656.9 | 50.29 | 50.29 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
656.95 | 50.26 | 50.26 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
657 | 50.24 | 50.24 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
657.05 | 50.21 | 50.21 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
657.1 | 50.18 | 50.18 | -0.81 | -0.81 | -8.1 | 50.47 | -1 | -1 | -10 | -9.05 | -9.05 | 0 | 12 | 1 | 1 | -9.05 | 10 | 0 | 0
657.15 | 50.16 | 50.16 | -0.62 | -0.62 | -6.2 | 50.45 | -1 | -1 | -10 | -8.1 | -8.1 | 0 | 12 | 1 | 1 | -8.1 | 10 | 0 | 0
657.2 | 50.13 | 50.13 | -0.335 | -0.335 | -3.35 | 50.42 | -1 | -1 | -10 | -6.675 | -6.675 | 0 | 12 | 1 | 1 | -6.675 | 10 | 0 | 0
657.25 | 50.11 | 50.11 | -0.145 | -0.145 | -1.45 | 50.39 | -1 | -1 | -10 | -5.725 | -5.725 | 0 | 12 | 1 | 1 | -5.725 | 10 | 0 | 0
657.3 | 50.08 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 50.37 | -1 | -1 | -10 | -5.1912 | -5.1912 | 0 | 12 | 1 | 1 | -5.1912 | 10 | 0 | 0
657.35 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.34 | -1 | -1 | -10 | -5.1029 | -5.1029 | 0 | 12 | 1 | 1 | -5.1029 | 10 | 0 | 0
657.4 | 50.03 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 50.32 | -1 | -1 | -10 | -5.0441 | -5.0441 | 0 | 12 | 1 | 1 | -5.0441 | 10 | 0 | 0
657.45 | 50 | 50 | 0 | 0 | 0 | 50.29 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
657.5 | 50 | 50 | 0 | 0 | 0 | 50.26 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
657.55 | 50 | 50 | 0 | 0 | 0 | 50.24 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
657.6 | 50 | 50 | 0 | 0 | 0 | 50.21 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
657.65 | 50 | 50 | 0 | 0 | 0 | 50.18 | -0.81 | -0.9 | -9 | -4.5 | -4.5 | 0 | 12 | 1 | 1 | -4.5 | 10 | 0 | 0
657.7 | 50 | 50 | 0 | 0 | 0 | 50.16 | -0.62 | -0.8 | -8 | -4 | -4 | 0 | 12 | 1 | 1 | -4 | 10 | 0 | 0
657.75 | 50 | 50 | 0 | 0 | 0 | 50.13 | -0.335 | -0.7 | -7 | -3.5 | -3.5 | 0 | 12 | 1 | 1 | -3.5 | 10 | 0 | 0
657.8 | 50.01 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.6 | -6 | -3 | -3 | 0 | 12 | 1 | 1 | -3 | 10 | 0 | 0
657.85 | 50.01 | 50 | 0 | 0 | 0 | 50.08 | -0.038235 | -0.5 | -5 | -2.5 | -2.5 | 0 | 12 | 1 | 1 | -2.5 | 10 | 0 | 0
657.9 | 49.99 | 49.99 | 0 | 0 | 0 | 50.05 | -0.020588 | -0.4 | -4 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
657.95 | 49.99 | 49.99 | 0 | 0 | 0 | 50.03 | -0.0088235 | -0.3 | -3 | -1.5 | -1.5 | 0 | 12 | 1 | 1 | -1.5 | 10 | 0 | 0
658 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | -0.2 | -2 | -0.83824 | -0.83824 | 0 | 12 | 1 | 1 | -0.83824 | 10 | 0 | 0
658.05 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | -0.1 | -1 | -0.33824 | -0.33824 | 0 | 12 | 1 | 1 | -0.33824 | 10 | 0 | 0
658.1 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
658.15 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
658.2 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
658.25 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
658.3 | 49.89 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
658.35 | 49.89 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
658.4 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50.01 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
658.45 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
658.5 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
658.55 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 2.7868 | 2.7868 | 0 | 12 | 1 | 1 | 2.7868 | 10 | 0 | 0
658.6 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 2.7868 | 2.7868 | 0 | 12 | 1 | 1 | 2.7868 | 10 | 0 | 0
658.65 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 2.8456 | 2.8456 | 0 | 12 | 1 | 1 | 2.8456 | 10 | 0 | 0
658.7 | 49.94 | 49.85 | 0.525 | 0.525 | 5.25 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 2.7574 | 2.7574 | 0 | 12 | 1 | 1 | 2.7574 | 10 | 0 | 0
658.75 | 49.94 | 49.85 | 0.525 | 0.525 | 5.25 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 2.7574 | 2.7574 | 0 | 12 | 1 | 1 | 2.7574 | 10 | 0 | 0
658.8 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
658.85 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
658.9 | 49.93 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
658.95 | 49.93 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
659 | 49.96 | 49.85 | 0.525 | 0.525 | 5.25 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 2.6985 | 2.6985 | 0 | 12 | 1 | 1 | 2.6985 | 10 | 0 | 0
659.05 | 49.96 | 49.85 | 0.525 | 0.525 | 5.25 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 2.6985 | 2.6985 | 0 | 12 | 1 | 1 | 2.6985 | 10 | 0 | 0
659.1 | 49.99 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
659.15 | 49.99 | 49.91 | 0.044118 | 0.425 | 4.25 | 49.99 | 0 | 0 | 0 | 2.125 | 2.125 | 0 | 12 | 1 | 1 | 2.125 | 10 | 0 | 0
659.2 | 49.99 | 49.91 | 0.044118 | 0.325 | 3.25 | 49.99 | 0 | 0 | 0 | 1.625 | 1.625 | 0 | 12 | 1 | 1 | 1.625 | 10 | 0 | 0
659.25 | 49.99 | 49.93 | 0.032353 | 0.225 | 2.25 | 49.99 | 0 | 0 | 0 | 1.125 | 1.125 | 0 | 12 | 1 | 1 | 1.125 | 10 | 0 | 0
659.3 | 49.96 | 49.93 | 0.032353 | 0.125 | 1.25 | 49.99 | 0 | 0 | 0 | 0.625 | 0.625 | 0 | 12 | 1 | 1 | 0.625 | 10 | 0 | 0
659.35 | 49.96 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 49.99 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
659.4 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
659.45 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
659.5 | 50.05 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.058824 | 0.058824 | 0 | 12 | 1 | 1 | 0.058824 | 10 | 0 | 0
659.55 | 50.05 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
659.6 | 49.97 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
659.65 | 49.97 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
659.7 | 49.92 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
659.75 | 49.92 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
659.8 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
659.85 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
659.9 | 49.94 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
659.95 | 49.94 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
660 | 50.01 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
660.05 | 50.01 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
660.1 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
660.15 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
660.2 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
660.25 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
660.3 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
660.35 | 49.95 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
660.4 | 49.97 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
660.45 | 49.97 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
660.5 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
660.55 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
660.6 | 49.87 | 49.87 | 0.335 | 0.335 | 3.35 | 50.01 | 0 | 0 | 0 | 1.675 | 1.675 | 0 | 12 | 1 | 1 | 1.675 | 10 | 0 | 0
660.65 | 49.87 | 49.87 | 0.335 | 0.335 | 3.35 | 49.99 | 0 | 0 | 0 | 1.675 | 1.675 | 0 | 12 | 1 | 1 | 1.675 | 10 | 0 | 0
660.7 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
660.75 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 2.6691 | 2.6691 | 0 | 12 | 1 | 1 | 2.6691 | 10 | 0 | 0
660.8 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
660.85 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
660.9 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
660.95 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
661 | 49.84 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
661.05 | 49.84 | 49.79 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
661.1 | 49.89 | 49.79 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
661.15 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.12647 | 1.2647 | 5.6324 | 5.6324 | 0 | 12 | 1 | 1 | 5.6324 | 10 | 0 | 0
661.2 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.145 | 1.45 | 5.725 | 5.725 | 0 | 12 | 1 | 1 | 5.725 | 10 | 0 | 0
661.25 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.145 | 1.45 | 5.725 | 5.725 | 0 | 12 | 1 | 1 | 5.725 | 10 | 0 | 0
661.3 | 49.96 | 49.79 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
661.35 | 49.96 | 49.79 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
661.4 | 50.02 | 49.79 | 1 | 1 | 10 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 4.9853 | 4.9853 | 0 | 12 | 1 | 1 | 4.9853 | 10 | 0 | 0
661.45 | 50.02 | 49.79 | 1 | 1 | 10 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 4.9853 | 4.9853 | 0 | 12 | 1 | 1 | 4.9853 | 10 | 0 | 0
661.5 | 50.03 | 49.79 | 1 | 1 | 10 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.9559 | 4.9559 | 0 | 12 | 1 | 1 | 4.9559 | 10 | 0 | 0
661.55 | 50.03 | 49.84 | 0.62 | 0.9 | 9 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.4559 | 4.4559 | 0 | 12 | 1 | 1 | 4.4559 | 10 | 0 | 0
661.6 | 50.02 | 49.84 | 0.62 | 0.8 | 8 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 3.9559 | 3.9559 | 0 | 12 | 1 | 1 | 3.9559 | 10 | 0 | 0
661.65 | 50.02 | 49.89 | 0.145 | 0.7 | 7 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 3.4559 | 3.4559 | 0 | 12 | 1 | 1 | 3.4559 | 10 | 0 | 0
661.7 | 50.08 | 49.89 | 0.145 | 0.6 | 6 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 2.8088 | 2.8088 | 0 | 12 | 1 | 1 | 2.8088 | 10 | 0 | 0
661.75 | 50.08 | 49.89 | 0.145 | 0.5 | 5 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 2.3088 | 2.3088 | 0 | 12 | 1 | 1 | 2.3088 | 10 | 0 | 0
661.8 | 50.01 | 49.89 | 0.145 | 0.4 | 4 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 1.8088 | 1.8088 | 0 | 12 | 1 | 1 | 1.8088 | 10 | 0 | 0
661.85 | 50.01 | 49.96 | 0.014706 | 0.3 | 3 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 1.3088 | 1.3088 | 0 | 12 | 1 | 1 | 1.3088 | 10 | 0 | 0
661.9 | 49.94 | 49.94 | 0.026471 | 0.2 | 2 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.80882 | 0.80882 | 0 | 12 | 1 | 1 | 0.80882 | 10 | 0 | 0
661.95 | 49.94 | 49.94 | 0.026471 | 0.1 | 1 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.30882 | 0.30882 | 0 | 12 | 1 | 1 | 0.30882 | 10 | 0 | 0
662 | 50 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
662.05 | 50 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
662.1 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
662.15 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
662.2 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
662.25 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
662.3 | 49.92 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
662.35 | 49.92 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
662.4 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50.01 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
662.45 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
662.5 | 49.92 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
662.55 | 49.92 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
662.6 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
662.65 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
662.7 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
662.75 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
662.8 | 49.87 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
662.85 | 49.87 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
662.9 | 49.8 | 49.8 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
662.95 | 49.8 | 49.8 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
663 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
663.05 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
663.1 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
663.15 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
663.2 | 49.72 | 49.72 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
663.25 | 49.72 | 49.72 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
663.3 | 49.67 | 49.67 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
663.35 | 49.67 | 49.67 | 1 | 1 | 10 | 49.87 | 0.335 | 0.14412 | 1.4412 | 5.7206 | 5.7206 | 0 | 12 | 1 | 1 | 5.7206 | 10 | 0 | 0
663.4 | 49.65 | 49.65 | 1 | 1 | 10 | 49.87 | 0.335 | 0.24412 | 2.4412 | 6.2206 | 6.2206 | 0 | 12 | 1 | 1 | 6.2206 | 10 | 0 | 0
663.45 | 49.65 | 49.65 | 1 | 1 | 10 | 49.8 | 1 | 0.34412 | 3.4412 | 6.7206 | 6.7206 | 0 | 12 | 1 | 1 | 6.7206 | 10 | 0 | 0
663.5 | 49.59 | 49.59 | 1 | 1 | 10 | 49.8 | 1 | 0.44412 | 4.4412 | 7.2206 | 7.2206 | 0 | 12 | 1 | 1 | 7.2206 | 10 | 0 | 0
663.55 | 49.59 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.54412 | 5.4412 | 7.7206 | 7.7206 | 0 | 12 | 1 | 1 | 7.7206 | 10 | 0 | 0
663.6 | 49.66 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.64412 | 6.4412 | 8.2206 | 8.2206 | 0 | 12 | 1 | 1 | 8.2206 | 10 | 0 | 0
663.65 | 49.66 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.74412 | 7.4412 | 8.7206 | 8.7206 | 0 | 12 | 1 | 1 | 8.7206 | 10 | 0 | 0
663.7 | 49.63 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.84412 | 8.4412 | 9.2206 | 9.2206 | 0 | 12 | 1 | 1 | 9.2206 | 10 | 0 | 0
663.75 | 49.63 | 49.59 | 1 | 1 | 10 | 49.72 | 1 | 0.94412 | 9.4412 | 9.7206 | 9.7206 | 0 | 12 | 1 | 1 | 9.7206 | 10 | 0 | 0
663.8 | 49.61 | 49.59 | 1 | 1 | 10 | 49.72 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
663.85 | 49.61 | 49.59 | 1 | 1 | 10 | 49.67 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
663.9 | 49.54 | 49.54 | 1 | 1 | 10 | 49.67 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
663.95 | 49.54 | 49.54 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
664 | 49.46 | 49.46 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
664.05 | 49.46 | 49.46 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
664.1 | 49.45 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
664.15 | 49.45 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
664.2 | 49.51 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
664.25 | 49.51 | 49.45 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
664.3 | 49.5 | 49.45 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
664.35 | 49.5 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
664.4 | 49.54 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
664.45 | 49.54 | 49.45 | 1 | 1 | 10 | 49.54 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
664.5 | 49.59 | 49.45 | 1 | 1 | 10 | 49.59 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
664.55 | 49.59 | 49.45 | 1 | 1 | 10 | 49.59 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
664.6 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
664.65 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
664.7 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
664.75 | 49.61 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
664.8 | 49.53 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
664.85 | 49.53 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
664.9 | 49.54 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
664.95 | 49.54 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
665 | 49.61 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
665.05 | 49.61 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
665.1 | 49.66 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
665.15 | 49.66 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
665.2 | 49.64 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
665.25 | 49.64 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
665.3 | 49.69 | 49.53 | 1 | 1 | 10 | 49.69 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
665.35 | 49.69 | 49.53 | 1 | 1 | 10 | 49.69 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
665.4 | 49.74 | 49.53 | 1 | 1 | 10 | 49.74 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
665.45 | 49.74 | 49.54 | 1 | 1 | 10 | 49.74 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
665.5 | 49.78 | 49.54 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
665.55 | 49.78 | 49.61 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
665.6 | 49.82 | 49.61 | 1 | 1 | 10 | 49.82 | 0.81 | 0.81 | 8.1 | 9.05 | 9.05 | 0 | 12 | 1 | 1 | 9.05 | 10 | 0 | 0
665.65 | 49.82 | 49.64 | 1 | 1 | 10 | 49.82 | 0.81 | 0.81 | 8.1 | 9.05 | 9.05 | 0 | 12 | 1 | 1 | 9.05 | 10 | 0 | 0
665.7 | 49.86 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
665.75 | 49.86 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
665.8 | 49.84 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
665.85 | 49.84 | 49.69 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
665.9 | 49.91 | 49.69 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
665.95 | 49.91 | 49.74 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
666 | 49.97 | 49.74 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
666.05 | 49.97 | 49.78 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
666.1 | 50.03 | 49.78 | 1 | 1 | 10 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.9559 | 4.9559 | 0 | 12 | 1 | 1 | 4.9559 | 10 | 0 | 0
666.15 | 50.03 | 49.82 | 0.81 | 0.9 | 9 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.4559 | 4.4559 | 0 | 12 | 1 | 1 | 4.4559 | 10 | 0 | 0
666.2 | 50.05 | 49.82 | 0.81 | 0.81 | 8.1 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 3.9471 | 3.9471 | 0 | 12 | 1 | 1 | 3.9471 | 10 | 0 | 0
666.25 | 50.05 | 49.84 | 0.62 | 0.71 | 7.1 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 3.4471 | 3.4471 | 0 | 12 | 1 | 1 | 3.4471 | 10 | 0 | 0
666.3 | 50.01 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
666.35 | 50.01 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
666.4 | 49.95 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
666.45 | 49.95 | 49.91 | 0.044118 | 0.52 | 5.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.4971 | 2.4971 | 0 | 12 | 1 | 1 | 2.4971 | 10 | 0 | 0
666.5 | 49.99 | 49.91 | 0.044118 | 0.42 | 4.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 1.9971 | 1.9971 | 0 | 12 | 1 | 1 | 1.9971 | 10 | 0 | 0
666.55 | 49.99 | 49.95 | 0.020588 | 0.32 | 3.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 1.4971 | 1.4971 | 0 | 12 | 1 | 1 | 1.4971 | 10 | 0 | 0
666.6 | 49.92 | 49.92 | 0.038235 | 0.22 | 2.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.99706 | 0.99706 | 0 | 12 | 1 | 1 | 0.99706 | 10 | 0 | 0
666.65 | 49.92 | 49.92 | 0.038235 | 0.12 | 1.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.49706 | 0.49706 | 0 | 12 | 1 | 1 | 0.49706 | 10 | 0 | 0
666.7 | 49.97 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
666.75 | 49.97 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
666.8 | 50.02 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
666.85 | 50.02 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.17647 | 0.17647 | 0 | 12 | 1 | 1 | 0.17647 | 10 | 0 | 0
666.9 | 50.07 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
666.95 | 50.07 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
667 | 50.06 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
667.05 | 50.06 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
667.1 | 50.13 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
667.15 | 50.13 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
667.2 | 50.09 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
667.25 | 50.09 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6309 | -1.6309 | 0 | 12 | 1 | 1 | -1.6309 | 10 | 0 | 0
667.3 | 50.07 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6309 | -1.6309 | 0 | 12 | 1 | 1 | -1.6309 | 10 | 0 | 0
667.35 | 50.07 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6897 | -1.6897 | 0 | 12 | 1 | 1 | -1.6897 | 10 | 0 | 0
667.4 | 50.07 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6897 | -1.6897 | 0 | 12 | 1 | 1 | -1.6897 | 10 | 0 | 0
667.45 | 50.07 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.13 | -0.335 | -0.335 | -3.35 | -1.8074 | -1.8074 | 0 | 12 | 1 | 1 | -1.8074 | 10 | 0 | 0
667.5 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.13 | -0.335 | -0.335 | -3.35 | -1.7779 | -1.7779 | 0 | 12 | 1 | 1 | -1.7779 | 10 | 0 | 0
667.55 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.13 | -0.335 | -0.335 | -3.35 | -1.7779 | -1.7779 | 0 | 12 | 1 | 1 | -1.7779 | 10 | 0 | 0
667.6 | 50.01 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
667.65 | 50.01 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
667.7 | 50.07 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
667.75 | 50.07 | 50.01 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.235 | -2.35 | -1.175 | -1.175 | 0 | 12 | 1 | 1 | -1.175 | 10 | 0 | 0
667.8 | 50.05 | 50.01 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.135 | -1.35 | -0.675 | -0.675 | 0 | 12 | 1 | 1 | -0.675 | 10 | 0 | 0
667.85 | 50.05 | 50.01 | 0 | 0 | 0 | 50.07 | -0.032353 | -0.035 | -0.35 | -0.175 | -0.175 | 0 | 12 | 1 | 1 | -0.175 | 10 | 0 | 0
667.9 | 50.1 | 50.01 | 0 | 0 | 0 | 50.1 | -0.05 | -0.05 | -0.5 | -0.25 | -0.25 | 0 | 12 | 1 | 1 | -0.25 | 10 | 0 | 0
667.95 | 50.1 | 50.01 | 0 | 0 | 0 | 50.1 | -0.05 | -0.05 | -0.5 | -0.25 | -0.25 | 0 | 12 | 1 | 1 | -0.25 | 10 | 0 | 0
668 | 50.11 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
668.05 | 50.11 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
668.1 | 50.06 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
668.15 | 50.06 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
668.2 | 50.04 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
668.25 | 50.04 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
668.3 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
668.35 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
668.4 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
668.45 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
668.5 | 50.11 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
668.55 | 50.11 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
668.6 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
668.65 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
668.7 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
668.75 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
668.8 | 50.02 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.11 | -0.145 | -0.145 | -1.45 | -0.73971 | -0.73971 | 0 | 12 | 1 | 1 | -0.73971 | 10 | 0 | 0
668.85 | 50.02 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.11 | -0.145 | -0.145 | -1.45 | -0.73971 | -0.73971 | 0 | 12 | 1 | 1 | -0.73971 | 10 | 0 | 0
668.9 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
668.95 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
669 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
669.05 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
669.1 | 50.01 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
669.15 | 50.01 | 50 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.045 | -0.45 | -0.225 | -0.225 | 0 | 12 | 1 | 1 | -0.225 | 10 | 0 | 0
669.2 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
669.25 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
669.3 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
669.35 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
669.4 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.14706 | 0.14706 | 0 | 12 | 1 | 1 | 0.14706 | 10 | 0 | 0
669.45 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
669.5 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
669.55 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
669.6 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
669.65 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
669.7 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
669.75 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
669.8 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
669.85 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
669.9 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
669.95 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
670 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
670.05 | 50 | 50 | 0 | 0 | 0 | 50.01 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
670.1 | 49.5 | 49.5 | 1 | 1 | 10 | 50.01 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
670.15 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
670.2 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
670.25 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
670.3 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
670.35 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
670.4 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
670.45 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
670.5 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
670.55 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
670.6 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
670.65 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.1 | 1 | 5.5 | 5.5 | 0 | 12 | 1 | 1 | 5.5 | 10 | 0 | 0
670.7 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.2 | 2 | 6 | 6 | 0 | 12 | 1 | 1 | 6 | 10 | 0 | 0
670.75 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.3 | 3 | 6.5 | 6.5 | 0 | 12 | 1 | 1 | 6.5 | 10 | 0 | 0
670.8 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.4 | 4 | 7 | 7 | 0 | 12 | 1 | 1 | 7 | 10 | 0 | 0
670.85 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.5 | 5 | 7.5 | 7.5 | 0 | 12 | 1 | 1 | 7.5 | 10 | 0 | 0
670.9 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.6 | 6 | 8 | 8 | 0 | 12 | 1 | 1 | 8 | 10 | 0 | 0
670.95 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.7 | 7 | 8.5 | 8.5 | 0 | 12 | 1 | 1 | 8.5 | 10 | 0 | 0
671 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.8 | 8 | 9 | 9 | 0 | 12 | 1 | 1 | 9 | 10 | 0 | 0
671.05 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.9 | 9 | 9.5 | 9.5 | 0 | 12 | 1 | 1 | 9.5 | 10 | 0 | 0
671.1 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
671.15 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
671.2 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
671.25 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
671.3 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
671.35 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
671.4 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
671.45 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
671.5 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
671.55 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
671.6 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
671.65 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
671.7 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
671.75 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
671.8 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
671.85 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
671.9 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
671.95 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
672 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
672.05 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
672.1 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
672.15 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
672.2 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
672.25 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
672.3 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
672.35 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
672.4 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
672.45 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
672.5 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
672.55 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
672.6 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
672.65 | 50.5 | 50.5 | -1 | 0.9 | 9 | 50.5 | -1 | -1 | -10 | -0.5 | -0.5 | 0 | 12 | 1 | 1 | -0.5 | 10 | 0 | 0
672.7 | 50.5 | 50.5 | -1 | 0.8 | 8 | 50.5 | -1 | -1 | -10 | -1 | -1 | 0 | 12 | 1 | 1 | -1 | 10 | 0 | 0
672.75 | 50.5 | 50.5 | -1 | 0.7 | 7 | 50.5 | -1 | -1 | -10 | -1.5 | -1.5 | 0 | 12 | 1 | 1 | -1.5 | 10 | 0 | 0
672.8 | 50.5 | 50.5 | -1 | 0.6 | 6 | 50.5 | -1 | -1 | -10 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
672.85 | 50.5 | 50.5 | -1 | 0.5 | 5 | 50.5 | -1 | -1 | -10 | -2.5 | -2.5 | 0 | 12 | 1 | 1 | -2.5 | 10 | 0 | 0
672.9 | 50.5 | 50.5 | -1 | 0.4 | 4 | 50.5 | -1 | -1 | -10 | -3 | -3 | 0 | 12 | 1 | 1 | -3 | 10 | 0 | 0
672.95 | 50.5 | 50.5 | -1 | 0.3 | 3 | 50.5 | -1 | -1 | -10 | -3.5 | -3.5 | 0 | 12 | 1 | 1 | -3.5 | 10 | 0 | 0
673 | 50.5 | 50.5 | -1 | 0.2 | 2 | 50.5 | -1 | -1 | -10 | -4 | -4 | 0 | 12 | 1 | 1 | -4 | 10 | 0 | 0
673.05 | 50.5 | 50.5 | -1 | 0.1 | 1 | 50.5 | -1 | -1 | -10 | -4.5 | -4.5 | 0 | 12 | 1 | 1 | -4.5 | 10 | 0 | 0
673.1 | 50.5 | 50.5 | -1 | 0 | 0 | 50.5 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
673.15 | 50.5 | 50.5 | -1 | -0.1 | -1 | 50.5 | -1 | -1 | -10 | -5.5 | -5.5 | 0 | 12 | 1 | 1 | -5.5 | 10 | 0 | 0
673.2 | 50.5 | 50.5 | -1 | -0.2 | -2 | 50.5 | -1 | -1 | -10 | -6 | -6 | 0 | 12 | 1 | 1 | -6 | 10 | 0 | 0
673.25 | 50.5 | 50.5 | -1 | -0.3 | -3 | 50.5 | -1 | -1 | -10 | -6.5 | -6.5 | 0 | 12 | 1 | 1 | -6.5 | 10 | 0 | 0
673.3 | 50.5 | 50.5 | -1 | -0.4 | -4 | 50.5 | -1 | -1 | -10 | -7 | -7 | 0 | 12 | 1 | 1 | -7 | 10 | 0 | 0
673.35 | 50.5 | 50.5 | -1 | -0.5 | -5 | 50.5 | -1 | -1 | -10 | -7.5 | -7.5 | 0 | 12 | 1 | 1 | -7.5 | 10 | 0 | 0
673.4 | 50.5 | 50.5 | -1 | -0.6 | -6 | 50.5 | -1 | -1 | -10 | -8 | -8 | 0 | 12 | 1 | 1 | -8 | 10 | 0 | 0
673.45 | 50.5 | 50.5 | -1 | -0.7 | -7 | 50.5 | -1 | -1 | -10 | -8.5 | -8.5 | 0 | 12 | 1 | 1 | -8.5 | 10 | 0 | 0
673.5 | 50.5 | 50.5 | -1 | -0.8 | -8 | 50.5 | -1 | -1 | -10 | -9 | -9 | 0 | 12 | 1 | 1 | -9 | 10 | 0 | 0
673.55 | 50.5 | 50.5 | -1 | -0.9 | -9 | 50.5 | -1 | -1 | -10 | -9.5 | -9.5 | 0 | 12 | 1 | 1 | -9.5 | 10 | 0 | 0
673.6 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
673.65 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
673.7 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
673.75 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
673.8 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
673.85 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
673.9 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
673.95 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
674 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
674.05 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
674.1 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
674.15 | 50.47 | 50.47 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
674.2 | 50.45 | 50.45 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
674.25 | 50.42 | 50.42 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
674.3 | 50.4 | 50.4 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
674.35 | 50.37 | 50.37 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
674.4 | 50.35 | 50.35 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
674.45 | 50.32 | 50.32 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
674.5 | 50.29 | 50.29 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
674.55 | 50.27 | 50.27 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
674.6 | 50.24 | 50.24 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
674.65 | 50.22 | 50.22 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
674.7 | 50.19 | 50.19 | -0.905 | -0.905 | -9.05 | 50.47 | -1 | -1 | -10 | -9.525 | -9.525 | 0 | 12 | 1 | 1 | -9.525 | 10 | 0 | 0
674.75 | 50.17 | 50.17 | -0.715 | -0.715 | -7.15 | 50.45 | -1 | -1 | -10 | -8.575 | -8.575 | 0 | 12 | 1 | 1 | -8.575 | 10 | 0 | 0
674.8 | 50.14 | 50.14 | -0.43 | -0.43 | -4.3 | 50.42 | -1 | -1 | -10 | -7.15 | -7.15 | 0 | 12 | 1 | 1 | -7.15 | 10 | 0 | 0
674.85 | 50.12 | 50.12 | -0.24 | -0.24 | -2.4 | 50.4 | -1 | -1 | -10 | -6.2 | -6.2 | 0 | 12 | 1 | 1 | -6.2 | 10 | 0 | 0
674.9 | 50.09 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 50.37 | -1 | -1 | -10 | -5.2206 | -5.2206 | 0 | 12 | 1 | 1 | -5.2206 | 10 | 0 | 0
674.95 | 50.06 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.35 | -1 | -1 | -10 | -5.1324 | -5.1324 | 0 | 12 | 1 | 1 | -5.1324 | 10 | 0 | 0
675 | 50.04 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.32 | -1 | -1 | -10 | -5.0735 | -5.0735 | 0 | 12 | 1 | 1 | -5.0735 | 10 | 0 | 0
675.05 | 50.01 | 50.01 | 0 | 0 | 0 | 50.29 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
675.1 | 49.99 | 49.99 | 0 | 0 | 0 | 50.27 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
675.15 | 49.96 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.24 | -1 | -1 | -10 | -4.9265 | -4.9265 | 0 | 12 | 1 | 1 | -4.9265 | 10 | 0 | 0
675.2 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.22 | -1 | -1 | -10 | -4.8676 | -4.8676 | 0 | 12 | 1 | 1 | -4.8676 | 10 | 0 | 0
675.25 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.19 | -0.905 | -0.905 | -9.05 | -4.3044 | -4.3044 | 0 | 12 | 1 | 1 | -4.3044 | 10 | 0 | 0
675.3 | 49.88 | 49.88 | 0.24 | 0.24 | 2.4 | 50.17 | -0.715 | -0.805 | -8.05 | -2.825 | -2.825 | 0 | 12 | 1 | 1 | -2.825 | 10 | 0 | 0
675.35 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.14 | -0.43 | -0.705 | -7.05 | -1.375 | -1.375 | 0 | 12 | 1 | 1 | -1.375 | 10 | 0 | 0
675.4 | 49.83 | 49.83 | 0.715 | 0.715 | 7.15 | 50.12 | -0.24 | -0.605 | -6.05 | 0.55 | 0.55 | 0 | 12 | 1 | 1 | 0.55 | 10 | 0 | 0
675.45 | 49.81 | 49.81 | 0.905 | 0.905 | 9.05 | 50.09 | -0.044118 | -0.505 | -5.05 | 2 | 2 | 0 | 12 | 1 | 1 | 2 | 10 | 0 | 0
675.5 | 49.78 | 49.78 | 1 | 1 | 10 | 50.06 | -0.026471 | -0.405 | -4.05 | 2.975 | 2.975 | 0 | 12 | 1 | 1 | 2.975 | 10 | 0 | 0
675.55 | 49.76 | 49.76 | 1 | 1 | 10 | 50.04 | -0.014706 | -0.305 | -3.05 | 3.475 | 3.475 | 0 | 12 | 1 | 1 | 3.475 | 10 | 0 | 0
675.6 | 49.73 | 49.73 | 1 | 1 | 10 | 50.01 | 0 | -0.205 | -2.05 | 3.975 | 3.975 | 0 | 12 | 1 | 1 | 3.975 | 10 | 0 | 0
675.65 | 49.71 | 49.71 | 1 | 1 | 10 | 49.99 | 0 | -0.105 | -1.05 | 4.475 | 4.475 | 0 | 12 | 1 | 1 | 4.475 | 10 | 0 | 0
675.7 | 49.68 | 49.68 | 1 | 1 | 10 | 49.96 | 0.014706 | -0.005 | -0.05 | 4.975 | 4.975 | 0 | 12 | 1 | 1 | 4.975 | 10 | 0 | 0
675.75 | 49.65 | 49.65 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
675.8 | 49.63 | 49.63 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
675.85 | 49.6 | 49.6 | 1 | 1 | 10 | 49.88 | 0.24 | 0.14412 | 1.4412 | 5.7206 | 5.7206 | 0 | 12 | 1 | 1 | 5.7206 | 10 | 0 | 0
675.9 | 49.58 | 49.58 | 1 | 1 | 10 | 49.86 | 0.43 | 0.24412 | 2.4412 | 6.2206 | 6.2206 | 0 | 12 | 1 | 1 | 6.2206 | 10 | 0 | 0
675.95 | 49.55 | 49.55 | 1 | 1 | 10 | 49.83 | 0.715 | 0.34412 | 3.4412 | 6.7206 | 6.7206 | 0 | 12 | 1 | 1 | 6.7206 | 10 | 0 | 0
676 | 49.53 | 49.53 | 1 | 1 | 10 | 49.81 | 0.905 | 0.44412 | 4.4412 | 7.2206 | 7.2206 | 0 | 12 | 1 | 1 | 7.2206 | 10 | 0 | 0
676.05 | 49.5 | 49.5 | 1 | 1 | 10 | 49.78 | 1 | 0.54412 | 5.4412 | 7.7206 | 7.7206 | 0 | 12 | 1 | 1 | 7.7206 | 10 | 0 | 0
676.1 | 49.5 | 49.5 | 1 | 1 | 10 | 49.76 | 1 | 0.64412 | 6.4412 | 8.2206 | 8.2206 | 0 | 12 | 1 | 1 | 8.2206 | 10 | 0 | 0
676.15 | 49.53 | 49.5 | 1 | 1 | 10 | 49.73 | 1 | 0.74412 | 7.4412 | 8.7206 | 8.7206 | 0 | 12 | 1 | 1 | 8.7206 | 10 | 0 | 0
676.2 | 49.55 | 49.5 | 1 | 1 | 10 | 49.71 | 1 | 0.84412 | 8.4412 | 9.2206 | 9.2206 | 0 | 12 | 1 | 1 | 9.2206 | 10 | 0 | 0
676.25 | 49.58 | 49.5 | 1 | 1 | 10 | 49.68 | 1 | 0.94412 | 9.4412 | 9.7206 | 9.7206 | 0 | 12 | 1 | 1 | 9.7206 | 10 | 0 | 0
676.3 | 49.6 | 49.5 | 1 | 1 | 10 | 49.65 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
676.35 | 49.63 | 49.5 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
676.4 | 49.65 | 49.5 | 1 | 1 | 10 | 49.65 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
676.45 | 49.68 | 49.5 | 1 | 1 | 10 | 49.68 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
676.5 | 49.71 | 49.5 | 1 | 1 | 10 | 49.71 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
676.55 | 49.73 | 49.5 | 1 | 1 | 10 | 49.73 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
676.6 | 49.76 | 49.5 | 1 | 1 | 10 | 49.76 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
676.65 | 49.78 | 49.5 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
676.7 | 49.81 | 49.53 | 1 | 1 | 10 | 49.81 | 0.905 | 0.905 | 9.05 | 9.525 | 9.525 | 0 | 12 | 1 | 1 | 9.525 | 10 | 0 | 0
676.75 | 49.83 | 49.55 | 1 | 1 | 10 | 49.83 | 0.715 | 0.715 | 7.15 | 8.575 | 8.575 | 0 | 12 | 1 | 1 | 8.575 | 10 | 0 | 0
676.8 | 49.86 | 49.58 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
676.85 | 49.88 | 49.6 | 1 | 1 | 10 | 49.88 | 0.24 | 0.24 | 2.4 | 6.2 | 6.2 | 0 | 12 | 1 | 1 | 6.2 | 10 | 0 | 0
676.9 | 49.91 | 49.63 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
676.95 | 49.94 | 49.65 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
677 | 49.96 | 49.68 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
677.05 | 49.99 | 49.71 | 1 | 1 | 10 | 49.99 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
677.1 | 50.01 | 49.73 | 1 | 1 | 10 | 50.01 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
677.15 | 50.04 | 49.76 | 1 | 1 | 10 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 4.9265 | 4.9265 | 0 | 12 | 1 | 1 | 4.9265 | 10 | 0 | 0
677.2 | 50.06 | 49.78 | 1 | 1 | 10 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 4.8676 | 4.8676 | 0 | 12 | 1 | 1 | 4.8676 | 10 | 0 | 0
677.25 | 50.09 | 49.81 | 0.905 | 0.905 | 9.05 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 4.3044 | 4.3044 | 0 | 12 | 1 | 1 | 4.3044 | 10 | 0 | 0
677.3 | 50.12 | 49.83 | 0.715 | 0.805 | 8.05 | 50.12 | -0.24 | -0.24 | -2.4 | 2.825 | 2.825 | 0 | 12 | 1 | 1 | 2.825 | 10 | 0 | 0
677.35 | 50.14 | 49.86 | 0.43 | 0.705 | 7.05 | 50.14 | -0.43 | -0.43 | -4.3 | 1.375 | 1.375 | 0 | 12 | 1 | 1 | 1.375 | 10 | 0 | 0
677.4 | 50.17 | 49.88 | 0.24 | 0.605 | 6.05 | 50.17 | -0.715 | -0.715 | -7.15 | -0.55 | -0.55 | 0 | 12 | 1 | 1 | -0.55 | 10 | 0 | 0
677.45 | 50.19 | 49.91 | 0.044118 | 0.505 | 5.05 | 50.19 | -0.905 | -0.905 | -9.05 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
677.5 | 50.22 | 49.94 | 0.026471 | 0.405 | 4.05 | 50.22 | -1 | -1 | -10 | -2.975 | -2.975 | 0 | 12 | 1 | 1 | -2.975 | 10 | 0 | 0
677.55 | 50.24 | 49.96 | 0.014706 | 0.305 | 3.05 | 50.24 | -1 | -1 | -10 | -3.475 | -3.475 | 0 | 12 | 1 | 1 | -3.475 | 10 | 0 | 0
677.6 | 50.27 | 49.99 | 0 | 0.205 | 2.05 | 50.27 | -1 | -1 | -10 | -3.975 | -3.975 | 0 | 12 | 1 | 1 | -3.975 | 10 | 0 | 0
677.65 | 50.29 | 50.01 | 0 | 0.105 | 1.05 | 50.29 | -1 | -1 | -10 | -4.475 | -4.475 | 0 | 12 | 1 | 1 | -4.475 | 10 | 0 | 0
677.7 | 50.32 | 50.04 | -0.014706 | 0.005 | 0.05 | 50.32 | -1 | -1 | -10 | -4.975 | -4.975 | 0 | 12 | 1 | 1 | -4.975 | 10 | 0 | 0
677.75 | 50.35 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.35 | -1 | -1 | -10 | -5.1324 | -5.1324 | 0 | 12 | 1 | 1 | -5.1324 | 10 | 0 | 0
677.8 | 50.37 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 50.37 | -1 | -1 | -10 | -5.2206 | -5.2206 | 0 | 12 | 1 | 1 | -5.2206 | 10 | 0 | 0
677.85 | 50.4 | 50.12 | -0.24 | -0.14412 | -1.4412 | 50.4 | -1 | -1 | -10 | -5.7206 | -5.7206 | 0 | 12 | 1 | 1 | -5.7206 | 10 | 0 | 0
677.9 | 50.42 | 50.14 | -0.43 | -0.24412 | -2.4412 | 50.42 | -1 | -1 | -10 | -6.2206 | -6.2206 | 0 | 12 | 1 | 1 | -6.2206 | 10 | 0 | 0
677.95 | 50.45 | 50.17 | -0.715 | -0.34412 | -3.4412 | 50.45 | -1 | -1 | -10 | -6.7206 | -6.7206 | 0 | 12 | 1 | 1 | -6.7206 | 10 | 0 | 0
678 | 50.47 | 50.19 | -0.905 | -0.44412 | -4.4412 | 50.47 | -1 | -1 | -10 | -7.2206 | -7.2206 | 0 | 12 | 1 | 1 | -7.2206 | 10 | 0 | 0
678.05 | 50.5 | 50.22 | -1 | -0.54412 | -5.4412 | 50.5 | -1 | -1 | -10 | -7.7206 | -7.7206 | 0 | 12 | 1 | 1 | -7.7206 | 10 | 0 | 0
678.1 | 50.5 | 50.24 | -1 | -0.64412 | -6.4412 | 50.5 | -1 | -1 | -10 | -8.2206 | -8.2206 | 0 | 12 | 1 | 1 | -8.2206 | 10 | 0 | 0
678.15 | 50.47 | 50.27 | -1 | -0.74412 | -7.4412 | 50.5 | -1 | -1 | -10 | -8.7206 | -8.7206 | 0 | 12 | 1 | 1 | -8.7206 | 10 | 0 | 0
678.2 | 50.45 | 50.29 | -1 | -0.84412 | -8.4412 | 50.5 | -1 | -1 | -10 | -9.2206 | -9.2206 | 0 | 12 | 1 | 1 | -9.2206 | 10 | 0 | 0
678.25 | 50.42 | 50.32 | -1 | -0.94412 | -9.4412 | 50.5 | -1 | -1 | -10 | -9.7206 | -9.7206 | 0 | 12 | 1 | 1 | -9.7206 | 10 | 0 | 0
678.3 | 50.39 | 50.35 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
678.35 | 50.37 | 50.37 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
678.4 | 50.34 | 50.34 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
678.45 | 50.32 | 50.32 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
678.5 | 50.29 | 50.29 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
678.55 | 50.26 | 50.26 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
678.6 | 50.24 | 50.24 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
678.65 | 50.21 | 50.21 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
678.7 | 50.18 | 50.18 | -0.81 | -0.81 | -8.1 | 50.47 | -1 | -1 | -10 | -9.05 | -9.05 | 0 | 12 | 1 | 1 | -9.05 | 10 | 0 | 0
678.75 | 50.16 | 50.16 | -0.62 | -0.62 | -6.2 | 50.45 | -1 | -1 | -10 | -8.1 | -8.1 | 0 | 12 | 1 | 1 | -8.1 | 10 | 0 | 0
678.8 | 50.13 | 50.13 | -0.335 | -0.335 | -3.35 | 50.42 | -1 | -1 | -10 | -6.675 | -6.675 | 0 | 12 | 1 | 1 | -6.675 | 10 | 0 | 0
678.85 | 50.11 | 50.11 | -0.145 | -0.145 | -1.45 | 50.39 | -1 | -1 | -10 | -5.725 | -5.725 | 0 | 12 | 1 | 1 | -5.725 | 10 | 0 | 0
678.9 | 50.08 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 50.37 | -1 | -1 | -10 | -5.1912 | -5.1912 | 0 | 12 | 1 | 1 | -5.1912 | 10 | 0 | 0
678.95 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.34 | -1 | -1 | -10 | -5.1029 | -5.1029 | 0 | 12 | 1 | 1 | -5.1029 | 10 | 0 | 0
679 | 50.03 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 50.32 | -1 | -1 | -10 | -5.0441 | -5.0441 | 0 | 12 | 1 | 1 | -5.0441 | 10 | 0 | 0
679.05 | 50 | 50 | 0 | 0 | 0 | 50.29 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
679.1 | 50 | 50 | 0 | 0 | 0 | 50.26 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
679.15 | 50 | 50 | 0 | 0 | 0 | 50.24 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
679.2 | 50 | 50 | 0 | 0 | 0 | 50.21 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
679.25 | 50 | 50 | 0 | 0 | 0 | 50.18 | -0.81 | -0.9 | -9 | -4.5 | -4.5 | 0 | 12 | 1 | 1 | -4.5 | 10 | 0 | 0
679.3 | 50 | 50 | 0 | 0 | 0 | 50.16 | -0.62 | -0.8 | -8 | -4 | -4 | 0 | 12 | 1 | 1 | -4 | 10 | 0 | 0
679.35 | 50 | 50 | 0 | 0 | 0 | 50.13 | -0.335 | -0.7 | -7 | -3.5 | -3.5 | 0 | 12 | 1 | 1 | -3.5 | 10 | 0 | 0
679.4 | 50.01 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.6 | -6 | -3 | -3 | 0 | 12 | 1 | 1 | -3 | 10 | 0 | 0
679.45 | 50.01 | 50 | 0 | 0 | 0 | 50.08 | -0.038235 | -0.5 | -5 | -2.5 | -2.5 | 0 | 12 | 1 | 1 | -2.5 | 10 | 0 | 0
679.5 | 49.99 | 49.99 | 0 | 0 | 0 | 50.05 | -0.020588 | -0.4 | -4 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
679.55 | 49.99 | 49.99 | 0 | 0 | 0 | 50.03 | -0.0088235 | -0.3 | -3 | -1.5 | -1.5 | 0 | 12 | 1 | 1 | -1.5 | 10 | 0 | 0
679.6 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | -0.2 | -2 | -0.83824 | -0.83824 | 0 | 12 | 1 | 1 | -0.83824 | 10 | 0 | 0
679.65 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | -0.1 | -1 | -0.33824 | -0.33824 | 0 | 12 | 1 | 1 | -0.33824 | 10 | 0 | 0
679.7 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
679.75 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
679.8 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
679.85 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
679.9 | 49.89 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
679.95 | 49.89 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
680 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50.01 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
680.05 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
680.1 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
680.15 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 2.7868 | 2.7868 | 0 | 12 | 1 | 1 | 2.7868 | 10 | 0 | 0
680.2 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 2.7868 | 2.7868 | 0 | 12 | 1 | 1 | 2.7868 | 10 | 0 | 0
680.25 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 2.8456 | 2.8456 | 0 | 12 | 1 | 1 | 2.8456 | 10 | 0 | 0
680.3 | 49.94 | 49.85 | 0.525 | 0.525 | 5.25 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 2.7574 | 2.7574 | 0 | 12 | 1 | 1 | 2.7574 | 10 | 0 | 0
680.35 | 49.94 | 49.85 | 0.525 | 0.525 | 5.25 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 2.7574 | 2.7574 | 0 | 12 | 1 | 1 | 2.7574 | 10 | 0 | 0
680.4 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
680.45 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
680.5 | 49.93 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
680.55 | 49.93 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
680.6 | 49.96 | 49.85 | 0.525 | 0.525 | 5.25 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 2.6985 | 2.6985 | 0 | 12 | 1 | 1 | 2.6985 | 10 | 0 | 0
680.65 | 49.96 | 49.85 | 0.525 | 0.525 | 5.25 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 2.6985 | 2.6985 | 0 | 12 | 1 | 1 | 2.6985 | 10 | 0 | 0
680.7 | 49.99 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
680.75 | 49.99 | 49.91 | 0.044118 | 0.425 | 4.25 | 49.99 | 0 | 0 | 0 | 2.125 | 2.125 | 0 | 12 | 1 | 1 | 2.125 | 10 | 0 | 0
680.8 | 49.99 | 49.91 | 0.044118 | 0.325 | 3.25 | 49.99 | 0 | 0 | 0 | 1.625 | 1.625 | 0 | 12 | 1 | 1 | 1.625 | 10 | 0 | 0
680.85 | 49.99 | 49.93 | 0.032353 | 0.225 | 2.25 | 49.99 | 0 | 0 | 0 | 1.125 | 1.125 | 0 | 12 | 1 | 1 | 1.125 | 10 | 0 | 0
680.9 | 49.96 | 49.93 | 0.032353 | 0.125 | 1.25 | 49.99 | 0 | 0 | 0 | 0.625 | 0.625 | 0 | 12 | 1 | 1 | 0.625 | 10 | 0 | 0
680.95 | 49.96 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 49.99 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
681 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
681.05 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
681.1 | 50.05 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.058824 | 0.058824 | 0 | 12 | 1 | 1 | 0.058824 | 10 | 0 | 0
681.15 | 50.05 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
681.2 | 49.97 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
681.25 | 49.97 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
681.3 | 49.92 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
681.35 | 49.92 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
681.4 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
681.45 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
681.5 | 49.94 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
681.55 | 49.94 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
681.6 | 50.01 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
681.65 | 50.01 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
681.7 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
681.75 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
681.8 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
681.85 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
681.9 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
681.95 | 49.95 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
682 | 49.97 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
682.05 | 49.97 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
682.1 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
682.15 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
682.2 | 49.87 | 49.87 | 0.335 | 0.335 | 3.35 | 50.01 | 0 | 0 | 0 | 1.675 | 1.675 | 0 | 12 | 1 | 1 | 1.675 | 10 | 0 | 0
682.25 | 49.87 | 49.87 | 0.335 | 0.335 | 3.35 | 49.99 | 0 | 0 | 0 | 1.675 | 1.675 | 0 | 12 | 1 | 1 | 1.675 | 10 | 0 | 0
682.3 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
682.35 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 2.6691 | 2.6691 | 0 | 12 | 1 | 1 | 2.6691 | 10 | 0 | 0
682.4 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
682.45 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
682.5 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
682.55 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
682.6 | 49.84 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
682.65 | 49.84 | 49.79 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
682.7 | 49.89 | 49.79 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
682.75 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.12647 | 1.2647 | 5.6324 | 5.6324 | 0 | 12 | 1 | 1 | 5.6324 | 10 | 0 | 0
682.8 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.145 | 1.45 | 5.725 | 5.725 | 0 | 12 | 1 | 1 | 5.725 | 10 | 0 | 0
682.85 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.145 | 1.45 | 5.725 | 5.725 | 0 | 12 | 1 | 1 | 5.725 | 10 | 0 | 0
682.9 | 49.96 | 49.79 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
682.95 | 49.96 | 49.79 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
683 | 50.02 | 49.79 | 1 | 1 | 10 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 4.9853 | 4.9853 | 0 | 12 | 1 | 1 | 4.9853 | 10 | 0 | 0
683.05 | 50.02 | 49.79 | 1 | 1 | 10 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 4.9853 | 4.9853 | 0 | 12 | 1 | 1 | 4.9853 | 10 | 0 | 0
683.1 | 50.03 | 49.79 | 1 | 1 | 10 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.9559 | 4.9559 | 0 | 12 | 1 | 1 | 4.9559 | 10 | 0 | 0
683.15 | 50.03 | 49.84 | 0.62 | 0.9 | 9 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.4559 | 4.4559 | 0 | 12 | 1 | 1 | 4.4559 | 10 | 0 | 0
683.2 | 50.02 | 49.84 | 0.62 | 0.8 | 8 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 3.9559 | 3.9559 | 0 | 12 | 1 | 1 | 3.9559 | 10 | 0 | 0
683.25 | 50.02 | 49.89 | 0.145 | 0.7 | 7 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 3.4559 | 3.4559 | 0 | 12 | 1 | 1 | 3.4559 | 10 | 0 | 0
683.3 | 50.08 | 49.89 | 0.145 | 0.6 | 6 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 2.8088 | 2.8088 | 0 | 12 | 1 | 1 | 2.8088 | 10 | 0 | 0
683.35 | 50.08 | 49.89 | 0.145 | 0.5 | 5 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 2.3088 | 2.3088 | 0 | 12 | 1 | 1 | 2.3088 | 10 | 0 | 0
683.4 | 50.01 | 49.89 | 0.145 | 0.4 | 4 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 1.8088 | 1.8088 | 0 | 12 | 1 | 1 | 1.8088 | 10 | 0 | 0
683.45 | 50.01 | 49.96 | 0.014706 | 0.3 | 3 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 1.3088 | 1.3088 | 0 | 12 | 1 | 1 | 1.3088 | 10 | 0 | 0
683.5 | 49.94 | 49.94 | 0.026471 | 0.2 | 2 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.80882 | 0.80882 | 0 | 12 | 1 | 1 | 0.80882 | 10 | 0 | 0
683.55 | 49.94 | 49.94 | 0.026471 | 0.1 | 1 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.30882 | 0.30882 | 0 | 12 | 1 | 1 | 0.30882 | 10 | 0 | 0
683.6 | 50 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
683.65 | 50 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
683.7 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
683.75 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
683.8 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
683.85 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
683.9 | 49.92 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
683.95 | 49.92 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
684 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50.01 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
684.05 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
684.1 | 49.92 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
684.15 | 49.92 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
684.2 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
684.25 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
684.3 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
684.35 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
684.4 | 49.87 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
684.45 | 49.87 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
684.5 | 49.8 | 49.8 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
684.55 | 49.8 | 49.8 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
684.6 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
684.65 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
684.7 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
684.75 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
684.8 | 49.72 | 49.72 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
684.85 | 49.72 | 49.72 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
684.9 | 49.67 | 49.67 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
684.95 | 49.67 | 49.67 | 1 | 1 | 10 | 49.87 | 0.335 | 0.14412 | 1.4412 | 5.7206 | 5.7206 | 0 | 12 | 1 | 1 | 5.7206 | 10 | 0 | 0
685 | 49.65 | 49.65 | 1 | 1 | 10 | 49.87 | 0.335 | 0.24412 | 2.4412 | 6.2206 | 6.2206 | 0 | 12 | 1 | 1 | 6.2206 | 10 | 0 | 0
685.05 | 49.65 | 49.65 | 1 | 1 | 10 | 49.8 | 1 | 0.34412 | 3.4412 | 6.7206 | 6.7206 | 0 | 12 | 1 | 1 | 6.7206 | 10 | 0 | 0
685.1 | 49.59 | 49.59 | 1 | 1 | 10 | 49.8 | 1 | 0.44412 | 4.4412 | 7.2206 | 7.2206 | 0 | 12 | 1 | 1 | 7.2206 | 10 | 0 | 0
685.15 | 49.59 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.54412 | 5.4412 | 7.7206 | 7.7206 | 0 | 12 | 1 | 1 | 7.7206 | 10 | 0 | 0
685.2 | 49.66 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.64412 | 6.4412 | 8.2206 | 8.2206 | 0 | 12 | 1 | 1 | 8.2206 | 10 | 0 | 0
685.25 | 49.66 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.74412 | 7.4412 | 8.7206 | 8.7206 | 0 | 12 | 1 | 1 | 8.7206 | 10 | 0 | 0
685.3 | 49.63 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.84412 | 8.4412 | 9.2206 | 9.2206 | 0 | 12 | 1 | 1 | 9.2206 | 10 | 0 | 0
685.35 | 49.63 | 49.59 | 1 | 1 | 10 | 49.72 | 1 | 0.94412 | 9.4412 | 9.7206 | 9.7206 | 0 | 12 | 1 | 1 | 9.7206 | 10 | 0 | 0
685.4 | 49.61 | 49.59 | 1 | 1 | 10 | 49.72 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
685.45 | 49.61 | 49.59 | 1 | 1 | 10 | 49.67 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
685.5 | 49.54 | 49.54 | 1 | 1 | 10 | 49.67 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
685.55 | 49.54 | 49.54 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
685.6 | 49.46 | 49.46 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
685.65 | 49.46 | 49.46 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
685.7 | 49.45 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
685.75 | 49.45 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
685.8 | 49.51 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
685.85 | 49.51 | 49.45 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
685.9 | 49.5 | 49.45 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
685.95 | 49.5 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
686 | 49.54 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
686.05 | 49.54 | 49.45 | 1 | 1 | 10 | 49.54 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
686.1 | 49.59 | 49.45 | 1 | 1 | 10 | 49.59 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
686.15 | 49.59 | 49.45 | 1 | 1 | 10 | 49.59 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
686.2 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
686.25 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
686.3 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
686.35 | 49.61 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
686.4 | 49.53 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
686.45 | 49.53 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
686.5 | 49.54 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
686.55 | 49.54 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
686.6 | 49.61 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
686.65 | 49.61 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
686.7 | 49.66 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
686.75 | 49.66 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
686.8 | 49.64 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
686.85 | 49.64 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
686.9 | 49.69 | 49.53 | 1 | 1 | 10 | 49.69 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
686.95 | 49.69 | 49.53 | 1 | 1 | 10 | 49.69 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
687 | 49.74 | 49.53 | 1 | 1 | 10 | 49.74 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
687.05 | 49.74 | 49.54 | 1 | 1 | 10 | 49.74 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
687.1 | 49.78 | 49.54 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
687.15 | 49.78 | 49.61 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
687.2 | 49.82 | 49.61 | 1 | 1 | 10 | 49.82 | 0.81 | 0.81 | 8.1 | 9.05 | 9.05 | 0 | 12 | 1 | 1 | 9.05 | 10 | 0 | 0
687.25 | 49.82 | 49.64 | 1 | 1 | 10 | 49.82 | 0.81 | 0.81 | 8.1 | 9.05 | 9.05 | 0 | 12 | 1 | 1 | 9.05 | 10 | 0 | 0
687.3 | 49.86 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
687.35 | 49.86 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
687.4 | 49.84 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
687.45 | 49.84 | 49.69 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
687.5 | 49.91 | 49.69 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
687.55 | 49.91 | 49.74 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
687.6 | 49.97 | 49.74 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
687.65 | 49.97 | 49.78 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
687.7 | 50.03 | 49.78 | 1 | 1 | 10 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.9559 | 4.9559 | 0 | 12 | 1 | 1 | 4.9559 | 10 | 0 | 0
687.75 | 50.03 | 49.82 | 0.81 | 0.9 | 9 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.4559 | 4.4559 | 0 | 12 | 1 | 1 | 4.4559 | 10 | 0 | 0
687.8 | 50.05 | 49.82 | 0.81 | 0.81 | 8.1 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 3.9471 | 3.9471 | 0 | 12 | 1 | 1 | 3.9471 | 10 | 0 | 0
687.85 | 50.05 | 49.84 | 0.62 | 0.71 | 7.1 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 3.4471 | 3.4471 | 0 | 12 | 1 | 1 | 3.4471 | 10 | 0 | 0
687.9 | 50.01 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
687.95 | 50.01 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
688 | 49.95 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
688.05 | 49.95 | 49.91 | 0.044118 | 0.52 | 5.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.4971 | 2.4971 | 0 | 12 | 1 | 1 | 2.4971 | 10 | 0 | 0
688.1 | 49.99 | 49.91 | 0.044118 | 0.42 | 4.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 1.9971 | 1.9971 | 0 | 12 | 1 | 1 | 1.9971 | 10 | 0 | 0
688.15 | 49.99 | 49.95 | 0.020588 | 0.32 | 3.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 1.4971 | 1.4971 | 0 | 12 | 1 | 1 | 1.4971 | 10 | 0 | 0
688.2 | 49.92 | 49.92 | 0.038235 | 0.22 | 2.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.99706 | 0.99706 | 0 | 12 | 1 | 1 | 0.99706 | 10 | 0 | 0
688.25 | 49.92 | 49.92 | 0.038235 | 0.12 | 1.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.49706 | 0.49706 | 0 | 12 | 1 | 1 | 0.49706 | 10 | 0 | 0
688.3 | 49.97 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
688.35 | 49.97 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
688.4 | 50.02 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
688.45 | 50.02 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.17647 | 0.17647 | 0 | 12 | 1 | 1 | 0.17647 | 10 | 0 | 0
688.5 | 50.07 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
688.55 | 50.07 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
688.6 | 50.06 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
688.65 | 50.06 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
688.7 | 50.13 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
688.75 | 50.13 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
688.8 | 50.09 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
688.85 | 50.09 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6309 | -1.6309 | 0 | 12 | 1 | 1 | -1.6309 | 10 | 0 | 0
688.9 | 50.07 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6309 | -1.6309 | 0 | 12 | 1 | 1 | -1.6309 | 10 | 0 | 0
688.95 | 50.07 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6897 | -1.6897 | 0 | 12 | 1 | 1 | -1.6897 | 10 | 0 | 0
689 | 50.07 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6897 | -1.6897 | 0 | 12 | 1 | 1 | -1.6897 | 10 | 0 | 0
689.05 | 50.07 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.13 | -0.335 | -0.335 | -3.35 | -1.8074 | -1.8074 | 0 | 12 | 1 | 1 | -1.8074 | 10 | 0 | 0
689.1 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.13 | -0.335 | -0.335 | -3.35 | -1.7779 | -1.7779 | 0 | 12 | 1 | 1 | -1.7779 | 10 | 0 | 0
689.15 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.13 | -0.335 | -0.335 | -3.35 | -1.7779 | -1.7779 | 0 | 12 | 1 | 1 | -1.7779 | 10 | 0 | 0
689.2 | 50.01 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
689.25 | 50.01 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
689.3 | 50.07 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
689.35 | 50.07 | 50.01 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.235 | -2.35 | -1.175 | -1.175 | 0 | 12 | 1 | 1 | -1.175 | 10 | 0 | 0
689.4 | 50.05 | 50.01 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.135 | -1.35 | -0.675 | -0.675 | 0 | 12 | 1 | 1 | -0.675 | 10 | 0 | 0
689.45 | 50.05 | 50.01 | 0 | 0 | 0 | 50.07 | -0.032353 | -0.035 | -0.35 | -0.175 | -0.175 | 0 | 12 | 1 | 1 | -0.175 | 10 | 0 | 0
689.5 | 50.1 | 50.01 | 0 | 0 | 0 | 50.1 | -0.05 | -0.05 | -0.5 | -0.25 | -0.25 | 0 | 12 | 1 | 1 | -0.25 | 10 | 0 | 0
689.55 | 50.1 | 50.01 | 0 | 0 | 0 | 50.1 | -0.05 | -0.05 | -0.5 | -0.25 | -0.25 | 0 | 12 | 1 | 1 | -0.25 | 10 | 0 | 0
689.6 | 50.11 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
689.65 | 50.11 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
689.7 | 50.06 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
689.75 | 50.06 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
689.8 | 50.04 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
689.85 | 50.04 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
689.9 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
689.95 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
690 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
690.05 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
690.1 | 50.11 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
690.15 | 50.11 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
690.2 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
690.25 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
690.3 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
690.35 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
690.4 | 50.02 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.11 | -0.145 | -0.145 | -1.45 | -0.73971 | -0.73971 | 0 | 12 | 1 | 1 | -0.73971 | 10 | 0 | 0
690.45 | 50.02 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.11 | -0.145 | -0.145 | -1.45 | -0.73971 | -0.73971 | 0 | 12 | 1 | 1 | -0.73971 | 10 | 0 | 0
690.5 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
690.55 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
690.6 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
690.65 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
690.7 | 50.01 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
690.75 | 50.01 | 50 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.045 | -0.45 | -0.225 | -0.225 | 0 | 12 | 1 | 1 | -0.225 | 10 | 0 | 0
690.8 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
690.85 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
690.9 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
690.95 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
691 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.14706 | 0.14706 | 0 | 12 | 1 | 1 | 0.14706 | 10 | 0 | 0
691.05 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
691.1 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
691.15 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
691.2 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
691.25 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
691.3 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
691.35 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
691.4 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
691.45 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
691.5 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
691.55 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
691.6 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
691.65 | 50 | 50 | 0 | 0 | 0 | 50.01 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
691.7 | 49.5 | 49.5 | 1 | 1 | 10 | 50.01 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
691.75 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
691.8 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
691.85 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
691.9 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
691.95 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
692 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
692.05 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
692.1 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
692.15 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
692.2 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
692.25 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.1 | 1 | 5.5 | 5.5 | 0 | 12 | 1 | 1 | 5.5 | 10 | 0 | 0
692.3 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.2 | 2 | 6 | 6 | 0 | 12 | 1 | 1 | 6 | 10 | 0 | 0
692.35 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.3 | 3 | 6.5 | 6.5 | 0 | 12 | 1 | 1 | 6.5 | 10 | 0 | 0
692.4 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.4 | 4 | 7 | 7 | 0 | 12 | 1 | 1 | 7 | 10 | 0 | 0
692.45 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.5 | 5 | 7.5 | 7.5 | 0 | 12 | 1 | 1 | 7.5 | 10 | 0 | 0
692.5 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.6 | 6 | 8 | 8 | 0 | 12 | 1 | 1 | 8 | 10 | 0 | 0
692.55 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.7 | 7 | 8.5 | 8.5 | 0 | 12 | 1 | 1 | 8.5 | 10 | 0 | 0
692.6 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.8 | 8 | 9 | 9 | 0 | 12 | 1 | 1 | 9 | 10 | 0 | 0
692.65 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.9 | 9 | 9.5 | 9.5 | 0 | 12 | 1 | 1 | 9.5 | 10 | 0 | 0
692.7 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
692.75 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
692.8 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
692.85 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
692.9 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
692.95 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
693 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
693.05 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
693.1 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
693.15 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
693.2 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
693.25 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
693.3 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
693.35 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
693.4 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
693.45 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
693.5 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
693.55 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
693.6 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
693.65 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
693.7 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
693.75 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
693.8 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
693.85 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
693.9 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
693.95 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
694 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
694.05 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
694.1 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
694.15 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
694.2 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
694.25 | 50.5 | 50.5 | -1 | 0.9 | 9 | 50.5 | -1 | -1 | -10 | -0.5 | -0.5 | 0 | 12 | 1 | 1 | -0.5 | 10 | 0 | 0
694.3 | 50.5 | 50.5 | -1 | 0.8 | 8 | 50.5 | -1 | -1 | -10 | -1 | -1 | 0 | 12 | 1 | 1 | -1 | 10 | 0 | 0
694.35 | 50.5 | 50.5 | -1 | 0.7 | 7 | 50.5 | -1 | -1 | -10 | -1.5 | -1.5 | 0 | 12 | 1 | 1 | -1.5 | 10 | 0 | 0
694.4 | 50.5 | 50.5 | -1 | 0.6 | 6 | 50.5 | -1 | -1 | -10 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
694.45 | 50.5 | 50.5 | -1 | 0.5 | 5 | 50.5 | -1 | -1 | -10 | -2.5 | -2.5 | 0 | 12 | 1 | 1 | -2.5 | 10 | 0 | 0
694.5 | 50.5 | 50.5 | -1 | 0.4 | 4 | 50.5 | -1 | -1 | -10 | -3 | -3 | 0 | 12 | 1 | 1 | -3 | 10 | 0 | 0
694.55 | 50.5 | 50.5 | -1 | 0.3 | 3 | 50.5 | -1 | -1 | -10 | -3.5 | -3.5 | 0 | 12 | 1 | 1 | -3.5 | 10 | 0 | 0
694.6 | 50.5 | 50.5 | -1 | 0.2 | 2 | 50.5 | -1 | -1 | -10 | -4 | -4 | 0 | 12 | 1 | 1 | -4 | 10 | 0 | 0
694.65 | 50.5 | 50.5 | -1 | 0.1 | 1 | 50.5 | -1 | -1 | -10 | -4.5 | -4.5 | 0 | 12 | 1 | 1 | -4.5 | 10 | 0 | 0
694.7 | 50.5 | 50.5 | -1 | 0 | 0 | 50.5 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
694.75 | 50.5 | 50.5 | -1 | -0.1 | -1 | 50.5 | -1 | -1 | -10 | -5.5 | -5.5 | 0 | 12 | 1 | 1 | -5.5 | 10 | 0 | 0
694.8 | 50.5 | 50.5 | -1 | -0.2 | -2 | 50.5 | -1 | -1 | -10 | -6 | -6 | 0 | 12 | 1 | 1 | -6 | 10 | 0 | 0
694.85 | 50.5 | 50.5 | -1 | -0.3 | -3 | 50.5 | -1 | -1 | -10 | -6.5 | -6.5 | 0 | 12 | 1 | 1 | -6.5 | 10 | 0 | 0
694.9 | 50.5 | 50.5 | -1 | -0.4 | -4 | 50.5 | -1 | -1 | -10 | -7 | -7 | 0 | 12 | 1 | 1 | -7 | 10 | 0 | 0
694.95 | 50.5 | 50.5 | -1 | -0.5 | -5 | 50.5 | -1 | -1 | -10 | -7.5 | -7.5 | 0 | 12 | 1 | 1 | -7.5 | 10 | 0 | 0
695 | 50.5 | 50.5 | -1 | -0.6 | -6 | 50.5 | -1 | -1 | -10 | -8 | -8 | 0 | 12 | 1 | 1 | -8 | 10 | 0 | 0
695.05 | 50.5 | 50.5 | -1 | -0.7 | -7 | 50.5 | -1 | -1 | -10 | -8.5 | -8.5 | 0 | 12 | 1 | 1 | -8.5 | 10 | 0 | 0
695.1 | 50.5 | 50.5 | -1 | -0.8 | -8 | 50.5 | -1 | -1 | -10 | -9 | -9 | 0 | 12 | 1 | 1 | -9 | 10 | 0 | 0
695.15 | 50.5 | 50.5 | -1 | -0.9 | -9 | 50.5 | -1 | -1 | -10 | -9.5 | -9.5 | 0 | 12 | 1 | 1 | -9.5 | 10 | 0 | 0
695.2 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
695.25 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
695.3 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
695.35 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
695.4 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
695.45 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
695.5 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
695.55 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
695.6 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
695.65 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
695.7 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
695.75 | 50.47 | 50.47 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
695.8 | 50.45 | 50.45 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
695.85 | 50.42 | 50.42 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
695.9 | 50.4 | 50.4 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
695.95 | 50.37 | 50.37 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
696 | 50.35 | 50.35 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
696.05 | 50.32 | 50.32 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
696.1 | 50.29 | 50.29 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
696.15 | 50.27 | 50.27 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
696.2 | 50.24 | 50.24 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
696.25 | 50.22 | 50.22 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
696.3 | 50.19 | 50.19 | -0.905 | -0.905 | -9.05 | 50.47 | -1 | -1 | -10 | -9.525 | -9.525 | 0 | 12 | 1 | 1 | -9.525 | 10 | 0 | 0
696.35 | 50.17 | 50.17 | -0.715 | -0.715 | -7.15 | 50.45 | -1 | -1 | -10 | -8.575 | -8.575 | 0 | 12 | 1 | 1 | -8.575 | 10 | 0 | 0
696.4 | 50.14 | 50.14 | -0.43 | -0.43 | -4.3 | 50.42 | -1 | -1 | -10 | -7.15 | -7.15 | 0 | 12 | 1 | 1 | -7.15 | 10 | 0 | 0
696.45 | 50.12 | 50.12 | -0.24 | -0.24 | -2.4 | 50.4 | -1 | -1 | -10 | -6.2 | -6.2 | 0 | 12 | 1 | 1 | -6.2 | 10 | 0 | 0
696.5 | 50.09 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 50.37 | -1 | -1 | -10 | -5.2206 | -5.2206 | 0 | 12 | 1 | 1 | -5.2206 | 10 | 0 | 0
696.55 | 50.06 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.35 | -1 | -1 | -10 | -5.1324 | -5.1324 | 0 | 12 | 1 | 1 | -5.1324 | 10 | 0 | 0
696.6 | 50.04 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.32 | -1 | -1 | -10 | -5.0735 | -5.0735 | 0 | 12 | 1 | 1 | -5.0735 | 10 | 0 | 0
696.65 | 50.01 | 50.01 | 0 | 0 | 0 | 50.29 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
696.7 | 49.99 | 49.99 | 0 | 0 | 0 | 50.27 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
696.75 | 49.96 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.24 | -1 | -1 | -10 | -4.9265 | -4.9265 | 0 | 12 | 1 | 1 | -4.9265 | 10 | 0 | 0
696.8 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.22 | -1 | -1 | -10 | -4.8676 | -4.8676 | 0 | 12 | 1 | 1 | -4.8676 | 10 | 0 | 0
696.85 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.19 | -0.905 | -0.905 | -9.05 | -4.3044 | -4.3044 | 0 | 12 | 1 | 1 | -4.3044 | 10 | 0 | 0
696.9 | 49.88 | 49.88 | 0.24 | 0.24 | 2.4 | 50.17 | -0.715 | -0.805 | -8.05 | -2.825 | -2.825 | 0 | 12 | 1 | 1 | -2.825 | 10 | 0 | 0
696.95 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.14 | -0.43 | -0.705 | -7.05 | -1.375 | -1.375 | 0 | 12 | 1 | 1 | -1.375 | 10 | 0 | 0
697 | 49.83 | 49.83 | 0.715 | 0.715 | 7.15 | 50.12 | -0.24 | -0.605 | -6.05 | 0.55 | 0.55 | 0 | 12 | 1 | 1 | 0.55 | 10 | 0 | 0
697.05 | 49.81 | 49.81 | 0.905 | 0.905 | 9.05 | 50.09 | -0.044118 | -0.505 | -5.05 | 2 | 2 | 0 | 12 | 1 | 1 | 2 | 10 | 0 | 0
697.1 | 49.78 | 49.78 | 1 | 1 | 10 | 50.06 | -0.026471 | -0.405 | -4.05 | 2.975 | 2.975 | 0 | 12 | 1 | 1 | 2.975 | 10 | 0 | 0
697.15 | 49.76 | 49.76 | 1 | 1 | 10 | 50.04 | -0.014706 | -0.305 | -3.05 | 3.475 | 3.475 | 0 | 12 | 1 | 1 | 3.475 | 10 | 0 | 0
697.2 | 49.73 | 49.73 | 1 | 1 | 10 | 50.01 | 0 | -0.205 | -2.05 | 3.975 | 3.975 | 0 | 12 | 1 | 1 | 3.975 | 10 | 0 | 0
697.25 | 49.71 | 49.71 | 1 | 1 | 10 | 49.99 | 0 | -0.105 | -1.05 | 4.475 | 4.475 | 0 | 12 | 1 | 1 | 4.475 | 10 | 0 | 0
697.3 | 49.68 | 49.68 | 1 | 1 | 10 | 49.96 | 0.014706 | -0.005 | -0.05 | 4.975 | 4.975 | 0 | 12 | 1 | 1 | 4.975 | 10 | 0 | 0
697.35 | 49.65 | 49.65 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
697.4 | 49.63 | 49.63 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
697.45 | 49.6 | 49.6 | 1 | 1 | 10 | 49.88 | 0.24 | 0.14412 | 1.4412 | 5.7206 | 5.7206 | 0 | 12 | 1 | 1 | 5.7206 | 10 | 0 | 0
697.5 | 49.58 | 49.58 | 1 | 1 | 10 | 49.86 | 0.43 | 0.24412 | 2.4412 | 6.2206 | 6.2206 | 0 | 12 | 1 | 1 | 6.2206 | 10 | 0 | 0
697.55 | 49.55 | 49.55 | 1 | 1 | 10 | 49.83 | 0.715 | 0.34412 | 3.4412 | 6.7206 | 6.7206 | 0 | 12 | 1 | 1 | 6.7206 | 10 | 0 | 0
697.6 | 49.53 | 49.53 | 1 | 1 | 10 | 49.81 | 0.905 | 0.44412 | 4.4412 | 7.2206 | 7.2206 | 0 | 12 | 1 | 1 | 7.2206 | 10 | 0 | 0
697.65 | 49.5 | 49.5 | 1 | 1 | 10 | 49.78 | 1 | 0.54412 | 5.4412 | 7.7206 | 7.7206 | 0 | 12 | 1 | 1 | 7.7206 | 10 | 0 | 0
697.7 | 49.5 | 49.5 | 1 | 1 | 10 | 49.76 | 1 | 0.64412 | 6.4412 | 8.2206 | 8.2206 | 0 | 12 | 1 | 1 | 8.2206 | 10 | 0 | 0
697.75 | 49.53 | 49.5 | 1 | 1 | 10 | 49.73 | 1 | 0.74412 | 7.4412 | 8.7206 | 8.7206 | 0 | 12 | 1 | 1 | 8.7206 | 10 | 0 | 0
697.8 | 49.55 | 49.5 | 1 | 1 | 10 | 49.71 | 1 | 0.84412 | 8.4412 | 9.2206 | 9.2206 | 0 | 12 | 1 | 1 | 9.2206 | 10 | 0 | 0
697.85 | 49.58 | 49.5 | 1 | 1 | 10 | 49.68 | 1 | 0.94412 | 9.4412 | 9.7206 | 9.7206 | 0 | 12 | 1 | 1 | 9.7206 | 10 | 0 | 0
697.9 | 49.6 | 49.5 | 1 | 1 | 10 | 49.65 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
697.95 | 49.63 | 49.5 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
698 | 49.65 | 49.5 | 1 | 1 | 10 | 49.65 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
698.05 | 49.68 | 49.5 | 1 | 1 | 10 | 49.68 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
698.1 | 49.71 | 49.5 | 1 | 1 | 10 | 49.71 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
698.15 | 49.73 | 49.5 | 1 | 1 | 10 | 49.73 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
698.2 | 49.76 | 49.5 | 1 | 1 | 10 | 49.76 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
698.25 | 49.78 | 49.5 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
698.3 | 49.81 | 49.53 | 1 | 1 | 10 | 49.81 | 0.905 | 0.905 | 9.05 | 9.525 | 9.525 | 0 | 12 | 1 | 1 | 9.525 | 10 | 0 | 0
698.35 | 49.83 | 49.55 | 1 | 1 | 10 | 49.83 | 0.715 | 0.715 | 7.15 | 8.575 | 8.575 | 0 | 12 | 1 | 1 | 8.575 | 10 | 0 | 0
698.4 | 49.86 | 49.58 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
698.45 | 49.88 | 49.6 | 1 | 1 | 10 | 49.88 | 0.24 | 0.24 | 2.4 | 6.2 | 6.2 | 0 | 12 | 1 | 1 | 6.2 | 10 | 0 | 0
698.5 | 49.91 | 49.63 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
698.55 | 49.94 | 49.65 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
698.6 | 49.96 | 49.68 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
698.65 | 49.99 | 49.71 | 1 | 1 | 10 | 49.99 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
698.7 | 50.01 | 49.73 | 1 | 1 | 10 | 50.01 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
698.75 | 50.04 | 49.76 | 1 | 1 | 10 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 4.9265 | 4.9265 | 0 | 12 | 1 | 1 | 4.9265 | 10 | 0 | 0
698.8 | 50.06 | 49.78 | 1 | 1 | 10 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 4.8676 | 4.8676 | 0 | 12 | 1 | 1 | 4.8676 | 10 | 0 | 0
698.85 | 50.09 | 49.81 | 0.905 | 0.905 | 9.05 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 4.3044 | 4.3044 | 0 | 12 | 1 | 1 | 4.3044 | 10 | 0 | 0
698.9 | 50.12 | 49.83 | 0.715 | 0.805 | 8.05 | 50.12 | -0.24 | -0.24 | -2.4 | 2.825 | 2.825 | 0 | 12 | 1 | 1 | 2.825 | 10 | 0 | 0
698.95 | 50.14 | 49.86 | 0.43 | 0.705 | 7.05 | 50.14 | -0.43 | -0.43 | -4.3 | 1.375 | 1.375 | 0 | 12 | 1 | 1 | 1.375 | 10 | 0 | 0
699 | 50.17 | 49.88 | 0.24 | 0.605 | 6.05 | 50.17 | -0.715 | -0.715 | -7.15 | -0.55 | -0.55 | 0 | 12 | 1 | 1 | -0.55 | 10 | 0 | 0
699.05 | 50.19 | 49.91 | 0.044118 | 0.505 | 5.05 | 50.19 | -0.905 | -0.905 | -9.05 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
699.1 | 50.22 | 49.94 | 0.026471 | 0.405 | 4.05 | 50.22 | -1 | -1 | -10 | -2.975 | -2.975 | 0 | 12 | 1 | 1 | -2.975 | 10 | 0 | 0
699.15 | 50.24 | 49.96 | 0.014706 | 0.305 | 3.05 | 50.24 | -1 | -1 | -10 | -3.475 | -3.475 | 0 | 12 | 1 | 1 | -3.475 | 10 | 0 | 0
699.2 | 50.27 | 49.99 | 0 | 0.205 | 2.05 | 50.27 | -1 | -1 | -10 | -3.975 | -3.975 | 0 | 12 | 1 | 1 | -3.975 | 10 | 0 | 0
699.25 | 50.29 | 50.01 | 0 | 0.105 | 1.05 | 50.29 | -1 | -1 | -10 | -4.475 | -4.475 | 0 | 12 | 1 | 1 | -4.475 | 10 | 0 | 0
699.3 | 50.32 | 50.04 | -0.014706 | 0.005 | 0.05 | 50.32 | -1 | -1 | -10 | -4.975 | -4.975 | 0 | 12 | 1 | 1 | -4.975 | 10 | 0 | 0
699.35 | 50.35 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.35 | -1 | -1 | -10 | -5.1324 | -5.1324 | 0 | 12 | 1 | 1 | -5.1324 | 10 | 0 | 0
699.4 | 50.37 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 50.37 | -1 | -1 | -10 | -5.2206 | -5.2206 | 0 | 12 | 1 | 1 | -5.2206 | 10 | 0 | 0
699.45 | 50.4 | 50.12 | -0.24 | -0.14412 | -1.4412 | 50.4 | -1 | -1 | -10 | -5.7206 | -5.7206 | 0 | 12 | 1 | 1 | -5.7206 | 10 | 0 | 0
699.5 | 50.42 | 50.14 | -0.43 | -0.24412 | -2.4412 | 50.42 | -1 | -1 | -10 | -6.2206 | -6.2206 | 0 | 12 | 1 | 1 | -6.2206 | 10 | 0 | 0
699.55 | 50.45 | 50.17 | -0.715 | -0.34412 | -3.4412 | 50.45 | -1 | -1 | -10 | -6.7206 | -6.7206 | 0 | 12 | 1 | 1 | -6.7206 | 10 | 0 | 0
699.6 | 50.47 | 50.19 | -0.905 | -0.44412 | -4.4412 | 50.47 | -1 | -1 | -10 | -7.2206 | -7.2206 | 0 | 12 | 1 | 1 | -7.2206 | 10 | 0 | 0
699.65 | 50.5 | 50.22 | -1 | -0.54412 | -5.4412 | 50.5 | -1 | -1 | -10 | -7.7206 | -7.7206 | 0 | 12 | 1 | 1 | -7.7206 | 10 | 0 | 0
699.7 | 50.5 | 50.24 | -1 | -0.64412 | -6.4412 | 50.5 | -1 | -1 | -10 | -8.2206 | -8.2206 | 0 | 12 | 1 | 1 | -8.2206 | 10 | 0 | 0
699.75 | 50.47 | 50.27 | -1 | -0.74412 | -7.4412 | 50.5 | -1 | -1 | -10 | -8.7206 | -8.7206 | 0 | 12 | 1 | 1 | -8.7206 | 10 | 0 | 0
699.8 | 50.45 | 50.29 | -1 | -0.84412 | -8.4412 | 50.5 | -1 | -1 | -10 | -9.2206 | -9.2206 | 0 | 12 | 1 | 1 | -9.2206 | 10 | 0 | 0
699.85 | 50.42 | 50.32 | -1 | -0.94412 | -9.4412 | 50.5 | -1 | -1 | -10 | -9.7206 | -9.7206 | 0 | 12 | 1 | 1 | -9.7206 | 10 | 0 | 0
699.9 | 50.39 | 50.35 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
699.95 | 50.37 | 50.37 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
700 | 50.34 | 50.34 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
700.05 | 50.32 | 50.32 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
700.1 | 50.29 | 50.29 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
700.15 | 50.26 | 50.26 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
700.2 | 50.24 | 50.24 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
700.25 | 50.21 | 50.21 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
700.3 | 50.18 | 50.18 | -0.81 | -0.81 | -8.1 | 50.47 | -1 | -1 | -10 | -9.05 | -9.05 | 0 | 12 | 1 | 1 | -9.05 | 10 | 0 | 0
700.35 | 50.16 | 50.16 | -0.62 | -0.62 | -6.2 | 50.45 | -1 | -1 | -10 | -8.1 | -8.1 | 0 | 12 | 1 | 1 | -8.1 | 10 | 0 | 0
700.4 | 50.13 | 50.13 | -0.335 | -0.335 | -3.35 | 50.42 | -1 | -1 | -10 | -6.675 | -6.675 | 0 | 12 | 1 | 1 | -6.675 | 10 | 0 | 0
700.45 | 50.11 | 50.11 | -0.145 | -0.145 | -1.45 | 50.39 | -1 | -1 | -10 | -5.725 | -5.725 | 0 | 12 | 1 | 1 | -5.725 | 10 | 0 | 0
700.5 | 50.08 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 50.37 | -1 | -1 | -10 | -5.1912 | -5.1912 | 0 | 12 | 1 | 1 | -5.1912 | 10 | 0 | 0
700.55 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.34 | -1 | -1 | -10 | -5.1029 | -5.1029 | 0 | 12 | 1 | 1 | -5.1029 | 10 | 0 | 0
700.6 | 50.03 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 50.32 | -1 | -1 | -10 | -5.0441 | -5.0441 | 0 | 12 | 1 | 1 | -5.0441 | 10 | 0 | 0
700.65 | 50 | 50 | 0 | 0 | 0 | 50.29 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
700.7 | 50 | 50 | 0 | 0 | 0 | 50.26 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
700.75 | 50 | 50 | 0 | 0 | 0 | 50.24 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
700.8 | 50 | 50 | 0 | 0 | 0 | 50.21 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
700.85 | 50 | 50 | 0 | 0 | 0 | 50.18 | -0.81 | -0.9 | -9 | -4.5 | -4.5 | 0 | 12 | 1 | 1 | -4.5 | 10 | 0 | 0
700.9 | 50 | 50 | 0 | 0 | 0 | 50.16 | -0.62 | -0.8 | -8 | -4 | -4 | 0 | 12 | 1 | 1 | -4 | 10 | 0 | 0
700.95 | 50 | 50 | 0 | 0 | 0 | 50.13 | -0.335 | -0.7 | -7 | -3.5 | -3.5 | 0 | 12 | 1 | 1 | -3.5 | 10 | 0 | 0
701 | 50.01 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.6 | -6 | -3 | -3 | 0 | 12 | 1 | 1 | -3 | 10 | 0 | 0
701.05 | 50.01 | 50 | 0 | 0 | 0 | 50.08 | -0.038235 | -0.5 | -5 | -2.5 | -2.5 | 0 | 12 | 1 | 1 | -2.5 | 10 | 0 | 0
701.1 | 49.99 | 49.99 | 0 | 0 | 0 | 50.05 | -0.020588 | -0.4 | -4 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
701.15 | 49.99 | 49.99 | 0 | 0 | 0 | 50.03 | -0.0088235 | -0.3 | -3 | -1.5 | -1.5 | 0 | 12 | 1 | 1 | -1.5 | 10 | 0 | 0
701.2 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | -0.2 | -2 | -0.83824 | -0.83824 | 0 | 12 | 1 | 1 | -0.83824 | 10 | 0 | 0
701.25 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | -0.1 | -1 | -0.33824 | -0.33824 | 0 | 12 | 1 | 1 | -0.33824 | 10 | 0 | 0
701.3 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
701.35 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
701.4 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
701.45 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
701.5 | 49.89 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
701.55 | 49.89 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
701.6 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50.01 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
701.65 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
701.7 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
701.75 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 2.7868 | 2.7868 | 0 | 12 | 1 | 1 | 2.7868 | 10 | 0 | 0
701.8 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 2.7868 | 2.7868 | 0 | 12 | 1 | 1 | 2.7868 | 10 | 0 | 0
701.85 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 2.8456 | 2.8456 | 0 | 12 | 1 | 1 | 2.8456 | 10 | 0 | 0
701.9 | 49.94 | 49.85 | 0.525 | 0.525 | 5.25 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 2.7574 | 2.7574 | 0 | 12 | 1 | 1 | 2.7574 | 10 | 0 | 0
701.95 | 49.94 | 49.85 | 0.525 | 0.525 | 5.25 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 2.7574 | 2.7574 | 0 | 12 | 1 | 1 | 2.7574 | 10 | 0 | 0
702 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
702.05 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
702.1 | 49.93 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
702.15 | 49.93 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
702.2 | 49.96 | 49.85 | 0.525 | 0.525 | 5.25 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 2.6985 | 2.6985 | 0 | 12 | 1 | 1 | 2.6985 | 10 | 0 | 0
702.25 | 49.96 | 49.85 | 0.525 | 0.525 | 5.25 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 2.6985 | 2.6985 | 0 | 12 | 1 | 1 | 2.6985 | 10 | 0 | 0
702.3 | 49.99 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
702.35 | 49.99 | 49.91 | 0.044118 | 0.425 | 4.25 | 49.99 | 0 | 0 | 0 | 2.125 | 2.125 | 0 | 12 | 1 | 1 | 2.125 | 10 | 0 | 0
702.4 | 49.99 | 49.91 | 0.044118 | 0.325 | 3.25 | 49.99 | 0 | 0 | 0 | 1.625 | 1.625 | 0 | 12 | 1 | 1 | 1.625 | 10 | 0 | 0
702.45 | 49.99 | 49.93 | 0.032353 | 0.225 | 2.25 | 49.99 | 0 | 0 | 0 | 1.125 | 1.125 | 0 | 12 | 1 | 1 | 1.125 | 10 | 0 | 0
702.5 | 49.96 | 49.93 | 0.032353 | 0.125 | 1.25 | 49.99 | 0 | 0 | 0 | 0.625 | 0.625 | 0 | 12 | 1 | 1 | 0.625 | 10 | 0 | 0
702.55 | 49.96 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 49.99 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
702.6 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
702.65 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
702.7 | 50.05 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.058824 | 0.058824 | 0 | 12 | 1 | 1 | 0.058824 | 10 | 0 | 0
702.75 | 50.05 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
702.8 | 49.97 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
702.85 | 49.97 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
702.9 | 49.92 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
702.95 | 49.92 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
703 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
703.05 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
703.1 | 49.94 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
703.15 | 49.94 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
703.2 | 50.01 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
703.25 | 50.01 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
703.3 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
703.35 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
703.4 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
703.45 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
703.5 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
703.55 | 49.95 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
703.6 | 49.97 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
703.65 | 49.97 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
703.7 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
703.75 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
703.8 | 49.87 | 49.87 | 0.335 | 0.335 | 3.35 | 50.01 | 0 | 0 | 0 | 1.675 | 1.675 | 0 | 12 | 1 | 1 | 1.675 | 10 | 0 | 0
703.85 | 49.87 | 49.87 | 0.335 | 0.335 | 3.35 | 49.99 | 0 | 0 | 0 | 1.675 | 1.675 | 0 | 12 | 1 | 1 | 1.675 | 10 | 0 | 0
703.9 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
703.95 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 2.6691 | 2.6691 | 0 | 12 | 1 | 1 | 2.6691 | 10 | 0 | 0
704 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
704.05 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
704.1 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
704.15 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
704.2 | 49.84 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
704.25 | 49.84 | 49.79 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
704.3 | 49.89 | 49.79 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
704.35 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.12647 | 1.2647 | 5.6324 | 5.6324 | 0 | 12 | 1 | 1 | 5.6324 | 10 | 0 | 0
704.4 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.145 | 1.45 | 5.725 | 5.725 | 0 | 12 | 1 | 1 | 5.725 | 10 | 0 | 0
704.45 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.145 | 1.45 | 5.725 | 5.725 | 0 | 12 | 1 | 1 | 5.725 | 10 | 0 | 0
704.5 | 49.96 | 49.79 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
704.55 | 49.96 | 49.79 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
704.6 | 50.02 | 49.79 | 1 | 1 | 10 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 4.9853 | 4.9853 | 0 | 12 | 1 | 1 | 4.9853 | 10 | 0 | 0
704.65 | 50.02 | 49.79 | 1 | 1 | 10 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 4.9853 | 4.9853 | 0 | 12 | 1 | 1 | 4.9853 | 10 | 0 | 0
704.7 | 50.03 | 49.79 | 1 | 1 | 10 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.9559 | 4.9559 | 0 | 12 | 1 | 1 | 4.9559 | 10 | 0 | 0
704.75 | 50.03 | 49.84 | 0.62 | 0.9 | 9 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.4559 | 4.4559 | 0 | 12 | 1 | 1 | 4.4559 | 10 | 0 | 0
704.8 | 50.02 | 49.84 | 0.62 | 0.8 | 8 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 3.9559 | 3.9559 | 0 | 12 | 1 | 1 | 3.9559 | 10 | 0 | 0
704.85 | 50.02 | 49.89 | 0.145 | 0.7 | 7 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 3.4559 | 3.4559 | 0 | 12 | 1 | 1 | 3.4559 | 10 | 0 | 0
704.9 | 50.08 | 49.89 | 0.145 | 0.6 | 6 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 2.8088 | 2.8088 | 0 | 12 | 1 | 1 | 2.8088 | 10 | 0 | 0
704.95 | 50.08 | 49.89 | 0.145 | 0.5 | 5 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 2.3088 | 2.3088 | 0 | 12 | 1 | 1 | 2.3088 | 10 | 0 | 0
705 | 50.01 | 49.89 | 0.145 | 0.4 | 4 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 1.8088 | 1.8088 | 0 | 12 | 1 | 1 | 1.8088 | 10 | 0 | 0
705.05 | 50.01 | 49.96 | 0.014706 | 0.3 | 3 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 1.3088 | 1.3088 | 0 | 12 | 1 | 1 | 1.3088 | 10 | 0 | 0
705.1 | 49.94 | 49.94 | 0.026471 | 0.2 | 2 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.80882 | 0.80882 | 0 | 12 | 1 | 1 | 0.80882 | 10 | 0 | 0
705.15 | 49.94 | 49.94 | 0.026471 | 0.1 | 1 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.30882 | 0.30882 | 0 | 12 | 1 | 1 | 0.30882 | 10 | 0 | 0
705.2 | 50 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
705.25 | 50 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
705.3 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
705.35 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
705.4 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
705.45 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
705.5 | 49.92 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
705.55 | 49.92 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
705.6 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50.01 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
705.65 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
705.7 | 49.92 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
705.75 | 49.92 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
705.8 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
705.85 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
705.9 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
705.95 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
706 | 49.87 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
706.05 | 49.87 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
706.1 | 49.8 | 49.8 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
706.15 | 49.8 | 49.8 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
706.2 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
706.25 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
706.3 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
706.35 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
706.4 | 49.72 | 49.72 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
706.45 | 49.72 | 49.72 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
706.5 | 49.67 | 49.67 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
706.55 | 49.67 | 49.67 | 1 | 1 | 10 | 49.87 | 0.335 | 0.14412 | 1.4412 | 5.7206 | 5.7206 | 0 | 12 | 1 | 1 | 5.7206 | 10 | 0 | 0
706.6 | 49.65 | 49.65 | 1 | 1 | 10 | 49.87 | 0.335 | 0.24412 | 2.4412 | 6.2206 | 6.2206 | 0 | 12 | 1 | 1 | 6.2206 | 10 | 0 | 0
706.65 | 49.65 | 49.65 | 1 | 1 | 10 | 49.8 | 1 | 0.34412 | 3.4412 | 6.7206 | 6.7206 | 0 | 12 | 1 | 1 | 6.7206 | 10 | 0 | 0
706.7 | 49.59 | 49.59 | 1 | 1 | 10 | 49.8 | 1 | 0.44412 | 4.4412 | 7.2206 | 7.2206 | 0 | 12 | 1 | 1 | 7.2206 | 10 | 0 | 0
706.75 | 49.59 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.54412 | 5.4412 | 7.7206 | 7.7206 | 0 | 12 | 1 | 1 | 7.7206 | 10 | 0 | 0
706.8 | 49.66 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.64412 | 6.4412 | 8.2206 | 8.2206 | 0 | 12 | 1 | 1 | 8.2206 | 10 | 0 | 0
706.85 | 49.66 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.74412 | 7.4412 | 8.7206 | 8.7206 | 0 | 12 | 1 | 1 | 8.7206 | 10 | 0 | 0
706.9 | 49.63 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.84412 | 8.4412 | 9.2206 | 9.2206 | 0 | 12 | 1 | 1 | 9.2206 | 10 | 0 | 0
706.95 | 49.63 | 49.59 | 1 | 1 | 10 | 49.72 | 1 | 0.94412 | 9.4412 | 9.7206 | 9.7206 | 0 | 12 | 1 | 1 | 9.7206 | 10 | 0 | 0
707 | 49.61 | 49.59 | 1 | 1 | 10 | 49.72 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
707.05 | 49.61 | 49.59 | 1 | 1 | 10 | 49.67 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
707.1 | 49.54 | 49.54 | 1 | 1 | 10 | 49.67 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
707.15 | 49.54 | 49.54 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
707.2 | 49.46 | 49.46 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
707.25 | 49.46 | 49.46 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
707.3 | 49.45 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
707.35 | 49.45 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
707.4 | 49.51 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
707.45 | 49.51 | 49.45 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
707.5 | 49.5 | 49.45 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
707.55 | 49.5 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
707.6 | 49.54 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
707.65 | 49.54 | 49.45 | 1 | 1 | 10 | 49.54 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
707.7 | 49.59 | 49.45 | 1 | 1 | 10 | 49.59 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
707.75 | 49.59 | 49.45 | 1 | 1 | 10 | 49.59 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
707.8 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
707.85 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
707.9 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
707.95 | 49.61 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
708 | 49.53 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
708.05 | 49.53 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
708.1 | 49.54 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
708.15 | 49.54 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
708.2 | 49.61 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
708.25 | 49.61 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
708.3 | 49.66 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
708.35 | 49.66 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
708.4 | 49.64 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
708.45 | 49.64 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
708.5 | 49.69 | 49.53 | 1 | 1 | 10 | 49.69 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
708.55 | 49.69 | 49.53 | 1 | 1 | 10 | 49.69 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
708.6 | 49.74 | 49.53 | 1 | 1 | 10 | 49.74 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
708.65 | 49.74 | 49.54 | 1 | 1 | 10 | 49.74 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
708.7 | 49.78 | 49.54 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
708.75 | 49.78 | 49.61 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
708.8 | 49.82 | 49.61 | 1 | 1 | 10 | 49.82 | 0.81 | 0.81 | 8.1 | 9.05 | 9.05 | 0 | 12 | 1 | 1 | 9.05 | 10 | 0 | 0
708.85 | 49.82 | 49.64 | 1 | 1 | 10 | 49.82 | 0.81 | 0.81 | 8.1 | 9.05 | 9.05 | 0 | 12 | 1 | 1 | 9.05 | 10 | 0 | 0
708.9 | 49.86 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
708.95 | 49.86 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
709 | 49.84 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
709.05 | 49.84 | 49.69 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
709.1 | 49.91 | 49.69 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
709.15 | 49.91 | 49.74 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
709.2 | 49.97 | 49.74 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
709.25 | 49.97 | 49.78 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
709.3 | 50.03 | 49.78 | 1 | 1 | 10 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.9559 | 4.9559 | 0 | 12 | 1 | 1 | 4.9559 | 10 | 0 | 0
709.35 | 50.03 | 49.82 | 0.81 | 0.9 | 9 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.4559 | 4.4559 | 0 | 12 | 1 | 1 | 4.4559 | 10 | 0 | 0
709.4 | 50.05 | 49.82 | 0.81 | 0.81 | 8.1 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 3.9471 | 3.9471 | 0 | 12 | 1 | 1 | 3.9471 | 10 | 0 | 0
709.45 | 50.05 | 49.84 | 0.62 | 0.71 | 7.1 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 3.4471 | 3.4471 | 0 | 12 | 1 | 1 | 3.4471 | 10 | 0 | 0
709.5 | 50.01 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
709.55 | 50.01 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
709.6 | 49.95 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
709.65 | 49.95 | 49.91 | 0.044118 | 0.52 | 5.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.4971 | 2.4971 | 0 | 12 | 1 | 1 | 2.4971 | 10 | 0 | 0
709.7 | 49.99 | 49.91 | 0.044118 | 0.42 | 4.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 1.9971 | 1.9971 | 0 | 12 | 1 | 1 | 1.9971 | 10 | 0 | 0
709.75 | 49.99 | 49.95 | 0.020588 | 0.32 | 3.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 1.4971 | 1.4971 | 0 | 12 | 1 | 1 | 1.4971 | 10 | 0 | 0
709.8 | 49.92 | 49.92 | 0.038235 | 0.22 | 2.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.99706 | 0.99706 | 0 | 12 | 1 | 1 | 0.99706 | 10 | 0 | 0
709.85 | 49.92 | 49.92 | 0.038235 | 0.12 | 1.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.49706 | 0.49706 | 0 | 12 | 1 | 1 | 0.49706 | 10 | 0 | 0
709.9 | 49.97 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
709.95 | 49.97 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
710 | 50.02 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
710.05 | 50.02 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.17647 | 0.17647 | 0 | 12 | 1 | 1 | 0.17647 | 10 | 0 | 0
710.1 | 50.07 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
710.15 | 50.07 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
710.2 | 50.06 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
710.25 | 50.06 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
710.3 | 50.13 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
710.35 | 50.13 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
710.4 | 50.09 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
710.45 | 50.09 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6309 | -1.6309 | 0 | 12 | 1 | 1 | -1.6309 | 10 | 0 | 0
710.5 | 50.07 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6309 | -1.6309 | 0 | 12 | 1 | 1 | -1.6309 | 10 | 0 | 0
710.55 | 50.07 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6897 | -1.6897 | 0 | 12 | 1 | 1 | -1.6897 | 10 | 0 | 0
710.6 | 50.07 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6897 | -1.6897 | 0 | 12 | 1 | 1 | -1.6897 | 10 | 0 | 0
710.65 | 50.07 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.13 | -0.335 | -0.335 | -3.35 | -1.8074 | -1.8074 | 0 | 12 | 1 | 1 | -1.8074 | 10 | 0 | 0
710.7 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.13 | -0.335 | -0.335 | -3.35 | -1.7779 | -1.7779 | 0 | 12 | 1 | 1 | -1.7779 | 10 | 0 | 0
710.75 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.13 | -0.335 | -0.335 | -3.35 | -1.7779 | -1.7779 | 0 | 12 | 1 | 1 | -1.7779 | 10 | 0 | 0
710.8 | 50.01 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
710.85 | 50.01 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
710.9 | 50.07 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
710.95 | 50.07 | 50.01 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.235 | -2.35 | -1.175 | -1.175 | 0 | 12 | 1 | 1 | -1.175 | 10 | 0 | 0
711 | 50.05 | 50.01 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.135 | -1.35 | -0.675 | -0.675 | 0 | 12 | 1 | 1 | -0.675 | 10 | 0 | 0
711.05 | 50.05 | 50.01 | 0 | 0 | 0 | 50.07 | -0.032353 | -0.035 | -0.35 | -0.175 | -0.175 | 0 | 12 | 1 | 1 | -0.175 | 10 | 0 | 0
711.1 | 50.1 | 50.01 | 0 | 0 | 0 | 50.1 | -0.05 | -0.05 | -0.5 | -0.25 | -0.25 | 0 | 12 | 1 | 1 | -0.25 | 10 | 0 | 0
711.15 | 50.1 | 50.01 | 0 | 0 | 0 | 50.1 | -0.05 | -0.05 | -0.5 | -0.25 | -0.25 | 0 | 12 | 1 | 1 | -0.25 | 10 | 0 | 0
711.2 | 50.11 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
711.25 | 50.11 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
711.3 | 50.06 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
711.35 | 50.06 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
711.4 | 50.04 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
711.45 | 50.04 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
711.5 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
711.55 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
711.6 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
711.65 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
711.7 | 50.11 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
711.75 | 50.11 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
711.8 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
711.85 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
711.9 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
711.95 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
712 | 50.02 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.11 | -0.145 | -0.145 | -1.45 | -0.73971 | -0.73971 | 0 | 12 | 1 | 1 | -0.73971 | 10 | 0 | 0
712.05 | 50.02 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.11 | -0.145 | -0.145 | -1.45 | -0.73971 | -0.73971 | 0 | 12 | 1 | 1 | -0.73971 | 10 | 0 | 0
712.1 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
712.15 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
712.2 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
712.25 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
712.3 | 50.01 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
712.35 | 50.01 | 50 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.045 | -0.45 | -0.225 | -0.225 | 0 | 12 | 1 | 1 | -0.225 | 10 | 0 | 0
712.4 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
712.45 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
712.5 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
712.55 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
712.6 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.14706 | 0.14706 | 0 | 12 | 1 | 1 | 0.14706 | 10 | 0 | 0
712.65 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
712.7 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
712.75 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
712.8 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
712.85 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
712.9 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
712.95 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
713 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
713.05 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
713.1 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
713.15 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
713.2 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
713.25 | 50 | 50 | 0 | 0 | 0 | 50.01 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
713.3 | 49.5 | 49.5 | 1 | 1 | 10 | 50.01 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
713.35 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
713.4 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
713.45 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
713.5 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
713.55 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
713.6 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
713.65 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
713.7 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
713.75 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
713.8 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
713.85 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.1 | 1 | 5.5 | 5.5 | 0 | 12 | 1 | 1 | 5.5 | 10 | 0 | 0
713.9 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.2 | 2 | 6 | 6 | 0 | 12 | 1 | 1 | 6 | 10 | 0 | 0
713.95 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.3 | 3 | 6.5 | 6.5 | 0 | 12 | 1 | 1 | 6.5 | 10 | 0 | 0
714 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.4 | 4 | 7 | 7 | 0 | 12 | 1 | 1 | 7 | 10 | 0 | 0
714.05 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.5 | 5 | 7.5 | 7.5 | 0 | 12 | 1 | 1 | 7.5 | 10 | 0 | 0
714.1 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.6 | 6 | 8 | 8 | 0 | 12 | 1 | 1 | 8 | 10 | 0 | 0
714.15 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.7 | 7 | 8.5 | 8.5 | 0 | 12 | 1 | 1 | 8.5 | 10 | 0 | 0
714.2 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.8 | 8 | 9 | 9 | 0 | 12 | 1 | 1 | 9 | 10 | 0 | 0
714.25 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.9 | 9 | 9.5 | 9.5 | 0 | 12 | 1 | 1 | 9.5 | 10 | 0 | 0
714.3 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
714.35 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
714.4 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
714.45 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
714.5 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
714.55 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
714.6 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
714.65 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
714.7 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
714.75 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
714.8 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
714.85 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
714.9 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
714.95 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
715 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
715.05 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
715.1 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
715.15 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
715.2 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
715.25 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
715.3 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
715.35 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
715.4 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
715.45 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
715.5 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
715.55 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
715.6 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
715.65 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
715.7 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
715.75 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
715.8 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
715.85 | 50.5 | 50.5 | -1 | 0.9 | 9 | 50.5 | -1 | -1 | -10 | -0.5 | -0.5 | 0 | 12 | 1 | 1 | -0.5 | 10 | 0 | 0
715.9 | 50.5 | 50.5 | -1 | 0.8 | 8 | 50.5 | -1 | -1 | -10 | -1 | -1 | 0 | 12 | 1 | 1 | -1 | 10 | 0 | 0
715.95 | 50.5 | 50.5 | -1 | 0.7 | 7 | 50.5 | -1 | -1 | -10 | -1.5 | -1.5 | 0 | 12 | 1 | 1 | -1.5 | 10 | 0 | 0
716 | 50.5 | 50.5 | -1 | 0.6 | 6 | 50.5 | -1 | -1 | -10 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
716.05 | 50.5 | 50.5 | -1 | 0.5 | 5 | 50.5 | -1 | -1 | -10 | -2.5 | -2.5 | 0 | 12 | 1 | 1 | -2.5 | 10 | 0 | 0
716.1 | 50.5 | 50.5 | -1 | 0.4 | 4 | 50.5 | -1 | -1 | -10 | -3 | -3 | 0 | 12 | 1 | 1 | -3 | 10 | 0 | 0
716.15 | 50.5 | 50.5 | -1 | 0.3 | 3 | 50.5 | -1 | -1 | -10 | -3.5 | -3.5 | 0 | 12 | 1 | 1 | -3.5 | 10 | 0 | 0
716.2 | 50.5 | 50.5 | -1 | 0.2 | 2 | 50.5 | -1 | -1 | -10 | -4 | -4 | 0 | 12 | 1 | 1 | -4 | 10 | 0 | 0
716.25 | 50.5 | 50.5 | -1 | 0.1 | 1 | 50.5 | -1 | -1 | -10 | -4.5 | -4.5 | 0 | 12 | 1 | 1 | -4.5 | 10 | 0 | 0
716.3 | 50.5 | 50.5 | -1 | 0 | 0 | 50.5 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
716.35 | 50.5 | 50.5 | -1 | -0.1 | -1 | 50.5 | -1 | -1 | -10 | -5.5 | -5.5 | 0 | 12 | 1 | 1 | -5.5 | 10 | 0 | 0
716.4 | 50.5 | 50.5 | -1 | -0.2 | -2 | 50.5 | -1 | -1 | -10 | -6 | -6 | 0 | 12 | 1 | 1 | -6 | 10 | 0 | 0
716.45 | 50.5 | 50.5 | -1 | -0.3 | -3 | 50.5 | -1 | -1 | -10 | -6.5 | -6.5 | 0 | 12 | 1 | 1 | -6.5 | 10 | 0 | 0
716.5 | 50.5 | 50.5 | -1 | -0.4 | -4 | 50.5 | -1 | -1 | -10 | -7 | -7 | 0 | 12 | 1 | 1 | -7 | 10 | 0 | 0
716.55 | 50.5 | 50.5 | -1 | -0.5 | -5 | 50.5 | -1 | -1 | -10 | -7.5 | -7.5 | 0 | 12 | 1 | 1 | -7.5 | 10 | 0 | 0
716.6 | 50.5 | 50.5 | -1 | -0.6 | -6 | 50.5 | -1 | -1 | -10 | -8 | -8 | 0 | 12 | 1 | 1 | -8 | 10 | 0 | 0
716.65 | 50.5 | 50.5 | -1 | -0.7 | -7 | 50.5 | -1 | -1 | -10 | -8.5 | -8.5 | 0 | 12 | 1 | 1 | -8.5 | 10 | 0 | 0
716.7 | 50.5 | 50.5 | -1 | -0.8 | -8 | 50.5 | -1 | -1 | -10 | -9 | -9 | 0 | 12 | 1 | 1 | -9 | 10 | 0 | 0
716.75 | 50.5 | 50.5 | -1 | -0.9 | -9 | 50.5 | -1 | -1 | -10 | -9.5 | -9.5 | 0 | 12 | 1 | 1 | -9.5 | 10 | 0 | 0
716.8 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
716.85 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
716.9 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
716.95 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
717 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
717.05 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
717.1 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
717.15 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
717.2 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
717.25 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
717.3 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
717.35 | 50.47 | 50.47 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
717.4 | 50.45 | 50.45 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
717.45 | 50.42 | 50.42 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
717.5 | 50.4 | 50.4 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
717.55 | 50.37 | 50.37 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
717.6 | 50.35 | 50.35 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
717.65 | 50.32 | 50.32 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
717.7 | 50.29 | 50.29 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
717.75 | 50.27 | 50.27 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
717.8 | 50.24 | 50.24 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
717.85 | 50.22 | 50.22 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
717.9 | 50.19 | 50.19 | -0.905 | -0.905 | -9.05 | 50.47 | -1 | -1 | -10 | -9.525 | -9.525 | 0 | 12 | 1 | 1 | -9.525 | 10 | 0 | 0
717.95 | 50.17 | 50.17 | -0.715 | -0.715 | -7.15 | 50.45 | -1 | -1 | -10 | -8.575 | -8.575 | 0 | 12 | 1 | 1 | -8.575 | 10 | 0 | 0
718 | 50.14 | 50.14 | -0.43 | -0.43 | -4.3 | 50.42 | -1 | -1 | -10 | -7.15 | -7.15 | 0 | 12 | 1 | 1 | -7.15 | 10 | 0 | 0
718.05 | 50.12 | 50.12 | -0.24 | -0.24 | -2.4 | 50.4 | -1 | -1 | -10 | -6.2 | -6.2 | 0 | 12 | 1 | 1 | -6.2 | 10 | 0 | 0
718.1 | 50.09 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 50.37 | -1 | -1 | -10 | -5.2206 | -5.2206 | 0 | 12 | 1 | 1 | -5.2206 | 10 | 0 | 0
718.15 | 50.06 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.35 | -1 | -1 | -10 | -5.1324 | -5.1324 | 0 | 12 | 1 | 1 | -5.1324 | 10 | 0 | 0
718.2 | 50.04 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.32 | -1 | -1 | -10 | -5.0735 | -5.0735 | 0 | 12 | 1 | 1 | -5.0735 | 10 | 0 | 0
718.25 | 50.01 | 50.01 | 0 | 0 | 0 | 50.29 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
718.3 | 49.99 | 49.99 | 0 | 0 | 0 | 50.27 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
718.35 | 49.96 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.24 | -1 | -1 | -10 | -4.9265 | -4.9265 | 0 | 12 | 1 | 1 | -4.9265 | 10 | 0 | 0
718.4 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.22 | -1 | -1 | -10 | -4.8676 | -4.8676 | 0 | 12 | 1 | 1 | -4.8676 | 10 | 0 | 0
718.45 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.19 | -0.905 | -0.905 | -9.05 | -4.3044 | -4.3044 | 0 | 12 | 1 | 1 | -4.3044 | 10 | 0 | 0
718.5 | 49.88 | 49.88 | 0.24 | 0.24 | 2.4 | 50.17 | -0.715 | -0.805 | -8.05 | -2.825 | -2.825 | 0 | 12 | 1 | 1 | -2.825 | 10 | 0 | 0
718.55 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.14 | -0.43 | -0.705 | -7.05 | -1.375 | -1.375 | 0 | 12 | 1 | 1 | -1.375 | 10 | 0 | 0
718.6 | 49.83 | 49.83 | 0.715 | 0.715 | 7.15 | 50.12 | -0.24 | -0.605 | -6.05 | 0.55 | 0.55 | 0 | 12 | 1 | 1 | 0.55 | 10 | 0 | 0
718.65 | 49.81 | 49.81 | 0.905 | 0.905 | 9.05 | 50.09 | -0.044118 | -0.505 | -5.05 | 2 | 2 | 0 | 12 | 1 | 1 | 2 | 10 | 0 | 0
718.7 | 49.78 | 49.78 | 1 | 1 | 10 | 50.06 | -0.026471 | -0.405 | -4.05 | 2.975 | 2.975 | 0 | 12 | 1 | 1 | 2.975 | 10 | 0 | 0
718.75 | 49.76 | 49.76 | 1 | 1 | 10 | 50.04 | -0.014706 | -0.305 | -3.05 | 3.475 | 3.475 | 0 | 12 | 1 | 1 | 3.475 | 10 | 0 | 0
718.8 | 49.73 | 49.73 | 1 | 1 | 10 | 50.01 | 0 | -0.205 | -2.05 | 3.975 | 3.975 | 0 | 12 | 1 | 1 | 3.975 | 10 | 0 | 0
718.85 | 49.71 | 49.71 | 1 | 1 | 10 | 49.99 | 0 | -0.105 | -1.05 | 4.475 | 4.475 | 0 | 12 | 1 | 1 | 4.475 | 10 | 0 | 0
718.9 | 49.68 | 49.68 | 1 | 1 | 10 | 49.96 | 0.014706 | -0.005 | -0.05 | 4.975 | 4.975 | 0 | 12 | 1 | 1 | 4.975 | 10 | 0 | 0
718.95 | 49.65 | 49.65 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
719 | 49.63 | 49.63 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
719.05 | 49.6 | 49.6 | 1 | 1 | 10 | 49.88 | 0.24 | 0.14412 | 1.4412 | 5.7206 | 5.7206 | 0 | 12 | 1 | 1 | 5.7206 | 10 | 0 | 0
719.1 | 49.58 | 49.58 | 1 | 1 | 10 | 49.86 | 0.43 | 0.24412 | 2.4412 | 6.2206 | 6.2206 | 0 | 12 | 1 | 1 | 6.2206 | 10 | 0 | 0
719.15 | 49.55 | 49.55 | 1 | 1 | 10 | 49.83 | 0.715 | 0.34412 | 3.4412 | 6.7206 | 6.7206 | 0 | 12 | 1 | 1 | 6.7206 | 10 | 0 | 0
719.2 | 49.53 | 49.53 | 1 | 1 | 10 | 49.81 | 0.905 | 0.44412 | 4.4412 | 7.2206 | 7.2206 | 0 | 12 | 1 | 1 | 7.2206 | 10 | 0 | 0
719.25 | 49.5 | 49.5 | 1 | 1 | 10 | 49.78 | 1 | 0.54412 | 5.4412 | 7.7206 | 7.7206 | 0 | 12 | 1 | 1 | 7.7206 | 10 | 0 | 0
719.3 | 49.5 | 49.5 | 1 | 1 | 10 | 49.76 | 1 | 0.64412 | 6.4412 | 8.2206 | 8.2206 | 0 | 12 | 1 | 1 | 8.2206 | 10 | 0 | 0
719.35 | 49.53 | 49.5 | 1 | 1 | 10 | 49.73 | 1 | 0.74412 | 7.4412 | 8.7206 | 8.7206 | 0 | 12 | 1 | 1 | 8.7206 | 10 | 0 | 0
719.4 | 49.55 | 49.5 | 1 | 1 | 10 | 49.71 | 1 | 0.84412 | 8.4412 | 9.2206 | 9.2206 | 0 | 12 | 1 | 1 | 9.2206 | 10 | 0 | 0
719.45 | 49.58 | 49.5 | 1 | 1 | 10 | 49.68 | 1 | 0.94412 | 9.4412 | 9.7206 | 9.7206 | 0 | 12 | 1 | 1 | 9.7206 | 10 | 0 | 0
719.5 | 49.6 | 49.5 | 1 | 1 | 10 | 49.65 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
719.55 | 49.63 | 49.5 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
719.6 | 49.65 | 49.5 | 1 | 1 | 10 | 49.65 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
719.65 | 49.68 | 49.5 | 1 | 1 | 10 | 49.68 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
719.7 | 49.71 | 49.5 | 1 | 1 | 10 | 49.71 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
719.75 | 49.73 | 49.5 | 1 | 1 | 10 | 49.73 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
719.8 | 49.76 | 49.5 | 1 | 1 | 10 | 49.76 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
719.85 | 49.78 | 49.5 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
719.9 | 49.81 | 49.53 | 1 | 1 | 10 | 49.81 | 0.905 | 0.905 | 9.05 | 9.525 | 9.525 | 0 | 12 | 1 | 1 | 9.525 | 10 | 0 | 0
719.95 | 49.83 | 49.55 | 1 | 1 | 10 | 49.83 | 0.715 | 0.715 | 7.15 | 8.575 | 8.575 | 0 | 12 | 1 | 1 | 8.575 | 10 | 0 | 0
720 | 49.86 | 49.58 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
720.05 | 49.88 | 49.6 | 1 | 1 | 10 | 49.88 | 0.24 | 0.24 | 2.4 | 6.2 | 6.2 | 0 | 12 | 1 | 1 | 6.2 | 10 | 0 | 0
720.1 | 49.91 | 49.63 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
720.15 | 49.94 | 49.65 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
720.2 | 49.96 | 49.68 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
720.25 | 49.99 | 49.71 | 1 | 1 | 10 | 49.99 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
720.3 | 50.01 | 49.73 | 1 | 1 | 10 | 50.01 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
720.35 | 50.04 | 49.76 | 1 | 1 | 10 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 4.9265 | 4.9265 | 0 | 12 | 1 | 1 | 4.9265 | 10 | 0 | 0
720.4 | 50.06 | 49.78 | 1 | 1 | 10 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 4.8676 | 4.8676 | 0 | 12 | 1 | 1 | 4.8676 | 10 | 0 | 0
720.45 | 50.09 | 49.81 | 0.905 | 0.905 | 9.05 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 4.3044 | 4.3044 | 0 | 12 | 1 | 1 | 4.3044 | 10 | 0 | 0
720.5 | 50.12 | 49.83 | 0.715 | 0.805 | 8.05 | 50.12 | -0.24 | -0.24 | -2.4 | 2.825 | 2.825 | 0 | 12 | 1 | 1 | 2.825 | 10 | 0 | 0
720.55 | 50.14 | 49.86 | 0.43 | 0.705 | 7.05 | 50.14 | -0.43 | -0.43 | -4.3 | 1.375 | 1.375 | 0 | 12 | 1 | 1 | 1.375 | 10 | 0 | 0
720.6 | 50.17 | 49.88 | 0.24 | 0.605 | 6.05 | 50.17 | -0.715 | -0.715 | -7.15 | -0.55 | -0.55 | 0 | 12 | 1 | 1 | -0.55 | 10 | 0 | 0
720.65 | 50.19 | 49.91 | 0.044118 | 0.505 | 5.05 | 50.19 | -0.905 | -0.905 | -9.05 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
720.7 | 50.22 | 49.94 | 0.026471 | 0.405 | 4.05 | 50.22 | -1 | -1 | -10 | -2.975 | -2.975 | 0 | 12 | 1 | 1 | -2.975 | 10 | 0 | 0
720.75 | 50.24 | 49.96 | 0.014706 | 0.305 | 3.05 | 50.24 | -1 | -1 | -10 | -3.475 | -3.475 | 0 | 12 | 1 | 1 | -3.475 | 10 | 0 | 0
720.8 | 50.27 | 49.99 | 0 | 0.205 | 2.05 | 50.27 | -1 | -1 | -10 | -3.975 | -3.975 | 0 | 12 | 1 | 1 | -3.975 | 10 | 0 | 0
720.85 | 50.29 | 50.01 | 0 | 0.105 | 1.05 | 50.29 | -1 | -1 | -10 | -4.475 | -4.475 | 0 | 12 | 1 | 1 | -4.475 | 10 | 0 | 0
720.9 | 50.32 | 50.04 | -0.014706 | 0.005 | 0.05 | 50.32 | -1 | -1 | -10 | -4.975 | -4.975 | 0 | 12 | 1 | 1 | -4.975 | 10 | 0 | 0
720.95 | 50.35 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.35 | -1 | -1 | -10 | -5.1324 | -5.1324 | 0 | 12 | 1 | 1 | -5.1324 | 10 | 0 | 0
721 | 50.37 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 50.37 | -1 | -1 | -10 | -5.2206 | -5.2206 | 0 | 12 | 1 | 1 | -5.2206 | 10 | 0 | 0
721.05 | 50.4 | 50.12 | -0.24 | -0.14412 | -1.4412 | 50.4 | -1 | -1 | -10 | -5.7206 | -5.7206 | 0 | 12 | 1 | 1 | -5.7206 | 10 | 0 | 0
721.1 | 50.42 | 50.14 | -0.43 | -0.24412 | -2.4412 | 50.42 | -1 | -1 | -10 | -6.2206 | -6.2206 | 0 | 12 | 1 | 1 | -6.2206 | 10 | 0 | 0
721.15 | 50.45 | 50.17 | -0.715 | -0.34412 | -3.4412 | 50.45 | -1 | -1 | -10 | -6.7206 | -6.7206 | 0 | 12 | 1 | 1 | -6.7206 | 10 | 0 | 0
721.2 | 50.47 | 50.19 | -0.905 | -0.44412 | -4.4412 | 50.47 | -1 | -1 | -10 | -7.2206 | -7.2206 | 0 | 12 | 1 | 1 | -7.2206 | 10 | 0 | 0
721.25 | 50.5 | 50.22 | -1 | -0.54412 | -5.4412 | 50.5 | -1 | -1 | -10 | -7.7206 | -7.7206 | 0 | 12 | 1 | 1 | -7.7206 | 10 | 0 | 0
721.3 | 50.5 | 50.24 | -1 | -0.64412 | -6.4412 | 50.5 | -1 | -1 | -10 | -8.2206 | -8.2206 | 0 | 12 | 1 | 1 | -8.2206 | 10 | 0 | 0
721.35 | 50.47 | 50.27 | -1 | -0.74412 | -7.4412 | 50.5 | -1 | -1 | -10 | -8.7206 | -8.7206 | 0 | 12 | 1 | 1 | -8.7206 | 10 | 0 | 0
721.4 | 50.45 | 50.29 | -1 | -0.84412 | -8.4412 | 50.5 | -1 | -1 | -10 | -9.2206 | -9.2206 | 0 | 12 | 1 | 1 | -9.2206 | 10 | 0 | 0
721.45 | 50.42 | 50.32 | -1 | -0.94412 | -9.4412 | 50.5 | -1 | -1 | -10 | -9.7206 | -9.7206 | 0 | 12 | 1 | 1 | -9.7206 | 10 | 0 | 0
721.5 | 50.39 | 50.35 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
721.55 | 50.37 | 50.37 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
721.6 | 50.34 | 50.34 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
721.65 | 50.32 | 50.32 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
721.7 | 50.29 | 50.29 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
721.75 | 50.26 | 50.26 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
721.8 | 50.24 | 50.24 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
721.85 | 50.21 | 50.21 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
721.9 | 50.18 | 50.18 | -0.81 | -0.81 | -8.1 | 50.47 | -1 | -1 | -10 | -9.05 | -9.05 | 0 | 12 | 1 | 1 | -9.05 | 10 | 0 | 0
721.95 | 50.16 | 50.16 | -0.62 | -0.62 | -6.2 | 50.45 | -1 | -1 | -10 | -8.1 | -8.1 | 0 | 12 | 1 | 1 | -8.1 | 10 | 0 | 0
722 | 50.13 | 50.13 | -0.335 | -0.335 | -3.35 | 50.42 | -1 | -1 | -10 | -6.675 | -6.675 | 0 | 12 | 1 | 1 | -6.675 | 10 | 0 | 0
722.05 | 50.11 | 50.11 | -0.145 | -0.145 | -1.45 | 50.39 | -1 | -1 | -10 | -5.725 | -5.725 | 0 | 12 | 1 | 1 | -5.725 | 10 | 0 | 0
722.1 | 50.08 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 50.37 | -1 | -1 | -10 | -5.1912 | -5.1912 | 0 | 12 | 1 | 1 | -5.1912 | 10 | 0 | 0
722.15 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.34 | -1 | -1 | -10 | -5.1029 | -5.1029 | 0 | 12 | 1 | 1 | -5.1029 | 10 | 0 | 0
722.2 | 50.03 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 50.32 | -1 | -1 | -10 | -5.0441 | -5.0441 | 0 | 12 | 1 | 1 | -5.0441 | 10 | 0 | 0
722.25 | 50 | 50 | 0 | 0 | 0 | 50.29 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
722.3 | 50 | 50 | 0 | 0 | 0 | 50.26 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
722.35 | 50 | 50 | 0 | 0 | 0 | 50.24 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
722.4 | 50 | 50 | 0 | 0 | 0 | 50.21 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
722.45 | 50 | 50 | 0 | 0 | 0 | 50.18 | -0.81 | -0.9 | -9 | -4.5 | -4.5 | 0 | 12 | 1 | 1 | -4.5 | 10 | 0 | 0
722.5 | 50 | 50 | 0 | 0 | 0 | 50.16 | -0.62 | -0.8 | -8 | -4 | -4 | 0 | 12 | 1 | 1 | -4 | 10 | 0 | 0
722.55 | 50 | 50 | 0 | 0 | 0 | 50.13 | -0.335 | -0.7 | -7 | -3.5 | -3.5 | 0 | 12 | 1 | 1 | -3.5 | 10 | 0 | 0
722.6 | 50.01 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.6 | -6 | -3 | -3 | 0 | 12 | 1 | 1 | -3 | 10 | 0 | 0
722.65 | 50.01 | 50 | 0 | 0 | 0 | 50.08 | -0.038235 | -0.5 | -5 | -2.5 | -2.5 | 0 | 12 | 1 | 1 | -2.5 | 10 | 0 | 0
722.7 | 49.99 | 49.99 | 0 | 0 | 0 | 50.05 | -0.020588 | -0.4 | -4 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
722.75 | 49.99 | 49.99 | 0 | 0 | 0 | 50.03 | -0.0088235 | -0.3 | -3 | -1.5 | -1.5 | 0 | 12 | 1 | 1 | -1.5 | 10 | 0 | 0
722.8 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | -0.2 | -2 | -0.83824 | -0.83824 | 0 | 12 | 1 | 1 | -0.83824 | 10 | 0 | 0
722.85 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | -0.1 | -1 | -0.33824 | -0.33824 | 0 | 12 | 1 | 1 | -0.33824 | 10 | 0 | 0
722.9 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
722.95 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
723 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
723.05 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
723.1 | 49.89 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
723.15 | 49.89 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
723.2 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50.01 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
723.25 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
723.3 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
723.35 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 2.7868 | 2.7868 | 0 | 12 | 1 | 1 | 2.7868 | 10 | 0 | 0
723.4 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 2.7868 | 2.7868 | 0 | 12 | 1 | 1 | 2.7868 | 10 | 0 | 0
723.45 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 2.8456 | 2.8456 | 0 | 12 | 1 | 1 | 2.8456 | 10 | 0 | 0
723.5 | 49.94 | 49.85 | 0.525 | 0.525 | 5.25 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 2.7574 | 2.7574 | 0 | 12 | 1 | 1 | 2.7574 | 10 | 0 | 0
723.55 | 49.94 | 49.85 | 0.525 | 0.525 | 5.25 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 2.7574 | 2.7574 | 0 | 12 | 1 | 1 | 2.7574 | 10 | 0 | 0
723.6 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
723.65 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
723.7 | 49.93 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
723.75 | 49.93 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
723.8 | 49.96 | 49.85 | 0.525 | 0.525 | 5.25 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 2.6985 | 2.6985 | 0 | 12 | 1 | 1 | 2.6985 | 10 | 0 | 0
723.85 | 49.96 | 49.85 | 0.525 | 0.525 | 5.25 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 2.6985 | 2.6985 | 0 | 12 | 1 | 1 | 2.6985 | 10 | 0 | 0
723.9 | 49.99 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
723.95 | 49.99 | 49.91 | 0.044118 | 0.425 | 4.25 | 49.99 | 0 | 0 | 0 | 2.125 | 2.125 | 0 | 12 | 1 | 1 | 2.125 | 10 | 0 | 0
724 | 49.99 | 49.91 | 0.044118 | 0.325 | 3.25 | 49.99 | 0 | 0 | 0 | 1.625 | 1.625 | 0 | 12 | 1 | 1 | 1.625 | 10 | 0 | 0
724.05 | 49.99 | 49.93 | 0.032353 | 0.225 | 2.25 | 49.99 | 0 | 0 | 0 | 1.125 | 1.125 | 0 | 12 | 1 | 1 | 1.125 | 10 | 0 | 0
724.1 | 49.96 | 49.93 | 0.032353 | 0.125 | 1.25 | 49.99 | 0 | 0 | 0 | 0.625 | 0.625 | 0 | 12 | 1 | 1 | 0.625 | 10 | 0 | 0
724.15 | 49.96 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 49.99 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
724.2 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
724.25 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
724.3 | 50.05 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.058824 | 0.058824 | 0 | 12 | 1 | 1 | 0.058824 | 10 | 0 | 0
724.35 | 50.05 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
724.4 | 49.97 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
724.45 | 49.97 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
724.5 | 49.92 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
724.55 | 49.92 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
724.6 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
724.65 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
724.7 | 49.94 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
724.75 | 49.94 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
724.8 | 50.01 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
724.85 | 50.01 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
724.9 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
724.95 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
725 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
725.05 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
725.1 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
725.15 | 49.95 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
725.2 | 49.97 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
725.25 | 49.97 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
725.3 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
725.35 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
725.4 | 49.87 | 49.87 | 0.335 | 0.335 | 3.35 | 50.01 | 0 | 0 | 0 | 1.675 | 1.675 | 0 | 12 | 1 | 1 | 1.675 | 10 | 0 | 0
725.45 | 49.87 | 49.87 | 0.335 | 0.335 | 3.35 | 49.99 | 0 | 0 | 0 | 1.675 | 1.675 | 0 | 12 | 1 | 1 | 1.675 | 10 | 0 | 0
725.5 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
725.55 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 2.6691 | 2.6691 | 0 | 12 | 1 | 1 | 2.6691 | 10 | 0 | 0
725.6 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
725.65 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
725.7 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
725.75 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
725.8 | 49.84 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
725.85 | 49.84 | 49.79 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
725.9 | 49.89 | 49.79 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
725.95 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.12647 | 1.2647 | 5.6324 | 5.6324 | 0 | 12 | 1 | 1 | 5.6324 | 10 | 0 | 0
726 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.145 | 1.45 | 5.725 | 5.725 | 0 | 12 | 1 | 1 | 5.725 | 10 | 0 | 0
726.05 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.145 | 1.45 | 5.725 | 5.725 | 0 | 12 | 1 | 1 | 5.725 | 10 | 0 | 0
726.1 | 49.96 | 49.79 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
726.15 | 49.96 | 49.79 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
726.2 | 50.02 | 49.79 | 1 | 1 | 10 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 4.9853 | 4.9853 | 0 | 12 | 1 | 1 | 4.9853 | 10 | 0 | 0
726.25 | 50.02 | 49.79 | 1 | 1 | 10 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 4.9853 | 4.9853 | 0 | 12 | 1 | 1 | 4.9853 | 10 | 0 | 0
726.3 | 50.03 | 49.79 | 1 | 1 | 10 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.9559 | 4.9559 | 0 | 12 | 1 | 1 | 4.9559 | 10 | 0 | 0
726.35 | 50.03 | 49.84 | 0.62 | 0.9 | 9 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.4559 | 4.4559 | 0 | 12 | 1 | 1 | 4.4559 | 10 | 0 | 0
726.4 | 50.02 | 49.84 | 0.62 | 0.8 | 8 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 3.9559 | 3.9559 | 0 | 12 | 1 | 1 | 3.9559 | 10 | 0 | 0
726.45 | 50.02 | 49.89 | 0.145 | 0.7 | 7 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 3.4559 | 3.4559 | 0 | 12 | 1 | 1 | 3.4559 | 10 | 0 | 0
726.5 | 50.08 | 49.89 | 0.145 | 0.6 | 6 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 2.8088 | 2.8088 | 0 | 12 | 1 | 1 | 2.8088 | 10 | 0 | 0
726.55 | 50.08 | 49.89 | 0.145 | 0.5 | 5 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 2.3088 | 2.3088 | 0 | 12 | 1 | 1 | 2.3088 | 10 | 0 | 0
726.6 | 50.01 | 49.89 | 0.145 | 0.4 | 4 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 1.8088 | 1.8088 | 0 | 12 | 1 | 1 | 1.8088 | 10 | 0 | 0
726.65 | 50.01 | 49.96 | 0.014706 | 0.3 | 3 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 1.3088 | 1.3088 | 0 | 12 | 1 | 1 | 1.3088 | 10 | 0 | 0
726.7 | 49.94 | 49.94 | 0.026471 | 0.2 | 2 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.80882 | 0.80882 | 0 | 12 | 1 | 1 | 0.80882 | 10 | 0 | 0
726.75 | 49.94 | 49.94 | 0.026471 | 0.1 | 1 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.30882 | 0.30882 | 0 | 12 | 1 | 1 | 0.30882 | 10 | 0 | 0
726.8 | 50 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
726.85 | 50 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
726.9 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
726.95 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
727 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
727.05 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
727.1 | 49.92 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
727.15 | 49.92 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
727.2 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50.01 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
727.25 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
727.3 | 49.92 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
727.35 | 49.92 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
727.4 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
727.45 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
727.5 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
727.55 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
727.6 | 49.87 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
727.65 | 49.87 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
727.7 | 49.8 | 49.8 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
727.75 | 49.8 | 49.8 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
727.8 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
727.85 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
727.9 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
727.95 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
728 | 49.72 | 49.72 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
728.05 | 49.72 | 49.72 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
728.1 | 49.67 | 49.67 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
728.15 | 49.67 | 49.67 | 1 | 1 | 10 | 49.87 | 0.335 | 0.14412 | 1.4412 | 5.7206 | 5.7206 | 0 | 12 | 1 | 1 | 5.7206 | 10 | 0 | 0
728.2 | 49.65 | 49.65 | 1 | 1 | 10 | 49.87 | 0.335 | 0.24412 | 2.4412 | 6.2206 | 6.2206 | 0 | 12 | 1 | 1 | 6.2206 | 10 | 0 | 0
728.25 | 49.65 | 49.65 | 1 | 1 | 10 | 49.8 | 1 | 0.34412 | 3.4412 | 6.7206 | 6.7206 | 0 | 12 | 1 | 1 | 6.7206 | 10 | 0 | 0
728.3 | 49.59 | 49.59 | 1 | 1 | 10 | 49.8 | 1 | 0.44412 | 4.4412 | 7.2206 | 7.2206 | 0 | 12 | 1 | 1 | 7.2206 | 10 | 0 | 0
728.35 | 49.59 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.54412 | 5.4412 | 7.7206 | 7.7206 | 0 | 12 | 1 | 1 | 7.7206 | 10 | 0 | 0
728.4 | 49.66 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.64412 | 6.4412 | 8.2206 | 8.2206 | 0 | 12 | 1 | 1 | 8.2206 | 10 | 0 | 0
728.45 | 49.66 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.74412 | 7.4412 | 8.7206 | 8.7206 | 0 | 12 | 1 | 1 | 8.7206 | 10 | 0 | 0
728.5 | 49.63 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.84412 | 8.4412 | 9.2206 | 9.2206 | 0 | 12 | 1 | 1 | 9.2206 | 10 | 0 | 0
728.55 | 49.63 | 49.59 | 1 | 1 | 10 | 49.72 | 1 | 0.94412 | 9.4412 | 9.7206 | 9.7206 | 0 | 12 | 1 | 1 | 9.7206 | 10 | 0 | 0
728.6 | 49.61 | 49.59 | 1 | 1 | 10 | 49.72 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
728.65 | 49.61 | 49.59 | 1 | 1 | 10 | 49.67 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
728.7 | 49.54 | 49.54 | 1 | 1 | 10 | 49.67 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
728.75 | 49.54 | 49.54 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
728.8 | 49.46 | 49.46 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
728.85 | 49.46 | 49.46 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
728.9 | 49.45 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
728.95 | 49.45 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
729 | 49.51 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
729.05 | 49.51 | 49.45 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
729.1 | 49.5 | 49.45 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
729.15 | 49.5 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
729.2 | 49.54 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
729.25 | 49.54 | 49.45 | 1 | 1 | 10 | 49.54 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
729.3 | 49.59 | 49.45 | 1 | 1 | 10 | 49.59 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
729.35 | 49.59 | 49.45 | 1 | 1 | 10 | 49.59 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
729.4 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
729.45 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
729.5 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
729.55 | 49.61 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
729.6 | 49.53 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
729.65 | 49.53 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
729.7 | 49.54 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
729.75 | 49.54 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
729.8 | 49.61 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
729.85 | 49.61 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
729.9 | 49.66 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
729.95 | 49.66 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
730 | 49.64 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
730.05 | 49.64 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
730.1 | 49.69 | 49.53 | 1 | 1 | 10 | 49.69 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
730.15 | 49.69 | 49.53 | 1 | 1 | 10 | 49.69 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
730.2 | 49.74 | 49.53 | 1 | 1 | 10 | 49.74 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
730.25 | 49.74 | 49.54 | 1 | 1 | 10 | 49.74 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
730.3 | 49.78 | 49.54 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
730.35 | 49.78 | 49.61 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
730.4 | 49.82 | 49.61 | 1 | 1 | 10 | 49.82 | 0.81 | 0.81 | 8.1 | 9.05 | 9.05 | 0 | 12 | 1 | 1 | 9.05 | 10 | 0 | 0
730.45 | 49.82 | 49.64 | 1 | 1 | 10 | 49.82 | 0.81 | 0.81 | 8.1 | 9.05 | 9.05 | 0 | 12 | 1 | 1 | 9.05 | 10 | 0 | 0
730.5 | 49.86 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
730.55 | 49.86 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
730.6 | 49.84 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
730.65 | 49.84 | 49.69 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
730.7 | 49.91 | 49.69 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
730.75 | 49.91 | 49.74 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
730.8 | 49.97 | 49.74 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
730.85 | 49.97 | 49.78 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
730.9 | 50.03 | 49.78 | 1 | 1 | 10 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.9559 | 4.9559 | 0 | 12 | 1 | 1 | 4.9559 | 10 | 0 | 0
730.95 | 50.03 | 49.82 | 0.81 | 0.9 | 9 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.4559 | 4.4559 | 0 | 12 | 1 | 1 | 4.4559 | 10 | 0 | 0
731 | 50.05 | 49.82 | 0.81 | 0.81 | 8.1 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 3.9471 | 3.9471 | 0 | 12 | 1 | 1 | 3.9471 | 10 | 0 | 0
731.05 | 50.05 | 49.84 | 0.62 | 0.71 | 7.1 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 3.4471 | 3.4471 | 0 | 12 | 1 | 1 | 3.4471 | 10 | 0 | 0
731.1 | 50.01 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
731.15 | 50.01 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
731.2 | 49.95 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
731.25 | 49.95 | 49.91 | 0.044118 | 0.52 | 5.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.4971 | 2.4971 | 0 | 12 | 1 | 1 | 2.4971 | 10 | 0 | 0
731.3 | 49.99 | 49.91 | 0.044118 | 0.42 | 4.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 1.9971 | 1.9971 | 0 | 12 | 1 | 1 | 1.9971 | 10 | 0 | 0
731.35 | 49.99 | 49.95 | 0.020588 | 0.32 | 3.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 1.4971 | 1.4971 | 0 | 12 | 1 | 1 | 1.4971 | 10 | 0 | 0
731.4 | 49.92 | 49.92 | 0.038235 | 0.22 | 2.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.99706 | 0.99706 | 0 | 12 | 1 | 1 | 0.99706 | 10 | 0 | 0
731.45 | 49.92 | 49.92 | 0.038235 | 0.12 | 1.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.49706 | 0.49706 | 0 | 12 | 1 | 1 | 0.49706 | 10 | 0 | 0
731.5 | 49.97 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
731.55 | 49.97 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
731.6 | 50.02 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
731.65 | 50.02 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.17647 | 0.17647 | 0 | 12 | 1 | 1 | 0.17647 | 10 | 0 | 0
731.7 | 50.07 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
731.75 | 50.07 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
731.8 | 50.06 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
731.85 | 50.06 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
731.9 | 50.13 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
731.95 | 50.13 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
732 | 50.09 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
732.05 | 50.09 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6309 | -1.6309 | 0 | 12 | 1 | 1 | -1.6309 | 10 | 0 | 0
732.1 | 50.07 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6309 | -1.6309 | 0 | 12 | 1 | 1 | -1.6309 | 10 | 0 | 0
732.15 | 50.07 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6897 | -1.6897 | 0 | 12 | 1 | 1 | -1.6897 | 10 | 0 | 0
732.2 | 50.07 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6897 | -1.6897 | 0 | 12 | 1 | 1 | -1.6897 | 10 | 0 | 0
732.25 | 50.07 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.13 | -0.335 | -0.335 | -3.35 | -1.8074 | -1.8074 | 0 | 12 | 1 | 1 | -1.8074 | 10 | 0 | 0
732.3 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.13 | -0.335 | -0.335 | -3.35 | -1.7779 | -1.7779 | 0 | 12 | 1 | 1 | -1.7779 | 10 | 0 | 0
732.35 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.13 | -0.335 | -0.335 | -3.35 | -1.7779 | -1.7779 | 0 | 12 | 1 | 1 | -1.7779 | 10 | 0 | 0
732.4 | 50.01 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
732.45 | 50.01 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
732.5 | 50.07 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
732.55 | 50.07 | 50.01 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.235 | -2.35 | -1.175 | -1.175 | 0 | 12 | 1 | 1 | -1.175 | 10 | 0 | 0
732.6 | 50.05 | 50.01 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.135 | -1.35 | -0.675 | -0.675 | 0 | 12 | 1 | 1 | -0.675 | 10 | 0 | 0
732.65 | 50.05 | 50.01 | 0 | 0 | 0 | 50.07 | -0.032353 | -0.035 | -0.35 | -0.175 | -0.175 | 0 | 12 | 1 | 1 | -0.175 | 10 | 0 | 0
732.7 | 50.1 | 50.01 | 0 | 0 | 0 | 50.1 | -0.05 | -0.05 | -0.5 | -0.25 | -0.25 | 0 | 12 | 1 | 1 | -0.25 | 10 | 0 | 0
732.75 | 50.1 | 50.01 | 0 | 0 | 0 | 50.1 | -0.05 | -0.05 | -0.5 | -0.25 | -0.25 | 0 | 12 | 1 | 1 | -0.25 | 10 | 0 | 0
732.8 | 50.11 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
732.85 | 50.11 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
732.9 | 50.06 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
732.95 | 50.06 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
733 | 50.04 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
733.05 | 50.04 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
733.1 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
733.15 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
733.2 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
733.25 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
733.3 | 50.11 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
733.35 | 50.11 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
733.4 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
733.45 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
733.5 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
733.55 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
733.6 | 50.02 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.11 | -0.145 | -0.145 | -1.45 | -0.73971 | -0.73971 | 0 | 12 | 1 | 1 | -0.73971 | 10 | 0 | 0
733.65 | 50.02 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.11 | -0.145 | -0.145 | -1.45 | -0.73971 | -0.73971 | 0 | 12 | 1 | 1 | -0.73971 | 10 | 0 | 0
733.7 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
733.75 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
733.8 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
733.85 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
733.9 | 50.01 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
733.95 | 50.01 | 50 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.045 | -0.45 | -0.225 | -0.225 | 0 | 12 | 1 | 1 | -0.225 | 10 | 0 | 0
734 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
734.05 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
734.1 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
734.15 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
734.2 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.14706 | 0.14706 | 0 | 12 | 1 | 1 | 0.14706 | 10 | 0 | 0
734.25 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
734.3 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
734.35 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
734.4 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
734.45 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
734.5 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
734.55 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
734.6 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
734.65 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
734.7 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
734.75 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
734.8 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
734.85 | 50 | 50 | 0 | 0 | 0 | 50.01 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
734.9 | 49.5 | 49.5 | 1 | 1 | 10 | 50.01 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
734.95 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
735 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
735.05 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
735.1 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
735.15 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
735.2 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
735.25 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
735.3 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
735.35 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
735.4 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
735.45 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.1 | 1 | 5.5 | 5.5 | 0 | 12 | 1 | 1 | 5.5 | 10 | 0 | 0
735.5 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.2 | 2 | 6 | 6 | 0 | 12 | 1 | 1 | 6 | 10 | 0 | 0
735.55 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.3 | 3 | 6.5 | 6.5 | 0 | 12 | 1 | 1 | 6.5 | 10 | 0 | 0
735.6 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.4 | 4 | 7 | 7 | 0 | 12 | 1 | 1 | 7 | 10 | 0 | 0
735.65 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.5 | 5 | 7.5 | 7.5 | 0 | 12 | 1 | 1 | 7.5 | 10 | 0 | 0
735.7 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.6 | 6 | 8 | 8 | 0 | 12 | 1 | 1 | 8 | 10 | 0 | 0
735.75 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.7 | 7 | 8.5 | 8.5 | 0 | 12 | 1 | 1 | 8.5 | 10 | 0 | 0
735.8 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.8 | 8 | 9 | 9 | 0 | 12 | 1 | 1 | 9 | 10 | 0 | 0
735.85 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.9 | 9 | 9.5 | 9.5 | 0 | 12 | 1 | 1 | 9.5 | 10 | 0 | 0
735.9 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
735.95 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
736 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
736.05 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
736.1 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
736.15 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
736.2 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
736.25 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
736.3 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
736.35 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
736.4 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
736.45 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
736.5 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
736.55 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
736.6 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
736.65 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
736.7 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
736.75 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
736.8 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
736.85 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
736.9 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
736.95 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
737 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
737.05 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
737.1 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
737.15 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
737.2 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
737.25 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
737.3 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
737.35 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
737.4 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
737.45 | 50.5 | 50.5 | -1 | 0.9 | 9 | 50.5 | -1 | -1 | -10 | -0.5 | -0.5 | 0 | 12 | 1 | 1 | -0.5 | 10 | 0 | 0
737.5 | 50.5 | 50.5 | -1 | 0.8 | 8 | 50.5 | -1 | -1 | -10 | -1 | -1 | 0 | 12 | 1 | 1 | -1 | 10 | 0 | 0
737.55 | 50.5 | 50.5 | -1 | 0.7 | 7 | 50.5 | -1 | -1 | -10 | -1.5 | -1.5 | 0 | 12 | 1 | 1 | -1.5 | 10 | 0 | 0
737.6 | 50.5 | 50.5 | -1 | 0.6 | 6 | 50.5 | -1 | -1 | -10 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
737.65 | 50.5 | 50.5 | -1 | 0.5 | 5 | 50.5 | -1 | -1 | -10 | -2.5 | -2.5 | 0 | 12 | 1 | 1 | -2.5 | 10 | 0 | 0
737.7 | 50.5 | 50.5 | -1 | 0.4 | 4 | 50.5 | -1 | -1 | -10 | -3 | -3 | 0 | 12 | 1 | 1 | -3 | 10 | 0 | 0
737.75 | 50.5 | 50.5 | -1 | 0.3 | 3 | 50.5 | -1 | -1 | -10 | -3.5 | -3.5 | 0 | 12 | 1 | 1 | -3.5 | 10 | 0 | 0
737.8 | 50.5 | 50.5 | -1 | 0.2 | 2 | 50.5 | -1 | -1 | -10 | -4 | -4 | 0 | 12 | 1 | 1 | -4 | 10 | 0 | 0
737.85 | 50.5 | 50.5 | -1 | 0.1 | 1 | 50.5 | -1 | -1 | -10 | -4.5 | -4.5 | 0 | 12 | 1 | 1 | -4.5 | 10 | 0 | 0
737.9 | 50.5 | 50.5 | -1 | 0 | 0 | 50.5 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
737.95 | 50.5 | 50.5 | -1 | -0.1 | -1 | 50.5 | -1 | -1 | -10 | -5.5 | -5.5 | 0 | 12 | 1 | 1 | -5.5 | 10 | 0 | 0
738 | 50.5 | 50.5 | -1 | -0.2 | -2 | 50.5 | -1 | -1 | -10 | -6 | -6 | 0 | 12 | 1 | 1 | -6 | 10 | 0 | 0
738.05 | 50.5 | 50.5 | -1 | -0.3 | -3 | 50.5 | -1 | -1 | -10 | -6.5 | -6.5 | 0 | 12 | 1 | 1 | -6.5 | 10 | 0 | 0
738.1 | 50.5 | 50.5 | -1 | -0.4 | -4 | 50.5 | -1 | -1 | -10 | -7 | -7 | 0 | 12 | 1 | 1 | -7 | 10 | 0 | 0
738.15 | 50.5 | 50.5 | -1 | -0.5 | -5 | 50.5 | -1 | -1 | -10 | -7.5 | -7.5 | 0 | 12 | 1 | 1 | -7.5 | 10 | 0 | 0
738.2 | 50.5 | 50.5 | -1 | -0.6 | -6 | 50.5 | -1 | -1 | -10 | -8 | -8 | 0 | 12 | 1 | 1 | -8 | 10 | 0 | 0
738.25 | 50.5 | 50.5 | -1 | -0.7 | -7 | 50.5 | -1 | -1 | -10 | -8.5 | -8.5 | 0 | 12 | 1 | 1 | -8.5 | 10 | 0 | 0
738.3 | 50.5 | 50.5 | -1 | -0.8 | -8 | 50.5 | -1 | -1 | -10 | -9 | -9 | 0 | 12 | 1 | 1 | -9 | 10 | 0 | 0
738.35 | 50.5 | 50.5 | -1 | -0.9 | -9 | 50.5 | -1 | -1 | -10 | -9.5 | -9.5 | 0 | 12 | 1 | 1 | -9.5 | 10 | 0 | 0
738.4 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
738.45 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
738.5 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
738.55 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
738.6 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
738.65 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
738.7 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
738.75 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
738.8 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
738.85 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
738.9 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
738.95 | 50.47 | 50.47 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
739 | 50.45 | 50.45 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
739.05 | 50.42 | 50.42 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
739.1 | 50.4 | 50.4 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
739.15 | 50.37 | 50.37 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
739.2 | 50.35 | 50.35 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
739.25 | 50.32 | 50.32 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
739.3 | 50.29 | 50.29 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
739.35 | 50.27 | 50.27 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
739.4 | 50.24 | 50.24 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
739.45 | 50.22 | 50.22 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
739.5 | 50.19 | 50.19 | -0.905 | -0.905 | -9.05 | 50.47 | -1 | -1 | -10 | -9.525 | -9.525 | 0 | 12 | 1 | 1 | -9.525 | 10 | 0 | 0
739.55 | 50.17 | 50.17 | -0.715 | -0.715 | -7.15 | 50.45 | -1 | -1 | -10 | -8.575 | -8.575 | 0 | 12 | 1 | 1 | -8.575 | 10 | 0 | 0
739.6 | 50.14 | 50.14 | -0.43 | -0.43 | -4.3 | 50.42 | -1 | -1 | -10 | -7.15 | -7.15 | 0 | 12 | 1 | 1 | -7.15 | 10 | 0 | 0
739.65 | 50.12 | 50.12 | -0.24 | -0.24 | -2.4 | 50.4 | -1 | -1 | -10 | -6.2 | -6.2 | 0 | 12 | 1 | 1 | -6.2 | 10 | 0 | 0
739.7 | 50.09 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 50.37 | -1 | -1 | -10 | -5.2206 | -5.2206 | 0 | 12 | 1 | 1 | -5.2206 | 10 | 0 | 0
739.75 | 50.06 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.35 | -1 | -1 | -10 | -5.1324 | -5.1324 | 0 | 12 | 1 | 1 | -5.1324 | 10 | 0 | 0
739.8 | 50.04 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.32 | -1 | -1 | -10 | -5.0735 | -5.0735 | 0 | 12 | 1 | 1 | -5.0735 | 10 | 0 | 0
739.85 | 50.01 | 50.01 | 0 | 0 | 0 | 50.29 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
739.9 | 49.99 | 49.99 | 0 | 0 | 0 | 50.27 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
739.95 | 49.96 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.24 | -1 | -1 | -10 | -4.9265 | -4.9265 | 0 | 12 | 1 | 1 | -4.9265 | 10 | 0 | 0
740 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.22 | -1 | -1 | -10 | -4.8676 | -4.8676 | 0 | 12 | 1 | 1 | -4.8676 | 10 | 0 | 0
740.05 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.19 | -0.905 | -0.905 | -9.05 | -4.3044 | -4.3044 | 0 | 12 | 1 | 1 | -4.3044 | 10 | 0 | 0
740.1 | 49.88 | 49.88 | 0.24 | 0.24 | 2.4 | 50.17 | -0.715 | -0.805 | -8.05 | -2.825 | -2.825 | 0 | 12 | 1 | 1 | -2.825 | 10 | 0 | 0
740.15 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.14 | -0.43 | -0.705 | -7.05 | -1.375 | -1.375 | 0 | 12 | 1 | 1 | -1.375 | 10 | 0 | 0
740.2 | 49.83 | 49.83 | 0.715 | 0.715 | 7.15 | 50.12 | -0.24 | -0.605 | -6.05 | 0.55 | 0.55 | 0 | 12 | 1 | 1 | 0.55 | 10 | 0 | 0
740.25 | 49.81 | 49.81 | 0.905 | 0.905 | 9.05 | 50.09 | -0.044118 | -0.505 | -5.05 | 2 | 2 | 0 | 12 | 1 | 1 | 2 | 10 | 0 | 0
740.3 | 49.78 | 49.78 | 1 | 1 | 10 | 50.06 | -0.026471 | -0.405 | -4.05 | 2.975 | 2.975 | 0 | 12 | 1 | 1 | 2.975 | 10 | 0 | 0
740.35 | 49.76 | 49.76 | 1 | 1 | 10 | 50.04 | -0.014706 | -0.305 | -3.05 | 3.475 | 3.475 | 0 | 12 | 1 | 1 | 3.475 | 10 | 0 | 0
740.4 | 49.73 | 49.73 | 1 | 1 | 10 | 50.01 | 0 | -0.205 | -2.05 | 3.975 | 3.975 | 0 | 12 | 1 | 1 | 3.975 | 10 | 0 | 0
740.45 | 49.71 | 49.71 | 1 | 1 | 10 | 49.99 | 0 | -0.105 | -1.05 | 4.475 | 4.475 | 0 | 12 | 1 | 1 | 4.475 | 10 | 0 | 0
740.5 | 49.68 | 49.68 | 1 | 1 | 10 | 49.96 | 0.014706 | -0.005 | -0.05 | 4.975 | 4.975 | 0 | 12 | 1 | 1 | 4.975 | 10 | 0 | 0
740.55 | 49.65 | 49.65 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
740.6 | 49.63 | 49.63 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
740.65 | 49.6 | 49.6 | 1 | 1 | 10 | 49.88 | 0.24 | 0.14412 | 1.4412 | 5.7206 | 5.7206 | 0 | 12 | 1 | 1 | 5.7206 | 10 | 0 | 0
740.7 | 49.58 | 49.58 | 1 | 1 | 10 | 49.86 | 0.43 | 0.24412 | 2.4412 | 6.2206 | 6.2206 | 0 | 12 | 1 | 1 | 6.2206 | 10 | 0 | 0
740.75 | 49.55 | 49.55 | 1 | 1 | 10 | 49.83 | 0.715 | 0.34412 | 3.4412 | 6.7206 | 6.7206 | 0 | 12 | 1 | 1 | 6.7206 | 10 | 0 | 0
740.8 | 49.53 | 49.53 | 1 | 1 | 10 | 49.81 | 0.905 | 0.44412 | 4.4412 | 7.2206 | 7.2206 | 0 | 12 | 1 | 1 | 7.2206 | 10 | 0 | 0
740.85 | 49.5 | 49.5 | 1 | 1 | 10 | 49.78 | 1 | 0.54412 | 5.4412 | 7.7206 | 7.7206 | 0 | 12 | 1 | 1 | 7.7206 | 10 | 0 | 0
740.9 | 49.5 | 49.5 | 1 | 1 | 10 | 49.76 | 1 | 0.64412 | 6.4412 | 8.2206 | 8.2206 | 0 | 12 | 1 | 1 | 8.2206 | 10 | 0 | 0
740.95 | 49.53 | 49.5 | 1 | 1 | 10 | 49.73 | 1 | 0.74412 | 7.4412 | 8.7206 | 8.7206 | 0 | 12 | 1 | 1 | 8.7206 | 10 | 0 | 0
741 | 49.55 | 49.5 | 1 | 1 | 10 | 49.71 | 1 | 0.84412 | 8.4412 | 9.2206 | 9.2206 | 0 | 12 | 1 | 1 | 9.2206 | 10 | 0 | 0
741.05 | 49.58 | 49.5 | 1 | 1 | 10 | 49.68 | 1 | 0.94412 | 9.4412 | 9.7206 | 9.7206 | 0 | 12 | 1 | 1 | 9.7206 | 10 | 0 | 0
741.1 | 49.6 | 49.5 | 1 | 1 | 10 | 49.65 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
741.15 | 49.63 | 49.5 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
741.2 | 49.65 | 49.5 | 1 | 1 | 10 | 49.65 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
741.25 | 49.68 | 49.5 | 1 | 1 | 10 | 49.68 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
741.3 | 49.71 | 49.5 | 1 | 1 | 10 | 49.71 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
741.35 | 49.73 | 49.5 | 1 | 1 | 10 | 49.73 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
741.4 | 49.76 | 49.5 | 1 | 1 | 10 | 49.76 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
741.45 | 49.78 | 49.5 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
741.5 | 49.81 | 49.53 | 1 | 1 | 10 | 49.81 | 0.905 | 0.905 | 9.05 | 9.525 | 9.525 | 0 | 12 | 1 | 1 | 9.525 | 10 | 0 | 0
741.55 | 49.83 | 49.55 | 1 | 1 | 10 | 49.83 | 0.715 | 0.715 | 7.15 | 8.575 | 8.575 | 0 | 12 | 1 | 1 | 8.575 | 10 | 0 | 0
741.6 | 49.86 | 49.58 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
741.65 | 49.88 | 49.6 | 1 | 1 | 10 | 49.88 | 0.24 | 0.24 | 2.4 | 6.2 | 6.2 | 0 | 12 | 1 | 1 | 6.2 | 10 | 0 | 0
741.7 | 49.91 | 49.63 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
741.75 | 49.94 | 49.65 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
741.8 | 49.96 | 49.68 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
741.85 | 49.99 | 49.71 | 1 | 1 | 10 | 49.99 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
741.9 | 50.01 | 49.73 | 1 | 1 | 10 | 50.01 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
741.95 | 50.04 | 49.76 | 1 | 1 | 10 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 4.9265 | 4.9265 | 0 | 12 | 1 | 1 | 4.9265 | 10 | 0 | 0
742 | 50.06 | 49.78 | 1 | 1 | 10 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 4.8676 | 4.8676 | 0 | 12 | 1 | 1 | 4.8676 | 10 | 0 | 0
742.05 | 50.09 | 49.81 | 0.905 | 0.905 | 9.05 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 4.3044 | 4.3044 | 0 | 12 | 1 | 1 | 4.3044 | 10 | 0 | 0
742.1 | 50.12 | 49.83 | 0.715 | 0.805 | 8.05 | 50.12 | -0.24 | -0.24 | -2.4 | 2.825 | 2.825 | 0 | 12 | 1 | 1 | 2.825 | 10 | 0 | 0
742.15 | 50.14 | 49.86 | 0.43 | 0.705 | 7.05 | 50.14 | -0.43 | -0.43 | -4.3 | 1.375 | 1.375 | 0 | 12 | 1 | 1 | 1.375 | 10 | 0 | 0
742.2 | 50.17 | 49.88 | 0.24 | 0.605 | 6.05 | 50.17 | -0.715 | -0.715 | -7.15 | -0.55 | -0.55 | 0 | 12 | 1 | 1 | -0.55 | 10 | 0 | 0
742.25 | 50.19 | 49.91 | 0.044118 | 0.505 | 5.05 | 50.19 | -0.905 | -0.905 | -9.05 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
742.3 | 50.22 | 49.94 | 0.026471 | 0.405 | 4.05 | 50.22 | -1 | -1 | -10 | -2.975 | -2.975 | 0 | 12 | 1 | 1 | -2.975 | 10 | 0 | 0
742.35 | 50.24 | 49.96 | 0.014706 | 0.305 | 3.05 | 50.24 | -1 | -1 | -10 | -3.475 | -3.475 | 0 | 12 | 1 | 1 | -3.475 | 10 | 0 | 0
742.4 | 50.27 | 49.99 | 0 | 0.205 | 2.05 | 50.27 | -1 | -1 | -10 | -3.975 | -3.975 | 0 | 12 | 1 | 1 | -3.975 | 10 | 0 | 0
742.45 | 50.29 | 50.01 | 0 | 0.105 | 1.05 | 50.29 | -1 | -1 | -10 | -4.475 | -4.475 | 0 | 12 | 1 | 1 | -4.475 | 10 | 0 | 0
742.5 | 50.32 | 50.04 | -0.014706 | 0.005 | 0.05 | 50.32 | -1 | -1 | -10 | -4.975 | -4.975 | 0 | 12 | 1 | 1 | -4.975 | 10 | 0 | 0
742.55 | 50.35 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.35 | -1 | -1 | -10 | -5.1324 | -5.1324 | 0 | 12 | 1 | 1 | -5.1324 | 10 | 0 | 0
742.6 | 50.37 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 50.37 | -1 | -1 | -10 | -5.2206 | -5.2206 | 0 | 12 | 1 | 1 | -5.2206 | 10 | 0 | 0
742.65 | 50.4 | 50.12 | -0.24 | -0.14412 | -1.4412 | 50.4 | -1 | -1 | -10 | -5.7206 | -5.7206 | 0 | 12 | 1 | 1 | -5.7206 | 10 | 0 | 0
742.7 | 50.42 | 50.14 | -0.43 | -0.24412 | -2.4412 | 50.42 | -1 | -1 | -10 | -6.2206 | -6.2206 | 0 | 12 | 1 | 1 | -6.2206 | 10 | 0 | 0
742.75 | 50.45 | 50.17 | -0.715 | -0.34412 | -3.4412 | 50.45 | -1 | -1 | -10 | -6.7206 | -6.7206 | 0 | 12 | 1 | 1 | -6.7206 | 10 | 0 | 0
742.8 | 50.47 | 50.19 | -0.905 | -0.44412 | -4.4412 | 50.47 | -1 | -1 | -10 | -7.2206 | -7.2206 | 0 | 12 | 1 | 1 | -7.2206 | 10 | 0 | 0
742.85 | 50.5 | 50.22 | -1 | -0.54412 | -5.4412 | 50.5 | -1 | -1 | -10 | -7.7206 | -7.7206 | 0 | 12 | 1 | 1 | -7.7206 | 10 | 0 | 0
742.9 | 50.5 | 50.24 | -1 | -0.64412 | -6.4412 | 50.5 | -1 | -1 | -10 | -8.2206 | -8.2206 | 0 | 12 | 1 | 1 | -8.2206 | 10 | 0 | 0
742.95 | 50.47 | 50.27 | -1 | -0.74412 | -7.4412 | 50.5 | -1 | -1 | -10 | -8.7206 | -8.7206 | 0 | 12 | 1 | 1 | -8.7206 | 10 | 0 | 0
743 | 50.45 | 50.29 | -1 | -0.84412 | -8.4412 | 50.5 | -1 | -1 | -10 | -9.2206 | -9.2206 | 0 | 12 | 1 | 1 | -9.2206 | 10 | 0 | 0
743.05 | 50.42 | 50.32 | -1 | -0.94412 | -9.4412 | 50.5 | -1 | -1 | -10 | -9.7206 | -9.7206 | 0 | 12 | 1 | 1 | -9.7206 | 10 | 0 | 0
743.1 | 50.39 | 50.35 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
743.15 | 50.37 | 50.37 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
743.2 | 50.34 | 50.34 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
743.25 | 50.32 | 50.32 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
743.3 | 50.29 | 50.29 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
743.35 | 50.26 | 50.26 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
743.4 | 50.24 | 50.24 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
743.45 | 50.21 | 50.21 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
743.5 | 50.18 | 50.18 | -0.81 | -0.81 | -8.1 | 50.47 | -1 | -1 | -10 | -9.05 | -9.05 | 0 | 12 | 1 | 1 | -9.05 | 10 | 0 | 0
743.55 | 50.16 | 50.16 | -0.62 | -0.62 | -6.2 | 50.45 | -1 | -1 | -10 | -8.1 | -8.1 | 0 | 12 | 1 | 1 | -8.1 | 10 | 0 | 0
743.6 | 50.13 | 50.13 | -0.335 | -0.335 | -3.35 | 50.42 | -1 | -1 | -10 | -6.675 | -6.675 | 0 | 12 | 1 | 1 | -6.675 | 10 | 0 | 0
743.65 | 50.11 | 50.11 | -0.145 | -0.145 | -1.45 | 50.39 | -1 | -1 | -10 | -5.725 | -5.725 | 0 | 12 | 1 | 1 | -5.725 | 10 | 0 | 0
743.7 | 50.08 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 50.37 | -1 | -1 | -10 | -5.1912 | -5.1912 | 0 | 12 | 1 | 1 | -5.1912 | 10 | 0 | 0
743.75 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.34 | -1 | -1 | -10 | -5.1029 | -5.1029 | 0 | 12 | 1 | 1 | -5.1029 | 10 | 0 | 0
743.8 | 50.03 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 50.32 | -1 | -1 | -10 | -5.0441 | -5.0441 | 0 | 12 | 1 | 1 | -5.0441 | 10 | 0 | 0
743.85 | 50 | 50 | 0 | 0 | 0 | 50.29 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
743.9 | 50 | 50 | 0 | 0 | 0 | 50.26 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
743.95 | 50 | 50 | 0 | 0 | 0 | 50.24 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
744 | 50 | 50 | 0 | 0 | 0 | 50.21 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
744.05 | 50 | 50 | 0 | 0 | 0 | 50.18 | -0.81 | -0.9 | -9 | -4.5 | -4.5 | 0 | 12 | 1 | 1 | -4.5 | 10 | 0 | 0
744.1 | 50 | 50 | 0 | 0 | 0 | 50.16 | -0.62 | -0.8 | -8 | -4 | -4 | 0 | 12 | 1 | 1 | -4 | 10 | 0 | 0
744.15 | 50 | 50 | 0 | 0 | 0 | 50.13 | -0.335 | -0.7 | -7 | -3.5 | -3.5 | 0 | 12 | 1 | 1 | -3.5 | 10 | 0 | 0
744.2 | 50.01 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.6 | -6 | -3 | -3 | 0 | 12 | 1 | 1 | -3 | 10 | 0 | 0
744.25 | 50.01 | 50 | 0 | 0 | 0 | 50.08 | -0.038235 | -0.5 | -5 | -2.5 | -2.5 | 0 | 12 | 1 | 1 | -2.5 | 10 | 0 | 0
744.3 | 49.99 | 49.99 | 0 | 0 | 0 | 50.05 | -0.020588 | -0.4 | -4 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
744.35 | 49.99 | 49.99 | 0 | 0 | 0 | 50.03 | -0.0088235 | -0.3 | -3 | -1.5 | -1.5 | 0 | 12 | 1 | 1 | -1.5 | 10 | 0 | 0
744.4 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | -0.2 | -2 | -0.83824 | -0.83824 | 0 | 12 | 1 | 1 | -0.83824 | 10 | 0 | 0
744.45 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | -0.1 | -1 | -0.33824 | -0.33824 | 0 | 12 | 1 | 1 | -0.33824 | 10 | 0 | 0
744.5 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
744.55 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
744.6 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
744.65 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
744.7 | 49.89 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
744.75 | 49.89 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
744.8 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50.01 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
744.85 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
744.9 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
744.95 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 2.7868 | 2.7868 | 0 | 12 | 1 | 1 | 2.7868 | 10 | 0 | 0
745 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 2.7868 | 2.7868 | 0 | 12 | 1 | 1 | 2.7868 | 10 | 0 | 0
745.05 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 2.8456 | 2.8456 | 0 | 12 | 1 | 1 | 2.8456 | 10 | 0 | 0
745.1 | 49.94 | 49.85 | 0.525 | 0.525 | 5.25 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 2.7574 | 2.7574 | 0 | 12 | 1 | 1 | 2.7574 | 10 | 0 | 0
745.15 | 49.94 | 49.85 | 0.525 | 0.525 | 5.25 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 2.7574 | 2.7574 | 0 | 12 | 1 | 1 | 2.7574 | 10 | 0 | 0
745.2 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
745.25 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
745.3 | 49.93 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
745.35 | 49.93 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
745.4 | 49.96 | 49.85 | 0.525 | 0.525 | 5.25 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 2.6985 | 2.6985 | 0 | 12 | 1 | 1 | 2.6985 | 10 | 0 | 0
745.45 | 49.96 | 49.85 | 0.525 | 0.525 | 5.25 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 2.6985 | 2.6985 | 0 | 12 | 1 | 1 | 2.6985 | 10 | 0 | 0
745.5 | 49.99 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
745.55 | 49.99 | 49.91 | 0.044118 | 0.425 | 4.25 | 49.99 | 0 | 0 | 0 | 2.125 | 2.125 | 0 | 12 | 1 | 1 | 2.125 | 10 | 0 | 0
745.6 | 49.99 | 49.91 | 0.044118 | 0.325 | 3.25 | 49.99 | 0 | 0 | 0 | 1.625 | 1.625 | 0 | 12 | 1 | 1 | 1.625 | 10 | 0 | 0
745.65 | 49.99 | 49.93 | 0.032353 | 0.225 | 2.25 | 49.99 | 0 | 0 | 0 | 1.125 | 1.125 | 0 | 12 | 1 | 1 | 1.125 | 10 | 0 | 0
745.7 | 49.96 | 49.93 | 0.032353 | 0.125 | 1.25 | 49.99 | 0 | 0 | 0 | 0.625 | 0.625 | 0 | 12 | 1 | 1 | 0.625 | 10 | 0 | 0
745.75 | 49.96 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 49.99 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
745.8 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
745.85 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
745.9 | 50.05 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.058824 | 0.058824 | 0 | 12 | 1 | 1 | 0.058824 | 10 | 0 | 0
745.95 | 50.05 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
746 | 49.97 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
746.05 | 49.97 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
746.1 | 49.92 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
746.15 | 49.92 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
746.2 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
746.25 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
746.3 | 49.94 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
746.35 | 49.94 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
746.4 | 50.01 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
746.45 | 50.01 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
746.5 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
746.55 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
746.6 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
746.65 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
746.7 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
746.75 | 49.95 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
746.8 | 49.97 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
746.85 | 49.97 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
746.9 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
746.95 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
747 | 49.87 | 49.87 | 0.335 | 0.335 | 3.35 | 50.01 | 0 | 0 | 0 | 1.675 | 1.675 | 0 | 12 | 1 | 1 | 1.675 | 10 | 0 | 0
747.05 | 49.87 | 49.87 | 0.335 | 0.335 | 3.35 | 49.99 | 0 | 0 | 0 | 1.675 | 1.675 | 0 | 12 | 1 | 1 | 1.675 | 10 | 0 | 0
747.1 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
747.15 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 2.6691 | 2.6691 | 0 | 12 | 1 | 1 | 2.6691 | 10 | 0 | 0
747.2 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
747.25 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
747.3 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
747.35 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
747.4 | 49.84 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
747.45 | 49.84 | 49.79 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
747.5 | 49.89 | 49.79 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
747.55 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.12647 | 1.2647 | 5.6324 | 5.6324 | 0 | 12 | 1 | 1 | 5.6324 | 10 | 0 | 0
747.6 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.145 | 1.45 | 5.725 | 5.725 | 0 | 12 | 1 | 1 | 5.725 | 10 | 0 | 0
747.65 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.145 | 1.45 | 5.725 | 5.725 | 0 | 12 | 1 | 1 | 5.725 | 10 | 0 | 0
747.7 | 49.96 | 49.79 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
747.75 | 49.96 | 49.79 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
747.8 | 50.02 | 49.79 | 1 | 1 | 10 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 4.9853 | 4.9853 | 0 | 12 | 1 | 1 | 4.9853 | 10 | 0 | 0
747.85 | 50.02 | 49.79 | 1 | 1 | 10 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 4.9853 | 4.9853 | 0 | 12 | 1 | 1 | 4.9853 | 10 | 0 | 0
747.9 | 50.03 | 49.79 | 1 | 1 | 10 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.9559 | 4.9559 | 0 | 12 | 1 | 1 | 4.9559 | 10 | 0 | 0
747.95 | 50.03 | 49.84 | 0.62 | 0.9 | 9 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.4559 | 4.4559 | 0 | 12 | 1 | 1 | 4.4559 | 10 | 0 | 0
748 | 50.02 | 49.84 | 0.62 | 0.8 | 8 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 3.9559 | 3.9559 | 0 | 12 | 1 | 1 | 3.9559 | 10 | 0 | 0
748.05 | 50.02 | 49.89 | 0.145 | 0.7 | 7 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 3.4559 | 3.4559 | 0 | 12 | 1 | 1 | 3.4559 | 10 | 0 | 0
748.1 | 50.08 | 49.89 | 0.145 | 0.6 | 6 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 2.8088 | 2.8088 | 0 | 12 | 1 | 1 | 2.8088 | 10 | 0 | 0
748.15 | 50.08 | 49.89 | 0.145 | 0.5 | 5 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 2.3088 | 2.3088 | 0 | 12 | 1 | 1 | 2.3088 | 10 | 0 | 0
748.2 | 50.01 | 49.89 | 0.145 | 0.4 | 4 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 1.8088 | 1.8088 | 0 | 12 | 1 | 1 | 1.8088 | 10 | 0 | 0
748.25 | 50.01 | 49.96 | 0.014706 | 0.3 | 3 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 1.3088 | 1.3088 | 0 | 12 | 1 | 1 | 1.3088 | 10 | 0 | 0
748.3 | 49.94 | 49.94 | 0.026471 | 0.2 | 2 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.80882 | 0.80882 | 0 | 12 | 1 | 1 | 0.80882 | 10 | 0 | 0
748.35 | 49.94 | 49.94 | 0.026471 | 0.1 | 1 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.30882 | 0.30882 | 0 | 12 | 1 | 1 | 0.30882 | 10 | 0 | 0
748.4 | 50 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
748.45 | 50 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
748.5 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
748.55 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
748.6 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
748.65 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
748.7 | 49.92 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
748.75 | 49.92 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
748.8 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50.01 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
748.85 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
748.9 | 49.92 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
748.95 | 49.92 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
749 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
749.05 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
749.1 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
749.15 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
749.2 | 49.87 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
749.25 | 49.87 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
749.3 | 49.8 | 49.8 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
749.35 | 49.8 | 49.8 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
749.4 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
749.45 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
749.5 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
749.55 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
749.6 | 49.72 | 49.72 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
749.65 | 49.72 | 49.72 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
749.7 | 49.67 | 49.67 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
749.75 | 49.67 | 49.67 | 1 | 1 | 10 | 49.87 | 0.335 | 0.14412 | 1.4412 | 5.7206 | 5.7206 | 0 | 12 | 1 | 1 | 5.7206 | 10 | 0 | 0
749.8 | 49.65 | 49.65 | 1 | 1 | 10 | 49.87 | 0.335 | 0.24412 | 2.4412 | 6.2206 | 6.2206 | 0 | 12 | 1 | 1 | 6.2206 | 10 | 0 | 0
749.85 | 49.65 | 49.65 | 1 | 1 | 10 | 49.8 | 1 | 0.34412 | 3.4412 | 6.7206 | 6.7206 | 0 | 12 | 1 | 1 | 6.7206 | 10 | 0 | 0
749.9 | 49.59 | 49.59 | 1 | 1 | 10 | 49.8 | 1 | 0.44412 | 4.4412 | 7.2206 | 7.2206 | 0 | 12 | 1 | 1 | 7.2206 | 10 | 0 | 0
749.95 | 49.59 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.54412 | 5.4412 | 7.7206 | 7.7206 | 0 | 12 | 1 | 1 | 7.7206 | 10 | 0 | 0
750 | 49.66 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.64412 | 6.4412 | 8.2206 | 8.2206 | 0 | 12 | 1 | 1 | 8.2206 | 10 | 0 | 0
750.05 | 49.66 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.74412 | 7.4412 | 8.7206 | 8.7206 | 0 | 12 | 1 | 1 | 8.7206 | 10 | 0 | 0
750.1 | 49.63 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.84412 | 8.4412 | 9.2206 | 9.2206 | 0 | 12 | 1 | 1 | 9.2206 | 10 | 0 | 0
750.15 | 49.63 | 49.59 | 1 | 1 | 10 | 49.72 | 1 | 0.94412 | 9.4412 | 9.7206 | 9.7206 | 0 | 12 | 1 | 1 | 9.7206 | 10 | 0 | 0
750.2 | 49.61 | 49.59 | 1 | 1 | 10 | 49.72 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
750.25 | 49.61 | 49.59 | 1 | 1 | 10 | 49.67 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
750.3 | 49.54 | 49.54 | 1 | 1 | 10 | 49.67 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
750.35 | 49.54 | 49.54 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
750.4 | 49.46 | 49.46 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
750.45 | 49.46 | 49.46 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
750.5 | 49.45 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
750.55 | 49.45 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
750.6 | 49.51 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
750.65 | 49.51 | 49.45 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
750.7 | 49.5 | 49.45 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
750.75 | 49.5 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
750.8 | 49.54 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
750.85 | 49.54 | 49.45 | 1 | 1 | 10 | 49.54 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
750.9 | 49.59 | 49.45 | 1 | 1 | 10 | 49.59 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
750.95 | 49.59 | 49.45 | 1 | 1 | 10 | 49.59 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
751 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
751.05 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
751.1 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
751.15 | 49.61 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
751.2 | 49.53 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
751.25 | 49.53 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
751.3 | 49.54 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
751.35 | 49.54 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
751.4 | 49.61 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
751.45 | 49.61 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
751.5 | 49.66 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
751.55 | 49.66 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
751.6 | 49.64 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
751.65 | 49.64 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
751.7 | 49.69 | 49.53 | 1 | 1 | 10 | 49.69 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
751.75 | 49.69 | 49.53 | 1 | 1 | 10 | 49.69 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
751.8 | 49.74 | 49.53 | 1 | 1 | 10 | 49.74 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
751.85 | 49.74 | 49.54 | 1 | 1 | 10 | 49.74 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
751.9 | 49.78 | 49.54 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
751.95 | 49.78 | 49.61 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
752 | 49.82 | 49.61 | 1 | 1 | 10 | 49.82 | 0.81 | 0.81 | 8.1 | 9.05 | 9.05 | 0 | 12 | 1 | 1 | 9.05 | 10 | 0 | 0
752.05 | 49.82 | 49.64 | 1 | 1 | 10 | 49.82 | 0.81 | 0.81 | 8.1 | 9.05 | 9.05 | 0 | 12 | 1 | 1 | 9.05 | 10 | 0 | 0
752.1 | 49.86 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
752.15 | 49.86 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
752.2 | 49.84 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
752.25 | 49.84 | 49.69 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
752.3 | 49.91 | 49.69 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
752.35 | 49.91 | 49.74 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
752.4 | 49.97 | 49.74 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
752.45 | 49.97 | 49.78 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
752.5 | 50.03 | 49.78 | 1 | 1 | 10 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.9559 | 4.9559 | 0 | 12 | 1 | 1 | 4.9559 | 10 | 0 | 0
752.55 | 50.03 | 49.82 | 0.81 | 0.9 | 9 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.4559 | 4.4559 | 0 | 12 | 1 | 1 | 4.4559 | 10 | 0 | 0
752.6 | 50.05 | 49.82 | 0.81 | 0.81 | 8.1 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 3.9471 | 3.9471 | 0 | 12 | 1 | 1 | 3.9471 | 10 | 0 | 0
752.65 | 50.05 | 49.84 | 0.62 | 0.71 | 7.1 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 3.4471 | 3.4471 | 0 | 12 | 1 | 1 | 3.4471 | 10 | 0 | 0
752.7 | 50.01 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
752.75 | 50.01 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
752.8 | 49.95 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
752.85 | 49.95 | 49.91 | 0.044118 | 0.52 | 5.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.4971 | 2.4971 | 0 | 12 | 1 | 1 | 2.4971 | 10 | 0 | 0
752.9 | 49.99 | 49.91 | 0.044118 | 0.42 | 4.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 1.9971 | 1.9971 | 0 | 12 | 1 | 1 | 1.9971 | 10 | 0 | 0
752.95 | 49.99 | 49.95 | 0.020588 | 0.32 | 3.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 1.4971 | 1.4971 | 0 | 12 | 1 | 1 | 1.4971 | 10 | 0 | 0
753 | 49.92 | 49.92 | 0.038235 | 0.22 | 2.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.99706 | 0.99706 | 0 | 12 | 1 | 1 | 0.99706 | 10 | 0 | 0
753.05 | 49.92 | 49.92 | 0.038235 | 0.12 | 1.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.49706 | 0.49706 | 0 | 12 | 1 | 1 | 0.49706 | 10 | 0 | 0
753.1 | 49.97 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
753.15 | 49.97 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
753.2 | 50.02 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
753.25 | 50.02 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.17647 | 0.17647 | 0 | 12 | 1 | 1 | 0.17647 | 10 | 0 | 0
753.3 | 50.07 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
753.35 | 50.07 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
753.4 | 50.06 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
753.45 | 50.06 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
753.5 | 50.13 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
753.55 | 50.13 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
753.6 | 50.09 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
753.65 | 50.09 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6309 | -1.6309 | 0 | 12 | 1 | 1 | -1.6309 | 10 | 0 | 0
753.7 | 50.07 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6309 | -1.6309 | 0 | 12 | 1 | 1 | -1.6309 | 10 | 0 | 0
753.75 | 50.07 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6897 | -1.6897 | 0 | 12 | 1 | 1 | -1.6897 | 10 | 0 | 0
753.8 | 50.07 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6897 | -1.6897 | 0 | 12 | 1 | 1 | -1.6897 | 10 | 0 | 0
753.85 | 50.07 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.13 | -0.335 | -0.335 | -3.35 | -1.8074 | -1.8074 | 0 | 12 | 1 | 1 | -1.8074 | 10 | 0 | 0
753.9 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.13 | -0.335 | -0.335 | -3.35 | -1.7779 | -1.7779 | 0 | 12 | 1 | 1 | -1.7779 | 10 | 0 | 0
753.95 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.13 | -0.335 | -0.335 | -3.35 | -1.7779 | -1.7779 | 0 | 12 | 1 | 1 | -1.7779 | 10 | 0 | 0
754 | 50.01 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
754.05 | 50.01 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
754.1 | 50.07 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
754.15 | 50.07 | 50.01 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.235 | -2.35 | -1.175 | -1.175 | 0 | 12 | 1 | 1 | -1.175 | 10 | 0 | 0
754.2 | 50.05 | 50.01 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.135 | -1.35 | -0.675 | -0.675 | 0 | 12 | 1 | 1 | -0.675 | 10 | 0 | 0
754.25 | 50.05 | 50.01 | 0 | 0 | 0 | 50.07 | -0.032353 | -0.035 | -0.35 | -0.175 | -0.175 | 0 | 12 | 1 | 1 | -0.175 | 10 | 0 | 0
754.3 | 50.1 | 50.01 | 0 | 0 | 0 | 50.1 | -0.05 | -0.05 | -0.5 | -0.25 | -0.25 | 0 | 12 | 1 | 1 | -0.25 | 10 | 0 | 0
754.35 | 50.1 | 50.01 | 0 | 0 | 0 | 50.1 | -0.05 | -0.05 | -0.5 | -0.25 | -0.25 | 0 | 12 | 1 | 1 | -0.25 | 10 | 0 | 0
754.4 | 50.11 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
754.45 | 50.11 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
754.5 | 50.06 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
754.55 | 50.06 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
754.6 | 50.04 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
754.65 | 50.04 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
754.7 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
754.75 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
754.8 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
754.85 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
754.9 | 50.11 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
754.95 | 50.11 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
755 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
755.05 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
755.1 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
755.15 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
755.2 | 50.02 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.11 | -0.145 | -0.145 | -1.45 | -0.73971 | -0.73971 | 0 | 12 | 1 | 1 | -0.73971 | 10 | 0 | 0
755.25 | 50.02 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.11 | -0.145 | -0.145 | -1.45 | -0.73971 | -0.73971 | 0 | 12 | 1 | 1 | -0.73971 | 10 | 0 | 0
755.3 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
755.35 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
755.4 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
755.45 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
755.5 | 50.01 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
755.55 | 50.01 | 50 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.045 | -0.45 | -0.225 | -0.225 | 0 | 12 | 1 | 1 | -0.225 | 10 | 0 | 0
755.6 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
755.65 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
755.7 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
755.75 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
755.8 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.14706 | 0.14706 | 0 | 12 | 1 | 1 | 0.14706 | 10 | 0 | 0
755.85 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
755.9 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
755.95 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
756 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
756.05 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
756.1 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
756.15 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
756.2 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
756.25 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
756.3 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
756.35 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
756.4 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
756.45 | 50 | 50 | 0 | 0 | 0 | 50.01 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
756.5 | 49.5 | 49.5 | 1 | 1 | 10 | 50.01 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
756.55 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
756.6 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
756.65 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
756.7 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
756.75 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
756.8 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
756.85 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
756.9 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
756.95 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
757 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
757.05 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.1 | 1 | 5.5 | 5.5 | 0 | 12 | 1 | 1 | 5.5 | 10 | 0 | 0
757.1 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.2 | 2 | 6 | 6 | 0 | 12 | 1 | 1 | 6 | 10 | 0 | 0
757.15 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.3 | 3 | 6.5 | 6.5 | 0 | 12 | 1 | 1 | 6.5 | 10 | 0 | 0
757.2 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.4 | 4 | 7 | 7 | 0 | 12 | 1 | 1 | 7 | 10 | 0 | 0
757.25 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.5 | 5 | 7.5 | 7.5 | 0 | 12 | 1 | 1 | 7.5 | 10 | 0 | 0
757.3 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.6 | 6 | 8 | 8 | 0 | 12 | 1 | 1 | 8 | 10 | 0 | 0
757.35 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.7 | 7 | 8.5 | 8.5 | 0 | 12 | 1 | 1 | 8.5 | 10 | 0 | 0
757.4 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.8 | 8 | 9 | 9 | 0 | 12 | 1 | 1 | 9 | 10 | 0 | 0
757.45 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.9 | 9 | 9.5 | 9.5 | 0 | 12 | 1 | 1 | 9.5 | 10 | 0 | 0
757.5 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
757.55 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
757.6 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
757.65 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
757.7 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
757.75 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
757.8 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
757.85 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
757.9 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
757.95 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
758 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
758.05 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
758.1 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
758.15 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
758.2 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
758.25 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
758.3 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
758.35 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
758.4 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
758.45 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
758.5 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
758.55 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
758.6 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
758.65 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
758.7 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
758.75 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
758.8 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
758.85 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
758.9 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
758.95 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
759 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
759.05 | 50.5 | 50.5 | -1 | 0.9 | 9 | 50.5 | -1 | -1 | -10 | -0.5 | -0.5 | 0 | 12 | 1 | 1 | -0.5 | 10 | 0 | 0
759.1 | 50.5 | 50.5 | -1 | 0.8 | 8 | 50.5 | -1 | -1 | -10 | -1 | -1 | 0 | 12 | 1 | 1 | -1 | 10 | 0 | 0
759.15 | 50.5 | 50.5 | -1 | 0.7 | 7 | 50.5 | -1 | -1 | -10 | -1.5 | -1.5 | 0 | 12 | 1 | 1 | -1.5 | 10 | 0 | 0
759.2 | 50.5 | 50.5 | -1 | 0.6 | 6 | 50.5 | -1 | -1 | -10 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
759.25 | 50.5 | 50.5 | -1 | 0.5 | 5 | 50.5 | -1 | -1 | -10 | -2.5 | -2.5 | 0 | 12 | 1 | 1 | -2.5 | 10 | 0 | 0
759.3 | 50.5 | 50.5 | -1 | 0.4 | 4 | 50.5 | -1 | -1 | -10 | -3 | -3 | 0 | 12 | 1 | 1 | -3 | 10 | 0 | 0
759.35 | 50.5 | 50.5 | -1 | 0.3 | 3 | 50.5 | -1 | -1 | -10 | -3.5 | -3.5 | 0 | 12 | 1 | 1 | -3.5 | 10 | 0 | 0
759.4 | 50.5 | 50.5 | -1 | 0.2 | 2 | 50.5 | -1 | -1 | -10 | -4 | -4 | 0 | 12 | 1 | 1 | -4 | 10 | 0 | 0
759.45 | 50.5 | 50.5 | -1 | 0.1 | 1 | 50.5 | -1 | -1 | -10 | -4.5 | -4.5 | 0 | 12 | 1 | 1 | -4.5 | 10 | 0 | 0
759.5 | 50.5 | 50.5 | -1 | 0 | 0 | 50.5 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
759.55 | 50.5 | 50.5 | -1 | -0.1 | -1 | 50.5 | -1 | -1 | -10 | -5.5 | -5.5 | 0 | 12 | 1 | 1 | -5.5 | 10 | 0 | 0
759.6 | 50.5 | 50.5 | -1 | -0.2 | -2 | 50.5 | -1 | -1 | -10 | -6 | -6 | 0 | 12 | 1 | 1 | -6 | 10 | 0 | 0
759.65 | 50.5 | 50.5 | -1 | -0.3 | -3 | 50.5 | -1 | -1 | -10 | -6.5 | -6.5 | 0 | 12 | 1 | 1 | -6.5 | 10 | 0 | 0
759.7 | 50.5 | 50.5 | -1 | -0.4 | -4 | 50.5 | -1 | -1 | -10 | -7 | -7 | 0 | 12 | 1 | 1 | -7 | 10 | 0 | 0
759.75 | 50.5 | 50.5 | -1 | -0.5 | -5 | 50.5 | -1 | -1 | -10 | -7.5 | -7.5 | 0 | 12 | 1 | 1 | -7.5 | 10 | 0 | 0
759.8 | 50.5 | 50.5 | -1 | -0.6 | -6 | 50.5 | -1 | -1 | -10 | -8 | -8 | 0 | 12 | 1 | 1 | -8 | 10 | 0 | 0
759.85 | 50.5 | 50.5 | -1 | -0.7 | -7 | 50.5 | -1 | -1 | -10 | -8.5 | -8.5 | 0 | 12 | 1 | 1 | -8.5 | 10 | 0 | 0
759.9 | 50.5 | 50.5 | -1 | -0.8 | -8 | 50.5 | -1 | -1 | -10 | -9 | -9 | 0 | 12 | 1 | 1 | -9 | 10 | 0 | 0
759.95 | 50.5 | 50.5 | -1 | -0.9 | -9 | 50.5 | -1 | -1 | -10 | -9.5 | -9.5 | 0 | 12 | 1 | 1 | -9.5 | 10 | 0 | 0
760 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
760.05 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
760.1 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
760.15 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
760.2 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
760.25 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
760.3 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
760.35 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
760.4 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
760.45 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
760.5 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
760.55 | 50.47 | 50.47 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
760.6 | 50.45 | 50.45 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
760.65 | 50.42 | 50.42 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
760.7 | 50.4 | 50.4 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
760.75 | 50.37 | 50.37 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
760.8 | 50.35 | 50.35 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
760.85 | 50.32 | 50.32 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
760.9 | 50.29 | 50.29 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
760.95 | 50.27 | 50.27 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
761 | 50.24 | 50.24 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
761.05 | 50.22 | 50.22 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
761.1 | 50.19 | 50.19 | -0.905 | -0.905 | -9.05 | 50.47 | -1 | -1 | -10 | -9.525 | -9.525 | 0 | 12 | 1 | 1 | -9.525 | 10 | 0 | 0
761.15 | 50.17 | 50.17 | -0.715 | -0.715 | -7.15 | 50.45 | -1 | -1 | -10 | -8.575 | -8.575 | 0 | 12 | 1 | 1 | -8.575 | 10 | 0 | 0
761.2 | 50.14 | 50.14 | -0.43 | -0.43 | -4.3 | 50.42 | -1 | -1 | -10 | -7.15 | -7.15 | 0 | 12 | 1 | 1 | -7.15 | 10 | 0 | 0
761.25 | 50.12 | 50.12 | -0.24 | -0.24 | -2.4 | 50.4 | -1 | -1 | -10 | -6.2 | -6.2 | 0 | 12 | 1 | 1 | -6.2 | 10 | 0 | 0
761.3 | 50.09 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 50.37 | -1 | -1 | -10 | -5.2206 | -5.2206 | 0 | 12 | 1 | 1 | -5.2206 | 10 | 0 | 0
761.35 | 50.06 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.35 | -1 | -1 | -10 | -5.1324 | -5.1324 | 0 | 12 | 1 | 1 | -5.1324 | 10 | 0 | 0
761.4 | 50.04 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.32 | -1 | -1 | -10 | -5.0735 | -5.0735 | 0 | 12 | 1 | 1 | -5.0735 | 10 | 0 | 0
761.45 | 50.01 | 50.01 | 0 | 0 | 0 | 50.29 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
761.5 | 49.99 | 49.99 | 0 | 0 | 0 | 50.27 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
761.55 | 49.96 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.24 | -1 | -1 | -10 | -4.9265 | -4.9265 | 0 | 12 | 1 | 1 | -4.9265 | 10 | 0 | 0
761.6 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.22 | -1 | -1 | -10 | -4.8676 | -4.8676 | 0 | 12 | 1 | 1 | -4.8676 | 10 | 0 | 0
761.65 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.19 | -0.905 | -0.905 | -9.05 | -4.3044 | -4.3044 | 0 | 12 | 1 | 1 | -4.3044 | 10 | 0 | 0
761.7 | 49.88 | 49.88 | 0.24 | 0.24 | 2.4 | 50.17 | -0.715 | -0.805 | -8.05 | -2.825 | -2.825 | 0 | 12 | 1 | 1 | -2.825 | 10 | 0 | 0
761.75 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.14 | -0.43 | -0.705 | -7.05 | -1.375 | -1.375 | 0 | 12 | 1 | 1 | -1.375 | 10 | 0 | 0
761.8 | 49.83 | 49.83 | 0.715 | 0.715 | 7.15 | 50.12 | -0.24 | -0.605 | -6.05 | 0.55 | 0.55 | 0 | 12 | 1 | 1 | 0.55 | 10 | 0 | 0
761.85 | 49.81 | 49.81 | 0.905 | 0.905 | 9.05 | 50.09 | -0.044118 | -0.505 | -5.05 | 2 | 2 | 0 | 12 | 1 | 1 | 2 | 10 | 0 | 0
761.9 | 49.78 | 49.78 | 1 | 1 | 10 | 50.06 | -0.026471 | -0.405 | -4.05 | 2.975 | 2.975 | 0 | 12 | 1 | 1 | 2.975 | 10 | 0 | 0
761.95 | 49.76 | 49.76 | 1 | 1 | 10 | 50.04 | -0.014706 | -0.305 | -3.05 | 3.475 | 3.475 | 0 | 12 | 1 | 1 | 3.475 | 10 | 0 | 0
762 | 49.73 | 49.73 | 1 | 1 | 10 | 50.01 | 0 | -0.205 | -2.05 | 3.975 | 3.975 | 0 | 12 | 1 | 1 | 3.975 | 10 | 0 | 0
762.05 | 49.71 | 49.71 | 1 | 1 | 10 | 49.99 | 0 | -0.105 | -1.05 | 4.475 | 4.475 | 0 | 12 | 1 | 1 | 4.475 | 10 | 0 | 0
762.1 | 49.68 | 49.68 | 1 | 1 | 10 | 49.96 | 0.014706 | -0.005 | -0.05 | 4.975 | 4.975 | 0 | 12 | 1 | 1 | 4.975 | 10 | 0 | 0
762.15 | 49.65 | 49.65 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
762.2 | 49.63 | 49.63 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
762.25 | 49.6 | 49.6 | 1 | 1 | 10 | 49.88 | 0.24 | 0.14412 | 1.4412 | 5.7206 | 5.7206 | 0 | 12 | 1 | 1 | 5.7206 | 10 | 0 | 0
762.3 | 49.58 | 49.58 | 1 | 1 | 10 | 49.86 | 0.43 | 0.24412 | 2.4412 | 6.2206 | 6.2206 | 0 | 12 | 1 | 1 | 6.2206 | 10 | 0 | 0
762.35 | 49.55 | 49.55 | 1 | 1 | 10 | 49.83 | 0.715 | 0.34412 | 3.4412 | 6.7206 | 6.7206 | 0 | 12 | 1 | 1 | 6.7206 | 10 | 0 | 0
762.4 | 49.53 | 49.53 | 1 | 1 | 10 | 49.81 | 0.905 | 0.44412 | 4.4412 | 7.2206 | 7.2206 | 0 | 12 | 1 | 1 | 7.2206 | 10 | 0 | 0
762.45 | 49.5 | 49.5 | 1 | 1 | 10 | 49.78 | 1 | 0.54412 | 5.4412 | 7.7206 | 7.7206 | 0 | 12 | 1 | 1 | 7.7206 | 10 | 0 | 0
762.5 | 49.5 | 49.5 | 1 | 1 | 10 | 49.76 | 1 | 0.64412 | 6.4412 | 8.2206 | 8.2206 | 0 | 12 | 1 | 1 | 8.2206 | 10 | 0 | 0
762.55 | 49.53 | 49.5 | 1 | 1 | 10 | 49.73 | 1 | 0.74412 | 7.4412 | 8.7206 | 8.7206 | 0 | 12 | 1 | 1 | 8.7206 | 10 | 0 | 0
762.6 | 49.55 | 49.5 | 1 | 1 | 10 | 49.71 | 1 | 0.84412 | 8.4412 | 9.2206 | 9.2206 | 0 | 12 | 1 | 1 | 9.2206 | 10 | 0 | 0
762.65 | 49.58 | 49.5 | 1 | 1 | 10 | 49.68 | 1 | 0.94412 | 9.4412 | 9.7206 | 9.7206 | 0 | 12 | 1 | 1 | 9.7206 | 10 | 0 | 0
762.7 | 49.6 | 49.5 | 1 | 1 | 10 | 49.65 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
762.75 | 49.63 | 49.5 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
762.8 | 49.65 | 49.5 | 1 | 1 | 10 | 49.65 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
762.85 | 49.68 | 49.5 | 1 | 1 | 10 | 49.68 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
762.9 | 49.71 | 49.5 | 1 | 1 | 10 | 49.71 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
762.95 | 49.73 | 49.5 | 1 | 1 | 10 | 49.73 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
763 | 49.76 | 49.5 | 1 | 1 | 10 | 49.76 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
763.05 | 49.78 | 49.5 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
763.1 | 49.81 | 49.53 | 1 | 1 | 10 | 49.81 | 0.905 | 0.905 | 9.05 | 9.525 | 9.525 | 0 | 12 | 1 | 1 | 9.525 | 10 | 0 | 0
763.15 | 49.83 | 49.55 | 1 | 1 | 10 | 49.83 | 0.715 | 0.715 | 7.15 | 8.575 | 8.575 | 0 | 12 | 1 | 1 | 8.575 | 10 | 0 | 0
763.2 | 49.86 | 49.58 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
763.25 | 49.88 | 49.6 | 1 | 1 | 10 | 49.88 | 0.24 | 0.24 | 2.4 | 6.2 | 6.2 | 0 | 12 | 1 | 1 | 6.2 | 10 | 0 | 0
763.3 | 49.91 | 49.63 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
763.35 | 49.94 | 49.65 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
763.4 | 49.96 | 49.68 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
763.45 | 49.99 | 49.71 | 1 | 1 | 10 | 49.99 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
763.5 | 50.01 | 49.73 | 1 | 1 | 10 | 50.01 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
763.55 | 50.04 | 49.76 | 1 | 1 | 10 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 4.9265 | 4.9265 | 0 | 12 | 1 | 1 | 4.9265 | 10 | 0 | 0
763.6 | 50.06 | 49.78 | 1 | 1 | 10 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 4.8676 | 4.8676 | 0 | 12 | 1 | 1 | 4.8676 | 10 | 0 | 0
763.65 | 50.09 | 49.81 | 0.905 | 0.905 | 9.05 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 4.3044 | 4.3044 | 0 | 12 | 1 | 1 | 4.3044 | 10 | 0 | 0
763.7 | 50.12 | 49.83 | 0.715 | 0.805 | 8.05 | 50.12 | -0.24 | -0.24 | -2.4 | 2.825 | 2.825 | 0 | 12 | 1 | 1 | 2.825 | 10 | 0 | 0
763.75 | 50.14 | 49.86 | 0.43 | 0.705 | 7.05 | 50.14 | -0.43 | -0.43 | -4.3 | 1.375 | 1.375 | 0 | 12 | 1 | 1 | 1.375 | 10 | 0 | 0
763.8 | 50.17 | 49.88 | 0.24 | 0.605 | 6.05 | 50.17 | -0.715 | -0.715 | -7.15 | -0.55 | -0.55 | 0 | 12 | 1 | 1 | -0.55 | 10 | 0 | 0
763.85 | 50.19 | 49.91 | 0.044118 | 0.505 | 5.05 | 50.19 | -0.905 | -0.905 | -9.05 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
763.9 | 50.22 | 49.94 | 0.026471 | 0.405 | 4.05 | 50.22 | -1 | -1 | -10 | -2.975 | -2.975 | 0 | 12 | 1 | 1 | -2.975 | 10 | 0 | 0
763.95 | 50.24 | 49.96 | 0.014706 | 0.305 | 3.05 | 50.24 | -1 | -1 | -10 | -3.475 | -3.475 | 0 | 12 | 1 | 1 | -3.475 | 10 | 0 | 0
764 | 50.27 | 49.99 | 0 | 0.205 | 2.05 | 50.27 | -1 | -1 | -10 | -3.975 | -3.975 | 0 | 12 | 1 | 1 | -3.975 | 10 | 0 | 0
764.05 | 50.29 | 50.01 | 0 | 0.105 | 1.05 | 50.29 | -1 | -1 | -10 | -4.475 | -4.475 | 0 | 12 | 1 | 1 | -4.475 | 10 | 0 | 0
764.1 | 50.32 | 50.04 | -0.014706 | 0.005 | 0.05 | 50.32 | -1 | -1 | -10 | -4.975 | -4.975 | 0 | 12 | 1 | 1 | -4.975 | 10 | 0 | 0
764.15 | 50.35 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.35 | -1 | -1 | -10 | -5.1324 | -5.1324 | 0 | 12 | 1 | 1 | -5.1324 | 10 | 0 | 0
764.2 | 50.37 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 50.37 | -1 | -1 | -10 | -5.2206 | -5.2206 | 0 | 12 | 1 | 1 | -5.2206 | 10 | 0 | 0
764.25 | 50.4 | 50.12 | -0.24 | -0.14412 | -1.4412 | 50.4 | -1 | -1 | -10 | -5.7206 | -5.7206 | 0 | 12 | 1 | 1 | -5.7206 | 10 | 0 | 0
764.3 | 50.42 | 50.14 | -0.43 | -0.24412 | -2.4412 | 50.42 | -1 | -1 | -10 | -6.2206 | -6.2206 | 0 | 12 | 1 | 1 | -6.2206 | 10 | 0 | 0
764.35 | 50.45 | 50.17 | -0.715 | -0.34412 | -3.4412 | 50.45 | -1 | -1 | -10 | -6.7206 | -6.7206 | 0 | 12 | 1 | 1 | -6.7206 | 10 | 0 | 0
764.4 | 50.47 | 50.19 | -0.905 | -0.44412 | -4.4412 | 50.47 | -1 | -1 | -10 | -7.2206 | -7.2206 | 0 | 12 | 1 | 1 | -7.2206 | 10 | 0 | 0
764.45 | 50.5 | 50.22 | -1 | -0.54412 | -5.4412 | 50.5 | -1 | -1 | -10 | -7.7206 | -7.7206 | 0 | 12 | 1 | 1 | -7.7206 | 10 | 0 | 0
764.5 | 50.5 | 50.24 | -1 | -0.64412 | -6.4412 | 50.5 | -1 | -1 | -10 | -8.2206 | -8.2206 | 0 | 12 | 1 | 1 | -8.2206 | 10 | 0 | 0
764.55 | 50.47 | 50.27 | -1 | -0.74412 | -7.4412 | 50.5 | -1 | -1 | -10 | -8.7206 | -8.7206 | 0 | 12 | 1 | 1 | -8.7206 | 10 | 0 | 0
764.6 | 50.45 | 50.29 | -1 | -0.84412 | -8.4412 | 50.5 | -1 | -1 | -10 | -9.2206 | -9.2206 | 0 | 12 | 1 | 1 | -9.2206 | 10 | 0 | 0
764.65 | 50.42 | 50.32 | -1 | -0.94412 | -9.4412 | 50.5 | -1 | -1 | -10 | -9.7206 | -9.7206 | 0 | 12 | 1 | 1 | -9.7206 | 10 | 0 | 0
764.7 | 50.39 | 50.35 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
764.75 | 50.37 | 50.37 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
764.8 | 50.34 | 50.34 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
764.85 | 50.32 | 50.32 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
764.9 | 50.29 | 50.29 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
764.95 | 50.26 | 50.26 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
765 | 50.24 | 50.24 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
765.05 | 50.21 | 50.21 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
765.1 | 50.18 | 50.18 | -0.81 | -0.81 | -8.1 | 50.47 | -1 | -1 | -10 | -9.05 | -9.05 | 0 | 12 | 1 | 1 | -9.05 | 10 | 0 | 0
765.15 | 50.16 | 50.16 | -0.62 | -0.62 | -6.2 | 50.45 | -1 | -1 | -10 | -8.1 | -8.1 | 0 | 12 | 1 | 1 | -8.1 | 10 | 0 | 0
765.2 | 50.13 | 50.13 | -0.335 | -0.335 | -3.35 | 50.42 | -1 | -1 | -10 | -6.675 | -6.675 | 0 | 12 | 1 | 1 | -6.675 | 10 | 0 | 0
765.25 | 50.11 | 50.11 | -0.145 | -0.145 | -1.45 | 50.39 | -1 | -1 | -10 | -5.725 | -5.725 | 0 | 12 | 1 | 1 | -5.725 | 10 | 0 | 0
765.3 | 50.08 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 50.37 | -1 | -1 | -10 | -5.1912 | -5.1912 | 0 | 12 | 1 | 1 | -5.1912 | 10 | 0 | 0
765.35 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.34 | -1 | -1 | -10 | -5.1029 | -5.1029 | 0 | 12 | 1 | 1 | -5.1029 | 10 | 0 | 0
765.4 | 50.03 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 50.32 | -1 | -1 | -10 | -5.0441 | -5.0441 | 0 | 12 | 1 | 1 | -5.0441 | 10 | 0 | 0
765.45 | 50 | 50 | 0 | 0 | 0 | 50.29 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
765.5 | 50 | 50 | 0 | 0 | 0 | 50.26 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
765.55 | 50 | 50 | 0 | 0 | 0 | 50.24 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
765.6 | 50 | 50 | 0 | 0 | 0 | 50.21 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
765.65 | 50 | 50 | 0 | 0 | 0 | 50.18 | -0.81 | -0.9 | -9 | -4.5 | -4.5 | 0 | 12 | 1 | 1 | -4.5 | 10 | 0 | 0
765.7 | 50 | 50 | 0 | 0 | 0 | 50.16 | -0.62 | -0.8 | -8 | -4 | -4 | 0 | 12 | 1 | 1 | -4 | 10 | 0 | 0
765.75 | 50 | 50 | 0 | 0 | 0 | 50.13 | -0.335 | -0.7 | -7 | -3.5 | -3.5 | 0 | 12 | 1 | 1 | -3.5 | 10 | 0 | 0
765.8 | 50.01 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.6 | -6 | -3 | -3 | 0 | 12 | 1 | 1 | -3 | 10 | 0 | 0
765.85 | 50.01 | 50 | 0 | 0 | 0 | 50.08 | -0.038235 | -0.5 | -5 | -2.5 | -2.5 | 0 | 12 | 1 | 1 | -2.5 | 10 | 0 | 0
765.9 | 49.99 | 49.99 | 0 | 0 | 0 | 50.05 | -0.020588 | -0.4 | -4 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
765.95 | 49.99 | 49.99 | 0 | 0 | 0 | 50.03 | -0.0088235 | -0.3 | -3 | -1.5 | -1.5 | 0 | 12 | 1 | 1 | -1.5 | 10 | 0 | 0
766 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | -0.2 | -2 | -0.83824 | -0.83824 | 0 | 12 | 1 | 1 | -0.83824 | 10 | 0 | 0
766.05 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | -0.1 | -1 | -0.33824 | -0.33824 | 0 | 12 | 1 | 1 | -0.33824 | 10 | 0 | 0
766.1 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
766.15 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
766.2 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
766.25 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
766.3 | 49.89 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
766.35 | 49.89 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
766.4 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50.01 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
766.45 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
766.5 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
766.55 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 2.7868 | 2.7868 | 0 | 12 | 1 | 1 | 2.7868 | 10 | 0 | 0
766.6 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 2.7868 | 2.7868 | 0 | 12 | 1 | 1 | 2.7868 | 10 | 0 | 0
766.65 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 2.8456 | 2.8456 | 0 | 12 | 1 | 1 | 2.8456 | 10 | 0 | 0
766.7 | 49.94 | 49.85 | 0.525 | 0.525 | 5.25 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 2.7574 | 2.7574 | 0 | 12 | 1 | 1 | 2.7574 | 10 | 0 | 0
766.75 | 49.94 | 49.85 | 0.525 | 0.525 | 5.25 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 2.7574 | 2.7574 | 0 | 12 | 1 | 1 | 2.7574 | 10 | 0 | 0
766.8 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
766.85 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
766.9 | 49.93 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
766.95 | 49.93 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
767 | 49.96 | 49.85 | 0.525 | 0.525 | 5.25 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 2.6985 | 2.6985 | 0 | 12 | 1 | 1 | 2.6985 | 10 | 0 | 0
767.05 | 49.96 | 49.85 | 0.525 | 0.525 | 5.25 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 2.6985 | 2.6985 | 0 | 12 | 1 | 1 | 2.6985 | 10 | 0 | 0
767.1 | 49.99 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
767.15 | 49.99 | 49.91 | 0.044118 | 0.425 | 4.25 | 49.99 | 0 | 0 | 0 | 2.125 | 2.125 | 0 | 12 | 1 | 1 | 2.125 | 10 | 0 | 0
767.2 | 49.99 | 49.91 | 0.044118 | 0.325 | 3.25 | 49.99 | 0 | 0 | 0 | 1.625 | 1.625 | 0 | 12 | 1 | 1 | 1.625 | 10 | 0 | 0
767.25 | 49.99 | 49.93 | 0.032353 | 0.225 | 2.25 | 49.99 | 0 | 0 | 0 | 1.125 | 1.125 | 0 | 12 | 1 | 1 | 1.125 | 10 | 0 | 0
767.3 | 49.96 | 49.93 | 0.032353 | 0.125 | 1.25 | 49.99 | 0 | 0 | 0 | 0.625 | 0.625 | 0 | 12 | 1 | 1 | 0.625 | 10 | 0 | 0
767.35 | 49.96 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 49.99 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
767.4 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
767.45 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
767.5 | 50.05 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.058824 | 0.058824 | 0 | 12 | 1 | 1 | 0.058824 | 10 | 0 | 0
767.55 | 50.05 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
767.6 | 49.97 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
767.65 | 49.97 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
767.7 | 49.92 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
767.75 | 49.92 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
767.8 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
767.85 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
767.9 | 49.94 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
767.95 | 49.94 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
768 | 50.01 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
768.05 | 50.01 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
768.1 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
768.15 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
768.2 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
768.25 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
768.3 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
768.35 | 49.95 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
768.4 | 49.97 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
768.45 | 49.97 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
768.5 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
768.55 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
768.6 | 49.87 | 49.87 | 0.335 | 0.335 | 3.35 | 50.01 | 0 | 0 | 0 | 1.675 | 1.675 | 0 | 12 | 1 | 1 | 1.675 | 10 | 0 | 0
768.65 | 49.87 | 49.87 | 0.335 | 0.335 | 3.35 | 49.99 | 0 | 0 | 0 | 1.675 | 1.675 | 0 | 12 | 1 | 1 | 1.675 | 10 | 0 | 0
768.7 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
768.75 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 2.6691 | 2.6691 | 0 | 12 | 1 | 1 | 2.6691 | 10 | 0 | 0
768.8 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
768.85 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
768.9 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
768.95 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
769 | 49.84 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
769.05 | 49.84 | 49.79 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
769.1 | 49.89 | 49.79 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
769.15 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.12647 | 1.2647 | 5.6324 | 5.6324 | 0 | 12 | 1 | 1 | 5.6324 | 10 | 0 | 0
769.2 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.145 | 1.45 | 5.725 | 5.725 | 0 | 12 | 1 | 1 | 5.725 | 10 | 0 | 0
769.25 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.145 | 1.45 | 5.725 | 5.725 | 0 | 12 | 1 | 1 | 5.725 | 10 | 0 | 0
769.3 | 49.96 | 49.79 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
769.35 | 49.96 | 49.79 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
769.4 | 50.02 | 49.79 | 1 | 1 | 10 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 4.9853 | 4.9853 | 0 | 12 | 1 | 1 | 4.9853 | 10 | 0 | 0
769.45 | 50.02 | 49.79 | 1 | 1 | 10 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 4.9853 | 4.9853 | 0 | 12 | 1 | 1 | 4.9853 | 10 | 0 | 0
769.5 | 50.03 | 49.79 | 1 | 1 | 10 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.9559 | 4.9559 | 0 | 12 | 1 | 1 | 4.9559 | 10 | 0 | 0
769.55 | 50.03 | 49.84 | 0.62 | 0.9 | 9 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.4559 | 4.4559 | 0 | 12 | 1 | 1 | 4.4559 | 10 | 0 | 0
769.6 | 50.02 | 49.84 | 0.62 | 0.8 | 8 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 3.9559 | 3.9559 | 0 | 12 | 1 | 1 | 3.9559 | 10 | 0 | 0
769.65 | 50.02 | 49.89 | 0.145 | 0.7 | 7 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 3.4559 | 3.4559 | 0 | 12 | 1 | 1 | 3.4559 | 10 | 0 | 0
769.7 | 50.08 | 49.89 | 0.145 | 0.6 | 6 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 2.8088 | 2.8088 | 0 | 12 | 1 | 1 | 2.8088 | 10 | 0 | 0
769.75 | 50.08 | 49.89 | 0.145 | 0.5 | 5 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 2.3088 | 2.3088 | 0 | 12 | 1 | 1 | 2.3088 | 10 | 0 | 0
769.8 | 50.01 | 49.89 | 0.145 | 0.4 | 4 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 1.8088 | 1.8088 | 0 | 12 | 1 | 1 | 1.8088 | 10 | 0 | 0
769.85 | 50.01 | 49.96 | 0.014706 | 0.3 | 3 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 1.3088 | 1.3088 | 0 | 12 | 1 | 1 | 1.3088 | 10 | 0 | 0
769.9 | 49.94 | 49.94 | 0.026471 | 0.2 | 2 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.80882 | 0.80882 | 0 | 12 | 1 | 1 | 0.80882 | 10 | 0 | 0
769.95 | 49.94 | 49.94 | 0.026471 | 0.1 | 1 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.30882 | 0.30882 | 0 | 12 | 1 | 1 | 0.30882 | 10 | 0 | 0
770 | 50 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
770.05 | 50 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
770.1 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
770.15 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
770.2 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
770.25 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
770.3 | 49.92 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
770.35 | 49.92 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
770.4 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50.01 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
770.45 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
770.5 | 49.92 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
770.55 | 49.92 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
770.6 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
770.65 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
770.7 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
770.75 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
770.8 | 49.87 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
770.85 | 49.87 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
770.9 | 49.8 | 49.8 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
770.95 | 49.8 | 49.8 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
771 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
771.05 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
771.1 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
771.15 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
771.2 | 49.72 | 49.72 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
771.25 | 49.72 | 49.72 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
771.3 | 49.67 | 49.67 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
771.35 | 49.67 | 49.67 | 1 | 1 | 10 | 49.87 | 0.335 | 0.14412 | 1.4412 | 5.7206 | 5.7206 | 0 | 12 | 1 | 1 | 5.7206 | 10 | 0 | 0
771.4 | 49.65 | 49.65 | 1 | 1 | 10 | 49.87 | 0.335 | 0.24412 | 2.4412 | 6.2206 | 6.2206 | 0 | 12 | 1 | 1 | 6.2206 | 10 | 0 | 0
771.45 | 49.65 | 49.65 | 1 | 1 | 10 | 49.8 | 1 | 0.34412 | 3.4412 | 6.7206 | 6.7206 | 0 | 12 | 1 | 1 | 6.7206 | 10 | 0 | 0
771.5 | 49.59 | 49.59 | 1 | 1 | 10 | 49.8 | 1 | 0.44412 | 4.4412 | 7.2206 | 7.2206 | 0 | 12 | 1 | 1 | 7.2206 | 10 | 0 | 0
771.55 | 49.59 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.54412 | 5.4412 | 7.7206 | 7.7206 | 0 | 12 | 1 | 1 | 7.7206 | 10 | 0 | 0
771.6 | 49.66 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.64412 | 6.4412 | 8.2206 | 8.2206 | 0 | 12 | 1 | 1 | 8.2206 | 10 | 0 | 0
771.65 | 49.66 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.74412 | 7.4412 | 8.7206 | 8.7206 | 0 | 12 | 1 | 1 | 8.7206 | 10 | 0 | 0
771.7 | 49.63 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.84412 | 8.4412 | 9.2206 | 9.2206 | 0 | 12 | 1 | 1 | 9.2206 | 10 | 0 | 0
771.75 | 49.63 | 49.59 | 1 | 1 | 10 | 49.72 | 1 | 0.94412 | 9.4412 | 9.7206 | 9.7206 | 0 | 12 | 1 | 1 | 9.7206 | 10 | 0 | 0
771.8 | 49.61 | 49.59 | 1 | 1 | 10 | 49.72 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
771.85 | 49.61 | 49.59 | 1 | 1 | 10 | 49.67 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
771.9 | 49.54 | 49.54 | 1 | 1 | 10 | 49.67 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
771.95 | 49.54 | 49.54 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
772 | 49.46 | 49.46 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
772.05 | 49.46 | 49.46 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
772.1 | 49.45 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
772.15 | 49.45 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
772.2 | 49.51 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
772.25 | 49.51 | 49.45 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
772.3 | 49.5 | 49.45 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
772.35 | 49.5 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
772.4 | 49.54 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
772.45 | 49.54 | 49.45 | 1 | 1 | 10 | 49.54 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
772.5 | 49.59 | 49.45 | 1 | 1 | 10 | 49.59 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
772.55 | 49.59 | 49.45 | 1 | 1 | 10 | 49.59 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
772.6 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
772.65 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
772.7 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
772.75 | 49.61 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
772.8 | 49.53 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
772.85 | 49.53 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
772.9 | 49.54 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
772.95 | 49.54 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
773 | 49.61 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
773.05 | 49.61 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
773.1 | 49.66 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
773.15 | 49.66 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
773.2 | 49.64 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
773.25 | 49.64 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
773.3 | 49.69 | 49.53 | 1 | 1 | 10 | 49.69 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
773.35 | 49.69 | 49.53 | 1 | 1 | 10 | 49.69 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
773.4 | 49.74 | 49.53 | 1 | 1 | 10 | 49.74 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
773.45 | 49.74 | 49.54 | 1 | 1 | 10 | 49.74 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
773.5 | 49.78 | 49.54 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
773.55 | 49.78 | 49.61 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
773.6 | 49.82 | 49.61 | 1 | 1 | 10 | 49.82 | 0.81 | 0.81 | 8.1 | 9.05 | 9.05 | 0 | 12 | 1 | 1 | 9.05 | 10 | 0 | 0
773.65 | 49.82 | 49.64 | 1 | 1 | 10 | 49.82 | 0.81 | 0.81 | 8.1 | 9.05 | 9.05 | 0 | 12 | 1 | 1 | 9.05 | 10 | 0 | 0
773.7 | 49.86 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
773.75 | 49.86 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
773.8 | 49.84 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
773.85 | 49.84 | 49.69 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
773.9 | 49.91 | 49.69 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
773.95 | 49.91 | 49.74 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
774 | 49.97 | 49.74 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
774.05 | 49.97 | 49.78 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
774.1 | 50.03 | 49.78 | 1 | 1 | 10 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.9559 | 4.9559 | 0 | 12 | 1 | 1 | 4.9559 | 10 | 0 | 0
774.15 | 50.03 | 49.82 | 0.81 | 0.9 | 9 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.4559 | 4.4559 | 0 | 12 | 1 | 1 | 4.4559 | 10 | 0 | 0
774.2 | 50.05 | 49.82 | 0.81 | 0.81 | 8.1 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 3.9471 | 3.9471 | 0 | 12 | 1 | 1 | 3.9471 | 10 | 0 | 0
774.25 | 50.05 | 49.84 | 0.62 | 0.71 | 7.1 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 3.4471 | 3.4471 | 0 | 12 | 1 | 1 | 3.4471 | 10 | 0 | 0
774.3 | 50.01 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
774.35 | 50.01 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
774.4 | 49.95 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
774.45 | 49.95 | 49.91 | 0.044118 | 0.52 | 5.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.4971 | 2.4971 | 0 | 12 | 1 | 1 | 2.4971 | 10 | 0 | 0
774.5 | 49.99 | 49.91 | 0.044118 | 0.42 | 4.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 1.9971 | 1.9971 | 0 | 12 | 1 | 1 | 1.9971 | 10 | 0 | 0
774.55 | 49.99 | 49.95 | 0.020588 | 0.32 | 3.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 1.4971 | 1.4971 | 0 | 12 | 1 | 1 | 1.4971 | 10 | 0 | 0
774.6 | 49.92 | 49.92 | 0.038235 | 0.22 | 2.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.99706 | 0.99706 | 0 | 12 | 1 | 1 | 0.99706 | 10 | 0 | 0
774.65 | 49.92 | 49.92 | 0.038235 | 0.12 | 1.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.49706 | 0.49706 | 0 | 12 | 1 | 1 | 0.49706 | 10 | 0 | 0
774.7 | 49.97 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
774.75 | 49.97 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
774.8 | 50.02 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
774.85 | 50.02 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.17647 | 0.17647 | 0 | 12 | 1 | 1 | 0.17647 | 10 | 0 | 0
774.9 | 50.07 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
774.95 | 50.07 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
775 | 50.06 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
775.05 | 50.06 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
775.1 | 50.13 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
775.15 | 50.13 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
775.2 | 50.09 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
775.25 | 50.09 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6309 | -1.6309 | 0 | 12 | 1 | 1 | -1.6309 | 10 | 0 | 0
775.3 | 50.07 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6309 | -1.6309 | 0 | 12 | 1 | 1 | -1.6309 | 10 | 0 | 0
775.35 | 50.07 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6897 | -1.6897 | 0 | 12 | 1 | 1 | -1.6897 | 10 | 0 | 0
775.4 | 50.07 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6897 | -1.6897 | 0 | 12 | 1 | 1 | -1.6897 | 10 | 0 | 0
775.45 | 50.07 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.13 | -0.335 | -0.335 | -3.35 | -1.8074 | -1.8074 | 0 | 12 | 1 | 1 | -1.8074 | 10 | 0 | 0
775.5 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.13 | -0.335 | -0.335 | -3.35 | -1.7779 | -1.7779 | 0 | 12 | 1 | 1 | -1.7779 | 10 | 0 | 0
775.55 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.13 | -0.335 | -0.335 | -3.35 | -1.7779 | -1.7779 | 0 | 12 | 1 | 1 | -1.7779 | 10 | 0 | 0
775.6 | 50.01 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
775.65 | 50.01 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
775.7 | 50.07 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
775.75 | 50.07 | 50.01 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.235 | -2.35 | -1.175 | -1.175 | 0 | 12 | 1 | 1 | -1.175 | 10 | 0 | 0
775.8 | 50.05 | 50.01 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.135 | -1.35 | -0.675 | -0.675 | 0 | 12 | 1 | 1 | -0.675 | 10 | 0 | 0
775.85 | 50.05 | 50.01 | 0 | 0 | 0 | 50.07 | -0.032353 | -0.035 | -0.35 | -0.175 | -0.175 | 0 | 12 | 1 | 1 | -0.175 | 10 | 0 | 0
775.9 | 50.1 | 50.01 | 0 | 0 | 0 | 50.1 | -0.05 | -0.05 | -0.5 | -0.25 | -0.25 | 0 | 12 | 1 | 1 | -0.25 | 10 | 0 | 0
775.95 | 50.1 | 50.01 | 0 | 0 | 0 | 50.1 | -0.05 | -0.05 | -0.5 | -0.25 | -0.25 | 0 | 12 | 1 | 1 | -0.25 | 10 | 0 | 0
776 | 50.11 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
776.05 | 50.11 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
776.1 | 50.06 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
776.15 | 50.06 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
776.2 | 50.04 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
776.25 | 50.04 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
776.3 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
776.35 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
776.4 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
776.45 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
776.5 | 50.11 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
776.55 | 50.11 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
776.6 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
776.65 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
776.7 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
776.75 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
776.8 | 50.02 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.11 | -0.145 | -0.145 | -1.45 | -0.73971 | -0.73971 | 0 | 12 | 1 | 1 | -0.73971 | 10 | 0 | 0
776.85 | 50.02 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.11 | -0.145 | -0.145 | -1.45 | -0.73971 | -0.73971 | 0 | 12 | 1 | 1 | -0.73971 | 10 | 0 | 0
776.9 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
776.95 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
777 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
777.05 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
777.1 | 50.01 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
777.15 | 50.01 | 50 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.045 | -0.45 | -0.225 | -0.225 | 0 | 12 | 1 | 1 | -0.225 | 10 | 0 | 0
777.2 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
777.25 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
777.3 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
777.35 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
777.4 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.14706 | 0.14706 | 0 | 12 | 1 | 1 | 0.14706 | 10 | 0 | 0
777.45 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
777.5 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
777.55 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
777.6 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
777.65 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
777.7 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
777.75 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
777.8 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
777.85 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
777.9 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
777.95 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
778 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
778.05 | 50 | 50 | 0 | 0 | 0 | 50.01 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
778.1 | 49.5 | 49.5 | 1 | 1 | 10 | 50.01 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
778.15 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
778.2 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
778.25 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
778.3 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
778.35 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
778.4 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
778.45 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
778.5 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
778.55 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
778.6 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
778.65 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.1 | 1 | 5.5 | 5.5 | 0 | 12 | 1 | 1 | 5.5 | 10 | 0 | 0
778.7 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.2 | 2 | 6 | 6 | 0 | 12 | 1 | 1 | 6 | 10 | 0 | 0
778.75 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.3 | 3 | 6.5 | 6.5 | 0 | 12 | 1 | 1 | 6.5 | 10 | 0 | 0
778.8 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.4 | 4 | 7 | 7 | 0 | 12 | 1 | 1 | 7 | 10 | 0 | 0
778.85 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.5 | 5 | 7.5 | 7.5 | 0 | 12 | 1 | 1 | 7.5 | 10 | 0 | 0
778.9 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.6 | 6 | 8 | 8 | 0 | 12 | 1 | 1 | 8 | 10 | 0 | 0
778.95 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.7 | 7 | 8.5 | 8.5 | 0 | 12 | 1 | 1 | 8.5 | 10 | 0 | 0
779 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.8 | 8 | 9 | 9 | 0 | 12 | 1 | 1 | 9 | 10 | 0 | 0
779.05 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.9 | 9 | 9.5 | 9.5 | 0 | 12 | 1 | 1 | 9.5 | 10 | 0 | 0
779.1 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
779.15 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
779.2 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
779.25 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
779.3 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
779.35 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
779.4 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
779.45 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
779.5 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
779.55 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
779.6 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
779.65 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
779.7 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
779.75 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
779.8 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
779.85 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
779.9 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
779.95 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
780 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
780.05 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
780.1 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
780.15 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
780.2 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
780.25 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
780.3 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
780.35 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
780.4 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
780.45 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
780.5 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
780.55 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
780.6 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
780.65 | 50.5 | 50.5 | -1 | 0.9 | 9 | 50.5 | -1 | -1 | -10 | -0.5 | -0.5 | 0 | 12 | 1 | 1 | -0.5 | 10 | 0 | 0
780.7 | 50.5 | 50.5 | -1 | 0.8 | 8 | 50.5 | -1 | -1 | -10 | -1 | -1 | 0 | 12 | 1 | 1 | -1 | 10 | 0 | 0
780.75 | 50.5 | 50.5 | -1 | 0.7 | 7 | 50.5 | -1 | -1 | -10 | -1.5 | -1.5 | 0 | 12 | 1 | 1 | -1.5 | 10 | 0 | 0
780.8 | 50.5 | 50.5 | -1 | 0.6 | 6 | 50.5 | -1 | -1 | -10 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
780.85 | 50.5 | 50.5 | -1 | 0.5 | 5 | 50.5 | -1 | -1 | -10 | -2.5 | -2.5 | 0 | 12 | 1 | 1 | -2.5 | 10 | 0 | 0
780.9 | 50.5 | 50.5 | -1 | 0.4 | 4 | 50.5 | -1 | -1 | -10 | -3 | -3 | 0 | 12 | 1 | 1 | -3 | 10 | 0 | 0
780.95 | 50.5 | 50.5 | -1 | 0.3 | 3 | 50.5 | -1 | -1 | -10 | -3.5 | -3.5 | 0 | 12 | 1 | 1 | -3.5 | 10 | 0 | 0
781 | 50.5 | 50.5 | -1 | 0.2 | 2 | 50.5 | -1 | -1 | -10 | -4 | -4 | 0 | 12 | 1 | 1 | -4 | 10 | 0 | 0
781.05 | 50.5 | 50.5 | -1 | 0.1 | 1 | 50.5 | -1 | -1 | -10 | -4.5 | -4.5 | 0 | 12 | 1 | 1 | -4.5 | 10 | 0 | 0
781.1 | 50.5 | 50.5 | -1 | 0 | 0 | 50.5 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
781.15 | 50.5 | 50.5 | -1 | -0.1 | -1 | 50.5 | -1 | -1 | -10 | -5.5 | -5.5 | 0 | 12 | 1 | 1 | -5.5 | 10 | 0 | 0
781.2 | 50.5 | 50.5 | -1 | -0.2 | -2 | 50.5 | -1 | -1 | -10 | -6 | -6 | 0 | 12 | 1 | 1 | -6 | 10 | 0 | 0
781.25 | 50.5 | 50.5 | -1 | -0.3 | -3 | 50.5 | -1 | -1 | -10 | -6.5 | -6.5 | 0 | 12 | 1 | 1 | -6.5 | 10 | 0 | 0
781.3 | 50.5 | 50.5 | -1 | -0.4 | -4 | 50.5 | -1 | -1 | -10 | -7 | -7 | 0 | 12 | 1 | 1 | -7 | 10 | 0 | 0
781.35 | 50.5 | 50.5 | -1 | -0.5 | -5 | 50.5 | -1 | -1 | -10 | -7.5 | -7.5 | 0 | 12 | 1 | 1 | -7.5 | 10 | 0 | 0
781.4 | 50.5 | 50.5 | -1 | -0.6 | -6 | 50.5 | -1 | -1 | -10 | -8 | -8 | 0 | 12 | 1 | 1 | -8 | 10 | 0 | 0
781.45 | 50.5 | 50.5 | -1 | -0.7 | -7 | 50.5 | -1 | -1 | -10 | -8.5 | -8.5 | 0 | 12 | 1 | 1 | -8.5 | 10 | 0 | 0
781.5 | 50.5 | 50.5 | -1 | -0.8 | -8 | 50.5 | -1 | -1 | -10 | -9 | -9 | 0 | 12 | 1 | 1 | -9 | 10 | 0 | 0
781.55 | 50.5 | 50.5 | -1 | -0.9 | -9 | 50.5 | -1 | -1 | -10 | -9.5 | -9.5 | 0 | 12 | 1 | 1 | -9.5 | 10 | 0 | 0
781.6 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
781.65 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
781.7 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
781.75 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
781.8 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
781.85 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
781.9 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
781.95 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
782 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
782.05 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
782.1 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
782.15 | 50.47 | 50.47 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
782.2 | 50.45 | 50.45 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
782.25 | 50.42 | 50.42 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
782.3 | 50.4 | 50.4 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
782.35 | 50.37 | 50.37 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
782.4 | 50.35 | 50.35 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
782.45 | 50.32 | 50.32 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
782.5 | 50.29 | 50.29 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
782.55 | 50.27 | 50.27 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
782.6 | 50.24 | 50.24 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
782.65 | 50.22 | 50.22 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
782.7 | 50.19 | 50.19 | -0.905 | -0.905 | -9.05 | 50.47 | -1 | -1 | -10 | -9.525 | -9.525 | 0 | 12 | 1 | 1 | -9.525 | 10 | 0 | 0
782.75 | 50.17 | 50.17 | -0.715 | -0.715 | -7.15 | 50.45 | -1 | -1 | -10 | -8.575 | -8.575 | 0 | 12 | 1 | 1 | -8.575 | 10 | 0 | 0
782.8 | 50.14 | 50.14 | -0.43 | -0.43 | -4.3 | 50.42 | -1 | -1 | -10 | -7.15 | -7.15 | 0 | 12 | 1 | 1 | -7.15 | 10 | 0 | 0
782.85 | 50.12 | 50.12 | -0.24 | -0.24 | -2.4 | 50.4 | -1 | -1 | -10 | -6.2 | -6.2 | 0 | 12 | 1 | 1 | -6.2 | 10 | 0 | 0
782.9 | 50.09 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 50.37 | -1 | -1 | -10 | -5.2206 | -5.2206 | 0 | 12 | 1 | 1 | -5.2206 | 10 | 0 | 0
782.95 | 50.06 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.35 | -1 | -1 | -10 | -5.1324 | -5.1324 | 0 | 12 | 1 | 1 | -5.1324 | 10 | 0 | 0
783 | 50.04 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.32 | -1 | -1 | -10 | -5.0735 | -5.0735 | 0 | 12 | 1 | 1 | -5.0735 | 10 | 0 | 0
783.05 | 50.01 | 50.01 | 0 | 0 | 0 | 50.29 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
783.1 | 49.99 | 49.99 | 0 | 0 | 0 | 50.27 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
783.15 | 49.96 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.24 | -1 | -1 | -10 | -4.9265 | -4.9265 | 0 | 12 | 1 | 1 | -4.9265 | 10 | 0 | 0
783.2 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.22 | -1 | -1 | -10 | -4.8676 | -4.8676 | 0 | 12 | 1 | 1 | -4.8676 | 10 | 0 | 0
783.25 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.19 | -0.905 | -0.905 | -9.05 | -4.3044 | -4.3044 | 0 | 12 | 1 | 1 | -4.3044 | 10 | 0 | 0
783.3 | 49.88 | 49.88 | 0.24 | 0.24 | 2.4 | 50.17 | -0.715 | -0.805 | -8.05 | -2.825 | -2.825 | 0 | 12 | 1 | 1 | -2.825 | 10 | 0 | 0
783.35 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.14 | -0.43 | -0.705 | -7.05 | -1.375 | -1.375 | 0 | 12 | 1 | 1 | -1.375 | 10 | 0 | 0
783.4 | 49.83 | 49.83 | 0.715 | 0.715 | 7.15 | 50.12 | -0.24 | -0.605 | -6.05 | 0.55 | 0.55 | 0 | 12 | 1 | 1 | 0.55 | 10 | 0 | 0
783.45 | 49.81 | 49.81 | 0.905 | 0.905 | 9.05 | 50.09 | -0.044118 | -0.505 | -5.05 | 2 | 2 | 0 | 12 | 1 | 1 | 2 | 10 | 0 | 0
783.5 | 49.78 | 49.78 | 1 | 1 | 10 | 50.06 | -0.026471 | -0.405 | -4.05 | 2.975 | 2.975 | 0 | 12 | 1 | 1 | 2.975 | 10 | 0 | 0
783.55 | 49.76 | 49.76 | 1 | 1 | 10 | 50.04 | -0.014706 | -0.305 | -3.05 | 3.475 | 3.475 | 0 | 12 | 1 | 1 | 3.475 | 10 | 0 | 0
783.6 | 49.73 | 49.73 | 1 | 1 | 10 | 50.01 | 0 | -0.205 | -2.05 | 3.975 | 3.975 | 0 | 12 | 1 | 1 | 3.975 | 10 | 0 | 0
783.65 | 49.71 | 49.71 | 1 | 1 | 10 | 49.99 | 0 | -0.105 | -1.05 | 4.475 | 4.475 | 0 | 12 | 1 | 1 | 4.475 | 10 | 0 | 0
783.7 | 49.68 | 49.68 | 1 | 1 | 10 | 49.96 | 0.014706 | -0.005 | -0.05 | 4.975 | 4.975 | 0 | 12 | 1 | 1 | 4.975 | 10 | 0 | 0
783.75 | 49.65 | 49.65 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
783.8 | 49.63 | 49.63 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
783.85 | 49.6 | 49.6 | 1 | 1 | 10 | 49.88 | 0.24 | 0.14412 | 1.4412 | 5.7206 | 5.7206 | 0 | 12 | 1 | 1 | 5.7206 | 10 | 0 | 0
783.9 | 49.58 | 49.58 | 1 | 1 | 10 | 49.86 | 0.43 | 0.24412 | 2.4412 | 6.2206 | 6.2206 | 0 | 12 | 1 | 1 | 6.2206 | 10 | 0 | 0
783.95 | 49.55 | 49.55 | 1 | 1 | 10 | 49.83 | 0.715 | 0.34412 | 3.4412 | 6.7206 | 6.7206 | 0 | 12 | 1 | 1 | 6.7206 | 10 | 0 | 0
784 | 49.53 | 49.53 | 1 | 1 | 10 | 49.81 | 0.905 | 0.44412 | 4.4412 | 7.2206 | 7.2206 | 0 | 12 | 1 | 1 | 7.2206 | 10 | 0 | 0
784.05 | 49.5 | 49.5 | 1 | 1 | 10 | 49.78 | 1 | 0.54412 | 5.4412 | 7.7206 | 7.7206 | 0 | 12 | 1 | 1 | 7.7206 | 10 | 0 | 0
784.1 | 49.5 | 49.5 | 1 | 1 | 10 | 49.76 | 1 | 0.64412 | 6.4412 | 8.2206 | 8.2206 | 0 | 12 | 1 | 1 | 8.2206 | 10 | 0 | 0
784.15 | 49.53 | 49.5 | 1 | 1 | 10 | 49.73 | 1 | 0.74412 | 7.4412 | 8.7206 | 8.7206 | 0 | 12 | 1 | 1 | 8.7206 | 10 | 0 | 0
784.2 | 49.55 | 49.5 | 1 | 1 | 10 | 49.71 | 1 | 0.84412 | 8.4412 | 9.2206 | 9.2206 | 0 | 12 | 1 | 1 | 9.2206 | 10 | 0 | 0
784.25 | 49.58 | 49.5 | 1 | 1 | 10 | 49.68 | 1 | 0.94412 | 9.4412 | 9.7206 | 9.7206 | 0 | 12 | 1 | 1 | 9.7206 | 10 | 0 | 0
784.3 | 49.6 | 49.5 | 1 | 1 | 10 | 49.65 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
784.35 | 49.63 | 49.5 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
784.4 | 49.65 | 49.5 | 1 | 1 | 10 | 49.65 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
784.45 | 49.68 | 49.5 | 1 | 1 | 10 | 49.68 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
784.5 | 49.71 | 49.5 | 1 | 1 | 10 | 49.71 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
784.55 | 49.73 | 49.5 | 1 | 1 | 10 | 49.73 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
784.6 | 49.76 | 49.5 | 1 | 1 | 10 | 49.76 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
784.65 | 49.78 | 49.5 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
784.7 | 49.81 | 49.53 | 1 | 1 | 10 | 49.81 | 0.905 | 0.905 | 9.05 | 9.525 | 9.525 | 0 | 12 | 1 | 1 | 9.525 | 10 | 0 | 0
784.75 | 49.83 | 49.55 | 1 | 1 | 10 | 49.83 | 0.715 | 0.715 | 7.15 | 8.575 | 8.575 | 0 | 12 | 1 | 1 | 8.575 | 10 | 0 | 0
784.8 | 49.86 | 49.58 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
784.85 | 49.88 | 49.6 | 1 | 1 | 10 | 49.88 | 0.24 | 0.24 | 2.4 | 6.2 | 6.2 | 0 | 12 | 1 | 1 | 6.2 | 10 | 0 | 0
784.9 | 49.91 | 49.63 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
784.95 | 49.94 | 49.65 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
785 | 49.96 | 49.68 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
785.05 | 49.99 | 49.71 | 1 | 1 | 10 | 49.99 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
785.1 | 50.01 | 49.73 | 1 | 1 | 10 | 50.01 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
785.15 | 50.04 | 49.76 | 1 | 1 | 10 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 4.9265 | 4.9265 | 0 | 12 | 1 | 1 | 4.9265 | 10 | 0 | 0
785.2 | 50.06 | 49.78 | 1 | 1 | 10 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 4.8676 | 4.8676 | 0 | 12 | 1 | 1 | 4.8676 | 10 | 0 | 0
785.25 | 50.09 | 49.81 | 0.905 | 0.905 | 9.05 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 4.3044 | 4.3044 | 0 | 12 | 1 | 1 | 4.3044 | 10 | 0 | 0
785.3 | 50.12 | 49.83 | 0.715 | 0.805 | 8.05 | 50.12 | -0.24 | -0.24 | -2.4 | 2.825 | 2.825 | 0 | 12 | 1 | 1 | 2.825 | 10 | 0 | 0
785.35 | 50.14 | 49.86 | 0.43 | 0.705 | 7.05 | 50.14 | -0.43 | -0.43 | -4.3 | 1.375 | 1.375 | 0 | 12 | 1 | 1 | 1.375 | 10 | 0 | 0
785.4 | 50.17 | 49.88 | 0.24 | 0.605 | 6.05 | 50.17 | -0.715 | -0.715 | -7.15 | -0.55 | -0.55 | 0 | 12 | 1 | 1 | -0.55 | 10 | 0 | 0
785.45 | 50.19 | 49.91 | 0.044118 | 0.505 | 5.05 | 50.19 | -0.905 | -0.905 | -9.05 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
785.5 | 50.22 | 49.94 | 0.026471 | 0.405 | 4.05 | 50.22 | -1 | -1 | -10 | -2.975 | -2.975 | 0 | 12 | 1 | 1 | -2.975 | 10 | 0 | 0
785.55 | 50.24 | 49.96 | 0.014706 | 0.305 | 3.05 | 50.24 | -1 | -1 | -10 | -3.475 | -3.475 | 0 | 12 | 1 | 1 | -3.475 | 10 | 0 | 0
785.6 | 50.27 | 49.99 | 0 | 0.205 | 2.05 | 50.27 | -1 | -1 | -10 | -3.975 | -3.975 | 0 | 12 | 1 | 1 | -3.975 | 10 | 0 | 0
785.65 | 50.29 | 50.01 | 0 | 0.105 | 1.05 | 50.29 | -1 | -1 | -10 | -4.475 | -4.475 | 0 | 12 | 1 | 1 | -4.475 | 10 | 0 | 0
785.7 | 50.32 | 50.04 | -0.014706 | 0.005 | 0.05 | 50.32 | -1 | -1 | -10 | -4.975 | -4.975 | 0 | 12 | 1 | 1 | -4.975 | 10 | 0 | 0
785.75 | 50.35 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.35 | -1 | -1 | -10 | -5.1324 | -5.1324 | 0 | 12 | 1 | 1 | -5.1324 | 10 | 0 | 0
785.8 | 50.37 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 50.37 | -1 | -1 | -10 | -5.2206 | -5.2206 | 0 | 12 | 1 | 1 | -5.2206 | 10 | 0 | 0
785.85 | 50.4 | 50.12 | -0.24 | -0.14412 | -1.4412 | 50.4 | -1 | -1 | -10 | -5.7206 | -5.7206 | 0 | 12 | 1 | 1 | -5.7206 | 10 | 0 | 0
785.9 | 50.42 | 50.14 | -0.43 | -0.24412 | -2.4412 | 50.42 | -1 | -1 | -10 | -6.2206 | -6.2206 | 0 | 12 | 1 | 1 | -6.2206 | 10 | 0 | 0
785.95 | 50.45 | 50.17 | -0.715 | -0.34412 | -3.4412 | 50.45 | -1 | -1 | -10 | -6.7206 | -6.7206 | 0 | 12 | 1 | 1 | -6.7206 | 10 | 0 | 0
786 | 50.47 | 50.19 | -0.905 | -0.44412 | -4.4412 | 50.47 | -1 | -1 | -10 | -7.2206 | -7.2206 | 0 | 12 | 1 | 1 | -7.2206 | 10 | 0 | 0
786.05 | 50.5 | 50.22 | -1 | -0.54412 | -5.4412 | 50.5 | -1 | -1 | -10 | -7.7206 | -7.7206 | 0 | 12 | 1 | 1 | -7.7206 | 10 | 0 | 0
786.1 | 50.5 | 50.24 | -1 | -0.64412 | -6.4412 | 50.5 | -1 | -1 | -10 | -8.2206 | -8.2206 | 0 | 12 | 1 | 1 | -8.2206 | 10 | 0 | 0
786.15 | 50.47 | 50.27 | -1 | -0.74412 | -7.4412 | 50.5 | -1 | -1 | -10 | -8.7206 | -8.7206 | 0 | 12 | 1 | 1 | -8.7206 | 10 | 0 | 0
786.2 | 50.45 | 50.29 | -1 | -0.84412 | -8.4412 | 50.5 | -1 | -1 | -10 | -9.2206 | -9.2206 | 0 | 12 | 1 | 1 | -9.2206 | 10 | 0 | 0
786.25 | 50.42 | 50.32 | -1 | -0.94412 | -9.4412 | 50.5 | -1 | -1 | -10 | -9.7206 | -9.7206 | 0 | 12 | 1 | 1 | -9.7206 | 10 | 0 | 0
786.3 | 50.39 | 50.35 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
786.35 | 50.37 | 50.37 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
786.4 | 50.34 | 50.34 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
786.45 | 50.32 | 50.32 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
786.5 | 50.29 | 50.29 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
786.55 | 50.26 | 50.26 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
786.6 | 50.24 | 50.24 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
786.65 | 50.21 | 50.21 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
786.7 | 50.18 | 50.18 | -0.81 | -0.81 | -8.1 | 50.47 | -1 | -1 | -10 | -9.05 | -9.05 | 0 | 12 | 1 | 1 | -9.05 | 10 | 0 | 0
786.75 | 50.16 | 50.16 | -0.62 | -0.62 | -6.2 | 50.45 | -1 | -1 | -10 | -8.1 | -8.1 | 0 | 12 | 1 | 1 | -8.1 | 10 | 0 | 0
786.8 | 50.13 | 50.13 | -0.335 | -0.335 | -3.35 | 50.42 | -1 | -1 | -10 | -6.675 | -6.675 | 0 | 12 | 1 | 1 | -6.675 | 10 | 0 | 0
786.85 | 50.11 | 50.11 | -0.145 | -0.145 | -1.45 | 50.39 | -1 | -1 | -10 | -5.725 | -5.725 | 0 | 12 | 1 | 1 | -5.725 | 10 | 0 | 0
786.9 | 50.08 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 50.37 | -1 | -1 | -10 | -5.1912 | -5.1912 | 0 | 12 | 1 | 1 | -5.1912 | 10 | 0 | 0
786.95 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.34 | -1 | -1 | -10 | -5.1029 | -5.1029 | 0 | 12 | 1 | 1 | -5.1029 | 10 | 0 | 0
787 | 50.03 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 50.32 | -1 | -1 | -10 | -5.0441 | -5.0441 | 0 | 12 | 1 | 1 | -5.0441 | 10 | 0 | 0
787.05 | 50 | 50 | 0 | 0 | 0 | 50.29 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
787.1 | 50 | 50 | 0 | 0 | 0 | 50.26 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
787.15 | 50 | 50 | 0 | 0 | 0 | 50.24 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
787.2 | 50 | 50 | 0 | 0 | 0 | 50.21 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
787.25 | 50 | 50 | 0 | 0 | 0 | 50.18 | -0.81 | -0.9 | -9 | -4.5 | -4.5 | 0 | 12 | 1 | 1 | -4.5 | 10 | 0 | 0
787.3 | 50 | 50 | 0 | 0 | 0 | 50.16 | -0.62 | -0.8 | -8 | -4 | -4 | 0 | 12 | 1 | 1 | -4 | 10 | 0 | 0
787.35 | 50 | 50 | 0 | 0 | 0 | 50.13 | -0.335 | -0.7 | -7 | -3.5 | -3.5 | 0 | 12 | 1 | 1 | -3.5 | 10 | 0 | 0
787.4 | 50.01 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.6 | -6 | -3 | -3 | 0 | 12 | 1 | 1 | -3 | 10 | 0 | 0
787.45 | 50.01 | 50 | 0 | 0 | 0 | 50.08 | -0.038235 | -0.5 | -5 | -2.5 | -2.5 | 0 | 12 | 1 | 1 | -2.5 | 10 | 0 | 0
787.5 | 49.99 | 49.99 | 0 | 0 | 0 | 50.05 | -0.020588 | -0.4 | -4 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
787.55 | 49.99 | 49.99 | 0 | 0 | 0 | 50.03 | -0.0088235 | -0.3 | -3 | -1.5 | -1.5 | 0 | 12 | 1 | 1 | -1.5 | 10 | 0 | 0
787.6 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | -0.2 | -2 | -0.83824 | -0.83824 | 0 | 12 | 1 | 1 | -0.83824 | 10 | 0 | 0
787.65 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | -0.1 | -1 | -0.33824 | -0.33824 | 0 | 12 | 1 | 1 | -0.33824 | 10 | 0 | 0
787.7 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
787.75 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
787.8 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
787.85 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
787.9 | 49.89 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
787.95 | 49.89 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
788 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50.01 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
788.05 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
788.1 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
788.15 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 2.7868 | 2.7868 | 0 | 12 | 1 | 1 | 2.7868 | 10 | 0 | 0
788.2 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 2.7868 | 2.7868 | 0 | 12 | 1 | 1 | 2.7868 | 10 | 0 | 0
788.25 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 2.8456 | 2.8456 | 0 | 12 | 1 | 1 | 2.8456 | 10 | 0 | 0
788.3 | 49.94 | 49.85 | 0.525 | 0.525 | 5.25 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 2.7574 | 2.7574 | 0 | 12 | 1 | 1 | 2.7574 | 10 | 0 | 0
788.35 | 49.94 | 49.85 | 0.525 | 0.525 | 5.25 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 2.7574 | 2.7574 | 0 | 12 | 1 | 1 | 2.7574 | 10 | 0 | 0
788.4 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
788.45 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
788.5 | 49.93 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
788.55 | 49.93 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
788.6 | 49.96 | 49.85 | 0.525 | 0.525 | 5.25 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 2.6985 | 2.6985 | 0 | 12 | 1 | 1 | 2.6985 | 10 | 0 | 0
788.65 | 49.96 | 49.85 | 0.525 | 0.525 | 5.25 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 2.6985 | 2.6985 | 0 | 12 | 1 | 1 | 2.6985 | 10 | 0 | 0
788.7 | 49.99 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
788.75 | 49.99 | 49.91 | 0.044118 | 0.425 | 4.25 | 49.99 | 0 | 0 | 0 | 2.125 | 2.125 | 0 | 12 | 1 | 1 | 2.125 | 10 | 0 | 0
788.8 | 49.99 | 49.91 | 0.044118 | 0.325 | 3.25 | 49.99 | 0 | 0 | 0 | 1.625 | 1.625 | 0 | 12 | 1 | 1 | 1.625 | 10 | 0 | 0
788.85 | 49.99 | 49.93 | 0.032353 | 0.225 | 2.25 | 49.99 | 0 | 0 | 0 | 1.125 | 1.125 | 0 | 12 | 1 | 1 | 1.125 | 10 | 0 | 0
788.9 | 49.96 | 49.93 | 0.032353 | 0.125 | 1.25 | 49.99 | 0 | 0 | 0 | 0.625 | 0.625 | 0 | 12 | 1 | 1 | 0.625 | 10 | 0 | 0
788.95 | 49.96 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 49.99 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
789 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
789.05 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
789.1 | 50.05 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.058824 | 0.058824 | 0 | 12 | 1 | 1 | 0.058824 | 10 | 0 | 0
789.15 | 50.05 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
789.2 | 49.97 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
789.25 | 49.97 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
789.3 | 49.92 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
789.35 | 49.92 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
789.4 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
789.45 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
789.5 | 49.94 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
789.55 | 49.94 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
789.6 | 50.01 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
789.65 | 50.01 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
789.7 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
789.75 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
789.8 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
789.85 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
789.9 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
789.95 | 49.95 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
790 | 49.97 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
790.05 | 49.97 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
790.1 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
790.15 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
790.2 | 49.87 | 49.87 | 0.335 | 0.335 | 3.35 | 50.01 | 0 | 0 | 0 | 1.675 | 1.675 | 0 | 12 | 1 | 1 | 1.675 | 10 | 0 | 0
790.25 | 49.87 | 49.87 | 0.335 | 0.335 | 3.35 | 49.99 | 0 | 0 | 0 | 1.675 | 1.675 | 0 | 12 | 1 | 1 | 1.675 | 10 | 0 | 0
790.3 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
790.35 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 2.6691 | 2.6691 | 0 | 12 | 1 | 1 | 2.6691 | 10 | 0 | 0
790.4 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
790.45 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
790.5 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
790.55 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
790.6 | 49.84 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
790.65 | 49.84 | 49.79 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
790.7 | 49.89 | 49.79 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
790.75 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.12647 | 1.2647 | 5.6324 | 5.6324 | 0 | 12 | 1 | 1 | 5.6324 | 10 | 0 | 0
790.8 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.145 | 1.45 | 5.725 | 5.725 | 0 | 12 | 1 | 1 | 5.725 | 10 | 0 | 0
790.85 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.145 | 1.45 | 5.725 | 5.725 | 0 | 12 | 1 | 1 | 5.725 | 10 | 0 | 0
790.9 | 49.96 | 49.79 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
790.95 | 49.96 | 49.79 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
791 | 50.02 | 49.79 | 1 | 1 | 10 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 4.9853 | 4.9853 | 0 | 12 | 1 | 1 | 4.9853 | 10 | 0 | 0
791.05 | 50.02 | 49.79 | 1 | 1 | 10 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 4.9853 | 4.9853 | 0 | 12 | 1 | 1 | 4.9853 | 10 | 0 | 0
791.1 | 50.03 | 49.79 | 1 | 1 | 10 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.9559 | 4.9559 | 0 | 12 | 1 | 1 | 4.9559 | 10 | 0 | 0
791.15 | 50.03 | 49.84 | 0.62 | 0.9 | 9 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.4559 | 4.4559 | 0 | 12 | 1 | 1 | 4.4559 | 10 | 0 | 0
791.2 | 50.02 | 49.84 | 0.62 | 0.8 | 8 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 3.9559 | 3.9559 | 0 | 12 | 1 | 1 | 3.9559 | 10 | 0 | 0
791.25 | 50.02 | 49.89 | 0.145 | 0.7 | 7 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 3.4559 | 3.4559 | 0 | 12 | 1 | 1 | 3.4559 | 10 | 0 | 0
791.3 | 50.08 | 49.89 | 0.145 | 0.6 | 6 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 2.8088 | 2.8088 | 0 | 12 | 1 | 1 | 2.8088 | 10 | 0 | 0
791.35 | 50.08 | 49.89 | 0.145 | 0.5 | 5 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 2.3088 | 2.3088 | 0 | 12 | 1 | 1 | 2.3088 | 10 | 0 | 0
791.4 | 50.01 | 49.89 | 0.145 | 0.4 | 4 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 1.8088 | 1.8088 | 0 | 12 | 1 | 1 | 1.8088 | 10 | 0 | 0
791.45 | 50.01 | 49.96 | 0.014706 | 0.3 | 3 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 1.3088 | 1.3088 | 0 | 12 | 1 | 1 | 1.3088 | 10 | 0 | 0
791.5 | 49.94 | 49.94 | 0.026471 | 0.2 | 2 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.80882 | 0.80882 | 0 | 12 | 1 | 1 | 0.80882 | 10 | 0 | 0
791.55 | 49.94 | 49.94 | 0.026471 | 0.1 | 1 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.30882 | 0.30882 | 0 | 12 | 1 | 1 | 0.30882 | 10 | 0 | 0
791.6 | 50 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
791.65 | 50 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
791.7 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
791.75 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
791.8 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
791.85 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
791.9 | 49.92 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
791.95 | 49.92 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
792 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50.01 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
792.05 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
792.1 | 49.92 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
792.15 | 49.92 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
792.2 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
792.25 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
792.3 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
792.35 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
792.4 | 49.87 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
792.45 | 49.87 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
792.5 | 49.8 | 49.8 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
792.55 | 49.8 | 49.8 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
792.6 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
792.65 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
792.7 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
792.75 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
792.8 | 49.72 | 49.72 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
792.85 | 49.72 | 49.72 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
792.9 | 49.67 | 49.67 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
792.95 | 49.67 | 49.67 | 1 | 1 | 10 | 49.87 | 0.335 | 0.14412 | 1.4412 | 5.7206 | 5.7206 | 0 | 12 | 1 | 1 | 5.7206 | 10 | 0 | 0
793 | 49.65 | 49.65 | 1 | 1 | 10 | 49.87 | 0.335 | 0.24412 | 2.4412 | 6.2206 | 6.2206 | 0 | 12 | 1 | 1 | 6.2206 | 10 | 0 | 0
793.05 | 49.65 | 49.65 | 1 | 1 | 10 | 49.8 | 1 | 0.34412 | 3.4412 | 6.7206 | 6.7206 | 0 | 12 | 1 | 1 | 6.7206 | 10 | 0 | 0
793.1 | 49.59 | 49.59 | 1 | 1 | 10 | 49.8 | 1 | 0.44412 | 4.4412 | 7.2206 | 7.2206 | 0 | 12 | 1 | 1 | 7.2206 | 10 | 0 | 0
793.15 | 49.59 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.54412 | 5.4412 | 7.7206 | 7.7206 | 0 | 12 | 1 | 1 | 7.7206 | 10 | 0 | 0
793.2 | 49.66 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.64412 | 6.4412 | 8.2206 | 8.2206 | 0 | 12 | 1 | 1 | 8.2206 | 10 | 0 | 0
793.25 | 49.66 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.74412 | 7.4412 | 8.7206 | 8.7206 | 0 | 12 | 1 | 1 | 8.7206 | 10 | 0 | 0
793.3 | 49.63 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.84412 | 8.4412 | 9.2206 | 9.2206 | 0 | 12 | 1 | 1 | 9.2206 | 10 | 0 | 0
793.35 | 49.63 | 49.59 | 1 | 1 | 10 | 49.72 | 1 | 0.94412 | 9.4412 | 9.7206 | 9.7206 | 0 | 12 | 1 | 1 | 9.7206 | 10 | 0 | 0
793.4 | 49.61 | 49.59 | 1 | 1 | 10 | 49.72 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
793.45 | 49.61 | 49.59 | 1 | 1 | 10 | 49.67 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
793.5 | 49.54 | 49.54 | 1 | 1 | 10 | 49.67 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
793.55 | 49.54 | 49.54 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
793.6 | 49.46 | 49.46 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
793.65 | 49.46 | 49.46 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
793.7 | 49.45 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
793.75 | 49.45 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
793.8 | 49.51 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
793.85 | 49.51 | 49.45 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
793.9 | 49.5 | 49.45 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
793.95 | 49.5 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
794 | 49.54 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
794.05 | 49.54 | 49.45 | 1 | 1 | 10 | 49.54 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
794.1 | 49.59 | 49.45 | 1 | 1 | 10 | 49.59 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
794.15 | 49.59 | 49.45 | 1 | 1 | 10 | 49.59 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
794.2 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
794.25 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
794.3 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
794.35 | 49.61 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
794.4 | 49.53 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
794.45 | 49.53 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
794.5 | 49.54 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
794.55 | 49.54 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
794.6 | 49.61 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
794.65 | 49.61 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
794.7 | 49.66 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
794.75 | 49.66 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
794.8 | 49.64 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
794.85 | 49.64 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
794.9 | 49.69 | 49.53 | 1 | 1 | 10 | 49.69 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
794.95 | 49.69 | 49.53 | 1 | 1 | 10 | 49.69 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
795 | 49.74 | 49.53 | 1 | 1 | 10 | 49.74 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
795.05 | 49.74 | 49.54 | 1 | 1 | 10 | 49.74 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
795.1 | 49.78 | 49.54 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
795.15 | 49.78 | 49.61 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
795.2 | 49.82 | 49.61 | 1 | 1 | 10 | 49.82 | 0.81 | 0.81 | 8.1 | 9.05 | 9.05 | 0 | 12 | 1 | 1 | 9.05 | 10 | 0 | 0
795.25 | 49.82 | 49.64 | 1 | 1 | 10 | 49.82 | 0.81 | 0.81 | 8.1 | 9.05 | 9.05 | 0 | 12 | 1 | 1 | 9.05 | 10 | 0 | 0
795.3 | 49.86 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
795.35 | 49.86 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
795.4 | 49.84 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
795.45 | 49.84 | 49.69 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
795.5 | 49.91 | 49.69 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
795.55 | 49.91 | 49.74 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
795.6 | 49.97 | 49.74 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
795.65 | 49.97 | 49.78 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
795.7 | 50.03 | 49.78 | 1 | 1 | 10 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.9559 | 4.9559 | 0 | 12 | 1 | 1 | 4.9559 | 10 | 0 | 0
795.75 | 50.03 | 49.82 | 0.81 | 0.9 | 9 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.4559 | 4.4559 | 0 | 12 | 1 | 1 | 4.4559 | 10 | 0 | 0
795.8 | 50.05 | 49.82 | 0.81 | 0.81 | 8.1 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 3.9471 | 3.9471 | 0 | 12 | 1 | 1 | 3.9471 | 10 | 0 | 0
795.85 | 50.05 | 49.84 | 0.62 | 0.71 | 7.1 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 3.4471 | 3.4471 | 0 | 12 | 1 | 1 | 3.4471 | 10 | 0 | 0
795.9 | 50.01 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
795.95 | 50.01 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
796 | 49.95 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
796.05 | 49.95 | 49.91 | 0.044118 | 0.52 | 5.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.4971 | 2.4971 | 0 | 12 | 1 | 1 | 2.4971 | 10 | 0 | 0
796.1 | 49.99 | 49.91 | 0.044118 | 0.42 | 4.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 1.9971 | 1.9971 | 0 | 12 | 1 | 1 | 1.9971 | 10 | 0 | 0
796.15 | 49.99 | 49.95 | 0.020588 | 0.32 | 3.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 1.4971 | 1.4971 | 0 | 12 | 1 | 1 | 1.4971 | 10 | 0 | 0
796.2 | 49.92 | 49.92 | 0.038235 | 0.22 | 2.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.99706 | 0.99706 | 0 | 12 | 1 | 1 | 0.99706 | 10 | 0 | 0
796.25 | 49.92 | 49.92 | 0.038235 | 0.12 | 1.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.49706 | 0.49706 | 0 | 12 | 1 | 1 | 0.49706 | 10 | 0 | 0
796.3 | 49.97 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
796.35 | 49.97 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
796.4 | 50.02 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
796.45 | 50.02 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.17647 | 0.17647 | 0 | 12 | 1 | 1 | 0.17647 | 10 | 0 | 0
796.5 | 50.07 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
796.55 | 50.07 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
796.6 | 50.06 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
796.65 | 50.06 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
796.7 | 50.13 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
796.75 | 50.13 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
796.8 | 50.09 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
796.85 | 50.09 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6309 | -1.6309 | 0 | 12 | 1 | 1 | -1.6309 | 10 | 0 | 0
796.9 | 50.07 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6309 | -1.6309 | 0 | 12 | 1 | 1 | -1.6309 | 10 | 0 | 0
796.95 | 50.07 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6897 | -1.6897 | 0 | 12 | 1 | 1 | -1.6897 | 10 | 0 | 0
797 | 50.07 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6897 | -1.6897 | 0 | 12 | 1 | 1 | -1.6897 | 10 | 0 | 0
797.05 | 50.07 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.13 | -0.335 | -0.335 | -3.35 | -1.8074 | -1.8074 | 0 | 12 | 1 | 1 | -1.8074 | 10 | 0 | 0
797.1 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.13 | -0.335 | -0.335 | -3.35 | -1.7779 | -1.7779 | 0 | 12 | 1 | 1 | -1.7779 | 10 | 0 | 0
797.15 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.13 | -0.335 | -0.335 | -3.35 | -1.7779 | -1.7779 | 0 | 12 | 1 | 1 | -1.7779 | 10 | 0 | 0
797.2 | 50.01 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
797.25 | 50.01 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
797.3 | 50.07 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
797.35 | 50.07 | 50.01 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.235 | -2.35 | -1.175 | -1.175 | 0 | 12 | 1 | 1 | -1.175 | 10 | 0 | 0
797.4 | 50.05 | 50.01 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.135 | -1.35 | -0.675 | -0.675 | 0 | 12 | 1 | 1 | -0.675 | 10 | 0 | 0
797.45 | 50.05 | 50.01 | 0 | 0 | 0 | 50.07 | -0.032353 | -0.035 | -0.35 | -0.175 | -0.175 | 0 | 12 | 1 | 1 | -0.175 | 10 | 0 | 0
797.5 | 50.1 | 50.01 | 0 | 0 | 0 | 50.1 | -0.05 | -0.05 | -0.5 | -0.25 | -0.25 | 0 | 12 | 1 | 1 | -0.25 | 10 | 0 | 0
797.55 | 50.1 | 50.01 | 0 | 0 | 0 | 50.1 | -0.05 | -0.05 | -0.5 | -0.25 | -0.25 | 0 | 12 | 1 | 1 | -0.25 | 10 | 0 | 0
797.6 | 50.11 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
797.65 | 50.11 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
797.7 | 50.06 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
797.75 | 50.06 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
797.8 | 50.04 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
797.85 | 50.04 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
797.9 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
797.95 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
798 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
798.05 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
798.1 | 50.11 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
798.15 | 50.11 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
798.2 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
798.25 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
798.3 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
798.35 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
798.4 | 50.02 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.11 | -0.145 | -0.145 | -1.45 | -0.73971 | -0.73971 | 0 | 12 | 1 | 1 | -0.73971 | 10 | 0 | 0
798.45 | 50.02 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.11 | -0.145 | -0.145 | -1.45 | -0.73971 | -0.73971 | 0 | 12 | 1 | 1 | -0.73971 | 10 | 0 | 0
798.5 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
798.55 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
798.6 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
798.65 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
798.7 | 50.01 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
798.75 | 50.01 | 50 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.045 | -0.45 | -0.225 | -0.225 | 0 | 12 | 1 | 1 | -0.225 | 10 | 0 | 0
798.8 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
798.85 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
798.9 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
798.95 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
799 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.14706 | 0.14706 | 0 | 12 | 1 | 1 | 0.14706 | 10 | 0 | 0
799.05 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
799.1 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
799.15 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
799.2 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
799.25 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
799.3 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
799.35 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
799.4 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
799.45 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
799.5 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
799.55 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
799.6 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
799.65 | 50 | 50 | 0 | 0 | 0 | 50.01 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
799.7 | 49.5 | 49.5 | 1 | 1 | 10 | 50.01 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
799.75 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
799.8 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
799.85 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
799.9 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
799.95 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
800 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
800.05 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
800.1 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
800.15 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
800.2 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
800.25 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.1 | 1 | 5.5 | 5.5 | 0 | 12 | 1 | 1 | 5.5 | 10 | 0 | 0
800.3 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.2 | 2 | 6 | 6 | 0 | 12 | 1 | 1 | 6 | 10 | 0 | 0
800.35 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.3 | 3 | 6.5 | 6.5 | 0 | 12 | 1 | 1 | 6.5 | 10 | 0 | 0
800.4 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.4 | 4 | 7 | 7 | 0 | 12 | 1 | 1 | 7 | 10 | 0 | 0
800.45 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.5 | 5 | 7.5 | 7.5 | 0 | 12 | 1 | 1 | 7.5 | 10 | 0 | 0
800.5 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.6 | 6 | 8 | 8 | 0 | 12 | 1 | 1 | 8 | 10 | 0 | 0
800.55 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.7 | 7 | 8.5 | 8.5 | 0 | 12 | 1 | 1 | 8.5 | 10 | 0 | 0
800.6 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.8 | 8 | 9 | 9 | 0 | 12 | 1 | 1 | 9 | 10 | 0 | 0
800.65 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.9 | 9 | 9.5 | 9.5 | 0 | 12 | 1 | 1 | 9.5 | 10 | 0 | 0
800.7 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
800.75 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
800.8 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
800.85 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
800.9 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
800.95 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
801 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
801.05 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
801.1 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
801.15 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
801.2 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
801.25 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
801.3 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
801.35 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
801.4 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
801.45 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
801.5 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
801.55 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
801.6 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
801.65 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
801.7 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
801.75 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
801.8 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
801.85 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
801.9 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
801.95 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
802 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
802.05 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
802.1 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
802.15 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
802.2 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
802.25 | 50.5 | 50.5 | -1 | 0.9 | 9 | 50.5 | -1 | -1 | -10 | -0.5 | -0.5 | 0 | 12 | 1 | 1 | -0.5 | 10 | 0 | 0
802.3 | 50.5 | 50.5 | -1 | 0.8 | 8 | 50.5 | -1 | -1 | -10 | -1 | -1 | 0 | 12 | 1 | 1 | -1 | 10 | 0 | 0
802.35 | 50.5 | 50.5 | -1 | 0.7 | 7 | 50.5 | -1 | -1 | -10 | -1.5 | -1.5 | 0 | 12 | 1 | 1 | -1.5 | 10 | 0 | 0
802.4 | 50.5 | 50.5 | -1 | 0.6 | 6 | 50.5 | -1 | -1 | -10 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
802.45 | 50.5 | 50.5 | -1 | 0.5 | 5 | 50.5 | -1 | -1 | -10 | -2.5 | -2.5 | 0 | 12 | 1 | 1 | -2.5 | 10 | 0 | 0
802.5 | 50.5 | 50.5 | -1 | 0.4 | 4 | 50.5 | -1 | -1 | -10 | -3 | -3 | 0 | 12 | 1 | 1 | -3 | 10 | 0 | 0
802.55 | 50.5 | 50.5 | -1 | 0.3 | 3 | 50.5 | -1 | -1 | -10 | -3.5 | -3.5 | 0 | 12 | 1 | 1 | -3.5 | 10 | 0 | 0
802.6 | 50.5 | 50.5 | -1 | 0.2 | 2 | 50.5 | -1 | -1 | -10 | -4 | -4 | 0 | 12 | 1 | 1 | -4 | 10 | 0 | 0
802.65 | 50.5 | 50.5 | -1 | 0.1 | 1 | 50.5 | -1 | -1 | -10 | -4.5 | -4.5 | 0 | 12 | 1 | 1 | -4.5 | 10 | 0 | 0
802.7 | 50.5 | 50.5 | -1 | 0 | 0 | 50.5 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
802.75 | 50.5 | 50.5 | -1 | -0.1 | -1 | 50.5 | -1 | -1 | -10 | -5.5 | -5.5 | 0 | 12 | 1 | 1 | -5.5 | 10 | 0 | 0
802.8 | 50.5 | 50.5 | -1 | -0.2 | -2 | 50.5 | -1 | -1 | -10 | -6 | -6 | 0 | 12 | 1 | 1 | -6 | 10 | 0 | 0
802.85 | 50.5 | 50.5 | -1 | -0.3 | -3 | 50.5 | -1 | -1 | -10 | -6.5 | -6.5 | 0 | 12 | 1 | 1 | -6.5 | 10 | 0 | 0
802.9 | 50.5 | 50.5 | -1 | -0.4 | -4 | 50.5 | -1 | -1 | -10 | -7 | -7 | 0 | 12 | 1 | 1 | -7 | 10 | 0 | 0
802.95 | 50.5 | 50.5 | -1 | -0.5 | -5 | 50.5 | -1 | -1 | -10 | -7.5 | -7.5 | 0 | 12 | 1 | 1 | -7.5 | 10 | 0 | 0
803 | 50.5 | 50.5 | -1 | -0.6 | -6 | 50.5 | -1 | -1 | -10 | -8 | -8 | 0 | 12 | 1 | 1 | -8 | 10 | 0 | 0
803.05 | 50.5 | 50.5 | -1 | -0.7 | -7 | 50.5 | -1 | -1 | -10 | -8.5 | -8.5 | 0 | 12 | 1 | 1 | -8.5 | 10 | 0 | 0
803.1 | 50.5 | 50.5 | -1 | -0.8 | -8 | 50.5 | -1 | -1 | -10 | -9 | -9 | 0 | 12 | 1 | 1 | -9 | 10 | 0 | 0
803.15 | 50.5 | 50.5 | -1 | -0.9 | -9 | 50.5 | -1 | -1 | -10 | -9.5 | -9.5 | 0 | 12 | 1 | 1 | -9.5 | 10 | 0 | 0
803.2 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
803.25 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
803.3 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
803.35 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
803.4 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
803.45 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
803.5 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
803.55 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
803.6 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
803.65 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
803.7 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
803.75 | 50.47 | 50.47 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
803.8 | 50.45 | 50.45 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
803.85 | 50.42 | 50.42 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
803.9 | 50.4 | 50.4 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
803.95 | 50.37 | 50.37 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
804 | 50.35 | 50.35 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
804.05 | 50.32 | 50.32 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
804.1 | 50.29 | 50.29 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
804.15 | 50.27 | 50.27 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
804.2 | 50.24 | 50.24 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
804.25 | 50.22 | 50.22 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
804.3 | 50.19 | 50.19 | -0.905 | -0.905 | -9.05 | 50.47 | -1 | -1 | -10 | -9.525 | -9.525 | 0 | 12 | 1 | 1 | -9.525 | 10 | 0 | 0
804.35 | 50.17 | 50.17 | -0.715 | -0.715 | -7.15 | 50.45 | -1 | -1 | -10 | -8.575 | -8.575 | 0 | 12 | 1 | 1 | -8.575 | 10 | 0 | 0
804.4 | 50.14 | 50.14 | -0.43 | -0.43 | -4.3 | 50.42 | -1 | -1 | -10 | -7.15 | -7.15 | 0 | 12 | 1 | 1 | -7.15 | 10 | 0 | 0
804.45 | 50.12 | 50.12 | -0.24 | -0.24 | -2.4 | 50.4 | -1 | -1 | -10 | -6.2 | -6.2 | 0 | 12 | 1 | 1 | -6.2 | 10 | 0 | 0
804.5 | 50.09 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 50.37 | -1 | -1 | -10 | -5.2206 | -5.2206 | 0 | 12 | 1 | 1 | -5.2206 | 10 | 0 | 0
804.55 | 50.06 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.35 | -1 | -1 | -10 | -5.1324 | -5.1324 | 0 | 12 | 1 | 1 | -5.1324 | 10 | 0 | 0
804.6 | 50.04 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.32 | -1 | -1 | -10 | -5.0735 | -5.0735 | 0 | 12 | 1 | 1 | -5.0735 | 10 | 0 | 0
804.65 | 50.01 | 50.01 | 0 | 0 | 0 | 50.29 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
804.7 | 49.99 | 49.99 | 0 | 0 | 0 | 50.27 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
804.75 | 49.96 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.24 | -1 | -1 | -10 | -4.9265 | -4.9265 | 0 | 12 | 1 | 1 | -4.9265 | 10 | 0 | 0
804.8 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.22 | -1 | -1 | -10 | -4.8676 | -4.8676 | 0 | 12 | 1 | 1 | -4.8676 | 10 | 0 | 0
804.85 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.19 | -0.905 | -0.905 | -9.05 | -4.3044 | -4.3044 | 0 | 12 | 1 | 1 | -4.3044 | 10 | 0 | 0
804.9 | 49.88 | 49.88 | 0.24 | 0.24 | 2.4 | 50.17 | -0.715 | -0.805 | -8.05 | -2.825 | -2.825 | 0 | 12 | 1 | 1 | -2.825 | 10 | 0 | 0
804.95 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.14 | -0.43 | -0.705 | -7.05 | -1.375 | -1.375 | 0 | 12 | 1 | 1 | -1.375 | 10 | 0 | 0
805 | 49.83 | 49.83 | 0.715 | 0.715 | 7.15 | 50.12 | -0.24 | -0.605 | -6.05 | 0.55 | 0.55 | 0 | 12 | 1 | 1 | 0.55 | 10 | 0 | 0
805.05 | 49.81 | 49.81 | 0.905 | 0.905 | 9.05 | 50.09 | -0.044118 | -0.505 | -5.05 | 2 | 2 | 0 | 12 | 1 | 1 | 2 | 10 | 0 | 0
805.1 | 49.78 | 49.78 | 1 | 1 | 10 | 50.06 | -0.026471 | -0.405 | -4.05 | 2.975 | 2.975 | 0 | 12 | 1 | 1 | 2.975 | 10 | 0 | 0
805.15 | 49.76 | 49.76 | 1 | 1 | 10 | 50.04 | -0.014706 | -0.305 | -3.05 | 3.475 | 3.475 | 0 | 12 | 1 | 1 | 3.475 | 10 | 0 | 0
805.2 | 49.73 | 49.73 | 1 | 1 | 10 | 50.01 | 0 | -0.205 | -2.05 | 3.975 | 3.975 | 0 | 12 | 1 | 1 | 3.975 | 10 | 0 | 0
805.25 | 49.71 | 49.71 | 1 | 1 | 10 | 49.99 | 0 | -0.105 | -1.05 | 4.475 | 4.475 | 0 | 12 | 1 | 1 | 4.475 | 10 | 0 | 0
805.3 | 49.68 | 49.68 | 1 | 1 | 10 | 49.96 | 0.014706 | -0.005 | -0.05 | 4.975 | 4.975 | 0 | 12 | 1 | 1 | 4.975 | 10 | 0 | 0
805.35 | 49.65 | 49.65 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
805.4 | 49.63 | 49.63 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
805.45 | 49.6 | 49.6 | 1 | 1 | 10 | 49.88 | 0.24 | 0.14412 | 1.4412 | 5.7206 | 5.7206 | 0 | 12 | 1 | 1 | 5.7206 | 10 | 0 | 0
805.5 | 49.58 | 49.58 | 1 | 1 | 10 | 49.86 | 0.43 | 0.24412 | 2.4412 | 6.2206 | 6.2206 | 0 | 12 | 1 | 1 | 6.2206 | 10 | 0 | 0
805.55 | 49.55 | 49.55 | 1 | 1 | 10 | 49.83 | 0.715 | 0.34412 | 3.4412 | 6.7206 | 6.7206 | 0 | 12 | 1 | 1 | 6.7206 | 10 | 0 | 0
805.6 | 49.53 | 49.53 | 1 | 1 | 10 | 49.81 | 0.905 | 0.44412 | 4.4412 | 7.2206 | 7.2206 | 0 | 12 | 1 | 1 | 7.2206 | 10 | 0 | 0
805.65 | 49.5 | 49.5 | 1 | 1 | 10 | 49.78 | 1 | 0.54412 | 5.4412 | 7.7206 | 7.7206 | 0 | 12 | 1 | 1 | 7.7206 | 10 | 0 | 0
805.7 | 49.5 | 49.5 | 1 | 1 | 10 | 49.76 | 1 | 0.64412 | 6.4412 | 8.2206 | 8.2206 | 0 | 12 | 1 | 1 | 8.2206 | 10 | 0 | 0
805.75 | 49.53 | 49.5 | 1 | 1 | 10 | 49.73 | 1 | 0.74412 | 7.4412 | 8.7206 | 8.7206 | 0 | 12 | 1 | 1 | 8.7206 | 10 | 0 | 0
805.8 | 49.55 | 49.5 | 1 | 1 | 10 | 49.71 | 1 | 0.84412 | 8.4412 | 9.2206 | 9.2206 | 0 | 12 | 1 | 1 | 9.2206 | 10 | 0 | 0
805.85 | 49.58 | 49.5 | 1 | 1 | 10 | 49.68 | 1 | 0.94412 | 9.4412 | 9.7206 | 9.7206 | 0 | 12 | 1 | 1 | 9.7206 | 10 | 0 | 0
805.9 | 49.6 | 49.5 | 1 | 1 | 10 | 49.65 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
805.95 | 49.63 | 49.5 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
806 | 49.65 | 49.5 | 1 | 1 | 10 | 49.65 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
806.05 | 49.68 | 49.5 | 1 | 1 | 10 | 49.68 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
806.1 | 49.71 | 49.5 | 1 | 1 | 10 | 49.71 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
806.15 | 49.73 | 49.5 | 1 | 1 | 10 | 49.73 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
806.2 | 49.76 | 49.5 | 1 | 1 | 10 | 49.76 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
806.25 | 49.78 | 49.5 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
806.3 | 49.81 | 49.53 | 1 | 1 | 10 | 49.81 | 0.905 | 0.905 | 9.05 | 9.525 | 9.525 | 0 | 12 | 1 | 1 | 9.525 | 10 | 0 | 0
806.35 | 49.83 | 49.55 | 1 | 1 | 10 | 49.83 | 0.715 | 0.715 | 7.15 | 8.575 | 8.575 | 0 | 12 | 1 | 1 | 8.575 | 10 | 0 | 0
806.4 | 49.86 | 49.58 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
806.45 | 49.88 | 49.6 | 1 | 1 | 10 | 49.88 | 0.24 | 0.24 | 2.4 | 6.2 | 6.2 | 0 | 12 | 1 | 1 | 6.2 | 10 | 0 | 0
806.5 | 49.91 | 49.63 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
806.55 | 49.94 | 49.65 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
806.6 | 49.96 | 49.68 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
806.65 | 49.99 | 49.71 | 1 | 1 | 10 | 49.99 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
806.7 | 50.01 | 49.73 | 1 | 1 | 10 | 50.01 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
806.75 | 50.04 | 49.76 | 1 | 1 | 10 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 4.9265 | 4.9265 | 0 | 12 | 1 | 1 | 4.9265 | 10 | 0 | 0
806.8 | 50.06 | 49.78 | 1 | 1 | 10 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 4.8676 | 4.8676 | 0 | 12 | 1 | 1 | 4.8676 | 10 | 0 | 0
806.85 | 50.09 | 49.81 | 0.905 | 0.905 | 9.05 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 4.3044 | 4.3044 | 0 | 12 | 1 | 1 | 4.3044 | 10 | 0 | 0
806.9 | 50.12 | 49.83 | 0.715 | 0.805 | 8.05 | 50.12 | -0.24 | -0.24 | -2.4 | 2.825 | 2.825 | 0 | 12 | 1 | 1 | 2.825 | 10 | 0 | 0
806.95 | 50.14 | 49.86 | 0.43 | 0.705 | 7.05 | 50.14 | -0.43 | -0.43 | -4.3 | 1.375 | 1.375 | 0 | 12 | 1 | 1 | 1.375 | 10 | 0 | 0
807 | 50.17 | 49.88 | 0.24 | 0.605 | 6.05 | 50.17 | -0.715 | -0.715 | -7.15 | -0.55 | -0.55 | 0 | 12 | 1 | 1 | -0.55 | 10 | 0 | 0
807.05 | 50.19 | 49.91 | 0.044118 | 0.505 | 5.05 | 50.19 | -0.905 | -0.905 | -9.05 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
807.1 | 50.22 | 49.94 | 0.026471 | 0.405 | 4.05 | 50.22 | -1 | -1 | -10 | -2.975 | -2.975 | 0 | 12 | 1 | 1 | -2.975 | 10 | 0 | 0
807.15 | 50.24 | 49.96 | 0.014706 | 0.305 | 3.05 | 50.24 | -1 | -1 | -10 | -3.475 | -3.475 | 0 | 12 | 1 | 1 | -3.475 | 10 | 0 | 0
807.2 | 50.27 | 49.99 | 0 | 0.205 | 2.05 | 50.27 | -1 | -1 | -10 | -3.975 | -3.975 | 0 | 12 | 1 | 1 | -3.975 | 10 | 0 | 0
807.25 | 50.29 | 50.01 | 0 | 0.105 | 1.05 | 50.29 | -1 | -1 | -10 | -4.475 | -4.475 | 0 | 12 | 1 | 1 | -4.475 | 10 | 0 | 0
807.3 | 50.32 | 50.04 | -0.014706 | 0.005 | 0.05 | 50.32 | -1 | -1 | -10 | -4.975 | -4.975 | 0 | 12 | 1 | 1 | -4.975 | 10 | 0 | 0
807.35 | 50.35 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.35 | -1 | -1 | -10 | -5.1324 | -5.1324 | 0 | 12 | 1 | 1 | -5.1324 | 10 | 0 | 0
807.4 | 50.37 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 50.37 | -1 | -1 | -10 | -5.2206 | -5.2206 | 0 | 12 | 1 | 1 | -5.2206 | 10 | 0 | 0
807.45 | 50.4 | 50.12 | -0.24 | -0.14412 | -1.4412 | 50.4 | -1 | -1 | -10 | -5.7206 | -5.7206 | 0 | 12 | 1 | 1 | -5.7206 | 10 | 0 | 0
807.5 | 50.42 | 50.14 | -0.43 | -0.24412 | -2.4412 | 50.42 | -1 | -1 | -10 | -6.2206 | -6.2206 | 0 | 12 | 1 | 1 | -6.2206 | 10 | 0 | 0
807.55 | 50.45 | 50.17 | -0.715 | -0.34412 | -3.4412 | 50.45 | -1 | -1 | -10 | -6.7206 | -6.7206 | 0 | 12 | 1 | 1 | -6.7206 | 10 | 0 | 0
807.6 | 50.47 | 50.19 | -0.905 | -0.44412 | -4.4412 | 50.47 | -1 | -1 | -10 | -7.2206 | -7.2206 | 0 | 12 | 1 | 1 | -7.2206 | 10 | 0 | 0
807.65 | 50.5 | 50.22 | -1 | -0.54412 | -5.4412 | 50.5 | -1 | -1 | -10 | -7.7206 | -7.7206 | 0 | 12 | 1 | 1 | -7.7206 | 10 | 0 | 0
807.7 | 50.5 | 50.24 | -1 | -0.64412 | -6.4412 | 50.5 | -1 | -1 | -10 | -8.2206 | -8.2206 | 0 | 12 | 1 | 1 | -8.2206 | 10 | 0 | 0
807.75 | 50.47 | 50.27 | -1 | -0.74412 | -7.4412 | 50.5 | -1 | -1 | -10 | -8.7206 | -8.7206 | 0 | 12 | 1 | 1 | -8.7206 | 10 | 0 | 0
807.8 | 50.45 | 50.29 | -1 | -0.84412 | -8.4412 | 50.5 | -1 | -1 | -10 | -9.2206 | -9.2206 | 0 | 12 | 1 | 1 | -9.2206 | 10 | 0 | 0
807.85 | 50.42 | 50.32 | -1 | -0.94412 | -9.4412 | 50.5 | -1 | -1 | -10 | -9.7206 | -9.7206 | 0 | 12 | 1 | 1 | -9.7206 | 10 | 0 | 0
807.9 | 50.39 | 50.35 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
807.95 | 50.37 | 50.37 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
808 | 50.34 | 50.34 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
808.05 | 50.32 | 50.32 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
808.1 | 50.29 | 50.29 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
808.15 | 50.26 | 50.26 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
808.2 | 50.24 | 50.24 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
808.25 | 50.21 | 50.21 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
808.3 | 50.18 | 50.18 | -0.81 | -0.81 | -8.1 | 50.47 | -1 | -1 | -10 | -9.05 | -9.05 | 0 | 12 | 1 | 1 | -9.05 | 10 | 0 | 0
808.35 | 50.16 | 50.16 | -0.62 | -0.62 | -6.2 | 50.45 | -1 | -1 | -10 | -8.1 | -8.1 | 0 | 12 | 1 | 1 | -8.1 | 10 | 0 | 0
808.4 | 50.13 | 50.13 | -0.335 | -0.335 | -3.35 | 50.42 | -1 | -1 | -10 | -6.675 | -6.675 | 0 | 12 | 1 | 1 | -6.675 | 10 | 0 | 0
808.45 | 50.11 | 50.11 | -0.145 | -0.145 | -1.45 | 50.39 | -1 | -1 | -10 | -5.725 | -5.725 | 0 | 12 | 1 | 1 | -5.725 | 10 | 0 | 0
808.5 | 50.08 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 50.37 | -1 | -1 | -10 | -5.1912 | -5.1912 | 0 | 12 | 1 | 1 | -5.1912 | 10 | 0 | 0
808.55 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.34 | -1 | -1 | -10 | -5.1029 | -5.1029 | 0 | 12 | 1 | 1 | -5.1029 | 10 | 0 | 0
808.6 | 50.03 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 50.32 | -1 | -1 | -10 | -5.0441 | -5.0441 | 0 | 12 | 1 | 1 | -5.0441 | 10 | 0 | 0
808.65 | 50 | 50 | 0 | 0 | 0 | 50.29 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
808.7 | 50 | 50 | 0 | 0 | 0 | 50.26 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
808.75 | 50 | 50 | 0 | 0 | 0 | 50.24 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
808.8 | 50 | 50 | 0 | 0 | 0 | 50.21 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
808.85 | 50 | 50 | 0 | 0 | 0 | 50.18 | -0.81 | -0.9 | -9 | -4.5 | -4.5 | 0 | 12 | 1 | 1 | -4.5 | 10 | 0 | 0
808.9 | 50 | 50 | 0 | 0 | 0 | 50.16 | -0.62 | -0.8 | -8 | -4 | -4 | 0 | 12 | 1 | 1 | -4 | 10 | 0 | 0
808.95 | 50 | 50 | 0 | 0 | 0 | 50.13 | -0.335 | -0.7 | -7 | -3.5 | -3.5 | 0 | 12 | 1 | 1 | -3.5 | 10 | 0 | 0
809 | 50.01 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.6 | -6 | -3 | -3 | 0 | 12 | 1 | 1 | -3 | 10 | 0 | 0
809.05 | 50.01 | 50 | 0 | 0 | 0 | 50.08 | -0.038235 | -0.5 | -5 | -2.5 | -2.5 | 0 | 12 | 1 | 1 | -2.5 | 10 | 0 | 0
809.1 | 49.99 | 49.99 | 0 | 0 | 0 | 50.05 | -0.020588 | -0.4 | -4 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
809.15 | 49.99 | 49.99 | 0 | 0 | 0 | 50.03 | -0.0088235 | -0.3 | -3 | -1.5 | -1.5 | 0 | 12 | 1 | 1 | -1.5 | 10 | 0 | 0
809.2 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | -0.2 | -2 | -0.83824 | -0.83824 | 0 | 12 | 1 | 1 | -0.83824 | 10 | 0 | 0
809.25 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | -0.1 | -1 | -0.33824 | -0.33824 | 0 | 12 | 1 | 1 | -0.33824 | 10 | 0 | 0
809.3 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
809.35 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
809.4 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
809.45 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
809.5 | 49.89 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
809.55 | 49.89 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
809.6 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50.01 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
809.65 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
809.7 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
809.75 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 2.7868 | 2.7868 | 0 | 12 | 1 | 1 | 2.7868 | 10 | 0 | 0
809.8 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 2.7868 | 2.7868 | 0 | 12 | 1 | 1 | 2.7868 | 10 | 0 | 0
809.85 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 2.8456 | 2.8456 | 0 | 12 | 1 | 1 | 2.8456 | 10 | 0 | 0
809.9 | 49.94 | 49.85 | 0.525 | 0.525 | 5.25 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 2.7574 | 2.7574 | 0 | 12 | 1 | 1 | 2.7574 | 10 | 0 | 0
809.95 | 49.94 | 49.85 | 0.525 | 0.525 | 5.25 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 2.7574 | 2.7574 | 0 | 12 | 1 | 1 | 2.7574 | 10 | 0 | 0
810 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
810.05 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
810.1 | 49.93 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
810.15 | 49.93 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
810.2 | 49.96 | 49.85 | 0.525 | 0.525 | 5.25 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 2.6985 | 2.6985 | 0 | 12 | 1 | 1 | 2.6985 | 10 | 0 | 0
810.25 | 49.96 | 49.85 | 0.525 | 0.525 | 5.25 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 2.6985 | 2.6985 | 0 | 12 | 1 | 1 | 2.6985 | 10 | 0 | 0
810.3 | 49.99 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
810.35 | 49.99 | 49.91 | 0.044118 | 0.425 | 4.25 | 49.99 | 0 | 0 | 0 | 2.125 | 2.125 | 0 | 12 | 1 | 1 | 2.125 | 10 | 0 | 0
810.4 | 49.99 | 49.91 | 0.044118 | 0.325 | 3.25 | 49.99 | 0 | 0 | 0 | 1.625 | 1.625 | 0 | 12 | 1 | 1 | 1.625 | 10 | 0 | 0
810.45 | 49.99 | 49.93 | 0.032353 | 0.225 | 2.25 | 49.99 | 0 | 0 | 0 | 1.125 | 1.125 | 0 | 12 | 1 | 1 | 1.125 | 10 | 0 | 0
810.5 | 49.96 | 49.93 | 0.032353 | 0.125 | 1.25 | 49.99 | 0 | 0 | 0 | 0.625 | 0.625 | 0 | 12 | 1 | 1 | 0.625 | 10 | 0 | 0
810.55 | 49.96 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 49.99 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
810.6 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
810.65 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
810.7 | 50.05 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.058824 | 0.058824 | 0 | 12 | 1 | 1 | 0.058824 | 10 | 0 | 0
810.75 | 50.05 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
810.8 | 49.97 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
810.85 | 49.97 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
810.9 | 49.92 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
810.95 | 49.92 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
811 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
811.05 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
811.1 | 49.94 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
811.15 | 49.94 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
811.2 | 50.01 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
811.25 | 50.01 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
811.3 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
811.35 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
811.4 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
811.45 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
811.5 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
811.55 | 49.95 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
811.6 | 49.97 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
811.65 | 49.97 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
811.7 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
811.75 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
811.8 | 49.87 | 49.87 | 0.335 | 0.335 | 3.35 | 50.01 | 0 | 0 | 0 | 1.675 | 1.675 | 0 | 12 | 1 | 1 | 1.675 | 10 | 0 | 0
811.85 | 49.87 | 49.87 | 0.335 | 0.335 | 3.35 | 49.99 | 0 | 0 | 0 | 1.675 | 1.675 | 0 | 12 | 1 | 1 | 1.675 | 10 | 0 | 0
811.9 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
811.95 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 2.6691 | 2.6691 | 0 | 12 | 1 | 1 | 2.6691 | 10 | 0 | 0
812 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
812.05 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
812.1 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
812.15 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
812.2 | 49.84 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
812.25 | 49.84 | 49.79 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
812.3 | 49.89 | 49.79 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
812.35 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.12647 | 1.2647 | 5.6324 | 5.6324 | 0 | 12 | 1 | 1 | 5.6324 | 10 | 0 | 0
812.4 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.145 | 1.45 | 5.725 | 5.725 | 0 | 12 | 1 | 1 | 5.725 | 10 | 0 | 0
812.45 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.145 | 1.45 | 5.725 | 5.725 | 0 | 12 | 1 | 1 | 5.725 | 10 | 0 | 0
812.5 | 49.96 | 49.79 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
812.55 | 49.96 | 49.79 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
812.6 | 50.02 | 49.79 | 1 | 1 | 10 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 4.9853 | 4.9853 | 0 | 12 | 1 | 1 | 4.9853 | 10 | 0 | 0
812.65 | 50.02 | 49.79 | 1 | 1 | 10 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 4.9853 | 4.9853 | 0 | 12 | 1 | 1 | 4.9853 | 10 | 0 | 0
812.7 | 50.03 | 49.79 | 1 | 1 | 10 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.9559 | 4.9559 | 0 | 12 | 1 | 1 | 4.9559 | 10 | 0 | 0
812.75 | 50.03 | 49.84 | 0.62 | 0.9 | 9 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.4559 | 4.4559 | 0 | 12 | 1 | 1 | 4.4559 | 10 | 0 | 0
812.8 | 50.02 | 49.84 | 0.62 | 0.8 | 8 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 3.9559 | 3.9559 | 0 | 12 | 1 | 1 | 3.9559 | 10 | 0 | 0
812.85 | 50.02 | 49.89 | 0.145 | 0.7 | 7 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 3.4559 | 3.4559 | 0 | 12 | 1 | 1 | 3.4559 | 10 | 0 | 0
812.9 | 50.08 | 49.89 | 0.145 | 0.6 | 6 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 2.8088 | 2.8088 | 0 | 12 | 1 | 1 | 2.8088 | 10 | 0 | 0
812.95 | 50.08 | 49.89 | 0.145 | 0.5 | 5 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 2.3088 | 2.3088 | 0 | 12 | 1 | 1 | 2.3088 | 10 | 0 | 0
813 | 50.01 | 49.89 | 0.145 | 0.4 | 4 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 1.8088 | 1.8088 | 0 | 12 | 1 | 1 | 1.8088 | 10 | 0 | 0
813.05 | 50.01 | 49.96 | 0.014706 | 0.3 | 3 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 1.3088 | 1.3088 | 0 | 12 | 1 | 1 | 1.3088 | 10 | 0 | 0
813.1 | 49.94 | 49.94 | 0.026471 | 0.2 | 2 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.80882 | 0.80882 | 0 | 12 | 1 | 1 | 0.80882 | 10 | 0 | 0
813.15 | 49.94 | 49.94 | 0.026471 | 0.1 | 1 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.30882 | 0.30882 | 0 | 12 | 1 | 1 | 0.30882 | 10 | 0 | 0
813.2 | 50 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
813.25 | 50 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
813.3 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
813.35 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
813.4 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
813.45 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
813.5 | 49.92 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
813.55 | 49.92 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
813.6 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50.01 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
813.65 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
813.7 | 49.92 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
813.75 | 49.92 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
813.8 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
813.85 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
813.9 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
813.95 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
814 | 49.87 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
814.05 | 49.87 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
814.1 | 49.8 | 49.8 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
814.15 | 49.8 | 49.8 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
814.2 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
814.25 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
814.3 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
814.35 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
814.4 | 49.72 | 49.72 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
814.45 | 49.72 | 49.72 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
814.5 | 49.67 | 49.67 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
814.55 | 49.67 | 49.67 | 1 | 1 | 10 | 49.87 | 0.335 | 0.14412 | 1.4412 | 5.7206 | 5.7206 | 0 | 12 | 1 | 1 | 5.7206 | 10 | 0 | 0
814.6 | 49.65 | 49.65 | 1 | 1 | 10 | 49.87 | 0.335 | 0.24412 | 2.4412 | 6.2206 | 6.2206 | 0 | 12 | 1 | 1 | 6.2206 | 10 | 0 | 0
814.65 | 49.65 | 49.65 | 1 | 1 | 10 | 49.8 | 1 | 0.34412 | 3.4412 | 6.7206 | 6.7206 | 0 | 12 | 1 | 1 | 6.7206 | 10 | 0 | 0
814.7 | 49.59 | 49.59 | 1 | 1 | 10 | 49.8 | 1 | 0.44412 | 4.4412 | 7.2206 | 7.2206 | 0 | 12 | 1 | 1 | 7.2206 | 10 | 0 | 0
814.75 | 49.59 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.54412 | 5.4412 | 7.7206 | 7.7206 | 0 | 12 | 1 | 1 | 7.7206 | 10 | 0 | 0
814.8 | 49.66 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.64412 | 6.4412 | 8.2206 | 8.2206 | 0 | 12 | 1 | 1 | 8.2206 | 10 | 0 | 0
814.85 | 49.66 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.74412 | 7.4412 | 8.7206 | 8.7206 | 0 | 12 | 1 | 1 | 8.7206 | 10 | 0 | 0
814.9 | 49.63 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.84412 | 8.4412 | 9.2206 | 9.2206 | 0 | 12 | 1 | 1 | 9.2206 | 10 | 0 | 0
814.95 | 49.63 | 49.59 | 1 | 1 | 10 | 49.72 | 1 | 0.94412 | 9.4412 | 9.7206 | 9.7206 | 0 | 12 | 1 | 1 | 9.7206 | 10 | 0 | 0
815 | 49.61 | 49.59 | 1 | 1 | 10 | 49.72 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
815.05 | 49.61 | 49.59 | 1 | 1 | 10 | 49.67 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
815.1 | 49.54 | 49.54 | 1 | 1 | 10 | 49.67 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
815.15 | 49.54 | 49.54 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
815.2 | 49.46 | 49.46 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
815.25 | 49.46 | 49.46 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
815.3 | 49.45 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
815.35 | 49.45 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
815.4 | 49.51 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
815.45 | 49.51 | 49.45 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
815.5 | 49.5 | 49.45 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
815.55 | 49.5 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
815.6 | 49.54 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
815.65 | 49.54 | 49.45 | 1 | 1 | 10 | 49.54 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
815.7 | 49.59 | 49.45 | 1 | 1 | 10 | 49.59 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
815.75 | 49.59 | 49.45 | 1 | 1 | 10 | 49.59 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
815.8 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
815.85 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
815.9 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
815.95 | 49.61 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
816 | 49.53 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
816.05 | 49.53 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
816.1 | 49.54 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
816.15 | 49.54 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
816.2 | 49.61 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
816.25 | 49.61 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
816.3 | 49.66 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
816.35 | 49.66 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
816.4 | 49.64 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
816.45 | 49.64 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
816.5 | 49.69 | 49.53 | 1 | 1 | 10 | 49.69 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
816.55 | 49.69 | 49.53 | 1 | 1 | 10 | 49.69 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
816.6 | 49.74 | 49.53 | 1 | 1 | 10 | 49.74 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
816.65 | 49.74 | 49.54 | 1 | 1 | 10 | 49.74 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
816.7 | 49.78 | 49.54 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
816.75 | 49.78 | 49.61 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
816.8 | 49.82 | 49.61 | 1 | 1 | 10 | 49.82 | 0.81 | 0.81 | 8.1 | 9.05 | 9.05 | 0 | 12 | 1 | 1 | 9.05 | 10 | 0 | 0
816.85 | 49.82 | 49.64 | 1 | 1 | 10 | 49.82 | 0.81 | 0.81 | 8.1 | 9.05 | 9.05 | 0 | 12 | 1 | 1 | 9.05 | 10 | 0 | 0
816.9 | 49.86 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
816.95 | 49.86 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
817 | 49.84 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
817.05 | 49.84 | 49.69 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
817.1 | 49.91 | 49.69 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
817.15 | 49.91 | 49.74 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
817.2 | 49.97 | 49.74 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
817.25 | 49.97 | 49.78 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
817.3 | 50.03 | 49.78 | 1 | 1 | 10 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.9559 | 4.9559 | 0 | 12 | 1 | 1 | 4.9559 | 10 | 0 | 0
817.35 | 50.03 | 49.82 | 0.81 | 0.9 | 9 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.4559 | 4.4559 | 0 | 12 | 1 | 1 | 4.4559 | 10 | 0 | 0
817.4 | 50.05 | 49.82 | 0.81 | 0.81 | 8.1 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 3.9471 | 3.9471 | 0 | 12 | 1 | 1 | 3.9471 | 10 | 0 | 0
817.45 | 50.05 | 49.84 | 0.62 | 0.71 | 7.1 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 3.4471 | 3.4471 | 0 | 12 | 1 | 1 | 3.4471 | 10 | 0 | 0
817.5 | 50.01 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
817.55 | 50.01 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
817.6 | 49.95 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
817.65 | 49.95 | 49.91 | 0.044118 | 0.52 | 5.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.4971 | 2.4971 | 0 | 12 | 1 | 1 | 2.4971 | 10 | 0 | 0
817.7 | 49.99 | 49.91 | 0.044118 | 0.42 | 4.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 1.9971 | 1.9971 | 0 | 12 | 1 | 1 | 1.9971 | 10 | 0 | 0
817.75 | 49.99 | 49.95 | 0.020588 | 0.32 | 3.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 1.4971 | 1.4971 | 0 | 12 | 1 | 1 | 1.4971 | 10 | 0 | 0
817.8 | 49.92 | 49.92 | 0.038235 | 0.22 | 2.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.99706 | 0.99706 | 0 | 12 | 1 | 1 | 0.99706 | 10 | 0 | 0
817.85 | 49.92 | 49.92 | 0.038235 | 0.12 | 1.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.49706 | 0.49706 | 0 | 12 | 1 | 1 | 0.49706 | 10 | 0 | 0
817.9 | 49.97 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
817.95 | 49.97 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
818 | 50.02 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
818.05 | 50.02 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.17647 | 0.17647 | 0 | 12 | 1 | 1 | 0.17647 | 10 | 0 | 0
818.1 | 50.07 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
818.15 | 50.07 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
818.2 | 50.06 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
818.25 | 50.06 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
818.3 | 50.13 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
818.35 | 50.13 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
818.4 | 50.09 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
818.45 | 50.09 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6309 | -1.6309 | 0 | 12 | 1 | 1 | -1.6309 | 10 | 0 | 0
818.5 | 50.07 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6309 | -1.6309 | 0 | 12 | 1 | 1 | -1.6309 | 10 | 0 | 0
818.55 | 50.07 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6897 | -1.6897 | 0 | 12 | 1 | 1 | -1.6897 | 10 | 0 | 0
818.6 | 50.07 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6897 | -1.6897 | 0 | 12 | 1 | 1 | -1.6897 | 10 | 0 | 0
818.65 | 50.07 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.13 | -0.335 | -0.335 | -3.35 | -1.8074 | -1.8074 | 0 | 12 | 1 | 1 | -1.8074 | 10 | 0 | 0
818.7 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.13 | -0.335 | -0.335 | -3.35 | -1.7779 | -1.7779 | 0 | 12 | 1 | 1 | -1.7779 | 10 | 0 | 0
818.75 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.13 | -0.335 | -0.335 | -3.35 | -1.7779 | -1.7779 | 0 | 12 | 1 | 1 | -1.7779 | 10 | 0 | 0
818.8 | 50.01 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
818.85 | 50.01 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
818.9 | 50.07 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
818.95 | 50.07 | 50.01 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.235 | -2.35 | -1.175 | -1.175 | 0 | 12 | 1 | 1 | -1.175 | 10 | 0 | 0
819 | 50.05 | 50.01 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.135 | -1.35 | -0.675 | -0.675 | 0 | 12 | 1 | 1 | -0.675 | 10 | 0 | 0
819.05 | 50.05 | 50.01 | 0 | 0 | 0 | 50.07 | -0.032353 | -0.035 | -0.35 | -0.175 | -0.175 | 0 | 12 | 1 | 1 | -0.175 | 10 | 0 | 0
819.1 | 50.1 | 50.01 | 0 | 0 | 0 | 50.1 | -0.05 | -0.05 | -0.5 | -0.25 | -0.25 | 0 | 12 | 1 | 1 | -0.25 | 10 | 0 | 0
819.15 | 50.1 | 50.01 | 0 | 0 | 0 | 50.1 | -0.05 | -0.05 | -0.5 | -0.25 | -0.25 | 0 | 12 | 1 | 1 | -0.25 | 10 | 0 | 0
819.2 | 50.11 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
819.25 | 50.11 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
819.3 | 50.06 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
819.35 | 50.06 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
819.4 | 50.04 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
819.45 | 50.04 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
819.5 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
819.55 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
819.6 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
819.65 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
819.7 | 50.11 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
819.75 | 50.11 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
819.8 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
819.85 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
819.9 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
819.95 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
820 | 50.02 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.11 | -0.145 | -0.145 | -1.45 | -0.73971 | -0.73971 | 0 | 12 | 1 | 1 | -0.73971 | 10 | 0 | 0
820.05 | 50.02 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.11 | -0.145 | -0.145 | -1.45 | -0.73971 | -0.73971 | 0 | 12 | 1 | 1 | -0.73971 | 10 | 0 | 0
820.1 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
820.15 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
820.2 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
820.25 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
820.3 | 50.01 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
820.35 | 50.01 | 50 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.045 | -0.45 | -0.225 | -0.225 | 0 | 12 | 1 | 1 | -0.225 | 10 | 0 | 0
820.4 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
820.45 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
820.5 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
820.55 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
820.6 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.14706 | 0.14706 | 0 | 12 | 1 | 1 | 0.14706 | 10 | 0 | 0
820.65 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
820.7 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
820.75 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
820.8 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
820.85 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
820.9 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
820.95 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
821 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
821.05 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
821.1 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
821.15 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
821.2 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
821.25 | 50 | 50 | 0 | 0 | 0 | 50.01 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
821.3 | 49.5 | 49.5 | 1 | 1 | 10 | 50.01 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
821.35 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
821.4 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
821.45 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
821.5 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
821.55 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
821.6 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
821.65 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
821.7 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
821.75 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
821.8 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
821.85 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.1 | 1 | 5.5 | 5.5 | 0 | 12 | 1 | 1 | 5.5 | 10 | 0 | 0
821.9 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.2 | 2 | 6 | 6 | 0 | 12 | 1 | 1 | 6 | 10 | 0 | 0
821.95 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.3 | 3 | 6.5 | 6.5 | 0 | 12 | 1 | 1 | 6.5 | 10 | 0 | 0
822 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.4 | 4 | 7 | 7 | 0 | 12 | 1 | 1 | 7 | 10 | 0 | 0
822.05 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.5 | 5 | 7.5 | 7.5 | 0 | 12 | 1 | 1 | 7.5 | 10 | 0 | 0
822.1 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.6 | 6 | 8 | 8 | 0 | 12 | 1 | 1 | 8 | 10 | 0 | 0
822.15 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.7 | 7 | 8.5 | 8.5 | 0 | 12 | 1 | 1 | 8.5 | 10 | 0 | 0
822.2 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.8 | 8 | 9 | 9 | 0 | 12 | 1 | 1 | 9 | 10 | 0 | 0
822.25 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.9 | 9 | 9.5 | 9.5 | 0 | 12 | 1 | 1 | 9.5 | 10 | 0 | 0
822.3 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
822.35 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
822.4 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
822.45 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
822.5 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
822.55 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
822.6 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
822.65 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
822.7 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
822.75 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
822.8 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
822.85 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
822.9 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
822.95 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
823 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
823.05 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
823.1 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
823.15 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
823.2 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
823.25 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
823.3 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
823.35 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
823.4 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
823.45 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
823.5 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
823.55 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
823.6 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
823.65 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
823.7 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
823.75 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
823.8 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
823.85 | 50.5 | 50.5 | -1 | 0.9 | 9 | 50.5 | -1 | -1 | -10 | -0.5 | -0.5 | 0 | 12 | 1 | 1 | -0.5 | 10 | 0 | 0
823.9 | 50.5 | 50.5 | -1 | 0.8 | 8 | 50.5 | -1 | -1 | -10 | -1 | -1 | 0 | 12 | 1 | 1 | -1 | 10 | 0 | 0
823.95 | 50.5 | 50.5 | -1 | 0.7 | 7 | 50.5 | -1 | -1 | -10 | -1.5 | -1.5 | 0 | 12 | 1 | 1 | -1.5 | 10 | 0 | 0
824 | 50.5 | 50.5 | -1 | 0.6 | 6 | 50.5 | -1 | -1 | -10 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
824.05 | 50.5 | 50.5 | -1 | 0.5 | 5 | 50.5 | -1 | -1 | -10 | -2.5 | -2.5 | 0 | 12 | 1 | 1 | -2.5 | 10 | 0 | 0
824.1 | 50.5 | 50.5 | -1 | 0.4 | 4 | 50.5 | -1 | -1 | -10 | -3 | -3 | 0 | 12 | 1 | 1 | -3 | 10 | 0 | 0
824.15 | 50.5 | 50.5 | -1 | 0.3 | 3 | 50.5 | -1 | -1 | -10 | -3.5 | -3.5 | 0 | 12 | 1 | 1 | -3.5 | 10 | 0 | 0
824.2 | 50.5 | 50.5 | -1 | 0.2 | 2 | 50.5 | -1 | -1 | -10 | -4 | -4 | 0 | 12 | 1 | 1 | -4 | 10 | 0 | 0
824.25 | 50.5 | 50.5 | -1 | 0.1 | 1 | 50.5 | -1 | -1 | -10 | -4.5 | -4.5 | 0 | 12 | 1 | 1 | -4.5 | 10 | 0 | 0
824.3 | 50.5 | 50.5 | -1 | 0 | 0 | 50.5 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
824.35 | 50.5 | 50.5 | -1 | -0.1 | -1 | 50.5 | -1 | -1 | -10 | -5.5 | -5.5 | 0 | 12 | 1 | 1 | -5.5 | 10 | 0 | 0
824.4 | 50.5 | 50.5 | -1 | -0.2 | -2 | 50.5 | -1 | -1 | -10 | -6 | -6 | 0 | 12 | 1 | 1 | -6 | 10 | 0 | 0
824.45 | 50.5 | 50.5 | -1 | -0.3 | -3 | 50.5 | -1 | -1 | -10 | -6.5 | -6.5 | 0 | 12 | 1 | 1 | -6.5 | 10 | 0 | 0
824.5 | 50.5 | 50.5 | -1 | -0.4 | -4 | 50.5 | -1 | -1 | -10 | -7 | -7 | 0 | 12 | 1 | 1 | -7 | 10 | 0 | 0
824.55 | 50.5 | 50.5 | -1 | -0.5 | -5 | 50.5 | -1 | -1 | -10 | -7.5 | -7.5 | 0 | 12 | 1 | 1 | -7.5 | 10 | 0 | 0
824.6 | 50.5 | 50.5 | -1 | -0.6 | -6 | 50.5 | -1 | -1 | -10 | -8 | -8 | 0 | 12 | 1 | 1 | -8 | 10 | 0 | 0
824.65 | 50.5 | 50.5 | -1 | -0.7 | -7 | 50.5 | -1 | -1 | -10 | -8.5 | -8.5 | 0 | 12 | 1 | 1 | -8.5 | 10 | 0 | 0
824.7 | 50.5 | 50.5 | -1 | -0.8 | -8 | 50.5 | -1 | -1 | -10 | -9 | -9 | 0 | 12 | 1 | 1 | -9 | 10 | 0 | 0
824.75 | 50.5 | 50.5 | -1 | -0.9 | -9 | 50.5 | -1 | -1 | -10 | -9.5 | -9.5 | 0 | 12 | 1 | 1 | -9.5 | 10 | 0 | 0
824.8 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
824.85 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
824.9 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
824.95 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
825 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
825.05 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
825.1 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
825.15 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
825.2 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
825.25 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
825.3 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
825.35 | 50.47 | 50.47 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
825.4 | 50.45 | 50.45 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
825.45 | 50.42 | 50.42 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
825.5 | 50.4 | 50.4 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
825.55 | 50.37 | 50.37 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
825.6 | 50.35 | 50.35 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
825.65 | 50.32 | 50.32 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
825.7 | 50.29 | 50.29 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
825.75 | 50.27 | 50.27 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
825.8 | 50.24 | 50.24 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
825.85 | 50.22 | 50.22 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
825.9 | 50.19 | 50.19 | -0.905 | -0.905 | -9.05 | 50.47 | -1 | -1 | -10 | -9.525 | -9.525 | 0 | 12 | 1 | 1 | -9.525 | 10 | 0 | 0
825.95 | 50.17 | 50.17 | -0.715 | -0.715 | -7.15 | 50.45 | -1 | -1 | -10 | -8.575 | -8.575 | 0 | 12 | 1 | 1 | -8.575 | 10 | 0 | 0
826 | 50.14 | 50.14 | -0.43 | -0.43 | -4.3 | 50.42 | -1 | -1 | -10 | -7.15 | -7.15 | 0 | 12 | 1 | 1 | -7.15 | 10 | 0 | 0
826.05 | 50.12 | 50.12 | -0.24 | -0.24 | -2.4 | 50.4 | -1 | -1 | -10 | -6.2 | -6.2 | 0 | 12 | 1 | 1 | -6.2 | 10 | 0 | 0
826.1 | 50.09 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 50.37 | -1 | -1 | -10 | -5.2206 | -5.2206 | 0 | 12 | 1 | 1 | -5.2206 | 10 | 0 | 0
826.15 | 50.06 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.35 | -1 | -1 | -10 | -5.1324 | -5.1324 | 0 | 12 | 1 | 1 | -5.1324 | 10 | 0 | 0
826.2 | 50.04 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.32 | -1 | -1 | -10 | -5.0735 | -5.0735 | 0 | 12 | 1 | 1 | -5.0735 | 10 | 0 | 0
826.25 | 50.01 | 50.01 | 0 | 0 | 0 | 50.29 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
826.3 | 49.99 | 49.99 | 0 | 0 | 0 | 50.27 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
826.35 | 49.96 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.24 | -1 | -1 | -10 | -4.9265 | -4.9265 | 0 | 12 | 1 | 1 | -4.9265 | 10 | 0 | 0
826.4 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.22 | -1 | -1 | -10 | -4.8676 | -4.8676 | 0 | 12 | 1 | 1 | -4.8676 | 10 | 0 | 0
826.45 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.19 | -0.905 | -0.905 | -9.05 | -4.3044 | -4.3044 | 0 | 12 | 1 | 1 | -4.3044 | 10 | 0 | 0
826.5 | 49.88 | 49.88 | 0.24 | 0.24 | 2.4 | 50.17 | -0.715 | -0.805 | -8.05 | -2.825 | -2.825 | 0 | 12 | 1 | 1 | -2.825 | 10 | 0 | 0
826.55 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.14 | -0.43 | -0.705 | -7.05 | -1.375 | -1.375 | 0 | 12 | 1 | 1 | -1.375 | 10 | 0 | 0
826.6 | 49.83 | 49.83 | 0.715 | 0.715 | 7.15 | 50.12 | -0.24 | -0.605 | -6.05 | 0.55 | 0.55 | 0 | 12 | 1 | 1 | 0.55 | 10 | 0 | 0
826.65 | 49.81 | 49.81 | 0.905 | 0.905 | 9.05 | 50.09 | -0.044118 | -0.505 | -5.05 | 2 | 2 | 0 | 12 | 1 | 1 | 2 | 10 | 0 | 0
826.7 | 49.78 | 49.78 | 1 | 1 | 10 | 50.06 | -0.026471 | -0.405 | -4.05 | 2.975 | 2.975 | 0 | 12 | 1 | 1 | 2.975 | 10 | 0 | 0
826.75 | 49.76 | 49.76 | 1 | 1 | 10 | 50.04 | -0.014706 | -0.305 | -3.05 | 3.475 | 3.475 | 0 | 12 | 1 | 1 | 3.475 | 10 | 0 | 0
826.8 | 49.73 | 49.73 | 1 | 1 | 10 | 50.01 | 0 | -0.205 | -2.05 | 3.975 | 3.975 | 0 | 12 | 1 | 1 | 3.975 | 10 | 0 | 0
826.85 | 49.71 | 49.71 | 1 | 1 | 10 | 49.99 | 0 | -0.105 | -1.05 | 4.475 | 4.475 | 0 | 12 | 1 | 1 | 4.475 | 10 | 0 | 0
826.9 | 49.68 | 49.68 | 1 | 1 | 10 | 49.96 | 0.014706 | -0.005 | -0.05 | 4.975 | 4.975 | 0 | 12 | 1 | 1 | 4.975 | 10 | 0 | 0
826.95 | 49.65 | 49.65 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
827 | 49.63 | 49.63 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
827.05 | 49.6 | 49.6 | 1 | 1 | 10 | 49.88 | 0.24 | 0.14412 | 1.4412 | 5.7206 | 5.7206 | 0 | 12 | 1 | 1 | 5.7206 | 10 | 0 | 0
827.1 | 49.58 | 49.58 | 1 | 1 | 10 | 49.86 | 0.43 | 0.24412 | 2.4412 | 6.2206 | 6.2206 | 0 | 12 | 1 | 1 | 6.2206 | 10 | 0 | 0
827.15 | 49.55 | 49.55 | 1 | 1 | 10 | 49.83 | 0.715 | 0.34412 | 3.4412 | 6.7206 | 6.7206 | 0 | 12 | 1 | 1 | 6.7206 | 10 | 0 | 0
827.2 | 49.53 | 49.53 | 1 | 1 | 10 | 49.81 | 0.905 | 0.44412 | 4.4412 | 7.2206 | 7.2206 | 0 | 12 | 1 | 1 | 7.2206 | 10 | 0 | 0
827.25 | 49.5 | 49.5 | 1 | 1 | 10 | 49.78 | 1 | 0.54412 | 5.4412 | 7.7206 | 7.7206 | 0 | 12 | 1 | 1 | 7.7206 | 10 | 0 | 0
827.3 | 49.5 | 49.5 | 1 | 1 | 10 | 49.76 | 1 | 0.64412 | 6.4412 | 8.2206 | 8.2206 | 0 | 12 | 1 | 1 | 8.2206 | 10 | 0 | 0
827.35 | 49.53 | 49.5 | 1 | 1 | 10 | 49.73 | 1 | 0.74412 | 7.4412 | 8.7206 | 8.7206 | 0 | 12 | 1 | 1 | 8.7206 | 10 | 0 | 0
827.4 | 49.55 | 49.5 | 1 | 1 | 10 | 49.71 | 1 | 0.84412 | 8.4412 | 9.2206 | 9.2206 | 0 | 12 | 1 | 1 | 9.2206 | 10 | 0 | 0
827.45 | 49.58 | 49.5 | 1 | 1 | 10 | 49.68 | 1 | 0.94412 | 9.4412 | 9.7206 | 9.7206 | 0 | 12 | 1 | 1 | 9.7206 | 10 | 0 | 0
827.5 | 49.6 | 49.5 | 1 | 1 | 10 | 49.65 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
827.55 | 49.63 | 49.5 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
827.6 | 49.65 | 49.5 | 1 | 1 | 10 | 49.65 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
827.65 | 49.68 | 49.5 | 1 | 1 | 10 | 49.68 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
827.7 | 49.71 | 49.5 | 1 | 1 | 10 | 49.71 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
827.75 | 49.73 | 49.5 | 1 | 1 | 10 | 49.73 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
827.8 | 49.76 | 49.5 | 1 | 1 | 10 | 49.76 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
827.85 | 49.78 | 49.5 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
827.9 | 49.81 | 49.53 | 1 | 1 | 10 | 49.81 | 0.905 | 0.905 | 9.05 | 9.525 | 9.525 | 0 | 12 | 1 | 1 | 9.525 | 10 | 0 | 0
827.95 | 49.83 | 49.55 | 1 | 1 | 10 | 49.83 | 0.715 | 0.715 | 7.15 | 8.575 | 8.575 | 0 | 12 | 1 | 1 | 8.575 | 10 | 0 | 0
828 | 49.86 | 49.58 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
828.05 | 49.88 | 49.6 | 1 | 1 | 10 | 49.88 | 0.24 | 0.24 | 2.4 | 6.2 | 6.2 | 0 | 12 | 1 | 1 | 6.2 | 10 | 0 | 0
828.1 | 49.91 | 49.63 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
828.15 | 49.94 | 49.65 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
828.2 | 49.96 | 49.68 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
828.25 | 49.99 | 49.71 | 1 | 1 | 10 | 49.99 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
828.3 | 50.01 | 49.73 | 1 | 1 | 10 | 50.01 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
828.35 | 50.04 | 49.76 | 1 | 1 | 10 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 4.9265 | 4.9265 | 0 | 12 | 1 | 1 | 4.9265 | 10 | 0 | 0
828.4 | 50.06 | 49.78 | 1 | 1 | 10 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 4.8676 | 4.8676 | 0 | 12 | 1 | 1 | 4.8676 | 10 | 0 | 0
828.45 | 50.09 | 49.81 | 0.905 | 0.905 | 9.05 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 4.3044 | 4.3044 | 0 | 12 | 1 | 1 | 4.3044 | 10 | 0 | 0
828.5 | 50.12 | 49.83 | 0.715 | 0.805 | 8.05 | 50.12 | -0.24 | -0.24 | -2.4 | 2.825 | 2.825 | 0 | 12 | 1 | 1 | 2.825 | 10 | 0 | 0
828.55 | 50.14 | 49.86 | 0.43 | 0.705 | 7.05 | 50.14 | -0.43 | -0.43 | -4.3 | 1.375 | 1.375 | 0 | 12 | 1 | 1 | 1.375 | 10 | 0 | 0
828.6 | 50.17 | 49.88 | 0.24 | 0.605 | 6.05 | 50.17 | -0.715 | -0.715 | -7.15 | -0.55 | -0.55 | 0 | 12 | 1 | 1 | -0.55 | 10 | 0 | 0
828.65 | 50.19 | 49.91 | 0.044118 | 0.505 | 5.05 | 50.19 | -0.905 | -0.905 | -9.05 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
828.7 | 50.22 | 49.94 | 0.026471 | 0.405 | 4.05 | 50.22 | -1 | -1 | -10 | -2.975 | -2.975 | 0 | 12 | 1 | 1 | -2.975 | 10 | 0 | 0
828.75 | 50.24 | 49.96 | 0.014706 | 0.305 | 3.05 | 50.24 | -1 | -1 | -10 | -3.475 | -3.475 | 0 | 12 | 1 | 1 | -3.475 | 10 | 0 | 0
828.8 | 50.27 | 49.99 | 0 | 0.205 | 2.05 | 50.27 | -1 | -1 | -10 | -3.975 | -3.975 | 0 | 12 | 1 | 1 | -3.975 | 10 | 0 | 0
828.85 | 50.29 | 50.01 | 0 | 0.105 | 1.05 | 50.29 | -1 | -1 | -10 | -4.475 | -4.475 | 0 | 12 | 1 | 1 | -4.475 | 10 | 0 | 0
828.9 | 50.32 | 50.04 | -0.014706 | 0.005 | 0.05 | 50.32 | -1 | -1 | -10 | -4.975 | -4.975 | 0 | 12 | 1 | 1 | -4.975 | 10 | 0 | 0
828.95 | 50.35 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.35 | -1 | -1 | -10 | -5.1324 | -5.1324 | 0 | 12 | 1 | 1 | -5.1324 | 10 | 0 | 0
829 | 50.37 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 50.37 | -1 | -1 | -10 | -5.2206 | -5.2206 | 0 | 12 | 1 | 1 | -5.2206 | 10 | 0 | 0
829.05 | 50.4 | 50.12 | -0.24 | -0.14412 | -1.4412 | 50.4 | -1 | -1 | -10 | -5.7206 | -5.7206 | 0 | 12 | 1 | 1 | -5.7206 | 10 | 0 | 0
829.1 | 50.42 | 50.14 | -0.43 | -0.24412 | -2.4412 | 50.42 | -1 | -1 | -10 | -6.2206 | -6.2206 | 0 | 12 | 1 | 1 | -6.2206 | 10 | 0 | 0
829.15 | 50.45 | 50.17 | -0.715 | -0.34412 | -3.4412 | 50.45 | -1 | -1 | -10 | -6.7206 | -6.7206 | 0 | 12 | 1 | 1 | -6.7206 | 10 | 0 | 0
829.2 | 50.47 | 50.19 | -0.905 | -0.44412 | -4.4412 | 50.47 | -1 | -1 | -10 | -7.2206 | -7.2206 | 0 | 12 | 1 | 1 | -7.2206 | 10 | 0 | 0
829.25 | 50.5 | 50.22 | -1 | -0.54412 | -5.4412 | 50.5 | -1 | -1 | -10 | -7.7206 | -7.7206 | 0 | 12 | 1 | 1 | -7.7206 | 10 | 0 | 0
829.3 | 50.5 | 50.24 | -1 | -0.64412 | -6.4412 | 50.5 | -1 | -1 | -10 | -8.2206 | -8.2206 | 0 | 12 | 1 | 1 | -8.2206 | 10 | 0 | 0
829.35 | 50.47 | 50.27 | -1 | -0.74412 | -7.4412 | 50.5 | -1 | -1 | -10 | -8.7206 | -8.7206 | 0 | 12 | 1 | 1 | -8.7206 | 10 | 0 | 0
829.4 | 50.45 | 50.29 | -1 | -0.84412 | -8.4412 | 50.5 | -1 | -1 | -10 | -9.2206 | -9.2206 | 0 | 12 | 1 | 1 | -9.2206 | 10 | 0 | 0
829.45 | 50.42 | 50.32 | -1 | -0.94412 | -9.4412 | 50.5 | -1 | -1 | -10 | -9.7206 | -9.7206 | 0 | 12 | 1 | 1 | -9.7206 | 10 | 0 | 0
829.5 | 50.39 | 50.35 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
829.55 | 50.37 | 50.37 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
829.6 | 50.34 | 50.34 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
829.65 | 50.32 | 50.32 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
829.7 | 50.29 | 50.29 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
829.75 | 50.26 | 50.26 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
829.8 | 50.24 | 50.24 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
829.85 | 50.21 | 50.21 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
829.9 | 50.18 | 50.18 | -0.81 | -0.81 | -8.1 | 50.47 | -1 | -1 | -10 | -9.05 | -9.05 | 0 | 12 | 1 | 1 | -9.05 | 10 | 0 | 0
829.95 | 50.16 | 50.16 | -0.62 | -0.62 | -6.2 | 50.45 | -1 | -1 | -10 | -8.1 | -8.1 | 0 | 12 | 1 | 1 | -8.1 | 10 | 0 | 0
830 | 50.13 | 50.13 | -0.335 | -0.335 | -3.35 | 50.42 | -1 | -1 | -10 | -6.675 | -6.675 | 0 | 12 | 1 | 1 | -6.675 | 10 | 0 | 0
830.05 | 50.11 | 50.11 | -0.145 | -0.145 | -1.45 | 50.39 | -1 | -1 | -10 | -5.725 | -5.725 | 0 | 12 | 1 | 1 | -5.725 | 10 | 0 | 0
830.1 | 50.08 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 50.37 | -1 | -1 | -10 | -5.1912 | -5.1912 | 0 | 12 | 1 | 1 | -5.1912 | 10 | 0 | 0
830.15 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.34 | -1 | -1 | -10 | -5.1029 | -5.1029 | 0 | 12 | 1 | 1 | -5.1029 | 10 | 0 | 0
830.2 | 50.03 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 50.32 | -1 | -1 | -10 | -5.0441 | -5.0441 | 0 | 12 | 1 | 1 | -5.0441 | 10 | 0 | 0
830.25 | 50 | 50 | 0 | 0 | 0 | 50.29 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
830.3 | 50 | 50 | 0 | 0 | 0 | 50.26 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
830.35 | 50 | 50 | 0 | 0 | 0 | 50.24 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
830.4 | 50 | 50 | 0 | 0 | 0 | 50.21 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
830.45 | 50 | 50 | 0 | 0 | 0 | 50.18 | -0.81 | -0.9 | -9 | -4.5 | -4.5 | 0 | 12 | 1 | 1 | -4.5 | 10 | 0 | 0
830.5 | 50 | 50 | 0 | 0 | 0 | 50.16 | -0.62 | -0.8 | -8 | -4 | -4 | 0 | 12 | 1 | 1 | -4 | 10 | 0 | 0
830.55 | 50 | 50 | 0 | 0 | 0 | 50.13 | -0.335 | -0.7 | -7 | -3.5 | -3.5 | 0 | 12 | 1 | 1 | -3.5 | 10 | 0 | 0
830.6 | 50.01 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.6 | -6 | -3 | -3 | 0 | 12 | 1 | 1 | -3 | 10 | 0 | 0
830.65 | 50.01 | 50 | 0 | 0 | 0 | 50.08 | -0.038235 | -0.5 | -5 | -2.5 | -2.5 | 0 | 12 | 1 | 1 | -2.5 | 10 | 0 | 0
830.7 | 49.99 | 49.99 | 0 | 0 | 0 | 50.05 | -0.020588 | -0.4 | -4 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
830.75 | 49.99 | 49.99 | 0 | 0 | 0 | 50.03 | -0.0088235 | -0.3 | -3 | -1.5 | -1.5 | 0 | 12 | 1 | 1 | -1.5 | 10 | 0 | 0
830.8 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | -0.2 | -2 | -0.83824 | -0.83824 | 0 | 12 | 1 | 1 | -0.83824 | 10 | 0 | 0
830.85 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | -0.1 | -1 | -0.33824 | -0.33824 | 0 | 12 | 1 | 1 | -0.33824 | 10 | 0 | 0
830.9 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
830.95 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
831 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
831.05 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
831.1 | 49.89 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
831.15 | 49.89 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
831.2 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50.01 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
831.25 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
831.3 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
831.35 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 2.7868 | 2.7868 | 0 | 12 | 1 | 1 | 2.7868 | 10 | 0 | 0
831.4 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 2.7868 | 2.7868 | 0 | 12 | 1 | 1 | 2.7868 | 10 | 0 | 0
831.45 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 2.8456 | 2.8456 | 0 | 12 | 1 | 1 | 2.8456 | 10 | 0 | 0
831.5 | 49.94 | 49.85 | 0.525 | 0.525 | 5.25 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 2.7574 | 2.7574 | 0 | 12 | 1 | 1 | 2.7574 | 10 | 0 | 0
831.55 | 49.94 | 49.85 | 0.525 | 0.525 | 5.25 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 2.7574 | 2.7574 | 0 | 12 | 1 | 1 | 2.7574 | 10 | 0 | 0
831.6 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
831.65 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
831.7 | 49.93 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
831.75 | 49.93 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
831.8 | 49.96 | 49.85 | 0.525 | 0.525 | 5.25 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 2.6985 | 2.6985 | 0 | 12 | 1 | 1 | 2.6985 | 10 | 0 | 0
831.85 | 49.96 | 49.85 | 0.525 | 0.525 | 5.25 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 2.6985 | 2.6985 | 0 | 12 | 1 | 1 | 2.6985 | 10 | 0 | 0
831.9 | 49.99 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
831.95 | 49.99 | 49.91 | 0.044118 | 0.425 | 4.25 | 49.99 | 0 | 0 | 0 | 2.125 | 2.125 | 0 | 12 | 1 | 1 | 2.125 | 10 | 0 | 0
832 | 49.99 | 49.91 | 0.044118 | 0.325 | 3.25 | 49.99 | 0 | 0 | 0 | 1.625 | 1.625 | 0 | 12 | 1 | 1 | 1.625 | 10 | 0 | 0
832.05 | 49.99 | 49.93 | 0.032353 | 0.225 | 2.25 | 49.99 | 0 | 0 | 0 | 1.125 | 1.125 | 0 | 12 | 1 | 1 | 1.125 | 10 | 0 | 0
832.1 | 49.96 | 49.93 | 0.032353 | 0.125 | 1.25 | 49.99 | 0 | 0 | 0 | 0.625 | 0.625 | 0 | 12 | 1 | 1 | 0.625 | 10 | 0 | 0
832.15 | 49.96 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 49.99 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
832.2 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
832.25 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
832.3 | 50.05 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.058824 | 0.058824 | 0 | 12 | 1 | 1 | 0.058824 | 10 | 0 | 0
832.35 | 50.05 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
832.4 | 49.97 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
832.45 | 49.97 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
832.5 | 49.92 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
832.55 | 49.92 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
832.6 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
832.65 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
832.7 | 49.94 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
832.75 | 49.94 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
832.8 | 50.01 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
832.85 | 50.01 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
832.9 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
832.95 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
833 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
833.05 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
833.1 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
833.15 | 49.95 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
833.2 | 49.97 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
833.25 | 49.97 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
833.3 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
833.35 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
833.4 | 49.87 | 49.87 | 0.335 | 0.335 | 3.35 | 50.01 | 0 | 0 | 0 | 1.675 | 1.675 | 0 | 12 | 1 | 1 | 1.675 | 10 | 0 | 0
833.45 | 49.87 | 49.87 | 0.335 | 0.335 | 3.35 | 49.99 | 0 | 0 | 0 | 1.675 | 1.675 | 0 | 12 | 1 | 1 | 1.675 | 10 | 0 | 0
833.5 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
833.55 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 2.6691 | 2.6691 | 0 | 12 | 1 | 1 | 2.6691 | 10 | 0 | 0
833.6 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
833.65 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
833.7 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
833.75 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
833.8 | 49.84 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
833.85 | 49.84 | 49.79 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
833.9 | 49.89 | 49.79 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
833.95 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.12647 | 1.2647 | 5.6324 | 5.6324 | 0 | 12 | 1 | 1 | 5.6324 | 10 | 0 | 0
834 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.145 | 1.45 | 5.725 | 5.725 | 0 | 12 | 1 | 1 | 5.725 | 10 | 0 | 0
834.05 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.145 | 1.45 | 5.725 | 5.725 | 0 | 12 | 1 | 1 | 5.725 | 10 | 0 | 0
834.1 | 49.96 | 49.79 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
834.15 | 49.96 | 49.79 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
834.2 | 50.02 | 49.79 | 1 | 1 | 10 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 4.9853 | 4.9853 | 0 | 12 | 1 | 1 | 4.9853 | 10 | 0 | 0
834.25 | 50.02 | 49.79 | 1 | 1 | 10 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 4.9853 | 4.9853 | 0 | 12 | 1 | 1 | 4.9853 | 10 | 0 | 0
834.3 | 50.03 | 49.79 | 1 | 1 | 10 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.9559 | 4.9559 | 0 | 12 | 1 | 1 | 4.9559 | 10 | 0 | 0
834.35 | 50.03 | 49.84 | 0.62 | 0.9 | 9 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.4559 | 4.4559 | 0 | 12 | 1 | 1 | 4.4559 | 10 | 0 | 0
834.4 | 50.02 | 49.84 | 0.62 | 0.8 | 8 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 3.9559 | 3.9559 | 0 | 12 | 1 | 1 | 3.9559 | 10 | 0 | 0
834.45 | 50.02 | 49.89 | 0.145 | 0.7 | 7 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 3.4559 | 3.4559 | 0 | 12 | 1 | 1 | 3.4559 | 10 | 0 | 0
834.5 | 50.08 | 49.89 | 0.145 | 0.6 | 6 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 2.8088 | 2.8088 | 0 | 12 | 1 | 1 | 2.8088 | 10 | 0 | 0
834.55 | 50.08 | 49.89 | 0.145 | 0.5 | 5 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 2.3088 | 2.3088 | 0 | 12 | 1 | 1 | 2.3088 | 10 | 0 | 0
834.6 | 50.01 | 49.89 | 0.145 | 0.4 | 4 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 1.8088 | 1.8088 | 0 | 12 | 1 | 1 | 1.8088 | 10 | 0 | 0
834.65 | 50.01 | 49.96 | 0.014706 | 0.3 | 3 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 1.3088 | 1.3088 | 0 | 12 | 1 | 1 | 1.3088 | 10 | 0 | 0
834.7 | 49.94 | 49.94 | 0.026471 | 0.2 | 2 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.80882 | 0.80882 | 0 | 12 | 1 | 1 | 0.80882 | 10 | 0 | 0
834.75 | 49.94 | 49.94 | 0.026471 | 0.1 | 1 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.30882 | 0.30882 | 0 | 12 | 1 | 1 | 0.30882 | 10 | 0 | 0
834.8 | 50 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
834.85 | 50 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
834.9 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
834.95 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
835 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
835.05 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
835.1 | 49.92 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
835.15 | 49.92 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
835.2 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50.01 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
835.25 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
835.3 | 49.92 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
835.35 | 49.92 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
835.4 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
835.45 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
835.5 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
835.55 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
835.6 | 49.87 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
835.65 | 49.87 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
835.7 | 49.8 | 49.8 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
835.75 | 49.8 | 49.8 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
835.8 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
835.85 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
835.9 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
835.95 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
836 | 49.72 | 49.72 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
836.05 | 49.72 | 49.72 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
836.1 | 49.67 | 49.67 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
836.15 | 49.67 | 49.67 | 1 | 1 | 10 | 49.87 | 0.335 | 0.14412 | 1.4412 | 5.7206 | 5.7206 | 0 | 12 | 1 | 1 | 5.7206 | 10 | 0 | 0
836.2 | 49.65 | 49.65 | 1 | 1 | 10 | 49.87 | 0.335 | 0.24412 | 2.4412 | 6.2206 | 6.2206 | 0 | 12 | 1 | 1 | 6.2206 | 10 | 0 | 0
836.25 | 49.65 | 49.65 | 1 | 1 | 10 | 49.8 | 1 | 0.34412 | 3.4412 | 6.7206 | 6.7206 | 0 | 12 | 1 | 1 | 6.7206 | 10 | 0 | 0
836.3 | 49.59 | 49.59 | 1 | 1 | 10 | 49.8 | 1 | 0.44412 | 4.4412 | 7.2206 | 7.2206 | 0 | 12 | 1 | 1 | 7.2206 | 10 | 0 | 0
836.35 | 49.59 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.54412 | 5.4412 | 7.7206 | 7.7206 | 0 | 12 | 1 | 1 | 7.7206 | 10 | 0 | 0
836.4 | 49.66 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.64412 | 6.4412 | 8.2206 | 8.2206 | 0 | 12 | 1 | 1 | 8.2206 | 10 | 0 | 0
836.45 | 49.66 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.74412 | 7.4412 | 8.7206 | 8.7206 | 0 | 12 | 1 | 1 | 8.7206 | 10 | 0 | 0
836.5 | 49.63 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.84412 | 8.4412 | 9.2206 | 9.2206 | 0 | 12 | 1 | 1 | 9.2206 | 10 | 0 | 0
836.55 | 49.63 | 49.59 | 1 | 1 | 10 | 49.72 | 1 | 0.94412 | 9.4412 | 9.7206 | 9.7206 | 0 | 12 | 1 | 1 | 9.7206 | 10 | 0 | 0
836.6 | 49.61 | 49.59 | 1 | 1 | 10 | 49.72 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
836.65 | 49.61 | 49.59 | 1 | 1 | 10 | 49.67 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
836.7 | 49.54 | 49.54 | 1 | 1 | 10 | 49.67 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
836.75 | 49.54 | 49.54 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
836.8 | 49.46 | 49.46 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
836.85 | 49.46 | 49.46 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
836.9 | 49.45 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
836.95 | 49.45 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
837 | 49.51 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
837.05 | 49.51 | 49.45 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
837.1 | 49.5 | 49.45 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
837.15 | 49.5 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
837.2 | 49.54 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
837.25 | 49.54 | 49.45 | 1 | 1 | 10 | 49.54 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
837.3 | 49.59 | 49.45 | 1 | 1 | 10 | 49.59 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
837.35 | 49.59 | 49.45 | 1 | 1 | 10 | 49.59 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
837.4 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
837.45 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
837.5 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
837.55 | 49.61 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
837.6 | 49.53 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
837.65 | 49.53 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
837.7 | 49.54 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
837.75 | 49.54 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
837.8 | 49.61 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
837.85 | 49.61 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
837.9 | 49.66 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
837.95 | 49.66 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
838 | 49.64 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
838.05 | 49.64 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
838.1 | 49.69 | 49.53 | 1 | 1 | 10 | 49.69 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
838.15 | 49.69 | 49.53 | 1 | 1 | 10 | 49.69 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
838.2 | 49.74 | 49.53 | 1 | 1 | 10 | 49.74 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
838.25 | 49.74 | 49.54 | 1 | 1 | 10 | 49.74 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
838.3 | 49.78 | 49.54 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
838.35 | 49.78 | 49.61 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
838.4 | 49.82 | 49.61 | 1 | 1 | 10 | 49.82 | 0.81 | 0.81 | 8.1 | 9.05 | 9.05 | 0 | 12 | 1 | 1 | 9.05 | 10 | 0 | 0
838.45 | 49.82 | 49.64 | 1 | 1 | 10 | 49.82 | 0.81 | 0.81 | 8.1 | 9.05 | 9.05 | 0 | 12 | 1 | 1 | 9.05 | 10 | 0 | 0
838.5 | 49.86 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
838.55 | 49.86 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
838.6 | 49.84 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
838.65 | 49.84 | 49.69 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
838.7 | 49.91 | 49.69 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
838.75 | 49.91 | 49.74 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
838.8 | 49.97 | 49.74 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
838.85 | 49.97 | 49.78 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
838.9 | 50.03 | 49.78 | 1 | 1 | 10 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.9559 | 4.9559 | 0 | 12 | 1 | 1 | 4.9559 | 10 | 0 | 0
838.95 | 50.03 | 49.82 | 0.81 | 0.9 | 9 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.4559 | 4.4559 | 0 | 12 | 1 | 1 | 4.4559 | 10 | 0 | 0
839 | 50.05 | 49.82 | 0.81 | 0.81 | 8.1 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 3.9471 | 3.9471 | 0 | 12 | 1 | 1 | 3.9471 | 10 | 0 | 0
839.05 | 50.05 | 49.84 | 0.62 | 0.71 | 7.1 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 3.4471 | 3.4471 | 0 | 12 | 1 | 1 | 3.4471 | 10 | 0 | 0
839.1 | 50.01 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
839.15 | 50.01 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
839.2 | 49.95 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
839.25 | 49.95 | 49.91 | 0.044118 | 0.52 | 5.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.4971 | 2.4971 | 0 | 12 | 1 | 1 | 2.4971 | 10 | 0 | 0
839.3 | 49.99 | 49.91 | 0.044118 | 0.42 | 4.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 1.9971 | 1.9971 | 0 | 12 | 1 | 1 | 1.9971 | 10 | 0 | 0
839.35 | 49.99 | 49.95 | 0.020588 | 0.32 | 3.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 1.4971 | 1.4971 | 0 | 12 | 1 | 1 | 1.4971 | 10 | 0 | 0
839.4 | 49.92 | 49.92 | 0.038235 | 0.22 | 2.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.99706 | 0.99706 | 0 | 12 | 1 | 1 | 0.99706 | 10 | 0 | 0
839.45 | 49.92 | 49.92 | 0.038235 | 0.12 | 1.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.49706 | 0.49706 | 0 | 12 | 1 | 1 | 0.49706 | 10 | 0 | 0
839.5 | 49.97 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
839.55 | 49.97 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
839.6 | 50.02 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
839.65 | 50.02 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.17647 | 0.17647 | 0 | 12 | 1 | 1 | 0.17647 | 10 | 0 | 0
839.7 | 50.07 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
839.75 | 50.07 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
839.8 | 50.06 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
839.85 | 50.06 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
839.9 | 50.13 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
839.95 | 50.13 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
840 | 50.09 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
840.05 | 50.09 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6309 | -1.6309 | 0 | 12 | 1 | 1 | -1.6309 | 10 | 0 | 0
840.1 | 50.07 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6309 | -1.6309 | 0 | 12 | 1 | 1 | -1.6309 | 10 | 0 | 0
840.15 | 50.07 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6897 | -1.6897 | 0 | 12 | 1 | 1 | -1.6897 | 10 | 0 | 0
840.2 | 50.07 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6897 | -1.6897 | 0 | 12 | 1 | 1 | -1.6897 | 10 | 0 | 0
840.25 | 50.07 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.13 | -0.335 | -0.335 | -3.35 | -1.8074 | -1.8074 | 0 | 12 | 1 | 1 | -1.8074 | 10 | 0 | 0
840.3 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.13 | -0.335 | -0.335 | -3.35 | -1.7779 | -1.7779 | 0 | 12 | 1 | 1 | -1.7779 | 10 | 0 | 0
840.35 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.13 | -0.335 | -0.335 | -3.35 | -1.7779 | -1.7779 | 0 | 12 | 1 | 1 | -1.7779 | 10 | 0 | 0
840.4 | 50.01 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
840.45 | 50.01 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
840.5 | 50.07 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
840.55 | 50.07 | 50.01 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.235 | -2.35 | -1.175 | -1.175 | 0 | 12 | 1 | 1 | -1.175 | 10 | 0 | 0
840.6 | 50.05 | 50.01 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.135 | -1.35 | -0.675 | -0.675 | 0 | 12 | 1 | 1 | -0.675 | 10 | 0 | 0
840.65 | 50.05 | 50.01 | 0 | 0 | 0 | 50.07 | -0.032353 | -0.035 | -0.35 | -0.175 | -0.175 | 0 | 12 | 1 | 1 | -0.175 | 10 | 0 | 0
840.7 | 50.1 | 50.01 | 0 | 0 | 0 | 50.1 | -0.05 | -0.05 | -0.5 | -0.25 | -0.25 | 0 | 12 | 1 | 1 | -0.25 | 10 | 0 | 0
840.75 | 50.1 | 50.01 | 0 | 0 | 0 | 50.1 | -0.05 | -0.05 | -0.5 | -0.25 | -0.25 | 0 | 12 | 1 | 1 | -0.25 | 10 | 0 | 0
840.8 | 50.11 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
840.85 | 50.11 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
840.9 | 50.06 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
840.95 | 50.06 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
841 | 50.04 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
841.05 | 50.04 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
841.1 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
841.15 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
841.2 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
841.25 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
841.3 | 50.11 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
841.35 | 50.11 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
841.4 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
841.45 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
841.5 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
841.55 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
841.6 | 50.02 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.11 | -0.145 | -0.145 | -1.45 | -0.73971 | -0.73971 | 0 | 12 | 1 | 1 | -0.73971 | 10 | 0 | 0
841.65 | 50.02 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.11 | -0.145 | -0.145 | -1.45 | -0.73971 | -0.73971 | 0 | 12 | 1 | 1 | -0.73971 | 10 | 0 | 0
841.7 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
841.75 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
841.8 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
841.85 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
841.9 | 50.01 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
841.95 | 50.01 | 50 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.045 | -0.45 | -0.225 | -0.225 | 0 | 12 | 1 | 1 | -0.225 | 10 | 0 | 0
842 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
842.05 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
842.1 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
842.15 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
842.2 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.14706 | 0.14706 | 0 | 12 | 1 | 1 | 0.14706 | 10 | 0 | 0
842.25 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
842.3 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
842.35 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
842.4 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
842.45 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
842.5 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
842.55 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
842.6 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
842.65 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
842.7 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
842.75 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
842.8 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
842.85 | 50 | 50 | 0 | 0 | 0 | 50.01 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
842.9 | 49.5 | 49.5 | 1 | 1 | 10 | 50.01 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
842.95 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
843 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
843.05 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
843.1 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
843.15 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
843.2 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
843.25 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
843.3 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
843.35 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
843.4 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
843.45 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.1 | 1 | 5.5 | 5.5 | 0 | 12 | 1 | 1 | 5.5 | 10 | 0 | 0
843.5 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.2 | 2 | 6 | 6 | 0 | 12 | 1 | 1 | 6 | 10 | 0 | 0
843.55 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.3 | 3 | 6.5 | 6.5 | 0 | 12 | 1 | 1 | 6.5 | 10 | 0 | 0
843.6 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.4 | 4 | 7 | 7 | 0 | 12 | 1 | 1 | 7 | 10 | 0 | 0
843.65 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.5 | 5 | 7.5 | 7.5 | 0 | 12 | 1 | 1 | 7.5 | 10 | 0 | 0
843.7 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.6 | 6 | 8 | 8 | 0 | 12 | 1 | 1 | 8 | 10 | 0 | 0
843.75 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.7 | 7 | 8.5 | 8.5 | 0 | 12 | 1 | 1 | 8.5 | 10 | 0 | 0
843.8 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.8 | 8 | 9 | 9 | 0 | 12 | 1 | 1 | 9 | 10 | 0 | 0
843.85 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.9 | 9 | 9.5 | 9.5 | 0 | 12 | 1 | 1 | 9.5 | 10 | 0 | 0
843.9 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
843.95 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
844 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
844.05 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
844.1 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
844.15 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
844.2 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
844.25 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
844.3 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
844.35 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
844.4 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
844.45 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
844.5 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
844.55 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
844.6 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
844.65 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
844.7 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
844.75 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
844.8 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
844.85 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
844.9 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
844.95 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
845 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
845.05 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
845.1 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
845.15 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
845.2 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
845.25 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
845.3 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
845.35 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
845.4 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
845.45 | 50.5 | 50.5 | -1 | 0.9 | 9 | 50.5 | -1 | -1 | -10 | -0.5 | -0.5 | 0 | 12 | 1 | 1 | -0.5 | 10 | 0 | 0
845.5 | 50.5 | 50.5 | -1 | 0.8 | 8 | 50.5 | -1 | -1 | -10 | -1 | -1 | 0 | 12 | 1 | 1 | -1 | 10 | 0 | 0
845.55 | 50.5 | 50.5 | -1 | 0.7 | 7 | 50.5 | -1 | -1 | -10 | -1.5 | -1.5 | 0 | 12 | 1 | 1 | -1.5 | 10 | 0 | 0
845.6 | 50.5 | 50.5 | -1 | 0.6 | 6 | 50.5 | -1 | -1 | -10 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
845.65 | 50.5 | 50.5 | -1 | 0.5 | 5 | 50.5 | -1 | -1 | -10 | -2.5 | -2.5 | 0 | 12 | 1 | 1 | -2.5 | 10 | 0 | 0
845.7 | 50.5 | 50.5 | -1 | 0.4 | 4 | 50.5 | -1 | -1 | -10 | -3 | -3 | 0 | 12 | 1 | 1 | -3 | 10 | 0 | 0
845.75 | 50.5 | 50.5 | -1 | 0.3 | 3 | 50.5 | -1 | -1 | -10 | -3.5 | -3.5 | 0 | 12 | 1 | 1 | -3.5 | 10 | 0 | 0
845.8 | 50.5 | 50.5 | -1 | 0.2 | 2 | 50.5 | -1 | -1 | -10 | -4 | -4 | 0 | 12 | 1 | 1 | -4 | 10 | 0 | 0
845.85 | 50.5 | 50.5 | -1 | 0.1 | 1 | 50.5 | -1 | -1 | -10 | -4.5 | -4.5 | 0 | 12 | 1 | 1 | -4.5 | 10 | 0 | 0
845.9 | 50.5 | 50.5 | -1 | 0 | 0 | 50.5 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
845.95 | 50.5 | 50.5 | -1 | -0.1 | -1 | 50.5 | -1 | -1 | -10 | -5.5 | -5.5 | 0 | 12 | 1 | 1 | -5.5 | 10 | 0 | 0
846 | 50.5 | 50.5 | -1 | -0.2 | -2 | 50.5 | -1 | -1 | -10 | -6 | -6 | 0 | 12 | 1 | 1 | -6 | 10 | 0 | 0
846.05 | 50.5 | 50.5 | -1 | -0.3 | -3 | 50.5 | -1 | -1 | -10 | -6.5 | -6.5 | 0 | 12 | 1 | 1 | -6.5 | 10 | 0 | 0
846.1 | 50.5 | 50.5 | -1 | -0.4 | -4 | 50.5 | -1 | -1 | -10 | -7 | -7 | 0 | 12 | 1 | 1 | -7 | 10 | 0 | 0
846.15 | 50.5 | 50.5 | -1 | -0.5 | -5 | 50.5 | -1 | -1 | -10 | -7.5 | -7.5 | 0 | 12 | 1 | 1 | -7.5 | 10 | 0 | 0
846.2 | 50.5 | 50.5 | -1 | -0.6 | -6 | 50.5 | -1 | -1 | -10 | -8 | -8 | 0 | 12 | 1 | 1 | -8 | 10 | 0 | 0
846.25 | 50.5 | 50.5 | -1 | -0.7 | -7 | 50.5 | -1 | -1 | -10 | -8.5 | -8.5 | 0 | 12 | 1 | 1 | -8.5 | 10 | 0 | 0
846.3 | 50.5 | 50.5 | -1 | -0.8 | -8 | 50.5 | -1 | -1 | -10 | -9 | -9 | 0 | 12 | 1 | 1 | -9 | 10 | 0 | 0
846.35 | 50.5 | 50.5 | -1 | -0.9 | -9 | 50.5 | -1 | -1 | -10 | -9.5 | -9.5 | 0 | 12 | 1 | 1 | -9.5 | 10 | 0 | 0
846.4 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
846.45 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
846.5 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
846.55 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
846.6 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
846.65 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
846.7 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
846.75 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
846.8 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
846.85 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
846.9 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
846.95 | 50.47 | 50.47 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
847 | 50.45 | 50.45 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
847.05 | 50.42 | 50.42 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
847.1 | 50.4 | 50.4 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
847.15 | 50.37 | 50.37 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
847.2 | 50.35 | 50.35 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
847.25 | 50.32 | 50.32 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
847.3 | 50.29 | 50.29 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
847.35 | 50.27 | 50.27 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
847.4 | 50.24 | 50.24 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
847.45 | 50.22 | 50.22 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
847.5 | 50.19 | 50.19 | -0.905 | -0.905 | -9.05 | 50.47 | -1 | -1 | -10 | -9.525 | -9.525 | 0 | 12 | 1 | 1 | -9.525 | 10 | 0 | 0
847.55 | 50.17 | 50.17 | -0.715 | -0.715 | -7.15 | 50.45 | -1 | -1 | -10 | -8.575 | -8.575 | 0 | 12 | 1 | 1 | -8.575 | 10 | 0 | 0
847.6 | 50.14 | 50.14 | -0.43 | -0.43 | -4.3 | 50.42 | -1 | -1 | -10 | -7.15 | -7.15 | 0 | 12 | 1 | 1 | -7.15 | 10 | 0 | 0
847.65 | 50.12 | 50.12 | -0.24 | -0.24 | -2.4 | 50.4 | -1 | -1 | -10 | -6.2 | -6.2 | 0 | 12 | 1 | 1 | -6.2 | 10 | 0 | 0
847.7 | 50.09 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 50.37 | -1 | -1 | -10 | -5.2206 | -5.2206 | 0 | 12 | 1 | 1 | -5.2206 | 10 | 0 | 0
847.75 | 50.06 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.35 | -1 | -1 | -10 | -5.1324 | -5.1324 | 0 | 12 | 1 | 1 | -5.1324 | 10 | 0 | 0
847.8 | 50.04 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.32 | -1 | -1 | -10 | -5.0735 | -5.0735 | 0 | 12 | 1 | 1 | -5.0735 | 10 | 0 | 0
847.85 | 50.01 | 50.01 | 0 | 0 | 0 | 50.29 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
847.9 | 49.99 | 49.99 | 0 | 0 | 0 | 50.27 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
847.95 | 49.96 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.24 | -1 | -1 | -10 | -4.9265 | -4.9265 | 0 | 12 | 1 | 1 | -4.9265 | 10 | 0 | 0
848 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.22 | -1 | -1 | -10 | -4.8676 | -4.8676 | 0 | 12 | 1 | 1 | -4.8676 | 10 | 0 | 0
848.05 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.19 | -0.905 | -0.905 | -9.05 | -4.3044 | -4.3044 | 0 | 12 | 1 | 1 | -4.3044 | 10 | 0 | 0
848.1 | 49.88 | 49.88 | 0.24 | 0.24 | 2.4 | 50.17 | -0.715 | -0.805 | -8.05 | -2.825 | -2.825 | 0 | 12 | 1 | 1 | -2.825 | 10 | 0 | 0
848.15 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.14 | -0.43 | -0.705 | -7.05 | -1.375 | -1.375 | 0 | 12 | 1 | 1 | -1.375 | 10 | 0 | 0
848.2 | 49.83 | 49.83 | 0.715 | 0.715 | 7.15 | 50.12 | -0.24 | -0.605 | -6.05 | 0.55 | 0.55 | 0 | 12 | 1 | 1 | 0.55 | 10 | 0 | 0
848.25 | 49.81 | 49.81 | 0.905 | 0.905 | 9.05 | 50.09 | -0.044118 | -0.505 | -5.05 | 2 | 2 | 0 | 12 | 1 | 1 | 2 | 10 | 0 | 0
848.3 | 49.78 | 49.78 | 1 | 1 | 10 | 50.06 | -0.026471 | -0.405 | -4.05 | 2.975 | 2.975 | 0 | 12 | 1 | 1 | 2.975 | 10 | 0 | 0
848.35 | 49.76 | 49.76 | 1 | 1 | 10 | 50.04 | -0.014706 | -0.305 | -3.05 | 3.475 | 3.475 | 0 | 12 | 1 | 1 | 3.475 | 10 | 0 | 0
848.4 | 49.73 | 49.73 | 1 | 1 | 10 | 50.01 | 0 | -0.205 | -2.05 | 3.975 | 3.975 | 0 | 12 | 1 | 1 | 3.975 | 10 | 0 | 0
848.45 | 49.71 | 49.71 | 1 | 1 | 10 | 49.99 | 0 | -0.105 | -1.05 | 4.475 | 4.475 | 0 | 12 | 1 | 1 | 4.475 | 10 | 0 | 0
848.5 | 49.68 | 49.68 | 1 | 1 | 10 | 49.96 | 0.014706 | -0.005 | -0.05 | 4.975 | 4.975 | 0 | 12 | 1 | 1 | 4.975 | 10 | 0 | 0
848.55 | 49.65 | 49.65 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
848.6 | 49.63 | 49.63 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
848.65 | 49.6 | 49.6 | 1 | 1 | 10 | 49.88 | 0.24 | 0.14412 | 1.4412 | 5.7206 | 5.7206 | 0 | 12 | 1 | 1 | 5.7206 | 10 | 0 | 0
848.7 | 49.58 | 49.58 | 1 | 1 | 10 | 49.86 | 0.43 | 0.24412 | 2.4412 | 6.2206 | 6.2206 | 0 | 12 | 1 | 1 | 6.2206 | 10 | 0 | 0
848.75 | 49.55 | 49.55 | 1 | 1 | 10 | 49.83 | 0.715 | 0.34412 | 3.4412 | 6.7206 | 6.7206 | 0 | 12 | 1 | 1 | 6.7206 | 10 | 0 | 0
848.8 | 49.53 | 49.53 | 1 | 1 | 10 | 49.81 | 0.905 | 0.44412 | 4.4412 | 7.2206 | 7.2206 | 0 | 12 | 1 | 1 | 7.2206 | 10 | 0 | 0
848.85 | 49.5 | 49.5 | 1 | 1 | 10 | 49.78 | 1 | 0.54412 | 5.4412 | 7.7206 | 7.7206 | 0 | 12 | 1 | 1 | 7.7206 | 10 | 0 | 0
848.9 | 49.5 | 49.5 | 1 | 1 | 10 | 49.76 | 1 | 0.64412 | 6.4412 | 8.2206 | 8.2206 | 0 | 12 | 1 | 1 | 8.2206 | 10 | 0 | 0
848.95 | 49.53 | 49.5 | 1 | 1 | 10 | 49.73 | 1 | 0.74412 | 7.4412 | 8.7206 | 8.7206 | 0 | 12 | 1 | 1 | 8.7206 | 10 | 0 | 0
849 | 49.55 | 49.5 | 1 | 1 | 10 | 49.71 | 1 | 0.84412 | 8.4412 | 9.2206 | 9.2206 | 0 | 12 | 1 | 1 | 9.2206 | 10 | 0 | 0
849.05 | 49.58 | 49.5 | 1 | 1 | 10 | 49.68 | 1 | 0.94412 | 9.4412 | 9.7206 | 9.7206 | 0 | 12 | 1 | 1 | 9.7206 | 10 | 0 | 0
849.1 | 49.6 | 49.5 | 1 | 1 | 10 | 49.65 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
849.15 | 49.63 | 49.5 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
849.2 | 49.65 | 49.5 | 1 | 1 | 10 | 49.65 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
849.25 | 49.68 | 49.5 | 1 | 1 | 10 | 49.68 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
849.3 | 49.71 | 49.5 | 1 | 1 | 10 | 49.71 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
849.35 | 49.73 | 49.5 | 1 | 1 | 10 | 49.73 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
849.4 | 49.76 | 49.5 | 1 | 1 | 10 | 49.76 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
849.45 | 49.78 | 49.5 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
849.5 | 49.81 | 49.53 | 1 | 1 | 10 | 49.81 | 0.905 | 0.905 | 9.05 | 9.525 | 9.525 | 0 | 12 | 1 | 1 | 9.525 | 10 | 0 | 0
849.55 | 49.83 | 49.55 | 1 | 1 | 10 | 49.83 | 0.715 | 0.715 | 7.15 | 8.575 | 8.575 | 0 | 12 | 1 | 1 | 8.575 | 10 | 0 | 0
849.6 | 49.86 | 49.58 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
849.65 | 49.88 | 49.6 | 1 | 1 | 10 | 49.88 | 0.24 | 0.24 | 2.4 | 6.2 | 6.2 | 0 | 12 | 1 | 1 | 6.2 | 10 | 0 | 0
849.7 | 49.91 | 49.63 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
849.75 | 49.94 | 49.65 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
849.8 | 49.96 | 49.68 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
849.85 | 49.99 | 49.71 | 1 | 1 | 10 | 49.99 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
849.9 | 50.01 | 49.73 | 1 | 1 | 10 | 50.01 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
849.95 | 50.04 | 49.76 | 1 | 1 | 10 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 4.9265 | 4.9265 | 0 | 12 | 1 | 1 | 4.9265 | 10 | 0 | 0
850 | 50.06 | 49.78 | 1 | 1 | 10 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 4.8676 | 4.8676 | 0 | 12 | 1 | 1 | 4.8676 | 10 | 0 | 0
850.05 | 50.09 | 49.81 | 0.905 | 0.905 | 9.05 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 4.3044 | 4.3044 | 0 | 12 | 1 | 1 | 4.3044 | 10 | 0 | 0
850.1 | 50.12 | 49.83 | 0.715 | 0.805 | 8.05 | 50.12 | -0.24 | -0.24 | -2.4 | 2.825 | 2.825 | 0 | 12 | 1 | 1 | 2.825 | 10 | 0 | 0
850.15 | 50.14 | 49.86 | 0.43 | 0.705 | 7.05 | 50.14 | -0.43 | -0.43 | -4.3 | 1.375 | 1.375 | 0 | 12 | 1 | 1 | 1.375 | 10 | 0 | 0
850.2 | 50.17 | 49.88 | 0.24 | 0.605 | 6.05 | 50.17 | -0.715 | -0.715 | -7.15 | -0.55 | -0.55 | 0 | 12 | 1 | 1 | -0.55 | 10 | 0 | 0
850.25 | 50.19 | 49.91 | 0.044118 | 0.505 | 5.05 | 50.19 | -0.905 | -0.905 | -9.05 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
850.3 | 50.22 | 49.94 | 0.026471 | 0.405 | 4.05 | 50.22 | -1 | -1 | -10 | -2.975 | -2.975 | 0 | 12 | 1 | 1 | -2.975 | 10 | 0 | 0
850.35 | 50.24 | 49.96 | 0.014706 | 0.305 | 3.05 | 50.24 | -1 | -1 | -10 | -3.475 | -3.475 | 0 | 12 | 1 | 1 | -3.475 | 10 | 0 | 0
850.4 | 50.27 | 49.99 | 0 | 0.205 | 2.05 | 50.27 | -1 | -1 | -10 | -3.975 | -3.975 | 0 | 12 | 1 | 1 | -3.975 | 10 | 0 | 0
850.45 | 50.29 | 50.01 | 0 | 0.105 | 1.05 | 50.29 | -1 | -1 | -10 | -4.475 | -4.475 | 0 | 12 | 1 | 1 | -4.475 | 10 | 0 | 0
850.5 | 50.32 | 50.04 | -0.014706 | 0.005 | 0.05 | 50.32 | -1 | -1 | -10 | -4.975 | -4.975 | 0 | 12 | 1 | 1 | -4.975 | 10 | 0 | 0
850.55 | 50.35 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.35 | -1 | -1 | -10 | -5.1324 | -5.1324 | 0 | 12 | 1 | 1 | -5.1324 | 10 | 0 | 0
850.6 | 50.37 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 50.37 | -1 | -1 | -10 | -5.2206 | -5.2206 | 0 | 12 | 1 | 1 | -5.2206 | 10 | 0 | 0
850.65 | 50.4 | 50.12 | -0.24 | -0.14412 | -1.4412 | 50.4 | -1 | -1 | -10 | -5.7206 | -5.7206 | 0 | 12 | 1 | 1 | -5.7206 | 10 | 0 | 0
850.7 | 50.42 | 50.14 | -0.43 | -0.24412 | -2.4412 | 50.42 | -1 | -1 | -10 | -6.2206 | -6.2206 | 0 | 12 | 1 | 1 | -6.2206 | 10 | 0 | 0
850.75 | 50.45 | 50.17 | -0.715 | -0.34412 | -3.4412 | 50.45 | -1 | -1 | -10 | -6.7206 | -6.7206 | 0 | 12 | 1 | 1 | -6.7206 | 10 | 0 | 0
850.8 | 50.47 | 50.19 | -0.905 | -0.44412 | -4.4412 | 50.47 | -1 | -1 | -10 | -7.2206 | -7.2206 | 0 | 12 | 1 | 1 | -7.2206 | 10 | 0 | 0
850.85 | 50.5 | 50.22 | -1 | -0.54412 | -5.4412 | 50.5 | -1 | -1 | -10 | -7.7206 | -7.7206 | 0 | 12 | 1 | 1 | -7.7206 | 10 | 0 | 0
850.9 | 50.5 | 50.24 | -1 | -0.64412 | -6.4412 | 50.5 | -1 | -1 | -10 | -8.2206 | -8.2206 | 0 | 12 | 1 | 1 | -8.2206 | 10 | 0 | 0
850.95 | 50.47 | 50.27 | -1 | -0.74412 | -7.4412 | 50.5 | -1 | -1 | -10 | -8.7206 | -8.7206 | 0 | 12 | 1 | 1 | -8.7206 | 10 | 0 | 0
851 | 50.45 | 50.29 | -1 | -0.84412 | -8.4412 | 50.5 | -1 | -1 | -10 | -9.2206 | -9.2206 | 0 | 12 | 1 | 1 | -9.2206 | 10 | 0 | 0
851.05 | 50.42 | 50.32 | -1 | -0.94412 | -9.4412 | 50.5 | -1 | -1 | -10 | -9.7206 | -9.7206 | 0 | 12 | 1 | 1 | -9.7206 | 10 | 0 | 0
851.1 | 50.39 | 50.35 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
851.15 | 50.37 | 50.37 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
851.2 | 50.34 | 50.34 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
851.25 | 50.32 | 50.32 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
851.3 | 50.29 | 50.29 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
851.35 | 50.26 | 50.26 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
851.4 | 50.24 | 50.24 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
851.45 | 50.21 | 50.21 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
851.5 | 50.18 | 50.18 | -0.81 | -0.81 | -8.1 | 50.47 | -1 | -1 | -10 | -9.05 | -9.05 | 0 | 12 | 1 | 1 | -9.05 | 10 | 0 | 0
851.55 | 50.16 | 50.16 | -0.62 | -0.62 | -6.2 | 50.45 | -1 | -1 | -10 | -8.1 | -8.1 | 0 | 12 | 1 | 1 | -8.1 | 10 | 0 | 0
851.6 | 50.13 | 50.13 | -0.335 | -0.335 | -3.35 | 50.42 | -1 | -1 | -10 | -6.675 | -6.675 | 0 | 12 | 1 | 1 | -6.675 | 10 | 0 | 0
851.65 | 50.11 | 50.11 | -0.145 | -0.145 | -1.45 | 50.39 | -1 | -1 | -10 | -5.725 | -5.725 | 0 | 12 | 1 | 1 | -5.725 | 10 | 0 | 0
851.7 | 50.08 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 50.37 | -1 | -1 | -10 | -5.1912 | -5.1912 | 0 | 12 | 1 | 1 | -5.1912 | 10 | 0 | 0
851.75 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.34 | -1 | -1 | -10 | -5.1029 | -5.1029 | 0 | 12 | 1 | 1 | -5.1029 | 10 | 0 | 0
851.8 | 50.03 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 50.32 | -1 | -1 | -10 | -5.0441 | -5.0441 | 0 | 12 | 1 | 1 | -5.0441 | 10 | 0 | 0
851.85 | 50 | 50 | 0 | 0 | 0 | 50.29 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
851.9 | 50 | 50 | 0 | 0 | 0 | 50.26 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
851.95 | 50 | 50 | 0 | 0 | 0 | 50.24 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
852 | 50 | 50 | 0 | 0 | 0 | 50.21 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
852.05 | 50 | 50 | 0 | 0 | 0 | 50.18 | -0.81 | -0.9 | -9 | -4.5 | -4.5 | 0 | 12 | 1 | 1 | -4.5 | 10 | 0 | 0
852.1 | 50 | 50 | 0 | 0 | 0 | 50.16 | -0.62 | -0.8 | -8 | -4 | -4 | 0 | 12 | 1 | 1 | -4 | 10 | 0 | 0
852.15 | 50 | 50 | 0 | 0 | 0 | 50.13 | -0.335 | -0.7 | -7 | -3.5 | -3.5 | 0 | 12 | 1 | 1 | -3.5 | 10 | 0 | 0
852.2 | 50.01 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.6 | -6 | -3 | -3 | 0 | 12 | 1 | 1 | -3 | 10 | 0 | 0
852.25 | 50.01 | 50 | 0 | 0 | 0 | 50.08 | -0.038235 | -0.5 | -5 | -2.5 | -2.5 | 0 | 12 | 1 | 1 | -2.5 | 10 | 0 | 0
852.3 | 49.99 | 49.99 | 0 | 0 | 0 | 50.05 | -0.020588 | -0.4 | -4 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
852.35 | 49.99 | 49.99 | 0 | 0 | 0 | 50.03 | -0.0088235 | -0.3 | -3 | -1.5 | -1.5 | 0 | 12 | 1 | 1 | -1.5 | 10 | 0 | 0
852.4 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | -0.2 | -2 | -0.83824 | -0.83824 | 0 | 12 | 1 | 1 | -0.83824 | 10 | 0 | 0
852.45 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | -0.1 | -1 | -0.33824 | -0.33824 | 0 | 12 | 1 | 1 | -0.33824 | 10 | 0 | 0
852.5 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
852.55 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
852.6 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
852.65 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
852.7 | 49.89 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
852.75 | 49.89 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
852.8 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50.01 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
852.85 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
852.9 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
852.95 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 2.7868 | 2.7868 | 0 | 12 | 1 | 1 | 2.7868 | 10 | 0 | 0
853 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 2.7868 | 2.7868 | 0 | 12 | 1 | 1 | 2.7868 | 10 | 0 | 0
853.05 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 2.8456 | 2.8456 | 0 | 12 | 1 | 1 | 2.8456 | 10 | 0 | 0
853.1 | 49.94 | 49.85 | 0.525 | 0.525 | 5.25 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 2.7574 | 2.7574 | 0 | 12 | 1 | 1 | 2.7574 | 10 | 0 | 0
853.15 | 49.94 | 49.85 | 0.525 | 0.525 | 5.25 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 2.7574 | 2.7574 | 0 | 12 | 1 | 1 | 2.7574 | 10 | 0 | 0
853.2 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
853.25 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
853.3 | 49.93 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
853.35 | 49.93 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
853.4 | 49.96 | 49.85 | 0.525 | 0.525 | 5.25 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 2.6985 | 2.6985 | 0 | 12 | 1 | 1 | 2.6985 | 10 | 0 | 0
853.45 | 49.96 | 49.85 | 0.525 | 0.525 | 5.25 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 2.6985 | 2.6985 | 0 | 12 | 1 | 1 | 2.6985 | 10 | 0 | 0
853.5 | 49.99 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
853.55 | 49.99 | 49.91 | 0.044118 | 0.425 | 4.25 | 49.99 | 0 | 0 | 0 | 2.125 | 2.125 | 0 | 12 | 1 | 1 | 2.125 | 10 | 0 | 0
853.6 | 49.99 | 49.91 | 0.044118 | 0.325 | 3.25 | 49.99 | 0 | 0 | 0 | 1.625 | 1.625 | 0 | 12 | 1 | 1 | 1.625 | 10 | 0 | 0
853.65 | 49.99 | 49.93 | 0.032353 | 0.225 | 2.25 | 49.99 | 0 | 0 | 0 | 1.125 | 1.125 | 0 | 12 | 1 | 1 | 1.125 | 10 | 0 | 0
853.7 | 49.96 | 49.93 | 0.032353 | 0.125 | 1.25 | 49.99 | 0 | 0 | 0 | 0.625 | 0.625 | 0 | 12 | 1 | 1 | 0.625 | 10 | 0 | 0
853.75 | 49.96 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 49.99 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
853.8 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
853.85 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
853.9 | 50.05 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.058824 | 0.058824 | 0 | 12 | 1 | 1 | 0.058824 | 10 | 0 | 0
853.95 | 50.05 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
854 | 49.97 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
854.05 | 49.97 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
854.1 | 49.92 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
854.15 | 49.92 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
854.2 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
854.25 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
854.3 | 49.94 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
854.35 | 49.94 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
854.4 | 50.01 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
854.45 | 50.01 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
854.5 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
854.55 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
854.6 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
854.65 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
854.7 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
854.75 | 49.95 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
854.8 | 49.97 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
854.85 | 49.97 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
854.9 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
854.95 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
855 | 49.87 | 49.87 | 0.335 | 0.335 | 3.35 | 50.01 | 0 | 0 | 0 | 1.675 | 1.675 | 0 | 12 | 1 | 1 | 1.675 | 10 | 0 | 0
855.05 | 49.87 | 49.87 | 0.335 | 0.335 | 3.35 | 49.99 | 0 | 0 | 0 | 1.675 | 1.675 | 0 | 12 | 1 | 1 | 1.675 | 10 | 0 | 0
855.1 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
855.15 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 2.6691 | 2.6691 | 0 | 12 | 1 | 1 | 2.6691 | 10 | 0 | 0
855.2 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
855.25 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
855.3 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
855.35 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
855.4 | 49.84 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
855.45 | 49.84 | 49.79 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
855.5 | 49.89 | 49.79 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
855.55 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.12647 | 1.2647 | 5.6324 | 5.6324 | 0 | 12 | 1 | 1 | 5.6324 | 10 | 0 | 0
855.6 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.145 | 1.45 | 5.725 | 5.725 | 0 | 12 | 1 | 1 | 5.725 | 10 | 0 | 0
855.65 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.145 | 1.45 | 5.725 | 5.725 | 0 | 12 | 1 | 1 | 5.725 | 10 | 0 | 0
855.7 | 49.96 | 49.79 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
855.75 | 49.96 | 49.79 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
855.8 | 50.02 | 49.79 | 1 | 1 | 10 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 4.9853 | 4.9853 | 0 | 12 | 1 | 1 | 4.9853 | 10 | 0 | 0
855.85 | 50.02 | 49.79 | 1 | 1 | 10 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 4.9853 | 4.9853 | 0 | 12 | 1 | 1 | 4.9853 | 10 | 0 | 0
855.9 | 50.03 | 49.79 | 1 | 1 | 10 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.9559 | 4.9559 | 0 | 12 | 1 | 1 | 4.9559 | 10 | 0 | 0
855.95 | 50.03 | 49.84 | 0.62 | 0.9 | 9 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.4559 | 4.4559 | 0 | 12 | 1 | 1 | 4.4559 | 10 | 0 | 0
856 | 50.02 | 49.84 | 0.62 | 0.8 | 8 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 3.9559 | 3.9559 | 0 | 12 | 1 | 1 | 3.9559 | 10 | 0 | 0
856.05 | 50.02 | 49.89 | 0.145 | 0.7 | 7 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 3.4559 | 3.4559 | 0 | 12 | 1 | 1 | 3.4559 | 10 | 0 | 0
856.1 | 50.08 | 49.89 | 0.145 | 0.6 | 6 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 2.8088 | 2.8088 | 0 | 12 | 1 | 1 | 2.8088 | 10 | 0 | 0
856.15 | 50.08 | 49.89 | 0.145 | 0.5 | 5 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 2.3088 | 2.3088 | 0 | 12 | 1 | 1 | 2.3088 | 10 | 0 | 0
856.2 | 50.01 | 49.89 | 0.145 | 0.4 | 4 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 1.8088 | 1.8088 | 0 | 12 | 1 | 1 | 1.8088 | 10 | 0 | 0
856.25 | 50.01 | 49.96 | 0.014706 | 0.3 | 3 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 1.3088 | 1.3088 | 0 | 12 | 1 | 1 | 1.3088 | 10 | 0 | 0
856.3 | 49.94 | 49.94 | 0.026471 | 0.2 | 2 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.80882 | 0.80882 | 0 | 12 | 1 | 1 | 0.80882 | 10 | 0 | 0
856.35 | 49.94 | 49.94 | 0.026471 | 0.1 | 1 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.30882 | 0.30882 | 0 | 12 | 1 | 1 | 0.30882 | 10 | 0 | 0
856.4 | 50 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
856.45 | 50 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
856.5 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
856.55 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
856.6 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
856.65 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
856.7 | 49.92 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
856.75 | 49.92 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
856.8 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50.01 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
856.85 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
856.9 | 49.92 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
856.95 | 49.92 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
857 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
857.05 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
857.1 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
857.15 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
857.2 | 49.87 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
857.25 | 49.87 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
857.3 | 49.8 | 49.8 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
857.35 | 49.8 | 49.8 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
857.4 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
857.45 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
857.5 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
857.55 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
857.6 | 49.72 | 49.72 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
857.65 | 49.72 | 49.72 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
857.7 | 49.67 | 49.67 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
857.75 | 49.67 | 49.67 | 1 | 1 | 10 | 49.87 | 0.335 | 0.14412 | 1.4412 | 5.7206 | 5.7206 | 0 | 12 | 1 | 1 | 5.7206 | 10 | 0 | 0
857.8 | 49.65 | 49.65 | 1 | 1 | 10 | 49.87 | 0.335 | 0.24412 | 2.4412 | 6.2206 | 6.2206 | 0 | 12 | 1 | 1 | 6.2206 | 10 | 0 | 0
857.85 | 49.65 | 49.65 | 1 | 1 | 10 | 49.8 | 1 | 0.34412 | 3.4412 | 6.7206 | 6.7206 | 0 | 12 | 1 | 1 | 6.7206 | 10 | 0 | 0
857.9 | 49.59 | 49.59 | 1 | 1 | 10 | 49.8 | 1 | 0.44412 | 4.4412 | 7.2206 | 7.2206 | 0 | 12 | 1 | 1 | 7.2206 | 10 | 0 | 0
857.95 | 49.59 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.54412 | 5.4412 | 7.7206 | 7.7206 | 0 | 12 | 1 | 1 | 7.7206 | 10 | 0 | 0
858 | 49.66 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.64412 | 6.4412 | 8.2206 | 8.2206 | 0 | 12 | 1 | 1 | 8.2206 | 10 | 0 | 0
858.05 | 49.66 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.74412 | 7.4412 | 8.7206 | 8.7206 | 0 | 12 | 1 | 1 | 8.7206 | 10 | 0 | 0
858.1 | 49.63 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.84412 | 8.4412 | 9.2206 | 9.2206 | 0 | 12 | 1 | 1 | 9.2206 | 10 | 0 | 0
858.15 | 49.63 | 49.59 | 1 | 1 | 10 | 49.72 | 1 | 0.94412 | 9.4412 | 9.7206 | 9.7206 | 0 | 12 | 1 | 1 | 9.7206 | 10 | 0 | 0
858.2 | 49.61 | 49.59 | 1 | 1 | 10 | 49.72 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
858.25 | 49.61 | 49.59 | 1 | 1 | 10 | 49.67 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
858.3 | 49.54 | 49.54 | 1 | 1 | 10 | 49.67 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
858.35 | 49.54 | 49.54 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
858.4 | 49.46 | 49.46 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
858.45 | 49.46 | 49.46 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
858.5 | 49.45 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
858.55 | 49.45 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
858.6 | 49.51 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
858.65 | 49.51 | 49.45 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
858.7 | 49.5 | 49.45 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
858.75 | 49.5 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
858.8 | 49.54 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
858.85 | 49.54 | 49.45 | 1 | 1 | 10 | 49.54 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
858.9 | 49.59 | 49.45 | 1 | 1 | 10 | 49.59 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
858.95 | 49.59 | 49.45 | 1 | 1 | 10 | 49.59 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
859 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
859.05 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
859.1 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
859.15 | 49.61 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
859.2 | 49.53 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
859.25 | 49.53 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
859.3 | 49.54 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
859.35 | 49.54 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
859.4 | 49.61 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
859.45 | 49.61 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
859.5 | 49.66 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
859.55 | 49.66 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
859.6 | 49.64 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
859.65 | 49.64 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
859.7 | 49.69 | 49.53 | 1 | 1 | 10 | 49.69 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
859.75 | 49.69 | 49.53 | 1 | 1 | 10 | 49.69 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
859.8 | 49.74 | 49.53 | 1 | 1 | 10 | 49.74 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
859.85 | 49.74 | 49.54 | 1 | 1 | 10 | 49.74 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
859.9 | 49.78 | 49.54 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
859.95 | 49.78 | 49.61 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
860 | 49.82 | 49.61 | 1 | 1 | 10 | 49.82 | 0.81 | 0.81 | 8.1 | 9.05 | 9.05 | 0 | 12 | 1 | 1 | 9.05 | 10 | 0 | 0
860.05 | 49.82 | 49.64 | 1 | 1 | 10 | 49.82 | 0.81 | 0.81 | 8.1 | 9.05 | 9.05 | 0 | 12 | 1 | 1 | 9.05 | 10 | 0 | 0
860.1 | 49.86 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
860.15 | 49.86 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
860.2 | 49.84 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
860.25 | 49.84 | 49.69 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
860.3 | 49.91 | 49.69 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
860.35 | 49.91 | 49.74 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
860.4 | 49.97 | 49.74 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
860.45 | 49.97 | 49.78 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
860.5 | 50.03 | 49.78 | 1 | 1 | 10 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.9559 | 4.9559 | 0 | 12 | 1 | 1 | 4.9559 | 10 | 0 | 0
860.55 | 50.03 | 49.82 | 0.81 | 0.9 | 9 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.4559 | 4.4559 | 0 | 12 | 1 | 1 | 4.4559 | 10 | 0 | 0
860.6 | 50.05 | 49.82 | 0.81 | 0.81 | 8.1 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 3.9471 | 3.9471 | 0 | 12 | 1 | 1 | 3.9471 | 10 | 0 | 0
860.65 | 50.05 | 49.84 | 0.62 | 0.71 | 7.1 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 3.4471 | 3.4471 | 0 | 12 | 1 | 1 | 3.4471 | 10 | 0 | 0
860.7 | 50.01 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
860.75 | 50.01 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
860.8 | 49.95 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
860.85 | 49.95 | 49.91 | 0.044118 | 0.52 | 5.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.4971 | 2.4971 | 0 | 12 | 1 | 1 | 2.4971 | 10 | 0 | 0
860.9 | 49.99 | 49.91 | 0.044118 | 0.42 | 4.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 1.9971 | 1.9971 | 0 | 12 | 1 | 1 | 1.9971 | 10 | 0 | 0
860.95 | 49.99 | 49.95 | 0.020588 | 0.32 | 3.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 1.4971 | 1.4971 | 0 | 12 | 1 | 1 | 1.4971 | 10 | 0 | 0
861 | 49.92 | 49.92 | 0.038235 | 0.22 | 2.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.99706 | 0.99706 | 0 | 12 | 1 | 1 | 0.99706 | 10 | 0 | 0
861.05 | 49.92 | 49.92 | 0.038235 | 0.12 | 1.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.49706 | 0.49706 | 0 | 12 | 1 | 1 | 0.49706 | 10 | 0 | 0
861.1 | 49.97 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
861.15 | 49.97 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
861.2 | 50.02 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
861.25 | 50.02 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.17647 | 0.17647 | 0 | 12 | 1 | 1 | 0.17647 | 10 | 0 | 0
861.3 | 50.07 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
861.35 | 50.07 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
861.4 | 50.06 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
861.45 | 50.06 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
861.5 | 50.13 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
861.55 | 50.13 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
861.6 | 50.09 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
861.65 | 50.09 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6309 | -1.6309 | 0 | 12 | 1 | 1 | -1.6309 | 10 | 0 | 0
861.7 | 50.07 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6309 | -1.6309 | 0 | 12 | 1 | 1 | -1.6309 | 10 | 0 | 0
861.75 | 50.07 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6897 | -1.6897 | 0 | 12 | 1 | 1 | -1.6897 | 10 | 0 | 0
861.8 | 50.07 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6897 | -1.6897 | 0 | 12 | 1 | 1 | -1.6897 | 10 | 0 | 0
861.85 | 50.07 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.13 | -0.335 | -0.335 | -3.35 | -1.8074 | -1.8074 | 0 | 12 | 1 | 1 | -1.8074 | 10 | 0 | 0
861.9 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.13 | -0.335 | -0.335 | -3.35 | -1.7779 | -1.7779 | 0 | 12 | 1 | 1 | -1.7779 | 10 | 0 | 0
861.95 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.13 | -0.335 | -0.335 | -3.35 | -1.7779 | -1.7779 | 0 | 12 | 1 | 1 | -1.7779 | 10 | 0 | 0
862 | 50.01 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
862.05 | 50.01 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
862.1 | 50.07 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
862.15 | 50.07 | 50.01 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.235 | -2.35 | -1.175 | -1.175 | 0 | 12 | 1 | 1 | -1.175 | 10 | 0 | 0
862.2 | 50.05 | 50.01 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.135 | -1.35 | -0.675 | -0.675 | 0 | 12 | 1 | 1 | -0.675 | 10 | 0 | 0
862.25 | 50.05 | 50.01 | 0 | 0 | 0 | 50.07 | -0.032353 | -0.035 | -0.35 | -0.175 | -0.175 | 0 | 12 | 1 | 1 | -0.175 | 10 | 0 | 0
862.3 | 50.1 | 50.01 | 0 | 0 | 0 | 50.1 | -0.05 | -0.05 | -0.5 | -0.25 | -0.25 | 0 | 12 | 1 | 1 | -0.25 | 10 | 0 | 0
862.35 | 50.1 | 50.01 | 0 | 0 | 0 | 50.1 | -0.05 | -0.05 | -0.5 | -0.25 | -0.25 | 0 | 12 | 1 | 1 | -0.25 | 10 | 0 | 0
862.4 | 50.11 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
862.45 | 50.11 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
862.5 | 50.06 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
862.55 | 50.06 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
862.6 | 50.04 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
862.65 | 50.04 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
862.7 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
862.75 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
862.8 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
862.85 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
862.9 | 50.11 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
862.95 | 50.11 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
863 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
863.05 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
863.1 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
863.15 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
863.2 | 50.02 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.11 | -0.145 | -0.145 | -1.45 | -0.73971 | -0.73971 | 0 | 12 | 1 | 1 | -0.73971 | 10 | 0 | 0
863.25 | 50.02 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.11 | -0.145 | -0.145 | -1.45 | -0.73971 | -0.73971 | 0 | 12 | 1 | 1 | -0.73971 | 10 | 0 | 0
863.3 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
863.35 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
863.4 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
863.45 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
863.5 | 50.01 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
863.55 | 50.01 | 50 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.045 | -0.45 | -0.225 | -0.225 | 0 | 12 | 1 | 1 | -0.225 | 10 | 0 | 0
863.6 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
863.65 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
863.7 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
863.75 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
863.8 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.14706 | 0.14706 | 0 | 12 | 1 | 1 | 0.14706 | 10 | 0 | 0
863.85 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
863.9 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
863.95 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
864 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
864.05 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
864.1 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
864.15 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
864.2 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
864.25 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
864.3 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
864.35 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
864.4 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
864.45 | 50 | 50 | 0 | 0 | 0 | 50.01 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
864.5 | 49.5 | 49.5 | 1 | 1 | 10 | 50.01 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
864.55 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
864.6 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
864.65 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
864.7 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
864.75 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
864.8 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
864.85 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
864.9 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
864.95 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
865 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
865.05 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.1 | 1 | 5.5 | 5.5 | 0 | 12 | 1 | 1 | 5.5 | 10 | 0 | 0
865.1 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.2 | 2 | 6 | 6 | 0 | 12 | 1 | 1 | 6 | 10 | 0 | 0
865.15 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.3 | 3 | 6.5 | 6.5 | 0 | 12 | 1 | 1 | 6.5 | 10 | 0 | 0
865.2 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.4 | 4 | 7 | 7 | 0 | 12 | 1 | 1 | 7 | 10 | 0 | 0
865.25 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.5 | 5 | 7.5 | 7.5 | 0 | 12 | 1 | 1 | 7.5 | 10 | 0 | 0
865.3 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.6 | 6 | 8 | 8 | 0 | 12 | 1 | 1 | 8 | 10 | 0 | 0
865.35 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.7 | 7 | 8.5 | 8.5 | 0 | 12 | 1 | 1 | 8.5 | 10 | 0 | 0
865.4 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.8 | 8 | 9 | 9 | 0 | 12 | 1 | 1 | 9 | 10 | 0 | 0
865.45 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.9 | 9 | 9.5 | 9.5 | 0 | 12 | 1 | 1 | 9.5 | 10 | 0 | 0
865.5 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
865.55 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
865.6 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
865.65 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
865.7 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
865.75 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
865.8 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
865.85 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
865.9 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
865.95 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
866 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
866.05 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
866.1 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
866.15 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
866.2 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
866.25 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
866.3 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
866.35 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
866.4 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
866.45 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
866.5 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
866.55 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
866.6 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
866.65 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
866.7 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
866.75 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
866.8 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
866.85 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
866.9 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
866.95 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
867 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
867.05 | 50.5 | 50.5 | -1 | 0.9 | 9 | 50.5 | -1 | -1 | -10 | -0.5 | -0.5 | 0 | 12 | 1 | 1 | -0.5 | 10 | 0 | 0
867.1 | 50.5 | 50.5 | -1 | 0.8 | 8 | 50.5 | -1 | -1 | -10 | -1 | -1 | 0 | 12 | 1 | 1 | -1 | 10 | 0 | 0
867.15 | 50.5 | 50.5 | -1 | 0.7 | 7 | 50.5 | -1 | -1 | -10 | -1.5 | -1.5 | 0 | 12 | 1 | 1 | -1.5 | 10 | 0 | 0
867.2 | 50.5 | 50.5 | -1 | 0.6 | 6 | 50.5 | -1 | -1 | -10 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
867.25 | 50.5 | 50.5 | -1 | 0.5 | 5 | 50.5 | -1 | -1 | -10 | -2.5 | -2.5 | 0 | 12 | 1 | 1 | -2.5 | 10 | 0 | 0
867.3 | 50.5 | 50.5 | -1 | 0.4 | 4 | 50.5 | -1 | -1 | -10 | -3 | -3 | 0 | 12 | 1 | 1 | -3 | 10 | 0 | 0
867.35 | 50.5 | 50.5 | -1 | 0.3 | 3 | 50.5 | -1 | -1 | -10 | -3.5 | -3.5 | 0 | 12 | 1 | 1 | -3.5 | 10 | 0 | 0
867.4 | 50.5 | 50.5 | -1 | 0.2 | 2 | 50.5 | -1 | -1 | -10 | -4 | -4 | 0 | 12 | 1 | 1 | -4 | 10 | 0 | 0
867.45 | 50.5 | 50.5 | -1 | 0.1 | 1 | 50.5 | -1 | -1 | -10 | -4.5 | -4.5 | 0 | 12 | 1 | 1 | -4.5 | 10 | 0 | 0
867.5 | 50.5 | 50.5 | -1 | 0 | 0 | 50.5 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
867.55 | 50.5 | 50.5 | -1 | -0.1 | -1 | 50.5 | -1 | -1 | -10 | -5.5 | -5.5 | 0 | 12 | 1 | 1 | -5.5 | 10 | 0 | 0
867.6 | 50.5 | 50.5 | -1 | -0.2 | -2 | 50.5 | -1 | -1 | -10 | -6 | -6 | 0 | 12 | 1 | 1 | -6 | 10 | 0 | 0
867.65 | 50.5 | 50.5 | -1 | -0.3 | -3 | 50.5 | -1 | -1 | -10 | -6.5 | -6.5 | 0 | 12 | 1 | 1 | -6.5 | 10 | 0 | 0
867.7 | 50.5 | 50.5 | -1 | -0.4 | -4 | 50.5 | -1 | -1 | -10 | -7 | -7 | 0 | 12 | 1 | 1 | -7 | 10 | 0 | 0
867.75 | 50.5 | 50.5 | -1 | -0.5 | -5 | 50.5 | -1 | -1 | -10 | -7.5 | -7.5 | 0 | 12 | 1 | 1 | -7.5 | 10 | 0 | 0
867.8 | 50.5 | 50.5 | -1 | -0.6 | -6 | 50.5 | -1 | -1 | -10 | -8 | -8 | 0 | 12 | 1 | 1 | -8 | 10 | 0 | 0
867.85 | 50.5 | 50.5 | -1 | -0.7 | -7 | 50.5 | -1 | -1 | -10 | -8.5 | -8.5 | 0 | 12 | 1 | 1 | -8.5 | 10 | 0 | 0
867.9 | 50.5 | 50.5 | -1 | -0.8 | -8 | 50.5 | -1 | -1 | -10 | -9 | -9 | 0 | 12 | 1 | 1 | -9 | 10 | 0 | 0
867.95 | 50.5 | 50.5 | -1 | -0.9 | -9 | 50.5 | -1 | -1 | -10 | -9.5 | -9.5 | 0 | 12 | 1 | 1 | -9.5 | 10 | 0 | 0
868 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
868.05 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
868.1 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
868.15 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
868.2 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
868.25 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
868.3 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
868.35 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
868.4 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
868.45 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
868.5 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
868.55 | 50.47 | 50.47 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
868.6 | 50.45 | 50.45 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
868.65 | 50.42 | 50.42 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
868.7 | 50.4 | 50.4 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
868.75 | 50.37 | 50.37 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
868.8 | 50.35 | 50.35 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
868.85 | 50.32 | 50.32 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
868.9 | 50.29 | 50.29 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
868.95 | 50.27 | 50.27 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
869 | 50.24 | 50.24 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
869.05 | 50.22 | 50.22 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
869.1 | 50.19 | 50.19 | -0.905 | -0.905 | -9.05 | 50.47 | -1 | -1 | -10 | -9.525 | -9.525 | 0 | 12 | 1 | 1 | -9.525 | 10 | 0 | 0
869.15 | 50.17 | 50.17 | -0.715 | -0.715 | -7.15 | 50.45 | -1 | -1 | -10 | -8.575 | -8.575 | 0 | 12 | 1 | 1 | -8.575 | 10 | 0 | 0
869.2 | 50.14 | 50.14 | -0.43 | -0.43 | -4.3 | 50.42 | -1 | -1 | -10 | -7.15 | -7.15 | 0 | 12 | 1 | 1 | -7.15 | 10 | 0 | 0
869.25 | 50.12 | 50.12 | -0.24 | -0.24 | -2.4 | 50.4 | -1 | -1 | -10 | -6.2 | -6.2 | 0 | 12 | 1 | 1 | -6.2 | 10 | 0 | 0
869.3 | 50.09 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 50.37 | -1 | -1 | -10 | -5.2206 | -5.2206 | 0 | 12 | 1 | 1 | -5.2206 | 10 | 0 | 0
869.35 | 50.06 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.35 | -1 | -1 | -10 | -5.1324 | -5.1324 | 0 | 12 | 1 | 1 | -5.1324 | 10 | 0 | 0
869.4 | 50.04 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.32 | -1 | -1 | -10 | -5.0735 | -5.0735 | 0 | 12 | 1 | 1 | -5.0735 | 10 | 0 | 0
869.45 | 50.01 | 50.01 | 0 | 0 | 0 | 50.29 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
869.5 | 49.99 | 49.99 | 0 | 0 | 0 | 50.27 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
869.55 | 49.96 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.24 | -1 | -1 | -10 | -4.9265 | -4.9265 | 0 | 12 | 1 | 1 | -4.9265 | 10 | 0 | 0
869.6 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.22 | -1 | -1 | -10 | -4.8676 | -4.8676 | 0 | 12 | 1 | 1 | -4.8676 | 10 | 0 | 0
869.65 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.19 | -0.905 | -0.905 | -9.05 | -4.3044 | -4.3044 | 0 | 12 | 1 | 1 | -4.3044 | 10 | 0 | 0
869.7 | 49.88 | 49.88 | 0.24 | 0.24 | 2.4 | 50.17 | -0.715 | -0.805 | -8.05 | -2.825 | -2.825 | 0 | 12 | 1 | 1 | -2.825 | 10 | 0 | 0
869.75 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.14 | -0.43 | -0.705 | -7.05 | -1.375 | -1.375 | 0 | 12 | 1 | 1 | -1.375 | 10 | 0 | 0
869.8 | 49.83 | 49.83 | 0.715 | 0.715 | 7.15 | 50.12 | -0.24 | -0.605 | -6.05 | 0.55 | 0.55 | 0 | 12 | 1 | 1 | 0.55 | 10 | 0 | 0
869.85 | 49.81 | 49.81 | 0.905 | 0.905 | 9.05 | 50.09 | -0.044118 | -0.505 | -5.05 | 2 | 2 | 0 | 12 | 1 | 1 | 2 | 10 | 0 | 0
869.9 | 49.78 | 49.78 | 1 | 1 | 10 | 50.06 | -0.026471 | -0.405 | -4.05 | 2.975 | 2.975 | 0 | 12 | 1 | 1 | 2.975 | 10 | 0 | 0
869.95 | 49.76 | 49.76 | 1 | 1 | 10 | 50.04 | -0.014706 | -0.305 | -3.05 | 3.475 | 3.475 | 0 | 12 | 1 | 1 | 3.475 | 10 | 0 | 0
870 | 49.73 | 49.73 | 1 | 1 | 10 | 50.01 | 0 | -0.205 | -2.05 | 3.975 | 3.975 | 0 | 12 | 1 | 1 | 3.975 | 10 | 0 | 0
870.05 | 49.71 | 49.71 | 1 | 1 | 10 | 49.99 | 0 | -0.105 | -1.05 | 4.475 | 4.475 | 0 | 12 | 1 | 1 | 4.475 | 10 | 0 | 0
870.1 | 49.68 | 49.68 | 1 | 1 | 10 | 49.96 | 0.014706 | -0.005 | -0.05 | 4.975 | 4.975 | 0 | 12 | 1 | 1 | 4.975 | 10 | 0 | 0
870.15 | 49.65 | 49.65 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
870.2 | 49.63 | 49.63 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
870.25 | 49.6 | 49.6 | 1 | 1 | 10 | 49.88 | 0.24 | 0.14412 | 1.4412 | 5.7206 | 5.7206 | 0 | 12 | 1 | 1 | 5.7206 | 10 | 0 | 0
870.3 | 49.58 | 49.58 | 1 | 1 | 10 | 49.86 | 0.43 | 0.24412 | 2.4412 | 6.2206 | 6.2206 | 0 | 12 | 1 | 1 | 6.2206 | 10 | 0 | 0
870.35 | 49.55 | 49.55 | 1 | 1 | 10 | 49.83 | 0.715 | 0.34412 | 3.4412 | 6.7206 | 6.7206 | 0 | 12 | 1 | 1 | 6.7206 | 10 | 0 | 0
870.4 | 49.53 | 49.53 | 1 | 1 | 10 | 49.81 | 0.905 | 0.44412 | 4.4412 | 7.2206 | 7.2206 | 0 | 12 | 1 | 1 | 7.2206 | 10 | 0 | 0
870.45 | 49.5 | 49.5 | 1 | 1 | 10 | 49.78 | 1 | 0.54412 | 5.4412 | 7.7206 | 7.7206 | 0 | 12 | 1 | 1 | 7.7206 | 10 | 0 | 0
870.5 | 49.5 | 49.5 | 1 | 1 | 10 | 49.76 | 1 | 0.64412 | 6.4412 | 8.2206 | 8.2206 | 0 | 12 | 1 | 1 | 8.2206 | 10 | 0 | 0
870.55 | 49.53 | 49.5 | 1 | 1 | 10 | 49.73 | 1 | 0.74412 | 7.4412 | 8.7206 | 8.7206 | 0 | 12 | 1 | 1 | 8.7206 | 10 | 0 | 0
870.6 | 49.55 | 49.5 | 1 | 1 | 10 | 49.71 | 1 | 0.84412 | 8.4412 | 9.2206 | 9.2206 | 0 | 12 | 1 | 1 | 9.2206 | 10 | 0 | 0
870.65 | 49.58 | 49.5 | 1 | 1 | 10 | 49.68 | 1 | 0.94412 | 9.4412 | 9.7206 | 9.7206 | 0 | 12 | 1 | 1 | 9.7206 | 10 | 0 | 0
870.7 | 49.6 | 49.5 | 1 | 1 | 10 | 49.65 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
870.75 | 49.63 | 49.5 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
870.8 | 49.65 | 49.5 | 1 | 1 | 10 | 49.65 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
870.85 | 49.68 | 49.5 | 1 | 1 | 10 | 49.68 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
870.9 | 49.71 | 49.5 | 1 | 1 | 10 | 49.71 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
870.95 | 49.73 | 49.5 | 1 | 1 | 10 | 49.73 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
871 | 49.76 | 49.5 | 1 | 1 | 10 | 49.76 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
871.05 | 49.78 | 49.5 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
871.1 | 49.81 | 49.53 | 1 | 1 | 10 | 49.81 | 0.905 | 0.905 | 9.05 | 9.525 | 9.525 | 0 | 12 | 1 | 1 | 9.525 | 10 | 0 | 0
871.15 | 49.83 | 49.55 | 1 | 1 | 10 | 49.83 | 0.715 | 0.715 | 7.15 | 8.575 | 8.575 | 0 | 12 | 1 | 1 | 8.575 | 10 | 0 | 0
871.2 | 49.86 | 49.58 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
871.25 | 49.88 | 49.6 | 1 | 1 | 10 | 49.88 | 0.24 | 0.24 | 2.4 | 6.2 | 6.2 | 0 | 12 | 1 | 1 | 6.2 | 10 | 0 | 0
871.3 | 49.91 | 49.63 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
871.35 | 49.94 | 49.65 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
871.4 | 49.96 | 49.68 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
871.45 | 49.99 | 49.71 | 1 | 1 | 10 | 49.99 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
871.5 | 50.01 | 49.73 | 1 | 1 | 10 | 50.01 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
871.55 | 50.04 | 49.76 | 1 | 1 | 10 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 4.9265 | 4.9265 | 0 | 12 | 1 | 1 | 4.9265 | 10 | 0 | 0
871.6 | 50.06 | 49.78 | 1 | 1 | 10 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 4.8676 | 4.8676 | 0 | 12 | 1 | 1 | 4.8676 | 10 | 0 | 0
871.65 | 50.09 | 49.81 | 0.905 | 0.905 | 9.05 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 4.3044 | 4.3044 | 0 | 12 | 1 | 1 | 4.3044 | 10 | 0 | 0
871.7 | 50.12 | 49.83 | 0.715 | 0.805 | 8.05 | 50.12 | -0.24 | -0.24 | -2.4 | 2.825 | 2.825 | 0 | 12 | 1 | 1 | 2.825 | 10 | 0 | 0
871.75 | 50.14 | 49.86 | 0.43 | 0.705 | 7.05 | 50.14 | -0.43 | -0.43 | -4.3 | 1.375 | 1.375 | 0 | 12 | 1 | 1 | 1.375 | 10 | 0 | 0
871.8 | 50.17 | 49.88 | 0.24 | 0.605 | 6.05 | 50.17 | -0.715 | -0.715 | -7.15 | -0.55 | -0.55 | 0 | 12 | 1 | 1 | -0.55 | 10 | 0 | 0
871.85 | 50.19 | 49.91 | 0.044118 | 0.505 | 5.05 | 50.19 | -0.905 | -0.905 | -9.05 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
871.9 | 50.22 | 49.94 | 0.026471 | 0.405 | 4.05 | 50.22 | -1 | -1 | -10 | -2.975 | -2.975 | 0 | 12 | 1 | 1 | -2.975 | 10 | 0 | 0
871.95 | 50.24 | 49.96 | 0.014706 | 0.305 | 3.05 | 50.24 | -1 | -1 | -10 | -3.475 | -3.475 | 0 | 12 | 1 | 1 | -3.475 | 10 | 0 | 0
872 | 50.27 | 49.99 | 0 | 0.205 | 2.05 | 50.27 | -1 | -1 | -10 | -3.975 | -3.975 | 0 | 12 | 1 | 1 | -3.975 | 10 | 0 | 0
872.05 | 50.29 | 50.01 | 0 | 0.105 | 1.05 | 50.29 | -1 | -1 | -10 | -4.475 | -4.475 | 0 | 12 | 1 | 1 | -4.475 | 10 | 0 | 0
872.1 | 50.32 | 50.04 | -0.014706 | 0.005 | 0.05 | 50.32 | -1 | -1 | -10 | -4.975 | -4.975 | 0 | 12 | 1 | 1 | -4.975 | 10 | 0 | 0
872.15 | 50.35 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.35 | -1 | -1 | -10 | -5.1324 | -5.1324 | 0 | 12 | 1 | 1 | -5.1324 | 10 | 0 | 0
872.2 | 50.37 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 50.37 | -1 | -1 | -10 | -5.2206 | -5.2206 | 0 | 12 | 1 | 1 | -5.2206 | 10 | 0 | 0
872.25 | 50.4 | 50.12 | -0.24 | -0.14412 | -1.4412 | 50.4 | -1 | -1 | -10 | -5.7206 | -5.7206 | 0 | 12 | 1 | 1 | -5.7206 | 10 | 0 | 0
872.3 | 50.42 | 50.14 | -0.43 | -0.24412 | -2.4412 | 50.42 | -1 | -1 | -10 | -6.2206 | -6.2206 | 0 | 12 | 1 | 1 | -6.2206 | 10 | 0 | 0
872.35 | 50.45 | 50.17 | -0.715 | -0.34412 | -3.4412 | 50.45 | -1 | -1 | -10 | -6.7206 | -6.7206 | 0 | 12 | 1 | 1 | -6.7206 | 10 | 0 | 0
872.4 | 50.47 | 50.19 | -0.905 | -0.44412 | -4.4412 | 50.47 | -1 | -1 | -10 | -7.2206 | -7.2206 | 0 | 12 | 1 | 1 | -7.2206 | 10 | 0 | 0
872.45 | 50.5 | 50.22 | -1 | -0.54412 | -5.4412 | 50.5 | -1 | -1 | -10 | -7.7206 | -7.7206 | 0 | 12 | 1 | 1 | -7.7206 | 10 | 0 | 0
872.5 | 50.5 | 50.24 | -1 | -0.64412 | -6.4412 | 50.5 | -1 | -1 | -10 | -8.2206 | -8.2206 | 0 | 12 | 1 | 1 | -8.2206 | 10 | 0 | 0
872.55 | 50.47 | 50.27 | -1 | -0.74412 | -7.4412 | 50.5 | -1 | -1 | -10 | -8.7206 | -8.7206 | 0 | 12 | 1 | 1 | -8.7206 | 10 | 0 | 0
872.6 | 50.45 | 50.29 | -1 | -0.84412 | -8.4412 | 50.5 | -1 | -1 | -10 | -9.2206 | -9.2206 | 0 | 12 | 1 | 1 | -9.2206 | 10 | 0 | 0
872.65 | 50.42 | 50.32 | -1 | -0.94412 | -9.4412 | 50.5 | -1 | -1 | -10 | -9.7206 | -9.7206 | 0 | 12 | 1 | 1 | -9.7206 | 10 | 0 | 0
872.7 | 50.39 | 50.35 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
872.75 | 50.37 | 50.37 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
872.8 | 50.34 | 50.34 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
872.85 | 50.32 | 50.32 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
872.9 | 50.29 | 50.29 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
872.95 | 50.26 | 50.26 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
873 | 50.24 | 50.24 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
873.05 | 50.21 | 50.21 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
873.1 | 50.18 | 50.18 | -0.81 | -0.81 | -8.1 | 50.47 | -1 | -1 | -10 | -9.05 | -9.05 | 0 | 12 | 1 | 1 | -9.05 | 10 | 0 | 0
873.15 | 50.16 | 50.16 | -0.62 | -0.62 | -6.2 | 50.45 | -1 | -1 | -10 | -8.1 | -8.1 | 0 | 12 | 1 | 1 | -8.1 | 10 | 0 | 0
873.2 | 50.13 | 50.13 | -0.335 | -0.335 | -3.35 | 50.42 | -1 | -1 | -10 | -6.675 | -6.675 | 0 | 12 | 1 | 1 | -6.675 | 10 | 0 | 0
873.25 | 50.11 | 50.11 | -0.145 | -0.145 | -1.45 | 50.39 | -1 | -1 | -10 | -5.725 | -5.725 | 0 | 12 | 1 | 1 | -5.725 | 10 | 0 | 0
873.3 | 50.08 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 50.37 | -1 | -1 | -10 | -5.1912 | -5.1912 | 0 | 12 | 1 | 1 | -5.1912 | 10 | 0 | 0
873.35 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.34 | -1 | -1 | -10 | -5.1029 | -5.1029 | 0 | 12 | 1 | 1 | -5.1029 | 10 | 0 | 0
873.4 | 50.03 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 50.32 | -1 | -1 | -10 | -5.0441 | -5.0441 | 0 | 12 | 1 | 1 | -5.0441 | 10 | 0 | 0
873.45 | 50 | 50 | 0 | 0 | 0 | 50.29 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
873.5 | 50 | 50 | 0 | 0 | 0 | 50.26 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
873.55 | 50 | 50 | 0 | 0 | 0 | 50.24 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
873.6 | 50 | 50 | 0 | 0 | 0 | 50.21 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
873.65 | 50 | 50 | 0 | 0 | 0 | 50.18 | -0.81 | -0.9 | -9 | -4.5 | -4.5 | 0 | 12 | 1 | 1 | -4.5 | 10 | 0 | 0
873.7 | 50 | 50 | 0 | 0 | 0 | 50.16 | -0.62 | -0.8 | -8 | -4 | -4 | 0 | 12 | 1 | 1 | -4 | 10 | 0 | 0
873.75 | 50 | 50 | 0 | 0 | 0 | 50.13 | -0.335 | -0.7 | -7 | -3.5 | -3.5 | 0 | 12 | 1 | 1 | -3.5 | 10 | 0 | 0
873.8 | 50.01 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.6 | -6 | -3 | -3 | 0 | 12 | 1 | 1 | -3 | 10 | 0 | 0
873.85 | 50.01 | 50 | 0 | 0 | 0 | 50.08 | -0.038235 | -0.5 | -5 | -2.5 | -2.5 | 0 | 12 | 1 | 1 | -2.5 | 10 | 0 | 0
873.9 | 49.99 | 49.99 | 0 | 0 | 0 | 50.05 | -0.020588 | -0.4 | -4 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
873.95 | 49.99 | 49.99 | 0 | 0 | 0 | 50.03 | -0.0088235 | -0.3 | -3 | -1.5 | -1.5 | 0 | 12 | 1 | 1 | -1.5 | 10 | 0 | 0
874 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | -0.2 | -2 | -0.83824 | -0.83824 | 0 | 12 | 1 | 1 | -0.83824 | 10 | 0 | 0
874.05 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | -0.1 | -1 | -0.33824 | -0.33824 | 0 | 12 | 1 | 1 | -0.33824 | 10 | 0 | 0
874.1 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
874.15 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
874.2 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
874.25 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
874.3 | 49.89 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
874.35 | 49.89 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
874.4 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50.01 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
874.45 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
874.5 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
874.55 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 2.7868 | 2.7868 | 0 | 12 | 1 | 1 | 2.7868 | 10 | 0 | 0
874.6 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 2.7868 | 2.7868 | 0 | 12 | 1 | 1 | 2.7868 | 10 | 0 | 0
874.65 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 2.8456 | 2.8456 | 0 | 12 | 1 | 1 | 2.8456 | 10 | 0 | 0
874.7 | 49.94 | 49.85 | 0.525 | 0.525 | 5.25 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 2.7574 | 2.7574 | 0 | 12 | 1 | 1 | 2.7574 | 10 | 0 | 0
874.75 | 49.94 | 49.85 | 0.525 | 0.525 | 5.25 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 2.7574 | 2.7574 | 0 | 12 | 1 | 1 | 2.7574 | 10 | 0 | 0
874.8 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
874.85 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
874.9 | 49.93 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
874.95 | 49.93 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
875 | 49.96 | 49.85 | 0.525 | 0.525 | 5.25 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 2.6985 | 2.6985 | 0 | 12 | 1 | 1 | 2.6985 | 10 | 0 | 0
875.05 | 49.96 | 49.85 | 0.525 | 0.525 | 5.25 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 2.6985 | 2.6985 | 0 | 12 | 1 | 1 | 2.6985 | 10 | 0 | 0
875.1 | 49.99 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
875.15 | 49.99 | 49.91 | 0.044118 | 0.425 | 4.25 | 49.99 | 0 | 0 | 0 | 2.125 | 2.125 | 0 | 12 | 1 | 1 | 2.125 | 10 | 0 | 0
875.2 | 49.99 | 49.91 | 0.044118 | 0.325 | 3.25 | 49.99 | 0 | 0 | 0 | 1.625 | 1.625 | 0 | 12 | 1 | 1 | 1.625 | 10 | 0 | 0
875.25 | 49.99 | 49.93 | 0.032353 | 0.225 | 2.25 | 49.99 | 0 | 0 | 0 | 1.125 | 1.125 | 0 | 12 | 1 | 1 | 1.125 | 10 | 0 | 0
875.3 | 49.96 | 49.93 | 0.032353 | 0.125 | 1.25 | 49.99 | 0 | 0 | 0 | 0.625 | 0.625 | 0 | 12 | 1 | 1 | 0.625 | 10 | 0 | 0
875.35 | 49.96 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 49.99 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
875.4 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
875.45 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
875.5 | 50.05 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.058824 | 0.058824 | 0 | 12 | 1 | 1 | 0.058824 | 10 | 0 | 0
875.55 | 50.05 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
875.6 | 49.97 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
875.65 | 49.97 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
875.7 | 49.92 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
875.75 | 49.92 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
875.8 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
875.85 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
875.9 | 49.94 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
875.95 | 49.94 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
876 | 50.01 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
876.05 | 50.01 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
876.1 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
876.15 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
876.2 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
876.25 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
876.3 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
876.35 | 49.95 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
876.4 | 49.97 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
876.45 | 49.97 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
876.5 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
876.55 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
876.6 | 49.87 | 49.87 | 0.335 | 0.335 | 3.35 | 50.01 | 0 | 0 | 0 | 1.675 | 1.675 | 0 | 12 | 1 | 1 | 1.675 | 10 | 0 | 0
876.65 | 49.87 | 49.87 | 0.335 | 0.335 | 3.35 | 49.99 | 0 | 0 | 0 | 1.675 | 1.675 | 0 | 12 | 1 | 1 | 1.675 | 10 | 0 | 0
876.7 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
876.75 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 2.6691 | 2.6691 | 0 | 12 | 1 | 1 | 2.6691 | 10 | 0 | 0
876.8 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
876.85 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
876.9 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
876.95 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
877 | 49.84 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
877.05 | 49.84 | 49.79 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
877.1 | 49.89 | 49.79 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
877.15 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.12647 | 1.2647 | 5.6324 | 5.6324 | 0 | 12 | 1 | 1 | 5.6324 | 10 | 0 | 0
877.2 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.145 | 1.45 | 5.725 | 5.725 | 0 | 12 | 1 | 1 | 5.725 | 10 | 0 | 0
877.25 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.145 | 1.45 | 5.725 | 5.725 | 0 | 12 | 1 | 1 | 5.725 | 10 | 0 | 0
877.3 | 49.96 | 49.79 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
877.35 | 49.96 | 49.79 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
877.4 | 50.02 | 49.79 | 1 | 1 | 10 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 4.9853 | 4.9853 | 0 | 12 | 1 | 1 | 4.9853 | 10 | 0 | 0
877.45 | 50.02 | 49.79 | 1 | 1 | 10 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 4.9853 | 4.9853 | 0 | 12 | 1 | 1 | 4.9853 | 10 | 0 | 0
877.5 | 50.03 | 49.79 | 1 | 1 | 10 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.9559 | 4.9559 | 0 | 12 | 1 | 1 | 4.9559 | 10 | 0 | 0
877.55 | 50.03 | 49.84 | 0.62 | 0.9 | 9 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.4559 | 4.4559 | 0 | 12 | 1 | 1 | 4.4559 | 10 | 0 | 0
877.6 | 50.02 | 49.84 | 0.62 | 0.8 | 8 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 3.9559 | 3.9559 | 0 | 12 | 1 | 1 | 3.9559 | 10 | 0 | 0
877.65 | 50.02 | 49.89 | 0.145 | 0.7 | 7 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 3.4559 | 3.4559 | 0 | 12 | 1 | 1 | 3.4559 | 10 | 0 | 0
877.7 | 50.08 | 49.89 | 0.145 | 0.6 | 6 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 2.8088 | 2.8088 | 0 | 12 | 1 | 1 | 2.8088 | 10 | 0 | 0
877.75 | 50.08 | 49.89 | 0.145 | 0.5 | 5 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 2.3088 | 2.3088 | 0 | 12 | 1 | 1 | 2.3088 | 10 | 0 | 0
877.8 | 50.01 | 49.89 | 0.145 | 0.4 | 4 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 1.8088 | 1.8088 | 0 | 12 | 1 | 1 | 1.8088 | 10 | 0 | 0
877.85 | 50.01 | 49.96 | 0.014706 | 0.3 | 3 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 1.3088 | 1.3088 | 0 | 12 | 1 | 1 | 1.3088 | 10 | 0 | 0
877.9 | 49.94 | 49.94 | 0.026471 | 0.2 | 2 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.80882 | 0.80882 | 0 | 12 | 1 | 1 | 0.80882 | 10 | 0 | 0
877.95 | 49.94 | 49.94 | 0.026471 | 0.1 | 1 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.30882 | 0.30882 | 0 | 12 | 1 | 1 | 0.30882 | 10 | 0 | 0
878 | 50 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
878.05 | 50 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
878.1 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
878.15 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
878.2 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
878.25 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
878.3 | 49.92 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
878.35 | 49.92 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
878.4 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50.01 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
878.45 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
878.5 | 49.92 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
878.55 | 49.92 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
878.6 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
878.65 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
878.7 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
878.75 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
878.8 | 49.87 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
878.85 | 49.87 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
878.9 | 49.8 | 49.8 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
878.95 | 49.8 | 49.8 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
879 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
879.05 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
879.1 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
879.15 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
879.2 | 49.72 | 49.72 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
879.25 | 49.72 | 49.72 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
879.3 | 49.67 | 49.67 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
879.35 | 49.67 | 49.67 | 1 | 1 | 10 | 49.87 | 0.335 | 0.14412 | 1.4412 | 5.7206 | 5.7206 | 0 | 12 | 1 | 1 | 5.7206 | 10 | 0 | 0
879.4 | 49.65 | 49.65 | 1 | 1 | 10 | 49.87 | 0.335 | 0.24412 | 2.4412 | 6.2206 | 6.2206 | 0 | 12 | 1 | 1 | 6.2206 | 10 | 0 | 0
879.45 | 49.65 | 49.65 | 1 | 1 | 10 | 49.8 | 1 | 0.34412 | 3.4412 | 6.7206 | 6.7206 | 0 | 12 | 1 | 1 | 6.7206 | 10 | 0 | 0
879.5 | 49.59 | 49.59 | 1 | 1 | 10 | 49.8 | 1 | 0.44412 | 4.4412 | 7.2206 | 7.2206 | 0 | 12 | 1 | 1 | 7.2206 | 10 | 0 | 0
879.55 | 49.59 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.54412 | 5.4412 | 7.7206 | 7.7206 | 0 | 12 | 1 | 1 | 7.7206 | 10 | 0 | 0
879.6 | 49.66 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.64412 | 6.4412 | 8.2206 | 8.2206 | 0 | 12 | 1 | 1 | 8.2206 | 10 | 0 | 0
879.65 | 49.66 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.74412 | 7.4412 | 8.7206 | 8.7206 | 0 | 12 | 1 | 1 | 8.7206 | 10 | 0 | 0
879.7 | 49.63 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.84412 | 8.4412 | 9.2206 | 9.2206 | 0 | 12 | 1 | 1 | 9.2206 | 10 | 0 | 0
879.75 | 49.63 | 49.59 | 1 | 1 | 10 | 49.72 | 1 | 0.94412 | 9.4412 | 9.7206 | 9.7206 | 0 | 12 | 1 | 1 | 9.7206 | 10 | 0 | 0
879.8 | 49.61 | 49.59 | 1 | 1 | 10 | 49.72 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
879.85 | 49.61 | 49.59 | 1 | 1 | 10 | 49.67 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
879.9 | 49.54 | 49.54 | 1 | 1 | 10 | 49.67 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
879.95 | 49.54 | 49.54 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
880 | 49.46 | 49.46 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
880.05 | 49.46 | 49.46 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
880.1 | 49.45 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
880.15 | 49.45 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
880.2 | 49.51 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
880.25 | 49.51 | 49.45 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
880.3 | 49.5 | 49.45 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
880.35 | 49.5 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
880.4 | 49.54 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
880.45 | 49.54 | 49.45 | 1 | 1 | 10 | 49.54 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
880.5 | 49.59 | 49.45 | 1 | 1 | 10 | 49.59 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
880.55 | 49.59 | 49.45 | 1 | 1 | 10 | 49.59 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
880.6 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
880.65 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
880.7 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
880.75 | 49.61 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
880.8 | 49.53 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
880.85 | 49.53 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
880.9 | 49.54 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
880.95 | 49.54 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
881 | 49.61 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
881.05 | 49.61 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
881.1 | 49.66 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
881.15 | 49.66 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
881.2 | 49.64 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
881.25 | 49.64 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
881.3 | 49.69 | 49.53 | 1 | 1 | 10 | 49.69 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
881.35 | 49.69 | 49.53 | 1 | 1 | 10 | 49.69 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
881.4 | 49.74 | 49.53 | 1 | 1 | 10 | 49.74 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
881.45 | 49.74 | 49.54 | 1 | 1 | 10 | 49.74 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
881.5 | 49.78 | 49.54 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
881.55 | 49.78 | 49.61 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
881.6 | 49.82 | 49.61 | 1 | 1 | 10 | 49.82 | 0.81 | 0.81 | 8.1 | 9.05 | 9.05 | 0 | 12 | 1 | 1 | 9.05 | 10 | 0 | 0
881.65 | 49.82 | 49.64 | 1 | 1 | 10 | 49.82 | 0.81 | 0.81 | 8.1 | 9.05 | 9.05 | 0 | 12 | 1 | 1 | 9.05 | 10 | 0 | 0
881.7 | 49.86 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
881.75 | 49.86 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
881.8 | 49.84 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
881.85 | 49.84 | 49.69 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
881.9 | 49.91 | 49.69 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
881.95 | 49.91 | 49.74 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
882 | 49.97 | 49.74 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
882.05 | 49.97 | 49.78 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
882.1 | 50.03 | 49.78 | 1 | 1 | 10 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.9559 | 4.9559 | 0 | 12 | 1 | 1 | 4.9559 | 10 | 0 | 0
882.15 | 50.03 | 49.82 | 0.81 | 0.9 | 9 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.4559 | 4.4559 | 0 | 12 | 1 | 1 | 4.4559 | 10 | 0 | 0
882.2 | 50.05 | 49.82 | 0.81 | 0.81 | 8.1 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 3.9471 | 3.9471 | 0 | 12 | 1 | 1 | 3.9471 | 10 | 0 | 0
882.25 | 50.05 | 49.84 | 0.62 | 0.71 | 7.1 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 3.4471 | 3.4471 | 0 | 12 | 1 | 1 | 3.4471 | 10 | 0 | 0
882.3 | 50.01 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
882.35 | 50.01 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
882.4 | 49.95 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
882.45 | 49.95 | 49.91 | 0.044118 | 0.52 | 5.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.4971 | 2.4971 | 0 | 12 | 1 | 1 | 2.4971 | 10 | 0 | 0
882.5 | 49.99 | 49.91 | 0.044118 | 0.42 | 4.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 1.9971 | 1.9971 | 0 | 12 | 1 | 1 | 1.9971 | 10 | 0 | 0
882.55 | 49.99 | 49.95 | 0.020588 | 0.32 | 3.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 1.4971 | 1.4971 | 0 | 12 | 1 | 1 | 1.4971 | 10 | 0 | 0
882.6 | 49.92 | 49.92 | 0.038235 | 0.22 | 2.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.99706 | 0.99706 | 0 | 12 | 1 | 1 | 0.99706 | 10 | 0 | 0
882.65 | 49.92 | 49.92 | 0.038235 | 0.12 | 1.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.49706 | 0.49706 | 0 | 12 | 1 | 1 | 0.49706 | 10 | 0 | 0
882.7 | 49.97 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
882.75 | 49.97 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
882.8 | 50.02 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
882.85 | 50.02 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.17647 | 0.17647 | 0 | 12 | 1 | 1 | 0.17647 | 10 | 0 | 0
882.9 | 50.07 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
882.95 | 50.07 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
883 | 50.06 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
883.05 | 50.06 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
883.1 | 50.13 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
883.15 | 50.13 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
883.2 | 50.09 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
883.25 | 50.09 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6309 | -1.6309 | 0 | 12 | 1 | 1 | -1.6309 | 10 | 0 | 0
883.3 | 50.07 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6309 | -1.6309 | 0 | 12 | 1 | 1 | -1.6309 | 10 | 0 | 0
883.35 | 50.07 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6897 | -1.6897 | 0 | 12 | 1 | 1 | -1.6897 | 10 | 0 | 0
883.4 | 50.07 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6897 | -1.6897 | 0 | 12 | 1 | 1 | -1.6897 | 10 | 0 | 0
883.45 | 50.07 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.13 | -0.335 | -0.335 | -3.35 | -1.8074 | -1.8074 | 0 | 12 | 1 | 1 | -1.8074 | 10 | 0 | 0
883.5 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.13 | -0.335 | -0.335 | -3.35 | -1.7779 | -1.7779 | 0 | 12 | 1 | 1 | -1.7779 | 10 | 0 | 0
883.55 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.13 | -0.335 | -0.335 | -3.35 | -1.7779 | -1.7779 | 0 | 12 | 1 | 1 | -1.7779 | 10 | 0 | 0
883.6 | 50.01 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
883.65 | 50.01 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
883.7 | 50.07 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
883.75 | 50.07 | 50.01 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.235 | -2.35 | -1.175 | -1.175 | 0 | 12 | 1 | 1 | -1.175 | 10 | 0 | 0
883.8 | 50.05 | 50.01 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.135 | -1.35 | -0.675 | -0.675 | 0 | 12 | 1 | 1 | -0.675 | 10 | 0 | 0
883.85 | 50.05 | 50.01 | 0 | 0 | 0 | 50.07 | -0.032353 | -0.035 | -0.35 | -0.175 | -0.175 | 0 | 12 | 1 | 1 | -0.175 | 10 | 0 | 0
883.9 | 50.1 | 50.01 | 0 | 0 | 0 | 50.1 | -0.05 | -0.05 | -0.5 | -0.25 | -0.25 | 0 | 12 | 1 | 1 | -0.25 | 10 | 0 | 0
883.95 | 50.1 | 50.01 | 0 | 0 | 0 | 50.1 | -0.05 | -0.05 | -0.5 | -0.25 | -0.25 | 0 | 12 | 1 | 1 | -0.25 | 10 | 0 | 0
884 | 50.11 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
884.05 | 50.11 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
884.1 | 50.06 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
884.15 | 50.06 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
884.2 | 50.04 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
884.25 | 50.04 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
884.3 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
884.35 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
884.4 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
884.45 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
884.5 | 50.11 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
884.55 | 50.11 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
884.6 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
884.65 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
884.7 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
884.75 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
884.8 | 50.02 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.11 | -0.145 | -0.145 | -1.45 | -0.73971 | -0.73971 | 0 | 12 | 1 | 1 | -0.73971 | 10 | 0 | 0
884.85 | 50.02 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.11 | -0.145 | -0.145 | -1.45 | -0.73971 | -0.73971 | 0 | 12 | 1 | 1 | -0.73971 | 10 | 0 | 0
884.9 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
884.95 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
885 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
885.05 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
885.1 | 50.01 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
885.15 | 50.01 | 50 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.045 | -0.45 | -0.225 | -0.225 | 0 | 12 | 1 | 1 | -0.225 | 10 | 0 | 0
885.2 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
885.25 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
885.3 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
885.35 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
885.4 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.14706 | 0.14706 | 0 | 12 | 1 | 1 | 0.14706 | 10 | 0 | 0
885.45 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
885.5 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
885.55 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
885.6 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
885.65 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
885.7 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
885.75 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
885.8 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
885.85 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
885.9 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
885.95 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
886 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
886.05 | 50 | 50 | 0 | 0 | 0 | 50.01 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
886.1 | 49.5 | 49.5 | 1 | 1 | 10 | 50.01 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
886.15 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
886.2 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
886.25 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
886.3 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
886.35 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
886.4 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
886.45 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
886.5 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
886.55 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
886.6 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
886.65 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.1 | 1 | 5.5 | 5.5 | 0 | 12 | 1 | 1 | 5.5 | 10 | 0 | 0
886.7 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.2 | 2 | 6 | 6 | 0 | 12 | 1 | 1 | 6 | 10 | 0 | 0
886.75 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.3 | 3 | 6.5 | 6.5 | 0 | 12 | 1 | 1 | 6.5 | 10 | 0 | 0
886.8 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.4 | 4 | 7 | 7 | 0 | 12 | 1 | 1 | 7 | 10 | 0 | 0
886.85 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.5 | 5 | 7.5 | 7.5 | 0 | 12 | 1 | 1 | 7.5 | 10 | 0 | 0
886.9 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.6 | 6 | 8 | 8 | 0 | 12 | 1 | 1 | 8 | 10 | 0 | 0
886.95 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.7 | 7 | 8.5 | 8.5 | 0 | 12 | 1 | 1 | 8.5 | 10 | 0 | 0
887 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.8 | 8 | 9 | 9 | 0 | 12 | 1 | 1 | 9 | 10 | 0 | 0
887.05 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.9 | 9 | 9.5 | 9.5 | 0 | 12 | 1 | 1 | 9.5 | 10 | 0 | 0
887.1 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
887.15 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
887.2 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
887.25 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
887.3 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
887.35 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
887.4 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
887.45 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
887.5 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
887.55 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
887.6 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
887.65 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
887.7 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
887.75 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
887.8 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
887.85 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
887.9 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
887.95 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
888 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
888.05 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
888.1 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
888.15 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
888.2 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
888.25 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
888.3 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
888.35 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
888.4 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
888.45 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
888.5 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
888.55 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
888.6 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
888.65 | 50.5 | 50.5 | -1 | 0.9 | 9 | 50.5 | -1 | -1 | -10 | -0.5 | -0.5 | 0 | 12 | 1 | 1 | -0.5 | 10 | 0 | 0
888.7 | 50.5 | 50.5 | -1 | 0.8 | 8 | 50.5 | -1 | -1 | -10 | -1 | -1 | 0 | 12 | 1 | 1 | -1 | 10 | 0 | 0
888.75 | 50.5 | 50.5 | -1 | 0.7 | 7 | 50.5 | -1 | -1 | -10 | -1.5 | -1.5 | 0 | 12 | 1 | 1 | -1.5 | 10 | 0 | 0
888.8 | 50.5 | 50.5 | -1 | 0.6 | 6 | 50.5 | -1 | -1 | -10 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
888.85 | 50.5 | 50.5 | -1 | 0.5 | 5 | 50.5 | -1 | -1 | -10 | -2.5 | -2.5 | 0 | 12 | 1 | 1 | -2.5 | 10 | 0 | 0
888.9 | 50.5 | 50.5 | -1 | 0.4 | 4 | 50.5 | -1 | -1 | -10 | -3 | -3 | 0 | 12 | 1 | 1 | -3 | 10 | 0 | 0
888.95 | 50.5 | 50.5 | -1 | 0.3 | 3 | 50.5 | -1 | -1 | -10 | -3.5 | -3.5 | 0 | 12 | 1 | 1 | -3.5 | 10 | 0 | 0
889 | 50.5 | 50.5 | -1 | 0.2 | 2 | 50.5 | -1 | -1 | -10 | -4 | -4 | 0 | 12 | 1 | 1 | -4 | 10 | 0 | 0
889.05 | 50.5 | 50.5 | -1 | 0.1 | 1 | 50.5 | -1 | -1 | -10 | -4.5 | -4.5 | 0 | 12 | 1 | 1 | -4.5 | 10 | 0 | 0
889.1 | 50.5 | 50.5 | -1 | 0 | 0 | 50.5 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
889.15 | 50.5 | 50.5 | -1 | -0.1 | -1 | 50.5 | -1 | -1 | -10 | -5.5 | -5.5 | 0 | 12 | 1 | 1 | -5.5 | 10 | 0 | 0
889.2 | 50.5 | 50.5 | -1 | -0.2 | -2 | 50.5 | -1 | -1 | -10 | -6 | -6 | 0 | 12 | 1 | 1 | -6 | 10 | 0 | 0
889.25 | 50.5 | 50.5 | -1 | -0.3 | -3 | 50.5 | -1 | -1 | -10 | -6.5 | -6.5 | 0 | 12 | 1 | 1 | -6.5 | 10 | 0 | 0
889.3 | 50.5 | 50.5 | -1 | -0.4 | -4 | 50.5 | -1 | -1 | -10 | -7 | -7 | 0 | 12 | 1 | 1 | -7 | 10 | 0 | 0
889.35 | 50.5 | 50.5 | -1 | -0.5 | -5 | 50.5 | -1 | -1 | -10 | -7.5 | -7.5 | 0 | 12 | 1 | 1 | -7.5 | 10 | 0 | 0
889.4 | 50.5 | 50.5 | -1 | -0.6 | -6 | 50.5 | -1 | -1 | -10 | -8 | -8 | 0 | 12 | 1 | 1 | -8 | 10 | 0 | 0
889.45 | 50.5 | 50.5 | -1 | -0.7 | -7 | 50.5 | -1 | -1 | -10 | -8.5 | -8.5 | 0 | 12 | 1 | 1 | -8.5 | 10 | 0 | 0
889.5 | 50.5 | 50.5 | -1 | -0.8 | -8 | 50.5 | -1 | -1 | -10 | -9 | -9 | 0 | 12 | 1 | 1 | -9 | 10 | 0 | 0
889.55 | 50.5 | 50.5 | -1 | -0.9 | -9 | 50.5 | -1 | -1 | -10 | -9.5 | -9.5 | 0 | 12 | 1 | 1 | -9.5 | 10 | 0 | 0
889.6 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
889.65 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
889.7 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
889.75 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
889.8 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
889.85 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
889.9 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
889.95 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
890 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
890.05 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
890.1 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
890.15 | 50.47 | 50.47 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
890.2 | 50.45 | 50.45 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
890.25 | 50.42 | 50.42 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
890.3 | 50.4 | 50.4 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
890.35 | 50.37 | 50.37 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
890.4 | 50.35 | 50.35 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
890.45 | 50.32 | 50.32 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
890.5 | 50.29 | 50.29 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
890.55 | 50.27 | 50.27 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
890.6 | 50.24 | 50.24 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
890.65 | 50.22 | 50.22 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
890.7 | 50.19 | 50.19 | -0.905 | -0.905 | -9.05 | 50.47 | -1 | -1 | -10 | -9.525 | -9.525 | 0 | 12 | 1 | 1 | -9.525 | 10 | 0 | 0
890.75 | 50.17 | 50.17 | -0.715 | -0.715 | -7.15 | 50.45 | -1 | -1 | -10 | -8.575 | -8.575 | 0 | 12 | 1 | 1 | -8.575 | 10 | 0 | 0
890.8 | 50.14 | 50.14 | -0.43 | -0.43 | -4.3 | 50.42 | -1 | -1 | -10 | -7.15 | -7.15 | 0 | 12 | 1 | 1 | -7.15 | 10 | 0 | 0
890.85 | 50.12 | 50.12 | -0.24 | -0.24 | -2.4 | 50.4 | -1 | -1 | -10 | -6.2 | -6.2 | 0 | 12 | 1 | 1 | -6.2 | 10 | 0 | 0
890.9 | 50.09 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 50.37 | -1 | -1 | -10 | -5.2206 | -5.2206 | 0 | 12 | 1 | 1 | -5.2206 | 10 | 0 | 0
890.95 | 50.06 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.35 | -1 | -1 | -10 | -5.1324 | -5.1324 | 0 | 12 | 1 | 1 | -5.1324 | 10 | 0 | 0
891 | 50.04 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.32 | -1 | -1 | -10 | -5.0735 | -5.0735 | 0 | 12 | 1 | 1 | -5.0735 | 10 | 0 | 0
891.05 | 50.01 | 50.01 | 0 | 0 | 0 | 50.29 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
891.1 | 49.99 | 49.99 | 0 | 0 | 0 | 50.27 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
891.15 | 49.96 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.24 | -1 | -1 | -10 | -4.9265 | -4.9265 | 0 | 12 | 1 | 1 | -4.9265 | 10 | 0 | 0
891.2 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.22 | -1 | -1 | -10 | -4.8676 | -4.8676 | 0 | 12 | 1 | 1 | -4.8676 | 10 | 0 | 0
891.25 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.19 | -0.905 | -0.905 | -9.05 | -4.3044 | -4.3044 | 0 | 12 | 1 | 1 | -4.3044 | 10 | 0 | 0
891.3 | 49.88 | 49.88 | 0.24 | 0.24 | 2.4 | 50.17 | -0.715 | -0.805 | -8.05 | -2.825 | -2.825 | 0 | 12 | 1 | 1 | -2.825 | 10 | 0 | 0
891.35 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.14 | -0.43 | -0.705 | -7.05 | -1.375 | -1.375 | 0 | 12 | 1 | 1 | -1.375 | 10 | 0 | 0
891.4 | 49.83 | 49.83 | 0.715 | 0.715 | 7.15 | 50.12 | -0.24 | -0.605 | -6.05 | 0.55 | 0.55 | 0 | 12 | 1 | 1 | 0.55 | 10 | 0 | 0
891.45 | 49.81 | 49.81 | 0.905 | 0.905 | 9.05 | 50.09 | -0.044118 | -0.505 | -5.05 | 2 | 2 | 0 | 12 | 1 | 1 | 2 | 10 | 0 | 0
891.5 | 49.78 | 49.78 | 1 | 1 | 10 | 50.06 | -0.026471 | -0.405 | -4.05 | 2.975 | 2.975 | 0 | 12 | 1 | 1 | 2.975 | 10 | 0 | 0
891.55 | 49.76 | 49.76 | 1 | 1 | 10 | 50.04 | -0.014706 | -0.305 | -3.05 | 3.475 | 3.475 | 0 | 12 | 1 | 1 | 3.475 | 10 | 0 | 0
891.6 | 49.73 | 49.73 | 1 | 1 | 10 | 50.01 | 0 | -0.205 | -2.05 | 3.975 | 3.975 | 0 | 12 | 1 | 1 | 3.975 | 10 | 0 | 0
891.65 | 49.71 | 49.71 | 1 | 1 | 10 | 49.99 | 0 | -0.105 | -1.05 | 4.475 | 4.475 | 0 | 12 | 1 | 1 | 4.475 | 10 | 0 | 0
891.7 | 49.68 | 49.68 | 1 | 1 | 10 | 49.96 | 0.014706 | -0.005 | -0.05 | 4.975 | 4.975 | 0 | 12 | 1 | 1 | 4.975 | 10 | 0 | 0
891.75 | 49.65 | 49.65 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
891.8 | 49.63 | 49.63 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
891.85 | 49.6 | 49.6 | 1 | 1 | 10 | 49.88 | 0.24 | 0.14412 | 1.4412 | 5.7206 | 5.7206 | 0 | 12 | 1 | 1 | 5.7206 | 10 | 0 | 0
891.9 | 49.58 | 49.58 | 1 | 1 | 10 | 49.86 | 0.43 | 0.24412 | 2.4412 | 6.2206 | 6.2206 | 0 | 12 | 1 | 1 | 6.2206 | 10 | 0 | 0
891.95 | 49.55 | 49.55 | 1 | 1 | 10 | 49.83 | 0.715 | 0.34412 | 3.4412 | 6.7206 | 6.7206 | 0 | 12 | 1 | 1 | 6.7206 | 10 | 0 | 0
892 | 49.53 | 49.53 | 1 | 1 | 10 | 49.81 | 0.905 | 0.44412 | 4.4412 | 7.2206 | 7.2206 | 0 | 12 | 1 | 1 | 7.2206 | 10 | 0 | 0
892.05 | 49.5 | 49.5 | 1 | 1 | 10 | 49.78 | 1 | 0.54412 | 5.4412 | 7.7206 | 7.7206 | 0 | 12 | 1 | 1 | 7.7206 | 10 | 0 | 0
892.1 | 49.5 | 49.5 | 1 | 1 | 10 | 49.76 | 1 | 0.64412 | 6.4412 | 8.2206 | 8.2206 | 0 | 12 | 1 | 1 | 8.2206 | 10 | 0 | 0
892.15 | 49.53 | 49.5 | 1 | 1 | 10 | 49.73 | 1 | 0.74412 | 7.4412 | 8.7206 | 8.7206 | 0 | 12 | 1 | 1 | 8.7206 | 10 | 0 | 0
892.2 | 49.55 | 49.5 | 1 | 1 | 10 | 49.71 | 1 | 0.84412 | 8.4412 | 9.2206 | 9.2206 | 0 | 12 | 1 | 1 | 9.2206 | 10 | 0 | 0
892.25 | 49.58 | 49.5 | 1 | 1 | 10 | 49.68 | 1 | 0.94412 | 9.4412 | 9.7206 | 9.7206 | 0 | 12 | 1 | 1 | 9.7206 | 10 | 0 | 0
892.3 | 49.6 | 49.5 | 1 | 1 | 10 | 49.65 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
892.35 | 49.63 | 49.5 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
892.4 | 49.65 | 49.5 | 1 | 1 | 10 | 49.65 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
892.45 | 49.68 | 49.5 | 1 | 1 | 10 | 49.68 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
892.5 | 49.71 | 49.5 | 1 | 1 | 10 | 49.71 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
892.55 | 49.73 | 49.5 | 1 | 1 | 10 | 49.73 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
892.6 | 49.76 | 49.5 | 1 | 1 | 10 | 49.76 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
892.65 | 49.78 | 49.5 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
892.7 | 49.81 | 49.53 | 1 | 1 | 10 | 49.81 | 0.905 | 0.905 | 9.05 | 9.525 | 9.525 | 0 | 12 | 1 | 1 | 9.525 | 10 | 0 | 0
892.75 | 49.83 | 49.55 | 1 | 1 | 10 | 49.83 | 0.715 | 0.715 | 7.15 | 8.575 | 8.575 | 0 | 12 | 1 | 1 | 8.575 | 10 | 0 | 0
892.8 | 49.86 | 49.58 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
892.85 | 49.88 | 49.6 | 1 | 1 | 10 | 49.88 | 0.24 | 0.24 | 2.4 | 6.2 | 6.2 | 0 | 12 | 1 | 1 | 6.2 | 10 | 0 | 0
892.9 | 49.91 | 49.63 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
892.95 | 49.94 | 49.65 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
893 | 49.96 | 49.68 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
893.05 | 49.99 | 49.71 | 1 | 1 | 10 | 49.99 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
893.1 | 50.01 | 49.73 | 1 | 1 | 10 | 50.01 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
893.15 | 50.04 | 49.76 | 1 | 1 | 10 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 4.9265 | 4.9265 | 0 | 12 | 1 | 1 | 4.9265 | 10 | 0 | 0
893.2 | 50.06 | 49.78 | 1 | 1 | 10 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 4.8676 | 4.8676 | 0 | 12 | 1 | 1 | 4.8676 | 10 | 0 | 0
893.25 | 50.09 | 49.81 | 0.905 | 0.905 | 9.05 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 4.3044 | 4.3044 | 0 | 12 | 1 | 1 | 4.3044 | 10 | 0 | 0
893.3 | 50.12 | 49.83 | 0.715 | 0.805 | 8.05 | 50.12 | -0.24 | -0.24 | -2.4 | 2.825 | 2.825 | 0 | 12 | 1 | 1 | 2.825 | 10 | 0 | 0
893.35 | 50.14 | 49.86 | 0.43 | 0.705 | 7.05 | 50.14 | -0.43 | -0.43 | -4.3 | 1.375 | 1.375 | 0 | 12 | 1 | 1 | 1.375 | 10 | 0 | 0
893.4 | 50.17 | 49.88 | 0.24 | 0.605 | 6.05 | 50.17 | -0.715 | -0.715 | -7.15 | -0.55 | -0.55 | 0 | 12 | 1 | 1 | -0.55 | 10 | 0 | 0
893.45 | 50.19 | 49.91 | 0.044118 | 0.505 | 5.05 | 50.19 | -0.905 | -0.905 | -9.05 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
893.5 | 50.22 | 49.94 | 0.026471 | 0.405 | 4.05 | 50.22 | -1 | -1 | -10 | -2.975 | -2.975 | 0 | 12 | 1 | 1 | -2.975 | 10 | 0 | 0
893.55 | 50.24 | 49.96 | 0.014706 | 0.305 | 3.05 | 50.24 | -1 | -1 | -10 | -3.475 | -3.475 | 0 | 12 | 1 | 1 | -3.475 | 10 | 0 | 0
893.6 | 50.27 | 49.99 | 0 | 0.205 | 2.05 | 50.27 | -1 | -1 | -10 | -3.975 | -3.975 | 0 | 12 | 1 | 1 | -3.975 | 10 | 0 | 0
893.65 | 50.29 | 50.01 | 0 | 0.105 | 1.05 | 50.29 | -1 | -1 | -10 | -4.475 | -4.475 | 0 | 12 | 1 | 1 | -4.475 | 10 | 0 | 0
893.7 | 50.32 | 50.04 | -0.014706 | 0.005 | 0.05 | 50.32 | -1 | -1 | -10 | -4.975 | -4.975 | 0 | 12 | 1 | 1 | -4.975 | 10 | 0 | 0
893.75 | 50.35 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.35 | -1 | -1 | -10 | -5.1324 | -5.1324 | 0 | 12 | 1 | 1 | -5.1324 | 10 | 0 | 0
893.8 | 50.37 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 50.37 | -1 | -1 | -10 | -5.2206 | -5.2206 | 0 | 12 | 1 | 1 | -5.2206 | 10 | 0 | 0
893.85 | 50.4 | 50.12 | -0.24 | -0.14412 | -1.4412 | 50.4 | -1 | -1 | -10 | -5.7206 | -5.7206 | 0 | 12 | 1 | 1 | -5.7206 | 10 | 0 | 0
893.9 | 50.42 | 50.14 | -0.43 | -0.24412 | -2.4412 | 50.42 | -1 | -1 | -10 | -6.2206 | -6.2206 | 0 | 12 | 1 | 1 | -6.2206 | 10 | 0 | 0
893.95 | 50.45 | 50.17 | -0.715 | -0.34412 | -3.4412 | 50.45 | -1 | -1 | -10 | -6.7206 | -6.7206 | 0 | 12 | 1 | 1 | -6.7206 | 10 | 0 | 0
894 | 50.47 | 50.19 | -0.905 | -0.44412 | -4.4412 | 50.47 | -1 | -1 | -10 | -7.2206 | -7.2206 | 0 | 12 | 1 | 1 | -7.2206 | 10 | 0 | 0
894.05 | 50.5 | 50.22 | -1 | -0.54412 | -5.4412 | 50.5 | -1 | -1 | -10 | -7.7206 | -7.7206 | 0 | 12 | 1 | 1 | -7.7206 | 10 | 0 | 0
894.1 | 50.5 | 50.24 | -1 | -0.64412 | -6.4412 | 50.5 | -1 | -1 | -10 | -8.2206 | -8.2206 | 0 | 12 | 1 | 1 | -8.2206 | 10 | 0 | 0
894.15 | 50.47 | 50.27 | -1 | -0.74412 | -7.4412 | 50.5 | -1 | -1 | -10 | -8.7206 | -8.7206 | 0 | 12 | 1 | 1 | -8.7206 | 10 | 0 | 0
894.2 | 50.45 | 50.29 | -1 | -0.84412 | -8.4412 | 50.5 | -1 | -1 | -10 | -9.2206 | -9.2206 | 0 | 12 | 1 | 1 | -9.2206 | 10 | 0 | 0
894.25 | 50.42 | 50.32 | -1 | -0.94412 | -9.4412 | 50.5 | -1 | -1 | -10 | -9.7206 | -9.7206 | 0 | 12 | 1 | 1 | -9.7206 | 10 | 0 | 0
894.3 | 50.39 | 50.35 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
894.35 | 50.37 | 50.37 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
894.4 | 50.34 | 50.34 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
894.45 | 50.32 | 50.32 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
894.5 | 50.29 | 50.29 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
894.55 | 50.26 | 50.26 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
894.6 | 50.24 | 50.24 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
894.65 | 50.21 | 50.21 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
894.7 | 50.18 | 50.18 | -0.81 | -0.81 | -8.1 | 50.47 | -1 | -1 | -10 | -9.05 | -9.05 | 0 | 12 | 1 | 1 | -9.05 | 10 | 0 | 0
894.75 | 50.16 | 50.16 | -0.62 | -0.62 | -6.2 | 50.45 | -1 | -1 | -10 | -8.1 | -8.1 | 0 | 12 | 1 | 1 | -8.1 | 10 | 0 | 0
894.8 | 50.13 | 50.13 | -0.335 | -0.335 | -3.35 | 50.42 | -1 | -1 | -10 | -6.675 | -6.675 | 0 | 12 | 1 | 1 | -6.675 | 10 | 0 | 0
894.85 | 50.11 | 50.11 | -0.145 | -0.145 | -1.45 | 50.39 | -1 | -1 | -10 | -5.725 | -5.725 | 0 | 12 | 1 | 1 | -5.725 | 10 | 0 | 0
894.9 | 50.08 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 50.37 | -1 | -1 | -10 | -5.1912 | -5.1912 | 0 | 12 | 1 | 1 | -5.1912 | 10 | 0 | 0
894.95 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.34 | -1 | -1 | -10 | -5.1029 | -5.1029 | 0 | 12 | 1 | 1 | -5.1029 | 10 | 0 | 0
895 | 50.03 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 50.32 | -1 | -1 | -10 | -5.0441 | -5.0441 | 0 | 12 | 1 | 1 | -5.0441 | 10 | 0 | 0
895.05 | 50 | 50 | 0 | 0 | 0 | 50.29 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
895.1 | 50 | 50 | 0 | 0 | 0 | 50.26 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
895.15 | 50 | 50 | 0 | 0 | 0 | 50.24 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
895.2 | 50 | 50 | 0 | 0 | 0 | 50.21 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
895.25 | 50 | 50 | 0 | 0 | 0 | 50.18 | -0.81 | -0.9 | -9 | -4.5 | -4.5 | 0 | 12 | 1 | 1 | -4.5 | 10 | 0 | 0
895.3 | 50 | 50 | 0 | 0 | 0 | 50.16 | -0.62 | -0.8 | -8 | -4 | -4 | 0 | 12 | 1 | 1 | -4 | 10 | 0 | 0
895.35 | 50 | 50 | 0 | 0 | 0 | 50.13 | -0.335 | -0.7 | -7 | -3.5 | -3.5 | 0 | 12 | 1 | 1 | -3.5 | 10 | 0 | 0
895.4 | 50.01 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.6 | -6 | -3 | -3 | 0 | 12 | 1 | 1 | -3 | 10 | 0 | 0
895.45 | 50.01 | 50 | 0 | 0 | 0 | 50.08 | -0.038235 | -0.5 | -5 | -2.5 | -2.5 | 0 | 12 | 1 | 1 | -2.5 | 10 | 0 | 0
895.5 | 49.99 | 49.99 | 0 | 0 | 0 | 50.05 | -0.020588 | -0.4 | -4 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
895.55 | 49.99 | 49.99 | 0 | 0 | 0 | 50.03 | -0.0088235 | -0.3 | -3 | -1.5 | -1.5 | 0 | 12 | 1 | 1 | -1.5 | 10 | 0 | 0
895.6 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | -0.2 | -2 | -0.83824 | -0.83824 | 0 | 12 | 1 | 1 | -0.83824 | 10 | 0 | 0
895.65 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | -0.1 | -1 | -0.33824 | -0.33824 | 0 | 12 | 1 | 1 | -0.33824 | 10 | 0 | 0
895.7 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
895.75 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
895.8 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
895.85 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
895.9 | 49.89 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
895.95 | 49.89 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
896 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50.01 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
896.05 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
896.1 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
896.15 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 2.7868 | 2.7868 | 0 | 12 | 1 | 1 | 2.7868 | 10 | 0 | 0
896.2 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 2.7868 | 2.7868 | 0 | 12 | 1 | 1 | 2.7868 | 10 | 0 | 0
896.25 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 2.8456 | 2.8456 | 0 | 12 | 1 | 1 | 2.8456 | 10 | 0 | 0
896.3 | 49.94 | 49.85 | 0.525 | 0.525 | 5.25 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 2.7574 | 2.7574 | 0 | 12 | 1 | 1 | 2.7574 | 10 | 0 | 0
896.35 | 49.94 | 49.85 | 0.525 | 0.525 | 5.25 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 2.7574 | 2.7574 | 0 | 12 | 1 | 1 | 2.7574 | 10 | 0 | 0
896.4 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
896.45 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
896.5 | 49.93 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
896.55 | 49.93 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
896.6 | 49.96 | 49.85 | 0.525 | 0.525 | 5.25 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 2.6985 | 2.6985 | 0 | 12 | 1 | 1 | 2.6985 | 10 | 0 | 0
896.65 | 49.96 | 49.85 | 0.525 | 0.525 | 5.25 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 2.6985 | 2.6985 | 0 | 12 | 1 | 1 | 2.6985 | 10 | 0 | 0
896.7 | 49.99 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
896.75 | 49.99 | 49.91 | 0.044118 | 0.425 | 4.25 | 49.99 | 0 | 0 | 0 | 2.125 | 2.125 | 0 | 12 | 1 | 1 | 2.125 | 10 | 0 | 0
896.8 | 49.99 | 49.91 | 0.044118 | 0.325 | 3.25 | 49.99 | 0 | 0 | 0 | 1.625 | 1.625 | 0 | 12 | 1 | 1 | 1.625 | 10 | 0 | 0
896.85 | 49.99 | 49.93 | 0.032353 | 0.225 | 2.25 | 49.99 | 0 | 0 | 0 | 1.125 | 1.125 | 0 | 12 | 1 | 1 | 1.125 | 10 | 0 | 0
896.9 | 49.96 | 49.93 | 0.032353 | 0.125 | 1.25 | 49.99 | 0 | 0 | 0 | 0.625 | 0.625 | 0 | 12 | 1 | 1 | 0.625 | 10 | 0 | 0
896.95 | 49.96 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 49.99 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
897 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
897.05 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
897.1 | 50.05 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.058824 | 0.058824 | 0 | 12 | 1 | 1 | 0.058824 | 10 | 0 | 0
897.15 | 50.05 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
897.2 | 49.97 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
897.25 | 49.97 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
897.3 | 49.92 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
897.35 | 49.92 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
897.4 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
897.45 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
897.5 | 49.94 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
897.55 | 49.94 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
897.6 | 50.01 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
897.65 | 50.01 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
897.7 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
897.75 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
897.8 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
897.85 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
897.9 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
897.95 | 49.95 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
898 | 49.97 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
898.05 | 49.97 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
898.1 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
898.15 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
898.2 | 49.87 | 49.87 | 0.335 | 0.335 | 3.35 | 50.01 | 0 | 0 | 0 | 1.675 | 1.675 | 0 | 12 | 1 | 1 | 1.675 | 10 | 0 | 0
898.25 | 49.87 | 49.87 | 0.335 | 0.335 | 3.35 | 49.99 | 0 | 0 | 0 | 1.675 | 1.675 | 0 | 12 | 1 | 1 | 1.675 | 10 | 0 | 0
898.3 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
898.35 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 2.6691 | 2.6691 | 0 | 12 | 1 | 1 | 2.6691 | 10 | 0 | 0
898.4 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
898.45 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
898.5 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
898.55 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
898.6 | 49.84 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
898.65 | 49.84 | 49.79 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
898.7 | 49.89 | 49.79 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
898.75 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.12647 | 1.2647 | 5.6324 | 5.6324 | 0 | 12 | 1 | 1 | 5.6324 | 10 | 0 | 0
898.8 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.145 | 1.45 | 5.725 | 5.725 | 0 | 12 | 1 | 1 | 5.725 | 10 | 0 | 0
898.85 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.145 | 1.45 | 5.725 | 5.725 | 0 | 12 | 1 | 1 | 5.725 | 10 | 0 | 0
898.9 | 49.96 | 49.79 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
898.95 | 49.96 | 49.79 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
899 | 50.02 | 49.79 | 1 | 1 | 10 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 4.9853 | 4.9853 | 0 | 12 | 1 | 1 | 4.9853 | 10 | 0 | 0
899.05 | 50.02 | 49.79 | 1 | 1 | 10 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 4.9853 | 4.9853 | 0 | 12 | 1 | 1 | 4.9853 | 10 | 0 | 0
899.1 | 50.03 | 49.79 | 1 | 1 | 10 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.9559 | 4.9559 | 0 | 12 | 1 | 1 | 4.9559 | 10 | 0 | 0
899.15 | 50.03 | 49.84 | 0.62 | 0.9 | 9 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.4559 | 4.4559 | 0 | 12 | 1 | 1 | 4.4559 | 10 | 0 | 0
899.2 | 50.02 | 49.84 | 0.62 | 0.8 | 8 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 3.9559 | 3.9559 | 0 | 12 | 1 | 1 | 3.9559 | 10 | 0 | 0
899.25 | 50.02 | 49.89 | 0.145 | 0.7 | 7 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 3.4559 | 3.4559 | 0 | 12 | 1 | 1 | 3.4559 | 10 | 0 | 0
899.3 | 50.08 | 49.89 | 0.145 | 0.6 | 6 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 2.8088 | 2.8088 | 0 | 12 | 1 | 1 | 2.8088 | 10 | 0 | 0
899.35 | 50.08 | 49.89 | 0.145 | 0.5 | 5 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 2.3088 | 2.3088 | 0 | 12 | 1 | 1 | 2.3088 | 10 | 0 | 0
899.4 | 50.01 | 49.89 | 0.145 | 0.4 | 4 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 1.8088 | 1.8088 | 0 | 12 | 1 | 1 | 1.8088 | 10 | 0 | 0
899.45 | 50.01 | 49.96 | 0.014706 | 0.3 | 3 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 1.3088 | 1.3088 | 0 | 12 | 1 | 1 | 1.3088 | 10 | 0 | 0
899.5 | 49.94 | 49.94 | 0.026471 | 0.2 | 2 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.80882 | 0.80882 | 0 | 12 | 1 | 1 | 0.80882 | 10 | 0 | 0
899.55 | 49.94 | 49.94 | 0.026471 | 0.1 | 1 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.30882 | 0.30882 | 0 | 12 | 1 | 1 | 0.30882 | 10 | 0 | 0
899.6 | 50 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
899.65 | 50 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
899.7 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
899.75 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
899.8 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
899.85 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
899.9 | 49.92 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
899.95 | 49.92 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
900 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50.01 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
900.05 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
900.1 | 49.92 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
900.15 | 49.92 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
900.2 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
900.25 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
900.3 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
900.35 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
900.4 | 49.87 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
900.45 | 49.87 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
900.5 | 49.8 | 49.8 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
900.55 | 49.8 | 49.8 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
900.6 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
900.65 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
900.7 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
900.75 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
900.8 | 49.72 | 49.72 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
900.85 | 49.72 | 49.72 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
900.9 | 49.67 | 49.67 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
900.95 | 49.67 | 49.67 | 1 | 1 | 10 | 49.87 | 0.335 | 0.14412 | 1.4412 | 5.7206 | 5.7206 | 0 | 12 | 1 | 1 | 5.7206 | 10 | 0 | 0
901 | 49.65 | 49.65 | 1 | 1 | 10 | 49.87 | 0.335 | 0.24412 | 2.4412 | 6.2206 | 6.2206 | 0 | 12 | 1 | 1 | 6.2206 | 10 | 0 | 0
901.05 | 49.65 | 49.65 | 1 | 1 | 10 | 49.8 | 1 | 0.34412 | 3.4412 | 6.7206 | 6.7206 | 0 | 12 | 1 | 1 | 6.7206 | 10 | 0 | 0
901.1 | 49.59 | 49.59 | 1 | 1 | 10 | 49.8 | 1 | 0.44412 | 4.4412 | 7.2206 | 7.2206 | 0 | 12 | 1 | 1 | 7.2206 | 10 | 0 | 0
901.15 | 49.59 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.54412 | 5.4412 | 7.7206 | 7.7206 | 0 | 12 | 1 | 1 | 7.7206 | 10 | 0 | 0
901.2 | 49.66 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.64412 | 6.4412 | 8.2206 | 8.2206 | 0 | 12 | 1 | 1 | 8.2206 | 10 | 0 | 0
901.25 | 49.66 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.74412 | 7.4412 | 8.7206 | 8.7206 | 0 | 12 | 1 | 1 | 8.7206 | 10 | 0 | 0
901.3 | 49.63 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.84412 | 8.4412 | 9.2206 | 9.2206 | 0 | 12 | 1 | 1 | 9.2206 | 10 | 0 | 0
901.35 | 49.63 | 49.59 | 1 | 1 | 10 | 49.72 | 1 | 0.94412 | 9.4412 | 9.7206 | 9.7206 | 0 | 12 | 1 | 1 | 9.7206 | 10 | 0 | 0
901.4 | 49.61 | 49.59 | 1 | 1 | 10 | 49.72 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
901.45 | 49.61 | 49.59 | 1 | 1 | 10 | 49.67 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
901.5 | 49.54 | 49.54 | 1 | 1 | 10 | 49.67 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
901.55 | 49.54 | 49.54 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
901.6 | 49.46 | 49.46 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
901.65 | 49.46 | 49.46 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
901.7 | 49.45 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
901.75 | 49.45 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
901.8 | 49.51 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
901.85 | 49.51 | 49.45 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
901.9 | 49.5 | 49.45 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
901.95 | 49.5 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
902 | 49.54 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
902.05 | 49.54 | 49.45 | 1 | 1 | 10 | 49.54 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
902.1 | 49.59 | 49.45 | 1 | 1 | 10 | 49.59 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
902.15 | 49.59 | 49.45 | 1 | 1 | 10 | 49.59 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
902.2 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
902.25 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
902.3 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
902.35 | 49.61 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
902.4 | 49.53 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
902.45 | 49.53 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
902.5 | 49.54 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
902.55 | 49.54 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
902.6 | 49.61 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
902.65 | 49.61 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
902.7 | 49.66 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
902.75 | 49.66 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
902.8 | 49.64 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
902.85 | 49.64 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
902.9 | 49.69 | 49.53 | 1 | 1 | 10 | 49.69 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
902.95 | 49.69 | 49.53 | 1 | 1 | 10 | 49.69 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
903 | 49.74 | 49.53 | 1 | 1 | 10 | 49.74 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
903.05 | 49.74 | 49.54 | 1 | 1 | 10 | 49.74 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
903.1 | 49.78 | 49.54 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
903.15 | 49.78 | 49.61 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
903.2 | 49.82 | 49.61 | 1 | 1 | 10 | 49.82 | 0.81 | 0.81 | 8.1 | 9.05 | 9.05 | 0 | 12 | 1 | 1 | 9.05 | 10 | 0 | 0
903.25 | 49.82 | 49.64 | 1 | 1 | 10 | 49.82 | 0.81 | 0.81 | 8.1 | 9.05 | 9.05 | 0 | 12 | 1 | 1 | 9.05 | 10 | 0 | 0
903.3 | 49.86 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
903.35 | 49.86 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
903.4 | 49.84 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
903.45 | 49.84 | 49.69 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
903.5 | 49.91 | 49.69 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
903.55 | 49.91 | 49.74 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
903.6 | 49.97 | 49.74 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
903.65 | 49.97 | 49.78 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
903.7 | 50.03 | 49.78 | 1 | 1 | 10 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.9559 | 4.9559 | 0 | 12 | 1 | 1 | 4.9559 | 10 | 0 | 0
903.75 | 50.03 | 49.82 | 0.81 | 0.9 | 9 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.4559 | 4.4559 | 0 | 12 | 1 | 1 | 4.4559 | 10 | 0 | 0
903.8 | 50.05 | 49.82 | 0.81 | 0.81 | 8.1 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 3.9471 | 3.9471 | 0 | 12 | 1 | 1 | 3.9471 | 10 | 0 | 0
903.85 | 50.05 | 49.84 | 0.62 | 0.71 | 7.1 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 3.4471 | 3.4471 | 0 | 12 | 1 | 1 | 3.4471 | 10 | 0 | 0
903.9 | 50.01 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
903.95 | 50.01 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
904 | 49.95 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
904.05 | 49.95 | 49.91 | 0.044118 | 0.52 | 5.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.4971 | 2.4971 | 0 | 12 | 1 | 1 | 2.4971 | 10 | 0 | 0
904.1 | 49.99 | 49.91 | 0.044118 | 0.42 | 4.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 1.9971 | 1.9971 | 0 | 12 | 1 | 1 | 1.9971 | 10 | 0 | 0
904.15 | 49.99 | 49.95 | 0.020588 | 0.32 | 3.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 1.4971 | 1.4971 | 0 | 12 | 1 | 1 | 1.4971 | 10 | 0 | 0
904.2 | 49.92 | 49.92 | 0.038235 | 0.22 | 2.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.99706 | 0.99706 | 0 | 12 | 1 | 1 | 0.99706 | 10 | 0 | 0
904.25 | 49.92 | 49.92 | 0.038235 | 0.12 | 1.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.49706 | 0.49706 | 0 | 12 | 1 | 1 | 0.49706 | 10 | 0 | 0
904.3 | 49.97 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
904.35 | 49.97 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
904.4 | 50.02 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
904.45 | 50.02 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.17647 | 0.17647 | 0 | 12 | 1 | 1 | 0.17647 | 10 | 0 | 0
904.5 | 50.07 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
904.55 | 50.07 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
904.6 | 50.06 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
904.65 | 50.06 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
904.7 | 50.13 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
904.75 | 50.13 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
904.8 | 50.09 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
904.85 | 50.09 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6309 | -1.6309 | 0 | 12 | 1 | 1 | -1.6309 | 10 | 0 | 0
904.9 | 50.07 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6309 | -1.6309 | 0 | 12 | 1 | 1 | -1.6309 | 10 | 0 | 0
904.95 | 50.07 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6897 | -1.6897 | 0 | 12 | 1 | 1 | -1.6897 | 10 | 0 | 0
905 | 50.07 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6897 | -1.6897 | 0 | 12 | 1 | 1 | -1.6897 | 10 | 0 | 0
905.05 | 50.07 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.13 | -0.335 | -0.335 | -3.35 | -1.8074 | -1.8074 | 0 | 12 | 1 | 1 | -1.8074 | 10 | 0 | 0
905.1 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.13 | -0.335 | -0.335 | -3.35 | -1.7779 | -1.7779 | 0 | 12 | 1 | 1 | -1.7779 | 10 | 0 | 0
905.15 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.13 | -0.335 | -0.335 | -3.35 | -1.7779 | -1.7779 | 0 | 12 | 1 | 1 | -1.7779 | 10 | 0 | 0
905.2 | 50.01 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
905.25 | 50.01 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
905.3 | 50.07 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
905.35 | 50.07 | 50.01 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.235 | -2.35 | -1.175 | -1.175 | 0 | 12 | 1 | 1 | -1.175 | 10 | 0 | 0
905.4 | 50.05 | 50.01 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.135 | -1.35 | -0.675 | -0.675 | 0 | 12 | 1 | 1 | -0.675 | 10 | 0 | 0
905.45 | 50.05 | 50.01 | 0 | 0 | 0 | 50.07 | -0.032353 | -0.035 | -0.35 | -0.175 | -0.175 | 0 | 12 | 1 | 1 | -0.175 | 10 | 0 | 0
905.5 | 50.1 | 50.01 | 0 | 0 | 0 | 50.1 | -0.05 | -0.05 | -0.5 | -0.25 | -0.25 | 0 | 12 | 1 | 1 | -0.25 | 10 | 0 | 0
905.55 | 50.1 | 50.01 | 0 | 0 | 0 | 50.1 | -0.05 | -0.05 | -0.5 | -0.25 | -0.25 | 0 | 12 | 1 | 1 | -0.25 | 10 | 0 | 0
905.6 | 50.11 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
905.65 | 50.11 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
905.7 | 50.06 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
905.75 | 50.06 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
905.8 | 50.04 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
905.85 | 50.04 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
905.9 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
905.95 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
906 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
906.05 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
906.1 | 50.11 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
906.15 | 50.11 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
906.2 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
906.25 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
906.3 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
906.35 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
906.4 | 50.02 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.11 | -0.145 | -0.145 | -1.45 | -0.73971 | -0.73971 | 0 | 12 | 1 | 1 | -0.73971 | 10 | 0 | 0
906.45 | 50.02 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.11 | -0.145 | -0.145 | -1.45 | -0.73971 | -0.73971 | 0 | 12 | 1 | 1 | -0.73971 | 10 | 0 | 0
906.5 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
906.55 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
906.6 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
906.65 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
906.7 | 50.01 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
906.75 | 50.01 | 50 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.045 | -0.45 | -0.225 | -0.225 | 0 | 12 | 1 | 1 | -0.225 | 10 | 0 | 0
906.8 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
906.85 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
906.9 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
906.95 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
907 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.14706 | 0.14706 | 0 | 12 | 1 | 1 | 0.14706 | 10 | 0 | 0
907.05 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
907.1 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
907.15 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
907.2 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
907.25 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
907.3 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
907.35 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
907.4 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
907.45 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
907.5 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
907.55 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
907.6 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
907.65 | 50 | 50 | 0 | 0 | 0 | 50.01 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
907.7 | 49.5 | 49.5 | 1 | 1 | 10 | 50.01 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
907.75 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
907.8 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
907.85 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
907.9 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
907.95 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
908 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
908.05 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
908.1 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
908.15 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
908.2 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
908.25 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.1 | 1 | 5.5 | 5.5 | 0 | 12 | 1 | 1 | 5.5 | 10 | 0 | 0
908.3 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.2 | 2 | 6 | 6 | 0 | 12 | 1 | 1 | 6 | 10 | 0 | 0
908.35 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.3 | 3 | 6.5 | 6.5 | 0 | 12 | 1 | 1 | 6.5 | 10 | 0 | 0
908.4 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.4 | 4 | 7 | 7 | 0 | 12 | 1 | 1 | 7 | 10 | 0 | 0
908.45 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.5 | 5 | 7.5 | 7.5 | 0 | 12 | 1 | 1 | 7.5 | 10 | 0 | 0
908.5 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.6 | 6 | 8 | 8 | 0 | 12 | 1 | 1 | 8 | 10 | 0 | 0
908.55 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.7 | 7 | 8.5 | 8.5 | 0 | 12 | 1 | 1 | 8.5 | 10 | 0 | 0
908.6 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.8 | 8 | 9 | 9 | 0 | 12 | 1 | 1 | 9 | 10 | 0 | 0
908.65 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.9 | 9 | 9.5 | 9.5 | 0 | 12 | 1 | 1 | 9.5 | 10 | 0 | 0
908.7 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
908.75 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
908.8 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
908.85 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
908.9 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
908.95 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
909 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
909.05 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
909.1 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
909.15 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
909.2 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
909.25 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
909.3 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
909.35 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
909.4 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
909.45 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
909.5 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
909.55 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
909.6 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
909.65 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
909.7 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
909.75 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
909.8 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
909.85 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
909.9 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
909.95 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
910 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
910.05 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
910.1 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
910.15 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
910.2 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
910.25 | 50.5 | 50.5 | -1 | 0.9 | 9 | 50.5 | -1 | -1 | -10 | -0.5 | -0.5 | 0 | 12 | 1 | 1 | -0.5 | 10 | 0 | 0
910.3 | 50.5 | 50.5 | -1 | 0.8 | 8 | 50.5 | -1 | -1 | -10 | -1 | -1 | 0 | 12 | 1 | 1 | -1 | 10 | 0 | 0
910.35 | 50.5 | 50.5 | -1 | 0.7 | 7 | 50.5 | -1 | -1 | -10 | -1.5 | -1.5 | 0 | 12 | 1 | 1 | -1.5 | 10 | 0 | 0
910.4 | 50.5 | 50.5 | -1 | 0.6 | 6 | 50.5 | -1 | -1 | -10 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
910.45 | 50.5 | 50.5 | -1 | 0.5 | 5 | 50.5 | -1 | -1 | -10 | -2.5 | -2.5 | 0 | 12 | 1 | 1 | -2.5 | 10 | 0 | 0
910.5 | 50.5 | 50.5 | -1 | 0.4 | 4 | 50.5 | -1 | -1 | -10 | -3 | -3 | 0 | 12 | 1 | 1 | -3 | 10 | 0 | 0
910.55 | 50.5 | 50.5 | -1 | 0.3 | 3 | 50.5 | -1 | -1 | -10 | -3.5 | -3.5 | 0 | 12 | 1 | 1 | -3.5 | 10 | 0 | 0
910.6 | 50.5 | 50.5 | -1 | 0.2 | 2 | 50.5 | -1 | -1 | -10 | -4 | -4 | 0 | 12 | 1 | 1 | -4 | 10 | 0 | 0
910.65 | 50.5 | 50.5 | -1 | 0.1 | 1 | 50.5 | -1 | -1 | -10 | -4.5 | -4.5 | 0 | 12 | 1 | 1 | -4.5 | 10 | 0 | 0
910.7 | 50.5 | 50.5 | -1 | 0 | 0 | 50.5 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
910.75 | 50.5 | 50.5 | -1 | -0.1 | -1 | 50.5 | -1 | -1 | -10 | -5.5 | -5.5 | 0 | 12 | 1 | 1 | -5.5 | 10 | 0 | 0
910.8 | 50.5 | 50.5 | -1 | -0.2 | -2 | 50.5 | -1 | -1 | -10 | -6 | -6 | 0 | 12 | 1 | 1 | -6 | 10 | 0 | 0
910.85 | 50.5 | 50.5 | -1 | -0.3 | -3 | 50.5 | -1 | -1 | -10 | -6.5 | -6.5 | 0 | 12 | 1 | 1 | -6.5 | 10 | 0 | 0
910.9 | 50.5 | 50.5 | -1 | -0.4 | -4 | 50.5 | -1 | -1 | -10 | -7 | -7 | 0 | 12 | 1 | 1 | -7 | 10 | 0 | 0
910.95 | 50.5 | 50.5 | -1 | -0.5 | -5 | 50.5 | -1 | -1 | -10 | -7.5 | -7.5 | 0 | 12 | 1 | 1 | -7.5 | 10 | 0 | 0
911 | 50.5 | 50.5 | -1 | -0.6 | -6 | 50.5 | -1 | -1 | -10 | -8 | -8 | 0 | 12 | 1 | 1 | -8 | 10 | 0 | 0
911.05 | 50.5 | 50.5 | -1 | -0.7 | -7 | 50.5 | -1 | -1 | -10 | -8.5 | -8.5 | 0 | 12 | 1 | 1 | -8.5 | 10 | 0 | 0
911.1 | 50.5 | 50.5 | -1 | -0.8 | -8 | 50.5 | -1 | -1 | -10 | -9 | -9 | 0 | 12 | 1 | 1 | -9 | 10 | 0 | 0
911.15 | 50.5 | 50.5 | -1 | -0.9 | -9 | 50.5 | -1 | -1 | -10 | -9.5 | -9.5 | 0 | 12 | 1 | 1 | -9.5 | 10 | 0 | 0
911.2 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
911.25 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
911.3 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
911.35 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
911.4 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
911.45 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
911.5 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
911.55 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
911.6 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
911.65 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
911.7 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
911.75 | 50.47 | 50.47 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
911.8 | 50.45 | 50.45 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
911.85 | 50.42 | 50.42 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
911.9 | 50.4 | 50.4 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
911.95 | 50.37 | 50.37 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
912 | 50.35 | 50.35 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
912.05 | 50.32 | 50.32 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
912.1 | 50.29 | 50.29 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
912.15 | 50.27 | 50.27 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
912.2 | 50.24 | 50.24 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
912.25 | 50.22 | 50.22 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
912.3 | 50.19 | 50.19 | -0.905 | -0.905 | -9.05 | 50.47 | -1 | -1 | -10 | -9.525 | -9.525 | 0 | 12 | 1 | 1 | -9.525 | 10 | 0 | 0
912.35 | 50.17 | 50.17 | -0.715 | -0.715 | -7.15 | 50.45 | -1 | -1 | -10 | -8.575 | -8.575 | 0 | 12 | 1 | 1 | -8.575 | 10 | 0 | 0
912.4 | 50.14 | 50.14 | -0.43 | -0.43 | -4.3 | 50.42 | -1 | -1 | -10 | -7.15 | -7.15 | 0 | 12 | 1 | 1 | -7.15 | 10 | 0 | 0
912.45 | 50.12 | 50.12 | -0.24 | -0.24 | -2.4 | 50.4 | -1 | -1 | -10 | -6.2 | -6.2 | 0 | 12 | 1 | 1 | -6.2 | 10 | 0 | 0
912.5 | 50.09 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 50.37 | -1 | -1 | -10 | -5.2206 | -5.2206 | 0 | 12 | 1 | 1 | -5.2206 | 10 | 0 | 0
912.55 | 50.06 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.35 | -1 | -1 | -10 | -5.1324 | -5.1324 | 0 | 12 | 1 | 1 | -5.1324 | 10 | 0 | 0
912.6 | 50.04 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.32 | -1 | -1 | -10 | -5.0735 | -5.0735 | 0 | 12 | 1 | 1 | -5.0735 | 10 | 0 | 0
912.65 | 50.01 | 50.01 | 0 | 0 | 0 | 50.29 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
912.7 | 49.99 | 49.99 | 0 | 0 | 0 | 50.27 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
912.75 | 49.96 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.24 | -1 | -1 | -10 | -4.9265 | -4.9265 | 0 | 12 | 1 | 1 | -4.9265 | 10 | 0 | 0
912.8 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.22 | -1 | -1 | -10 | -4.8676 | -4.8676 | 0 | 12 | 1 | 1 | -4.8676 | 10 | 0 | 0
912.85 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.19 | -0.905 | -0.905 | -9.05 | -4.3044 | -4.3044 | 0 | 12 | 1 | 1 | -4.3044 | 10 | 0 | 0
912.9 | 49.88 | 49.88 | 0.24 | 0.24 | 2.4 | 50.17 | -0.715 | -0.805 | -8.05 | -2.825 | -2.825 | 0 | 12 | 1 | 1 | -2.825 | 10 | 0 | 0
912.95 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.14 | -0.43 | -0.705 | -7.05 | -1.375 | -1.375 | 0 | 12 | 1 | 1 | -1.375 | 10 | 0 | 0
913 | 49.83 | 49.83 | 0.715 | 0.715 | 7.15 | 50.12 | -0.24 | -0.605 | -6.05 | 0.55 | 0.55 | 0 | 12 | 1 | 1 | 0.55 | 10 | 0 | 0
913.05 | 49.81 | 49.81 | 0.905 | 0.905 | 9.05 | 50.09 | -0.044118 | -0.505 | -5.05 | 2 | 2 | 0 | 12 | 1 | 1 | 2 | 10 | 0 | 0
913.1 | 49.78 | 49.78 | 1 | 1 | 10 | 50.06 | -0.026471 | -0.405 | -4.05 | 2.975 | 2.975 | 0 | 12 | 1 | 1 | 2.975 | 10 | 0 | 0
913.15 | 49.76 | 49.76 | 1 | 1 | 10 | 50.04 | -0.014706 | -0.305 | -3.05 | 3.475 | 3.475 | 0 | 12 | 1 | 1 | 3.475 | 10 | 0 | 0
913.2 | 49.73 | 49.73 | 1 | 1 | 10 | 50.01 | 0 | -0.205 | -2.05 | 3.975 | 3.975 | 0 | 12 | 1 | 1 | 3.975 | 10 | 0 | 0
913.25 | 49.71 | 49.71 | 1 | 1 | 10 | 49.99 | 0 | -0.105 | -1.05 | 4.475 | 4.475 | 0 | 12 | 1 | 1 | 4.475 | 10 | 0 | 0
913.3 | 49.68 | 49.68 | 1 | 1 | 10 | 49.96 | 0.014706 | -0.005 | -0.05 | 4.975 | 4.975 | 0 | 12 | 1 | 1 | 4.975 | 10 | 0 | 0
913.35 | 49.65 | 49.65 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
913.4 | 49.63 | 49.63 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
913.45 | 49.6 | 49.6 | 1 | 1 | 10 | 49.88 | 0.24 | 0.14412 | 1.4412 | 5.7206 | 5.7206 | 0 | 12 | 1 | 1 | 5.7206 | 10 | 0 | 0
913.5 | 49.58 | 49.58 | 1 | 1 | 10 | 49.86 | 0.43 | 0.24412 | 2.4412 | 6.2206 | 6.2206 | 0 | 12 | 1 | 1 | 6.2206 | 10 | 0 | 0
913.55 | 49.55 | 49.55 | 1 | 1 | 10 | 49.83 | 0.715 | 0.34412 | 3.4412 | 6.7206 | 6.7206 | 0 | 12 | 1 | 1 | 6.7206 | 10 | 0 | 0
913.6 | 49.53 | 49.53 | 1 | 1 | 10 | 49.81 | 0.905 | 0.44412 | 4.4412 | 7.2206 | 7.2206 | 0 | 12 | 1 | 1 | 7.2206 | 10 | 0 | 0
913.65 | 49.5 | 49.5 | 1 | 1 | 10 | 49.78 | 1 | 0.54412 | 5.4412 | 7.7206 | 7.7206 | 0 | 12 | 1 | 1 | 7.7206 | 10 | 0 | 0
913.7 | 49.5 | 49.5 | 1 | 1 | 10 | 49.76 | 1 | 0.64412 | 6.4412 | 8.2206 | 8.2206 | 0 | 12 | 1 | 1 | 8.2206 | 10 | 0 | 0
913.75 | 49.53 | 49.5 | 1 | 1 | 10 | 49.73 | 1 | 0.74412 | 7.4412 | 8.7206 | 8.7206 | 0 | 12 | 1 | 1 | 8.7206 | 10 | 0 | 0
913.8 | 49.55 | 49.5 | 1 | 1 | 10 | 49.71 | 1 | 0.84412 | 8.4412 | 9.2206 | 9.2206 | 0 | 12 | 1 | 1 | 9.2206 | 10 | 0 | 0
913.85 | 49.58 | 49.5 | 1 | 1 | 10 | 49.68 | 1 | 0.94412 | 9.4412 | 9.7206 | 9.7206 | 0 | 12 | 1 | 1 | 9.7206 | 10 | 0 | 0
913.9 | 49.6 | 49.5 | 1 | 1 | 10 | 49.65 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
913.95 | 49.63 | 49.5 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
914 | 49.65 | 49.5 | 1 | 1 | 10 | 49.65 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
914.05 | 49.68 | 49.5 | 1 | 1 | 10 | 49.68 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
914.1 | 49.71 | 49.5 | 1 | 1 | 10 | 49.71 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
914.15 | 49.73 | 49.5 | 1 | 1 | 10 | 49.73 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
914.2 | 49.76 | 49.5 | 1 | 1 | 10 | 49.76 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
914.25 | 49.78 | 49.5 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
914.3 | 49.81 | 49.53 | 1 | 1 | 10 | 49.81 | 0.905 | 0.905 | 9.05 | 9.525 | 9.525 | 0 | 12 | 1 | 1 | 9.525 | 10 | 0 | 0
914.35 | 49.83 | 49.55 | 1 | 1 | 10 | 49.83 | 0.715 | 0.715 | 7.15 | 8.575 | 8.575 | 0 | 12 | 1 | 1 | 8.575 | 10 | 0 | 0
914.4 | 49.86 | 49.58 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
914.45 | 49.88 | 49.6 | 1 | 1 | 10 | 49.88 | 0.24 | 0.24 | 2.4 | 6.2 | 6.2 | 0 | 12 | 1 | 1 | 6.2 | 10 | 0 | 0
914.5 | 49.91 | 49.63 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
914.55 | 49.94 | 49.65 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
914.6 | 49.96 | 49.68 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
914.65 | 49.99 | 49.71 | 1 | 1 | 10 | 49.99 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
914.7 | 50.01 | 49.73 | 1 | 1 | 10 | 50.01 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
914.75 | 50.04 | 49.76 | 1 | 1 | 10 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 4.9265 | 4.9265 | 0 | 12 | 1 | 1 | 4.9265 | 10 | 0 | 0
914.8 | 50.06 | 49.78 | 1 | 1 | 10 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 4.8676 | 4.8676 | 0 | 12 | 1 | 1 | 4.8676 | 10 | 0 | 0
914.85 | 50.09 | 49.81 | 0.905 | 0.905 | 9.05 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 4.3044 | 4.3044 | 0 | 12 | 1 | 1 | 4.3044 | 10 | 0 | 0
914.9 | 50.12 | 49.83 | 0.715 | 0.805 | 8.05 | 50.12 | -0.24 | -0.24 | -2.4 | 2.825 | 2.825 | 0 | 12 | 1 | 1 | 2.825 | 10 | 0 | 0
914.95 | 50.14 | 49.86 | 0.43 | 0.705 | 7.05 | 50.14 | -0.43 | -0.43 | -4.3 | 1.375 | 1.375 | 0 | 12 | 1 | 1 | 1.375 | 10 | 0 | 0
915 | 50.17 | 49.88 | 0.24 | 0.605 | 6.05 | 50.17 | -0.715 | -0.715 | -7.15 | -0.55 | -0.55 | 0 | 12 | 1 | 1 | -0.55 | 10 | 0 | 0
915.05 | 50.19 | 49.91 | 0.044118 | 0.505 | 5.05 | 50.19 | -0.905 | -0.905 | -9.05 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
915.1 | 50.22 | 49.94 | 0.026471 | 0.405 | 4.05 | 50.22 | -1 | -1 | -10 | -2.975 | -2.975 | 0 | 12 | 1 | 1 | -2.975 | 10 | 0 | 0
915.15 | 50.24 | 49.96 | 0.014706 | 0.305 | 3.05 | 50.24 | -1 | -1 | -10 | -3.475 | -3.475 | 0 | 12 | 1 | 1 | -3.475 | 10 | 0 | 0
915.2 | 50.27 | 49.99 | 0 | 0.205 | 2.05 | 50.27 | -1 | -1 | -10 | -3.975 | -3.975 | 0 | 12 | 1 | 1 | -3.975 | 10 | 0 | 0
915.25 | 50.29 | 50.01 | 0 | 0.105 | 1.05 | 50.29 | -1 | -1 | -10 | -4.475 | -4.475 | 0 | 12 | 1 | 1 | -4.475 | 10 | 0 | 0
915.3 | 50.32 | 50.04 | -0.014706 | 0.005 | 0.05 | 50.32 | -1 | -1 | -10 | -4.975 | -4.975 | 0 | 12 | 1 | 1 | -4.975 | 10 | 0 | 0
915.35 | 50.35 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.35 | -1 | -1 | -10 | -5.1324 | -5.1324 | 0 | 12 | 1 | 1 | -5.1324 | 10 | 0 | 0
915.4 | 50.37 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 50.37 | -1 | -1 | -10 | -5.2206 | -5.2206 | 0 | 12 | 1 | 1 | -5.2206 | 10 | 0 | 0
915.45 | 50.4 | 50.12 | -0.24 | -0.14412 | -1.4412 | 50.4 | -1 | -1 | -10 | -5.7206 | -5.7206 | 0 | 12 | 1 | 1 | -5.7206 | 10 | 0 | 0
915.5 | 50.42 | 50.14 | -0.43 | -0.24412 | -2.4412 | 50.42 | -1 | -1 | -10 | -6.2206 | -6.2206 | 0 | 12 | 1 | 1 | -6.2206 | 10 | 0 | 0
915.55 | 50.45 | 50.17 | -0.715 | -0.34412 | -3.4412 | 50.45 | -1 | -1 | -10 | -6.7206 | -6.7206 | 0 | 12 | 1 | 1 | -6.7206 | 10 | 0 | 0
915.6 | 50.47 | 50.19 | -0.905 | -0.44412 | -4.4412 | 50.47 | -1 | -1 | -10 | -7.2206 | -7.2206 | 0 | 12 | 1 | 1 | -7.2206 | 10 | 0 | 0
915.65 | 50.5 | 50.22 | -1 | -0.54412 | -5.4412 | 50.5 | -1 | -1 | -10 | -7.7206 | -7.7206 | 0 | 12 | 1 | 1 | -7.7206 | 10 | 0 | 0
915.7 | 50.5 | 50.24 | -1 | -0.64412 | -6.4412 | 50.5 | -1 | -1 | -10 | -8.2206 | -8.2206 | 0 | 12 | 1 | 1 | -8.2206 | 10 | 0 | 0
915.75 | 50.47 | 50.27 | -1 | -0.74412 | -7.4412 | 50.5 | -1 | -1 | -10 | -8.7206 | -8.7206 | 0 | 12 | 1 | 1 | -8.7206 | 10 | 0 | 0
915.8 | 50.45 | 50.29 | -1 | -0.84412 | -8.4412 | 50.5 | -1 | -1 | -10 | -9.2206 | -9.2206 | 0 | 12 | 1 | 1 | -9.2206 | 10 | 0 | 0
915.85 | 50.42 | 50.32 | -1 | -0.94412 | -9.4412 | 50.5 | -1 | -1 | -10 | -9.7206 | -9.7206 | 0 | 12 | 1 | 1 | -9.7206 | 10 | 0 | 0
915.9 | 50.39 | 50.35 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
915.95 | 50.37 | 50.37 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
916 | 50.34 | 50.34 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
916.05 | 50.32 | 50.32 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
916.1 | 50.29 | 50.29 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
916.15 | 50.26 | 50.26 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
916.2 | 50.24 | 50.24 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
916.25 | 50.21 | 50.21 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
916.3 | 50.18 | 50.18 | -0.81 | -0.81 | -8.1 | 50.47 | -1 | -1 | -10 | -9.05 | -9.05 | 0 | 12 | 1 | 1 | -9.05 | 10 | 0 | 0
916.35 | 50.16 | 50.16 | -0.62 | -0.62 | -6.2 | 50.45 | -1 | -1 | -10 | -8.1 | -8.1 | 0 | 12 | 1 | 1 | -8.1 | 10 | 0 | 0
916.4 | 50.13 | 50.13 | -0.335 | -0.335 | -3.35 | 50.42 | -1 | -1 | -10 | -6.675 | -6.675 | 0 | 12 | 1 | 1 | -6.675 | 10 | 0 | 0
916.45 | 50.11 | 50.11 | -0.145 | -0.145 | -1.45 | 50.39 | -1 | -1 | -10 | -5.725 | -5.725 | 0 | 12 | 1 | 1 | -5.725 | 10 | 0 | 0
916.5 | 50.08 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 50.37 | -1 | -1 | -10 | -5.1912 | -5.1912 | 0 | 12 | 1 | 1 | -5.1912 | 10 | 0 | 0
916.55 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.34 | -1 | -1 | -10 | -5.1029 | -5.1029 | 0 | 12 | 1 | 1 | -5.1029 | 10 | 0 | 0
916.6 | 50.03 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 50.32 | -1 | -1 | -10 | -5.0441 | -5.0441 | 0 | 12 | 1 | 1 | -5.0441 | 10 | 0 | 0
916.65 | 50 | 50 | 0 | 0 | 0 | 50.29 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
916.7 | 50 | 50 | 0 | 0 | 0 | 50.26 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
916.75 | 50 | 50 | 0 | 0 | 0 | 50.24 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
916.8 | 50 | 50 | 0 | 0 | 0 | 50.21 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
916.85 | 50 | 50 | 0 | 0 | 0 | 50.18 | -0.81 | -0.9 | -9 | -4.5 | -4.5 | 0 | 12 | 1 | 1 | -4.5 | 10 | 0 | 0
916.9 | 50 | 50 | 0 | 0 | 0 | 50.16 | -0.62 | -0.8 | -8 | -4 | -4 | 0 | 12 | 1 | 1 | -4 | 10 | 0 | 0
916.95 | 50 | 50 | 0 | 0 | 0 | 50.13 | -0.335 | -0.7 | -7 | -3.5 | -3.5 | 0 | 12 | 1 | 1 | -3.5 | 10 | 0 | 0
917 | 50.01 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.6 | -6 | -3 | -3 | 0 | 12 | 1 | 1 | -3 | 10 | 0 | 0
917.05 | 50.01 | 50 | 0 | 0 | 0 | 50.08 | -0.038235 | -0.5 | -5 | -2.5 | -2.5 | 0 | 12 | 1 | 1 | -2.5 | 10 | 0 | 0
917.1 | 49.99 | 49.99 | 0 | 0 | 0 | 50.05 | -0.020588 | -0.4 | -4 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
917.15 | 49.99 | 49.99 | 0 | 0 | 0 | 50.03 | -0.0088235 | -0.3 | -3 | -1.5 | -1.5 | 0 | 12 | 1 | 1 | -1.5 | 10 | 0 | 0
917.2 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | -0.2 | -2 | -0.83824 | -0.83824 | 0 | 12 | 1 | 1 | -0.83824 | 10 | 0 | 0
917.25 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | -0.1 | -1 | -0.33824 | -0.33824 | 0 | 12 | 1 | 1 | -0.33824 | 10 | 0 | 0
917.3 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
917.35 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
917.4 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
917.45 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
917.5 | 49.89 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
917.55 | 49.89 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
917.6 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50.01 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
917.65 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
917.7 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
917.75 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 2.7868 | 2.7868 | 0 | 12 | 1 | 1 | 2.7868 | 10 | 0 | 0
917.8 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 2.7868 | 2.7868 | 0 | 12 | 1 | 1 | 2.7868 | 10 | 0 | 0
917.85 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 2.8456 | 2.8456 | 0 | 12 | 1 | 1 | 2.8456 | 10 | 0 | 0
917.9 | 49.94 | 49.85 | 0.525 | 0.525 | 5.25 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 2.7574 | 2.7574 | 0 | 12 | 1 | 1 | 2.7574 | 10 | 0 | 0
917.95 | 49.94 | 49.85 | 0.525 | 0.525 | 5.25 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 2.7574 | 2.7574 | 0 | 12 | 1 | 1 | 2.7574 | 10 | 0 | 0
918 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
918.05 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
918.1 | 49.93 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
918.15 | 49.93 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
918.2 | 49.96 | 49.85 | 0.525 | 0.525 | 5.25 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 2.6985 | 2.6985 | 0 | 12 | 1 | 1 | 2.6985 | 10 | 0 | 0
918.25 | 49.96 | 49.85 | 0.525 | 0.525 | 5.25 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 2.6985 | 2.6985 | 0 | 12 | 1 | 1 | 2.6985 | 10 | 0 | 0
918.3 | 49.99 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
918.35 | 49.99 | 49.91 | 0.044118 | 0.425 | 4.25 | 49.99 | 0 | 0 | 0 | 2.125 | 2.125 | 0 | 12 | 1 | 1 | 2.125 | 10 | 0 | 0
918.4 | 49.99 | 49.91 | 0.044118 | 0.325 | 3.25 | 49.99 | 0 | 0 | 0 | 1.625 | 1.625 | 0 | 12 | 1 | 1 | 1.625 | 10 | 0 | 0
918.45 | 49.99 | 49.93 | 0.032353 | 0.225 | 2.25 | 49.99 | 0 | 0 | 0 | 1.125 | 1.125 | 0 | 12 | 1 | 1 | 1.125 | 10 | 0 | 0
918.5 | 49.96 | 49.93 | 0.032353 | 0.125 | 1.25 | 49.99 | 0 | 0 | 0 | 0.625 | 0.625 | 0 | 12 | 1 | 1 | 0.625 | 10 | 0 | 0
918.55 | 49.96 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 49.99 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
918.6 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
918.65 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
918.7 | 50.05 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.058824 | 0.058824 | 0 | 12 | 1 | 1 | 0.058824 | 10 | 0 | 0
918.75 | 50.05 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
918.8 | 49.97 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
918.85 | 49.97 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
918.9 | 49.92 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
918.95 | 49.92 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
919 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
919.05 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
919.1 | 49.94 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
919.15 | 49.94 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
919.2 | 50.01 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
919.25 | 50.01 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
919.3 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
919.35 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
919.4 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
919.45 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
919.5 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
919.55 | 49.95 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
919.6 | 49.97 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
919.65 | 49.97 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
919.7 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
919.75 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
919.8 | 49.87 | 49.87 | 0.335 | 0.335 | 3.35 | 50.01 | 0 | 0 | 0 | 1.675 | 1.675 | 0 | 12 | 1 | 1 | 1.675 | 10 | 0 | 0
919.85 | 49.87 | 49.87 | 0.335 | 0.335 | 3.35 | 49.99 | 0 | 0 | 0 | 1.675 | 1.675 | 0 | 12 | 1 | 1 | 1.675 | 10 | 0 | 0
919.9 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
919.95 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 2.6691 | 2.6691 | 0 | 12 | 1 | 1 | 2.6691 | 10 | 0 | 0
920 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
920.05 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
920.1 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
920.15 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
920.2 | 49.84 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
920.25 | 49.84 | 49.79 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
920.3 | 49.89 | 49.79 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
920.35 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.12647 | 1.2647 | 5.6324 | 5.6324 | 0 | 12 | 1 | 1 | 5.6324 | 10 | 0 | 0
920.4 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.145 | 1.45 | 5.725 | 5.725 | 0 | 12 | 1 | 1 | 5.725 | 10 | 0 | 0
920.45 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.145 | 1.45 | 5.725 | 5.725 | 0 | 12 | 1 | 1 | 5.725 | 10 | 0 | 0
920.5 | 49.96 | 49.79 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
920.55 | 49.96 | 49.79 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
920.6 | 50.02 | 49.79 | 1 | 1 | 10 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 4.9853 | 4.9853 | 0 | 12 | 1 | 1 | 4.9853 | 10 | 0 | 0
920.65 | 50.02 | 49.79 | 1 | 1 | 10 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 4.9853 | 4.9853 | 0 | 12 | 1 | 1 | 4.9853 | 10 | 0 | 0
920.7 | 50.03 | 49.79 | 1 | 1 | 10 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.9559 | 4.9559 | 0 | 12 | 1 | 1 | 4.9559 | 10 | 0 | 0
920.75 | 50.03 | 49.84 | 0.62 | 0.9 | 9 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.4559 | 4.4559 | 0 | 12 | 1 | 1 | 4.4559 | 10 | 0 | 0
920.8 | 50.02 | 49.84 | 0.62 | 0.8 | 8 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 3.9559 | 3.9559 | 0 | 12 | 1 | 1 | 3.9559 | 10 | 0 | 0
920.85 | 50.02 | 49.89 | 0.145 | 0.7 | 7 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 3.4559 | 3.4559 | 0 | 12 | 1 | 1 | 3.4559 | 10 | 0 | 0
920.9 | 50.08 | 49.89 | 0.145 | 0.6 | 6 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 2.8088 | 2.8088 | 0 | 12 | 1 | 1 | 2.8088 | 10 | 0 | 0
920.95 | 50.08 | 49.89 | 0.145 | 0.5 | 5 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 2.3088 | 2.3088 | 0 | 12 | 1 | 1 | 2.3088 | 10 | 0 | 0
921 | 50.01 | 49.89 | 0.145 | 0.4 | 4 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 1.8088 | 1.8088 | 0 | 12 | 1 | 1 | 1.8088 | 10 | 0 | 0
921.05 | 50.01 | 49.96 | 0.014706 | 0.3 | 3 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 1.3088 | 1.3088 | 0 | 12 | 1 | 1 | 1.3088 | 10 | 0 | 0
921.1 | 49.94 | 49.94 | 0.026471 | 0.2 | 2 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.80882 | 0.80882 | 0 | 12 | 1 | 1 | 0.80882 | 10 | 0 | 0
921.15 | 49.94 | 49.94 | 0.026471 | 0.1 | 1 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.30882 | 0.30882 | 0 | 12 | 1 | 1 | 0.30882 | 10 | 0 | 0
921.2 | 50 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
921.25 | 50 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
921.3 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
921.35 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
921.4 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
921.45 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
921.5 | 49.92 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
921.55 | 49.92 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
921.6 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50.01 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
921.65 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
921.7 | 49.92 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
921.75 | 49.92 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
921.8 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
921.85 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
921.9 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
921.95 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
922 | 49.87 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
922.05 | 49.87 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
922.1 | 49.8 | 49.8 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
922.15 | 49.8 | 49.8 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
922.2 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
922.25 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
922.3 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
922.35 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
922.4 | 49.72 | 49.72 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
922.45 | 49.72 | 49.72 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
922.5 | 49.67 | 49.67 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
922.55 | 49.67 | 49.67 | 1 | 1 | 10 | 49.87 | 0.335 | 0.14412 | 1.4412 | 5.7206 | 5.7206 | 0 | 12 | 1 | 1 | 5.7206 | 10 | 0 | 0
922.6 | 49.65 | 49.65 | 1 | 1 | 10 | 49.87 | 0.335 | 0.24412 | 2.4412 | 6.2206 | 6.2206 | 0 | 12 | 1 | 1 | 6.2206 | 10 | 0 | 0
922.65 | 49.65 | 49.65 | 1 | 1 | 10 | 49.8 | 1 | 0.34412 | 3.4412 | 6.7206 | 6.7206 | 0 | 12 | 1 | 1 | 6.7206 | 10 | 0 | 0
922.7 | 49.59 | 49.59 | 1 | 1 | 10 | 49.8 | 1 | 0.44412 | 4.4412 | 7.2206 | 7.2206 | 0 | 12 | 1 | 1 | 7.2206 | 10 | 0 | 0
922.75 | 49.59 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.54412 | 5.4412 | 7.7206 | 7.7206 | 0 | 12 | 1 | 1 | 7.7206 | 10 | 0 | 0
922.8 | 49.66 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.64412 | 6.4412 | 8.2206 | 8.2206 | 0 | 12 | 1 | 1 | 8.2206 | 10 | 0 | 0
922.85 | 49.66 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.74412 | 7.4412 | 8.7206 | 8.7206 | 0 | 12 | 1 | 1 | 8.7206 | 10 | 0 | 0
922.9 | 49.63 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.84412 | 8.4412 | 9.2206 | 9.2206 | 0 | 12 | 1 | 1 | 9.2206 | 10 | 0 | 0
922.95 | 49.63 | 49.59 | 1 | 1 | 10 | 49.72 | 1 | 0.94412 | 9.4412 | 9.7206 | 9.7206 | 0 | 12 | 1 | 1 | 9.7206 | 10 | 0 | 0
923 | 49.61 | 49.59 | 1 | 1 | 10 | 49.72 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
923.05 | 49.61 | 49.59 | 1 | 1 | 10 | 49.67 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
923.1 | 49.54 | 49.54 | 1 | 1 | 10 | 49.67 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
923.15 | 49.54 | 49.54 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
923.2 | 49.46 | 49.46 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
923.25 | 49.46 | 49.46 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
923.3 | 49.45 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
923.35 | 49.45 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
923.4 | 49.51 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
923.45 | 49.51 | 49.45 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
923.5 | 49.5 | 49.45 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
923.55 | 49.5 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
923.6 | 49.54 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
923.65 | 49.54 | 49.45 | 1 | 1 | 10 | 49.54 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
923.7 | 49.59 | 49.45 | 1 | 1 | 10 | 49.59 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
923.75 | 49.59 | 49.45 | 1 | 1 | 10 | 49.59 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
923.8 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
923.85 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
923.9 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
923.95 | 49.61 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
924 | 49.53 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
924.05 | 49.53 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
924.1 | 49.54 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
924.15 | 49.54 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
924.2 | 49.61 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
924.25 | 49.61 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
924.3 | 49.66 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
924.35 | 49.66 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
924.4 | 49.64 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
924.45 | 49.64 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
924.5 | 49.69 | 49.53 | 1 | 1 | 10 | 49.69 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
924.55 | 49.69 | 49.53 | 1 | 1 | 10 | 49.69 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
924.6 | 49.74 | 49.53 | 1 | 1 | 10 | 49.74 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
924.65 | 49.74 | 49.54 | 1 | 1 | 10 | 49.74 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
924.7 | 49.78 | 49.54 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
924.75 | 49.78 | 49.61 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
924.8 | 49.82 | 49.61 | 1 | 1 | 10 | 49.82 | 0.81 | 0.81 | 8.1 | 9.05 | 9.05 | 0 | 12 | 1 | 1 | 9.05 | 10 | 0 | 0
924.85 | 49.82 | 49.64 | 1 | 1 | 10 | 49.82 | 0.81 | 0.81 | 8.1 | 9.05 | 9.05 | 0 | 12 | 1 | 1 | 9.05 | 10 | 0 | 0
924.9 | 49.86 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
924.95 | 49.86 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
925 | 49.84 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
925.05 | 49.84 | 49.69 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
925.1 | 49.91 | 49.69 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
925.15 | 49.91 | 49.74 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
925.2 | 49.97 | 49.74 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
925.25 | 49.97 | 49.78 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
925.3 | 50.03 | 49.78 | 1 | 1 | 10 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.9559 | 4.9559 | 0 | 12 | 1 | 1 | 4.9559 | 10 | 0 | 0
925.35 | 50.03 | 49.82 | 0.81 | 0.9 | 9 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.4559 | 4.4559 | 0 | 12 | 1 | 1 | 4.4559 | 10 | 0 | 0
925.4 | 50.05 | 49.82 | 0.81 | 0.81 | 8.1 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 3.9471 | 3.9471 | 0 | 12 | 1 | 1 | 3.9471 | 10 | 0 | 0
925.45 | 50.05 | 49.84 | 0.62 | 0.71 | 7.1 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 3.4471 | 3.4471 | 0 | 12 | 1 | 1 | 3.4471 | 10 | 0 | 0
925.5 | 50.01 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
925.55 | 50.01 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
925.6 | 49.95 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
925.65 | 49.95 | 49.91 | 0.044118 | 0.52 | 5.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.4971 | 2.4971 | 0 | 12 | 1 | 1 | 2.4971 | 10 | 0 | 0
925.7 | 49.99 | 49.91 | 0.044118 | 0.42 | 4.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 1.9971 | 1.9971 | 0 | 12 | 1 | 1 | 1.9971 | 10 | 0 | 0
925.75 | 49.99 | 49.95 | 0.020588 | 0.32 | 3.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 1.4971 | 1.4971 | 0 | 12 | 1 | 1 | 1.4971 | 10 | 0 | 0
925.8 | 49.92 | 49.92 | 0.038235 | 0.22 | 2.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.99706 | 0.99706 | 0 | 12 | 1 | 1 | 0.99706 | 10 | 0 | 0
925.85 | 49.92 | 49.92 | 0.038235 | 0.12 | 1.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.49706 | 0.49706 | 0 | 12 | 1 | 1 | 0.49706 | 10 | 0 | 0
925.9 | 49.97 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
925.95 | 49.97 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
926 | 50.02 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
926.05 | 50.02 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.17647 | 0.17647 | 0 | 12 | 1 | 1 | 0.17647 | 10 | 0 | 0
926.1 | 50.07 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
926.15 | 50.07 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
926.2 | 50.06 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
926.25 | 50.06 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
926.3 | 50.13 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
926.35 | 50.13 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
926.4 | 50.09 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
926.45 | 50.09 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6309 | -1.6309 | 0 | 12 | 1 | 1 | -1.6309 | 10 | 0 | 0
926.5 | 50.07 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6309 | -1.6309 | 0 | 12 | 1 | 1 | -1.6309 | 10 | 0 | 0
926.55 | 50.07 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6897 | -1.6897 | 0 | 12 | 1 | 1 | -1.6897 | 10 | 0 | 0
926.6 | 50.07 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6897 | -1.6897 | 0 | 12 | 1 | 1 | -1.6897 | 10 | 0 | 0
926.65 | 50.07 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.13 | -0.335 | -0.335 | -3.35 | -1.8074 | -1.8074 | 0 | 12 | 1 | 1 | -1.8074 | 10 | 0 | 0
926.7 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.13 | -0.335 | -0.335 | -3.35 | -1.7779 | -1.7779 | 0 | 12 | 1 | 1 | -1.7779 | 10 | 0 | 0
926.75 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.13 | -0.335 | -0.335 | -3.35 | -1.7779 | -1.7779 | 0 | 12 | 1 | 1 | -1.7779 | 10 | 0 | 0
926.8 | 50.01 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
926.85 | 50.01 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
926.9 | 50.07 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
926.95 | 50.07 | 50.01 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.235 | -2.35 | -1.175 | -1.175 | 0 | 12 | 1 | 1 | -1.175 | 10 | 0 | 0
927 | 50.05 | 50.01 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.135 | -1.35 | -0.675 | -0.675 | 0 | 12 | 1 | 1 | -0.675 | 10 | 0 | 0
927.05 | 50.05 | 50.01 | 0 | 0 | 0 | 50.07 | -0.032353 | -0.035 | -0.35 | -0.175 | -0.175 | 0 | 12 | 1 | 1 | -0.175 | 10 | 0 | 0
927.1 | 50.1 | 50.01 | 0 | 0 | 0 | 50.1 | -0.05 | -0.05 | -0.5 | -0.25 | -0.25 | 0 | 12 | 1 | 1 | -0.25 | 10 | 0 | 0
927.15 | 50.1 | 50.01 | 0 | 0 | 0 | 50.1 | -0.05 | -0.05 | -0.5 | -0.25 | -0.25 | 0 | 12 | 1 | 1 | -0.25 | 10 | 0 | 0
927.2 | 50.11 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
927.25 | 50.11 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
927.3 | 50.06 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
927.35 | 50.06 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
927.4 | 50.04 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
927.45 | 50.04 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
927.5 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
927.55 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
927.6 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
927.65 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
927.7 | 50.11 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
927.75 | 50.11 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
927.8 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
927.85 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
927.9 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
927.95 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
928 | 50.02 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.11 | -0.145 | -0.145 | -1.45 | -0.73971 | -0.73971 | 0 | 12 | 1 | 1 | -0.73971 | 10 | 0 | 0
928.05 | 50.02 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.11 | -0.145 | -0.145 | -1.45 | -0.73971 | -0.73971 | 0 | 12 | 1 | 1 | -0.73971 | 10 | 0 | 0
928.1 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
928.15 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
928.2 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
928.25 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
928.3 | 50.01 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
928.35 | 50.01 | 50 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.045 | -0.45 | -0.225 | -0.225 | 0 | 12 | 1 | 1 | -0.225 | 10 | 0 | 0
928.4 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
928.45 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
928.5 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
928.55 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
928.6 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.14706 | 0.14706 | 0 | 12 | 1 | 1 | 0.14706 | 10 | 0 | 0
928.65 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
928.7 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
928.75 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
928.8 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
928.85 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
928.9 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
928.95 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
929 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
929.05 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
929.1 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
929.15 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
929.2 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
929.25 | 50 | 50 | 0 | 0 | 0 | 50.01 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
929.3 | 49.5 | 49.5 | 1 | 1 | 10 | 50.01 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
929.35 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
929.4 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
929.45 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
929.5 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
929.55 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
929.6 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
929.65 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
929.7 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
929.75 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
929.8 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
929.85 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.1 | 1 | 5.5 | 5.5 | 0 | 12 | 1 | 1 | 5.5 | 10 | 0 | 0
929.9 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.2 | 2 | 6 | 6 | 0 | 12 | 1 | 1 | 6 | 10 | 0 | 0
929.95 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.3 | 3 | 6.5 | 6.5 | 0 | 12 | 1 | 1 | 6.5 | 10 | 0 | 0
930 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.4 | 4 | 7 | 7 | 0 | 12 | 1 | 1 | 7 | 10 | 0 | 0
930.05 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.5 | 5 | 7.5 | 7.5 | 0 | 12 | 1 | 1 | 7.5 | 10 | 0 | 0
930.1 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.6 | 6 | 8 | 8 | 0 | 12 | 1 | 1 | 8 | 10 | 0 | 0
930.15 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.7 | 7 | 8.5 | 8.5 | 0 | 12 | 1 | 1 | 8.5 | 10 | 0 | 0
930.2 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.8 | 8 | 9 | 9 | 0 | 12 | 1 | 1 | 9 | 10 | 0 | 0
930.25 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.9 | 9 | 9.5 | 9.5 | 0 | 12 | 1 | 1 | 9.5 | 10 | 0 | 0
930.3 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
930.35 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
930.4 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
930.45 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
930.5 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
930.55 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
930.6 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
930.65 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
930.7 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
930.75 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
930.8 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
930.85 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
930.9 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
930.95 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
931 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
931.05 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
931.1 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
931.15 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
931.2 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
931.25 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
931.3 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
931.35 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
931.4 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
931.45 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
931.5 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
931.55 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
931.6 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
931.65 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
931.7 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
931.75 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
931.8 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
931.85 | 50.5 | 50.5 | -1 | 0.9 | 9 | 50.5 | -1 | -1 | -10 | -0.5 | -0.5 | 0 | 12 | 1 | 1 | -0.5 | 10 | 0 | 0
931.9 | 50.5 | 50.5 | -1 | 0.8 | 8 | 50.5 | -1 | -1 | -10 | -1 | -1 | 0 | 12 | 1 | 1 | -1 | 10 | 0 | 0
931.95 | 50.5 | 50.5 | -1 | 0.7 | 7 | 50.5 | -1 | -1 | -10 | -1.5 | -1.5 | 0 | 12 | 1 | 1 | -1.5 | 10 | 0 | 0
932 | 50.5 | 50.5 | -1 | 0.6 | 6 | 50.5 | -1 | -1 | -10 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
932.05 | 50.5 | 50.5 | -1 | 0.5 | 5 | 50.5 | -1 | -1 | -10 | -2.5 | -2.5 | 0 | 12 | 1 | 1 | -2.5 | 10 | 0 | 0
932.1 | 50.5 | 50.5 | -1 | 0.4 | 4 | 50.5 | -1 | -1 | -10 | -3 | -3 | 0 | 12 | 1 | 1 | -3 | 10 | 0 | 0
932.15 | 50.5 | 50.5 | -1 | 0.3 | 3 | 50.5 | -1 | -1 | -10 | -3.5 | -3.5 | 0 | 12 | 1 | 1 | -3.5 | 10 | 0 | 0
932.2 | 50.5 | 50.5 | -1 | 0.2 | 2 | 50.5 | -1 | -1 | -10 | -4 | -4 | 0 | 12 | 1 | 1 | -4 | 10 | 0 | 0
932.25 | 50.5 | 50.5 | -1 | 0.1 | 1 | 50.5 | -1 | -1 | -10 | -4.5 | -4.5 | 0 | 12 | 1 | 1 | -4.5 | 10 | 0 | 0
932.3 | 50.5 | 50.5 | -1 | 0 | 0 | 50.5 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
932.35 | 50.5 | 50.5 | -1 | -0.1 | -1 | 50.5 | -1 | -1 | -10 | -5.5 | -5.5 | 0 | 12 | 1 | 1 | -5.5 | 10 | 0 | 0
932.4 | 50.5 | 50.5 | -1 | -0.2 | -2 | 50.5 | -1 | -1 | -10 | -6 | -6 | 0 | 12 | 1 | 1 | -6 | 10 | 0 | 0
932.45 | 50.5 | 50.5 | -1 | -0.3 | -3 | 50.5 | -1 | -1 | -10 | -6.5 | -6.5 | 0 | 12 | 1 | 1 | -6.5 | 10 | 0 | 0
932.5 | 50.5 | 50.5 | -1 | -0.4 | -4 | 50.5 | -1 | -1 | -10 | -7 | -7 | 0 | 12 | 1 | 1 | -7 | 10 | 0 | 0
932.55 | 50.5 | 50.5 | -1 | -0.5 | -5 | 50.5 | -1 | -1 | -10 | -7.5 | -7.5 | 0 | 12 | 1 | 1 | -7.5 | 10 | 0 | 0
932.6 | 50.5 | 50.5 | -1 | -0.6 | -6 | 50.5 | -1 | -1 | -10 | -8 | -8 | 0 | 12 | 1 | 1 | -8 | 10 | 0 | 0
932.65 | 50.5 | 50.5 | -1 | -0.7 | -7 | 50.5 | -1 | -1 | -10 | -8.5 | -8.5 | 0 | 12 | 1 | 1 | -8.5 | 10 | 0 | 0
932.7 | 50.5 | 50.5 | -1 | -0.8 | -8 | 50.5 | -1 | -1 | -10 | -9 | -9 | 0 | 12 | 1 | 1 | -9 | 10 | 0 | 0
932.75 | 50.5 | 50.5 | -1 | -0.9 | -9 | 50.5 | -1 | -1 | -10 | -9.5 | -9.5 | 0 | 12 | 1 | 1 | -9.5 | 10 | 0 | 0
932.8 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
932.85 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
932.9 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
932.95 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
933 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
933.05 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
933.1 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
933.15 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
933.2 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
933.25 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
933.3 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
933.35 | 50.47 | 50.47 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
933.4 | 50.45 | 50.45 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
933.45 | 50.42 | 50.42 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
933.5 | 50.4 | 50.4 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
933.55 | 50.37 | 50.37 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
933.6 | 50.35 | 50.35 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
933.65 | 50.32 | 50.32 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
933.7 | 50.29 | 50.29 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
933.75 | 50.27 | 50.27 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
933.8 | 50.24 | 50.24 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
933.85 | 50.22 | 50.22 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
933.9 | 50.19 | 50.19 | -0.905 | -0.905 | -9.05 | 50.47 | -1 | -1 | -10 | -9.525 | -9.525 | 0 | 12 | 1 | 1 | -9.525 | 10 | 0 | 0
933.95 | 50.17 | 50.17 | -0.715 | -0.715 | -7.15 | 50.45 | -1 | -1 | -10 | -8.575 | -8.575 | 0 | 12 | 1 | 1 | -8.575 | 10 | 0 | 0
934 | 50.14 | 50.14 | -0.43 | -0.43 | -4.3 | 50.42 | -1 | -1 | -10 | -7.15 | -7.15 | 0 | 12 | 1 | 1 | -7.15 | 10 | 0 | 0
934.05 | 50.12 | 50.12 | -0.24 | -0.24 | -2.4 | 50.4 | -1 | -1 | -10 | -6.2 | -6.2 | 0 | 12 | 1 | 1 | -6.2 | 10 | 0 | 0
934.1 | 50.09 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 50.37 | -1 | -1 | -10 | -5.2206 | -5.2206 | 0 | 12 | 1 | 1 | -5.2206 | 10 | 0 | 0
934.15 | 50.06 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.35 | -1 | -1 | -10 | -5.1324 | -5.1324 | 0 | 12 | 1 | 1 | -5.1324 | 10 | 0 | 0
934.2 | 50.04 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.32 | -1 | -1 | -10 | -5.0735 | -5.0735 | 0 | 12 | 1 | 1 | -5.0735 | 10 | 0 | 0
934.25 | 50.01 | 50.01 | 0 | 0 | 0 | 50.29 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
934.3 | 49.99 | 49.99 | 0 | 0 | 0 | 50.27 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
934.35 | 49.96 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.24 | -1 | -1 | -10 | -4.9265 | -4.9265 | 0 | 12 | 1 | 1 | -4.9265 | 10 | 0 | 0
934.4 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.22 | -1 | -1 | -10 | -4.8676 | -4.8676 | 0 | 12 | 1 | 1 | -4.8676 | 10 | 0 | 0
934.45 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.19 | -0.905 | -0.905 | -9.05 | -4.3044 | -4.3044 | 0 | 12 | 1 | 1 | -4.3044 | 10 | 0 | 0
934.5 | 49.88 | 49.88 | 0.24 | 0.24 | 2.4 | 50.17 | -0.715 | -0.805 | -8.05 | -2.825 | -2.825 | 0 | 12 | 1 | 1 | -2.825 | 10 | 0 | 0
934.55 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.14 | -0.43 | -0.705 | -7.05 | -1.375 | -1.375 | 0 | 12 | 1 | 1 | -1.375 | 10 | 0 | 0
934.6 | 49.83 | 49.83 | 0.715 | 0.715 | 7.15 | 50.12 | -0.24 | -0.605 | -6.05 | 0.55 | 0.55 | 0 | 12 | 1 | 1 | 0.55 | 10 | 0 | 0
934.65 | 49.81 | 49.81 | 0.905 | 0.905 | 9.05 | 50.09 | -0.044118 | -0.505 | -5.05 | 2 | 2 | 0 | 12 | 1 | 1 | 2 | 10 | 0 | 0
934.7 | 49.78 | 49.78 | 1 | 1 | 10 | 50.06 | -0.026471 | -0.405 | -4.05 | 2.975 | 2.975 | 0 | 12 | 1 | 1 | 2.975 | 10 | 0 | 0
934.75 | 49.76 | 49.76 | 1 | 1 | 10 | 50.04 | -0.014706 | -0.305 | -3.05 | 3.475 | 3.475 | 0 | 12 | 1 | 1 | 3.475 | 10 | 0 | 0
934.8 | 49.73 | 49.73 | 1 | 1 | 10 | 50.01 | 0 | -0.205 | -2.05 | 3.975 | 3.975 | 0 | 12 | 1 | 1 | 3.975 | 10 | 0 | 0
934.85 | 49.71 | 49.71 | 1 | 1 | 10 | 49.99 | 0 | -0.105 | -1.05 | 4.475 | 4.475 | 0 | 12 | 1 | 1 | 4.475 | 10 | 0 | 0
934.9 | 49.68 | 49.68 | 1 | 1 | 10 | 49.96 | 0.014706 | -0.005 | -0.05 | 4.975 | 4.975 | 0 | 12 | 1 | 1 | 4.975 | 10 | 0 | 0
934.95 | 49.65 | 49.65 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
935 | 49.63 | 49.63 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
935.05 | 49.6 | 49.6 | 1 | 1 | 10 | 49.88 | 0.24 | 0.14412 | 1.4412 | 5.7206 | 5.7206 | 0 | 12 | 1 | 1 | 5.7206 | 10 | 0 | 0
935.1 | 49.58 | 49.58 | 1 | 1 | 10 | 49.86 | 0.43 | 0.24412 | 2.4412 | 6.2206 | 6.2206 | 0 | 12 | 1 | 1 | 6.2206 | 10 | 0 | 0
935.15 | 49.55 | 49.55 | 1 | 1 | 10 | 49.83 | 0.715 | 0.34412 | 3.4412 | 6.7206 | 6.7206 | 0 | 12 | 1 | 1 | 6.7206 | 10 | 0 | 0
935.2 | 49.53 | 49.53 | 1 | 1 | 10 | 49.81 | 0.905 | 0.44412 | 4.4412 | 7.2206 | 7.2206 | 0 | 12 | 1 | 1 | 7.2206 | 10 | 0 | 0
935.25 | 49.5 | 49.5 | 1 | 1 | 10 | 49.78 | 1 | 0.54412 | 5.4412 | 7.7206 | 7.7206 | 0 | 12 | 1 | 1 | 7.7206 | 10 | 0 | 0
935.3 | 49.5 | 49.5 | 1 | 1 | 10 | 49.76 | 1 | 0.64412 | 6.4412 | 8.2206 | 8.2206 | 0 | 12 | 1 | 1 | 8.2206 | 10 | 0 | 0
935.35 | 49.53 | 49.5 | 1 | 1 | 10 | 49.73 | 1 | 0.74412 | 7.4412 | 8.7206 | 8.7206 | 0 | 12 | 1 | 1 | 8.7206 | 10 | 0 | 0
935.4 | 49.55 | 49.5 | 1 | 1 | 10 | 49.71 | 1 | 0.84412 | 8.4412 | 9.2206 | 9.2206 | 0 | 12 | 1 | 1 | 9.2206 | 10 | 0 | 0
935.45 | 49.58 | 49.5 | 1 | 1 | 10 | 49.68 | 1 | 0.94412 | 9.4412 | 9.7206 | 9.7206 | 0 | 12 | 1 | 1 | 9.7206 | 10 | 0 | 0
935.5 | 49.6 | 49.5 | 1 | 1 | 10 | 49.65 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
935.55 | 49.63 | 49.5 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
935.6 | 49.65 | 49.5 | 1 | 1 | 10 | 49.65 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
935.65 | 49.68 | 49.5 | 1 | 1 | 10 | 49.68 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
935.7 | 49.71 | 49.5 | 1 | 1 | 10 | 49.71 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
935.75 | 49.73 | 49.5 | 1 | 1 | 10 | 49.73 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
935.8 | 49.76 | 49.5 | 1 | 1 | 10 | 49.76 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
935.85 | 49.78 | 49.5 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
935.9 | 49.81 | 49.53 | 1 | 1 | 10 | 49.81 | 0.905 | 0.905 | 9.05 | 9.525 | 9.525 | 0 | 12 | 1 | 1 | 9.525 | 10 | 0 | 0
935.95 | 49.83 | 49.55 | 1 | 1 | 10 | 49.83 | 0.715 | 0.715 | 7.15 | 8.575 | 8.575 | 0 | 12 | 1 | 1 | 8.575 | 10 | 0 | 0
936 | 49.86 | 49.58 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
936.05 | 49.88 | 49.6 | 1 | 1 | 10 | 49.88 | 0.24 | 0.24 | 2.4 | 6.2 | 6.2 | 0 | 12 | 1 | 1 | 6.2 | 10 | 0 | 0
936.1 | 49.91 | 49.63 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
936.15 | 49.94 | 49.65 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
936.2 | 49.96 | 49.68 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
936.25 | 49.99 | 49.71 | 1 | 1 | 10 | 49.99 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
936.3 | 50.01 | 49.73 | 1 | 1 | 10 | 50.01 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
936.35 | 50.04 | 49.76 | 1 | 1 | 10 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 4.9265 | 4.9265 | 0 | 12 | 1 | 1 | 4.9265 | 10 | 0 | 0
936.4 | 50.06 | 49.78 | 1 | 1 | 10 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 4.8676 | 4.8676 | 0 | 12 | 1 | 1 | 4.8676 | 10 | 0 | 0
936.45 | 50.09 | 49.81 | 0.905 | 0.905 | 9.05 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 4.3044 | 4.3044 | 0 | 12 | 1 | 1 | 4.3044 | 10 | 0 | 0
936.5 | 50.12 | 49.83 | 0.715 | 0.805 | 8.05 | 50.12 | -0.24 | -0.24 | -2.4 | 2.825 | 2.825 | 0 | 12 | 1 | 1 | 2.825 | 10 | 0 | 0
936.55 | 50.14 | 49.86 | 0.43 | 0.705 | 7.05 | 50.14 | -0.43 | -0.43 | -4.3 | 1.375 | 1.375 | 0 | 12 | 1 | 1 | 1.375 | 10 | 0 | 0
936.6 | 50.17 | 49.88 | 0.24 | 0.605 | 6.05 | 50.17 | -0.715 | -0.715 | -7.15 | -0.55 | -0.55 | 0 | 12 | 1 | 1 | -0.55 | 10 | 0 | 0
936.65 | 50.19 | 49.91 | 0.044118 | 0.505 | 5.05 | 50.19 | -0.905 | -0.905 | -9.05 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
936.7 | 50.22 | 49.94 | 0.026471 | 0.405 | 4.05 | 50.22 | -1 | -1 | -10 | -2.975 | -2.975 | 0 | 12 | 1 | 1 | -2.975 | 10 | 0 | 0
936.75 | 50.24 | 49.96 | 0.014706 | 0.305 | 3.05 | 50.24 | -1 | -1 | -10 | -3.475 | -3.475 | 0 | 12 | 1 | 1 | -3.475 | 10 | 0 | 0
936.8 | 50.27 | 49.99 | 0 | 0.205 | 2.05 | 50.27 | -1 | -1 | -10 | -3.975 | -3.975 | 0 | 12 | 1 | 1 | -3.975 | 10 | 0 | 0
936.85 | 50.29 | 50.01 | 0 | 0.105 | 1.05 | 50.29 | -1 | -1 | -10 | -4.475 | -4.475 | 0 | 12 | 1 | 1 | -4.475 | 10 | 0 | 0
936.9 | 50.32 | 50.04 | -0.014706 | 0.005 | 0.05 | 50.32 | -1 | -1 | -10 | -4.975 | -4.975 | 0 | 12 | 1 | 1 | -4.975 | 10 | 0 | 0
936.95 | 50.35 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.35 | -1 | -1 | -10 | -5.1324 | -5.1324 | 0 | 12 | 1 | 1 | -5.1324 | 10 | 0 | 0
937 | 50.37 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 50.37 | -1 | -1 | -10 | -5.2206 | -5.2206 | 0 | 12 | 1 | 1 | -5.2206 | 10 | 0 | 0
937.05 | 50.4 | 50.12 | -0.24 | -0.14412 | -1.4412 | 50.4 | -1 | -1 | -10 | -5.7206 | -5.7206 | 0 | 12 | 1 | 1 | -5.7206 | 10 | 0 | 0
937.1 | 50.42 | 50.14 | -0.43 | -0.24412 | -2.4412 | 50.42 | -1 | -1 | -10 | -6.2206 | -6.2206 | 0 | 12 | 1 | 1 | -6.2206 | 10 | 0 | 0
937.15 | 50.45 | 50.17 | -0.715 | -0.34412 | -3.4412 | 50.45 | -1 | -1 | -10 | -6.7206 | -6.7206 | 0 | 12 | 1 | 1 | -6.7206 | 10 | 0 | 0
937.2 | 50.47 | 50.19 | -0.905 | -0.44412 | -4.4412 | 50.47 | -1 | -1 | -10 | -7.2206 | -7.2206 | 0 | 12 | 1 | 1 | -7.2206 | 10 | 0 | 0
937.25 | 50.5 | 50.22 | -1 | -0.54412 | -5.4412 | 50.5 | -1 | -1 | -10 | -7.7206 | -7.7206 | 0 | 12 | 1 | 1 | -7.7206 | 10 | 0 | 0
937.3 | 50.5 | 50.24 | -1 | -0.64412 | -6.4412 | 50.5 | -1 | -1 | -10 | -8.2206 | -8.2206 | 0 | 12 | 1 | 1 | -8.2206 | 10 | 0 | 0
937.35 | 50.47 | 50.27 | -1 | -0.74412 | -7.4412 | 50.5 | -1 | -1 | -10 | -8.7206 | -8.7206 | 0 | 12 | 1 | 1 | -8.7206 | 10 | 0 | 0
937.4 | 50.45 | 50.29 | -1 | -0.84412 | -8.4412 | 50.5 | -1 | -1 | -10 | -9.2206 | -9.2206 | 0 | 12 | 1 | 1 | -9.2206 | 10 | 0 | 0
937.45 | 50.42 | 50.32 | -1 | -0.94412 | -9.4412 | 50.5 | -1 | -1 | -10 | -9.7206 | -9.7206 | 0 | 12 | 1 | 1 | -9.7206 | 10 | 0 | 0
937.5 | 50.39 | 50.35 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
937.55 | 50.37 | 50.37 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
937.6 | 50.34 | 50.34 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
937.65 | 50.32 | 50.32 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
937.7 | 50.29 | 50.29 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
937.75 | 50.26 | 50.26 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
937.8 | 50.24 | 50.24 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
937.85 | 50.21 | 50.21 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
937.9 | 50.18 | 50.18 | -0.81 | -0.81 | -8.1 | 50.47 | -1 | -1 | -10 | -9.05 | -9.05 | 0 | 12 | 1 | 1 | -9.05 | 10 | 0 | 0
937.95 | 50.16 | 50.16 | -0.62 | -0.62 | -6.2 | 50.45 | -1 | -1 | -10 | -8.1 | -8.1 | 0 | 12 | 1 | 1 | -8.1 | 10 | 0 | 0
938 | 50.13 | 50.13 | -0.335 | -0.335 | -3.35 | 50.42 | -1 | -1 | -10 | -6.675 | -6.675 | 0 | 12 | 1 | 1 | -6.675 | 10 | 0 | 0
938.05 | 50.11 | 50.11 | -0.145 | -0.145 | -1.45 | 50.39 | -1 | -1 | -10 | -5.725 | -5.725 | 0 | 12 | 1 | 1 | -5.725 | 10 | 0 | 0
938.1 | 50.08 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 50.37 | -1 | -1 | -10 | -5.1912 | -5.1912 | 0 | 12 | 1 | 1 | -5.1912 | 10 | 0 | 0
938.15 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.34 | -1 | -1 | -10 | -5.1029 | -5.1029 | 0 | 12 | 1 | 1 | -5.1029 | 10 | 0 | 0
938.2 | 50.03 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 50.32 | -1 | -1 | -10 | -5.0441 | -5.0441 | 0 | 12 | 1 | 1 | -5.0441 | 10 | 0 | 0
938.25 | 50 | 50 | 0 | 0 | 0 | 50.29 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
938.3 | 50 | 50 | 0 | 0 | 0 | 50.26 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
938.35 | 50 | 50 | 0 | 0 | 0 | 50.24 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
938.4 | 50 | 50 | 0 | 0 | 0 | 50.21 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
938.45 | 50 | 50 | 0 | 0 | 0 | 50.18 | -0.81 | -0.9 | -9 | -4.5 | -4.5 | 0 | 12 | 1 | 1 | -4.5 | 10 | 0 | 0
938.5 | 50 | 50 | 0 | 0 | 0 | 50.16 | -0.62 | -0.8 | -8 | -4 | -4 | 0 | 12 | 1 | 1 | -4 | 10 | 0 | 0
938.55 | 50 | 50 | 0 | 0 | 0 | 50.13 | -0.335 | -0.7 | -7 | -3.5 | -3.5 | 0 | 12 | 1 | 1 | -3.5 | 10 | 0 | 0
938.6 | 50.01 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.6 | -6 | -3 | -3 | 0 | 12 | 1 | 1 | -3 | 10 | 0 | 0
938.65 | 50.01 | 50 | 0 | 0 | 0 | 50.08 | -0.038235 | -0.5 | -5 | -2.5 | -2.5 | 0 | 12 | 1 | 1 | -2.5 | 10 | 0 | 0
938.7 | 49.99 | 49.99 | 0 | 0 | 0 | 50.05 | -0.020588 | -0.4 | -4 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
938.75 | 49.99 | 49.99 | 0 | 0 | 0 | 50.03 | -0.0088235 | -0.3 | -3 | -1.5 | -1.5 | 0 | 12 | 1 | 1 | -1.5 | 10 | 0 | 0
938.8 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | -0.2 | -2 | -0.83824 | -0.83824 | 0 | 12 | 1 | 1 | -0.83824 | 10 | 0 | 0
938.85 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | -0.1 | -1 | -0.33824 | -0.33824 | 0 | 12 | 1 | 1 | -0.33824 | 10 | 0 | 0
938.9 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
938.95 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
939 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
939.05 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
939.1 | 49.89 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
939.15 | 49.89 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
939.2 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50.01 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
939.25 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
939.3 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
939.35 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 2.7868 | 2.7868 | 0 | 12 | 1 | 1 | 2.7868 | 10 | 0 | 0
939.4 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 2.7868 | 2.7868 | 0 | 12 | 1 | 1 | 2.7868 | 10 | 0 | 0
939.45 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 2.8456 | 2.8456 | 0 | 12 | 1 | 1 | 2.8456 | 10 | 0 | 0
939.5 | 49.94 | 49.85 | 0.525 | 0.525 | 5.25 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 2.7574 | 2.7574 | 0 | 12 | 1 | 1 | 2.7574 | 10 | 0 | 0
939.55 | 49.94 | 49.85 | 0.525 | 0.525 | 5.25 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 2.7574 | 2.7574 | 0 | 12 | 1 | 1 | 2.7574 | 10 | 0 | 0
939.6 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
939.65 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
939.7 | 49.93 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
939.75 | 49.93 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
939.8 | 49.96 | 49.85 | 0.525 | 0.525 | 5.25 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 2.6985 | 2.6985 | 0 | 12 | 1 | 1 | 2.6985 | 10 | 0 | 0
939.85 | 49.96 | 49.85 | 0.525 | 0.525 | 5.25 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 2.6985 | 2.6985 | 0 | 12 | 1 | 1 | 2.6985 | 10 | 0 | 0
939.9 | 49.99 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
939.95 | 49.99 | 49.91 | 0.044118 | 0.425 | 4.25 | 49.99 | 0 | 0 | 0 | 2.125 | 2.125 | 0 | 12 | 1 | 1 | 2.125 | 10 | 0 | 0
940 | 49.99 | 49.91 | 0.044118 | 0.325 | 3.25 | 49.99 | 0 | 0 | 0 | 1.625 | 1.625 | 0 | 12 | 1 | 1 | 1.625 | 10 | 0 | 0
940.05 | 49.99 | 49.93 | 0.032353 | 0.225 | 2.25 | 49.99 | 0 | 0 | 0 | 1.125 | 1.125 | 0 | 12 | 1 | 1 | 1.125 | 10 | 0 | 0
940.1 | 49.96 | 49.93 | 0.032353 | 0.125 | 1.25 | 49.99 | 0 | 0 | 0 | 0.625 | 0.625 | 0 | 12 | 1 | 1 | 0.625 | 10 | 0 | 0
940.15 | 49.96 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 49.99 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
940.2 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
940.25 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
940.3 | 50.05 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.058824 | 0.058824 | 0 | 12 | 1 | 1 | 0.058824 | 10 | 0 | 0
940.35 | 50.05 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
940.4 | 49.97 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
940.45 | 49.97 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
940.5 | 49.92 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
940.55 | 49.92 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
940.6 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
940.65 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
940.7 | 49.94 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
940.75 | 49.94 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
940.8 | 50.01 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
940.85 | 50.01 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
940.9 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
940.95 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
941 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
941.05 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
941.1 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
941.15 | 49.95 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
941.2 | 49.97 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
941.25 | 49.97 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
941.3 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
941.35 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
941.4 | 49.87 | 49.87 | 0.335 | 0.335 | 3.35 | 50.01 | 0 | 0 | 0 | 1.675 | 1.675 | 0 | 12 | 1 | 1 | 1.675 | 10 | 0 | 0
941.45 | 49.87 | 49.87 | 0.335 | 0.335 | 3.35 | 49.99 | 0 | 0 | 0 | 1.675 | 1.675 | 0 | 12 | 1 | 1 | 1.675 | 10 | 0 | 0
941.5 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
941.55 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 2.6691 | 2.6691 | 0 | 12 | 1 | 1 | 2.6691 | 10 | 0 | 0
941.6 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
941.65 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
941.7 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
941.75 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
941.8 | 49.84 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
941.85 | 49.84 | 49.79 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
941.9 | 49.89 | 49.79 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
941.95 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.12647 | 1.2647 | 5.6324 | 5.6324 | 0 | 12 | 1 | 1 | 5.6324 | 10 | 0 | 0
942 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.145 | 1.45 | 5.725 | 5.725 | 0 | 12 | 1 | 1 | 5.725 | 10 | 0 | 0
942.05 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.145 | 1.45 | 5.725 | 5.725 | 0 | 12 | 1 | 1 | 5.725 | 10 | 0 | 0
942.1 | 49.96 | 49.79 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
942.15 | 49.96 | 49.79 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
942.2 | 50.02 | 49.79 | 1 | 1 | 10 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 4.9853 | 4.9853 | 0 | 12 | 1 | 1 | 4.9853 | 10 | 0 | 0
942.25 | 50.02 | 49.79 | 1 | 1 | 10 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 4.9853 | 4.9853 | 0 | 12 | 1 | 1 | 4.9853 | 10 | 0 | 0
942.3 | 50.03 | 49.79 | 1 | 1 | 10 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.9559 | 4.9559 | 0 | 12 | 1 | 1 | 4.9559 | 10 | 0 | 0
942.35 | 50.03 | 49.84 | 0.62 | 0.9 | 9 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.4559 | 4.4559 | 0 | 12 | 1 | 1 | 4.4559 | 10 | 0 | 0
942.4 | 50.02 | 49.84 | 0.62 | 0.8 | 8 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 3.9559 | 3.9559 | 0 | 12 | 1 | 1 | 3.9559 | 10 | 0 | 0
942.45 | 50.02 | 49.89 | 0.145 | 0.7 | 7 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 3.4559 | 3.4559 | 0 | 12 | 1 | 1 | 3.4559 | 10 | 0 | 0
942.5 | 50.08 | 49.89 | 0.145 | 0.6 | 6 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 2.8088 | 2.8088 | 0 | 12 | 1 | 1 | 2.8088 | 10 | 0 | 0
942.55 | 50.08 | 49.89 | 0.145 | 0.5 | 5 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 2.3088 | 2.3088 | 0 | 12 | 1 | 1 | 2.3088 | 10 | 0 | 0
942.6 | 50.01 | 49.89 | 0.145 | 0.4 | 4 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 1.8088 | 1.8088 | 0 | 12 | 1 | 1 | 1.8088 | 10 | 0 | 0
942.65 | 50.01 | 49.96 | 0.014706 | 0.3 | 3 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 1.3088 | 1.3088 | 0 | 12 | 1 | 1 | 1.3088 | 10 | 0 | 0
942.7 | 49.94 | 49.94 | 0.026471 | 0.2 | 2 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.80882 | 0.80882 | 0 | 12 | 1 | 1 | 0.80882 | 10 | 0 | 0
942.75 | 49.94 | 49.94 | 0.026471 | 0.1 | 1 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.30882 | 0.30882 | 0 | 12 | 1 | 1 | 0.30882 | 10 | 0 | 0
942.8 | 50 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
942.85 | 50 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
942.9 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
942.95 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
943 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
943.05 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
943.1 | 49.92 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
943.15 | 49.92 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
943.2 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50.01 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
943.25 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
943.3 | 49.92 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
943.35 | 49.92 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
943.4 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
943.45 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
943.5 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
943.55 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
943.6 | 49.87 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
943.65 | 49.87 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
943.7 | 49.8 | 49.8 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
943.75 | 49.8 | 49.8 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
943.8 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
943.85 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
943.9 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
943.95 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
944 | 49.72 | 49.72 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
944.05 | 49.72 | 49.72 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
944.1 | 49.67 | 49.67 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
944.15 | 49.67 | 49.67 | 1 | 1 | 10 | 49.87 | 0.335 | 0.14412 | 1.4412 | 5.7206 | 5.7206 | 0 | 12 | 1 | 1 | 5.7206 | 10 | 0 | 0
944.2 | 49.65 | 49.65 | 1 | 1 | 10 | 49.87 | 0.335 | 0.24412 | 2.4412 | 6.2206 | 6.2206 | 0 | 12 | 1 | 1 | 6.2206 | 10 | 0 | 0
944.25 | 49.65 | 49.65 | 1 | 1 | 10 | 49.8 | 1 | 0.34412 | 3.4412 | 6.7206 | 6.7206 | 0 | 12 | 1 | 1 | 6.7206 | 10 | 0 | 0
944.3 | 49.59 | 49.59 | 1 | 1 | 10 | 49.8 | 1 | 0.44412 | 4.4412 | 7.2206 | 7.2206 | 0 | 12 | 1 | 1 | 7.2206 | 10 | 0 | 0
944.35 | 49.59 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.54412 | 5.4412 | 7.7206 | 7.7206 | 0 | 12 | 1 | 1 | 7.7206 | 10 | 0 | 0
944.4 | 49.66 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.64412 | 6.4412 | 8.2206 | 8.2206 | 0 | 12 | 1 | 1 | 8.2206 | 10 | 0 | 0
944.45 | 49.66 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.74412 | 7.4412 | 8.7206 | 8.7206 | 0 | 12 | 1 | 1 | 8.7206 | 10 | 0 | 0
944.5 | 49.63 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.84412 | 8.4412 | 9.2206 | 9.2206 | 0 | 12 | 1 | 1 | 9.2206 | 10 | 0 | 0
944.55 | 49.63 | 49.59 | 1 | 1 | 10 | 49.72 | 1 | 0.94412 | 9.4412 | 9.7206 | 9.7206 | 0 | 12 | 1 | 1 | 9.7206 | 10 | 0 | 0
944.6 | 49.61 | 49.59 | 1 | 1 | 10 | 49.72 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
944.65 | 49.61 | 49.59 | 1 | 1 | 10 | 49.67 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
944.7 | 49.54 | 49.54 | 1 | 1 | 10 | 49.67 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
944.75 | 49.54 | 49.54 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
944.8 | 49.46 | 49.46 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
944.85 | 49.46 | 49.46 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
944.9 | 49.45 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
944.95 | 49.45 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
945 | 49.51 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
945.05 | 49.51 | 49.45 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
945.1 | 49.5 | 49.45 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
945.15 | 49.5 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
945.2 | 49.54 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
945.25 | 49.54 | 49.45 | 1 | 1 | 10 | 49.54 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
945.3 | 49.59 | 49.45 | 1 | 1 | 10 | 49.59 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
945.35 | 49.59 | 49.45 | 1 | 1 | 10 | 49.59 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
945.4 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
945.45 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
945.5 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
945.55 | 49.61 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
945.6 | 49.53 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
945.65 | 49.53 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
945.7 | 49.54 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
945.75 | 49.54 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
945.8 | 49.61 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
945.85 | 49.61 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
945.9 | 49.66 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
945.95 | 49.66 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
946 | 49.64 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
946.05 | 49.64 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
946.1 | 49.69 | 49.53 | 1 | 1 | 10 | 49.69 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
946.15 | 49.69 | 49.53 | 1 | 1 | 10 | 49.69 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
946.2 | 49.74 | 49.53 | 1 | 1 | 10 | 49.74 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
946.25 | 49.74 | 49.54 | 1 | 1 | 10 | 49.74 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
946.3 | 49.78 | 49.54 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
946.35 | 49.78 | 49.61 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
946.4 | 49.82 | 49.61 | 1 | 1 | 10 | 49.82 | 0.81 | 0.81 | 8.1 | 9.05 | 9.05 | 0 | 12 | 1 | 1 | 9.05 | 10 | 0 | 0
946.45 | 49.82 | 49.64 | 1 | 1 | 10 | 49.82 | 0.81 | 0.81 | 8.1 | 9.05 | 9.05 | 0 | 12 | 1 | 1 | 9.05 | 10 | 0 | 0
946.5 | 49.86 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
946.55 | 49.86 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
946.6 | 49.84 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
946.65 | 49.84 | 49.69 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
946.7 | 49.91 | 49.69 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
946.75 | 49.91 | 49.74 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
946.8 | 49.97 | 49.74 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
946.85 | 49.97 | 49.78 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
946.9 | 50.03 | 49.78 | 1 | 1 | 10 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.9559 | 4.9559 | 0 | 12 | 1 | 1 | 4.9559 | 10 | 0 | 0
946.95 | 50.03 | 49.82 | 0.81 | 0.9 | 9 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.4559 | 4.4559 | 0 | 12 | 1 | 1 | 4.4559 | 10 | 0 | 0
947 | 50.05 | 49.82 | 0.81 | 0.81 | 8.1 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 3.9471 | 3.9471 | 0 | 12 | 1 | 1 | 3.9471 | 10 | 0 | 0
947.05 | 50.05 | 49.84 | 0.62 | 0.71 | 7.1 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 3.4471 | 3.4471 | 0 | 12 | 1 | 1 | 3.4471 | 10 | 0 | 0
947.1 | 50.01 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
947.15 | 50.01 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
947.2 | 49.95 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
947.25 | 49.95 | 49.91 | 0.044118 | 0.52 | 5.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.4971 | 2.4971 | 0 | 12 | 1 | 1 | 2.4971 | 10 | 0 | 0
947.3 | 49.99 | 49.91 | 0.044118 | 0.42 | 4.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 1.9971 | 1.9971 | 0 | 12 | 1 | 1 | 1.9971 | 10 | 0 | 0
947.35 | 49.99 | 49.95 | 0.020588 | 0.32 | 3.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 1.4971 | 1.4971 | 0 | 12 | 1 | 1 | 1.4971 | 10 | 0 | 0
947.4 | 49.92 | 49.92 | 0.038235 | 0.22 | 2.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.99706 | 0.99706 | 0 | 12 | 1 | 1 | 0.99706 | 10 | 0 | 0
947.45 | 49.92 | 49.92 | 0.038235 | 0.12 | 1.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.49706 | 0.49706 | 0 | 12 | 1 | 1 | 0.49706 | 10 | 0 | 0
947.5 | 49.97 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
947.55 | 49.97 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
947.6 | 50.02 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
947.65 | 50.02 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.17647 | 0.17647 | 0 | 12 | 1 | 1 | 0.17647 | 10 | 0 | 0
947.7 | 50.07 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
947.75 | 50.07 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
947.8 | 50.06 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
947.85 | 50.06 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
947.9 | 50.13 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
947.95 | 50.13 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
948 | 50.09 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
948.05 | 50.09 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6309 | -1.6309 | 0 | 12 | 1 | 1 | -1.6309 | 10 | 0 | 0
948.1 | 50.07 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6309 | -1.6309 | 0 | 12 | 1 | 1 | -1.6309 | 10 | 0 | 0
948.15 | 50.07 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6897 | -1.6897 | 0 | 12 | 1 | 1 | -1.6897 | 10 | 0 | 0
948.2 | 50.07 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6897 | -1.6897 | 0 | 12 | 1 | 1 | -1.6897 | 10 | 0 | 0
948.25 | 50.07 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.13 | -0.335 | -0.335 | -3.35 | -1.8074 | -1.8074 | 0 | 12 | 1 | 1 | -1.8074 | 10 | 0 | 0
948.3 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.13 | -0.335 | -0.335 | -3.35 | -1.7779 | -1.7779 | 0 | 12 | 1 | 1 | -1.7779 | 10 | 0 | 0
948.35 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.13 | -0.335 | -0.335 | -3.35 | -1.7779 | -1.7779 | 0 | 12 | 1 | 1 | -1.7779 | 10 | 0 | 0
948.4 | 50.01 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
948.45 | 50.01 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
948.5 | 50.07 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
948.55 | 50.07 | 50.01 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.235 | -2.35 | -1.175 | -1.175 | 0 | 12 | 1 | 1 | -1.175 | 10 | 0 | 0
948.6 | 50.05 | 50.01 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.135 | -1.35 | -0.675 | -0.675 | 0 | 12 | 1 | 1 | -0.675 | 10 | 0 | 0
948.65 | 50.05 | 50.01 | 0 | 0 | 0 | 50.07 | -0.032353 | -0.035 | -0.35 | -0.175 | -0.175 | 0 | 12 | 1 | 1 | -0.175 | 10 | 0 | 0
948.7 | 50.1 | 50.01 | 0 | 0 | 0 | 50.1 | -0.05 | -0.05 | -0.5 | -0.25 | -0.25 | 0 | 12 | 1 | 1 | -0.25 | 10 | 0 | 0
948.75 | 50.1 | 50.01 | 0 | 0 | 0 | 50.1 | -0.05 | -0.05 | -0.5 | -0.25 | -0.25 | 0 | 12 | 1 | 1 | -0.25 | 10 | 0 | 0
948.8 | 50.11 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
948.85 | 50.11 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
948.9 | 50.06 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
948.95 | 50.06 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
949 | 50.04 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
949.05 | 50.04 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
949.1 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
949.15 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
949.2 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
949.25 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
949.3 | 50.11 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
949.35 | 50.11 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
949.4 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
949.45 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
949.5 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
949.55 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
949.6 | 50.02 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.11 | -0.145 | -0.145 | -1.45 | -0.73971 | -0.73971 | 0 | 12 | 1 | 1 | -0.73971 | 10 | 0 | 0
949.65 | 50.02 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.11 | -0.145 | -0.145 | -1.45 | -0.73971 | -0.73971 | 0 | 12 | 1 | 1 | -0.73971 | 10 | 0 | 0
949.7 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
949.75 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
949.8 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
949.85 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
949.9 | 50.01 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
949.95 | 50.01 | 50 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.045 | -0.45 | -0.225 | -0.225 | 0 | 12 | 1 | 1 | -0.225 | 10 | 0 | 0
950 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
950.05 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
950.1 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
950.15 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
950.2 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.14706 | 0.14706 | 0 | 12 | 1 | 1 | 0.14706 | 10 | 0 | 0
950.25 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
950.3 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
950.35 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
950.4 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
950.45 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
950.5 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
950.55 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
950.6 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
950.65 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
950.7 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
950.75 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
950.8 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
950.85 | 50 | 50 | 0 | 0 | 0 | 50.01 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
950.9 | 49.5 | 49.5 | 1 | 1 | 10 | 50.01 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
950.95 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
951 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
951.05 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
951.1 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
951.15 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
951.2 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
951.25 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
951.3 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
951.35 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
951.4 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
951.45 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.1 | 1 | 5.5 | 5.5 | 0 | 12 | 1 | 1 | 5.5 | 10 | 0 | 0
951.5 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.2 | 2 | 6 | 6 | 0 | 12 | 1 | 1 | 6 | 10 | 0 | 0
951.55 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.3 | 3 | 6.5 | 6.5 | 0 | 12 | 1 | 1 | 6.5 | 10 | 0 | 0
951.6 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.4 | 4 | 7 | 7 | 0 | 12 | 1 | 1 | 7 | 10 | 0 | 0
951.65 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.5 | 5 | 7.5 | 7.5 | 0 | 12 | 1 | 1 | 7.5 | 10 | 0 | 0
951.7 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.6 | 6 | 8 | 8 | 0 | 12 | 1 | 1 | 8 | 10 | 0 | 0
951.75 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.7 | 7 | 8.5 | 8.5 | 0 | 12 | 1 | 1 | 8.5 | 10 | 0 | 0
951.8 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.8 | 8 | 9 | 9 | 0 | 12 | 1 | 1 | 9 | 10 | 0 | 0
951.85 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.9 | 9 | 9.5 | 9.5 | 0 | 12 | 1 | 1 | 9.5 | 10 | 0 | 0
951.9 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
951.95 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
952 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
952.05 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
952.1 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
952.15 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
952.2 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
952.25 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
952.3 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
952.35 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
952.4 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
952.45 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
952.5 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
952.55 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
952.6 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
952.65 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
952.7 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
952.75 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
952.8 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
952.85 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
952.9 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
952.95 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
953 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
953.05 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
953.1 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
953.15 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
953.2 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
953.25 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
953.3 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
953.35 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
953.4 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
953.45 | 50.5 | 50.5 | -1 | 0.9 | 9 | 50.5 | -1 | -1 | -10 | -0.5 | -0.5 | 0 | 12 | 1 | 1 | -0.5 | 10 | 0 | 0
953.5 | 50.5 | 50.5 | -1 | 0.8 | 8 | 50.5 | -1 | -1 | -10 | -1 | -1 | 0 | 12 | 1 | 1 | -1 | 10 | 0 | 0
953.55 | 50.5 | 50.5 | -1 | 0.7 | 7 | 50.5 | -1 | -1 | -10 | -1.5 | -1.5 | 0 | 12 | 1 | 1 | -1.5 | 10 | 0 | 0
953.6 | 50.5 | 50.5 | -1 | 0.6 | 6 | 50.5 | -1 | -1 | -10 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
953.65 | 50.5 | 50.5 | -1 | 0.5 | 5 | 50.5 | -1 | -1 | -10 | -2.5 | -2.5 | 0 | 12 | 1 | 1 | -2.5 | 10 | 0 | 0
953.7 | 50.5 | 50.5 | -1 | 0.4 | 4 | 50.5 | -1 | -1 | -10 | -3 | -3 | 0 | 12 | 1 | 1 | -3 | 10 | 0 | 0
953.75 | 50.5 | 50.5 | -1 | 0.3 | 3 | 50.5 | -1 | -1 | -10 | -3.5 | -3.5 | 0 | 12 | 1 | 1 | -3.5 | 10 | 0 | 0
953.8 | 50.5 | 50.5 | -1 | 0.2 | 2 | 50.5 | -1 | -1 | -10 | -4 | -4 | 0 | 12 | 1 | 1 | -4 | 10 | 0 | 0
953.85 | 50.5 | 50.5 | -1 | 0.1 | 1 | 50.5 | -1 | -1 | -10 | -4.5 | -4.5 | 0 | 12 | 1 | 1 | -4.5 | 10 | 0 | 0
953.9 | 50.5 | 50.5 | -1 | 0 | 0 | 50.5 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
953.95 | 50.5 | 50.5 | -1 | -0.1 | -1 | 50.5 | -1 | -1 | -10 | -5.5 | -5.5 | 0 | 12 | 1 | 1 | -5.5 | 10 | 0 | 0
954 | 50.5 | 50.5 | -1 | -0.2 | -2 | 50.5 | -1 | -1 | -10 | -6 | -6 | 0 | 12 | 1 | 1 | -6 | 10 | 0 | 0
954.05 | 50.5 | 50.5 | -1 | -0.3 | -3 | 50.5 | -1 | -1 | -10 | -6.5 | -6.5 | 0 | 12 | 1 | 1 | -6.5 | 10 | 0 | 0
954.1 | 50.5 | 50.5 | -1 | -0.4 | -4 | 50.5 | -1 | -1 | -10 | -7 | -7 | 0 | 12 | 1 | 1 | -7 | 10 | 0 | 0
954.15 | 50.5 | 50.5 | -1 | -0.5 | -5 | 50.5 | -1 | -1 | -10 | -7.5 | -7.5 | 0 | 12 | 1 | 1 | -7.5 | 10 | 0 | 0
954.2 | 50.5 | 50.5 | -1 | -0.6 | -6 | 50.5 | -1 | -1 | -10 | -8 | -8 | 0 | 12 | 1 | 1 | -8 | 10 | 0 | 0
954.25 | 50.5 | 50.5 | -1 | -0.7 | -7 | 50.5 | -1 | -1 | -10 | -8.5 | -8.5 | 0 | 12 | 1 | 1 | -8.5 | 10 | 0 | 0
954.3 | 50.5 | 50.5 | -1 | -0.8 | -8 | 50.5 | -1 | -1 | -10 | -9 | -9 | 0 | 12 | 1 | 1 | -9 | 10 | 0 | 0
954.35 | 50.5 | 50.5 | -1 | -0.9 | -9 | 50.5 | -1 | -1 | -10 | -9.5 | -9.5 | 0 | 12 | 1 | 1 | -9.5 | 10 | 0 | 0
954.4 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
954.45 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
954.5 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
954.55 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
954.6 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
954.65 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
954.7 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
954.75 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
954.8 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
954.85 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
954.9 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
954.95 | 50.47 | 50.47 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
955 | 50.45 | 50.45 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
955.05 | 50.42 | 50.42 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
955.1 | 50.4 | 50.4 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
955.15 | 50.37 | 50.37 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
955.2 | 50.35 | 50.35 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
955.25 | 50.32 | 50.32 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
955.3 | 50.29 | 50.29 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
955.35 | 50.27 | 50.27 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
955.4 | 50.24 | 50.24 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
955.45 | 50.22 | 50.22 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
955.5 | 50.19 | 50.19 | -0.905 | -0.905 | -9.05 | 50.47 | -1 | -1 | -10 | -9.525 | -9.525 | 0 | 12 | 1 | 1 | -9.525 | 10 | 0 | 0
955.55 | 50.17 | 50.17 | -0.715 | -0.715 | -7.15 | 50.45 | -1 | -1 | -10 | -8.575 | -8.575 | 0 | 12 | 1 | 1 | -8.575 | 10 | 0 | 0
955.6 | 50.14 | 50.14 | -0.43 | -0.43 | -4.3 | 50.42 | -1 | -1 | -10 | -7.15 | -7.15 | 0 | 12 | 1 | 1 | -7.15 | 10 | 0 | 0
955.65 | 50.12 | 50.12 | -0.24 | -0.24 | -2.4 | 50.4 | -1 | -1 | -10 | -6.2 | -6.2 | 0 | 12 | 1 | 1 | -6.2 | 10 | 0 | 0
955.7 | 50.09 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 50.37 | -1 | -1 | -10 | -5.2206 | -5.2206 | 0 | 12 | 1 | 1 | -5.2206 | 10 | 0 | 0
955.75 | 50.06 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.35 | -1 | -1 | -10 | -5.1324 | -5.1324 | 0 | 12 | 1 | 1 | -5.1324 | 10 | 0 | 0
955.8 | 50.04 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.32 | -1 | -1 | -10 | -5.0735 | -5.0735 | 0 | 12 | 1 | 1 | -5.0735 | 10 | 0 | 0
955.85 | 50.01 | 50.01 | 0 | 0 | 0 | 50.29 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
955.9 | 49.99 | 49.99 | 0 | 0 | 0 | 50.27 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
955.95 | 49.96 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.24 | -1 | -1 | -10 | -4.9265 | -4.9265 | 0 | 12 | 1 | 1 | -4.9265 | 10 | 0 | 0
956 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.22 | -1 | -1 | -10 | -4.8676 | -4.8676 | 0 | 12 | 1 | 1 | -4.8676 | 10 | 0 | 0
956.05 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.19 | -0.905 | -0.905 | -9.05 | -4.3044 | -4.3044 | 0 | 12 | 1 | 1 | -4.3044 | 10 | 0 | 0
956.1 | 49.88 | 49.88 | 0.24 | 0.24 | 2.4 | 50.17 | -0.715 | -0.805 | -8.05 | -2.825 | -2.825 | 0 | 12 | 1 | 1 | -2.825 | 10 | 0 | 0
956.15 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.14 | -0.43 | -0.705 | -7.05 | -1.375 | -1.375 | 0 | 12 | 1 | 1 | -1.375 | 10 | 0 | 0
956.2 | 49.83 | 49.83 | 0.715 | 0.715 | 7.15 | 50.12 | -0.24 | -0.605 | -6.05 | 0.55 | 0.55 | 0 | 12 | 1 | 1 | 0.55 | 10 | 0 | 0
956.25 | 49.81 | 49.81 | 0.905 | 0.905 | 9.05 | 50.09 | -0.044118 | -0.505 | -5.05 | 2 | 2 | 0 | 12 | 1 | 1 | 2 | 10 | 0 | 0
956.3 | 49.78 | 49.78 | 1 | 1 | 10 | 50.06 | -0.026471 | -0.405 | -4.05 | 2.975 | 2.975 | 0 | 12 | 1 | 1 | 2.975 | 10 | 0 | 0
956.35 | 49.76 | 49.76 | 1 | 1 | 10 | 50.04 | -0.014706 | -0.305 | -3.05 | 3.475 | 3.475 | 0 | 12 | 1 | 1 | 3.475 | 10 | 0 | 0
956.4 | 49.73 | 49.73 | 1 | 1 | 10 | 50.01 | 0 | -0.205 | -2.05 | 3.975 | 3.975 | 0 | 12 | 1 | 1 | 3.975 | 10 | 0 | 0
956.45 | 49.71 | 49.71 | 1 | 1 | 10 | 49.99 | 0 | -0.105 | -1.05 | 4.475 | 4.475 | 0 | 12 | 1 | 1 | 4.475 | 10 | 0 | 0
956.5 | 49.68 | 49.68 | 1 | 1 | 10 | 49.96 | 0.014706 | -0.005 | -0.05 | 4.975 | 4.975 | 0 | 12 | 1 | 1 | 4.975 | 10 | 0 | 0
956.55 | 49.65 | 49.65 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
956.6 | 49.63 | 49.63 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
956.65 | 49.6 | 49.6 | 1 | 1 | 10 | 49.88 | 0.24 | 0.14412 | 1.4412 | 5.7206 | 5.7206 | 0 | 12 | 1 | 1 | 5.7206 | 10 | 0 | 0
956.7 | 49.58 | 49.58 | 1 | 1 | 10 | 49.86 | 0.43 | 0.24412 | 2.4412 | 6.2206 | 6.2206 | 0 | 12 | 1 | 1 | 6.2206 | 10 | 0 | 0
956.75 | 49.55 | 49.55 | 1 | 1 | 10 | 49.83 | 0.715 | 0.34412 | 3.4412 | 6.7206 | 6.7206 | 0 | 12 | 1 | 1 | 6.7206 | 10 | 0 | 0
956.8 | 49.53 | 49.53 | 1 | 1 | 10 | 49.81 | 0.905 | 0.44412 | 4.4412 | 7.2206 | 7.2206 | 0 | 12 | 1 | 1 | 7.2206 | 10 | 0 | 0
956.85 | 49.5 | 49.5 | 1 | 1 | 10 | 49.78 | 1 | 0.54412 | 5.4412 | 7.7206 | 7.7206 | 0 | 12 | 1 | 1 | 7.7206 | 10 | 0 | 0
956.9 | 49.5 | 49.5 | 1 | 1 | 10 | 49.76 | 1 | 0.64412 | 6.4412 | 8.2206 | 8.2206 | 0 | 12 | 1 | 1 | 8.2206 | 10 | 0 | 0
956.95 | 49.53 | 49.5 | 1 | 1 | 10 | 49.73 | 1 | 0.74412 | 7.4412 | 8.7206 | 8.7206 | 0 | 12 | 1 | 1 | 8.7206 | 10 | 0 | 0
957 | 49.55 | 49.5 | 1 | 1 | 10 | 49.71 | 1 | 0.84412 | 8.4412 | 9.2206 | 9.2206 | 0 | 12 | 1 | 1 | 9.2206 | 10 | 0 | 0
957.05 | 49.58 | 49.5 | 1 | 1 | 10 | 49.68 | 1 | 0.94412 | 9.4412 | 9.7206 | 9.7206 | 0 | 12 | 1 | 1 | 9.7206 | 10 | 0 | 0
957.1 | 49.6 | 49.5 | 1 | 1 | 10 | 49.65 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
957.15 | 49.63 | 49.5 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
957.2 | 49.65 | 49.5 | 1 | 1 | 10 | 49.65 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
957.25 | 49.68 | 49.5 | 1 | 1 | 10 | 49.68 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
957.3 | 49.71 | 49.5 | 1 | 1 | 10 | 49.71 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
957.35 | 49.73 | 49.5 | 1 | 1 | 10 | 49.73 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
957.4 | 49.76 | 49.5 | 1 | 1 | 10 | 49.76 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
957.45 | 49.78 | 49.5 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
957.5 | 49.81 | 49.53 | 1 | 1 | 10 | 49.81 | 0.905 | 0.905 | 9.05 | 9.525 | 9.525 | 0 | 12 | 1 | 1 | 9.525 | 10 | 0 | 0
957.55 | 49.83 | 49.55 | 1 | 1 | 10 | 49.83 | 0.715 | 0.715 | 7.15 | 8.575 | 8.575 | 0 | 12 | 1 | 1 | 8.575 | 10 | 0 | 0
957.6 | 49.86 | 49.58 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
957.65 | 49.88 | 49.6 | 1 | 1 | 10 | 49.88 | 0.24 | 0.24 | 2.4 | 6.2 | 6.2 | 0 | 12 | 1 | 1 | 6.2 | 10 | 0 | 0
957.7 | 49.91 | 49.63 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
957.75 | 49.94 | 49.65 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
957.8 | 49.96 | 49.68 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
957.85 | 49.99 | 49.71 | 1 | 1 | 10 | 49.99 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
957.9 | 50.01 | 49.73 | 1 | 1 | 10 | 50.01 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
957.95 | 50.04 | 49.76 | 1 | 1 | 10 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 4.9265 | 4.9265 | 0 | 12 | 1 | 1 | 4.9265 | 10 | 0 | 0
958 | 50.06 | 49.78 | 1 | 1 | 10 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 4.8676 | 4.8676 | 0 | 12 | 1 | 1 | 4.8676 | 10 | 0 | 0
958.05 | 50.09 | 49.81 | 0.905 | 0.905 | 9.05 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 4.3044 | 4.3044 | 0 | 12 | 1 | 1 | 4.3044 | 10 | 0 | 0
958.1 | 50.12 | 49.83 | 0.715 | 0.805 | 8.05 | 50.12 | -0.24 | -0.24 | -2.4 | 2.825 | 2.825 | 0 | 12 | 1 | 1 | 2.825 | 10 | 0 | 0
958.15 | 50.14 | 49.86 | 0.43 | 0.705 | 7.05 | 50.14 | -0.43 | -0.43 | -4.3 | 1.375 | 1.375 | 0 | 12 | 1 | 1 | 1.375 | 10 | 0 | 0
958.2 | 50.17 | 49.88 | 0.24 | 0.605 | 6.05 | 50.17 | -0.715 | -0.715 | -7.15 | -0.55 | -0.55 | 0 | 12 | 1 | 1 | -0.55 | 10 | 0 | 0
958.25 | 50.19 | 49.91 | 0.044118 | 0.505 | 5.05 | 50.19 | -0.905 | -0.905 | -9.05 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
958.3 | 50.22 | 49.94 | 0.026471 | 0.405 | 4.05 | 50.22 | -1 | -1 | -10 | -2.975 | -2.975 | 0 | 12 | 1 | 1 | -2.975 | 10 | 0 | 0
958.35 | 50.24 | 49.96 | 0.014706 | 0.305 | 3.05 | 50.24 | -1 | -1 | -10 | -3.475 | -3.475 | 0 | 12 | 1 | 1 | -3.475 | 10 | 0 | 0
958.4 | 50.27 | 49.99 | 0 | 0.205 | 2.05 | 50.27 | -1 | -1 | -10 | -3.975 | -3.975 | 0 | 12 | 1 | 1 | -3.975 | 10 | 0 | 0
958.45 | 50.29 | 50.01 | 0 | 0.105 | 1.05 | 50.29 | -1 | -1 | -10 | -4.475 | -4.475 | 0 | 12 | 1 | 1 | -4.475 | 10 | 0 | 0
958.5 | 50.32 | 50.04 | -0.014706 | 0.005 | 0.05 | 50.32 | -1 | -1 | -10 | -4.975 | -4.975 | 0 | 12 | 1 | 1 | -4.975 | 10 | 0 | 0
958.55 | 50.35 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.35 | -1 | -1 | -10 | -5.1324 | -5.1324 | 0 | 12 | 1 | 1 | -5.1324 | 10 | 0 | 0
958.6 | 50.37 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 50.37 | -1 | -1 | -10 | -5.2206 | -5.2206 | 0 | 12 | 1 | 1 | -5.2206 | 10 | 0 | 0
958.65 | 50.4 | 50.12 | -0.24 | -0.14412 | -1.4412 | 50.4 | -1 | -1 | -10 | -5.7206 | -5.7206 | 0 | 12 | 1 | 1 | -5.7206 | 10 | 0 | 0
958.7 | 50.42 | 50.14 | -0.43 | -0.24412 | -2.4412 | 50.42 | -1 | -1 | -10 | -6.2206 | -6.2206 | 0 | 12 | 1 | 1 | -6.2206 | 10 | 0 | 0
958.75 | 50.45 | 50.17 | -0.715 | -0.34412 | -3.4412 | 50.45 | -1 | -1 | -10 | -6.7206 | -6.7206 | 0 | 12 | 1 | 1 | -6.7206 | 10 | 0 | 0
958.8 | 50.47 | 50.19 | -0.905 | -0.44412 | -4.4412 | 50.47 | -1 | -1 | -10 | -7.2206 | -7.2206 | 0 | 12 | 1 | 1 | -7.2206 | 10 | 0 | 0
958.85 | 50.5 | 50.22 | -1 | -0.54412 | -5.4412 | 50.5 | -1 | -1 | -10 | -7.7206 | -7.7206 | 0 | 12 | 1 | 1 | -7.7206 | 10 | 0 | 0
958.9 | 50.5 | 50.24 | -1 | -0.64412 | -6.4412 | 50.5 | -1 | -1 | -10 | -8.2206 | -8.2206 | 0 | 12 | 1 | 1 | -8.2206 | 10 | 0 | 0
958.95 | 50.47 | 50.27 | -1 | -0.74412 | -7.4412 | 50.5 | -1 | -1 | -10 | -8.7206 | -8.7206 | 0 | 12 | 1 | 1 | -8.7206 | 10 | 0 | 0
959 | 50.45 | 50.29 | -1 | -0.84412 | -8.4412 | 50.5 | -1 | -1 | -10 | -9.2206 | -9.2206 | 0 | 12 | 1 | 1 | -9.2206 | 10 | 0 | 0
959.05 | 50.42 | 50.32 | -1 | -0.94412 | -9.4412 | 50.5 | -1 | -1 | -10 | -9.7206 | -9.7206 | 0 | 12 | 1 | 1 | -9.7206 | 10 | 0 | 0
959.1 | 50.39 | 50.35 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
959.15 | 50.37 | 50.37 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
959.2 | 50.34 | 50.34 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
959.25 | 50.32 | 50.32 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
959.3 | 50.29 | 50.29 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
959.35 | 50.26 | 50.26 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
959.4 | 50.24 | 50.24 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
959.45 | 50.21 | 50.21 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
959.5 | 50.18 | 50.18 | -0.81 | -0.81 | -8.1 | 50.47 | -1 | -1 | -10 | -9.05 | -9.05 | 0 | 12 | 1 | 1 | -9.05 | 10 | 0 | 0
959.55 | 50.16 | 50.16 | -0.62 | -0.62 | -6.2 | 50.45 | -1 | -1 | -10 | -8.1 | -8.1 | 0 | 12 | 1 | 1 | -8.1 | 10 | 0 | 0
959.6 | 50.13 | 50.13 | -0.335 | -0.335 | -3.35 | 50.42 | -1 | -1 | -10 | -6.675 | -6.675 | 0 | 12 | 1 | 1 | -6.675 | 10 | 0 | 0
959.65 | 50.11 | 50.11 | -0.145 | -0.145 | -1.45 | 50.39 | -1 | -1 | -10 | -5.725 | -5.725 | 0 | 12 | 1 | 1 | -5.725 | 10 | 0 | 0
959.7 | 50.08 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 50.37 | -1 | -1 | -10 | -5.1912 | -5.1912 | 0 | 12 | 1 | 1 | -5.1912 | 10 | 0 | 0
959.75 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.34 | -1 | -1 | -10 | -5.1029 | -5.1029 | 0 | 12 | 1 | 1 | -5.1029 | 10 | 0 | 0
959.8 | 50.03 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 50.32 | -1 | -1 | -10 | -5.0441 | -5.0441 | 0 | 12 | 1 | 1 | -5.0441 | 10 | 0 | 0
959.85 | 50 | 50 | 0 | 0 | 0 | 50.29 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
959.9 | 50 | 50 | 0 | 0 | 0 | 50.26 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
959.95 | 50 | 50 | 0 | 0 | 0 | 50.24 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
960 | 50 | 50 | 0 | 0 | 0 | 50.21 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
960.05 | 50 | 50 | 0 | 0 | 0 | 50.18 | -0.81 | -0.9 | -9 | -4.5 | -4.5 | 0 | 12 | 1 | 1 | -4.5 | 10 | 0 | 0
960.1 | 50 | 50 | 0 | 0 | 0 | 50.16 | -0.62 | -0.8 | -8 | -4 | -4 | 0 | 12 | 1 | 1 | -4 | 10 | 0 | 0
960.15 | 50 | 50 | 0 | 0 | 0 | 50.13 | -0.335 | -0.7 | -7 | -3.5 | -3.5 | 0 | 12 | 1 | 1 | -3.5 | 10 | 0 | 0
960.2 | 50.01 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.6 | -6 | -3 | -3 | 0 | 12 | 1 | 1 | -3 | 10 | 0 | 0
960.25 | 50.01 | 50 | 0 | 0 | 0 | 50.08 | -0.038235 | -0.5 | -5 | -2.5 | -2.5 | 0 | 12 | 1 | 1 | -2.5 | 10 | 0 | 0
960.3 | 49.99 | 49.99 | 0 | 0 | 0 | 50.05 | -0.020588 | -0.4 | -4 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
960.35 | 49.99 | 49.99 | 0 | 0 | 0 | 50.03 | -0.0088235 | -0.3 | -3 | -1.5 | -1.5 | 0 | 12 | 1 | 1 | -1.5 | 10 | 0 | 0
960.4 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | -0.2 | -2 | -0.83824 | -0.83824 | 0 | 12 | 1 | 1 | -0.83824 | 10 | 0 | 0
960.45 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | -0.1 | -1 | -0.33824 | -0.33824 | 0 | 12 | 1 | 1 | -0.33824 | 10 | 0 | 0
960.5 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
960.55 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
960.6 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
960.65 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
960.7 | 49.89 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
960.75 | 49.89 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
960.8 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50.01 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
960.85 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
960.9 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
960.95 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 2.7868 | 2.7868 | 0 | 12 | 1 | 1 | 2.7868 | 10 | 0 | 0
961 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 2.7868 | 2.7868 | 0 | 12 | 1 | 1 | 2.7868 | 10 | 0 | 0
961.05 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 2.8456 | 2.8456 | 0 | 12 | 1 | 1 | 2.8456 | 10 | 0 | 0
961.1 | 49.94 | 49.85 | 0.525 | 0.525 | 5.25 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 2.7574 | 2.7574 | 0 | 12 | 1 | 1 | 2.7574 | 10 | 0 | 0
961.15 | 49.94 | 49.85 | 0.525 | 0.525 | 5.25 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 2.7574 | 2.7574 | 0 | 12 | 1 | 1 | 2.7574 | 10 | 0 | 0
961.2 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
961.25 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
961.3 | 49.93 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
961.35 | 49.93 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
961.4 | 49.96 | 49.85 | 0.525 | 0.525 | 5.25 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 2.6985 | 2.6985 | 0 | 12 | 1 | 1 | 2.6985 | 10 | 0 | 0
961.45 | 49.96 | 49.85 | 0.525 | 0.525 | 5.25 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 2.6985 | 2.6985 | 0 | 12 | 1 | 1 | 2.6985 | 10 | 0 | 0
961.5 | 49.99 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
961.55 | 49.99 | 49.91 | 0.044118 | 0.425 | 4.25 | 49.99 | 0 | 0 | 0 | 2.125 | 2.125 | 0 | 12 | 1 | 1 | 2.125 | 10 | 0 | 0
961.6 | 49.99 | 49.91 | 0.044118 | 0.325 | 3.25 | 49.99 | 0 | 0 | 0 | 1.625 | 1.625 | 0 | 12 | 1 | 1 | 1.625 | 10 | 0 | 0
961.65 | 49.99 | 49.93 | 0.032353 | 0.225 | 2.25 | 49.99 | 0 | 0 | 0 | 1.125 | 1.125 | 0 | 12 | 1 | 1 | 1.125 | 10 | 0 | 0
961.7 | 49.96 | 49.93 | 0.032353 | 0.125 | 1.25 | 49.99 | 0 | 0 | 0 | 0.625 | 0.625 | 0 | 12 | 1 | 1 | 0.625 | 10 | 0 | 0
961.75 | 49.96 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 49.99 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
961.8 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
961.85 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
961.9 | 50.05 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.058824 | 0.058824 | 0 | 12 | 1 | 1 | 0.058824 | 10 | 0 | 0
961.95 | 50.05 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
962 | 49.97 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
962.05 | 49.97 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
962.1 | 49.92 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
962.15 | 49.92 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
962.2 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
962.25 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
962.3 | 49.94 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
962.35 | 49.94 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
962.4 | 50.01 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
962.45 | 50.01 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
962.5 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
962.55 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
962.6 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
962.65 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
962.7 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
962.75 | 49.95 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
962.8 | 49.97 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
962.85 | 49.97 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
962.9 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
962.95 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
963 | 49.87 | 49.87 | 0.335 | 0.335 | 3.35 | 50.01 | 0 | 0 | 0 | 1.675 | 1.675 | 0 | 12 | 1 | 1 | 1.675 | 10 | 0 | 0
963.05 | 49.87 | 49.87 | 0.335 | 0.335 | 3.35 | 49.99 | 0 | 0 | 0 | 1.675 | 1.675 | 0 | 12 | 1 | 1 | 1.675 | 10 | 0 | 0
963.1 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
963.15 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 2.6691 | 2.6691 | 0 | 12 | 1 | 1 | 2.6691 | 10 | 0 | 0
963.2 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
963.25 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
963.3 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
963.35 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
963.4 | 49.84 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
963.45 | 49.84 | 49.79 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
963.5 | 49.89 | 49.79 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
963.55 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.12647 | 1.2647 | 5.6324 | 5.6324 | 0 | 12 | 1 | 1 | 5.6324 | 10 | 0 | 0
963.6 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.145 | 1.45 | 5.725 | 5.725 | 0 | 12 | 1 | 1 | 5.725 | 10 | 0 | 0
963.65 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.145 | 1.45 | 5.725 | 5.725 | 0 | 12 | 1 | 1 | 5.725 | 10 | 0 | 0
963.7 | 49.96 | 49.79 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
963.75 | 49.96 | 49.79 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
963.8 | 50.02 | 49.79 | 1 | 1 | 10 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 4.9853 | 4.9853 | 0 | 12 | 1 | 1 | 4.9853 | 10 | 0 | 0
963.85 | 50.02 | 49.79 | 1 | 1 | 10 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 4.9853 | 4.9853 | 0 | 12 | 1 | 1 | 4.9853 | 10 | 0 | 0
963.9 | 50.03 | 49.79 | 1 | 1 | 10 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.9559 | 4.9559 | 0 | 12 | 1 | 1 | 4.9559 | 10 | 0 | 0
963.95 | 50.03 | 49.84 | 0.62 | 0.9 | 9 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.4559 | 4.4559 | 0 | 12 | 1 | 1 | 4.4559 | 10 | 0 | 0
964 | 50.02 | 49.84 | 0.62 | 0.8 | 8 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 3.9559 | 3.9559 | 0 | 12 | 1 | 1 | 3.9559 | 10 | 0 | 0
964.05 | 50.02 | 49.89 | 0.145 | 0.7 | 7 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 3.4559 | 3.4559 | 0 | 12 | 1 | 1 | 3.4559 | 10 | 0 | 0
964.1 | 50.08 | 49.89 | 0.145 | 0.6 | 6 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 2.8088 | 2.8088 | 0 | 12 | 1 | 1 | 2.8088 | 10 | 0 | 0
964.15 | 50.08 | 49.89 | 0.145 | 0.5 | 5 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 2.3088 | 2.3088 | 0 | 12 | 1 | 1 | 2.3088 | 10 | 0 | 0
964.2 | 50.01 | 49.89 | 0.145 | 0.4 | 4 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 1.8088 | 1.8088 | 0 | 12 | 1 | 1 | 1.8088 | 10 | 0 | 0
964.25 | 50.01 | 49.96 | 0.014706 | 0.3 | 3 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 1.3088 | 1.3088 | 0 | 12 | 1 | 1 | 1.3088 | 10 | 0 | 0
964.3 | 49.94 | 49.94 | 0.026471 | 0.2 | 2 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.80882 | 0.80882 | 0 | 12 | 1 | 1 | 0.80882 | 10 | 0 | 0
964.35 | 49.94 | 49.94 | 0.026471 | 0.1 | 1 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.30882 | 0.30882 | 0 | 12 | 1 | 1 | 0.30882 | 10 | 0 | 0
964.4 | 50 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
964.45 | 50 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
964.5 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
964.55 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
964.6 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
964.65 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
964.7 | 49.92 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
964.75 | 49.92 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
964.8 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50.01 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
964.85 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
964.9 | 49.92 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
964.95 | 49.92 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
965 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
965.05 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
965.1 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
965.15 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
965.2 | 49.87 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
965.25 | 49.87 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
965.3 | 49.8 | 49.8 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
965.35 | 49.8 | 49.8 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
965.4 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
965.45 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
965.5 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
965.55 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
965.6 | 49.72 | 49.72 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
965.65 | 49.72 | 49.72 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
965.7 | 49.67 | 49.67 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
965.75 | 49.67 | 49.67 | 1 | 1 | 10 | 49.87 | 0.335 | 0.14412 | 1.4412 | 5.7206 | 5.7206 | 0 | 12 | 1 | 1 | 5.7206 | 10 | 0 | 0
965.8 | 49.65 | 49.65 | 1 | 1 | 10 | 49.87 | 0.335 | 0.24412 | 2.4412 | 6.2206 | 6.2206 | 0 | 12 | 1 | 1 | 6.2206 | 10 | 0 | 0
965.85 | 49.65 | 49.65 | 1 | 1 | 10 | 49.8 | 1 | 0.34412 | 3.4412 | 6.7206 | 6.7206 | 0 | 12 | 1 | 1 | 6.7206 | 10 | 0 | 0
965.9 | 49.59 | 49.59 | 1 | 1 | 10 | 49.8 | 1 | 0.44412 | 4.4412 | 7.2206 | 7.2206 | 0 | 12 | 1 | 1 | 7.2206 | 10 | 0 | 0
965.95 | 49.59 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.54412 | 5.4412 | 7.7206 | 7.7206 | 0 | 12 | 1 | 1 | 7.7206 | 10 | 0 | 0
966 | 49.66 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.64412 | 6.4412 | 8.2206 | 8.2206 | 0 | 12 | 1 | 1 | 8.2206 | 10 | 0 | 0
966.05 | 49.66 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.74412 | 7.4412 | 8.7206 | 8.7206 | 0 | 12 | 1 | 1 | 8.7206 | 10 | 0 | 0
966.1 | 49.63 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.84412 | 8.4412 | 9.2206 | 9.2206 | 0 | 12 | 1 | 1 | 9.2206 | 10 | 0 | 0
966.15 | 49.63 | 49.59 | 1 | 1 | 10 | 49.72 | 1 | 0.94412 | 9.4412 | 9.7206 | 9.7206 | 0 | 12 | 1 | 1 | 9.7206 | 10 | 0 | 0
966.2 | 49.61 | 49.59 | 1 | 1 | 10 | 49.72 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
966.25 | 49.61 | 49.59 | 1 | 1 | 10 | 49.67 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
966.3 | 49.54 | 49.54 | 1 | 1 | 10 | 49.67 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
966.35 | 49.54 | 49.54 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
966.4 | 49.46 | 49.46 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
966.45 | 49.46 | 49.46 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
966.5 | 49.45 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
966.55 | 49.45 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
966.6 | 49.51 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
966.65 | 49.51 | 49.45 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
966.7 | 49.5 | 49.45 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
966.75 | 49.5 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
966.8 | 49.54 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
966.85 | 49.54 | 49.45 | 1 | 1 | 10 | 49.54 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
966.9 | 49.59 | 49.45 | 1 | 1 | 10 | 49.59 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
966.95 | 49.59 | 49.45 | 1 | 1 | 10 | 49.59 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
967 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
967.05 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
967.1 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
967.15 | 49.61 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
967.2 | 49.53 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
967.25 | 49.53 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
967.3 | 49.54 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
967.35 | 49.54 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
967.4 | 49.61 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
967.45 | 49.61 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
967.5 | 49.66 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
967.55 | 49.66 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
967.6 | 49.64 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
967.65 | 49.64 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
967.7 | 49.69 | 49.53 | 1 | 1 | 10 | 49.69 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
967.75 | 49.69 | 49.53 | 1 | 1 | 10 | 49.69 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
967.8 | 49.74 | 49.53 | 1 | 1 | 10 | 49.74 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
967.85 | 49.74 | 49.54 | 1 | 1 | 10 | 49.74 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
967.9 | 49.78 | 49.54 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
967.95 | 49.78 | 49.61 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
968 | 49.82 | 49.61 | 1 | 1 | 10 | 49.82 | 0.81 | 0.81 | 8.1 | 9.05 | 9.05 | 0 | 12 | 1 | 1 | 9.05 | 10 | 0 | 0
968.05 | 49.82 | 49.64 | 1 | 1 | 10 | 49.82 | 0.81 | 0.81 | 8.1 | 9.05 | 9.05 | 0 | 12 | 1 | 1 | 9.05 | 10 | 0 | 0
968.1 | 49.86 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
968.15 | 49.86 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
968.2 | 49.84 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
968.25 | 49.84 | 49.69 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
968.3 | 49.91 | 49.69 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
968.35 | 49.91 | 49.74 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
968.4 | 49.97 | 49.74 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
968.45 | 49.97 | 49.78 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
968.5 | 50.03 | 49.78 | 1 | 1 | 10 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.9559 | 4.9559 | 0 | 12 | 1 | 1 | 4.9559 | 10 | 0 | 0
968.55 | 50.03 | 49.82 | 0.81 | 0.9 | 9 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.4559 | 4.4559 | 0 | 12 | 1 | 1 | 4.4559 | 10 | 0 | 0
968.6 | 50.05 | 49.82 | 0.81 | 0.81 | 8.1 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 3.9471 | 3.9471 | 0 | 12 | 1 | 1 | 3.9471 | 10 | 0 | 0
968.65 | 50.05 | 49.84 | 0.62 | 0.71 | 7.1 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 3.4471 | 3.4471 | 0 | 12 | 1 | 1 | 3.4471 | 10 | 0 | 0
968.7 | 50.01 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
968.75 | 50.01 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
968.8 | 49.95 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
968.85 | 49.95 | 49.91 | 0.044118 | 0.52 | 5.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.4971 | 2.4971 | 0 | 12 | 1 | 1 | 2.4971 | 10 | 0 | 0
968.9 | 49.99 | 49.91 | 0.044118 | 0.42 | 4.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 1.9971 | 1.9971 | 0 | 12 | 1 | 1 | 1.9971 | 10 | 0 | 0
968.95 | 49.99 | 49.95 | 0.020588 | 0.32 | 3.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 1.4971 | 1.4971 | 0 | 12 | 1 | 1 | 1.4971 | 10 | 0 | 0
969 | 49.92 | 49.92 | 0.038235 | 0.22 | 2.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.99706 | 0.99706 | 0 | 12 | 1 | 1 | 0.99706 | 10 | 0 | 0
969.05 | 49.92 | 49.92 | 0.038235 | 0.12 | 1.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.49706 | 0.49706 | 0 | 12 | 1 | 1 | 0.49706 | 10 | 0 | 0
969.1 | 49.97 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
969.15 | 49.97 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
969.2 | 50.02 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
969.25 | 50.02 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.17647 | 0.17647 | 0 | 12 | 1 | 1 | 0.17647 | 10 | 0 | 0
969.3 | 50.07 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
969.35 | 50.07 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
969.4 | 50.06 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
969.45 | 50.06 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
969.5 | 50.13 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
969.55 | 50.13 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
969.6 | 50.09 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
969.65 | 50.09 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6309 | -1.6309 | 0 | 12 | 1 | 1 | -1.6309 | 10 | 0 | 0
969.7 | 50.07 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6309 | -1.6309 | 0 | 12 | 1 | 1 | -1.6309 | 10 | 0 | 0
969.75 | 50.07 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6897 | -1.6897 | 0 | 12 | 1 | 1 | -1.6897 | 10 | 0 | 0
969.8 | 50.07 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6897 | -1.6897 | 0 | 12 | 1 | 1 | -1.6897 | 10 | 0 | 0
969.85 | 50.07 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.13 | -0.335 | -0.335 | -3.35 | -1.8074 | -1.8074 | 0 | 12 | 1 | 1 | -1.8074 | 10 | 0 | 0
969.9 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.13 | -0.335 | -0.335 | -3.35 | -1.7779 | -1.7779 | 0 | 12 | 1 | 1 | -1.7779 | 10 | 0 | 0
969.95 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.13 | -0.335 | -0.335 | -3.35 | -1.7779 | -1.7779 | 0 | 12 | 1 | 1 | -1.7779 | 10 | 0 | 0
970 | 50.01 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
970.05 | 50.01 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
970.1 | 50.07 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
970.15 | 50.07 | 50.01 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.235 | -2.35 | -1.175 | -1.175 | 0 | 12 | 1 | 1 | -1.175 | 10 | 0 | 0
970.2 | 50.05 | 50.01 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.135 | -1.35 | -0.675 | -0.675 | 0 | 12 | 1 | 1 | -0.675 | 10 | 0 | 0
970.25 | 50.05 | 50.01 | 0 | 0 | 0 | 50.07 | -0.032353 | -0.035 | -0.35 | -0.175 | -0.175 | 0 | 12 | 1 | 1 | -0.175 | 10 | 0 | 0
970.3 | 50.1 | 50.01 | 0 | 0 | 0 | 50.1 | -0.05 | -0.05 | -0.5 | -0.25 | -0.25 | 0 | 12 | 1 | 1 | -0.25 | 10 | 0 | 0
970.35 | 50.1 | 50.01 | 0 | 0 | 0 | 50.1 | -0.05 | -0.05 | -0.5 | -0.25 | -0.25 | 0 | 12 | 1 | 1 | -0.25 | 10 | 0 | 0
970.4 | 50.11 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
970.45 | 50.11 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
970.5 | 50.06 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
970.55 | 50.06 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
970.6 | 50.04 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
970.65 | 50.04 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
970.7 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
970.75 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
970.8 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
970.85 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
970.9 | 50.11 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
970.95 | 50.11 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
971 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
971.05 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
971.1 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
971.15 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
971.2 | 50.02 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.11 | -0.145 | -0.145 | -1.45 | -0.73971 | -0.73971 | 0 | 12 | 1 | 1 | -0.73971 | 10 | 0 | 0
971.25 | 50.02 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.11 | -0.145 | -0.145 | -1.45 | -0.73971 | -0.73971 | 0 | 12 | 1 | 1 | -0.73971 | 10 | 0 | 0
971.3 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
971.35 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
971.4 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
971.45 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
971.5 | 50.01 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
971.55 | 50.01 | 50 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.045 | -0.45 | -0.225 | -0.225 | 0 | 12 | 1 | 1 | -0.225 | 10 | 0 | 0
971.6 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
971.65 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
971.7 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
971.75 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
971.8 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.14706 | 0.14706 | 0 | 12 | 1 | 1 | 0.14706 | 10 | 0 | 0
971.85 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
971.9 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
971.95 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
972 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
972.05 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
972.1 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
972.15 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
972.2 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
972.25 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
972.3 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
972.35 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
972.4 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
972.45 | 50 | 50 | 0 | 0 | 0 | 50.01 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
972.5 | 49.5 | 49.5 | 1 | 1 | 10 | 50.01 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
972.55 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
972.6 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
972.65 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
972.7 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
972.75 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
972.8 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
972.85 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
972.9 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
972.95 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
973 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
973.05 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.1 | 1 | 5.5 | 5.5 | 0 | 12 | 1 | 1 | 5.5 | 10 | 0 | 0
973.1 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.2 | 2 | 6 | 6 | 0 | 12 | 1 | 1 | 6 | 10 | 0 | 0
973.15 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.3 | 3 | 6.5 | 6.5 | 0 | 12 | 1 | 1 | 6.5 | 10 | 0 | 0
973.2 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.4 | 4 | 7 | 7 | 0 | 12 | 1 | 1 | 7 | 10 | 0 | 0
973.25 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.5 | 5 | 7.5 | 7.5 | 0 | 12 | 1 | 1 | 7.5 | 10 | 0 | 0
973.3 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.6 | 6 | 8 | 8 | 0 | 12 | 1 | 1 | 8 | 10 | 0 | 0
973.35 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.7 | 7 | 8.5 | 8.5 | 0 | 12 | 1 | 1 | 8.5 | 10 | 0 | 0
973.4 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.8 | 8 | 9 | 9 | 0 | 12 | 1 | 1 | 9 | 10 | 0 | 0
973.45 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.9 | 9 | 9.5 | 9.5 | 0 | 12 | 1 | 1 | 9.5 | 10 | 0 | 0
973.5 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
973.55 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
973.6 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
973.65 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
973.7 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
973.75 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
973.8 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
973.85 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
973.9 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
973.95 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
974 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
974.05 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
974.1 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
974.15 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
974.2 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
974.25 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
974.3 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
974.35 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
974.4 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
974.45 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
974.5 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
974.55 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
974.6 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
974.65 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
974.7 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
974.75 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
974.8 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
974.85 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
974.9 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
974.95 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
975 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
975.05 | 50.5 | 50.5 | -1 | 0.9 | 9 | 50.5 | -1 | -1 | -10 | -0.5 | -0.5 | 0 | 12 | 1 | 1 | -0.5 | 10 | 0 | 0
975.1 | 50.5 | 50.5 | -1 | 0.8 | 8 | 50.5 | -1 | -1 | -10 | -1 | -1 | 0 | 12 | 1 | 1 | -1 | 10 | 0 | 0
975.15 | 50.5 | 50.5 | -1 | 0.7 | 7 | 50.5 | -1 | -1 | -10 | -1.5 | -1.5 | 0 | 12 | 1 | 1 | -1.5 | 10 | 0 | 0
975.2 | 50.5 | 50.5 | -1 | 0.6 | 6 | 50.5 | -1 | -1 | -10 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
975.25 | 50.5 | 50.5 | -1 | 0.5 | 5 | 50.5 | -1 | -1 | -10 | -2.5 | -2.5 | 0 | 12 | 1 | 1 | -2.5 | 10 | 0 | 0
975.3 | 50.5 | 50.5 | -1 | 0.4 | 4 | 50.5 | -1 | -1 | -10 | -3 | -3 | 0 | 12 | 1 | 1 | -3 | 10 | 0 | 0
975.35 | 50.5 | 50.5 | -1 | 0.3 | 3 | 50.5 | -1 | -1 | -10 | -3.5 | -3.5 | 0 | 12 | 1 | 1 | -3.5 | 10 | 0 | 0
975.4 | 50.5 | 50.5 | -1 | 0.2 | 2 | 50.5 | -1 | -1 | -10 | -4 | -4 | 0 | 12 | 1 | 1 | -4 | 10 | 0 | 0
975.45 | 50.5 | 50.5 | -1 | 0.1 | 1 | 50.5 | -1 | -1 | -10 | -4.5 | -4.5 | 0 | 12 | 1 | 1 | -4.5 | 10 | 0 | 0
975.5 | 50.5 | 50.5 | -1 | 0 | 0 | 50.5 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
975.55 | 50.5 | 50.5 | -1 | -0.1 | -1 | 50.5 | -1 | -1 | -10 | -5.5 | -5.5 | 0 | 12 | 1 | 1 | -5.5 | 10 | 0 | 0
975.6 | 50.5 | 50.5 | -1 | -0.2 | -2 | 50.5 | -1 | -1 | -10 | -6 | -6 | 0 | 12 | 1 | 1 | -6 | 10 | 0 | 0
975.65 | 50.5 | 50.5 | -1 | -0.3 | -3 | 50.5 | -1 | -1 | -10 | -6.5 | -6.5 | 0 | 12 | 1 | 1 | -6.5 | 10 | 0 | 0
975.7 | 50.5 | 50.5 | -1 | -0.4 | -4 | 50.5 | -1 | -1 | -10 | -7 | -7 | 0 | 12 | 1 | 1 | -7 | 10 | 0 | 0
975.75 | 50.5 | 50.5 | -1 | -0.5 | -5 | 50.5 | -1 | -1 | -10 | -7.5 | -7.5 | 0 | 12 | 1 | 1 | -7.5 | 10 | 0 | 0
975.8 | 50.5 | 50.5 | -1 | -0.6 | -6 | 50.5 | -1 | -1 | -10 | -8 | -8 | 0 | 12 | 1 | 1 | -8 | 10 | 0 | 0
975.85 | 50.5 | 50.5 | -1 | -0.7 | -7 | 50.5 | -1 | -1 | -10 | -8.5 | -8.5 | 0 | 12 | 1 | 1 | -8.5 | 10 | 0 | 0
975.9 | 50.5 | 50.5 | -1 | -0.8 | -8 | 50.5 | -1 | -1 | -10 | -9 | -9 | 0 | 12 | 1 | 1 | -9 | 10 | 0 | 0
975.95 | 50.5 | 50.5 | -1 | -0.9 | -9 | 50.5 | -1 | -1 | -10 | -9.5 | -9.5 | 0 | 12 | 1 | 1 | -9.5 | 10 | 0 | 0
976 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
976.05 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
976.1 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
976.15 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
976.2 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
976.25 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
976.3 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
976.35 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
976.4 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
976.45 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
976.5 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
976.55 | 50.47 | 50.47 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
976.6 | 50.45 | 50.45 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
976.65 | 50.42 | 50.42 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
976.7 | 50.4 | 50.4 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
976.75 | 50.37 | 50.37 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
976.8 | 50.35 | 50.35 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
976.85 | 50.32 | 50.32 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
976.9 | 50.29 | 50.29 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
976.95 | 50.27 | 50.27 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
977 | 50.24 | 50.24 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
977.05 | 50.22 | 50.22 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
977.1 | 50.19 | 50.19 | -0.905 | -0.905 | -9.05 | 50.47 | -1 | -1 | -10 | -9.525 | -9.525 | 0 | 12 | 1 | 1 | -9.525 | 10 | 0 | 0
977.15 | 50.17 | 50.17 | -0.715 | -0.715 | -7.15 | 50.45 | -1 | -1 | -10 | -8.575 | -8.575 | 0 | 12 | 1 | 1 | -8.575 | 10 | 0 | 0
977.2 | 50.14 | 50.14 | -0.43 | -0.43 | -4.3 | 50.42 | -1 | -1 | -10 | -7.15 | -7.15 | 0 | 12 | 1 | 1 | -7.15 | 10 | 0 | 0
977.25 | 50.12 | 50.12 | -0.24 | -0.24 | -2.4 | 50.4 | -1 | -1 | -10 | -6.2 | -6.2 | 0 | 12 | 1 | 1 | -6.2 | 10 | 0 | 0
977.3 | 50.09 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 50.37 | -1 | -1 | -10 | -5.2206 | -5.2206 | 0 | 12 | 1 | 1 | -5.2206 | 10 | 0 | 0
977.35 | 50.06 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.35 | -1 | -1 | -10 | -5.1324 | -5.1324 | 0 | 12 | 1 | 1 | -5.1324 | 10 | 0 | 0
977.4 | 50.04 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.32 | -1 | -1 | -10 | -5.0735 | -5.0735 | 0 | 12 | 1 | 1 | -5.0735 | 10 | 0 | 0
977.45 | 50.01 | 50.01 | 0 | 0 | 0 | 50.29 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
977.5 | 49.99 | 49.99 | 0 | 0 | 0 | 50.27 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
977.55 | 49.96 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.24 | -1 | -1 | -10 | -4.9265 | -4.9265 | 0 | 12 | 1 | 1 | -4.9265 | 10 | 0 | 0
977.6 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.22 | -1 | -1 | -10 | -4.8676 | -4.8676 | 0 | 12 | 1 | 1 | -4.8676 | 10 | 0 | 0
977.65 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.19 | -0.905 | -0.905 | -9.05 | -4.3044 | -4.3044 | 0 | 12 | 1 | 1 | -4.3044 | 10 | 0 | 0
977.7 | 49.88 | 49.88 | 0.24 | 0.24 | 2.4 | 50.17 | -0.715 | -0.805 | -8.05 | -2.825 | -2.825 | 0 | 12 | 1 | 1 | -2.825 | 10 | 0 | 0
977.75 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.14 | -0.43 | -0.705 | -7.05 | -1.375 | -1.375 | 0 | 12 | 1 | 1 | -1.375 | 10 | 0 | 0
977.8 | 49.83 | 49.83 | 0.715 | 0.715 | 7.15 | 50.12 | -0.24 | -0.605 | -6.05 | 0.55 | 0.55 | 0 | 12 | 1 | 1 | 0.55 | 10 | 0 | 0
977.85 | 49.81 | 49.81 | 0.905 | 0.905 | 9.05 | 50.09 | -0.044118 | -0.505 | -5.05 | 2 | 2 | 0 | 12 | 1 | 1 | 2 | 10 | 0 | 0
977.9 | 49.78 | 49.78 | 1 | 1 | 10 | 50.06 | -0.026471 | -0.405 | -4.05 | 2.975 | 2.975 | 0 | 12 | 1 | 1 | 2.975 | 10 | 0 | 0
977.95 | 49.76 | 49.76 | 1 | 1 | 10 | 50.04 | -0.014706 | -0.305 | -3.05 | 3.475 | 3.475 | 0 | 12 | 1 | 1 | 3.475 | 10 | 0 | 0
978 | 49.73 | 49.73 | 1 | 1 | 10 | 50.01 | 0 | -0.205 | -2.05 | 3.975 | 3.975 | 0 | 12 | 1 | 1 | 3.975 | 10 | 0 | 0
978.05 | 49.71 | 49.71 | 1 | 1 | 10 | 49.99 | 0 | -0.105 | -1.05 | 4.475 | 4.475 | 0 | 12 | 1 | 1 | 4.475 | 10 | 0 | 0
978.1 | 49.68 | 49.68 | 1 | 1 | 10 | 49.96 | 0.014706 | -0.005 | -0.05 | 4.975 | 4.975 | 0 | 12 | 1 | 1 | 4.975 | 10 | 0 | 0
978.15 | 49.65 | 49.65 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
978.2 | 49.63 | 49.63 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
978.25 | 49.6 | 49.6 | 1 | 1 | 10 | 49.88 | 0.24 | 0.14412 | 1.4412 | 5.7206 | 5.7206 | 0 | 12 | 1 | 1 | 5.7206 | 10 | 0 | 0
978.3 | 49.58 | 49.58 | 1 | 1 | 10 | 49.86 | 0.43 | 0.24412 | 2.4412 | 6.2206 | 6.2206 | 0 | 12 | 1 | 1 | 6.2206 | 10 | 0 | 0
978.35 | 49.55 | 49.55 | 1 | 1 | 10 | 49.83 | 0.715 | 0.34412 | 3.4412 | 6.7206 | 6.7206 | 0 | 12 | 1 | 1 | 6.7206 | 10 | 0 | 0
978.4 | 49.53 | 49.53 | 1 | 1 | 10 | 49.81 | 0.905 | 0.44412 | 4.4412 | 7.2206 | 7.2206 | 0 | 12 | 1 | 1 | 7.2206 | 10 | 0 | 0
978.45 | 49.5 | 49.5 | 1 | 1 | 10 | 49.78 | 1 | 0.54412 | 5.4412 | 7.7206 | 7.7206 | 0 | 12 | 1 | 1 | 7.7206 | 10 | 0 | 0
978.5 | 49.5 | 49.5 | 1 | 1 | 10 | 49.76 | 1 | 0.64412 | 6.4412 | 8.2206 | 8.2206 | 0 | 12 | 1 | 1 | 8.2206 | 10 | 0 | 0
978.55 | 49.53 | 49.5 | 1 | 1 | 10 | 49.73 | 1 | 0.74412 | 7.4412 | 8.7206 | 8.7206 | 0 | 12 | 1 | 1 | 8.7206 | 10 | 0 | 0
978.6 | 49.55 | 49.5 | 1 | 1 | 10 | 49.71 | 1 | 0.84412 | 8.4412 | 9.2206 | 9.2206 | 0 | 12 | 1 | 1 | 9.2206 | 10 | 0 | 0
978.65 | 49.58 | 49.5 | 1 | 1 | 10 | 49.68 | 1 | 0.94412 | 9.4412 | 9.7206 | 9.7206 | 0 | 12 | 1 | 1 | 9.7206 | 10 | 0 | 0
978.7 | 49.6 | 49.5 | 1 | 1 | 10 | 49.65 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
978.75 | 49.63 | 49.5 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
978.8 | 49.65 | 49.5 | 1 | 1 | 10 | 49.65 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
978.85 | 49.68 | 49.5 | 1 | 1 | 10 | 49.68 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
978.9 | 49.71 | 49.5 | 1 | 1 | 10 | 49.71 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
978.95 | 49.73 | 49.5 | 1 | 1 | 10 | 49.73 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
979 | 49.76 | 49.5 | 1 | 1 | 10 | 49.76 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
979.05 | 49.78 | 49.5 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
979.1 | 49.81 | 49.53 | 1 | 1 | 10 | 49.81 | 0.905 | 0.905 | 9.05 | 9.525 | 9.525 | 0 | 12 | 1 | 1 | 9.525 | 10 | 0 | 0
979.15 | 49.83 | 49.55 | 1 | 1 | 10 | 49.83 | 0.715 | 0.715 | 7.15 | 8.575 | 8.575 | 0 | 12 | 1 | 1 | 8.575 | 10 | 0 | 0
979.2 | 49.86 | 49.58 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
979.25 | 49.88 | 49.6 | 1 | 1 | 10 | 49.88 | 0.24 | 0.24 | 2.4 | 6.2 | 6.2 | 0 | 12 | 1 | 1 | 6.2 | 10 | 0 | 0
979.3 | 49.91 | 49.63 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
979.35 | 49.94 | 49.65 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
979.4 | 49.96 | 49.68 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
979.45 | 49.99 | 49.71 | 1 | 1 | 10 | 49.99 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
979.5 | 50.01 | 49.73 | 1 | 1 | 10 | 50.01 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
979.55 | 50.04 | 49.76 | 1 | 1 | 10 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 4.9265 | 4.9265 | 0 | 12 | 1 | 1 | 4.9265 | 10 | 0 | 0
979.6 | 50.06 | 49.78 | 1 | 1 | 10 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 4.8676 | 4.8676 | 0 | 12 | 1 | 1 | 4.8676 | 10 | 0 | 0
979.65 | 50.09 | 49.81 | 0.905 | 0.905 | 9.05 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 4.3044 | 4.3044 | 0 | 12 | 1 | 1 | 4.3044 | 10 | 0 | 0
979.7 | 50.12 | 49.83 | 0.715 | 0.805 | 8.05 | 50.12 | -0.24 | -0.24 | -2.4 | 2.825 | 2.825 | 0 | 12 | 1 | 1 | 2.825 | 10 | 0 | 0
979.75 | 50.14 | 49.86 | 0.43 | 0.705 | 7.05 | 50.14 | -0.43 | -0.43 | -4.3 | 1.375 | 1.375 | 0 | 12 | 1 | 1 | 1.375 | 10 | 0 | 0
979.8 | 50.17 | 49.88 | 0.24 | 0.605 | 6.05 | 50.17 | -0.715 | -0.715 | -7.15 | -0.55 | -0.55 | 0 | 12 | 1 | 1 | -0.55 | 10 | 0 | 0
979.85 | 50.19 | 49.91 | 0.044118 | 0.505 | 5.05 | 50.19 | -0.905 | -0.905 | -9.05 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
979.9 | 50.22 | 49.94 | 0.026471 | 0.405 | 4.05 | 50.22 | -1 | -1 | -10 | -2.975 | -2.975 | 0 | 12 | 1 | 1 | -2.975 | 10 | 0 | 0
979.95 | 50.24 | 49.96 | 0.014706 | 0.305 | 3.05 | 50.24 | -1 | -1 | -10 | -3.475 | -3.475 | 0 | 12 | 1 | 1 | -3.475 | 10 | 0 | 0
980 | 50.27 | 49.99 | 0 | 0.205 | 2.05 | 50.27 | -1 | -1 | -10 | -3.975 | -3.975 | 0 | 12 | 1 | 1 | -3.975 | 10 | 0 | 0
980.05 | 50.29 | 50.01 | 0 | 0.105 | 1.05 | 50.29 | -1 | -1 | -10 | -4.475 | -4.475 | 0 | 12 | 1 | 1 | -4.475 | 10 | 0 | 0
980.1 | 50.32 | 50.04 | -0.014706 | 0.005 | 0.05 | 50.32 | -1 | -1 | -10 | -4.975 | -4.975 | 0 | 12 | 1 | 1 | -4.975 | 10 | 0 | 0
980.15 | 50.35 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.35 | -1 | -1 | -10 | -5.1324 | -5.1324 | 0 | 12 | 1 | 1 | -5.1324 | 10 | 0 | 0
980.2 | 50.37 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 50.37 | -1 | -1 | -10 | -5.2206 | -5.2206 | 0 | 12 | 1 | 1 | -5.2206 | 10 | 0 | 0
980.25 | 50.4 | 50.12 | -0.24 | -0.14412 | -1.4412 | 50.4 | -1 | -1 | -10 | -5.7206 | -5.7206 | 0 | 12 | 1 | 1 | -5.7206 | 10 | 0 | 0
980.3 | 50.42 | 50.14 | -0.43 | -0.24412 | -2.4412 | 50.42 | -1 | -1 | -10 | -6.2206 | -6.2206 | 0 | 12 | 1 | 1 | -6.2206 | 10 | 0 | 0
980.35 | 50.45 | 50.17 | -0.715 | -0.34412 | -3.4412 | 50.45 | -1 | -1 | -10 | -6.7206 | -6.7206 | 0 | 12 | 1 | 1 | -6.7206 | 10 | 0 | 0
980.4 | 50.47 | 50.19 | -0.905 | -0.44412 | -4.4412 | 50.47 | -1 | -1 | -10 | -7.2206 | -7.2206 | 0 | 12 | 1 | 1 | -7.2206 | 10 | 0 | 0
980.45 | 50.5 | 50.22 | -1 | -0.54412 | -5.4412 | 50.5 | -1 | -1 | -10 | -7.7206 | -7.7206 | 0 | 12 | 1 | 1 | -7.7206 | 10 | 0 | 0
980.5 | 50.5 | 50.24 | -1 | -0.64412 | -6.4412 | 50.5 | -1 | -1 | -10 | -8.2206 | -8.2206 | 0 | 12 | 1 | 1 | -8.2206 | 10 | 0 | 0
980.55 | 50.47 | 50.27 | -1 | -0.74412 | -7.4412 | 50.5 | -1 | -1 | -10 | -8.7206 | -8.7206 | 0 | 12 | 1 | 1 | -8.7206 | 10 | 0 | 0
980.6 | 50.45 | 50.29 | -1 | -0.84412 | -8.4412 | 50.5 | -1 | -1 | -10 | -9.2206 | -9.2206 | 0 | 12 | 1 | 1 | -9.2206 | 10 | 0 | 0
980.65 | 50.42 | 50.32 | -1 | -0.94412 | -9.4412 | 50.5 | -1 | -1 | -10 | -9.7206 | -9.7206 | 0 | 12 | 1 | 1 | -9.7206 | 10 | 0 | 0
980.7 | 50.39 | 50.35 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
980.75 | 50.37 | 50.37 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
980.8 | 50.34 | 50.34 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
980.85 | 50.32 | 50.32 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
980.9 | 50.29 | 50.29 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
980.95 | 50.26 | 50.26 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
981 | 50.24 | 50.24 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
981.05 | 50.21 | 50.21 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
981.1 | 50.18 | 50.18 | -0.81 | -0.81 | -8.1 | 50.47 | -1 | -1 | -10 | -9.05 | -9.05 | 0 | 12 | 1 | 1 | -9.05 | 10 | 0 | 0
981.15 | 50.16 | 50.16 | -0.62 | -0.62 | -6.2 | 50.45 | -1 | -1 | -10 | -8.1 | -8.1 | 0 | 12 | 1 | 1 | -8.1 | 10 | 0 | 0
981.2 | 50.13 | 50.13 | -0.335 | -0.335 | -3.35 | 50.42 | -1 | -1 | -10 | -6.675 | -6.675 | 0 | 12 | 1 | 1 | -6.675 | 10 | 0 | 0
981.25 | 50.11 | 50.11 | -0.145 | -0.145 | -1.45 | 50.39 | -1 | -1 | -10 | -5.725 | -5.725 | 0 | 12 | 1 | 1 | -5.725 | 10 | 0 | 0
981.3 | 50.08 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 50.37 | -1 | -1 | -10 | -5.1912 | -5.1912 | 0 | 12 | 1 | 1 | -5.1912 | 10 | 0 | 0
981.35 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.34 | -1 | -1 | -10 | -5.1029 | -5.1029 | 0 | 12 | 1 | 1 | -5.1029 | 10 | 0 | 0
981.4 | 50.03 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 50.32 | -1 | -1 | -10 | -5.0441 | -5.0441 | 0 | 12 | 1 | 1 | -5.0441 | 10 | 0 | 0
981.45 | 50 | 50 | 0 | 0 | 0 | 50.29 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
981.5 | 50 | 50 | 0 | 0 | 0 | 50.26 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
981.55 | 50 | 50 | 0 | 0 | 0 | 50.24 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
981.6 | 50 | 50 | 0 | 0 | 0 | 50.21 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
981.65 | 50 | 50 | 0 | 0 | 0 | 50.18 | -0.81 | -0.9 | -9 | -4.5 | -4.5 | 0 | 12 | 1 | 1 | -4.5 | 10 | 0 | 0
981.7 | 50 | 50 | 0 | 0 | 0 | 50.16 | -0.62 | -0.8 | -8 | -4 | -4 | 0 | 12 | 1 | 1 | -4 | 10 | 0 | 0
981.75 | 50 | 50 | 0 | 0 | 0 | 50.13 | -0.335 | -0.7 | -7 | -3.5 | -3.5 | 0 | 12 | 1 | 1 | -3.5 | 10 | 0 | 0
981.8 | 50.01 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.6 | -6 | -3 | -3 | 0 | 12 | 1 | 1 | -3 | 10 | 0 | 0
981.85 | 50.01 | 50 | 0 | 0 | 0 | 50.08 | -0.038235 | -0.5 | -5 | -2.5 | -2.5 | 0 | 12 | 1 | 1 | -2.5 | 10 | 0 | 0
981.9 | 49.99 | 49.99 | 0 | 0 | 0 | 50.05 | -0.020588 | -0.4 | -4 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
981.95 | 49.99 | 49.99 | 0 | 0 | 0 | 50.03 | -0.0088235 | -0.3 | -3 | -1.5 | -1.5 | 0 | 12 | 1 | 1 | -1.5 | 10 | 0 | 0
982 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | -0.2 | -2 | -0.83824 | -0.83824 | 0 | 12 | 1 | 1 | -0.83824 | 10 | 0 | 0
982.05 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | -0.1 | -1 | -0.33824 | -0.33824 | 0 | 12 | 1 | 1 | -0.33824 | 10 | 0 | 0
982.1 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
982.15 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
982.2 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
982.25 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
982.3 | 49.89 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
982.35 | 49.89 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
982.4 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50.01 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
982.45 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
982.5 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
982.55 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 2.7868 | 2.7868 | 0 | 12 | 1 | 1 | 2.7868 | 10 | 0 | 0
982.6 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 2.7868 | 2.7868 | 0 | 12 | 1 | 1 | 2.7868 | 10 | 0 | 0
982.65 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 2.8456 | 2.8456 | 0 | 12 | 1 | 1 | 2.8456 | 10 | 0 | 0
982.7 | 49.94 | 49.85 | 0.525 | 0.525 | 5.25 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 2.7574 | 2.7574 | 0 | 12 | 1 | 1 | 2.7574 | 10 | 0 | 0
982.75 | 49.94 | 49.85 | 0.525 | 0.525 | 5.25 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 2.7574 | 2.7574 | 0 | 12 | 1 | 1 | 2.7574 | 10 | 0 | 0
982.8 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
982.85 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
982.9 | 49.93 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
982.95 | 49.93 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
983 | 49.96 | 49.85 | 0.525 | 0.525 | 5.25 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 2.6985 | 2.6985 | 0 | 12 | 1 | 1 | 2.6985 | 10 | 0 | 0
983.05 | 49.96 | 49.85 | 0.525 | 0.525 | 5.25 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 2.6985 | 2.6985 | 0 | 12 | 1 | 1 | 2.6985 | 10 | 0 | 0
983.1 | 49.99 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
983.15 | 49.99 | 49.91 | 0.044118 | 0.425 | 4.25 | 49.99 | 0 | 0 | 0 | 2.125 | 2.125 | 0 | 12 | 1 | 1 | 2.125 | 10 | 0 | 0
983.2 | 49.99 | 49.91 | 0.044118 | 0.325 | 3.25 | 49.99 | 0 | 0 | 0 | 1.625 | 1.625 | 0 | 12 | 1 | 1 | 1.625 | 10 | 0 | 0
983.25 | 49.99 | 49.93 | 0.032353 | 0.225 | 2.25 | 49.99 | 0 | 0 | 0 | 1.125 | 1.125 | 0 | 12 | 1 | 1 | 1.125 | 10 | 0 | 0
983.3 | 49.96 | 49.93 | 0.032353 | 0.125 | 1.25 | 49.99 | 0 | 0 | 0 | 0.625 | 0.625 | 0 | 12 | 1 | 1 | 0.625 | 10 | 0 | 0
983.35 | 49.96 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 49.99 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
983.4 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
983.45 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
983.5 | 50.05 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.058824 | 0.058824 | 0 | 12 | 1 | 1 | 0.058824 | 10 | 0 | 0
983.55 | 50.05 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
983.6 | 49.97 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
983.65 | 49.97 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
983.7 | 49.92 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
983.75 | 49.92 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
983.8 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
983.85 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
983.9 | 49.94 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
983.95 | 49.94 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
984 | 50.01 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
984.05 | 50.01 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
984.1 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
984.15 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
984.2 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
984.25 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
984.3 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
984.35 | 49.95 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
984.4 | 49.97 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
984.45 | 49.97 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
984.5 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
984.55 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
984.6 | 49.87 | 49.87 | 0.335 | 0.335 | 3.35 | 50.01 | 0 | 0 | 0 | 1.675 | 1.675 | 0 | 12 | 1 | 1 | 1.675 | 10 | 0 | 0
984.65 | 49.87 | 49.87 | 0.335 | 0.335 | 3.35 | 49.99 | 0 | 0 | 0 | 1.675 | 1.675 | 0 | 12 | 1 | 1 | 1.675 | 10 | 0 | 0
984.7 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
984.75 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 2.6691 | 2.6691 | 0 | 12 | 1 | 1 | 2.6691 | 10 | 0 | 0
984.8 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
984.85 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
984.9 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
984.95 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
985 | 49.84 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
985.05 | 49.84 | 49.79 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
985.1 | 49.89 | 49.79 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
985.15 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.12647 | 1.2647 | 5.6324 | 5.6324 | 0 | 12 | 1 | 1 | 5.6324 | 10 | 0 | 0
985.2 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.145 | 1.45 | 5.725 | 5.725 | 0 | 12 | 1 | 1 | 5.725 | 10 | 0 | 0
985.25 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.145 | 1.45 | 5.725 | 5.725 | 0 | 12 | 1 | 1 | 5.725 | 10 | 0 | 0
985.3 | 49.96 | 49.79 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
985.35 | 49.96 | 49.79 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
985.4 | 50.02 | 49.79 | 1 | 1 | 10 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 4.9853 | 4.9853 | 0 | 12 | 1 | 1 | 4.9853 | 10 | 0 | 0
985.45 | 50.02 | 49.79 | 1 | 1 | 10 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 4.9853 | 4.9853 | 0 | 12 | 1 | 1 | 4.9853 | 10 | 0 | 0
985.5 | 50.03 | 49.79 | 1 | 1 | 10 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.9559 | 4.9559 | 0 | 12 | 1 | 1 | 4.9559 | 10 | 0 | 0
985.55 | 50.03 | 49.84 | 0.62 | 0.9 | 9 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.4559 | 4.4559 | 0 | 12 | 1 | 1 | 4.4559 | 10 | 0 | 0
985.6 | 50.02 | 49.84 | 0.62 | 0.8 | 8 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 3.9559 | 3.9559 | 0 | 12 | 1 | 1 | 3.9559 | 10 | 0 | 0
985.65 | 50.02 | 49.89 | 0.145 | 0.7 | 7 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 3.4559 | 3.4559 | 0 | 12 | 1 | 1 | 3.4559 | 10 | 0 | 0
985.7 | 50.08 | 49.89 | 0.145 | 0.6 | 6 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 2.8088 | 2.8088 | 0 | 12 | 1 | 1 | 2.8088 | 10 | 0 | 0
985.75 | 50.08 | 49.89 | 0.145 | 0.5 | 5 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 2.3088 | 2.3088 | 0 | 12 | 1 | 1 | 2.3088 | 10 | 0 | 0
985.8 | 50.01 | 49.89 | 0.145 | 0.4 | 4 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 1.8088 | 1.8088 | 0 | 12 | 1 | 1 | 1.8088 | 10 | 0 | 0
985.85 | 50.01 | 49.96 | 0.014706 | 0.3 | 3 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 1.3088 | 1.3088 | 0 | 12 | 1 | 1 | 1.3088 | 10 | 0 | 0
985.9 | 49.94 | 49.94 | 0.026471 | 0.2 | 2 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.80882 | 0.80882 | 0 | 12 | 1 | 1 | 0.80882 | 10 | 0 | 0
985.95 | 49.94 | 49.94 | 0.026471 | 0.1 | 1 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.30882 | 0.30882 | 0 | 12 | 1 | 1 | 0.30882 | 10 | 0 | 0
986 | 50 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
986.05 | 50 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
986.1 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
986.15 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
986.2 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
986.25 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
986.3 | 49.92 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
986.35 | 49.92 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
986.4 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50.01 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
986.45 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
986.5 | 49.92 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
986.55 | 49.92 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
986.6 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
986.65 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
986.7 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
986.75 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
986.8 | 49.87 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
986.85 | 49.87 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
986.9 | 49.8 | 49.8 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
986.95 | 49.8 | 49.8 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
987 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
987.05 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
987.1 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
987.15 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
987.2 | 49.72 | 49.72 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
987.25 | 49.72 | 49.72 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
987.3 | 49.67 | 49.67 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
987.35 | 49.67 | 49.67 | 1 | 1 | 10 | 49.87 | 0.335 | 0.14412 | 1.4412 | 5.7206 | 5.7206 | 0 | 12 | 1 | 1 | 5.7206 | 10 | 0 | 0
987.4 | 49.65 | 49.65 | 1 | 1 | 10 | 49.87 | 0.335 | 0.24412 | 2.4412 | 6.2206 | 6.2206 | 0 | 12 | 1 | 1 | 6.2206 | 10 | 0 | 0
987.45 | 49.65 | 49.65 | 1 | 1 | 10 | 49.8 | 1 | 0.34412 | 3.4412 | 6.7206 | 6.7206 | 0 | 12 | 1 | 1 | 6.7206 | 10 | 0 | 0
987.5 | 49.59 | 49.59 | 1 | 1 | 10 | 49.8 | 1 | 0.44412 | 4.4412 | 7.2206 | 7.2206 | 0 | 12 | 1 | 1 | 7.2206 | 10 | 0 | 0
987.55 | 49.59 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.54412 | 5.4412 | 7.7206 | 7.7206 | 0 | 12 | 1 | 1 | 7.7206 | 10 | 0 | 0
987.6 | 49.66 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.64412 | 6.4412 | 8.2206 | 8.2206 | 0 | 12 | 1 | 1 | 8.2206 | 10 | 0 | 0
987.65 | 49.66 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.74412 | 7.4412 | 8.7206 | 8.7206 | 0 | 12 | 1 | 1 | 8.7206 | 10 | 0 | 0
987.7 | 49.63 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.84412 | 8.4412 | 9.2206 | 9.2206 | 0 | 12 | 1 | 1 | 9.2206 | 10 | 0 | 0
987.75 | 49.63 | 49.59 | 1 | 1 | 10 | 49.72 | 1 | 0.94412 | 9.4412 | 9.7206 | 9.7206 | 0 | 12 | 1 | 1 | 9.7206 | 10 | 0 | 0
987.8 | 49.61 | 49.59 | 1 | 1 | 10 | 49.72 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
987.85 | 49.61 | 49.59 | 1 | 1 | 10 | 49.67 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
987.9 | 49.54 | 49.54 | 1 | 1 | 10 | 49.67 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
987.95 | 49.54 | 49.54 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
988 | 49.46 | 49.46 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
988.05 | 49.46 | 49.46 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
988.1 | 49.45 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
988.15 | 49.45 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
988.2 | 49.51 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
988.25 | 49.51 | 49.45 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
988.3 | 49.5 | 49.45 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
988.35 | 49.5 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
988.4 | 49.54 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
988.45 | 49.54 | 49.45 | 1 | 1 | 10 | 49.54 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
988.5 | 49.59 | 49.45 | 1 | 1 | 10 | 49.59 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
988.55 | 49.59 | 49.45 | 1 | 1 | 10 | 49.59 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
988.6 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
988.65 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
988.7 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
988.75 | 49.61 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
988.8 | 49.53 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
988.85 | 49.53 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
988.9 | 49.54 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
988.95 | 49.54 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
989 | 49.61 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
989.05 | 49.61 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
989.1 | 49.66 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
989.15 | 49.66 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
989.2 | 49.64 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
989.25 | 49.64 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
989.3 | 49.69 | 49.53 | 1 | 1 | 10 | 49.69 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
989.35 | 49.69 | 49.53 | 1 | 1 | 10 | 49.69 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
989.4 | 49.74 | 49.53 | 1 | 1 | 10 | 49.74 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
989.45 | 49.74 | 49.54 | 1 | 1 | 10 | 49.74 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
989.5 | 49.78 | 49.54 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
989.55 | 49.78 | 49.61 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
989.6 | 49.82 | 49.61 | 1 | 1 | 10 | 49.82 | 0.81 | 0.81 | 8.1 | 9.05 | 9.05 | 0 | 12 | 1 | 1 | 9.05 | 10 | 0 | 0
989.65 | 49.82 | 49.64 | 1 | 1 | 10 | 49.82 | 0.81 | 0.81 | 8.1 | 9.05 | 9.05 | 0 | 12 | 1 | 1 | 9.05 | 10 | 0 | 0
989.7 | 49.86 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
989.75 | 49.86 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
989.8 | 49.84 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
989.85 | 49.84 | 49.69 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
989.9 | 49.91 | 49.69 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
989.95 | 49.91 | 49.74 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
990 | 49.97 | 49.74 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
990.05 | 49.97 | 49.78 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
990.1 | 50.03 | 49.78 | 1 | 1 | 10 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.9559 | 4.9559 | 0 | 12 | 1 | 1 | 4.9559 | 10 | 0 | 0
990.15 | 50.03 | 49.82 | 0.81 | 0.9 | 9 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.4559 | 4.4559 | 0 | 12 | 1 | 1 | 4.4559 | 10 | 0 | 0
990.2 | 50.05 | 49.82 | 0.81 | 0.81 | 8.1 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 3.9471 | 3.9471 | 0 | 12 | 1 | 1 | 3.9471 | 10 | 0 | 0
990.25 | 50.05 | 49.84 | 0.62 | 0.71 | 7.1 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 3.4471 | 3.4471 | 0 | 12 | 1 | 1 | 3.4471 | 10 | 0 | 0
990.3 | 50.01 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
990.35 | 50.01 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
990.4 | 49.95 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
990.45 | 49.95 | 49.91 | 0.044118 | 0.52 | 5.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.4971 | 2.4971 | 0 | 12 | 1 | 1 | 2.4971 | 10 | 0 | 0
990.5 | 49.99 | 49.91 | 0.044118 | 0.42 | 4.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 1.9971 | 1.9971 | 0 | 12 | 1 | 1 | 1.9971 | 10 | 0 | 0
990.55 | 49.99 | 49.95 | 0.020588 | 0.32 | 3.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 1.4971 | 1.4971 | 0 | 12 | 1 | 1 | 1.4971 | 10 | 0 | 0
990.6 | 49.92 | 49.92 | 0.038235 | 0.22 | 2.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.99706 | 0.99706 | 0 | 12 | 1 | 1 | 0.99706 | 10 | 0 | 0
990.65 | 49.92 | 49.92 | 0.038235 | 0.12 | 1.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.49706 | 0.49706 | 0 | 12 | 1 | 1 | 0.49706 | 10 | 0 | 0
990.7 | 49.97 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
990.75 | 49.97 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
990.8 | 50.02 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
990.85 | 50.02 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.17647 | 0.17647 | 0 | 12 | 1 | 1 | 0.17647 | 10 | 0 | 0
990.9 | 50.07 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
990.95 | 50.07 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
991 | 50.06 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
991.05 | 50.06 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
991.1 | 50.13 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
991.15 | 50.13 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
991.2 | 50.09 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
991.25 | 50.09 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6309 | -1.6309 | 0 | 12 | 1 | 1 | -1.6309 | 10 | 0 | 0
991.3 | 50.07 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6309 | -1.6309 | 0 | 12 | 1 | 1 | -1.6309 | 10 | 0 | 0
991.35 | 50.07 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6897 | -1.6897 | 0 | 12 | 1 | 1 | -1.6897 | 10 | 0 | 0
991.4 | 50.07 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6897 | -1.6897 | 0 | 12 | 1 | 1 | -1.6897 | 10 | 0 | 0
991.45 | 50.07 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.13 | -0.335 | -0.335 | -3.35 | -1.8074 | -1.8074 | 0 | 12 | 1 | 1 | -1.8074 | 10 | 0 | 0
991.5 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.13 | -0.335 | -0.335 | -3.35 | -1.7779 | -1.7779 | 0 | 12 | 1 | 1 | -1.7779 | 10 | 0 | 0
991.55 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.13 | -0.335 | -0.335 | -3.35 | -1.7779 | -1.7779 | 0 | 12 | 1 | 1 | -1.7779 | 10 | 0 | 0
991.6 | 50.01 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
991.65 | 50.01 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
991.7 | 50.07 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
991.75 | 50.07 | 50.01 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.235 | -2.35 | -1.175 | -1.175 | 0 | 12 | 1 | 1 | -1.175 | 10 | 0 | 0
991.8 | 50.05 | 50.01 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.135 | -1.35 | -0.675 | -0.675 | 0 | 12 | 1 | 1 | -0.675 | 10 | 0 | 0
991.85 | 50.05 | 50.01 | 0 | 0 | 0 | 50.07 | -0.032353 | -0.035 | -0.35 | -0.175 | -0.175 | 0 | 12 | 1 | 1 | -0.175 | 10 | 0 | 0
991.9 | 50.1 | 50.01 | 0 | 0 | 0 | 50.1 | -0.05 | -0.05 | -0.5 | -0.25 | -0.25 | 0 | 12 | 1 | 1 | -0.25 | 10 | 0 | 0
991.95 | 50.1 | 50.01 | 0 | 0 | 0 | 50.1 | -0.05 | -0.05 | -0.5 | -0.25 | -0.25 | 0 | 12 | 1 | 1 | -0.25 | 10 | 0 | 0
992 | 50.11 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
992.05 | 50.11 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
992.1 | 50.06 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
992.15 | 50.06 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
992.2 | 50.04 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
992.25 | 50.04 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
992.3 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
992.35 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
992.4 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
992.45 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
992.5 | 50.11 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
992.55 | 50.11 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
992.6 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
992.65 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
992.7 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
992.75 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
992.8 | 50.02 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.11 | -0.145 | -0.145 | -1.45 | -0.73971 | -0.73971 | 0 | 12 | 1 | 1 | -0.73971 | 10 | 0 | 0
992.85 | 50.02 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.11 | -0.145 | -0.145 | -1.45 | -0.73971 | -0.73971 | 0 | 12 | 1 | 1 | -0.73971 | 10 | 0 | 0
992.9 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
992.95 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
993 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
993.05 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
993.1 | 50.01 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
993.15 | 50.01 | 50 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.045 | -0.45 | -0.225 | -0.225 | 0 | 12 | 1 | 1 | -0.225 | 10 | 0 | 0
993.2 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
993.25 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
993.3 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
993.35 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
993.4 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.14706 | 0.14706 | 0 | 12 | 1 | 1 | 0.14706 | 10 | 0 | 0
993.45 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
993.5 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
993.55 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
993.6 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
993.65 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
993.7 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
993.75 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
993.8 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
993.85 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
993.9 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
993.95 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
994 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
994.05 | 50 | 50 | 0 | 0 | 0 | 50.01 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
994.1 | 49.5 | 49.5 | 1 | 1 | 10 | 50.01 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
994.15 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
994.2 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
994.25 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
994.3 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
994.35 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
994.4 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
994.45 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
994.5 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
994.55 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
994.6 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
994.65 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.1 | 1 | 5.5 | 5.5 | 0 | 12 | 1 | 1 | 5.5 | 10 | 0 | 0
994.7 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.2 | 2 | 6 | 6 | 0 | 12 | 1 | 1 | 6 | 10 | 0 | 0
994.75 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.3 | 3 | 6.5 | 6.5 | 0 | 12 | 1 | 1 | 6.5 | 10 | 0 | 0
994.8 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.4 | 4 | 7 | 7 | 0 | 12 | 1 | 1 | 7 | 10 | 0 | 0
994.85 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.5 | 5 | 7.5 | 7.5 | 0 | 12 | 1 | 1 | 7.5 | 10 | 0 | 0
994.9 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.6 | 6 | 8 | 8 | 0 | 12 | 1 | 1 | 8 | 10 | 0 | 0
994.95 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.7 | 7 | 8.5 | 8.5 | 0 | 12 | 1 | 1 | 8.5 | 10 | 0 | 0
995 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.8 | 8 | 9 | 9 | 0 | 12 | 1 | 1 | 9 | 10 | 0 | 0
995.05 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.9 | 9 | 9.5 | 9.5 | 0 | 12 | 1 | 1 | 9.5 | 10 | 0 | 0
995.1 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
995.15 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
995.2 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
995.25 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
995.3 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
995.35 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
995.4 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
995.45 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
995.5 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
995.55 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
995.6 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
995.65 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
995.7 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
995.75 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
995.8 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
995.85 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
995.9 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
995.95 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
996 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
996.05 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
996.1 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
996.15 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
996.2 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
996.25 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
996.3 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
996.35 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
996.4 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
996.45 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
996.5 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
996.55 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
996.6 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
996.65 | 50.5 | 50.5 | -1 | 0.9 | 9 | 50.5 | -1 | -1 | -10 | -0.5 | -0.5 | 0 | 12 | 1 | 1 | -0.5 | 10 | 0 | 0
996.7 | 50.5 | 50.5 | -1 | 0.8 | 8 | 50.5 | -1 | -1 | -10 | -1 | -1 | 0 | 12 | 1 | 1 | -1 | 10 | 0 | 0
996.75 | 50.5 | 50.5 | -1 | 0.7 | 7 | 50.5 | -1 | -1 | -10 | -1.5 | -1.5 | 0 | 12 | 1 | 1 | -1.5 | 10 | 0 | 0
996.8 | 50.5 | 50.5 | -1 | 0.6 | 6 | 50.5 | -1 | -1 | -10 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
996.85 | 50.5 | 50.5 | -1 | 0.5 | 5 | 50.5 | -1 | -1 | -10 | -2.5 | -2.5 | 0 | 12 | 1 | 1 | -2.5 | 10 | 0 | 0
996.9 | 50.5 | 50.5 | -1 | 0.4 | 4 | 50.5 | -1 | -1 | -10 | -3 | -3 | 0 | 12 | 1 | 1 | -3 | 10 | 0 | 0
996.95 | 50.5 | 50.5 | -1 | 0.3 | 3 | 50.5 | -1 | -1 | -10 | -3.5 | -3.5 | 0 | 12 | 1 | 1 | -3.5 | 10 | 0 | 0
997 | 50.5 | 50.5 | -1 | 0.2 | 2 | 50.5 | -1 | -1 | -10 | -4 | -4 | 0 | 12 | 1 | 1 | -4 | 10 | 0 | 0
997.05 | 50.5 | 50.5 | -1 | 0.1 | 1 | 50.5 | -1 | -1 | -10 | -4.5 | -4.5 | 0 | 12 | 1 | 1 | -4.5 | 10 | 0 | 0
997.1 | 50.5 | 50.5 | -1 | 0 | 0 | 50.5 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
997.15 | 50.5 | 50.5 | -1 | -0.1 | -1 | 50.5 | -1 | -1 | -10 | -5.5 | -5.5 | 0 | 12 | 1 | 1 | -5.5 | 10 | 0 | 0
997.2 | 50.5 | 50.5 | -1 | -0.2 | -2 | 50.5 | -1 | -1 | -10 | -6 | -6 | 0 | 12 | 1 | 1 | -6 | 10 | 0 | 0
997.25 | 50.5 | 50.5 | -1 | -0.3 | -3 | 50.5 | -1 | -1 | -10 | -6.5 | -6.5 | 0 | 12 | 1 | 1 | -6.5 | 10 | 0 | 0
997.3 | 50.5 | 50.5 | -1 | -0.4 | -4 | 50.5 | -1 | -1 | -10 | -7 | -7 | 0 | 12 | 1 | 1 | -7 | 10 | 0 | 0
997.35 | 50.5 | 50.5 | -1 | -0.5 | -5 | 50.5 | -1 | -1 | -10 | -7.5 | -7.5 | 0 | 12 | 1 | 1 | -7.5 | 10 | 0 | 0
997.4 | 50.5 | 50.5 | -1 | -0.6 | -6 | 50.5 | -1 | -1 | -10 | -8 | -8 | 0 | 12 | 1 | 1 | -8 | 10 | 0 | 0
997.45 | 50.5 | 50.5 | -1 | -0.7 | -7 | 50.5 | -1 | -1 | -10 | -8.5 | -8.5 | 0 | 12 | 1 | 1 | -8.5 | 10 | 0 | 0
997.5 | 50.5 | 50.5 | -1 | -0.8 | -8 | 50.5 | -1 | -1 | -10 | -9 | -9 | 0 | 12 | 1 | 1 | -9 | 10 | 0 | 0
997.55 | 50.5 | 50.5 | -1 | -0.9 | -9 | 50.5 | -1 | -1 | -10 | -9.5 | -9.5 | 0 | 12 | 1 | 1 | -9.5 | 10 | 0 | 0
997.6 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
997.65 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
997.7 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
997.75 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
997.8 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
997.85 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
997.9 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
997.95 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
998 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
998.05 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
998.1 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
998.15 | 50.47 | 50.47 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
998.2 | 50.45 | 50.45 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
998.25 | 50.42 | 50.42 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
998.3 | 50.4 | 50.4 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
998.35 | 50.37 | 50.37 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
998.4 | 50.35 | 50.35 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
998.45 | 50.32 | 50.32 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
998.5 | 50.29 | 50.29 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
998.55 | 50.27 | 50.27 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
998.6 | 50.24 | 50.24 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
998.65 | 50.22 | 50.22 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
998.7 | 50.19 | 50.19 | -0.905 | -0.905 | -9.05 | 50.47 | -1 | -1 | -10 | -9.525 | -9.525 | 0 | 12 | 1 | 1 | -9.525 | 10 | 0 | 0
998.75 | 50.17 | 50.17 | -0.715 | -0.715 | -7.15 | 50.45 | -1 | -1 | -10 | -8.575 | -8.575 | 0 | 12 | 1 | 1 | -8.575 | 10 | 0 | 0
998.8 | 50.14 | 50.14 | -0.43 | -0.43 | -4.3 | 50.42 | -1 | -1 | -10 | -7.15 | -7.15 | 0 | 12 | 1 | 1 | -7.15 | 10 | 0 | 0
998.85 | 50.12 | 50.12 | -0.24 | -0.24 | -2.4 | 50.4 | -1 | -1 | -10 | -6.2 | -6.2 | 0 | 12 | 1 | 1 | -6.2 | 10 | 0 | 0
998.9 | 50.09 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 50.37 | -1 | -1 | -10 | -5.2206 | -5.2206 | 0 | 12 | 1 | 1 | -5.2206 | 10 | 0 | 0
998.95 | 50.06 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.35 | -1 | -1 | -10 | -5.1324 | -5.1324 | 0 | 12 | 1 | 1 | -5.1324 | 10 | 0 | 0
999 | 50.04 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.32 | -1 | -1 | -10 | -5.0735 | -5.0735 | 0 | 12 | 1 | 1 | -5.0735 | 10 | 0 | 0
999.05 | 50.01 | 50.01 | 0 | 0 | 0 | 50.29 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
999.1 | 49.99 | 49.99 | 0 | 0 | 0 | 50.27 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
999.15 | 49.96 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.24 | -1 | -1 | -10 | -4.9265 | -4.9265 | 0 | 12 | 1 | 1 | -4.9265 | 10 | 0 | 0
999.2 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.22 | -1 | -1 | -10 | -4.8676 | -4.8676 | 0 | 12 | 1 | 1 | -4.8676 | 10 | 0 | 0
999.25 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.19 | -0.905 | -0.905 | -9.05 | -4.3044 | -4.3044 | 0 | 12 | 1 | 1 | -4.3044 | 10 | 0 | 0
999.3 | 49.88 | 49.88 | 0.24 | 0.24 | 2.4 | 50.17 | -0.715 | -0.805 | -8.05 | -2.825 | -2.825 | 0 | 12 | 1 | 1 | -2.825 | 10 | 0 | 0
999.35 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.14 | -0.43 | -0.705 | -7.05 | -1.375 | -1.375 | 0 | 12 | 1 | 1 | -1.375 | 10 | 0 | 0
999.4 | 49.83 | 49.83 | 0.715 | 0.715 | 7.15 | 50.12 | -0.24 | -0.605 | -6.05 | 0.55 | 0.55 | 0 | 12 | 1 | 1 | 0.55 | 10 | 0 | 0
999.45 | 49.81 | 49.81 | 0.905 | 0.905 | 9.05 | 50.09 | -0.044118 | -0.505 | -5.05 | 2 | 2 | 0 | 12 | 1 | 1 | 2 | 10 | 0 | 0
999.5 | 49.78 | 49.78 | 1 | 1 | 10 | 50.06 | -0.026471 | -0.405 | -4.05 | 2.975 | 2.975 | 0 | 12 | 1 | 1 | 2.975 | 10 | 0 | 0
999.55 | 49.76 | 49.76 | 1 | 1 | 10 | 50.04 | -0.014706 | -0.305 | -3.05 | 3.475 | 3.475 | 0 | 12 | 1 | 1 | 3.475 | 10 | 0 | 0
999.6 | 49.73 | 49.73 | 1 | 1 | 10 | 50.01 | 0 | -0.205 | -2.05 | 3.975 | 3.975 | 0 | 12 | 1 | 1 | 3.975 | 10 | 0 | 0
999.65 | 49.71 | 49.71 | 1 | 1 | 10 | 49.99 | 0 | -0.105 | -1.05 | 4.475 | 4.475 | 0 | 12 | 1 | 1 | 4.475 | 10 | 0 | 0
999.7 | 49.68 | 49.68 | 1 | 1 | 10 | 49.96 | 0.014706 | -0.005 | -0.05 | 4.975 | 4.975 | 0 | 12 | 1 | 1 | 4.975 | 10 | 0 | 0
999.75 | 49.65 | 49.65 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
999.8 | 49.63 | 49.63 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
999.85 | 49.6 | 49.6 | 1 | 1 | 10 | 49.88 | 0.24 | 0.14412 | 1.4412 | 5.7206 | 5.7206 | 0 | 12 | 1 | 1 | 5.7206 | 10 | 0 | 0
999.9 | 49.58 | 49.58 | 1 | 1 | 10 | 49.86 | 0.43 | 0.24412 | 2.4412 | 6.2206 | 6.2206 | 0 | 12 | 1 | 1 | 6.2206 | 10 | 0 | 0
999.95 | 49.55 | 49.55 | 1 | 1 | 10 | 49.83 | 0.715 | 0.34412 | 3.4412 | 6.7206 | 6.7206 | 0 | 12 | 1 | 1 | 6.7206 | 10 | 0 | 0
1000 | 49.53 | 49.53 | 1 | 1 | 10 | 49.81 | 0.905 | 0.44412 | 4.4412 | 7.2206 | 7.2206 | 0 | 12 | 1 | 1 | 7.2206 | 10 | 0 | 0
1000.05 | 49.5 | 49.5 | 1 | 1 | 10 | 49.78 | 1 | 0.54412 | 5.4412 | 7.7206 | 7.7206 | 0 | 12 | 1 | 1 | 7.7206 | 10 | 0 | 0
1000.1 | 49.5 | 49.5 | 1 | 1 | 10 | 49.76 | 1 | 0.64412 | 6.4412 | 8.2206 | 8.2206 | 0 | 12 | 1 | 1 | 8.2206 | 10 | 0 | 0
1000.15 | 49.53 | 49.5 | 1 | 1 | 10 | 49.73 | 1 | 0.74412 | 7.4412 | 8.7206 | 8.7206 | 0 | 12 | 1 | 1 | 8.7206 | 10 | 0 | 0
1000.2 | 49.55 | 49.5 | 1 | 1 | 10 | 49.71 | 1 | 0.84412 | 8.4412 | 9.2206 | 9.2206 | 0 | 12 | 1 | 1 | 9.2206 | 10 | 0 | 0
1000.25 | 49.58 | 49.5 | 1 | 1 | 10 | 49.68 | 1 | 0.94412 | 9.4412 | 9.7206 | 9.7206 | 0 | 12 | 1 | 1 | 9.7206 | 10 | 0 | 0
1000.3 | 49.6 | 49.5 | 1 | 1 | 10 | 49.65 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1000.35 | 49.63 | 49.5 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1000.4 | 49.65 | 49.5 | 1 | 1 | 10 | 49.65 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1000.45 | 49.68 | 49.5 | 1 | 1 | 10 | 49.68 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1000.5 | 49.71 | 49.5 | 1 | 1 | 10 | 49.71 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1000.55 | 49.73 | 49.5 | 1 | 1 | 10 | 49.73 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1000.6 | 49.76 | 49.5 | 1 | 1 | 10 | 49.76 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1000.65 | 49.78 | 49.5 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1000.7 | 49.81 | 49.53 | 1 | 1 | 10 | 49.81 | 0.905 | 0.905 | 9.05 | 9.525 | 9.525 | 0 | 12 | 1 | 1 | 9.525 | 10 | 0 | 0
1000.75 | 49.83 | 49.55 | 1 | 1 | 10 | 49.83 | 0.715 | 0.715 | 7.15 | 8.575 | 8.575 | 0 | 12 | 1 | 1 | 8.575 | 10 | 0 | 0
1000.8 | 49.86 | 49.58 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
1000.85 | 49.88 | 49.6 | 1 | 1 | 10 | 49.88 | 0.24 | 0.24 | 2.4 | 6.2 | 6.2 | 0 | 12 | 1 | 1 | 6.2 | 10 | 0 | 0
1000.9 | 49.91 | 49.63 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1000.95 | 49.94 | 49.65 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
1001 | 49.96 | 49.68 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
1001.05 | 49.99 | 49.71 | 1 | 1 | 10 | 49.99 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1001.1 | 50.01 | 49.73 | 1 | 1 | 10 | 50.01 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1001.15 | 50.04 | 49.76 | 1 | 1 | 10 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 4.9265 | 4.9265 | 0 | 12 | 1 | 1 | 4.9265 | 10 | 0 | 0
1001.2 | 50.06 | 49.78 | 1 | 1 | 10 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 4.8676 | 4.8676 | 0 | 12 | 1 | 1 | 4.8676 | 10 | 0 | 0
1001.25 | 50.09 | 49.81 | 0.905 | 0.905 | 9.05 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 4.3044 | 4.3044 | 0 | 12 | 1 | 1 | 4.3044 | 10 | 0 | 0
1001.3 | 50.12 | 49.83 | 0.715 | 0.805 | 8.05 | 50.12 | -0.24 | -0.24 | -2.4 | 2.825 | 2.825 | 0 | 12 | 1 | 1 | 2.825 | 10 | 0 | 0
1001.35 | 50.14 | 49.86 | 0.43 | 0.705 | 7.05 | 50.14 | -0.43 | -0.43 | -4.3 | 1.375 | 1.375 | 0 | 12 | 1 | 1 | 1.375 | 10 | 0 | 0
1001.4 | 50.17 | 49.88 | 0.24 | 0.605 | 6.05 | 50.17 | -0.715 | -0.715 | -7.15 | -0.55 | -0.55 | 0 | 12 | 1 | 1 | -0.55 | 10 | 0 | 0
1001.45 | 50.19 | 49.91 | 0.044118 | 0.505 | 5.05 | 50.19 | -0.905 | -0.905 | -9.05 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
1001.5 | 50.22 | 49.94 | 0.026471 | 0.405 | 4.05 | 50.22 | -1 | -1 | -10 | -2.975 | -2.975 | 0 | 12 | 1 | 1 | -2.975 | 10 | 0 | 0
1001.55 | 50.24 | 49.96 | 0.014706 | 0.305 | 3.05 | 50.24 | -1 | -1 | -10 | -3.475 | -3.475 | 0 | 12 | 1 | 1 | -3.475 | 10 | 0 | 0
1001.6 | 50.27 | 49.99 | 0 | 0.205 | 2.05 | 50.27 | -1 | -1 | -10 | -3.975 | -3.975 | 0 | 12 | 1 | 1 | -3.975 | 10 | 0 | 0
1001.65 | 50.29 | 50.01 | 0 | 0.105 | 1.05 | 50.29 | -1 | -1 | -10 | -4.475 | -4.475 | 0 | 12 | 1 | 1 | -4.475 | 10 | 0 | 0
1001.7 | 50.32 | 50.04 | -0.014706 | 0.005 | 0.05 | 50.32 | -1 | -1 | -10 | -4.975 | -4.975 | 0 | 12 | 1 | 1 | -4.975 | 10 | 0 | 0
1001.75 | 50.35 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.35 | -1 | -1 | -10 | -5.1324 | -5.1324 | 0 | 12 | 1 | 1 | -5.1324 | 10 | 0 | 0
1001.8 | 50.37 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 50.37 | -1 | -1 | -10 | -5.2206 | -5.2206 | 0 | 12 | 1 | 1 | -5.2206 | 10 | 0 | 0
1001.85 | 50.4 | 50.12 | -0.24 | -0.14412 | -1.4412 | 50.4 | -1 | -1 | -10 | -5.7206 | -5.7206 | 0 | 12 | 1 | 1 | -5.7206 | 10 | 0 | 0
1001.9 | 50.42 | 50.14 | -0.43 | -0.24412 | -2.4412 | 50.42 | -1 | -1 | -10 | -6.2206 | -6.2206 | 0 | 12 | 1 | 1 | -6.2206 | 10 | 0 | 0
1001.95 | 50.45 | 50.17 | -0.715 | -0.34412 | -3.4412 | 50.45 | -1 | -1 | -10 | -6.7206 | -6.7206 | 0 | 12 | 1 | 1 | -6.7206 | 10 | 0 | 0
1002 | 50.47 | 50.19 | -0.905 | -0.44412 | -4.4412 | 50.47 | -1 | -1 | -10 | -7.2206 | -7.2206 | 0 | 12 | 1 | 1 | -7.2206 | 10 | 0 | 0
1002.05 | 50.5 | 50.22 | -1 | -0.54412 | -5.4412 | 50.5 | -1 | -1 | -10 | -7.7206 | -7.7206 | 0 | 12 | 1 | 1 | -7.7206 | 10 | 0 | 0
1002.1 | 50.5 | 50.24 | -1 | -0.64412 | -6.4412 | 50.5 | -1 | -1 | -10 | -8.2206 | -8.2206 | 0 | 12 | 1 | 1 | -8.2206 | 10 | 0 | 0
1002.15 | 50.47 | 50.27 | -1 | -0.74412 | -7.4412 | 50.5 | -1 | -1 | -10 | -8.7206 | -8.7206 | 0 | 12 | 1 | 1 | -8.7206 | 10 | 0 | 0
1002.2 | 50.45 | 50.29 | -1 | -0.84412 | -8.4412 | 50.5 | -1 | -1 | -10 | -9.2206 | -9.2206 | 0 | 12 | 1 | 1 | -9.2206 | 10 | 0 | 0
1002.25 | 50.42 | 50.32 | -1 | -0.94412 | -9.4412 | 50.5 | -1 | -1 | -10 | -9.7206 | -9.7206 | 0 | 12 | 1 | 1 | -9.7206 | 10 | 0 | 0
1002.3 | 50.39 | 50.35 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1002.35 | 50.37 | 50.37 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1002.4 | 50.34 | 50.34 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1002.45 | 50.32 | 50.32 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1002.5 | 50.29 | 50.29 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1002.55 | 50.26 | 50.26 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1002.6 | 50.24 | 50.24 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1002.65 | 50.21 | 50.21 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1002.7 | 50.18 | 50.18 | -0.81 | -0.81 | -8.1 | 50.47 | -1 | -1 | -10 | -9.05 | -9.05 | 0 | 12 | 1 | 1 | -9.05 | 10 | 0 | 0
1002.75 | 50.16 | 50.16 | -0.62 | -0.62 | -6.2 | 50.45 | -1 | -1 | -10 | -8.1 | -8.1 | 0 | 12 | 1 | 1 | -8.1 | 10 | 0 | 0
1002.8 | 50.13 | 50.13 | -0.335 | -0.335 | -3.35 | 50.42 | -1 | -1 | -10 | -6.675 | -6.675 | 0 | 12 | 1 | 1 | -6.675 | 10 | 0 | 0
1002.85 | 50.11 | 50.11 | -0.145 | -0.145 | -1.45 | 50.39 | -1 | -1 | -10 | -5.725 | -5.725 | 0 | 12 | 1 | 1 | -5.725 | 10 | 0 | 0
1002.9 | 50.08 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 50.37 | -1 | -1 | -10 | -5.1912 | -5.1912 | 0 | 12 | 1 | 1 | -5.1912 | 10 | 0 | 0
1002.95 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.34 | -1 | -1 | -10 | -5.1029 | -5.1029 | 0 | 12 | 1 | 1 | -5.1029 | 10 | 0 | 0
1003 | 50.03 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 50.32 | -1 | -1 | -10 | -5.0441 | -5.0441 | 0 | 12 | 1 | 1 | -5.0441 | 10 | 0 | 0
1003.05 | 50 | 50 | 0 | 0 | 0 | 50.29 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1003.1 | 50 | 50 | 0 | 0 | 0 | 50.26 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1003.15 | 50 | 50 | 0 | 0 | 0 | 50.24 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1003.2 | 50 | 50 | 0 | 0 | 0 | 50.21 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1003.25 | 50 | 50 | 0 | 0 | 0 | 50.18 | -0.81 | -0.9 | -9 | -4.5 | -4.5 | 0 | 12 | 1 | 1 | -4.5 | 10 | 0 | 0
1003.3 | 50 | 50 | 0 | 0 | 0 | 50.16 | -0.62 | -0.8 | -8 | -4 | -4 | 0 | 12 | 1 | 1 | -4 | 10 | 0 | 0
1003.35 | 50 | 50 | 0 | 0 | 0 | 50.13 | -0.335 | -0.7 | -7 | -3.5 | -3.5 | 0 | 12 | 1 | 1 | -3.5 | 10 | 0 | 0
1003.4 | 50.01 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.6 | -6 | -3 | -3 | 0 | 12 | 1 | 1 | -3 | 10 | 0 | 0
1003.45 | 50.01 | 50 | 0 | 0 | 0 | 50.08 | -0.038235 | -0.5 | -5 | -2.5 | -2.5 | 0 | 12 | 1 | 1 | -2.5 | 10 | 0 | 0
1003.5 | 49.99 | 49.99 | 0 | 0 | 0 | 50.05 | -0.020588 | -0.4 | -4 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
1003.55 | 49.99 | 49.99 | 0 | 0 | 0 | 50.03 | -0.0088235 | -0.3 | -3 | -1.5 | -1.5 | 0 | 12 | 1 | 1 | -1.5 | 10 | 0 | 0
1003.6 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | -0.2 | -2 | -0.83824 | -0.83824 | 0 | 12 | 1 | 1 | -0.83824 | 10 | 0 | 0
1003.65 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | -0.1 | -1 | -0.33824 | -0.33824 | 0 | 12 | 1 | 1 | -0.33824 | 10 | 0 | 0
1003.7 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
1003.75 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
1003.8 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
1003.85 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
1003.9 | 49.89 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
1003.95 | 49.89 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
1004 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50.01 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1004.05 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1004.1 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1004.15 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 2.7868 | 2.7868 | 0 | 12 | 1 | 1 | 2.7868 | 10 | 0 | 0
1004.2 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 2.7868 | 2.7868 | 0 | 12 | 1 | 1 | 2.7868 | 10 | 0 | 0
1004.25 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 2.8456 | 2.8456 | 0 | 12 | 1 | 1 | 2.8456 | 10 | 0 | 0
1004.3 | 49.94 | 49.85 | 0.525 | 0.525 | 5.25 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 2.7574 | 2.7574 | 0 | 12 | 1 | 1 | 2.7574 | 10 | 0 | 0
1004.35 | 49.94 | 49.85 | 0.525 | 0.525 | 5.25 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 2.7574 | 2.7574 | 0 | 12 | 1 | 1 | 2.7574 | 10 | 0 | 0
1004.4 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1004.45 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1004.5 | 49.93 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1004.55 | 49.93 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1004.6 | 49.96 | 49.85 | 0.525 | 0.525 | 5.25 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 2.6985 | 2.6985 | 0 | 12 | 1 | 1 | 2.6985 | 10 | 0 | 0
1004.65 | 49.96 | 49.85 | 0.525 | 0.525 | 5.25 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 2.6985 | 2.6985 | 0 | 12 | 1 | 1 | 2.6985 | 10 | 0 | 0
1004.7 | 49.99 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1004.75 | 49.99 | 49.91 | 0.044118 | 0.425 | 4.25 | 49.99 | 0 | 0 | 0 | 2.125 | 2.125 | 0 | 12 | 1 | 1 | 2.125 | 10 | 0 | 0
1004.8 | 49.99 | 49.91 | 0.044118 | 0.325 | 3.25 | 49.99 | 0 | 0 | 0 | 1.625 | 1.625 | 0 | 12 | 1 | 1 | 1.625 | 10 | 0 | 0
1004.85 | 49.99 | 49.93 | 0.032353 | 0.225 | 2.25 | 49.99 | 0 | 0 | 0 | 1.125 | 1.125 | 0 | 12 | 1 | 1 | 1.125 | 10 | 0 | 0
1004.9 | 49.96 | 49.93 | 0.032353 | 0.125 | 1.25 | 49.99 | 0 | 0 | 0 | 0.625 | 0.625 | 0 | 12 | 1 | 1 | 0.625 | 10 | 0 | 0
1004.95 | 49.96 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 49.99 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1005 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1005.05 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1005.1 | 50.05 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.058824 | 0.058824 | 0 | 12 | 1 | 1 | 0.058824 | 10 | 0 | 0
1005.15 | 50.05 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
1005.2 | 49.97 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
1005.25 | 49.97 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
1005.3 | 49.92 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1005.35 | 49.92 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1005.4 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1005.45 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1005.5 | 49.94 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1005.55 | 49.94 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1005.6 | 50.01 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1005.65 | 50.01 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1005.7 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1005.75 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
1005.8 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
1005.85 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
1005.9 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
1005.95 | 49.95 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
1006 | 49.97 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
1006.05 | 49.97 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
1006.1 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
1006.15 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
1006.2 | 49.87 | 49.87 | 0.335 | 0.335 | 3.35 | 50.01 | 0 | 0 | 0 | 1.675 | 1.675 | 0 | 12 | 1 | 1 | 1.675 | 10 | 0 | 0
1006.25 | 49.87 | 49.87 | 0.335 | 0.335 | 3.35 | 49.99 | 0 | 0 | 0 | 1.675 | 1.675 | 0 | 12 | 1 | 1 | 1.675 | 10 | 0 | 0
1006.3 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1006.35 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 2.6691 | 2.6691 | 0 | 12 | 1 | 1 | 2.6691 | 10 | 0 | 0
1006.4 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1006.45 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1006.5 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1006.55 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1006.6 | 49.84 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1006.65 | 49.84 | 49.79 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
1006.7 | 49.89 | 49.79 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
1006.75 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.12647 | 1.2647 | 5.6324 | 5.6324 | 0 | 12 | 1 | 1 | 5.6324 | 10 | 0 | 0
1006.8 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.145 | 1.45 | 5.725 | 5.725 | 0 | 12 | 1 | 1 | 5.725 | 10 | 0 | 0
1006.85 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.145 | 1.45 | 5.725 | 5.725 | 0 | 12 | 1 | 1 | 5.725 | 10 | 0 | 0
1006.9 | 49.96 | 49.79 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
1006.95 | 49.96 | 49.79 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
1007 | 50.02 | 49.79 | 1 | 1 | 10 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 4.9853 | 4.9853 | 0 | 12 | 1 | 1 | 4.9853 | 10 | 0 | 0
1007.05 | 50.02 | 49.79 | 1 | 1 | 10 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 4.9853 | 4.9853 | 0 | 12 | 1 | 1 | 4.9853 | 10 | 0 | 0
1007.1 | 50.03 | 49.79 | 1 | 1 | 10 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.9559 | 4.9559 | 0 | 12 | 1 | 1 | 4.9559 | 10 | 0 | 0
1007.15 | 50.03 | 49.84 | 0.62 | 0.9 | 9 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.4559 | 4.4559 | 0 | 12 | 1 | 1 | 4.4559 | 10 | 0 | 0
1007.2 | 50.02 | 49.84 | 0.62 | 0.8 | 8 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 3.9559 | 3.9559 | 0 | 12 | 1 | 1 | 3.9559 | 10 | 0 | 0
1007.25 | 50.02 | 49.89 | 0.145 | 0.7 | 7 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 3.4559 | 3.4559 | 0 | 12 | 1 | 1 | 3.4559 | 10 | 0 | 0
1007.3 | 50.08 | 49.89 | 0.145 | 0.6 | 6 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 2.8088 | 2.8088 | 0 | 12 | 1 | 1 | 2.8088 | 10 | 0 | 0
1007.35 | 50.08 | 49.89 | 0.145 | 0.5 | 5 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 2.3088 | 2.3088 | 0 | 12 | 1 | 1 | 2.3088 | 10 | 0 | 0
1007.4 | 50.01 | 49.89 | 0.145 | 0.4 | 4 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 1.8088 | 1.8088 | 0 | 12 | 1 | 1 | 1.8088 | 10 | 0 | 0
1007.45 | 50.01 | 49.96 | 0.014706 | 0.3 | 3 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 1.3088 | 1.3088 | 0 | 12 | 1 | 1 | 1.3088 | 10 | 0 | 0
1007.5 | 49.94 | 49.94 | 0.026471 | 0.2 | 2 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.80882 | 0.80882 | 0 | 12 | 1 | 1 | 0.80882 | 10 | 0 | 0
1007.55 | 49.94 | 49.94 | 0.026471 | 0.1 | 1 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.30882 | 0.30882 | 0 | 12 | 1 | 1 | 0.30882 | 10 | 0 | 0
1007.6 | 50 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
1007.65 | 50 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
1007.7 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
1007.75 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
1007.8 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1007.85 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1007.9 | 49.92 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1007.95 | 49.92 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
1008 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50.01 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1008.05 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1008.1 | 49.92 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1008.15 | 49.92 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1008.2 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1008.25 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1008.3 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1008.35 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1008.4 | 49.87 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1008.45 | 49.87 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1008.5 | 49.8 | 49.8 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1008.55 | 49.8 | 49.8 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1008.6 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1008.65 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1008.7 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1008.75 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1008.8 | 49.72 | 49.72 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1008.85 | 49.72 | 49.72 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1008.9 | 49.67 | 49.67 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1008.95 | 49.67 | 49.67 | 1 | 1 | 10 | 49.87 | 0.335 | 0.14412 | 1.4412 | 5.7206 | 5.7206 | 0 | 12 | 1 | 1 | 5.7206 | 10 | 0 | 0
1009 | 49.65 | 49.65 | 1 | 1 | 10 | 49.87 | 0.335 | 0.24412 | 2.4412 | 6.2206 | 6.2206 | 0 | 12 | 1 | 1 | 6.2206 | 10 | 0 | 0
1009.05 | 49.65 | 49.65 | 1 | 1 | 10 | 49.8 | 1 | 0.34412 | 3.4412 | 6.7206 | 6.7206 | 0 | 12 | 1 | 1 | 6.7206 | 10 | 0 | 0
1009.1 | 49.59 | 49.59 | 1 | 1 | 10 | 49.8 | 1 | 0.44412 | 4.4412 | 7.2206 | 7.2206 | 0 | 12 | 1 | 1 | 7.2206 | 10 | 0 | 0
1009.15 | 49.59 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.54412 | 5.4412 | 7.7206 | 7.7206 | 0 | 12 | 1 | 1 | 7.7206 | 10 | 0 | 0
1009.2 | 49.66 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.64412 | 6.4412 | 8.2206 | 8.2206 | 0 | 12 | 1 | 1 | 8.2206 | 10 | 0 | 0
1009.25 | 49.66 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.74412 | 7.4412 | 8.7206 | 8.7206 | 0 | 12 | 1 | 1 | 8.7206 | 10 | 0 | 0
1009.3 | 49.63 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.84412 | 8.4412 | 9.2206 | 9.2206 | 0 | 12 | 1 | 1 | 9.2206 | 10 | 0 | 0
1009.35 | 49.63 | 49.59 | 1 | 1 | 10 | 49.72 | 1 | 0.94412 | 9.4412 | 9.7206 | 9.7206 | 0 | 12 | 1 | 1 | 9.7206 | 10 | 0 | 0
1009.4 | 49.61 | 49.59 | 1 | 1 | 10 | 49.72 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1009.45 | 49.61 | 49.59 | 1 | 1 | 10 | 49.67 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1009.5 | 49.54 | 49.54 | 1 | 1 | 10 | 49.67 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1009.55 | 49.54 | 49.54 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1009.6 | 49.46 | 49.46 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1009.65 | 49.46 | 49.46 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1009.7 | 49.45 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1009.75 | 49.45 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1009.8 | 49.51 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1009.85 | 49.51 | 49.45 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1009.9 | 49.5 | 49.45 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1009.95 | 49.5 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1010 | 49.54 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1010.05 | 49.54 | 49.45 | 1 | 1 | 10 | 49.54 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1010.1 | 49.59 | 49.45 | 1 | 1 | 10 | 49.59 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1010.15 | 49.59 | 49.45 | 1 | 1 | 10 | 49.59 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1010.2 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1010.25 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1010.3 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1010.35 | 49.61 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1010.4 | 49.53 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1010.45 | 49.53 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1010.5 | 49.54 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1010.55 | 49.54 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1010.6 | 49.61 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1010.65 | 49.61 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1010.7 | 49.66 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1010.75 | 49.66 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1010.8 | 49.64 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1010.85 | 49.64 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1010.9 | 49.69 | 49.53 | 1 | 1 | 10 | 49.69 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1010.95 | 49.69 | 49.53 | 1 | 1 | 10 | 49.69 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1011 | 49.74 | 49.53 | 1 | 1 | 10 | 49.74 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1011.05 | 49.74 | 49.54 | 1 | 1 | 10 | 49.74 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1011.1 | 49.78 | 49.54 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1011.15 | 49.78 | 49.61 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1011.2 | 49.82 | 49.61 | 1 | 1 | 10 | 49.82 | 0.81 | 0.81 | 8.1 | 9.05 | 9.05 | 0 | 12 | 1 | 1 | 9.05 | 10 | 0 | 0
1011.25 | 49.82 | 49.64 | 1 | 1 | 10 | 49.82 | 0.81 | 0.81 | 8.1 | 9.05 | 9.05 | 0 | 12 | 1 | 1 | 9.05 | 10 | 0 | 0
1011.3 | 49.86 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
1011.35 | 49.86 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
1011.4 | 49.84 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
1011.45 | 49.84 | 49.69 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
1011.5 | 49.91 | 49.69 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1011.55 | 49.91 | 49.74 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1011.6 | 49.97 | 49.74 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1011.65 | 49.97 | 49.78 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1011.7 | 50.03 | 49.78 | 1 | 1 | 10 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.9559 | 4.9559 | 0 | 12 | 1 | 1 | 4.9559 | 10 | 0 | 0
1011.75 | 50.03 | 49.82 | 0.81 | 0.9 | 9 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.4559 | 4.4559 | 0 | 12 | 1 | 1 | 4.4559 | 10 | 0 | 0
1011.8 | 50.05 | 49.82 | 0.81 | 0.81 | 8.1 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 3.9471 | 3.9471 | 0 | 12 | 1 | 1 | 3.9471 | 10 | 0 | 0
1011.85 | 50.05 | 49.84 | 0.62 | 0.71 | 7.1 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 3.4471 | 3.4471 | 0 | 12 | 1 | 1 | 3.4471 | 10 | 0 | 0
1011.9 | 50.01 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
1011.95 | 50.01 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
1012 | 49.95 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
1012.05 | 49.95 | 49.91 | 0.044118 | 0.52 | 5.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.4971 | 2.4971 | 0 | 12 | 1 | 1 | 2.4971 | 10 | 0 | 0
1012.1 | 49.99 | 49.91 | 0.044118 | 0.42 | 4.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 1.9971 | 1.9971 | 0 | 12 | 1 | 1 | 1.9971 | 10 | 0 | 0
1012.15 | 49.99 | 49.95 | 0.020588 | 0.32 | 3.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 1.4971 | 1.4971 | 0 | 12 | 1 | 1 | 1.4971 | 10 | 0 | 0
1012.2 | 49.92 | 49.92 | 0.038235 | 0.22 | 2.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.99706 | 0.99706 | 0 | 12 | 1 | 1 | 0.99706 | 10 | 0 | 0
1012.25 | 49.92 | 49.92 | 0.038235 | 0.12 | 1.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.49706 | 0.49706 | 0 | 12 | 1 | 1 | 0.49706 | 10 | 0 | 0
1012.3 | 49.97 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1012.35 | 49.97 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1012.4 | 50.02 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1012.45 | 50.02 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.17647 | 0.17647 | 0 | 12 | 1 | 1 | 0.17647 | 10 | 0 | 0
1012.5 | 50.07 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1012.55 | 50.07 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1012.6 | 50.06 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1012.65 | 50.06 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1012.7 | 50.13 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
1012.75 | 50.13 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
1012.8 | 50.09 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
1012.85 | 50.09 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6309 | -1.6309 | 0 | 12 | 1 | 1 | -1.6309 | 10 | 0 | 0
1012.9 | 50.07 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6309 | -1.6309 | 0 | 12 | 1 | 1 | -1.6309 | 10 | 0 | 0
1012.95 | 50.07 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6897 | -1.6897 | 0 | 12 | 1 | 1 | -1.6897 | 10 | 0 | 0
1013 | 50.07 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6897 | -1.6897 | 0 | 12 | 1 | 1 | -1.6897 | 10 | 0 | 0
1013.05 | 50.07 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.13 | -0.335 | -0.335 | -3.35 | -1.8074 | -1.8074 | 0 | 12 | 1 | 1 | -1.8074 | 10 | 0 | 0
1013.1 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.13 | -0.335 | -0.335 | -3.35 | -1.7779 | -1.7779 | 0 | 12 | 1 | 1 | -1.7779 | 10 | 0 | 0
1013.15 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.13 | -0.335 | -0.335 | -3.35 | -1.7779 | -1.7779 | 0 | 12 | 1 | 1 | -1.7779 | 10 | 0 | 0
1013.2 | 50.01 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
1013.25 | 50.01 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
1013.3 | 50.07 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
1013.35 | 50.07 | 50.01 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.235 | -2.35 | -1.175 | -1.175 | 0 | 12 | 1 | 1 | -1.175 | 10 | 0 | 0
1013.4 | 50.05 | 50.01 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.135 | -1.35 | -0.675 | -0.675 | 0 | 12 | 1 | 1 | -0.675 | 10 | 0 | 0
1013.45 | 50.05 | 50.01 | 0 | 0 | 0 | 50.07 | -0.032353 | -0.035 | -0.35 | -0.175 | -0.175 | 0 | 12 | 1 | 1 | -0.175 | 10 | 0 | 0
1013.5 | 50.1 | 50.01 | 0 | 0 | 0 | 50.1 | -0.05 | -0.05 | -0.5 | -0.25 | -0.25 | 0 | 12 | 1 | 1 | -0.25 | 10 | 0 | 0
1013.55 | 50.1 | 50.01 | 0 | 0 | 0 | 50.1 | -0.05 | -0.05 | -0.5 | -0.25 | -0.25 | 0 | 12 | 1 | 1 | -0.25 | 10 | 0 | 0
1013.6 | 50.11 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1013.65 | 50.11 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1013.7 | 50.06 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1013.75 | 50.06 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1013.8 | 50.04 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1013.85 | 50.04 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1013.9 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1013.95 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1014 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1014.05 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1014.1 | 50.11 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1014.15 | 50.11 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1014.2 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1014.25 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1014.3 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1014.35 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1014.4 | 50.02 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.11 | -0.145 | -0.145 | -1.45 | -0.73971 | -0.73971 | 0 | 12 | 1 | 1 | -0.73971 | 10 | 0 | 0
1014.45 | 50.02 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.11 | -0.145 | -0.145 | -1.45 | -0.73971 | -0.73971 | 0 | 12 | 1 | 1 | -0.73971 | 10 | 0 | 0
1014.5 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1014.55 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1014.6 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1014.65 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1014.7 | 50.01 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1014.75 | 50.01 | 50 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.045 | -0.45 | -0.225 | -0.225 | 0 | 12 | 1 | 1 | -0.225 | 10 | 0 | 0
1014.8 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
1014.85 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
1014.9 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
1014.95 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1015 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.14706 | 0.14706 | 0 | 12 | 1 | 1 | 0.14706 | 10 | 0 | 0
1015.05 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1015.1 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1015.15 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1015.2 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1015.25 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1015.3 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1015.35 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1015.4 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1015.45 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1015.5 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1015.55 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1015.6 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1015.65 | 50 | 50 | 0 | 0 | 0 | 50.01 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1015.7 | 49.5 | 49.5 | 1 | 1 | 10 | 50.01 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1015.75 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1015.8 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1015.85 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1015.9 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1015.95 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1016 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1016.05 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1016.1 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1016.15 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1016.2 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1016.25 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.1 | 1 | 5.5 | 5.5 | 0 | 12 | 1 | 1 | 5.5 | 10 | 0 | 0
1016.3 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.2 | 2 | 6 | 6 | 0 | 12 | 1 | 1 | 6 | 10 | 0 | 0
1016.35 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.3 | 3 | 6.5 | 6.5 | 0 | 12 | 1 | 1 | 6.5 | 10 | 0 | 0
1016.4 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.4 | 4 | 7 | 7 | 0 | 12 | 1 | 1 | 7 | 10 | 0 | 0
1016.45 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.5 | 5 | 7.5 | 7.5 | 0 | 12 | 1 | 1 | 7.5 | 10 | 0 | 0
1016.5 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.6 | 6 | 8 | 8 | 0 | 12 | 1 | 1 | 8 | 10 | 0 | 0
1016.55 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.7 | 7 | 8.5 | 8.5 | 0 | 12 | 1 | 1 | 8.5 | 10 | 0 | 0
1016.6 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.8 | 8 | 9 | 9 | 0 | 12 | 1 | 1 | 9 | 10 | 0 | 0
1016.65 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.9 | 9 | 9.5 | 9.5 | 0 | 12 | 1 | 1 | 9.5 | 10 | 0 | 0
1016.7 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1016.75 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1016.8 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1016.85 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1016.9 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1016.95 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1017 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1017.05 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1017.1 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1017.15 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1017.2 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1017.25 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1017.3 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1017.35 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1017.4 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1017.45 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1017.5 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1017.55 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1017.6 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1017.65 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1017.7 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1017.75 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1017.8 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1017.85 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1017.9 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1017.95 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1018 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1018.05 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1018.1 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1018.15 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1018.2 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1018.25 | 50.5 | 50.5 | -1 | 0.9 | 9 | 50.5 | -1 | -1 | -10 | -0.5 | -0.5 | 0 | 12 | 1 | 1 | -0.5 | 10 | 0 | 0
1018.3 | 50.5 | 50.5 | -1 | 0.8 | 8 | 50.5 | -1 | -1 | -10 | -1 | -1 | 0 | 12 | 1 | 1 | -1 | 10 | 0 | 0
1018.35 | 50.5 | 50.5 | -1 | 0.7 | 7 | 50.5 | -1 | -1 | -10 | -1.5 | -1.5 | 0 | 12 | 1 | 1 | -1.5 | 10 | 0 | 0
1018.4 | 50.5 | 50.5 | -1 | 0.6 | 6 | 50.5 | -1 | -1 | -10 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
1018.45 | 50.5 | 50.5 | -1 | 0.5 | 5 | 50.5 | -1 | -1 | -10 | -2.5 | -2.5 | 0 | 12 | 1 | 1 | -2.5 | 10 | 0 | 0
1018.5 | 50.5 | 50.5 | -1 | 0.4 | 4 | 50.5 | -1 | -1 | -10 | -3 | -3 | 0 | 12 | 1 | 1 | -3 | 10 | 0 | 0
1018.55 | 50.5 | 50.5 | -1 | 0.3 | 3 | 50.5 | -1 | -1 | -10 | -3.5 | -3.5 | 0 | 12 | 1 | 1 | -3.5 | 10 | 0 | 0
1018.6 | 50.5 | 50.5 | -1 | 0.2 | 2 | 50.5 | -1 | -1 | -10 | -4 | -4 | 0 | 12 | 1 | 1 | -4 | 10 | 0 | 0
1018.65 | 50.5 | 50.5 | -1 | 0.1 | 1 | 50.5 | -1 | -1 | -10 | -4.5 | -4.5 | 0 | 12 | 1 | 1 | -4.5 | 10 | 0 | 0
1018.7 | 50.5 | 50.5 | -1 | 0 | 0 | 50.5 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1018.75 | 50.5 | 50.5 | -1 | -0.1 | -1 | 50.5 | -1 | -1 | -10 | -5.5 | -5.5 | 0 | 12 | 1 | 1 | -5.5 | 10 | 0 | 0
1018.8 | 50.5 | 50.5 | -1 | -0.2 | -2 | 50.5 | -1 | -1 | -10 | -6 | -6 | 0 | 12 | 1 | 1 | -6 | 10 | 0 | 0
1018.85 | 50.5 | 50.5 | -1 | -0.3 | -3 | 50.5 | -1 | -1 | -10 | -6.5 | -6.5 | 0 | 12 | 1 | 1 | -6.5 | 10 | 0 | 0
1018.9 | 50.5 | 50.5 | -1 | -0.4 | -4 | 50.5 | -1 | -1 | -10 | -7 | -7 | 0 | 12 | 1 | 1 | -7 | 10 | 0 | 0
1018.95 | 50.5 | 50.5 | -1 | -0.5 | -5 | 50.5 | -1 | -1 | -10 | -7.5 | -7.5 | 0 | 12 | 1 | 1 | -7.5 | 10 | 0 | 0
1019 | 50.5 | 50.5 | -1 | -0.6 | -6 | 50.5 | -1 | -1 | -10 | -8 | -8 | 0 | 12 | 1 | 1 | -8 | 10 | 0 | 0
1019.05 | 50.5 | 50.5 | -1 | -0.7 | -7 | 50.5 | -1 | -1 | -10 | -8.5 | -8.5 | 0 | 12 | 1 | 1 | -8.5 | 10 | 0 | 0
1019.1 | 50.5 | 50.5 | -1 | -0.8 | -8 | 50.5 | -1 | -1 | -10 | -9 | -9 | 0 | 12 | 1 | 1 | -9 | 10 | 0 | 0
1019.15 | 50.5 | 50.5 | -1 | -0.9 | -9 | 50.5 | -1 | -1 | -10 | -9.5 | -9.5 | 0 | 12 | 1 | 1 | -9.5 | 10 | 0 | 0
1019.2 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1019.25 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1019.3 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1019.35 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1019.4 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1019.45 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1019.5 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1019.55 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1019.6 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1019.65 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1019.7 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1019.75 | 50.47 | 50.47 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1019.8 | 50.45 | 50.45 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1019.85 | 50.42 | 50.42 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1019.9 | 50.4 | 50.4 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1019.95 | 50.37 | 50.37 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1020 | 50.35 | 50.35 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1020.05 | 50.32 | 50.32 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1020.1 | 50.29 | 50.29 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1020.15 | 50.27 | 50.27 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1020.2 | 50.24 | 50.24 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1020.25 | 50.22 | 50.22 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1020.3 | 50.19 | 50.19 | -0.905 | -0.905 | -9.05 | 50.47 | -1 | -1 | -10 | -9.525 | -9.525 | 0 | 12 | 1 | 1 | -9.525 | 10 | 0 | 0
1020.35 | 50.17 | 50.17 | -0.715 | -0.715 | -7.15 | 50.45 | -1 | -1 | -10 | -8.575 | -8.575 | 0 | 12 | 1 | 1 | -8.575 | 10 | 0 | 0
1020.4 | 50.14 | 50.14 | -0.43 | -0.43 | -4.3 | 50.42 | -1 | -1 | -10 | -7.15 | -7.15 | 0 | 12 | 1 | 1 | -7.15 | 10 | 0 | 0
1020.45 | 50.12 | 50.12 | -0.24 | -0.24 | -2.4 | 50.4 | -1 | -1 | -10 | -6.2 | -6.2 | 0 | 12 | 1 | 1 | -6.2 | 10 | 0 | 0
1020.5 | 50.09 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 50.37 | -1 | -1 | -10 | -5.2206 | -5.2206 | 0 | 12 | 1 | 1 | -5.2206 | 10 | 0 | 0
1020.55 | 50.06 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.35 | -1 | -1 | -10 | -5.1324 | -5.1324 | 0 | 12 | 1 | 1 | -5.1324 | 10 | 0 | 0
1020.6 | 50.04 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.32 | -1 | -1 | -10 | -5.0735 | -5.0735 | 0 | 12 | 1 | 1 | -5.0735 | 10 | 0 | 0
1020.65 | 50.01 | 50.01 | 0 | 0 | 0 | 50.29 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1020.7 | 49.99 | 49.99 | 0 | 0 | 0 | 50.27 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1020.75 | 49.96 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.24 | -1 | -1 | -10 | -4.9265 | -4.9265 | 0 | 12 | 1 | 1 | -4.9265 | 10 | 0 | 0
1020.8 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.22 | -1 | -1 | -10 | -4.8676 | -4.8676 | 0 | 12 | 1 | 1 | -4.8676 | 10 | 0 | 0
1020.85 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.19 | -0.905 | -0.905 | -9.05 | -4.3044 | -4.3044 | 0 | 12 | 1 | 1 | -4.3044 | 10 | 0 | 0
1020.9 | 49.88 | 49.88 | 0.24 | 0.24 | 2.4 | 50.17 | -0.715 | -0.805 | -8.05 | -2.825 | -2.825 | 0 | 12 | 1 | 1 | -2.825 | 10 | 0 | 0
1020.95 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.14 | -0.43 | -0.705 | -7.05 | -1.375 | -1.375 | 0 | 12 | 1 | 1 | -1.375 | 10 | 0 | 0
1021 | 49.83 | 49.83 | 0.715 | 0.715 | 7.15 | 50.12 | -0.24 | -0.605 | -6.05 | 0.55 | 0.55 | 0 | 12 | 1 | 1 | 0.55 | 10 | 0 | 0
1021.05 | 49.81 | 49.81 | 0.905 | 0.905 | 9.05 | 50.09 | -0.044118 | -0.505 | -5.05 | 2 | 2 | 0 | 12 | 1 | 1 | 2 | 10 | 0 | 0
1021.1 | 49.78 | 49.78 | 1 | 1 | 10 | 50.06 | -0.026471 | -0.405 | -4.05 | 2.975 | 2.975 | 0 | 12 | 1 | 1 | 2.975 | 10 | 0 | 0
1021.15 | 49.76 | 49.76 | 1 | 1 | 10 | 50.04 | -0.014706 | -0.305 | -3.05 | 3.475 | 3.475 | 0 | 12 | 1 | 1 | 3.475 | 10 | 0 | 0
1021.2 | 49.73 | 49.73 | 1 | 1 | 10 | 50.01 | 0 | -0.205 | -2.05 | 3.975 | 3.975 | 0 | 12 | 1 | 1 | 3.975 | 10 | 0 | 0
1021.25 | 49.71 | 49.71 | 1 | 1 | 10 | 49.99 | 0 | -0.105 | -1.05 | 4.475 | 4.475 | 0 | 12 | 1 | 1 | 4.475 | 10 | 0 | 0
1021.3 | 49.68 | 49.68 | 1 | 1 | 10 | 49.96 | 0.014706 | -0.005 | -0.05 | 4.975 | 4.975 | 0 | 12 | 1 | 1 | 4.975 | 10 | 0 | 0
1021.35 | 49.65 | 49.65 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
1021.4 | 49.63 | 49.63 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1021.45 | 49.6 | 49.6 | 1 | 1 | 10 | 49.88 | 0.24 | 0.14412 | 1.4412 | 5.7206 | 5.7206 | 0 | 12 | 1 | 1 | 5.7206 | 10 | 0 | 0
1021.5 | 49.58 | 49.58 | 1 | 1 | 10 | 49.86 | 0.43 | 0.24412 | 2.4412 | 6.2206 | 6.2206 | 0 | 12 | 1 | 1 | 6.2206 | 10 | 0 | 0
1021.55 | 49.55 | 49.55 | 1 | 1 | 10 | 49.83 | 0.715 | 0.34412 | 3.4412 | 6.7206 | 6.7206 | 0 | 12 | 1 | 1 | 6.7206 | 10 | 0 | 0
1021.6 | 49.53 | 49.53 | 1 | 1 | 10 | 49.81 | 0.905 | 0.44412 | 4.4412 | 7.2206 | 7.2206 | 0 | 12 | 1 | 1 | 7.2206 | 10 | 0 | 0
1021.65 | 49.5 | 49.5 | 1 | 1 | 10 | 49.78 | 1 | 0.54412 | 5.4412 | 7.7206 | 7.7206 | 0 | 12 | 1 | 1 | 7.7206 | 10 | 0 | 0
1021.7 | 49.5 | 49.5 | 1 | 1 | 10 | 49.76 | 1 | 0.64412 | 6.4412 | 8.2206 | 8.2206 | 0 | 12 | 1 | 1 | 8.2206 | 10 | 0 | 0
1021.75 | 49.53 | 49.5 | 1 | 1 | 10 | 49.73 | 1 | 0.74412 | 7.4412 | 8.7206 | 8.7206 | 0 | 12 | 1 | 1 | 8.7206 | 10 | 0 | 0
1021.8 | 49.55 | 49.5 | 1 | 1 | 10 | 49.71 | 1 | 0.84412 | 8.4412 | 9.2206 | 9.2206 | 0 | 12 | 1 | 1 | 9.2206 | 10 | 0 | 0
1021.85 | 49.58 | 49.5 | 1 | 1 | 10 | 49.68 | 1 | 0.94412 | 9.4412 | 9.7206 | 9.7206 | 0 | 12 | 1 | 1 | 9.7206 | 10 | 0 | 0
1021.9 | 49.6 | 49.5 | 1 | 1 | 10 | 49.65 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1021.95 | 49.63 | 49.5 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1022 | 49.65 | 49.5 | 1 | 1 | 10 | 49.65 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1022.05 | 49.68 | 49.5 | 1 | 1 | 10 | 49.68 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1022.1 | 49.71 | 49.5 | 1 | 1 | 10 | 49.71 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1022.15 | 49.73 | 49.5 | 1 | 1 | 10 | 49.73 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1022.2 | 49.76 | 49.5 | 1 | 1 | 10 | 49.76 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1022.25 | 49.78 | 49.5 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1022.3 | 49.81 | 49.53 | 1 | 1 | 10 | 49.81 | 0.905 | 0.905 | 9.05 | 9.525 | 9.525 | 0 | 12 | 1 | 1 | 9.525 | 10 | 0 | 0
1022.35 | 49.83 | 49.55 | 1 | 1 | 10 | 49.83 | 0.715 | 0.715 | 7.15 | 8.575 | 8.575 | 0 | 12 | 1 | 1 | 8.575 | 10 | 0 | 0
1022.4 | 49.86 | 49.58 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
1022.45 | 49.88 | 49.6 | 1 | 1 | 10 | 49.88 | 0.24 | 0.24 | 2.4 | 6.2 | 6.2 | 0 | 12 | 1 | 1 | 6.2 | 10 | 0 | 0
1022.5 | 49.91 | 49.63 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1022.55 | 49.94 | 49.65 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
1022.6 | 49.96 | 49.68 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
1022.65 | 49.99 | 49.71 | 1 | 1 | 10 | 49.99 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1022.7 | 50.01 | 49.73 | 1 | 1 | 10 | 50.01 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1022.75 | 50.04 | 49.76 | 1 | 1 | 10 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 4.9265 | 4.9265 | 0 | 12 | 1 | 1 | 4.9265 | 10 | 0 | 0
1022.8 | 50.06 | 49.78 | 1 | 1 | 10 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 4.8676 | 4.8676 | 0 | 12 | 1 | 1 | 4.8676 | 10 | 0 | 0
1022.85 | 50.09 | 49.81 | 0.905 | 0.905 | 9.05 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 4.3044 | 4.3044 | 0 | 12 | 1 | 1 | 4.3044 | 10 | 0 | 0
1022.9 | 50.12 | 49.83 | 0.715 | 0.805 | 8.05 | 50.12 | -0.24 | -0.24 | -2.4 | 2.825 | 2.825 | 0 | 12 | 1 | 1 | 2.825 | 10 | 0 | 0
1022.95 | 50.14 | 49.86 | 0.43 | 0.705 | 7.05 | 50.14 | -0.43 | -0.43 | -4.3 | 1.375 | 1.375 | 0 | 12 | 1 | 1 | 1.375 | 10 | 0 | 0
1023 | 50.17 | 49.88 | 0.24 | 0.605 | 6.05 | 50.17 | -0.715 | -0.715 | -7.15 | -0.55 | -0.55 | 0 | 12 | 1 | 1 | -0.55 | 10 | 0 | 0
1023.05 | 50.19 | 49.91 | 0.044118 | 0.505 | 5.05 | 50.19 | -0.905 | -0.905 | -9.05 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
1023.1 | 50.22 | 49.94 | 0.026471 | 0.405 | 4.05 | 50.22 | -1 | -1 | -10 | -2.975 | -2.975 | 0 | 12 | 1 | 1 | -2.975 | 10 | 0 | 0
1023.15 | 50.24 | 49.96 | 0.014706 | 0.305 | 3.05 | 50.24 | -1 | -1 | -10 | -3.475 | -3.475 | 0 | 12 | 1 | 1 | -3.475 | 10 | 0 | 0
1023.2 | 50.27 | 49.99 | 0 | 0.205 | 2.05 | 50.27 | -1 | -1 | -10 | -3.975 | -3.975 | 0 | 12 | 1 | 1 | -3.975 | 10 | 0 | 0
1023.25 | 50.29 | 50.01 | 0 | 0.105 | 1.05 | 50.29 | -1 | -1 | -10 | -4.475 | -4.475 | 0 | 12 | 1 | 1 | -4.475 | 10 | 0 | 0
1023.3 | 50.32 | 50.04 | -0.014706 | 0.005 | 0.05 | 50.32 | -1 | -1 | -10 | -4.975 | -4.975 | 0 | 12 | 1 | 1 | -4.975 | 10 | 0 | 0
1023.35 | 50.35 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.35 | -1 | -1 | -10 | -5.1324 | -5.1324 | 0 | 12 | 1 | 1 | -5.1324 | 10 | 0 | 0
1023.4 | 50.37 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 50.37 | -1 | -1 | -10 | -5.2206 | -5.2206 | 0 | 12 | 1 | 1 | -5.2206 | 10 | 0 | 0
1023.45 | 50.4 | 50.12 | -0.24 | -0.14412 | -1.4412 | 50.4 | -1 | -1 | -10 | -5.7206 | -5.7206 | 0 | 12 | 1 | 1 | -5.7206 | 10 | 0 | 0
1023.5 | 50.42 | 50.14 | -0.43 | -0.24412 | -2.4412 | 50.42 | -1 | -1 | -10 | -6.2206 | -6.2206 | 0 | 12 | 1 | 1 | -6.2206 | 10 | 0 | 0
1023.55 | 50.45 | 50.17 | -0.715 | -0.34412 | -3.4412 | 50.45 | -1 | -1 | -10 | -6.7206 | -6.7206 | 0 | 12 | 1 | 1 | -6.7206 | 10 | 0 | 0
1023.6 | 50.47 | 50.19 | -0.905 | -0.44412 | -4.4412 | 50.47 | -1 | -1 | -10 | -7.2206 | -7.2206 | 0 | 12 | 1 | 1 | -7.2206 | 10 | 0 | 0
1023.65 | 50.5 | 50.22 | -1 | -0.54412 | -5.4412 | 50.5 | -1 | -1 | -10 | -7.7206 | -7.7206 | 0 | 12 | 1 | 1 | -7.7206 | 10 | 0 | 0
1023.7 | 50.5 | 50.24 | -1 | -0.64412 | -6.4412 | 50.5 | -1 | -1 | -10 | -8.2206 | -8.2206 | 0 | 12 | 1 | 1 | -8.2206 | 10 | 0 | 0
1023.75 | 50.47 | 50.27 | -1 | -0.74412 | -7.4412 | 50.5 | -1 | -1 | -10 | -8.7206 | -8.7206 | 0 | 12 | 1 | 1 | -8.7206 | 10 | 0 | 0
1023.8 | 50.45 | 50.29 | -1 | -0.84412 | -8.4412 | 50.5 | -1 | -1 | -10 | -9.2206 | -9.2206 | 0 | 12 | 1 | 1 | -9.2206 | 10 | 0 | 0
1023.85 | 50.42 | 50.32 | -1 | -0.94412 | -9.4412 | 50.5 | -1 | -1 | -10 | -9.7206 | -9.7206 | 0 | 12 | 1 | 1 | -9.7206 | 10 | 0 | 0
1023.9 | 50.39 | 50.35 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1023.95 | 50.37 | 50.37 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1024 | 50.34 | 50.34 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1024.05 | 50.32 | 50.32 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1024.1 | 50.29 | 50.29 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1024.15 | 50.26 | 50.26 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1024.2 | 50.24 | 50.24 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1024.25 | 50.21 | 50.21 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1024.3 | 50.18 | 50.18 | -0.81 | -0.81 | -8.1 | 50.47 | -1 | -1 | -10 | -9.05 | -9.05 | 0 | 12 | 1 | 1 | -9.05 | 10 | 0 | 0
1024.35 | 50.16 | 50.16 | -0.62 | -0.62 | -6.2 | 50.45 | -1 | -1 | -10 | -8.1 | -8.1 | 0 | 12 | 1 | 1 | -8.1 | 10 | 0 | 0
1024.4 | 50.13 | 50.13 | -0.335 | -0.335 | -3.35 | 50.42 | -1 | -1 | -10 | -6.675 | -6.675 | 0 | 12 | 1 | 1 | -6.675 | 10 | 0 | 0
1024.45 | 50.11 | 50.11 | -0.145 | -0.145 | -1.45 | 50.39 | -1 | -1 | -10 | -5.725 | -5.725 | 0 | 12 | 1 | 1 | -5.725 | 10 | 0 | 0
1024.5 | 50.08 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 50.37 | -1 | -1 | -10 | -5.1912 | -5.1912 | 0 | 12 | 1 | 1 | -5.1912 | 10 | 0 | 0
1024.55 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.34 | -1 | -1 | -10 | -5.1029 | -5.1029 | 0 | 12 | 1 | 1 | -5.1029 | 10 | 0 | 0
1024.6 | 50.03 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 50.32 | -1 | -1 | -10 | -5.0441 | -5.0441 | 0 | 12 | 1 | 1 | -5.0441 | 10 | 0 | 0
1024.65 | 50 | 50 | 0 | 0 | 0 | 50.29 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1024.7 | 50 | 50 | 0 | 0 | 0 | 50.26 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1024.75 | 50 | 50 | 0 | 0 | 0 | 50.24 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1024.8 | 50 | 50 | 0 | 0 | 0 | 50.21 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1024.85 | 50 | 50 | 0 | 0 | 0 | 50.18 | -0.81 | -0.9 | -9 | -4.5 | -4.5 | 0 | 12 | 1 | 1 | -4.5 | 10 | 0 | 0
1024.9 | 50 | 50 | 0 | 0 | 0 | 50.16 | -0.62 | -0.8 | -8 | -4 | -4 | 0 | 12 | 1 | 1 | -4 | 10 | 0 | 0
1024.95 | 50 | 50 | 0 | 0 | 0 | 50.13 | -0.335 | -0.7 | -7 | -3.5 | -3.5 | 0 | 12 | 1 | 1 | -3.5 | 10 | 0 | 0
1025 | 50.01 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.6 | -6 | -3 | -3 | 0 | 12 | 1 | 1 | -3 | 10 | 0 | 0
1025.05 | 50.01 | 50 | 0 | 0 | 0 | 50.08 | -0.038235 | -0.5 | -5 | -2.5 | -2.5 | 0 | 12 | 1 | 1 | -2.5 | 10 | 0 | 0
1025.1 | 49.99 | 49.99 | 0 | 0 | 0 | 50.05 | -0.020588 | -0.4 | -4 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
1025.15 | 49.99 | 49.99 | 0 | 0 | 0 | 50.03 | -0.0088235 | -0.3 | -3 | -1.5 | -1.5 | 0 | 12 | 1 | 1 | -1.5 | 10 | 0 | 0
1025.2 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | -0.2 | -2 | -0.83824 | -0.83824 | 0 | 12 | 1 | 1 | -0.83824 | 10 | 0 | 0
1025.25 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | -0.1 | -1 | -0.33824 | -0.33824 | 0 | 12 | 1 | 1 | -0.33824 | 10 | 0 | 0
1025.3 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
1025.35 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
1025.4 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
1025.45 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
1025.5 | 49.89 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
1025.55 | 49.89 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
1025.6 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50.01 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1025.65 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1025.7 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1025.75 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 2.7868 | 2.7868 | 0 | 12 | 1 | 1 | 2.7868 | 10 | 0 | 0
1025.8 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 2.7868 | 2.7868 | 0 | 12 | 1 | 1 | 2.7868 | 10 | 0 | 0
1025.85 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 2.8456 | 2.8456 | 0 | 12 | 1 | 1 | 2.8456 | 10 | 0 | 0
1025.9 | 49.94 | 49.85 | 0.525 | 0.525 | 5.25 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 2.7574 | 2.7574 | 0 | 12 | 1 | 1 | 2.7574 | 10 | 0 | 0
1025.95 | 49.94 | 49.85 | 0.525 | 0.525 | 5.25 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 2.7574 | 2.7574 | 0 | 12 | 1 | 1 | 2.7574 | 10 | 0 | 0
1026 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1026.05 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1026.1 | 49.93 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1026.15 | 49.93 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1026.2 | 49.96 | 49.85 | 0.525 | 0.525 | 5.25 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 2.6985 | 2.6985 | 0 | 12 | 1 | 1 | 2.6985 | 10 | 0 | 0
1026.25 | 49.96 | 49.85 | 0.525 | 0.525 | 5.25 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 2.6985 | 2.6985 | 0 | 12 | 1 | 1 | 2.6985 | 10 | 0 | 0
1026.3 | 49.99 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1026.35 | 49.99 | 49.91 | 0.044118 | 0.425 | 4.25 | 49.99 | 0 | 0 | 0 | 2.125 | 2.125 | 0 | 12 | 1 | 1 | 2.125 | 10 | 0 | 0
1026.4 | 49.99 | 49.91 | 0.044118 | 0.325 | 3.25 | 49.99 | 0 | 0 | 0 | 1.625 | 1.625 | 0 | 12 | 1 | 1 | 1.625 | 10 | 0 | 0
1026.45 | 49.99 | 49.93 | 0.032353 | 0.225 | 2.25 | 49.99 | 0 | 0 | 0 | 1.125 | 1.125 | 0 | 12 | 1 | 1 | 1.125 | 10 | 0 | 0
1026.5 | 49.96 | 49.93 | 0.032353 | 0.125 | 1.25 | 49.99 | 0 | 0 | 0 | 0.625 | 0.625 | 0 | 12 | 1 | 1 | 0.625 | 10 | 0 | 0
1026.55 | 49.96 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 49.99 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1026.6 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1026.65 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1026.7 | 50.05 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.058824 | 0.058824 | 0 | 12 | 1 | 1 | 0.058824 | 10 | 0 | 0
1026.75 | 50.05 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
1026.8 | 49.97 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
1026.85 | 49.97 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
1026.9 | 49.92 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1026.95 | 49.92 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1027 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1027.05 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1027.1 | 49.94 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1027.15 | 49.94 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1027.2 | 50.01 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1027.25 | 50.01 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1027.3 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1027.35 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
1027.4 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
1027.45 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
1027.5 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
1027.55 | 49.95 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
1027.6 | 49.97 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
1027.65 | 49.97 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
1027.7 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
1027.75 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
1027.8 | 49.87 | 49.87 | 0.335 | 0.335 | 3.35 | 50.01 | 0 | 0 | 0 | 1.675 | 1.675 | 0 | 12 | 1 | 1 | 1.675 | 10 | 0 | 0
1027.85 | 49.87 | 49.87 | 0.335 | 0.335 | 3.35 | 49.99 | 0 | 0 | 0 | 1.675 | 1.675 | 0 | 12 | 1 | 1 | 1.675 | 10 | 0 | 0
1027.9 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1027.95 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 2.6691 | 2.6691 | 0 | 12 | 1 | 1 | 2.6691 | 10 | 0 | 0
1028 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1028.05 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1028.1 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1028.15 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1028.2 | 49.84 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1028.25 | 49.84 | 49.79 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
1028.3 | 49.89 | 49.79 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
1028.35 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.12647 | 1.2647 | 5.6324 | 5.6324 | 0 | 12 | 1 | 1 | 5.6324 | 10 | 0 | 0
1028.4 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.145 | 1.45 | 5.725 | 5.725 | 0 | 12 | 1 | 1 | 5.725 | 10 | 0 | 0
1028.45 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.145 | 1.45 | 5.725 | 5.725 | 0 | 12 | 1 | 1 | 5.725 | 10 | 0 | 0
1028.5 | 49.96 | 49.79 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
1028.55 | 49.96 | 49.79 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
1028.6 | 50.02 | 49.79 | 1 | 1 | 10 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 4.9853 | 4.9853 | 0 | 12 | 1 | 1 | 4.9853 | 10 | 0 | 0
1028.65 | 50.02 | 49.79 | 1 | 1 | 10 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 4.9853 | 4.9853 | 0 | 12 | 1 | 1 | 4.9853 | 10 | 0 | 0
1028.7 | 50.03 | 49.79 | 1 | 1 | 10 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.9559 | 4.9559 | 0 | 12 | 1 | 1 | 4.9559 | 10 | 0 | 0
1028.75 | 50.03 | 49.84 | 0.62 | 0.9 | 9 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.4559 | 4.4559 | 0 | 12 | 1 | 1 | 4.4559 | 10 | 0 | 0
1028.8 | 50.02 | 49.84 | 0.62 | 0.8 | 8 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 3.9559 | 3.9559 | 0 | 12 | 1 | 1 | 3.9559 | 10 | 0 | 0
1028.85 | 50.02 | 49.89 | 0.145 | 0.7 | 7 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 3.4559 | 3.4559 | 0 | 12 | 1 | 1 | 3.4559 | 10 | 0 | 0
1028.9 | 50.08 | 49.89 | 0.145 | 0.6 | 6 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 2.8088 | 2.8088 | 0 | 12 | 1 | 1 | 2.8088 | 10 | 0 | 0
1028.95 | 50.08 | 49.89 | 0.145 | 0.5 | 5 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 2.3088 | 2.3088 | 0 | 12 | 1 | 1 | 2.3088 | 10 | 0 | 0
1029 | 50.01 | 49.89 | 0.145 | 0.4 | 4 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 1.8088 | 1.8088 | 0 | 12 | 1 | 1 | 1.8088 | 10 | 0 | 0
1029.05 | 50.01 | 49.96 | 0.014706 | 0.3 | 3 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 1.3088 | 1.3088 | 0 | 12 | 1 | 1 | 1.3088 | 10 | 0 | 0
1029.1 | 49.94 | 49.94 | 0.026471 | 0.2 | 2 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.80882 | 0.80882 | 0 | 12 | 1 | 1 | 0.80882 | 10 | 0 | 0
1029.15 | 49.94 | 49.94 | 0.026471 | 0.1 | 1 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.30882 | 0.30882 | 0 | 12 | 1 | 1 | 0.30882 | 10 | 0 | 0
1029.2 | 50 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
1029.25 | 50 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
1029.3 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
1029.35 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
1029.4 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1029.45 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1029.5 | 49.92 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1029.55 | 49.92 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
1029.6 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50.01 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1029.65 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1029.7 | 49.92 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1029.75 | 49.92 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1029.8 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1029.85 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1029.9 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1029.95 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1030 | 49.87 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1030.05 | 49.87 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1030.1 | 49.8 | 49.8 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1030.15 | 49.8 | 49.8 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1030.2 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1030.25 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1030.3 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1030.35 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1030.4 | 49.72 | 49.72 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1030.45 | 49.72 | 49.72 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1030.5 | 49.67 | 49.67 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1030.55 | 49.67 | 49.67 | 1 | 1 | 10 | 49.87 | 0.335 | 0.14412 | 1.4412 | 5.7206 | 5.7206 | 0 | 12 | 1 | 1 | 5.7206 | 10 | 0 | 0
1030.6 | 49.65 | 49.65 | 1 | 1 | 10 | 49.87 | 0.335 | 0.24412 | 2.4412 | 6.2206 | 6.2206 | 0 | 12 | 1 | 1 | 6.2206 | 10 | 0 | 0
1030.65 | 49.65 | 49.65 | 1 | 1 | 10 | 49.8 | 1 | 0.34412 | 3.4412 | 6.7206 | 6.7206 | 0 | 12 | 1 | 1 | 6.7206 | 10 | 0 | 0
1030.7 | 49.59 | 49.59 | 1 | 1 | 10 | 49.8 | 1 | 0.44412 | 4.4412 | 7.2206 | 7.2206 | 0 | 12 | 1 | 1 | 7.2206 | 10 | 0 | 0
1030.75 | 49.59 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.54412 | 5.4412 | 7.7206 | 7.7206 | 0 | 12 | 1 | 1 | 7.7206 | 10 | 0 | 0
1030.8 | 49.66 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.64412 | 6.4412 | 8.2206 | 8.2206 | 0 | 12 | 1 | 1 | 8.2206 | 10 | 0 | 0
1030.85 | 49.66 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.74412 | 7.4412 | 8.7206 | 8.7206 | 0 | 12 | 1 | 1 | 8.7206 | 10 | 0 | 0
1030.9 | 49.63 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.84412 | 8.4412 | 9.2206 | 9.2206 | 0 | 12 | 1 | 1 | 9.2206 | 10 | 0 | 0
1030.95 | 49.63 | 49.59 | 1 | 1 | 10 | 49.72 | 1 | 0.94412 | 9.4412 | 9.7206 | 9.7206 | 0 | 12 | 1 | 1 | 9.7206 | 10 | 0 | 0
1031 | 49.61 | 49.59 | 1 | 1 | 10 | 49.72 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1031.05 | 49.61 | 49.59 | 1 | 1 | 10 | 49.67 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1031.1 | 49.54 | 49.54 | 1 | 1 | 10 | 49.67 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1031.15 | 49.54 | 49.54 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1031.2 | 49.46 | 49.46 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1031.25 | 49.46 | 49.46 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1031.3 | 49.45 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1031.35 | 49.45 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1031.4 | 49.51 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1031.45 | 49.51 | 49.45 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1031.5 | 49.5 | 49.45 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1031.55 | 49.5 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1031.6 | 49.54 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1031.65 | 49.54 | 49.45 | 1 | 1 | 10 | 49.54 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1031.7 | 49.59 | 49.45 | 1 | 1 | 10 | 49.59 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1031.75 | 49.59 | 49.45 | 1 | 1 | 10 | 49.59 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1031.8 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1031.85 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1031.9 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1031.95 | 49.61 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1032 | 49.53 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1032.05 | 49.53 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1032.1 | 49.54 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1032.15 | 49.54 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1032.2 | 49.61 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1032.25 | 49.61 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1032.3 | 49.66 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1032.35 | 49.66 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1032.4 | 49.64 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1032.45 | 49.64 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1032.5 | 49.69 | 49.53 | 1 | 1 | 10 | 49.69 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1032.55 | 49.69 | 49.53 | 1 | 1 | 10 | 49.69 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1032.6 | 49.74 | 49.53 | 1 | 1 | 10 | 49.74 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1032.65 | 49.74 | 49.54 | 1 | 1 | 10 | 49.74 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1032.7 | 49.78 | 49.54 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1032.75 | 49.78 | 49.61 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1032.8 | 49.82 | 49.61 | 1 | 1 | 10 | 49.82 | 0.81 | 0.81 | 8.1 | 9.05 | 9.05 | 0 | 12 | 1 | 1 | 9.05 | 10 | 0 | 0
1032.85 | 49.82 | 49.64 | 1 | 1 | 10 | 49.82 | 0.81 | 0.81 | 8.1 | 9.05 | 9.05 | 0 | 12 | 1 | 1 | 9.05 | 10 | 0 | 0
1032.9 | 49.86 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
1032.95 | 49.86 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
1033 | 49.84 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
1033.05 | 49.84 | 49.69 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
1033.1 | 49.91 | 49.69 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1033.15 | 49.91 | 49.74 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1033.2 | 49.97 | 49.74 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1033.25 | 49.97 | 49.78 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1033.3 | 50.03 | 49.78 | 1 | 1 | 10 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.9559 | 4.9559 | 0 | 12 | 1 | 1 | 4.9559 | 10 | 0 | 0
1033.35 | 50.03 | 49.82 | 0.81 | 0.9 | 9 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.4559 | 4.4559 | 0 | 12 | 1 | 1 | 4.4559 | 10 | 0 | 0
1033.4 | 50.05 | 49.82 | 0.81 | 0.81 | 8.1 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 3.9471 | 3.9471 | 0 | 12 | 1 | 1 | 3.9471 | 10 | 0 | 0
1033.45 | 50.05 | 49.84 | 0.62 | 0.71 | 7.1 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 3.4471 | 3.4471 | 0 | 12 | 1 | 1 | 3.4471 | 10 | 0 | 0
1033.5 | 50.01 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
1033.55 | 50.01 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
1033.6 | 49.95 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
1033.65 | 49.95 | 49.91 | 0.044118 | 0.52 | 5.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.4971 | 2.4971 | 0 | 12 | 1 | 1 | 2.4971 | 10 | 0 | 0
1033.7 | 49.99 | 49.91 | 0.044118 | 0.42 | 4.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 1.9971 | 1.9971 | 0 | 12 | 1 | 1 | 1.9971 | 10 | 0 | 0
1033.75 | 49.99 | 49.95 | 0.020588 | 0.32 | 3.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 1.4971 | 1.4971 | 0 | 12 | 1 | 1 | 1.4971 | 10 | 0 | 0
1033.8 | 49.92 | 49.92 | 0.038235 | 0.22 | 2.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.99706 | 0.99706 | 0 | 12 | 1 | 1 | 0.99706 | 10 | 0 | 0
1033.85 | 49.92 | 49.92 | 0.038235 | 0.12 | 1.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.49706 | 0.49706 | 0 | 12 | 1 | 1 | 0.49706 | 10 | 0 | 0
1033.9 | 49.97 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1033.95 | 49.97 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1034 | 50.02 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1034.05 | 50.02 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.17647 | 0.17647 | 0 | 12 | 1 | 1 | 0.17647 | 10 | 0 | 0
1034.1 | 50.07 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1034.15 | 50.07 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1034.2 | 50.06 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1034.25 | 50.06 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1034.3 | 50.13 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
1034.35 | 50.13 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
1034.4 | 50.09 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
1034.45 | 50.09 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6309 | -1.6309 | 0 | 12 | 1 | 1 | -1.6309 | 10 | 0 | 0
1034.5 | 50.07 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6309 | -1.6309 | 0 | 12 | 1 | 1 | -1.6309 | 10 | 0 | 0
1034.55 | 50.07 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6897 | -1.6897 | 0 | 12 | 1 | 1 | -1.6897 | 10 | 0 | 0
1034.6 | 50.07 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6897 | -1.6897 | 0 | 12 | 1 | 1 | -1.6897 | 10 | 0 | 0
1034.65 | 50.07 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.13 | -0.335 | -0.335 | -3.35 | -1.8074 | -1.8074 | 0 | 12 | 1 | 1 | -1.8074 | 10 | 0 | 0
1034.7 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.13 | -0.335 | -0.335 | -3.35 | -1.7779 | -1.7779 | 0 | 12 | 1 | 1 | -1.7779 | 10 | 0 | 0
1034.75 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.13 | -0.335 | -0.335 | -3.35 | -1.7779 | -1.7779 | 0 | 12 | 1 | 1 | -1.7779 | 10 | 0 | 0
1034.8 | 50.01 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
1034.85 | 50.01 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
1034.9 | 50.07 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
1034.95 | 50.07 | 50.01 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.235 | -2.35 | -1.175 | -1.175 | 0 | 12 | 1 | 1 | -1.175 | 10 | 0 | 0
1035 | 50.05 | 50.01 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.135 | -1.35 | -0.675 | -0.675 | 0 | 12 | 1 | 1 | -0.675 | 10 | 0 | 0
1035.05 | 50.05 | 50.01 | 0 | 0 | 0 | 50.07 | -0.032353 | -0.035 | -0.35 | -0.175 | -0.175 | 0 | 12 | 1 | 1 | -0.175 | 10 | 0 | 0
1035.1 | 50.1 | 50.01 | 0 | 0 | 0 | 50.1 | -0.05 | -0.05 | -0.5 | -0.25 | -0.25 | 0 | 12 | 1 | 1 | -0.25 | 10 | 0 | 0
1035.15 | 50.1 | 50.01 | 0 | 0 | 0 | 50.1 | -0.05 | -0.05 | -0.5 | -0.25 | -0.25 | 0 | 12 | 1 | 1 | -0.25 | 10 | 0 | 0
1035.2 | 50.11 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1035.25 | 50.11 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1035.3 | 50.06 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1035.35 | 50.06 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1035.4 | 50.04 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1035.45 | 50.04 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1035.5 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1035.55 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1035.6 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1035.65 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1035.7 | 50.11 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1035.75 | 50.11 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1035.8 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1035.85 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1035.9 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1035.95 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1036 | 50.02 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.11 | -0.145 | -0.145 | -1.45 | -0.73971 | -0.73971 | 0 | 12 | 1 | 1 | -0.73971 | 10 | 0 | 0
1036.05 | 50.02 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.11 | -0.145 | -0.145 | -1.45 | -0.73971 | -0.73971 | 0 | 12 | 1 | 1 | -0.73971 | 10 | 0 | 0
1036.1 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1036.15 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1036.2 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1036.25 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1036.3 | 50.01 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1036.35 | 50.01 | 50 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.045 | -0.45 | -0.225 | -0.225 | 0 | 12 | 1 | 1 | -0.225 | 10 | 0 | 0
1036.4 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
1036.45 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
1036.5 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
1036.55 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1036.6 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.14706 | 0.14706 | 0 | 12 | 1 | 1 | 0.14706 | 10 | 0 | 0
1036.65 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1036.7 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1036.75 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1036.8 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1036.85 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1036.9 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1036.95 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1037 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1037.05 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1037.1 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1037.15 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1037.2 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1037.25 | 50 | 50 | 0 | 0 | 0 | 50.01 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1037.3 | 49.5 | 49.5 | 1 | 1 | 10 | 50.01 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1037.35 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1037.4 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1037.45 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1037.5 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1037.55 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1037.6 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1037.65 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1037.7 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1037.75 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1037.8 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1037.85 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.1 | 1 | 5.5 | 5.5 | 0 | 12 | 1 | 1 | 5.5 | 10 | 0 | 0
1037.9 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.2 | 2 | 6 | 6 | 0 | 12 | 1 | 1 | 6 | 10 | 0 | 0
1037.95 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.3 | 3 | 6.5 | 6.5 | 0 | 12 | 1 | 1 | 6.5 | 10 | 0 | 0
1038 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.4 | 4 | 7 | 7 | 0 | 12 | 1 | 1 | 7 | 10 | 0 | 0
1038.05 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.5 | 5 | 7.5 | 7.5 | 0 | 12 | 1 | 1 | 7.5 | 10 | 0 | 0
1038.1 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.6 | 6 | 8 | 8 | 0 | 12 | 1 | 1 | 8 | 10 | 0 | 0
1038.15 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.7 | 7 | 8.5 | 8.5 | 0 | 12 | 1 | 1 | 8.5 | 10 | 0 | 0
1038.2 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.8 | 8 | 9 | 9 | 0 | 12 | 1 | 1 | 9 | 10 | 0 | 0
1038.25 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.9 | 9 | 9.5 | 9.5 | 0 | 12 | 1 | 1 | 9.5 | 10 | 0 | 0
1038.3 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1038.35 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1038.4 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1038.45 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1038.5 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1038.55 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1038.6 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1038.65 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1038.7 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1038.75 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1038.8 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1038.85 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1038.9 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1038.95 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1039 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1039.05 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1039.1 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1039.15 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1039.2 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1039.25 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1039.3 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1039.35 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1039.4 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1039.45 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1039.5 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1039.55 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1039.6 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1039.65 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1039.7 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1039.75 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1039.8 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1039.85 | 50.5 | 50.5 | -1 | 0.9 | 9 | 50.5 | -1 | -1 | -10 | -0.5 | -0.5 | 0 | 12 | 1 | 1 | -0.5 | 10 | 0 | 0
1039.9 | 50.5 | 50.5 | -1 | 0.8 | 8 | 50.5 | -1 | -1 | -10 | -1 | -1 | 0 | 12 | 1 | 1 | -1 | 10 | 0 | 0
1039.95 | 50.5 | 50.5 | -1 | 0.7 | 7 | 50.5 | -1 | -1 | -10 | -1.5 | -1.5 | 0 | 12 | 1 | 1 | -1.5 | 10 | 0 | 0
1040 | 50.5 | 50.5 | -1 | 0.6 | 6 | 50.5 | -1 | -1 | -10 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
1040.05 | 50.5 | 50.5 | -1 | 0.5 | 5 | 50.5 | -1 | -1 | -10 | -2.5 | -2.5 | 0 | 12 | 1 | 1 | -2.5 | 10 | 0 | 0
1040.1 | 50.5 | 50.5 | -1 | 0.4 | 4 | 50.5 | -1 | -1 | -10 | -3 | -3 | 0 | 12 | 1 | 1 | -3 | 10 | 0 | 0
1040.15 | 50.5 | 50.5 | -1 | 0.3 | 3 | 50.5 | -1 | -1 | -10 | -3.5 | -3.5 | 0 | 12 | 1 | 1 | -3.5 | 10 | 0 | 0
1040.2 | 50.5 | 50.5 | -1 | 0.2 | 2 | 50.5 | -1 | -1 | -10 | -4 | -4 | 0 | 12 | 1 | 1 | -4 | 10 | 0 | 0
1040.25 | 50.5 | 50.5 | -1 | 0.1 | 1 | 50.5 | -1 | -1 | -10 | -4.5 | -4.5 | 0 | 12 | 1 | 1 | -4.5 | 10 | 0 | 0
1040.3 | 50.5 | 50.5 | -1 | 0 | 0 | 50.5 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1040.35 | 50.5 | 50.5 | -1 | -0.1 | -1 | 50.5 | -1 | -1 | -10 | -5.5 | -5.5 | 0 | 12 | 1 | 1 | -5.5 | 10 | 0 | 0
1040.4 | 50.5 | 50.5 | -1 | -0.2 | -2 | 50.5 | -1 | -1 | -10 | -6 | -6 | 0 | 12 | 1 | 1 | -6 | 10 | 0 | 0
1040.45 | 50.5 | 50.5 | -1 | -0.3 | -3 | 50.5 | -1 | -1 | -10 | -6.5 | -6.5 | 0 | 12 | 1 | 1 | -6.5 | 10 | 0 | 0
1040.5 | 50.5 | 50.5 | -1 | -0.4 | -4 | 50.5 | -1 | -1 | -10 | -7 | -7 | 0 | 12 | 1 | 1 | -7 | 10 | 0 | 0
1040.55 | 50.5 | 50.5 | -1 | -0.5 | -5 | 50.5 | -1 | -1 | -10 | -7.5 | -7.5 | 0 | 12 | 1 | 1 | -7.5 | 10 | 0 | 0
1040.6 | 50.5 | 50.5 | -1 | -0.6 | -6 | 50.5 | -1 | -1 | -10 | -8 | -8 | 0 | 12 | 1 | 1 | -8 | 10 | 0 | 0
1040.65 | 50.5 | 50.5 | -1 | -0.7 | -7 | 50.5 | -1 | -1 | -10 | -8.5 | -8.5 | 0 | 12 | 1 | 1 | -8.5 | 10 | 0 | 0
1040.7 | 50.5 | 50.5 | -1 | -0.8 | -8 | 50.5 | -1 | -1 | -10 | -9 | -9 | 0 | 12 | 1 | 1 | -9 | 10 | 0 | 0
1040.75 | 50.5 | 50.5 | -1 | -0.9 | -9 | 50.5 | -1 | -1 | -10 | -9.5 | -9.5 | 0 | 12 | 1 | 1 | -9.5 | 10 | 0 | 0
1040.8 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1040.85 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1040.9 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1040.95 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1041 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1041.05 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1041.1 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1041.15 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1041.2 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1041.25 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1041.3 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1041.35 | 50.47 | 50.47 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1041.4 | 50.45 | 50.45 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1041.45 | 50.42 | 50.42 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1041.5 | 50.4 | 50.4 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1041.55 | 50.37 | 50.37 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1041.6 | 50.35 | 50.35 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1041.65 | 50.32 | 50.32 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1041.7 | 50.29 | 50.29 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1041.75 | 50.27 | 50.27 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1041.8 | 50.24 | 50.24 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1041.85 | 50.22 | 50.22 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1041.9 | 50.19 | 50.19 | -0.905 | -0.905 | -9.05 | 50.47 | -1 | -1 | -10 | -9.525 | -9.525 | 0 | 12 | 1 | 1 | -9.525 | 10 | 0 | 0
1041.95 | 50.17 | 50.17 | -0.715 | -0.715 | -7.15 | 50.45 | -1 | -1 | -10 | -8.575 | -8.575 | 0 | 12 | 1 | 1 | -8.575 | 10 | 0 | 0
1042 | 50.14 | 50.14 | -0.43 | -0.43 | -4.3 | 50.42 | -1 | -1 | -10 | -7.15 | -7.15 | 0 | 12 | 1 | 1 | -7.15 | 10 | 0 | 0
1042.05 | 50.12 | 50.12 | -0.24 | -0.24 | -2.4 | 50.4 | -1 | -1 | -10 | -6.2 | -6.2 | 0 | 12 | 1 | 1 | -6.2 | 10 | 0 | 0
1042.1 | 50.09 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 50.37 | -1 | -1 | -10 | -5.2206 | -5.2206 | 0 | 12 | 1 | 1 | -5.2206 | 10 | 0 | 0
1042.15 | 50.06 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.35 | -1 | -1 | -10 | -5.1324 | -5.1324 | 0 | 12 | 1 | 1 | -5.1324 | 10 | 0 | 0
1042.2 | 50.04 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.32 | -1 | -1 | -10 | -5.0735 | -5.0735 | 0 | 12 | 1 | 1 | -5.0735 | 10 | 0 | 0
1042.25 | 50.01 | 50.01 | 0 | 0 | 0 | 50.29 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1042.3 | 49.99 | 49.99 | 0 | 0 | 0 | 50.27 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1042.35 | 49.96 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.24 | -1 | -1 | -10 | -4.9265 | -4.9265 | 0 | 12 | 1 | 1 | -4.9265 | 10 | 0 | 0
1042.4 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.22 | -1 | -1 | -10 | -4.8676 | -4.8676 | 0 | 12 | 1 | 1 | -4.8676 | 10 | 0 | 0
1042.45 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.19 | -0.905 | -0.905 | -9.05 | -4.3044 | -4.3044 | 0 | 12 | 1 | 1 | -4.3044 | 10 | 0 | 0
1042.5 | 49.88 | 49.88 | 0.24 | 0.24 | 2.4 | 50.17 | -0.715 | -0.805 | -8.05 | -2.825 | -2.825 | 0 | 12 | 1 | 1 | -2.825 | 10 | 0 | 0
1042.55 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.14 | -0.43 | -0.705 | -7.05 | -1.375 | -1.375 | 0 | 12 | 1 | 1 | -1.375 | 10 | 0 | 0
1042.6 | 49.83 | 49.83 | 0.715 | 0.715 | 7.15 | 50.12 | -0.24 | -0.605 | -6.05 | 0.55 | 0.55 | 0 | 12 | 1 | 1 | 0.55 | 10 | 0 | 0
1042.65 | 49.81 | 49.81 | 0.905 | 0.905 | 9.05 | 50.09 | -0.044118 | -0.505 | -5.05 | 2 | 2 | 0 | 12 | 1 | 1 | 2 | 10 | 0 | 0
1042.7 | 49.78 | 49.78 | 1 | 1 | 10 | 50.06 | -0.026471 | -0.405 | -4.05 | 2.975 | 2.975 | 0 | 12 | 1 | 1 | 2.975 | 10 | 0 | 0
1042.75 | 49.76 | 49.76 | 1 | 1 | 10 | 50.04 | -0.014706 | -0.305 | -3.05 | 3.475 | 3.475 | 0 | 12 | 1 | 1 | 3.475 | 10 | 0 | 0
1042.8 | 49.73 | 49.73 | 1 | 1 | 10 | 50.01 | 0 | -0.205 | -2.05 | 3.975 | 3.975 | 0 | 12 | 1 | 1 | 3.975 | 10 | 0 | 0
1042.85 | 49.71 | 49.71 | 1 | 1 | 10 | 49.99 | 0 | -0.105 | -1.05 | 4.475 | 4.475 | 0 | 12 | 1 | 1 | 4.475 | 10 | 0 | 0
1042.9 | 49.68 | 49.68 | 1 | 1 | 10 | 49.96 | 0.014706 | -0.005 | -0.05 | 4.975 | 4.975 | 0 | 12 | 1 | 1 | 4.975 | 10 | 0 | 0
1042.95 | 49.65 | 49.65 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
1043 | 49.63 | 49.63 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1043.05 | 49.6 | 49.6 | 1 | 1 | 10 | 49.88 | 0.24 | 0.14412 | 1.4412 | 5.7206 | 5.7206 | 0 | 12 | 1 | 1 | 5.7206 | 10 | 0 | 0
1043.1 | 49.58 | 49.58 | 1 | 1 | 10 | 49.86 | 0.43 | 0.24412 | 2.4412 | 6.2206 | 6.2206 | 0 | 12 | 1 | 1 | 6.2206 | 10 | 0 | 0
1043.15 | 49.55 | 49.55 | 1 | 1 | 10 | 49.83 | 0.715 | 0.34412 | 3.4412 | 6.7206 | 6.7206 | 0 | 12 | 1 | 1 | 6.7206 | 10 | 0 | 0
1043.2 | 49.53 | 49.53 | 1 | 1 | 10 | 49.81 | 0.905 | 0.44412 | 4.4412 | 7.2206 | 7.2206 | 0 | 12 | 1 | 1 | 7.2206 | 10 | 0 | 0
1043.25 | 49.5 | 49.5 | 1 | 1 | 10 | 49.78 | 1 | 0.54412 | 5.4412 | 7.7206 | 7.7206 | 0 | 12 | 1 | 1 | 7.7206 | 10 | 0 | 0
1043.3 | 49.5 | 49.5 | 1 | 1 | 10 | 49.76 | 1 | 0.64412 | 6.4412 | 8.2206 | 8.2206 | 0 | 12 | 1 | 1 | 8.2206 | 10 | 0 | 0
1043.35 | 49.53 | 49.5 | 1 | 1 | 10 | 49.73 | 1 | 0.74412 | 7.4412 | 8.7206 | 8.7206 | 0 | 12 | 1 | 1 | 8.7206 | 10 | 0 | 0
1043.4 | 49.55 | 49.5 | 1 | 1 | 10 | 49.71 | 1 | 0.84412 | 8.4412 | 9.2206 | 9.2206 | 0 | 12 | 1 | 1 | 9.2206 | 10 | 0 | 0
1043.45 | 49.58 | 49.5 | 1 | 1 | 10 | 49.68 | 1 | 0.94412 | 9.4412 | 9.7206 | 9.7206 | 0 | 12 | 1 | 1 | 9.7206 | 10 | 0 | 0
1043.5 | 49.6 | 49.5 | 1 | 1 | 10 | 49.65 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1043.55 | 49.63 | 49.5 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1043.6 | 49.65 | 49.5 | 1 | 1 | 10 | 49.65 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1043.65 | 49.68 | 49.5 | 1 | 1 | 10 | 49.68 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1043.7 | 49.71 | 49.5 | 1 | 1 | 10 | 49.71 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1043.75 | 49.73 | 49.5 | 1 | 1 | 10 | 49.73 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1043.8 | 49.76 | 49.5 | 1 | 1 | 10 | 49.76 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1043.85 | 49.78 | 49.5 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1043.9 | 49.81 | 49.53 | 1 | 1 | 10 | 49.81 | 0.905 | 0.905 | 9.05 | 9.525 | 9.525 | 0 | 12 | 1 | 1 | 9.525 | 10 | 0 | 0
1043.95 | 49.83 | 49.55 | 1 | 1 | 10 | 49.83 | 0.715 | 0.715 | 7.15 | 8.575 | 8.575 | 0 | 12 | 1 | 1 | 8.575 | 10 | 0 | 0
1044 | 49.86 | 49.58 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
1044.05 | 49.88 | 49.6 | 1 | 1 | 10 | 49.88 | 0.24 | 0.24 | 2.4 | 6.2 | 6.2 | 0 | 12 | 1 | 1 | 6.2 | 10 | 0 | 0
1044.1 | 49.91 | 49.63 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1044.15 | 49.94 | 49.65 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
1044.2 | 49.96 | 49.68 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
1044.25 | 49.99 | 49.71 | 1 | 1 | 10 | 49.99 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1044.3 | 50.01 | 49.73 | 1 | 1 | 10 | 50.01 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1044.35 | 50.04 | 49.76 | 1 | 1 | 10 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 4.9265 | 4.9265 | 0 | 12 | 1 | 1 | 4.9265 | 10 | 0 | 0
1044.4 | 50.06 | 49.78 | 1 | 1 | 10 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 4.8676 | 4.8676 | 0 | 12 | 1 | 1 | 4.8676 | 10 | 0 | 0
1044.45 | 50.09 | 49.81 | 0.905 | 0.905 | 9.05 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 4.3044 | 4.3044 | 0 | 12 | 1 | 1 | 4.3044 | 10 | 0 | 0
1044.5 | 50.12 | 49.83 | 0.715 | 0.805 | 8.05 | 50.12 | -0.24 | -0.24 | -2.4 | 2.825 | 2.825 | 0 | 12 | 1 | 1 | 2.825 | 10 | 0 | 0
1044.55 | 50.14 | 49.86 | 0.43 | 0.705 | 7.05 | 50.14 | -0.43 | -0.43 | -4.3 | 1.375 | 1.375 | 0 | 12 | 1 | 1 | 1.375 | 10 | 0 | 0
1044.6 | 50.17 | 49.88 | 0.24 | 0.605 | 6.05 | 50.17 | -0.715 | -0.715 | -7.15 | -0.55 | -0.55 | 0 | 12 | 1 | 1 | -0.55 | 10 | 0 | 0
1044.65 | 50.19 | 49.91 | 0.044118 | 0.505 | 5.05 | 50.19 | -0.905 | -0.905 | -9.05 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
1044.7 | 50.22 | 49.94 | 0.026471 | 0.405 | 4.05 | 50.22 | -1 | -1 | -10 | -2.975 | -2.975 | 0 | 12 | 1 | 1 | -2.975 | 10 | 0 | 0
1044.75 | 50.24 | 49.96 | 0.014706 | 0.305 | 3.05 | 50.24 | -1 | -1 | -10 | -3.475 | -3.475 | 0 | 12 | 1 | 1 | -3.475 | 10 | 0 | 0
1044.8 | 50.27 | 49.99 | 0 | 0.205 | 2.05 | 50.27 | -1 | -1 | -10 | -3.975 | -3.975 | 0 | 12 | 1 | 1 | -3.975 | 10 | 0 | 0
1044.85 | 50.29 | 50.01 | 0 | 0.105 | 1.05 | 50.29 | -1 | -1 | -10 | -4.475 | -4.475 | 0 | 12 | 1 | 1 | -4.475 | 10 | 0 | 0
1044.9 | 50.32 | 50.04 | -0.014706 | 0.005 | 0.05 | 50.32 | -1 | -1 | -10 | -4.975 | -4.975 | 0 | 12 | 1 | 1 | -4.975 | 10 | 0 | 0
1044.95 | 50.35 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.35 | -1 | -1 | -10 | -5.1324 | -5.1324 | 0 | 12 | 1 | 1 | -5.1324 | 10 | 0 | 0
1045 | 50.37 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 50.37 | -1 | -1 | -10 | -5.2206 | -5.2206 | 0 | 12 | 1 | 1 | -5.2206 | 10 | 0 | 0
1045.05 | 50.4 | 50.12 | -0.24 | -0.14412 | -1.4412 | 50.4 | -1 | -1 | -10 | -5.7206 | -5.7206 | 0 | 12 | 1 | 1 | -5.7206 | 10 | 0 | 0
1045.1 | 50.42 | 50.14 | -0.43 | -0.24412 | -2.4412 | 50.42 | -1 | -1 | -10 | -6.2206 | -6.2206 | 0 | 12 | 1 | 1 | -6.2206 | 10 | 0 | 0
1045.15 | 50.45 | 50.17 | -0.715 | -0.34412 | -3.4412 | 50.45 | -1 | -1 | -10 | -6.7206 | -6.7206 | 0 | 12 | 1 | 1 | -6.7206 | 10 | 0 | 0
1045.2 | 50.47 | 50.19 | -0.905 | -0.44412 | -4.4412 | 50.47 | -1 | -1 | -10 | -7.2206 | -7.2206 | 0 | 12 | 1 | 1 | -7.2206 | 10 | 0 | 0
1045.25 | 50.5 | 50.22 | -1 | -0.54412 | -5.4412 | 50.5 | -1 | -1 | -10 | -7.7206 | -7.7206 | 0 | 12 | 1 | 1 | -7.7206 | 10 | 0 | 0
1045.3 | 50.5 | 50.24 | -1 | -0.64412 | -6.4412 | 50.5 | -1 | -1 | -10 | -8.2206 | -8.2206 | 0 | 12 | 1 | 1 | -8.2206 | 10 | 0 | 0
1045.35 | 50.47 | 50.27 | -1 | -0.74412 | -7.4412 | 50.5 | -1 | -1 | -10 | -8.7206 | -8.7206 | 0 | 12 | 1 | 1 | -8.7206 | 10 | 0 | 0
1045.4 | 50.45 | 50.29 | -1 | -0.84412 | -8.4412 | 50.5 | -1 | -1 | -10 | -9.2206 | -9.2206 | 0 | 12 | 1 | 1 | -9.2206 | 10 | 0 | 0
1045.45 | 50.42 | 50.32 | -1 | -0.94412 | -9.4412 | 50.5 | -1 | -1 | -10 | -9.7206 | -9.7206 | 0 | 12 | 1 | 1 | -9.7206 | 10 | 0 | 0
1045.5 | 50.39 | 50.35 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1045.55 | 50.37 | 50.37 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1045.6 | 50.34 | 50.34 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1045.65 | 50.32 | 50.32 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1045.7 | 50.29 | 50.29 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1045.75 | 50.26 | 50.26 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1045.8 | 50.24 | 50.24 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1045.85 | 50.21 | 50.21 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1045.9 | 50.18 | 50.18 | -0.81 | -0.81 | -8.1 | 50.47 | -1 | -1 | -10 | -9.05 | -9.05 | 0 | 12 | 1 | 1 | -9.05 | 10 | 0 | 0
1045.95 | 50.16 | 50.16 | -0.62 | -0.62 | -6.2 | 50.45 | -1 | -1 | -10 | -8.1 | -8.1 | 0 | 12 | 1 | 1 | -8.1 | 10 | 0 | 0
1046 | 50.13 | 50.13 | -0.335 | -0.335 | -3.35 | 50.42 | -1 | -1 | -10 | -6.675 | -6.675 | 0 | 12 | 1 | 1 | -6.675 | 10 | 0 | 0
1046.05 | 50.11 | 50.11 | -0.145 | -0.145 | -1.45 | 50.39 | -1 | -1 | -10 | -5.725 | -5.725 | 0 | 12 | 1 | 1 | -5.725 | 10 | 0 | 0
1046.1 | 50.08 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 50.37 | -1 | -1 | -10 | -5.1912 | -5.1912 | 0 | 12 | 1 | 1 | -5.1912 | 10 | 0 | 0
1046.15 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.34 | -1 | -1 | -10 | -5.1029 | -5.1029 | 0 | 12 | 1 | 1 | -5.1029 | 10 | 0 | 0
1046.2 | 50.03 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 50.32 | -1 | -1 | -10 | -5.0441 | -5.0441 | 0 | 12 | 1 | 1 | -5.0441 | 10 | 0 | 0
1046.25 | 50 | 50 | 0 | 0 | 0 | 50.29 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1046.3 | 50 | 50 | 0 | 0 | 0 | 50.26 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1046.35 | 50 | 50 | 0 | 0 | 0 | 50.24 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1046.4 | 50 | 50 | 0 | 0 | 0 | 50.21 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1046.45 | 50 | 50 | 0 | 0 | 0 | 50.18 | -0.81 | -0.9 | -9 | -4.5 | -4.5 | 0 | 12 | 1 | 1 | -4.5 | 10 | 0 | 0
1046.5 | 50 | 50 | 0 | 0 | 0 | 50.16 | -0.62 | -0.8 | -8 | -4 | -4 | 0 | 12 | 1 | 1 | -4 | 10 | 0 | 0
1046.55 | 50 | 50 | 0 | 0 | 0 | 50.13 | -0.335 | -0.7 | -7 | -3.5 | -3.5 | 0 | 12 | 1 | 1 | -3.5 | 10 | 0 | 0
1046.6 | 50.01 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.6 | -6 | -3 | -3 | 0 | 12 | 1 | 1 | -3 | 10 | 0 | 0
1046.65 | 50.01 | 50 | 0 | 0 | 0 | 50.08 | -0.038235 | -0.5 | -5 | -2.5 | -2.5 | 0 | 12 | 1 | 1 | -2.5 | 10 | 0 | 0
1046.7 | 49.99 | 49.99 | 0 | 0 | 0 | 50.05 | -0.020588 | -0.4 | -4 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
1046.75 | 49.99 | 49.99 | 0 | 0 | 0 | 50.03 | -0.0088235 | -0.3 | -3 | -1.5 | -1.5 | 0 | 12 | 1 | 1 | -1.5 | 10 | 0 | 0
1046.8 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | -0.2 | -2 | -0.83824 | -0.83824 | 0 | 12 | 1 | 1 | -0.83824 | 10 | 0 | 0
1046.85 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | -0.1 | -1 | -0.33824 | -0.33824 | 0 | 12 | 1 | 1 | -0.33824 | 10 | 0 | 0
1046.9 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
1046.95 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
1047 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
1047.05 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
1047.1 | 49.89 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
1047.15 | 49.89 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
1047.2 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50.01 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1047.25 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1047.3 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1047.35 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 2.7868 | 2.7868 | 0 | 12 | 1 | 1 | 2.7868 | 10 | 0 | 0
1047.4 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 2.7868 | 2.7868 | 0 | 12 | 1 | 1 | 2.7868 | 10 | 0 | 0
1047.45 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 2.8456 | 2.8456 | 0 | 12 | 1 | 1 | 2.8456 | 10 | 0 | 0
1047.5 | 49.94 | 49.85 | 0.525 | 0.525 | 5.25 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 2.7574 | 2.7574 | 0 | 12 | 1 | 1 | 2.7574 | 10 | 0 | 0
1047.55 | 49.94 | 49.85 | 0.525 | 0.525 | 5.25 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 2.7574 | 2.7574 | 0 | 12 | 1 | 1 | 2.7574 | 10 | 0 | 0
1047.6 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1047.65 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1047.7 | 49.93 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1047.75 | 49.93 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1047.8 | 49.96 | 49.85 | 0.525 | 0.525 | 5.25 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 2.6985 | 2.6985 | 0 | 12 | 1 | 1 | 2.6985 | 10 | 0 | 0
1047.85 | 49.96 | 49.85 | 0.525 | 0.525 | 5.25 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 2.6985 | 2.6985 | 0 | 12 | 1 | 1 | 2.6985 | 10 | 0 | 0
1047.9 | 49.99 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1047.95 | 49.99 | 49.91 | 0.044118 | 0.425 | 4.25 | 49.99 | 0 | 0 | 0 | 2.125 | 2.125 | 0 | 12 | 1 | 1 | 2.125 | 10 | 0 | 0
1048 | 49.99 | 49.91 | 0.044118 | 0.325 | 3.25 | 49.99 | 0 | 0 | 0 | 1.625 | 1.625 | 0 | 12 | 1 | 1 | 1.625 | 10 | 0 | 0
1048.05 | 49.99 | 49.93 | 0.032353 | 0.225 | 2.25 | 49.99 | 0 | 0 | 0 | 1.125 | 1.125 | 0 | 12 | 1 | 1 | 1.125 | 10 | 0 | 0
1048.1 | 49.96 | 49.93 | 0.032353 | 0.125 | 1.25 | 49.99 | 0 | 0 | 0 | 0.625 | 0.625 | 0 | 12 | 1 | 1 | 0.625 | 10 | 0 | 0
1048.15 | 49.96 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 49.99 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1048.2 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1048.25 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1048.3 | 50.05 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.058824 | 0.058824 | 0 | 12 | 1 | 1 | 0.058824 | 10 | 0 | 0
1048.35 | 50.05 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
1048.4 | 49.97 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
1048.45 | 49.97 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
1048.5 | 49.92 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1048.55 | 49.92 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1048.6 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1048.65 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1048.7 | 49.94 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1048.75 | 49.94 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1048.8 | 50.01 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1048.85 | 50.01 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1048.9 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1048.95 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
1049 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
1049.05 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
1049.1 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
1049.15 | 49.95 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
1049.2 | 49.97 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
1049.25 | 49.97 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
1049.3 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
1049.35 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
1049.4 | 49.87 | 49.87 | 0.335 | 0.335 | 3.35 | 50.01 | 0 | 0 | 0 | 1.675 | 1.675 | 0 | 12 | 1 | 1 | 1.675 | 10 | 0 | 0
1049.45 | 49.87 | 49.87 | 0.335 | 0.335 | 3.35 | 49.99 | 0 | 0 | 0 | 1.675 | 1.675 | 0 | 12 | 1 | 1 | 1.675 | 10 | 0 | 0
1049.5 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1049.55 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 2.6691 | 2.6691 | 0 | 12 | 1 | 1 | 2.6691 | 10 | 0 | 0
1049.6 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1049.65 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1049.7 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1049.75 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1049.8 | 49.84 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1049.85 | 49.84 | 49.79 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
1049.9 | 49.89 | 49.79 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
1049.95 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.12647 | 1.2647 | 5.6324 | 5.6324 | 0 | 12 | 1 | 1 | 5.6324 | 10 | 0 | 0
1050 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.145 | 1.45 | 5.725 | 5.725 | 0 | 12 | 1 | 1 | 5.725 | 10 | 0 | 0
1050.05 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.145 | 1.45 | 5.725 | 5.725 | 0 | 12 | 1 | 1 | 5.725 | 10 | 0 | 0
1050.1 | 49.96 | 49.79 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
1050.15 | 49.96 | 49.79 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
1050.2 | 50.02 | 49.79 | 1 | 1 | 10 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 4.9853 | 4.9853 | 0 | 12 | 1 | 1 | 4.9853 | 10 | 0 | 0
1050.25 | 50.02 | 49.79 | 1 | 1 | 10 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 4.9853 | 4.9853 | 0 | 12 | 1 | 1 | 4.9853 | 10 | 0 | 0
1050.3 | 50.03 | 49.79 | 1 | 1 | 10 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.9559 | 4.9559 | 0 | 12 | 1 | 1 | 4.9559 | 10 | 0 | 0
1050.35 | 50.03 | 49.84 | 0.62 | 0.9 | 9 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.4559 | 4.4559 | 0 | 12 | 1 | 1 | 4.4559 | 10 | 0 | 0
1050.4 | 50.02 | 49.84 | 0.62 | 0.8 | 8 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 3.9559 | 3.9559 | 0 | 12 | 1 | 1 | 3.9559 | 10 | 0 | 0
1050.45 | 50.02 | 49.89 | 0.145 | 0.7 | 7 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 3.4559 | 3.4559 | 0 | 12 | 1 | 1 | 3.4559 | 10 | 0 | 0
1050.5 | 50.08 | 49.89 | 0.145 | 0.6 | 6 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 2.8088 | 2.8088 | 0 | 12 | 1 | 1 | 2.8088 | 10 | 0 | 0
1050.55 | 50.08 | 49.89 | 0.145 | 0.5 | 5 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 2.3088 | 2.3088 | 0 | 12 | 1 | 1 | 2.3088 | 10 | 0 | 0
1050.6 | 50.01 | 49.89 | 0.145 | 0.4 | 4 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 1.8088 | 1.8088 | 0 | 12 | 1 | 1 | 1.8088 | 10 | 0 | 0
1050.65 | 50.01 | 49.96 | 0.014706 | 0.3 | 3 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 1.3088 | 1.3088 | 0 | 12 | 1 | 1 | 1.3088 | 10 | 0 | 0
1050.7 | 49.94 | 49.94 | 0.026471 | 0.2 | 2 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.80882 | 0.80882 | 0 | 12 | 1 | 1 | 0.80882 | 10 | 0 | 0
1050.75 | 49.94 | 49.94 | 0.026471 | 0.1 | 1 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.30882 | 0.30882 | 0 | 12 | 1 | 1 | 0.30882 | 10 | 0 | 0
1050.8 | 50 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
1050.85 | 50 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
1050.9 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
1050.95 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
1051 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1051.05 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1051.1 | 49.92 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1051.15 | 49.92 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
1051.2 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50.01 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1051.25 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1051.3 | 49.92 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1051.35 | 49.92 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1051.4 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1051.45 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1051.5 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1051.55 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1051.6 | 49.87 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1051.65 | 49.87 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1051.7 | 49.8 | 49.8 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1051.75 | 49.8 | 49.8 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1051.8 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1051.85 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1051.9 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1051.95 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1052 | 49.72 | 49.72 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1052.05 | 49.72 | 49.72 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1052.1 | 49.67 | 49.67 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1052.15 | 49.67 | 49.67 | 1 | 1 | 10 | 49.87 | 0.335 | 0.14412 | 1.4412 | 5.7206 | 5.7206 | 0 | 12 | 1 | 1 | 5.7206 | 10 | 0 | 0
1052.2 | 49.65 | 49.65 | 1 | 1 | 10 | 49.87 | 0.335 | 0.24412 | 2.4412 | 6.2206 | 6.2206 | 0 | 12 | 1 | 1 | 6.2206 | 10 | 0 | 0
1052.25 | 49.65 | 49.65 | 1 | 1 | 10 | 49.8 | 1 | 0.34412 | 3.4412 | 6.7206 | 6.7206 | 0 | 12 | 1 | 1 | 6.7206 | 10 | 0 | 0
1052.3 | 49.59 | 49.59 | 1 | 1 | 10 | 49.8 | 1 | 0.44412 | 4.4412 | 7.2206 | 7.2206 | 0 | 12 | 1 | 1 | 7.2206 | 10 | 0 | 0
1052.35 | 49.59 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.54412 | 5.4412 | 7.7206 | 7.7206 | 0 | 12 | 1 | 1 | 7.7206 | 10 | 0 | 0
1052.4 | 49.66 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.64412 | 6.4412 | 8.2206 | 8.2206 | 0 | 12 | 1 | 1 | 8.2206 | 10 | 0 | 0
1052.45 | 49.66 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.74412 | 7.4412 | 8.7206 | 8.7206 | 0 | 12 | 1 | 1 | 8.7206 | 10 | 0 | 0
1052.5 | 49.63 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.84412 | 8.4412 | 9.2206 | 9.2206 | 0 | 12 | 1 | 1 | 9.2206 | 10 | 0 | 0
1052.55 | 49.63 | 49.59 | 1 | 1 | 10 | 49.72 | 1 | 0.94412 | 9.4412 | 9.7206 | 9.7206 | 0 | 12 | 1 | 1 | 9.7206 | 10 | 0 | 0
1052.6 | 49.61 | 49.59 | 1 | 1 | 10 | 49.72 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1052.65 | 49.61 | 49.59 | 1 | 1 | 10 | 49.67 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1052.7 | 49.54 | 49.54 | 1 | 1 | 10 | 49.67 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1052.75 | 49.54 | 49.54 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1052.8 | 49.46 | 49.46 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1052.85 | 49.46 | 49.46 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1052.9 | 49.45 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1052.95 | 49.45 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1053 | 49.51 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1053.05 | 49.51 | 49.45 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1053.1 | 49.5 | 49.45 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1053.15 | 49.5 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1053.2 | 49.54 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1053.25 | 49.54 | 49.45 | 1 | 1 | 10 | 49.54 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1053.3 | 49.59 | 49.45 | 1 | 1 | 10 | 49.59 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1053.35 | 49.59 | 49.45 | 1 | 1 | 10 | 49.59 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1053.4 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1053.45 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1053.5 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1053.55 | 49.61 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1053.6 | 49.53 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1053.65 | 49.53 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1053.7 | 49.54 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1053.75 | 49.54 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1053.8 | 49.61 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1053.85 | 49.61 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1053.9 | 49.66 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1053.95 | 49.66 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1054 | 49.64 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1054.05 | 49.64 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1054.1 | 49.69 | 49.53 | 1 | 1 | 10 | 49.69 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1054.15 | 49.69 | 49.53 | 1 | 1 | 10 | 49.69 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1054.2 | 49.74 | 49.53 | 1 | 1 | 10 | 49.74 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1054.25 | 49.74 | 49.54 | 1 | 1 | 10 | 49.74 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1054.3 | 49.78 | 49.54 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1054.35 | 49.78 | 49.61 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1054.4 | 49.82 | 49.61 | 1 | 1 | 10 | 49.82 | 0.81 | 0.81 | 8.1 | 9.05 | 9.05 | 0 | 12 | 1 | 1 | 9.05 | 10 | 0 | 0
1054.45 | 49.82 | 49.64 | 1 | 1 | 10 | 49.82 | 0.81 | 0.81 | 8.1 | 9.05 | 9.05 | 0 | 12 | 1 | 1 | 9.05 | 10 | 0 | 0
1054.5 | 49.86 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
1054.55 | 49.86 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
1054.6 | 49.84 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
1054.65 | 49.84 | 49.69 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
1054.7 | 49.91 | 49.69 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1054.75 | 49.91 | 49.74 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1054.8 | 49.97 | 49.74 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1054.85 | 49.97 | 49.78 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1054.9 | 50.03 | 49.78 | 1 | 1 | 10 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.9559 | 4.9559 | 0 | 12 | 1 | 1 | 4.9559 | 10 | 0 | 0
1054.95 | 50.03 | 49.82 | 0.81 | 0.9 | 9 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.4559 | 4.4559 | 0 | 12 | 1 | 1 | 4.4559 | 10 | 0 | 0
1055 | 50.05 | 49.82 | 0.81 | 0.81 | 8.1 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 3.9471 | 3.9471 | 0 | 12 | 1 | 1 | 3.9471 | 10 | 0 | 0
1055.05 | 50.05 | 49.84 | 0.62 | 0.71 | 7.1 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 3.4471 | 3.4471 | 0 | 12 | 1 | 1 | 3.4471 | 10 | 0 | 0
1055.1 | 50.01 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
1055.15 | 50.01 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
1055.2 | 49.95 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
1055.25 | 49.95 | 49.91 | 0.044118 | 0.52 | 5.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.4971 | 2.4971 | 0 | 12 | 1 | 1 | 2.4971 | 10 | 0 | 0
1055.3 | 49.99 | 49.91 | 0.044118 | 0.42 | 4.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 1.9971 | 1.9971 | 0 | 12 | 1 | 1 | 1.9971 | 10 | 0 | 0
1055.35 | 49.99 | 49.95 | 0.020588 | 0.32 | 3.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 1.4971 | 1.4971 | 0 | 12 | 1 | 1 | 1.4971 | 10 | 0 | 0
1055.4 | 49.92 | 49.92 | 0.038235 | 0.22 | 2.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.99706 | 0.99706 | 0 | 12 | 1 | 1 | 0.99706 | 10 | 0 | 0
1055.45 | 49.92 | 49.92 | 0.038235 | 0.12 | 1.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.49706 | 0.49706 | 0 | 12 | 1 | 1 | 0.49706 | 10 | 0 | 0
1055.5 | 49.97 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1055.55 | 49.97 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1055.6 | 50.02 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1055.65 | 50.02 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.17647 | 0.17647 | 0 | 12 | 1 | 1 | 0.17647 | 10 | 0 | 0
1055.7 | 50.07 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1055.75 | 50.07 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1055.8 | 50.06 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1055.85 | 50.06 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1055.9 | 50.13 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
1055.95 | 50.13 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
1056 | 50.09 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
1056.05 | 50.09 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6309 | -1.6309 | 0 | 12 | 1 | 1 | -1.6309 | 10 | 0 | 0
1056.1 | 50.07 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6309 | -1.6309 | 0 | 12 | 1 | 1 | -1.6309 | 10 | 0 | 0
1056.15 | 50.07 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6897 | -1.6897 | 0 | 12 | 1 | 1 | -1.6897 | 10 | 0 | 0
1056.2 | 50.07 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6897 | -1.6897 | 0 | 12 | 1 | 1 | -1.6897 | 10 | 0 | 0
1056.25 | 50.07 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.13 | -0.335 | -0.335 | -3.35 | -1.8074 | -1.8074 | 0 | 12 | 1 | 1 | -1.8074 | 10 | 0 | 0
1056.3 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.13 | -0.335 | -0.335 | -3.35 | -1.7779 | -1.7779 | 0 | 12 | 1 | 1 | -1.7779 | 10 | 0 | 0
1056.35 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.13 | -0.335 | -0.335 | -3.35 | -1.7779 | -1.7779 | 0 | 12 | 1 | 1 | -1.7779 | 10 | 0 | 0
1056.4 | 50.01 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
1056.45 | 50.01 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
1056.5 | 50.07 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
1056.55 | 50.07 | 50.01 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.235 | -2.35 | -1.175 | -1.175 | 0 | 12 | 1 | 1 | -1.175 | 10 | 0 | 0
1056.6 | 50.05 | 50.01 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.135 | -1.35 | -0.675 | -0.675 | 0 | 12 | 1 | 1 | -0.675 | 10 | 0 | 0
1056.65 | 50.05 | 50.01 | 0 | 0 | 0 | 50.07 | -0.032353 | -0.035 | -0.35 | -0.175 | -0.175 | 0 | 12 | 1 | 1 | -0.175 | 10 | 0 | 0
1056.7 | 50.1 | 50.01 | 0 | 0 | 0 | 50.1 | -0.05 | -0.05 | -0.5 | -0.25 | -0.25 | 0 | 12 | 1 | 1 | -0.25 | 10 | 0 | 0
1056.75 | 50.1 | 50.01 | 0 | 0 | 0 | 50.1 | -0.05 | -0.05 | -0.5 | -0.25 | -0.25 | 0 | 12 | 1 | 1 | -0.25 | 10 | 0 | 0
1056.8 | 50.11 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1056.85 | 50.11 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1056.9 | 50.06 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1056.95 | 50.06 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1057 | 50.04 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1057.05 | 50.04 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1057.1 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1057.15 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1057.2 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1057.25 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1057.3 | 50.11 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1057.35 | 50.11 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1057.4 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1057.45 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1057.5 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1057.55 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1057.6 | 50.02 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.11 | -0.145 | -0.145 | -1.45 | -0.73971 | -0.73971 | 0 | 12 | 1 | 1 | -0.73971 | 10 | 0 | 0
1057.65 | 50.02 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.11 | -0.145 | -0.145 | -1.45 | -0.73971 | -0.73971 | 0 | 12 | 1 | 1 | -0.73971 | 10 | 0 | 0
1057.7 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1057.75 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1057.8 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1057.85 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1057.9 | 50.01 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1057.95 | 50.01 | 50 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.045 | -0.45 | -0.225 | -0.225 | 0 | 12 | 1 | 1 | -0.225 | 10 | 0 | 0
1058 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
1058.05 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
1058.1 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
1058.15 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1058.2 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.14706 | 0.14706 | 0 | 12 | 1 | 1 | 0.14706 | 10 | 0 | 0
1058.25 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1058.3 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1058.35 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1058.4 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1058.45 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1058.5 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1058.55 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1058.6 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1058.65 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1058.7 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1058.75 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1058.8 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1058.85 | 50 | 50 | 0 | 0 | 0 | 50.01 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1058.9 | 49.5 | 49.5 | 1 | 1 | 10 | 50.01 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1058.95 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1059 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1059.05 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1059.1 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1059.15 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1059.2 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1059.25 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1059.3 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1059.35 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1059.4 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1059.45 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.1 | 1 | 5.5 | 5.5 | 0 | 12 | 1 | 1 | 5.5 | 10 | 0 | 0
1059.5 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.2 | 2 | 6 | 6 | 0 | 12 | 1 | 1 | 6 | 10 | 0 | 0
1059.55 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.3 | 3 | 6.5 | 6.5 | 0 | 12 | 1 | 1 | 6.5 | 10 | 0 | 0
1059.6 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.4 | 4 | 7 | 7 | 0 | 12 | 1 | 1 | 7 | 10 | 0 | 0
1059.65 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.5 | 5 | 7.5 | 7.5 | 0 | 12 | 1 | 1 | 7.5 | 10 | 0 | 0
1059.7 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.6 | 6 | 8 | 8 | 0 | 12 | 1 | 1 | 8 | 10 | 0 | 0
1059.75 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.7 | 7 | 8.5 | 8.5 | 0 | 12 | 1 | 1 | 8.5 | 10 | 0 | 0
1059.8 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.8 | 8 | 9 | 9 | 0 | 12 | 1 | 1 | 9 | 10 | 0 | 0
1059.85 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.9 | 9 | 9.5 | 9.5 | 0 | 12 | 1 | 1 | 9.5 | 10 | 0 | 0
1059.9 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1059.95 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1060 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1060.05 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1060.1 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1060.15 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1060.2 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1060.25 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1060.3 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1060.35 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1060.4 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1060.45 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1060.5 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1060.55 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1060.6 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1060.65 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1060.7 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1060.75 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1060.8 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1060.85 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1060.9 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1060.95 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1061 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1061.05 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1061.1 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1061.15 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1061.2 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1061.25 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1061.3 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1061.35 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1061.4 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1061.45 | 50.5 | 50.5 | -1 | 0.9 | 9 | 50.5 | -1 | -1 | -10 | -0.5 | -0.5 | 0 | 12 | 1 | 1 | -0.5 | 10 | 0 | 0
1061.5 | 50.5 | 50.5 | -1 | 0.8 | 8 | 50.5 | -1 | -1 | -10 | -1 | -1 | 0 | 12 | 1 | 1 | -1 | 10 | 0 | 0
1061.55 | 50.5 | 50.5 | -1 | 0.7 | 7 | 50.5 | -1 | -1 | -10 | -1.5 | -1.5 | 0 | 12 | 1 | 1 | -1.5 | 10 | 0 | 0
1061.6 | 50.5 | 50.5 | -1 | 0.6 | 6 | 50.5 | -1 | -1 | -10 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
1061.65 | 50.5 | 50.5 | -1 | 0.5 | 5 | 50.5 | -1 | -1 | -10 | -2.5 | -2.5 | 0 | 12 | 1 | 1 | -2.5 | 10 | 0 | 0
1061.7 | 50.5 | 50.5 | -1 | 0.4 | 4 | 50.5 | -1 | -1 | -10 | -3 | -3 | 0 | 12 | 1 | 1 | -3 | 10 | 0 | 0
1061.75 | 50.5 | 50.5 | -1 | 0.3 | 3 | 50.5 | -1 | -1 | -10 | -3.5 | -3.5 | 0 | 12 | 1 | 1 | -3.5 | 10 | 0 | 0
1061.8 | 50.5 | 50.5 | -1 | 0.2 | 2 | 50.5 | -1 | -1 | -10 | -4 | -4 | 0 | 12 | 1 | 1 | -4 | 10 | 0 | 0
1061.85 | 50.5 | 50.5 | -1 | 0.1 | 1 | 50.5 | -1 | -1 | -10 | -4.5 | -4.5 | 0 | 12 | 1 | 1 | -4.5 | 10 | 0 | 0
1061.9 | 50.5 | 50.5 | -1 | 0 | 0 | 50.5 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1061.95 | 50.5 | 50.5 | -1 | -0.1 | -1 | 50.5 | -1 | -1 | -10 | -5.5 | -5.5 | 0 | 12 | 1 | 1 | -5.5 | 10 | 0 | 0
1062 | 50.5 | 50.5 | -1 | -0.2 | -2 | 50.5 | -1 | -1 | -10 | -6 | -6 | 0 | 12 | 1 | 1 | -6 | 10 | 0 | 0
1062.05 | 50.5 | 50.5 | -1 | -0.3 | -3 | 50.5 | -1 | -1 | -10 | -6.5 | -6.5 | 0 | 12 | 1 | 1 | -6.5 | 10 | 0 | 0
1062.1 | 50.5 | 50.5 | -1 | -0.4 | -4 | 50.5 | -1 | -1 | -10 | -7 | -7 | 0 | 12 | 1 | 1 | -7 | 10 | 0 | 0
1062.15 | 50.5 | 50.5 | -1 | -0.5 | -5 | 50.5 | -1 | -1 | -10 | -7.5 | -7.5 | 0 | 12 | 1 | 1 | -7.5 | 10 | 0 | 0
1062.2 | 50.5 | 50.5 | -1 | -0.6 | -6 | 50.5 | -1 | -1 | -10 | -8 | -8 | 0 | 12 | 1 | 1 | -8 | 10 | 0 | 0
1062.25 | 50.5 | 50.5 | -1 | -0.7 | -7 | 50.5 | -1 | -1 | -10 | -8.5 | -8.5 | 0 | 12 | 1 | 1 | -8.5 | 10 | 0 | 0
1062.3 | 50.5 | 50.5 | -1 | -0.8 | -8 | 50.5 | -1 | -1 | -10 | -9 | -9 | 0 | 12 | 1 | 1 | -9 | 10 | 0 | 0
1062.35 | 50.5 | 50.5 | -1 | -0.9 | -9 | 50.5 | -1 | -1 | -10 | -9.5 | -9.5 | 0 | 12 | 1 | 1 | -9.5 | 10 | 0 | 0
1062.4 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1062.45 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1062.5 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1062.55 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1062.6 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1062.65 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1062.7 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1062.75 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1062.8 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1062.85 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1062.9 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1062.95 | 50.47 | 50.47 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1063 | 50.45 | 50.45 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1063.05 | 50.42 | 50.42 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1063.1 | 50.4 | 50.4 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1063.15 | 50.37 | 50.37 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1063.2 | 50.35 | 50.35 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1063.25 | 50.32 | 50.32 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1063.3 | 50.29 | 50.29 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1063.35 | 50.27 | 50.27 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1063.4 | 50.24 | 50.24 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1063.45 | 50.22 | 50.22 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1063.5 | 50.19 | 50.19 | -0.905 | -0.905 | -9.05 | 50.47 | -1 | -1 | -10 | -9.525 | -9.525 | 0 | 12 | 1 | 1 | -9.525 | 10 | 0 | 0
1063.55 | 50.17 | 50.17 | -0.715 | -0.715 | -7.15 | 50.45 | -1 | -1 | -10 | -8.575 | -8.575 | 0 | 12 | 1 | 1 | -8.575 | 10 | 0 | 0
1063.6 | 50.14 | 50.14 | -0.43 | -0.43 | -4.3 | 50.42 | -1 | -1 | -10 | -7.15 | -7.15 | 0 | 12 | 1 | 1 | -7.15 | 10 | 0 | 0
1063.65 | 50.12 | 50.12 | -0.24 | -0.24 | -2.4 | 50.4 | -1 | -1 | -10 | -6.2 | -6.2 | 0 | 12 | 1 | 1 | -6.2 | 10 | 0 | 0
1063.7 | 50.09 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 50.37 | -1 | -1 | -10 | -5.2206 | -5.2206 | 0 | 12 | 1 | 1 | -5.2206 | 10 | 0 | 0
1063.75 | 50.06 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.35 | -1 | -1 | -10 | -5.1324 | -5.1324 | 0 | 12 | 1 | 1 | -5.1324 | 10 | 0 | 0
1063.8 | 50.04 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.32 | -1 | -1 | -10 | -5.0735 | -5.0735 | 0 | 12 | 1 | 1 | -5.0735 | 10 | 0 | 0
1063.85 | 50.01 | 50.01 | 0 | 0 | 0 | 50.29 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1063.9 | 49.99 | 49.99 | 0 | 0 | 0 | 50.27 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1063.95 | 49.96 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.24 | -1 | -1 | -10 | -4.9265 | -4.9265 | 0 | 12 | 1 | 1 | -4.9265 | 10 | 0 | 0
1064 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.22 | -1 | -1 | -10 | -4.8676 | -4.8676 | 0 | 12 | 1 | 1 | -4.8676 | 10 | 0 | 0
1064.05 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.19 | -0.905 | -0.905 | -9.05 | -4.3044 | -4.3044 | 0 | 12 | 1 | 1 | -4.3044 | 10 | 0 | 0
1064.1 | 49.88 | 49.88 | 0.24 | 0.24 | 2.4 | 50.17 | -0.715 | -0.805 | -8.05 | -2.825 | -2.825 | 0 | 12 | 1 | 1 | -2.825 | 10 | 0 | 0
1064.15 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.14 | -0.43 | -0.705 | -7.05 | -1.375 | -1.375 | 0 | 12 | 1 | 1 | -1.375 | 10 | 0 | 0
1064.2 | 49.83 | 49.83 | 0.715 | 0.715 | 7.15 | 50.12 | -0.24 | -0.605 | -6.05 | 0.55 | 0.55 | 0 | 12 | 1 | 1 | 0.55 | 10 | 0 | 0
1064.25 | 49.81 | 49.81 | 0.905 | 0.905 | 9.05 | 50.09 | -0.044118 | -0.505 | -5.05 | 2 | 2 | 0 | 12 | 1 | 1 | 2 | 10 | 0 | 0
1064.3 | 49.78 | 49.78 | 1 | 1 | 10 | 50.06 | -0.026471 | -0.405 | -4.05 | 2.975 | 2.975 | 0 | 12 | 1 | 1 | 2.975 | 10 | 0 | 0
1064.35 | 49.76 | 49.76 | 1 | 1 | 10 | 50.04 | -0.014706 | -0.305 | -3.05 | 3.475 | 3.475 | 0 | 12 | 1 | 1 | 3.475 | 10 | 0 | 0
1064.4 | 49.73 | 49.73 | 1 | 1 | 10 | 50.01 | 0 | -0.205 | -2.05 | 3.975 | 3.975 | 0 | 12 | 1 | 1 | 3.975 | 10 | 0 | 0
1064.45 | 49.71 | 49.71 | 1 | 1 | 10 | 49.99 | 0 | -0.105 | -1.05 | 4.475 | 4.475 | 0 | 12 | 1 | 1 | 4.475 | 10 | 0 | 0
1064.5 | 49.68 | 49.68 | 1 | 1 | 10 | 49.96 | 0.014706 | -0.005 | -0.05 | 4.975 | 4.975 | 0 | 12 | 1 | 1 | 4.975 | 10 | 0 | 0
1064.55 | 49.65 | 49.65 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
1064.6 | 49.63 | 49.63 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1064.65 | 49.6 | 49.6 | 1 | 1 | 10 | 49.88 | 0.24 | 0.14412 | 1.4412 | 5.7206 | 5.7206 | 0 | 12 | 1 | 1 | 5.7206 | 10 | 0 | 0
1064.7 | 49.58 | 49.58 | 1 | 1 | 10 | 49.86 | 0.43 | 0.24412 | 2.4412 | 6.2206 | 6.2206 | 0 | 12 | 1 | 1 | 6.2206 | 10 | 0 | 0
1064.75 | 49.55 | 49.55 | 1 | 1 | 10 | 49.83 | 0.715 | 0.34412 | 3.4412 | 6.7206 | 6.7206 | 0 | 12 | 1 | 1 | 6.7206 | 10 | 0 | 0
1064.8 | 49.53 | 49.53 | 1 | 1 | 10 | 49.81 | 0.905 | 0.44412 | 4.4412 | 7.2206 | 7.2206 | 0 | 12 | 1 | 1 | 7.2206 | 10 | 0 | 0
1064.85 | 49.5 | 49.5 | 1 | 1 | 10 | 49.78 | 1 | 0.54412 | 5.4412 | 7.7206 | 7.7206 | 0 | 12 | 1 | 1 | 7.7206 | 10 | 0 | 0
1064.9 | 49.5 | 49.5 | 1 | 1 | 10 | 49.76 | 1 | 0.64412 | 6.4412 | 8.2206 | 8.2206 | 0 | 12 | 1 | 1 | 8.2206 | 10 | 0 | 0
1064.95 | 49.53 | 49.5 | 1 | 1 | 10 | 49.73 | 1 | 0.74412 | 7.4412 | 8.7206 | 8.7206 | 0 | 12 | 1 | 1 | 8.7206 | 10 | 0 | 0
1065 | 49.55 | 49.5 | 1 | 1 | 10 | 49.71 | 1 | 0.84412 | 8.4412 | 9.2206 | 9.2206 | 0 | 12 | 1 | 1 | 9.2206 | 10 | 0 | 0
1065.05 | 49.58 | 49.5 | 1 | 1 | 10 | 49.68 | 1 | 0.94412 | 9.4412 | 9.7206 | 9.7206 | 0 | 12 | 1 | 1 | 9.7206 | 10 | 0 | 0
1065.1 | 49.6 | 49.5 | 1 | 1 | 10 | 49.65 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1065.15 | 49.63 | 49.5 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1065.2 | 49.65 | 49.5 | 1 | 1 | 10 | 49.65 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1065.25 | 49.68 | 49.5 | 1 | 1 | 10 | 49.68 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1065.3 | 49.71 | 49.5 | 1 | 1 | 10 | 49.71 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1065.35 | 49.73 | 49.5 | 1 | 1 | 10 | 49.73 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1065.4 | 49.76 | 49.5 | 1 | 1 | 10 | 49.76 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1065.45 | 49.78 | 49.5 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1065.5 | 49.81 | 49.53 | 1 | 1 | 10 | 49.81 | 0.905 | 0.905 | 9.05 | 9.525 | 9.525 | 0 | 12 | 1 | 1 | 9.525 | 10 | 0 | 0
1065.55 | 49.83 | 49.55 | 1 | 1 | 10 | 49.83 | 0.715 | 0.715 | 7.15 | 8.575 | 8.575 | 0 | 12 | 1 | 1 | 8.575 | 10 | 0 | 0
1065.6 | 49.86 | 49.58 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
1065.65 | 49.88 | 49.6 | 1 | 1 | 10 | 49.88 | 0.24 | 0.24 | 2.4 | 6.2 | 6.2 | 0 | 12 | 1 | 1 | 6.2 | 10 | 0 | 0
1065.7 | 49.91 | 49.63 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1065.75 | 49.94 | 49.65 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
1065.8 | 49.96 | 49.68 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
1065.85 | 49.99 | 49.71 | 1 | 1 | 10 | 49.99 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1065.9 | 50.01 | 49.73 | 1 | 1 | 10 | 50.01 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1065.95 | 50.04 | 49.76 | 1 | 1 | 10 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 4.9265 | 4.9265 | 0 | 12 | 1 | 1 | 4.9265 | 10 | 0 | 0
1066 | 50.06 | 49.78 | 1 | 1 | 10 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 4.8676 | 4.8676 | 0 | 12 | 1 | 1 | 4.8676 | 10 | 0 | 0
1066.05 | 50.09 | 49.81 | 0.905 | 0.905 | 9.05 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 4.3044 | 4.3044 | 0 | 12 | 1 | 1 | 4.3044 | 10 | 0 | 0
1066.1 | 50.12 | 49.83 | 0.715 | 0.805 | 8.05 | 50.12 | -0.24 | -0.24 | -2.4 | 2.825 | 2.825 | 0 | 12 | 1 | 1 | 2.825 | 10 | 0 | 0
1066.15 | 50.14 | 49.86 | 0.43 | 0.705 | 7.05 | 50.14 | -0.43 | -0.43 | -4.3 | 1.375 | 1.375 | 0 | 12 | 1 | 1 | 1.375 | 10 | 0 | 0
1066.2 | 50.17 | 49.88 | 0.24 | 0.605 | 6.05 | 50.17 | -0.715 | -0.715 | -7.15 | -0.55 | -0.55 | 0 | 12 | 1 | 1 | -0.55 | 10 | 0 | 0
1066.25 | 50.19 | 49.91 | 0.044118 | 0.505 | 5.05 | 50.19 | -0.905 | -0.905 | -9.05 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
1066.3 | 50.22 | 49.94 | 0.026471 | 0.405 | 4.05 | 50.22 | -1 | -1 | -10 | -2.975 | -2.975 | 0 | 12 | 1 | 1 | -2.975 | 10 | 0 | 0
1066.35 | 50.24 | 49.96 | 0.014706 | 0.305 | 3.05 | 50.24 | -1 | -1 | -10 | -3.475 | -3.475 | 0 | 12 | 1 | 1 | -3.475 | 10 | 0 | 0
1066.4 | 50.27 | 49.99 | 0 | 0.205 | 2.05 | 50.27 | -1 | -1 | -10 | -3.975 | -3.975 | 0 | 12 | 1 | 1 | -3.975 | 10 | 0 | 0
1066.45 | 50.29 | 50.01 | 0 | 0.105 | 1.05 | 50.29 | -1 | -1 | -10 | -4.475 | -4.475 | 0 | 12 | 1 | 1 | -4.475 | 10 | 0 | 0
1066.5 | 50.32 | 50.04 | -0.014706 | 0.005 | 0.05 | 50.32 | -1 | -1 | -10 | -4.975 | -4.975 | 0 | 12 | 1 | 1 | -4.975 | 10 | 0 | 0
1066.55 | 50.35 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.35 | -1 | -1 | -10 | -5.1324 | -5.1324 | 0 | 12 | 1 | 1 | -5.1324 | 10 | 0 | 0
1066.6 | 50.37 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 50.37 | -1 | -1 | -10 | -5.2206 | -5.2206 | 0 | 12 | 1 | 1 | -5.2206 | 10 | 0 | 0
1066.65 | 50.4 | 50.12 | -0.24 | -0.14412 | -1.4412 | 50.4 | -1 | -1 | -10 | -5.7206 | -5.7206 | 0 | 12 | 1 | 1 | -5.7206 | 10 | 0 | 0
1066.7 | 50.42 | 50.14 | -0.43 | -0.24412 | -2.4412 | 50.42 | -1 | -1 | -10 | -6.2206 | -6.2206 | 0 | 12 | 1 | 1 | -6.2206 | 10 | 0 | 0
1066.75 | 50.45 | 50.17 | -0.715 | -0.34412 | -3.4412 | 50.45 | -1 | -1 | -10 | -6.7206 | -6.7206 | 0 | 12 | 1 | 1 | -6.7206 | 10 | 0 | 0
1066.8 | 50.47 | 50.19 | -0.905 | -0.44412 | -4.4412 | 50.47 | -1 | -1 | -10 | -7.2206 | -7.2206 | 0 | 12 | 1 | 1 | -7.2206 | 10 | 0 | 0
1066.85 | 50.5 | 50.22 | -1 | -0.54412 | -5.4412 | 50.5 | -1 | -1 | -10 | -7.7206 | -7.7206 | 0 | 12 | 1 | 1 | -7.7206 | 10 | 0 | 0
1066.9 | 50.5 | 50.24 | -1 | -0.64412 | -6.4412 | 50.5 | -1 | -1 | -10 | -8.2206 | -8.2206 | 0 | 12 | 1 | 1 | -8.2206 | 10 | 0 | 0
1066.95 | 50.47 | 50.27 | -1 | -0.74412 | -7.4412 | 50.5 | -1 | -1 | -10 | -8.7206 | -8.7206 | 0 | 12 | 1 | 1 | -8.7206 | 10 | 0 | 0
1067 | 50.45 | 50.29 | -1 | -0.84412 | -8.4412 | 50.5 | -1 | -1 | -10 | -9.2206 | -9.2206 | 0 | 12 | 1 | 1 | -9.2206 | 10 | 0 | 0
1067.05 | 50.42 | 50.32 | -1 | -0.94412 | -9.4412 | 50.5 | -1 | -1 | -10 | -9.7206 | -9.7206 | 0 | 12 | 1 | 1 | -9.7206 | 10 | 0 | 0
1067.1 | 50.39 | 50.35 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1067.15 | 50.37 | 50.37 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1067.2 | 50.34 | 50.34 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1067.25 | 50.32 | 50.32 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1067.3 | 50.29 | 50.29 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1067.35 | 50.26 | 50.26 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1067.4 | 50.24 | 50.24 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1067.45 | 50.21 | 50.21 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1067.5 | 50.18 | 50.18 | -0.81 | -0.81 | -8.1 | 50.47 | -1 | -1 | -10 | -9.05 | -9.05 | 0 | 12 | 1 | 1 | -9.05 | 10 | 0 | 0
1067.55 | 50.16 | 50.16 | -0.62 | -0.62 | -6.2 | 50.45 | -1 | -1 | -10 | -8.1 | -8.1 | 0 | 12 | 1 | 1 | -8.1 | 10 | 0 | 0
1067.6 | 50.13 | 50.13 | -0.335 | -0.335 | -3.35 | 50.42 | -1 | -1 | -10 | -6.675 | -6.675 | 0 | 12 | 1 | 1 | -6.675 | 10 | 0 | 0
1067.65 | 50.11 | 50.11 | -0.145 | -0.145 | -1.45 | 50.39 | -1 | -1 | -10 | -5.725 | -5.725 | 0 | 12 | 1 | 1 | -5.725 | 10 | 0 | 0
1067.7 | 50.08 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 50.37 | -1 | -1 | -10 | -5.1912 | -5.1912 | 0 | 12 | 1 | 1 | -5.1912 | 10 | 0 | 0
1067.75 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.34 | -1 | -1 | -10 | -5.1029 | -5.1029 | 0 | 12 | 1 | 1 | -5.1029 | 10 | 0 | 0
1067.8 | 50.03 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 50.32 | -1 | -1 | -10 | -5.0441 | -5.0441 | 0 | 12 | 1 | 1 | -5.0441 | 10 | 0 | 0
1067.85 | 50 | 50 | 0 | 0 | 0 | 50.29 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1067.9 | 50 | 50 | 0 | 0 | 0 | 50.26 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1067.95 | 50 | 50 | 0 | 0 | 0 | 50.24 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1068 | 50 | 50 | 0 | 0 | 0 | 50.21 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1068.05 | 50 | 50 | 0 | 0 | 0 | 50.18 | -0.81 | -0.9 | -9 | -4.5 | -4.5 | 0 | 12 | 1 | 1 | -4.5 | 10 | 0 | 0
1068.1 | 50 | 50 | 0 | 0 | 0 | 50.16 | -0.62 | -0.8 | -8 | -4 | -4 | 0 | 12 | 1 | 1 | -4 | 10 | 0 | 0
1068.15 | 50 | 50 | 0 | 0 | 0 | 50.13 | -0.335 | -0.7 | -7 | -3.5 | -3.5 | 0 | 12 | 1 | 1 | -3.5 | 10 | 0 | 0
1068.2 | 50.01 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.6 | -6 | -3 | -3 | 0 | 12 | 1 | 1 | -3 | 10 | 0 | 0
1068.25 | 50.01 | 50 | 0 | 0 | 0 | 50.08 | -0.038235 | -0.5 | -5 | -2.5 | -2.5 | 0 | 12 | 1 | 1 | -2.5 | 10 | 0 | 0
1068.3 | 49.99 | 49.99 | 0 | 0 | 0 | 50.05 | -0.020588 | -0.4 | -4 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
1068.35 | 49.99 | 49.99 | 0 | 0 | 0 | 50.03 | -0.0088235 | -0.3 | -3 | -1.5 | -1.5 | 0 | 12 | 1 | 1 | -1.5 | 10 | 0 | 0
1068.4 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | -0.2 | -2 | -0.83824 | -0.83824 | 0 | 12 | 1 | 1 | -0.83824 | 10 | 0 | 0
1068.45 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | -0.1 | -1 | -0.33824 | -0.33824 | 0 | 12 | 1 | 1 | -0.33824 | 10 | 0 | 0
1068.5 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
1068.55 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
1068.6 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
1068.65 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
1068.7 | 49.89 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
1068.75 | 49.89 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
1068.8 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50.01 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1068.85 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1068.9 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1068.95 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 2.7868 | 2.7868 | 0 | 12 | 1 | 1 | 2.7868 | 10 | 0 | 0
1069 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 2.7868 | 2.7868 | 0 | 12 | 1 | 1 | 2.7868 | 10 | 0 | 0
1069.05 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 2.8456 | 2.8456 | 0 | 12 | 1 | 1 | 2.8456 | 10 | 0 | 0
1069.1 | 49.94 | 49.85 | 0.525 | 0.525 | 5.25 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 2.7574 | 2.7574 | 0 | 12 | 1 | 1 | 2.7574 | 10 | 0 | 0
1069.15 | 49.94 | 49.85 | 0.525 | 0.525 | 5.25 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 2.7574 | 2.7574 | 0 | 12 | 1 | 1 | 2.7574 | 10 | 0 | 0
1069.2 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1069.25 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1069.3 | 49.93 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1069.35 | 49.93 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1069.4 | 49.96 | 49.85 | 0.525 | 0.525 | 5.25 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 2.6985 | 2.6985 | 0 | 12 | 1 | 1 | 2.6985 | 10 | 0 | 0
1069.45 | 49.96 | 49.85 | 0.525 | 0.525 | 5.25 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 2.6985 | 2.6985 | 0 | 12 | 1 | 1 | 2.6985 | 10 | 0 | 0
1069.5 | 49.99 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1069.55 | 49.99 | 49.91 | 0.044118 | 0.425 | 4.25 | 49.99 | 0 | 0 | 0 | 2.125 | 2.125 | 0 | 12 | 1 | 1 | 2.125 | 10 | 0 | 0
1069.6 | 49.99 | 49.91 | 0.044118 | 0.325 | 3.25 | 49.99 | 0 | 0 | 0 | 1.625 | 1.625 | 0 | 12 | 1 | 1 | 1.625 | 10 | 0 | 0
1069.65 | 49.99 | 49.93 | 0.032353 | 0.225 | 2.25 | 49.99 | 0 | 0 | 0 | 1.125 | 1.125 | 0 | 12 | 1 | 1 | 1.125 | 10 | 0 | 0
1069.7 | 49.96 | 49.93 | 0.032353 | 0.125 | 1.25 | 49.99 | 0 | 0 | 0 | 0.625 | 0.625 | 0 | 12 | 1 | 1 | 0.625 | 10 | 0 | 0
1069.75 | 49.96 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 49.99 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1069.8 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1069.85 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1069.9 | 50.05 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.058824 | 0.058824 | 0 | 12 | 1 | 1 | 0.058824 | 10 | 0 | 0
1069.95 | 50.05 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
1070 | 49.97 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
1070.05 | 49.97 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
1070.1 | 49.92 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1070.15 | 49.92 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1070.2 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1070.25 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1070.3 | 49.94 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1070.35 | 49.94 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1070.4 | 50.01 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1070.45 | 50.01 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1070.5 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1070.55 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
1070.6 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
1070.65 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
1070.7 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
1070.75 | 49.95 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
1070.8 | 49.97 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
1070.85 | 49.97 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
1070.9 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
1070.95 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
1071 | 49.87 | 49.87 | 0.335 | 0.335 | 3.35 | 50.01 | 0 | 0 | 0 | 1.675 | 1.675 | 0 | 12 | 1 | 1 | 1.675 | 10 | 0 | 0
1071.05 | 49.87 | 49.87 | 0.335 | 0.335 | 3.35 | 49.99 | 0 | 0 | 0 | 1.675 | 1.675 | 0 | 12 | 1 | 1 | 1.675 | 10 | 0 | 0
1071.1 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1071.15 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 2.6691 | 2.6691 | 0 | 12 | 1 | 1 | 2.6691 | 10 | 0 | 0
1071.2 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1071.25 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1071.3 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1071.35 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1071.4 | 49.84 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1071.45 | 49.84 | 49.79 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
1071.5 | 49.89 | 49.79 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
1071.55 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.12647 | 1.2647 | 5.6324 | 5.6324 | 0 | 12 | 1 | 1 | 5.6324 | 10 | 0 | 0
1071.6 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.145 | 1.45 | 5.725 | 5.725 | 0 | 12 | 1 | 1 | 5.725 | 10 | 0 | 0
1071.65 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.145 | 1.45 | 5.725 | 5.725 | 0 | 12 | 1 | 1 | 5.725 | 10 | 0 | 0
1071.7 | 49.96 | 49.79 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
1071.75 | 49.96 | 49.79 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
1071.8 | 50.02 | 49.79 | 1 | 1 | 10 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 4.9853 | 4.9853 | 0 | 12 | 1 | 1 | 4.9853 | 10 | 0 | 0
1071.85 | 50.02 | 49.79 | 1 | 1 | 10 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 4.9853 | 4.9853 | 0 | 12 | 1 | 1 | 4.9853 | 10 | 0 | 0
1071.9 | 50.03 | 49.79 | 1 | 1 | 10 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.9559 | 4.9559 | 0 | 12 | 1 | 1 | 4.9559 | 10 | 0 | 0
1071.95 | 50.03 | 49.84 | 0.62 | 0.9 | 9 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.4559 | 4.4559 | 0 | 12 | 1 | 1 | 4.4559 | 10 | 0 | 0
1072 | 50.02 | 49.84 | 0.62 | 0.8 | 8 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 3.9559 | 3.9559 | 0 | 12 | 1 | 1 | 3.9559 | 10 | 0 | 0
1072.05 | 50.02 | 49.89 | 0.145 | 0.7 | 7 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 3.4559 | 3.4559 | 0 | 12 | 1 | 1 | 3.4559 | 10 | 0 | 0
1072.1 | 50.08 | 49.89 | 0.145 | 0.6 | 6 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 2.8088 | 2.8088 | 0 | 12 | 1 | 1 | 2.8088 | 10 | 0 | 0
1072.15 | 50.08 | 49.89 | 0.145 | 0.5 | 5 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 2.3088 | 2.3088 | 0 | 12 | 1 | 1 | 2.3088 | 10 | 0 | 0
1072.2 | 50.01 | 49.89 | 0.145 | 0.4 | 4 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 1.8088 | 1.8088 | 0 | 12 | 1 | 1 | 1.8088 | 10 | 0 | 0
1072.25 | 50.01 | 49.96 | 0.014706 | 0.3 | 3 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 1.3088 | 1.3088 | 0 | 12 | 1 | 1 | 1.3088 | 10 | 0 | 0
1072.3 | 49.94 | 49.94 | 0.026471 | 0.2 | 2 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.80882 | 0.80882 | 0 | 12 | 1 | 1 | 0.80882 | 10 | 0 | 0
1072.35 | 49.94 | 49.94 | 0.026471 | 0.1 | 1 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.30882 | 0.30882 | 0 | 12 | 1 | 1 | 0.30882 | 10 | 0 | 0
1072.4 | 50 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
1072.45 | 50 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
1072.5 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
1072.55 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
1072.6 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1072.65 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1072.7 | 49.92 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1072.75 | 49.92 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
1072.8 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50.01 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1072.85 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1072.9 | 49.92 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1072.95 | 49.92 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1073 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1073.05 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1073.1 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1073.15 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1073.2 | 49.87 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1073.25 | 49.87 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1073.3 | 49.8 | 49.8 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1073.35 | 49.8 | 49.8 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1073.4 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1073.45 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1073.5 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1073.55 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1073.6 | 49.72 | 49.72 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1073.65 | 49.72 | 49.72 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1073.7 | 49.67 | 49.67 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1073.75 | 49.67 | 49.67 | 1 | 1 | 10 | 49.87 | 0.335 | 0.14412 | 1.4412 | 5.7206 | 5.7206 | 0 | 12 | 1 | 1 | 5.7206 | 10 | 0 | 0
1073.8 | 49.65 | 49.65 | 1 | 1 | 10 | 49.87 | 0.335 | 0.24412 | 2.4412 | 6.2206 | 6.2206 | 0 | 12 | 1 | 1 | 6.2206 | 10 | 0 | 0
1073.85 | 49.65 | 49.65 | 1 | 1 | 10 | 49.8 | 1 | 0.34412 | 3.4412 | 6.7206 | 6.7206 | 0 | 12 | 1 | 1 | 6.7206 | 10 | 0 | 0
1073.9 | 49.59 | 49.59 | 1 | 1 | 10 | 49.8 | 1 | 0.44412 | 4.4412 | 7.2206 | 7.2206 | 0 | 12 | 1 | 1 | 7.2206 | 10 | 0 | 0
1073.95 | 49.59 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.54412 | 5.4412 | 7.7206 | 7.7206 | 0 | 12 | 1 | 1 | 7.7206 | 10 | 0 | 0
1074 | 49.66 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.64412 | 6.4412 | 8.2206 | 8.2206 | 0 | 12 | 1 | 1 | 8.2206 | 10 | 0 | 0
1074.05 | 49.66 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.74412 | 7.4412 | 8.7206 | 8.7206 | 0 | 12 | 1 | 1 | 8.7206 | 10 | 0 | 0
1074.1 | 49.63 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.84412 | 8.4412 | 9.2206 | 9.2206 | 0 | 12 | 1 | 1 | 9.2206 | 10 | 0 | 0
1074.15 | 49.63 | 49.59 | 1 | 1 | 10 | 49.72 | 1 | 0.94412 | 9.4412 | 9.7206 | 9.7206 | 0 | 12 | 1 | 1 | 9.7206 | 10 | 0 | 0
1074.2 | 49.61 | 49.59 | 1 | 1 | 10 | 49.72 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1074.25 | 49.61 | 49.59 | 1 | 1 | 10 | 49.67 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1074.3 | 49.54 | 49.54 | 1 | 1 | 10 | 49.67 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1074.35 | 49.54 | 49.54 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1074.4 | 49.46 | 49.46 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1074.45 | 49.46 | 49.46 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1074.5 | 49.45 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1074.55 | 49.45 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1074.6 | 49.51 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1074.65 | 49.51 | 49.45 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1074.7 | 49.5 | 49.45 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1074.75 | 49.5 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1074.8 | 49.54 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1074.85 | 49.54 | 49.45 | 1 | 1 | 10 | 49.54 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1074.9 | 49.59 | 49.45 | 1 | 1 | 10 | 49.59 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1074.95 | 49.59 | 49.45 | 1 | 1 | 10 | 49.59 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1075 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1075.05 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1075.1 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1075.15 | 49.61 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1075.2 | 49.53 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1075.25 | 49.53 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1075.3 | 49.54 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1075.35 | 49.54 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1075.4 | 49.61 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1075.45 | 49.61 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1075.5 | 49.66 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1075.55 | 49.66 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1075.6 | 49.64 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1075.65 | 49.64 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1075.7 | 49.69 | 49.53 | 1 | 1 | 10 | 49.69 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1075.75 | 49.69 | 49.53 | 1 | 1 | 10 | 49.69 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1075.8 | 49.74 | 49.53 | 1 | 1 | 10 | 49.74 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1075.85 | 49.74 | 49.54 | 1 | 1 | 10 | 49.74 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1075.9 | 49.78 | 49.54 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1075.95 | 49.78 | 49.61 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1076 | 49.82 | 49.61 | 1 | 1 | 10 | 49.82 | 0.81 | 0.81 | 8.1 | 9.05 | 9.05 | 0 | 12 | 1 | 1 | 9.05 | 10 | 0 | 0
1076.05 | 49.82 | 49.64 | 1 | 1 | 10 | 49.82 | 0.81 | 0.81 | 8.1 | 9.05 | 9.05 | 0 | 12 | 1 | 1 | 9.05 | 10 | 0 | 0
1076.1 | 49.86 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
1076.15 | 49.86 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
1076.2 | 49.84 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
1076.25 | 49.84 | 49.69 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
1076.3 | 49.91 | 49.69 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1076.35 | 49.91 | 49.74 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1076.4 | 49.97 | 49.74 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1076.45 | 49.97 | 49.78 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1076.5 | 50.03 | 49.78 | 1 | 1 | 10 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.9559 | 4.9559 | 0 | 12 | 1 | 1 | 4.9559 | 10 | 0 | 0
1076.55 | 50.03 | 49.82 | 0.81 | 0.9 | 9 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.4559 | 4.4559 | 0 | 12 | 1 | 1 | 4.4559 | 10 | 0 | 0
1076.6 | 50.05 | 49.82 | 0.81 | 0.81 | 8.1 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 3.9471 | 3.9471 | 0 | 12 | 1 | 1 | 3.9471 | 10 | 0 | 0
1076.65 | 50.05 | 49.84 | 0.62 | 0.71 | 7.1 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 3.4471 | 3.4471 | 0 | 12 | 1 | 1 | 3.4471 | 10 | 0 | 0
1076.7 | 50.01 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
1076.75 | 50.01 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
1076.8 | 49.95 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
1076.85 | 49.95 | 49.91 | 0.044118 | 0.52 | 5.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.4971 | 2.4971 | 0 | 12 | 1 | 1 | 2.4971 | 10 | 0 | 0
1076.9 | 49.99 | 49.91 | 0.044118 | 0.42 | 4.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 1.9971 | 1.9971 | 0 | 12 | 1 | 1 | 1.9971 | 10 | 0 | 0
1076.95 | 49.99 | 49.95 | 0.020588 | 0.32 | 3.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 1.4971 | 1.4971 | 0 | 12 | 1 | 1 | 1.4971 | 10 | 0 | 0
1077 | 49.92 | 49.92 | 0.038235 | 0.22 | 2.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.99706 | 0.99706 | 0 | 12 | 1 | 1 | 0.99706 | 10 | 0 | 0
1077.05 | 49.92 | 49.92 | 0.038235 | 0.12 | 1.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.49706 | 0.49706 | 0 | 12 | 1 | 1 | 0.49706 | 10 | 0 | 0
1077.1 | 49.97 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1077.15 | 49.97 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1077.2 | 50.02 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1077.25 | 50.02 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.17647 | 0.17647 | 0 | 12 | 1 | 1 | 0.17647 | 10 | 0 | 0
1077.3 | 50.07 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1077.35 | 50.07 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1077.4 | 50.06 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1077.45 | 50.06 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1077.5 | 50.13 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
1077.55 | 50.13 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
1077.6 | 50.09 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
1077.65 | 50.09 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6309 | -1.6309 | 0 | 12 | 1 | 1 | -1.6309 | 10 | 0 | 0
1077.7 | 50.07 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6309 | -1.6309 | 0 | 12 | 1 | 1 | -1.6309 | 10 | 0 | 0
1077.75 | 50.07 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6897 | -1.6897 | 0 | 12 | 1 | 1 | -1.6897 | 10 | 0 | 0
1077.8 | 50.07 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6897 | -1.6897 | 0 | 12 | 1 | 1 | -1.6897 | 10 | 0 | 0
1077.85 | 50.07 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.13 | -0.335 | -0.335 | -3.35 | -1.8074 | -1.8074 | 0 | 12 | 1 | 1 | -1.8074 | 10 | 0 | 0
1077.9 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.13 | -0.335 | -0.335 | -3.35 | -1.7779 | -1.7779 | 0 | 12 | 1 | 1 | -1.7779 | 10 | 0 | 0
1077.95 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.13 | -0.335 | -0.335 | -3.35 | -1.7779 | -1.7779 | 0 | 12 | 1 | 1 | -1.7779 | 10 | 0 | 0
1078 | 50.01 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
1078.05 | 50.01 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
1078.1 | 50.07 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
1078.15 | 50.07 | 50.01 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.235 | -2.35 | -1.175 | -1.175 | 0 | 12 | 1 | 1 | -1.175 | 10 | 0 | 0
1078.2 | 50.05 | 50.01 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.135 | -1.35 | -0.675 | -0.675 | 0 | 12 | 1 | 1 | -0.675 | 10 | 0 | 0
1078.25 | 50.05 | 50.01 | 0 | 0 | 0 | 50.07 | -0.032353 | -0.035 | -0.35 | -0.175 | -0.175 | 0 | 12 | 1 | 1 | -0.175 | 10 | 0 | 0
1078.3 | 50.1 | 50.01 | 0 | 0 | 0 | 50.1 | -0.05 | -0.05 | -0.5 | -0.25 | -0.25 | 0 | 12 | 1 | 1 | -0.25 | 10 | 0 | 0
1078.35 | 50.1 | 50.01 | 0 | 0 | 0 | 50.1 | -0.05 | -0.05 | -0.5 | -0.25 | -0.25 | 0 | 12 | 1 | 1 | -0.25 | 10 | 0 | 0
1078.4 | 50.11 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1078.45 | 50.11 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1078.5 | 50.06 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1078.55 | 50.06 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1078.6 | 50.04 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1078.65 | 50.04 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1078.7 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1078.75 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1078.8 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1078.85 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1078.9 | 50.11 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1078.95 | 50.11 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1079 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1079.05 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1079.1 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1079.15 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1079.2 | 50.02 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.11 | -0.145 | -0.145 | -1.45 | -0.73971 | -0.73971 | 0 | 12 | 1 | 1 | -0.73971 | 10 | 0 | 0
1079.25 | 50.02 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.11 | -0.145 | -0.145 | -1.45 | -0.73971 | -0.73971 | 0 | 12 | 1 | 1 | -0.73971 | 10 | 0 | 0
1079.3 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1079.35 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1079.4 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1079.45 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1079.5 | 50.01 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1079.55 | 50.01 | 50 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.045 | -0.45 | -0.225 | -0.225 | 0 | 12 | 1 | 1 | -0.225 | 10 | 0 | 0
1079.6 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
1079.65 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
1079.7 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
1079.75 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1079.8 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.14706 | 0.14706 | 0 | 12 | 1 | 1 | 0.14706 | 10 | 0 | 0
1079.85 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1079.9 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1079.95 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1080 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1080.05 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1080.1 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1080.15 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1080.2 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1080.25 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1080.3 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1080.35 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1080.4 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1080.45 | 50 | 50 | 0 | 0 | 0 | 50.01 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1080.5 | 49.5 | 49.5 | 1 | 1 | 10 | 50.01 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1080.55 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1080.6 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1080.65 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1080.7 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1080.75 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1080.8 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1080.85 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1080.9 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1080.95 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1081 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1081.05 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.1 | 1 | 5.5 | 5.5 | 0 | 12 | 1 | 1 | 5.5 | 10 | 0 | 0
1081.1 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.2 | 2 | 6 | 6 | 0 | 12 | 1 | 1 | 6 | 10 | 0 | 0
1081.15 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.3 | 3 | 6.5 | 6.5 | 0 | 12 | 1 | 1 | 6.5 | 10 | 0 | 0
1081.2 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.4 | 4 | 7 | 7 | 0 | 12 | 1 | 1 | 7 | 10 | 0 | 0
1081.25 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.5 | 5 | 7.5 | 7.5 | 0 | 12 | 1 | 1 | 7.5 | 10 | 0 | 0
1081.3 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.6 | 6 | 8 | 8 | 0 | 12 | 1 | 1 | 8 | 10 | 0 | 0
1081.35 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.7 | 7 | 8.5 | 8.5 | 0 | 12 | 1 | 1 | 8.5 | 10 | 0 | 0
1081.4 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.8 | 8 | 9 | 9 | 0 | 12 | 1 | 1 | 9 | 10 | 0 | 0
1081.45 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.9 | 9 | 9.5 | 9.5 | 0 | 12 | 1 | 1 | 9.5 | 10 | 0 | 0
1081.5 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1081.55 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1081.6 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1081.65 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1081.7 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1081.75 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1081.8 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1081.85 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1081.9 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1081.95 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1082 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1082.05 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1082.1 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1082.15 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1082.2 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1082.25 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1082.3 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1082.35 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1082.4 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1082.45 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1082.5 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1082.55 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1082.6 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1082.65 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1082.7 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1082.75 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1082.8 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1082.85 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1082.9 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1082.95 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1083 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1083.05 | 50.5 | 50.5 | -1 | 0.9 | 9 | 50.5 | -1 | -1 | -10 | -0.5 | -0.5 | 0 | 12 | 1 | 1 | -0.5 | 10 | 0 | 0
1083.1 | 50.5 | 50.5 | -1 | 0.8 | 8 | 50.5 | -1 | -1 | -10 | -1 | -1 | 0 | 12 | 1 | 1 | -1 | 10 | 0 | 0
1083.15 | 50.5 | 50.5 | -1 | 0.7 | 7 | 50.5 | -1 | -1 | -10 | -1.5 | -1.5 | 0 | 12 | 1 | 1 | -1.5 | 10 | 0 | 0
1083.2 | 50.5 | 50.5 | -1 | 0.6 | 6 | 50.5 | -1 | -1 | -10 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
1083.25 | 50.5 | 50.5 | -1 | 0.5 | 5 | 50.5 | -1 | -1 | -10 | -2.5 | -2.5 | 0 | 12 | 1 | 1 | -2.5 | 10 | 0 | 0
1083.3 | 50.5 | 50.5 | -1 | 0.4 | 4 | 50.5 | -1 | -1 | -10 | -3 | -3 | 0 | 12 | 1 | 1 | -3 | 10 | 0 | 0
1083.35 | 50.5 | 50.5 | -1 | 0.3 | 3 | 50.5 | -1 | -1 | -10 | -3.5 | -3.5 | 0 | 12 | 1 | 1 | -3.5 | 10 | 0 | 0
1083.4 | 50.5 | 50.5 | -1 | 0.2 | 2 | 50.5 | -1 | -1 | -10 | -4 | -4 | 0 | 12 | 1 | 1 | -4 | 10 | 0 | 0
1083.45 | 50.5 | 50.5 | -1 | 0.1 | 1 | 50.5 | -1 | -1 | -10 | -4.5 | -4.5 | 0 | 12 | 1 | 1 | -4.5 | 10 | 0 | 0
1083.5 | 50.5 | 50.5 | -1 | 0 | 0 | 50.5 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1083.55 | 50.5 | 50.5 | -1 | -0.1 | -1 | 50.5 | -1 | -1 | -10 | -5.5 | -5.5 | 0 | 12 | 1 | 1 | -5.5 | 10 | 0 | 0
1083.6 | 50.5 | 50.5 | -1 | -0.2 | -2 | 50.5 | -1 | -1 | -10 | -6 | -6 | 0 | 12 | 1 | 1 | -6 | 10 | 0 | 0
1083.65 | 50.5 | 50.5 | -1 | -0.3 | -3 | 50.5 | -1 | -1 | -10 | -6.5 | -6.5 | 0 | 12 | 1 | 1 | -6.5 | 10 | 0 | 0
1083.7 | 50.5 | 50.5 | -1 | -0.4 | -4 | 50.5 | -1 | -1 | -10 | -7 | -7 | 0 | 12 | 1 | 1 | -7 | 10 | 0 | 0
1083.75 | 50.5 | 50.5 | -1 | -0.5 | -5 | 50.5 | -1 | -1 | -10 | -7.5 | -7.5 | 0 | 12 | 1 | 1 | -7.5 | 10 | 0 | 0
1083.8 | 50.5 | 50.5 | -1 | -0.6 | -6 | 50.5 | -1 | -1 | -10 | -8 | -8 | 0 | 12 | 1 | 1 | -8 | 10 | 0 | 0
1083.85 | 50.5 | 50.5 | -1 | -0.7 | -7 | 50.5 | -1 | -1 | -10 | -8.5 | -8.5 | 0 | 12 | 1 | 1 | -8.5 | 10 | 0 | 0
1083.9 | 50.5 | 50.5 | -1 | -0.8 | -8 | 50.5 | -1 | -1 | -10 | -9 | -9 | 0 | 12 | 1 | 1 | -9 | 10 | 0 | 0
1083.95 | 50.5 | 50.5 | -1 | -0.9 | -9 | 50.5 | -1 | -1 | -10 | -9.5 | -9.5 | 0 | 12 | 1 | 1 | -9.5 | 10 | 0 | 0
1084 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1084.05 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1084.1 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1084.15 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1084.2 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1084.25 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1084.3 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1084.35 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1084.4 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1084.45 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1084.5 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1084.55 | 50.47 | 50.47 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1084.6 | 50.45 | 50.45 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1084.65 | 50.42 | 50.42 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1084.7 | 50.4 | 50.4 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1084.75 | 50.37 | 50.37 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1084.8 | 50.35 | 50.35 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1084.85 | 50.32 | 50.32 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1084.9 | 50.29 | 50.29 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1084.95 | 50.27 | 50.27 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1085 | 50.24 | 50.24 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1085.05 | 50.22 | 50.22 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1085.1 | 50.19 | 50.19 | -0.905 | -0.905 | -9.05 | 50.47 | -1 | -1 | -10 | -9.525 | -9.525 | 0 | 12 | 1 | 1 | -9.525 | 10 | 0 | 0
1085.15 | 50.17 | 50.17 | -0.715 | -0.715 | -7.15 | 50.45 | -1 | -1 | -10 | -8.575 | -8.575 | 0 | 12 | 1 | 1 | -8.575 | 10 | 0 | 0
1085.2 | 50.14 | 50.14 | -0.43 | -0.43 | -4.3 | 50.42 | -1 | -1 | -10 | -7.15 | -7.15 | 0 | 12 | 1 | 1 | -7.15 | 10 | 0 | 0
1085.25 | 50.12 | 50.12 | -0.24 | -0.24 | -2.4 | 50.4 | -1 | -1 | -10 | -6.2 | -6.2 | 0 | 12 | 1 | 1 | -6.2 | 10 | 0 | 0
1085.3 | 50.09 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 50.37 | -1 | -1 | -10 | -5.2206 | -5.2206 | 0 | 12 | 1 | 1 | -5.2206 | 10 | 0 | 0
1085.35 | 50.06 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.35 | -1 | -1 | -10 | -5.1324 | -5.1324 | 0 | 12 | 1 | 1 | -5.1324 | 10 | 0 | 0
1085.4 | 50.04 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.32 | -1 | -1 | -10 | -5.0735 | -5.0735 | 0 | 12 | 1 | 1 | -5.0735 | 10 | 0 | 0
1085.45 | 50.01 | 50.01 | 0 | 0 | 0 | 50.29 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1085.5 | 49.99 | 49.99 | 0 | 0 | 0 | 50.27 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1085.55 | 49.96 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.24 | -1 | -1 | -10 | -4.9265 | -4.9265 | 0 | 12 | 1 | 1 | -4.9265 | 10 | 0 | 0
1085.6 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.22 | -1 | -1 | -10 | -4.8676 | -4.8676 | 0 | 12 | 1 | 1 | -4.8676 | 10 | 0 | 0
1085.65 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.19 | -0.905 | -0.905 | -9.05 | -4.3044 | -4.3044 | 0 | 12 | 1 | 1 | -4.3044 | 10 | 0 | 0
1085.7 | 49.88 | 49.88 | 0.24 | 0.24 | 2.4 | 50.17 | -0.715 | -0.805 | -8.05 | -2.825 | -2.825 | 0 | 12 | 1 | 1 | -2.825 | 10 | 0 | 0
1085.75 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.14 | -0.43 | -0.705 | -7.05 | -1.375 | -1.375 | 0 | 12 | 1 | 1 | -1.375 | 10 | 0 | 0
1085.8 | 49.83 | 49.83 | 0.715 | 0.715 | 7.15 | 50.12 | -0.24 | -0.605 | -6.05 | 0.55 | 0.55 | 0 | 12 | 1 | 1 | 0.55 | 10 | 0 | 0
1085.85 | 49.81 | 49.81 | 0.905 | 0.905 | 9.05 | 50.09 | -0.044118 | -0.505 | -5.05 | 2 | 2 | 0 | 12 | 1 | 1 | 2 | 10 | 0 | 0
1085.9 | 49.78 | 49.78 | 1 | 1 | 10 | 50.06 | -0.026471 | -0.405 | -4.05 | 2.975 | 2.975 | 0 | 12 | 1 | 1 | 2.975 | 10 | 0 | 0
1085.95 | 49.76 | 49.76 | 1 | 1 | 10 | 50.04 | -0.014706 | -0.305 | -3.05 | 3.475 | 3.475 | 0 | 12 | 1 | 1 | 3.475 | 10 | 0 | 0
1086 | 49.73 | 49.73 | 1 | 1 | 10 | 50.01 | 0 | -0.205 | -2.05 | 3.975 | 3.975 | 0 | 12 | 1 | 1 | 3.975 | 10 | 0 | 0
1086.05 | 49.71 | 49.71 | 1 | 1 | 10 | 49.99 | 0 | -0.105 | -1.05 | 4.475 | 4.475 | 0 | 12 | 1 | 1 | 4.475 | 10 | 0 | 0
1086.1 | 49.68 | 49.68 | 1 | 1 | 10 | 49.96 | 0.014706 | -0.005 | -0.05 | 4.975 | 4.975 | 0 | 12 | 1 | 1 | 4.975 | 10 | 0 | 0
1086.15 | 49.65 | 49.65 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
1086.2 | 49.63 | 49.63 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1086.25 | 49.6 | 49.6 | 1 | 1 | 10 | 49.88 | 0.24 | 0.14412 | 1.4412 | 5.7206 | 5.7206 | 0 | 12 | 1 | 1 | 5.7206 | 10 | 0 | 0
1086.3 | 49.58 | 49.58 | 1 | 1 | 10 | 49.86 | 0.43 | 0.24412 | 2.4412 | 6.2206 | 6.2206 | 0 | 12 | 1 | 1 | 6.2206 | 10 | 0 | 0
1086.35 | 49.55 | 49.55 | 1 | 1 | 10 | 49.83 | 0.715 | 0.34412 | 3.4412 | 6.7206 | 6.7206 | 0 | 12 | 1 | 1 | 6.7206 | 10 | 0 | 0
1086.4 | 49.53 | 49.53 | 1 | 1 | 10 | 49.81 | 0.905 | 0.44412 | 4.4412 | 7.2206 | 7.2206 | 0 | 12 | 1 | 1 | 7.2206 | 10 | 0 | 0
1086.45 | 49.5 | 49.5 | 1 | 1 | 10 | 49.78 | 1 | 0.54412 | 5.4412 | 7.7206 | 7.7206 | 0 | 12 | 1 | 1 | 7.7206 | 10 | 0 | 0
1086.5 | 49.5 | 49.5 | 1 | 1 | 10 | 49.76 | 1 | 0.64412 | 6.4412 | 8.2206 | 8.2206 | 0 | 12 | 1 | 1 | 8.2206 | 10 | 0 | 0
1086.55 | 49.53 | 49.5 | 1 | 1 | 10 | 49.73 | 1 | 0.74412 | 7.4412 | 8.7206 | 8.7206 | 0 | 12 | 1 | 1 | 8.7206 | 10 | 0 | 0
1086.6 | 49.55 | 49.5 | 1 | 1 | 10 | 49.71 | 1 | 0.84412 | 8.4412 | 9.2206 | 9.2206 | 0 | 12 | 1 | 1 | 9.2206 | 10 | 0 | 0
1086.65 | 49.58 | 49.5 | 1 | 1 | 10 | 49.68 | 1 | 0.94412 | 9.4412 | 9.7206 | 9.7206 | 0 | 12 | 1 | 1 | 9.7206 | 10 | 0 | 0
1086.7 | 49.6 | 49.5 | 1 | 1 | 10 | 49.65 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1086.75 | 49.63 | 49.5 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1086.8 | 49.65 | 49.5 | 1 | 1 | 10 | 49.65 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1086.85 | 49.68 | 49.5 | 1 | 1 | 10 | 49.68 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1086.9 | 49.71 | 49.5 | 1 | 1 | 10 | 49.71 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1086.95 | 49.73 | 49.5 | 1 | 1 | 10 | 49.73 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1087 | 49.76 | 49.5 | 1 | 1 | 10 | 49.76 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1087.05 | 49.78 | 49.5 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1087.1 | 49.81 | 49.53 | 1 | 1 | 10 | 49.81 | 0.905 | 0.905 | 9.05 | 9.525 | 9.525 | 0 | 12 | 1 | 1 | 9.525 | 10 | 0 | 0
1087.15 | 49.83 | 49.55 | 1 | 1 | 10 | 49.83 | 0.715 | 0.715 | 7.15 | 8.575 | 8.575 | 0 | 12 | 1 | 1 | 8.575 | 10 | 0 | 0
1087.2 | 49.86 | 49.58 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
1087.25 | 49.88 | 49.6 | 1 | 1 | 10 | 49.88 | 0.24 | 0.24 | 2.4 | 6.2 | 6.2 | 0 | 12 | 1 | 1 | 6.2 | 10 | 0 | 0
1087.3 | 49.91 | 49.63 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1087.35 | 49.94 | 49.65 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
1087.4 | 49.96 | 49.68 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
1087.45 | 49.99 | 49.71 | 1 | 1 | 10 | 49.99 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1087.5 | 50.01 | 49.73 | 1 | 1 | 10 | 50.01 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1087.55 | 50.04 | 49.76 | 1 | 1 | 10 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 4.9265 | 4.9265 | 0 | 12 | 1 | 1 | 4.9265 | 10 | 0 | 0
1087.6 | 50.06 | 49.78 | 1 | 1 | 10 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 4.8676 | 4.8676 | 0 | 12 | 1 | 1 | 4.8676 | 10 | 0 | 0
1087.65 | 50.09 | 49.81 | 0.905 | 0.905 | 9.05 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 4.3044 | 4.3044 | 0 | 12 | 1 | 1 | 4.3044 | 10 | 0 | 0
1087.7 | 50.12 | 49.83 | 0.715 | 0.805 | 8.05 | 50.12 | -0.24 | -0.24 | -2.4 | 2.825 | 2.825 | 0 | 12 | 1 | 1 | 2.825 | 10 | 0 | 0
1087.75 | 50.14 | 49.86 | 0.43 | 0.705 | 7.05 | 50.14 | -0.43 | -0.43 | -4.3 | 1.375 | 1.375 | 0 | 12 | 1 | 1 | 1.375 | 10 | 0 | 0
1087.8 | 50.17 | 49.88 | 0.24 | 0.605 | 6.05 | 50.17 | -0.715 | -0.715 | -7.15 | -0.55 | -0.55 | 0 | 12 | 1 | 1 | -0.55 | 10 | 0 | 0
1087.85 | 50.19 | 49.91 | 0.044118 | 0.505 | 5.05 | 50.19 | -0.905 | -0.905 | -9.05 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
1087.9 | 50.22 | 49.94 | 0.026471 | 0.405 | 4.05 | 50.22 | -1 | -1 | -10 | -2.975 | -2.975 | 0 | 12 | 1 | 1 | -2.975 | 10 | 0 | 0
1087.95 | 50.24 | 49.96 | 0.014706 | 0.305 | 3.05 | 50.24 | -1 | -1 | -10 | -3.475 | -3.475 | 0 | 12 | 1 | 1 | -3.475 | 10 | 0 | 0
1088 | 50.27 | 49.99 | 0 | 0.205 | 2.05 | 50.27 | -1 | -1 | -10 | -3.975 | -3.975 | 0 | 12 | 1 | 1 | -3.975 | 10 | 0 | 0
1088.05 | 50.29 | 50.01 | 0 | 0.105 | 1.05 | 50.29 | -1 | -1 | -10 | -4.475 | -4.475 | 0 | 12 | 1 | 1 | -4.475 | 10 | 0 | 0
1088.1 | 50.32 | 50.04 | -0.014706 | 0.005 | 0.05 | 50.32 | -1 | -1 | -10 | -4.975 | -4.975 | 0 | 12 | 1 | 1 | -4.975 | 10 | 0 | 0
1088.15 | 50.35 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.35 | -1 | -1 | -10 | -5.1324 | -5.1324 | 0 | 12 | 1 | 1 | -5.1324 | 10 | 0 | 0
1088.2 | 50.37 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 50.37 | -1 | -1 | -10 | -5.2206 | -5.2206 | 0 | 12 | 1 | 1 | -5.2206 | 10 | 0 | 0
1088.25 | 50.4 | 50.12 | -0.24 | -0.14412 | -1.4412 | 50.4 | -1 | -1 | -10 | -5.7206 | -5.7206 | 0 | 12 | 1 | 1 | -5.7206 | 10 | 0 | 0
1088.3 | 50.42 | 50.14 | -0.43 | -0.24412 | -2.4412 | 50.42 | -1 | -1 | -10 | -6.2206 | -6.2206 | 0 | 12 | 1 | 1 | -6.2206 | 10 | 0 | 0
1088.35 | 50.45 | 50.17 | -0.715 | -0.34412 | -3.4412 | 50.45 | -1 | -1 | -10 | -6.7206 | -6.7206 | 0 | 12 | 1 | 1 | -6.7206 | 10 | 0 | 0
1088.4 | 50.47 | 50.19 | -0.905 | -0.44412 | -4.4412 | 50.47 | -1 | -1 | -10 | -7.2206 | -7.2206 | 0 | 12 | 1 | 1 | -7.2206 | 10 | 0 | 0
1088.45 | 50.5 | 50.22 | -1 | -0.54412 | -5.4412 | 50.5 | -1 | -1 | -10 | -7.7206 | -7.7206 | 0 | 12 | 1 | 1 | -7.7206 | 10 | 0 | 0
1088.5 | 50.5 | 50.24 | -1 | -0.64412 | -6.4412 | 50.5 | -1 | -1 | -10 | -8.2206 | -8.2206 | 0 | 12 | 1 | 1 | -8.2206 | 10 | 0 | 0
1088.55 | 50.47 | 50.27 | -1 | -0.74412 | -7.4412 | 50.5 | -1 | -1 | -10 | -8.7206 | -8.7206 | 0 | 12 | 1 | 1 | -8.7206 | 10 | 0 | 0
1088.6 | 50.45 | 50.29 | -1 | -0.84412 | -8.4412 | 50.5 | -1 | -1 | -10 | -9.2206 | -9.2206 | 0 | 12 | 1 | 1 | -9.2206 | 10 | 0 | 0
1088.65 | 50.42 | 50.32 | -1 | -0.94412 | -9.4412 | 50.5 | -1 | -1 | -10 | -9.7206 | -9.7206 | 0 | 12 | 1 | 1 | -9.7206 | 10 | 0 | 0
1088.7 | 50.39 | 50.35 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1088.75 | 50.37 | 50.37 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1088.8 | 50.34 | 50.34 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1088.85 | 50.32 | 50.32 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1088.9 | 50.29 | 50.29 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1088.95 | 50.26 | 50.26 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1089 | 50.24 | 50.24 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1089.05 | 50.21 | 50.21 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1089.1 | 50.18 | 50.18 | -0.81 | -0.81 | -8.1 | 50.47 | -1 | -1 | -10 | -9.05 | -9.05 | 0 | 12 | 1 | 1 | -9.05 | 10 | 0 | 0
1089.15 | 50.16 | 50.16 | -0.62 | -0.62 | -6.2 | 50.45 | -1 | -1 | -10 | -8.1 | -8.1 | 0 | 12 | 1 | 1 | -8.1 | 10 | 0 | 0
1089.2 | 50.13 | 50.13 | -0.335 | -0.335 | -3.35 | 50.42 | -1 | -1 | -10 | -6.675 | -6.675 | 0 | 12 | 1 | 1 | -6.675 | 10 | 0 | 0
1089.25 | 50.11 | 50.11 | -0.145 | -0.145 | -1.45 | 50.39 | -1 | -1 | -10 | -5.725 | -5.725 | 0 | 12 | 1 | 1 | -5.725 | 10 | 0 | 0
1089.3 | 50.08 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 50.37 | -1 | -1 | -10 | -5.1912 | -5.1912 | 0 | 12 | 1 | 1 | -5.1912 | 10 | 0 | 0
1089.35 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.34 | -1 | -1 | -10 | -5.1029 | -5.1029 | 0 | 12 | 1 | 1 | -5.1029 | 10 | 0 | 0
1089.4 | 50.03 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 50.32 | -1 | -1 | -10 | -5.0441 | -5.0441 | 0 | 12 | 1 | 1 | -5.0441 | 10 | 0 | 0
1089.45 | 50 | 50 | 0 | 0 | 0 | 50.29 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1089.5 | 50 | 50 | 0 | 0 | 0 | 50.26 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1089.55 | 50 | 50 | 0 | 0 | 0 | 50.24 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1089.6 | 50 | 50 | 0 | 0 | 0 | 50.21 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1089.65 | 50 | 50 | 0 | 0 | 0 | 50.18 | -0.81 | -0.9 | -9 | -4.5 | -4.5 | 0 | 12 | 1 | 1 | -4.5 | 10 | 0 | 0
1089.7 | 50 | 50 | 0 | 0 | 0 | 50.16 | -0.62 | -0.8 | -8 | -4 | -4 | 0 | 12 | 1 | 1 | -4 | 10 | 0 | 0
1089.75 | 50 | 50 | 0 | 0 | 0 | 50.13 | -0.335 | -0.7 | -7 | -3.5 | -3.5 | 0 | 12 | 1 | 1 | -3.5 | 10 | 0 | 0
1089.8 | 50.01 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.6 | -6 | -3 | -3 | 0 | 12 | 1 | 1 | -3 | 10 | 0 | 0
1089.85 | 50.01 | 50 | 0 | 0 | 0 | 50.08 | -0.038235 | -0.5 | -5 | -2.5 | -2.5 | 0 | 12 | 1 | 1 | -2.5 | 10 | 0 | 0
1089.9 | 49.99 | 49.99 | 0 | 0 | 0 | 50.05 | -0.020588 | -0.4 | -4 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
1089.95 | 49.99 | 49.99 | 0 | 0 | 0 | 50.03 | -0.0088235 | -0.3 | -3 | -1.5 | -1.5 | 0 | 12 | 1 | 1 | -1.5 | 10 | 0 | 0
1090 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | -0.2 | -2 | -0.83824 | -0.83824 | 0 | 12 | 1 | 1 | -0.83824 | 10 | 0 | 0
1090.05 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | -0.1 | -1 | -0.33824 | -0.33824 | 0 | 12 | 1 | 1 | -0.33824 | 10 | 0 | 0
1090.1 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
1090.15 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
1090.2 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
1090.25 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
1090.3 | 49.89 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
1090.35 | 49.89 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
1090.4 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50.01 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1090.45 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1090.5 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1090.55 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 2.7868 | 2.7868 | 0 | 12 | 1 | 1 | 2.7868 | 10 | 0 | 0
1090.6 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 2.7868 | 2.7868 | 0 | 12 | 1 | 1 | 2.7868 | 10 | 0 | 0
1090.65 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 2.8456 | 2.8456 | 0 | 12 | 1 | 1 | 2.8456 | 10 | 0 | 0
1090.7 | 49.94 | 49.85 | 0.525 | 0.525 | 5.25 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 2.7574 | 2.7574 | 0 | 12 | 1 | 1 | 2.7574 | 10 | 0 | 0
1090.75 | 49.94 | 49.85 | 0.525 | 0.525 | 5.25 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 2.7574 | 2.7574 | 0 | 12 | 1 | 1 | 2.7574 | 10 | 0 | 0
1090.8 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1090.85 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1090.9 | 49.93 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1090.95 | 49.93 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1091 | 49.96 | 49.85 | 0.525 | 0.525 | 5.25 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 2.6985 | 2.6985 | 0 | 12 | 1 | 1 | 2.6985 | 10 | 0 | 0
1091.05 | 49.96 | 49.85 | 0.525 | 0.525 | 5.25 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 2.6985 | 2.6985 | 0 | 12 | 1 | 1 | 2.6985 | 10 | 0 | 0
1091.1 | 49.99 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1091.15 | 49.99 | 49.91 | 0.044118 | 0.425 | 4.25 | 49.99 | 0 | 0 | 0 | 2.125 | 2.125 | 0 | 12 | 1 | 1 | 2.125 | 10 | 0 | 0
1091.2 | 49.99 | 49.91 | 0.044118 | 0.325 | 3.25 | 49.99 | 0 | 0 | 0 | 1.625 | 1.625 | 0 | 12 | 1 | 1 | 1.625 | 10 | 0 | 0
1091.25 | 49.99 | 49.93 | 0.032353 | 0.225 | 2.25 | 49.99 | 0 | 0 | 0 | 1.125 | 1.125 | 0 | 12 | 1 | 1 | 1.125 | 10 | 0 | 0
1091.3 | 49.96 | 49.93 | 0.032353 | 0.125 | 1.25 | 49.99 | 0 | 0 | 0 | 0.625 | 0.625 | 0 | 12 | 1 | 1 | 0.625 | 10 | 0 | 0
1091.35 | 49.96 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 49.99 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1091.4 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1091.45 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1091.5 | 50.05 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.058824 | 0.058824 | 0 | 12 | 1 | 1 | 0.058824 | 10 | 0 | 0
1091.55 | 50.05 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
1091.6 | 49.97 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
1091.65 | 49.97 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
1091.7 | 49.92 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1091.75 | 49.92 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1091.8 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1091.85 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1091.9 | 49.94 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1091.95 | 49.94 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1092 | 50.01 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1092.05 | 50.01 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1092.1 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1092.15 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
1092.2 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
1092.25 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
1092.3 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
1092.35 | 49.95 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
1092.4 | 49.97 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
1092.45 | 49.97 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
1092.5 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
1092.55 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
1092.6 | 49.87 | 49.87 | 0.335 | 0.335 | 3.35 | 50.01 | 0 | 0 | 0 | 1.675 | 1.675 | 0 | 12 | 1 | 1 | 1.675 | 10 | 0 | 0
1092.65 | 49.87 | 49.87 | 0.335 | 0.335 | 3.35 | 49.99 | 0 | 0 | 0 | 1.675 | 1.675 | 0 | 12 | 1 | 1 | 1.675 | 10 | 0 | 0
1092.7 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1092.75 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 2.6691 | 2.6691 | 0 | 12 | 1 | 1 | 2.6691 | 10 | 0 | 0
1092.8 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1092.85 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1092.9 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1092.95 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1093 | 49.84 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1093.05 | 49.84 | 49.79 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
1093.1 | 49.89 | 49.79 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
1093.15 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.12647 | 1.2647 | 5.6324 | 5.6324 | 0 | 12 | 1 | 1 | 5.6324 | 10 | 0 | 0
1093.2 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.145 | 1.45 | 5.725 | 5.725 | 0 | 12 | 1 | 1 | 5.725 | 10 | 0 | 0
1093.25 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.145 | 1.45 | 5.725 | 5.725 | 0 | 12 | 1 | 1 | 5.725 | 10 | 0 | 0
1093.3 | 49.96 | 49.79 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
1093.35 | 49.96 | 49.79 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
1093.4 | 50.02 | 49.79 | 1 | 1 | 10 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 4.9853 | 4.9853 | 0 | 12 | 1 | 1 | 4.9853 | 10 | 0 | 0
1093.45 | 50.02 | 49.79 | 1 | 1 | 10 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 4.9853 | 4.9853 | 0 | 12 | 1 | 1 | 4.9853 | 10 | 0 | 0
1093.5 | 50.03 | 49.79 | 1 | 1 | 10 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.9559 | 4.9559 | 0 | 12 | 1 | 1 | 4.9559 | 10 | 0 | 0
1093.55 | 50.03 | 49.84 | 0.62 | 0.9 | 9 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.4559 | 4.4559 | 0 | 12 | 1 | 1 | 4.4559 | 10 | 0 | 0
1093.6 | 50.02 | 49.84 | 0.62 | 0.8 | 8 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 3.9559 | 3.9559 | 0 | 12 | 1 | 1 | 3.9559 | 10 | 0 | 0
1093.65 | 50.02 | 49.89 | 0.145 | 0.7 | 7 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 3.4559 | 3.4559 | 0 | 12 | 1 | 1 | 3.4559 | 10 | 0 | 0
1093.7 | 50.08 | 49.89 | 0.145 | 0.6 | 6 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 2.8088 | 2.8088 | 0 | 12 | 1 | 1 | 2.8088 | 10 | 0 | 0
1093.75 | 50.08 | 49.89 | 0.145 | 0.5 | 5 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 2.3088 | 2.3088 | 0 | 12 | 1 | 1 | 2.3088 | 10 | 0 | 0
1093.8 | 50.01 | 49.89 | 0.145 | 0.4 | 4 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 1.8088 | 1.8088 | 0 | 12 | 1 | 1 | 1.8088 | 10 | 0 | 0
1093.85 | 50.01 | 49.96 | 0.014706 | 0.3 | 3 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 1.3088 | 1.3088 | 0 | 12 | 1 | 1 | 1.3088 | 10 | 0 | 0
1093.9 | 49.94 | 49.94 | 0.026471 | 0.2 | 2 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.80882 | 0.80882 | 0 | 12 | 1 | 1 | 0.80882 | 10 | 0 | 0
1093.95 | 49.94 | 49.94 | 0.026471 | 0.1 | 1 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.30882 | 0.30882 | 0 | 12 | 1 | 1 | 0.30882 | 10 | 0 | 0
1094 | 50 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
1094.05 | 50 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
1094.1 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
1094.15 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
1094.2 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1094.25 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1094.3 | 49.92 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1094.35 | 49.92 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
1094.4 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50.01 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1094.45 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1094.5 | 49.92 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1094.55 | 49.92 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1094.6 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1094.65 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1094.7 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1094.75 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1094.8 | 49.87 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1094.85 | 49.87 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1094.9 | 49.8 | 49.8 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1094.95 | 49.8 | 49.8 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1095 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1095.05 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1095.1 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1095.15 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1095.2 | 49.72 | 49.72 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1095.25 | 49.72 | 49.72 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1095.3 | 49.67 | 49.67 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1095.35 | 49.67 | 49.67 | 1 | 1 | 10 | 49.87 | 0.335 | 0.14412 | 1.4412 | 5.7206 | 5.7206 | 0 | 12 | 1 | 1 | 5.7206 | 10 | 0 | 0
1095.4 | 49.65 | 49.65 | 1 | 1 | 10 | 49.87 | 0.335 | 0.24412 | 2.4412 | 6.2206 | 6.2206 | 0 | 12 | 1 | 1 | 6.2206 | 10 | 0 | 0
1095.45 | 49.65 | 49.65 | 1 | 1 | 10 | 49.8 | 1 | 0.34412 | 3.4412 | 6.7206 | 6.7206 | 0 | 12 | 1 | 1 | 6.7206 | 10 | 0 | 0
1095.5 | 49.59 | 49.59 | 1 | 1 | 10 | 49.8 | 1 | 0.44412 | 4.4412 | 7.2206 | 7.2206 | 0 | 12 | 1 | 1 | 7.2206 | 10 | 0 | 0
1095.55 | 49.59 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.54412 | 5.4412 | 7.7206 | 7.7206 | 0 | 12 | 1 | 1 | 7.7206 | 10 | 0 | 0
1095.6 | 49.66 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.64412 | 6.4412 | 8.2206 | 8.2206 | 0 | 12 | 1 | 1 | 8.2206 | 10 | 0 | 0
1095.65 | 49.66 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.74412 | 7.4412 | 8.7206 | 8.7206 | 0 | 12 | 1 | 1 | 8.7206 | 10 | 0 | 0
1095.7 | 49.63 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.84412 | 8.4412 | 9.2206 | 9.2206 | 0 | 12 | 1 | 1 | 9.2206 | 10 | 0 | 0
1095.75 | 49.63 | 49.59 | 1 | 1 | 10 | 49.72 | 1 | 0.94412 | 9.4412 | 9.7206 | 9.7206 | 0 | 12 | 1 | 1 | 9.7206 | 10 | 0 | 0
1095.8 | 49.61 | 49.59 | 1 | 1 | 10 | 49.72 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1095.85 | 49.61 | 49.59 | 1 | 1 | 10 | 49.67 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1095.9 | 49.54 | 49.54 | 1 | 1 | 10 | 49.67 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1095.95 | 49.54 | 49.54 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1096 | 49.46 | 49.46 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1096.05 | 49.46 | 49.46 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1096.1 | 49.45 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1096.15 | 49.45 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1096.2 | 49.51 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1096.25 | 49.51 | 49.45 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1096.3 | 49.5 | 49.45 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1096.35 | 49.5 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1096.4 | 49.54 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1096.45 | 49.54 | 49.45 | 1 | 1 | 10 | 49.54 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1096.5 | 49.59 | 49.45 | 1 | 1 | 10 | 49.59 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1096.55 | 49.59 | 49.45 | 1 | 1 | 10 | 49.59 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1096.6 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1096.65 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1096.7 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1096.75 | 49.61 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1096.8 | 49.53 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1096.85 | 49.53 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1096.9 | 49.54 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1096.95 | 49.54 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1097 | 49.61 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1097.05 | 49.61 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1097.1 | 49.66 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1097.15 | 49.66 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1097.2 | 49.64 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1097.25 | 49.64 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1097.3 | 49.69 | 49.53 | 1 | 1 | 10 | 49.69 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1097.35 | 49.69 | 49.53 | 1 | 1 | 10 | 49.69 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1097.4 | 49.74 | 49.53 | 1 | 1 | 10 | 49.74 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1097.45 | 49.74 | 49.54 | 1 | 1 | 10 | 49.74 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1097.5 | 49.78 | 49.54 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1097.55 | 49.78 | 49.61 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1097.6 | 49.82 | 49.61 | 1 | 1 | 10 | 49.82 | 0.81 | 0.81 | 8.1 | 9.05 | 9.05 | 0 | 12 | 1 | 1 | 9.05 | 10 | 0 | 0
1097.65 | 49.82 | 49.64 | 1 | 1 | 10 | 49.82 | 0.81 | 0.81 | 8.1 | 9.05 | 9.05 | 0 | 12 | 1 | 1 | 9.05 | 10 | 0 | 0
1097.7 | 49.86 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
1097.75 | 49.86 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
1097.8 | 49.84 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
1097.85 | 49.84 | 49.69 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
1097.9 | 49.91 | 49.69 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1097.95 | 49.91 | 49.74 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1098 | 49.97 | 49.74 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1098.05 | 49.97 | 49.78 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1098.1 | 50.03 | 49.78 | 1 | 1 | 10 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.9559 | 4.9559 | 0 | 12 | 1 | 1 | 4.9559 | 10 | 0 | 0
1098.15 | 50.03 | 49.82 | 0.81 | 0.9 | 9 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.4559 | 4.4559 | 0 | 12 | 1 | 1 | 4.4559 | 10 | 0 | 0
1098.2 | 50.05 | 49.82 | 0.81 | 0.81 | 8.1 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 3.9471 | 3.9471 | 0 | 12 | 1 | 1 | 3.9471 | 10 | 0 | 0
1098.25 | 50.05 | 49.84 | 0.62 | 0.71 | 7.1 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 3.4471 | 3.4471 | 0 | 12 | 1 | 1 | 3.4471 | 10 | 0 | 0
1098.3 | 50.01 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
1098.35 | 50.01 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
1098.4 | 49.95 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
1098.45 | 49.95 | 49.91 | 0.044118 | 0.52 | 5.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.4971 | 2.4971 | 0 | 12 | 1 | 1 | 2.4971 | 10 | 0 | 0
1098.5 | 49.99 | 49.91 | 0.044118 | 0.42 | 4.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 1.9971 | 1.9971 | 0 | 12 | 1 | 1 | 1.9971 | 10 | 0 | 0
1098.55 | 49.99 | 49.95 | 0.020588 | 0.32 | 3.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 1.4971 | 1.4971 | 0 | 12 | 1 | 1 | 1.4971 | 10 | 0 | 0
1098.6 | 49.92 | 49.92 | 0.038235 | 0.22 | 2.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.99706 | 0.99706 | 0 | 12 | 1 | 1 | 0.99706 | 10 | 0 | 0
1098.65 | 49.92 | 49.92 | 0.038235 | 0.12 | 1.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.49706 | 0.49706 | 0 | 12 | 1 | 1 | 0.49706 | 10 | 0 | 0
1098.7 | 49.97 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1098.75 | 49.97 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1098.8 | 50.02 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1098.85 | 50.02 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.17647 | 0.17647 | 0 | 12 | 1 | 1 | 0.17647 | 10 | 0 | 0
1098.9 | 50.07 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1098.95 | 50.07 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1099 | 50.06 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1099.05 | 50.06 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1099.1 | 50.13 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
1099.15 | 50.13 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
1099.2 | 50.09 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
1099.25 | 50.09 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6309 | -1.6309 | 0 | 12 | 1 | 1 | -1.6309 | 10 | 0 | 0
1099.3 | 50.07 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6309 | -1.6309 | 0 | 12 | 1 | 1 | -1.6309 | 10 | 0 | 0
1099.35 | 50.07 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6897 | -1.6897 | 0 | 12 | 1 | 1 | -1.6897 | 10 | 0 | 0
1099.4 | 50.07 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6897 | -1.6897 | 0 | 12 | 1 | 1 | -1.6897 | 10 | 0 | 0
1099.45 | 50.07 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.13 | -0.335 | -0.335 | -3.35 | -1.8074 | -1.8074 | 0 | 12 | 1 | 1 | -1.8074 | 10 | 0 | 0
1099.5 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.13 | -0.335 | -0.335 | -3.35 | -1.7779 | -1.7779 | 0 | 12 | 1 | 1 | -1.7779 | 10 | 0 | 0
1099.55 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.13 | -0.335 | -0.335 | -3.35 | -1.7779 | -1.7779 | 0 | 12 | 1 | 1 | -1.7779 | 10 | 0 | 0
1099.6 | 50.01 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
1099.65 | 50.01 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
1099.7 | 50.07 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
1099.75 | 50.07 | 50.01 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.235 | -2.35 | -1.175 | -1.175 | 0 | 12 | 1 | 1 | -1.175 | 10 | 0 | 0
1099.8 | 50.05 | 50.01 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.135 | -1.35 | -0.675 | -0.675 | 0 | 12 | 1 | 1 | -0.675 | 10 | 0 | 0
1099.85 | 50.05 | 50.01 | 0 | 0 | 0 | 50.07 | -0.032353 | -0.035 | -0.35 | -0.175 | -0.175 | 0 | 12 | 1 | 1 | -0.175 | 10 | 0 | 0
1099.9 | 50.1 | 50.01 | 0 | 0 | 0 | 50.1 | -0.05 | -0.05 | -0.5 | -0.25 | -0.25 | 0 | 12 | 1 | 1 | -0.25 | 10 | 0 | 0
1099.95 | 50.1 | 50.01 | 0 | 0 | 0 | 50.1 | -0.05 | -0.05 | -0.5 | -0.25 | -0.25 | 0 | 12 | 1 | 1 | -0.25 | 10 | 0 | 0
1100 | 50.11 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1100.05 | 50.11 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1100.1 | 50.06 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1100.15 | 50.06 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1100.2 | 50.04 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1100.25 | 50.04 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1100.3 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1100.35 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1100.4 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1100.45 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1100.5 | 50.11 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1100.55 | 50.11 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1100.6 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1100.65 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1100.7 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1100.75 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1100.8 | 50.02 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.11 | -0.145 | -0.145 | -1.45 | -0.73971 | -0.73971 | 0 | 12 | 1 | 1 | -0.73971 | 10 | 0 | 0
1100.85 | 50.02 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.11 | -0.145 | -0.145 | -1.45 | -0.73971 | -0.73971 | 0 | 12 | 1 | 1 | -0.73971 | 10 | 0 | 0
1100.9 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1100.95 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1101 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1101.05 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1101.1 | 50.01 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1101.15 | 50.01 | 50 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.045 | -0.45 | -0.225 | -0.225 | 0 | 12 | 1 | 1 | -0.225 | 10 | 0 | 0
1101.2 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
1101.25 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
1101.3 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
1101.35 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1101.4 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.14706 | 0.14706 | 0 | 12 | 1 | 1 | 0.14706 | 10 | 0 | 0
1101.45 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1101.5 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1101.55 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1101.6 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1101.65 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1101.7 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1101.75 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1101.8 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1101.85 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1101.9 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1101.95 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1102 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1102.05 | 50 | 50 | 0 | 0 | 0 | 50.01 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1102.1 | 49.5 | 49.5 | 1 | 1 | 10 | 50.01 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1102.15 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1102.2 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1102.25 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1102.3 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1102.35 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1102.4 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1102.45 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1102.5 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1102.55 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1102.6 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1102.65 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.1 | 1 | 5.5 | 5.5 | 0 | 12 | 1 | 1 | 5.5 | 10 | 0 | 0
1102.7 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.2 | 2 | 6 | 6 | 0 | 12 | 1 | 1 | 6 | 10 | 0 | 0
1102.75 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.3 | 3 | 6.5 | 6.5 | 0 | 12 | 1 | 1 | 6.5 | 10 | 0 | 0
1102.8 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.4 | 4 | 7 | 7 | 0 | 12 | 1 | 1 | 7 | 10 | 0 | 0
1102.85 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.5 | 5 | 7.5 | 7.5 | 0 | 12 | 1 | 1 | 7.5 | 10 | 0 | 0
1102.9 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.6 | 6 | 8 | 8 | 0 | 12 | 1 | 1 | 8 | 10 | 0 | 0
1102.95 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.7 | 7 | 8.5 | 8.5 | 0 | 12 | 1 | 1 | 8.5 | 10 | 0 | 0
1103 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.8 | 8 | 9 | 9 | 0 | 12 | 1 | 1 | 9 | 10 | 0 | 0
1103.05 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.9 | 9 | 9.5 | 9.5 | 0 | 12 | 1 | 1 | 9.5 | 10 | 0 | 0
1103.1 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1103.15 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1103.2 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1103.25 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1103.3 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1103.35 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1103.4 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1103.45 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1103.5 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1103.55 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1103.6 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1103.65 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1103.7 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1103.75 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1103.8 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1103.85 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1103.9 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1103.95 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1104 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1104.05 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1104.1 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1104.15 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1104.2 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1104.25 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1104.3 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1104.35 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1104.4 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1104.45 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1104.5 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1104.55 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1104.6 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1104.65 | 50.5 | 50.5 | -1 | 0.9 | 9 | 50.5 | -1 | -1 | -10 | -0.5 | -0.5 | 0 | 12 | 1 | 1 | -0.5 | 10 | 0 | 0
1104.7 | 50.5 | 50.5 | -1 | 0.8 | 8 | 50.5 | -1 | -1 | -10 | -1 | -1 | 0 | 12 | 1 | 1 | -1 | 10 | 0 | 0
1104.75 | 50.5 | 50.5 | -1 | 0.7 | 7 | 50.5 | -1 | -1 | -10 | -1.5 | -1.5 | 0 | 12 | 1 | 1 | -1.5 | 10 | 0 | 0
1104.8 | 50.5 | 50.5 | -1 | 0.6 | 6 | 50.5 | -1 | -1 | -10 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
1104.85 | 50.5 | 50.5 | -1 | 0.5 | 5 | 50.5 | -1 | -1 | -10 | -2.5 | -2.5 | 0 | 12 | 1 | 1 | -2.5 | 10 | 0 | 0
1104.9 | 50.5 | 50.5 | -1 | 0.4 | 4 | 50.5 | -1 | -1 | -10 | -3 | -3 | 0 | 12 | 1 | 1 | -3 | 10 | 0 | 0
1104.95 | 50.5 | 50.5 | -1 | 0.3 | 3 | 50.5 | -1 | -1 | -10 | -3.5 | -3.5 | 0 | 12 | 1 | 1 | -3.5 | 10 | 0 | 0
1105 | 50.5 | 50.5 | -1 | 0.2 | 2 | 50.5 | -1 | -1 | -10 | -4 | -4 | 0 | 12 | 1 | 1 | -4 | 10 | 0 | 0
1105.05 | 50.5 | 50.5 | -1 | 0.1 | 1 | 50.5 | -1 | -1 | -10 | -4.5 | -4.5 | 0 | 12 | 1 | 1 | -4.5 | 10 | 0 | 0
1105.1 | 50.5 | 50.5 | -1 | 0 | 0 | 50.5 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1105.15 | 50.5 | 50.5 | -1 | -0.1 | -1 | 50.5 | -1 | -1 | -10 | -5.5 | -5.5 | 0 | 12 | 1 | 1 | -5.5 | 10 | 0 | 0
1105.2 | 50.5 | 50.5 | -1 | -0.2 | -2 | 50.5 | -1 | -1 | -10 | -6 | -6 | 0 | 12 | 1 | 1 | -6 | 10 | 0 | 0
1105.25 | 50.5 | 50.5 | -1 | -0.3 | -3 | 50.5 | -1 | -1 | -10 | -6.5 | -6.5 | 0 | 12 | 1 | 1 | -6.5 | 10 | 0 | 0
1105.3 | 50.5 | 50.5 | -1 | -0.4 | -4 | 50.5 | -1 | -1 | -10 | -7 | -7 | 0 | 12 | 1 | 1 | -7 | 10 | 0 | 0
1105.35 | 50.5 | 50.5 | -1 | -0.5 | -5 | 50.5 | -1 | -1 | -10 | -7.5 | -7.5 | 0 | 12 | 1 | 1 | -7.5 | 10 | 0 | 0
1105.4 | 50.5 | 50.5 | -1 | -0.6 | -6 | 50.5 | -1 | -1 | -10 | -8 | -8 | 0 | 12 | 1 | 1 | -8 | 10 | 0 | 0
1105.45 | 50.5 | 50.5 | -1 | -0.7 | -7 | 50.5 | -1 | -1 | -10 | -8.5 | -8.5 | 0 | 12 | 1 | 1 | -8.5 | 10 | 0 | 0
1105.5 | 50.5 | 50.5 | -1 | -0.8 | -8 | 50.5 | -1 | -1 | -10 | -9 | -9 | 0 | 12 | 1 | 1 | -9 | 10 | 0 | 0
1105.55 | 50.5 | 50.5 | -1 | -0.9 | -9 | 50.5 | -1 | -1 | -10 | -9.5 | -9.5 | 0 | 12 | 1 | 1 | -9.5 | 10 | 0 | 0
1105.6 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1105.65 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1105.7 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1105.75 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1105.8 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1105.85 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1105.9 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1105.95 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1106 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1106.05 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1106.1 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1106.15 | 50.47 | 50.47 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1106.2 | 50.45 | 50.45 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1106.25 | 50.42 | 50.42 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1106.3 | 50.4 | 50.4 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1106.35 | 50.37 | 50.37 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1106.4 | 50.35 | 50.35 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1106.45 | 50.32 | 50.32 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1106.5 | 50.29 | 50.29 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1106.55 | 50.27 | 50.27 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1106.6 | 50.24 | 50.24 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1106.65 | 50.22 | 50.22 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1106.7 | 50.19 | 50.19 | -0.905 | -0.905 | -9.05 | 50.47 | -1 | -1 | -10 | -9.525 | -9.525 | 0 | 12 | 1 | 1 | -9.525 | 10 | 0 | 0
1106.75 | 50.17 | 50.17 | -0.715 | -0.715 | -7.15 | 50.45 | -1 | -1 | -10 | -8.575 | -8.575 | 0 | 12 | 1 | 1 | -8.575 | 10 | 0 | 0
1106.8 | 50.14 | 50.14 | -0.43 | -0.43 | -4.3 | 50.42 | -1 | -1 | -10 | -7.15 | -7.15 | 0 | 12 | 1 | 1 | -7.15 | 10 | 0 | 0
1106.85 | 50.12 | 50.12 | -0.24 | -0.24 | -2.4 | 50.4 | -1 | -1 | -10 | -6.2 | -6.2 | 0 | 12 | 1 | 1 | -6.2 | 10 | 0 | 0
1106.9 | 50.09 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 50.37 | -1 | -1 | -10 | -5.2206 | -5.2206 | 0 | 12 | 1 | 1 | -5.2206 | 10 | 0 | 0
1106.95 | 50.06 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.35 | -1 | -1 | -10 | -5.1324 | -5.1324 | 0 | 12 | 1 | 1 | -5.1324 | 10 | 0 | 0
1107 | 50.04 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.32 | -1 | -1 | -10 | -5.0735 | -5.0735 | 0 | 12 | 1 | 1 | -5.0735 | 10 | 0 | 0
1107.05 | 50.01 | 50.01 | 0 | 0 | 0 | 50.29 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1107.1 | 49.99 | 49.99 | 0 | 0 | 0 | 50.27 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1107.15 | 49.96 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.24 | -1 | -1 | -10 | -4.9265 | -4.9265 | 0 | 12 | 1 | 1 | -4.9265 | 10 | 0 | 0
1107.2 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.22 | -1 | -1 | -10 | -4.8676 | -4.8676 | 0 | 12 | 1 | 1 | -4.8676 | 10 | 0 | 0
1107.25 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.19 | -0.905 | -0.905 | -9.05 | -4.3044 | -4.3044 | 0 | 12 | 1 | 1 | -4.3044 | 10 | 0 | 0
1107.3 | 49.88 | 49.88 | 0.24 | 0.24 | 2.4 | 50.17 | -0.715 | -0.805 | -8.05 | -2.825 | -2.825 | 0 | 12 | 1 | 1 | -2.825 | 10 | 0 | 0
1107.35 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.14 | -0.43 | -0.705 | -7.05 | -1.375 | -1.375 | 0 | 12 | 1 | 1 | -1.375 | 10 | 0 | 0
1107.4 | 49.83 | 49.83 | 0.715 | 0.715 | 7.15 | 50.12 | -0.24 | -0.605 | -6.05 | 0.55 | 0.55 | 0 | 12 | 1 | 1 | 0.55 | 10 | 0 | 0
1107.45 | 49.81 | 49.81 | 0.905 | 0.905 | 9.05 | 50.09 | -0.044118 | -0.505 | -5.05 | 2 | 2 | 0 | 12 | 1 | 1 | 2 | 10 | 0 | 0
1107.5 | 49.78 | 49.78 | 1 | 1 | 10 | 50.06 | -0.026471 | -0.405 | -4.05 | 2.975 | 2.975 | 0 | 12 | 1 | 1 | 2.975 | 10 | 0 | 0
1107.55 | 49.76 | 49.76 | 1 | 1 | 10 | 50.04 | -0.014706 | -0.305 | -3.05 | 3.475 | 3.475 | 0 | 12 | 1 | 1 | 3.475 | 10 | 0 | 0
1107.6 | 49.73 | 49.73 | 1 | 1 | 10 | 50.01 | 0 | -0.205 | -2.05 | 3.975 | 3.975 | 0 | 12 | 1 | 1 | 3.975 | 10 | 0 | 0
1107.65 | 49.71 | 49.71 | 1 | 1 | 10 | 49.99 | 0 | -0.105 | -1.05 | 4.475 | 4.475 | 0 | 12 | 1 | 1 | 4.475 | 10 | 0 | 0
1107.7 | 49.68 | 49.68 | 1 | 1 | 10 | 49.96 | 0.014706 | -0.005 | -0.05 | 4.975 | 4.975 | 0 | 12 | 1 | 1 | 4.975 | 10 | 0 | 0
1107.75 | 49.65 | 49.65 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
1107.8 | 49.63 | 49.63 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1107.85 | 49.6 | 49.6 | 1 | 1 | 10 | 49.88 | 0.24 | 0.14412 | 1.4412 | 5.7206 | 5.7206 | 0 | 12 | 1 | 1 | 5.7206 | 10 | 0 | 0
1107.9 | 49.58 | 49.58 | 1 | 1 | 10 | 49.86 | 0.43 | 0.24412 | 2.4412 | 6.2206 | 6.2206 | 0 | 12 | 1 | 1 | 6.2206 | 10 | 0 | 0
1107.95 | 49.55 | 49.55 | 1 | 1 | 10 | 49.83 | 0.715 | 0.34412 | 3.4412 | 6.7206 | 6.7206 | 0 | 12 | 1 | 1 | 6.7206 | 10 | 0 | 0
1108 | 49.53 | 49.53 | 1 | 1 | 10 | 49.81 | 0.905 | 0.44412 | 4.4412 | 7.2206 | 7.2206 | 0 | 12 | 1 | 1 | 7.2206 | 10 | 0 | 0
1108.05 | 49.5 | 49.5 | 1 | 1 | 10 | 49.78 | 1 | 0.54412 | 5.4412 | 7.7206 | 7.7206 | 0 | 12 | 1 | 1 | 7.7206 | 10 | 0 | 0
1108.1 | 49.5 | 49.5 | 1 | 1 | 10 | 49.76 | 1 | 0.64412 | 6.4412 | 8.2206 | 8.2206 | 0 | 12 | 1 | 1 | 8.2206 | 10 | 0 | 0
1108.15 | 49.53 | 49.5 | 1 | 1 | 10 | 49.73 | 1 | 0.74412 | 7.4412 | 8.7206 | 8.7206 | 0 | 12 | 1 | 1 | 8.7206 | 10 | 0 | 0
1108.2 | 49.55 | 49.5 | 1 | 1 | 10 | 49.71 | 1 | 0.84412 | 8.4412 | 9.2206 | 9.2206 | 0 | 12 | 1 | 1 | 9.2206 | 10 | 0 | 0
1108.25 | 49.58 | 49.5 | 1 | 1 | 10 | 49.68 | 1 | 0.94412 | 9.4412 | 9.7206 | 9.7206 | 0 | 12 | 1 | 1 | 9.7206 | 10 | 0 | 0
1108.3 | 49.6 | 49.5 | 1 | 1 | 10 | 49.65 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1108.35 | 49.63 | 49.5 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1108.4 | 49.65 | 49.5 | 1 | 1 | 10 | 49.65 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1108.45 | 49.68 | 49.5 | 1 | 1 | 10 | 49.68 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1108.5 | 49.71 | 49.5 | 1 | 1 | 10 | 49.71 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1108.55 | 49.73 | 49.5 | 1 | 1 | 10 | 49.73 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1108.6 | 49.76 | 49.5 | 1 | 1 | 10 | 49.76 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1108.65 | 49.78 | 49.5 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1108.7 | 49.81 | 49.53 | 1 | 1 | 10 | 49.81 | 0.905 | 0.905 | 9.05 | 9.525 | 9.525 | 0 | 12 | 1 | 1 | 9.525 | 10 | 0 | 0
1108.75 | 49.83 | 49.55 | 1 | 1 | 10 | 49.83 | 0.715 | 0.715 | 7.15 | 8.575 | 8.575 | 0 | 12 | 1 | 1 | 8.575 | 10 | 0 | 0
1108.8 | 49.86 | 49.58 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
1108.85 | 49.88 | 49.6 | 1 | 1 | 10 | 49.88 | 0.24 | 0.24 | 2.4 | 6.2 | 6.2 | 0 | 12 | 1 | 1 | 6.2 | 10 | 0 | 0
1108.9 | 49.91 | 49.63 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1108.95 | 49.94 | 49.65 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
1109 | 49.96 | 49.68 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
1109.05 | 49.99 | 49.71 | 1 | 1 | 10 | 49.99 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1109.1 | 50.01 | 49.73 | 1 | 1 | 10 | 50.01 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1109.15 | 50.04 | 49.76 | 1 | 1 | 10 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 4.9265 | 4.9265 | 0 | 12 | 1 | 1 | 4.9265 | 10 | 0 | 0
1109.2 | 50.06 | 49.78 | 1 | 1 | 10 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 4.8676 | 4.8676 | 0 | 12 | 1 | 1 | 4.8676 | 10 | 0 | 0
1109.25 | 50.09 | 49.81 | 0.905 | 0.905 | 9.05 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 4.3044 | 4.3044 | 0 | 12 | 1 | 1 | 4.3044 | 10 | 0 | 0
1109.3 | 50.12 | 49.83 | 0.715 | 0.805 | 8.05 | 50.12 | -0.24 | -0.24 | -2.4 | 2.825 | 2.825 | 0 | 12 | 1 | 1 | 2.825 | 10 | 0 | 0
1109.35 | 50.14 | 49.86 | 0.43 | 0.705 | 7.05 | 50.14 | -0.43 | -0.43 | -4.3 | 1.375 | 1.375 | 0 | 12 | 1 | 1 | 1.375 | 10 | 0 | 0
1109.4 | 50.17 | 49.88 | 0.24 | 0.605 | 6.05 | 50.17 | -0.715 | -0.715 | -7.15 | -0.55 | -0.55 | 0 | 12 | 1 | 1 | -0.55 | 10 | 0 | 0
1109.45 | 50.19 | 49.91 | 0.044118 | 0.505 | 5.05 | 50.19 | -0.905 | -0.905 | -9.05 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
1109.5 | 50.22 | 49.94 | 0.026471 | 0.405 | 4.05 | 50.22 | -1 | -1 | -10 | -2.975 | -2.975 | 0 | 12 | 1 | 1 | -2.975 | 10 | 0 | 0
1109.55 | 50.24 | 49.96 | 0.014706 | 0.305 | 3.05 | 50.24 | -1 | -1 | -10 | -3.475 | -3.475 | 0 | 12 | 1 | 1 | -3.475 | 10 | 0 | 0
1109.6 | 50.27 | 49.99 | 0 | 0.205 | 2.05 | 50.27 | -1 | -1 | -10 | -3.975 | -3.975 | 0 | 12 | 1 | 1 | -3.975 | 10 | 0 | 0
1109.65 | 50.29 | 50.01 | 0 | 0.105 | 1.05 | 50.29 | -1 | -1 | -10 | -4.475 | -4.475 | 0 | 12 | 1 | 1 | -4.475 | 10 | 0 | 0
1109.7 | 50.32 | 50.04 | -0.014706 | 0.005 | 0.05 | 50.32 | -1 | -1 | -10 | -4.975 | -4.975 | 0 | 12 | 1 | 1 | -4.975 | 10 | 0 | 0
1109.75 | 50.35 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.35 | -1 | -1 | -10 | -5.1324 | -5.1324 | 0 | 12 | 1 | 1 | -5.1324 | 10 | 0 | 0
1109.8 | 50.37 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 50.37 | -1 | -1 | -10 | -5.2206 | -5.2206 | 0 | 12 | 1 | 1 | -5.2206 | 10 | 0 | 0
1109.85 | 50.4 | 50.12 | -0.24 | -0.14412 | -1.4412 | 50.4 | -1 | -1 | -10 | -5.7206 | -5.7206 | 0 | 12 | 1 | 1 | -5.7206 | 10 | 0 | 0
1109.9 | 50.42 | 50.14 | -0.43 | -0.24412 | -2.4412 | 50.42 | -1 | -1 | -10 | -6.2206 | -6.2206 | 0 | 12 | 1 | 1 | -6.2206 | 10 | 0 | 0
1109.95 | 50.45 | 50.17 | -0.715 | -0.34412 | -3.4412 | 50.45 | -1 | -1 | -10 | -6.7206 | -6.7206 | 0 | 12 | 1 | 1 | -6.7206 | 10 | 0 | 0
1110 | 50.47 | 50.19 | -0.905 | -0.44412 | -4.4412 | 50.47 | -1 | -1 | -10 | -7.2206 | -7.2206 | 0 | 12 | 1 | 1 | -7.2206 | 10 | 0 | 0
1110.05 | 50.5 | 50.22 | -1 | -0.54412 | -5.4412 | 50.5 | -1 | -1 | -10 | -7.7206 | -7.7206 | 0 | 12 | 1 | 1 | -7.7206 | 10 | 0 | 0
1110.1 | 50.5 | 50.24 | -1 | -0.64412 | -6.4412 | 50.5 | -1 | -1 | -10 | -8.2206 | -8.2206 | 0 | 12 | 1 | 1 | -8.2206 | 10 | 0 | 0
1110.15 | 50.47 | 50.27 | -1 | -0.74412 | -7.4412 | 50.5 | -1 | -1 | -10 | -8.7206 | -8.7206 | 0 | 12 | 1 | 1 | -8.7206 | 10 | 0 | 0
1110.2 | 50.45 | 50.29 | -1 | -0.84412 | -8.4412 | 50.5 | -1 | -1 | -10 | -9.2206 | -9.2206 | 0 | 12 | 1 | 1 | -9.2206 | 10 | 0 | 0
1110.25 | 50.42 | 50.32 | -1 | -0.94412 | -9.4412 | 50.5 | -1 | -1 | -10 | -9.7206 | -9.7206 | 0 | 12 | 1 | 1 | -9.7206 | 10 | 0 | 0
1110.3 | 50.39 | 50.35 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1110.35 | 50.37 | 50.37 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1110.4 | 50.34 | 50.34 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1110.45 | 50.32 | 50.32 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1110.5 | 50.29 | 50.29 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1110.55 | 50.26 | 50.26 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1110.6 | 50.24 | 50.24 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1110.65 | 50.21 | 50.21 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1110.7 | 50.18 | 50.18 | -0.81 | -0.81 | -8.1 | 50.47 | -1 | -1 | -10 | -9.05 | -9.05 | 0 | 12 | 1 | 1 | -9.05 | 10 | 0 | 0
1110.75 | 50.16 | 50.16 | -0.62 | -0.62 | -6.2 | 50.45 | -1 | -1 | -10 | -8.1 | -8.1 | 0 | 12 | 1 | 1 | -8.1 | 10 | 0 | 0
1110.8 | 50.13 | 50.13 | -0.335 | -0.335 | -3.35 | 50.42 | -1 | -1 | -10 | -6.675 | -6.675 | 0 | 12 | 1 | 1 | -6.675 | 10 | 0 | 0
1110.85 | 50.11 | 50.11 | -0.145 | -0.145 | -1.45 | 50.39 | -1 | -1 | -10 | -5.725 | -5.725 | 0 | 12 | 1 | 1 | -5.725 | 10 | 0 | 0
1110.9 | 50.08 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 50.37 | -1 | -1 | -10 | -5.1912 | -5.1912 | 0 | 12 | 1 | 1 | -5.1912 | 10 | 0 | 0
1110.95 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.34 | -1 | -1 | -10 | -5.1029 | -5.1029 | 0 | 12 | 1 | 1 | -5.1029 | 10 | 0 | 0
1111 | 50.03 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 50.32 | -1 | -1 | -10 | -5.0441 | -5.0441 | 0 | 12 | 1 | 1 | -5.0441 | 10 | 0 | 0
1111.05 | 50 | 50 | 0 | 0 | 0 | 50.29 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1111.1 | 50 | 50 | 0 | 0 | 0 | 50.26 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1111.15 | 50 | 50 | 0 | 0 | 0 | 50.24 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1111.2 | 50 | 50 | 0 | 0 | 0 | 50.21 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1111.25 | 50 | 50 | 0 | 0 | 0 | 50.18 | -0.81 | -0.9 | -9 | -4.5 | -4.5 | 0 | 12 | 1 | 1 | -4.5 | 10 | 0 | 0
1111.3 | 50 | 50 | 0 | 0 | 0 | 50.16 | -0.62 | -0.8 | -8 | -4 | -4 | 0 | 12 | 1 | 1 | -4 | 10 | 0 | 0
1111.35 | 50 | 50 | 0 | 0 | 0 | 50.13 | -0.335 | -0.7 | -7 | -3.5 | -3.5 | 0 | 12 | 1 | 1 | -3.5 | 10 | 0 | 0
1111.4 | 50.01 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.6 | -6 | -3 | -3 | 0 | 12 | 1 | 1 | -3 | 10 | 0 | 0
1111.45 | 50.01 | 50 | 0 | 0 | 0 | 50.08 | -0.038235 | -0.5 | -5 | -2.5 | -2.5 | 0 | 12 | 1 | 1 | -2.5 | 10 | 0 | 0
1111.5 | 49.99 | 49.99 | 0 | 0 | 0 | 50.05 | -0.020588 | -0.4 | -4 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
1111.55 | 49.99 | 49.99 | 0 | 0 | 0 | 50.03 | -0.0088235 | -0.3 | -3 | -1.5 | -1.5 | 0 | 12 | 1 | 1 | -1.5 | 10 | 0 | 0
1111.6 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | -0.2 | -2 | -0.83824 | -0.83824 | 0 | 12 | 1 | 1 | -0.83824 | 10 | 0 | 0
1111.65 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | -0.1 | -1 | -0.33824 | -0.33824 | 0 | 12 | 1 | 1 | -0.33824 | 10 | 0 | 0
1111.7 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
1111.75 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
1111.8 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
1111.85 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
1111.9 | 49.89 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
1111.95 | 49.89 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
1112 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50.01 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1112.05 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1112.1 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1112.15 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 2.7868 | 2.7868 | 0 | 12 | 1 | 1 | 2.7868 | 10 | 0 | 0
1112.2 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 2.7868 | 2.7868 | 0 | 12 | 1 | 1 | 2.7868 | 10 | 0 | 0
1112.25 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 2.8456 | 2.8456 | 0 | 12 | 1 | 1 | 2.8456 | 10 | 0 | 0
1112.3 | 49.94 | 49.85 | 0.525 | 0.525 | 5.25 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 2.7574 | 2.7574 | 0 | 12 | 1 | 1 | 2.7574 | 10 | 0 | 0
1112.35 | 49.94 | 49.85 | 0.525 | 0.525 | 5.25 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 2.7574 | 2.7574 | 0 | 12 | 1 | 1 | 2.7574 | 10 | 0 | 0
1112.4 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1112.45 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1112.5 | 49.93 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1112.55 | 49.93 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1112.6 | 49.96 | 49.85 | 0.525 | 0.525 | 5.25 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 2.6985 | 2.6985 | 0 | 12 | 1 | 1 | 2.6985 | 10 | 0 | 0
1112.65 | 49.96 | 49.85 | 0.525 | 0.525 | 5.25 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 2.6985 | 2.6985 | 0 | 12 | 1 | 1 | 2.6985 | 10 | 0 | 0
1112.7 | 49.99 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1112.75 | 49.99 | 49.91 | 0.044118 | 0.425 | 4.25 | 49.99 | 0 | 0 | 0 | 2.125 | 2.125 | 0 | 12 | 1 | 1 | 2.125 | 10 | 0 | 0
1112.8 | 49.99 | 49.91 | 0.044118 | 0.325 | 3.25 | 49.99 | 0 | 0 | 0 | 1.625 | 1.625 | 0 | 12 | 1 | 1 | 1.625 | 10 | 0 | 0
1112.85 | 49.99 | 49.93 | 0.032353 | 0.225 | 2.25 | 49.99 | 0 | 0 | 0 | 1.125 | 1.125 | 0 | 12 | 1 | 1 | 1.125 | 10 | 0 | 0
1112.9 | 49.96 | 49.93 | 0.032353 | 0.125 | 1.25 | 49.99 | 0 | 0 | 0 | 0.625 | 0.625 | 0 | 12 | 1 | 1 | 0.625 | 10 | 0 | 0
1112.95 | 49.96 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 49.99 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1113 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1113.05 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1113.1 | 50.05 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.058824 | 0.058824 | 0 | 12 | 1 | 1 | 0.058824 | 10 | 0 | 0
1113.15 | 50.05 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
1113.2 | 49.97 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
1113.25 | 49.97 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
1113.3 | 49.92 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1113.35 | 49.92 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1113.4 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1113.45 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1113.5 | 49.94 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1113.55 | 49.94 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1113.6 | 50.01 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1113.65 | 50.01 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1113.7 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1113.75 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
1113.8 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
1113.85 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
1113.9 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
1113.95 | 49.95 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
1114 | 49.97 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
1114.05 | 49.97 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
1114.1 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
1114.15 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
1114.2 | 49.87 | 49.87 | 0.335 | 0.335 | 3.35 | 50.01 | 0 | 0 | 0 | 1.675 | 1.675 | 0 | 12 | 1 | 1 | 1.675 | 10 | 0 | 0
1114.25 | 49.87 | 49.87 | 0.335 | 0.335 | 3.35 | 49.99 | 0 | 0 | 0 | 1.675 | 1.675 | 0 | 12 | 1 | 1 | 1.675 | 10 | 0 | 0
1114.3 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1114.35 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 2.6691 | 2.6691 | 0 | 12 | 1 | 1 | 2.6691 | 10 | 0 | 0
1114.4 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1114.45 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1114.5 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1114.55 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1114.6 | 49.84 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1114.65 | 49.84 | 49.79 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
1114.7 | 49.89 | 49.79 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
1114.75 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.12647 | 1.2647 | 5.6324 | 5.6324 | 0 | 12 | 1 | 1 | 5.6324 | 10 | 0 | 0
1114.8 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.145 | 1.45 | 5.725 | 5.725 | 0 | 12 | 1 | 1 | 5.725 | 10 | 0 | 0
1114.85 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.145 | 1.45 | 5.725 | 5.725 | 0 | 12 | 1 | 1 | 5.725 | 10 | 0 | 0
1114.9 | 49.96 | 49.79 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
1114.95 | 49.96 | 49.79 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
1115 | 50.02 | 49.79 | 1 | 1 | 10 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 4.9853 | 4.9853 | 0 | 12 | 1 | 1 | 4.9853 | 10 | 0 | 0
1115.05 | 50.02 | 49.79 | 1 | 1 | 10 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 4.9853 | 4.9853 | 0 | 12 | 1 | 1 | 4.9853 | 10 | 0 | 0
1115.1 | 50.03 | 49.79 | 1 | 1 | 10 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.9559 | 4.9559 | 0 | 12 | 1 | 1 | 4.9559 | 10 | 0 | 0
1115.15 | 50.03 | 49.84 | 0.62 | 0.9 | 9 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.4559 | 4.4559 | 0 | 12 | 1 | 1 | 4.4559 | 10 | 0 | 0
1115.2 | 50.02 | 49.84 | 0.62 | 0.8 | 8 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 3.9559 | 3.9559 | 0 | 12 | 1 | 1 | 3.9559 | 10 | 0 | 0
1115.25 | 50.02 | 49.89 | 0.145 | 0.7 | 7 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 3.4559 | 3.4559 | 0 | 12 | 1 | 1 | 3.4559 | 10 | 0 | 0
1115.3 | 50.08 | 49.89 | 0.145 | 0.6 | 6 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 2.8088 | 2.8088 | 0 | 12 | 1 | 1 | 2.8088 | 10 | 0 | 0
1115.35 | 50.08 | 49.89 | 0.145 | 0.5 | 5 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 2.3088 | 2.3088 | 0 | 12 | 1 | 1 | 2.3088 | 10 | 0 | 0
1115.4 | 50.01 | 49.89 | 0.145 | 0.4 | 4 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 1.8088 | 1.8088 | 0 | 12 | 1 | 1 | 1.8088 | 10 | 0 | 0
1115.45 | 50.01 | 49.96 | 0.014706 | 0.3 | 3 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 1.3088 | 1.3088 | 0 | 12 | 1 | 1 | 1.3088 | 10 | 0 | 0
1115.5 | 49.94 | 49.94 | 0.026471 | 0.2 | 2 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.80882 | 0.80882 | 0 | 12 | 1 | 1 | 0.80882 | 10 | 0 | 0
1115.55 | 49.94 | 49.94 | 0.026471 | 0.1 | 1 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.30882 | 0.30882 | 0 | 12 | 1 | 1 | 0.30882 | 10 | 0 | 0
1115.6 | 50 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
1115.65 | 50 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
1115.7 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
1115.75 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
1115.8 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1115.85 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1115.9 | 49.92 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1115.95 | 49.92 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
1116 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50.01 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1116.05 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1116.1 | 49.92 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1116.15 | 49.92 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1116.2 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1116.25 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1116.3 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1116.35 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1116.4 | 49.87 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1116.45 | 49.87 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1116.5 | 49.8 | 49.8 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1116.55 | 49.8 | 49.8 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1116.6 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1116.65 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1116.7 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1116.75 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1116.8 | 49.72 | 49.72 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1116.85 | 49.72 | 49.72 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1116.9 | 49.67 | 49.67 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1116.95 | 49.67 | 49.67 | 1 | 1 | 10 | 49.87 | 0.335 | 0.14412 | 1.4412 | 5.7206 | 5.7206 | 0 | 12 | 1 | 1 | 5.7206 | 10 | 0 | 0
1117 | 49.65 | 49.65 | 1 | 1 | 10 | 49.87 | 0.335 | 0.24412 | 2.4412 | 6.2206 | 6.2206 | 0 | 12 | 1 | 1 | 6.2206 | 10 | 0 | 0
1117.05 | 49.65 | 49.65 | 1 | 1 | 10 | 49.8 | 1 | 0.34412 | 3.4412 | 6.7206 | 6.7206 | 0 | 12 | 1 | 1 | 6.7206 | 10 | 0 | 0
1117.1 | 49.59 | 49.59 | 1 | 1 | 10 | 49.8 | 1 | 0.44412 | 4.4412 | 7.2206 | 7.2206 | 0 | 12 | 1 | 1 | 7.2206 | 10 | 0 | 0
1117.15 | 49.59 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.54412 | 5.4412 | 7.7206 | 7.7206 | 0 | 12 | 1 | 1 | 7.7206 | 10 | 0 | 0
1117.2 | 49.66 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.64412 | 6.4412 | 8.2206 | 8.2206 | 0 | 12 | 1 | 1 | 8.2206 | 10 | 0 | 0
1117.25 | 49.66 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.74412 | 7.4412 | 8.7206 | 8.7206 | 0 | 12 | 1 | 1 | 8.7206 | 10 | 0 | 0
1117.3 | 49.63 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.84412 | 8.4412 | 9.2206 | 9.2206 | 0 | 12 | 1 | 1 | 9.2206 | 10 | 0 | 0
1117.35 | 49.63 | 49.59 | 1 | 1 | 10 | 49.72 | 1 | 0.94412 | 9.4412 | 9.7206 | 9.7206 | 0 | 12 | 1 | 1 | 9.7206 | 10 | 0 | 0
1117.4 | 49.61 | 49.59 | 1 | 1 | 10 | 49.72 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1117.45 | 49.61 | 49.59 | 1 | 1 | 10 | 49.67 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1117.5 | 49.54 | 49.54 | 1 | 1 | 10 | 49.67 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1117.55 | 49.54 | 49.54 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1117.6 | 49.46 | 49.46 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1117.65 | 49.46 | 49.46 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1117.7 | 49.45 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1117.75 | 49.45 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1117.8 | 49.51 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1117.85 | 49.51 | 49.45 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1117.9 | 49.5 | 49.45 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1117.95 | 49.5 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1118 | 49.54 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1118.05 | 49.54 | 49.45 | 1 | 1 | 10 | 49.54 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1118.1 | 49.59 | 49.45 | 1 | 1 | 10 | 49.59 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1118.15 | 49.59 | 49.45 | 1 | 1 | 10 | 49.59 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1118.2 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1118.25 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1118.3 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1118.35 | 49.61 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1118.4 | 49.53 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1118.45 | 49.53 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1118.5 | 49.54 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1118.55 | 49.54 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1118.6 | 49.61 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1118.65 | 49.61 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1118.7 | 49.66 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1118.75 | 49.66 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1118.8 | 49.64 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1118.85 | 49.64 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1118.9 | 49.69 | 49.53 | 1 | 1 | 10 | 49.69 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1118.95 | 49.69 | 49.53 | 1 | 1 | 10 | 49.69 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1119 | 49.74 | 49.53 | 1 | 1 | 10 | 49.74 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1119.05 | 49.74 | 49.54 | 1 | 1 | 10 | 49.74 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1119.1 | 49.78 | 49.54 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1119.15 | 49.78 | 49.61 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1119.2 | 49.82 | 49.61 | 1 | 1 | 10 | 49.82 | 0.81 | 0.81 | 8.1 | 9.05 | 9.05 | 0 | 12 | 1 | 1 | 9.05 | 10 | 0 | 0
1119.25 | 49.82 | 49.64 | 1 | 1 | 10 | 49.82 | 0.81 | 0.81 | 8.1 | 9.05 | 9.05 | 0 | 12 | 1 | 1 | 9.05 | 10 | 0 | 0
1119.3 | 49.86 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
1119.35 | 49.86 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
1119.4 | 49.84 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
1119.45 | 49.84 | 49.69 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
1119.5 | 49.91 | 49.69 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1119.55 | 49.91 | 49.74 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1119.6 | 49.97 | 49.74 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1119.65 | 49.97 | 49.78 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1119.7 | 50.03 | 49.78 | 1 | 1 | 10 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.9559 | 4.9559 | 0 | 12 | 1 | 1 | 4.9559 | 10 | 0 | 0
1119.75 | 50.03 | 49.82 | 0.81 | 0.9 | 9 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.4559 | 4.4559 | 0 | 12 | 1 | 1 | 4.4559 | 10 | 0 | 0
1119.8 | 50.05 | 49.82 | 0.81 | 0.81 | 8.1 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 3.9471 | 3.9471 | 0 | 12 | 1 | 1 | 3.9471 | 10 | 0 | 0
1119.85 | 50.05 | 49.84 | 0.62 | 0.71 | 7.1 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 3.4471 | 3.4471 | 0 | 12 | 1 | 1 | 3.4471 | 10 | 0 | 0
1119.9 | 50.01 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
1119.95 | 50.01 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
1120 | 49.95 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
1120.05 | 49.95 | 49.91 | 0.044118 | 0.52 | 5.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.4971 | 2.4971 | 0 | 12 | 1 | 1 | 2.4971 | 10 | 0 | 0
1120.1 | 49.99 | 49.91 | 0.044118 | 0.42 | 4.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 1.9971 | 1.9971 | 0 | 12 | 1 | 1 | 1.9971 | 10 | 0 | 0
1120.15 | 49.99 | 49.95 | 0.020588 | 0.32 | 3.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 1.4971 | 1.4971 | 0 | 12 | 1 | 1 | 1.4971 | 10 | 0 | 0
1120.2 | 49.92 | 49.92 | 0.038235 | 0.22 | 2.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.99706 | 0.99706 | 0 | 12 | 1 | 1 | 0.99706 | 10 | 0 | 0
1120.25 | 49.92 | 49.92 | 0.038235 | 0.12 | 1.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.49706 | 0.49706 | 0 | 12 | 1 | 1 | 0.49706 | 10 | 0 | 0
1120.3 | 49.97 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1120.35 | 49.97 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1120.4 | 50.02 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1120.45 | 50.02 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.17647 | 0.17647 | 0 | 12 | 1 | 1 | 0.17647 | 10 | 0 | 0
1120.5 | 50.07 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1120.55 | 50.07 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1120.6 | 50.06 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1120.65 | 50.06 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1120.7 | 50.13 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
1120.75 | 50.13 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
1120.8 | 50.09 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
1120.85 | 50.09 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6309 | -1.6309 | 0 | 12 | 1 | 1 | -1.6309 | 10 | 0 | 0
1120.9 | 50.07 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6309 | -1.6309 | 0 | 12 | 1 | 1 | -1.6309 | 10 | 0 | 0
1120.95 | 50.07 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6897 | -1.6897 | 0 | 12 | 1 | 1 | -1.6897 | 10 | 0 | 0
1121 | 50.07 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6897 | -1.6897 | 0 | 12 | 1 | 1 | -1.6897 | 10 | 0 | 0
1121.05 | 50.07 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.13 | -0.335 | -0.335 | -3.35 | -1.8074 | -1.8074 | 0 | 12 | 1 | 1 | -1.8074 | 10 | 0 | 0
1121.1 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.13 | -0.335 | -0.335 | -3.35 | -1.7779 | -1.7779 | 0 | 12 | 1 | 1 | -1.7779 | 10 | 0 | 0
1121.15 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.13 | -0.335 | -0.335 | -3.35 | -1.7779 | -1.7779 | 0 | 12 | 1 | 1 | -1.7779 | 10 | 0 | 0
1121.2 | 50.01 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
1121.25 | 50.01 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
1121.3 | 50.07 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
1121.35 | 50.07 | 50.01 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.235 | -2.35 | -1.175 | -1.175 | 0 | 12 | 1 | 1 | -1.175 | 10 | 0 | 0
1121.4 | 50.05 | 50.01 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.135 | -1.35 | -0.675 | -0.675 | 0 | 12 | 1 | 1 | -0.675 | 10 | 0 | 0
1121.45 | 50.05 | 50.01 | 0 | 0 | 0 | 50.07 | -0.032353 | -0.035 | -0.35 | -0.175 | -0.175 | 0 | 12 | 1 | 1 | -0.175 | 10 | 0 | 0
1121.5 | 50.1 | 50.01 | 0 | 0 | 0 | 50.1 | -0.05 | -0.05 | -0.5 | -0.25 | -0.25 | 0 | 12 | 1 | 1 | -0.25 | 10 | 0 | 0
1121.55 | 50.1 | 50.01 | 0 | 0 | 0 | 50.1 | -0.05 | -0.05 | -0.5 | -0.25 | -0.25 | 0 | 12 | 1 | 1 | -0.25 | 10 | 0 | 0
1121.6 | 50.11 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1121.65 | 50.11 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1121.7 | 50.06 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1121.75 | 50.06 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1121.8 | 50.04 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1121.85 | 50.04 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1121.9 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1121.95 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1122 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1122.05 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1122.1 | 50.11 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1122.15 | 50.11 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1122.2 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1122.25 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1122.3 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1122.35 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1122.4 | 50.02 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.11 | -0.145 | -0.145 | -1.45 | -0.73971 | -0.73971 | 0 | 12 | 1 | 1 | -0.73971 | 10 | 0 | 0
1122.45 | 50.02 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.11 | -0.145 | -0.145 | -1.45 | -0.73971 | -0.73971 | 0 | 12 | 1 | 1 | -0.73971 | 10 | 0 | 0
1122.5 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1122.55 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1122.6 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1122.65 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1122.7 | 50.01 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1122.75 | 50.01 | 50 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.045 | -0.45 | -0.225 | -0.225 | 0 | 12 | 1 | 1 | -0.225 | 10 | 0 | 0
1122.8 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
1122.85 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
1122.9 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
1122.95 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1123 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.14706 | 0.14706 | 0 | 12 | 1 | 1 | 0.14706 | 10 | 0 | 0
1123.05 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1123.1 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1123.15 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1123.2 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1123.25 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1123.3 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1123.35 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1123.4 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1123.45 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1123.5 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1123.55 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1123.6 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1123.65 | 50 | 50 | 0 | 0 | 0 | 50.01 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1123.7 | 49.5 | 49.5 | 1 | 1 | 10 | 50.01 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1123.75 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1123.8 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1123.85 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1123.9 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1123.95 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1124 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1124.05 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1124.1 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1124.15 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1124.2 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1124.25 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.1 | 1 | 5.5 | 5.5 | 0 | 12 | 1 | 1 | 5.5 | 10 | 0 | 0
1124.3 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.2 | 2 | 6 | 6 | 0 | 12 | 1 | 1 | 6 | 10 | 0 | 0
1124.35 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.3 | 3 | 6.5 | 6.5 | 0 | 12 | 1 | 1 | 6.5 | 10 | 0 | 0
1124.4 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.4 | 4 | 7 | 7 | 0 | 12 | 1 | 1 | 7 | 10 | 0 | 0
1124.45 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.5 | 5 | 7.5 | 7.5 | 0 | 12 | 1 | 1 | 7.5 | 10 | 0 | 0
1124.5 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.6 | 6 | 8 | 8 | 0 | 12 | 1 | 1 | 8 | 10 | 0 | 0
1124.55 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.7 | 7 | 8.5 | 8.5 | 0 | 12 | 1 | 1 | 8.5 | 10 | 0 | 0
1124.6 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.8 | 8 | 9 | 9 | 0 | 12 | 1 | 1 | 9 | 10 | 0 | 0
1124.65 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.9 | 9 | 9.5 | 9.5 | 0 | 12 | 1 | 1 | 9.5 | 10 | 0 | 0
1124.7 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1124.75 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1124.8 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1124.85 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1124.9 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1124.95 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1125 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1125.05 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1125.1 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1125.15 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1125.2 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1125.25 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1125.3 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1125.35 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1125.4 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1125.45 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1125.5 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1125.55 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1125.6 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1125.65 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1125.7 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1125.75 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1125.8 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1125.85 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1125.9 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1125.95 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1126 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1126.05 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1126.1 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1126.15 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1126.2 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1126.25 | 50.5 | 50.5 | -1 | 0.9 | 9 | 50.5 | -1 | -1 | -10 | -0.5 | -0.5 | 0 | 12 | 1 | 1 | -0.5 | 10 | 0 | 0
1126.3 | 50.5 | 50.5 | -1 | 0.8 | 8 | 50.5 | -1 | -1 | -10 | -1 | -1 | 0 | 12 | 1 | 1 | -1 | 10 | 0 | 0
1126.35 | 50.5 | 50.5 | -1 | 0.7 | 7 | 50.5 | -1 | -1 | -10 | -1.5 | -1.5 | 0 | 12 | 1 | 1 | -1.5 | 10 | 0 | 0
1126.4 | 50.5 | 50.5 | -1 | 0.6 | 6 | 50.5 | -1 | -1 | -10 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
1126.45 | 50.5 | 50.5 | -1 | 0.5 | 5 | 50.5 | -1 | -1 | -10 | -2.5 | -2.5 | 0 | 12 | 1 | 1 | -2.5 | 10 | 0 | 0
1126.5 | 50.5 | 50.5 | -1 | 0.4 | 4 | 50.5 | -1 | -1 | -10 | -3 | -3 | 0 | 12 | 1 | 1 | -3 | 10 | 0 | 0
1126.55 | 50.5 | 50.5 | -1 | 0.3 | 3 | 50.5 | -1 | -1 | -10 | -3.5 | -3.5 | 0 | 12 | 1 | 1 | -3.5 | 10 | 0 | 0
1126.6 | 50.5 | 50.5 | -1 | 0.2 | 2 | 50.5 | -1 | -1 | -10 | -4 | -4 | 0 | 12 | 1 | 1 | -4 | 10 | 0 | 0
1126.65 | 50.5 | 50.5 | -1 | 0.1 | 1 | 50.5 | -1 | -1 | -10 | -4.5 | -4.5 | 0 | 12 | 1 | 1 | -4.5 | 10 | 0 | 0
1126.7 | 50.5 | 50.5 | -1 | 0 | 0 | 50.5 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1126.75 | 50.5 | 50.5 | -1 | -0.1 | -1 | 50.5 | -1 | -1 | -10 | -5.5 | -5.5 | 0 | 12 | 1 | 1 | -5.5 | 10 | 0 | 0
1126.8 | 50.5 | 50.5 | -1 | -0.2 | -2 | 50.5 | -1 | -1 | -10 | -6 | -6 | 0 | 12 | 1 | 1 | -6 | 10 | 0 | 0
1126.85 | 50.5 | 50.5 | -1 | -0.3 | -3 | 50.5 | -1 | -1 | -10 | -6.5 | -6.5 | 0 | 12 | 1 | 1 | -6.5 | 10 | 0 | 0
1126.9 | 50.5 | 50.5 | -1 | -0.4 | -4 | 50.5 | -1 | -1 | -10 | -7 | -7 | 0 | 12 | 1 | 1 | -7 | 10 | 0 | 0
1126.95 | 50.5 | 50.5 | -1 | -0.5 | -5 | 50.5 | -1 | -1 | -10 | -7.5 | -7.5 | 0 | 12 | 1 | 1 | -7.5 | 10 | 0 | 0
1127 | 50.5 | 50.5 | -1 | -0.6 | -6 | 50.5 | -1 | -1 | -10 | -8 | -8 | 0 | 12 | 1 | 1 | -8 | 10 | 0 | 0
1127.05 | 50.5 | 50.5 | -1 | -0.7 | -7 | 50.5 | -1 | -1 | -10 | -8.5 | -8.5 | 0 | 12 | 1 | 1 | -8.5 | 10 | 0 | 0
1127.1 | 50.5 | 50.5 | -1 | -0.8 | -8 | 50.5 | -1 | -1 | -10 | -9 | -9 | 0 | 12 | 1 | 1 | -9 | 10 | 0 | 0
1127.15 | 50.5 | 50.5 | -1 | -0.9 | -9 | 50.5 | -1 | -1 | -10 | -9.5 | -9.5 | 0 | 12 | 1 | 1 | -9.5 | 10 | 0 | 0
1127.2 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1127.25 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1127.3 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1127.35 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1127.4 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1127.45 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1127.5 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1127.55 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1127.6 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1127.65 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1127.7 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1127.75 | 50.47 | 50.47 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1127.8 | 50.45 | 50.45 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1127.85 | 50.42 | 50.42 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1127.9 | 50.4 | 50.4 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1127.95 | 50.37 | 50.37 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1128 | 50.35 | 50.35 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1128.05 | 50.32 | 50.32 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1128.1 | 50.29 | 50.29 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1128.15 | 50.27 | 50.27 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1128.2 | 50.24 | 50.24 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1128.25 | 50.22 | 50.22 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1128.3 | 50.19 | 50.19 | -0.905 | -0.905 | -9.05 | 50.47 | -1 | -1 | -10 | -9.525 | -9.525 | 0 | 12 | 1 | 1 | -9.525 | 10 | 0 | 0
1128.35 | 50.17 | 50.17 | -0.715 | -0.715 | -7.15 | 50.45 | -1 | -1 | -10 | -8.575 | -8.575 | 0 | 12 | 1 | 1 | -8.575 | 10 | 0 | 0
1128.4 | 50.14 | 50.14 | -0.43 | -0.43 | -4.3 | 50.42 | -1 | -1 | -10 | -7.15 | -7.15 | 0 | 12 | 1 | 1 | -7.15 | 10 | 0 | 0
1128.45 | 50.12 | 50.12 | -0.24 | -0.24 | -2.4 | 50.4 | -1 | -1 | -10 | -6.2 | -6.2 | 0 | 12 | 1 | 1 | -6.2 | 10 | 0 | 0
1128.5 | 50.09 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 50.37 | -1 | -1 | -10 | -5.2206 | -5.2206 | 0 | 12 | 1 | 1 | -5.2206 | 10 | 0 | 0
1128.55 | 50.06 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.35 | -1 | -1 | -10 | -5.1324 | -5.1324 | 0 | 12 | 1 | 1 | -5.1324 | 10 | 0 | 0
1128.6 | 50.04 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.32 | -1 | -1 | -10 | -5.0735 | -5.0735 | 0 | 12 | 1 | 1 | -5.0735 | 10 | 0 | 0
1128.65 | 50.01 | 50.01 | 0 | 0 | 0 | 50.29 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1128.7 | 49.99 | 49.99 | 0 | 0 | 0 | 50.27 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1128.75 | 49.96 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.24 | -1 | -1 | -10 | -4.9265 | -4.9265 | 0 | 12 | 1 | 1 | -4.9265 | 10 | 0 | 0
1128.8 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.22 | -1 | -1 | -10 | -4.8676 | -4.8676 | 0 | 12 | 1 | 1 | -4.8676 | 10 | 0 | 0
1128.85 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.19 | -0.905 | -0.905 | -9.05 | -4.3044 | -4.3044 | 0 | 12 | 1 | 1 | -4.3044 | 10 | 0 | 0
1128.9 | 49.88 | 49.88 | 0.24 | 0.24 | 2.4 | 50.17 | -0.715 | -0.805 | -8.05 | -2.825 | -2.825 | 0 | 12 | 1 | 1 | -2.825 | 10 | 0 | 0
1128.95 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.14 | -0.43 | -0.705 | -7.05 | -1.375 | -1.375 | 0 | 12 | 1 | 1 | -1.375 | 10 | 0 | 0
1129 | 49.83 | 49.83 | 0.715 | 0.715 | 7.15 | 50.12 | -0.24 | -0.605 | -6.05 | 0.55 | 0.55 | 0 | 12 | 1 | 1 | 0.55 | 10 | 0 | 0
1129.05 | 49.81 | 49.81 | 0.905 | 0.905 | 9.05 | 50.09 | -0.044118 | -0.505 | -5.05 | 2 | 2 | 0 | 12 | 1 | 1 | 2 | 10 | 0 | 0
1129.1 | 49.78 | 49.78 | 1 | 1 | 10 | 50.06 | -0.026471 | -0.405 | -4.05 | 2.975 | 2.975 | 0 | 12 | 1 | 1 | 2.975 | 10 | 0 | 0
1129.15 | 49.76 | 49.76 | 1 | 1 | 10 | 50.04 | -0.014706 | -0.305 | -3.05 | 3.475 | 3.475 | 0 | 12 | 1 | 1 | 3.475 | 10 | 0 | 0
1129.2 | 49.73 | 49.73 | 1 | 1 | 10 | 50.01 | 0 | -0.205 | -2.05 | 3.975 | 3.975 | 0 | 12 | 1 | 1 | 3.975 | 10 | 0 | 0
1129.25 | 49.71 | 49.71 | 1 | 1 | 10 | 49.99 | 0 | -0.105 | -1.05 | 4.475 | 4.475 | 0 | 12 | 1 | 1 | 4.475 | 10 | 0 | 0
1129.3 | 49.68 | 49.68 | 1 | 1 | 10 | 49.96 | 0.014706 | -0.005 | -0.05 | 4.975 | 4.975 | 0 | 12 | 1 | 1 | 4.975 | 10 | 0 | 0
1129.35 | 49.65 | 49.65 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
1129.4 | 49.63 | 49.63 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1129.45 | 49.6 | 49.6 | 1 | 1 | 10 | 49.88 | 0.24 | 0.14412 | 1.4412 | 5.7206 | 5.7206 | 0 | 12 | 1 | 1 | 5.7206 | 10 | 0 | 0
1129.5 | 49.58 | 49.58 | 1 | 1 | 10 | 49.86 | 0.43 | 0.24412 | 2.4412 | 6.2206 | 6.2206 | 0 | 12 | 1 | 1 | 6.2206 | 10 | 0 | 0
1129.55 | 49.55 | 49.55 | 1 | 1 | 10 | 49.83 | 0.715 | 0.34412 | 3.4412 | 6.7206 | 6.7206 | 0 | 12 | 1 | 1 | 6.7206 | 10 | 0 | 0
1129.6 | 49.53 | 49.53 | 1 | 1 | 10 | 49.81 | 0.905 | 0.44412 | 4.4412 | 7.2206 | 7.2206 | 0 | 12 | 1 | 1 | 7.2206 | 10 | 0 | 0
1129.65 | 49.5 | 49.5 | 1 | 1 | 10 | 49.78 | 1 | 0.54412 | 5.4412 | 7.7206 | 7.7206 | 0 | 12 | 1 | 1 | 7.7206 | 10 | 0 | 0
1129.7 | 49.5 | 49.5 | 1 | 1 | 10 | 49.76 | 1 | 0.64412 | 6.4412 | 8.2206 | 8.2206 | 0 | 12 | 1 | 1 | 8.2206 | 10 | 0 | 0
1129.75 | 49.53 | 49.5 | 1 | 1 | 10 | 49.73 | 1 | 0.74412 | 7.4412 | 8.7206 | 8.7206 | 0 | 12 | 1 | 1 | 8.7206 | 10 | 0 | 0
1129.8 | 49.55 | 49.5 | 1 | 1 | 10 | 49.71 | 1 | 0.84412 | 8.4412 | 9.2206 | 9.2206 | 0 | 12 | 1 | 1 | 9.2206 | 10 | 0 | 0
1129.85 | 49.58 | 49.5 | 1 | 1 | 10 | 49.68 | 1 | 0.94412 | 9.4412 | 9.7206 | 9.7206 | 0 | 12 | 1 | 1 | 9.7206 | 10 | 0 | 0
1129.9 | 49.6 | 49.5 | 1 | 1 | 10 | 49.65 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1129.95 | 49.63 | 49.5 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1130 | 49.65 | 49.5 | 1 | 1 | 10 | 49.65 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1130.05 | 49.68 | 49.5 | 1 | 1 | 10 | 49.68 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1130.1 | 49.71 | 49.5 | 1 | 1 | 10 | 49.71 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1130.15 | 49.73 | 49.5 | 1 | 1 | 10 | 49.73 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1130.2 | 49.76 | 49.5 | 1 | 1 | 10 | 49.76 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1130.25 | 49.78 | 49.5 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1130.3 | 49.81 | 49.53 | 1 | 1 | 10 | 49.81 | 0.905 | 0.905 | 9.05 | 9.525 | 9.525 | 0 | 12 | 1 | 1 | 9.525 | 10 | 0 | 0
1130.35 | 49.83 | 49.55 | 1 | 1 | 10 | 49.83 | 0.715 | 0.715 | 7.15 | 8.575 | 8.575 | 0 | 12 | 1 | 1 | 8.575 | 10 | 0 | 0
1130.4 | 49.86 | 49.58 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
1130.45 | 49.88 | 49.6 | 1 | 1 | 10 | 49.88 | 0.24 | 0.24 | 2.4 | 6.2 | 6.2 | 0 | 12 | 1 | 1 | 6.2 | 10 | 0 | 0
1130.5 | 49.91 | 49.63 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1130.55 | 49.94 | 49.65 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
1130.6 | 49.96 | 49.68 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
1130.65 | 49.99 | 49.71 | 1 | 1 | 10 | 49.99 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1130.7 | 50.01 | 49.73 | 1 | 1 | 10 | 50.01 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1130.75 | 50.04 | 49.76 | 1 | 1 | 10 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 4.9265 | 4.9265 | 0 | 12 | 1 | 1 | 4.9265 | 10 | 0 | 0
1130.8 | 50.06 | 49.78 | 1 | 1 | 10 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 4.8676 | 4.8676 | 0 | 12 | 1 | 1 | 4.8676 | 10 | 0 | 0
1130.85 | 50.09 | 49.81 | 0.905 | 0.905 | 9.05 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 4.3044 | 4.3044 | 0 | 12 | 1 | 1 | 4.3044 | 10 | 0 | 0
1130.9 | 50.12 | 49.83 | 0.715 | 0.805 | 8.05 | 50.12 | -0.24 | -0.24 | -2.4 | 2.825 | 2.825 | 0 | 12 | 1 | 1 | 2.825 | 10 | 0 | 0
1130.95 | 50.14 | 49.86 | 0.43 | 0.705 | 7.05 | 50.14 | -0.43 | -0.43 | -4.3 | 1.375 | 1.375 | 0 | 12 | 1 | 1 | 1.375 | 10 | 0 | 0
1131 | 50.17 | 49.88 | 0.24 | 0.605 | 6.05 | 50.17 | -0.715 | -0.715 | -7.15 | -0.55 | -0.55 | 0 | 12 | 1 | 1 | -0.55 | 10 | 0 | 0
1131.05 | 50.19 | 49.91 | 0.044118 | 0.505 | 5.05 | 50.19 | -0.905 | -0.905 | -9.05 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
1131.1 | 50.22 | 49.94 | 0.026471 | 0.405 | 4.05 | 50.22 | -1 | -1 | -10 | -2.975 | -2.975 | 0 | 12 | 1 | 1 | -2.975 | 10 | 0 | 0
1131.15 | 50.24 | 49.96 | 0.014706 | 0.305 | 3.05 | 50.24 | -1 | -1 | -10 | -3.475 | -3.475 | 0 | 12 | 1 | 1 | -3.475 | 10 | 0 | 0
1131.2 | 50.27 | 49.99 | 0 | 0.205 | 2.05 | 50.27 | -1 | -1 | -10 | -3.975 | -3.975 | 0 | 12 | 1 | 1 | -3.975 | 10 | 0 | 0
1131.25 | 50.29 | 50.01 | 0 | 0.105 | 1.05 | 50.29 | -1 | -1 | -10 | -4.475 | -4.475 | 0 | 12 | 1 | 1 | -4.475 | 10 | 0 | 0
1131.3 | 50.32 | 50.04 | -0.014706 | 0.005 | 0.05 | 50.32 | -1 | -1 | -10 | -4.975 | -4.975 | 0 | 12 | 1 | 1 | -4.975 | 10 | 0 | 0
1131.35 | 50.35 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.35 | -1 | -1 | -10 | -5.1324 | -5.1324 | 0 | 12 | 1 | 1 | -5.1324 | 10 | 0 | 0
1131.4 | 50.37 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 50.37 | -1 | -1 | -10 | -5.2206 | -5.2206 | 0 | 12 | 1 | 1 | -5.2206 | 10 | 0 | 0
1131.45 | 50.4 | 50.12 | -0.24 | -0.14412 | -1.4412 | 50.4 | -1 | -1 | -10 | -5.7206 | -5.7206 | 0 | 12 | 1 | 1 | -5.7206 | 10 | 0 | 0
1131.5 | 50.42 | 50.14 | -0.43 | -0.24412 | -2.4412 | 50.42 | -1 | -1 | -10 | -6.2206 | -6.2206 | 0 | 12 | 1 | 1 | -6.2206 | 10 | 0 | 0
1131.55 | 50.45 | 50.17 | -0.715 | -0.34412 | -3.4412 | 50.45 | -1 | -1 | -10 | -6.7206 | -6.7206 | 0 | 12 | 1 | 1 | -6.7206 | 10 | 0 | 0
1131.6 | 50.47 | 50.19 | -0.905 | -0.44412 | -4.4412 | 50.47 | -1 | -1 | -10 | -7.2206 | -7.2206 | 0 | 12 | 1 | 1 | -7.2206 | 10 | 0 | 0
1131.65 | 50.5 | 50.22 | -1 | -0.54412 | -5.4412 | 50.5 | -1 | -1 | -10 | -7.7206 | -7.7206 | 0 | 12 | 1 | 1 | -7.7206 | 10 | 0 | 0
1131.7 | 50.5 | 50.24 | -1 | -0.64412 | -6.4412 | 50.5 | -1 | -1 | -10 | -8.2206 | -8.2206 | 0 | 12 | 1 | 1 | -8.2206 | 10 | 0 | 0
1131.75 | 50.47 | 50.27 | -1 | -0.74412 | -7.4412 | 50.5 | -1 | -1 | -10 | -8.7206 | -8.7206 | 0 | 12 | 1 | 1 | -8.7206 | 10 | 0 | 0
1131.8 | 50.45 | 50.29 | -1 | -0.84412 | -8.4412 | 50.5 | -1 | -1 | -10 | -9.2206 | -9.2206 | 0 | 12 | 1 | 1 | -9.2206 | 10 | 0 | 0
1131.85 | 50.42 | 50.32 | -1 | -0.94412 | -9.4412 | 50.5 | -1 | -1 | -10 | -9.7206 | -9.7206 | 0 | 12 | 1 | 1 | -9.7206 | 10 | 0 | 0
1131.9 | 50.39 | 50.35 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1131.95 | 50.37 | 50.37 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1132 | 50.34 | 50.34 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1132.05 | 50.32 | 50.32 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1132.1 | 50.29 | 50.29 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1132.15 | 50.26 | 50.26 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1132.2 | 50.24 | 50.24 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1132.25 | 50.21 | 50.21 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1132.3 | 50.18 | 50.18 | -0.81 | -0.81 | -8.1 | 50.47 | -1 | -1 | -10 | -9.05 | -9.05 | 0 | 12 | 1 | 1 | -9.05 | 10 | 0 | 0
1132.35 | 50.16 | 50.16 | -0.62 | -0.62 | -6.2 | 50.45 | -1 | -1 | -10 | -8.1 | -8.1 | 0 | 12 | 1 | 1 | -8.1 | 10 | 0 | 0
1132.4 | 50.13 | 50.13 | -0.335 | -0.335 | -3.35 | 50.42 | -1 | -1 | -10 | -6.675 | -6.675 | 0 | 12 | 1 | 1 | -6.675 | 10 | 0 | 0
1132.45 | 50.11 | 50.11 | -0.145 | -0.145 | -1.45 | 50.39 | -1 | -1 | -10 | -5.725 | -5.725 | 0 | 12 | 1 | 1 | -5.725 | 10 | 0 | 0
1132.5 | 50.08 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 50.37 | -1 | -1 | -10 | -5.1912 | -5.1912 | 0 | 12 | 1 | 1 | -5.1912 | 10 | 0 | 0
1132.55 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.34 | -1 | -1 | -10 | -5.1029 | -5.1029 | 0 | 12 | 1 | 1 | -5.1029 | 10 | 0 | 0
1132.6 | 50.03 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 50.32 | -1 | -1 | -10 | -5.0441 | -5.0441 | 0 | 12 | 1 | 1 | -5.0441 | 10 | 0 | 0
1132.65 | 50 | 50 | 0 | 0 | 0 | 50.29 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1132.7 | 50 | 50 | 0 | 0 | 0 | 50.26 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1132.75 | 50 | 50 | 0 | 0 | 0 | 50.24 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1132.8 | 50 | 50 | 0 | 0 | 0 | 50.21 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1132.85 | 50 | 50 | 0 | 0 | 0 | 50.18 | -0.81 | -0.9 | -9 | -4.5 | -4.5 | 0 | 12 | 1 | 1 | -4.5 | 10 | 0 | 0
1132.9 | 50 | 50 | 0 | 0 | 0 | 50.16 | -0.62 | -0.8 | -8 | -4 | -4 | 0 | 12 | 1 | 1 | -4 | 10 | 0 | 0
1132.95 | 50 | 50 | 0 | 0 | 0 | 50.13 | -0.335 | -0.7 | -7 | -3.5 | -3.5 | 0 | 12 | 1 | 1 | -3.5 | 10 | 0 | 0
1133 | 50.01 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.6 | -6 | -3 | -3 | 0 | 12 | 1 | 1 | -3 | 10 | 0 | 0
1133.05 | 50.01 | 50 | 0 | 0 | 0 | 50.08 | -0.038235 | -0.5 | -5 | -2.5 | -2.5 | 0 | 12 | 1 | 1 | -2.5 | 10 | 0 | 0
1133.1 | 49.99 | 49.99 | 0 | 0 | 0 | 50.05 | -0.020588 | -0.4 | -4 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
1133.15 | 49.99 | 49.99 | 0 | 0 | 0 | 50.03 | -0.0088235 | -0.3 | -3 | -1.5 | -1.5 | 0 | 12 | 1 | 1 | -1.5 | 10 | 0 | 0
1133.2 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | -0.2 | -2 | -0.83824 | -0.83824 | 0 | 12 | 1 | 1 | -0.83824 | 10 | 0 | 0
1133.25 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | -0.1 | -1 | -0.33824 | -0.33824 | 0 | 12 | 1 | 1 | -0.33824 | 10 | 0 | 0
1133.3 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
1133.35 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
1133.4 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
1133.45 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
1133.5 | 49.89 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
1133.55 | 49.89 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
1133.6 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50.01 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1133.65 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1133.7 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1133.75 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 2.7868 | 2.7868 | 0 | 12 | 1 | 1 | 2.7868 | 10 | 0 | 0
1133.8 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 2.7868 | 2.7868 | 0 | 12 | 1 | 1 | 2.7868 | 10 | 0 | 0
1133.85 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 2.8456 | 2.8456 | 0 | 12 | 1 | 1 | 2.8456 | 10 | 0 | 0
1133.9 | 49.94 | 49.85 | 0.525 | 0.525 | 5.25 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 2.7574 | 2.7574 | 0 | 12 | 1 | 1 | 2.7574 | 10 | 0 | 0
1133.95 | 49.94 | 49.85 | 0.525 | 0.525 | 5.25 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 2.7574 | 2.7574 | 0 | 12 | 1 | 1 | 2.7574 | 10 | 0 | 0
1134 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1134.05 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1134.1 | 49.93 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1134.15 | 49.93 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1134.2 | 49.96 | 49.85 | 0.525 | 0.525 | 5.25 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 2.6985 | 2.6985 | 0 | 12 | 1 | 1 | 2.6985 | 10 | 0 | 0
1134.25 | 49.96 | 49.85 | 0.525 | 0.525 | 5.25 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 2.6985 | 2.6985 | 0 | 12 | 1 | 1 | 2.6985 | 10 | 0 | 0
1134.3 | 49.99 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1134.35 | 49.99 | 49.91 | 0.044118 | 0.425 | 4.25 | 49.99 | 0 | 0 | 0 | 2.125 | 2.125 | 0 | 12 | 1 | 1 | 2.125 | 10 | 0 | 0
1134.4 | 49.99 | 49.91 | 0.044118 | 0.325 | 3.25 | 49.99 | 0 | 0 | 0 | 1.625 | 1.625 | 0 | 12 | 1 | 1 | 1.625 | 10 | 0 | 0
1134.45 | 49.99 | 49.93 | 0.032353 | 0.225 | 2.25 | 49.99 | 0 | 0 | 0 | 1.125 | 1.125 | 0 | 12 | 1 | 1 | 1.125 | 10 | 0 | 0
1134.5 | 49.96 | 49.93 | 0.032353 | 0.125 | 1.25 | 49.99 | 0 | 0 | 0 | 0.625 | 0.625 | 0 | 12 | 1 | 1 | 0.625 | 10 | 0 | 0
1134.55 | 49.96 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 49.99 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1134.6 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1134.65 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1134.7 | 50.05 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.058824 | 0.058824 | 0 | 12 | 1 | 1 | 0.058824 | 10 | 0 | 0
1134.75 | 50.05 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
1134.8 | 49.97 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
1134.85 | 49.97 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
1134.9 | 49.92 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1134.95 | 49.92 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1135 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1135.05 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1135.1 | 49.94 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1135.15 | 49.94 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1135.2 | 50.01 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1135.25 | 50.01 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1135.3 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1135.35 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
1135.4 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
1135.45 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
1135.5 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
1135.55 | 49.95 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
1135.6 | 49.97 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
1135.65 | 49.97 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
1135.7 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
1135.75 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
1135.8 | 49.87 | 49.87 | 0.335 | 0.335 | 3.35 | 50.01 | 0 | 0 | 0 | 1.675 | 1.675 | 0 | 12 | 1 | 1 | 1.675 | 10 | 0 | 0
1135.85 | 49.87 | 49.87 | 0.335 | 0.335 | 3.35 | 49.99 | 0 | 0 | 0 | 1.675 | 1.675 | 0 | 12 | 1 | 1 | 1.675 | 10 | 0 | 0
1135.9 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1135.95 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 2.6691 | 2.6691 | 0 | 12 | 1 | 1 | 2.6691 | 10 | 0 | 0
1136 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1136.05 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1136.1 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1136.15 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1136.2 | 49.84 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1136.25 | 49.84 | 49.79 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
1136.3 | 49.89 | 49.79 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
1136.35 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.12647 | 1.2647 | 5.6324 | 5.6324 | 0 | 12 | 1 | 1 | 5.6324 | 10 | 0 | 0
1136.4 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.145 | 1.45 | 5.725 | 5.725 | 0 | 12 | 1 | 1 | 5.725 | 10 | 0 | 0
1136.45 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.145 | 1.45 | 5.725 | 5.725 | 0 | 12 | 1 | 1 | 5.725 | 10 | 0 | 0
1136.5 | 49.96 | 49.79 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
1136.55 | 49.96 | 49.79 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
1136.6 | 50.02 | 49.79 | 1 | 1 | 10 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 4.9853 | 4.9853 | 0 | 12 | 1 | 1 | 4.9853 | 10 | 0 | 0
1136.65 | 50.02 | 49.79 | 1 | 1 | 10 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 4.9853 | 4.9853 | 0 | 12 | 1 | 1 | 4.9853 | 10 | 0 | 0
1136.7 | 50.03 | 49.79 | 1 | 1 | 10 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.9559 | 4.9559 | 0 | 12 | 1 | 1 | 4.9559 | 10 | 0 | 0
1136.75 | 50.03 | 49.84 | 0.62 | 0.9 | 9 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.4559 | 4.4559 | 0 | 12 | 1 | 1 | 4.4559 | 10 | 0 | 0
1136.8 | 50.02 | 49.84 | 0.62 | 0.8 | 8 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 3.9559 | 3.9559 | 0 | 12 | 1 | 1 | 3.9559 | 10 | 0 | 0
1136.85 | 50.02 | 49.89 | 0.145 | 0.7 | 7 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 3.4559 | 3.4559 | 0 | 12 | 1 | 1 | 3.4559 | 10 | 0 | 0
1136.9 | 50.08 | 49.89 | 0.145 | 0.6 | 6 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 2.8088 | 2.8088 | 0 | 12 | 1 | 1 | 2.8088 | 10 | 0 | 0
1136.95 | 50.08 | 49.89 | 0.145 | 0.5 | 5 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 2.3088 | 2.3088 | 0 | 12 | 1 | 1 | 2.3088 | 10 | 0 | 0
1137 | 50.01 | 49.89 | 0.145 | 0.4 | 4 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 1.8088 | 1.8088 | 0 | 12 | 1 | 1 | 1.8088 | 10 | 0 | 0
1137.05 | 50.01 | 49.96 | 0.014706 | 0.3 | 3 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 1.3088 | 1.3088 | 0 | 12 | 1 | 1 | 1.3088 | 10 | 0 | 0
1137.1 | 49.94 | 49.94 | 0.026471 | 0.2 | 2 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.80882 | 0.80882 | 0 | 12 | 1 | 1 | 0.80882 | 10 | 0 | 0
1137.15 | 49.94 | 49.94 | 0.026471 | 0.1 | 1 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.30882 | 0.30882 | 0 | 12 | 1 | 1 | 0.30882 | 10 | 0 | 0
1137.2 | 50 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
1137.25 | 50 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
1137.3 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
1137.35 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
1137.4 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1137.45 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1137.5 | 49.92 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1137.55 | 49.92 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
1137.6 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50.01 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1137.65 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1137.7 | 49.92 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1137.75 | 49.92 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1137.8 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1137.85 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1137.9 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1137.95 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1138 | 49.87 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1138.05 | 49.87 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1138.1 | 49.8 | 49.8 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1138.15 | 49.8 | 49.8 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1138.2 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1138.25 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1138.3 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1138.35 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1138.4 | 49.72 | 49.72 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1138.45 | 49.72 | 49.72 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1138.5 | 49.67 | 49.67 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1138.55 | 49.67 | 49.67 | 1 | 1 | 10 | 49.87 | 0.335 | 0.14412 | 1.4412 | 5.7206 | 5.7206 | 0 | 12 | 1 | 1 | 5.7206 | 10 | 0 | 0
1138.6 | 49.65 | 49.65 | 1 | 1 | 10 | 49.87 | 0.335 | 0.24412 | 2.4412 | 6.2206 | 6.2206 | 0 | 12 | 1 | 1 | 6.2206 | 10 | 0 | 0
1138.65 | 49.65 | 49.65 | 1 | 1 | 10 | 49.8 | 1 | 0.34412 | 3.4412 | 6.7206 | 6.7206 | 0 | 12 | 1 | 1 | 6.7206 | 10 | 0 | 0
1138.7 | 49.59 | 49.59 | 1 | 1 | 10 | 49.8 | 1 | 0.44412 | 4.4412 | 7.2206 | 7.2206 | 0 | 12 | 1 | 1 | 7.2206 | 10 | 0 | 0
1138.75 | 49.59 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.54412 | 5.4412 | 7.7206 | 7.7206 | 0 | 12 | 1 | 1 | 7.7206 | 10 | 0 | 0
1138.8 | 49.66 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.64412 | 6.4412 | 8.2206 | 8.2206 | 0 | 12 | 1 | 1 | 8.2206 | 10 | 0 | 0
1138.85 | 49.66 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.74412 | 7.4412 | 8.7206 | 8.7206 | 0 | 12 | 1 | 1 | 8.7206 | 10 | 0 | 0
1138.9 | 49.63 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.84412 | 8.4412 | 9.2206 | 9.2206 | 0 | 12 | 1 | 1 | 9.2206 | 10 | 0 | 0
1138.95 | 49.63 | 49.59 | 1 | 1 | 10 | 49.72 | 1 | 0.94412 | 9.4412 | 9.7206 | 9.7206 | 0 | 12 | 1 | 1 | 9.7206 | 10 | 0 | 0
1139 | 49.61 | 49.59 | 1 | 1 | 10 | 49.72 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1139.05 | 49.61 | 49.59 | 1 | 1 | 10 | 49.67 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1139.1 | 49.54 | 49.54 | 1 | 1 | 10 | 49.67 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1139.15 | 49.54 | 49.54 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1139.2 | 49.46 | 49.46 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1139.25 | 49.46 | 49.46 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1139.3 | 49.45 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1139.35 | 49.45 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1139.4 | 49.51 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1139.45 | 49.51 | 49.45 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1139.5 | 49.5 | 49.45 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1139.55 | 49.5 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1139.6 | 49.54 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1139.65 | 49.54 | 49.45 | 1 | 1 | 10 | 49.54 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1139.7 | 49.59 | 49.45 | 1 | 1 | 10 | 49.59 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1139.75 | 49.59 | 49.45 | 1 | 1 | 10 | 49.59 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1139.8 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1139.85 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1139.9 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1139.95 | 49.61 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1140 | 49.53 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1140.05 | 49.53 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1140.1 | 49.54 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1140.15 | 49.54 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1140.2 | 49.61 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1140.25 | 49.61 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1140.3 | 49.66 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1140.35 | 49.66 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1140.4 | 49.64 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1140.45 | 49.64 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1140.5 | 49.69 | 49.53 | 1 | 1 | 10 | 49.69 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1140.55 | 49.69 | 49.53 | 1 | 1 | 10 | 49.69 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1140.6 | 49.74 | 49.53 | 1 | 1 | 10 | 49.74 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1140.65 | 49.74 | 49.54 | 1 | 1 | 10 | 49.74 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1140.7 | 49.78 | 49.54 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1140.75 | 49.78 | 49.61 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1140.8 | 49.82 | 49.61 | 1 | 1 | 10 | 49.82 | 0.81 | 0.81 | 8.1 | 9.05 | 9.05 | 0 | 12 | 1 | 1 | 9.05 | 10 | 0 | 0
1140.85 | 49.82 | 49.64 | 1 | 1 | 10 | 49.82 | 0.81 | 0.81 | 8.1 | 9.05 | 9.05 | 0 | 12 | 1 | 1 | 9.05 | 10 | 0 | 0
1140.9 | 49.86 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
1140.95 | 49.86 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
1141 | 49.84 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
1141.05 | 49.84 | 49.69 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
1141.1 | 49.91 | 49.69 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1141.15 | 49.91 | 49.74 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1141.2 | 49.97 | 49.74 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1141.25 | 49.97 | 49.78 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1141.3 | 50.03 | 49.78 | 1 | 1 | 10 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.9559 | 4.9559 | 0 | 12 | 1 | 1 | 4.9559 | 10 | 0 | 0
1141.35 | 50.03 | 49.82 | 0.81 | 0.9 | 9 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.4559 | 4.4559 | 0 | 12 | 1 | 1 | 4.4559 | 10 | 0 | 0
1141.4 | 50.05 | 49.82 | 0.81 | 0.81 | 8.1 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 3.9471 | 3.9471 | 0 | 12 | 1 | 1 | 3.9471 | 10 | 0 | 0
1141.45 | 50.05 | 49.84 | 0.62 | 0.71 | 7.1 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 3.4471 | 3.4471 | 0 | 12 | 1 | 1 | 3.4471 | 10 | 0 | 0
1141.5 | 50.01 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
1141.55 | 50.01 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
1141.6 | 49.95 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
1141.65 | 49.95 | 49.91 | 0.044118 | 0.52 | 5.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.4971 | 2.4971 | 0 | 12 | 1 | 1 | 2.4971 | 10 | 0 | 0
1141.7 | 49.99 | 49.91 | 0.044118 | 0.42 | 4.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 1.9971 | 1.9971 | 0 | 12 | 1 | 1 | 1.9971 | 10 | 0 | 0
1141.75 | 49.99 | 49.95 | 0.020588 | 0.32 | 3.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 1.4971 | 1.4971 | 0 | 12 | 1 | 1 | 1.4971 | 10 | 0 | 0
1141.8 | 49.92 | 49.92 | 0.038235 | 0.22 | 2.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.99706 | 0.99706 | 0 | 12 | 1 | 1 | 0.99706 | 10 | 0 | 0
1141.85 | 49.92 | 49.92 | 0.038235 | 0.12 | 1.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.49706 | 0.49706 | 0 | 12 | 1 | 1 | 0.49706 | 10 | 0 | 0
1141.9 | 49.97 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1141.95 | 49.97 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1142 | 50.02 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1142.05 | 50.02 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.17647 | 0.17647 | 0 | 12 | 1 | 1 | 0.17647 | 10 | 0 | 0
1142.1 | 50.07 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1142.15 | 50.07 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1142.2 | 50.06 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1142.25 | 50.06 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1142.3 | 50.13 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
1142.35 | 50.13 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
1142.4 | 50.09 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
1142.45 | 50.09 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6309 | -1.6309 | 0 | 12 | 1 | 1 | -1.6309 | 10 | 0 | 0
1142.5 | 50.07 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6309 | -1.6309 | 0 | 12 | 1 | 1 | -1.6309 | 10 | 0 | 0
1142.55 | 50.07 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6897 | -1.6897 | 0 | 12 | 1 | 1 | -1.6897 | 10 | 0 | 0
1142.6 | 50.07 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6897 | -1.6897 | 0 | 12 | 1 | 1 | -1.6897 | 10 | 0 | 0
1142.65 | 50.07 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.13 | -0.335 | -0.335 | -3.35 | -1.8074 | -1.8074 | 0 | 12 | 1 | 1 | -1.8074 | 10 | 0 | 0
1142.7 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.13 | -0.335 | -0.335 | -3.35 | -1.7779 | -1.7779 | 0 | 12 | 1 | 1 | -1.7779 | 10 | 0 | 0
1142.75 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.13 | -0.335 | -0.335 | -3.35 | -1.7779 | -1.7779 | 0 | 12 | 1 | 1 | -1.7779 | 10 | 0 | 0
1142.8 | 50.01 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
1142.85 | 50.01 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
1142.9 | 50.07 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
1142.95 | 50.07 | 50.01 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.235 | -2.35 | -1.175 | -1.175 | 0 | 12 | 1 | 1 | -1.175 | 10 | 0 | 0
1143 | 50.05 | 50.01 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.135 | -1.35 | -0.675 | -0.675 | 0 | 12 | 1 | 1 | -0.675 | 10 | 0 | 0
1143.05 | 50.05 | 50.01 | 0 | 0 | 0 | 50.07 | -0.032353 | -0.035 | -0.35 | -0.175 | -0.175 | 0 | 12 | 1 | 1 | -0.175 | 10 | 0 | 0
1143.1 | 50.1 | 50.01 | 0 | 0 | 0 | 50.1 | -0.05 | -0.05 | -0.5 | -0.25 | -0.25 | 0 | 12 | 1 | 1 | -0.25 | 10 | 0 | 0
1143.15 | 50.1 | 50.01 | 0 | 0 | 0 | 50.1 | -0.05 | -0.05 | -0.5 | -0.25 | -0.25 | 0 | 12 | 1 | 1 | -0.25 | 10 | 0 | 0
1143.2 | 50.11 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1143.25 | 50.11 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1143.3 | 50.06 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1143.35 | 50.06 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1143.4 | 50.04 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1143.45 | 50.04 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1143.5 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1143.55 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1143.6 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1143.65 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1143.7 | 50.11 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1143.75 | 50.11 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1143.8 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1143.85 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1143.9 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1143.95 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1144 | 50.02 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.11 | -0.145 | -0.145 | -1.45 | -0.73971 | -0.73971 | 0 | 12 | 1 | 1 | -0.73971 | 10 | 0 | 0
1144.05 | 50.02 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.11 | -0.145 | -0.145 | -1.45 | -0.73971 | -0.73971 | 0 | 12 | 1 | 1 | -0.73971 | 10 | 0 | 0
1144.1 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1144.15 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1144.2 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1144.25 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1144.3 | 50.01 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1144.35 | 50.01 | 50 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.045 | -0.45 | -0.225 | -0.225 | 0 | 12 | 1 | 1 | -0.225 | 10 | 0 | 0
1144.4 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
1144.45 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
1144.5 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
1144.55 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1144.6 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.14706 | 0.14706 | 0 | 12 | 1 | 1 | 0.14706 | 10 | 0 | 0
1144.65 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1144.7 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1144.75 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1144.8 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1144.85 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1144.9 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1144.95 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1145 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1145.05 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1145.1 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1145.15 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1145.2 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1145.25 | 50 | 50 | 0 | 0 | 0 | 50.01 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1145.3 | 49.5 | 49.5 | 1 | 1 | 10 | 50.01 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1145.35 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1145.4 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1145.45 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1145.5 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1145.55 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1145.6 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1145.65 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1145.7 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1145.75 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1145.8 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1145.85 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.1 | 1 | 5.5 | 5.5 | 0 | 12 | 1 | 1 | 5.5 | 10 | 0 | 0
1145.9 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.2 | 2 | 6 | 6 | 0 | 12 | 1 | 1 | 6 | 10 | 0 | 0
1145.95 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.3 | 3 | 6.5 | 6.5 | 0 | 12 | 1 | 1 | 6.5 | 10 | 0 | 0
1146 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.4 | 4 | 7 | 7 | 0 | 12 | 1 | 1 | 7 | 10 | 0 | 0
1146.05 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.5 | 5 | 7.5 | 7.5 | 0 | 12 | 1 | 1 | 7.5 | 10 | 0 | 0
1146.1 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.6 | 6 | 8 | 8 | 0 | 12 | 1 | 1 | 8 | 10 | 0 | 0
1146.15 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.7 | 7 | 8.5 | 8.5 | 0 | 12 | 1 | 1 | 8.5 | 10 | 0 | 0
1146.2 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.8 | 8 | 9 | 9 | 0 | 12 | 1 | 1 | 9 | 10 | 0 | 0
1146.25 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.9 | 9 | 9.5 | 9.5 | 0 | 12 | 1 | 1 | 9.5 | 10 | 0 | 0
1146.3 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1146.35 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1146.4 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1146.45 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1146.5 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1146.55 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1146.6 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1146.65 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1146.7 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1146.75 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1146.8 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1146.85 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1146.9 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1146.95 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1147 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1147.05 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1147.1 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1147.15 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1147.2 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1147.25 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1147.3 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1147.35 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1147.4 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1147.45 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1147.5 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1147.55 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1147.6 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1147.65 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1147.7 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1147.75 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1147.8 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1147.85 | 50.5 | 50.5 | -1 | 0.9 | 9 | 50.5 | -1 | -1 | -10 | -0.5 | -0.5 | 0 | 12 | 1 | 1 | -0.5 | 10 | 0 | 0
1147.9 | 50.5 | 50.5 | -1 | 0.8 | 8 | 50.5 | -1 | -1 | -10 | -1 | -1 | 0 | 12 | 1 | 1 | -1 | 10 | 0 | 0
1147.95 | 50.5 | 50.5 | -1 | 0.7 | 7 | 50.5 | -1 | -1 | -10 | -1.5 | -1.5 | 0 | 12 | 1 | 1 | -1.5 | 10 | 0 | 0
1148 | 50.5 | 50.5 | -1 | 0.6 | 6 | 50.5 | -1 | -1 | -10 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
1148.05 | 50.5 | 50.5 | -1 | 0.5 | 5 | 50.5 | -1 | -1 | -10 | -2.5 | -2.5 | 0 | 12 | 1 | 1 | -2.5 | 10 | 0 | 0
1148.1 | 50.5 | 50.5 | -1 | 0.4 | 4 | 50.5 | -1 | -1 | -10 | -3 | -3 | 0 | 12 | 1 | 1 | -3 | 10 | 0 | 0
1148.15 | 50.5 | 50.5 | -1 | 0.3 | 3 | 50.5 | -1 | -1 | -10 | -3.5 | -3.5 | 0 | 12 | 1 | 1 | -3.5 | 10 | 0 | 0
1148.2 | 50.5 | 50.5 | -1 | 0.2 | 2 | 50.5 | -1 | -1 | -10 | -4 | -4 | 0 | 12 | 1 | 1 | -4 | 10 | 0 | 0
1148.25 | 50.5 | 50.5 | -1 | 0.1 | 1 | 50.5 | -1 | -1 | -10 | -4.5 | -4.5 | 0 | 12 | 1 | 1 | -4.5 | 10 | 0 | 0
1148.3 | 50.5 | 50.5 | -1 | 0 | 0 | 50.5 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1148.35 | 50.5 | 50.5 | -1 | -0.1 | -1 | 50.5 | -1 | -1 | -10 | -5.5 | -5.5 | 0 | 12 | 1 | 1 | -5.5 | 10 | 0 | 0
1148.4 | 50.5 | 50.5 | -1 | -0.2 | -2 | 50.5 | -1 | -1 | -10 | -6 | -6 | 0 | 12 | 1 | 1 | -6 | 10 | 0 | 0
1148.45 | 50.5 | 50.5 | -1 | -0.3 | -3 | 50.5 | -1 | -1 | -10 | -6.5 | -6.5 | 0 | 12 | 1 | 1 | -6.5 | 10 | 0 | 0
1148.5 | 50.5 | 50.5 | -1 | -0.4 | -4 | 50.5 | -1 | -1 | -10 | -7 | -7 | 0 | 12 | 1 | 1 | -7 | 10 | 0 | 0
1148.55 | 50.5 | 50.5 | -1 | -0.5 | -5 | 50.5 | -1 | -1 | -10 | -7.5 | -7.5 | 0 | 12 | 1 | 1 | -7.5 | 10 | 0 | 0
1148.6 | 50.5 | 50.5 | -1 | -0.6 | -6 | 50.5 | -1 | -1 | -10 | -8 | -8 | 0 | 12 | 1 | 1 | -8 | 10 | 0 | 0
1148.65 | 50.5 | 50.5 | -1 | -0.7 | -7 | 50.5 | -1 | -1 | -10 | -8.5 | -8.5 | 0 | 12 | 1 | 1 | -8.5 | 10 | 0 | 0
1148.7 | 50.5 | 50.5 | -1 | -0.8 | -8 | 50.5 | -1 | -1 | -10 | -9 | -9 | 0 | 12 | 1 | 1 | -9 | 10 | 0 | 0
1148.75 | 50.5 | 50.5 | -1 | -0.9 | -9 | 50.5 | -1 | -1 | -10 | -9.5 | -9.5 | 0 | 12 | 1 | 1 | -9.5 | 10 | 0 | 0
1148.8 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1148.85 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1148.9 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1148.95 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1149 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1149.05 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1149.1 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1149.15 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1149.2 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1149.25 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1149.3 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1149.35 | 50.47 | 50.47 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1149.4 | 50.45 | 50.45 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1149.45 | 50.42 | 50.42 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1149.5 | 50.4 | 50.4 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1149.55 | 50.37 | 50.37 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1149.6 | 50.35 | 50.35 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1149.65 | 50.32 | 50.32 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1149.7 | 50.29 | 50.29 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1149.75 | 50.27 | 50.27 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1149.8 | 50.24 | 50.24 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1149.85 | 50.22 | 50.22 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1149.9 | 50.19 | 50.19 | -0.905 | -0.905 | -9.05 | 50.47 | -1 | -1 | -10 | -9.525 | -9.525 | 0 | 12 | 1 | 1 | -9.525 | 10 | 0 | 0
1149.95 | 50.17 | 50.17 | -0.715 | -0.715 | -7.15 | 50.45 | -1 | -1 | -10 | -8.575 | -8.575 | 0 | 12 | 1 | 1 | -8.575 | 10 | 0 | 0
1150 | 50.14 | 50.14 | -0.43 | -0.43 | -4.3 | 50.42 | -1 | -1 | -10 | -7.15 | -7.15 | 0 | 12 | 1 | 1 | -7.15 | 10 | 0 | 0
1150.05 | 50.12 | 50.12 | -0.24 | -0.24 | -2.4 | 50.4 | -1 | -1 | -10 | -6.2 | -6.2 | 0 | 12 | 1 | 1 | -6.2 | 10 | 0 | 0
1150.1 | 50.09 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 50.37 | -1 | -1 | -10 | -5.2206 | -5.2206 | 0 | 12 | 1 | 1 | -5.2206 | 10 | 0 | 0
1150.15 | 50.06 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.35 | -1 | -1 | -10 | -5.1324 | -5.1324 | 0 | 12 | 1 | 1 | -5.1324 | 10 | 0 | 0
1150.2 | 50.04 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.32 | -1 | -1 | -10 | -5.0735 | -5.0735 | 0 | 12 | 1 | 1 | -5.0735 | 10 | 0 | 0
1150.25 | 50.01 | 50.01 | 0 | 0 | 0 | 50.29 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1150.3 | 49.99 | 49.99 | 0 | 0 | 0 | 50.27 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1150.35 | 49.96 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.24 | -1 | -1 | -10 | -4.9265 | -4.9265 | 0 | 12 | 1 | 1 | -4.9265 | 10 | 0 | 0
1150.4 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.22 | -1 | -1 | -10 | -4.8676 | -4.8676 | 0 | 12 | 1 | 1 | -4.8676 | 10 | 0 | 0
1150.45 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.19 | -0.905 | -0.905 | -9.05 | -4.3044 | -4.3044 | 0 | 12 | 1 | 1 | -4.3044 | 10 | 0 | 0
1150.5 | 49.88 | 49.88 | 0.24 | 0.24 | 2.4 | 50.17 | -0.715 | -0.805 | -8.05 | -2.825 | -2.825 | 0 | 12 | 1 | 1 | -2.825 | 10 | 0 | 0
1150.55 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.14 | -0.43 | -0.705 | -7.05 | -1.375 | -1.375 | 0 | 12 | 1 | 1 | -1.375 | 10 | 0 | 0
1150.6 | 49.83 | 49.83 | 0.715 | 0.715 | 7.15 | 50.12 | -0.24 | -0.605 | -6.05 | 0.55 | 0.55 | 0 | 12 | 1 | 1 | 0.55 | 10 | 0 | 0
1150.65 | 49.81 | 49.81 | 0.905 | 0.905 | 9.05 | 50.09 | -0.044118 | -0.505 | -5.05 | 2 | 2 | 0 | 12 | 1 | 1 | 2 | 10 | 0 | 0
1150.7 | 49.78 | 49.78 | 1 | 1 | 10 | 50.06 | -0.026471 | -0.405 | -4.05 | 2.975 | 2.975 | 0 | 12 | 1 | 1 | 2.975 | 10 | 0 | 0
1150.75 | 49.76 | 49.76 | 1 | 1 | 10 | 50.04 | -0.014706 | -0.305 | -3.05 | 3.475 | 3.475 | 0 | 12 | 1 | 1 | 3.475 | 10 | 0 | 0
1150.8 | 49.73 | 49.73 | 1 | 1 | 10 | 50.01 | 0 | -0.205 | -2.05 | 3.975 | 3.975 | 0 | 12 | 1 | 1 | 3.975 | 10 | 0 | 0
1150.85 | 49.71 | 49.71 | 1 | 1 | 10 | 49.99 | 0 | -0.105 | -1.05 | 4.475 | 4.475 | 0 | 12 | 1 | 1 | 4.475 | 10 | 0 | 0
1150.9 | 49.68 | 49.68 | 1 | 1 | 10 | 49.96 | 0.014706 | -0.005 | -0.05 | 4.975 | 4.975 | 0 | 12 | 1 | 1 | 4.975 | 10 | 0 | 0
1150.95 | 49.65 | 49.65 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
1151 | 49.63 | 49.63 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1151.05 | 49.6 | 49.6 | 1 | 1 | 10 | 49.88 | 0.24 | 0.14412 | 1.4412 | 5.7206 | 5.7206 | 0 | 12 | 1 | 1 | 5.7206 | 10 | 0 | 0
1151.1 | 49.58 | 49.58 | 1 | 1 | 10 | 49.86 | 0.43 | 0.24412 | 2.4412 | 6.2206 | 6.2206 | 0 | 12 | 1 | 1 | 6.2206 | 10 | 0 | 0
1151.15 | 49.55 | 49.55 | 1 | 1 | 10 | 49.83 | 0.715 | 0.34412 | 3.4412 | 6.7206 | 6.7206 | 0 | 12 | 1 | 1 | 6.7206 | 10 | 0 | 0
1151.2 | 49.53 | 49.53 | 1 | 1 | 10 | 49.81 | 0.905 | 0.44412 | 4.4412 | 7.2206 | 7.2206 | 0 | 12 | 1 | 1 | 7.2206 | 10 | 0 | 0
1151.25 | 49.5 | 49.5 | 1 | 1 | 10 | 49.78 | 1 | 0.54412 | 5.4412 | 7.7206 | 7.7206 | 0 | 12 | 1 | 1 | 7.7206 | 10 | 0 | 0
1151.3 | 49.5 | 49.5 | 1 | 1 | 10 | 49.76 | 1 | 0.64412 | 6.4412 | 8.2206 | 8.2206 | 0 | 12 | 1 | 1 | 8.2206 | 10 | 0 | 0
1151.35 | 49.53 | 49.5 | 1 | 1 | 10 | 49.73 | 1 | 0.74412 | 7.4412 | 8.7206 | 8.7206 | 0 | 12 | 1 | 1 | 8.7206 | 10 | 0 | 0
1151.4 | 49.55 | 49.5 | 1 | 1 | 10 | 49.71 | 1 | 0.84412 | 8.4412 | 9.2206 | 9.2206 | 0 | 12 | 1 | 1 | 9.2206 | 10 | 0 | 0
1151.45 | 49.58 | 49.5 | 1 | 1 | 10 | 49.68 | 1 | 0.94412 | 9.4412 | 9.7206 | 9.7206 | 0 | 12 | 1 | 1 | 9.7206 | 10 | 0 | 0
1151.5 | 49.6 | 49.5 | 1 | 1 | 10 | 49.65 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1151.55 | 49.63 | 49.5 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1151.6 | 49.65 | 49.5 | 1 | 1 | 10 | 49.65 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1151.65 | 49.68 | 49.5 | 1 | 1 | 10 | 49.68 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1151.7 | 49.71 | 49.5 | 1 | 1 | 10 | 49.71 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1151.75 | 49.73 | 49.5 | 1 | 1 | 10 | 49.73 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1151.8 | 49.76 | 49.5 | 1 | 1 | 10 | 49.76 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1151.85 | 49.78 | 49.5 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1151.9 | 49.81 | 49.53 | 1 | 1 | 10 | 49.81 | 0.905 | 0.905 | 9.05 | 9.525 | 9.525 | 0 | 12 | 1 | 1 | 9.525 | 10 | 0 | 0
1151.95 | 49.83 | 49.55 | 1 | 1 | 10 | 49.83 | 0.715 | 0.715 | 7.15 | 8.575 | 8.575 | 0 | 12 | 1 | 1 | 8.575 | 10 | 0 | 0
1152 | 49.86 | 49.58 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
1152.05 | 49.88 | 49.6 | 1 | 1 | 10 | 49.88 | 0.24 | 0.24 | 2.4 | 6.2 | 6.2 | 0 | 12 | 1 | 1 | 6.2 | 10 | 0 | 0
1152.1 | 49.91 | 49.63 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1152.15 | 49.94 | 49.65 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
1152.2 | 49.96 | 49.68 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
1152.25 | 49.99 | 49.71 | 1 | 1 | 10 | 49.99 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1152.3 | 50.01 | 49.73 | 1 | 1 | 10 | 50.01 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1152.35 | 50.04 | 49.76 | 1 | 1 | 10 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 4.9265 | 4.9265 | 0 | 12 | 1 | 1 | 4.9265 | 10 | 0 | 0
1152.4 | 50.06 | 49.78 | 1 | 1 | 10 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 4.8676 | 4.8676 | 0 | 12 | 1 | 1 | 4.8676 | 10 | 0 | 0
1152.45 | 50.09 | 49.81 | 0.905 | 0.905 | 9.05 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 4.3044 | 4.3044 | 0 | 12 | 1 | 1 | 4.3044 | 10 | 0 | 0
1152.5 | 50.12 | 49.83 | 0.715 | 0.805 | 8.05 | 50.12 | -0.24 | -0.24 | -2.4 | 2.825 | 2.825 | 0 | 12 | 1 | 1 | 2.825 | 10 | 0 | 0
1152.55 | 50.14 | 49.86 | 0.43 | 0.705 | 7.05 | 50.14 | -0.43 | -0.43 | -4.3 | 1.375 | 1.375 | 0 | 12 | 1 | 1 | 1.375 | 10 | 0 | 0
1152.6 | 50.17 | 49.88 | 0.24 | 0.605 | 6.05 | 50.17 | -0.715 | -0.715 | -7.15 | -0.55 | -0.55 | 0 | 12 | 1 | 1 | -0.55 | 10 | 0 | 0
1152.65 | 50.19 | 49.91 | 0.044118 | 0.505 | 5.05 | 50.19 | -0.905 | -0.905 | -9.05 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
1152.7 | 50.22 | 49.94 | 0.026471 | 0.405 | 4.05 | 50.22 | -1 | -1 | -10 | -2.975 | -2.975 | 0 | 12 | 1 | 1 | -2.975 | 10 | 0 | 0
1152.75 | 50.24 | 49.96 | 0.014706 | 0.305 | 3.05 | 50.24 | -1 | -1 | -10 | -3.475 | -3.475 | 0 | 12 | 1 | 1 | -3.475 | 10 | 0 | 0
1152.8 | 50.27 | 49.99 | 0 | 0.205 | 2.05 | 50.27 | -1 | -1 | -10 | -3.975 | -3.975 | 0 | 12 | 1 | 1 | -3.975 | 10 | 0 | 0
1152.85 | 50.29 | 50.01 | 0 | 0.105 | 1.05 | 50.29 | -1 | -1 | -10 | -4.475 | -4.475 | 0 | 12 | 1 | 1 | -4.475 | 10 | 0 | 0
1152.9 | 50.32 | 50.04 | -0.014706 | 0.005 | 0.05 | 50.32 | -1 | -1 | -10 | -4.975 | -4.975 | 0 | 12 | 1 | 1 | -4.975 | 10 | 0 | 0
1152.95 | 50.35 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.35 | -1 | -1 | -10 | -5.1324 | -5.1324 | 0 | 12 | 1 | 1 | -5.1324 | 10 | 0 | 0
1153 | 50.37 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 50.37 | -1 | -1 | -10 | -5.2206 | -5.2206 | 0 | 12 | 1 | 1 | -5.2206 | 10 | 0 | 0
1153.05 | 50.4 | 50.12 | -0.24 | -0.14412 | -1.4412 | 50.4 | -1 | -1 | -10 | -5.7206 | -5.7206 | 0 | 12 | 1 | 1 | -5.7206 | 10 | 0 | 0
1153.1 | 50.42 | 50.14 | -0.43 | -0.24412 | -2.4412 | 50.42 | -1 | -1 | -10 | -6.2206 | -6.2206 | 0 | 12 | 1 | 1 | -6.2206 | 10 | 0 | 0
1153.15 | 50.45 | 50.17 | -0.715 | -0.34412 | -3.4412 | 50.45 | -1 | -1 | -10 | -6.7206 | -6.7206 | 0 | 12 | 1 | 1 | -6.7206 | 10 | 0 | 0
1153.2 | 50.47 | 50.19 | -0.905 | -0.44412 | -4.4412 | 50.47 | -1 | -1 | -10 | -7.2206 | -7.2206 | 0 | 12 | 1 | 1 | -7.2206 | 10 | 0 | 0
1153.25 | 50.5 | 50.22 | -1 | -0.54412 | -5.4412 | 50.5 | -1 | -1 | -10 | -7.7206 | -7.7206 | 0 | 12 | 1 | 1 | -7.7206 | 10 | 0 | 0
1153.3 | 50.5 | 50.24 | -1 | -0.64412 | -6.4412 | 50.5 | -1 | -1 | -10 | -8.2206 | -8.2206 | 0 | 12 | 1 | 1 | -8.2206 | 10 | 0 | 0
1153.35 | 50.47 | 50.27 | -1 | -0.74412 | -7.4412 | 50.5 | -1 | -1 | -10 | -8.7206 | -8.7206 | 0 | 12 | 1 | 1 | -8.7206 | 10 | 0 | 0
1153.4 | 50.45 | 50.29 | -1 | -0.84412 | -8.4412 | 50.5 | -1 | -1 | -10 | -9.2206 | -9.2206 | 0 | 12 | 1 | 1 | -9.2206 | 10 | 0 | 0
1153.45 | 50.42 | 50.32 | -1 | -0.94412 | -9.4412 | 50.5 | -1 | -1 | -10 | -9.7206 | -9.7206 | 0 | 12 | 1 | 1 | -9.7206 | 10 | 0 | 0
1153.5 | 50.39 | 50.35 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1153.55 | 50.37 | 50.37 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1153.6 | 50.34 | 50.34 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1153.65 | 50.32 | 50.32 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1153.7 | 50.29 | 50.29 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1153.75 | 50.26 | 50.26 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1153.8 | 50.24 | 50.24 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1153.85 | 50.21 | 50.21 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1153.9 | 50.18 | 50.18 | -0.81 | -0.81 | -8.1 | 50.47 | -1 | -1 | -10 | -9.05 | -9.05 | 0 | 12 | 1 | 1 | -9.05 | 10 | 0 | 0
1153.95 | 50.16 | 50.16 | -0.62 | -0.62 | -6.2 | 50.45 | -1 | -1 | -10 | -8.1 | -8.1 | 0 | 12 | 1 | 1 | -8.1 | 10 | 0 | 0
1154 | 50.13 | 50.13 | -0.335 | -0.335 | -3.35 | 50.42 | -1 | -1 | -10 | -6.675 | -6.675 | 0 | 12 | 1 | 1 | -6.675 | 10 | 0 | 0
1154.05 | 50.11 | 50.11 | -0.145 | -0.145 | -1.45 | 50.39 | -1 | -1 | -10 | -5.725 | -5.725 | 0 | 12 | 1 | 1 | -5.725 | 10 | 0 | 0
1154.1 | 50.08 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 50.37 | -1 | -1 | -10 | -5.1912 | -5.1912 | 0 | 12 | 1 | 1 | -5.1912 | 10 | 0 | 0
1154.15 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.34 | -1 | -1 | -10 | -5.1029 | -5.1029 | 0 | 12 | 1 | 1 | -5.1029 | 10 | 0 | 0
1154.2 | 50.03 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 50.32 | -1 | -1 | -10 | -5.0441 | -5.0441 | 0 | 12 | 1 | 1 | -5.0441 | 10 | 0 | 0
1154.25 | 50 | 50 | 0 | 0 | 0 | 50.29 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1154.3 | 50 | 50 | 0 | 0 | 0 | 50.26 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1154.35 | 50 | 50 | 0 | 0 | 0 | 50.24 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1154.4 | 50 | 50 | 0 | 0 | 0 | 50.21 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1154.45 | 50 | 50 | 0 | 0 | 0 | 50.18 | -0.81 | -0.9 | -9 | -4.5 | -4.5 | 0 | 12 | 1 | 1 | -4.5 | 10 | 0 | 0
1154.5 | 50 | 50 | 0 | 0 | 0 | 50.16 | -0.62 | -0.8 | -8 | -4 | -4 | 0 | 12 | 1 | 1 | -4 | 10 | 0 | 0
1154.55 | 50 | 50 | 0 | 0 | 0 | 50.13 | -0.335 | -0.7 | -7 | -3.5 | -3.5 | 0 | 12 | 1 | 1 | -3.5 | 10 | 0 | 0
1154.6 | 50.01 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.6 | -6 | -3 | -3 | 0 | 12 | 1 | 1 | -3 | 10 | 0 | 0
1154.65 | 50.01 | 50 | 0 | 0 | 0 | 50.08 | -0.038235 | -0.5 | -5 | -2.5 | -2.5 | 0 | 12 | 1 | 1 | -2.5 | 10 | 0 | 0
1154.7 | 49.99 | 49.99 | 0 | 0 | 0 | 50.05 | -0.020588 | -0.4 | -4 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
1154.75 | 49.99 | 49.99 | 0 | 0 | 0 | 50.03 | -0.0088235 | -0.3 | -3 | -1.5 | -1.5 | 0 | 12 | 1 | 1 | -1.5 | 10 | 0 | 0
1154.8 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | -0.2 | -2 | -0.83824 | -0.83824 | 0 | 12 | 1 | 1 | -0.83824 | 10 | 0 | 0
1154.85 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | -0.1 | -1 | -0.33824 | -0.33824 | 0 | 12 | 1 | 1 | -0.33824 | 10 | 0 | 0
1154.9 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
1154.95 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
1155 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
1155.05 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
1155.1 | 49.89 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
1155.15 | 49.89 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
1155.2 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50.01 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1155.25 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1155.3 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1155.35 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 2.7868 | 2.7868 | 0 | 12 | 1 | 1 | 2.7868 | 10 | 0 | 0
1155.4 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 2.7868 | 2.7868 | 0 | 12 | 1 | 1 | 2.7868 | 10 | 0 | 0
1155.45 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 2.8456 | 2.8456 | 0 | 12 | 1 | 1 | 2.8456 | 10 | 0 | 0
1155.5 | 49.94 | 49.85 | 0.525 | 0.525 | 5.25 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 2.7574 | 2.7574 | 0 | 12 | 1 | 1 | 2.7574 | 10 | 0 | 0
1155.55 | 49.94 | 49.85 | 0.525 | 0.525 | 5.25 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 2.7574 | 2.7574 | 0 | 12 | 1 | 1 | 2.7574 | 10 | 0 | 0
1155.6 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1155.65 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1155.7 | 49.93 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1155.75 | 49.93 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1155.8 | 49.96 | 49.85 | 0.525 | 0.525 | 5.25 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 2.6985 | 2.6985 | 0 | 12 | 1 | 1 | 2.6985 | 10 | 0 | 0
1155.85 | 49.96 | 49.85 | 0.525 | 0.525 | 5.25 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 2.6985 | 2.6985 | 0 | 12 | 1 | 1 | 2.6985 | 10 | 0 | 0
1155.9 | 49.99 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1155.95 | 49.99 | 49.91 | 0.044118 | 0.425 | 4.25 | 49.99 | 0 | 0 | 0 | 2.125 | 2.125 | 0 | 12 | 1 | 1 | 2.125 | 10 | 0 | 0
1156 | 49.99 | 49.91 | 0.044118 | 0.325 | 3.25 | 49.99 | 0 | 0 | 0 | 1.625 | 1.625 | 0 | 12 | 1 | 1 | 1.625 | 10 | 0 | 0
1156.05 | 49.99 | 49.93 | 0.032353 | 0.225 | 2.25 | 49.99 | 0 | 0 | 0 | 1.125 | 1.125 | 0 | 12 | 1 | 1 | 1.125 | 10 | 0 | 0
1156.1 | 49.96 | 49.93 | 0.032353 | 0.125 | 1.25 | 49.99 | 0 | 0 | 0 | 0.625 | 0.625 | 0 | 12 | 1 | 1 | 0.625 | 10 | 0 | 0
1156.15 | 49.96 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 49.99 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1156.2 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1156.25 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1156.3 | 50.05 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.058824 | 0.058824 | 0 | 12 | 1 | 1 | 0.058824 | 10 | 0 | 0
1156.35 | 50.05 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
1156.4 | 49.97 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
1156.45 | 49.97 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
1156.5 | 49.92 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1156.55 | 49.92 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1156.6 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1156.65 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1156.7 | 49.94 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1156.75 | 49.94 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1156.8 | 50.01 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1156.85 | 50.01 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1156.9 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1156.95 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
1157 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
1157.05 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
1157.1 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
1157.15 | 49.95 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
1157.2 | 49.97 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
1157.25 | 49.97 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
1157.3 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
1157.35 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
1157.4 | 49.87 | 49.87 | 0.335 | 0.335 | 3.35 | 50.01 | 0 | 0 | 0 | 1.675 | 1.675 | 0 | 12 | 1 | 1 | 1.675 | 10 | 0 | 0
1157.45 | 49.87 | 49.87 | 0.335 | 0.335 | 3.35 | 49.99 | 0 | 0 | 0 | 1.675 | 1.675 | 0 | 12 | 1 | 1 | 1.675 | 10 | 0 | 0
1157.5 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1157.55 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 2.6691 | 2.6691 | 0 | 12 | 1 | 1 | 2.6691 | 10 | 0 | 0
1157.6 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1157.65 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1157.7 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1157.75 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1157.8 | 49.84 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1157.85 | 49.84 | 49.79 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
1157.9 | 49.89 | 49.79 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
1157.95 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.12647 | 1.2647 | 5.6324 | 5.6324 | 0 | 12 | 1 | 1 | 5.6324 | 10 | 0 | 0
1158 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.145 | 1.45 | 5.725 | 5.725 | 0 | 12 | 1 | 1 | 5.725 | 10 | 0 | 0
1158.05 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.145 | 1.45 | 5.725 | 5.725 | 0 | 12 | 1 | 1 | 5.725 | 10 | 0 | 0
1158.1 | 49.96 | 49.79 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
1158.15 | 49.96 | 49.79 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
1158.2 | 50.02 | 49.79 | 1 | 1 | 10 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 4.9853 | 4.9853 | 0 | 12 | 1 | 1 | 4.9853 | 10 | 0 | 0
1158.25 | 50.02 | 49.79 | 1 | 1 | 10 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 4.9853 | 4.9853 | 0 | 12 | 1 | 1 | 4.9853 | 10 | 0 | 0
1158.3 | 50.03 | 49.79 | 1 | 1 | 10 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.9559 | 4.9559 | 0 | 12 | 1 | 1 | 4.9559 | 10 | 0 | 0
1158.35 | 50.03 | 49.84 | 0.62 | 0.9 | 9 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.4559 | 4.4559 | 0 | 12 | 1 | 1 | 4.4559 | 10 | 0 | 0
1158.4 | 50.02 | 49.84 | 0.62 | 0.8 | 8 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 3.9559 | 3.9559 | 0 | 12 | 1 | 1 | 3.9559 | 10 | 0 | 0
1158.45 | 50.02 | 49.89 | 0.145 | 0.7 | 7 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 3.4559 | 3.4559 | 0 | 12 | 1 | 1 | 3.4559 | 10 | 0 | 0
1158.5 | 50.08 | 49.89 | 0.145 | 0.6 | 6 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 2.8088 | 2.8088 | 0 | 12 | 1 | 1 | 2.8088 | 10 | 0 | 0
1158.55 | 50.08 | 49.89 | 0.145 | 0.5 | 5 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 2.3088 | 2.3088 | 0 | 12 | 1 | 1 | 2.3088 | 10 | 0 | 0
1158.6 | 50.01 | 49.89 | 0.145 | 0.4 | 4 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 1.8088 | 1.8088 | 0 | 12 | 1 | 1 | 1.8088 | 10 | 0 | 0
1158.65 | 50.01 | 49.96 | 0.014706 | 0.3 | 3 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 1.3088 | 1.3088 | 0 | 12 | 1 | 1 | 1.3088 | 10 | 0 | 0
1158.7 | 49.94 | 49.94 | 0.026471 | 0.2 | 2 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.80882 | 0.80882 | 0 | 12 | 1 | 1 | 0.80882 | 10 | 0 | 0
1158.75 | 49.94 | 49.94 | 0.026471 | 0.1 | 1 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.30882 | 0.30882 | 0 | 12 | 1 | 1 | 0.30882 | 10 | 0 | 0
1158.8 | 50 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
1158.85 | 50 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
1158.9 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
1158.95 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
1159 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1159.05 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1159.1 | 49.92 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1159.15 | 49.92 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
1159.2 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50.01 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1159.25 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1159.3 | 49.92 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1159.35 | 49.92 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1159.4 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1159.45 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1159.5 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1159.55 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1159.6 | 49.87 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1159.65 | 49.87 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1159.7 | 49.8 | 49.8 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1159.75 | 49.8 | 49.8 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1159.8 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1159.85 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1159.9 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1159.95 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1160 | 49.72 | 49.72 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1160.05 | 49.72 | 49.72 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1160.1 | 49.67 | 49.67 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1160.15 | 49.67 | 49.67 | 1 | 1 | 10 | 49.87 | 0.335 | 0.14412 | 1.4412 | 5.7206 | 5.7206 | 0 | 12 | 1 | 1 | 5.7206 | 10 | 0 | 0
1160.2 | 49.65 | 49.65 | 1 | 1 | 10 | 49.87 | 0.335 | 0.24412 | 2.4412 | 6.2206 | 6.2206 | 0 | 12 | 1 | 1 | 6.2206 | 10 | 0 | 0
1160.25 | 49.65 | 49.65 | 1 | 1 | 10 | 49.8 | 1 | 0.34412 | 3.4412 | 6.7206 | 6.7206 | 0 | 12 | 1 | 1 | 6.7206 | 10 | 0 | 0
1160.3 | 49.59 | 49.59 | 1 | 1 | 10 | 49.8 | 1 | 0.44412 | 4.4412 | 7.2206 | 7.2206 | 0 | 12 | 1 | 1 | 7.2206 | 10 | 0 | 0
1160.35 | 49.59 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.54412 | 5.4412 | 7.7206 | 7.7206 | 0 | 12 | 1 | 1 | 7.7206 | 10 | 0 | 0
1160.4 | 49.66 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.64412 | 6.4412 | 8.2206 | 8.2206 | 0 | 12 | 1 | 1 | 8.2206 | 10 | 0 | 0
1160.45 | 49.66 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.74412 | 7.4412 | 8.7206 | 8.7206 | 0 | 12 | 1 | 1 | 8.7206 | 10 | 0 | 0
1160.5 | 49.63 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.84412 | 8.4412 | 9.2206 | 9.2206 | 0 | 12 | 1 | 1 | 9.2206 | 10 | 0 | 0
1160.55 | 49.63 | 49.59 | 1 | 1 | 10 | 49.72 | 1 | 0.94412 | 9.4412 | 9.7206 | 9.7206 | 0 | 12 | 1 | 1 | 9.7206 | 10 | 0 | 0
1160.6 | 49.61 | 49.59 | 1 | 1 | 10 | 49.72 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1160.65 | 49.61 | 49.59 | 1 | 1 | 10 | 49.67 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1160.7 | 49.54 | 49.54 | 1 | 1 | 10 | 49.67 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1160.75 | 49.54 | 49.54 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1160.8 | 49.46 | 49.46 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1160.85 | 49.46 | 49.46 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1160.9 | 49.45 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1160.95 | 49.45 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1161 | 49.51 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1161.05 | 49.51 | 49.45 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1161.1 | 49.5 | 49.45 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1161.15 | 49.5 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1161.2 | 49.54 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1161.25 | 49.54 | 49.45 | 1 | 1 | 10 | 49.54 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1161.3 | 49.59 | 49.45 | 1 | 1 | 10 | 49.59 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1161.35 | 49.59 | 49.45 | 1 | 1 | 10 | 49.59 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1161.4 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1161.45 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1161.5 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1161.55 | 49.61 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1161.6 | 49.53 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1161.65 | 49.53 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1161.7 | 49.54 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1161.75 | 49.54 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1161.8 | 49.61 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1161.85 | 49.61 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1161.9 | 49.66 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1161.95 | 49.66 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1162 | 49.64 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1162.05 | 49.64 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1162.1 | 49.69 | 49.53 | 1 | 1 | 10 | 49.69 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1162.15 | 49.69 | 49.53 | 1 | 1 | 10 | 49.69 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1162.2 | 49.74 | 49.53 | 1 | 1 | 10 | 49.74 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1162.25 | 49.74 | 49.54 | 1 | 1 | 10 | 49.74 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1162.3 | 49.78 | 49.54 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1162.35 | 49.78 | 49.61 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1162.4 | 49.82 | 49.61 | 1 | 1 | 10 | 49.82 | 0.81 | 0.81 | 8.1 | 9.05 | 9.05 | 0 | 12 | 1 | 1 | 9.05 | 10 | 0 | 0
1162.45 | 49.82 | 49.64 | 1 | 1 | 10 | 49.82 | 0.81 | 0.81 | 8.1 | 9.05 | 9.05 | 0 | 12 | 1 | 1 | 9.05 | 10 | 0 | 0
1162.5 | 49.86 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
1162.55 | 49.86 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
1162.6 | 49.84 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
1162.65 | 49.84 | 49.69 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
1162.7 | 49.91 | 49.69 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1162.75 | 49.91 | 49.74 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1162.8 | 49.97 | 49.74 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1162.85 | 49.97 | 49.78 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1162.9 | 50.03 | 49.78 | 1 | 1 | 10 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.9559 | 4.9559 | 0 | 12 | 1 | 1 | 4.9559 | 10 | 0 | 0
1162.95 | 50.03 | 49.82 | 0.81 | 0.9 | 9 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.4559 | 4.4559 | 0 | 12 | 1 | 1 | 4.4559 | 10 | 0 | 0
1163 | 50.05 | 49.82 | 0.81 | 0.81 | 8.1 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 3.9471 | 3.9471 | 0 | 12 | 1 | 1 | 3.9471 | 10 | 0 | 0
1163.05 | 50.05 | 49.84 | 0.62 | 0.71 | 7.1 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 3.4471 | 3.4471 | 0 | 12 | 1 | 1 | 3.4471 | 10 | 0 | 0
1163.1 | 50.01 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
1163.15 | 50.01 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
1163.2 | 49.95 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
1163.25 | 49.95 | 49.91 | 0.044118 | 0.52 | 5.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.4971 | 2.4971 | 0 | 12 | 1 | 1 | 2.4971 | 10 | 0 | 0
1163.3 | 49.99 | 49.91 | 0.044118 | 0.42 | 4.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 1.9971 | 1.9971 | 0 | 12 | 1 | 1 | 1.9971 | 10 | 0 | 0
1163.35 | 49.99 | 49.95 | 0.020588 | 0.32 | 3.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 1.4971 | 1.4971 | 0 | 12 | 1 | 1 | 1.4971 | 10 | 0 | 0
1163.4 | 49.92 | 49.92 | 0.038235 | 0.22 | 2.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.99706 | 0.99706 | 0 | 12 | 1 | 1 | 0.99706 | 10 | 0 | 0
1163.45 | 49.92 | 49.92 | 0.038235 | 0.12 | 1.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.49706 | 0.49706 | 0 | 12 | 1 | 1 | 0.49706 | 10 | 0 | 0
1163.5 | 49.97 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1163.55 | 49.97 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1163.6 | 50.02 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1163.65 | 50.02 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.17647 | 0.17647 | 0 | 12 | 1 | 1 | 0.17647 | 10 | 0 | 0
1163.7 | 50.07 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1163.75 | 50.07 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1163.8 | 50.06 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1163.85 | 50.06 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1163.9 | 50.13 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
1163.95 | 50.13 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
1164 | 50.09 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
1164.05 | 50.09 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6309 | -1.6309 | 0 | 12 | 1 | 1 | -1.6309 | 10 | 0 | 0
1164.1 | 50.07 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6309 | -1.6309 | 0 | 12 | 1 | 1 | -1.6309 | 10 | 0 | 0
1164.15 | 50.07 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6897 | -1.6897 | 0 | 12 | 1 | 1 | -1.6897 | 10 | 0 | 0
1164.2 | 50.07 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6897 | -1.6897 | 0 | 12 | 1 | 1 | -1.6897 | 10 | 0 | 0
1164.25 | 50.07 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.13 | -0.335 | -0.335 | -3.35 | -1.8074 | -1.8074 | 0 | 12 | 1 | 1 | -1.8074 | 10 | 0 | 0
1164.3 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.13 | -0.335 | -0.335 | -3.35 | -1.7779 | -1.7779 | 0 | 12 | 1 | 1 | -1.7779 | 10 | 0 | 0
1164.35 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.13 | -0.335 | -0.335 | -3.35 | -1.7779 | -1.7779 | 0 | 12 | 1 | 1 | -1.7779 | 10 | 0 | 0
1164.4 | 50.01 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
1164.45 | 50.01 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
1164.5 | 50.07 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
1164.55 | 50.07 | 50.01 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.235 | -2.35 | -1.175 | -1.175 | 0 | 12 | 1 | 1 | -1.175 | 10 | 0 | 0
1164.6 | 50.05 | 50.01 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.135 | -1.35 | -0.675 | -0.675 | 0 | 12 | 1 | 1 | -0.675 | 10 | 0 | 0
1164.65 | 50.05 | 50.01 | 0 | 0 | 0 | 50.07 | -0.032353 | -0.035 | -0.35 | -0.175 | -0.175 | 0 | 12 | 1 | 1 | -0.175 | 10 | 0 | 0
1164.7 | 50.1 | 50.01 | 0 | 0 | 0 | 50.1 | -0.05 | -0.05 | -0.5 | -0.25 | -0.25 | 0 | 12 | 1 | 1 | -0.25 | 10 | 0 | 0
1164.75 | 50.1 | 50.01 | 0 | 0 | 0 | 50.1 | -0.05 | -0.05 | -0.5 | -0.25 | -0.25 | 0 | 12 | 1 | 1 | -0.25 | 10 | 0 | 0
1164.8 | 50.11 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1164.85 | 50.11 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1164.9 | 50.06 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1164.95 | 50.06 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1165 | 50.04 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1165.05 | 50.04 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1165.1 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1165.15 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1165.2 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1165.25 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1165.3 | 50.11 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1165.35 | 50.11 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1165.4 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1165.45 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1165.5 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1165.55 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1165.6 | 50.02 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.11 | -0.145 | -0.145 | -1.45 | -0.73971 | -0.73971 | 0 | 12 | 1 | 1 | -0.73971 | 10 | 0 | 0
1165.65 | 50.02 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.11 | -0.145 | -0.145 | -1.45 | -0.73971 | -0.73971 | 0 | 12 | 1 | 1 | -0.73971 | 10 | 0 | 0
1165.7 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1165.75 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1165.8 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1165.85 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1165.9 | 50.01 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1165.95 | 50.01 | 50 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.045 | -0.45 | -0.225 | -0.225 | 0 | 12 | 1 | 1 | -0.225 | 10 | 0 | 0
1166 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
1166.05 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
1166.1 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
1166.15 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1166.2 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.14706 | 0.14706 | 0 | 12 | 1 | 1 | 0.14706 | 10 | 0 | 0
1166.25 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1166.3 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1166.35 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1166.4 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1166.45 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1166.5 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1166.55 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1166.6 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1166.65 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1166.7 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1166.75 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1166.8 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1166.85 | 50 | 50 | 0 | 0 | 0 | 50.01 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1166.9 | 49.5 | 49.5 | 1 | 1 | 10 | 50.01 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1166.95 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1167 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1167.05 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1167.1 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1167.15 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1167.2 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1167.25 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1167.3 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1167.35 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1167.4 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1167.45 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.1 | 1 | 5.5 | 5.5 | 0 | 12 | 1 | 1 | 5.5 | 10 | 0 | 0
1167.5 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.2 | 2 | 6 | 6 | 0 | 12 | 1 | 1 | 6 | 10 | 0 | 0
1167.55 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.3 | 3 | 6.5 | 6.5 | 0 | 12 | 1 | 1 | 6.5 | 10 | 0 | 0
1167.6 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.4 | 4 | 7 | 7 | 0 | 12 | 1 | 1 | 7 | 10 | 0 | 0
1167.65 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.5 | 5 | 7.5 | 7.5 | 0 | 12 | 1 | 1 | 7.5 | 10 | 0 | 0
1167.7 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.6 | 6 | 8 | 8 | 0 | 12 | 1 | 1 | 8 | 10 | 0 | 0
1167.75 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.7 | 7 | 8.5 | 8.5 | 0 | 12 | 1 | 1 | 8.5 | 10 | 0 | 0
1167.8 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.8 | 8 | 9 | 9 | 0 | 12 | 1 | 1 | 9 | 10 | 0 | 0
1167.85 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.9 | 9 | 9.5 | 9.5 | 0 | 12 | 1 | 1 | 9.5 | 10 | 0 | 0
1167.9 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1167.95 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1168 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1168.05 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1168.1 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1168.15 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1168.2 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1168.25 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1168.3 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1168.35 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1168.4 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1168.45 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1168.5 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1168.55 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1168.6 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1168.65 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1168.7 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1168.75 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1168.8 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1168.85 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1168.9 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1168.95 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1169 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1169.05 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1169.1 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1169.15 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1169.2 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1169.25 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1169.3 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1169.35 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1169.4 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1169.45 | 50.5 | 50.5 | -1 | 0.9 | 9 | 50.5 | -1 | -1 | -10 | -0.5 | -0.5 | 0 | 12 | 1 | 1 | -0.5 | 10 | 0 | 0
1169.5 | 50.5 | 50.5 | -1 | 0.8 | 8 | 50.5 | -1 | -1 | -10 | -1 | -1 | 0 | 12 | 1 | 1 | -1 | 10 | 0 | 0
1169.55 | 50.5 | 50.5 | -1 | 0.7 | 7 | 50.5 | -1 | -1 | -10 | -1.5 | -1.5 | 0 | 12 | 1 | 1 | -1.5 | 10 | 0 | 0
1169.6 | 50.5 | 50.5 | -1 | 0.6 | 6 | 50.5 | -1 | -1 | -10 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
1169.65 | 50.5 | 50.5 | -1 | 0.5 | 5 | 50.5 | -1 | -1 | -10 | -2.5 | -2.5 | 0 | 12 | 1 | 1 | -2.5 | 10 | 0 | 0
1169.7 | 50.5 | 50.5 | -1 | 0.4 | 4 | 50.5 | -1 | -1 | -10 | -3 | -3 | 0 | 12 | 1 | 1 | -3 | 10 | 0 | 0
1169.75 | 50.5 | 50.5 | -1 | 0.3 | 3 | 50.5 | -1 | -1 | -10 | -3.5 | -3.5 | 0 | 12 | 1 | 1 | -3.5 | 10 | 0 | 0
1169.8 | 50.5 | 50.5 | -1 | 0.2 | 2 | 50.5 | -1 | -1 | -10 | -4 | -4 | 0 | 12 | 1 | 1 | -4 | 10 | 0 | 0
1169.85 | 50.5 | 50.5 | -1 | 0.1 | 1 | 50.5 | -1 | -1 | -10 | -4.5 | -4.5 | 0 | 12 | 1 | 1 | -4.5 | 10 | 0 | 0
1169.9 | 50.5 | 50.5 | -1 | 0 | 0 | 50.5 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1169.95 | 50.5 | 50.5 | -1 | -0.1 | -1 | 50.5 | -1 | -1 | -10 | -5.5 | -5.5 | 0 | 12 | 1 | 1 | -5.5 | 10 | 0 | 0
1170 | 50.5 | 50.5 | -1 | -0.2 | -2 | 50.5 | -1 | -1 | -10 | -6 | -6 | 0 | 12 | 1 | 1 | -6 | 10 | 0 | 0
1170.05 | 50.5 | 50.5 | -1 | -0.3 | -3 | 50.5 | -1 | -1 | -10 | -6.5 | -6.5 | 0 | 12 | 1 | 1 | -6.5 | 10 | 0 | 0
1170.1 | 50.5 | 50.5 | -1 | -0.4 | -4 | 50.5 | -1 | -1 | -10 | -7 | -7 | 0 | 12 | 1 | 1 | -7 | 10 | 0 | 0
1170.15 | 50.5 | 50.5 | -1 | -0.5 | -5 | 50.5 | -1 | -1 | -10 | -7.5 | -7.5 | 0 | 12 | 1 | 1 | -7.5 | 10 | 0 | 0
1170.2 | 50.5 | 50.5 | -1 | -0.6 | -6 | 50.5 | -1 | -1 | -10 | -8 | -8 | 0 | 12 | 1 | 1 | -8 | 10 | 0 | 0
1170.25 | 50.5 | 50.5 | -1 | -0.7 | -7 | 50.5 | -1 | -1 | -10 | -8.5 | -8.5 | 0 | 12 | 1 | 1 | -8.5 | 10 | 0 | 0
1170.3 | 50.5 | 50.5 | -1 | -0.8 | -8 | 50.5 | -1 | -1 | -10 | -9 | -9 | 0 | 12 | 1 | 1 | -9 | 10 | 0 | 0
1170.35 | 50.5 | 50.5 | -1 | -0.9 | -9 | 50.5 | -1 | -1 | -10 | -9.5 | -9.5 | 0 | 12 | 1 | 1 | -9.5 | 10 | 0 | 0
1170.4 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1170.45 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1170.5 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1170.55 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1170.6 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1170.65 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1170.7 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1170.75 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1170.8 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1170.85 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1170.9 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1170.95 | 50.47 | 50.47 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1171 | 50.45 | 50.45 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1171.05 | 50.42 | 50.42 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1171.1 | 50.4 | 50.4 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1171.15 | 50.37 | 50.37 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1171.2 | 50.35 | 50.35 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1171.25 | 50.32 | 50.32 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1171.3 | 50.29 | 50.29 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1171.35 | 50.27 | 50.27 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1171.4 | 50.24 | 50.24 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1171.45 | 50.22 | 50.22 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1171.5 | 50.19 | 50.19 | -0.905 | -0.905 | -9.05 | 50.47 | -1 | -1 | -10 | -9.525 | -9.525 | 0 | 12 | 1 | 1 | -9.525 | 10 | 0 | 0
1171.55 | 50.17 | 50.17 | -0.715 | -0.715 | -7.15 | 50.45 | -1 | -1 | -10 | -8.575 | -8.575 | 0 | 12 | 1 | 1 | -8.575 | 10 | 0 | 0
1171.6 | 50.14 | 50.14 | -0.43 | -0.43 | -4.3 | 50.42 | -1 | -1 | -10 | -7.15 | -7.15 | 0 | 12 | 1 | 1 | -7.15 | 10 | 0 | 0
1171.65 | 50.12 | 50.12 | -0.24 | -0.24 | -2.4 | 50.4 | -1 | -1 | -10 | -6.2 | -6.2 | 0 | 12 | 1 | 1 | -6.2 | 10 | 0 | 0
1171.7 | 50.09 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 50.37 | -1 | -1 | -10 | -5.2206 | -5.2206 | 0 | 12 | 1 | 1 | -5.2206 | 10 | 0 | 0
1171.75 | 50.06 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.35 | -1 | -1 | -10 | -5.1324 | -5.1324 | 0 | 12 | 1 | 1 | -5.1324 | 10 | 0 | 0
1171.8 | 50.04 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.32 | -1 | -1 | -10 | -5.0735 | -5.0735 | 0 | 12 | 1 | 1 | -5.0735 | 10 | 0 | 0
1171.85 | 50.01 | 50.01 | 0 | 0 | 0 | 50.29 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1171.9 | 49.99 | 49.99 | 0 | 0 | 0 | 50.27 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1171.95 | 49.96 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.24 | -1 | -1 | -10 | -4.9265 | -4.9265 | 0 | 12 | 1 | 1 | -4.9265 | 10 | 0 | 0
1172 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.22 | -1 | -1 | -10 | -4.8676 | -4.8676 | 0 | 12 | 1 | 1 | -4.8676 | 10 | 0 | 0
1172.05 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.19 | -0.905 | -0.905 | -9.05 | -4.3044 | -4.3044 | 0 | 12 | 1 | 1 | -4.3044 | 10 | 0 | 0
1172.1 | 49.88 | 49.88 | 0.24 | 0.24 | 2.4 | 50.17 | -0.715 | -0.805 | -8.05 | -2.825 | -2.825 | 0 | 12 | 1 | 1 | -2.825 | 10 | 0 | 0
1172.15 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.14 | -0.43 | -0.705 | -7.05 | -1.375 | -1.375 | 0 | 12 | 1 | 1 | -1.375 | 10 | 0 | 0
1172.2 | 49.83 | 49.83 | 0.715 | 0.715 | 7.15 | 50.12 | -0.24 | -0.605 | -6.05 | 0.55 | 0.55 | 0 | 12 | 1 | 1 | 0.55 | 10 | 0 | 0
1172.25 | 49.81 | 49.81 | 0.905 | 0.905 | 9.05 | 50.09 | -0.044118 | -0.505 | -5.05 | 2 | 2 | 0 | 12 | 1 | 1 | 2 | 10 | 0 | 0
1172.3 | 49.78 | 49.78 | 1 | 1 | 10 | 50.06 | -0.026471 | -0.405 | -4.05 | 2.975 | 2.975 | 0 | 12 | 1 | 1 | 2.975 | 10 | 0 | 0
1172.35 | 49.76 | 49.76 | 1 | 1 | 10 | 50.04 | -0.014706 | -0.305 | -3.05 | 3.475 | 3.475 | 0 | 12 | 1 | 1 | 3.475 | 10 | 0 | 0
1172.4 | 49.73 | 49.73 | 1 | 1 | 10 | 50.01 | 0 | -0.205 | -2.05 | 3.975 | 3.975 | 0 | 12 | 1 | 1 | 3.975 | 10 | 0 | 0
1172.45 | 49.71 | 49.71 | 1 | 1 | 10 | 49.99 | 0 | -0.105 | -1.05 | 4.475 | 4.475 | 0 | 12 | 1 | 1 | 4.475 | 10 | 0 | 0
1172.5 | 49.68 | 49.68 | 1 | 1 | 10 | 49.96 | 0.014706 | -0.005 | -0.05 | 4.975 | 4.975 | 0 | 12 | 1 | 1 | 4.975 | 10 | 0 | 0
1172.55 | 49.65 | 49.65 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
1172.6 | 49.63 | 49.63 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1172.65 | 49.6 | 49.6 | 1 | 1 | 10 | 49.88 | 0.24 | 0.14412 | 1.4412 | 5.7206 | 5.7206 | 0 | 12 | 1 | 1 | 5.7206 | 10 | 0 | 0
1172.7 | 49.58 | 49.58 | 1 | 1 | 10 | 49.86 | 0.43 | 0.24412 | 2.4412 | 6.2206 | 6.2206 | 0 | 12 | 1 | 1 | 6.2206 | 10 | 0 | 0
1172.75 | 49.55 | 49.55 | 1 | 1 | 10 | 49.83 | 0.715 | 0.34412 | 3.4412 | 6.7206 | 6.7206 | 0 | 12 | 1 | 1 | 6.7206 | 10 | 0 | 0
1172.8 | 49.53 | 49.53 | 1 | 1 | 10 | 49.81 | 0.905 | 0.44412 | 4.4412 | 7.2206 | 7.2206 | 0 | 12 | 1 | 1 | 7.2206 | 10 | 0 | 0
1172.85 | 49.5 | 49.5 | 1 | 1 | 10 | 49.78 | 1 | 0.54412 | 5.4412 | 7.7206 | 7.7206 | 0 | 12 | 1 | 1 | 7.7206 | 10 | 0 | 0
1172.9 | 49.5 | 49.5 | 1 | 1 | 10 | 49.76 | 1 | 0.64412 | 6.4412 | 8.2206 | 8.2206 | 0 | 12 | 1 | 1 | 8.2206 | 10 | 0 | 0
1172.95 | 49.53 | 49.5 | 1 | 1 | 10 | 49.73 | 1 | 0.74412 | 7.4412 | 8.7206 | 8.7206 | 0 | 12 | 1 | 1 | 8.7206 | 10 | 0 | 0
1173 | 49.55 | 49.5 | 1 | 1 | 10 | 49.71 | 1 | 0.84412 | 8.4412 | 9.2206 | 9.2206 | 0 | 12 | 1 | 1 | 9.2206 | 10 | 0 | 0
1173.05 | 49.58 | 49.5 | 1 | 1 | 10 | 49.68 | 1 | 0.94412 | 9.4412 | 9.7206 | 9.7206 | 0 | 12 | 1 | 1 | 9.7206 | 10 | 0 | 0
1173.1 | 49.6 | 49.5 | 1 | 1 | 10 | 49.65 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1173.15 | 49.63 | 49.5 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1173.2 | 49.65 | 49.5 | 1 | 1 | 10 | 49.65 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1173.25 | 49.68 | 49.5 | 1 | 1 | 10 | 49.68 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1173.3 | 49.71 | 49.5 | 1 | 1 | 10 | 49.71 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1173.35 | 49.73 | 49.5 | 1 | 1 | 10 | 49.73 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1173.4 | 49.76 | 49.5 | 1 | 1 | 10 | 49.76 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1173.45 | 49.78 | 49.5 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1173.5 | 49.81 | 49.53 | 1 | 1 | 10 | 49.81 | 0.905 | 0.905 | 9.05 | 9.525 | 9.525 | 0 | 12 | 1 | 1 | 9.525 | 10 | 0 | 0
1173.55 | 49.83 | 49.55 | 1 | 1 | 10 | 49.83 | 0.715 | 0.715 | 7.15 | 8.575 | 8.575 | 0 | 12 | 1 | 1 | 8.575 | 10 | 0 | 0
1173.6 | 49.86 | 49.58 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
1173.65 | 49.88 | 49.6 | 1 | 1 | 10 | 49.88 | 0.24 | 0.24 | 2.4 | 6.2 | 6.2 | 0 | 12 | 1 | 1 | 6.2 | 10 | 0 | 0
1173.7 | 49.91 | 49.63 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1173.75 | 49.94 | 49.65 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
1173.8 | 49.96 | 49.68 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
1173.85 | 49.99 | 49.71 | 1 | 1 | 10 | 49.99 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1173.9 | 50.01 | 49.73 | 1 | 1 | 10 | 50.01 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1173.95 | 50.04 | 49.76 | 1 | 1 | 10 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 4.9265 | 4.9265 | 0 | 12 | 1 | 1 | 4.9265 | 10 | 0 | 0
1174 | 50.06 | 49.78 | 1 | 1 | 10 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 4.8676 | 4.8676 | 0 | 12 | 1 | 1 | 4.8676 | 10 | 0 | 0
1174.05 | 50.09 | 49.81 | 0.905 | 0.905 | 9.05 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 4.3044 | 4.3044 | 0 | 12 | 1 | 1 | 4.3044 | 10 | 0 | 0
1174.1 | 50.12 | 49.83 | 0.715 | 0.805 | 8.05 | 50.12 | -0.24 | -0.24 | -2.4 | 2.825 | 2.825 | 0 | 12 | 1 | 1 | 2.825 | 10 | 0 | 0
1174.15 | 50.14 | 49.86 | 0.43 | 0.705 | 7.05 | 50.14 | -0.43 | -0.43 | -4.3 | 1.375 | 1.375 | 0 | 12 | 1 | 1 | 1.375 | 10 | 0 | 0
1174.2 | 50.17 | 49.88 | 0.24 | 0.605 | 6.05 | 50.17 | -0.715 | -0.715 | -7.15 | -0.55 | -0.55 | 0 | 12 | 1 | 1 | -0.55 | 10 | 0 | 0
1174.25 | 50.19 | 49.91 | 0.044118 | 0.505 | 5.05 | 50.19 | -0.905 | -0.905 | -9.05 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
1174.3 | 50.22 | 49.94 | 0.026471 | 0.405 | 4.05 | 50.22 | -1 | -1 | -10 | -2.975 | -2.975 | 0 | 12 | 1 | 1 | -2.975 | 10 | 0 | 0
1174.35 | 50.24 | 49.96 | 0.014706 | 0.305 | 3.05 | 50.24 | -1 | -1 | -10 | -3.475 | -3.475 | 0 | 12 | 1 | 1 | -3.475 | 10 | 0 | 0
1174.4 | 50.27 | 49.99 | 0 | 0.205 | 2.05 | 50.27 | -1 | -1 | -10 | -3.975 | -3.975 | 0 | 12 | 1 | 1 | -3.975 | 10 | 0 | 0
1174.45 | 50.29 | 50.01 | 0 | 0.105 | 1.05 | 50.29 | -1 | -1 | -10 | -4.475 | -4.475 | 0 | 12 | 1 | 1 | -4.475 | 10 | 0 | 0
1174.5 | 50.32 | 50.04 | -0.014706 | 0.005 | 0.05 | 50.32 | -1 | -1 | -10 | -4.975 | -4.975 | 0 | 12 | 1 | 1 | -4.975 | 10 | 0 | 0
1174.55 | 50.35 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.35 | -1 | -1 | -10 | -5.1324 | -5.1324 | 0 | 12 | 1 | 1 | -5.1324 | 10 | 0 | 0
1174.6 | 50.37 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 50.37 | -1 | -1 | -10 | -5.2206 | -5.2206 | 0 | 12 | 1 | 1 | -5.2206 | 10 | 0 | 0
1174.65 | 50.4 | 50.12 | -0.24 | -0.14412 | -1.4412 | 50.4 | -1 | -1 | -10 | -5.7206 | -5.7206 | 0 | 12 | 1 | 1 | -5.7206 | 10 | 0 | 0
1174.7 | 50.42 | 50.14 | -0.43 | -0.24412 | -2.4412 | 50.42 | -1 | -1 | -10 | -6.2206 | -6.2206 | 0 | 12 | 1 | 1 | -6.2206 | 10 | 0 | 0
1174.75 | 50.45 | 50.17 | -0.715 | -0.34412 | -3.4412 | 50.45 | -1 | -1 | -10 | -6.7206 | -6.7206 | 0 | 12 | 1 | 1 | -6.7206 | 10 | 0 | 0
1174.8 | 50.47 | 50.19 | -0.905 | -0.44412 | -4.4412 | 50.47 | -1 | -1 | -10 | -7.2206 | -7.2206 | 0 | 12 | 1 | 1 | -7.2206 | 10 | 0 | 0
1174.85 | 50.5 | 50.22 | -1 | -0.54412 | -5.4412 | 50.5 | -1 | -1 | -10 | -7.7206 | -7.7206 | 0 | 12 | 1 | 1 | -7.7206 | 10 | 0 | 0
1174.9 | 50.5 | 50.24 | -1 | -0.64412 | -6.4412 | 50.5 | -1 | -1 | -10 | -8.2206 | -8.2206 | 0 | 12 | 1 | 1 | -8.2206 | 10 | 0 | 0
1174.95 | 50.47 | 50.27 | -1 | -0.74412 | -7.4412 | 50.5 | -1 | -1 | -10 | -8.7206 | -8.7206 | 0 | 12 | 1 | 1 | -8.7206 | 10 | 0 | 0
1175 | 50.45 | 50.29 | -1 | -0.84412 | -8.4412 | 50.5 | -1 | -1 | -10 | -9.2206 | -9.2206 | 0 | 12 | 1 | 1 | -9.2206 | 10 | 0 | 0
1175.05 | 50.42 | 50.32 | -1 | -0.94412 | -9.4412 | 50.5 | -1 | -1 | -10 | -9.7206 | -9.7206 | 0 | 12 | 1 | 1 | -9.7206 | 10 | 0 | 0
1175.1 | 50.39 | 50.35 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1175.15 | 50.37 | 50.37 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1175.2 | 50.34 | 50.34 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1175.25 | 50.32 | 50.32 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1175.3 | 50.29 | 50.29 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1175.35 | 50.26 | 50.26 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1175.4 | 50.24 | 50.24 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1175.45 | 50.21 | 50.21 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1175.5 | 50.18 | 50.18 | -0.81 | -0.81 | -8.1 | 50.47 | -1 | -1 | -10 | -9.05 | -9.05 | 0 | 12 | 1 | 1 | -9.05 | 10 | 0 | 0
1175.55 | 50.16 | 50.16 | -0.62 | -0.62 | -6.2 | 50.45 | -1 | -1 | -10 | -8.1 | -8.1 | 0 | 12 | 1 | 1 | -8.1 | 10 | 0 | 0
1175.6 | 50.13 | 50.13 | -0.335 | -0.335 | -3.35 | 50.42 | -1 | -1 | -10 | -6.675 | -6.675 | 0 | 12 | 1 | 1 | -6.675 | 10 | 0 | 0
1175.65 | 50.11 | 50.11 | -0.145 | -0.145 | -1.45 | 50.39 | -1 | -1 | -10 | -5.725 | -5.725 | 0 | 12 | 1 | 1 | -5.725 | 10 | 0 | 0
1175.7 | 50.08 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 50.37 | -1 | -1 | -10 | -5.1912 | -5.1912 | 0 | 12 | 1 | 1 | -5.1912 | 10 | 0 | 0
1175.75 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.34 | -1 | -1 | -10 | -5.1029 | -5.1029 | 0 | 12 | 1 | 1 | -5.1029 | 10 | 0 | 0
1175.8 | 50.03 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 50.32 | -1 | -1 | -10 | -5.0441 | -5.0441 | 0 | 12 | 1 | 1 | -5.0441 | 10 | 0 | 0
1175.85 | 50 | 50 | 0 | 0 | 0 | 50.29 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1175.9 | 50 | 50 | 0 | 0 | 0 | 50.26 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1175.95 | 50 | 50 | 0 | 0 | 0 | 50.24 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1176 | 50 | 50 | 0 | 0 | 0 | 50.21 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1176.05 | 50 | 50 | 0 | 0 | 0 | 50.18 | -0.81 | -0.9 | -9 | -4.5 | -4.5 | 0 | 12 | 1 | 1 | -4.5 | 10 | 0 | 0
1176.1 | 50 | 50 | 0 | 0 | 0 | 50.16 | -0.62 | -0.8 | -8 | -4 | -4 | 0 | 12 | 1 | 1 | -4 | 10 | 0 | 0
1176.15 | 50 | 50 | 0 | 0 | 0 | 50.13 | -0.335 | -0.7 | -7 | -3.5 | -3.5 | 0 | 12 | 1 | 1 | -3.5 | 10 | 0 | 0
1176.2 | 50.01 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.6 | -6 | -3 | -3 | 0 | 12 | 1 | 1 | -3 | 10 | 0 | 0
1176.25 | 50.01 | 50 | 0 | 0 | 0 | 50.08 | -0.038235 | -0.5 | -5 | -2.5 | -2.5 | 0 | 12 | 1 | 1 | -2.5 | 10 | 0 | 0
1176.3 | 49.99 | 49.99 | 0 | 0 | 0 | 50.05 | -0.020588 | -0.4 | -4 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
1176.35 | 49.99 | 49.99 | 0 | 0 | 0 | 50.03 | -0.0088235 | -0.3 | -3 | -1.5 | -1.5 | 0 | 12 | 1 | 1 | -1.5 | 10 | 0 | 0
1176.4 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | -0.2 | -2 | -0.83824 | -0.83824 | 0 | 12 | 1 | 1 | -0.83824 | 10 | 0 | 0
1176.45 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | -0.1 | -1 | -0.33824 | -0.33824 | 0 | 12 | 1 | 1 | -0.33824 | 10 | 0 | 0
1176.5 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
1176.55 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
1176.6 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
1176.65 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
1176.7 | 49.89 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
1176.75 | 49.89 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
1176.8 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50.01 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1176.85 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1176.9 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1176.95 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 2.7868 | 2.7868 | 0 | 12 | 1 | 1 | 2.7868 | 10 | 0 | 0
1177 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 2.7868 | 2.7868 | 0 | 12 | 1 | 1 | 2.7868 | 10 | 0 | 0
1177.05 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 2.8456 | 2.8456 | 0 | 12 | 1 | 1 | 2.8456 | 10 | 0 | 0
1177.1 | 49.94 | 49.85 | 0.525 | 0.525 | 5.25 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 2.7574 | 2.7574 | 0 | 12 | 1 | 1 | 2.7574 | 10 | 0 | 0
1177.15 | 49.94 | 49.85 | 0.525 | 0.525 | 5.25 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 2.7574 | 2.7574 | 0 | 12 | 1 | 1 | 2.7574 | 10 | 0 | 0
1177.2 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1177.25 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1177.3 | 49.93 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1177.35 | 49.93 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1177.4 | 49.96 | 49.85 | 0.525 | 0.525 | 5.25 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 2.6985 | 2.6985 | 0 | 12 | 1 | 1 | 2.6985 | 10 | 0 | 0
1177.45 | 49.96 | 49.85 | 0.525 | 0.525 | 5.25 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 2.6985 | 2.6985 | 0 | 12 | 1 | 1 | 2.6985 | 10 | 0 | 0
1177.5 | 49.99 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1177.55 | 49.99 | 49.91 | 0.044118 | 0.425 | 4.25 | 49.99 | 0 | 0 | 0 | 2.125 | 2.125 | 0 | 12 | 1 | 1 | 2.125 | 10 | 0 | 0
1177.6 | 49.99 | 49.91 | 0.044118 | 0.325 | 3.25 | 49.99 | 0 | 0 | 0 | 1.625 | 1.625 | 0 | 12 | 1 | 1 | 1.625 | 10 | 0 | 0
1177.65 | 49.99 | 49.93 | 0.032353 | 0.225 | 2.25 | 49.99 | 0 | 0 | 0 | 1.125 | 1.125 | 0 | 12 | 1 | 1 | 1.125 | 10 | 0 | 0
1177.7 | 49.96 | 49.93 | 0.032353 | 0.125 | 1.25 | 49.99 | 0 | 0 | 0 | 0.625 | 0.625 | 0 | 12 | 1 | 1 | 0.625 | 10 | 0 | 0
1177.75 | 49.96 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 49.99 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1177.8 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1177.85 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1177.9 | 50.05 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.058824 | 0.058824 | 0 | 12 | 1 | 1 | 0.058824 | 10 | 0 | 0
1177.95 | 50.05 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
1178 | 49.97 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
1178.05 | 49.97 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
1178.1 | 49.92 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1178.15 | 49.92 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1178.2 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1178.25 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1178.3 | 49.94 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1178.35 | 49.94 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1178.4 | 50.01 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1178.45 | 50.01 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1178.5 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1178.55 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
1178.6 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
1178.65 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
1178.7 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
1178.75 | 49.95 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
1178.8 | 49.97 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
1178.85 | 49.97 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
1178.9 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
1178.95 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
1179 | 49.87 | 49.87 | 0.335 | 0.335 | 3.35 | 50.01 | 0 | 0 | 0 | 1.675 | 1.675 | 0 | 12 | 1 | 1 | 1.675 | 10 | 0 | 0
1179.05 | 49.87 | 49.87 | 0.335 | 0.335 | 3.35 | 49.99 | 0 | 0 | 0 | 1.675 | 1.675 | 0 | 12 | 1 | 1 | 1.675 | 10 | 0 | 0
1179.1 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1179.15 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 2.6691 | 2.6691 | 0 | 12 | 1 | 1 | 2.6691 | 10 | 0 | 0
1179.2 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1179.25 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1179.3 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1179.35 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1179.4 | 49.84 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1179.45 | 49.84 | 49.79 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
1179.5 | 49.89 | 49.79 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
1179.55 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.12647 | 1.2647 | 5.6324 | 5.6324 | 0 | 12 | 1 | 1 | 5.6324 | 10 | 0 | 0
1179.6 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.145 | 1.45 | 5.725 | 5.725 | 0 | 12 | 1 | 1 | 5.725 | 10 | 0 | 0
1179.65 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.145 | 1.45 | 5.725 | 5.725 | 0 | 12 | 1 | 1 | 5.725 | 10 | 0 | 0
1179.7 | 49.96 | 49.79 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
1179.75 | 49.96 | 49.79 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
1179.8 | 50.02 | 49.79 | 1 | 1 | 10 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 4.9853 | 4.9853 | 0 | 12 | 1 | 1 | 4.9853 | 10 | 0 | 0
1179.85 | 50.02 | 49.79 | 1 | 1 | 10 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 4.9853 | 4.9853 | 0 | 12 | 1 | 1 | 4.9853 | 10 | 0 | 0
1179.9 | 50.03 | 49.79 | 1 | 1 | 10 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.9559 | 4.9559 | 0 | 12 | 1 | 1 | 4.9559 | 10 | 0 | 0
1179.95 | 50.03 | 49.84 | 0.62 | 0.9 | 9 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.4559 | 4.4559 | 0 | 12 | 1 | 1 | 4.4559 | 10 | 0 | 0
1180 | 50.02 | 49.84 | 0.62 | 0.8 | 8 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 3.9559 | 3.9559 | 0 | 12 | 1 | 1 | 3.9559 | 10 | 0 | 0
1180.05 | 50.02 | 49.89 | 0.145 | 0.7 | 7 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 3.4559 | 3.4559 | 0 | 12 | 1 | 1 | 3.4559 | 10 | 0 | 0
1180.1 | 50.08 | 49.89 | 0.145 | 0.6 | 6 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 2.8088 | 2.8088 | 0 | 12 | 1 | 1 | 2.8088 | 10 | 0 | 0
1180.15 | 50.08 | 49.89 | 0.145 | 0.5 | 5 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 2.3088 | 2.3088 | 0 | 12 | 1 | 1 | 2.3088 | 10 | 0 | 0
1180.2 | 50.01 | 49.89 | 0.145 | 0.4 | 4 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 1.8088 | 1.8088 | 0 | 12 | 1 | 1 | 1.8088 | 10 | 0 | 0
1180.25 | 50.01 | 49.96 | 0.014706 | 0.3 | 3 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 1.3088 | 1.3088 | 0 | 12 | 1 | 1 | 1.3088 | 10 | 0 | 0
1180.3 | 49.94 | 49.94 | 0.026471 | 0.2 | 2 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.80882 | 0.80882 | 0 | 12 | 1 | 1 | 0.80882 | 10 | 0 | 0
1180.35 | 49.94 | 49.94 | 0.026471 | 0.1 | 1 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.30882 | 0.30882 | 0 | 12 | 1 | 1 | 0.30882 | 10 | 0 | 0
1180.4 | 50 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
1180.45 | 50 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
1180.5 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
1180.55 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
1180.6 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1180.65 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1180.7 | 49.92 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1180.75 | 49.92 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
1180.8 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50.01 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1180.85 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1180.9 | 49.92 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1180.95 | 49.92 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1181 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1181.05 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1181.1 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1181.15 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1181.2 | 49.87 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1181.25 | 49.87 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1181.3 | 49.8 | 49.8 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1181.35 | 49.8 | 49.8 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1181.4 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1181.45 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1181.5 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1181.55 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1181.6 | 49.72 | 49.72 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1181.65 | 49.72 | 49.72 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1181.7 | 49.67 | 49.67 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1181.75 | 49.67 | 49.67 | 1 | 1 | 10 | 49.87 | 0.335 | 0.14412 | 1.4412 | 5.7206 | 5.7206 | 0 | 12 | 1 | 1 | 5.7206 | 10 | 0 | 0
1181.8 | 49.65 | 49.65 | 1 | 1 | 10 | 49.87 | 0.335 | 0.24412 | 2.4412 | 6.2206 | 6.2206 | 0 | 12 | 1 | 1 | 6.2206 | 10 | 0 | 0
1181.85 | 49.65 | 49.65 | 1 | 1 | 10 | 49.8 | 1 | 0.34412 | 3.4412 | 6.7206 | 6.7206 | 0 | 12 | 1 | 1 | 6.7206 | 10 | 0 | 0
1181.9 | 49.59 | 49.59 | 1 | 1 | 10 | 49.8 | 1 | 0.44412 | 4.4412 | 7.2206 | 7.2206 | 0 | 12 | 1 | 1 | 7.2206 | 10 | 0 | 0
1181.95 | 49.59 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.54412 | 5.4412 | 7.7206 | 7.7206 | 0 | 12 | 1 | 1 | 7.7206 | 10 | 0 | 0
1182 | 49.66 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.64412 | 6.4412 | 8.2206 | 8.2206 | 0 | 12 | 1 | 1 | 8.2206 | 10 | 0 | 0
1182.05 | 49.66 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.74412 | 7.4412 | 8.7206 | 8.7206 | 0 | 12 | 1 | 1 | 8.7206 | 10 | 0 | 0
1182.1 | 49.63 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.84412 | 8.4412 | 9.2206 | 9.2206 | 0 | 12 | 1 | 1 | 9.2206 | 10 | 0 | 0
1182.15 | 49.63 | 49.59 | 1 | 1 | 10 | 49.72 | 1 | 0.94412 | 9.4412 | 9.7206 | 9.7206 | 0 | 12 | 1 | 1 | 9.7206 | 10 | 0 | 0
1182.2 | 49.61 | 49.59 | 1 | 1 | 10 | 49.72 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1182.25 | 49.61 | 49.59 | 1 | 1 | 10 | 49.67 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1182.3 | 49.54 | 49.54 | 1 | 1 | 10 | 49.67 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1182.35 | 49.54 | 49.54 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1182.4 | 49.46 | 49.46 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1182.45 | 49.46 | 49.46 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1182.5 | 49.45 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1182.55 | 49.45 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1182.6 | 49.51 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1182.65 | 49.51 | 49.45 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1182.7 | 49.5 | 49.45 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1182.75 | 49.5 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1182.8 | 49.54 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1182.85 | 49.54 | 49.45 | 1 | 1 | 10 | 49.54 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1182.9 | 49.59 | 49.45 | 1 | 1 | 10 | 49.59 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1182.95 | 49.59 | 49.45 | 1 | 1 | 10 | 49.59 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1183 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1183.05 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1183.1 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1183.15 | 49.61 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1183.2 | 49.53 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1183.25 | 49.53 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1183.3 | 49.54 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1183.35 | 49.54 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1183.4 | 49.61 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1183.45 | 49.61 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1183.5 | 49.66 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1183.55 | 49.66 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1183.6 | 49.64 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1183.65 | 49.64 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1183.7 | 49.69 | 49.53 | 1 | 1 | 10 | 49.69 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1183.75 | 49.69 | 49.53 | 1 | 1 | 10 | 49.69 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1183.8 | 49.74 | 49.53 | 1 | 1 | 10 | 49.74 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1183.85 | 49.74 | 49.54 | 1 | 1 | 10 | 49.74 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1183.9 | 49.78 | 49.54 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1183.95 | 49.78 | 49.61 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1184 | 49.82 | 49.61 | 1 | 1 | 10 | 49.82 | 0.81 | 0.81 | 8.1 | 9.05 | 9.05 | 0 | 12 | 1 | 1 | 9.05 | 10 | 0 | 0
1184.05 | 49.82 | 49.64 | 1 | 1 | 10 | 49.82 | 0.81 | 0.81 | 8.1 | 9.05 | 9.05 | 0 | 12 | 1 | 1 | 9.05 | 10 | 0 | 0
1184.1 | 49.86 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
1184.15 | 49.86 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
1184.2 | 49.84 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
1184.25 | 49.84 | 49.69 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
1184.3 | 49.91 | 49.69 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1184.35 | 49.91 | 49.74 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1184.4 | 49.97 | 49.74 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1184.45 | 49.97 | 49.78 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1184.5 | 50.03 | 49.78 | 1 | 1 | 10 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.9559 | 4.9559 | 0 | 12 | 1 | 1 | 4.9559 | 10 | 0 | 0
1184.55 | 50.03 | 49.82 | 0.81 | 0.9 | 9 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.4559 | 4.4559 | 0 | 12 | 1 | 1 | 4.4559 | 10 | 0 | 0
1184.6 | 50.05 | 49.82 | 0.81 | 0.81 | 8.1 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 3.9471 | 3.9471 | 0 | 12 | 1 | 1 | 3.9471 | 10 | 0 | 0
1184.65 | 50.05 | 49.84 | 0.62 | 0.71 | 7.1 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 3.4471 | 3.4471 | 0 | 12 | 1 | 1 | 3.4471 | 10 | 0 | 0
1184.7 | 50.01 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
1184.75 | 50.01 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
1184.8 | 49.95 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
1184.85 | 49.95 | 49.91 | 0.044118 | 0.52 | 5.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.4971 | 2.4971 | 0 | 12 | 1 | 1 | 2.4971 | 10 | 0 | 0
1184.9 | 49.99 | 49.91 | 0.044118 | 0.42 | 4.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 1.9971 | 1.9971 | 0 | 12 | 1 | 1 | 1.9971 | 10 | 0 | 0
1184.95 | 49.99 | 49.95 | 0.020588 | 0.32 | 3.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 1.4971 | 1.4971 | 0 | 12 | 1 | 1 | 1.4971 | 10 | 0 | 0
1185 | 49.92 | 49.92 | 0.038235 | 0.22 | 2.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.99706 | 0.99706 | 0 | 12 | 1 | 1 | 0.99706 | 10 | 0 | 0
1185.05 | 49.92 | 49.92 | 0.038235 | 0.12 | 1.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.49706 | 0.49706 | 0 | 12 | 1 | 1 | 0.49706 | 10 | 0 | 0
1185.1 | 49.97 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1185.15 | 49.97 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1185.2 | 50.02 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1185.25 | 50.02 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.17647 | 0.17647 | 0 | 12 | 1 | 1 | 0.17647 | 10 | 0 | 0
1185.3 | 50.07 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1185.35 | 50.07 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1185.4 | 50.06 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1185.45 | 50.06 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1185.5 | 50.13 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
1185.55 | 50.13 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
1185.6 | 50.09 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
1185.65 | 50.09 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6309 | -1.6309 | 0 | 12 | 1 | 1 | -1.6309 | 10 | 0 | 0
1185.7 | 50.07 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6309 | -1.6309 | 0 | 12 | 1 | 1 | -1.6309 | 10 | 0 | 0
1185.75 | 50.07 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6897 | -1.6897 | 0 | 12 | 1 | 1 | -1.6897 | 10 | 0 | 0
1185.8 | 50.07 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6897 | -1.6897 | 0 | 12 | 1 | 1 | -1.6897 | 10 | 0 | 0
1185.85 | 50.07 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.13 | -0.335 | -0.335 | -3.35 | -1.8074 | -1.8074 | 0 | 12 | 1 | 1 | -1.8074 | 10 | 0 | 0
1185.9 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.13 | -0.335 | -0.335 | -3.35 | -1.7779 | -1.7779 | 0 | 12 | 1 | 1 | -1.7779 | 10 | 0 | 0
1185.95 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.13 | -0.335 | -0.335 | -3.35 | -1.7779 | -1.7779 | 0 | 12 | 1 | 1 | -1.7779 | 10 | 0 | 0
1186 | 50.01 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
1186.05 | 50.01 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
1186.1 | 50.07 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
1186.15 | 50.07 | 50.01 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.235 | -2.35 | -1.175 | -1.175 | 0 | 12 | 1 | 1 | -1.175 | 10 | 0 | 0
1186.2 | 50.05 | 50.01 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.135 | -1.35 | -0.675 | -0.675 | 0 | 12 | 1 | 1 | -0.675 | 10 | 0 | 0
1186.25 | 50.05 | 50.01 | 0 | 0 | 0 | 50.07 | -0.032353 | -0.035 | -0.35 | -0.175 | -0.175 | 0 | 12 | 1 | 1 | -0.175 | 10 | 0 | 0
1186.3 | 50.1 | 50.01 | 0 | 0 | 0 | 50.1 | -0.05 | -0.05 | -0.5 | -0.25 | -0.25 | 0 | 12 | 1 | 1 | -0.25 | 10 | 0 | 0
1186.35 | 50.1 | 50.01 | 0 | 0 | 0 | 50.1 | -0.05 | -0.05 | -0.5 | -0.25 | -0.25 | 0 | 12 | 1 | 1 | -0.25 | 10 | 0 | 0
1186.4 | 50.11 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1186.45 | 50.11 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1186.5 | 50.06 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1186.55 | 50.06 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1186.6 | 50.04 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1186.65 | 50.04 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1186.7 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1186.75 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1186.8 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1186.85 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1186.9 | 50.11 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1186.95 | 50.11 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1187 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1187.05 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1187.1 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1187.15 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1187.2 | 50.02 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.11 | -0.145 | -0.145 | -1.45 | -0.73971 | -0.73971 | 0 | 12 | 1 | 1 | -0.73971 | 10 | 0 | 0
1187.25 | 50.02 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.11 | -0.145 | -0.145 | -1.45 | -0.73971 | -0.73971 | 0 | 12 | 1 | 1 | -0.73971 | 10 | 0 | 0
1187.3 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1187.35 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1187.4 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1187.45 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1187.5 | 50.01 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1187.55 | 50.01 | 50 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.045 | -0.45 | -0.225 | -0.225 | 0 | 12 | 1 | 1 | -0.225 | 10 | 0 | 0
1187.6 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
1187.65 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
1187.7 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
1187.75 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1187.8 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.14706 | 0.14706 | 0 | 12 | 1 | 1 | 0.14706 | 10 | 0 | 0
1187.85 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1187.9 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1187.95 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1188 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1188.05 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1188.1 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1188.15 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1188.2 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1188.25 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1188.3 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1188.35 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1188.4 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1188.45 | 50 | 50 | 0 | 0 | 0 | 50.01 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1188.5 | 49.5 | 49.5 | 1 | 1 | 10 | 50.01 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1188.55 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1188.6 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1188.65 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1188.7 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1188.75 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1188.8 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1188.85 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1188.9 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1188.95 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1189 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1189.05 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.1 | 1 | 5.5 | 5.5 | 0 | 12 | 1 | 1 | 5.5 | 10 | 0 | 0
1189.1 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.2 | 2 | 6 | 6 | 0 | 12 | 1 | 1 | 6 | 10 | 0 | 0
1189.15 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.3 | 3 | 6.5 | 6.5 | 0 | 12 | 1 | 1 | 6.5 | 10 | 0 | 0
1189.2 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.4 | 4 | 7 | 7 | 0 | 12 | 1 | 1 | 7 | 10 | 0 | 0
1189.25 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.5 | 5 | 7.5 | 7.5 | 0 | 12 | 1 | 1 | 7.5 | 10 | 0 | 0
1189.3 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.6 | 6 | 8 | 8 | 0 | 12 | 1 | 1 | 8 | 10 | 0 | 0
1189.35 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.7 | 7 | 8.5 | 8.5 | 0 | 12 | 1 | 1 | 8.5 | 10 | 0 | 0
1189.4 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.8 | 8 | 9 | 9 | 0 | 12 | 1 | 1 | 9 | 10 | 0 | 0
1189.45 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.9 | 9 | 9.5 | 9.5 | 0 | 12 | 1 | 1 | 9.5 | 10 | 0 | 0
1189.5 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1189.55 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1189.6 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1189.65 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1189.7 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1189.75 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1189.8 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1189.85 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1189.9 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1189.95 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1190 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1190.05 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1190.1 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1190.15 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1190.2 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1190.25 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1190.3 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1190.35 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1190.4 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1190.45 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1190.5 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1190.55 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1190.6 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1190.65 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1190.7 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1190.75 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1190.8 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1190.85 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1190.9 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1190.95 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1191 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1191.05 | 50.5 | 50.5 | -1 | 0.9 | 9 | 50.5 | -1 | -1 | -10 | -0.5 | -0.5 | 0 | 12 | 1 | 1 | -0.5 | 10 | 0 | 0
1191.1 | 50.5 | 50.5 | -1 | 0.8 | 8 | 50.5 | -1 | -1 | -10 | -1 | -1 | 0 | 12 | 1 | 1 | -1 | 10 | 0 | 0
1191.15 | 50.5 | 50.5 | -1 | 0.7 | 7 | 50.5 | -1 | -1 | -10 | -1.5 | -1.5 | 0 | 12 | 1 | 1 | -1.5 | 10 | 0 | 0
1191.2 | 50.5 | 50.5 | -1 | 0.6 | 6 | 50.5 | -1 | -1 | -10 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
1191.25 | 50.5 | 50.5 | -1 | 0.5 | 5 | 50.5 | -1 | -1 | -10 | -2.5 | -2.5 | 0 | 12 | 1 | 1 | -2.5 | 10 | 0 | 0
1191.3 | 50.5 | 50.5 | -1 | 0.4 | 4 | 50.5 | -1 | -1 | -10 | -3 | -3 | 0 | 12 | 1 | 1 | -3 | 10 | 0 | 0
1191.35 | 50.5 | 50.5 | -1 | 0.3 | 3 | 50.5 | -1 | -1 | -10 | -3.5 | -3.5 | 0 | 12 | 1 | 1 | -3.5 | 10 | 0 | 0
1191.4 | 50.5 | 50.5 | -1 | 0.2 | 2 | 50.5 | -1 | -1 | -10 | -4 | -4 | 0 | 12 | 1 | 1 | -4 | 10 | 0 | 0
1191.45 | 50.5 | 50.5 | -1 | 0.1 | 1 | 50.5 | -1 | -1 | -10 | -4.5 | -4.5 | 0 | 12 | 1 | 1 | -4.5 | 10 | 0 | 0
1191.5 | 50.5 | 50.5 | -1 | 0 | 0 | 50.5 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1191.55 | 50.5 | 50.5 | -1 | -0.1 | -1 | 50.5 | -1 | -1 | -10 | -5.5 | -5.5 | 0 | 12 | 1 | 1 | -5.5 | 10 | 0 | 0
1191.6 | 50.5 | 50.5 | -1 | -0.2 | -2 | 50.5 | -1 | -1 | -10 | -6 | -6 | 0 | 12 | 1 | 1 | -6 | 10 | 0 | 0
1191.65 | 50.5 | 50.5 | -1 | -0.3 | -3 | 50.5 | -1 | -1 | -10 | -6.5 | -6.5 | 0 | 12 | 1 | 1 | -6.5 | 10 | 0 | 0
1191.7 | 50.5 | 50.5 | -1 | -0.4 | -4 | 50.5 | -1 | -1 | -10 | -7 | -7 | 0 | 12 | 1 | 1 | -7 | 10 | 0 | 0
1191.75 | 50.5 | 50.5 | -1 | -0.5 | -5 | 50.5 | -1 | -1 | -10 | -7.5 | -7.5 | 0 | 12 | 1 | 1 | -7.5 | 10 | 0 | 0
1191.8 | 50.5 | 50.5 | -1 | -0.6 | -6 | 50.5 | -1 | -1 | -10 | -8 | -8 | 0 | 12 | 1 | 1 | -8 | 10 | 0 | 0
1191.85 | 50.5 | 50.5 | -1 | -0.7 | -7 | 50.5 | -1 | -1 | -10 | -8.5 | -8.5 | 0 | 12 | 1 | 1 | -8.5 | 10 | 0 | 0
1191.9 | 50.5 | 50.5 | -1 | -0.8 | -8 | 50.5 | -1 | -1 | -10 | -9 | -9 | 0 | 12 | 1 | 1 | -9 | 10 | 0 | 0
1191.95 | 50.5 | 50.5 | -1 | -0.9 | -9 | 50.5 | -1 | -1 | -10 | -9.5 | -9.5 | 0 | 12 | 1 | 1 | -9.5 | 10 | 0 | 0
1192 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1192.05 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1192.1 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1192.15 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1192.2 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1192.25 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1192.3 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1192.35 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1192.4 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1192.45 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1192.5 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1192.55 | 50.47 | 50.47 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1192.6 | 50.45 | 50.45 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1192.65 | 50.42 | 50.42 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1192.7 | 50.4 | 50.4 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1192.75 | 50.37 | 50.37 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1192.8 | 50.35 | 50.35 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1192.85 | 50.32 | 50.32 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1192.9 | 50.29 | 50.29 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1192.95 | 50.27 | 50.27 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1193 | 50.24 | 50.24 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1193.05 | 50.22 | 50.22 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1193.1 | 50.19 | 50.19 | -0.905 | -0.905 | -9.05 | 50.47 | -1 | -1 | -10 | -9.525 | -9.525 | 0 | 12 | 1 | 1 | -9.525 | 10 | 0 | 0
1193.15 | 50.17 | 50.17 | -0.715 | -0.715 | -7.15 | 50.45 | -1 | -1 | -10 | -8.575 | -8.575 | 0 | 12 | 1 | 1 | -8.575 | 10 | 0 | 0
1193.2 | 50.14 | 50.14 | -0.43 | -0.43 | -4.3 | 50.42 | -1 | -1 | -10 | -7.15 | -7.15 | 0 | 12 | 1 | 1 | -7.15 | 10 | 0 | 0
1193.25 | 50.12 | 50.12 | -0.24 | -0.24 | -2.4 | 50.4 | -1 | -1 | -10 | -6.2 | -6.2 | 0 | 12 | 1 | 1 | -6.2 | 10 | 0 | 0
1193.3 | 50.09 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 50.37 | -1 | -1 | -10 | -5.2206 | -5.2206 | 0 | 12 | 1 | 1 | -5.2206 | 10 | 0 | 0
1193.35 | 50.06 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.35 | -1 | -1 | -10 | -5.1324 | -5.1324 | 0 | 12 | 1 | 1 | -5.1324 | 10 | 0 | 0
1193.4 | 50.04 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.32 | -1 | -1 | -10 | -5.0735 | -5.0735 | 0 | 12 | 1 | 1 | -5.0735 | 10 | 0 | 0
1193.45 | 50.01 | 50.01 | 0 | 0 | 0 | 50.29 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1193.5 | 49.99 | 49.99 | 0 | 0 | 0 | 50.27 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1193.55 | 49.96 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.24 | -1 | -1 | -10 | -4.9265 | -4.9265 | 0 | 12 | 1 | 1 | -4.9265 | 10 | 0 | 0
1193.6 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.22 | -1 | -1 | -10 | -4.8676 | -4.8676 | 0 | 12 | 1 | 1 | -4.8676 | 10 | 0 | 0
1193.65 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.19 | -0.905 | -0.905 | -9.05 | -4.3044 | -4.3044 | 0 | 12 | 1 | 1 | -4.3044 | 10 | 0 | 0
1193.7 | 49.88 | 49.88 | 0.24 | 0.24 | 2.4 | 50.17 | -0.715 | -0.805 | -8.05 | -2.825 | -2.825 | 0 | 12 | 1 | 1 | -2.825 | 10 | 0 | 0
1193.75 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.14 | -0.43 | -0.705 | -7.05 | -1.375 | -1.375 | 0 | 12 | 1 | 1 | -1.375 | 10 | 0 | 0
1193.8 | 49.83 | 49.83 | 0.715 | 0.715 | 7.15 | 50.12 | -0.24 | -0.605 | -6.05 | 0.55 | 0.55 | 0 | 12 | 1 | 1 | 0.55 | 10 | 0 | 0
1193.85 | 49.81 | 49.81 | 0.905 | 0.905 | 9.05 | 50.09 | -0.044118 | -0.505 | -5.05 | 2 | 2 | 0 | 12 | 1 | 1 | 2 | 10 | 0 | 0
1193.9 | 49.78 | 49.78 | 1 | 1 | 10 | 50.06 | -0.026471 | -0.405 | -4.05 | 2.975 | 2.975 | 0 | 12 | 1 | 1 | 2.975 | 10 | 0 | 0
1193.95 | 49.76 | 49.76 | 1 | 1 | 10 | 50.04 | -0.014706 | -0.305 | -3.05 | 3.475 | 3.475 | 0 | 12 | 1 | 1 | 3.475 | 10 | 0 | 0
1194 | 49.73 | 49.73 | 1 | 1 | 10 | 50.01 | 0 | -0.205 | -2.05 | 3.975 | 3.975 | 0 | 12 | 1 | 1 | 3.975 | 10 | 0 | 0
1194.05 | 49.71 | 49.71 | 1 | 1 | 10 | 49.99 | 0 | -0.105 | -1.05 | 4.475 | 4.475 | 0 | 12 | 1 | 1 | 4.475 | 10 | 0 | 0
1194.1 | 49.68 | 49.68 | 1 | 1 | 10 | 49.96 | 0.014706 | -0.005 | -0.05 | 4.975 | 4.975 | 0 | 12 | 1 | 1 | 4.975 | 10 | 0 | 0
1194.15 | 49.65 | 49.65 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
1194.2 | 49.63 | 49.63 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1194.25 | 49.6 | 49.6 | 1 | 1 | 10 | 49.88 | 0.24 | 0.14412 | 1.4412 | 5.7206 | 5.7206 | 0 | 12 | 1 | 1 | 5.7206 | 10 | 0 | 0
1194.3 | 49.58 | 49.58 | 1 | 1 | 10 | 49.86 | 0.43 | 0.24412 | 2.4412 | 6.2206 | 6.2206 | 0 | 12 | 1 | 1 | 6.2206 | 10 | 0 | 0
1194.35 | 49.55 | 49.55 | 1 | 1 | 10 | 49.83 | 0.715 | 0.34412 | 3.4412 | 6.7206 | 6.7206 | 0 | 12 | 1 | 1 | 6.7206 | 10 | 0 | 0
1194.4 | 49.53 | 49.53 | 1 | 1 | 10 | 49.81 | 0.905 | 0.44412 | 4.4412 | 7.2206 | 7.2206 | 0 | 12 | 1 | 1 | 7.2206 | 10 | 0 | 0
1194.45 | 49.5 | 49.5 | 1 | 1 | 10 | 49.78 | 1 | 0.54412 | 5.4412 | 7.7206 | 7.7206 | 0 | 12 | 1 | 1 | 7.7206 | 10 | 0 | 0
1194.5 | 49.5 | 49.5 | 1 | 1 | 10 | 49.76 | 1 | 0.64412 | 6.4412 | 8.2206 | 8.2206 | 0 | 12 | 1 | 1 | 8.2206 | 10 | 0 | 0
1194.55 | 49.53 | 49.5 | 1 | 1 | 10 | 49.73 | 1 | 0.74412 | 7.4412 | 8.7206 | 8.7206 | 0 | 12 | 1 | 1 | 8.7206 | 10 | 0 | 0
1194.6 | 49.55 | 49.5 | 1 | 1 | 10 | 49.71 | 1 | 0.84412 | 8.4412 | 9.2206 | 9.2206 | 0 | 12 | 1 | 1 | 9.2206 | 10 | 0 | 0
1194.65 | 49.58 | 49.5 | 1 | 1 | 10 | 49.68 | 1 | 0.94412 | 9.4412 | 9.7206 | 9.7206 | 0 | 12 | 1 | 1 | 9.7206 | 10 | 0 | 0
1194.7 | 49.6 | 49.5 | 1 | 1 | 10 | 49.65 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1194.75 | 49.63 | 49.5 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1194.8 | 49.65 | 49.5 | 1 | 1 | 10 | 49.65 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1194.85 | 49.68 | 49.5 | 1 | 1 | 10 | 49.68 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1194.9 | 49.71 | 49.5 | 1 | 1 | 10 | 49.71 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1194.95 | 49.73 | 49.5 | 1 | 1 | 10 | 49.73 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1195 | 49.76 | 49.5 | 1 | 1 | 10 | 49.76 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1195.05 | 49.78 | 49.5 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1195.1 | 49.81 | 49.53 | 1 | 1 | 10 | 49.81 | 0.905 | 0.905 | 9.05 | 9.525 | 9.525 | 0 | 12 | 1 | 1 | 9.525 | 10 | 0 | 0
1195.15 | 49.83 | 49.55 | 1 | 1 | 10 | 49.83 | 0.715 | 0.715 | 7.15 | 8.575 | 8.575 | 0 | 12 | 1 | 1 | 8.575 | 10 | 0 | 0
1195.2 | 49.86 | 49.58 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
1195.25 | 49.88 | 49.6 | 1 | 1 | 10 | 49.88 | 0.24 | 0.24 | 2.4 | 6.2 | 6.2 | 0 | 12 | 1 | 1 | 6.2 | 10 | 0 | 0
1195.3 | 49.91 | 49.63 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1195.35 | 49.94 | 49.65 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
1195.4 | 49.96 | 49.68 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
1195.45 | 49.99 | 49.71 | 1 | 1 | 10 | 49.99 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1195.5 | 50.01 | 49.73 | 1 | 1 | 10 | 50.01 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1195.55 | 50.04 | 49.76 | 1 | 1 | 10 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 4.9265 | 4.9265 | 0 | 12 | 1 | 1 | 4.9265 | 10 | 0 | 0
1195.6 | 50.06 | 49.78 | 1 | 1 | 10 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 4.8676 | 4.8676 | 0 | 12 | 1 | 1 | 4.8676 | 10 | 0 | 0
1195.65 | 50.09 | 49.81 | 0.905 | 0.905 | 9.05 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 4.3044 | 4.3044 | 0 | 12 | 1 | 1 | 4.3044 | 10 | 0 | 0
1195.7 | 50.12 | 49.83 | 0.715 | 0.805 | 8.05 | 50.12 | -0.24 | -0.24 | -2.4 | 2.825 | 2.825 | 0 | 12 | 1 | 1 | 2.825 | 10 | 0 | 0
1195.75 | 50.14 | 49.86 | 0.43 | 0.705 | 7.05 | 50.14 | -0.43 | -0.43 | -4.3 | 1.375 | 1.375 | 0 | 12 | 1 | 1 | 1.375 | 10 | 0 | 0
1195.8 | 50.17 | 49.88 | 0.24 | 0.605 | 6.05 | 50.17 | -0.715 | -0.715 | -7.15 | -0.55 | -0.55 | 0 | 12 | 1 | 1 | -0.55 | 10 | 0 | 0
1195.85 | 50.19 | 49.91 | 0.044118 | 0.505 | 5.05 | 50.19 | -0.905 | -0.905 | -9.05 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
1195.9 | 50.22 | 49.94 | 0.026471 | 0.405 | 4.05 | 50.22 | -1 | -1 | -10 | -2.975 | -2.975 | 0 | 12 | 1 | 1 | -2.975 | 10 | 0 | 0
1195.95 | 50.24 | 49.96 | 0.014706 | 0.305 | 3.05 | 50.24 | -1 | -1 | -10 | -3.475 | -3.475 | 0 | 12 | 1 | 1 | -3.475 | 10 | 0 | 0
1196 | 50.27 | 49.99 | 0 | 0.205 | 2.05 | 50.27 | -1 | -1 | -10 | -3.975 | -3.975 | 0 | 12 | 1 | 1 | -3.975 | 10 | 0 | 0
1196.05 | 50.29 | 50.01 | 0 | 0.105 | 1.05 | 50.29 | -1 | -1 | -10 | -4.475 | -4.475 | 0 | 12 | 1 | 1 | -4.475 | 10 | 0 | 0
1196.1 | 50.32 | 50.04 | -0.014706 | 0.005 | 0.05 | 50.32 | -1 | -1 | -10 | -4.975 | -4.975 | 0 | 12 | 1 | 1 | -4.975 | 10 | 0 | 0
1196.15 | 50.35 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.35 | -1 | -1 | -10 | -5.1324 | -5.1324 | 0 | 12 | 1 | 1 | -5.1324 | 10 | 0 | 0
1196.2 | 50.37 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 50.37 | -1 | -1 | -10 | -5.2206 | -5.2206 | 0 | 12 | 1 | 1 | -5.2206 | 10 | 0 | 0
1196.25 | 50.4 | 50.12 | -0.24 | -0.14412 | -1.4412 | 50.4 | -1 | -1 | -10 | -5.7206 | -5.7206 | 0 | 12 | 1 | 1 | -5.7206 | 10 | 0 | 0
1196.3 | 50.42 | 50.14 | -0.43 | -0.24412 | -2.4412 | 50.42 | -1 | -1 | -10 | -6.2206 | -6.2206 | 0 | 12 | 1 | 1 | -6.2206 | 10 | 0 | 0
1196.35 | 50.45 | 50.17 | -0.715 | -0.34412 | -3.4412 | 50.45 | -1 | -1 | -10 | -6.7206 | -6.7206 | 0 | 12 | 1 | 1 | -6.7206 | 10 | 0 | 0
1196.4 | 50.47 | 50.19 | -0.905 | -0.44412 | -4.4412 | 50.47 | -1 | -1 | -10 | -7.2206 | -7.2206 | 0 | 12 | 1 | 1 | -7.2206 | 10 | 0 | 0
1196.45 | 50.5 | 50.22 | -1 | -0.54412 | -5.4412 | 50.5 | -1 | -1 | -10 | -7.7206 | -7.7206 | 0 | 12 | 1 | 1 | -7.7206 | 10 | 0 | 0
1196.5 | 50.5 | 50.24 | -1 | -0.64412 | -6.4412 | 50.5 | -1 | -1 | -10 | -8.2206 | -8.2206 | 0 | 12 | 1 | 1 | -8.2206 | 10 | 0 | 0
1196.55 | 50.47 | 50.27 | -1 | -0.74412 | -7.4412 | 50.5 | -1 | -1 | -10 | -8.7206 | -8.7206 | 0 | 12 | 1 | 1 | -8.7206 | 10 | 0 | 0
1196.6 | 50.45 | 50.29 | -1 | -0.84412 | -8.4412 | 50.5 | -1 | -1 | -10 | -9.2206 | -9.2206 | 0 | 12 | 1 | 1 | -9.2206 | 10 | 0 | 0
1196.65 | 50.42 | 50.32 | -1 | -0.94412 | -9.4412 | 50.5 | -1 | -1 | -10 | -9.7206 | -9.7206 | 0 | 12 | 1 | 1 | -9.7206 | 10 | 0 | 0
1196.7 | 50.39 | 50.35 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1196.75 | 50.37 | 50.37 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1196.8 | 50.34 | 50.34 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1196.85 | 50.32 | 50.32 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1196.9 | 50.29 | 50.29 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1196.95 | 50.26 | 50.26 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1197 | 50.24 | 50.24 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1197.05 | 50.21 | 50.21 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1197.1 | 50.18 | 50.18 | -0.81 | -0.81 | -8.1 | 50.47 | -1 | -1 | -10 | -9.05 | -9.05 | 0 | 12 | 1 | 1 | -9.05 | 10 | 0 | 0
1197.15 | 50.16 | 50.16 | -0.62 | -0.62 | -6.2 | 50.45 | -1 | -1 | -10 | -8.1 | -8.1 | 0 | 12 | 1 | 1 | -8.1 | 10 | 0 | 0
1197.2 | 50.13 | 50.13 | -0.335 | -0.335 | -3.35 | 50.42 | -1 | -1 | -10 | -6.675 | -6.675 | 0 | 12 | 1 | 1 | -6.675 | 10 | 0 | 0
1197.25 | 50.11 | 50.11 | -0.145 | -0.145 | -1.45 | 50.39 | -1 | -1 | -10 | -5.725 | -5.725 | 0 | 12 | 1 | 1 | -5.725 | 10 | 0 | 0
1197.3 | 50.08 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 50.37 | -1 | -1 | -10 | -5.1912 | -5.1912 | 0 | 12 | 1 | 1 | -5.1912 | 10 | 0 | 0
1197.35 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.34 | -1 | -1 | -10 | -5.1029 | -5.1029 | 0 | 12 | 1 | 1 | -5.1029 | 10 | 0 | 0
1197.4 | 50.03 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 50.32 | -1 | -1 | -10 | -5.0441 | -5.0441 | 0 | 12 | 1 | 1 | -5.0441 | 10 | 0 | 0
1197.45 | 50 | 50 | 0 | 0 | 0 | 50.29 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1197.5 | 50 | 50 | 0 | 0 | 0 | 50.26 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1197.55 | 50 | 50 | 0 | 0 | 0 | 50.24 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1197.6 | 50 | 50 | 0 | 0 | 0 | 50.21 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1197.65 | 50 | 50 | 0 | 0 | 0 | 50.18 | -0.81 | -0.9 | -9 | -4.5 | -4.5 | 0 | 12 | 1 | 1 | -4.5 | 10 | 0 | 0
1197.7 | 50 | 50 | 0 | 0 | 0 | 50.16 | -0.62 | -0.8 | -8 | -4 | -4 | 0 | 12 | 1 | 1 | -4 | 10 | 0 | 0
1197.75 | 50 | 50 | 0 | 0 | 0 | 50.13 | -0.335 | -0.7 | -7 | -3.5 | -3.5 | 0 | 12 | 1 | 1 | -3.5 | 10 | 0 | 0
1197.8 | 50.01 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.6 | -6 | -3 | -3 | 0 | 12 | 1 | 1 | -3 | 10 | 0 | 0
1197.85 | 50.01 | 50 | 0 | 0 | 0 | 50.08 | -0.038235 | -0.5 | -5 | -2.5 | -2.5 | 0 | 12 | 1 | 1 | -2.5 | 10 | 0 | 0
1197.9 | 49.99 | 49.99 | 0 | 0 | 0 | 50.05 | -0.020588 | -0.4 | -4 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
1197.95 | 49.99 | 49.99 | 0 | 0 | 0 | 50.03 | -0.0088235 | -0.3 | -3 | -1.5 | -1.5 | 0 | 12 | 1 | 1 | -1.5 | 10 | 0 | 0
1198 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | -0.2 | -2 | -0.83824 | -0.83824 | 0 | 12 | 1 | 1 | -0.83824 | 10 | 0 | 0
1198.05 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | -0.1 | -1 | -0.33824 | -0.33824 | 0 | 12 | 1 | 1 | -0.33824 | 10 | 0 | 0
1198.1 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
1198.15 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
1198.2 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
1198.25 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
1198.3 | 49.89 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
1198.35 | 49.89 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
1198.4 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50.01 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1198.45 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1198.5 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1198.55 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 2.7868 | 2.7868 | 0 | 12 | 1 | 1 | 2.7868 | 10 | 0 | 0
1198.6 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 2.7868 | 2.7868 | 0 | 12 | 1 | 1 | 2.7868 | 10 | 0 | 0
1198.65 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 2.8456 | 2.8456 | 0 | 12 | 1 | 1 | 2.8456 | 10 | 0 | 0
1198.7 | 49.94 | 49.85 | 0.525 | 0.525 | 5.25 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 2.7574 | 2.7574 | 0 | 12 | 1 | 1 | 2.7574 | 10 | 0 | 0
1198.75 | 49.94 | 49.85 | 0.525 | 0.525 | 5.25 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 2.7574 | 2.7574 | 0 | 12 | 1 | 1 | 2.7574 | 10 | 0 | 0
1198.8 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1198.85 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1198.9 | 49.93 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1198.95 | 49.93 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1199 | 49.96 | 49.85 | 0.525 | 0.525 | 5.25 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 2.6985 | 2.6985 | 0 | 12 | 1 | 1 | 2.6985 | 10 | 0 | 0
1199.05 | 49.96 | 49.85 | 0.525 | 0.525 | 5.25 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 2.6985 | 2.6985 | 0 | 12 | 1 | 1 | 2.6985 | 10 | 0 | 0
1199.1 | 49.99 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1199.15 | 49.99 | 49.91 | 0.044118 | 0.425 | 4.25 | 49.99 | 0 | 0 | 0 | 2.125 | 2.125 | 0 | 12 | 1 | 1 | 2.125 | 10 | 0 | 0
1199.2 | 49.99 | 49.91 | 0.044118 | 0.325 | 3.25 | 49.99 | 0 | 0 | 0 | 1.625 | 1.625 | 0 | 12 | 1 | 1 | 1.625 | 10 | 0 | 0
1199.25 | 49.99 | 49.93 | 0.032353 | 0.225 | 2.25 | 49.99 | 0 | 0 | 0 | 1.125 | 1.125 | 0 | 12 | 1 | 1 | 1.125 | 10 | 0 | 0
1199.3 | 49.96 | 49.93 | 0.032353 | 0.125 | 1.25 | 49.99 | 0 | 0 | 0 | 0.625 | 0.625 | 0 | 12 | 1 | 1 | 0.625 | 10 | 0 | 0
1199.35 | 49.96 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 49.99 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1199.4 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1199.45 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1199.5 | 50.05 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.058824 | 0.058824 | 0 | 12 | 1 | 1 | 0.058824 | 10 | 0 | 0
1199.55 | 50.05 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
1199.6 | 49.97 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
1199.65 | 49.97 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
1199.7 | 49.92 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1199.75 | 49.92 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1199.8 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1199.85 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1199.9 | 49.94 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1199.95 | 49.94 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1200 | 50.01 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1200.05 | 50.01 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1200.1 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1200.15 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
1200.2 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
1200.25 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
1200.3 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
1200.35 | 49.95 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
1200.4 | 49.97 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
1200.45 | 49.97 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
1200.5 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
1200.55 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
1200.6 | 49.87 | 49.87 | 0.335 | 0.335 | 3.35 | 50.01 | 0 | 0 | 0 | 1.675 | 1.675 | 0 | 12 | 1 | 1 | 1.675 | 10 | 0 | 0
1200.65 | 49.87 | 49.87 | 0.335 | 0.335 | 3.35 | 49.99 | 0 | 0 | 0 | 1.675 | 1.675 | 0 | 12 | 1 | 1 | 1.675 | 10 | 0 | 0
1200.7 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1200.75 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 2.6691 | 2.6691 | 0 | 12 | 1 | 1 | 2.6691 | 10 | 0 | 0
1200.8 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1200.85 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1200.9 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1200.95 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1201 | 49.84 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1201.05 | 49.84 | 49.79 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
1201.1 | 49.89 | 49.79 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
1201.15 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.12647 | 1.2647 | 5.6324 | 5.6324 | 0 | 12 | 1 | 1 | 5.6324 | 10 | 0 | 0
1201.2 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.145 | 1.45 | 5.725 | 5.725 | 0 | 12 | 1 | 1 | 5.725 | 10 | 0 | 0
1201.25 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.145 | 1.45 | 5.725 | 5.725 | 0 | 12 | 1 | 1 | 5.725 | 10 | 0 | 0
1201.3 | 49.96 | 49.79 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
1201.35 | 49.96 | 49.79 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
1201.4 | 50.02 | 49.79 | 1 | 1 | 10 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 4.9853 | 4.9853 | 0 | 12 | 1 | 1 | 4.9853 | 10 | 0 | 0
1201.45 | 50.02 | 49.79 | 1 | 1 | 10 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 4.9853 | 4.9853 | 0 | 12 | 1 | 1 | 4.9853 | 10 | 0 | 0
1201.5 | 50.03 | 49.79 | 1 | 1 | 10 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.9559 | 4.9559 | 0 | 12 | 1 | 1 | 4.9559 | 10 | 0 | 0
1201.55 | 50.03 | 49.84 | 0.62 | 0.9 | 9 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.4559 | 4.4559 | 0 | 12 | 1 | 1 | 4.4559 | 10 | 0 | 0
1201.6 | 50.02 | 49.84 | 0.62 | 0.8 | 8 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 3.9559 | 3.9559 | 0 | 12 | 1 | 1 | 3.9559 | 10 | 0 | 0
1201.65 | 50.02 | 49.89 | 0.145 | 0.7 | 7 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 3.4559 | 3.4559 | 0 | 12 | 1 | 1 | 3.4559 | 10 | 0 | 0
1201.7 | 50.08 | 49.89 | 0.145 | 0.6 | 6 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 2.8088 | 2.8088 | 0 | 12 | 1 | 1 | 2.8088 | 10 | 0 | 0
1201.75 | 50.08 | 49.89 | 0.145 | 0.5 | 5 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 2.3088 | 2.3088 | 0 | 12 | 1 | 1 | 2.3088 | 10 | 0 | 0
1201.8 | 50.01 | 49.89 | 0.145 | 0.4 | 4 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 1.8088 | 1.8088 | 0 | 12 | 1 | 1 | 1.8088 | 10 | 0 | 0
1201.85 | 50.01 | 49.96 | 0.014706 | 0.3 | 3 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 1.3088 | 1.3088 | 0 | 12 | 1 | 1 | 1.3088 | 10 | 0 | 0
1201.9 | 49.94 | 49.94 | 0.026471 | 0.2 | 2 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.80882 | 0.80882 | 0 | 12 | 1 | 1 | 0.80882 | 10 | 0 | 0
1201.95 | 49.94 | 49.94 | 0.026471 | 0.1 | 1 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.30882 | 0.30882 | 0 | 12 | 1 | 1 | 0.30882 | 10 | 0 | 0
1202 | 50 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
1202.05 | 50 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
1202.1 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
1202.15 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
1202.2 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1202.25 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1202.3 | 49.92 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1202.35 | 49.92 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
1202.4 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50.01 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1202.45 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1202.5 | 49.92 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1202.55 | 49.92 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1202.6 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1202.65 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1202.7 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1202.75 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1202.8 | 49.87 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1202.85 | 49.87 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1202.9 | 49.8 | 49.8 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1202.95 | 49.8 | 49.8 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1203 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1203.05 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1203.1 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1203.15 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1203.2 | 49.72 | 49.72 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1203.25 | 49.72 | 49.72 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1203.3 | 49.67 | 49.67 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1203.35 | 49.67 | 49.67 | 1 | 1 | 10 | 49.87 | 0.335 | 0.14412 | 1.4412 | 5.7206 | 5.7206 | 0 | 12 | 1 | 1 | 5.7206 | 10 | 0 | 0
1203.4 | 49.65 | 49.65 | 1 | 1 | 10 | 49.87 | 0.335 | 0.24412 | 2.4412 | 6.2206 | 6.2206 | 0 | 12 | 1 | 1 | 6.2206 | 10 | 0 | 0
1203.45 | 49.65 | 49.65 | 1 | 1 | 10 | 49.8 | 1 | 0.34412 | 3.4412 | 6.7206 | 6.7206 | 0 | 12 | 1 | 1 | 6.7206 | 10 | 0 | 0
1203.5 | 49.59 | 49.59 | 1 | 1 | 10 | 49.8 | 1 | 0.44412 | 4.4412 | 7.2206 | 7.2206 | 0 | 12 | 1 | 1 | 7.2206 | 10 | 0 | 0
1203.55 | 49.59 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.54412 | 5.4412 | 7.7206 | 7.7206 | 0 | 12 | 1 | 1 | 7.7206 | 10 | 0 | 0
1203.6 | 49.66 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.64412 | 6.4412 | 8.2206 | 8.2206 | 0 | 12 | 1 | 1 | 8.2206 | 10 | 0 | 0
1203.65 | 49.66 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.74412 | 7.4412 | 8.7206 | 8.7206 | 0 | 12 | 1 | 1 | 8.7206 | 10 | 0 | 0
1203.7 | 49.63 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.84412 | 8.4412 | 9.2206 | 9.2206 | 0 | 12 | 1 | 1 | 9.2206 | 10 | 0 | 0
1203.75 | 49.63 | 49.59 | 1 | 1 | 10 | 49.72 | 1 | 0.94412 | 9.4412 | 9.7206 | 9.7206 | 0 | 12 | 1 | 1 | 9.7206 | 10 | 0 | 0
1203.8 | 49.61 | 49.59 | 1 | 1 | 10 | 49.72 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1203.85 | 49.61 | 49.59 | 1 | 1 | 10 | 49.67 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1203.9 | 49.54 | 49.54 | 1 | 1 | 10 | 49.67 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1203.95 | 49.54 | 49.54 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1204 | 49.46 | 49.46 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1204.05 | 49.46 | 49.46 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1204.1 | 49.45 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1204.15 | 49.45 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1204.2 | 49.51 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1204.25 | 49.51 | 49.45 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1204.3 | 49.5 | 49.45 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1204.35 | 49.5 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1204.4 | 49.54 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1204.45 | 49.54 | 49.45 | 1 | 1 | 10 | 49.54 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1204.5 | 49.59 | 49.45 | 1 | 1 | 10 | 49.59 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1204.55 | 49.59 | 49.45 | 1 | 1 | 10 | 49.59 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1204.6 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1204.65 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1204.7 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1204.75 | 49.61 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1204.8 | 49.53 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1204.85 | 49.53 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1204.9 | 49.54 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1204.95 | 49.54 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1205 | 49.61 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1205.05 | 49.61 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1205.1 | 49.66 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1205.15 | 49.66 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1205.2 | 49.64 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1205.25 | 49.64 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1205.3 | 49.69 | 49.53 | 1 | 1 | 10 | 49.69 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1205.35 | 49.69 | 49.53 | 1 | 1 | 10 | 49.69 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1205.4 | 49.74 | 49.53 | 1 | 1 | 10 | 49.74 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1205.45 | 49.74 | 49.54 | 1 | 1 | 10 | 49.74 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1205.5 | 49.78 | 49.54 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1205.55 | 49.78 | 49.61 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1205.6 | 49.82 | 49.61 | 1 | 1 | 10 | 49.82 | 0.81 | 0.81 | 8.1 | 9.05 | 9.05 | 0 | 12 | 1 | 1 | 9.05 | 10 | 0 | 0
1205.65 | 49.82 | 49.64 | 1 | 1 | 10 | 49.82 | 0.81 | 0.81 | 8.1 | 9.05 | 9.05 | 0 | 12 | 1 | 1 | 9.05 | 10 | 0 | 0
1205.7 | 49.86 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
1205.75 | 49.86 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
1205.8 | 49.84 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
1205.85 | 49.84 | 49.69 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
1205.9 | 49.91 | 49.69 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1205.95 | 49.91 | 49.74 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1206 | 49.97 | 49.74 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1206.05 | 49.97 | 49.78 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1206.1 | 50.03 | 49.78 | 1 | 1 | 10 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.9559 | 4.9559 | 0 | 12 | 1 | 1 | 4.9559 | 10 | 0 | 0
1206.15 | 50.03 | 49.82 | 0.81 | 0.9 | 9 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.4559 | 4.4559 | 0 | 12 | 1 | 1 | 4.4559 | 10 | 0 | 0
1206.2 | 50.05 | 49.82 | 0.81 | 0.81 | 8.1 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 3.9471 | 3.9471 | 0 | 12 | 1 | 1 | 3.9471 | 10 | 0 | 0
1206.25 | 50.05 | 49.84 | 0.62 | 0.71 | 7.1 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 3.4471 | 3.4471 | 0 | 12 | 1 | 1 | 3.4471 | 10 | 0 | 0
1206.3 | 50.01 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
1206.35 | 50.01 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
1206.4 | 49.95 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
1206.45 | 49.95 | 49.91 | 0.044118 | 0.52 | 5.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.4971 | 2.4971 | 0 | 12 | 1 | 1 | 2.4971 | 10 | 0 | 0
1206.5 | 49.99 | 49.91 | 0.044118 | 0.42 | 4.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 1.9971 | 1.9971 | 0 | 12 | 1 | 1 | 1.9971 | 10 | 0 | 0
1206.55 | 49.99 | 49.95 | 0.020588 | 0.32 | 3.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 1.4971 | 1.4971 | 0 | 12 | 1 | 1 | 1.4971 | 10 | 0 | 0
1206.6 | 49.92 | 49.92 | 0.038235 | 0.22 | 2.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.99706 | 0.99706 | 0 | 12 | 1 | 1 | 0.99706 | 10 | 0 | 0
1206.65 | 49.92 | 49.92 | 0.038235 | 0.12 | 1.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.49706 | 0.49706 | 0 | 12 | 1 | 1 | 0.49706 | 10 | 0 | 0
1206.7 | 49.97 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1206.75 | 49.97 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1206.8 | 50.02 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1206.85 | 50.02 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.17647 | 0.17647 | 0 | 12 | 1 | 1 | 0.17647 | 10 | 0 | 0
1206.9 | 50.07 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1206.95 | 50.07 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1207 | 50.06 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1207.05 | 50.06 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1207.1 | 50.13 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
1207.15 | 50.13 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
1207.2 | 50.09 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
1207.25 | 50.09 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6309 | -1.6309 | 0 | 12 | 1 | 1 | -1.6309 | 10 | 0 | 0
1207.3 | 50.07 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6309 | -1.6309 | 0 | 12 | 1 | 1 | -1.6309 | 10 | 0 | 0
1207.35 | 50.07 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6897 | -1.6897 | 0 | 12 | 1 | 1 | -1.6897 | 10 | 0 | 0
1207.4 | 50.07 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6897 | -1.6897 | 0 | 12 | 1 | 1 | -1.6897 | 10 | 0 | 0
1207.45 | 50.07 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.13 | -0.335 | -0.335 | -3.35 | -1.8074 | -1.8074 | 0 | 12 | 1 | 1 | -1.8074 | 10 | 0 | 0
1207.5 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.13 | -0.335 | -0.335 | -3.35 | -1.7779 | -1.7779 | 0 | 12 | 1 | 1 | -1.7779 | 10 | 0 | 0
1207.55 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.13 | -0.335 | -0.335 | -3.35 | -1.7779 | -1.7779 | 0 | 12 | 1 | 1 | -1.7779 | 10 | 0 | 0
1207.6 | 50.01 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
1207.65 | 50.01 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
1207.7 | 50.07 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
1207.75 | 50.07 | 50.01 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.235 | -2.35 | -1.175 | -1.175 | 0 | 12 | 1 | 1 | -1.175 | 10 | 0 | 0
1207.8 | 50.05 | 50.01 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.135 | -1.35 | -0.675 | -0.675 | 0 | 12 | 1 | 1 | -0.675 | 10 | 0 | 0
1207.85 | 50.05 | 50.01 | 0 | 0 | 0 | 50.07 | -0.032353 | -0.035 | -0.35 | -0.175 | -0.175 | 0 | 12 | 1 | 1 | -0.175 | 10 | 0 | 0
1207.9 | 50.1 | 50.01 | 0 | 0 | 0 | 50.1 | -0.05 | -0.05 | -0.5 | -0.25 | -0.25 | 0 | 12 | 1 | 1 | -0.25 | 10 | 0 | 0
1207.95 | 50.1 | 50.01 | 0 | 0 | 0 | 50.1 | -0.05 | -0.05 | -0.5 | -0.25 | -0.25 | 0 | 12 | 1 | 1 | -0.25 | 10 | 0 | 0
1208 | 50.11 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1208.05 | 50.11 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1208.1 | 50.06 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1208.15 | 50.06 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1208.2 | 50.04 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1208.25 | 50.04 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1208.3 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1208.35 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1208.4 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1208.45 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1208.5 | 50.11 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1208.55 | 50.11 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1208.6 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1208.65 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1208.7 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1208.75 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1208.8 | 50.02 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.11 | -0.145 | -0.145 | -1.45 | -0.73971 | -0.73971 | 0 | 12 | 1 | 1 | -0.73971 | 10 | 0 | 0
1208.85 | 50.02 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.11 | -0.145 | -0.145 | -1.45 | -0.73971 | -0.73971 | 0 | 12 | 1 | 1 | -0.73971 | 10 | 0 | 0
1208.9 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1208.95 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1209 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1209.05 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1209.1 | 50.01 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1209.15 | 50.01 | 50 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.045 | -0.45 | -0.225 | -0.225 | 0 | 12 | 1 | 1 | -0.225 | 10 | 0 | 0
1209.2 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
1209.25 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
1209.3 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
1209.35 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1209.4 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.14706 | 0.14706 | 0 | 12 | 1 | 1 | 0.14706 | 10 | 0 | 0
1209.45 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1209.5 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1209.55 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1209.6 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1209.65 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1209.7 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1209.75 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1209.8 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1209.85 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1209.9 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1209.95 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1210 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1210.05 | 50 | 50 | 0 | 0 | 0 | 50.01 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1210.1 | 49.5 | 49.5 | 1 | 1 | 10 | 50.01 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1210.15 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1210.2 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1210.25 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1210.3 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1210.35 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1210.4 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1210.45 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1210.5 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1210.55 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1210.6 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1210.65 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.1 | 1 | 5.5 | 5.5 | 0 | 12 | 1 | 1 | 5.5 | 10 | 0 | 0
1210.7 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.2 | 2 | 6 | 6 | 0 | 12 | 1 | 1 | 6 | 10 | 0 | 0
1210.75 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.3 | 3 | 6.5 | 6.5 | 0 | 12 | 1 | 1 | 6.5 | 10 | 0 | 0
1210.8 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.4 | 4 | 7 | 7 | 0 | 12 | 1 | 1 | 7 | 10 | 0 | 0
1210.85 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.5 | 5 | 7.5 | 7.5 | 0 | 12 | 1 | 1 | 7.5 | 10 | 0 | 0
1210.9 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.6 | 6 | 8 | 8 | 0 | 12 | 1 | 1 | 8 | 10 | 0 | 0
1210.95 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.7 | 7 | 8.5 | 8.5 | 0 | 12 | 1 | 1 | 8.5 | 10 | 0 | 0
1211 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.8 | 8 | 9 | 9 | 0 | 12 | 1 | 1 | 9 | 10 | 0 | 0
1211.05 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.9 | 9 | 9.5 | 9.5 | 0 | 12 | 1 | 1 | 9.5 | 10 | 0 | 0
1211.1 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1211.15 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1211.2 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1211.25 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1211.3 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1211.35 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1211.4 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1211.45 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1211.5 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1211.55 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1211.6 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1211.65 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1211.7 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1211.75 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1211.8 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1211.85 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1211.9 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1211.95 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1212 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1212.05 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1212.1 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1212.15 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1212.2 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1212.25 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1212.3 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1212.35 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1212.4 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1212.45 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1212.5 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1212.55 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1212.6 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1212.65 | 50.5 | 50.5 | -1 | 0.9 | 9 | 50.5 | -1 | -1 | -10 | -0.5 | -0.5 | 0 | 12 | 1 | 1 | -0.5 | 10 | 0 | 0
1212.7 | 50.5 | 50.5 | -1 | 0.8 | 8 | 50.5 | -1 | -1 | -10 | -1 | -1 | 0 | 12 | 1 | 1 | -1 | 10 | 0 | 0
1212.75 | 50.5 | 50.5 | -1 | 0.7 | 7 | 50.5 | -1 | -1 | -10 | -1.5 | -1.5 | 0 | 12 | 1 | 1 | -1.5 | 10 | 0 | 0
1212.8 | 50.5 | 50.5 | -1 | 0.6 | 6 | 50.5 | -1 | -1 | -10 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
1212.85 | 50.5 | 50.5 | -1 | 0.5 | 5 | 50.5 | -1 | -1 | -10 | -2.5 | -2.5 | 0 | 12 | 1 | 1 | -2.5 | 10 | 0 | 0
1212.9 | 50.5 | 50.5 | -1 | 0.4 | 4 | 50.5 | -1 | -1 | -10 | -3 | -3 | 0 | 12 | 1 | 1 | -3 | 10 | 0 | 0
1212.95 | 50.5 | 50.5 | -1 | 0.3 | 3 | 50.5 | -1 | -1 | -10 | -3.5 | -3.5 | 0 | 12 | 1 | 1 | -3.5 | 10 | 0 | 0
1213 | 50.5 | 50.5 | -1 | 0.2 | 2 | 50.5 | -1 | -1 | -10 | -4 | -4 | 0 | 12 | 1 | 1 | -4 | 10 | 0 | 0
1213.05 | 50.5 | 50.5 | -1 | 0.1 | 1 | 50.5 | -1 | -1 | -10 | -4.5 | -4.5 | 0 | 12 | 1 | 1 | -4.5 | 10 | 0 | 0
1213.1 | 50.5 | 50.5 | -1 | 0 | 0 | 50.5 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1213.15 | 50.5 | 50.5 | -1 | -0.1 | -1 | 50.5 | -1 | -1 | -10 | -5.5 | -5.5 | 0 | 12 | 1 | 1 | -5.5 | 10 | 0 | 0
1213.2 | 50.5 | 50.5 | -1 | -0.2 | -2 | 50.5 | -1 | -1 | -10 | -6 | -6 | 0 | 12 | 1 | 1 | -6 | 10 | 0 | 0
1213.25 | 50.5 | 50.5 | -1 | -0.3 | -3 | 50.5 | -1 | -1 | -10 | -6.5 | -6.5 | 0 | 12 | 1 | 1 | -6.5 | 10 | 0 | 0
1213.3 | 50.5 | 50.5 | -1 | -0.4 | -4 | 50.5 | -1 | -1 | -10 | -7 | -7 | 0 | 12 | 1 | 1 | -7 | 10 | 0 | 0
1213.35 | 50.5 | 50.5 | -1 | -0.5 | -5 | 50.5 | -1 | -1 | -10 | -7.5 | -7.5 | 0 | 12 | 1 | 1 | -7.5 | 10 | 0 | 0
1213.4 | 50.5 | 50.5 | -1 | -0.6 | -6 | 50.5 | -1 | -1 | -10 | -8 | -8 | 0 | 12 | 1 | 1 | -8 | 10 | 0 | 0
1213.45 | 50.5 | 50.5 | -1 | -0.7 | -7 | 50.5 | -1 | -1 | -10 | -8.5 | -8.5 | 0 | 12 | 1 | 1 | -8.5 | 10 | 0 | 0
1213.5 | 50.5 | 50.5 | -1 | -0.8 | -8 | 50.5 | -1 | -1 | -10 | -9 | -9 | 0 | 12 | 1 | 1 | -9 | 10 | 0 | 0
1213.55 | 50.5 | 50.5 | -1 | -0.9 | -9 | 50.5 | -1 | -1 | -10 | -9.5 | -9.5 | 0 | 12 | 1 | 1 | -9.5 | 10 | 0 | 0
1213.6 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1213.65 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1213.7 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1213.75 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1213.8 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1213.85 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1213.9 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1213.95 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1214 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1214.05 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1214.1 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1214.15 | 50.47 | 50.47 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1214.2 | 50.45 | 50.45 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1214.25 | 50.42 | 50.42 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1214.3 | 50.4 | 50.4 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1214.35 | 50.37 | 50.37 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1214.4 | 50.35 | 50.35 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1214.45 | 50.32 | 50.32 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1214.5 | 50.29 | 50.29 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1214.55 | 50.27 | 50.27 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1214.6 | 50.24 | 50.24 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1214.65 | 50.22 | 50.22 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1214.7 | 50.19 | 50.19 | -0.905 | -0.905 | -9.05 | 50.47 | -1 | -1 | -10 | -9.525 | -9.525 | 0 | 12 | 1 | 1 | -9.525 | 10 | 0 | 0
1214.75 | 50.17 | 50.17 | -0.715 | -0.715 | -7.15 | 50.45 | -1 | -1 | -10 | -8.575 | -8.575 | 0 | 12 | 1 | 1 | -8.575 | 10 | 0 | 0
1214.8 | 50.14 | 50.14 | -0.43 | -0.43 | -4.3 | 50.42 | -1 | -1 | -10 | -7.15 | -7.15 | 0 | 12 | 1 | 1 | -7.15 | 10 | 0 | 0
1214.85 | 50.12 | 50.12 | -0.24 | -0.24 | -2.4 | 50.4 | -1 | -1 | -10 | -6.2 | -6.2 | 0 | 12 | 1 | 1 | -6.2 | 10 | 0 | 0
1214.9 | 50.09 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 50.37 | -1 | -1 | -10 | -5.2206 | -5.2206 | 0 | 12 | 1 | 1 | -5.2206 | 10 | 0 | 0
1214.95 | 50.06 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.35 | -1 | -1 | -10 | -5.1324 | -5.1324 | 0 | 12 | 1 | 1 | -5.1324 | 10 | 0 | 0
1215 | 50.04 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.32 | -1 | -1 | -10 | -5.0735 | -5.0735 | 0 | 12 | 1 | 1 | -5.0735 | 10 | 0 | 0
1215.05 | 50.01 | 50.01 | 0 | 0 | 0 | 50.29 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1215.1 | 49.99 | 49.99 | 0 | 0 | 0 | 50.27 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1215.15 | 49.96 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.24 | -1 | -1 | -10 | -4.9265 | -4.9265 | 0 | 12 | 1 | 1 | -4.9265 | 10 | 0 | 0
1215.2 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.22 | -1 | -1 | -10 | -4.8676 | -4.8676 | 0 | 12 | 1 | 1 | -4.8676 | 10 | 0 | 0
1215.25 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.19 | -0.905 | -0.905 | -9.05 | -4.3044 | -4.3044 | 0 | 12 | 1 | 1 | -4.3044 | 10 | 0 | 0
1215.3 | 49.88 | 49.88 | 0.24 | 0.24 | 2.4 | 50.17 | -0.715 | -0.805 | -8.05 | -2.825 | -2.825 | 0 | 12 | 1 | 1 | -2.825 | 10 | 0 | 0
1215.35 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.14 | -0.43 | -0.705 | -7.05 | -1.375 | -1.375 | 0 | 12 | 1 | 1 | -1.375 | 10 | 0 | 0
1215.4 | 49.83 | 49.83 | 0.715 | 0.715 | 7.15 | 50.12 | -0.24 | -0.605 | -6.05 | 0.55 | 0.55 | 0 | 12 | 1 | 1 | 0.55 | 10 | 0 | 0
1215.45 | 49.81 | 49.81 | 0.905 | 0.905 | 9.05 | 50.09 | -0.044118 | -0.505 | -5.05 | 2 | 2 | 0 | 12 | 1 | 1 | 2 | 10 | 0 | 0
1215.5 | 49.78 | 49.78 | 1 | 1 | 10 | 50.06 | -0.026471 | -0.405 | -4.05 | 2.975 | 2.975 | 0 | 12 | 1 | 1 | 2.975 | 10 | 0 | 0
1215.55 | 49.76 | 49.76 | 1 | 1 | 10 | 50.04 | -0.014706 | -0.305 | -3.05 | 3.475 | 3.475 | 0 | 12 | 1 | 1 | 3.475 | 10 | 0 | 0
1215.6 | 49.73 | 49.73 | 1 | 1 | 10 | 50.01 | 0 | -0.205 | -2.05 | 3.975 | 3.975 | 0 | 12 | 1 | 1 | 3.975 | 10 | 0 | 0
1215.65 | 49.71 | 49.71 | 1 | 1 | 10 | 49.99 | 0 | -0.105 | -1.05 | 4.475 | 4.475 | 0 | 12 | 1 | 1 | 4.475 | 10 | 0 | 0
1215.7 | 49.68 | 49.68 | 1 | 1 | 10 | 49.96 | 0.014706 | -0.005 | -0.05 | 4.975 | 4.975 | 0 | 12 | 1 | 1 | 4.975 | 10 | 0 | 0
1215.75 | 49.65 | 49.65 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
1215.8 | 49.63 | 49.63 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1215.85 | 49.6 | 49.6 | 1 | 1 | 10 | 49.88 | 0.24 | 0.14412 | 1.4412 | 5.7206 | 5.7206 | 0 | 12 | 1 | 1 | 5.7206 | 10 | 0 | 0
1215.9 | 49.58 | 49.58 | 1 | 1 | 10 | 49.86 | 0.43 | 0.24412 | 2.4412 | 6.2206 | 6.2206 | 0 | 12 | 1 | 1 | 6.2206 | 10 | 0 | 0
1215.95 | 49.55 | 49.55 | 1 | 1 | 10 | 49.83 | 0.715 | 0.34412 | 3.4412 | 6.7206 | 6.7206 | 0 | 12 | 1 | 1 | 6.7206 | 10 | 0 | 0
1216 | 49.53 | 49.53 | 1 | 1 | 10 | 49.81 | 0.905 | 0.44412 | 4.4412 | 7.2206 | 7.2206 | 0 | 12 | 1 | 1 | 7.2206 | 10 | 0 | 0
1216.05 | 49.5 | 49.5 | 1 | 1 | 10 | 49.78 | 1 | 0.54412 | 5.4412 | 7.7206 | 7.7206 | 0 | 12 | 1 | 1 | 7.7206 | 10 | 0 | 0
1216.1 | 49.5 | 49.5 | 1 | 1 | 10 | 49.76 | 1 | 0.64412 | 6.4412 | 8.2206 | 8.2206 | 0 | 12 | 1 | 1 | 8.2206 | 10 | 0 | 0
1216.15 | 49.53 | 49.5 | 1 | 1 | 10 | 49.73 | 1 | 0.74412 | 7.4412 | 8.7206 | 8.7206 | 0 | 12 | 1 | 1 | 8.7206 | 10 | 0 | 0
1216.2 | 49.55 | 49.5 | 1 | 1 | 10 | 49.71 | 1 | 0.84412 | 8.4412 | 9.2206 | 9.2206 | 0 | 12 | 1 | 1 | 9.2206 | 10 | 0 | 0
1216.25 | 49.58 | 49.5 | 1 | 1 | 10 | 49.68 | 1 | 0.94412 | 9.4412 | 9.7206 | 9.7206 | 0 | 12 | 1 | 1 | 9.7206 | 10 | 0 | 0
1216.3 | 49.6 | 49.5 | 1 | 1 | 10 | 49.65 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1216.35 | 49.63 | 49.5 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1216.4 | 49.65 | 49.5 | 1 | 1 | 10 | 49.65 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1216.45 | 49.68 | 49.5 | 1 | 1 | 10 | 49.68 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1216.5 | 49.71 | 49.5 | 1 | 1 | 10 | 49.71 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1216.55 | 49.73 | 49.5 | 1 | 1 | 10 | 49.73 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1216.6 | 49.76 | 49.5 | 1 | 1 | 10 | 49.76 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1216.65 | 49.78 | 49.5 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1216.7 | 49.81 | 49.53 | 1 | 1 | 10 | 49.81 | 0.905 | 0.905 | 9.05 | 9.525 | 9.525 | 0 | 12 | 1 | 1 | 9.525 | 10 | 0 | 0
1216.75 | 49.83 | 49.55 | 1 | 1 | 10 | 49.83 | 0.715 | 0.715 | 7.15 | 8.575 | 8.575 | 0 | 12 | 1 | 1 | 8.575 | 10 | 0 | 0
1216.8 | 49.86 | 49.58 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
1216.85 | 49.88 | 49.6 | 1 | 1 | 10 | 49.88 | 0.24 | 0.24 | 2.4 | 6.2 | 6.2 | 0 | 12 | 1 | 1 | 6.2 | 10 | 0 | 0
1216.9 | 49.91 | 49.63 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1216.95 | 49.94 | 49.65 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
1217 | 49.96 | 49.68 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
1217.05 | 49.99 | 49.71 | 1 | 1 | 10 | 49.99 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1217.1 | 50.01 | 49.73 | 1 | 1 | 10 | 50.01 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1217.15 | 50.04 | 49.76 | 1 | 1 | 10 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 4.9265 | 4.9265 | 0 | 12 | 1 | 1 | 4.9265 | 10 | 0 | 0
1217.2 | 50.06 | 49.78 | 1 | 1 | 10 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 4.8676 | 4.8676 | 0 | 12 | 1 | 1 | 4.8676 | 10 | 0 | 0
1217.25 | 50.09 | 49.81 | 0.905 | 0.905 | 9.05 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 4.3044 | 4.3044 | 0 | 12 | 1 | 1 | 4.3044 | 10 | 0 | 0
1217.3 | 50.12 | 49.83 | 0.715 | 0.805 | 8.05 | 50.12 | -0.24 | -0.24 | -2.4 | 2.825 | 2.825 | 0 | 12 | 1 | 1 | 2.825 | 10 | 0 | 0
1217.35 | 50.14 | 49.86 | 0.43 | 0.705 | 7.05 | 50.14 | -0.43 | -0.43 | -4.3 | 1.375 | 1.375 | 0 | 12 | 1 | 1 | 1.375 | 10 | 0 | 0
1217.4 | 50.17 | 49.88 | 0.24 | 0.605 | 6.05 | 50.17 | -0.715 | -0.715 | -7.15 | -0.55 | -0.55 | 0 | 12 | 1 | 1 | -0.55 | 10 | 0 | 0
1217.45 | 50.19 | 49.91 | 0.044118 | 0.505 | 5.05 | 50.19 | -0.905 | -0.905 | -9.05 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
1217.5 | 50.22 | 49.94 | 0.026471 | 0.405 | 4.05 | 50.22 | -1 | -1 | -10 | -2.975 | -2.975 | 0 | 12 | 1 | 1 | -2.975 | 10 | 0 | 0
1217.55 | 50.24 | 49.96 | 0.014706 | 0.305 | 3.05 | 50.24 | -1 | -1 | -10 | -3.475 | -3.475 | 0 | 12 | 1 | 1 | -3.475 | 10 | 0 | 0
1217.6 | 50.27 | 49.99 | 0 | 0.205 | 2.05 | 50.27 | -1 | -1 | -10 | -3.975 | -3.975 | 0 | 12 | 1 | 1 | -3.975 | 10 | 0 | 0
1217.65 | 50.29 | 50.01 | 0 | 0.105 | 1.05 | 50.29 | -1 | -1 | -10 | -4.475 | -4.475 | 0 | 12 | 1 | 1 | -4.475 | 10 | 0 | 0
1217.7 | 50.32 | 50.04 | -0.014706 | 0.005 | 0.05 | 50.32 | -1 | -1 | -10 | -4.975 | -4.975 | 0 | 12 | 1 | 1 | -4.975 | 10 | 0 | 0
1217.75 | 50.35 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.35 | -1 | -1 | -10 | -5.1324 | -5.1324 | 0 | 12 | 1 | 1 | -5.1324 | 10 | 0 | 0
1217.8 | 50.37 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 50.37 | -1 | -1 | -10 | -5.2206 | -5.2206 | 0 | 12 | 1 | 1 | -5.2206 | 10 | 0 | 0
1217.85 | 50.4 | 50.12 | -0.24 | -0.14412 | -1.4412 | 50.4 | -1 | -1 | -10 | -5.7206 | -5.7206 | 0 | 12 | 1 | 1 | -5.7206 | 10 | 0 | 0
1217.9 | 50.42 | 50.14 | -0.43 | -0.24412 | -2.4412 | 50.42 | -1 | -1 | -10 | -6.2206 | -6.2206 | 0 | 12 | 1 | 1 | -6.2206 | 10 | 0 | 0
1217.95 | 50.45 | 50.17 | -0.715 | -0.34412 | -3.4412 | 50.45 | -1 | -1 | -10 | -6.7206 | -6.7206 | 0 | 12 | 1 | 1 | -6.7206 | 10 | 0 | 0
1218 | 50.47 | 50.19 | -0.905 | -0.44412 | -4.4412 | 50.47 | -1 | -1 | -10 | -7.2206 | -7.2206 | 0 | 12 | 1 | 1 | -7.2206 | 10 | 0 | 0
1218.05 | 50.5 | 50.22 | -1 | -0.54412 | -5.4412 | 50.5 | -1 | -1 | -10 | -7.7206 | -7.7206 | 0 | 12 | 1 | 1 | -7.7206 | 10 | 0 | 0
1218.1 | 50.5 | 50.24 | -1 | -0.64412 | -6.4412 | 50.5 | -1 | -1 | -10 | -8.2206 | -8.2206 | 0 | 12 | 1 | 1 | -8.2206 | 10 | 0 | 0
1218.15 | 50.47 | 50.27 | -1 | -0.74412 | -7.4412 | 50.5 | -1 | -1 | -10 | -8.7206 | -8.7206 | 0 | 12 | 1 | 1 | -8.7206 | 10 | 0 | 0
1218.2 | 50.45 | 50.29 | -1 | -0.84412 | -8.4412 | 50.5 | -1 | -1 | -10 | -9.2206 | -9.2206 | 0 | 12 | 1 | 1 | -9.2206 | 10 | 0 | 0
1218.25 | 50.42 | 50.32 | -1 | -0.94412 | -9.4412 | 50.5 | -1 | -1 | -10 | -9.7206 | -9.7206 | 0 | 12 | 1 | 1 | -9.7206 | 10 | 0 | 0
1218.3 | 50.39 | 50.35 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1218.35 | 50.37 | 50.37 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1218.4 | 50.34 | 50.34 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1218.45 | 50.32 | 50.32 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1218.5 | 50.29 | 50.29 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1218.55 | 50.26 | 50.26 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1218.6 | 50.24 | 50.24 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1218.65 | 50.21 | 50.21 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1218.7 | 50.18 | 50.18 | -0.81 | -0.81 | -8.1 | 50.47 | -1 | -1 | -10 | -9.05 | -9.05 | 0 | 12 | 1 | 1 | -9.05 | 10 | 0 | 0
1218.75 | 50.16 | 50.16 | -0.62 | -0.62 | -6.2 | 50.45 | -1 | -1 | -10 | -8.1 | -8.1 | 0 | 12 | 1 | 1 | -8.1 | 10 | 0 | 0
1218.8 | 50.13 | 50.13 | -0.335 | -0.335 | -3.35 | 50.42 | -1 | -1 | -10 | -6.675 | -6.675 | 0 | 12 | 1 | 1 | -6.675 | 10 | 0 | 0
1218.85 | 50.11 | 50.11 | -0.145 | -0.145 | -1.45 | 50.39 | -1 | -1 | -10 | -5.725 | -5.725 | 0 | 12 | 1 | 1 | -5.725 | 10 | 0 | 0
1218.9 | 50.08 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 50.37 | -1 | -1 | -10 | -5.1912 | -5.1912 | 0 | 12 | 1 | 1 | -5.1912 | 10 | 0 | 0
1218.95 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.34 | -1 | -1 | -10 | -5.1029 | -5.1029 | 0 | 12 | 1 | 1 | -5.1029 | 10 | 0 | 0
1219 | 50.03 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 50.32 | -1 | -1 | -10 | -5.0441 | -5.0441 | 0 | 12 | 1 | 1 | -5.0441 | 10 | 0 | 0
1219.05 | 50 | 50 | 0 | 0 | 0 | 50.29 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1219.1 | 50 | 50 | 0 | 0 | 0 | 50.26 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1219.15 | 50 | 50 | 0 | 0 | 0 | 50.24 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1219.2 | 50 | 50 | 0 | 0 | 0 | 50.21 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1219.25 | 50 | 50 | 0 | 0 | 0 | 50.18 | -0.81 | -0.9 | -9 | -4.5 | -4.5 | 0 | 12 | 1 | 1 | -4.5 | 10 | 0 | 0
1219.3 | 50 | 50 | 0 | 0 | 0 | 50.16 | -0.62 | -0.8 | -8 | -4 | -4 | 0 | 12 | 1 | 1 | -4 | 10 | 0 | 0
1219.35 | 50 | 50 | 0 | 0 | 0 | 50.13 | -0.335 | -0.7 | -7 | -3.5 | -3.5 | 0 | 12 | 1 | 1 | -3.5 | 10 | 0 | 0
1219.4 | 50.01 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.6 | -6 | -3 | -3 | 0 | 12 | 1 | 1 | -3 | 10 | 0 | 0
1219.45 | 50.01 | 50 | 0 | 0 | 0 | 50.08 | -0.038235 | -0.5 | -5 | -2.5 | -2.5 | 0 | 12 | 1 | 1 | -2.5 | 10 | 0 | 0
1219.5 | 49.99 | 49.99 | 0 | 0 | 0 | 50.05 | -0.020588 | -0.4 | -4 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
1219.55 | 49.99 | 49.99 | 0 | 0 | 0 | 50.03 | -0.0088235 | -0.3 | -3 | -1.5 | -1.5 | 0 | 12 | 1 | 1 | -1.5 | 10 | 0 | 0
1219.6 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | -0.2 | -2 | -0.83824 | -0.83824 | 0 | 12 | 1 | 1 | -0.83824 | 10 | 0 | 0
1219.65 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | -0.1 | -1 | -0.33824 | -0.33824 | 0 | 12 | 1 | 1 | -0.33824 | 10 | 0 | 0
1219.7 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
1219.75 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
1219.8 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
1219.85 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
1219.9 | 49.89 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
1219.95 | 49.89 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
1220 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50.01 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1220.05 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1220.1 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1220.15 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 2.7868 | 2.7868 | 0 | 12 | 1 | 1 | 2.7868 | 10 | 0 | 0
1220.2 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 2.7868 | 2.7868 | 0 | 12 | 1 | 1 | 2.7868 | 10 | 0 | 0
1220.25 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 2.8456 | 2.8456 | 0 | 12 | 1 | 1 | 2.8456 | 10 | 0 | 0
1220.3 | 49.94 | 49.85 | 0.525 | 0.525 | 5.25 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 2.7574 | 2.7574 | 0 | 12 | 1 | 1 | 2.7574 | 10 | 0 | 0
1220.35 | 49.94 | 49.85 | 0.525 | 0.525 | 5.25 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 2.7574 | 2.7574 | 0 | 12 | 1 | 1 | 2.7574 | 10 | 0 | 0
1220.4 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1220.45 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1220.5 | 49.93 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1220.55 | 49.93 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1220.6 | 49.96 | 49.85 | 0.525 | 0.525 | 5.25 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 2.6985 | 2.6985 | 0 | 12 | 1 | 1 | 2.6985 | 10 | 0 | 0
1220.65 | 49.96 | 49.85 | 0.525 | 0.525 | 5.25 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 2.6985 | 2.6985 | 0 | 12 | 1 | 1 | 2.6985 | 10 | 0 | 0
1220.7 | 49.99 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1220.75 | 49.99 | 49.91 | 0.044118 | 0.425 | 4.25 | 49.99 | 0 | 0 | 0 | 2.125 | 2.125 | 0 | 12 | 1 | 1 | 2.125 | 10 | 0 | 0
1220.8 | 49.99 | 49.91 | 0.044118 | 0.325 | 3.25 | 49.99 | 0 | 0 | 0 | 1.625 | 1.625 | 0 | 12 | 1 | 1 | 1.625 | 10 | 0 | 0
1220.85 | 49.99 | 49.93 | 0.032353 | 0.225 | 2.25 | 49.99 | 0 | 0 | 0 | 1.125 | 1.125 | 0 | 12 | 1 | 1 | 1.125 | 10 | 0 | 0
1220.9 | 49.96 | 49.93 | 0.032353 | 0.125 | 1.25 | 49.99 | 0 | 0 | 0 | 0.625 | 0.625 | 0 | 12 | 1 | 1 | 0.625 | 10 | 0 | 0
1220.95 | 49.96 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 49.99 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1221 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1221.05 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1221.1 | 50.05 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.058824 | 0.058824 | 0 | 12 | 1 | 1 | 0.058824 | 10 | 0 | 0
1221.15 | 50.05 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
1221.2 | 49.97 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
1221.25 | 49.97 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
1221.3 | 49.92 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1221.35 | 49.92 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1221.4 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1221.45 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1221.5 | 49.94 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1221.55 | 49.94 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1221.6 | 50.01 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1221.65 | 50.01 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1221.7 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1221.75 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
1221.8 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
1221.85 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
1221.9 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
1221.95 | 49.95 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
1222 | 49.97 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
1222.05 | 49.97 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
1222.1 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
1222.15 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
1222.2 | 49.87 | 49.87 | 0.335 | 0.335 | 3.35 | 50.01 | 0 | 0 | 0 | 1.675 | 1.675 | 0 | 12 | 1 | 1 | 1.675 | 10 | 0 | 0
1222.25 | 49.87 | 49.87 | 0.335 | 0.335 | 3.35 | 49.99 | 0 | 0 | 0 | 1.675 | 1.675 | 0 | 12 | 1 | 1 | 1.675 | 10 | 0 | 0
1222.3 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1222.35 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 2.6691 | 2.6691 | 0 | 12 | 1 | 1 | 2.6691 | 10 | 0 | 0
1222.4 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1222.45 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1222.5 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1222.55 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1222.6 | 49.84 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1222.65 | 49.84 | 49.79 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
1222.7 | 49.89 | 49.79 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
1222.75 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.12647 | 1.2647 | 5.6324 | 5.6324 | 0 | 12 | 1 | 1 | 5.6324 | 10 | 0 | 0
1222.8 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.145 | 1.45 | 5.725 | 5.725 | 0 | 12 | 1 | 1 | 5.725 | 10 | 0 | 0
1222.85 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.145 | 1.45 | 5.725 | 5.725 | 0 | 12 | 1 | 1 | 5.725 | 10 | 0 | 0
1222.9 | 49.96 | 49.79 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
1222.95 | 49.96 | 49.79 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
1223 | 50.02 | 49.79 | 1 | 1 | 10 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 4.9853 | 4.9853 | 0 | 12 | 1 | 1 | 4.9853 | 10 | 0 | 0
1223.05 | 50.02 | 49.79 | 1 | 1 | 10 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 4.9853 | 4.9853 | 0 | 12 | 1 | 1 | 4.9853 | 10 | 0 | 0
1223.1 | 50.03 | 49.79 | 1 | 1 | 10 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.9559 | 4.9559 | 0 | 12 | 1 | 1 | 4.9559 | 10 | 0 | 0
1223.15 | 50.03 | 49.84 | 0.62 | 0.9 | 9 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.4559 | 4.4559 | 0 | 12 | 1 | 1 | 4.4559 | 10 | 0 | 0
1223.2 | 50.02 | 49.84 | 0.62 | 0.8 | 8 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 3.9559 | 3.9559 | 0 | 12 | 1 | 1 | 3.9559 | 10 | 0 | 0
1223.25 | 50.02 | 49.89 | 0.145 | 0.7 | 7 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 3.4559 | 3.4559 | 0 | 12 | 1 | 1 | 3.4559 | 10 | 0 | 0
1223.3 | 50.08 | 49.89 | 0.145 | 0.6 | 6 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 2.8088 | 2.8088 | 0 | 12 | 1 | 1 | 2.8088 | 10 | 0 | 0
1223.35 | 50.08 | 49.89 | 0.145 | 0.5 | 5 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 2.3088 | 2.3088 | 0 | 12 | 1 | 1 | 2.3088 | 10 | 0 | 0
1223.4 | 50.01 | 49.89 | 0.145 | 0.4 | 4 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 1.8088 | 1.8088 | 0 | 12 | 1 | 1 | 1.8088 | 10 | 0 | 0
1223.45 | 50.01 | 49.96 | 0.014706 | 0.3 | 3 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 1.3088 | 1.3088 | 0 | 12 | 1 | 1 | 1.3088 | 10 | 0 | 0
1223.5 | 49.94 | 49.94 | 0.026471 | 0.2 | 2 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.80882 | 0.80882 | 0 | 12 | 1 | 1 | 0.80882 | 10 | 0 | 0
1223.55 | 49.94 | 49.94 | 0.026471 | 0.1 | 1 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.30882 | 0.30882 | 0 | 12 | 1 | 1 | 0.30882 | 10 | 0 | 0
1223.6 | 50 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
1223.65 | 50 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
1223.7 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
1223.75 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
1223.8 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1223.85 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1223.9 | 49.92 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1223.95 | 49.92 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
1224 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50.01 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1224.05 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1224.1 | 49.92 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1224.15 | 49.92 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1224.2 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1224.25 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1224.3 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1224.35 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1224.4 | 49.87 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1224.45 | 49.87 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1224.5 | 49.8 | 49.8 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1224.55 | 49.8 | 49.8 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1224.6 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1224.65 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1224.7 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1224.75 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1224.8 | 49.72 | 49.72 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1224.85 | 49.72 | 49.72 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1224.9 | 49.67 | 49.67 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1224.95 | 49.67 | 49.67 | 1 | 1 | 10 | 49.87 | 0.335 | 0.14412 | 1.4412 | 5.7206 | 5.7206 | 0 | 12 | 1 | 1 | 5.7206 | 10 | 0 | 0
1225 | 49.65 | 49.65 | 1 | 1 | 10 | 49.87 | 0.335 | 0.24412 | 2.4412 | 6.2206 | 6.2206 | 0 | 12 | 1 | 1 | 6.2206 | 10 | 0 | 0
1225.05 | 49.65 | 49.65 | 1 | 1 | 10 | 49.8 | 1 | 0.34412 | 3.4412 | 6.7206 | 6.7206 | 0 | 12 | 1 | 1 | 6.7206 | 10 | 0 | 0
1225.1 | 49.59 | 49.59 | 1 | 1 | 10 | 49.8 | 1 | 0.44412 | 4.4412 | 7.2206 | 7.2206 | 0 | 12 | 1 | 1 | 7.2206 | 10 | 0 | 0
1225.15 | 49.59 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.54412 | 5.4412 | 7.7206 | 7.7206 | 0 | 12 | 1 | 1 | 7.7206 | 10 | 0 | 0
1225.2 | 49.66 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.64412 | 6.4412 | 8.2206 | 8.2206 | 0 | 12 | 1 | 1 | 8.2206 | 10 | 0 | 0
1225.25 | 49.66 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.74412 | 7.4412 | 8.7206 | 8.7206 | 0 | 12 | 1 | 1 | 8.7206 | 10 | 0 | 0
1225.3 | 49.63 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.84412 | 8.4412 | 9.2206 | 9.2206 | 0 | 12 | 1 | 1 | 9.2206 | 10 | 0 | 0
1225.35 | 49.63 | 49.59 | 1 | 1 | 10 | 49.72 | 1 | 0.94412 | 9.4412 | 9.7206 | 9.7206 | 0 | 12 | 1 | 1 | 9.7206 | 10 | 0 | 0
1225.4 | 49.61 | 49.59 | 1 | 1 | 10 | 49.72 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1225.45 | 49.61 | 49.59 | 1 | 1 | 10 | 49.67 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1225.5 | 49.54 | 49.54 | 1 | 1 | 10 | 49.67 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1225.55 | 49.54 | 49.54 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1225.6 | 49.46 | 49.46 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1225.65 | 49.46 | 49.46 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1225.7 | 49.45 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1225.75 | 49.45 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1225.8 | 49.51 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1225.85 | 49.51 | 49.45 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1225.9 | 49.5 | 49.45 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1225.95 | 49.5 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1226 | 49.54 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1226.05 | 49.54 | 49.45 | 1 | 1 | 10 | 49.54 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1226.1 | 49.59 | 49.45 | 1 | 1 | 10 | 49.59 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1226.15 | 49.59 | 49.45 | 1 | 1 | 10 | 49.59 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1226.2 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1226.25 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1226.3 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1226.35 | 49.61 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1226.4 | 49.53 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1226.45 | 49.53 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1226.5 | 49.54 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1226.55 | 49.54 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1226.6 | 49.61 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1226.65 | 49.61 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1226.7 | 49.66 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1226.75 | 49.66 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1226.8 | 49.64 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1226.85 | 49.64 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1226.9 | 49.69 | 49.53 | 1 | 1 | 10 | 49.69 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1226.95 | 49.69 | 49.53 | 1 | 1 | 10 | 49.69 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1227 | 49.74 | 49.53 | 1 | 1 | 10 | 49.74 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1227.05 | 49.74 | 49.54 | 1 | 1 | 10 | 49.74 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1227.1 | 49.78 | 49.54 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1227.15 | 49.78 | 49.61 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1227.2 | 49.82 | 49.61 | 1 | 1 | 10 | 49.82 | 0.81 | 0.81 | 8.1 | 9.05 | 9.05 | 0 | 12 | 1 | 1 | 9.05 | 10 | 0 | 0
1227.25 | 49.82 | 49.64 | 1 | 1 | 10 | 49.82 | 0.81 | 0.81 | 8.1 | 9.05 | 9.05 | 0 | 12 | 1 | 1 | 9.05 | 10 | 0 | 0
1227.3 | 49.86 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
1227.35 | 49.86 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
1227.4 | 49.84 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
1227.45 | 49.84 | 49.69 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
1227.5 | 49.91 | 49.69 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1227.55 | 49.91 | 49.74 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1227.6 | 49.97 | 49.74 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1227.65 | 49.97 | 49.78 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1227.7 | 50.03 | 49.78 | 1 | 1 | 10 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.9559 | 4.9559 | 0 | 12 | 1 | 1 | 4.9559 | 10 | 0 | 0
1227.75 | 50.03 | 49.82 | 0.81 | 0.9 | 9 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.4559 | 4.4559 | 0 | 12 | 1 | 1 | 4.4559 | 10 | 0 | 0
1227.8 | 50.05 | 49.82 | 0.81 | 0.81 | 8.1 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 3.9471 | 3.9471 | 0 | 12 | 1 | 1 | 3.9471 | 10 | 0 | 0
1227.85 | 50.05 | 49.84 | 0.62 | 0.71 | 7.1 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 3.4471 | 3.4471 | 0 | 12 | 1 | 1 | 3.4471 | 10 | 0 | 0
1227.9 | 50.01 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
1227.95 | 50.01 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
1228 | 49.95 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
1228.05 | 49.95 | 49.91 | 0.044118 | 0.52 | 5.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.4971 | 2.4971 | 0 | 12 | 1 | 1 | 2.4971 | 10 | 0 | 0
1228.1 | 49.99 | 49.91 | 0.044118 | 0.42 | 4.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 1.9971 | 1.9971 | 0 | 12 | 1 | 1 | 1.9971 | 10 | 0 | 0
1228.15 | 49.99 | 49.95 | 0.020588 | 0.32 | 3.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 1.4971 | 1.4971 | 0 | 12 | 1 | 1 | 1.4971 | 10 | 0 | 0
1228.2 | 49.92 | 49.92 | 0.038235 | 0.22 | 2.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.99706 | 0.99706 | 0 | 12 | 1 | 1 | 0.99706 | 10 | 0 | 0
1228.25 | 49.92 | 49.92 | 0.038235 | 0.12 | 1.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.49706 | 0.49706 | 0 | 12 | 1 | 1 | 0.49706 | 10 | 0 | 0
1228.3 | 49.97 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1228.35 | 49.97 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1228.4 | 50.02 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1228.45 | 50.02 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.17647 | 0.17647 | 0 | 12 | 1 | 1 | 0.17647 | 10 | 0 | 0
1228.5 | 50.07 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1228.55 | 50.07 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1228.6 | 50.06 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1228.65 | 50.06 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1228.7 | 50.13 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
1228.75 | 50.13 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
1228.8 | 50.09 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
1228.85 | 50.09 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6309 | -1.6309 | 0 | 12 | 1 | 1 | -1.6309 | 10 | 0 | 0
1228.9 | 50.07 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6309 | -1.6309 | 0 | 12 | 1 | 1 | -1.6309 | 10 | 0 | 0
1228.95 | 50.07 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6897 | -1.6897 | 0 | 12 | 1 | 1 | -1.6897 | 10 | 0 | 0
1229 | 50.07 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6897 | -1.6897 | 0 | 12 | 1 | 1 | -1.6897 | 10 | 0 | 0
1229.05 | 50.07 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.13 | -0.335 | -0.335 | -3.35 | -1.8074 | -1.8074 | 0 | 12 | 1 | 1 | -1.8074 | 10 | 0 | 0
1229.1 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.13 | -0.335 | -0.335 | -3.35 | -1.7779 | -1.7779 | 0 | 12 | 1 | 1 | -1.7779 | 10 | 0 | 0
1229.15 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.13 | -0.335 | -0.335 | -3.35 | -1.7779 | -1.7779 | 0 | 12 | 1 | 1 | -1.7779 | 10 | 0 | 0
1229.2 | 50.01 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
1229.25 | 50.01 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
1229.3 | 50.07 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
1229.35 | 50.07 | 50.01 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.235 | -2.35 | -1.175 | -1.175 | 0 | 12 | 1 | 1 | -1.175 | 10 | 0 | 0
1229.4 | 50.05 | 50.01 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.135 | -1.35 | -0.675 | -0.675 | 0 | 12 | 1 | 1 | -0.675 | 10 | 0 | 0
1229.45 | 50.05 | 50.01 | 0 | 0 | 0 | 50.07 | -0.032353 | -0.035 | -0.35 | -0.175 | -0.175 | 0 | 12 | 1 | 1 | -0.175 | 10 | 0 | 0
1229.5 | 50.1 | 50.01 | 0 | 0 | 0 | 50.1 | -0.05 | -0.05 | -0.5 | -0.25 | -0.25 | 0 | 12 | 1 | 1 | -0.25 | 10 | 0 | 0
1229.55 | 50.1 | 50.01 | 0 | 0 | 0 | 50.1 | -0.05 | -0.05 | -0.5 | -0.25 | -0.25 | 0 | 12 | 1 | 1 | -0.25 | 10 | 0 | 0
1229.6 | 50.11 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1229.65 | 50.11 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1229.7 | 50.06 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1229.75 | 50.06 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1229.8 | 50.04 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1229.85 | 50.04 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1229.9 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1229.95 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1230 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1230.05 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1230.1 | 50.11 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1230.15 | 50.11 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1230.2 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1230.25 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1230.3 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1230.35 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1230.4 | 50.02 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.11 | -0.145 | -0.145 | -1.45 | -0.73971 | -0.73971 | 0 | 12 | 1 | 1 | -0.73971 | 10 | 0 | 0
1230.45 | 50.02 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.11 | -0.145 | -0.145 | -1.45 | -0.73971 | -0.73971 | 0 | 12 | 1 | 1 | -0.73971 | 10 | 0 | 0
1230.5 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1230.55 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1230.6 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1230.65 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1230.7 | 50.01 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1230.75 | 50.01 | 50 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.045 | -0.45 | -0.225 | -0.225 | 0 | 12 | 1 | 1 | -0.225 | 10 | 0 | 0
1230.8 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
1230.85 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
1230.9 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
1230.95 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1231 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.14706 | 0.14706 | 0 | 12 | 1 | 1 | 0.14706 | 10 | 0 | 0
1231.05 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1231.1 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1231.15 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1231.2 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1231.25 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1231.3 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1231.35 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1231.4 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1231.45 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1231.5 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1231.55 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1231.6 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1231.65 | 50 | 50 | 0 | 0 | 0 | 50.01 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1231.7 | 49.5 | 49.5 | 1 | 1 | 10 | 50.01 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1231.75 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1231.8 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1231.85 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1231.9 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1231.95 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1232 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1232.05 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1232.1 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1232.15 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1232.2 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1232.25 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.1 | 1 | 5.5 | 5.5 | 0 | 12 | 1 | 1 | 5.5 | 10 | 0 | 0
1232.3 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.2 | 2 | 6 | 6 | 0 | 12 | 1 | 1 | 6 | 10 | 0 | 0
1232.35 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.3 | 3 | 6.5 | 6.5 | 0 | 12 | 1 | 1 | 6.5 | 10 | 0 | 0
1232.4 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.4 | 4 | 7 | 7 | 0 | 12 | 1 | 1 | 7 | 10 | 0 | 0
1232.45 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.5 | 5 | 7.5 | 7.5 | 0 | 12 | 1 | 1 | 7.5 | 10 | 0 | 0
1232.5 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.6 | 6 | 8 | 8 | 0 | 12 | 1 | 1 | 8 | 10 | 0 | 0
1232.55 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.7 | 7 | 8.5 | 8.5 | 0 | 12 | 1 | 1 | 8.5 | 10 | 0 | 0
1232.6 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.8 | 8 | 9 | 9 | 0 | 12 | 1 | 1 | 9 | 10 | 0 | 0
1232.65 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.9 | 9 | 9.5 | 9.5 | 0 | 12 | 1 | 1 | 9.5 | 10 | 0 | 0
1232.7 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1232.75 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1232.8 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1232.85 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1232.9 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1232.95 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1233 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1233.05 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1233.1 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1233.15 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1233.2 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1233.25 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1233.3 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1233.35 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1233.4 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1233.45 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1233.5 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1233.55 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1233.6 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1233.65 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1233.7 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1233.75 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1233.8 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1233.85 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1233.9 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1233.95 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1234 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1234.05 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1234.1 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1234.15 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1234.2 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1234.25 | 50.5 | 50.5 | -1 | 0.9 | 9 | 50.5 | -1 | -1 | -10 | -0.5 | -0.5 | 0 | 12 | 1 | 1 | -0.5 | 10 | 0 | 0
1234.3 | 50.5 | 50.5 | -1 | 0.8 | 8 | 50.5 | -1 | -1 | -10 | -1 | -1 | 0 | 12 | 1 | 1 | -1 | 10 | 0 | 0
1234.35 | 50.5 | 50.5 | -1 | 0.7 | 7 | 50.5 | -1 | -1 | -10 | -1.5 | -1.5 | 0 | 12 | 1 | 1 | -1.5 | 10 | 0 | 0
1234.4 | 50.5 | 50.5 | -1 | 0.6 | 6 | 50.5 | -1 | -1 | -10 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
1234.45 | 50.5 | 50.5 | -1 | 0.5 | 5 | 50.5 | -1 | -1 | -10 | -2.5 | -2.5 | 0 | 12 | 1 | 1 | -2.5 | 10 | 0 | 0
1234.5 | 50.5 | 50.5 | -1 | 0.4 | 4 | 50.5 | -1 | -1 | -10 | -3 | -3 | 0 | 12 | 1 | 1 | -3 | 10 | 0 | 0
1234.55 | 50.5 | 50.5 | -1 | 0.3 | 3 | 50.5 | -1 | -1 | -10 | -3.5 | -3.5 | 0 | 12 | 1 | 1 | -3.5 | 10 | 0 | 0
1234.6 | 50.5 | 50.5 | -1 | 0.2 | 2 | 50.5 | -1 | -1 | -10 | -4 | -4 | 0 | 12 | 1 | 1 | -4 | 10 | 0 | 0
1234.65 | 50.5 | 50.5 | -1 | 0.1 | 1 | 50.5 | -1 | -1 | -10 | -4.5 | -4.5 | 0 | 12 | 1 | 1 | -4.5 | 10 | 0 | 0
1234.7 | 50.5 | 50.5 | -1 | 0 | 0 | 50.5 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1234.75 | 50.5 | 50.5 | -1 | -0.1 | -1 | 50.5 | -1 | -1 | -10 | -5.5 | -5.5 | 0 | 12 | 1 | 1 | -5.5 | 10 | 0 | 0
1234.8 | 50.5 | 50.5 | -1 | -0.2 | -2 | 50.5 | -1 | -1 | -10 | -6 | -6 | 0 | 12 | 1 | 1 | -6 | 10 | 0 | 0
1234.85 | 50.5 | 50.5 | -1 | -0.3 | -3 | 50.5 | -1 | -1 | -10 | -6.5 | -6.5 | 0 | 12 | 1 | 1 | -6.5 | 10 | 0 | 0
1234.9 | 50.5 | 50.5 | -1 | -0.4 | -4 | 50.5 | -1 | -1 | -10 | -7 | -7 | 0 | 12 | 1 | 1 | -7 | 10 | 0 | 0
1234.95 | 50.5 | 50.5 | -1 | -0.5 | -5 | 50.5 | -1 | -1 | -10 | -7.5 | -7.5 | 0 | 12 | 1 | 1 | -7.5 | 10 | 0 | 0
1235 | 50.5 | 50.5 | -1 | -0.6 | -6 | 50.5 | -1 | -1 | -10 | -8 | -8 | 0 | 12 | 1 | 1 | -8 | 10 | 0 | 0
1235.05 | 50.5 | 50.5 | -1 | -0.7 | -7 | 50.5 | -1 | -1 | -10 | -8.5 | -8.5 | 0 | 12 | 1 | 1 | -8.5 | 10 | 0 | 0
1235.1 | 50.5 | 50.5 | -1 | -0.8 | -8 | 50.5 | -1 | -1 | -10 | -9 | -9 | 0 | 12 | 1 | 1 | -9 | 10 | 0 | 0
1235.15 | 50.5 | 50.5 | -1 | -0.9 | -9 | 50.5 | -1 | -1 | -10 | -9.5 | -9.5 | 0 | 12 | 1 | 1 | -9.5 | 10 | 0 | 0
1235.2 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1235.25 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1235.3 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1235.35 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1235.4 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1235.45 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1235.5 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1235.55 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1235.6 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1235.65 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1235.7 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1235.75 | 50.47 | 50.47 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1235.8 | 50.45 | 50.45 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1235.85 | 50.42 | 50.42 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1235.9 | 50.4 | 50.4 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1235.95 | 50.37 | 50.37 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1236 | 50.35 | 50.35 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1236.05 | 50.32 | 50.32 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1236.1 | 50.29 | 50.29 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1236.15 | 50.27 | 50.27 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1236.2 | 50.24 | 50.24 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1236.25 | 50.22 | 50.22 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1236.3 | 50.19 | 50.19 | -0.905 | -0.905 | -9.05 | 50.47 | -1 | -1 | -10 | -9.525 | -9.525 | 0 | 12 | 1 | 1 | -9.525 | 10 | 0 | 0
1236.35 | 50.17 | 50.17 | -0.715 | -0.715 | -7.15 | 50.45 | -1 | -1 | -10 | -8.575 | -8.575 | 0 | 12 | 1 | 1 | -8.575 | 10 | 0 | 0
1236.4 | 50.14 | 50.14 | -0.43 | -0.43 | -4.3 | 50.42 | -1 | -1 | -10 | -7.15 | -7.15 | 0 | 12 | 1 | 1 | -7.15 | 10 | 0 | 0
1236.45 | 50.12 | 50.12 | -0.24 | -0.24 | -2.4 | 50.4 | -1 | -1 | -10 | -6.2 | -6.2 | 0 | 12 | 1 | 1 | -6.2 | 10 | 0 | 0
1236.5 | 50.09 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 50.37 | -1 | -1 | -10 | -5.2206 | -5.2206 | 0 | 12 | 1 | 1 | -5.2206 | 10 | 0 | 0
1236.55 | 50.06 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.35 | -1 | -1 | -10 | -5.1324 | -5.1324 | 0 | 12 | 1 | 1 | -5.1324 | 10 | 0 | 0
1236.6 | 50.04 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.32 | -1 | -1 | -10 | -5.0735 | -5.0735 | 0 | 12 | 1 | 1 | -5.0735 | 10 | 0 | 0
1236.65 | 50.01 | 50.01 | 0 | 0 | 0 | 50.29 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1236.7 | 49.99 | 49.99 | 0 | 0 | 0 | 50.27 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1236.75 | 49.96 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.24 | -1 | -1 | -10 | -4.9265 | -4.9265 | 0 | 12 | 1 | 1 | -4.9265 | 10 | 0 | 0
1236.8 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.22 | -1 | -1 | -10 | -4.8676 | -4.8676 | 0 | 12 | 1 | 1 | -4.8676 | 10 | 0 | 0
1236.85 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.19 | -0.905 | -0.905 | -9.05 | -4.3044 | -4.3044 | 0 | 12 | 1 | 1 | -4.3044 | 10 | 0 | 0
1236.9 | 49.88 | 49.88 | 0.24 | 0.24 | 2.4 | 50.17 | -0.715 | -0.805 | -8.05 | -2.825 | -2.825 | 0 | 12 | 1 | 1 | -2.825 | 10 | 0 | 0
1236.95 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.14 | -0.43 | -0.705 | -7.05 | -1.375 | -1.375 | 0 | 12 | 1 | 1 | -1.375 | 10 | 0 | 0
1237 | 49.83 | 49.83 | 0.715 | 0.715 | 7.15 | 50.12 | -0.24 | -0.605 | -6.05 | 0.55 | 0.55 | 0 | 12 | 1 | 1 | 0.55 | 10 | 0 | 0
1237.05 | 49.81 | 49.81 | 0.905 | 0.905 | 9.05 | 50.09 | -0.044118 | -0.505 | -5.05 | 2 | 2 | 0 | 12 | 1 | 1 | 2 | 10 | 0 | 0
1237.1 | 49.78 | 49.78 | 1 | 1 | 10 | 50.06 | -0.026471 | -0.405 | -4.05 | 2.975 | 2.975 | 0 | 12 | 1 | 1 | 2.975 | 10 | 0 | 0
1237.15 | 49.76 | 49.76 | 1 | 1 | 10 | 50.04 | -0.014706 | -0.305 | -3.05 | 3.475 | 3.475 | 0 | 12 | 1 | 1 | 3.475 | 10 | 0 | 0
1237.2 | 49.73 | 49.73 | 1 | 1 | 10 | 50.01 | 0 | -0.205 | -2.05 | 3.975 | 3.975 | 0 | 12 | 1 | 1 | 3.975 | 10 | 0 | 0
1237.25 | 49.71 | 49.71 | 1 | 1 | 10 | 49.99 | 0 | -0.105 | -1.05 | 4.475 | 4.475 | 0 | 12 | 1 | 1 | 4.475 | 10 | 0 | 0
1237.3 | 49.68 | 49.68 | 1 | 1 | 10 | 49.96 | 0.014706 | -0.005 | -0.05 | 4.975 | 4.975 | 0 | 12 | 1 | 1 | 4.975 | 10 | 0 | 0
1237.35 | 49.65 | 49.65 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
1237.4 | 49.63 | 49.63 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1237.45 | 49.6 | 49.6 | 1 | 1 | 10 | 49.88 | 0.24 | 0.14412 | 1.4412 | 5.7206 | 5.7206 | 0 | 12 | 1 | 1 | 5.7206 | 10 | 0 | 0
1237.5 | 49.58 | 49.58 | 1 | 1 | 10 | 49.86 | 0.43 | 0.24412 | 2.4412 | 6.2206 | 6.2206 | 0 | 12 | 1 | 1 | 6.2206 | 10 | 0 | 0
1237.55 | 49.55 | 49.55 | 1 | 1 | 10 | 49.83 | 0.715 | 0.34412 | 3.4412 | 6.7206 | 6.7206 | 0 | 12 | 1 | 1 | 6.7206 | 10 | 0 | 0
1237.6 | 49.53 | 49.53 | 1 | 1 | 10 | 49.81 | 0.905 | 0.44412 | 4.4412 | 7.2206 | 7.2206 | 0 | 12 | 1 | 1 | 7.2206 | 10 | 0 | 0
1237.65 | 49.5 | 49.5 | 1 | 1 | 10 | 49.78 | 1 | 0.54412 | 5.4412 | 7.7206 | 7.7206 | 0 | 12 | 1 | 1 | 7.7206 | 10 | 0 | 0
1237.7 | 49.5 | 49.5 | 1 | 1 | 10 | 49.76 | 1 | 0.64412 | 6.4412 | 8.2206 | 8.2206 | 0 | 12 | 1 | 1 | 8.2206 | 10 | 0 | 0
1237.75 | 49.53 | 49.5 | 1 | 1 | 10 | 49.73 | 1 | 0.74412 | 7.4412 | 8.7206 | 8.7206 | 0 | 12 | 1 | 1 | 8.7206 | 10 | 0 | 0
1237.8 | 49.55 | 49.5 | 1 | 1 | 10 | 49.71 | 1 | 0.84412 | 8.4412 | 9.2206 | 9.2206 | 0 | 12 | 1 | 1 | 9.2206 | 10 | 0 | 0
1237.85 | 49.58 | 49.5 | 1 | 1 | 10 | 49.68 | 1 | 0.94412 | 9.4412 | 9.7206 | 9.7206 | 0 | 12 | 1 | 1 | 9.7206 | 10 | 0 | 0
1237.9 | 49.6 | 49.5 | 1 | 1 | 10 | 49.65 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1237.95 | 49.63 | 49.5 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1238 | 49.65 | 49.5 | 1 | 1 | 10 | 49.65 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1238.05 | 49.68 | 49.5 | 1 | 1 | 10 | 49.68 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1238.1 | 49.71 | 49.5 | 1 | 1 | 10 | 49.71 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1238.15 | 49.73 | 49.5 | 1 | 1 | 10 | 49.73 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1238.2 | 49.76 | 49.5 | 1 | 1 | 10 | 49.76 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1238.25 | 49.78 | 49.5 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1238.3 | 49.81 | 49.53 | 1 | 1 | 10 | 49.81 | 0.905 | 0.905 | 9.05 | 9.525 | 9.525 | 0 | 12 | 1 | 1 | 9.525 | 10 | 0 | 0
1238.35 | 49.83 | 49.55 | 1 | 1 | 10 | 49.83 | 0.715 | 0.715 | 7.15 | 8.575 | 8.575 | 0 | 12 | 1 | 1 | 8.575 | 10 | 0 | 0
1238.4 | 49.86 | 49.58 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
1238.45 | 49.88 | 49.6 | 1 | 1 | 10 | 49.88 | 0.24 | 0.24 | 2.4 | 6.2 | 6.2 | 0 | 12 | 1 | 1 | 6.2 | 10 | 0 | 0
1238.5 | 49.91 | 49.63 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1238.55 | 49.94 | 49.65 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
1238.6 | 49.96 | 49.68 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
1238.65 | 49.99 | 49.71 | 1 | 1 | 10 | 49.99 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1238.7 | 50.01 | 49.73 | 1 | 1 | 10 | 50.01 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1238.75 | 50.04 | 49.76 | 1 | 1 | 10 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 4.9265 | 4.9265 | 0 | 12 | 1 | 1 | 4.9265 | 10 | 0 | 0
1238.8 | 50.06 | 49.78 | 1 | 1 | 10 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 4.8676 | 4.8676 | 0 | 12 | 1 | 1 | 4.8676 | 10 | 0 | 0
1238.85 | 50.09 | 49.81 | 0.905 | 0.905 | 9.05 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 4.3044 | 4.3044 | 0 | 12 | 1 | 1 | 4.3044 | 10 | 0 | 0
1238.9 | 50.12 | 49.83 | 0.715 | 0.805 | 8.05 | 50.12 | -0.24 | -0.24 | -2.4 | 2.825 | 2.825 | 0 | 12 | 1 | 1 | 2.825 | 10 | 0 | 0
1238.95 | 50.14 | 49.86 | 0.43 | 0.705 | 7.05 | 50.14 | -0.43 | -0.43 | -4.3 | 1.375 | 1.375 | 0 | 12 | 1 | 1 | 1.375 | 10 | 0 | 0
1239 | 50.17 | 49.88 | 0.24 | 0.605 | 6.05 | 50.17 | -0.715 | -0.715 | -7.15 | -0.55 | -0.55 | 0 | 12 | 1 | 1 | -0.55 | 10 | 0 | 0
1239.05 | 50.19 | 49.91 | 0.044118 | 0.505 | 5.05 | 50.19 | -0.905 | -0.905 | -9.05 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
1239.1 | 50.22 | 49.94 | 0.026471 | 0.405 | 4.05 | 50.22 | -1 | -1 | -10 | -2.975 | -2.975 | 0 | 12 | 1 | 1 | -2.975 | 10 | 0 | 0
1239.15 | 50.24 | 49.96 | 0.014706 | 0.305 | 3.05 | 50.24 | -1 | -1 | -10 | -3.475 | -3.475 | 0 | 12 | 1 | 1 | -3.475 | 10 | 0 | 0
1239.2 | 50.27 | 49.99 | 0 | 0.205 | 2.05 | 50.27 | -1 | -1 | -10 | -3.975 | -3.975 | 0 | 12 | 1 | 1 | -3.975 | 10 | 0 | 0
1239.25 | 50.29 | 50.01 | 0 | 0.105 | 1.05 | 50.29 | -1 | -1 | -10 | -4.475 | -4.475 | 0 | 12 | 1 | 1 | -4.475 | 10 | 0 | 0
1239.3 | 50.32 | 50.04 | -0.014706 | 0.005 | 0.05 | 50.32 | -1 | -1 | -10 | -4.975 | -4.975 | 0 | 12 | 1 | 1 | -4.975 | 10 | 0 | 0
1239.35 | 50.35 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.35 | -1 | -1 | -10 | -5.1324 | -5.1324 | 0 | 12 | 1 | 1 | -5.1324 | 10 | 0 | 0
1239.4 | 50.37 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 50.37 | -1 | -1 | -10 | -5.2206 | -5.2206 | 0 | 12 | 1 | 1 | -5.2206 | 10 | 0 | 0
1239.45 | 50.4 | 50.12 | -0.24 | -0.14412 | -1.4412 | 50.4 | -1 | -1 | -10 | -5.7206 | -5.7206 | 0 | 12 | 1 | 1 | -5.7206 | 10 | 0 | 0
1239.5 | 50.42 | 50.14 | -0.43 | -0.24412 | -2.4412 | 50.42 | -1 | -1 | -10 | -6.2206 | -6.2206 | 0 | 12 | 1 | 1 | -6.2206 | 10 | 0 | 0
1239.55 | 50.45 | 50.17 | -0.715 | -0.34412 | -3.4412 | 50.45 | -1 | -1 | -10 | -6.7206 | -6.7206 | 0 | 12 | 1 | 1 | -6.7206 | 10 | 0 | 0
1239.6 | 50.47 | 50.19 | -0.905 | -0.44412 | -4.4412 | 50.47 | -1 | -1 | -10 | -7.2206 | -7.2206 | 0 | 12 | 1 | 1 | -7.2206 | 10 | 0 | 0
1239.65 | 50.5 | 50.22 | -1 | -0.54412 | -5.4412 | 50.5 | -1 | -1 | -10 | -7.7206 | -7.7206 | 0 | 12 | 1 | 1 | -7.7206 | 10 | 0 | 0
1239.7 | 50.5 | 50.24 | -1 | -0.64412 | -6.4412 | 50.5 | -1 | -1 | -10 | -8.2206 | -8.2206 | 0 | 12 | 1 | 1 | -8.2206 | 10 | 0 | 0
1239.75 | 50.47 | 50.27 | -1 | -0.74412 | -7.4412 | 50.5 | -1 | -1 | -10 | -8.7206 | -8.7206 | 0 | 12 | 1 | 1 | -8.7206 | 10 | 0 | 0
1239.8 | 50.45 | 50.29 | -1 | -0.84412 | -8.4412 | 50.5 | -1 | -1 | -10 | -9.2206 | -9.2206 | 0 | 12 | 1 | 1 | -9.2206 | 10 | 0 | 0
1239.85 | 50.42 | 50.32 | -1 | -0.94412 | -9.4412 | 50.5 | -1 | -1 | -10 | -9.7206 | -9.7206 | 0 | 12 | 1 | 1 | -9.7206 | 10 | 0 | 0
1239.9 | 50.39 | 50.35 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1239.95 | 50.37 | 50.37 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1240 | 50.34 | 50.34 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1240.05 | 50.32 | 50.32 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1240.1 | 50.29 | 50.29 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1240.15 | 50.26 | 50.26 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1240.2 | 50.24 | 50.24 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1240.25 | 50.21 | 50.21 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1240.3 | 50.18 | 50.18 | -0.81 | -0.81 | -8.1 | 50.47 | -1 | -1 | -10 | -9.05 | -9.05 | 0 | 12 | 1 | 1 | -9.05 | 10 | 0 | 0
1240.35 | 50.16 | 50.16 | -0.62 | -0.62 | -6.2 | 50.45 | -1 | -1 | -10 | -8.1 | -8.1 | 0 | 12 | 1 | 1 | -8.1 | 10 | 0 | 0
1240.4 | 50.13 | 50.13 | -0.335 | -0.335 | -3.35 | 50.42 | -1 | -1 | -10 | -6.675 | -6.675 | 0 | 12 | 1 | 1 | -6.675 | 10 | 0 | 0
1240.45 | 50.11 | 50.11 | -0.145 | -0.145 | -1.45 | 50.39 | -1 | -1 | -10 | -5.725 | -5.725 | 0 | 12 | 1 | 1 | -5.725 | 10 | 0 | 0
1240.5 | 50.08 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 50.37 | -1 | -1 | -10 | -5.1912 | -5.1912 | 0 | 12 | 1 | 1 | -5.1912 | 10 | 0 | 0
1240.55 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.34 | -1 | -1 | -10 | -5.1029 | -5.1029 | 0 | 12 | 1 | 1 | -5.1029 | 10 | 0 | 0
1240.6 | 50.03 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 50.32 | -1 | -1 | -10 | -5.0441 | -5.0441 | 0 | 12 | 1 | 1 | -5.0441 | 10 | 0 | 0
1240.65 | 50 | 50 | 0 | 0 | 0 | 50.29 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1240.7 | 50 | 50 | 0 | 0 | 0 | 50.26 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1240.75 | 50 | 50 | 0 | 0 | 0 | 50.24 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1240.8 | 50 | 50 | 0 | 0 | 0 | 50.21 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1240.85 | 50 | 50 | 0 | 0 | 0 | 50.18 | -0.81 | -0.9 | -9 | -4.5 | -4.5 | 0 | 12 | 1 | 1 | -4.5 | 10 | 0 | 0
1240.9 | 50 | 50 | 0 | 0 | 0 | 50.16 | -0.62 | -0.8 | -8 | -4 | -4 | 0 | 12 | 1 | 1 | -4 | 10 | 0 | 0
1240.95 | 50 | 50 | 0 | 0 | 0 | 50.13 | -0.335 | -0.7 | -7 | -3.5 | -3.5 | 0 | 12 | 1 | 1 | -3.5 | 10 | 0 | 0
1241 | 50.01 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.6 | -6 | -3 | -3 | 0 | 12 | 1 | 1 | -3 | 10 | 0 | 0
1241.05 | 50.01 | 50 | 0 | 0 | 0 | 50.08 | -0.038235 | -0.5 | -5 | -2.5 | -2.5 | 0 | 12 | 1 | 1 | -2.5 | 10 | 0 | 0
1241.1 | 49.99 | 49.99 | 0 | 0 | 0 | 50.05 | -0.020588 | -0.4 | -4 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
1241.15 | 49.99 | 49.99 | 0 | 0 | 0 | 50.03 | -0.0088235 | -0.3 | -3 | -1.5 | -1.5 | 0 | 12 | 1 | 1 | -1.5 | 10 | 0 | 0
1241.2 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | -0.2 | -2 | -0.83824 | -0.83824 | 0 | 12 | 1 | 1 | -0.83824 | 10 | 0 | 0
1241.25 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | -0.1 | -1 | -0.33824 | -0.33824 | 0 | 12 | 1 | 1 | -0.33824 | 10 | 0 | 0
1241.3 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
1241.35 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
1241.4 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
1241.45 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
1241.5 | 49.89 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
1241.55 | 49.89 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
1241.6 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50.01 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1241.65 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1241.7 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1241.75 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 2.7868 | 2.7868 | 0 | 12 | 1 | 1 | 2.7868 | 10 | 0 | 0
1241.8 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 2.7868 | 2.7868 | 0 | 12 | 1 | 1 | 2.7868 | 10 | 0 | 0
1241.85 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 2.8456 | 2.8456 | 0 | 12 | 1 | 1 | 2.8456 | 10 | 0 | 0
1241.9 | 49.94 | 49.85 | 0.525 | 0.525 | 5.25 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 2.7574 | 2.7574 | 0 | 12 | 1 | 1 | 2.7574 | 10 | 0 | 0
1241.95 | 49.94 | 49.85 | 0.525 | 0.525 | 5.25 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 2.7574 | 2.7574 | 0 | 12 | 1 | 1 | 2.7574 | 10 | 0 | 0
1242 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1242.05 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1242.1 | 49.93 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1242.15 | 49.93 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1242.2 | 49.96 | 49.85 | 0.525 | 0.525 | 5.25 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 2.6985 | 2.6985 | 0 | 12 | 1 | 1 | 2.6985 | 10 | 0 | 0
1242.25 | 49.96 | 49.85 | 0.525 | 0.525 | 5.25 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 2.6985 | 2.6985 | 0 | 12 | 1 | 1 | 2.6985 | 10 | 0 | 0
1242.3 | 49.99 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1242.35 | 49.99 | 49.91 | 0.044118 | 0.425 | 4.25 | 49.99 | 0 | 0 | 0 | 2.125 | 2.125 | 0 | 12 | 1 | 1 | 2.125 | 10 | 0 | 0
1242.4 | 49.99 | 49.91 | 0.044118 | 0.325 | 3.25 | 49.99 | 0 | 0 | 0 | 1.625 | 1.625 | 0 | 12 | 1 | 1 | 1.625 | 10 | 0 | 0
1242.45 | 49.99 | 49.93 | 0.032353 | 0.225 | 2.25 | 49.99 | 0 | 0 | 0 | 1.125 | 1.125 | 0 | 12 | 1 | 1 | 1.125 | 10 | 0 | 0
1242.5 | 49.96 | 49.93 | 0.032353 | 0.125 | 1.25 | 49.99 | 0 | 0 | 0 | 0.625 | 0.625 | 0 | 12 | 1 | 1 | 0.625 | 10 | 0 | 0
1242.55 | 49.96 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 49.99 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1242.6 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1242.65 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1242.7 | 50.05 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.058824 | 0.058824 | 0 | 12 | 1 | 1 | 0.058824 | 10 | 0 | 0
1242.75 | 50.05 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
1242.8 | 49.97 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
1242.85 | 49.97 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
1242.9 | 49.92 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1242.95 | 49.92 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1243 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1243.05 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1243.1 | 49.94 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1243.15 | 49.94 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1243.2 | 50.01 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1243.25 | 50.01 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1243.3 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1243.35 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
1243.4 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
1243.45 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
1243.5 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
1243.55 | 49.95 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
1243.6 | 49.97 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
1243.65 | 49.97 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
1243.7 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
1243.75 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
1243.8 | 49.87 | 49.87 | 0.335 | 0.335 | 3.35 | 50.01 | 0 | 0 | 0 | 1.675 | 1.675 | 0 | 12 | 1 | 1 | 1.675 | 10 | 0 | 0
1243.85 | 49.87 | 49.87 | 0.335 | 0.335 | 3.35 | 49.99 | 0 | 0 | 0 | 1.675 | 1.675 | 0 | 12 | 1 | 1 | 1.675 | 10 | 0 | 0
1243.9 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1243.95 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 2.6691 | 2.6691 | 0 | 12 | 1 | 1 | 2.6691 | 10 | 0 | 0
1244 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1244.05 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1244.1 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1244.15 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1244.2 | 49.84 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1244.25 | 49.84 | 49.79 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
1244.3 | 49.89 | 49.79 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
1244.35 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.12647 | 1.2647 | 5.6324 | 5.6324 | 0 | 12 | 1 | 1 | 5.6324 | 10 | 0 | 0
1244.4 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.145 | 1.45 | 5.725 | 5.725 | 0 | 12 | 1 | 1 | 5.725 | 10 | 0 | 0
1244.45 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.145 | 1.45 | 5.725 | 5.725 | 0 | 12 | 1 | 1 | 5.725 | 10 | 0 | 0
1244.5 | 49.96 | 49.79 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
1244.55 | 49.96 | 49.79 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
1244.6 | 50.02 | 49.79 | 1 | 1 | 10 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 4.9853 | 4.9853 | 0 | 12 | 1 | 1 | 4.9853 | 10 | 0 | 0
1244.65 | 50.02 | 49.79 | 1 | 1 | 10 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 4.9853 | 4.9853 | 0 | 12 | 1 | 1 | 4.9853 | 10 | 0 | 0
1244.7 | 50.03 | 49.79 | 1 | 1 | 10 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.9559 | 4.9559 | 0 | 12 | 1 | 1 | 4.9559 | 10 | 0 | 0
1244.75 | 50.03 | 49.84 | 0.62 | 0.9 | 9 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.4559 | 4.4559 | 0 | 12 | 1 | 1 | 4.4559 | 10 | 0 | 0
1244.8 | 50.02 | 49.84 | 0.62 | 0.8 | 8 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 3.9559 | 3.9559 | 0 | 12 | 1 | 1 | 3.9559 | 10 | 0 | 0
1244.85 | 50.02 | 49.89 | 0.145 | 0.7 | 7 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 3.4559 | 3.4559 | 0 | 12 | 1 | 1 | 3.4559 | 10 | 0 | 0
1244.9 | 50.08 | 49.89 | 0.145 | 0.6 | 6 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 2.8088 | 2.8088 | 0 | 12 | 1 | 1 | 2.8088 | 10 | 0 | 0
1244.95 | 50.08 | 49.89 | 0.145 | 0.5 | 5 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 2.3088 | 2.3088 | 0 | 12 | 1 | 1 | 2.3088 | 10 | 0 | 0
1245 | 50.01 | 49.89 | 0.145 | 0.4 | 4 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 1.8088 | 1.8088 | 0 | 12 | 1 | 1 | 1.8088 | 10 | 0 | 0
1245.05 | 50.01 | 49.96 | 0.014706 | 0.3 | 3 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 1.3088 | 1.3088 | 0 | 12 | 1 | 1 | 1.3088 | 10 | 0 | 0
1245.1 | 49.94 | 49.94 | 0.026471 | 0.2 | 2 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.80882 | 0.80882 | 0 | 12 | 1 | 1 | 0.80882 | 10 | 0 | 0
1245.15 | 49.94 | 49.94 | 0.026471 | 0.1 | 1 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.30882 | 0.30882 | 0 | 12 | 1 | 1 | 0.30882 | 10 | 0 | 0
1245.2 | 50 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
1245.25 | 50 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
1245.3 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
1245.35 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
1245.4 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1245.45 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1245.5 | 49.92 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1245.55 | 49.92 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
1245.6 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50.01 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1245.65 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1245.7 | 49.92 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1245.75 | 49.92 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1245.8 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1245.85 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1245.9 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1245.95 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1246 | 49.87 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1246.05 | 49.87 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1246.1 | 49.8 | 49.8 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1246.15 | 49.8 | 49.8 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1246.2 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1246.25 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1246.3 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1246.35 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1246.4 | 49.72 | 49.72 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1246.45 | 49.72 | 49.72 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1246.5 | 49.67 | 49.67 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1246.55 | 49.67 | 49.67 | 1 | 1 | 10 | 49.87 | 0.335 | 0.14412 | 1.4412 | 5.7206 | 5.7206 | 0 | 12 | 1 | 1 | 5.7206 | 10 | 0 | 0
1246.6 | 49.65 | 49.65 | 1 | 1 | 10 | 49.87 | 0.335 | 0.24412 | 2.4412 | 6.2206 | 6.2206 | 0 | 12 | 1 | 1 | 6.2206 | 10 | 0 | 0
1246.65 | 49.65 | 49.65 | 1 | 1 | 10 | 49.8 | 1 | 0.34412 | 3.4412 | 6.7206 | 6.7206 | 0 | 12 | 1 | 1 | 6.7206 | 10 | 0 | 0
1246.7 | 49.59 | 49.59 | 1 | 1 | 10 | 49.8 | 1 | 0.44412 | 4.4412 | 7.2206 | 7.2206 | 0 | 12 | 1 | 1 | 7.2206 | 10 | 0 | 0
1246.75 | 49.59 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.54412 | 5.4412 | 7.7206 | 7.7206 | 0 | 12 | 1 | 1 | 7.7206 | 10 | 0 | 0
1246.8 | 49.66 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.64412 | 6.4412 | 8.2206 | 8.2206 | 0 | 12 | 1 | 1 | 8.2206 | 10 | 0 | 0
1246.85 | 49.66 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.74412 | 7.4412 | 8.7206 | 8.7206 | 0 | 12 | 1 | 1 | 8.7206 | 10 | 0 | 0
1246.9 | 49.63 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.84412 | 8.4412 | 9.2206 | 9.2206 | 0 | 12 | 1 | 1 | 9.2206 | 10 | 0 | 0
1246.95 | 49.63 | 49.59 | 1 | 1 | 10 | 49.72 | 1 | 0.94412 | 9.4412 | 9.7206 | 9.7206 | 0 | 12 | 1 | 1 | 9.7206 | 10 | 0 | 0
1247 | 49.61 | 49.59 | 1 | 1 | 10 | 49.72 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1247.05 | 49.61 | 49.59 | 1 | 1 | 10 | 49.67 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1247.1 | 49.54 | 49.54 | 1 | 1 | 10 | 49.67 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1247.15 | 49.54 | 49.54 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1247.2 | 49.46 | 49.46 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1247.25 | 49.46 | 49.46 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1247.3 | 49.45 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1247.35 | 49.45 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1247.4 | 49.51 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1247.45 | 49.51 | 49.45 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1247.5 | 49.5 | 49.45 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1247.55 | 49.5 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1247.6 | 49.54 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1247.65 | 49.54 | 49.45 | 1 | 1 | 10 | 49.54 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1247.7 | 49.59 | 49.45 | 1 | 1 | 10 | 49.59 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1247.75 | 49.59 | 49.45 | 1 | 1 | 10 | 49.59 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1247.8 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1247.85 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1247.9 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1247.95 | 49.61 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1248 | 49.53 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1248.05 | 49.53 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1248.1 | 49.54 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1248.15 | 49.54 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1248.2 | 49.61 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1248.25 | 49.61 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1248.3 | 49.66 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1248.35 | 49.66 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1248.4 | 49.64 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1248.45 | 49.64 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1248.5 | 49.69 | 49.53 | 1 | 1 | 10 | 49.69 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1248.55 | 49.69 | 49.53 | 1 | 1 | 10 | 49.69 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1248.6 | 49.74 | 49.53 | 1 | 1 | 10 | 49.74 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1248.65 | 49.74 | 49.54 | 1 | 1 | 10 | 49.74 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1248.7 | 49.78 | 49.54 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1248.75 | 49.78 | 49.61 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1248.8 | 49.82 | 49.61 | 1 | 1 | 10 | 49.82 | 0.81 | 0.81 | 8.1 | 9.05 | 9.05 | 0 | 12 | 1 | 1 | 9.05 | 10 | 0 | 0
1248.85 | 49.82 | 49.64 | 1 | 1 | 10 | 49.82 | 0.81 | 0.81 | 8.1 | 9.05 | 9.05 | 0 | 12 | 1 | 1 | 9.05 | 10 | 0 | 0
1248.9 | 49.86 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
1248.95 | 49.86 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
1249 | 49.84 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
1249.05 | 49.84 | 49.69 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
1249.1 | 49.91 | 49.69 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1249.15 | 49.91 | 49.74 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1249.2 | 49.97 | 49.74 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1249.25 | 49.97 | 49.78 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1249.3 | 50.03 | 49.78 | 1 | 1 | 10 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.9559 | 4.9559 | 0 | 12 | 1 | 1 | 4.9559 | 10 | 0 | 0
1249.35 | 50.03 | 49.82 | 0.81 | 0.9 | 9 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.4559 | 4.4559 | 0 | 12 | 1 | 1 | 4.4559 | 10 | 0 | 0
1249.4 | 50.05 | 49.82 | 0.81 | 0.81 | 8.1 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 3.9471 | 3.9471 | 0 | 12 | 1 | 1 | 3.9471 | 10 | 0 | 0
1249.45 | 50.05 | 49.84 | 0.62 | 0.71 | 7.1 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 3.4471 | 3.4471 | 0 | 12 | 1 | 1 | 3.4471 | 10 | 0 | 0
1249.5 | 50.01 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
1249.55 | 50.01 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
1249.6 | 49.95 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
1249.65 | 49.95 | 49.91 | 0.044118 | 0.52 | 5.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.4971 | 2.4971 | 0 | 12 | 1 | 1 | 2.4971 | 10 | 0 | 0
1249.7 | 49.99 | 49.91 | 0.044118 | 0.42 | 4.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 1.9971 | 1.9971 | 0 | 12 | 1 | 1 | 1.9971 | 10 | 0 | 0
1249.75 | 49.99 | 49.95 | 0.020588 | 0.32 | 3.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 1.4971 | 1.4971 | 0 | 12 | 1 | 1 | 1.4971 | 10 | 0 | 0
1249.8 | 49.92 | 49.92 | 0.038235 | 0.22 | 2.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.99706 | 0.99706 | 0 | 12 | 1 | 1 | 0.99706 | 10 | 0 | 0
1249.85 | 49.92 | 49.92 | 0.038235 | 0.12 | 1.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.49706 | 0.49706 | 0 | 12 | 1 | 1 | 0.49706 | 10 | 0 | 0
1249.9 | 49.97 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1249.95 | 49.97 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1250 | 50.02 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1250.05 | 50.02 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.17647 | 0.17647 | 0 | 12 | 1 | 1 | 0.17647 | 10 | 0 | 0
1250.1 | 50.07 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1250.15 | 50.07 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1250.2 | 50.06 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1250.25 | 50.06 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1250.3 | 50.13 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
1250.35 | 50.13 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
1250.4 | 50.09 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
1250.45 | 50.09 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6309 | -1.6309 | 0 | 12 | 1 | 1 | -1.6309 | 10 | 0 | 0
1250.5 | 50.07 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6309 | -1.6309 | 0 | 12 | 1 | 1 | -1.6309 | 10 | 0 | 0
1250.55 | 50.07 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6897 | -1.6897 | 0 | 12 | 1 | 1 | -1.6897 | 10 | 0 | 0
1250.6 | 50.07 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6897 | -1.6897 | 0 | 12 | 1 | 1 | -1.6897 | 10 | 0 | 0
1250.65 | 50.07 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.13 | -0.335 | -0.335 | -3.35 | -1.8074 | -1.8074 | 0 | 12 | 1 | 1 | -1.8074 | 10 | 0 | 0
1250.7 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.13 | -0.335 | -0.335 | -3.35 | -1.7779 | -1.7779 | 0 | 12 | 1 | 1 | -1.7779 | 10 | 0 | 0
1250.75 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.13 | -0.335 | -0.335 | -3.35 | -1.7779 | -1.7779 | 0 | 12 | 1 | 1 | -1.7779 | 10 | 0 | 0
1250.8 | 50.01 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
1250.85 | 50.01 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
1250.9 | 50.07 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
1250.95 | 50.07 | 50.01 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.235 | -2.35 | -1.175 | -1.175 | 0 | 12 | 1 | 1 | -1.175 | 10 | 0 | 0
1251 | 50.05 | 50.01 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.135 | -1.35 | -0.675 | -0.675 | 0 | 12 | 1 | 1 | -0.675 | 10 | 0 | 0
1251.05 | 50.05 | 50.01 | 0 | 0 | 0 | 50.07 | -0.032353 | -0.035 | -0.35 | -0.175 | -0.175 | 0 | 12 | 1 | 1 | -0.175 | 10 | 0 | 0
1251.1 | 50.1 | 50.01 | 0 | 0 | 0 | 50.1 | -0.05 | -0.05 | -0.5 | -0.25 | -0.25 | 0 | 12 | 1 | 1 | -0.25 | 10 | 0 | 0
1251.15 | 50.1 | 50.01 | 0 | 0 | 0 | 50.1 | -0.05 | -0.05 | -0.5 | -0.25 | -0.25 | 0 | 12 | 1 | 1 | -0.25 | 10 | 0 | 0
1251.2 | 50.11 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1251.25 | 50.11 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1251.3 | 50.06 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1251.35 | 50.06 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1251.4 | 50.04 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1251.45 | 50.04 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1251.5 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1251.55 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1251.6 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1251.65 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1251.7 | 50.11 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1251.75 | 50.11 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1251.8 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1251.85 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1251.9 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1251.95 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1252 | 50.02 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.11 | -0.145 | -0.145 | -1.45 | -0.73971 | -0.73971 | 0 | 12 | 1 | 1 | -0.73971 | 10 | 0 | 0
1252.05 | 50.02 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.11 | -0.145 | -0.145 | -1.45 | -0.73971 | -0.73971 | 0 | 12 | 1 | 1 | -0.73971 | 10 | 0 | 0
1252.1 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1252.15 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1252.2 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1252.25 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1252.3 | 50.01 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1252.35 | 50.01 | 50 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.045 | -0.45 | -0.225 | -0.225 | 0 | 12 | 1 | 1 | -0.225 | 10 | 0 | 0
1252.4 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
1252.45 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
1252.5 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
1252.55 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1252.6 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.14706 | 0.14706 | 0 | 12 | 1 | 1 | 0.14706 | 10 | 0 | 0
1252.65 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1252.7 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1252.75 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1252.8 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1252.85 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1252.9 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1252.95 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1253 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1253.05 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1253.1 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1253.15 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1253.2 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1253.25 | 50 | 50 | 0 | 0 | 0 | 50.01 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1253.3 | 49.5 | 49.5 | 1 | 1 | 10 | 50.01 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1253.35 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1253.4 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1253.45 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1253.5 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1253.55 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1253.6 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1253.65 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1253.7 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1253.75 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1253.8 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1253.85 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.1 | 1 | 5.5 | 5.5 | 0 | 12 | 1 | 1 | 5.5 | 10 | 0 | 0
1253.9 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.2 | 2 | 6 | 6 | 0 | 12 | 1 | 1 | 6 | 10 | 0 | 0
1253.95 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.3 | 3 | 6.5 | 6.5 | 0 | 12 | 1 | 1 | 6.5 | 10 | 0 | 0
1254 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.4 | 4 | 7 | 7 | 0 | 12 | 1 | 1 | 7 | 10 | 0 | 0
1254.05 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.5 | 5 | 7.5 | 7.5 | 0 | 12 | 1 | 1 | 7.5 | 10 | 0 | 0
1254.1 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.6 | 6 | 8 | 8 | 0 | 12 | 1 | 1 | 8 | 10 | 0 | 0
1254.15 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.7 | 7 | 8.5 | 8.5 | 0 | 12 | 1 | 1 | 8.5 | 10 | 0 | 0
1254.2 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.8 | 8 | 9 | 9 | 0 | 12 | 1 | 1 | 9 | 10 | 0 | 0
1254.25 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.9 | 9 | 9.5 | 9.5 | 0 | 12 | 1 | 1 | 9.5 | 10 | 0 | 0
1254.3 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1254.35 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1254.4 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1254.45 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1254.5 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1254.55 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1254.6 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1254.65 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1254.7 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1254.75 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1254.8 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1254.85 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1254.9 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1254.95 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1255 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1255.05 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1255.1 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1255.15 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1255.2 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1255.25 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1255.3 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1255.35 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1255.4 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1255.45 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1255.5 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1255.55 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1255.6 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1255.65 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1255.7 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1255.75 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1255.8 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1255.85 | 50.5 | 50.5 | -1 | 0.9 | 9 | 50.5 | -1 | -1 | -10 | -0.5 | -0.5 | 0 | 12 | 1 | 1 | -0.5 | 10 | 0 | 0
1255.9 | 50.5 | 50.5 | -1 | 0.8 | 8 | 50.5 | -1 | -1 | -10 | -1 | -1 | 0 | 12 | 1 | 1 | -1 | 10 | 0 | 0
1255.95 | 50.5 | 50.5 | -1 | 0.7 | 7 | 50.5 | -1 | -1 | -10 | -1.5 | -1.5 | 0 | 12 | 1 | 1 | -1.5 | 10 | 0 | 0
1256 | 50.5 | 50.5 | -1 | 0.6 | 6 | 50.5 | -1 | -1 | -10 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
1256.05 | 50.5 | 50.5 | -1 | 0.5 | 5 | 50.5 | -1 | -1 | -10 | -2.5 | -2.5 | 0 | 12 | 1 | 1 | -2.5 | 10 | 0 | 0
1256.1 | 50.5 | 50.5 | -1 | 0.4 | 4 | 50.5 | -1 | -1 | -10 | -3 | -3 | 0 | 12 | 1 | 1 | -3 | 10 | 0 | 0
1256.15 | 50.5 | 50.5 | -1 | 0.3 | 3 | 50.5 | -1 | -1 | -10 | -3.5 | -3.5 | 0 | 12 | 1 | 1 | -3.5 | 10 | 0 | 0
1256.2 | 50.5 | 50.5 | -1 | 0.2 | 2 | 50.5 | -1 | -1 | -10 | -4 | -4 | 0 | 12 | 1 | 1 | -4 | 10 | 0 | 0
1256.25 | 50.5 | 50.5 | -1 | 0.1 | 1 | 50.5 | -1 | -1 | -10 | -4.5 | -4.5 | 0 | 12 | 1 | 1 | -4.5 | 10 | 0 | 0
1256.3 | 50.5 | 50.5 | -1 | 0 | 0 | 50.5 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1256.35 | 50.5 | 50.5 | -1 | -0.1 | -1 | 50.5 | -1 | -1 | -10 | -5.5 | -5.5 | 0 | 12 | 1 | 1 | -5.5 | 10 | 0 | 0
1256.4 | 50.5 | 50.5 | -1 | -0.2 | -2 | 50.5 | -1 | -1 | -10 | -6 | -6 | 0 | 12 | 1 | 1 | -6 | 10 | 0 | 0
1256.45 | 50.5 | 50.5 | -1 | -0.3 | -3 | 50.5 | -1 | -1 | -10 | -6.5 | -6.5 | 0 | 12 | 1 | 1 | -6.5 | 10 | 0 | 0
1256.5 | 50.5 | 50.5 | -1 | -0.4 | -4 | 50.5 | -1 | -1 | -10 | -7 | -7 | 0 | 12 | 1 | 1 | -7 | 10 | 0 | 0
1256.55 | 50.5 | 50.5 | -1 | -0.5 | -5 | 50.5 | -1 | -1 | -10 | -7.5 | -7.5 | 0 | 12 | 1 | 1 | -7.5 | 10 | 0 | 0
1256.6 | 50.5 | 50.5 | -1 | -0.6 | -6 | 50.5 | -1 | -1 | -10 | -8 | -8 | 0 | 12 | 1 | 1 | -8 | 10 | 0 | 0
1256.65 | 50.5 | 50.5 | -1 | -0.7 | -7 | 50.5 | -1 | -1 | -10 | -8.5 | -8.5 | 0 | 12 | 1 | 1 | -8.5 | 10 | 0 | 0
1256.7 | 50.5 | 50.5 | -1 | -0.8 | -8 | 50.5 | -1 | -1 | -10 | -9 | -9 | 0 | 12 | 1 | 1 | -9 | 10 | 0 | 0
1256.75 | 50.5 | 50.5 | -1 | -0.9 | -9 | 50.5 | -1 | -1 | -10 | -9.5 | -9.5 | 0 | 12 | 1 | 1 | -9.5 | 10 | 0 | 0
1256.8 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1256.85 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1256.9 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1256.95 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1257 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1257.05 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1257.1 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1257.15 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1257.2 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1257.25 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1257.3 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1257.35 | 50.47 | 50.47 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1257.4 | 50.45 | 50.45 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1257.45 | 50.42 | 50.42 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1257.5 | 50.4 | 50.4 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1257.55 | 50.37 | 50.37 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1257.6 | 50.35 | 50.35 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1257.65 | 50.32 | 50.32 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1257.7 | 50.29 | 50.29 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1257.75 | 50.27 | 50.27 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1257.8 | 50.24 | 50.24 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1257.85 | 50.22 | 50.22 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1257.9 | 50.19 | 50.19 | -0.905 | -0.905 | -9.05 | 50.47 | -1 | -1 | -10 | -9.525 | -9.525 | 0 | 12 | 1 | 1 | -9.525 | 10 | 0 | 0
1257.95 | 50.17 | 50.17 | -0.715 | -0.715 | -7.15 | 50.45 | -1 | -1 | -10 | -8.575 | -8.575 | 0 | 12 | 1 | 1 | -8.575 | 10 | 0 | 0
1258 | 50.14 | 50.14 | -0.43 | -0.43 | -4.3 | 50.42 | -1 | -1 | -10 | -7.15 | -7.15 | 0 | 12 | 1 | 1 | -7.15 | 10 | 0 | 0
1258.05 | 50.12 | 50.12 | -0.24 | -0.24 | -2.4 | 50.4 | -1 | -1 | -10 | -6.2 | -6.2 | 0 | 12 | 1 | 1 | -6.2 | 10 | 0 | 0
1258.1 | 50.09 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 50.37 | -1 | -1 | -10 | -5.2206 | -5.2206 | 0 | 12 | 1 | 1 | -5.2206 | 10 | 0 | 0
1258.15 | 50.06 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.35 | -1 | -1 | -10 | -5.1324 | -5.1324 | 0 | 12 | 1 | 1 | -5.1324 | 10 | 0 | 0
1258.2 | 50.04 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.32 | -1 | -1 | -10 | -5.0735 | -5.0735 | 0 | 12 | 1 | 1 | -5.0735 | 10 | 0 | 0
1258.25 | 50.01 | 50.01 | 0 | 0 | 0 | 50.29 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1258.3 | 49.99 | 49.99 | 0 | 0 | 0 | 50.27 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1258.35 | 49.96 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.24 | -1 | -1 | -10 | -4.9265 | -4.9265 | 0 | 12 | 1 | 1 | -4.9265 | 10 | 0 | 0
1258.4 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.22 | -1 | -1 | -10 | -4.8676 | -4.8676 | 0 | 12 | 1 | 1 | -4.8676 | 10 | 0 | 0
1258.45 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.19 | -0.905 | -0.905 | -9.05 | -4.3044 | -4.3044 | 0 | 12 | 1 | 1 | -4.3044 | 10 | 0 | 0
1258.5 | 49.88 | 49.88 | 0.24 | 0.24 | 2.4 | 50.17 | -0.715 | -0.805 | -8.05 | -2.825 | -2.825 | 0 | 12 | 1 | 1 | -2.825 | 10 | 0 | 0
1258.55 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.14 | -0.43 | -0.705 | -7.05 | -1.375 | -1.375 | 0 | 12 | 1 | 1 | -1.375 | 10 | 0 | 0
1258.6 | 49.83 | 49.83 | 0.715 | 0.715 | 7.15 | 50.12 | -0.24 | -0.605 | -6.05 | 0.55 | 0.55 | 0 | 12 | 1 | 1 | 0.55 | 10 | 0 | 0
1258.65 | 49.81 | 49.81 | 0.905 | 0.905 | 9.05 | 50.09 | -0.044118 | -0.505 | -5.05 | 2 | 2 | 0 | 12 | 1 | 1 | 2 | 10 | 0 | 0
1258.7 | 49.78 | 49.78 | 1 | 1 | 10 | 50.06 | -0.026471 | -0.405 | -4.05 | 2.975 | 2.975 | 0 | 12 | 1 | 1 | 2.975 | 10 | 0 | 0
1258.75 | 49.76 | 49.76 | 1 | 1 | 10 | 50.04 | -0.014706 | -0.305 | -3.05 | 3.475 | 3.475 | 0 | 12 | 1 | 1 | 3.475 | 10 | 0 | 0
1258.8 | 49.73 | 49.73 | 1 | 1 | 10 | 50.01 | 0 | -0.205 | -2.05 | 3.975 | 3.975 | 0 | 12 | 1 | 1 | 3.975 | 10 | 0 | 0
1258.85 | 49.71 | 49.71 | 1 | 1 | 10 | 49.99 | 0 | -0.105 | -1.05 | 4.475 | 4.475 | 0 | 12 | 1 | 1 | 4.475 | 10 | 0 | 0
1258.9 | 49.68 | 49.68 | 1 | 1 | 10 | 49.96 | 0.014706 | -0.005 | -0.05 | 4.975 | 4.975 | 0 | 12 | 1 | 1 | 4.975 | 10 | 0 | 0
1258.95 | 49.65 | 49.65 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
1259 | 49.63 | 49.63 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1259.05 | 49.6 | 49.6 | 1 | 1 | 10 | 49.88 | 0.24 | 0.14412 | 1.4412 | 5.7206 | 5.7206 | 0 | 12 | 1 | 1 | 5.7206 | 10 | 0 | 0
1259.1 | 49.58 | 49.58 | 1 | 1 | 10 | 49.86 | 0.43 | 0.24412 | 2.4412 | 6.2206 | 6.2206 | 0 | 12 | 1 | 1 | 6.2206 | 10 | 0 | 0
1259.15 | 49.55 | 49.55 | 1 | 1 | 10 | 49.83 | 0.715 | 0.34412 | 3.4412 | 6.7206 | 6.7206 | 0 | 12 | 1 | 1 | 6.7206 | 10 | 0 | 0
1259.2 | 49.53 | 49.53 | 1 | 1 | 10 | 49.81 | 0.905 | 0.44412 | 4.4412 | 7.2206 | 7.2206 | 0 | 12 | 1 | 1 | 7.2206 | 10 | 0 | 0
1259.25 | 49.5 | 49.5 | 1 | 1 | 10 | 49.78 | 1 | 0.54412 | 5.4412 | 7.7206 | 7.7206 | 0 | 12 | 1 | 1 | 7.7206 | 10 | 0 | 0
1259.3 | 49.5 | 49.5 | 1 | 1 | 10 | 49.76 | 1 | 0.64412 | 6.4412 | 8.2206 | 8.2206 | 0 | 12 | 1 | 1 | 8.2206 | 10 | 0 | 0
1259.35 | 49.53 | 49.5 | 1 | 1 | 10 | 49.73 | 1 | 0.74412 | 7.4412 | 8.7206 | 8.7206 | 0 | 12 | 1 | 1 | 8.7206 | 10 | 0 | 0
1259.4 | 49.55 | 49.5 | 1 | 1 | 10 | 49.71 | 1 | 0.84412 | 8.4412 | 9.2206 | 9.2206 | 0 | 12 | 1 | 1 | 9.2206 | 10 | 0 | 0
1259.45 | 49.58 | 49.5 | 1 | 1 | 10 | 49.68 | 1 | 0.94412 | 9.4412 | 9.7206 | 9.7206 | 0 | 12 | 1 | 1 | 9.7206 | 10 | 0 | 0
1259.5 | 49.6 | 49.5 | 1 | 1 | 10 | 49.65 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1259.55 | 49.63 | 49.5 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1259.6 | 49.65 | 49.5 | 1 | 1 | 10 | 49.65 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1259.65 | 49.68 | 49.5 | 1 | 1 | 10 | 49.68 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1259.7 | 49.71 | 49.5 | 1 | 1 | 10 | 49.71 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1259.75 | 49.73 | 49.5 | 1 | 1 | 10 | 49.73 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1259.8 | 49.76 | 49.5 | 1 | 1 | 10 | 49.76 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1259.85 | 49.78 | 49.5 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1259.9 | 49.81 | 49.53 | 1 | 1 | 10 | 49.81 | 0.905 | 0.905 | 9.05 | 9.525 | 9.525 | 0 | 12 | 1 | 1 | 9.525 | 10 | 0 | 0
1259.95 | 49.83 | 49.55 | 1 | 1 | 10 | 49.83 | 0.715 | 0.715 | 7.15 | 8.575 | 8.575 | 0 | 12 | 1 | 1 | 8.575 | 10 | 0 | 0
1260 | 49.86 | 49.58 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
1260.05 | 49.88 | 49.6 | 1 | 1 | 10 | 49.88 | 0.24 | 0.24 | 2.4 | 6.2 | 6.2 | 0 | 12 | 1 | 1 | 6.2 | 10 | 0 | 0
1260.1 | 49.91 | 49.63 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1260.15 | 49.94 | 49.65 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
1260.2 | 49.96 | 49.68 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
1260.25 | 49.99 | 49.71 | 1 | 1 | 10 | 49.99 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1260.3 | 50.01 | 49.73 | 1 | 1 | 10 | 50.01 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1260.35 | 50.04 | 49.76 | 1 | 1 | 10 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 4.9265 | 4.9265 | 0 | 12 | 1 | 1 | 4.9265 | 10 | 0 | 0
1260.4 | 50.06 | 49.78 | 1 | 1 | 10 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 4.8676 | 4.8676 | 0 | 12 | 1 | 1 | 4.8676 | 10 | 0 | 0
1260.45 | 50.09 | 49.81 | 0.905 | 0.905 | 9.05 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 4.3044 | 4.3044 | 0 | 12 | 1 | 1 | 4.3044 | 10 | 0 | 0
1260.5 | 50.12 | 49.83 | 0.715 | 0.805 | 8.05 | 50.12 | -0.24 | -0.24 | -2.4 | 2.825 | 2.825 | 0 | 12 | 1 | 1 | 2.825 | 10 | 0 | 0
1260.55 | 50.14 | 49.86 | 0.43 | 0.705 | 7.05 | 50.14 | -0.43 | -0.43 | -4.3 | 1.375 | 1.375 | 0 | 12 | 1 | 1 | 1.375 | 10 | 0 | 0
1260.6 | 50.17 | 49.88 | 0.24 | 0.605 | 6.05 | 50.17 | -0.715 | -0.715 | -7.15 | -0.55 | -0.55 | 0 | 12 | 1 | 1 | -0.55 | 10 | 0 | 0
1260.65 | 50.19 | 49.91 | 0.044118 | 0.505 | 5.05 | 50.19 | -0.905 | -0.905 | -9.05 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
1260.7 | 50.22 | 49.94 | 0.026471 | 0.405 | 4.05 | 50.22 | -1 | -1 | -10 | -2.975 | -2.975 | 0 | 12 | 1 | 1 | -2.975 | 10 | 0 | 0
1260.75 | 50.24 | 49.96 | 0.014706 | 0.305 | 3.05 | 50.24 | -1 | -1 | -10 | -3.475 | -3.475 | 0 | 12 | 1 | 1 | -3.475 | 10 | 0 | 0
1260.8 | 50.27 | 49.99 | 0 | 0.205 | 2.05 | 50.27 | -1 | -1 | -10 | -3.975 | -3.975 | 0 | 12 | 1 | 1 | -3.975 | 10 | 0 | 0
1260.85 | 50.29 | 50.01 | 0 | 0.105 | 1.05 | 50.29 | -1 | -1 | -10 | -4.475 | -4.475 | 0 | 12 | 1 | 1 | -4.475 | 10 | 0 | 0
1260.9 | 50.32 | 50.04 | -0.014706 | 0.005 | 0.05 | 50.32 | -1 | -1 | -10 | -4.975 | -4.975 | 0 | 12 | 1 | 1 | -4.975 | 10 | 0 | 0
1260.95 | 50.35 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.35 | -1 | -1 | -10 | -5.1324 | -5.1324 | 0 | 12 | 1 | 1 | -5.1324 | 10 | 0 | 0
1261 | 50.37 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 50.37 | -1 | -1 | -10 | -5.2206 | -5.2206 | 0 | 12 | 1 | 1 | -5.2206 | 10 | 0 | 0
1261.05 | 50.4 | 50.12 | -0.24 | -0.14412 | -1.4412 | 50.4 | -1 | -1 | -10 | -5.7206 | -5.7206 | 0 | 12 | 1 | 1 | -5.7206 | 10 | 0 | 0
1261.1 | 50.42 | 50.14 | -0.43 | -0.24412 | -2.4412 | 50.42 | -1 | -1 | -10 | -6.2206 | -6.2206 | 0 | 12 | 1 | 1 | -6.2206 | 10 | 0 | 0
1261.15 | 50.45 | 50.17 | -0.715 | -0.34412 | -3.4412 | 50.45 | -1 | -1 | -10 | -6.7206 | -6.7206 | 0 | 12 | 1 | 1 | -6.7206 | 10 | 0 | 0
1261.2 | 50.47 | 50.19 | -0.905 | -0.44412 | -4.4412 | 50.47 | -1 | -1 | -10 | -7.2206 | -7.2206 | 0 | 12 | 1 | 1 | -7.2206 | 10 | 0 | 0
1261.25 | 50.5 | 50.22 | -1 | -0.54412 | -5.4412 | 50.5 | -1 | -1 | -10 | -7.7206 | -7.7206 | 0 | 12 | 1 | 1 | -7.7206 | 10 | 0 | 0
1261.3 | 50.5 | 50.24 | -1 | -0.64412 | -6.4412 | 50.5 | -1 | -1 | -10 | -8.2206 | -8.2206 | 0 | 12 | 1 | 1 | -8.2206 | 10 | 0 | 0
1261.35 | 50.47 | 50.27 | -1 | -0.74412 | -7.4412 | 50.5 | -1 | -1 | -10 | -8.7206 | -8.7206 | 0 | 12 | 1 | 1 | -8.7206 | 10 | 0 | 0
1261.4 | 50.45 | 50.29 | -1 | -0.84412 | -8.4412 | 50.5 | -1 | -1 | -10 | -9.2206 | -9.2206 | 0 | 12 | 1 | 1 | -9.2206 | 10 | 0 | 0
1261.45 | 50.42 | 50.32 | -1 | -0.94412 | -9.4412 | 50.5 | -1 | -1 | -10 | -9.7206 | -9.7206 | 0 | 12 | 1 | 1 | -9.7206 | 10 | 0 | 0
1261.5 | 50.39 | 50.35 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1261.55 | 50.37 | 50.37 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1261.6 | 50.34 | 50.34 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1261.65 | 50.32 | 50.32 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1261.7 | 50.29 | 50.29 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1261.75 | 50.26 | 50.26 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1261.8 | 50.24 | 50.24 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1261.85 | 50.21 | 50.21 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1261.9 | 50.18 | 50.18 | -0.81 | -0.81 | -8.1 | 50.47 | -1 | -1 | -10 | -9.05 | -9.05 | 0 | 12 | 1 | 1 | -9.05 | 10 | 0 | 0
1261.95 | 50.16 | 50.16 | -0.62 | -0.62 | -6.2 | 50.45 | -1 | -1 | -10 | -8.1 | -8.1 | 0 | 12 | 1 | 1 | -8.1 | 10 | 0 | 0
1262 | 50.13 | 50.13 | -0.335 | -0.335 | -3.35 | 50.42 | -1 | -1 | -10 | -6.675 | -6.675 | 0 | 12 | 1 | 1 | -6.675 | 10 | 0 | 0
1262.05 | 50.11 | 50.11 | -0.145 | -0.145 | -1.45 | 50.39 | -1 | -1 | -10 | -5.725 | -5.725 | 0 | 12 | 1 | 1 | -5.725 | 10 | 0 | 0
1262.1 | 50.08 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 50.37 | -1 | -1 | -10 | -5.1912 | -5.1912 | 0 | 12 | 1 | 1 | -5.1912 | 10 | 0 | 0
1262.15 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.34 | -1 | -1 | -10 | -5.1029 | -5.1029 | 0 | 12 | 1 | 1 | -5.1029 | 10 | 0 | 0
1262.2 | 50.03 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 50.32 | -1 | -1 | -10 | -5.0441 | -5.0441 | 0 | 12 | 1 | 1 | -5.0441 | 10 | 0 | 0
1262.25 | 50 | 50 | 0 | 0 | 0 | 50.29 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1262.3 | 50 | 50 | 0 | 0 | 0 | 50.26 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1262.35 | 50 | 50 | 0 | 0 | 0 | 50.24 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1262.4 | 50 | 50 | 0 | 0 | 0 | 50.21 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1262.45 | 50 | 50 | 0 | 0 | 0 | 50.18 | -0.81 | -0.9 | -9 | -4.5 | -4.5 | 0 | 12 | 1 | 1 | -4.5 | 10 | 0 | 0
1262.5 | 50 | 50 | 0 | 0 | 0 | 50.16 | -0.62 | -0.8 | -8 | -4 | -4 | 0 | 12 | 1 | 1 | -4 | 10 | 0 | 0
1262.55 | 50 | 50 | 0 | 0 | 0 | 50.13 | -0.335 | -0.7 | -7 | -3.5 | -3.5 | 0 | 12 | 1 | 1 | -3.5 | 10 | 0 | 0
1262.6 | 50.01 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.6 | -6 | -3 | -3 | 0 | 12 | 1 | 1 | -3 | 10 | 0 | 0
1262.65 | 50.01 | 50 | 0 | 0 | 0 | 50.08 | -0.038235 | -0.5 | -5 | -2.5 | -2.5 | 0 | 12 | 1 | 1 | -2.5 | 10 | 0 | 0
1262.7 | 49.99 | 49.99 | 0 | 0 | 0 | 50.05 | -0.020588 | -0.4 | -4 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
1262.75 | 49.99 | 49.99 | 0 | 0 | 0 | 50.03 | -0.0088235 | -0.3 | -3 | -1.5 | -1.5 | 0 | 12 | 1 | 1 | -1.5 | 10 | 0 | 0
1262.8 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | -0.2 | -2 | -0.83824 | -0.83824 | 0 | 12 | 1 | 1 | -0.83824 | 10 | 0 | 0
1262.85 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | -0.1 | -1 | -0.33824 | -0.33824 | 0 | 12 | 1 | 1 | -0.33824 | 10 | 0 | 0
1262.9 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
1262.95 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
1263 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
1263.05 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
1263.1 | 49.89 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
1263.15 | 49.89 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
1263.2 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50.01 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1263.25 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1263.3 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1263.35 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 2.7868 | 2.7868 | 0 | 12 | 1 | 1 | 2.7868 | 10 | 0 | 0
1263.4 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 2.7868 | 2.7868 | 0 | 12 | 1 | 1 | 2.7868 | 10 | 0 | 0
1263.45 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 2.8456 | 2.8456 | 0 | 12 | 1 | 1 | 2.8456 | 10 | 0 | 0
1263.5 | 49.94 | 49.85 | 0.525 | 0.525 | 5.25 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 2.7574 | 2.7574 | 0 | 12 | 1 | 1 | 2.7574 | 10 | 0 | 0
1263.55 | 49.94 | 49.85 | 0.525 | 0.525 | 5.25 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 2.7574 | 2.7574 | 0 | 12 | 1 | 1 | 2.7574 | 10 | 0 | 0
1263.6 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1263.65 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1263.7 | 49.93 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1263.75 | 49.93 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1263.8 | 49.96 | 49.85 | 0.525 | 0.525 | 5.25 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 2.6985 | 2.6985 | 0 | 12 | 1 | 1 | 2.6985 | 10 | 0 | 0
1263.85 | 49.96 | 49.85 | 0.525 | 0.525 | 5.25 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 2.6985 | 2.6985 | 0 | 12 | 1 | 1 | 2.6985 | 10 | 0 | 0
1263.9 | 49.99 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1263.95 | 49.99 | 49.91 | 0.044118 | 0.425 | 4.25 | 49.99 | 0 | 0 | 0 | 2.125 | 2.125 | 0 | 12 | 1 | 1 | 2.125 | 10 | 0 | 0
1264 | 49.99 | 49.91 | 0.044118 | 0.325 | 3.25 | 49.99 | 0 | 0 | 0 | 1.625 | 1.625 | 0 | 12 | 1 | 1 | 1.625 | 10 | 0 | 0
1264.05 | 49.99 | 49.93 | 0.032353 | 0.225 | 2.25 | 49.99 | 0 | 0 | 0 | 1.125 | 1.125 | 0 | 12 | 1 | 1 | 1.125 | 10 | 0 | 0
1264.1 | 49.96 | 49.93 | 0.032353 | 0.125 | 1.25 | 49.99 | 0 | 0 | 0 | 0.625 | 0.625 | 0 | 12 | 1 | 1 | 0.625 | 10 | 0 | 0
1264.15 | 49.96 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 49.99 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1264.2 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1264.25 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1264.3 | 50.05 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.058824 | 0.058824 | 0 | 12 | 1 | 1 | 0.058824 | 10 | 0 | 0
1264.35 | 50.05 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
1264.4 | 49.97 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
1264.45 | 49.97 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
1264.5 | 49.92 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1264.55 | 49.92 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1264.6 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1264.65 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1264.7 | 49.94 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1264.75 | 49.94 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1264.8 | 50.01 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1264.85 | 50.01 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1264.9 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1264.95 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
1265 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
1265.05 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
1265.1 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
1265.15 | 49.95 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
1265.2 | 49.97 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
1265.25 | 49.97 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
1265.3 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
1265.35 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
1265.4 | 49.87 | 49.87 | 0.335 | 0.335 | 3.35 | 50.01 | 0 | 0 | 0 | 1.675 | 1.675 | 0 | 12 | 1 | 1 | 1.675 | 10 | 0 | 0
1265.45 | 49.87 | 49.87 | 0.335 | 0.335 | 3.35 | 49.99 | 0 | 0 | 0 | 1.675 | 1.675 | 0 | 12 | 1 | 1 | 1.675 | 10 | 0 | 0
1265.5 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1265.55 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 2.6691 | 2.6691 | 0 | 12 | 1 | 1 | 2.6691 | 10 | 0 | 0
1265.6 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1265.65 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1265.7 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1265.75 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1265.8 | 49.84 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1265.85 | 49.84 | 49.79 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
1265.9 | 49.89 | 49.79 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
1265.95 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.12647 | 1.2647 | 5.6324 | 5.6324 | 0 | 12 | 1 | 1 | 5.6324 | 10 | 0 | 0
1266 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.145 | 1.45 | 5.725 | 5.725 | 0 | 12 | 1 | 1 | 5.725 | 10 | 0 | 0
1266.05 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.145 | 1.45 | 5.725 | 5.725 | 0 | 12 | 1 | 1 | 5.725 | 10 | 0 | 0
1266.1 | 49.96 | 49.79 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
1266.15 | 49.96 | 49.79 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
1266.2 | 50.02 | 49.79 | 1 | 1 | 10 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 4.9853 | 4.9853 | 0 | 12 | 1 | 1 | 4.9853 | 10 | 0 | 0
1266.25 | 50.02 | 49.79 | 1 | 1 | 10 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 4.9853 | 4.9853 | 0 | 12 | 1 | 1 | 4.9853 | 10 | 0 | 0
1266.3 | 50.03 | 49.79 | 1 | 1 | 10 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.9559 | 4.9559 | 0 | 12 | 1 | 1 | 4.9559 | 10 | 0 | 0
1266.35 | 50.03 | 49.84 | 0.62 | 0.9 | 9 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.4559 | 4.4559 | 0 | 12 | 1 | 1 | 4.4559 | 10 | 0 | 0
1266.4 | 50.02 | 49.84 | 0.62 | 0.8 | 8 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 3.9559 | 3.9559 | 0 | 12 | 1 | 1 | 3.9559 | 10 | 0 | 0
1266.45 | 50.02 | 49.89 | 0.145 | 0.7 | 7 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 3.4559 | 3.4559 | 0 | 12 | 1 | 1 | 3.4559 | 10 | 0 | 0
1266.5 | 50.08 | 49.89 | 0.145 | 0.6 | 6 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 2.8088 | 2.8088 | 0 | 12 | 1 | 1 | 2.8088 | 10 | 0 | 0
1266.55 | 50.08 | 49.89 | 0.145 | 0.5 | 5 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 2.3088 | 2.3088 | 0 | 12 | 1 | 1 | 2.3088 | 10 | 0 | 0
1266.6 | 50.01 | 49.89 | 0.145 | 0.4 | 4 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 1.8088 | 1.8088 | 0 | 12 | 1 | 1 | 1.8088 | 10 | 0 | 0
1266.65 | 50.01 | 49.96 | 0.014706 | 0.3 | 3 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 1.3088 | 1.3088 | 0 | 12 | 1 | 1 | 1.3088 | 10 | 0 | 0
1266.7 | 49.94 | 49.94 | 0.026471 | 0.2 | 2 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.80882 | 0.80882 | 0 | 12 | 1 | 1 | 0.80882 | 10 | 0 | 0
1266.75 | 49.94 | 49.94 | 0.026471 | 0.1 | 1 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.30882 | 0.30882 | 0 | 12 | 1 | 1 | 0.30882 | 10 | 0 | 0
1266.8 | 50 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
1266.85 | 50 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
1266.9 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
1266.95 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
1267 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1267.05 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1267.1 | 49.92 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1267.15 | 49.92 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
1267.2 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50.01 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1267.25 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1267.3 | 49.92 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1267.35 | 49.92 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1267.4 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1267.45 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1267.5 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1267.55 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1267.6 | 49.87 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1267.65 | 49.87 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1267.7 | 49.8 | 49.8 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1267.75 | 49.8 | 49.8 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1267.8 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1267.85 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1267.9 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1267.95 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1268 | 49.72 | 49.72 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1268.05 | 49.72 | 49.72 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1268.1 | 49.67 | 49.67 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1268.15 | 49.67 | 49.67 | 1 | 1 | 10 | 49.87 | 0.335 | 0.14412 | 1.4412 | 5.7206 | 5.7206 | 0 | 12 | 1 | 1 | 5.7206 | 10 | 0 | 0
1268.2 | 49.65 | 49.65 | 1 | 1 | 10 | 49.87 | 0.335 | 0.24412 | 2.4412 | 6.2206 | 6.2206 | 0 | 12 | 1 | 1 | 6.2206 | 10 | 0 | 0
1268.25 | 49.65 | 49.65 | 1 | 1 | 10 | 49.8 | 1 | 0.34412 | 3.4412 | 6.7206 | 6.7206 | 0 | 12 | 1 | 1 | 6.7206 | 10 | 0 | 0
1268.3 | 49.59 | 49.59 | 1 | 1 | 10 | 49.8 | 1 | 0.44412 | 4.4412 | 7.2206 | 7.2206 | 0 | 12 | 1 | 1 | 7.2206 | 10 | 0 | 0
1268.35 | 49.59 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.54412 | 5.4412 | 7.7206 | 7.7206 | 0 | 12 | 1 | 1 | 7.7206 | 10 | 0 | 0
1268.4 | 49.66 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.64412 | 6.4412 | 8.2206 | 8.2206 | 0 | 12 | 1 | 1 | 8.2206 | 10 | 0 | 0
1268.45 | 49.66 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.74412 | 7.4412 | 8.7206 | 8.7206 | 0 | 12 | 1 | 1 | 8.7206 | 10 | 0 | 0
1268.5 | 49.63 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.84412 | 8.4412 | 9.2206 | 9.2206 | 0 | 12 | 1 | 1 | 9.2206 | 10 | 0 | 0
1268.55 | 49.63 | 49.59 | 1 | 1 | 10 | 49.72 | 1 | 0.94412 | 9.4412 | 9.7206 | 9.7206 | 0 | 12 | 1 | 1 | 9.7206 | 10 | 0 | 0
1268.6 | 49.61 | 49.59 | 1 | 1 | 10 | 49.72 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1268.65 | 49.61 | 49.59 | 1 | 1 | 10 | 49.67 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1268.7 | 49.54 | 49.54 | 1 | 1 | 10 | 49.67 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1268.75 | 49.54 | 49.54 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1268.8 | 49.46 | 49.46 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1268.85 | 49.46 | 49.46 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1268.9 | 49.45 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1268.95 | 49.45 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1269 | 49.51 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1269.05 | 49.51 | 49.45 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1269.1 | 49.5 | 49.45 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1269.15 | 49.5 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1269.2 | 49.54 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1269.25 | 49.54 | 49.45 | 1 | 1 | 10 | 49.54 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1269.3 | 49.59 | 49.45 | 1 | 1 | 10 | 49.59 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1269.35 | 49.59 | 49.45 | 1 | 1 | 10 | 49.59 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1269.4 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1269.45 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1269.5 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1269.55 | 49.61 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1269.6 | 49.53 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1269.65 | 49.53 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1269.7 | 49.54 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1269.75 | 49.54 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1269.8 | 49.61 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1269.85 | 49.61 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1269.9 | 49.66 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1269.95 | 49.66 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1270 | 49.64 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1270.05 | 49.64 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1270.1 | 49.69 | 49.53 | 1 | 1 | 10 | 49.69 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1270.15 | 49.69 | 49.53 | 1 | 1 | 10 | 49.69 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1270.2 | 49.74 | 49.53 | 1 | 1 | 10 | 49.74 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1270.25 | 49.74 | 49.54 | 1 | 1 | 10 | 49.74 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1270.3 | 49.78 | 49.54 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1270.35 | 49.78 | 49.61 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1270.4 | 49.82 | 49.61 | 1 | 1 | 10 | 49.82 | 0.81 | 0.81 | 8.1 | 9.05 | 9.05 | 0 | 12 | 1 | 1 | 9.05 | 10 | 0 | 0
1270.45 | 49.82 | 49.64 | 1 | 1 | 10 | 49.82 | 0.81 | 0.81 | 8.1 | 9.05 | 9.05 | 0 | 12 | 1 | 1 | 9.05 | 10 | 0 | 0
1270.5 | 49.86 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
1270.55 | 49.86 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
1270.6 | 49.84 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
1270.65 | 49.84 | 49.69 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
1270.7 | 49.91 | 49.69 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1270.75 | 49.91 | 49.74 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1270.8 | 49.97 | 49.74 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1270.85 | 49.97 | 49.78 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1270.9 | 50.03 | 49.78 | 1 | 1 | 10 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.9559 | 4.9559 | 0 | 12 | 1 | 1 | 4.9559 | 10 | 0 | 0
1270.95 | 50.03 | 49.82 | 0.81 | 0.9 | 9 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.4559 | 4.4559 | 0 | 12 | 1 | 1 | 4.4559 | 10 | 0 | 0
1271 | 50.05 | 49.82 | 0.81 | 0.81 | 8.1 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 3.9471 | 3.9471 | 0 | 12 | 1 | 1 | 3.9471 | 10 | 0 | 0
1271.05 | 50.05 | 49.84 | 0.62 | 0.71 | 7.1 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 3.4471 | 3.4471 | 0 | 12 | 1 | 1 | 3.4471 | 10 | 0 | 0
1271.1 | 50.01 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
1271.15 | 50.01 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
1271.2 | 49.95 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
1271.25 | 49.95 | 49.91 | 0.044118 | 0.52 | 5.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.4971 | 2.4971 | 0 | 12 | 1 | 1 | 2.4971 | 10 | 0 | 0
1271.3 | 49.99 | 49.91 | 0.044118 | 0.42 | 4.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 1.9971 | 1.9971 | 0 | 12 | 1 | 1 | 1.9971 | 10 | 0 | 0
1271.35 | 49.99 | 49.95 | 0.020588 | 0.32 | 3.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 1.4971 | 1.4971 | 0 | 12 | 1 | 1 | 1.4971 | 10 | 0 | 0
1271.4 | 49.92 | 49.92 | 0.038235 | 0.22 | 2.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.99706 | 0.99706 | 0 | 12 | 1 | 1 | 0.99706 | 10 | 0 | 0
1271.45 | 49.92 | 49.92 | 0.038235 | 0.12 | 1.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.49706 | 0.49706 | 0 | 12 | 1 | 1 | 0.49706 | 10 | 0 | 0
1271.5 | 49.97 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1271.55 | 49.97 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1271.6 | 50.02 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1271.65 | 50.02 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.17647 | 0.17647 | 0 | 12 | 1 | 1 | 0.17647 | 10 | 0 | 0
1271.7 | 50.07 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1271.75 | 50.07 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1271.8 | 50.06 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1271.85 | 50.06 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1271.9 | 50.13 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
1271.95 | 50.13 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
1272 | 50.09 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
1272.05 | 50.09 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6309 | -1.6309 | 0 | 12 | 1 | 1 | -1.6309 | 10 | 0 | 0
1272.1 | 50.07 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6309 | -1.6309 | 0 | 12 | 1 | 1 | -1.6309 | 10 | 0 | 0
1272.15 | 50.07 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6897 | -1.6897 | 0 | 12 | 1 | 1 | -1.6897 | 10 | 0 | 0
1272.2 | 50.07 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6897 | -1.6897 | 0 | 12 | 1 | 1 | -1.6897 | 10 | 0 | 0
1272.25 | 50.07 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.13 | -0.335 | -0.335 | -3.35 | -1.8074 | -1.8074 | 0 | 12 | 1 | 1 | -1.8074 | 10 | 0 | 0
1272.3 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.13 | -0.335 | -0.335 | -3.35 | -1.7779 | -1.7779 | 0 | 12 | 1 | 1 | -1.7779 | 10 | 0 | 0
1272.35 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.13 | -0.335 | -0.335 | -3.35 | -1.7779 | -1.7779 | 0 | 12 | 1 | 1 | -1.7779 | 10 | 0 | 0
1272.4 | 50.01 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
1272.45 | 50.01 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
1272.5 | 50.07 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
1272.55 | 50.07 | 50.01 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.235 | -2.35 | -1.175 | -1.175 | 0 | 12 | 1 | 1 | -1.175 | 10 | 0 | 0
1272.6 | 50.05 | 50.01 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.135 | -1.35 | -0.675 | -0.675 | 0 | 12 | 1 | 1 | -0.675 | 10 | 0 | 0
1272.65 | 50.05 | 50.01 | 0 | 0 | 0 | 50.07 | -0.032353 | -0.035 | -0.35 | -0.175 | -0.175 | 0 | 12 | 1 | 1 | -0.175 | 10 | 0 | 0
1272.7 | 50.1 | 50.01 | 0 | 0 | 0 | 50.1 | -0.05 | -0.05 | -0.5 | -0.25 | -0.25 | 0 | 12 | 1 | 1 | -0.25 | 10 | 0 | 0
1272.75 | 50.1 | 50.01 | 0 | 0 | 0 | 50.1 | -0.05 | -0.05 | -0.5 | -0.25 | -0.25 | 0 | 12 | 1 | 1 | -0.25 | 10 | 0 | 0
1272.8 | 50.11 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1272.85 | 50.11 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1272.9 | 50.06 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1272.95 | 50.06 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1273 | 50.04 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1273.05 | 50.04 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1273.1 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1273.15 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1273.2 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1273.25 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1273.3 | 50.11 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1273.35 | 50.11 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1273.4 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1273.45 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1273.5 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1273.55 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1273.6 | 50.02 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.11 | -0.145 | -0.145 | -1.45 | -0.73971 | -0.73971 | 0 | 12 | 1 | 1 | -0.73971 | 10 | 0 | 0
1273.65 | 50.02 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.11 | -0.145 | -0.145 | -1.45 | -0.73971 | -0.73971 | 0 | 12 | 1 | 1 | -0.73971 | 10 | 0 | 0
1273.7 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1273.75 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1273.8 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1273.85 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1273.9 | 50.01 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1273.95 | 50.01 | 50 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.045 | -0.45 | -0.225 | -0.225 | 0 | 12 | 1 | 1 | -0.225 | 10 | 0 | 0
1274 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
1274.05 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
1274.1 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
1274.15 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1274.2 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.14706 | 0.14706 | 0 | 12 | 1 | 1 | 0.14706 | 10 | 0 | 0
1274.25 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1274.3 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1274.35 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1274.4 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1274.45 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1274.5 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1274.55 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1274.6 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1274.65 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1274.7 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1274.75 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1274.8 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1274.85 | 50 | 50 | 0 | 0 | 0 | 50.01 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1274.9 | 49.5 | 49.5 | 1 | 1 | 10 | 50.01 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1274.95 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1275 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1275.05 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1275.1 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1275.15 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1275.2 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1275.25 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1275.3 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1275.35 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1275.4 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1275.45 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.1 | 1 | 5.5 | 5.5 | 0 | 12 | 1 | 1 | 5.5 | 10 | 0 | 0
1275.5 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.2 | 2 | 6 | 6 | 0 | 12 | 1 | 1 | 6 | 10 | 0 | 0
1275.55 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.3 | 3 | 6.5 | 6.5 | 0 | 12 | 1 | 1 | 6.5 | 10 | 0 | 0
1275.6 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.4 | 4 | 7 | 7 | 0 | 12 | 1 | 1 | 7 | 10 | 0 | 0
1275.65 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.5 | 5 | 7.5 | 7.5 | 0 | 12 | 1 | 1 | 7.5 | 10 | 0 | 0
1275.7 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.6 | 6 | 8 | 8 | 0 | 12 | 1 | 1 | 8 | 10 | 0 | 0
1275.75 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.7 | 7 | 8.5 | 8.5 | 0 | 12 | 1 | 1 | 8.5 | 10 | 0 | 0
1275.8 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.8 | 8 | 9 | 9 | 0 | 12 | 1 | 1 | 9 | 10 | 0 | 0
1275.85 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.9 | 9 | 9.5 | 9.5 | 0 | 12 | 1 | 1 | 9.5 | 10 | 0 | 0
1275.9 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1275.95 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1276 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1276.05 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1276.1 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1276.15 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1276.2 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1276.25 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1276.3 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1276.35 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1276.4 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1276.45 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1276.5 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1276.55 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1276.6 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1276.65 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1276.7 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1276.75 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1276.8 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1276.85 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1276.9 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1276.95 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1277 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1277.05 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1277.1 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1277.15 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1277.2 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1277.25 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1277.3 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1277.35 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1277.4 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1277.45 | 50.5 | 50.5 | -1 | 0.9 | 9 | 50.5 | -1 | -1 | -10 | -0.5 | -0.5 | 0 | 12 | 1 | 1 | -0.5 | 10 | 0 | 0
1277.5 | 50.5 | 50.5 | -1 | 0.8 | 8 | 50.5 | -1 | -1 | -10 | -1 | -1 | 0 | 12 | 1 | 1 | -1 | 10 | 0 | 0
1277.55 | 50.5 | 50.5 | -1 | 0.7 | 7 | 50.5 | -1 | -1 | -10 | -1.5 | -1.5 | 0 | 12 | 1 | 1 | -1.5 | 10 | 0 | 0
1277.6 | 50.5 | 50.5 | -1 | 0.6 | 6 | 50.5 | -1 | -1 | -10 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
1277.65 | 50.5 | 50.5 | -1 | 0.5 | 5 | 50.5 | -1 | -1 | -10 | -2.5 | -2.5 | 0 | 12 | 1 | 1 | -2.5 | 10 | 0 | 0
1277.7 | 50.5 | 50.5 | -1 | 0.4 | 4 | 50.5 | -1 | -1 | -10 | -3 | -3 | 0 | 12 | 1 | 1 | -3 | 10 | 0 | 0
1277.75 | 50.5 | 50.5 | -1 | 0.3 | 3 | 50.5 | -1 | -1 | -10 | -3.5 | -3.5 | 0 | 12 | 1 | 1 | -3.5 | 10 | 0 | 0
1277.8 | 50.5 | 50.5 | -1 | 0.2 | 2 | 50.5 | -1 | -1 | -10 | -4 | -4 | 0 | 12 | 1 | 1 | -4 | 10 | 0 | 0
1277.85 | 50.5 | 50.5 | -1 | 0.1 | 1 | 50.5 | -1 | -1 | -10 | -4.5 | -4.5 | 0 | 12 | 1 | 1 | -4.5 | 10 | 0 | 0
1277.9 | 50.5 | 50.5 | -1 | 0 | 0 | 50.5 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1277.95 | 50.5 | 50.5 | -1 | -0.1 | -1 | 50.5 | -1 | -1 | -10 | -5.5 | -5.5 | 0 | 12 | 1 | 1 | -5.5 | 10 | 0 | 0
1278 | 50.5 | 50.5 | -1 | -0.2 | -2 | 50.5 | -1 | -1 | -10 | -6 | -6 | 0 | 12 | 1 | 1 | -6 | 10 | 0 | 0
1278.05 | 50.5 | 50.5 | -1 | -0.3 | -3 | 50.5 | -1 | -1 | -10 | -6.5 | -6.5 | 0 | 12 | 1 | 1 | -6.5 | 10 | 0 | 0
1278.1 | 50.5 | 50.5 | -1 | -0.4 | -4 | 50.5 | -1 | -1 | -10 | -7 | -7 | 0 | 12 | 1 | 1 | -7 | 10 | 0 | 0
1278.15 | 50.5 | 50.5 | -1 | -0.5 | -5 | 50.5 | -1 | -1 | -10 | -7.5 | -7.5 | 0 | 12 | 1 | 1 | -7.5 | 10 | 0 | 0
1278.2 | 50.5 | 50.5 | -1 | -0.6 | -6 | 50.5 | -1 | -1 | -10 | -8 | -8 | 0 | 12 | 1 | 1 | -8 | 10 | 0 | 0
1278.25 | 50.5 | 50.5 | -1 | -0.7 | -7 | 50.5 | -1 | -1 | -10 | -8.5 | -8.5 | 0 | 12 | 1 | 1 | -8.5 | 10 | 0 | 0
1278.3 | 50.5 | 50.5 | -1 | -0.8 | -8 | 50.5 | -1 | -1 | -10 | -9 | -9 | 0 | 12 | 1 | 1 | -9 | 10 | 0 | 0
1278.35 | 50.5 | 50.5 | -1 | -0.9 | -9 | 50.5 | -1 | -1 | -10 | -9.5 | -9.5 | 0 | 12 | 1 | 1 | -9.5 | 10 | 0 | 0
1278.4 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1278.45 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1278.5 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1278.55 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1278.6 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1278.65 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1278.7 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1278.75 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1278.8 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1278.85 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1278.9 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1278.95 | 50.47 | 50.47 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1279 | 50.45 | 50.45 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1279.05 | 50.42 | 50.42 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1279.1 | 50.4 | 50.4 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1279.15 | 50.37 | 50.37 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1279.2 | 50.35 | 50.35 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1279.25 | 50.32 | 50.32 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1279.3 | 50.29 | 50.29 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1279.35 | 50.27 | 50.27 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1279.4 | 50.24 | 50.24 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1279.45 | 50.22 | 50.22 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1279.5 | 50.19 | 50.19 | -0.905 | -0.905 | -9.05 | 50.47 | -1 | -1 | -10 | -9.525 | -9.525 | 0 | 12 | 1 | 1 | -9.525 | 10 | 0 | 0
1279.55 | 50.17 | 50.17 | -0.715 | -0.715 | -7.15 | 50.45 | -1 | -1 | -10 | -8.575 | -8.575 | 0 | 12 | 1 | 1 | -8.575 | 10 | 0 | 0
1279.6 | 50.14 | 50.14 | -0.43 | -0.43 | -4.3 | 50.42 | -1 | -1 | -10 | -7.15 | -7.15 | 0 | 12 | 1 | 1 | -7.15 | 10 | 0 | 0
1279.65 | 50.12 | 50.12 | -0.24 | -0.24 | -2.4 | 50.4 | -1 | -1 | -10 | -6.2 | -6.2 | 0 | 12 | 1 | 1 | -6.2 | 10 | 0 | 0
1279.7 | 50.09 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 50.37 | -1 | -1 | -10 | -5.2206 | -5.2206 | 0 | 12 | 1 | 1 | -5.2206 | 10 | 0 | 0
1279.75 | 50.06 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.35 | -1 | -1 | -10 | -5.1324 | -5.1324 | 0 | 12 | 1 | 1 | -5.1324 | 10 | 0 | 0
1279.8 | 50.04 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.32 | -1 | -1 | -10 | -5.0735 | -5.0735 | 0 | 12 | 1 | 1 | -5.0735 | 10 | 0 | 0
1279.85 | 50.01 | 50.01 | 0 | 0 | 0 | 50.29 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1279.9 | 49.99 | 49.99 | 0 | 0 | 0 | 50.27 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1279.95 | 49.96 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.24 | -1 | -1 | -10 | -4.9265 | -4.9265 | 0 | 12 | 1 | 1 | -4.9265 | 10 | 0 | 0
1280 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.22 | -1 | -1 | -10 | -4.8676 | -4.8676 | 0 | 12 | 1 | 1 | -4.8676 | 10 | 0 | 0
1280.05 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.19 | -0.905 | -0.905 | -9.05 | -4.3044 | -4.3044 | 0 | 12 | 1 | 1 | -4.3044 | 10 | 0 | 0
1280.1 | 49.88 | 49.88 | 0.24 | 0.24 | 2.4 | 50.17 | -0.715 | -0.805 | -8.05 | -2.825 | -2.825 | 0 | 12 | 1 | 1 | -2.825 | 10 | 0 | 0
1280.15 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.14 | -0.43 | -0.705 | -7.05 | -1.375 | -1.375 | 0 | 12 | 1 | 1 | -1.375 | 10 | 0 | 0
1280.2 | 49.83 | 49.83 | 0.715 | 0.715 | 7.15 | 50.12 | -0.24 | -0.605 | -6.05 | 0.55 | 0.55 | 0 | 12 | 1 | 1 | 0.55 | 10 | 0 | 0
1280.25 | 49.81 | 49.81 | 0.905 | 0.905 | 9.05 | 50.09 | -0.044118 | -0.505 | -5.05 | 2 | 2 | 0 | 12 | 1 | 1 | 2 | 10 | 0 | 0
1280.3 | 49.78 | 49.78 | 1 | 1 | 10 | 50.06 | -0.026471 | -0.405 | -4.05 | 2.975 | 2.975 | 0 | 12 | 1 | 1 | 2.975 | 10 | 0 | 0
1280.35 | 49.76 | 49.76 | 1 | 1 | 10 | 50.04 | -0.014706 | -0.305 | -3.05 | 3.475 | 3.475 | 0 | 12 | 1 | 1 | 3.475 | 10 | 0 | 0
1280.4 | 49.73 | 49.73 | 1 | 1 | 10 | 50.01 | 0 | -0.205 | -2.05 | 3.975 | 3.975 | 0 | 12 | 1 | 1 | 3.975 | 10 | 0 | 0
1280.45 | 49.71 | 49.71 | 1 | 1 | 10 | 49.99 | 0 | -0.105 | -1.05 | 4.475 | 4.475 | 0 | 12 | 1 | 1 | 4.475 | 10 | 0 | 0
1280.5 | 49.68 | 49.68 | 1 | 1 | 10 | 49.96 | 0.014706 | -0.005 | -0.05 | 4.975 | 4.975 | 0 | 12 | 1 | 1 | 4.975 | 10 | 0 | 0
1280.55 | 49.65 | 49.65 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
1280.6 | 49.63 | 49.63 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1280.65 | 49.6 | 49.6 | 1 | 1 | 10 | 49.88 | 0.24 | 0.14412 | 1.4412 | 5.7206 | 5.7206 | 0 | 12 | 1 | 1 | 5.7206 | 10 | 0 | 0
1280.7 | 49.58 | 49.58 | 1 | 1 | 10 | 49.86 | 0.43 | 0.24412 | 2.4412 | 6.2206 | 6.2206 | 0 | 12 | 1 | 1 | 6.2206 | 10 | 0 | 0
1280.75 | 49.55 | 49.55 | 1 | 1 | 10 | 49.83 | 0.715 | 0.34412 | 3.4412 | 6.7206 | 6.7206 | 0 | 12 | 1 | 1 | 6.7206 | 10 | 0 | 0
1280.8 | 49.53 | 49.53 | 1 | 1 | 10 | 49.81 | 0.905 | 0.44412 | 4.4412 | 7.2206 | 7.2206 | 0 | 12 | 1 | 1 | 7.2206 | 10 | 0 | 0
1280.85 | 49.5 | 49.5 | 1 | 1 | 10 | 49.78 | 1 | 0.54412 | 5.4412 | 7.7206 | 7.7206 | 0 | 12 | 1 | 1 | 7.7206 | 10 | 0 | 0
1280.9 | 49.5 | 49.5 | 1 | 1 | 10 | 49.76 | 1 | 0.64412 | 6.4412 | 8.2206 | 8.2206 | 0 | 12 | 1 | 1 | 8.2206 | 10 | 0 | 0
1280.95 | 49.53 | 49.5 | 1 | 1 | 10 | 49.73 | 1 | 0.74412 | 7.4412 | 8.7206 | 8.7206 | 0 | 12 | 1 | 1 | 8.7206 | 10 | 0 | 0
1281 | 49.55 | 49.5 | 1 | 1 | 10 | 49.71 | 1 | 0.84412 | 8.4412 | 9.2206 | 9.2206 | 0 | 12 | 1 | 1 | 9.2206 | 10 | 0 | 0
1281.05 | 49.58 | 49.5 | 1 | 1 | 10 | 49.68 | 1 | 0.94412 | 9.4412 | 9.7206 | 9.7206 | 0 | 12 | 1 | 1 | 9.7206 | 10 | 0 | 0
1281.1 | 49.6 | 49.5 | 1 | 1 | 10 | 49.65 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1281.15 | 49.63 | 49.5 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1281.2 | 49.65 | 49.5 | 1 | 1 | 10 | 49.65 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1281.25 | 49.68 | 49.5 | 1 | 1 | 10 | 49.68 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1281.3 | 49.71 | 49.5 | 1 | 1 | 10 | 49.71 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1281.35 | 49.73 | 49.5 | 1 | 1 | 10 | 49.73 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1281.4 | 49.76 | 49.5 | 1 | 1 | 10 | 49.76 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1281.45 | 49.78 | 49.5 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1281.5 | 49.81 | 49.53 | 1 | 1 | 10 | 49.81 | 0.905 | 0.905 | 9.05 | 9.525 | 9.525 | 0 | 12 | 1 | 1 | 9.525 | 10 | 0 | 0
1281.55 | 49.83 | 49.55 | 1 | 1 | 10 | 49.83 | 0.715 | 0.715 | 7.15 | 8.575 | 8.575 | 0 | 12 | 1 | 1 | 8.575 | 10 | 0 | 0
1281.6 | 49.86 | 49.58 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
1281.65 | 49.88 | 49.6 | 1 | 1 | 10 | 49.88 | 0.24 | 0.24 | 2.4 | 6.2 | 6.2 | 0 | 12 | 1 | 1 | 6.2 | 10 | 0 | 0
1281.7 | 49.91 | 49.63 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1281.75 | 49.94 | 49.65 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
1281.8 | 49.96 | 49.68 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
1281.85 | 49.99 | 49.71 | 1 | 1 | 10 | 49.99 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1281.9 | 50.01 | 49.73 | 1 | 1 | 10 | 50.01 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1281.95 | 50.04 | 49.76 | 1 | 1 | 10 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 4.9265 | 4.9265 | 0 | 12 | 1 | 1 | 4.9265 | 10 | 0 | 0
1282 | 50.06 | 49.78 | 1 | 1 | 10 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 4.8676 | 4.8676 | 0 | 12 | 1 | 1 | 4.8676 | 10 | 0 | 0
1282.05 | 50.09 | 49.81 | 0.905 | 0.905 | 9.05 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 4.3044 | 4.3044 | 0 | 12 | 1 | 1 | 4.3044 | 10 | 0 | 0
1282.1 | 50.12 | 49.83 | 0.715 | 0.805 | 8.05 | 50.12 | -0.24 | -0.24 | -2.4 | 2.825 | 2.825 | 0 | 12 | 1 | 1 | 2.825 | 10 | 0 | 0
1282.15 | 50.14 | 49.86 | 0.43 | 0.705 | 7.05 | 50.14 | -0.43 | -0.43 | -4.3 | 1.375 | 1.375 | 0 | 12 | 1 | 1 | 1.375 | 10 | 0 | 0
1282.2 | 50.17 | 49.88 | 0.24 | 0.605 | 6.05 | 50.17 | -0.715 | -0.715 | -7.15 | -0.55 | -0.55 | 0 | 12 | 1 | 1 | -0.55 | 10 | 0 | 0
1282.25 | 50.19 | 49.91 | 0.044118 | 0.505 | 5.05 | 50.19 | -0.905 | -0.905 | -9.05 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
1282.3 | 50.22 | 49.94 | 0.026471 | 0.405 | 4.05 | 50.22 | -1 | -1 | -10 | -2.975 | -2.975 | 0 | 12 | 1 | 1 | -2.975 | 10 | 0 | 0
1282.35 | 50.24 | 49.96 | 0.014706 | 0.305 | 3.05 | 50.24 | -1 | -1 | -10 | -3.475 | -3.475 | 0 | 12 | 1 | 1 | -3.475 | 10 | 0 | 0
1282.4 | 50.27 | 49.99 | 0 | 0.205 | 2.05 | 50.27 | -1 | -1 | -10 | -3.975 | -3.975 | 0 | 12 | 1 | 1 | -3.975 | 10 | 0 | 0
1282.45 | 50.29 | 50.01 | 0 | 0.105 | 1.05 | 50.29 | -1 | -1 | -10 | -4.475 | -4.475 | 0 | 12 | 1 | 1 | -4.475 | 10 | 0 | 0
1282.5 | 50.32 | 50.04 | -0.014706 | 0.005 | 0.05 | 50.32 | -1 | -1 | -10 | -4.975 | -4.975 | 0 | 12 | 1 | 1 | -4.975 | 10 | 0 | 0
1282.55 | 50.35 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.35 | -1 | -1 | -10 | -5.1324 | -5.1324 | 0 | 12 | 1 | 1 | -5.1324 | 10 | 0 | 0
1282.6 | 50.37 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 50.37 | -1 | -1 | -10 | -5.2206 | -5.2206 | 0 | 12 | 1 | 1 | -5.2206 | 10 | 0 | 0
1282.65 | 50.4 | 50.12 | -0.24 | -0.14412 | -1.4412 | 50.4 | -1 | -1 | -10 | -5.7206 | -5.7206 | 0 | 12 | 1 | 1 | -5.7206 | 10 | 0 | 0
1282.7 | 50.42 | 50.14 | -0.43 | -0.24412 | -2.4412 | 50.42 | -1 | -1 | -10 | -6.2206 | -6.2206 | 0 | 12 | 1 | 1 | -6.2206 | 10 | 0 | 0
1282.75 | 50.45 | 50.17 | -0.715 | -0.34412 | -3.4412 | 50.45 | -1 | -1 | -10 | -6.7206 | -6.7206 | 0 | 12 | 1 | 1 | -6.7206 | 10 | 0 | 0
1282.8 | 50.47 | 50.19 | -0.905 | -0.44412 | -4.4412 | 50.47 | -1 | -1 | -10 | -7.2206 | -7.2206 | 0 | 12 | 1 | 1 | -7.2206 | 10 | 0 | 0
1282.85 | 50.5 | 50.22 | -1 | -0.54412 | -5.4412 | 50.5 | -1 | -1 | -10 | -7.7206 | -7.7206 | 0 | 12 | 1 | 1 | -7.7206 | 10 | 0 | 0
1282.9 | 50.5 | 50.24 | -1 | -0.64412 | -6.4412 | 50.5 | -1 | -1 | -10 | -8.2206 | -8.2206 | 0 | 12 | 1 | 1 | -8.2206 | 10 | 0 | 0
1282.95 | 50.47 | 50.27 | -1 | -0.74412 | -7.4412 | 50.5 | -1 | -1 | -10 | -8.7206 | -8.7206 | 0 | 12 | 1 | 1 | -8.7206 | 10 | 0 | 0
1283 | 50.45 | 50.29 | -1 | -0.84412 | -8.4412 | 50.5 | -1 | -1 | -10 | -9.2206 | -9.2206 | 0 | 12 | 1 | 1 | -9.2206 | 10 | 0 | 0
1283.05 | 50.42 | 50.32 | -1 | -0.94412 | -9.4412 | 50.5 | -1 | -1 | -10 | -9.7206 | -9.7206 | 0 | 12 | 1 | 1 | -9.7206 | 10 | 0 | 0
1283.1 | 50.39 | 50.35 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1283.15 | 50.37 | 50.37 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1283.2 | 50.34 | 50.34 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1283.25 | 50.32 | 50.32 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1283.3 | 50.29 | 50.29 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1283.35 | 50.26 | 50.26 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1283.4 | 50.24 | 50.24 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1283.45 | 50.21 | 50.21 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1283.5 | 50.18 | 50.18 | -0.81 | -0.81 | -8.1 | 50.47 | -1 | -1 | -10 | -9.05 | -9.05 | 0 | 12 | 1 | 1 | -9.05 | 10 | 0 | 0
1283.55 | 50.16 | 50.16 | -0.62 | -0.62 | -6.2 | 50.45 | -1 | -1 | -10 | -8.1 | -8.1 | 0 | 12 | 1 | 1 | -8.1 | 10 | 0 | 0
1283.6 | 50.13 | 50.13 | -0.335 | -0.335 | -3.35 | 50.42 | -1 | -1 | -10 | -6.675 | -6.675 | 0 | 12 | 1 | 1 | -6.675 | 10 | 0 | 0
1283.65 | 50.11 | 50.11 | -0.145 | -0.145 | -1.45 | 50.39 | -1 | -1 | -10 | -5.725 | -5.725 | 0 | 12 | 1 | 1 | -5.725 | 10 | 0 | 0
1283.7 | 50.08 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 50.37 | -1 | -1 | -10 | -5.1912 | -5.1912 | 0 | 12 | 1 | 1 | -5.1912 | 10 | 0 | 0
1283.75 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.34 | -1 | -1 | -10 | -5.1029 | -5.1029 | 0 | 12 | 1 | 1 | -5.1029 | 10 | 0 | 0
1283.8 | 50.03 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 50.32 | -1 | -1 | -10 | -5.0441 | -5.0441 | 0 | 12 | 1 | 1 | -5.0441 | 10 | 0 | 0
1283.85 | 50 | 50 | 0 | 0 | 0 | 50.29 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1283.9 | 50 | 50 | 0 | 0 | 0 | 50.26 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1283.95 | 50 | 50 | 0 | 0 | 0 | 50.24 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1284 | 50 | 50 | 0 | 0 | 0 | 50.21 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1284.05 | 50 | 50 | 0 | 0 | 0 | 50.18 | -0.81 | -0.9 | -9 | -4.5 | -4.5 | 0 | 12 | 1 | 1 | -4.5 | 10 | 0 | 0
1284.1 | 50 | 50 | 0 | 0 | 0 | 50.16 | -0.62 | -0.8 | -8 | -4 | -4 | 0 | 12 | 1 | 1 | -4 | 10 | 0 | 0
1284.15 | 50 | 50 | 0 | 0 | 0 | 50.13 | -0.335 | -0.7 | -7 | -3.5 | -3.5 | 0 | 12 | 1 | 1 | -3.5 | 10 | 0 | 0
1284.2 | 50.01 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.6 | -6 | -3 | -3 | 0 | 12 | 1 | 1 | -3 | 10 | 0 | 0
1284.25 | 50.01 | 50 | 0 | 0 | 0 | 50.08 | -0.038235 | -0.5 | -5 | -2.5 | -2.5 | 0 | 12 | 1 | 1 | -2.5 | 10 | 0 | 0
1284.3 | 49.99 | 49.99 | 0 | 0 | 0 | 50.05 | -0.020588 | -0.4 | -4 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
1284.35 | 49.99 | 49.99 | 0 | 0 | 0 | 50.03 | -0.0088235 | -0.3 | -3 | -1.5 | -1.5 | 0 | 12 | 1 | 1 | -1.5 | 10 | 0 | 0
1284.4 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | -0.2 | -2 | -0.83824 | -0.83824 | 0 | 12 | 1 | 1 | -0.83824 | 10 | 0 | 0
1284.45 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | -0.1 | -1 | -0.33824 | -0.33824 | 0 | 12 | 1 | 1 | -0.33824 | 10 | 0 | 0
1284.5 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
1284.55 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
1284.6 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
1284.65 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
1284.7 | 49.89 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
1284.75 | 49.89 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
1284.8 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50.01 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1284.85 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1284.9 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1284.95 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 2.7868 | 2.7868 | 0 | 12 | 1 | 1 | 2.7868 | 10 | 0 | 0
1285 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 2.7868 | 2.7868 | 0 | 12 | 1 | 1 | 2.7868 | 10 | 0 | 0
1285.05 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 2.8456 | 2.8456 | 0 | 12 | 1 | 1 | 2.8456 | 10 | 0 | 0
1285.1 | 49.94 | 49.85 | 0.525 | 0.525 | 5.25 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 2.7574 | 2.7574 | 0 | 12 | 1 | 1 | 2.7574 | 10 | 0 | 0
1285.15 | 49.94 | 49.85 | 0.525 | 0.525 | 5.25 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 2.7574 | 2.7574 | 0 | 12 | 1 | 1 | 2.7574 | 10 | 0 | 0
1285.2 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1285.25 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1285.3 | 49.93 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1285.35 | 49.93 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1285.4 | 49.96 | 49.85 | 0.525 | 0.525 | 5.25 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 2.6985 | 2.6985 | 0 | 12 | 1 | 1 | 2.6985 | 10 | 0 | 0
1285.45 | 49.96 | 49.85 | 0.525 | 0.525 | 5.25 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 2.6985 | 2.6985 | 0 | 12 | 1 | 1 | 2.6985 | 10 | 0 | 0
1285.5 | 49.99 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1285.55 | 49.99 | 49.91 | 0.044118 | 0.425 | 4.25 | 49.99 | 0 | 0 | 0 | 2.125 | 2.125 | 0 | 12 | 1 | 1 | 2.125 | 10 | 0 | 0
1285.6 | 49.99 | 49.91 | 0.044118 | 0.325 | 3.25 | 49.99 | 0 | 0 | 0 | 1.625 | 1.625 | 0 | 12 | 1 | 1 | 1.625 | 10 | 0 | 0
1285.65 | 49.99 | 49.93 | 0.032353 | 0.225 | 2.25 | 49.99 | 0 | 0 | 0 | 1.125 | 1.125 | 0 | 12 | 1 | 1 | 1.125 | 10 | 0 | 0
1285.7 | 49.96 | 49.93 | 0.032353 | 0.125 | 1.25 | 49.99 | 0 | 0 | 0 | 0.625 | 0.625 | 0 | 12 | 1 | 1 | 0.625 | 10 | 0 | 0
1285.75 | 49.96 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 49.99 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1285.8 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1285.85 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1285.9 | 50.05 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.058824 | 0.058824 | 0 | 12 | 1 | 1 | 0.058824 | 10 | 0 | 0
1285.95 | 50.05 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
1286 | 49.97 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
1286.05 | 49.97 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
1286.1 | 49.92 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1286.15 | 49.92 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1286.2 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1286.25 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1286.3 | 49.94 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1286.35 | 49.94 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1286.4 | 50.01 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1286.45 | 50.01 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1286.5 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1286.55 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
1286.6 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
1286.65 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
1286.7 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
1286.75 | 49.95 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
1286.8 | 49.97 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
1286.85 | 49.97 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
1286.9 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
1286.95 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
1287 | 49.87 | 49.87 | 0.335 | 0.335 | 3.35 | 50.01 | 0 | 0 | 0 | 1.675 | 1.675 | 0 | 12 | 1 | 1 | 1.675 | 10 | 0 | 0
1287.05 | 49.87 | 49.87 | 0.335 | 0.335 | 3.35 | 49.99 | 0 | 0 | 0 | 1.675 | 1.675 | 0 | 12 | 1 | 1 | 1.675 | 10 | 0 | 0
1287.1 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1287.15 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 2.6691 | 2.6691 | 0 | 12 | 1 | 1 | 2.6691 | 10 | 0 | 0
1287.2 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1287.25 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1287.3 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1287.35 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1287.4 | 49.84 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1287.45 | 49.84 | 49.79 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
1287.5 | 49.89 | 49.79 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
1287.55 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.12647 | 1.2647 | 5.6324 | 5.6324 | 0 | 12 | 1 | 1 | 5.6324 | 10 | 0 | 0
1287.6 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.145 | 1.45 | 5.725 | 5.725 | 0 | 12 | 1 | 1 | 5.725 | 10 | 0 | 0
1287.65 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.145 | 1.45 | 5.725 | 5.725 | 0 | 12 | 1 | 1 | 5.725 | 10 | 0 | 0
1287.7 | 49.96 | 49.79 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
1287.75 | 49.96 | 49.79 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
1287.8 | 50.02 | 49.79 | 1 | 1 | 10 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 4.9853 | 4.9853 | 0 | 12 | 1 | 1 | 4.9853 | 10 | 0 | 0
1287.85 | 50.02 | 49.79 | 1 | 1 | 10 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 4.9853 | 4.9853 | 0 | 12 | 1 | 1 | 4.9853 | 10 | 0 | 0
1287.9 | 50.03 | 49.79 | 1 | 1 | 10 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.9559 | 4.9559 | 0 | 12 | 1 | 1 | 4.9559 | 10 | 0 | 0
1287.95 | 50.03 | 49.84 | 0.62 | 0.9 | 9 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.4559 | 4.4559 | 0 | 12 | 1 | 1 | 4.4559 | 10 | 0 | 0
1288 | 50.02 | 49.84 | 0.62 | 0.8 | 8 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 3.9559 | 3.9559 | 0 | 12 | 1 | 1 | 3.9559 | 10 | 0 | 0
1288.05 | 50.02 | 49.89 | 0.145 | 0.7 | 7 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 3.4559 | 3.4559 | 0 | 12 | 1 | 1 | 3.4559 | 10 | 0 | 0
1288.1 | 50.08 | 49.89 | 0.145 | 0.6 | 6 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 2.8088 | 2.8088 | 0 | 12 | 1 | 1 | 2.8088 | 10 | 0 | 0
1288.15 | 50.08 | 49.89 | 0.145 | 0.5 | 5 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 2.3088 | 2.3088 | 0 | 12 | 1 | 1 | 2.3088 | 10 | 0 | 0
1288.2 | 50.01 | 49.89 | 0.145 | 0.4 | 4 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 1.8088 | 1.8088 | 0 | 12 | 1 | 1 | 1.8088 | 10 | 0 | 0
1288.25 | 50.01 | 49.96 | 0.014706 | 0.3 | 3 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 1.3088 | 1.3088 | 0 | 12 | 1 | 1 | 1.3088 | 10 | 0 | 0
1288.3 | 49.94 | 49.94 | 0.026471 | 0.2 | 2 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.80882 | 0.80882 | 0 | 12 | 1 | 1 | 0.80882 | 10 | 0 | 0
1288.35 | 49.94 | 49.94 | 0.026471 | 0.1 | 1 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.30882 | 0.30882 | 0 | 12 | 1 | 1 | 0.30882 | 10 | 0 | 0
1288.4 | 50 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
1288.45 | 50 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
1288.5 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
1288.55 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
1288.6 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1288.65 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1288.7 | 49.92 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1288.75 | 49.92 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
1288.8 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50.01 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1288.85 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1288.9 | 49.92 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1288.95 | 49.92 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1289 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1289.05 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1289.1 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1289.15 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1289.2 | 49.87 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1289.25 | 49.87 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1289.3 | 49.8 | 49.8 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1289.35 | 49.8 | 49.8 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1289.4 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1289.45 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1289.5 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1289.55 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1289.6 | 49.72 | 49.72 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1289.65 | 49.72 | 49.72 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1289.7 | 49.67 | 49.67 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1289.75 | 49.67 | 49.67 | 1 | 1 | 10 | 49.87 | 0.335 | 0.14412 | 1.4412 | 5.7206 | 5.7206 | 0 | 12 | 1 | 1 | 5.7206 | 10 | 0 | 0
1289.8 | 49.65 | 49.65 | 1 | 1 | 10 | 49.87 | 0.335 | 0.24412 | 2.4412 | 6.2206 | 6.2206 | 0 | 12 | 1 | 1 | 6.2206 | 10 | 0 | 0
1289.85 | 49.65 | 49.65 | 1 | 1 | 10 | 49.8 | 1 | 0.34412 | 3.4412 | 6.7206 | 6.7206 | 0 | 12 | 1 | 1 | 6.7206 | 10 | 0 | 0
1289.9 | 49.59 | 49.59 | 1 | 1 | 10 | 49.8 | 1 | 0.44412 | 4.4412 | 7.2206 | 7.2206 | 0 | 12 | 1 | 1 | 7.2206 | 10 | 0 | 0
1289.95 | 49.59 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.54412 | 5.4412 | 7.7206 | 7.7206 | 0 | 12 | 1 | 1 | 7.7206 | 10 | 0 | 0
1290 | 49.66 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.64412 | 6.4412 | 8.2206 | 8.2206 | 0 | 12 | 1 | 1 | 8.2206 | 10 | 0 | 0
1290.05 | 49.66 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.74412 | 7.4412 | 8.7206 | 8.7206 | 0 | 12 | 1 | 1 | 8.7206 | 10 | 0 | 0
1290.1 | 49.63 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.84412 | 8.4412 | 9.2206 | 9.2206 | 0 | 12 | 1 | 1 | 9.2206 | 10 | 0 | 0
1290.15 | 49.63 | 49.59 | 1 | 1 | 10 | 49.72 | 1 | 0.94412 | 9.4412 | 9.7206 | 9.7206 | 0 | 12 | 1 | 1 | 9.7206 | 10 | 0 | 0
1290.2 | 49.61 | 49.59 | 1 | 1 | 10 | 49.72 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1290.25 | 49.61 | 49.59 | 1 | 1 | 10 | 49.67 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1290.3 | 49.54 | 49.54 | 1 | 1 | 10 | 49.67 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1290.35 | 49.54 | 49.54 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1290.4 | 49.46 | 49.46 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1290.45 | 49.46 | 49.46 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1290.5 | 49.45 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1290.55 | 49.45 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1290.6 | 49.51 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1290.65 | 49.51 | 49.45 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1290.7 | 49.5 | 49.45 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1290.75 | 49.5 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1290.8 | 49.54 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1290.85 | 49.54 | 49.45 | 1 | 1 | 10 | 49.54 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1290.9 | 49.59 | 49.45 | 1 | 1 | 10 | 49.59 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1290.95 | 49.59 | 49.45 | 1 | 1 | 10 | 49.59 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1291 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1291.05 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1291.1 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1291.15 | 49.61 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1291.2 | 49.53 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1291.25 | 49.53 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1291.3 | 49.54 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1291.35 | 49.54 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1291.4 | 49.61 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1291.45 | 49.61 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1291.5 | 49.66 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1291.55 | 49.66 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1291.6 | 49.64 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1291.65 | 49.64 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1291.7 | 49.69 | 49.53 | 1 | 1 | 10 | 49.69 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1291.75 | 49.69 | 49.53 | 1 | 1 | 10 | 49.69 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1291.8 | 49.74 | 49.53 | 1 | 1 | 10 | 49.74 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1291.85 | 49.74 | 49.54 | 1 | 1 | 10 | 49.74 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1291.9 | 49.78 | 49.54 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1291.95 | 49.78 | 49.61 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1292 | 49.82 | 49.61 | 1 | 1 | 10 | 49.82 | 0.81 | 0.81 | 8.1 | 9.05 | 9.05 | 0 | 12 | 1 | 1 | 9.05 | 10 | 0 | 0
1292.05 | 49.82 | 49.64 | 1 | 1 | 10 | 49.82 | 0.81 | 0.81 | 8.1 | 9.05 | 9.05 | 0 | 12 | 1 | 1 | 9.05 | 10 | 0 | 0
1292.1 | 49.86 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
1292.15 | 49.86 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
1292.2 | 49.84 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
1292.25 | 49.84 | 49.69 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
1292.3 | 49.91 | 49.69 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1292.35 | 49.91 | 49.74 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1292.4 | 49.97 | 49.74 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1292.45 | 49.97 | 49.78 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1292.5 | 50.03 | 49.78 | 1 | 1 | 10 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.9559 | 4.9559 | 0 | 12 | 1 | 1 | 4.9559 | 10 | 0 | 0
1292.55 | 50.03 | 49.82 | 0.81 | 0.9 | 9 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.4559 | 4.4559 | 0 | 12 | 1 | 1 | 4.4559 | 10 | 0 | 0
1292.6 | 50.05 | 49.82 | 0.81 | 0.81 | 8.1 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 3.9471 | 3.9471 | 0 | 12 | 1 | 1 | 3.9471 | 10 | 0 | 0
1292.65 | 50.05 | 49.84 | 0.62 | 0.71 | 7.1 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 3.4471 | 3.4471 | 0 | 12 | 1 | 1 | 3.4471 | 10 | 0 | 0
1292.7 | 50.01 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
1292.75 | 50.01 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
1292.8 | 49.95 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
1292.85 | 49.95 | 49.91 | 0.044118 | 0.52 | 5.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.4971 | 2.4971 | 0 | 12 | 1 | 1 | 2.4971 | 10 | 0 | 0
1292.9 | 49.99 | 49.91 | 0.044118 | 0.42 | 4.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 1.9971 | 1.9971 | 0 | 12 | 1 | 1 | 1.9971 | 10 | 0 | 0
1292.95 | 49.99 | 49.95 | 0.020588 | 0.32 | 3.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 1.4971 | 1.4971 | 0 | 12 | 1 | 1 | 1.4971 | 10 | 0 | 0
1293 | 49.92 | 49.92 | 0.038235 | 0.22 | 2.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.99706 | 0.99706 | 0 | 12 | 1 | 1 | 0.99706 | 10 | 0 | 0
1293.05 | 49.92 | 49.92 | 0.038235 | 0.12 | 1.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.49706 | 0.49706 | 0 | 12 | 1 | 1 | 0.49706 | 10 | 0 | 0
1293.1 | 49.97 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1293.15 | 49.97 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1293.2 | 50.02 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1293.25 | 50.02 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.17647 | 0.17647 | 0 | 12 | 1 | 1 | 0.17647 | 10 | 0 | 0
1293.3 | 50.07 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1293.35 | 50.07 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1293.4 | 50.06 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1293.45 | 50.06 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1293.5 | 50.13 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
1293.55 | 50.13 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
1293.6 | 50.09 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
1293.65 | 50.09 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6309 | -1.6309 | 0 | 12 | 1 | 1 | -1.6309 | 10 | 0 | 0
1293.7 | 50.07 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6309 | -1.6309 | 0 | 12 | 1 | 1 | -1.6309 | 10 | 0 | 0
1293.75 | 50.07 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6897 | -1.6897 | 0 | 12 | 1 | 1 | -1.6897 | 10 | 0 | 0
1293.8 | 50.07 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6897 | -1.6897 | 0 | 12 | 1 | 1 | -1.6897 | 10 | 0 | 0
1293.85 | 50.07 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.13 | -0.335 | -0.335 | -3.35 | -1.8074 | -1.8074 | 0 | 12 | 1 | 1 | -1.8074 | 10 | 0 | 0
1293.9 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.13 | -0.335 | -0.335 | -3.35 | -1.7779 | -1.7779 | 0 | 12 | 1 | 1 | -1.7779 | 10 | 0 | 0
1293.95 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.13 | -0.335 | -0.335 | -3.35 | -1.7779 | -1.7779 | 0 | 12 | 1 | 1 | -1.7779 | 10 | 0 | 0
1294 | 50.01 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
1294.05 | 50.01 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
1294.1 | 50.07 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
1294.15 | 50.07 | 50.01 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.235 | -2.35 | -1.175 | -1.175 | 0 | 12 | 1 | 1 | -1.175 | 10 | 0 | 0
1294.2 | 50.05 | 50.01 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.135 | -1.35 | -0.675 | -0.675 | 0 | 12 | 1 | 1 | -0.675 | 10 | 0 | 0
1294.25 | 50.05 | 50.01 | 0 | 0 | 0 | 50.07 | -0.032353 | -0.035 | -0.35 | -0.175 | -0.175 | 0 | 12 | 1 | 1 | -0.175 | 10 | 0 | 0
1294.3 | 50.1 | 50.01 | 0 | 0 | 0 | 50.1 | -0.05 | -0.05 | -0.5 | -0.25 | -0.25 | 0 | 12 | 1 | 1 | -0.25 | 10 | 0 | 0
1294.35 | 50.1 | 50.01 | 0 | 0 | 0 | 50.1 | -0.05 | -0.05 | -0.5 | -0.25 | -0.25 | 0 | 12 | 1 | 1 | -0.25 | 10 | 0 | 0
1294.4 | 50.11 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1294.45 | 50.11 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1294.5 | 50.06 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1294.55 | 50.06 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1294.6 | 50.04 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1294.65 | 50.04 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1294.7 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1294.75 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1294.8 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1294.85 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1294.9 | 50.11 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1294.95 | 50.11 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1295 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1295.05 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1295.1 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1295.15 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1295.2 | 50.02 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.11 | -0.145 | -0.145 | -1.45 | -0.73971 | -0.73971 | 0 | 12 | 1 | 1 | -0.73971 | 10 | 0 | 0
1295.25 | 50.02 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.11 | -0.145 | -0.145 | -1.45 | -0.73971 | -0.73971 | 0 | 12 | 1 | 1 | -0.73971 | 10 | 0 | 0
1295.3 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1295.35 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1295.4 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1295.45 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1295.5 | 50.01 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1295.55 | 50.01 | 50 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.045 | -0.45 | -0.225 | -0.225 | 0 | 12 | 1 | 1 | -0.225 | 10 | 0 | 0
1295.6 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
1295.65 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
1295.7 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
1295.75 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1295.8 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.14706 | 0.14706 | 0 | 12 | 1 | 1 | 0.14706 | 10 | 0 | 0
1295.85 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1295.9 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1295.95 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1296 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1296.05 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1296.1 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1296.15 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1296.2 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1296.25 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1296.3 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1296.35 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1296.4 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1296.45 | 50 | 50 | 0 | 0 | 0 | 50.01 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1296.5 | 49.5 | 49.5 | 1 | 1 | 10 | 50.01 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1296.55 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1296.6 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1296.65 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1296.7 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1296.75 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1296.8 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1296.85 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1296.9 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1296.95 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1297 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1297.05 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.1 | 1 | 5.5 | 5.5 | 0 | 12 | 1 | 1 | 5.5 | 10 | 0 | 0
1297.1 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.2 | 2 | 6 | 6 | 0 | 12 | 1 | 1 | 6 | 10 | 0 | 0
1297.15 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.3 | 3 | 6.5 | 6.5 | 0 | 12 | 1 | 1 | 6.5 | 10 | 0 | 0
1297.2 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.4 | 4 | 7 | 7 | 0 | 12 | 1 | 1 | 7 | 10 | 0 | 0
1297.25 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.5 | 5 | 7.5 | 7.5 | 0 | 12 | 1 | 1 | 7.5 | 10 | 0 | 0
1297.3 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.6 | 6 | 8 | 8 | 0 | 12 | 1 | 1 | 8 | 10 | 0 | 0
1297.35 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.7 | 7 | 8.5 | 8.5 | 0 | 12 | 1 | 1 | 8.5 | 10 | 0 | 0
1297.4 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.8 | 8 | 9 | 9 | 0 | 12 | 1 | 1 | 9 | 10 | 0 | 0
1297.45 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.9 | 9 | 9.5 | 9.5 | 0 | 12 | 1 | 1 | 9.5 | 10 | 0 | 0
1297.5 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1297.55 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1297.6 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1297.65 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1297.7 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1297.75 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1297.8 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1297.85 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1297.9 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1297.95 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1298 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1298.05 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1298.1 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1298.15 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1298.2 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1298.25 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1298.3 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1298.35 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1298.4 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1298.45 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1298.5 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1298.55 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1298.6 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1298.65 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1298.7 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1298.75 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1298.8 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1298.85 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1298.9 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1298.95 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1299 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1299.05 | 50.5 | 50.5 | -1 | 0.9 | 9 | 50.5 | -1 | -1 | -10 | -0.5 | -0.5 | 0 | 12 | 1 | 1 | -0.5 | 10 | 0 | 0
1299.1 | 50.5 | 50.5 | -1 | 0.8 | 8 | 50.5 | -1 | -1 | -10 | -1 | -1 | 0 | 12 | 1 | 1 | -1 | 10 | 0 | 0
1299.15 | 50.5 | 50.5 | -1 | 0.7 | 7 | 50.5 | -1 | -1 | -10 | -1.5 | -1.5 | 0 | 12 | 1 | 1 | -1.5 | 10 | 0 | 0
1299.2 | 50.5 | 50.5 | -1 | 0.6 | 6 | 50.5 | -1 | -1 | -10 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
1299.25 | 50.5 | 50.5 | -1 | 0.5 | 5 | 50.5 | -1 | -1 | -10 | -2.5 | -2.5 | 0 | 12 | 1 | 1 | -2.5 | 10 | 0 | 0
1299.3 | 50.5 | 50.5 | -1 | 0.4 | 4 | 50.5 | -1 | -1 | -10 | -3 | -3 | 0 | 12 | 1 | 1 | -3 | 10 | 0 | 0
1299.35 | 50.5 | 50.5 | -1 | 0.3 | 3 | 50.5 | -1 | -1 | -10 | -3.5 | -3.5 | 0 | 12 | 1 | 1 | -3.5 | 10 | 0 | 0
1299.4 | 50.5 | 50.5 | -1 | 0.2 | 2 | 50.5 | -1 | -1 | -10 | -4 | -4 | 0 | 12 | 1 | 1 | -4 | 10 | 0 | 0
1299.45 | 50.5 | 50.5 | -1 | 0.1 | 1 | 50.5 | -1 | -1 | -10 | -4.5 | -4.5 | 0 | 12 | 1 | 1 | -4.5 | 10 | 0 | 0
1299.5 | 50.5 | 50.5 | -1 | 0 | 0 | 50.5 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1299.55 | 50.5 | 50.5 | -1 | -0.1 | -1 | 50.5 | -1 | -1 | -10 | -5.5 | -5.5 | 0 | 12 | 1 | 1 | -5.5 | 10 | 0 | 0
1299.6 | 50.5 | 50.5 | -1 | -0.2 | -2 | 50.5 | -1 | -1 | -10 | -6 | -6 | 0 | 12 | 1 | 1 | -6 | 10 | 0 | 0
1299.65 | 50.5 | 50.5 | -1 | -0.3 | -3 | 50.5 | -1 | -1 | -10 | -6.5 | -6.5 | 0 | 12 | 1 | 1 | -6.5 | 10 | 0 | 0
1299.7 | 50.5 | 50.5 | -1 | -0.4 | -4 | 50.5 | -1 | -1 | -10 | -7 | -7 | 0 | 12 | 1 | 1 | -7 | 10 | 0 | 0
1299.75 | 50.5 | 50.5 | -1 | -0.5 | -5 | 50.5 | -1 | -1 | -10 | -7.5 | -7.5 | 0 | 12 | 1 | 1 | -7.5 | 10 | 0 | 0
1299.8 | 50.5 | 50.5 | -1 | -0.6 | -6 | 50.5 | -1 | -1 | -10 | -8 | -8 | 0 | 12 | 1 | 1 | -8 | 10 | 0 | 0
1299.85 | 50.5 | 50.5 | -1 | -0.7 | -7 | 50.5 | -1 | -1 | -10 | -8.5 | -8.5 | 0 | 12 | 1 | 1 | -8.5 | 10 | 0 | 0
1299.9 | 50.5 | 50.5 | -1 | -0.8 | -8 | 50.5 | -1 | -1 | -10 | -9 | -9 | 0 | 12 | 1 | 1 | -9 | 10 | 0 | 0
1299.95 | 50.5 | 50.5 | -1 | -0.9 | -9 | 50.5 | -1 | -1 | -10 | -9.5 | -9.5 | 0 | 12 | 1 | 1 | -9.5 | 10 | 0 | 0
1300 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1300.05 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1300.1 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1300.15 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1300.2 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1300.25 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1300.3 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1300.35 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1300.4 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1300.45 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1300.5 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1300.55 | 50.47 | 50.47 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1300.6 | 50.45 | 50.45 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1300.65 | 50.42 | 50.42 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1300.7 | 50.4 | 50.4 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1300.75 | 50.37 | 50.37 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1300.8 | 50.35 | 50.35 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1300.85 | 50.32 | 50.32 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1300.9 | 50.29 | 50.29 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1300.95 | 50.27 | 50.27 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1301 | 50.24 | 50.24 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1301.05 | 50.22 | 50.22 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1301.1 | 50.19 | 50.19 | -0.905 | -0.905 | -9.05 | 50.47 | -1 | -1 | -10 | -9.525 | -9.525 | 0 | 12 | 1 | 1 | -9.525 | 10 | 0 | 0
1301.15 | 50.17 | 50.17 | -0.715 | -0.715 | -7.15 | 50.45 | -1 | -1 | -10 | -8.575 | -8.575 | 0 | 12 | 1 | 1 | -8.575 | 10 | 0 | 0
1301.2 | 50.14 | 50.14 | -0.43 | -0.43 | -4.3 | 50.42 | -1 | -1 | -10 | -7.15 | -7.15 | 0 | 12 | 1 | 1 | -7.15 | 10 | 0 | 0
1301.25 | 50.12 | 50.12 | -0.24 | -0.24 | -2.4 | 50.4 | -1 | -1 | -10 | -6.2 | -6.2 | 0 | 12 | 1 | 1 | -6.2 | 10 | 0 | 0
1301.3 | 50.09 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 50.37 | -1 | -1 | -10 | -5.2206 | -5.2206 | 0 | 12 | 1 | 1 | -5.2206 | 10 | 0 | 0
1301.35 | 50.06 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.35 | -1 | -1 | -10 | -5.1324 | -5.1324 | 0 | 12 | 1 | 1 | -5.1324 | 10 | 0 | 0
1301.4 | 50.04 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.32 | -1 | -1 | -10 | -5.0735 | -5.0735 | 0 | 12 | 1 | 1 | -5.0735 | 10 | 0 | 0
1301.45 | 50.01 | 50.01 | 0 | 0 | 0 | 50.29 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1301.5 | 49.99 | 49.99 | 0 | 0 | 0 | 50.27 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1301.55 | 49.96 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.24 | -1 | -1 | -10 | -4.9265 | -4.9265 | 0 | 12 | 1 | 1 | -4.9265 | 10 | 0 | 0
1301.6 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.22 | -1 | -1 | -10 | -4.8676 | -4.8676 | 0 | 12 | 1 | 1 | -4.8676 | 10 | 0 | 0
1301.65 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.19 | -0.905 | -0.905 | -9.05 | -4.3044 | -4.3044 | 0 | 12 | 1 | 1 | -4.3044 | 10 | 0 | 0
1301.7 | 49.88 | 49.88 | 0.24 | 0.24 | 2.4 | 50.17 | -0.715 | -0.805 | -8.05 | -2.825 | -2.825 | 0 | 12 | 1 | 1 | -2.825 | 10 | 0 | 0
1301.75 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.14 | -0.43 | -0.705 | -7.05 | -1.375 | -1.375 | 0 | 12 | 1 | 1 | -1.375 | 10 | 0 | 0
1301.8 | 49.83 | 49.83 | 0.715 | 0.715 | 7.15 | 50.12 | -0.24 | -0.605 | -6.05 | 0.55 | 0.55 | 0 | 12 | 1 | 1 | 0.55 | 10 | 0 | 0
1301.85 | 49.81 | 49.81 | 0.905 | 0.905 | 9.05 | 50.09 | -0.044118 | -0.505 | -5.05 | 2 | 2 | 0 | 12 | 1 | 1 | 2 | 10 | 0 | 0
1301.9 | 49.78 | 49.78 | 1 | 1 | 10 | 50.06 | -0.026471 | -0.405 | -4.05 | 2.975 | 2.975 | 0 | 12 | 1 | 1 | 2.975 | 10 | 0 | 0
1301.95 | 49.76 | 49.76 | 1 | 1 | 10 | 50.04 | -0.014706 | -0.305 | -3.05 | 3.475 | 3.475 | 0 | 12 | 1 | 1 | 3.475 | 10 | 0 | 0
1302 | 49.73 | 49.73 | 1 | 1 | 10 | 50.01 | 0 | -0.205 | -2.05 | 3.975 | 3.975 | 0 | 12 | 1 | 1 | 3.975 | 10 | 0 | 0
1302.05 | 49.71 | 49.71 | 1 | 1 | 10 | 49.99 | 0 | -0.105 | -1.05 | 4.475 | 4.475 | 0 | 12 | 1 | 1 | 4.475 | 10 | 0 | 0
1302.1 | 49.68 | 49.68 | 1 | 1 | 10 | 49.96 | 0.014706 | -0.005 | -0.05 | 4.975 | 4.975 | 0 | 12 | 1 | 1 | 4.975 | 10 | 0 | 0
1302.15 | 49.65 | 49.65 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
1302.2 | 49.63 | 49.63 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1302.25 | 49.6 | 49.6 | 1 | 1 | 10 | 49.88 | 0.24 | 0.14412 | 1.4412 | 5.7206 | 5.7206 | 0 | 12 | 1 | 1 | 5.7206 | 10 | 0 | 0
1302.3 | 49.58 | 49.58 | 1 | 1 | 10 | 49.86 | 0.43 | 0.24412 | 2.4412 | 6.2206 | 6.2206 | 0 | 12 | 1 | 1 | 6.2206 | 10 | 0 | 0
1302.35 | 49.55 | 49.55 | 1 | 1 | 10 | 49.83 | 0.715 | 0.34412 | 3.4412 | 6.7206 | 6.7206 | 0 | 12 | 1 | 1 | 6.7206 | 10 | 0 | 0
1302.4 | 49.53 | 49.53 | 1 | 1 | 10 | 49.81 | 0.905 | 0.44412 | 4.4412 | 7.2206 | 7.2206 | 0 | 12 | 1 | 1 | 7.2206 | 10 | 0 | 0
1302.45 | 49.5 | 49.5 | 1 | 1 | 10 | 49.78 | 1 | 0.54412 | 5.4412 | 7.7206 | 7.7206 | 0 | 12 | 1 | 1 | 7.7206 | 10 | 0 | 0
1302.5 | 49.5 | 49.5 | 1 | 1 | 10 | 49.76 | 1 | 0.64412 | 6.4412 | 8.2206 | 8.2206 | 0 | 12 | 1 | 1 | 8.2206 | 10 | 0 | 0
1302.55 | 49.53 | 49.5 | 1 | 1 | 10 | 49.73 | 1 | 0.74412 | 7.4412 | 8.7206 | 8.7206 | 0 | 12 | 1 | 1 | 8.7206 | 10 | 0 | 0
1302.6 | 49.55 | 49.5 | 1 | 1 | 10 | 49.71 | 1 | 0.84412 | 8.4412 | 9.2206 | 9.2206 | 0 | 12 | 1 | 1 | 9.2206 | 10 | 0 | 0
1302.65 | 49.58 | 49.5 | 1 | 1 | 10 | 49.68 | 1 | 0.94412 | 9.4412 | 9.7206 | 9.7206 | 0 | 12 | 1 | 1 | 9.7206 | 10 | 0 | 0
1302.7 | 49.6 | 49.5 | 1 | 1 | 10 | 49.65 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1302.75 | 49.63 | 49.5 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1302.8 | 49.65 | 49.5 | 1 | 1 | 10 | 49.65 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1302.85 | 49.68 | 49.5 | 1 | 1 | 10 | 49.68 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1302.9 | 49.71 | 49.5 | 1 | 1 | 10 | 49.71 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1302.95 | 49.73 | 49.5 | 1 | 1 | 10 | 49.73 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1303 | 49.76 | 49.5 | 1 | 1 | 10 | 49.76 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1303.05 | 49.78 | 49.5 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1303.1 | 49.81 | 49.53 | 1 | 1 | 10 | 49.81 | 0.905 | 0.905 | 9.05 | 9.525 | 9.525 | 0 | 12 | 1 | 1 | 9.525 | 10 | 0 | 0
1303.15 | 49.83 | 49.55 | 1 | 1 | 10 | 49.83 | 0.715 | 0.715 | 7.15 | 8.575 | 8.575 | 0 | 12 | 1 | 1 | 8.575 | 10 | 0 | 0
1303.2 | 49.86 | 49.58 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
1303.25 | 49.88 | 49.6 | 1 | 1 | 10 | 49.88 | 0.24 | 0.24 | 2.4 | 6.2 | 6.2 | 0 | 12 | 1 | 1 | 6.2 | 10 | 0 | 0
1303.3 | 49.91 | 49.63 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1303.35 | 49.94 | 49.65 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
1303.4 | 49.96 | 49.68 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
1303.45 | 49.99 | 49.71 | 1 | 1 | 10 | 49.99 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1303.5 | 50.01 | 49.73 | 1 | 1 | 10 | 50.01 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1303.55 | 50.04 | 49.76 | 1 | 1 | 10 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 4.9265 | 4.9265 | 0 | 12 | 1 | 1 | 4.9265 | 10 | 0 | 0
1303.6 | 50.06 | 49.78 | 1 | 1 | 10 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 4.8676 | 4.8676 | 0 | 12 | 1 | 1 | 4.8676 | 10 | 0 | 0
1303.65 | 50.09 | 49.81 | 0.905 | 0.905 | 9.05 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 4.3044 | 4.3044 | 0 | 12 | 1 | 1 | 4.3044 | 10 | 0 | 0
1303.7 | 50.12 | 49.83 | 0.715 | 0.805 | 8.05 | 50.12 | -0.24 | -0.24 | -2.4 | 2.825 | 2.825 | 0 | 12 | 1 | 1 | 2.825 | 10 | 0 | 0
1303.75 | 50.14 | 49.86 | 0.43 | 0.705 | 7.05 | 50.14 | -0.43 | -0.43 | -4.3 | 1.375 | 1.375 | 0 | 12 | 1 | 1 | 1.375 | 10 | 0 | 0
1303.8 | 50.17 | 49.88 | 0.24 | 0.605 | 6.05 | 50.17 | -0.715 | -0.715 | -7.15 | -0.55 | -0.55 | 0 | 12 | 1 | 1 | -0.55 | 10 | 0 | 0
1303.85 | 50.19 | 49.91 | 0.044118 | 0.505 | 5.05 | 50.19 | -0.905 | -0.905 | -9.05 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
1303.9 | 50.22 | 49.94 | 0.026471 | 0.405 | 4.05 | 50.22 | -1 | -1 | -10 | -2.975 | -2.975 | 0 | 12 | 1 | 1 | -2.975 | 10 | 0 | 0
1303.95 | 50.24 | 49.96 | 0.014706 | 0.305 | 3.05 | 50.24 | -1 | -1 | -10 | -3.475 | -3.475 | 0 | 12 | 1 | 1 | -3.475 | 10 | 0 | 0
1304 | 50.27 | 49.99 | 0 | 0.205 | 2.05 | 50.27 | -1 | -1 | -10 | -3.975 | -3.975 | 0 | 12 | 1 | 1 | -3.975 | 10 | 0 | 0
1304.05 | 50.29 | 50.01 | 0 | 0.105 | 1.05 | 50.29 | -1 | -1 | -10 | -4.475 | -4.475 | 0 | 12 | 1 | 1 | -4.475 | 10 | 0 | 0
1304.1 | 50.32 | 50.04 | -0.014706 | 0.005 | 0.05 | 50.32 | -1 | -1 | -10 | -4.975 | -4.975 | 0 | 12 | 1 | 1 | -4.975 | 10 | 0 | 0
1304.15 | 50.35 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.35 | -1 | -1 | -10 | -5.1324 | -5.1324 | 0 | 12 | 1 | 1 | -5.1324 | 10 | 0 | 0
1304.2 | 50.37 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 50.37 | -1 | -1 | -10 | -5.2206 | -5.2206 | 0 | 12 | 1 | 1 | -5.2206 | 10 | 0 | 0
1304.25 | 50.4 | 50.12 | -0.24 | -0.14412 | -1.4412 | 50.4 | -1 | -1 | -10 | -5.7206 | -5.7206 | 0 | 12 | 1 | 1 | -5.7206 | 10 | 0 | 0
1304.3 | 50.42 | 50.14 | -0.43 | -0.24412 | -2.4412 | 50.42 | -1 | -1 | -10 | -6.2206 | -6.2206 | 0 | 12 | 1 | 1 | -6.2206 | 10 | 0 | 0
1304.35 | 50.45 | 50.17 | -0.715 | -0.34412 | -3.4412 | 50.45 | -1 | -1 | -10 | -6.7206 | -6.7206 | 0 | 12 | 1 | 1 | -6.7206 | 10 | 0 | 0
1304.4 | 50.47 | 50.19 | -0.905 | -0.44412 | -4.4412 | 50.47 | -1 | -1 | -10 | -7.2206 | -7.2206 | 0 | 12 | 1 | 1 | -7.2206 | 10 | 0 | 0
1304.45 | 50.5 | 50.22 | -1 | -0.54412 | -5.4412 | 50.5 | -1 | -1 | -10 | -7.7206 | -7.7206 | 0 | 12 | 1 | 1 | -7.7206 | 10 | 0 | 0
1304.5 | 50.5 | 50.24 | -1 | -0.64412 | -6.4412 | 50.5 | -1 | -1 | -10 | -8.2206 | -8.2206 | 0 | 12 | 1 | 1 | -8.2206 | 10 | 0 | 0
1304.55 | 50.47 | 50.27 | -1 | -0.74412 | -7.4412 | 50.5 | -1 | -1 | -10 | -8.7206 | -8.7206 | 0 | 12 | 1 | 1 | -8.7206 | 10 | 0 | 0
1304.6 | 50.45 | 50.29 | -1 | -0.84412 | -8.4412 | 50.5 | -1 | -1 | -10 | -9.2206 | -9.2206 | 0 | 12 | 1 | 1 | -9.2206 | 10 | 0 | 0
1304.65 | 50.42 | 50.32 | -1 | -0.94412 | -9.4412 | 50.5 | -1 | -1 | -10 | -9.7206 | -9.7206 | 0 | 12 | 1 | 1 | -9.7206 | 10 | 0 | 0
1304.7 | 50.39 | 50.35 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1304.75 | 50.37 | 50.37 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1304.8 | 50.34 | 50.34 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1304.85 | 50.32 | 50.32 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1304.9 | 50.29 | 50.29 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1304.95 | 50.26 | 50.26 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1305 | 50.24 | 50.24 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1305.05 | 50.21 | 50.21 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1305.1 | 50.18 | 50.18 | -0.81 | -0.81 | -8.1 | 50.47 | -1 | -1 | -10 | -9.05 | -9.05 | 0 | 12 | 1 | 1 | -9.05 | 10 | 0 | 0
1305.15 | 50.16 | 50.16 | -0.62 | -0.62 | -6.2 | 50.45 | -1 | -1 | -10 | -8.1 | -8.1 | 0 | 12 | 1 | 1 | -8.1 | 10 | 0 | 0
1305.2 | 50.13 | 50.13 | -0.335 | -0.335 | -3.35 | 50.42 | -1 | -1 | -10 | -6.675 | -6.675 | 0 | 12 | 1 | 1 | -6.675 | 10 | 0 | 0
1305.25 | 50.11 | 50.11 | -0.145 | -0.145 | -1.45 | 50.39 | -1 | -1 | -10 | -5.725 | -5.725 | 0 | 12 | 1 | 1 | -5.725 | 10 | 0 | 0
1305.3 | 50.08 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 50.37 | -1 | -1 | -10 | -5.1912 | -5.1912 | 0 | 12 | 1 | 1 | -5.1912 | 10 | 0 | 0
1305.35 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.34 | -1 | -1 | -10 | -5.1029 | -5.1029 | 0 | 12 | 1 | 1 | -5.1029 | 10 | 0 | 0
1305.4 | 50.03 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 50.32 | -1 | -1 | -10 | -5.0441 | -5.0441 | 0 | 12 | 1 | 1 | -5.0441 | 10 | 0 | 0
1305.45 | 50 | 50 | 0 | 0 | 0 | 50.29 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1305.5 | 50 | 50 | 0 | 0 | 0 | 50.26 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1305.55 | 50 | 50 | 0 | 0 | 0 | 50.24 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1305.6 | 50 | 50 | 0 | 0 | 0 | 50.21 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1305.65 | 50 | 50 | 0 | 0 | 0 | 50.18 | -0.81 | -0.9 | -9 | -4.5 | -4.5 | 0 | 12 | 1 | 1 | -4.5 | 10 | 0 | 0
1305.7 | 50 | 50 | 0 | 0 | 0 | 50.16 | -0.62 | -0.8 | -8 | -4 | -4 | 0 | 12 | 1 | 1 | -4 | 10 | 0 | 0
1305.75 | 50 | 50 | 0 | 0 | 0 | 50.13 | -0.335 | -0.7 | -7 | -3.5 | -3.5 | 0 | 12 | 1 | 1 | -3.5 | 10 | 0 | 0
1305.8 | 50.01 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.6 | -6 | -3 | -3 | 0 | 12 | 1 | 1 | -3 | 10 | 0 | 0
1305.85 | 50.01 | 50 | 0 | 0 | 0 | 50.08 | -0.038235 | -0.5 | -5 | -2.5 | -2.5 | 0 | 12 | 1 | 1 | -2.5 | 10 | 0 | 0
1305.9 | 49.99 | 49.99 | 0 | 0 | 0 | 50.05 | -0.020588 | -0.4 | -4 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
1305.95 | 49.99 | 49.99 | 0 | 0 | 0 | 50.03 | -0.0088235 | -0.3 | -3 | -1.5 | -1.5 | 0 | 12 | 1 | 1 | -1.5 | 10 | 0 | 0
1306 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | -0.2 | -2 | -0.83824 | -0.83824 | 0 | 12 | 1 | 1 | -0.83824 | 10 | 0 | 0
1306.05 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | -0.1 | -1 | -0.33824 | -0.33824 | 0 | 12 | 1 | 1 | -0.33824 | 10 | 0 | 0
1306.1 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
1306.15 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
1306.2 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
1306.25 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
1306.3 | 49.89 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
1306.35 | 49.89 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
1306.4 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50.01 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1306.45 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1306.5 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1306.55 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 2.7868 | 2.7868 | 0 | 12 | 1 | 1 | 2.7868 | 10 | 0 | 0
1306.6 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 2.7868 | 2.7868 | 0 | 12 | 1 | 1 | 2.7868 | 10 | 0 | 0
1306.65 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 2.8456 | 2.8456 | 0 | 12 | 1 | 1 | 2.8456 | 10 | 0 | 0
1306.7 | 49.94 | 49.85 | 0.525 | 0.525 | 5.25 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 2.7574 | 2.7574 | 0 | 12 | 1 | 1 | 2.7574 | 10 | 0 | 0
1306.75 | 49.94 | 49.85 | 0.525 | 0.525 | 5.25 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 2.7574 | 2.7574 | 0 | 12 | 1 | 1 | 2.7574 | 10 | 0 | 0
1306.8 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1306.85 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1306.9 | 49.93 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1306.95 | 49.93 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1307 | 49.96 | 49.85 | 0.525 | 0.525 | 5.25 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 2.6985 | 2.6985 | 0 | 12 | 1 | 1 | 2.6985 | 10 | 0 | 0
1307.05 | 49.96 | 49.85 | 0.525 | 0.525 | 5.25 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 2.6985 | 2.6985 | 0 | 12 | 1 | 1 | 2.6985 | 10 | 0 | 0
1307.1 | 49.99 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1307.15 | 49.99 | 49.91 | 0.044118 | 0.425 | 4.25 | 49.99 | 0 | 0 | 0 | 2.125 | 2.125 | 0 | 12 | 1 | 1 | 2.125 | 10 | 0 | 0
1307.2 | 49.99 | 49.91 | 0.044118 | 0.325 | 3.25 | 49.99 | 0 | 0 | 0 | 1.625 | 1.625 | 0 | 12 | 1 | 1 | 1.625 | 10 | 0 | 0
1307.25 | 49.99 | 49.93 | 0.032353 | 0.225 | 2.25 | 49.99 | 0 | 0 | 0 | 1.125 | 1.125 | 0 | 12 | 1 | 1 | 1.125 | 10 | 0 | 0
1307.3 | 49.96 | 49.93 | 0.032353 | 0.125 | 1.25 | 49.99 | 0 | 0 | 0 | 0.625 | 0.625 | 0 | 12 | 1 | 1 | 0.625 | 10 | 0 | 0
1307.35 | 49.96 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 49.99 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1307.4 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1307.45 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1307.5 | 50.05 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.058824 | 0.058824 | 0 | 12 | 1 | 1 | 0.058824 | 10 | 0 | 0
1307.55 | 50.05 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
1307.6 | 49.97 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
1307.65 | 49.97 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
1307.7 | 49.92 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1307.75 | 49.92 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1307.8 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1307.85 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1307.9 | 49.94 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1307.95 | 49.94 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1308 | 50.01 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1308.05 | 50.01 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1308.1 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1308.15 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
1308.2 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
1308.25 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
1308.3 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
1308.35 | 49.95 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
1308.4 | 49.97 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
1308.45 | 49.97 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
1308.5 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
1308.55 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
1308.6 | 49.87 | 49.87 | 0.335 | 0.335 | 3.35 | 50.01 | 0 | 0 | 0 | 1.675 | 1.675 | 0 | 12 | 1 | 1 | 1.675 | 10 | 0 | 0
1308.65 | 49.87 | 49.87 | 0.335 | 0.335 | 3.35 | 49.99 | 0 | 0 | 0 | 1.675 | 1.675 | 0 | 12 | 1 | 1 | 1.675 | 10 | 0 | 0
1308.7 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1308.75 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 2.6691 | 2.6691 | 0 | 12 | 1 | 1 | 2.6691 | 10 | 0 | 0
1308.8 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1308.85 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1308.9 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1308.95 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1309 | 49.84 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1309.05 | 49.84 | 49.79 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
1309.1 | 49.89 | 49.79 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
1309.15 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.12647 | 1.2647 | 5.6324 | 5.6324 | 0 | 12 | 1 | 1 | 5.6324 | 10 | 0 | 0
1309.2 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.145 | 1.45 | 5.725 | 5.725 | 0 | 12 | 1 | 1 | 5.725 | 10 | 0 | 0
1309.25 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.145 | 1.45 | 5.725 | 5.725 | 0 | 12 | 1 | 1 | 5.725 | 10 | 0 | 0
1309.3 | 49.96 | 49.79 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
1309.35 | 49.96 | 49.79 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
1309.4 | 50.02 | 49.79 | 1 | 1 | 10 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 4.9853 | 4.9853 | 0 | 12 | 1 | 1 | 4.9853 | 10 | 0 | 0
1309.45 | 50.02 | 49.79 | 1 | 1 | 10 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 4.9853 | 4.9853 | 0 | 12 | 1 | 1 | 4.9853 | 10 | 0 | 0
1309.5 | 50.03 | 49.79 | 1 | 1 | 10 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.9559 | 4.9559 | 0 | 12 | 1 | 1 | 4.9559 | 10 | 0 | 0
1309.55 | 50.03 | 49.84 | 0.62 | 0.9 | 9 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.4559 | 4.4559 | 0 | 12 | 1 | 1 | 4.4559 | 10 | 0 | 0
1309.6 | 50.02 | 49.84 | 0.62 | 0.8 | 8 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 3.9559 | 3.9559 | 0 | 12 | 1 | 1 | 3.9559 | 10 | 0 | 0
1309.65 | 50.02 | 49.89 | 0.145 | 0.7 | 7 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 3.4559 | 3.4559 | 0 | 12 | 1 | 1 | 3.4559 | 10 | 0 | 0
1309.7 | 50.08 | 49.89 | 0.145 | 0.6 | 6 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 2.8088 | 2.8088 | 0 | 12 | 1 | 1 | 2.8088 | 10 | 0 | 0
1309.75 | 50.08 | 49.89 | 0.145 | 0.5 | 5 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 2.3088 | 2.3088 | 0 | 12 | 1 | 1 | 2.3088 | 10 | 0 | 0
1309.8 | 50.01 | 49.89 | 0.145 | 0.4 | 4 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 1.8088 | 1.8088 | 0 | 12 | 1 | 1 | 1.8088 | 10 | 0 | 0
1309.85 | 50.01 | 49.96 | 0.014706 | 0.3 | 3 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 1.3088 | 1.3088 | 0 | 12 | 1 | 1 | 1.3088 | 10 | 0 | 0
1309.9 | 49.94 | 49.94 | 0.026471 | 0.2 | 2 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.80882 | 0.80882 | 0 | 12 | 1 | 1 | 0.80882 | 10 | 0 | 0
1309.95 | 49.94 | 49.94 | 0.026471 | 0.1 | 1 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.30882 | 0.30882 | 0 | 12 | 1 | 1 | 0.30882 | 10 | 0 | 0
1310 | 50 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
1310.05 | 50 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
1310.1 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
1310.15 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
1310.2 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1310.25 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1310.3 | 49.92 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1310.35 | 49.92 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
1310.4 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50.01 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1310.45 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1310.5 | 49.92 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1310.55 | 49.92 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1310.6 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1310.65 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1310.7 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1310.75 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1310.8 | 49.87 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1310.85 | 49.87 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1310.9 | 49.8 | 49.8 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1310.95 | 49.8 | 49.8 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1311 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1311.05 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1311.1 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1311.15 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1311.2 | 49.72 | 49.72 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1311.25 | 49.72 | 49.72 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1311.3 | 49.67 | 49.67 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1311.35 | 49.67 | 49.67 | 1 | 1 | 10 | 49.87 | 0.335 | 0.14412 | 1.4412 | 5.7206 | 5.7206 | 0 | 12 | 1 | 1 | 5.7206 | 10 | 0 | 0
1311.4 | 49.65 | 49.65 | 1 | 1 | 10 | 49.87 | 0.335 | 0.24412 | 2.4412 | 6.2206 | 6.2206 | 0 | 12 | 1 | 1 | 6.2206 | 10 | 0 | 0
1311.45 | 49.65 | 49.65 | 1 | 1 | 10 | 49.8 | 1 | 0.34412 | 3.4412 | 6.7206 | 6.7206 | 0 | 12 | 1 | 1 | 6.7206 | 10 | 0 | 0
1311.5 | 49.59 | 49.59 | 1 | 1 | 10 | 49.8 | 1 | 0.44412 | 4.4412 | 7.2206 | 7.2206 | 0 | 12 | 1 | 1 | 7.2206 | 10 | 0 | 0
1311.55 | 49.59 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.54412 | 5.4412 | 7.7206 | 7.7206 | 0 | 12 | 1 | 1 | 7.7206 | 10 | 0 | 0
1311.6 | 49.66 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.64412 | 6.4412 | 8.2206 | 8.2206 | 0 | 12 | 1 | 1 | 8.2206 | 10 | 0 | 0
1311.65 | 49.66 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.74412 | 7.4412 | 8.7206 | 8.7206 | 0 | 12 | 1 | 1 | 8.7206 | 10 | 0 | 0
1311.7 | 49.63 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.84412 | 8.4412 | 9.2206 | 9.2206 | 0 | 12 | 1 | 1 | 9.2206 | 10 | 0 | 0
1311.75 | 49.63 | 49.59 | 1 | 1 | 10 | 49.72 | 1 | 0.94412 | 9.4412 | 9.7206 | 9.7206 | 0 | 12 | 1 | 1 | 9.7206 | 10 | 0 | 0
1311.8 | 49.61 | 49.59 | 1 | 1 | 10 | 49.72 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1311.85 | 49.61 | 49.59 | 1 | 1 | 10 | 49.67 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1311.9 | 49.54 | 49.54 | 1 | 1 | 10 | 49.67 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1311.95 | 49.54 | 49.54 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1312 | 49.46 | 49.46 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1312.05 | 49.46 | 49.46 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1312.1 | 49.45 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1312.15 | 49.45 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1312.2 | 49.51 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1312.25 | 49.51 | 49.45 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1312.3 | 49.5 | 49.45 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1312.35 | 49.5 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1312.4 | 49.54 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1312.45 | 49.54 | 49.45 | 1 | 1 | 10 | 49.54 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1312.5 | 49.59 | 49.45 | 1 | 1 | 10 | 49.59 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1312.55 | 49.59 | 49.45 | 1 | 1 | 10 | 49.59 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1312.6 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1312.65 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1312.7 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1312.75 | 49.61 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1312.8 | 49.53 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1312.85 | 49.53 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1312.9 | 49.54 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1312.95 | 49.54 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1313 | 49.61 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1313.05 | 49.61 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1313.1 | 49.66 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1313.15 | 49.66 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1313.2 | 49.64 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1313.25 | 49.64 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1313.3 | 49.69 | 49.53 | 1 | 1 | 10 | 49.69 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1313.35 | 49.69 | 49.53 | 1 | 1 | 10 | 49.69 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1313.4 | 49.74 | 49.53 | 1 | 1 | 10 | 49.74 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1313.45 | 49.74 | 49.54 | 1 | 1 | 10 | 49.74 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1313.5 | 49.78 | 49.54 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1313.55 | 49.78 | 49.61 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1313.6 | 49.82 | 49.61 | 1 | 1 | 10 | 49.82 | 0.81 | 0.81 | 8.1 | 9.05 | 9.05 | 0 | 12 | 1 | 1 | 9.05 | 10 | 0 | 0
1313.65 | 49.82 | 49.64 | 1 | 1 | 10 | 49.82 | 0.81 | 0.81 | 8.1 | 9.05 | 9.05 | 0 | 12 | 1 | 1 | 9.05 | 10 | 0 | 0
1313.7 | 49.86 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
1313.75 | 49.86 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
1313.8 | 49.84 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
1313.85 | 49.84 | 49.69 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
1313.9 | 49.91 | 49.69 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1313.95 | 49.91 | 49.74 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1314 | 49.97 | 49.74 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1314.05 | 49.97 | 49.78 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1314.1 | 50.03 | 49.78 | 1 | 1 | 10 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.9559 | 4.9559 | 0 | 12 | 1 | 1 | 4.9559 | 10 | 0 | 0
1314.15 | 50.03 | 49.82 | 0.81 | 0.9 | 9 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.4559 | 4.4559 | 0 | 12 | 1 | 1 | 4.4559 | 10 | 0 | 0
1314.2 | 50.05 | 49.82 | 0.81 | 0.81 | 8.1 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 3.9471 | 3.9471 | 0 | 12 | 1 | 1 | 3.9471 | 10 | 0 | 0
1314.25 | 50.05 | 49.84 | 0.62 | 0.71 | 7.1 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 3.4471 | 3.4471 | 0 | 12 | 1 | 1 | 3.4471 | 10 | 0 | 0
1314.3 | 50.01 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
1314.35 | 50.01 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
1314.4 | 49.95 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
1314.45 | 49.95 | 49.91 | 0.044118 | 0.52 | 5.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.4971 | 2.4971 | 0 | 12 | 1 | 1 | 2.4971 | 10 | 0 | 0
1314.5 | 49.99 | 49.91 | 0.044118 | 0.42 | 4.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 1.9971 | 1.9971 | 0 | 12 | 1 | 1 | 1.9971 | 10 | 0 | 0
1314.55 | 49.99 | 49.95 | 0.020588 | 0.32 | 3.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 1.4971 | 1.4971 | 0 | 12 | 1 | 1 | 1.4971 | 10 | 0 | 0
1314.6 | 49.92 | 49.92 | 0.038235 | 0.22 | 2.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.99706 | 0.99706 | 0 | 12 | 1 | 1 | 0.99706 | 10 | 0 | 0
1314.65 | 49.92 | 49.92 | 0.038235 | 0.12 | 1.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.49706 | 0.49706 | 0 | 12 | 1 | 1 | 0.49706 | 10 | 0 | 0
1314.7 | 49.97 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1314.75 | 49.97 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1314.8 | 50.02 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1314.85 | 50.02 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.17647 | 0.17647 | 0 | 12 | 1 | 1 | 0.17647 | 10 | 0 | 0
1314.9 | 50.07 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1314.95 | 50.07 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1315 | 50.06 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1315.05 | 50.06 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1315.1 | 50.13 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
1315.15 | 50.13 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
1315.2 | 50.09 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
1315.25 | 50.09 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6309 | -1.6309 | 0 | 12 | 1 | 1 | -1.6309 | 10 | 0 | 0
1315.3 | 50.07 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6309 | -1.6309 | 0 | 12 | 1 | 1 | -1.6309 | 10 | 0 | 0
1315.35 | 50.07 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6897 | -1.6897 | 0 | 12 | 1 | 1 | -1.6897 | 10 | 0 | 0
1315.4 | 50.07 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6897 | -1.6897 | 0 | 12 | 1 | 1 | -1.6897 | 10 | 0 | 0
1315.45 | 50.07 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.13 | -0.335 | -0.335 | -3.35 | -1.8074 | -1.8074 | 0 | 12 | 1 | 1 | -1.8074 | 10 | 0 | 0
1315.5 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.13 | -0.335 | -0.335 | -3.35 | -1.7779 | -1.7779 | 0 | 12 | 1 | 1 | -1.7779 | 10 | 0 | 0
1315.55 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.13 | -0.335 | -0.335 | -3.35 | -1.7779 | -1.7779 | 0 | 12 | 1 | 1 | -1.7779 | 10 | 0 | 0
1315.6 | 50.01 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
1315.65 | 50.01 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
1315.7 | 50.07 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
1315.75 | 50.07 | 50.01 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.235 | -2.35 | -1.175 | -1.175 | 0 | 12 | 1 | 1 | -1.175 | 10 | 0 | 0
1315.8 | 50.05 | 50.01 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.135 | -1.35 | -0.675 | -0.675 | 0 | 12 | 1 | 1 | -0.675 | 10 | 0 | 0
1315.85 | 50.05 | 50.01 | 0 | 0 | 0 | 50.07 | -0.032353 | -0.035 | -0.35 | -0.175 | -0.175 | 0 | 12 | 1 | 1 | -0.175 | 10 | 0 | 0
1315.9 | 50.1 | 50.01 | 0 | 0 | 0 | 50.1 | -0.05 | -0.05 | -0.5 | -0.25 | -0.25 | 0 | 12 | 1 | 1 | -0.25 | 10 | 0 | 0
1315.95 | 50.1 | 50.01 | 0 | 0 | 0 | 50.1 | -0.05 | -0.05 | -0.5 | -0.25 | -0.25 | 0 | 12 | 1 | 1 | -0.25 | 10 | 0 | 0
1316 | 50.11 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1316.05 | 50.11 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1316.1 | 50.06 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1316.15 | 50.06 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1316.2 | 50.04 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1316.25 | 50.04 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1316.3 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1316.35 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1316.4 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1316.45 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1316.5 | 50.11 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1316.55 | 50.11 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1316.6 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1316.65 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1316.7 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1316.75 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1316.8 | 50.02 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.11 | -0.145 | -0.145 | -1.45 | -0.73971 | -0.73971 | 0 | 12 | 1 | 1 | -0.73971 | 10 | 0 | 0
1316.85 | 50.02 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.11 | -0.145 | -0.145 | -1.45 | -0.73971 | -0.73971 | 0 | 12 | 1 | 1 | -0.73971 | 10 | 0 | 0
1316.9 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1316.95 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1317 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1317.05 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1317.1 | 50.01 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1317.15 | 50.01 | 50 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.045 | -0.45 | -0.225 | -0.225 | 0 | 12 | 1 | 1 | -0.225 | 10 | 0 | 0
1317.2 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
1317.25 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
1317.3 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
1317.35 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1317.4 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.14706 | 0.14706 | 0 | 12 | 1 | 1 | 0.14706 | 10 | 0 | 0
1317.45 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1317.5 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1317.55 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1317.6 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1317.65 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1317.7 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1317.75 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1317.8 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1317.85 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1317.9 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1317.95 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1318 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1318.05 | 50 | 50 | 0 | 0 | 0 | 50.01 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1318.1 | 49.5 | 49.5 | 1 | 1 | 10 | 50.01 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1318.15 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1318.2 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1318.25 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1318.3 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1318.35 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1318.4 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1318.45 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1318.5 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1318.55 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1318.6 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1318.65 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.1 | 1 | 5.5 | 5.5 | 0 | 12 | 1 | 1 | 5.5 | 10 | 0 | 0
1318.7 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.2 | 2 | 6 | 6 | 0 | 12 | 1 | 1 | 6 | 10 | 0 | 0
1318.75 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.3 | 3 | 6.5 | 6.5 | 0 | 12 | 1 | 1 | 6.5 | 10 | 0 | 0
1318.8 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.4 | 4 | 7 | 7 | 0 | 12 | 1 | 1 | 7 | 10 | 0 | 0
1318.85 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.5 | 5 | 7.5 | 7.5 | 0 | 12 | 1 | 1 | 7.5 | 10 | 0 | 0
1318.9 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.6 | 6 | 8 | 8 | 0 | 12 | 1 | 1 | 8 | 10 | 0 | 0
1318.95 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.7 | 7 | 8.5 | 8.5 | 0 | 12 | 1 | 1 | 8.5 | 10 | 0 | 0
1319 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.8 | 8 | 9 | 9 | 0 | 12 | 1 | 1 | 9 | 10 | 0 | 0
1319.05 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.9 | 9 | 9.5 | 9.5 | 0 | 12 | 1 | 1 | 9.5 | 10 | 0 | 0
1319.1 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1319.15 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1319.2 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1319.25 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1319.3 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1319.35 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1319.4 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1319.45 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1319.5 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1319.55 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1319.6 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1319.65 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1319.7 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1319.75 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1319.8 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1319.85 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1319.9 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1319.95 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1320 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1320.05 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1320.1 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1320.15 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1320.2 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1320.25 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1320.3 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1320.35 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1320.4 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1320.45 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1320.5 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1320.55 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1320.6 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1320.65 | 50.5 | 50.5 | -1 | 0.9 | 9 | 50.5 | -1 | -1 | -10 | -0.5 | -0.5 | 0 | 12 | 1 | 1 | -0.5 | 10 | 0 | 0
1320.7 | 50.5 | 50.5 | -1 | 0.8 | 8 | 50.5 | -1 | -1 | -10 | -1 | -1 | 0 | 12 | 1 | 1 | -1 | 10 | 0 | 0
1320.75 | 50.5 | 50.5 | -1 | 0.7 | 7 | 50.5 | -1 | -1 | -10 | -1.5 | -1.5 | 0 | 12 | 1 | 1 | -1.5 | 10 | 0 | 0
1320.8 | 50.5 | 50.5 | -1 | 0.6 | 6 | 50.5 | -1 | -1 | -10 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
1320.85 | 50.5 | 50.5 | -1 | 0.5 | 5 | 50.5 | -1 | -1 | -10 | -2.5 | -2.5 | 0 | 12 | 1 | 1 | -2.5 | 10 | 0 | 0
1320.9 | 50.5 | 50.5 | -1 | 0.4 | 4 | 50.5 | -1 | -1 | -10 | -3 | -3 | 0 | 12 | 1 | 1 | -3 | 10 | 0 | 0
1320.95 | 50.5 | 50.5 | -1 | 0.3 | 3 | 50.5 | -1 | -1 | -10 | -3.5 | -3.5 | 0 | 12 | 1 | 1 | -3.5 | 10 | 0 | 0
1321 | 50.5 | 50.5 | -1 | 0.2 | 2 | 50.5 | -1 | -1 | -10 | -4 | -4 | 0 | 12 | 1 | 1 | -4 | 10 | 0 | 0
1321.05 | 50.5 | 50.5 | -1 | 0.1 | 1 | 50.5 | -1 | -1 | -10 | -4.5 | -4.5 | 0 | 12 | 1 | 1 | -4.5 | 10 | 0 | 0
1321.1 | 50.5 | 50.5 | -1 | 0 | 0 | 50.5 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1321.15 | 50.5 | 50.5 | -1 | -0.1 | -1 | 50.5 | -1 | -1 | -10 | -5.5 | -5.5 | 0 | 12 | 1 | 1 | -5.5 | 10 | 0 | 0
1321.2 | 50.5 | 50.5 | -1 | -0.2 | -2 | 50.5 | -1 | -1 | -10 | -6 | -6 | 0 | 12 | 1 | 1 | -6 | 10 | 0 | 0
1321.25 | 50.5 | 50.5 | -1 | -0.3 | -3 | 50.5 | -1 | -1 | -10 | -6.5 | -6.5 | 0 | 12 | 1 | 1 | -6.5 | 10 | 0 | 0
1321.3 | 50.5 | 50.5 | -1 | -0.4 | -4 | 50.5 | -1 | -1 | -10 | -7 | -7 | 0 | 12 | 1 | 1 | -7 | 10 | 0 | 0
1321.35 | 50.5 | 50.5 | -1 | -0.5 | -5 | 50.5 | -1 | -1 | -10 | -7.5 | -7.5 | 0 | 12 | 1 | 1 | -7.5 | 10 | 0 | 0
1321.4 | 50.5 | 50.5 | -1 | -0.6 | -6 | 50.5 | -1 | -1 | -10 | -8 | -8 | 0 | 12 | 1 | 1 | -8 | 10 | 0 | 0
1321.45 | 50.5 | 50.5 | -1 | -0.7 | -7 | 50.5 | -1 | -1 | -10 | -8.5 | -8.5 | 0 | 12 | 1 | 1 | -8.5 | 10 | 0 | 0
1321.5 | 50.5 | 50.5 | -1 | -0.8 | -8 | 50.5 | -1 | -1 | -10 | -9 | -9 | 0 | 12 | 1 | 1 | -9 | 10 | 0 | 0
1321.55 | 50.5 | 50.5 | -1 | -0.9 | -9 | 50.5 | -1 | -1 | -10 | -9.5 | -9.5 | 0 | 12 | 1 | 1 | -9.5 | 10 | 0 | 0
1321.6 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1321.65 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1321.7 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1321.75 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1321.8 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1321.85 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1321.9 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1321.95 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1322 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1322.05 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1322.1 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1322.15 | 50.47 | 50.47 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1322.2 | 50.45 | 50.45 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1322.25 | 50.42 | 50.42 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1322.3 | 50.4 | 50.4 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1322.35 | 50.37 | 50.37 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1322.4 | 50.35 | 50.35 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1322.45 | 50.32 | 50.32 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1322.5 | 50.29 | 50.29 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1322.55 | 50.27 | 50.27 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1322.6 | 50.24 | 50.24 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1322.65 | 50.22 | 50.22 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1322.7 | 50.19 | 50.19 | -0.905 | -0.905 | -9.05 | 50.47 | -1 | -1 | -10 | -9.525 | -9.525 | 0 | 12 | 1 | 1 | -9.525 | 10 | 0 | 0
1322.75 | 50.17 | 50.17 | -0.715 | -0.715 | -7.15 | 50.45 | -1 | -1 | -10 | -8.575 | -8.575 | 0 | 12 | 1 | 1 | -8.575 | 10 | 0 | 0
1322.8 | 50.14 | 50.14 | -0.43 | -0.43 | -4.3 | 50.42 | -1 | -1 | -10 | -7.15 | -7.15 | 0 | 12 | 1 | 1 | -7.15 | 10 | 0 | 0
1322.85 | 50.12 | 50.12 | -0.24 | -0.24 | -2.4 | 50.4 | -1 | -1 | -10 | -6.2 | -6.2 | 0 | 12 | 1 | 1 | -6.2 | 10 | 0 | 0
1322.9 | 50.09 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 50.37 | -1 | -1 | -10 | -5.2206 | -5.2206 | 0 | 12 | 1 | 1 | -5.2206 | 10 | 0 | 0
1322.95 | 50.06 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.35 | -1 | -1 | -10 | -5.1324 | -5.1324 | 0 | 12 | 1 | 1 | -5.1324 | 10 | 0 | 0
1323 | 50.04 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.32 | -1 | -1 | -10 | -5.0735 | -5.0735 | 0 | 12 | 1 | 1 | -5.0735 | 10 | 0 | 0
1323.05 | 50.01 | 50.01 | 0 | 0 | 0 | 50.29 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1323.1 | 49.99 | 49.99 | 0 | 0 | 0 | 50.27 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1323.15 | 49.96 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.24 | -1 | -1 | -10 | -4.9265 | -4.9265 | 0 | 12 | 1 | 1 | -4.9265 | 10 | 0 | 0
1323.2 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.22 | -1 | -1 | -10 | -4.8676 | -4.8676 | 0 | 12 | 1 | 1 | -4.8676 | 10 | 0 | 0
1323.25 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.19 | -0.905 | -0.905 | -9.05 | -4.3044 | -4.3044 | 0 | 12 | 1 | 1 | -4.3044 | 10 | 0 | 0
1323.3 | 49.88 | 49.88 | 0.24 | 0.24 | 2.4 | 50.17 | -0.715 | -0.805 | -8.05 | -2.825 | -2.825 | 0 | 12 | 1 | 1 | -2.825 | 10 | 0 | 0
1323.35 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.14 | -0.43 | -0.705 | -7.05 | -1.375 | -1.375 | 0 | 12 | 1 | 1 | -1.375 | 10 | 0 | 0
1323.4 | 49.83 | 49.83 | 0.715 | 0.715 | 7.15 | 50.12 | -0.24 | -0.605 | -6.05 | 0.55 | 0.55 | 0 | 12 | 1 | 1 | 0.55 | 10 | 0 | 0
1323.45 | 49.81 | 49.81 | 0.905 | 0.905 | 9.05 | 50.09 | -0.044118 | -0.505 | -5.05 | 2 | 2 | 0 | 12 | 1 | 1 | 2 | 10 | 0 | 0
1323.5 | 49.78 | 49.78 | 1 | 1 | 10 | 50.06 | -0.026471 | -0.405 | -4.05 | 2.975 | 2.975 | 0 | 12 | 1 | 1 | 2.975 | 10 | 0 | 0
1323.55 | 49.76 | 49.76 | 1 | 1 | 10 | 50.04 | -0.014706 | -0.305 | -3.05 | 3.475 | 3.475 | 0 | 12 | 1 | 1 | 3.475 | 10 | 0 | 0
1323.6 | 49.73 | 49.73 | 1 | 1 | 10 | 50.01 | 0 | -0.205 | -2.05 | 3.975 | 3.975 | 0 | 12 | 1 | 1 | 3.975 | 10 | 0 | 0
1323.65 | 49.71 | 49.71 | 1 | 1 | 10 | 49.99 | 0 | -0.105 | -1.05 | 4.475 | 4.475 | 0 | 12 | 1 | 1 | 4.475 | 10 | 0 | 0
1323.7 | 49.68 | 49.68 | 1 | 1 | 10 | 49.96 | 0.014706 | -0.005 | -0.05 | 4.975 | 4.975 | 0 | 12 | 1 | 1 | 4.975 | 10 | 0 | 0
1323.75 | 49.65 | 49.65 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
1323.8 | 49.63 | 49.63 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1323.85 | 49.6 | 49.6 | 1 | 1 | 10 | 49.88 | 0.24 | 0.14412 | 1.4412 | 5.7206 | 5.7206 | 0 | 12 | 1 | 1 | 5.7206 | 10 | 0 | 0
1323.9 | 49.58 | 49.58 | 1 | 1 | 10 | 49.86 | 0.43 | 0.24412 | 2.4412 | 6.2206 | 6.2206 | 0 | 12 | 1 | 1 | 6.2206 | 10 | 0 | 0
1323.95 | 49.55 | 49.55 | 1 | 1 | 10 | 49.83 | 0.715 | 0.34412 | 3.4412 | 6.7206 | 6.7206 | 0 | 12 | 1 | 1 | 6.7206 | 10 | 0 | 0
1324 | 49.53 | 49.53 | 1 | 1 | 10 | 49.81 | 0.905 | 0.44412 | 4.4412 | 7.2206 | 7.2206 | 0 | 12 | 1 | 1 | 7.2206 | 10 | 0 | 0
1324.05 | 49.5 | 49.5 | 1 | 1 | 10 | 49.78 | 1 | 0.54412 | 5.4412 | 7.7206 | 7.7206 | 0 | 12 | 1 | 1 | 7.7206 | 10 | 0 | 0
1324.1 | 49.5 | 49.5 | 1 | 1 | 10 | 49.76 | 1 | 0.64412 | 6.4412 | 8.2206 | 8.2206 | 0 | 12 | 1 | 1 | 8.2206 | 10 | 0 | 0
1324.15 | 49.53 | 49.5 | 1 | 1 | 10 | 49.73 | 1 | 0.74412 | 7.4412 | 8.7206 | 8.7206 | 0 | 12 | 1 | 1 | 8.7206 | 10 | 0 | 0
1324.2 | 49.55 | 49.5 | 1 | 1 | 10 | 49.71 | 1 | 0.84412 | 8.4412 | 9.2206 | 9.2206 | 0 | 12 | 1 | 1 | 9.2206 | 10 | 0 | 0
1324.25 | 49.58 | 49.5 | 1 | 1 | 10 | 49.68 | 1 | 0.94412 | 9.4412 | 9.7206 | 9.7206 | 0 | 12 | 1 | 1 | 9.7206 | 10 | 0 | 0
1324.3 | 49.6 | 49.5 | 1 | 1 | 10 | 49.65 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1324.35 | 49.63 | 49.5 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1324.4 | 49.65 | 49.5 | 1 | 1 | 10 | 49.65 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1324.45 | 49.68 | 49.5 | 1 | 1 | 10 | 49.68 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1324.5 | 49.71 | 49.5 | 1 | 1 | 10 | 49.71 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1324.55 | 49.73 | 49.5 | 1 | 1 | 10 | 49.73 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1324.6 | 49.76 | 49.5 | 1 | 1 | 10 | 49.76 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1324.65 | 49.78 | 49.5 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1324.7 | 49.81 | 49.53 | 1 | 1 | 10 | 49.81 | 0.905 | 0.905 | 9.05 | 9.525 | 9.525 | 0 | 12 | 1 | 1 | 9.525 | 10 | 0 | 0
1324.75 | 49.83 | 49.55 | 1 | 1 | 10 | 49.83 | 0.715 | 0.715 | 7.15 | 8.575 | 8.575 | 0 | 12 | 1 | 1 | 8.575 | 10 | 0 | 0
1324.8 | 49.86 | 49.58 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
1324.85 | 49.88 | 49.6 | 1 | 1 | 10 | 49.88 | 0.24 | 0.24 | 2.4 | 6.2 | 6.2 | 0 | 12 | 1 | 1 | 6.2 | 10 | 0 | 0
1324.9 | 49.91 | 49.63 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1324.95 | 49.94 | 49.65 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
1325 | 49.96 | 49.68 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
1325.05 | 49.99 | 49.71 | 1 | 1 | 10 | 49.99 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1325.1 | 50.01 | 49.73 | 1 | 1 | 10 | 50.01 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1325.15 | 50.04 | 49.76 | 1 | 1 | 10 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 4.9265 | 4.9265 | 0 | 12 | 1 | 1 | 4.9265 | 10 | 0 | 0
1325.2 | 50.06 | 49.78 | 1 | 1 | 10 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 4.8676 | 4.8676 | 0 | 12 | 1 | 1 | 4.8676 | 10 | 0 | 0
1325.25 | 50.09 | 49.81 | 0.905 | 0.905 | 9.05 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 4.3044 | 4.3044 | 0 | 12 | 1 | 1 | 4.3044 | 10 | 0 | 0
1325.3 | 50.12 | 49.83 | 0.715 | 0.805 | 8.05 | 50.12 | -0.24 | -0.24 | -2.4 | 2.825 | 2.825 | 0 | 12 | 1 | 1 | 2.825 | 10 | 0 | 0
1325.35 | 50.14 | 49.86 | 0.43 | 0.705 | 7.05 | 50.14 | -0.43 | -0.43 | -4.3 | 1.375 | 1.375 | 0 | 12 | 1 | 1 | 1.375 | 10 | 0 | 0
1325.4 | 50.17 | 49.88 | 0.24 | 0.605 | 6.05 | 50.17 | -0.715 | -0.715 | -7.15 | -0.55 | -0.55 | 0 | 12 | 1 | 1 | -0.55 | 10 | 0 | 0
1325.45 | 50.19 | 49.91 | 0.044118 | 0.505 | 5.05 | 50.19 | -0.905 | -0.905 | -9.05 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
1325.5 | 50.22 | 49.94 | 0.026471 | 0.405 | 4.05 | 50.22 | -1 | -1 | -10 | -2.975 | -2.975 | 0 | 12 | 1 | 1 | -2.975 | 10 | 0 | 0
1325.55 | 50.24 | 49.96 | 0.014706 | 0.305 | 3.05 | 50.24 | -1 | -1 | -10 | -3.475 | -3.475 | 0 | 12 | 1 | 1 | -3.475 | 10 | 0 | 0
1325.6 | 50.27 | 49.99 | 0 | 0.205 | 2.05 | 50.27 | -1 | -1 | -10 | -3.975 | -3.975 | 0 | 12 | 1 | 1 | -3.975 | 10 | 0 | 0
1325.65 | 50.29 | 50.01 | 0 | 0.105 | 1.05 | 50.29 | -1 | -1 | -10 | -4.475 | -4.475 | 0 | 12 | 1 | 1 | -4.475 | 10 | 0 | 0
1325.7 | 50.32 | 50.04 | -0.014706 | 0.005 | 0.05 | 50.32 | -1 | -1 | -10 | -4.975 | -4.975 | 0 | 12 | 1 | 1 | -4.975 | 10 | 0 | 0
1325.75 | 50.35 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.35 | -1 | -1 | -10 | -5.1324 | -5.1324 | 0 | 12 | 1 | 1 | -5.1324 | 10 | 0 | 0
1325.8 | 50.37 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 50.37 | -1 | -1 | -10 | -5.2206 | -5.2206 | 0 | 12 | 1 | 1 | -5.2206 | 10 | 0 | 0
1325.85 | 50.4 | 50.12 | -0.24 | -0.14412 | -1.4412 | 50.4 | -1 | -1 | -10 | -5.7206 | -5.7206 | 0 | 12 | 1 | 1 | -5.7206 | 10 | 0 | 0
1325.9 | 50.42 | 50.14 | -0.43 | -0.24412 | -2.4412 | 50.42 | -1 | -1 | -10 | -6.2206 | -6.2206 | 0 | 12 | 1 | 1 | -6.2206 | 10 | 0 | 0
1325.95 | 50.45 | 50.17 | -0.715 | -0.34412 | -3.4412 | 50.45 | -1 | -1 | -10 | -6.7206 | -6.7206 | 0 | 12 | 1 | 1 | -6.7206 | 10 | 0 | 0
1326 | 50.47 | 50.19 | -0.905 | -0.44412 | -4.4412 | 50.47 | -1 | -1 | -10 | -7.2206 | -7.2206 | 0 | 12 | 1 | 1 | -7.2206 | 10 | 0 | 0
1326.05 | 50.5 | 50.22 | -1 | -0.54412 | -5.4412 | 50.5 | -1 | -1 | -10 | -7.7206 | -7.7206 | 0 | 12 | 1 | 1 | -7.7206 | 10 | 0 | 0
1326.1 | 50.5 | 50.24 | -1 | -0.64412 | -6.4412 | 50.5 | -1 | -1 | -10 | -8.2206 | -8.2206 | 0 | 12 | 1 | 1 | -8.2206 | 10 | 0 | 0
1326.15 | 50.47 | 50.27 | -1 | -0.74412 | -7.4412 | 50.5 | -1 | -1 | -10 | -8.7206 | -8.7206 | 0 | 12 | 1 | 1 | -8.7206 | 10 | 0 | 0
1326.2 | 50.45 | 50.29 | -1 | -0.84412 | -8.4412 | 50.5 | -1 | -1 | -10 | -9.2206 | -9.2206 | 0 | 12 | 1 | 1 | -9.2206 | 10 | 0 | 0
1326.25 | 50.42 | 50.32 | -1 | -0.94412 | -9.4412 | 50.5 | -1 | -1 | -10 | -9.7206 | -9.7206 | 0 | 12 | 1 | 1 | -9.7206 | 10 | 0 | 0
1326.3 | 50.39 | 50.35 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1326.35 | 50.37 | 50.37 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1326.4 | 50.34 | 50.34 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1326.45 | 50.32 | 50.32 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1326.5 | 50.29 | 50.29 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1326.55 | 50.26 | 50.26 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1326.6 | 50.24 | 50.24 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1326.65 | 50.21 | 50.21 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1326.7 | 50.18 | 50.18 | -0.81 | -0.81 | -8.1 | 50.47 | -1 | -1 | -10 | -9.05 | -9.05 | 0 | 12 | 1 | 1 | -9.05 | 10 | 0 | 0
1326.75 | 50.16 | 50.16 | -0.62 | -0.62 | -6.2 | 50.45 | -1 | -1 | -10 | -8.1 | -8.1 | 0 | 12 | 1 | 1 | -8.1 | 10 | 0 | 0
1326.8 | 50.13 | 50.13 | -0.335 | -0.335 | -3.35 | 50.42 | -1 | -1 | -10 | -6.675 | -6.675 | 0 | 12 | 1 | 1 | -6.675 | 10 | 0 | 0
1326.85 | 50.11 | 50.11 | -0.145 | -0.145 | -1.45 | 50.39 | -1 | -1 | -10 | -5.725 | -5.725 | 0 | 12 | 1 | 1 | -5.725 | 10 | 0 | 0
1326.9 | 50.08 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 50.37 | -1 | -1 | -10 | -5.1912 | -5.1912 | 0 | 12 | 1 | 1 | -5.1912 | 10 | 0 | 0
1326.95 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.34 | -1 | -1 | -10 | -5.1029 | -5.1029 | 0 | 12 | 1 | 1 | -5.1029 | 10 | 0 | 0
1327 | 50.03 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 50.32 | -1 | -1 | -10 | -5.0441 | -5.0441 | 0 | 12 | 1 | 1 | -5.0441 | 10 | 0 | 0
1327.05 | 50 | 50 | 0 | 0 | 0 | 50.29 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1327.1 | 50 | 50 | 0 | 0 | 0 | 50.26 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1327.15 | 50 | 50 | 0 | 0 | 0 | 50.24 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1327.2 | 50 | 50 | 0 | 0 | 0 | 50.21 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1327.25 | 50 | 50 | 0 | 0 | 0 | 50.18 | -0.81 | -0.9 | -9 | -4.5 | -4.5 | 0 | 12 | 1 | 1 | -4.5 | 10 | 0 | 0
1327.3 | 50 | 50 | 0 | 0 | 0 | 50.16 | -0.62 | -0.8 | -8 | -4 | -4 | 0 | 12 | 1 | 1 | -4 | 10 | 0 | 0
1327.35 | 50 | 50 | 0 | 0 | 0 | 50.13 | -0.335 | -0.7 | -7 | -3.5 | -3.5 | 0 | 12 | 1 | 1 | -3.5 | 10 | 0 | 0
1327.4 | 50.01 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.6 | -6 | -3 | -3 | 0 | 12 | 1 | 1 | -3 | 10 | 0 | 0
1327.45 | 50.01 | 50 | 0 | 0 | 0 | 50.08 | -0.038235 | -0.5 | -5 | -2.5 | -2.5 | 0 | 12 | 1 | 1 | -2.5 | 10 | 0 | 0
1327.5 | 49.99 | 49.99 | 0 | 0 | 0 | 50.05 | -0.020588 | -0.4 | -4 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
1327.55 | 49.99 | 49.99 | 0 | 0 | 0 | 50.03 | -0.0088235 | -0.3 | -3 | -1.5 | -1.5 | 0 | 12 | 1 | 1 | -1.5 | 10 | 0 | 0
1327.6 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | -0.2 | -2 | -0.83824 | -0.83824 | 0 | 12 | 1 | 1 | -0.83824 | 10 | 0 | 0
1327.65 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | -0.1 | -1 | -0.33824 | -0.33824 | 0 | 12 | 1 | 1 | -0.33824 | 10 | 0 | 0
1327.7 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
1327.75 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
1327.8 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
1327.85 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
1327.9 | 49.89 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
1327.95 | 49.89 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
1328 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50.01 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1328.05 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1328.1 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1328.15 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 2.7868 | 2.7868 | 0 | 12 | 1 | 1 | 2.7868 | 10 | 0 | 0
1328.2 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 2.7868 | 2.7868 | 0 | 12 | 1 | 1 | 2.7868 | 10 | 0 | 0
1328.25 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 2.8456 | 2.8456 | 0 | 12 | 1 | 1 | 2.8456 | 10 | 0 | 0
1328.3 | 49.94 | 49.85 | 0.525 | 0.525 | 5.25 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 2.7574 | 2.7574 | 0 | 12 | 1 | 1 | 2.7574 | 10 | 0 | 0
1328.35 | 49.94 | 49.85 | 0.525 | 0.525 | 5.25 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 2.7574 | 2.7574 | 0 | 12 | 1 | 1 | 2.7574 | 10 | 0 | 0
1328.4 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1328.45 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1328.5 | 49.93 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1328.55 | 49.93 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1328.6 | 49.96 | 49.85 | 0.525 | 0.525 | 5.25 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 2.6985 | 2.6985 | 0 | 12 | 1 | 1 | 2.6985 | 10 | 0 | 0
1328.65 | 49.96 | 49.85 | 0.525 | 0.525 | 5.25 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 2.6985 | 2.6985 | 0 | 12 | 1 | 1 | 2.6985 | 10 | 0 | 0
1328.7 | 49.99 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1328.75 | 49.99 | 49.91 | 0.044118 | 0.425 | 4.25 | 49.99 | 0 | 0 | 0 | 2.125 | 2.125 | 0 | 12 | 1 | 1 | 2.125 | 10 | 0 | 0
1328.8 | 49.99 | 49.91 | 0.044118 | 0.325 | 3.25 | 49.99 | 0 | 0 | 0 | 1.625 | 1.625 | 0 | 12 | 1 | 1 | 1.625 | 10 | 0 | 0
1328.85 | 49.99 | 49.93 | 0.032353 | 0.225 | 2.25 | 49.99 | 0 | 0 | 0 | 1.125 | 1.125 | 0 | 12 | 1 | 1 | 1.125 | 10 | 0 | 0
1328.9 | 49.96 | 49.93 | 0.032353 | 0.125 | 1.25 | 49.99 | 0 | 0 | 0 | 0.625 | 0.625 | 0 | 12 | 1 | 1 | 0.625 | 10 | 0 | 0
1328.95 | 49.96 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 49.99 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1329 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1329.05 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1329.1 | 50.05 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.058824 | 0.058824 | 0 | 12 | 1 | 1 | 0.058824 | 10 | 0 | 0
1329.15 | 50.05 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
1329.2 | 49.97 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
1329.25 | 49.97 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
1329.3 | 49.92 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1329.35 | 49.92 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1329.4 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1329.45 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1329.5 | 49.94 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1329.55 | 49.94 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1329.6 | 50.01 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1329.65 | 50.01 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1329.7 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1329.75 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
1329.8 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
1329.85 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
1329.9 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
1329.95 | 49.95 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
1330 | 49.97 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
1330.05 | 49.97 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
1330.1 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
1330.15 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
1330.2 | 49.87 | 49.87 | 0.335 | 0.335 | 3.35 | 50.01 | 0 | 0 | 0 | 1.675 | 1.675 | 0 | 12 | 1 | 1 | 1.675 | 10 | 0 | 0
1330.25 | 49.87 | 49.87 | 0.335 | 0.335 | 3.35 | 49.99 | 0 | 0 | 0 | 1.675 | 1.675 | 0 | 12 | 1 | 1 | 1.675 | 10 | 0 | 0
1330.3 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1330.35 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 2.6691 | 2.6691 | 0 | 12 | 1 | 1 | 2.6691 | 10 | 0 | 0
1330.4 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1330.45 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1330.5 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1330.55 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1330.6 | 49.84 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1330.65 | 49.84 | 49.79 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
1330.7 | 49.89 | 49.79 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
1330.75 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.12647 | 1.2647 | 5.6324 | 5.6324 | 0 | 12 | 1 | 1 | 5.6324 | 10 | 0 | 0
1330.8 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.145 | 1.45 | 5.725 | 5.725 | 0 | 12 | 1 | 1 | 5.725 | 10 | 0 | 0
1330.85 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.145 | 1.45 | 5.725 | 5.725 | 0 | 12 | 1 | 1 | 5.725 | 10 | 0 | 0
1330.9 | 49.96 | 49.79 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
1330.95 | 49.96 | 49.79 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
1331 | 50.02 | 49.79 | 1 | 1 | 10 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 4.9853 | 4.9853 | 0 | 12 | 1 | 1 | 4.9853 | 10 | 0 | 0
1331.05 | 50.02 | 49.79 | 1 | 1 | 10 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 4.9853 | 4.9853 | 0 | 12 | 1 | 1 | 4.9853 | 10 | 0 | 0
1331.1 | 50.03 | 49.79 | 1 | 1 | 10 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.9559 | 4.9559 | 0 | 12 | 1 | 1 | 4.9559 | 10 | 0 | 0
1331.15 | 50.03 | 49.84 | 0.62 | 0.9 | 9 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.4559 | 4.4559 | 0 | 12 | 1 | 1 | 4.4559 | 10 | 0 | 0
1331.2 | 50.02 | 49.84 | 0.62 | 0.8 | 8 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 3.9559 | 3.9559 | 0 | 12 | 1 | 1 | 3.9559 | 10 | 0 | 0
1331.25 | 50.02 | 49.89 | 0.145 | 0.7 | 7 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 3.4559 | 3.4559 | 0 | 12 | 1 | 1 | 3.4559 | 10 | 0 | 0
1331.3 | 50.08 | 49.89 | 0.145 | 0.6 | 6 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 2.8088 | 2.8088 | 0 | 12 | 1 | 1 | 2.8088 | 10 | 0 | 0
1331.35 | 50.08 | 49.89 | 0.145 | 0.5 | 5 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 2.3088 | 2.3088 | 0 | 12 | 1 | 1 | 2.3088 | 10 | 0 | 0
1331.4 | 50.01 | 49.89 | 0.145 | 0.4 | 4 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 1.8088 | 1.8088 | 0 | 12 | 1 | 1 | 1.8088 | 10 | 0 | 0
1331.45 | 50.01 | 49.96 | 0.014706 | 0.3 | 3 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 1.3088 | 1.3088 | 0 | 12 | 1 | 1 | 1.3088 | 10 | 0 | 0
1331.5 | 49.94 | 49.94 | 0.026471 | 0.2 | 2 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.80882 | 0.80882 | 0 | 12 | 1 | 1 | 0.80882 | 10 | 0 | 0
1331.55 | 49.94 | 49.94 | 0.026471 | 0.1 | 1 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.30882 | 0.30882 | 0 | 12 | 1 | 1 | 0.30882 | 10 | 0 | 0
1331.6 | 50 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
1331.65 | 50 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
1331.7 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
1331.75 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
1331.8 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1331.85 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1331.9 | 49.92 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1331.95 | 49.92 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
1332 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50.01 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1332.05 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1332.1 | 49.92 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1332.15 | 49.92 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1332.2 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1332.25 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1332.3 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1332.35 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1332.4 | 49.87 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1332.45 | 49.87 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1332.5 | 49.8 | 49.8 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1332.55 | 49.8 | 49.8 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1332.6 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1332.65 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1332.7 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1332.75 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1332.8 | 49.72 | 49.72 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1332.85 | 49.72 | 49.72 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1332.9 | 49.67 | 49.67 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1332.95 | 49.67 | 49.67 | 1 | 1 | 10 | 49.87 | 0.335 | 0.14412 | 1.4412 | 5.7206 | 5.7206 | 0 | 12 | 1 | 1 | 5.7206 | 10 | 0 | 0
1333 | 49.65 | 49.65 | 1 | 1 | 10 | 49.87 | 0.335 | 0.24412 | 2.4412 | 6.2206 | 6.2206 | 0 | 12 | 1 | 1 | 6.2206 | 10 | 0 | 0
1333.05 | 49.65 | 49.65 | 1 | 1 | 10 | 49.8 | 1 | 0.34412 | 3.4412 | 6.7206 | 6.7206 | 0 | 12 | 1 | 1 | 6.7206 | 10 | 0 | 0
1333.1 | 49.59 | 49.59 | 1 | 1 | 10 | 49.8 | 1 | 0.44412 | 4.4412 | 7.2206 | 7.2206 | 0 | 12 | 1 | 1 | 7.2206 | 10 | 0 | 0
1333.15 | 49.59 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.54412 | 5.4412 | 7.7206 | 7.7206 | 0 | 12 | 1 | 1 | 7.7206 | 10 | 0 | 0
1333.2 | 49.66 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.64412 | 6.4412 | 8.2206 | 8.2206 | 0 | 12 | 1 | 1 | 8.2206 | 10 | 0 | 0
1333.25 | 49.66 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.74412 | 7.4412 | 8.7206 | 8.7206 | 0 | 12 | 1 | 1 | 8.7206 | 10 | 0 | 0
1333.3 | 49.63 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.84412 | 8.4412 | 9.2206 | 9.2206 | 0 | 12 | 1 | 1 | 9.2206 | 10 | 0 | 0
1333.35 | 49.63 | 49.59 | 1 | 1 | 10 | 49.72 | 1 | 0.94412 | 9.4412 | 9.7206 | 9.7206 | 0 | 12 | 1 | 1 | 9.7206 | 10 | 0 | 0
1333.4 | 49.61 | 49.59 | 1 | 1 | 10 | 49.72 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1333.45 | 49.61 | 49.59 | 1 | 1 | 10 | 49.67 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1333.5 | 49.54 | 49.54 | 1 | 1 | 10 | 49.67 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1333.55 | 49.54 | 49.54 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1333.6 | 49.46 | 49.46 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1333.65 | 49.46 | 49.46 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1333.7 | 49.45 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1333.75 | 49.45 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1333.8 | 49.51 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1333.85 | 49.51 | 49.45 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1333.9 | 49.5 | 49.45 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1333.95 | 49.5 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1334 | 49.54 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1334.05 | 49.54 | 49.45 | 1 | 1 | 10 | 49.54 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1334.1 | 49.59 | 49.45 | 1 | 1 | 10 | 49.59 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1334.15 | 49.59 | 49.45 | 1 | 1 | 10 | 49.59 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1334.2 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1334.25 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1334.3 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1334.35 | 49.61 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1334.4 | 49.53 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1334.45 | 49.53 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1334.5 | 49.54 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1334.55 | 49.54 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1334.6 | 49.61 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1334.65 | 49.61 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1334.7 | 49.66 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1334.75 | 49.66 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1334.8 | 49.64 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1334.85 | 49.64 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1334.9 | 49.69 | 49.53 | 1 | 1 | 10 | 49.69 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1334.95 | 49.69 | 49.53 | 1 | 1 | 10 | 49.69 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1335 | 49.74 | 49.53 | 1 | 1 | 10 | 49.74 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1335.05 | 49.74 | 49.54 | 1 | 1 | 10 | 49.74 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1335.1 | 49.78 | 49.54 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1335.15 | 49.78 | 49.61 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1335.2 | 49.82 | 49.61 | 1 | 1 | 10 | 49.82 | 0.81 | 0.81 | 8.1 | 9.05 | 9.05 | 0 | 12 | 1 | 1 | 9.05 | 10 | 0 | 0
1335.25 | 49.82 | 49.64 | 1 | 1 | 10 | 49.82 | 0.81 | 0.81 | 8.1 | 9.05 | 9.05 | 0 | 12 | 1 | 1 | 9.05 | 10 | 0 | 0
1335.3 | 49.86 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
1335.35 | 49.86 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
1335.4 | 49.84 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
1335.45 | 49.84 | 49.69 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
1335.5 | 49.91 | 49.69 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1335.55 | 49.91 | 49.74 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1335.6 | 49.97 | 49.74 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1335.65 | 49.97 | 49.78 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1335.7 | 50.03 | 49.78 | 1 | 1 | 10 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.9559 | 4.9559 | 0 | 12 | 1 | 1 | 4.9559 | 10 | 0 | 0
1335.75 | 50.03 | 49.82 | 0.81 | 0.9 | 9 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.4559 | 4.4559 | 0 | 12 | 1 | 1 | 4.4559 | 10 | 0 | 0
1335.8 | 50.05 | 49.82 | 0.81 | 0.81 | 8.1 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 3.9471 | 3.9471 | 0 | 12 | 1 | 1 | 3.9471 | 10 | 0 | 0
1335.85 | 50.05 | 49.84 | 0.62 | 0.71 | 7.1 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 3.4471 | 3.4471 | 0 | 12 | 1 | 1 | 3.4471 | 10 | 0 | 0
1335.9 | 50.01 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
1335.95 | 50.01 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
1336 | 49.95 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
1336.05 | 49.95 | 49.91 | 0.044118 | 0.52 | 5.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.4971 | 2.4971 | 0 | 12 | 1 | 1 | 2.4971 | 10 | 0 | 0
1336.1 | 49.99 | 49.91 | 0.044118 | 0.42 | 4.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 1.9971 | 1.9971 | 0 | 12 | 1 | 1 | 1.9971 | 10 | 0 | 0
1336.15 | 49.99 | 49.95 | 0.020588 | 0.32 | 3.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 1.4971 | 1.4971 | 0 | 12 | 1 | 1 | 1.4971 | 10 | 0 | 0
1336.2 | 49.92 | 49.92 | 0.038235 | 0.22 | 2.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.99706 | 0.99706 | 0 | 12 | 1 | 1 | 0.99706 | 10 | 0 | 0
1336.25 | 49.92 | 49.92 | 0.038235 | 0.12 | 1.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.49706 | 0.49706 | 0 | 12 | 1 | 1 | 0.49706 | 10 | 0 | 0
1336.3 | 49.97 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1336.35 | 49.97 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1336.4 | 50.02 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1336.45 | 50.02 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.17647 | 0.17647 | 0 | 12 | 1 | 1 | 0.17647 | 10 | 0 | 0
1336.5 | 50.07 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1336.55 | 50.07 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1336.6 | 50.06 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1336.65 | 50.06 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1336.7 | 50.13 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
1336.75 | 50.13 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
1336.8 | 50.09 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
1336.85 | 50.09 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6309 | -1.6309 | 0 | 12 | 1 | 1 | -1.6309 | 10 | 0 | 0
1336.9 | 50.07 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6309 | -1.6309 | 0 | 12 | 1 | 1 | -1.6309 | 10 | 0 | 0
1336.95 | 50.07 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6897 | -1.6897 | 0 | 12 | 1 | 1 | -1.6897 | 10 | 0 | 0
1337 | 50.07 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6897 | -1.6897 | 0 | 12 | 1 | 1 | -1.6897 | 10 | 0 | 0
1337.05 | 50.07 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.13 | -0.335 | -0.335 | -3.35 | -1.8074 | -1.8074 | 0 | 12 | 1 | 1 | -1.8074 | 10 | 0 | 0
1337.1 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.13 | -0.335 | -0.335 | -3.35 | -1.7779 | -1.7779 | 0 | 12 | 1 | 1 | -1.7779 | 10 | 0 | 0
1337.15 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.13 | -0.335 | -0.335 | -3.35 | -1.7779 | -1.7779 | 0 | 12 | 1 | 1 | -1.7779 | 10 | 0 | 0
1337.2 | 50.01 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
1337.25 | 50.01 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
1337.3 | 50.07 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
1337.35 | 50.07 | 50.01 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.235 | -2.35 | -1.175 | -1.175 | 0 | 12 | 1 | 1 | -1.175 | 10 | 0 | 0
1337.4 | 50.05 | 50.01 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.135 | -1.35 | -0.675 | -0.675 | 0 | 12 | 1 | 1 | -0.675 | 10 | 0 | 0
1337.45 | 50.05 | 50.01 | 0 | 0 | 0 | 50.07 | -0.032353 | -0.035 | -0.35 | -0.175 | -0.175 | 0 | 12 | 1 | 1 | -0.175 | 10 | 0 | 0
1337.5 | 50.1 | 50.01 | 0 | 0 | 0 | 50.1 | -0.05 | -0.05 | -0.5 | -0.25 | -0.25 | 0 | 12 | 1 | 1 | -0.25 | 10 | 0 | 0
1337.55 | 50.1 | 50.01 | 0 | 0 | 0 | 50.1 | -0.05 | -0.05 | -0.5 | -0.25 | -0.25 | 0 | 12 | 1 | 1 | -0.25 | 10 | 0 | 0
1337.6 | 50.11 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1337.65 | 50.11 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1337.7 | 50.06 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1337.75 | 50.06 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1337.8 | 50.04 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1337.85 | 50.04 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1337.9 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1337.95 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1338 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1338.05 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1338.1 | 50.11 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1338.15 | 50.11 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1338.2 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1338.25 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1338.3 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1338.35 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1338.4 | 50.02 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.11 | -0.145 | -0.145 | -1.45 | -0.73971 | -0.73971 | 0 | 12 | 1 | 1 | -0.73971 | 10 | 0 | 0
1338.45 | 50.02 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.11 | -0.145 | -0.145 | -1.45 | -0.73971 | -0.73971 | 0 | 12 | 1 | 1 | -0.73971 | 10 | 0 | 0
1338.5 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1338.55 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1338.6 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1338.65 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1338.7 | 50.01 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1338.75 | 50.01 | 50 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.045 | -0.45 | -0.225 | -0.225 | 0 | 12 | 1 | 1 | -0.225 | 10 | 0 | 0
1338.8 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
1338.85 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
1338.9 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
1338.95 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1339 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.14706 | 0.14706 | 0 | 12 | 1 | 1 | 0.14706 | 10 | 0 | 0
1339.05 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1339.1 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1339.15 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1339.2 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1339.25 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1339.3 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1339.35 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1339.4 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1339.45 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1339.5 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1339.55 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1339.6 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1339.65 | 50 | 50 | 0 | 0 | 0 | 50.01 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1339.7 | 49.5 | 49.5 | 1 | 1 | 10 | 50.01 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1339.75 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1339.8 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1339.85 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1339.9 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1339.95 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1340 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1340.05 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1340.1 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1340.15 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1340.2 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1340.25 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.1 | 1 | 5.5 | 5.5 | 0 | 12 | 1 | 1 | 5.5 | 10 | 0 | 0
1340.3 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.2 | 2 | 6 | 6 | 0 | 12 | 1 | 1 | 6 | 10 | 0 | 0
1340.35 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.3 | 3 | 6.5 | 6.5 | 0 | 12 | 1 | 1 | 6.5 | 10 | 0 | 0
1340.4 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.4 | 4 | 7 | 7 | 0 | 12 | 1 | 1 | 7 | 10 | 0 | 0
1340.45 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.5 | 5 | 7.5 | 7.5 | 0 | 12 | 1 | 1 | 7.5 | 10 | 0 | 0
1340.5 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.6 | 6 | 8 | 8 | 0 | 12 | 1 | 1 | 8 | 10 | 0 | 0
1340.55 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.7 | 7 | 8.5 | 8.5 | 0 | 12 | 1 | 1 | 8.5 | 10 | 0 | 0
1340.6 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.8 | 8 | 9 | 9 | 0 | 12 | 1 | 1 | 9 | 10 | 0 | 0
1340.65 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.9 | 9 | 9.5 | 9.5 | 0 | 12 | 1 | 1 | 9.5 | 10 | 0 | 0
1340.7 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1340.75 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1340.8 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1340.85 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1340.9 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1340.95 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1341 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1341.05 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1341.1 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1341.15 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1341.2 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1341.25 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1341.3 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1341.35 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1341.4 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1341.45 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1341.5 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1341.55 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1341.6 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1341.65 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1341.7 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1341.75 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1341.8 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1341.85 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1341.9 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1341.95 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1342 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1342.05 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1342.1 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1342.15 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1342.2 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1342.25 | 50.5 | 50.5 | -1 | 0.9 | 9 | 50.5 | -1 | -1 | -10 | -0.5 | -0.5 | 0 | 12 | 1 | 1 | -0.5 | 10 | 0 | 0
1342.3 | 50.5 | 50.5 | -1 | 0.8 | 8 | 50.5 | -1 | -1 | -10 | -1 | -1 | 0 | 12 | 1 | 1 | -1 | 10 | 0 | 0
1342.35 | 50.5 | 50.5 | -1 | 0.7 | 7 | 50.5 | -1 | -1 | -10 | -1.5 | -1.5 | 0 | 12 | 1 | 1 | -1.5 | 10 | 0 | 0
1342.4 | 50.5 | 50.5 | -1 | 0.6 | 6 | 50.5 | -1 | -1 | -10 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
1342.45 | 50.5 | 50.5 | -1 | 0.5 | 5 | 50.5 | -1 | -1 | -10 | -2.5 | -2.5 | 0 | 12 | 1 | 1 | -2.5 | 10 | 0 | 0
1342.5 | 50.5 | 50.5 | -1 | 0.4 | 4 | 50.5 | -1 | -1 | -10 | -3 | -3 | 0 | 12 | 1 | 1 | -3 | 10 | 0 | 0
1342.55 | 50.5 | 50.5 | -1 | 0.3 | 3 | 50.5 | -1 | -1 | -10 | -3.5 | -3.5 | 0 | 12 | 1 | 1 | -3.5 | 10 | 0 | 0
1342.6 | 50.5 | 50.5 | -1 | 0.2 | 2 | 50.5 | -1 | -1 | -10 | -4 | -4 | 0 | 12 | 1 | 1 | -4 | 10 | 0 | 0
1342.65 | 50.5 | 50.5 | -1 | 0.1 | 1 | 50.5 | -1 | -1 | -10 | -4.5 | -4.5 | 0 | 12 | 1 | 1 | -4.5 | 10 | 0 | 0
1342.7 | 50.5 | 50.5 | -1 | 0 | 0 | 50.5 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1342.75 | 50.5 | 50.5 | -1 | -0.1 | -1 | 50.5 | -1 | -1 | -10 | -5.5 | -5.5 | 0 | 12 | 1 | 1 | -5.5 | 10 | 0 | 0
1342.8 | 50.5 | 50.5 | -1 | -0.2 | -2 | 50.5 | -1 | -1 | -10 | -6 | -6 | 0 | 12 | 1 | 1 | -6 | 10 | 0 | 0
1342.85 | 50.5 | 50.5 | -1 | -0.3 | -3 | 50.5 | -1 | -1 | -10 | -6.5 | -6.5 | 0 | 12 | 1 | 1 | -6.5 | 10 | 0 | 0
1342.9 | 50.5 | 50.5 | -1 | -0.4 | -4 | 50.5 | -1 | -1 | -10 | -7 | -7 | 0 | 12 | 1 | 1 | -7 | 10 | 0 | 0
1342.95 | 50.5 | 50.5 | -1 | -0.5 | -5 | 50.5 | -1 | -1 | -10 | -7.5 | -7.5 | 0 | 12 | 1 | 1 | -7.5 | 10 | 0 | 0
1343 | 50.5 | 50.5 | -1 | -0.6 | -6 | 50.5 | -1 | -1 | -10 | -8 | -8 | 0 | 12 | 1 | 1 | -8 | 10 | 0 | 0
1343.05 | 50.5 | 50.5 | -1 | -0.7 | -7 | 50.5 | -1 | -1 | -10 | -8.5 | -8.5 | 0 | 12 | 1 | 1 | -8.5 | 10 | 0 | 0
1343.1 | 50.5 | 50.5 | -1 | -0.8 | -8 | 50.5 | -1 | -1 | -10 | -9 | -9 | 0 | 12 | 1 | 1 | -9 | 10 | 0 | 0
1343.15 | 50.5 | 50.5 | -1 | -0.9 | -9 | 50.5 | -1 | -1 | -10 | -9.5 | -9.5 | 0 | 12 | 1 | 1 | -9.5 | 10 | 0 | 0
1343.2 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1343.25 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1343.3 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1343.35 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1343.4 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1343.45 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1343.5 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1343.55 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1343.6 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1343.65 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1343.7 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1343.75 | 50.47 | 50.47 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1343.8 | 50.45 | 50.45 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1343.85 | 50.42 | 50.42 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1343.9 | 50.4 | 50.4 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1343.95 | 50.37 | 50.37 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1344 | 50.35 | 50.35 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1344.05 | 50.32 | 50.32 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1344.1 | 50.29 | 50.29 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1344.15 | 50.27 | 50.27 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1344.2 | 50.24 | 50.24 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1344.25 | 50.22 | 50.22 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1344.3 | 50.19 | 50.19 | -0.905 | -0.905 | -9.05 | 50.47 | -1 | -1 | -10 | -9.525 | -9.525 | 0 | 12 | 1 | 1 | -9.525 | 10 | 0 | 0
1344.35 | 50.17 | 50.17 | -0.715 | -0.715 | -7.15 | 50.45 | -1 | -1 | -10 | -8.575 | -8.575 | 0 | 12 | 1 | 1 | -8.575 | 10 | 0 | 0
1344.4 | 50.14 | 50.14 | -0.43 | -0.43 | -4.3 | 50.42 | -1 | -1 | -10 | -7.15 | -7.15 | 0 | 12 | 1 | 1 | -7.15 | 10 | 0 | 0
1344.45 | 50.12 | 50.12 | -0.24 | -0.24 | -2.4 | 50.4 | -1 | -1 | -10 | -6.2 | -6.2 | 0 | 12 | 1 | 1 | -6.2 | 10 | 0 | 0
1344.5 | 50.09 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 50.37 | -1 | -1 | -10 | -5.2206 | -5.2206 | 0 | 12 | 1 | 1 | -5.2206 | 10 | 0 | 0
1344.55 | 50.06 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.35 | -1 | -1 | -10 | -5.1324 | -5.1324 | 0 | 12 | 1 | 1 | -5.1324 | 10 | 0 | 0
1344.6 | 50.04 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.32 | -1 | -1 | -10 | -5.0735 | -5.0735 | 0 | 12 | 1 | 1 | -5.0735 | 10 | 0 | 0
1344.65 | 50.01 | 50.01 | 0 | 0 | 0 | 50.29 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1344.7 | 49.99 | 49.99 | 0 | 0 | 0 | 50.27 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1344.75 | 49.96 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.24 | -1 | -1 | -10 | -4.9265 | -4.9265 | 0 | 12 | 1 | 1 | -4.9265 | 10 | 0 | 0
1344.8 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.22 | -1 | -1 | -10 | -4.8676 | -4.8676 | 0 | 12 | 1 | 1 | -4.8676 | 10 | 0 | 0
1344.85 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.19 | -0.905 | -0.905 | -9.05 | -4.3044 | -4.3044 | 0 | 12 | 1 | 1 | -4.3044 | 10 | 0 | 0
1344.9 | 49.88 | 49.88 | 0.24 | 0.24 | 2.4 | 50.17 | -0.715 | -0.805 | -8.05 | -2.825 | -2.825 | 0 | 12 | 1 | 1 | -2.825 | 10 | 0 | 0
1344.95 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.14 | -0.43 | -0.705 | -7.05 | -1.375 | -1.375 | 0 | 12 | 1 | 1 | -1.375 | 10 | 0 | 0
1345 | 49.83 | 49.83 | 0.715 | 0.715 | 7.15 | 50.12 | -0.24 | -0.605 | -6.05 | 0.55 | 0.55 | 0 | 12 | 1 | 1 | 0.55 | 10 | 0 | 0
1345.05 | 49.81 | 49.81 | 0.905 | 0.905 | 9.05 | 50.09 | -0.044118 | -0.505 | -5.05 | 2 | 2 | 0 | 12 | 1 | 1 | 2 | 10 | 0 | 0
1345.1 | 49.78 | 49.78 | 1 | 1 | 10 | 50.06 | -0.026471 | -0.405 | -4.05 | 2.975 | 2.975 | 0 | 12 | 1 | 1 | 2.975 | 10 | 0 | 0
1345.15 | 49.76 | 49.76 | 1 | 1 | 10 | 50.04 | -0.014706 | -0.305 | -3.05 | 3.475 | 3.475 | 0 | 12 | 1 | 1 | 3.475 | 10 | 0 | 0
1345.2 | 49.73 | 49.73 | 1 | 1 | 10 | 50.01 | 0 | -0.205 | -2.05 | 3.975 | 3.975 | 0 | 12 | 1 | 1 | 3.975 | 10 | 0 | 0
1345.25 | 49.71 | 49.71 | 1 | 1 | 10 | 49.99 | 0 | -0.105 | -1.05 | 4.475 | 4.475 | 0 | 12 | 1 | 1 | 4.475 | 10 | 0 | 0
1345.3 | 49.68 | 49.68 | 1 | 1 | 10 | 49.96 | 0.014706 | -0.005 | -0.05 | 4.975 | 4.975 | 0 | 12 | 1 | 1 | 4.975 | 10 | 0 | 0
1345.35 | 49.65 | 49.65 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
1345.4 | 49.63 | 49.63 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1345.45 | 49.6 | 49.6 | 1 | 1 | 10 | 49.88 | 0.24 | 0.14412 | 1.4412 | 5.7206 | 5.7206 | 0 | 12 | 1 | 1 | 5.7206 | 10 | 0 | 0
1345.5 | 49.58 | 49.58 | 1 | 1 | 10 | 49.86 | 0.43 | 0.24412 | 2.4412 | 6.2206 | 6.2206 | 0 | 12 | 1 | 1 | 6.2206 | 10 | 0 | 0
1345.55 | 49.55 | 49.55 | 1 | 1 | 10 | 49.83 | 0.715 | 0.34412 | 3.4412 | 6.7206 | 6.7206 | 0 | 12 | 1 | 1 | 6.7206 | 10 | 0 | 0
1345.6 | 49.53 | 49.53 | 1 | 1 | 10 | 49.81 | 0.905 | 0.44412 | 4.4412 | 7.2206 | 7.2206 | 0 | 12 | 1 | 1 | 7.2206 | 10 | 0 | 0
1345.65 | 49.5 | 49.5 | 1 | 1 | 10 | 49.78 | 1 | 0.54412 | 5.4412 | 7.7206 | 7.7206 | 0 | 12 | 1 | 1 | 7.7206 | 10 | 0 | 0
1345.7 | 49.5 | 49.5 | 1 | 1 | 10 | 49.76 | 1 | 0.64412 | 6.4412 | 8.2206 | 8.2206 | 0 | 12 | 1 | 1 | 8.2206 | 10 | 0 | 0
1345.75 | 49.53 | 49.5 | 1 | 1 | 10 | 49.73 | 1 | 0.74412 | 7.4412 | 8.7206 | 8.7206 | 0 | 12 | 1 | 1 | 8.7206 | 10 | 0 | 0
1345.8 | 49.55 | 49.5 | 1 | 1 | 10 | 49.71 | 1 | 0.84412 | 8.4412 | 9.2206 | 9.2206 | 0 | 12 | 1 | 1 | 9.2206 | 10 | 0 | 0
1345.85 | 49.58 | 49.5 | 1 | 1 | 10 | 49.68 | 1 | 0.94412 | 9.4412 | 9.7206 | 9.7206 | 0 | 12 | 1 | 1 | 9.7206 | 10 | 0 | 0
1345.9 | 49.6 | 49.5 | 1 | 1 | 10 | 49.65 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1345.95 | 49.63 | 49.5 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1346 | 49.65 | 49.5 | 1 | 1 | 10 | 49.65 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1346.05 | 49.68 | 49.5 | 1 | 1 | 10 | 49.68 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1346.1 | 49.71 | 49.5 | 1 | 1 | 10 | 49.71 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1346.15 | 49.73 | 49.5 | 1 | 1 | 10 | 49.73 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1346.2 | 49.76 | 49.5 | 1 | 1 | 10 | 49.76 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1346.25 | 49.78 | 49.5 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1346.3 | 49.81 | 49.53 | 1 | 1 | 10 | 49.81 | 0.905 | 0.905 | 9.05 | 9.525 | 9.525 | 0 | 12 | 1 | 1 | 9.525 | 10 | 0 | 0
1346.35 | 49.83 | 49.55 | 1 | 1 | 10 | 49.83 | 0.715 | 0.715 | 7.15 | 8.575 | 8.575 | 0 | 12 | 1 | 1 | 8.575 | 10 | 0 | 0
1346.4 | 49.86 | 49.58 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
1346.45 | 49.88 | 49.6 | 1 | 1 | 10 | 49.88 | 0.24 | 0.24 | 2.4 | 6.2 | 6.2 | 0 | 12 | 1 | 1 | 6.2 | 10 | 0 | 0
1346.5 | 49.91 | 49.63 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1346.55 | 49.94 | 49.65 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
1346.6 | 49.96 | 49.68 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
1346.65 | 49.99 | 49.71 | 1 | 1 | 10 | 49.99 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1346.7 | 50.01 | 49.73 | 1 | 1 | 10 | 50.01 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1346.75 | 50.04 | 49.76 | 1 | 1 | 10 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 4.9265 | 4.9265 | 0 | 12 | 1 | 1 | 4.9265 | 10 | 0 | 0
1346.8 | 50.06 | 49.78 | 1 | 1 | 10 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 4.8676 | 4.8676 | 0 | 12 | 1 | 1 | 4.8676 | 10 | 0 | 0
1346.85 | 50.09 | 49.81 | 0.905 | 0.905 | 9.05 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 4.3044 | 4.3044 | 0 | 12 | 1 | 1 | 4.3044 | 10 | 0 | 0
1346.9 | 50.12 | 49.83 | 0.715 | 0.805 | 8.05 | 50.12 | -0.24 | -0.24 | -2.4 | 2.825 | 2.825 | 0 | 12 | 1 | 1 | 2.825 | 10 | 0 | 0
1346.95 | 50.14 | 49.86 | 0.43 | 0.705 | 7.05 | 50.14 | -0.43 | -0.43 | -4.3 | 1.375 | 1.375 | 0 | 12 | 1 | 1 | 1.375 | 10 | 0 | 0
1347 | 50.17 | 49.88 | 0.24 | 0.605 | 6.05 | 50.17 | -0.715 | -0.715 | -7.15 | -0.55 | -0.55 | 0 | 12 | 1 | 1 | -0.55 | 10 | 0 | 0
1347.05 | 50.19 | 49.91 | 0.044118 | 0.505 | 5.05 | 50.19 | -0.905 | -0.905 | -9.05 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
1347.1 | 50.22 | 49.94 | 0.026471 | 0.405 | 4.05 | 50.22 | -1 | -1 | -10 | -2.975 | -2.975 | 0 | 12 | 1 | 1 | -2.975 | 10 | 0 | 0
1347.15 | 50.24 | 49.96 | 0.014706 | 0.305 | 3.05 | 50.24 | -1 | -1 | -10 | -3.475 | -3.475 | 0 | 12 | 1 | 1 | -3.475 | 10 | 0 | 0
1347.2 | 50.27 | 49.99 | 0 | 0.205 | 2.05 | 50.27 | -1 | -1 | -10 | -3.975 | -3.975 | 0 | 12 | 1 | 1 | -3.975 | 10 | 0 | 0
1347.25 | 50.29 | 50.01 | 0 | 0.105 | 1.05 | 50.29 | -1 | -1 | -10 | -4.475 | -4.475 | 0 | 12 | 1 | 1 | -4.475 | 10 | 0 | 0
1347.3 | 50.32 | 50.04 | -0.014706 | 0.005 | 0.05 | 50.32 | -1 | -1 | -10 | -4.975 | -4.975 | 0 | 12 | 1 | 1 | -4.975 | 10 | 0 | 0
1347.35 | 50.35 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.35 | -1 | -1 | -10 | -5.1324 | -5.1324 | 0 | 12 | 1 | 1 | -5.1324 | 10 | 0 | 0
1347.4 | 50.37 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 50.37 | -1 | -1 | -10 | -5.2206 | -5.2206 | 0 | 12 | 1 | 1 | -5.2206 | 10 | 0 | 0
1347.45 | 50.4 | 50.12 | -0.24 | -0.14412 | -1.4412 | 50.4 | -1 | -1 | -10 | -5.7206 | -5.7206 | 0 | 12 | 1 | 1 | -5.7206 | 10 | 0 | 0
1347.5 | 50.42 | 50.14 | -0.43 | -0.24412 | -2.4412 | 50.42 | -1 | -1 | -10 | -6.2206 | -6.2206 | 0 | 12 | 1 | 1 | -6.2206 | 10 | 0 | 0
1347.55 | 50.45 | 50.17 | -0.715 | -0.34412 | -3.4412 | 50.45 | -1 | -1 | -10 | -6.7206 | -6.7206 | 0 | 12 | 1 | 1 | -6.7206 | 10 | 0 | 0
1347.6 | 50.47 | 50.19 | -0.905 | -0.44412 | -4.4412 | 50.47 | -1 | -1 | -10 | -7.2206 | -7.2206 | 0 | 12 | 1 | 1 | -7.2206 | 10 | 0 | 0
1347.65 | 50.5 | 50.22 | -1 | -0.54412 | -5.4412 | 50.5 | -1 | -1 | -10 | -7.7206 | -7.7206 | 0 | 12 | 1 | 1 | -7.7206 | 10 | 0 | 0
1347.7 | 50.5 | 50.24 | -1 | -0.64412 | -6.4412 | 50.5 | -1 | -1 | -10 | -8.2206 | -8.2206 | 0 | 12 | 1 | 1 | -8.2206 | 10 | 0 | 0
1347.75 | 50.47 | 50.27 | -1 | -0.74412 | -7.4412 | 50.5 | -1 | -1 | -10 | -8.7206 | -8.7206 | 0 | 12 | 1 | 1 | -8.7206 | 10 | 0 | 0
1347.8 | 50.45 | 50.29 | -1 | -0.84412 | -8.4412 | 50.5 | -1 | -1 | -10 | -9.2206 | -9.2206 | 0 | 12 | 1 | 1 | -9.2206 | 10 | 0 | 0
1347.85 | 50.42 | 50.32 | -1 | -0.94412 | -9.4412 | 50.5 | -1 | -1 | -10 | -9.7206 | -9.7206 | 0 | 12 | 1 | 1 | -9.7206 | 10 | 0 | 0
1347.9 | 50.39 | 50.35 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1347.95 | 50.37 | 50.37 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1348 | 50.34 | 50.34 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1348.05 | 50.32 | 50.32 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1348.1 | 50.29 | 50.29 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1348.15 | 50.26 | 50.26 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1348.2 | 50.24 | 50.24 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1348.25 | 50.21 | 50.21 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1348.3 | 50.18 | 50.18 | -0.81 | -0.81 | -8.1 | 50.47 | -1 | -1 | -10 | -9.05 | -9.05 | 0 | 12 | 1 | 1 | -9.05 | 10 | 0 | 0
1348.35 | 50.16 | 50.16 | -0.62 | -0.62 | -6.2 | 50.45 | -1 | -1 | -10 | -8.1 | -8.1 | 0 | 12 | 1 | 1 | -8.1 | 10 | 0 | 0
1348.4 | 50.13 | 50.13 | -0.335 | -0.335 | -3.35 | 50.42 | -1 | -1 | -10 | -6.675 | -6.675 | 0 | 12 | 1 | 1 | -6.675 | 10 | 0 | 0
1348.45 | 50.11 | 50.11 | -0.145 | -0.145 | -1.45 | 50.39 | -1 | -1 | -10 | -5.725 | -5.725 | 0 | 12 | 1 | 1 | -5.725 | 10 | 0 | 0
1348.5 | 50.08 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 50.37 | -1 | -1 | -10 | -5.1912 | -5.1912 | 0 | 12 | 1 | 1 | -5.1912 | 10 | 0 | 0
1348.55 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.34 | -1 | -1 | -10 | -5.1029 | -5.1029 | 0 | 12 | 1 | 1 | -5.1029 | 10 | 0 | 0
1348.6 | 50.03 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 50.32 | -1 | -1 | -10 | -5.0441 | -5.0441 | 0 | 12 | 1 | 1 | -5.0441 | 10 | 0 | 0
1348.65 | 50 | 50 | 0 | 0 | 0 | 50.29 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1348.7 | 50 | 50 | 0 | 0 | 0 | 50.26 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1348.75 | 50 | 50 | 0 | 0 | 0 | 50.24 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1348.8 | 50 | 50 | 0 | 0 | 0 | 50.21 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1348.85 | 50 | 50 | 0 | 0 | 0 | 50.18 | -0.81 | -0.9 | -9 | -4.5 | -4.5 | 0 | 12 | 1 | 1 | -4.5 | 10 | 0 | 0
1348.9 | 50 | 50 | 0 | 0 | 0 | 50.16 | -0.62 | -0.8 | -8 | -4 | -4 | 0 | 12 | 1 | 1 | -4 | 10 | 0 | 0
1348.95 | 50 | 50 | 0 | 0 | 0 | 50.13 | -0.335 | -0.7 | -7 | -3.5 | -3.5 | 0 | 12 | 1 | 1 | -3.5 | 10 | 0 | 0
1349 | 50.01 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.6 | -6 | -3 | -3 | 0 | 12 | 1 | 1 | -3 | 10 | 0 | 0
1349.05 | 50.01 | 50 | 0 | 0 | 0 | 50.08 | -0.038235 | -0.5 | -5 | -2.5 | -2.5 | 0 | 12 | 1 | 1 | -2.5 | 10 | 0 | 0
1349.1 | 49.99 | 49.99 | 0 | 0 | 0 | 50.05 | -0.020588 | -0.4 | -4 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
1349.15 | 49.99 | 49.99 | 0 | 0 | 0 | 50.03 | -0.0088235 | -0.3 | -3 | -1.5 | -1.5 | 0 | 12 | 1 | 1 | -1.5 | 10 | 0 | 0
1349.2 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | -0.2 | -2 | -0.83824 | -0.83824 | 0 | 12 | 1 | 1 | -0.83824 | 10 | 0 | 0
1349.25 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | -0.1 | -1 | -0.33824 | -0.33824 | 0 | 12 | 1 | 1 | -0.33824 | 10 | 0 | 0
1349.3 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
1349.35 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
1349.4 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
1349.45 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
1349.5 | 49.89 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
1349.55 | 49.89 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
1349.6 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50.01 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1349.65 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1349.7 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1349.75 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 2.7868 | 2.7868 | 0 | 12 | 1 | 1 | 2.7868 | 10 | 0 | 0
1349.8 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 2.7868 | 2.7868 | 0 | 12 | 1 | 1 | 2.7868 | 10 | 0 | 0
1349.85 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 2.8456 | 2.8456 | 0 | 12 | 1 | 1 | 2.8456 | 10 | 0 | 0
1349.9 | 49.94 | 49.85 | 0.525 | 0.525 | 5.25 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 2.7574 | 2.7574 | 0 | 12 | 1 | 1 | 2.7574 | 10 | 0 | 0
1349.95 | 49.94 | 49.85 | 0.525 | 0.525 | 5.25 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 2.7574 | 2.7574 | 0 | 12 | 1 | 1 | 2.7574 | 10 | 0 | 0
1350 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1350.05 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1350.1 | 49.93 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1350.15 | 49.93 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1350.2 | 49.96 | 49.85 | 0.525 | 0.525 | 5.25 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 2.6985 | 2.6985 | 0 | 12 | 1 | 1 | 2.6985 | 10 | 0 | 0
1350.25 | 49.96 | 49.85 | 0.525 | 0.525 | 5.25 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 2.6985 | 2.6985 | 0 | 12 | 1 | 1 | 2.6985 | 10 | 0 | 0
1350.3 | 49.99 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1350.35 | 49.99 | 49.91 | 0.044118 | 0.425 | 4.25 | 49.99 | 0 | 0 | 0 | 2.125 | 2.125 | 0 | 12 | 1 | 1 | 2.125 | 10 | 0 | 0
1350.4 | 49.99 | 49.91 | 0.044118 | 0.325 | 3.25 | 49.99 | 0 | 0 | 0 | 1.625 | 1.625 | 0 | 12 | 1 | 1 | 1.625 | 10 | 0 | 0
1350.45 | 49.99 | 49.93 | 0.032353 | 0.225 | 2.25 | 49.99 | 0 | 0 | 0 | 1.125 | 1.125 | 0 | 12 | 1 | 1 | 1.125 | 10 | 0 | 0
1350.5 | 49.96 | 49.93 | 0.032353 | 0.125 | 1.25 | 49.99 | 0 | 0 | 0 | 0.625 | 0.625 | 0 | 12 | 1 | 1 | 0.625 | 10 | 0 | 0
1350.55 | 49.96 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 49.99 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1350.6 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1350.65 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1350.7 | 50.05 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.058824 | 0.058824 | 0 | 12 | 1 | 1 | 0.058824 | 10 | 0 | 0
1350.75 | 50.05 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
1350.8 | 49.97 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
1350.85 | 49.97 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
1350.9 | 49.92 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1350.95 | 49.92 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1351 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1351.05 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1351.1 | 49.94 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1351.15 | 49.94 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1351.2 | 50.01 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1351.25 | 50.01 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1351.3 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1351.35 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
1351.4 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
1351.45 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
1351.5 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
1351.55 | 49.95 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
1351.6 | 49.97 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
1351.65 | 49.97 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
1351.7 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
1351.75 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
1351.8 | 49.87 | 49.87 | 0.335 | 0.335 | 3.35 | 50.01 | 0 | 0 | 0 | 1.675 | 1.675 | 0 | 12 | 1 | 1 | 1.675 | 10 | 0 | 0
1351.85 | 49.87 | 49.87 | 0.335 | 0.335 | 3.35 | 49.99 | 0 | 0 | 0 | 1.675 | 1.675 | 0 | 12 | 1 | 1 | 1.675 | 10 | 0 | 0
1351.9 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1351.95 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 2.6691 | 2.6691 | 0 | 12 | 1 | 1 | 2.6691 | 10 | 0 | 0
1352 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1352.05 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1352.1 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1352.15 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1352.2 | 49.84 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1352.25 | 49.84 | 49.79 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
1352.3 | 49.89 | 49.79 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
1352.35 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.12647 | 1.2647 | 5.6324 | 5.6324 | 0 | 12 | 1 | 1 | 5.6324 | 10 | 0 | 0
1352.4 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.145 | 1.45 | 5.725 | 5.725 | 0 | 12 | 1 | 1 | 5.725 | 10 | 0 | 0
1352.45 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.145 | 1.45 | 5.725 | 5.725 | 0 | 12 | 1 | 1 | 5.725 | 10 | 0 | 0
1352.5 | 49.96 | 49.79 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
1352.55 | 49.96 | 49.79 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
1352.6 | 50.02 | 49.79 | 1 | 1 | 10 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 4.9853 | 4.9853 | 0 | 12 | 1 | 1 | 4.9853 | 10 | 0 | 0
1352.65 | 50.02 | 49.79 | 1 | 1 | 10 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 4.9853 | 4.9853 | 0 | 12 | 1 | 1 | 4.9853 | 10 | 0 | 0
1352.7 | 50.03 | 49.79 | 1 | 1 | 10 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.9559 | 4.9559 | 0 | 12 | 1 | 1 | 4.9559 | 10 | 0 | 0
1352.75 | 50.03 | 49.84 | 0.62 | 0.9 | 9 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.4559 | 4.4559 | 0 | 12 | 1 | 1 | 4.4559 | 10 | 0 | 0
1352.8 | 50.02 | 49.84 | 0.62 | 0.8 | 8 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 3.9559 | 3.9559 | 0 | 12 | 1 | 1 | 3.9559 | 10 | 0 | 0
1352.85 | 50.02 | 49.89 | 0.145 | 0.7 | 7 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 3.4559 | 3.4559 | 0 | 12 | 1 | 1 | 3.4559 | 10 | 0 | 0
1352.9 | 50.08 | 49.89 | 0.145 | 0.6 | 6 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 2.8088 | 2.8088 | 0 | 12 | 1 | 1 | 2.8088 | 10 | 0 | 0
1352.95 | 50.08 | 49.89 | 0.145 | 0.5 | 5 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 2.3088 | 2.3088 | 0 | 12 | 1 | 1 | 2.3088 | 10 | 0 | 0
1353 | 50.01 | 49.89 | 0.145 | 0.4 | 4 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 1.8088 | 1.8088 | 0 | 12 | 1 | 1 | 1.8088 | 10 | 0 | 0
1353.05 | 50.01 | 49.96 | 0.014706 | 0.3 | 3 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 1.3088 | 1.3088 | 0 | 12 | 1 | 1 | 1.3088 | 10 | 0 | 0
1353.1 | 49.94 | 49.94 | 0.026471 | 0.2 | 2 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.80882 | 0.80882 | 0 | 12 | 1 | 1 | 0.80882 | 10 | 0 | 0
1353.15 | 49.94 | 49.94 | 0.026471 | 0.1 | 1 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.30882 | 0.30882 | 0 | 12 | 1 | 1 | 0.30882 | 10 | 0 | 0
1353.2 | 50 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
1353.25 | 50 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
1353.3 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
1353.35 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
1353.4 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1353.45 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1353.5 | 49.92 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1353.55 | 49.92 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
1353.6 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50.01 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1353.65 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1353.7 | 49.92 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1353.75 | 49.92 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1353.8 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1353.85 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1353.9 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1353.95 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1354 | 49.87 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1354.05 | 49.87 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1354.1 | 49.8 | 49.8 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1354.15 | 49.8 | 49.8 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1354.2 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1354.25 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1354.3 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1354.35 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1354.4 | 49.72 | 49.72 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1354.45 | 49.72 | 49.72 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1354.5 | 49.67 | 49.67 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1354.55 | 49.67 | 49.67 | 1 | 1 | 10 | 49.87 | 0.335 | 0.14412 | 1.4412 | 5.7206 | 5.7206 | 0 | 12 | 1 | 1 | 5.7206 | 10 | 0 | 0
1354.6 | 49.65 | 49.65 | 1 | 1 | 10 | 49.87 | 0.335 | 0.24412 | 2.4412 | 6.2206 | 6.2206 | 0 | 12 | 1 | 1 | 6.2206 | 10 | 0 | 0
1354.65 | 49.65 | 49.65 | 1 | 1 | 10 | 49.8 | 1 | 0.34412 | 3.4412 | 6.7206 | 6.7206 | 0 | 12 | 1 | 1 | 6.7206 | 10 | 0 | 0
1354.7 | 49.59 | 49.59 | 1 | 1 | 10 | 49.8 | 1 | 0.44412 | 4.4412 | 7.2206 | 7.2206 | 0 | 12 | 1 | 1 | 7.2206 | 10 | 0 | 0
1354.75 | 49.59 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.54412 | 5.4412 | 7.7206 | 7.7206 | 0 | 12 | 1 | 1 | 7.7206 | 10 | 0 | 0
1354.8 | 49.66 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.64412 | 6.4412 | 8.2206 | 8.2206 | 0 | 12 | 1 | 1 | 8.2206 | 10 | 0 | 0
1354.85 | 49.66 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.74412 | 7.4412 | 8.7206 | 8.7206 | 0 | 12 | 1 | 1 | 8.7206 | 10 | 0 | 0
1354.9 | 49.63 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.84412 | 8.4412 | 9.2206 | 9.2206 | 0 | 12 | 1 | 1 | 9.2206 | 10 | 0 | 0
1354.95 | 49.63 | 49.59 | 1 | 1 | 10 | 49.72 | 1 | 0.94412 | 9.4412 | 9.7206 | 9.7206 | 0 | 12 | 1 | 1 | 9.7206 | 10 | 0 | 0
1355 | 49.61 | 49.59 | 1 | 1 | 10 | 49.72 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1355.05 | 49.61 | 49.59 | 1 | 1 | 10 | 49.67 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1355.1 | 49.54 | 49.54 | 1 | 1 | 10 | 49.67 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1355.15 | 49.54 | 49.54 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1355.2 | 49.46 | 49.46 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1355.25 | 49.46 | 49.46 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1355.3 | 49.45 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1355.35 | 49.45 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1355.4 | 49.51 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1355.45 | 49.51 | 49.45 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1355.5 | 49.5 | 49.45 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1355.55 | 49.5 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1355.6 | 49.54 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1355.65 | 49.54 | 49.45 | 1 | 1 | 10 | 49.54 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1355.7 | 49.59 | 49.45 | 1 | 1 | 10 | 49.59 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1355.75 | 49.59 | 49.45 | 1 | 1 | 10 | 49.59 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1355.8 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1355.85 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1355.9 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1355.95 | 49.61 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1356 | 49.53 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1356.05 | 49.53 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1356.1 | 49.54 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1356.15 | 49.54 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1356.2 | 49.61 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1356.25 | 49.61 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1356.3 | 49.66 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1356.35 | 49.66 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1356.4 | 49.64 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1356.45 | 49.64 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1356.5 | 49.69 | 49.53 | 1 | 1 | 10 | 49.69 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1356.55 | 49.69 | 49.53 | 1 | 1 | 10 | 49.69 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1356.6 | 49.74 | 49.53 | 1 | 1 | 10 | 49.74 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1356.65 | 49.74 | 49.54 | 1 | 1 | 10 | 49.74 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1356.7 | 49.78 | 49.54 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1356.75 | 49.78 | 49.61 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1356.8 | 49.82 | 49.61 | 1 | 1 | 10 | 49.82 | 0.81 | 0.81 | 8.1 | 9.05 | 9.05 | 0 | 12 | 1 | 1 | 9.05 | 10 | 0 | 0
1356.85 | 49.82 | 49.64 | 1 | 1 | 10 | 49.82 | 0.81 | 0.81 | 8.1 | 9.05 | 9.05 | 0 | 12 | 1 | 1 | 9.05 | 10 | 0 | 0
1356.9 | 49.86 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
1356.95 | 49.86 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
1357 | 49.84 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
1357.05 | 49.84 | 49.69 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
1357.1 | 49.91 | 49.69 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1357.15 | 49.91 | 49.74 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1357.2 | 49.97 | 49.74 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1357.25 | 49.97 | 49.78 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1357.3 | 50.03 | 49.78 | 1 | 1 | 10 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.9559 | 4.9559 | 0 | 12 | 1 | 1 | 4.9559 | 10 | 0 | 0
1357.35 | 50.03 | 49.82 | 0.81 | 0.9 | 9 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.4559 | 4.4559 | 0 | 12 | 1 | 1 | 4.4559 | 10 | 0 | 0
1357.4 | 50.05 | 49.82 | 0.81 | 0.81 | 8.1 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 3.9471 | 3.9471 | 0 | 12 | 1 | 1 | 3.9471 | 10 | 0 | 0
1357.45 | 50.05 | 49.84 | 0.62 | 0.71 | 7.1 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 3.4471 | 3.4471 | 0 | 12 | 1 | 1 | 3.4471 | 10 | 0 | 0
1357.5 | 50.01 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
1357.55 | 50.01 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
1357.6 | 49.95 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
1357.65 | 49.95 | 49.91 | 0.044118 | 0.52 | 5.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.4971 | 2.4971 | 0 | 12 | 1 | 1 | 2.4971 | 10 | 0 | 0
1357.7 | 49.99 | 49.91 | 0.044118 | 0.42 | 4.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 1.9971 | 1.9971 | 0 | 12 | 1 | 1 | 1.9971 | 10 | 0 | 0
1357.75 | 49.99 | 49.95 | 0.020588 | 0.32 | 3.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 1.4971 | 1.4971 | 0 | 12 | 1 | 1 | 1.4971 | 10 | 0 | 0
1357.8 | 49.92 | 49.92 | 0.038235 | 0.22 | 2.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.99706 | 0.99706 | 0 | 12 | 1 | 1 | 0.99706 | 10 | 0 | 0
1357.85 | 49.92 | 49.92 | 0.038235 | 0.12 | 1.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.49706 | 0.49706 | 0 | 12 | 1 | 1 | 0.49706 | 10 | 0 | 0
1357.9 | 49.97 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1357.95 | 49.97 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1358 | 50.02 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1358.05 | 50.02 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.17647 | 0.17647 | 0 | 12 | 1 | 1 | 0.17647 | 10 | 0 | 0
1358.1 | 50.07 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1358.15 | 50.07 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1358.2 | 50.06 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1358.25 | 50.06 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1358.3 | 50.13 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
1358.35 | 50.13 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
1358.4 | 50.09 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
1358.45 | 50.09 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6309 | -1.6309 | 0 | 12 | 1 | 1 | -1.6309 | 10 | 0 | 0
1358.5 | 50.07 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6309 | -1.6309 | 0 | 12 | 1 | 1 | -1.6309 | 10 | 0 | 0
1358.55 | 50.07 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6897 | -1.6897 | 0 | 12 | 1 | 1 | -1.6897 | 10 | 0 | 0
1358.6 | 50.07 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6897 | -1.6897 | 0 | 12 | 1 | 1 | -1.6897 | 10 | 0 | 0
1358.65 | 50.07 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.13 | -0.335 | -0.335 | -3.35 | -1.8074 | -1.8074 | 0 | 12 | 1 | 1 | -1.8074 | 10 | 0 | 0
1358.7 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.13 | -0.335 | -0.335 | -3.35 | -1.7779 | -1.7779 | 0 | 12 | 1 | 1 | -1.7779 | 10 | 0 | 0
1358.75 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.13 | -0.335 | -0.335 | -3.35 | -1.7779 | -1.7779 | 0 | 12 | 1 | 1 | -1.7779 | 10 | 0 | 0
1358.8 | 50.01 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
1358.85 | 50.01 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
1358.9 | 50.07 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
1358.95 | 50.07 | 50.01 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.235 | -2.35 | -1.175 | -1.175 | 0 | 12 | 1 | 1 | -1.175 | 10 | 0 | 0
1359 | 50.05 | 50.01 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.135 | -1.35 | -0.675 | -0.675 | 0 | 12 | 1 | 1 | -0.675 | 10 | 0 | 0
1359.05 | 50.05 | 50.01 | 0 | 0 | 0 | 50.07 | -0.032353 | -0.035 | -0.35 | -0.175 | -0.175 | 0 | 12 | 1 | 1 | -0.175 | 10 | 0 | 0
1359.1 | 50.1 | 50.01 | 0 | 0 | 0 | 50.1 | -0.05 | -0.05 | -0.5 | -0.25 | -0.25 | 0 | 12 | 1 | 1 | -0.25 | 10 | 0 | 0
1359.15 | 50.1 | 50.01 | 0 | 0 | 0 | 50.1 | -0.05 | -0.05 | -0.5 | -0.25 | -0.25 | 0 | 12 | 1 | 1 | -0.25 | 10 | 0 | 0
1359.2 | 50.11 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1359.25 | 50.11 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1359.3 | 50.06 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1359.35 | 50.06 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1359.4 | 50.04 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1359.45 | 50.04 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1359.5 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1359.55 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1359.6 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1359.65 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1359.7 | 50.11 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1359.75 | 50.11 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1359.8 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1359.85 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1359.9 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1359.95 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1360 | 50.02 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.11 | -0.145 | -0.145 | -1.45 | -0.73971 | -0.73971 | 0 | 12 | 1 | 1 | -0.73971 | 10 | 0 | 0
1360.05 | 50.02 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.11 | -0.145 | -0.145 | -1.45 | -0.73971 | -0.73971 | 0 | 12 | 1 | 1 | -0.73971 | 10 | 0 | 0
1360.1 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1360.15 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1360.2 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1360.25 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1360.3 | 50.01 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1360.35 | 50.01 | 50 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.045 | -0.45 | -0.225 | -0.225 | 0 | 12 | 1 | 1 | -0.225 | 10 | 0 | 0
1360.4 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
1360.45 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
1360.5 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
1360.55 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1360.6 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.14706 | 0.14706 | 0 | 12 | 1 | 1 | 0.14706 | 10 | 0 | 0
1360.65 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1360.7 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1360.75 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1360.8 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1360.85 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1360.9 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1360.95 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1361 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1361.05 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1361.1 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1361.15 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1361.2 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1361.25 | 50 | 50 | 0 | 0 | 0 | 50.01 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1361.3 | 49.5 | 49.5 | 1 | 1 | 10 | 50.01 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1361.35 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1361.4 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1361.45 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1361.5 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1361.55 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1361.6 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1361.65 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1361.7 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1361.75 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1361.8 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1361.85 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.1 | 1 | 5.5 | 5.5 | 0 | 12 | 1 | 1 | 5.5 | 10 | 0 | 0
1361.9 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.2 | 2 | 6 | 6 | 0 | 12 | 1 | 1 | 6 | 10 | 0 | 0
1361.95 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.3 | 3 | 6.5 | 6.5 | 0 | 12 | 1 | 1 | 6.5 | 10 | 0 | 0
1362 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.4 | 4 | 7 | 7 | 0 | 12 | 1 | 1 | 7 | 10 | 0 | 0
1362.05 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.5 | 5 | 7.5 | 7.5 | 0 | 12 | 1 | 1 | 7.5 | 10 | 0 | 0
1362.1 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.6 | 6 | 8 | 8 | 0 | 12 | 1 | 1 | 8 | 10 | 0 | 0
1362.15 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.7 | 7 | 8.5 | 8.5 | 0 | 12 | 1 | 1 | 8.5 | 10 | 0 | 0
1362.2 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.8 | 8 | 9 | 9 | 0 | 12 | 1 | 1 | 9 | 10 | 0 | 0
1362.25 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.9 | 9 | 9.5 | 9.5 | 0 | 12 | 1 | 1 | 9.5 | 10 | 0 | 0
1362.3 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1362.35 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1362.4 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1362.45 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1362.5 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1362.55 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1362.6 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1362.65 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1362.7 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1362.75 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1362.8 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1362.85 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1362.9 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1362.95 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1363 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1363.05 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1363.1 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1363.15 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1363.2 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1363.25 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1363.3 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1363.35 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1363.4 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1363.45 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1363.5 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1363.55 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1363.6 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1363.65 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1363.7 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1363.75 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1363.8 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1363.85 | 50.5 | 50.5 | -1 | 0.9 | 9 | 50.5 | -1 | -1 | -10 | -0.5 | -0.5 | 0 | 12 | 1 | 1 | -0.5 | 10 | 0 | 0
1363.9 | 50.5 | 50.5 | -1 | 0.8 | 8 | 50.5 | -1 | -1 | -10 | -1 | -1 | 0 | 12 | 1 | 1 | -1 | 10 | 0 | 0
1363.95 | 50.5 | 50.5 | -1 | 0.7 | 7 | 50.5 | -1 | -1 | -10 | -1.5 | -1.5 | 0 | 12 | 1 | 1 | -1.5 | 10 | 0 | 0
1364 | 50.5 | 50.5 | -1 | 0.6 | 6 | 50.5 | -1 | -1 | -10 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
1364.05 | 50.5 | 50.5 | -1 | 0.5 | 5 | 50.5 | -1 | -1 | -10 | -2.5 | -2.5 | 0 | 12 | 1 | 1 | -2.5 | 10 | 0 | 0
1364.1 | 50.5 | 50.5 | -1 | 0.4 | 4 | 50.5 | -1 | -1 | -10 | -3 | -3 | 0 | 12 | 1 | 1 | -3 | 10 | 0 | 0
1364.15 | 50.5 | 50.5 | -1 | 0.3 | 3 | 50.5 | -1 | -1 | -10 | -3.5 | -3.5 | 0 | 12 | 1 | 1 | -3.5 | 10 | 0 | 0
1364.2 | 50.5 | 50.5 | -1 | 0.2 | 2 | 50.5 | -1 | -1 | -10 | -4 | -4 | 0 | 12 | 1 | 1 | -4 | 10 | 0 | 0
1364.25 | 50.5 | 50.5 | -1 | 0.1 | 1 | 50.5 | -1 | -1 | -10 | -4.5 | -4.5 | 0 | 12 | 1 | 1 | -4.5 | 10 | 0 | 0
1364.3 | 50.5 | 50.5 | -1 | 0 | 0 | 50.5 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1364.35 | 50.5 | 50.5 | -1 | -0.1 | -1 | 50.5 | -1 | -1 | -10 | -5.5 | -5.5 | 0 | 12 | 1 | 1 | -5.5 | 10 | 0 | 0
1364.4 | 50.5 | 50.5 | -1 | -0.2 | -2 | 50.5 | -1 | -1 | -10 | -6 | -6 | 0 | 12 | 1 | 1 | -6 | 10 | 0 | 0
1364.45 | 50.5 | 50.5 | -1 | -0.3 | -3 | 50.5 | -1 | -1 | -10 | -6.5 | -6.5 | 0 | 12 | 1 | 1 | -6.5 | 10 | 0 | 0
1364.5 | 50.5 | 50.5 | -1 | -0.4 | -4 | 50.5 | -1 | -1 | -10 | -7 | -7 | 0 | 12 | 1 | 1 | -7 | 10 | 0 | 0
1364.55 | 50.5 | 50.5 | -1 | -0.5 | -5 | 50.5 | -1 | -1 | -10 | -7.5 | -7.5 | 0 | 12 | 1 | 1 | -7.5 | 10 | 0 | 0
1364.6 | 50.5 | 50.5 | -1 | -0.6 | -6 | 50.5 | -1 | -1 | -10 | -8 | -8 | 0 | 12 | 1 | 1 | -8 | 10 | 0 | 0
1364.65 | 50.5 | 50.5 | -1 | -0.7 | -7 | 50.5 | -1 | -1 | -10 | -8.5 | -8.5 | 0 | 12 | 1 | 1 | -8.5 | 10 | 0 | 0
1364.7 | 50.5 | 50.5 | -1 | -0.8 | -8 | 50.5 | -1 | -1 | -10 | -9 | -9 | 0 | 12 | 1 | 1 | -9 | 10 | 0 | 0
1364.75 | 50.5 | 50.5 | -1 | -0.9 | -9 | 50.5 | -1 | -1 | -10 | -9.5 | -9.5 | 0 | 12 | 1 | 1 | -9.5 | 10 | 0 | 0
1364.8 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1364.85 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1364.9 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1364.95 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1365 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1365.05 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1365.1 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1365.15 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1365.2 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1365.25 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1365.3 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1365.35 | 50.47 | 50.47 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1365.4 | 50.45 | 50.45 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1365.45 | 50.42 | 50.42 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1365.5 | 50.4 | 50.4 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1365.55 | 50.37 | 50.37 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1365.6 | 50.35 | 50.35 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1365.65 | 50.32 | 50.32 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1365.7 | 50.29 | 50.29 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1365.75 | 50.27 | 50.27 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1365.8 | 50.24 | 50.24 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1365.85 | 50.22 | 50.22 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1365.9 | 50.19 | 50.19 | -0.905 | -0.905 | -9.05 | 50.47 | -1 | -1 | -10 | -9.525 | -9.525 | 0 | 12 | 1 | 1 | -9.525 | 10 | 0 | 0
1365.95 | 50.17 | 50.17 | -0.715 | -0.715 | -7.15 | 50.45 | -1 | -1 | -10 | -8.575 | -8.575 | 0 | 12 | 1 | 1 | -8.575 | 10 | 0 | 0
1366 | 50.14 | 50.14 | -0.43 | -0.43 | -4.3 | 50.42 | -1 | -1 | -10 | -7.15 | -7.15 | 0 | 12 | 1 | 1 | -7.15 | 10 | 0 | 0
1366.05 | 50.12 | 50.12 | -0.24 | -0.24 | -2.4 | 50.4 | -1 | -1 | -10 | -6.2 | -6.2 | 0 | 12 | 1 | 1 | -6.2 | 10 | 0 | 0
1366.1 | 50.09 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 50.37 | -1 | -1 | -10 | -5.2206 | -5.2206 | 0 | 12 | 1 | 1 | -5.2206 | 10 | 0 | 0
1366.15 | 50.06 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.35 | -1 | -1 | -10 | -5.1324 | -5.1324 | 0 | 12 | 1 | 1 | -5.1324 | 10 | 0 | 0
1366.2 | 50.04 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.32 | -1 | -1 | -10 | -5.0735 | -5.0735 | 0 | 12 | 1 | 1 | -5.0735 | 10 | 0 | 0
1366.25 | 50.01 | 50.01 | 0 | 0 | 0 | 50.29 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1366.3 | 49.99 | 49.99 | 0 | 0 | 0 | 50.27 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1366.35 | 49.96 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.24 | -1 | -1 | -10 | -4.9265 | -4.9265 | 0 | 12 | 1 | 1 | -4.9265 | 10 | 0 | 0
1366.4 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.22 | -1 | -1 | -10 | -4.8676 | -4.8676 | 0 | 12 | 1 | 1 | -4.8676 | 10 | 0 | 0
1366.45 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.19 | -0.905 | -0.905 | -9.05 | -4.3044 | -4.3044 | 0 | 12 | 1 | 1 | -4.3044 | 10 | 0 | 0
1366.5 | 49.88 | 49.88 | 0.24 | 0.24 | 2.4 | 50.17 | -0.715 | -0.805 | -8.05 | -2.825 | -2.825 | 0 | 12 | 1 | 1 | -2.825 | 10 | 0 | 0
1366.55 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.14 | -0.43 | -0.705 | -7.05 | -1.375 | -1.375 | 0 | 12 | 1 | 1 | -1.375 | 10 | 0 | 0
1366.6 | 49.83 | 49.83 | 0.715 | 0.715 | 7.15 | 50.12 | -0.24 | -0.605 | -6.05 | 0.55 | 0.55 | 0 | 12 | 1 | 1 | 0.55 | 10 | 0 | 0
1366.65 | 49.81 | 49.81 | 0.905 | 0.905 | 9.05 | 50.09 | -0.044118 | -0.505 | -5.05 | 2 | 2 | 0 | 12 | 1 | 1 | 2 | 10 | 0 | 0
1366.7 | 49.78 | 49.78 | 1 | 1 | 10 | 50.06 | -0.026471 | -0.405 | -4.05 | 2.975 | 2.975 | 0 | 12 | 1 | 1 | 2.975 | 10 | 0 | 0
1366.75 | 49.76 | 49.76 | 1 | 1 | 10 | 50.04 | -0.014706 | -0.305 | -3.05 | 3.475 | 3.475 | 0 | 12 | 1 | 1 | 3.475 | 10 | 0 | 0
1366.8 | 49.73 | 49.73 | 1 | 1 | 10 | 50.01 | 0 | -0.205 | -2.05 | 3.975 | 3.975 | 0 | 12 | 1 | 1 | 3.975 | 10 | 0 | 0
1366.85 | 49.71 | 49.71 | 1 | 1 | 10 | 49.99 | 0 | -0.105 | -1.05 | 4.475 | 4.475 | 0 | 12 | 1 | 1 | 4.475 | 10 | 0 | 0
1366.9 | 49.68 | 49.68 | 1 | 1 | 10 | 49.96 | 0.014706 | -0.005 | -0.05 | 4.975 | 4.975 | 0 | 12 | 1 | 1 | 4.975 | 10 | 0 | 0
1366.95 | 49.65 | 49.65 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
1367 | 49.63 | 49.63 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1367.05 | 49.6 | 49.6 | 1 | 1 | 10 | 49.88 | 0.24 | 0.14412 | 1.4412 | 5.7206 | 5.7206 | 0 | 12 | 1 | 1 | 5.7206 | 10 | 0 | 0
1367.1 | 49.58 | 49.58 | 1 | 1 | 10 | 49.86 | 0.43 | 0.24412 | 2.4412 | 6.2206 | 6.2206 | 0 | 12 | 1 | 1 | 6.2206 | 10 | 0 | 0
1367.15 | 49.55 | 49.55 | 1 | 1 | 10 | 49.83 | 0.715 | 0.34412 | 3.4412 | 6.7206 | 6.7206 | 0 | 12 | 1 | 1 | 6.7206 | 10 | 0 | 0
1367.2 | 49.53 | 49.53 | 1 | 1 | 10 | 49.81 | 0.905 | 0.44412 | 4.4412 | 7.2206 | 7.2206 | 0 | 12 | 1 | 1 | 7.2206 | 10 | 0 | 0
1367.25 | 49.5 | 49.5 | 1 | 1 | 10 | 49.78 | 1 | 0.54412 | 5.4412 | 7.7206 | 7.7206 | 0 | 12 | 1 | 1 | 7.7206 | 10 | 0 | 0
1367.3 | 49.5 | 49.5 | 1 | 1 | 10 | 49.76 | 1 | 0.64412 | 6.4412 | 8.2206 | 8.2206 | 0 | 12 | 1 | 1 | 8.2206 | 10 | 0 | 0
1367.35 | 49.53 | 49.5 | 1 | 1 | 10 | 49.73 | 1 | 0.74412 | 7.4412 | 8.7206 | 8.7206 | 0 | 12 | 1 | 1 | 8.7206 | 10 | 0 | 0
1367.4 | 49.55 | 49.5 | 1 | 1 | 10 | 49.71 | 1 | 0.84412 | 8.4412 | 9.2206 | 9.2206 | 0 | 12 | 1 | 1 | 9.2206 | 10 | 0 | 0
1367.45 | 49.58 | 49.5 | 1 | 1 | 10 | 49.68 | 1 | 0.94412 | 9.4412 | 9.7206 | 9.7206 | 0 | 12 | 1 | 1 | 9.7206 | 10 | 0 | 0
1367.5 | 49.6 | 49.5 | 1 | 1 | 10 | 49.65 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1367.55 | 49.63 | 49.5 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1367.6 | 49.65 | 49.5 | 1 | 1 | 10 | 49.65 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1367.65 | 49.68 | 49.5 | 1 | 1 | 10 | 49.68 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1367.7 | 49.71 | 49.5 | 1 | 1 | 10 | 49.71 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1367.75 | 49.73 | 49.5 | 1 | 1 | 10 | 49.73 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1367.8 | 49.76 | 49.5 | 1 | 1 | 10 | 49.76 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1367.85 | 49.78 | 49.5 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1367.9 | 49.81 | 49.53 | 1 | 1 | 10 | 49.81 | 0.905 | 0.905 | 9.05 | 9.525 | 9.525 | 0 | 12 | 1 | 1 | 9.525 | 10 | 0 | 0
1367.95 | 49.83 | 49.55 | 1 | 1 | 10 | 49.83 | 0.715 | 0.715 | 7.15 | 8.575 | 8.575 | 0 | 12 | 1 | 1 | 8.575 | 10 | 0 | 0
1368 | 49.86 | 49.58 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
1368.05 | 49.88 | 49.6 | 1 | 1 | 10 | 49.88 | 0.24 | 0.24 | 2.4 | 6.2 | 6.2 | 0 | 12 | 1 | 1 | 6.2 | 10 | 0 | 0
1368.1 | 49.91 | 49.63 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1368.15 | 49.94 | 49.65 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
1368.2 | 49.96 | 49.68 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
1368.25 | 49.99 | 49.71 | 1 | 1 | 10 | 49.99 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1368.3 | 50.01 | 49.73 | 1 | 1 | 10 | 50.01 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1368.35 | 50.04 | 49.76 | 1 | 1 | 10 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 4.9265 | 4.9265 | 0 | 12 | 1 | 1 | 4.9265 | 10 | 0 | 0
1368.4 | 50.06 | 49.78 | 1 | 1 | 10 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 4.8676 | 4.8676 | 0 | 12 | 1 | 1 | 4.8676 | 10 | 0 | 0
1368.45 | 50.09 | 49.81 | 0.905 | 0.905 | 9.05 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 4.3044 | 4.3044 | 0 | 12 | 1 | 1 | 4.3044 | 10 | 0 | 0
1368.5 | 50.12 | 49.83 | 0.715 | 0.805 | 8.05 | 50.12 | -0.24 | -0.24 | -2.4 | 2.825 | 2.825 | 0 | 12 | 1 | 1 | 2.825 | 10 | 0 | 0
1368.55 | 50.14 | 49.86 | 0.43 | 0.705 | 7.05 | 50.14 | -0.43 | -0.43 | -4.3 | 1.375 | 1.375 | 0 | 12 | 1 | 1 | 1.375 | 10 | 0 | 0
1368.6 | 50.17 | 49.88 | 0.24 | 0.605 | 6.05 | 50.17 | -0.715 | -0.715 | -7.15 | -0.55 | -0.55 | 0 | 12 | 1 | 1 | -0.55 | 10 | 0 | 0
1368.65 | 50.19 | 49.91 | 0.044118 | 0.505 | 5.05 | 50.19 | -0.905 | -0.905 | -9.05 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
1368.7 | 50.22 | 49.94 | 0.026471 | 0.405 | 4.05 | 50.22 | -1 | -1 | -10 | -2.975 | -2.975 | 0 | 12 | 1 | 1 | -2.975 | 10 | 0 | 0
1368.75 | 50.24 | 49.96 | 0.014706 | 0.305 | 3.05 | 50.24 | -1 | -1 | -10 | -3.475 | -3.475 | 0 | 12 | 1 | 1 | -3.475 | 10 | 0 | 0
1368.8 | 50.27 | 49.99 | 0 | 0.205 | 2.05 | 50.27 | -1 | -1 | -10 | -3.975 | -3.975 | 0 | 12 | 1 | 1 | -3.975 | 10 | 0 | 0
1368.85 | 50.29 | 50.01 | 0 | 0.105 | 1.05 | 50.29 | -1 | -1 | -10 | -4.475 | -4.475 | 0 | 12 | 1 | 1 | -4.475 | 10 | 0 | 0
1368.9 | 50.32 | 50.04 | -0.014706 | 0.005 | 0.05 | 50.32 | -1 | -1 | -10 | -4.975 | -4.975 | 0 | 12 | 1 | 1 | -4.975 | 10 | 0 | 0
1368.95 | 50.35 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.35 | -1 | -1 | -10 | -5.1324 | -5.1324 | 0 | 12 | 1 | 1 | -5.1324 | 10 | 0 | 0
1369 | 50.37 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 50.37 | -1 | -1 | -10 | -5.2206 | -5.2206 | 0 | 12 | 1 | 1 | -5.2206 | 10 | 0 | 0
1369.05 | 50.4 | 50.12 | -0.24 | -0.14412 | -1.4412 | 50.4 | -1 | -1 | -10 | -5.7206 | -5.7206 | 0 | 12 | 1 | 1 | -5.7206 | 10 | 0 | 0
1369.1 | 50.42 | 50.14 | -0.43 | -0.24412 | -2.4412 | 50.42 | -1 | -1 | -10 | -6.2206 | -6.2206 | 0 | 12 | 1 | 1 | -6.2206 | 10 | 0 | 0
1369.15 | 50.45 | 50.17 | -0.715 | -0.34412 | -3.4412 | 50.45 | -1 | -1 | -10 | -6.7206 | -6.7206 | 0 | 12 | 1 | 1 | -6.7206 | 10 | 0 | 0
1369.2 | 50.47 | 50.19 | -0.905 | -0.44412 | -4.4412 | 50.47 | -1 | -1 | -10 | -7.2206 | -7.2206 | 0 | 12 | 1 | 1 | -7.2206 | 10 | 0 | 0
1369.25 | 50.5 | 50.22 | -1 | -0.54412 | -5.4412 | 50.5 | -1 | -1 | -10 | -7.7206 | -7.7206 | 0 | 12 | 1 | 1 | -7.7206 | 10 | 0 | 0
1369.3 | 50.5 | 50.24 | -1 | -0.64412 | -6.4412 | 50.5 | -1 | -1 | -10 | -8.2206 | -8.2206 | 0 | 12 | 1 | 1 | -8.2206 | 10 | 0 | 0
1369.35 | 50.47 | 50.27 | -1 | -0.74412 | -7.4412 | 50.5 | -1 | -1 | -10 | -8.7206 | -8.7206 | 0 | 12 | 1 | 1 | -8.7206 | 10 | 0 | 0
1369.4 | 50.45 | 50.29 | -1 | -0.84412 | -8.4412 | 50.5 | -1 | -1 | -10 | -9.2206 | -9.2206 | 0 | 12 | 1 | 1 | -9.2206 | 10 | 0 | 0
1369.45 | 50.42 | 50.32 | -1 | -0.94412 | -9.4412 | 50.5 | -1 | -1 | -10 | -9.7206 | -9.7206 | 0 | 12 | 1 | 1 | -9.7206 | 10 | 0 | 0
1369.5 | 50.39 | 50.35 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1369.55 | 50.37 | 50.37 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1369.6 | 50.34 | 50.34 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1369.65 | 50.32 | 50.32 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1369.7 | 50.29 | 50.29 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1369.75 | 50.26 | 50.26 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1369.8 | 50.24 | 50.24 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1369.85 | 50.21 | 50.21 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1369.9 | 50.18 | 50.18 | -0.81 | -0.81 | -8.1 | 50.47 | -1 | -1 | -10 | -9.05 | -9.05 | 0 | 12 | 1 | 1 | -9.05 | 10 | 0 | 0
1369.95 | 50.16 | 50.16 | -0.62 | -0.62 | -6.2 | 50.45 | -1 | -1 | -10 | -8.1 | -8.1 | 0 | 12 | 1 | 1 | -8.1 | 10 | 0 | 0
1370 | 50.13 | 50.13 | -0.335 | -0.335 | -3.35 | 50.42 | -1 | -1 | -10 | -6.675 | -6.675 | 0 | 12 | 1 | 1 | -6.675 | 10 | 0 | 0
1370.05 | 50.11 | 50.11 | -0.145 | -0.145 | -1.45 | 50.39 | -1 | -1 | -10 | -5.725 | -5.725 | 0 | 12 | 1 | 1 | -5.725 | 10 | 0 | 0
1370.1 | 50.08 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 50.37 | -1 | -1 | -10 | -5.1912 | -5.1912 | 0 | 12 | 1 | 1 | -5.1912 | 10 | 0 | 0
1370.15 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.34 | -1 | -1 | -10 | -5.1029 | -5.1029 | 0 | 12 | 1 | 1 | -5.1029 | 10 | 0 | 0
1370.2 | 50.03 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 50.32 | -1 | -1 | -10 | -5.0441 | -5.0441 | 0 | 12 | 1 | 1 | -5.0441 | 10 | 0 | 0
1370.25 | 50 | 50 | 0 | 0 | 0 | 50.29 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1370.3 | 50 | 50 | 0 | 0 | 0 | 50.26 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1370.35 | 50 | 50 | 0 | 0 | 0 | 50.24 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1370.4 | 50 | 50 | 0 | 0 | 0 | 50.21 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1370.45 | 50 | 50 | 0 | 0 | 0 | 50.18 | -0.81 | -0.9 | -9 | -4.5 | -4.5 | 0 | 12 | 1 | 1 | -4.5 | 10 | 0 | 0
1370.5 | 50 | 50 | 0 | 0 | 0 | 50.16 | -0.62 | -0.8 | -8 | -4 | -4 | 0 | 12 | 1 | 1 | -4 | 10 | 0 | 0
1370.55 | 50 | 50 | 0 | 0 | 0 | 50.13 | -0.335 | -0.7 | -7 | -3.5 | -3.5 | 0 | 12 | 1 | 1 | -3.5 | 10 | 0 | 0
1370.6 | 50.01 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.6 | -6 | -3 | -3 | 0 | 12 | 1 | 1 | -3 | 10 | 0 | 0
1370.65 | 50.01 | 50 | 0 | 0 | 0 | 50.08 | -0.038235 | -0.5 | -5 | -2.5 | -2.5 | 0 | 12 | 1 | 1 | -2.5 | 10 | 0 | 0
1370.7 | 49.99 | 49.99 | 0 | 0 | 0 | 50.05 | -0.020588 | -0.4 | -4 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
1370.75 | 49.99 | 49.99 | 0 | 0 | 0 | 50.03 | -0.0088235 | -0.3 | -3 | -1.5 | -1.5 | 0 | 12 | 1 | 1 | -1.5 | 10 | 0 | 0
1370.8 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | -0.2 | -2 | -0.83824 | -0.83824 | 0 | 12 | 1 | 1 | -0.83824 | 10 | 0 | 0
1370.85 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | -0.1 | -1 | -0.33824 | -0.33824 | 0 | 12 | 1 | 1 | -0.33824 | 10 | 0 | 0
1370.9 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
1370.95 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
1371 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
1371.05 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
1371.1 | 49.89 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
1371.15 | 49.89 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
1371.2 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50.01 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1371.25 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1371.3 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1371.35 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 2.7868 | 2.7868 | 0 | 12 | 1 | 1 | 2.7868 | 10 | 0 | 0
1371.4 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 2.7868 | 2.7868 | 0 | 12 | 1 | 1 | 2.7868 | 10 | 0 | 0
1371.45 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 2.8456 | 2.8456 | 0 | 12 | 1 | 1 | 2.8456 | 10 | 0 | 0
1371.5 | 49.94 | 49.85 | 0.525 | 0.525 | 5.25 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 2.7574 | 2.7574 | 0 | 12 | 1 | 1 | 2.7574 | 10 | 0 | 0
1371.55 | 49.94 | 49.85 | 0.525 | 0.525 | 5.25 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 2.7574 | 2.7574 | 0 | 12 | 1 | 1 | 2.7574 | 10 | 0 | 0
1371.6 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1371.65 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1371.7 | 49.93 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1371.75 | 49.93 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1371.8 | 49.96 | 49.85 | 0.525 | 0.525 | 5.25 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 2.6985 | 2.6985 | 0 | 12 | 1 | 1 | 2.6985 | 10 | 0 | 0
1371.85 | 49.96 | 49.85 | 0.525 | 0.525 | 5.25 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 2.6985 | 2.6985 | 0 | 12 | 1 | 1 | 2.6985 | 10 | 0 | 0
1371.9 | 49.99 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1371.95 | 49.99 | 49.91 | 0.044118 | 0.425 | 4.25 | 49.99 | 0 | 0 | 0 | 2.125 | 2.125 | 0 | 12 | 1 | 1 | 2.125 | 10 | 0 | 0
1372 | 49.99 | 49.91 | 0.044118 | 0.325 | 3.25 | 49.99 | 0 | 0 | 0 | 1.625 | 1.625 | 0 | 12 | 1 | 1 | 1.625 | 10 | 0 | 0
1372.05 | 49.99 | 49.93 | 0.032353 | 0.225 | 2.25 | 49.99 | 0 | 0 | 0 | 1.125 | 1.125 | 0 | 12 | 1 | 1 | 1.125 | 10 | 0 | 0
1372.1 | 49.96 | 49.93 | 0.032353 | 0.125 | 1.25 | 49.99 | 0 | 0 | 0 | 0.625 | 0.625 | 0 | 12 | 1 | 1 | 0.625 | 10 | 0 | 0
1372.15 | 49.96 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 49.99 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1372.2 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1372.25 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1372.3 | 50.05 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.058824 | 0.058824 | 0 | 12 | 1 | 1 | 0.058824 | 10 | 0 | 0
1372.35 | 50.05 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
1372.4 | 49.97 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
1372.45 | 49.97 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
1372.5 | 49.92 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1372.55 | 49.92 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1372.6 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1372.65 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1372.7 | 49.94 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1372.75 | 49.94 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1372.8 | 50.01 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1372.85 | 50.01 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1372.9 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1372.95 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
1373 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
1373.05 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
1373.1 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
1373.15 | 49.95 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
1373.2 | 49.97 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
1373.25 | 49.97 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
1373.3 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
1373.35 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
1373.4 | 49.87 | 49.87 | 0.335 | 0.335 | 3.35 | 50.01 | 0 | 0 | 0 | 1.675 | 1.675 | 0 | 12 | 1 | 1 | 1.675 | 10 | 0 | 0
1373.45 | 49.87 | 49.87 | 0.335 | 0.335 | 3.35 | 49.99 | 0 | 0 | 0 | 1.675 | 1.675 | 0 | 12 | 1 | 1 | 1.675 | 10 | 0 | 0
1373.5 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1373.55 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 2.6691 | 2.6691 | 0 | 12 | 1 | 1 | 2.6691 | 10 | 0 | 0
1373.6 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1373.65 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1373.7 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1373.75 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1373.8 | 49.84 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1373.85 | 49.84 | 49.79 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
1373.9 | 49.89 | 49.79 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
1373.95 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.12647 | 1.2647 | 5.6324 | 5.6324 | 0 | 12 | 1 | 1 | 5.6324 | 10 | 0 | 0
1374 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.145 | 1.45 | 5.725 | 5.725 | 0 | 12 | 1 | 1 | 5.725 | 10 | 0 | 0
1374.05 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.145 | 1.45 | 5.725 | 5.725 | 0 | 12 | 1 | 1 | 5.725 | 10 | 0 | 0
1374.1 | 49.96 | 49.79 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
1374.15 | 49.96 | 49.79 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
1374.2 | 50.02 | 49.79 | 1 | 1 | 10 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 4.9853 | 4.9853 | 0 | 12 | 1 | 1 | 4.9853 | 10 | 0 | 0
1374.25 | 50.02 | 49.79 | 1 | 1 | 10 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 4.9853 | 4.9853 | 0 | 12 | 1 | 1 | 4.9853 | 10 | 0 | 0
1374.3 | 50.03 | 49.79 | 1 | 1 | 10 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.9559 | 4.9559 | 0 | 12 | 1 | 1 | 4.9559 | 10 | 0 | 0
1374.35 | 50.03 | 49.84 | 0.62 | 0.9 | 9 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.4559 | 4.4559 | 0 | 12 | 1 | 1 | 4.4559 | 10 | 0 | 0
1374.4 | 50.02 | 49.84 | 0.62 | 0.8 | 8 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 3.9559 | 3.9559 | 0 | 12 | 1 | 1 | 3.9559 | 10 | 0 | 0
1374.45 | 50.02 | 49.89 | 0.145 | 0.7 | 7 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 3.4559 | 3.4559 | 0 | 12 | 1 | 1 | 3.4559 | 10 | 0 | 0
1374.5 | 50.08 | 49.89 | 0.145 | 0.6 | 6 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 2.8088 | 2.8088 | 0 | 12 | 1 | 1 | 2.8088 | 10 | 0 | 0
1374.55 | 50.08 | 49.89 | 0.145 | 0.5 | 5 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 2.3088 | 2.3088 | 0 | 12 | 1 | 1 | 2.3088 | 10 | 0 | 0
1374.6 | 50.01 | 49.89 | 0.145 | 0.4 | 4 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 1.8088 | 1.8088 | 0 | 12 | 1 | 1 | 1.8088 | 10 | 0 | 0
1374.65 | 50.01 | 49.96 | 0.014706 | 0.3 | 3 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 1.3088 | 1.3088 | 0 | 12 | 1 | 1 | 1.3088 | 10 | 0 | 0
1374.7 | 49.94 | 49.94 | 0.026471 | 0.2 | 2 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.80882 | 0.80882 | 0 | 12 | 1 | 1 | 0.80882 | 10 | 0 | 0
1374.75 | 49.94 | 49.94 | 0.026471 | 0.1 | 1 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.30882 | 0.30882 | 0 | 12 | 1 | 1 | 0.30882 | 10 | 0 | 0
1374.8 | 50 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
1374.85 | 50 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
1374.9 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
1374.95 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
1375 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1375.05 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1375.1 | 49.92 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1375.15 | 49.92 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
1375.2 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50.01 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1375.25 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1375.3 | 49.92 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1375.35 | 49.92 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1375.4 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1375.45 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1375.5 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1375.55 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1375.6 | 49.87 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1375.65 | 49.87 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1375.7 | 49.8 | 49.8 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1375.75 | 49.8 | 49.8 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1375.8 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1375.85 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1375.9 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1375.95 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1376 | 49.72 | 49.72 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1376.05 | 49.72 | 49.72 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1376.1 | 49.67 | 49.67 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1376.15 | 49.67 | 49.67 | 1 | 1 | 10 | 49.87 | 0.335 | 0.14412 | 1.4412 | 5.7206 | 5.7206 | 0 | 12 | 1 | 1 | 5.7206 | 10 | 0 | 0
1376.2 | 49.65 | 49.65 | 1 | 1 | 10 | 49.87 | 0.335 | 0.24412 | 2.4412 | 6.2206 | 6.2206 | 0 | 12 | 1 | 1 | 6.2206 | 10 | 0 | 0
1376.25 | 49.65 | 49.65 | 1 | 1 | 10 | 49.8 | 1 | 0.34412 | 3.4412 | 6.7206 | 6.7206 | 0 | 12 | 1 | 1 | 6.7206 | 10 | 0 | 0
1376.3 | 49.59 | 49.59 | 1 | 1 | 10 | 49.8 | 1 | 0.44412 | 4.4412 | 7.2206 | 7.2206 | 0 | 12 | 1 | 1 | 7.2206 | 10 | 0 | 0
1376.35 | 49.59 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.54412 | 5.4412 | 7.7206 | 7.7206 | 0 | 12 | 1 | 1 | 7.7206 | 10 | 0 | 0
1376.4 | 49.66 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.64412 | 6.4412 | 8.2206 | 8.2206 | 0 | 12 | 1 | 1 | 8.2206 | 10 | 0 | 0
1376.45 | 49.66 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.74412 | 7.4412 | 8.7206 | 8.7206 | 0 | 12 | 1 | 1 | 8.7206 | 10 | 0 | 0
1376.5 | 49.63 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.84412 | 8.4412 | 9.2206 | 9.2206 | 0 | 12 | 1 | 1 | 9.2206 | 10 | 0 | 0
1376.55 | 49.63 | 49.59 | 1 | 1 | 10 | 49.72 | 1 | 0.94412 | 9.4412 | 9.7206 | 9.7206 | 0 | 12 | 1 | 1 | 9.7206 | 10 | 0 | 0
1376.6 | 49.61 | 49.59 | 1 | 1 | 10 | 49.72 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1376.65 | 49.61 | 49.59 | 1 | 1 | 10 | 49.67 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1376.7 | 49.54 | 49.54 | 1 | 1 | 10 | 49.67 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1376.75 | 49.54 | 49.54 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1376.8 | 49.46 | 49.46 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1376.85 | 49.46 | 49.46 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1376.9 | 49.45 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1376.95 | 49.45 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1377 | 49.51 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1377.05 | 49.51 | 49.45 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1377.1 | 49.5 | 49.45 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1377.15 | 49.5 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1377.2 | 49.54 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1377.25 | 49.54 | 49.45 | 1 | 1 | 10 | 49.54 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1377.3 | 49.59 | 49.45 | 1 | 1 | 10 | 49.59 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1377.35 | 49.59 | 49.45 | 1 | 1 | 10 | 49.59 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1377.4 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1377.45 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1377.5 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1377.55 | 49.61 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1377.6 | 49.53 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1377.65 | 49.53 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1377.7 | 49.54 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1377.75 | 49.54 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1377.8 | 49.61 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1377.85 | 49.61 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1377.9 | 49.66 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1377.95 | 49.66 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1378 | 49.64 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1378.05 | 49.64 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1378.1 | 49.69 | 49.53 | 1 | 1 | 10 | 49.69 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1378.15 | 49.69 | 49.53 | 1 | 1 | 10 | 49.69 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1378.2 | 49.74 | 49.53 | 1 | 1 | 10 | 49.74 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1378.25 | 49.74 | 49.54 | 1 | 1 | 10 | 49.74 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1378.3 | 49.78 | 49.54 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1378.35 | 49.78 | 49.61 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1378.4 | 49.82 | 49.61 | 1 | 1 | 10 | 49.82 | 0.81 | 0.81 | 8.1 | 9.05 | 9.05 | 0 | 12 | 1 | 1 | 9.05 | 10 | 0 | 0
1378.45 | 49.82 | 49.64 | 1 | 1 | 10 | 49.82 | 0.81 | 0.81 | 8.1 | 9.05 | 9.05 | 0 | 12 | 1 | 1 | 9.05 | 10 | 0 | 0
1378.5 | 49.86 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
1378.55 | 49.86 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
1378.6 | 49.84 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
1378.65 | 49.84 | 49.69 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
1378.7 | 49.91 | 49.69 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1378.75 | 49.91 | 49.74 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1378.8 | 49.97 | 49.74 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1378.85 | 49.97 | 49.78 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1378.9 | 50.03 | 49.78 | 1 | 1 | 10 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.9559 | 4.9559 | 0 | 12 | 1 | 1 | 4.9559 | 10 | 0 | 0
1378.95 | 50.03 | 49.82 | 0.81 | 0.9 | 9 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.4559 | 4.4559 | 0 | 12 | 1 | 1 | 4.4559 | 10 | 0 | 0
1379 | 50.05 | 49.82 | 0.81 | 0.81 | 8.1 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 3.9471 | 3.9471 | 0 | 12 | 1 | 1 | 3.9471 | 10 | 0 | 0
1379.05 | 50.05 | 49.84 | 0.62 | 0.71 | 7.1 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 3.4471 | 3.4471 | 0 | 12 | 1 | 1 | 3.4471 | 10 | 0 | 0
1379.1 | 50.01 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
1379.15 | 50.01 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
1379.2 | 49.95 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
1379.25 | 49.95 | 49.91 | 0.044118 | 0.52 | 5.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.4971 | 2.4971 | 0 | 12 | 1 | 1 | 2.4971 | 10 | 0 | 0
1379.3 | 49.99 | 49.91 | 0.044118 | 0.42 | 4.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 1.9971 | 1.9971 | 0 | 12 | 1 | 1 | 1.9971 | 10 | 0 | 0
1379.35 | 49.99 | 49.95 | 0.020588 | 0.32 | 3.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 1.4971 | 1.4971 | 0 | 12 | 1 | 1 | 1.4971 | 10 | 0 | 0
1379.4 | 49.92 | 49.92 | 0.038235 | 0.22 | 2.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.99706 | 0.99706 | 0 | 12 | 1 | 1 | 0.99706 | 10 | 0 | 0
1379.45 | 49.92 | 49.92 | 0.038235 | 0.12 | 1.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.49706 | 0.49706 | 0 | 12 | 1 | 1 | 0.49706 | 10 | 0 | 0
1379.5 | 49.97 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1379.55 | 49.97 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1379.6 | 50.02 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1379.65 | 50.02 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.17647 | 0.17647 | 0 | 12 | 1 | 1 | 0.17647 | 10 | 0 | 0
1379.7 | 50.07 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1379.75 | 50.07 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1379.8 | 50.06 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1379.85 | 50.06 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1379.9 | 50.13 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
1379.95 | 50.13 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
1380 | 50.09 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
1380.05 | 50.09 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6309 | -1.6309 | 0 | 12 | 1 | 1 | -1.6309 | 10 | 0 | 0
1380.1 | 50.07 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6309 | -1.6309 | 0 | 12 | 1 | 1 | -1.6309 | 10 | 0 | 0
1380.15 | 50.07 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6897 | -1.6897 | 0 | 12 | 1 | 1 | -1.6897 | 10 | 0 | 0
1380.2 | 50.07 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6897 | -1.6897 | 0 | 12 | 1 | 1 | -1.6897 | 10 | 0 | 0
1380.25 | 50.07 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.13 | -0.335 | -0.335 | -3.35 | -1.8074 | -1.8074 | 0 | 12 | 1 | 1 | -1.8074 | 10 | 0 | 0
1380.3 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.13 | -0.335 | -0.335 | -3.35 | -1.7779 | -1.7779 | 0 | 12 | 1 | 1 | -1.7779 | 10 | 0 | 0
1380.35 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.13 | -0.335 | -0.335 | -3.35 | -1.7779 | -1.7779 | 0 | 12 | 1 | 1 | -1.7779 | 10 | 0 | 0
1380.4 | 50.01 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
1380.45 | 50.01 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
1380.5 | 50.07 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
1380.55 | 50.07 | 50.01 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.235 | -2.35 | -1.175 | -1.175 | 0 | 12 | 1 | 1 | -1.175 | 10 | 0 | 0
1380.6 | 50.05 | 50.01 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.135 | -1.35 | -0.675 | -0.675 | 0 | 12 | 1 | 1 | -0.675 | 10 | 0 | 0
1380.65 | 50.05 | 50.01 | 0 | 0 | 0 | 50.07 | -0.032353 | -0.035 | -0.35 | -0.175 | -0.175 | 0 | 12 | 1 | 1 | -0.175 | 10 | 0 | 0
1380.7 | 50.1 | 50.01 | 0 | 0 | 0 | 50.1 | -0.05 | -0.05 | -0.5 | -0.25 | -0.25 | 0 | 12 | 1 | 1 | -0.25 | 10 | 0 | 0
1380.75 | 50.1 | 50.01 | 0 | 0 | 0 | 50.1 | -0.05 | -0.05 | -0.5 | -0.25 | -0.25 | 0 | 12 | 1 | 1 | -0.25 | 10 | 0 | 0
1380.8 | 50.11 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1380.85 | 50.11 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1380.9 | 50.06 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1380.95 | 50.06 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1381 | 50.04 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1381.05 | 50.04 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1381.1 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1381.15 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1381.2 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1381.25 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1381.3 | 50.11 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1381.35 | 50.11 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1381.4 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1381.45 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1381.5 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1381.55 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1381.6 | 50.02 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.11 | -0.145 | -0.145 | -1.45 | -0.73971 | -0.73971 | 0 | 12 | 1 | 1 | -0.73971 | 10 | 0 | 0
1381.65 | 50.02 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.11 | -0.145 | -0.145 | -1.45 | -0.73971 | -0.73971 | 0 | 12 | 1 | 1 | -0.73971 | 10 | 0 | 0
1381.7 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1381.75 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1381.8 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1381.85 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1381.9 | 50.01 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1381.95 | 50.01 | 50 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.045 | -0.45 | -0.225 | -0.225 | 0 | 12 | 1 | 1 | -0.225 | 10 | 0 | 0
1382 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
1382.05 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
1382.1 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
1382.15 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1382.2 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.14706 | 0.14706 | 0 | 12 | 1 | 1 | 0.14706 | 10 | 0 | 0
1382.25 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1382.3 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1382.35 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1382.4 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1382.45 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1382.5 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1382.55 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1382.6 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1382.65 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1382.7 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1382.75 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1382.8 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1382.85 | 50 | 50 | 0 | 0 | 0 | 50.01 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1382.9 | 49.5 | 49.5 | 1 | 1 | 10 | 50.01 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1382.95 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1383 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1383.05 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1383.1 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1383.15 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1383.2 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1383.25 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1383.3 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1383.35 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1383.4 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1383.45 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.1 | 1 | 5.5 | 5.5 | 0 | 12 | 1 | 1 | 5.5 | 10 | 0 | 0
1383.5 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.2 | 2 | 6 | 6 | 0 | 12 | 1 | 1 | 6 | 10 | 0 | 0
1383.55 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.3 | 3 | 6.5 | 6.5 | 0 | 12 | 1 | 1 | 6.5 | 10 | 0 | 0
1383.6 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.4 | 4 | 7 | 7 | 0 | 12 | 1 | 1 | 7 | 10 | 0 | 0
1383.65 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.5 | 5 | 7.5 | 7.5 | 0 | 12 | 1 | 1 | 7.5 | 10 | 0 | 0
1383.7 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.6 | 6 | 8 | 8 | 0 | 12 | 1 | 1 | 8 | 10 | 0 | 0
1383.75 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.7 | 7 | 8.5 | 8.5 | 0 | 12 | 1 | 1 | 8.5 | 10 | 0 | 0
1383.8 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.8 | 8 | 9 | 9 | 0 | 12 | 1 | 1 | 9 | 10 | 0 | 0
1383.85 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.9 | 9 | 9.5 | 9.5 | 0 | 12 | 1 | 1 | 9.5 | 10 | 0 | 0
1383.9 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1383.95 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1384 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1384.05 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1384.1 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1384.15 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1384.2 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1384.25 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1384.3 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1384.35 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1384.4 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1384.45 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1384.5 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1384.55 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1384.6 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1384.65 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1384.7 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1384.75 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1384.8 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1384.85 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1384.9 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1384.95 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1385 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1385.05 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1385.1 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1385.15 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1385.2 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1385.25 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1385.3 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1385.35 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1385.4 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1385.45 | 50.5 | 50.5 | -1 | 0.9 | 9 | 50.5 | -1 | -1 | -10 | -0.5 | -0.5 | 0 | 12 | 1 | 1 | -0.5 | 10 | 0 | 0
1385.5 | 50.5 | 50.5 | -1 | 0.8 | 8 | 50.5 | -1 | -1 | -10 | -1 | -1 | 0 | 12 | 1 | 1 | -1 | 10 | 0 | 0
1385.55 | 50.5 | 50.5 | -1 | 0.7 | 7 | 50.5 | -1 | -1 | -10 | -1.5 | -1.5 | 0 | 12 | 1 | 1 | -1.5 | 10 | 0 | 0
1385.6 | 50.5 | 50.5 | -1 | 0.6 | 6 | 50.5 | -1 | -1 | -10 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
1385.65 | 50.5 | 50.5 | -1 | 0.5 | 5 | 50.5 | -1 | -1 | -10 | -2.5 | -2.5 | 0 | 12 | 1 | 1 | -2.5 | 10 | 0 | 0
1385.7 | 50.5 | 50.5 | -1 | 0.4 | 4 | 50.5 | -1 | -1 | -10 | -3 | -3 | 0 | 12 | 1 | 1 | -3 | 10 | 0 | 0
1385.75 | 50.5 | 50.5 | -1 | 0.3 | 3 | 50.5 | -1 | -1 | -10 | -3.5 | -3.5 | 0 | 12 | 1 | 1 | -3.5 | 10 | 0 | 0
1385.8 | 50.5 | 50.5 | -1 | 0.2 | 2 | 50.5 | -1 | -1 | -10 | -4 | -4 | 0 | 12 | 1 | 1 | -4 | 10 | 0 | 0
1385.85 | 50.5 | 50.5 | -1 | 0.1 | 1 | 50.5 | -1 | -1 | -10 | -4.5 | -4.5 | 0 | 12 | 1 | 1 | -4.5 | 10 | 0 | 0
1385.9 | 50.5 | 50.5 | -1 | 0 | 0 | 50.5 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1385.95 | 50.5 | 50.5 | -1 | -0.1 | -1 | 50.5 | -1 | -1 | -10 | -5.5 | -5.5 | 0 | 12 | 1 | 1 | -5.5 | 10 | 0 | 0
1386 | 50.5 | 50.5 | -1 | -0.2 | -2 | 50.5 | -1 | -1 | -10 | -6 | -6 | 0 | 12 | 1 | 1 | -6 | 10 | 0 | 0
1386.05 | 50.5 | 50.5 | -1 | -0.3 | -3 | 50.5 | -1 | -1 | -10 | -6.5 | -6.5 | 0 | 12 | 1 | 1 | -6.5 | 10 | 0 | 0
1386.1 | 50.5 | 50.5 | -1 | -0.4 | -4 | 50.5 | -1 | -1 | -10 | -7 | -7 | 0 | 12 | 1 | 1 | -7 | 10 | 0 | 0
1386.15 | 50.5 | 50.5 | -1 | -0.5 | -5 | 50.5 | -1 | -1 | -10 | -7.5 | -7.5 | 0 | 12 | 1 | 1 | -7.5 | 10 | 0 | 0
1386.2 | 50.5 | 50.5 | -1 | -0.6 | -6 | 50.5 | -1 | -1 | -10 | -8 | -8 | 0 | 12 | 1 | 1 | -8 | 10 | 0 | 0
1386.25 | 50.5 | 50.5 | -1 | -0.7 | -7 | 50.5 | -1 | -1 | -10 | -8.5 | -8.5 | 0 | 12 | 1 | 1 | -8.5 | 10 | 0 | 0
1386.3 | 50.5 | 50.5 | -1 | -0.8 | -8 | 50.5 | -1 | -1 | -10 | -9 | -9 | 0 | 12 | 1 | 1 | -9 | 10 | 0 | 0
1386.35 | 50.5 | 50.5 | -1 | -0.9 | -9 | 50.5 | -1 | -1 | -10 | -9.5 | -9.5 | 0 | 12 | 1 | 1 | -9.5 | 10 | 0 | 0
1386.4 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1386.45 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1386.5 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1386.55 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1386.6 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1386.65 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1386.7 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1386.75 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1386.8 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1386.85 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1386.9 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1386.95 | 50.47 | 50.47 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1387 | 50.45 | 50.45 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1387.05 | 50.42 | 50.42 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1387.1 | 50.4 | 50.4 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1387.15 | 50.37 | 50.37 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1387.2 | 50.35 | 50.35 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1387.25 | 50.32 | 50.32 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1387.3 | 50.29 | 50.29 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1387.35 | 50.27 | 50.27 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1387.4 | 50.24 | 50.24 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1387.45 | 50.22 | 50.22 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1387.5 | 50.19 | 50.19 | -0.905 | -0.905 | -9.05 | 50.47 | -1 | -1 | -10 | -9.525 | -9.525 | 0 | 12 | 1 | 1 | -9.525 | 10 | 0 | 0
1387.55 | 50.17 | 50.17 | -0.715 | -0.715 | -7.15 | 50.45 | -1 | -1 | -10 | -8.575 | -8.575 | 0 | 12 | 1 | 1 | -8.575 | 10 | 0 | 0
1387.6 | 50.14 | 50.14 | -0.43 | -0.43 | -4.3 | 50.42 | -1 | -1 | -10 | -7.15 | -7.15 | 0 | 12 | 1 | 1 | -7.15 | 10 | 0 | 0
1387.65 | 50.12 | 50.12 | -0.24 | -0.24 | -2.4 | 50.4 | -1 | -1 | -10 | -6.2 | -6.2 | 0 | 12 | 1 | 1 | -6.2 | 10 | 0 | 0
1387.7 | 50.09 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 50.37 | -1 | -1 | -10 | -5.2206 | -5.2206 | 0 | 12 | 1 | 1 | -5.2206 | 10 | 0 | 0
1387.75 | 50.06 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.35 | -1 | -1 | -10 | -5.1324 | -5.1324 | 0 | 12 | 1 | 1 | -5.1324 | 10 | 0 | 0
1387.8 | 50.04 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.32 | -1 | -1 | -10 | -5.0735 | -5.0735 | 0 | 12 | 1 | 1 | -5.0735 | 10 | 0 | 0
1387.85 | 50.01 | 50.01 | 0 | 0 | 0 | 50.29 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1387.9 | 49.99 | 49.99 | 0 | 0 | 0 | 50.27 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1387.95 | 49.96 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.24 | -1 | -1 | -10 | -4.9265 | -4.9265 | 0 | 12 | 1 | 1 | -4.9265 | 10 | 0 | 0
1388 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.22 | -1 | -1 | -10 | -4.8676 | -4.8676 | 0 | 12 | 1 | 1 | -4.8676 | 10 | 0 | 0
1388.05 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.19 | -0.905 | -0.905 | -9.05 | -4.3044 | -4.3044 | 0 | 12 | 1 | 1 | -4.3044 | 10 | 0 | 0
1388.1 | 49.88 | 49.88 | 0.24 | 0.24 | 2.4 | 50.17 | -0.715 | -0.805 | -8.05 | -2.825 | -2.825 | 0 | 12 | 1 | 1 | -2.825 | 10 | 0 | 0
1388.15 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.14 | -0.43 | -0.705 | -7.05 | -1.375 | -1.375 | 0 | 12 | 1 | 1 | -1.375 | 10 | 0 | 0
1388.2 | 49.83 | 49.83 | 0.715 | 0.715 | 7.15 | 50.12 | -0.24 | -0.605 | -6.05 | 0.55 | 0.55 | 0 | 12 | 1 | 1 | 0.55 | 10 | 0 | 0
1388.25 | 49.81 | 49.81 | 0.905 | 0.905 | 9.05 | 50.09 | -0.044118 | -0.505 | -5.05 | 2 | 2 | 0 | 12 | 1 | 1 | 2 | 10 | 0 | 0
1388.3 | 49.78 | 49.78 | 1 | 1 | 10 | 50.06 | -0.026471 | -0.405 | -4.05 | 2.975 | 2.975 | 0 | 12 | 1 | 1 | 2.975 | 10 | 0 | 0
1388.35 | 49.76 | 49.76 | 1 | 1 | 10 | 50.04 | -0.014706 | -0.305 | -3.05 | 3.475 | 3.475 | 0 | 12 | 1 | 1 | 3.475 | 10 | 0 | 0
1388.4 | 49.73 | 49.73 | 1 | 1 | 10 | 50.01 | 0 | -0.205 | -2.05 | 3.975 | 3.975 | 0 | 12 | 1 | 1 | 3.975 | 10 | 0 | 0
1388.45 | 49.71 | 49.71 | 1 | 1 | 10 | 49.99 | 0 | -0.105 | -1.05 | 4.475 | 4.475 | 0 | 12 | 1 | 1 | 4.475 | 10 | 0 | 0
1388.5 | 49.68 | 49.68 | 1 | 1 | 10 | 49.96 | 0.014706 | -0.005 | -0.05 | 4.975 | 4.975 | 0 | 12 | 1 | 1 | 4.975 | 10 | 0 | 0
1388.55 | 49.65 | 49.65 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
1388.6 | 49.63 | 49.63 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1388.65 | 49.6 | 49.6 | 1 | 1 | 10 | 49.88 | 0.24 | 0.14412 | 1.4412 | 5.7206 | 5.7206 | 0 | 12 | 1 | 1 | 5.7206 | 10 | 0 | 0
1388.7 | 49.58 | 49.58 | 1 | 1 | 10 | 49.86 | 0.43 | 0.24412 | 2.4412 | 6.2206 | 6.2206 | 0 | 12 | 1 | 1 | 6.2206 | 10 | 0 | 0
1388.75 | 49.55 | 49.55 | 1 | 1 | 10 | 49.83 | 0.715 | 0.34412 | 3.4412 | 6.7206 | 6.7206 | 0 | 12 | 1 | 1 | 6.7206 | 10 | 0 | 0
1388.8 | 49.53 | 49.53 | 1 | 1 | 10 | 49.81 | 0.905 | 0.44412 | 4.4412 | 7.2206 | 7.2206 | 0 | 12 | 1 | 1 | 7.2206 | 10 | 0 | 0
1388.85 | 49.5 | 49.5 | 1 | 1 | 10 | 49.78 | 1 | 0.54412 | 5.4412 | 7.7206 | 7.7206 | 0 | 12 | 1 | 1 | 7.7206 | 10 | 0 | 0
1388.9 | 49.5 | 49.5 | 1 | 1 | 10 | 49.76 | 1 | 0.64412 | 6.4412 | 8.2206 | 8.2206 | 0 | 12 | 1 | 1 | 8.2206 | 10 | 0 | 0
1388.95 | 49.53 | 49.5 | 1 | 1 | 10 | 49.73 | 1 | 0.74412 | 7.4412 | 8.7206 | 8.7206 | 0 | 12 | 1 | 1 | 8.7206 | 10 | 0 | 0
1389 | 49.55 | 49.5 | 1 | 1 | 10 | 49.71 | 1 | 0.84412 | 8.4412 | 9.2206 | 9.2206 | 0 | 12 | 1 | 1 | 9.2206 | 10 | 0 | 0
1389.05 | 49.58 | 49.5 | 1 | 1 | 10 | 49.68 | 1 | 0.94412 | 9.4412 | 9.7206 | 9.7206 | 0 | 12 | 1 | 1 | 9.7206 | 10 | 0 | 0
1389.1 | 49.6 | 49.5 | 1 | 1 | 10 | 49.65 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1389.15 | 49.63 | 49.5 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1389.2 | 49.65 | 49.5 | 1 | 1 | 10 | 49.65 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1389.25 | 49.68 | 49.5 | 1 | 1 | 10 | 49.68 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1389.3 | 49.71 | 49.5 | 1 | 1 | 10 | 49.71 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1389.35 | 49.73 | 49.5 | 1 | 1 | 10 | 49.73 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1389.4 | 49.76 | 49.5 | 1 | 1 | 10 | 49.76 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1389.45 | 49.78 | 49.5 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1389.5 | 49.81 | 49.53 | 1 | 1 | 10 | 49.81 | 0.905 | 0.905 | 9.05 | 9.525 | 9.525 | 0 | 12 | 1 | 1 | 9.525 | 10 | 0 | 0
1389.55 | 49.83 | 49.55 | 1 | 1 | 10 | 49.83 | 0.715 | 0.715 | 7.15 | 8.575 | 8.575 | 0 | 12 | 1 | 1 | 8.575 | 10 | 0 | 0
1389.6 | 49.86 | 49.58 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
1389.65 | 49.88 | 49.6 | 1 | 1 | 10 | 49.88 | 0.24 | 0.24 | 2.4 | 6.2 | 6.2 | 0 | 12 | 1 | 1 | 6.2 | 10 | 0 | 0
1389.7 | 49.91 | 49.63 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1389.75 | 49.94 | 49.65 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
1389.8 | 49.96 | 49.68 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
1389.85 | 49.99 | 49.71 | 1 | 1 | 10 | 49.99 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1389.9 | 50.01 | 49.73 | 1 | 1 | 10 | 50.01 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1389.95 | 50.04 | 49.76 | 1 | 1 | 10 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 4.9265 | 4.9265 | 0 | 12 | 1 | 1 | 4.9265 | 10 | 0 | 0
1390 | 50.06 | 49.78 | 1 | 1 | 10 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 4.8676 | 4.8676 | 0 | 12 | 1 | 1 | 4.8676 | 10 | 0 | 0
1390.05 | 50.09 | 49.81 | 0.905 | 0.905 | 9.05 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 4.3044 | 4.3044 | 0 | 12 | 1 | 1 | 4.3044 | 10 | 0 | 0
1390.1 | 50.12 | 49.83 | 0.715 | 0.805 | 8.05 | 50.12 | -0.24 | -0.24 | -2.4 | 2.825 | 2.825 | 0 | 12 | 1 | 1 | 2.825 | 10 | 0 | 0
1390.15 | 50.14 | 49.86 | 0.43 | 0.705 | 7.05 | 50.14 | -0.43 | -0.43 | -4.3 | 1.375 | 1.375 | 0 | 12 | 1 | 1 | 1.375 | 10 | 0 | 0
1390.2 | 50.17 | 49.88 | 0.24 | 0.605 | 6.05 | 50.17 | -0.715 | -0.715 | -7.15 | -0.55 | -0.55 | 0 | 12 | 1 | 1 | -0.55 | 10 | 0 | 0
1390.25 | 50.19 | 49.91 | 0.044118 | 0.505 | 5.05 | 50.19 | -0.905 | -0.905 | -9.05 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
1390.3 | 50.22 | 49.94 | 0.026471 | 0.405 | 4.05 | 50.22 | -1 | -1 | -10 | -2.975 | -2.975 | 0 | 12 | 1 | 1 | -2.975 | 10 | 0 | 0
1390.35 | 50.24 | 49.96 | 0.014706 | 0.305 | 3.05 | 50.24 | -1 | -1 | -10 | -3.475 | -3.475 | 0 | 12 | 1 | 1 | -3.475 | 10 | 0 | 0
1390.4 | 50.27 | 49.99 | 0 | 0.205 | 2.05 | 50.27 | -1 | -1 | -10 | -3.975 | -3.975 | 0 | 12 | 1 | 1 | -3.975 | 10 | 0 | 0
1390.45 | 50.29 | 50.01 | 0 | 0.105 | 1.05 | 50.29 | -1 | -1 | -10 | -4.475 | -4.475 | 0 | 12 | 1 | 1 | -4.475 | 10 | 0 | 0
1390.5 | 50.32 | 50.04 | -0.014706 | 0.005 | 0.05 | 50.32 | -1 | -1 | -10 | -4.975 | -4.975 | 0 | 12 | 1 | 1 | -4.975 | 10 | 0 | 0
1390.55 | 50.35 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.35 | -1 | -1 | -10 | -5.1324 | -5.1324 | 0 | 12 | 1 | 1 | -5.1324 | 10 | 0 | 0
1390.6 | 50.37 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 50.37 | -1 | -1 | -10 | -5.2206 | -5.2206 | 0 | 12 | 1 | 1 | -5.2206 | 10 | 0 | 0
1390.65 | 50.4 | 50.12 | -0.24 | -0.14412 | -1.4412 | 50.4 | -1 | -1 | -10 | -5.7206 | -5.7206 | 0 | 12 | 1 | 1 | -5.7206 | 10 | 0 | 0
1390.7 | 50.42 | 50.14 | -0.43 | -0.24412 | -2.4412 | 50.42 | -1 | -1 | -10 | -6.2206 | -6.2206 | 0 | 12 | 1 | 1 | -6.2206 | 10 | 0 | 0
1390.75 | 50.45 | 50.17 | -0.715 | -0.34412 | -3.4412 | 50.45 | -1 | -1 | -10 | -6.7206 | -6.7206 | 0 | 12 | 1 | 1 | -6.7206 | 10 | 0 | 0
1390.8 | 50.47 | 50.19 | -0.905 | -0.44412 | -4.4412 | 50.47 | -1 | -1 | -10 | -7.2206 | -7.2206 | 0 | 12 | 1 | 1 | -7.2206 | 10 | 0 | 0
1390.85 | 50.5 | 50.22 | -1 | -0.54412 | -5.4412 | 50.5 | -1 | -1 | -10 | -7.7206 | -7.7206 | 0 | 12 | 1 | 1 | -7.7206 | 10 | 0 | 0
1390.9 | 50.5 | 50.24 | -1 | -0.64412 | -6.4412 | 50.5 | -1 | -1 | -10 | -8.2206 | -8.2206 | 0 | 12 | 1 | 1 | -8.2206 | 10 | 0 | 0
1390.95 | 50.47 | 50.27 | -1 | -0.74412 | -7.4412 | 50.5 | -1 | -1 | -10 | -8.7206 | -8.7206 | 0 | 12 | 1 | 1 | -8.7206 | 10 | 0 | 0
1391 | 50.45 | 50.29 | -1 | -0.84412 | -8.4412 | 50.5 | -1 | -1 | -10 | -9.2206 | -9.2206 | 0 | 12 | 1 | 1 | -9.2206 | 10 | 0 | 0
1391.05 | 50.42 | 50.32 | -1 | -0.94412 | -9.4412 | 50.5 | -1 | -1 | -10 | -9.7206 | -9.7206 | 0 | 12 | 1 | 1 | -9.7206 | 10 | 0 | 0
1391.1 | 50.39 | 50.35 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1391.15 | 50.37 | 50.37 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1391.2 | 50.34 | 50.34 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1391.25 | 50.32 | 50.32 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1391.3 | 50.29 | 50.29 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1391.35 | 50.26 | 50.26 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1391.4 | 50.24 | 50.24 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1391.45 | 50.21 | 50.21 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1391.5 | 50.18 | 50.18 | -0.81 | -0.81 | -8.1 | 50.47 | -1 | -1 | -10 | -9.05 | -9.05 | 0 | 12 | 1 | 1 | -9.05 | 10 | 0 | 0
1391.55 | 50.16 | 50.16 | -0.62 | -0.62 | -6.2 | 50.45 | -1 | -1 | -10 | -8.1 | -8.1 | 0 | 12 | 1 | 1 | -8.1 | 10 | 0 | 0
1391.6 | 50.13 | 50.13 | -0.335 | -0.335 | -3.35 | 50.42 | -1 | -1 | -10 | -6.675 | -6.675 | 0 | 12 | 1 | 1 | -6.675 | 10 | 0 | 0
1391.65 | 50.11 | 50.11 | -0.145 | -0.145 | -1.45 | 50.39 | -1 | -1 | -10 | -5.725 | -5.725 | 0 | 12 | 1 | 1 | -5.725 | 10 | 0 | 0
1391.7 | 50.08 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 50.37 | -1 | -1 | -10 | -5.1912 | -5.1912 | 0 | 12 | 1 | 1 | -5.1912 | 10 | 0 | 0
1391.75 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.34 | -1 | -1 | -10 | -5.1029 | -5.1029 | 0 | 12 | 1 | 1 | -5.1029 | 10 | 0 | 0
1391.8 | 50.03 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 50.32 | -1 | -1 | -10 | -5.0441 | -5.0441 | 0 | 12 | 1 | 1 | -5.0441 | 10 | 0 | 0
1391.85 | 50 | 50 | 0 | 0 | 0 | 50.29 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1391.9 | 50 | 50 | 0 | 0 | 0 | 50.26 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1391.95 | 50 | 50 | 0 | 0 | 0 | 50.24 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1392 | 50 | 50 | 0 | 0 | 0 | 50.21 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1392.05 | 50 | 50 | 0 | 0 | 0 | 50.18 | -0.81 | -0.9 | -9 | -4.5 | -4.5 | 0 | 12 | 1 | 1 | -4.5 | 10 | 0 | 0
1392.1 | 50 | 50 | 0 | 0 | 0 | 50.16 | -0.62 | -0.8 | -8 | -4 | -4 | 0 | 12 | 1 | 1 | -4 | 10 | 0 | 0
1392.15 | 50 | 50 | 0 | 0 | 0 | 50.13 | -0.335 | -0.7 | -7 | -3.5 | -3.5 | 0 | 12 | 1 | 1 | -3.5 | 10 | 0 | 0
1392.2 | 50.01 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.6 | -6 | -3 | -3 | 0 | 12 | 1 | 1 | -3 | 10 | 0 | 0
1392.25 | 50.01 | 50 | 0 | 0 | 0 | 50.08 | -0.038235 | -0.5 | -5 | -2.5 | -2.5 | 0 | 12 | 1 | 1 | -2.5 | 10 | 0 | 0
1392.3 | 49.99 | 49.99 | 0 | 0 | 0 | 50.05 | -0.020588 | -0.4 | -4 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
1392.35 | 49.99 | 49.99 | 0 | 0 | 0 | 50.03 | -0.0088235 | -0.3 | -3 | -1.5 | -1.5 | 0 | 12 | 1 | 1 | -1.5 | 10 | 0 | 0
1392.4 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | -0.2 | -2 | -0.83824 | -0.83824 | 0 | 12 | 1 | 1 | -0.83824 | 10 | 0 | 0
1392.45 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | -0.1 | -1 | -0.33824 | -0.33824 | 0 | 12 | 1 | 1 | -0.33824 | 10 | 0 | 0
1392.5 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
1392.55 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
1392.6 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
1392.65 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
1392.7 | 49.89 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
1392.75 | 49.89 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
1392.8 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50.01 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1392.85 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1392.9 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1392.95 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 2.7868 | 2.7868 | 0 | 12 | 1 | 1 | 2.7868 | 10 | 0 | 0
1393 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 2.7868 | 2.7868 | 0 | 12 | 1 | 1 | 2.7868 | 10 | 0 | 0
1393.05 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 2.8456 | 2.8456 | 0 | 12 | 1 | 1 | 2.8456 | 10 | 0 | 0
1393.1 | 49.94 | 49.85 | 0.525 | 0.525 | 5.25 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 2.7574 | 2.7574 | 0 | 12 | 1 | 1 | 2.7574 | 10 | 0 | 0
1393.15 | 49.94 | 49.85 | 0.525 | 0.525 | 5.25 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 2.7574 | 2.7574 | 0 | 12 | 1 | 1 | 2.7574 | 10 | 0 | 0
1393.2 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1393.25 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1393.3 | 49.93 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1393.35 | 49.93 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1393.4 | 49.96 | 49.85 | 0.525 | 0.525 | 5.25 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 2.6985 | 2.6985 | 0 | 12 | 1 | 1 | 2.6985 | 10 | 0 | 0
1393.45 | 49.96 | 49.85 | 0.525 | 0.525 | 5.25 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 2.6985 | 2.6985 | 0 | 12 | 1 | 1 | 2.6985 | 10 | 0 | 0
1393.5 | 49.99 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1393.55 | 49.99 | 49.91 | 0.044118 | 0.425 | 4.25 | 49.99 | 0 | 0 | 0 | 2.125 | 2.125 | 0 | 12 | 1 | 1 | 2.125 | 10 | 0 | 0
1393.6 | 49.99 | 49.91 | 0.044118 | 0.325 | 3.25 | 49.99 | 0 | 0 | 0 | 1.625 | 1.625 | 0 | 12 | 1 | 1 | 1.625 | 10 | 0 | 0
1393.65 | 49.99 | 49.93 | 0.032353 | 0.225 | 2.25 | 49.99 | 0 | 0 | 0 | 1.125 | 1.125 | 0 | 12 | 1 | 1 | 1.125 | 10 | 0 | 0
1393.7 | 49.96 | 49.93 | 0.032353 | 0.125 | 1.25 | 49.99 | 0 | 0 | 0 | 0.625 | 0.625 | 0 | 12 | 1 | 1 | 0.625 | 10 | 0 | 0
1393.75 | 49.96 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 49.99 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1393.8 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1393.85 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1393.9 | 50.05 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.058824 | 0.058824 | 0 | 12 | 1 | 1 | 0.058824 | 10 | 0 | 0
1393.95 | 50.05 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
1394 | 49.97 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
1394.05 | 49.97 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
1394.1 | 49.92 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1394.15 | 49.92 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1394.2 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1394.25 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1394.3 | 49.94 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1394.35 | 49.94 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1394.4 | 50.01 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1394.45 | 50.01 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1394.5 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1394.55 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
1394.6 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
1394.65 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
1394.7 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
1394.75 | 49.95 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
1394.8 | 49.97 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
1394.85 | 49.97 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
1394.9 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
1394.95 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
1395 | 49.87 | 49.87 | 0.335 | 0.335 | 3.35 | 50.01 | 0 | 0 | 0 | 1.675 | 1.675 | 0 | 12 | 1 | 1 | 1.675 | 10 | 0 | 0
1395.05 | 49.87 | 49.87 | 0.335 | 0.335 | 3.35 | 49.99 | 0 | 0 | 0 | 1.675 | 1.675 | 0 | 12 | 1 | 1 | 1.675 | 10 | 0 | 0
1395.1 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1395.15 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 2.6691 | 2.6691 | 0 | 12 | 1 | 1 | 2.6691 | 10 | 0 | 0
1395.2 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1395.25 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1395.3 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1395.35 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1395.4 | 49.84 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1395.45 | 49.84 | 49.79 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
1395.5 | 49.89 | 49.79 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
1395.55 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.12647 | 1.2647 | 5.6324 | 5.6324 | 0 | 12 | 1 | 1 | 5.6324 | 10 | 0 | 0
1395.6 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.145 | 1.45 | 5.725 | 5.725 | 0 | 12 | 1 | 1 | 5.725 | 10 | 0 | 0
1395.65 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.145 | 1.45 | 5.725 | 5.725 | 0 | 12 | 1 | 1 | 5.725 | 10 | 0 | 0
1395.7 | 49.96 | 49.79 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
1395.75 | 49.96 | 49.79 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
1395.8 | 50.02 | 49.79 | 1 | 1 | 10 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 4.9853 | 4.9853 | 0 | 12 | 1 | 1 | 4.9853 | 10 | 0 | 0
1395.85 | 50.02 | 49.79 | 1 | 1 | 10 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 4.9853 | 4.9853 | 0 | 12 | 1 | 1 | 4.9853 | 10 | 0 | 0
1395.9 | 50.03 | 49.79 | 1 | 1 | 10 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.9559 | 4.9559 | 0 | 12 | 1 | 1 | 4.9559 | 10 | 0 | 0
1395.95 | 50.03 | 49.84 | 0.62 | 0.9 | 9 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.4559 | 4.4559 | 0 | 12 | 1 | 1 | 4.4559 | 10 | 0 | 0
1396 | 50.02 | 49.84 | 0.62 | 0.8 | 8 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 3.9559 | 3.9559 | 0 | 12 | 1 | 1 | 3.9559 | 10 | 0 | 0
1396.05 | 50.02 | 49.89 | 0.145 | 0.7 | 7 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 3.4559 | 3.4559 | 0 | 12 | 1 | 1 | 3.4559 | 10 | 0 | 0
1396.1 | 50.08 | 49.89 | 0.145 | 0.6 | 6 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 2.8088 | 2.8088 | 0 | 12 | 1 | 1 | 2.8088 | 10 | 0 | 0
1396.15 | 50.08 | 49.89 | 0.145 | 0.5 | 5 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 2.3088 | 2.3088 | 0 | 12 | 1 | 1 | 2.3088 | 10 | 0 | 0
1396.2 | 50.01 | 49.89 | 0.145 | 0.4 | 4 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 1.8088 | 1.8088 | 0 | 12 | 1 | 1 | 1.8088 | 10 | 0 | 0
1396.25 | 50.01 | 49.96 | 0.014706 | 0.3 | 3 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 1.3088 | 1.3088 | 0 | 12 | 1 | 1 | 1.3088 | 10 | 0 | 0
1396.3 | 49.94 | 49.94 | 0.026471 | 0.2 | 2 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.80882 | 0.80882 | 0 | 12 | 1 | 1 | 0.80882 | 10 | 0 | 0
1396.35 | 49.94 | 49.94 | 0.026471 | 0.1 | 1 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.30882 | 0.30882 | 0 | 12 | 1 | 1 | 0.30882 | 10 | 0 | 0
1396.4 | 50 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
1396.45 | 50 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
1396.5 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
1396.55 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
1396.6 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1396.65 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1396.7 | 49.92 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1396.75 | 49.92 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
1396.8 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50.01 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1396.85 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1396.9 | 49.92 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1396.95 | 49.92 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1397 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1397.05 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1397.1 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1397.15 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1397.2 | 49.87 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1397.25 | 49.87 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1397.3 | 49.8 | 49.8 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1397.35 | 49.8 | 49.8 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1397.4 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1397.45 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1397.5 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1397.55 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1397.6 | 49.72 | 49.72 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1397.65 | 49.72 | 49.72 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1397.7 | 49.67 | 49.67 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1397.75 | 49.67 | 49.67 | 1 | 1 | 10 | 49.87 | 0.335 | 0.14412 | 1.4412 | 5.7206 | 5.7206 | 0 | 12 | 1 | 1 | 5.7206 | 10 | 0 | 0
1397.8 | 49.65 | 49.65 | 1 | 1 | 10 | 49.87 | 0.335 | 0.24412 | 2.4412 | 6.2206 | 6.2206 | 0 | 12 | 1 | 1 | 6.2206 | 10 | 0 | 0
1397.85 | 49.65 | 49.65 | 1 | 1 | 10 | 49.8 | 1 | 0.34412 | 3.4412 | 6.7206 | 6.7206 | 0 | 12 | 1 | 1 | 6.7206 | 10 | 0 | 0
1397.9 | 49.59 | 49.59 | 1 | 1 | 10 | 49.8 | 1 | 0.44412 | 4.4412 | 7.2206 | 7.2206 | 0 | 12 | 1 | 1 | 7.2206 | 10 | 0 | 0
1397.95 | 49.59 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.54412 | 5.4412 | 7.7206 | 7.7206 | 0 | 12 | 1 | 1 | 7.7206 | 10 | 0 | 0
1398 | 49.66 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.64412 | 6.4412 | 8.2206 | 8.2206 | 0 | 12 | 1 | 1 | 8.2206 | 10 | 0 | 0
1398.05 | 49.66 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.74412 | 7.4412 | 8.7206 | 8.7206 | 0 | 12 | 1 | 1 | 8.7206 | 10 | 0 | 0
1398.1 | 49.63 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.84412 | 8.4412 | 9.2206 | 9.2206 | 0 | 12 | 1 | 1 | 9.2206 | 10 | 0 | 0
1398.15 | 49.63 | 49.59 | 1 | 1 | 10 | 49.72 | 1 | 0.94412 | 9.4412 | 9.7206 | 9.7206 | 0 | 12 | 1 | 1 | 9.7206 | 10 | 0 | 0
1398.2 | 49.61 | 49.59 | 1 | 1 | 10 | 49.72 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1398.25 | 49.61 | 49.59 | 1 | 1 | 10 | 49.67 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1398.3 | 49.54 | 49.54 | 1 | 1 | 10 | 49.67 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1398.35 | 49.54 | 49.54 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1398.4 | 49.46 | 49.46 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1398.45 | 49.46 | 49.46 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1398.5 | 49.45 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1398.55 | 49.45 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1398.6 | 49.51 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1398.65 | 49.51 | 49.45 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1398.7 | 49.5 | 49.45 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1398.75 | 49.5 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1398.8 | 49.54 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1398.85 | 49.54 | 49.45 | 1 | 1 | 10 | 49.54 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1398.9 | 49.59 | 49.45 | 1 | 1 | 10 | 49.59 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1398.95 | 49.59 | 49.45 | 1 | 1 | 10 | 49.59 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1399 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1399.05 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1399.1 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1399.15 | 49.61 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1399.2 | 49.53 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1399.25 | 49.53 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1399.3 | 49.54 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1399.35 | 49.54 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1399.4 | 49.61 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1399.45 | 49.61 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1399.5 | 49.66 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1399.55 | 49.66 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1399.6 | 49.64 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1399.65 | 49.64 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1399.7 | 49.69 | 49.53 | 1 | 1 | 10 | 49.69 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1399.75 | 49.69 | 49.53 | 1 | 1 | 10 | 49.69 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1399.8 | 49.74 | 49.53 | 1 | 1 | 10 | 49.74 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1399.85 | 49.74 | 49.54 | 1 | 1 | 10 | 49.74 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1399.9 | 49.78 | 49.54 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1399.95 | 49.78 | 49.61 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1400 | 49.82 | 49.61 | 1 | 1 | 10 | 49.82 | 0.81 | 0.81 | 8.1 | 9.05 | 9.05 | 0 | 12 | 1 | 1 | 9.05 | 10 | 0 | 0
1400.05 | 49.82 | 49.64 | 1 | 1 | 10 | 49.82 | 0.81 | 0.81 | 8.1 | 9.05 | 9.05 | 0 | 12 | 1 | 1 | 9.05 | 10 | 0 | 0
1400.1 | 49.86 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
1400.15 | 49.86 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
1400.2 | 49.84 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
1400.25 | 49.84 | 49.69 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
1400.3 | 49.91 | 49.69 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1400.35 | 49.91 | 49.74 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1400.4 | 49.97 | 49.74 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1400.45 | 49.97 | 49.78 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1400.5 | 50.03 | 49.78 | 1 | 1 | 10 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.9559 | 4.9559 | 0 | 12 | 1 | 1 | 4.9559 | 10 | 0 | 0
1400.55 | 50.03 | 49.82 | 0.81 | 0.9 | 9 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.4559 | 4.4559 | 0 | 12 | 1 | 1 | 4.4559 | 10 | 0 | 0
1400.6 | 50.05 | 49.82 | 0.81 | 0.81 | 8.1 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 3.9471 | 3.9471 | 0 | 12 | 1 | 1 | 3.9471 | 10 | 0 | 0
1400.65 | 50.05 | 49.84 | 0.62 | 0.71 | 7.1 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 3.4471 | 3.4471 | 0 | 12 | 1 | 1 | 3.4471 | 10 | 0 | 0
1400.7 | 50.01 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
1400.75 | 50.01 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
1400.8 | 49.95 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
1400.85 | 49.95 | 49.91 | 0.044118 | 0.52 | 5.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.4971 | 2.4971 | 0 | 12 | 1 | 1 | 2.4971 | 10 | 0 | 0
1400.9 | 49.99 | 49.91 | 0.044118 | 0.42 | 4.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 1.9971 | 1.9971 | 0 | 12 | 1 | 1 | 1.9971 | 10 | 0 | 0
1400.95 | 49.99 | 49.95 | 0.020588 | 0.32 | 3.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 1.4971 | 1.4971 | 0 | 12 | 1 | 1 | 1.4971 | 10 | 0 | 0
1401 | 49.92 | 49.92 | 0.038235 | 0.22 | 2.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.99706 | 0.99706 | 0 | 12 | 1 | 1 | 0.99706 | 10 | 0 | 0
1401.05 | 49.92 | 49.92 | 0.038235 | 0.12 | 1.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.49706 | 0.49706 | 0 | 12 | 1 | 1 | 0.49706 | 10 | 0 | 0
1401.1 | 49.97 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1401.15 | 49.97 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1401.2 | 50.02 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1401.25 | 50.02 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.17647 | 0.17647 | 0 | 12 | 1 | 1 | 0.17647 | 10 | 0 | 0
1401.3 | 50.07 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1401.35 | 50.07 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1401.4 | 50.06 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1401.45 | 50.06 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1401.5 | 50.13 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
1401.55 | 50.13 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
1401.6 | 50.09 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
1401.65 | 50.09 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6309 | -1.6309 | 0 | 12 | 1 | 1 | -1.6309 | 10 | 0 | 0
1401.7 | 50.07 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6309 | -1.6309 | 0 | 12 | 1 | 1 | -1.6309 | 10 | 0 | 0
1401.75 | 50.07 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6897 | -1.6897 | 0 | 12 | 1 | 1 | -1.6897 | 10 | 0 | 0
1401.8 | 50.07 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6897 | -1.6897 | 0 | 12 | 1 | 1 | -1.6897 | 10 | 0 | 0
1401.85 | 50.07 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.13 | -0.335 | -0.335 | -3.35 | -1.8074 | -1.8074 | 0 | 12 | 1 | 1 | -1.8074 | 10 | 0 | 0
1401.9 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.13 | -0.335 | -0.335 | -3.35 | -1.7779 | -1.7779 | 0 | 12 | 1 | 1 | -1.7779 | 10 | 0 | 0
1401.95 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.13 | -0.335 | -0.335 | -3.35 | -1.7779 | -1.7779 | 0 | 12 | 1 | 1 | -1.7779 | 10 | 0 | 0
1402 | 50.01 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
1402.05 | 50.01 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
1402.1 | 50.07 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
1402.15 | 50.07 | 50.01 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.235 | -2.35 | -1.175 | -1.175 | 0 | 12 | 1 | 1 | -1.175 | 10 | 0 | 0
1402.2 | 50.05 | 50.01 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.135 | -1.35 | -0.675 | -0.675 | 0 | 12 | 1 | 1 | -0.675 | 10 | 0 | 0
1402.25 | 50.05 | 50.01 | 0 | 0 | 0 | 50.07 | -0.032353 | -0.035 | -0.35 | -0.175 | -0.175 | 0 | 12 | 1 | 1 | -0.175 | 10 | 0 | 0
1402.3 | 50.1 | 50.01 | 0 | 0 | 0 | 50.1 | -0.05 | -0.05 | -0.5 | -0.25 | -0.25 | 0 | 12 | 1 | 1 | -0.25 | 10 | 0 | 0
1402.35 | 50.1 | 50.01 | 0 | 0 | 0 | 50.1 | -0.05 | -0.05 | -0.5 | -0.25 | -0.25 | 0 | 12 | 1 | 1 | -0.25 | 10 | 0 | 0
1402.4 | 50.11 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1402.45 | 50.11 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1402.5 | 50.06 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1402.55 | 50.06 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1402.6 | 50.04 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1402.65 | 50.04 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1402.7 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1402.75 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1402.8 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1402.85 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1402.9 | 50.11 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1402.95 | 50.11 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1403 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1403.05 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1403.1 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1403.15 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1403.2 | 50.02 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.11 | -0.145 | -0.145 | -1.45 | -0.73971 | -0.73971 | 0 | 12 | 1 | 1 | -0.73971 | 10 | 0 | 0
1403.25 | 50.02 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.11 | -0.145 | -0.145 | -1.45 | -0.73971 | -0.73971 | 0 | 12 | 1 | 1 | -0.73971 | 10 | 0 | 0
1403.3 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1403.35 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1403.4 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1403.45 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1403.5 | 50.01 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1403.55 | 50.01 | 50 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.045 | -0.45 | -0.225 | -0.225 | 0 | 12 | 1 | 1 | -0.225 | 10 | 0 | 0
1403.6 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
1403.65 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
1403.7 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
1403.75 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1403.8 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.14706 | 0.14706 | 0 | 12 | 1 | 1 | 0.14706 | 10 | 0 | 0
1403.85 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1403.9 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1403.95 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1404 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1404.05 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1404.1 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1404.15 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1404.2 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1404.25 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1404.3 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1404.35 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1404.4 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1404.45 | 50 | 50 | 0 | 0 | 0 | 50.01 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1404.5 | 49.5 | 49.5 | 1 | 1 | 10 | 50.01 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1404.55 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1404.6 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1404.65 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1404.7 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1404.75 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1404.8 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1404.85 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1404.9 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1404.95 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1405 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1405.05 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.1 | 1 | 5.5 | 5.5 | 0 | 12 | 1 | 1 | 5.5 | 10 | 0 | 0
1405.1 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.2 | 2 | 6 | 6 | 0 | 12 | 1 | 1 | 6 | 10 | 0 | 0
1405.15 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.3 | 3 | 6.5 | 6.5 | 0 | 12 | 1 | 1 | 6.5 | 10 | 0 | 0
1405.2 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.4 | 4 | 7 | 7 | 0 | 12 | 1 | 1 | 7 | 10 | 0 | 0
1405.25 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.5 | 5 | 7.5 | 7.5 | 0 | 12 | 1 | 1 | 7.5 | 10 | 0 | 0
1405.3 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.6 | 6 | 8 | 8 | 0 | 12 | 1 | 1 | 8 | 10 | 0 | 0
1405.35 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.7 | 7 | 8.5 | 8.5 | 0 | 12 | 1 | 1 | 8.5 | 10 | 0 | 0
1405.4 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.8 | 8 | 9 | 9 | 0 | 12 | 1 | 1 | 9 | 10 | 0 | 0
1405.45 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.9 | 9 | 9.5 | 9.5 | 0 | 12 | 1 | 1 | 9.5 | 10 | 0 | 0
1405.5 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1405.55 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1405.6 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1405.65 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1405.7 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1405.75 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1405.8 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1405.85 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1405.9 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1405.95 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1406 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1406.05 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1406.1 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1406.15 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1406.2 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1406.25 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1406.3 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1406.35 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1406.4 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1406.45 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1406.5 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1406.55 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1406.6 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1406.65 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1406.7 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1406.75 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1406.8 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1406.85 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1406.9 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1406.95 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1407 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1407.05 | 50.5 | 50.5 | -1 | 0.9 | 9 | 50.5 | -1 | -1 | -10 | -0.5 | -0.5 | 0 | 12 | 1 | 1 | -0.5 | 10 | 0 | 0
1407.1 | 50.5 | 50.5 | -1 | 0.8 | 8 | 50.5 | -1 | -1 | -10 | -1 | -1 | 0 | 12 | 1 | 1 | -1 | 10 | 0 | 0
1407.15 | 50.5 | 50.5 | -1 | 0.7 | 7 | 50.5 | -1 | -1 | -10 | -1.5 | -1.5 | 0 | 12 | 1 | 1 | -1.5 | 10 | 0 | 0
1407.2 | 50.5 | 50.5 | -1 | 0.6 | 6 | 50.5 | -1 | -1 | -10 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
1407.25 | 50.5 | 50.5 | -1 | 0.5 | 5 | 50.5 | -1 | -1 | -10 | -2.5 | -2.5 | 0 | 12 | 1 | 1 | -2.5 | 10 | 0 | 0
1407.3 | 50.5 | 50.5 | -1 | 0.4 | 4 | 50.5 | -1 | -1 | -10 | -3 | -3 | 0 | 12 | 1 | 1 | -3 | 10 | 0 | 0
1407.35 | 50.5 | 50.5 | -1 | 0.3 | 3 | 50.5 | -1 | -1 | -10 | -3.5 | -3.5 | 0 | 12 | 1 | 1 | -3.5 | 10 | 0 | 0
1407.4 | 50.5 | 50.5 | -1 | 0.2 | 2 | 50.5 | -1 | -1 | -10 | -4 | -4 | 0 | 12 | 1 | 1 | -4 | 10 | 0 | 0
1407.45 | 50.5 | 50.5 | -1 | 0.1 | 1 | 50.5 | -1 | -1 | -10 | -4.5 | -4.5 | 0 | 12 | 1 | 1 | -4.5 | 10 | 0 | 0
1407.5 | 50.5 | 50.5 | -1 | 0 | 0 | 50.5 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1407.55 | 50.5 | 50.5 | -1 | -0.1 | -1 | 50.5 | -1 | -1 | -10 | -5.5 | -5.5 | 0 | 12 | 1 | 1 | -5.5 | 10 | 0 | 0
1407.6 | 50.5 | 50.5 | -1 | -0.2 | -2 | 50.5 | -1 | -1 | -10 | -6 | -6 | 0 | 12 | 1 | 1 | -6 | 10 | 0 | 0
1407.65 | 50.5 | 50.5 | -1 | -0.3 | -3 | 50.5 | -1 | -1 | -10 | -6.5 | -6.5 | 0 | 12 | 1 | 1 | -6.5 | 10 | 0 | 0
1407.7 | 50.5 | 50.5 | -1 | -0.4 | -4 | 50.5 | -1 | -1 | -10 | -7 | -7 | 0 | 12 | 1 | 1 | -7 | 10 | 0 | 0
1407.75 | 50.5 | 50.5 | -1 | -0.5 | -5 | 50.5 | -1 | -1 | -10 | -7.5 | -7.5 | 0 | 12 | 1 | 1 | -7.5 | 10 | 0 | 0
1407.8 | 50.5 | 50.5 | -1 | -0.6 | -6 | 50.5 | -1 | -1 | -10 | -8 | -8 | 0 | 12 | 1 | 1 | -8 | 10 | 0 | 0
1407.85 | 50.5 | 50.5 | -1 | -0.7 | -7 | 50.5 | -1 | -1 | -10 | -8.5 | -8.5 | 0 | 12 | 1 | 1 | -8.5 | 10 | 0 | 0
1407.9 | 50.5 | 50.5 | -1 | -0.8 | -8 | 50.5 | -1 | -1 | -10 | -9 | -9 | 0 | 12 | 1 | 1 | -9 | 10 | 0 | 0
1407.95 | 50.5 | 50.5 | -1 | -0.9 | -9 | 50.5 | -1 | -1 | -10 | -9.5 | -9.5 | 0 | 12 | 1 | 1 | -9.5 | 10 | 0 | 0
1408 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1408.05 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1408.1 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1408.15 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1408.2 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1408.25 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1408.3 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1408.35 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1408.4 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1408.45 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1408.5 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1408.55 | 50.47 | 50.47 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1408.6 | 50.45 | 50.45 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1408.65 | 50.42 | 50.42 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1408.7 | 50.4 | 50.4 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1408.75 | 50.37 | 50.37 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1408.8 | 50.35 | 50.35 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1408.85 | 50.32 | 50.32 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1408.9 | 50.29 | 50.29 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1408.95 | 50.27 | 50.27 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1409 | 50.24 | 50.24 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1409.05 | 50.22 | 50.22 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1409.1 | 50.19 | 50.19 | -0.905 | -0.905 | -9.05 | 50.47 | -1 | -1 | -10 | -9.525 | -9.525 | 0 | 12 | 1 | 1 | -9.525 | 10 | 0 | 0
1409.15 | 50.17 | 50.17 | -0.715 | -0.715 | -7.15 | 50.45 | -1 | -1 | -10 | -8.575 | -8.575 | 0 | 12 | 1 | 1 | -8.575 | 10 | 0 | 0
1409.2 | 50.14 | 50.14 | -0.43 | -0.43 | -4.3 | 50.42 | -1 | -1 | -10 | -7.15 | -7.15 | 0 | 12 | 1 | 1 | -7.15 | 10 | 0 | 0
1409.25 | 50.12 | 50.12 | -0.24 | -0.24 | -2.4 | 50.4 | -1 | -1 | -10 | -6.2 | -6.2 | 0 | 12 | 1 | 1 | -6.2 | 10 | 0 | 0
1409.3 | 50.09 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 50.37 | -1 | -1 | -10 | -5.2206 | -5.2206 | 0 | 12 | 1 | 1 | -5.2206 | 10 | 0 | 0
1409.35 | 50.06 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.35 | -1 | -1 | -10 | -5.1324 | -5.1324 | 0 | 12 | 1 | 1 | -5.1324 | 10 | 0 | 0
1409.4 | 50.04 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.32 | -1 | -1 | -10 | -5.0735 | -5.0735 | 0 | 12 | 1 | 1 | -5.0735 | 10 | 0 | 0
1409.45 | 50.01 | 50.01 | 0 | 0 | 0 | 50.29 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1409.5 | 49.99 | 49.99 | 0 | 0 | 0 | 50.27 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1409.55 | 49.96 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.24 | -1 | -1 | -10 | -4.9265 | -4.9265 | 0 | 12 | 1 | 1 | -4.9265 | 10 | 0 | 0
1409.6 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.22 | -1 | -1 | -10 | -4.8676 | -4.8676 | 0 | 12 | 1 | 1 | -4.8676 | 10 | 0 | 0
1409.65 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.19 | -0.905 | -0.905 | -9.05 | -4.3044 | -4.3044 | 0 | 12 | 1 | 1 | -4.3044 | 10 | 0 | 0
1409.7 | 49.88 | 49.88 | 0.24 | 0.24 | 2.4 | 50.17 | -0.715 | -0.805 | -8.05 | -2.825 | -2.825 | 0 | 12 | 1 | 1 | -2.825 | 10 | 0 | 0
1409.75 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.14 | -0.43 | -0.705 | -7.05 | -1.375 | -1.375 | 0 | 12 | 1 | 1 | -1.375 | 10 | 0 | 0
1409.8 | 49.83 | 49.83 | 0.715 | 0.715 | 7.15 | 50.12 | -0.24 | -0.605 | -6.05 | 0.55 | 0.55 | 0 | 12 | 1 | 1 | 0.55 | 10 | 0 | 0
1409.85 | 49.81 | 49.81 | 0.905 | 0.905 | 9.05 | 50.09 | -0.044118 | -0.505 | -5.05 | 2 | 2 | 0 | 12 | 1 | 1 | 2 | 10 | 0 | 0
1409.9 | 49.78 | 49.78 | 1 | 1 | 10 | 50.06 | -0.026471 | -0.405 | -4.05 | 2.975 | 2.975 | 0 | 12 | 1 | 1 | 2.975 | 10 | 0 | 0
1409.95 | 49.76 | 49.76 | 1 | 1 | 10 | 50.04 | -0.014706 | -0.305 | -3.05 | 3.475 | 3.475 | 0 | 12 | 1 | 1 | 3.475 | 10 | 0 | 0
1410 | 49.73 | 49.73 | 1 | 1 | 10 | 50.01 | 0 | -0.205 | -2.05 | 3.975 | 3.975 | 0 | 12 | 1 | 1 | 3.975 | 10 | 0 | 0
1410.05 | 49.71 | 49.71 | 1 | 1 | 10 | 49.99 | 0 | -0.105 | -1.05 | 4.475 | 4.475 | 0 | 12 | 1 | 1 | 4.475 | 10 | 0 | 0
1410.1 | 49.68 | 49.68 | 1 | 1 | 10 | 49.96 | 0.014706 | -0.005 | -0.05 | 4.975 | 4.975 | 0 | 12 | 1 | 1 | 4.975 | 10 | 0 | 0
1410.15 | 49.65 | 49.65 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
1410.2 | 49.63 | 49.63 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1410.25 | 49.6 | 49.6 | 1 | 1 | 10 | 49.88 | 0.24 | 0.14412 | 1.4412 | 5.7206 | 5.7206 | 0 | 12 | 1 | 1 | 5.7206 | 10 | 0 | 0
1410.3 | 49.58 | 49.58 | 1 | 1 | 10 | 49.86 | 0.43 | 0.24412 | 2.4412 | 6.2206 | 6.2206 | 0 | 12 | 1 | 1 | 6.2206 | 10 | 0 | 0
1410.35 | 49.55 | 49.55 | 1 | 1 | 10 | 49.83 | 0.715 | 0.34412 | 3.4412 | 6.7206 | 6.7206 | 0 | 12 | 1 | 1 | 6.7206 | 10 | 0 | 0
1410.4 | 49.53 | 49.53 | 1 | 1 | 10 | 49.81 | 0.905 | 0.44412 | 4.4412 | 7.2206 | 7.2206 | 0 | 12 | 1 | 1 | 7.2206 | 10 | 0 | 0
1410.45 | 49.5 | 49.5 | 1 | 1 | 10 | 49.78 | 1 | 0.54412 | 5.4412 | 7.7206 | 7.7206 | 0 | 12 | 1 | 1 | 7.7206 | 10 | 0 | 0
1410.5 | 49.5 | 49.5 | 1 | 1 | 10 | 49.76 | 1 | 0.64412 | 6.4412 | 8.2206 | 8.2206 | 0 | 12 | 1 | 1 | 8.2206 | 10 | 0 | 0
1410.55 | 49.53 | 49.5 | 1 | 1 | 10 | 49.73 | 1 | 0.74412 | 7.4412 | 8.7206 | 8.7206 | 0 | 12 | 1 | 1 | 8.7206 | 10 | 0 | 0
1410.6 | 49.55 | 49.5 | 1 | 1 | 10 | 49.71 | 1 | 0.84412 | 8.4412 | 9.2206 | 9.2206 | 0 | 12 | 1 | 1 | 9.2206 | 10 | 0 | 0
1410.65 | 49.58 | 49.5 | 1 | 1 | 10 | 49.68 | 1 | 0.94412 | 9.4412 | 9.7206 | 9.7206 | 0 | 12 | 1 | 1 | 9.7206 | 10 | 0 | 0
1410.7 | 49.6 | 49.5 | 1 | 1 | 10 | 49.65 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1410.75 | 49.63 | 49.5 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1410.8 | 49.65 | 49.5 | 1 | 1 | 10 | 49.65 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1410.85 | 49.68 | 49.5 | 1 | 1 | 10 | 49.68 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1410.9 | 49.71 | 49.5 | 1 | 1 | 10 | 49.71 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1410.95 | 49.73 | 49.5 | 1 | 1 | 10 | 49.73 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1411 | 49.76 | 49.5 | 1 | 1 | 10 | 49.76 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1411.05 | 49.78 | 49.5 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1411.1 | 49.81 | 49.53 | 1 | 1 | 10 | 49.81 | 0.905 | 0.905 | 9.05 | 9.525 | 9.525 | 0 | 12 | 1 | 1 | 9.525 | 10 | 0 | 0
1411.15 | 49.83 | 49.55 | 1 | 1 | 10 | 49.83 | 0.715 | 0.715 | 7.15 | 8.575 | 8.575 | 0 | 12 | 1 | 1 | 8.575 | 10 | 0 | 0
1411.2 | 49.86 | 49.58 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
1411.25 | 49.88 | 49.6 | 1 | 1 | 10 | 49.88 | 0.24 | 0.24 | 2.4 | 6.2 | 6.2 | 0 | 12 | 1 | 1 | 6.2 | 10 | 0 | 0
1411.3 | 49.91 | 49.63 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1411.35 | 49.94 | 49.65 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
1411.4 | 49.96 | 49.68 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
1411.45 | 49.99 | 49.71 | 1 | 1 | 10 | 49.99 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1411.5 | 50.01 | 49.73 | 1 | 1 | 10 | 50.01 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1411.55 | 50.04 | 49.76 | 1 | 1 | 10 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 4.9265 | 4.9265 | 0 | 12 | 1 | 1 | 4.9265 | 10 | 0 | 0
1411.6 | 50.06 | 49.78 | 1 | 1 | 10 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 4.8676 | 4.8676 | 0 | 12 | 1 | 1 | 4.8676 | 10 | 0 | 0
1411.65 | 50.09 | 49.81 | 0.905 | 0.905 | 9.05 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 4.3044 | 4.3044 | 0 | 12 | 1 | 1 | 4.3044 | 10 | 0 | 0
1411.7 | 50.12 | 49.83 | 0.715 | 0.805 | 8.05 | 50.12 | -0.24 | -0.24 | -2.4 | 2.825 | 2.825 | 0 | 12 | 1 | 1 | 2.825 | 10 | 0 | 0
1411.75 | 50.14 | 49.86 | 0.43 | 0.705 | 7.05 | 50.14 | -0.43 | -0.43 | -4.3 | 1.375 | 1.375 | 0 | 12 | 1 | 1 | 1.375 | 10 | 0 | 0
1411.8 | 50.17 | 49.88 | 0.24 | 0.605 | 6.05 | 50.17 | -0.715 | -0.715 | -7.15 | -0.55 | -0.55 | 0 | 12 | 1 | 1 | -0.55 | 10 | 0 | 0
1411.85 | 50.19 | 49.91 | 0.044118 | 0.505 | 5.05 | 50.19 | -0.905 | -0.905 | -9.05 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
1411.9 | 50.22 | 49.94 | 0.026471 | 0.405 | 4.05 | 50.22 | -1 | -1 | -10 | -2.975 | -2.975 | 0 | 12 | 1 | 1 | -2.975 | 10 | 0 | 0
1411.95 | 50.24 | 49.96 | 0.014706 | 0.305 | 3.05 | 50.24 | -1 | -1 | -10 | -3.475 | -3.475 | 0 | 12 | 1 | 1 | -3.475 | 10 | 0 | 0
1412 | 50.27 | 49.99 | 0 | 0.205 | 2.05 | 50.27 | -1 | -1 | -10 | -3.975 | -3.975 | 0 | 12 | 1 | 1 | -3.975 | 10 | 0 | 0
1412.05 | 50.29 | 50.01 | 0 | 0.105 | 1.05 | 50.29 | -1 | -1 | -10 | -4.475 | -4.475 | 0 | 12 | 1 | 1 | -4.475 | 10 | 0 | 0
1412.1 | 50.32 | 50.04 | -0.014706 | 0.005 | 0.05 | 50.32 | -1 | -1 | -10 | -4.975 | -4.975 | 0 | 12 | 1 | 1 | -4.975 | 10 | 0 | 0
1412.15 | 50.35 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.35 | -1 | -1 | -10 | -5.1324 | -5.1324 | 0 | 12 | 1 | 1 | -5.1324 | 10 | 0 | 0
1412.2 | 50.37 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 50.37 | -1 | -1 | -10 | -5.2206 | -5.2206 | 0 | 12 | 1 | 1 | -5.2206 | 10 | 0 | 0
1412.25 | 50.4 | 50.12 | -0.24 | -0.14412 | -1.4412 | 50.4 | -1 | -1 | -10 | -5.7206 | -5.7206 | 0 | 12 | 1 | 1 | -5.7206 | 10 | 0 | 0
1412.3 | 50.42 | 50.14 | -0.43 | -0.24412 | -2.4412 | 50.42 | -1 | -1 | -10 | -6.2206 | -6.2206 | 0 | 12 | 1 | 1 | -6.2206 | 10 | 0 | 0
1412.35 | 50.45 | 50.17 | -0.715 | -0.34412 | -3.4412 | 50.45 | -1 | -1 | -10 | -6.7206 | -6.7206 | 0 | 12 | 1 | 1 | -6.7206 | 10 | 0 | 0
1412.4 | 50.47 | 50.19 | -0.905 | -0.44412 | -4.4412 | 50.47 | -1 | -1 | -10 | -7.2206 | -7.2206 | 0 | 12 | 1 | 1 | -7.2206 | 10 | 0 | 0
1412.45 | 50.5 | 50.22 | -1 | -0.54412 | -5.4412 | 50.5 | -1 | -1 | -10 | -7.7206 | -7.7206 | 0 | 12 | 1 | 1 | -7.7206 | 10 | 0 | 0
1412.5 | 50.5 | 50.24 | -1 | -0.64412 | -6.4412 | 50.5 | -1 | -1 | -10 | -8.2206 | -8.2206 | 0 | 12 | 1 | 1 | -8.2206 | 10 | 0 | 0
1412.55 | 50.47 | 50.27 | -1 | -0.74412 | -7.4412 | 50.5 | -1 | -1 | -10 | -8.7206 | -8.7206 | 0 | 12 | 1 | 1 | -8.7206 | 10 | 0 | 0
1412.6 | 50.45 | 50.29 | -1 | -0.84412 | -8.4412 | 50.5 | -1 | -1 | -10 | -9.2206 | -9.2206 | 0 | 12 | 1 | 1 | -9.2206 | 10 | 0 | 0
1412.65 | 50.42 | 50.32 | -1 | -0.94412 | -9.4412 | 50.5 | -1 | -1 | -10 | -9.7206 | -9.7206 | 0 | 12 | 1 | 1 | -9.7206 | 10 | 0 | 0
1412.7 | 50.39 | 50.35 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1412.75 | 50.37 | 50.37 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1412.8 | 50.34 | 50.34 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1412.85 | 50.32 | 50.32 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1412.9 | 50.29 | 50.29 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1412.95 | 50.26 | 50.26 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1413 | 50.24 | 50.24 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1413.05 | 50.21 | 50.21 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1413.1 | 50.18 | 50.18 | -0.81 | -0.81 | -8.1 | 50.47 | -1 | -1 | -10 | -9.05 | -9.05 | 0 | 12 | 1 | 1 | -9.05 | 10 | 0 | 0
1413.15 | 50.16 | 50.16 | -0.62 | -0.62 | -6.2 | 50.45 | -1 | -1 | -10 | -8.1 | -8.1 | 0 | 12 | 1 | 1 | -8.1 | 10 | 0 | 0
1413.2 | 50.13 | 50.13 | -0.335 | -0.335 | -3.35 | 50.42 | -1 | -1 | -10 | -6.675 | -6.675 | 0 | 12 | 1 | 1 | -6.675 | 10 | 0 | 0
1413.25 | 50.11 | 50.11 | -0.145 | -0.145 | -1.45 | 50.39 | -1 | -1 | -10 | -5.725 | -5.725 | 0 | 12 | 1 | 1 | -5.725 | 10 | 0 | 0
1413.3 | 50.08 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 50.37 | -1 | -1 | -10 | -5.1912 | -5.1912 | 0 | 12 | 1 | 1 | -5.1912 | 10 | 0 | 0
1413.35 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.34 | -1 | -1 | -10 | -5.1029 | -5.1029 | 0 | 12 | 1 | 1 | -5.1029 | 10 | 0 | 0
1413.4 | 50.03 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 50.32 | -1 | -1 | -10 | -5.0441 | -5.0441 | 0 | 12 | 1 | 1 | -5.0441 | 10 | 0 | 0
1413.45 | 50 | 50 | 0 | 0 | 0 | 50.29 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1413.5 | 50 | 50 | 0 | 0 | 0 | 50.26 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1413.55 | 50 | 50 | 0 | 0 | 0 | 50.24 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1413.6 | 50 | 50 | 0 | 0 | 0 | 50.21 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1413.65 | 50 | 50 | 0 | 0 | 0 | 50.18 | -0.81 | -0.9 | -9 | -4.5 | -4.5 | 0 | 12 | 1 | 1 | -4.5 | 10 | 0 | 0
1413.7 | 50 | 50 | 0 | 0 | 0 | 50.16 | -0.62 | -0.8 | -8 | -4 | -4 | 0 | 12 | 1 | 1 | -4 | 10 | 0 | 0
1413.75 | 50 | 50 | 0 | 0 | 0 | 50.13 | -0.335 | -0.7 | -7 | -3.5 | -3.5 | 0 | 12 | 1 | 1 | -3.5 | 10 | 0 | 0
1413.8 | 50.01 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.6 | -6 | -3 | -3 | 0 | 12 | 1 | 1 | -3 | 10 | 0 | 0
1413.85 | 50.01 | 50 | 0 | 0 | 0 | 50.08 | -0.038235 | -0.5 | -5 | -2.5 | -2.5 | 0 | 12 | 1 | 1 | -2.5 | 10 | 0 | 0
1413.9 | 49.99 | 49.99 | 0 | 0 | 0 | 50.05 | -0.020588 | -0.4 | -4 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
1413.95 | 49.99 | 49.99 | 0 | 0 | 0 | 50.03 | -0.0088235 | -0.3 | -3 | -1.5 | -1.5 | 0 | 12 | 1 | 1 | -1.5 | 10 | 0 | 0
1414 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | -0.2 | -2 | -0.83824 | -0.83824 | 0 | 12 | 1 | 1 | -0.83824 | 10 | 0 | 0
1414.05 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | -0.1 | -1 | -0.33824 | -0.33824 | 0 | 12 | 1 | 1 | -0.33824 | 10 | 0 | 0
1414.1 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
1414.15 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
1414.2 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
1414.25 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
1414.3 | 49.89 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
1414.35 | 49.89 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
1414.4 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50.01 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1414.45 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1414.5 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1414.55 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 2.7868 | 2.7868 | 0 | 12 | 1 | 1 | 2.7868 | 10 | 0 | 0
1414.6 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 2.7868 | 2.7868 | 0 | 12 | 1 | 1 | 2.7868 | 10 | 0 | 0
1414.65 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 2.8456 | 2.8456 | 0 | 12 | 1 | 1 | 2.8456 | 10 | 0 | 0
1414.7 | 49.94 | 49.85 | 0.525 | 0.525 | 5.25 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 2.7574 | 2.7574 | 0 | 12 | 1 | 1 | 2.7574 | 10 | 0 | 0
1414.75 | 49.94 | 49.85 | 0.525 | 0.525 | 5.25 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 2.7574 | 2.7574 | 0 | 12 | 1 | 1 | 2.7574 | 10 | 0 | 0
1414.8 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1414.85 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1414.9 | 49.93 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1414.95 | 49.93 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1415 | 49.96 | 49.85 | 0.525 | 0.525 | 5.25 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 2.6985 | 2.6985 | 0 | 12 | 1 | 1 | 2.6985 | 10 | 0 | 0
1415.05 | 49.96 | 49.85 | 0.525 | 0.525 | 5.25 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 2.6985 | 2.6985 | 0 | 12 | 1 | 1 | 2.6985 | 10 | 0 | 0
1415.1 | 49.99 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1415.15 | 49.99 | 49.91 | 0.044118 | 0.425 | 4.25 | 49.99 | 0 | 0 | 0 | 2.125 | 2.125 | 0 | 12 | 1 | 1 | 2.125 | 10 | 0 | 0
1415.2 | 49.99 | 49.91 | 0.044118 | 0.325 | 3.25 | 49.99 | 0 | 0 | 0 | 1.625 | 1.625 | 0 | 12 | 1 | 1 | 1.625 | 10 | 0 | 0
1415.25 | 49.99 | 49.93 | 0.032353 | 0.225 | 2.25 | 49.99 | 0 | 0 | 0 | 1.125 | 1.125 | 0 | 12 | 1 | 1 | 1.125 | 10 | 0 | 0
1415.3 | 49.96 | 49.93 | 0.032353 | 0.125 | 1.25 | 49.99 | 0 | 0 | 0 | 0.625 | 0.625 | 0 | 12 | 1 | 1 | 0.625 | 10 | 0 | 0
1415.35 | 49.96 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 49.99 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1415.4 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1415.45 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1415.5 | 50.05 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.058824 | 0.058824 | 0 | 12 | 1 | 1 | 0.058824 | 10 | 0 | 0
1415.55 | 50.05 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
1415.6 | 49.97 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
1415.65 | 49.97 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
1415.7 | 49.92 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1415.75 | 49.92 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1415.8 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1415.85 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1415.9 | 49.94 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1415.95 | 49.94 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1416 | 50.01 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1416.05 | 50.01 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1416.1 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1416.15 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
1416.2 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
1416.25 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
1416.3 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
1416.35 | 49.95 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
1416.4 | 49.97 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
1416.45 | 49.97 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
1416.5 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
1416.55 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
1416.6 | 49.87 | 49.87 | 0.335 | 0.335 | 3.35 | 50.01 | 0 | 0 | 0 | 1.675 | 1.675 | 0 | 12 | 1 | 1 | 1.675 | 10 | 0 | 0
1416.65 | 49.87 | 49.87 | 0.335 | 0.335 | 3.35 | 49.99 | 0 | 0 | 0 | 1.675 | 1.675 | 0 | 12 | 1 | 1 | 1.675 | 10 | 0 | 0
1416.7 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1416.75 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 2.6691 | 2.6691 | 0 | 12 | 1 | 1 | 2.6691 | 10 | 0 | 0
1416.8 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1416.85 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1416.9 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1416.95 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1417 | 49.84 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1417.05 | 49.84 | 49.79 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
1417.1 | 49.89 | 49.79 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
1417.15 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.12647 | 1.2647 | 5.6324 | 5.6324 | 0 | 12 | 1 | 1 | 5.6324 | 10 | 0 | 0
1417.2 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.145 | 1.45 | 5.725 | 5.725 | 0 | 12 | 1 | 1 | 5.725 | 10 | 0 | 0
1417.25 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.145 | 1.45 | 5.725 | 5.725 | 0 | 12 | 1 | 1 | 5.725 | 10 | 0 | 0
1417.3 | 49.96 | 49.79 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
1417.35 | 49.96 | 49.79 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
1417.4 | 50.02 | 49.79 | 1 | 1 | 10 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 4.9853 | 4.9853 | 0 | 12 | 1 | 1 | 4.9853 | 10 | 0 | 0
1417.45 | 50.02 | 49.79 | 1 | 1 | 10 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 4.9853 | 4.9853 | 0 | 12 | 1 | 1 | 4.9853 | 10 | 0 | 0
1417.5 | 50.03 | 49.79 | 1 | 1 | 10 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.9559 | 4.9559 | 0 | 12 | 1 | 1 | 4.9559 | 10 | 0 | 0
1417.55 | 50.03 | 49.84 | 0.62 | 0.9 | 9 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.4559 | 4.4559 | 0 | 12 | 1 | 1 | 4.4559 | 10 | 0 | 0
1417.6 | 50.02 | 49.84 | 0.62 | 0.8 | 8 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 3.9559 | 3.9559 | 0 | 12 | 1 | 1 | 3.9559 | 10 | 0 | 0
1417.65 | 50.02 | 49.89 | 0.145 | 0.7 | 7 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 3.4559 | 3.4559 | 0 | 12 | 1 | 1 | 3.4559 | 10 | 0 | 0
1417.7 | 50.08 | 49.89 | 0.145 | 0.6 | 6 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 2.8088 | 2.8088 | 0 | 12 | 1 | 1 | 2.8088 | 10 | 0 | 0
1417.75 | 50.08 | 49.89 | 0.145 | 0.5 | 5 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 2.3088 | 2.3088 | 0 | 12 | 1 | 1 | 2.3088 | 10 | 0 | 0
1417.8 | 50.01 | 49.89 | 0.145 | 0.4 | 4 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 1.8088 | 1.8088 | 0 | 12 | 1 | 1 | 1.8088 | 10 | 0 | 0
1417.85 | 50.01 | 49.96 | 0.014706 | 0.3 | 3 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 1.3088 | 1.3088 | 0 | 12 | 1 | 1 | 1.3088 | 10 | 0 | 0
1417.9 | 49.94 | 49.94 | 0.026471 | 0.2 | 2 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.80882 | 0.80882 | 0 | 12 | 1 | 1 | 0.80882 | 10 | 0 | 0
1417.95 | 49.94 | 49.94 | 0.026471 | 0.1 | 1 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.30882 | 0.30882 | 0 | 12 | 1 | 1 | 0.30882 | 10 | 0 | 0
1418 | 50 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
1418.05 | 50 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
1418.1 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
1418.15 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
1418.2 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1418.25 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1418.3 | 49.92 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1418.35 | 49.92 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
1418.4 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50.01 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1418.45 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1418.5 | 49.92 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1418.55 | 49.92 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1418.6 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1418.65 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1418.7 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1418.75 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1418.8 | 49.87 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1418.85 | 49.87 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1418.9 | 49.8 | 49.8 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1418.95 | 49.8 | 49.8 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1419 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1419.05 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1419.1 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1419.15 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1419.2 | 49.72 | 49.72 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1419.25 | 49.72 | 49.72 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1419.3 | 49.67 | 49.67 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1419.35 | 49.67 | 49.67 | 1 | 1 | 10 | 49.87 | 0.335 | 0.14412 | 1.4412 | 5.7206 | 5.7206 | 0 | 12 | 1 | 1 | 5.7206 | 10 | 0 | 0
1419.4 | 49.65 | 49.65 | 1 | 1 | 10 | 49.87 | 0.335 | 0.24412 | 2.4412 | 6.2206 | 6.2206 | 0 | 12 | 1 | 1 | 6.2206 | 10 | 0 | 0
1419.45 | 49.65 | 49.65 | 1 | 1 | 10 | 49.8 | 1 | 0.34412 | 3.4412 | 6.7206 | 6.7206 | 0 | 12 | 1 | 1 | 6.7206 | 10 | 0 | 0
1419.5 | 49.59 | 49.59 | 1 | 1 | 10 | 49.8 | 1 | 0.44412 | 4.4412 | 7.2206 | 7.2206 | 0 | 12 | 1 | 1 | 7.2206 | 10 | 0 | 0
1419.55 | 49.59 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.54412 | 5.4412 | 7.7206 | 7.7206 | 0 | 12 | 1 | 1 | 7.7206 | 10 | 0 | 0
1419.6 | 49.66 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.64412 | 6.4412 | 8.2206 | 8.2206 | 0 | 12 | 1 | 1 | 8.2206 | 10 | 0 | 0
1419.65 | 49.66 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.74412 | 7.4412 | 8.7206 | 8.7206 | 0 | 12 | 1 | 1 | 8.7206 | 10 | 0 | 0
1419.7 | 49.63 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.84412 | 8.4412 | 9.2206 | 9.2206 | 0 | 12 | 1 | 1 | 9.2206 | 10 | 0 | 0
1419.75 | 49.63 | 49.59 | 1 | 1 | 10 | 49.72 | 1 | 0.94412 | 9.4412 | 9.7206 | 9.7206 | 0 | 12 | 1 | 1 | 9.7206 | 10 | 0 | 0
1419.8 | 49.61 | 49.59 | 1 | 1 | 10 | 49.72 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1419.85 | 49.61 | 49.59 | 1 | 1 | 10 | 49.67 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1419.9 | 49.54 | 49.54 | 1 | 1 | 10 | 49.67 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1419.95 | 49.54 | 49.54 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1420 | 49.46 | 49.46 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1420.05 | 49.46 | 49.46 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1420.1 | 49.45 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1420.15 | 49.45 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1420.2 | 49.51 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1420.25 | 49.51 | 49.45 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1420.3 | 49.5 | 49.45 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1420.35 | 49.5 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1420.4 | 49.54 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1420.45 | 49.54 | 49.45 | 1 | 1 | 10 | 49.54 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1420.5 | 49.59 | 49.45 | 1 | 1 | 10 | 49.59 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1420.55 | 49.59 | 49.45 | 1 | 1 | 10 | 49.59 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1420.6 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1420.65 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1420.7 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1420.75 | 49.61 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1420.8 | 49.53 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1420.85 | 49.53 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1420.9 | 49.54 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1420.95 | 49.54 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1421 | 49.61 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1421.05 | 49.61 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1421.1 | 49.66 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1421.15 | 49.66 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1421.2 | 49.64 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1421.25 | 49.64 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1421.3 | 49.69 | 49.53 | 1 | 1 | 10 | 49.69 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1421.35 | 49.69 | 49.53 | 1 | 1 | 10 | 49.69 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1421.4 | 49.74 | 49.53 | 1 | 1 | 10 | 49.74 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1421.45 | 49.74 | 49.54 | 1 | 1 | 10 | 49.74 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1421.5 | 49.78 | 49.54 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1421.55 | 49.78 | 49.61 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1421.6 | 49.82 | 49.61 | 1 | 1 | 10 | 49.82 | 0.81 | 0.81 | 8.1 | 9.05 | 9.05 | 0 | 12 | 1 | 1 | 9.05 | 10 | 0 | 0
1421.65 | 49.82 | 49.64 | 1 | 1 | 10 | 49.82 | 0.81 | 0.81 | 8.1 | 9.05 | 9.05 | 0 | 12 | 1 | 1 | 9.05 | 10 | 0 | 0
1421.7 | 49.86 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
1421.75 | 49.86 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
1421.8 | 49.84 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
1421.85 | 49.84 | 49.69 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
1421.9 | 49.91 | 49.69 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1421.95 | 49.91 | 49.74 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1422 | 49.97 | 49.74 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1422.05 | 49.97 | 49.78 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1422.1 | 50.03 | 49.78 | 1 | 1 | 10 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.9559 | 4.9559 | 0 | 12 | 1 | 1 | 4.9559 | 10 | 0 | 0
1422.15 | 50.03 | 49.82 | 0.81 | 0.9 | 9 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.4559 | 4.4559 | 0 | 12 | 1 | 1 | 4.4559 | 10 | 0 | 0
1422.2 | 50.05 | 49.82 | 0.81 | 0.81 | 8.1 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 3.9471 | 3.9471 | 0 | 12 | 1 | 1 | 3.9471 | 10 | 0 | 0
1422.25 | 50.05 | 49.84 | 0.62 | 0.71 | 7.1 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 3.4471 | 3.4471 | 0 | 12 | 1 | 1 | 3.4471 | 10 | 0 | 0
1422.3 | 50.01 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
1422.35 | 50.01 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
1422.4 | 49.95 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
1422.45 | 49.95 | 49.91 | 0.044118 | 0.52 | 5.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.4971 | 2.4971 | 0 | 12 | 1 | 1 | 2.4971 | 10 | 0 | 0
1422.5 | 49.99 | 49.91 | 0.044118 | 0.42 | 4.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 1.9971 | 1.9971 | 0 | 12 | 1 | 1 | 1.9971 | 10 | 0 | 0
1422.55 | 49.99 | 49.95 | 0.020588 | 0.32 | 3.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 1.4971 | 1.4971 | 0 | 12 | 1 | 1 | 1.4971 | 10 | 0 | 0
1422.6 | 49.92 | 49.92 | 0.038235 | 0.22 | 2.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.99706 | 0.99706 | 0 | 12 | 1 | 1 | 0.99706 | 10 | 0 | 0
1422.65 | 49.92 | 49.92 | 0.038235 | 0.12 | 1.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.49706 | 0.49706 | 0 | 12 | 1 | 1 | 0.49706 | 10 | 0 | 0
1422.7 | 49.97 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1422.75 | 49.97 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1422.8 | 50.02 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1422.85 | 50.02 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.17647 | 0.17647 | 0 | 12 | 1 | 1 | 0.17647 | 10 | 0 | 0
1422.9 | 50.07 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1422.95 | 50.07 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1423 | 50.06 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1423.05 | 50.06 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1423.1 | 50.13 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
1423.15 | 50.13 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
1423.2 | 50.09 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
1423.25 | 50.09 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6309 | -1.6309 | 0 | 12 | 1 | 1 | -1.6309 | 10 | 0 | 0
1423.3 | 50.07 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6309 | -1.6309 | 0 | 12 | 1 | 1 | -1.6309 | 10 | 0 | 0
1423.35 | 50.07 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6897 | -1.6897 | 0 | 12 | 1 | 1 | -1.6897 | 10 | 0 | 0
1423.4 | 50.07 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6897 | -1.6897 | 0 | 12 | 1 | 1 | -1.6897 | 10 | 0 | 0
1423.45 | 50.07 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.13 | -0.335 | -0.335 | -3.35 | -1.8074 | -1.8074 | 0 | 12 | 1 | 1 | -1.8074 | 10 | 0 | 0
1423.5 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.13 | -0.335 | -0.335 | -3.35 | -1.7779 | -1.7779 | 0 | 12 | 1 | 1 | -1.7779 | 10 | 0 | 0
1423.55 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.13 | -0.335 | -0.335 | -3.35 | -1.7779 | -1.7779 | 0 | 12 | 1 | 1 | -1.7779 | 10 | 0 | 0
1423.6 | 50.01 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
1423.65 | 50.01 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
1423.7 | 50.07 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
1423.75 | 50.07 | 50.01 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.235 | -2.35 | -1.175 | -1.175 | 0 | 12 | 1 | 1 | -1.175 | 10 | 0 | 0
1423.8 | 50.05 | 50.01 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.135 | -1.35 | -0.675 | -0.675 | 0 | 12 | 1 | 1 | -0.675 | 10 | 0 | 0
1423.85 | 50.05 | 50.01 | 0 | 0 | 0 | 50.07 | -0.032353 | -0.035 | -0.35 | -0.175 | -0.175 | 0 | 12 | 1 | 1 | -0.175 | 10 | 0 | 0
1423.9 | 50.1 | 50.01 | 0 | 0 | 0 | 50.1 | -0.05 | -0.05 | -0.5 | -0.25 | -0.25 | 0 | 12 | 1 | 1 | -0.25 | 10 | 0 | 0
1423.95 | 50.1 | 50.01 | 0 | 0 | 0 | 50.1 | -0.05 | -0.05 | -0.5 | -0.25 | -0.25 | 0 | 12 | 1 | 1 | -0.25 | 10 | 0 | 0
1424 | 50.11 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1424.05 | 50.11 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1424.1 | 50.06 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1424.15 | 50.06 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1424.2 | 50.04 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1424.25 | 50.04 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1424.3 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1424.35 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1424.4 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1424.45 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1424.5 | 50.11 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1424.55 | 50.11 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1424.6 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1424.65 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1424.7 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1424.75 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1424.8 | 50.02 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.11 | -0.145 | -0.145 | -1.45 | -0.73971 | -0.73971 | 0 | 12 | 1 | 1 | -0.73971 | 10 | 0 | 0
1424.85 | 50.02 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.11 | -0.145 | -0.145 | -1.45 | -0.73971 | -0.73971 | 0 | 12 | 1 | 1 | -0.73971 | 10 | 0 | 0
1424.9 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1424.95 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1425 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1425.05 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1425.1 | 50.01 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1425.15 | 50.01 | 50 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.045 | -0.45 | -0.225 | -0.225 | 0 | 12 | 1 | 1 | -0.225 | 10 | 0 | 0
1425.2 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
1425.25 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
1425.3 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
1425.35 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1425.4 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.14706 | 0.14706 | 0 | 12 | 1 | 1 | 0.14706 | 10 | 0 | 0
1425.45 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1425.5 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1425.55 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1425.6 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1425.65 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1425.7 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1425.75 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1425.8 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1425.85 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1425.9 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1425.95 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1426 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1426.05 | 50 | 50 | 0 | 0 | 0 | 50.01 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1426.1 | 49.5 | 49.5 | 1 | 1 | 10 | 50.01 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1426.15 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1426.2 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1426.25 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1426.3 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1426.35 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1426.4 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1426.45 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1426.5 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1426.55 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1426.6 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1426.65 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.1 | 1 | 5.5 | 5.5 | 0 | 12 | 1 | 1 | 5.5 | 10 | 0 | 0
1426.7 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.2 | 2 | 6 | 6 | 0 | 12 | 1 | 1 | 6 | 10 | 0 | 0
1426.75 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.3 | 3 | 6.5 | 6.5 | 0 | 12 | 1 | 1 | 6.5 | 10 | 0 | 0
1426.8 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.4 | 4 | 7 | 7 | 0 | 12 | 1 | 1 | 7 | 10 | 0 | 0
1426.85 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.5 | 5 | 7.5 | 7.5 | 0 | 12 | 1 | 1 | 7.5 | 10 | 0 | 0
1426.9 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.6 | 6 | 8 | 8 | 0 | 12 | 1 | 1 | 8 | 10 | 0 | 0
1426.95 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.7 | 7 | 8.5 | 8.5 | 0 | 12 | 1 | 1 | 8.5 | 10 | 0 | 0
1427 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.8 | 8 | 9 | 9 | 0 | 12 | 1 | 1 | 9 | 10 | 0 | 0
1427.05 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.9 | 9 | 9.5 | 9.5 | 0 | 12 | 1 | 1 | 9.5 | 10 | 0 | 0
1427.1 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1427.15 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1427.2 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1427.25 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1427.3 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1427.35 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1427.4 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1427.45 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1427.5 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1427.55 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1427.6 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1427.65 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1427.7 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1427.75 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1427.8 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1427.85 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1427.9 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1427.95 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1428 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1428.05 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1428.1 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1428.15 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1428.2 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1428.25 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1428.3 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1428.35 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1428.4 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1428.45 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1428.5 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1428.55 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1428.6 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1428.65 | 50.5 | 50.5 | -1 | 0.9 | 9 | 50.5 | -1 | -1 | -10 | -0.5 | -0.5 | 0 | 12 | 1 | 1 | -0.5 | 10 | 0 | 0
1428.7 | 50.5 | 50.5 | -1 | 0.8 | 8 | 50.5 | -1 | -1 | -10 | -1 | -1 | 0 | 12 | 1 | 1 | -1 | 10 | 0 | 0
1428.75 | 50.5 | 50.5 | -1 | 0.7 | 7 | 50.5 | -1 | -1 | -10 | -1.5 | -1.5 | 0 | 12 | 1 | 1 | -1.5 | 10 | 0 | 0
1428.8 | 50.5 | 50.5 | -1 | 0.6 | 6 | 50.5 | -1 | -1 | -10 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
1428.85 | 50.5 | 50.5 | -1 | 0.5 | 5 | 50.5 | -1 | -1 | -10 | -2.5 | -2.5 | 0 | 12 | 1 | 1 | -2.5 | 10 | 0 | 0
1428.9 | 50.5 | 50.5 | -1 | 0.4 | 4 | 50.5 | -1 | -1 | -10 | -3 | -3 | 0 | 12 | 1 | 1 | -3 | 10 | 0 | 0
1428.95 | 50.5 | 50.5 | -1 | 0.3 | 3 | 50.5 | -1 | -1 | -10 | -3.5 | -3.5 | 0 | 12 | 1 | 1 | -3.5 | 10 | 0 | 0
1429 | 50.5 | 50.5 | -1 | 0.2 | 2 | 50.5 | -1 | -1 | -10 | -4 | -4 | 0 | 12 | 1 | 1 | -4 | 10 | 0 | 0
1429.05 | 50.5 | 50.5 | -1 | 0.1 | 1 | 50.5 | -1 | -1 | -10 | -4.5 | -4.5 | 0 | 12 | 1 | 1 | -4.5 | 10 | 0 | 0
1429.1 | 50.5 | 50.5 | -1 | 0 | 0 | 50.5 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1429.15 | 50.5 | 50.5 | -1 | -0.1 | -1 | 50.5 | -1 | -1 | -10 | -5.5 | -5.5 | 0 | 12 | 1 | 1 | -5.5 | 10 | 0 | 0
1429.2 | 50.5 | 50.5 | -1 | -0.2 | -2 | 50.5 | -1 | -1 | -10 | -6 | -6 | 0 | 12 | 1 | 1 | -6 | 10 | 0 | 0
1429.25 | 50.5 | 50.5 | -1 | -0.3 | -3 | 50.5 | -1 | -1 | -10 | -6.5 | -6.5 | 0 | 12 | 1 | 1 | -6.5 | 10 | 0 | 0
1429.3 | 50.5 | 50.5 | -1 | -0.4 | -4 | 50.5 | -1 | -1 | -10 | -7 | -7 | 0 | 12 | 1 | 1 | -7 | 10 | 0 | 0
1429.35 | 50.5 | 50.5 | -1 | -0.5 | -5 | 50.5 | -1 | -1 | -10 | -7.5 | -7.5 | 0 | 12 | 1 | 1 | -7.5 | 10 | 0 | 0
1429.4 | 50.5 | 50.5 | -1 | -0.6 | -6 | 50.5 | -1 | -1 | -10 | -8 | -8 | 0 | 12 | 1 | 1 | -8 | 10 | 0 | 0
1429.45 | 50.5 | 50.5 | -1 | -0.7 | -7 | 50.5 | -1 | -1 | -10 | -8.5 | -8.5 | 0 | 12 | 1 | 1 | -8.5 | 10 | 0 | 0
1429.5 | 50.5 | 50.5 | -1 | -0.8 | -8 | 50.5 | -1 | -1 | -10 | -9 | -9 | 0 | 12 | 1 | 1 | -9 | 10 | 0 | 0
1429.55 | 50.5 | 50.5 | -1 | -0.9 | -9 | 50.5 | -1 | -1 | -10 | -9.5 | -9.5 | 0 | 12 | 1 | 1 | -9.5 | 10 | 0 | 0
1429.6 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1429.65 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1429.7 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1429.75 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1429.8 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1429.85 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1429.9 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1429.95 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1430 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1430.05 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1430.1 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1430.15 | 50.47 | 50.47 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1430.2 | 50.45 | 50.45 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1430.25 | 50.42 | 50.42 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1430.3 | 50.4 | 50.4 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1430.35 | 50.37 | 50.37 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1430.4 | 50.35 | 50.35 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1430.45 | 50.32 | 50.32 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1430.5 | 50.29 | 50.29 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1430.55 | 50.27 | 50.27 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1430.6 | 50.24 | 50.24 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1430.65 | 50.22 | 50.22 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1430.7 | 50.19 | 50.19 | -0.905 | -0.905 | -9.05 | 50.47 | -1 | -1 | -10 | -9.525 | -9.525 | 0 | 12 | 1 | 1 | -9.525 | 10 | 0 | 0
1430.75 | 50.17 | 50.17 | -0.715 | -0.715 | -7.15 | 50.45 | -1 | -1 | -10 | -8.575 | -8.575 | 0 | 12 | 1 | 1 | -8.575 | 10 | 0 | 0
1430.8 | 50.14 | 50.14 | -0.43 | -0.43 | -4.3 | 50.42 | -1 | -1 | -10 | -7.15 | -7.15 | 0 | 12 | 1 | 1 | -7.15 | 10 | 0 | 0
1430.85 | 50.12 | 50.12 | -0.24 | -0.24 | -2.4 | 50.4 | -1 | -1 | -10 | -6.2 | -6.2 | 0 | 12 | 1 | 1 | -6.2 | 10 | 0 | 0
1430.9 | 50.09 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 50.37 | -1 | -1 | -10 | -5.2206 | -5.2206 | 0 | 12 | 1 | 1 | -5.2206 | 10 | 0 | 0
1430.95 | 50.06 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.35 | -1 | -1 | -10 | -5.1324 | -5.1324 | 0 | 12 | 1 | 1 | -5.1324 | 10 | 0 | 0
1431 | 50.04 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.32 | -1 | -1 | -10 | -5.0735 | -5.0735 | 0 | 12 | 1 | 1 | -5.0735 | 10 | 0 | 0
1431.05 | 50.01 | 50.01 | 0 | 0 | 0 | 50.29 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1431.1 | 49.99 | 49.99 | 0 | 0 | 0 | 50.27 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1431.15 | 49.96 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.24 | -1 | -1 | -10 | -4.9265 | -4.9265 | 0 | 12 | 1 | 1 | -4.9265 | 10 | 0 | 0
1431.2 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.22 | -1 | -1 | -10 | -4.8676 | -4.8676 | 0 | 12 | 1 | 1 | -4.8676 | 10 | 0 | 0
1431.25 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.19 | -0.905 | -0.905 | -9.05 | -4.3044 | -4.3044 | 0 | 12 | 1 | 1 | -4.3044 | 10 | 0 | 0
1431.3 | 49.88 | 49.88 | 0.24 | 0.24 | 2.4 | 50.17 | -0.715 | -0.805 | -8.05 | -2.825 | -2.825 | 0 | 12 | 1 | 1 | -2.825 | 10 | 0 | 0
1431.35 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.14 | -0.43 | -0.705 | -7.05 | -1.375 | -1.375 | 0 | 12 | 1 | 1 | -1.375 | 10 | 0 | 0
1431.4 | 49.83 | 49.83 | 0.715 | 0.715 | 7.15 | 50.12 | -0.24 | -0.605 | -6.05 | 0.55 | 0.55 | 0 | 12 | 1 | 1 | 0.55 | 10 | 0 | 0
1431.45 | 49.81 | 49.81 | 0.905 | 0.905 | 9.05 | 50.09 | -0.044118 | -0.505 | -5.05 | 2 | 2 | 0 | 12 | 1 | 1 | 2 | 10 | 0 | 0
1431.5 | 49.78 | 49.78 | 1 | 1 | 10 | 50.06 | -0.026471 | -0.405 | -4.05 | 2.975 | 2.975 | 0 | 12 | 1 | 1 | 2.975 | 10 | 0 | 0
1431.55 | 49.76 | 49.76 | 1 | 1 | 10 | 50.04 | -0.014706 | -0.305 | -3.05 | 3.475 | 3.475 | 0 | 12 | 1 | 1 | 3.475 | 10 | 0 | 0
1431.6 | 49.73 | 49.73 | 1 | 1 | 10 | 50.01 | 0 | -0.205 | -2.05 | 3.975 | 3.975 | 0 | 12 | 1 | 1 | 3.975 | 10 | 0 | 0
1431.65 | 49.71 | 49.71 | 1 | 1 | 10 | 49.99 | 0 | -0.105 | -1.05 | 4.475 | 4.475 | 0 | 12 | 1 | 1 | 4.475 | 10 | 0 | 0
1431.7 | 49.68 | 49.68 | 1 | 1 | 10 | 49.96 | 0.014706 | -0.005 | -0.05 | 4.975 | 4.975 | 0 | 12 | 1 | 1 | 4.975 | 10 | 0 | 0
1431.75 | 49.65 | 49.65 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
1431.8 | 49.63 | 49.63 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1431.85 | 49.6 | 49.6 | 1 | 1 | 10 | 49.88 | 0.24 | 0.14412 | 1.4412 | 5.7206 | 5.7206 | 0 | 12 | 1 | 1 | 5.7206 | 10 | 0 | 0
1431.9 | 49.58 | 49.58 | 1 | 1 | 10 | 49.86 | 0.43 | 0.24412 | 2.4412 | 6.2206 | 6.2206 | 0 | 12 | 1 | 1 | 6.2206 | 10 | 0 | 0
1431.95 | 49.55 | 49.55 | 1 | 1 | 10 | 49.83 | 0.715 | 0.34412 | 3.4412 | 6.7206 | 6.7206 | 0 | 12 | 1 | 1 | 6.7206 | 10 | 0 | 0
1432 | 49.53 | 49.53 | 1 | 1 | 10 | 49.81 | 0.905 | 0.44412 | 4.4412 | 7.2206 | 7.2206 | 0 | 12 | 1 | 1 | 7.2206 | 10 | 0 | 0
1432.05 | 49.5 | 49.5 | 1 | 1 | 10 | 49.78 | 1 | 0.54412 | 5.4412 | 7.7206 | 7.7206 | 0 | 12 | 1 | 1 | 7.7206 | 10 | 0 | 0
1432.1 | 49.5 | 49.5 | 1 | 1 | 10 | 49.76 | 1 | 0.64412 | 6.4412 | 8.2206 | 8.2206 | 0 | 12 | 1 | 1 | 8.2206 | 10 | 0 | 0
1432.15 | 49.53 | 49.5 | 1 | 1 | 10 | 49.73 | 1 | 0.74412 | 7.4412 | 8.7206 | 8.7206 | 0 | 12 | 1 | 1 | 8.7206 | 10 | 0 | 0
1432.2 | 49.55 | 49.5 | 1 | 1 | 10 | 49.71 | 1 | 0.84412 | 8.4412 | 9.2206 | 9.2206 | 0 | 12 | 1 | 1 | 9.2206 | 10 | 0 | 0
1432.25 | 49.58 | 49.5 | 1 | 1 | 10 | 49.68 | 1 | 0.94412 | 9.4412 | 9.7206 | 9.7206 | 0 | 12 | 1 | 1 | 9.7206 | 10 | 0 | 0
1432.3 | 49.6 | 49.5 | 1 | 1 | 10 | 49.65 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1432.35 | 49.63 | 49.5 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1432.4 | 49.65 | 49.5 | 1 | 1 | 10 | 49.65 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1432.45 | 49.68 | 49.5 | 1 | 1 | 10 | 49.68 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1432.5 | 49.71 | 49.5 | 1 | 1 | 10 | 49.71 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1432.55 | 49.73 | 49.5 | 1 | 1 | 10 | 49.73 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1432.6 | 49.76 | 49.5 | 1 | 1 | 10 | 49.76 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1432.65 | 49.78 | 49.5 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1432.7 | 49.81 | 49.53 | 1 | 1 | 10 | 49.81 | 0.905 | 0.905 | 9.05 | 9.525 | 9.525 | 0 | 12 | 1 | 1 | 9.525 | 10 | 0 | 0
1432.75 | 49.83 | 49.55 | 1 | 1 | 10 | 49.83 | 0.715 | 0.715 | 7.15 | 8.575 | 8.575 | 0 | 12 | 1 | 1 | 8.575 | 10 | 0 | 0
1432.8 | 49.86 | 49.58 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
1432.85 | 49.88 | 49.6 | 1 | 1 | 10 | 49.88 | 0.24 | 0.24 | 2.4 | 6.2 | 6.2 | 0 | 12 | 1 | 1 | 6.2 | 10 | 0 | 0
1432.9 | 49.91 | 49.63 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1432.95 | 49.94 | 49.65 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
1433 | 49.96 | 49.68 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
1433.05 | 49.99 | 49.71 | 1 | 1 | 10 | 49.99 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1433.1 | 50.01 | 49.73 | 1 | 1 | 10 | 50.01 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1433.15 | 50.04 | 49.76 | 1 | 1 | 10 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 4.9265 | 4.9265 | 0 | 12 | 1 | 1 | 4.9265 | 10 | 0 | 0
1433.2 | 50.06 | 49.78 | 1 | 1 | 10 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 4.8676 | 4.8676 | 0 | 12 | 1 | 1 | 4.8676 | 10 | 0 | 0
1433.25 | 50.09 | 49.81 | 0.905 | 0.905 | 9.05 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 4.3044 | 4.3044 | 0 | 12 | 1 | 1 | 4.3044 | 10 | 0 | 0
1433.3 | 50.12 | 49.83 | 0.715 | 0.805 | 8.05 | 50.12 | -0.24 | -0.24 | -2.4 | 2.825 | 2.825 | 0 | 12 | 1 | 1 | 2.825 | 10 | 0 | 0
1433.35 | 50.14 | 49.86 | 0.43 | 0.705 | 7.05 | 50.14 | -0.43 | -0.43 | -4.3 | 1.375 | 1.375 | 0 | 12 | 1 | 1 | 1.375 | 10 | 0 | 0
1433.4 | 50.17 | 49.88 | 0.24 | 0.605 | 6.05 | 50.17 | -0.715 | -0.715 | -7.15 | -0.55 | -0.55 | 0 | 12 | 1 | 1 | -0.55 | 10 | 0 | 0
1433.45 | 50.19 | 49.91 | 0.044118 | 0.505 | 5.05 | 50.19 | -0.905 | -0.905 | -9.05 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
1433.5 | 50.22 | 49.94 | 0.026471 | 0.405 | 4.05 | 50.22 | -1 | -1 | -10 | -2.975 | -2.975 | 0 | 12 | 1 | 1 | -2.975 | 10 | 0 | 0
1433.55 | 50.24 | 49.96 | 0.014706 | 0.305 | 3.05 | 50.24 | -1 | -1 | -10 | -3.475 | -3.475 | 0 | 12 | 1 | 1 | -3.475 | 10 | 0 | 0
1433.6 | 50.27 | 49.99 | 0 | 0.205 | 2.05 | 50.27 | -1 | -1 | -10 | -3.975 | -3.975 | 0 | 12 | 1 | 1 | -3.975 | 10 | 0 | 0
1433.65 | 50.29 | 50.01 | 0 | 0.105 | 1.05 | 50.29 | -1 | -1 | -10 | -4.475 | -4.475 | 0 | 12 | 1 | 1 | -4.475 | 10 | 0 | 0
1433.7 | 50.32 | 50.04 | -0.014706 | 0.005 | 0.05 | 50.32 | -1 | -1 | -10 | -4.975 | -4.975 | 0 | 12 | 1 | 1 | -4.975 | 10 | 0 | 0
1433.75 | 50.35 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.35 | -1 | -1 | -10 | -5.1324 | -5.1324 | 0 | 12 | 1 | 1 | -5.1324 | 10 | 0 | 0
1433.8 | 50.37 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 50.37 | -1 | -1 | -10 | -5.2206 | -5.2206 | 0 | 12 | 1 | 1 | -5.2206 | 10 | 0 | 0
1433.85 | 50.4 | 50.12 | -0.24 | -0.14412 | -1.4412 | 50.4 | -1 | -1 | -10 | -5.7206 | -5.7206 | 0 | 12 | 1 | 1 | -5.7206 | 10 | 0 | 0
1433.9 | 50.42 | 50.14 | -0.43 | -0.24412 | -2.4412 | 50.42 | -1 | -1 | -10 | -6.2206 | -6.2206 | 0 | 12 | 1 | 1 | -6.2206 | 10 | 0 | 0
1433.95 | 50.45 | 50.17 | -0.715 | -0.34412 | -3.4412 | 50.45 | -1 | -1 | -10 | -6.7206 | -6.7206 | 0 | 12 | 1 | 1 | -6.7206 | 10 | 0 | 0
1434 | 50.47 | 50.19 | -0.905 | -0.44412 | -4.4412 | 50.47 | -1 | -1 | -10 | -7.2206 | -7.2206 | 0 | 12 | 1 | 1 | -7.2206 | 10 | 0 | 0
1434.05 | 50.5 | 50.22 | -1 | -0.54412 | -5.4412 | 50.5 | -1 | -1 | -10 | -7.7206 | -7.7206 | 0 | 12 | 1 | 1 | -7.7206 | 10 | 0 | 0
1434.1 | 50.5 | 50.24 | -1 | -0.64412 | -6.4412 | 50.5 | -1 | -1 | -10 | -8.2206 | -8.2206 | 0 | 12 | 1 | 1 | -8.2206 | 10 | 0 | 0
1434.15 | 50.47 | 50.27 | -1 | -0.74412 | -7.4412 | 50.5 | -1 | -1 | -10 | -8.7206 | -8.7206 | 0 | 12 | 1 | 1 | -8.7206 | 10 | 0 | 0
1434.2 | 50.45 | 50.29 | -1 | -0.84412 | -8.4412 | 50.5 | -1 | -1 | -10 | -9.2206 | -9.2206 | 0 | 12 | 1 | 1 | -9.2206 | 10 | 0 | 0
1434.25 | 50.42 | 50.32 | -1 | -0.94412 | -9.4412 | 50.5 | -1 | -1 | -10 | -9.7206 | -9.7206 | 0 | 12 | 1 | 1 | -9.7206 | 10 | 0 | 0
1434.3 | 50.39 | 50.35 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1434.35 | 50.37 | 50.37 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1434.4 | 50.34 | 50.34 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1434.45 | 50.32 | 50.32 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1434.5 | 50.29 | 50.29 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1434.55 | 50.26 | 50.26 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1434.6 | 50.24 | 50.24 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1434.65 | 50.21 | 50.21 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1434.7 | 50.18 | 50.18 | -0.81 | -0.81 | -8.1 | 50.47 | -1 | -1 | -10 | -9.05 | -9.05 | 0 | 12 | 1 | 1 | -9.05 | 10 | 0 | 0
1434.75 | 50.16 | 50.16 | -0.62 | -0.62 | -6.2 | 50.45 | -1 | -1 | -10 | -8.1 | -8.1 | 0 | 12 | 1 | 1 | -8.1 | 10 | 0 | 0
1434.8 | 50.13 | 50.13 | -0.335 | -0.335 | -3.35 | 50.42 | -1 | -1 | -10 | -6.675 | -6.675 | 0 | 12 | 1 | 1 | -6.675 | 10 | 0 | 0
1434.85 | 50.11 | 50.11 | -0.145 | -0.145 | -1.45 | 50.39 | -1 | -1 | -10 | -5.725 | -5.725 | 0 | 12 | 1 | 1 | -5.725 | 10 | 0 | 0
1434.9 | 50.08 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 50.37 | -1 | -1 | -10 | -5.1912 | -5.1912 | 0 | 12 | 1 | 1 | -5.1912 | 10 | 0 | 0
1434.95 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.34 | -1 | -1 | -10 | -5.1029 | -5.1029 | 0 | 12 | 1 | 1 | -5.1029 | 10 | 0 | 0
1435 | 50.03 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 50.32 | -1 | -1 | -10 | -5.0441 | -5.0441 | 0 | 12 | 1 | 1 | -5.0441 | 10 | 0 | 0
1435.05 | 50 | 50 | 0 | 0 | 0 | 50.29 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1435.1 | 50 | 50 | 0 | 0 | 0 | 50.26 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1435.15 | 50 | 50 | 0 | 0 | 0 | 50.24 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1435.2 | 50 | 50 | 0 | 0 | 0 | 50.21 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1435.25 | 50 | 50 | 0 | 0 | 0 | 50.18 | -0.81 | -0.9 | -9 | -4.5 | -4.5 | 0 | 12 | 1 | 1 | -4.5 | 10 | 0 | 0
1435.3 | 50 | 50 | 0 | 0 | 0 | 50.16 | -0.62 | -0.8 | -8 | -4 | -4 | 0 | 12 | 1 | 1 | -4 | 10 | 0 | 0
1435.35 | 50 | 50 | 0 | 0 | 0 | 50.13 | -0.335 | -0.7 | -7 | -3.5 | -3.5 | 0 | 12 | 1 | 1 | -3.5 | 10 | 0 | 0
1435.4 | 50.01 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.6 | -6 | -3 | -3 | 0 | 12 | 1 | 1 | -3 | 10 | 0 | 0
1435.45 | 50.01 | 50 | 0 | 0 | 0 | 50.08 | -0.038235 | -0.5 | -5 | -2.5 | -2.5 | 0 | 12 | 1 | 1 | -2.5 | 10 | 0 | 0
1435.5 | 49.99 | 49.99 | 0 | 0 | 0 | 50.05 | -0.020588 | -0.4 | -4 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
1435.55 | 49.99 | 49.99 | 0 | 0 | 0 | 50.03 | -0.0088235 | -0.3 | -3 | -1.5 | -1.5 | 0 | 12 | 1 | 1 | -1.5 | 10 | 0 | 0
1435.6 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | -0.2 | -2 | -0.83824 | -0.83824 | 0 | 12 | 1 | 1 | -0.83824 | 10 | 0 | 0
1435.65 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | -0.1 | -1 | -0.33824 | -0.33824 | 0 | 12 | 1 | 1 | -0.33824 | 10 | 0 | 0
1435.7 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
1435.75 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
1435.8 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
1435.85 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
1435.9 | 49.89 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
1435.95 | 49.89 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
1436 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50.01 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1436.05 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1436.1 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1436.15 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 2.7868 | 2.7868 | 0 | 12 | 1 | 1 | 2.7868 | 10 | 0 | 0
1436.2 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 2.7868 | 2.7868 | 0 | 12 | 1 | 1 | 2.7868 | 10 | 0 | 0
1436.25 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 2.8456 | 2.8456 | 0 | 12 | 1 | 1 | 2.8456 | 10 | 0 | 0
1436.3 | 49.94 | 49.85 | 0.525 | 0.525 | 5.25 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 2.7574 | 2.7574 | 0 | 12 | 1 | 1 | 2.7574 | 10 | 0 | 0
1436.35 | 49.94 | 49.85 | 0.525 | 0.525 | 5.25 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 2.7574 | 2.7574 | 0 | 12 | 1 | 1 | 2.7574 | 10 | 0 | 0
1436.4 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1436.45 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1436.5 | 49.93 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1436.55 | 49.93 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1436.6 | 49.96 | 49.85 | 0.525 | 0.525 | 5.25 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 2.6985 | 2.6985 | 0 | 12 | 1 | 1 | 2.6985 | 10 | 0 | 0
1436.65 | 49.96 | 49.85 | 0.525 | 0.525 | 5.25 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 2.6985 | 2.6985 | 0 | 12 | 1 | 1 | 2.6985 | 10 | 0 | 0
1436.7 | 49.99 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1436.75 | 49.99 | 49.91 | 0.044118 | 0.425 | 4.25 | 49.99 | 0 | 0 | 0 | 2.125 | 2.125 | 0 | 12 | 1 | 1 | 2.125 | 10 | 0 | 0
1436.8 | 49.99 | 49.91 | 0.044118 | 0.325 | 3.25 | 49.99 | 0 | 0 | 0 | 1.625 | 1.625 | 0 | 12 | 1 | 1 | 1.625 | 10 | 0 | 0
1436.85 | 49.99 | 49.93 | 0.032353 | 0.225 | 2.25 | 49.99 | 0 | 0 | 0 | 1.125 | 1.125 | 0 | 12 | 1 | 1 | 1.125 | 10 | 0 | 0
1436.9 | 49.96 | 49.93 | 0.032353 | 0.125 | 1.25 | 49.99 | 0 | 0 | 0 | 0.625 | 0.625 | 0 | 12 | 1 | 1 | 0.625 | 10 | 0 | 0
1436.95 | 49.96 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 49.99 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1437 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1437.05 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1437.1 | 50.05 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.058824 | 0.058824 | 0 | 12 | 1 | 1 | 0.058824 | 10 | 0 | 0
1437.15 | 50.05 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
1437.2 | 49.97 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
1437.25 | 49.97 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
1437.3 | 49.92 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1437.35 | 49.92 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1437.4 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1437.45 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1437.5 | 49.94 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1437.55 | 49.94 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1437.6 | 50.01 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1437.65 | 50.01 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1437.7 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1437.75 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
1437.8 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
1437.85 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
1437.9 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
1437.95 | 49.95 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
1438 | 49.97 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
1438.05 | 49.97 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
1438.1 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
1438.15 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
1438.2 | 49.87 | 49.87 | 0.335 | 0.335 | 3.35 | 50.01 | 0 | 0 | 0 | 1.675 | 1.675 | 0 | 12 | 1 | 1 | 1.675 | 10 | 0 | 0
1438.25 | 49.87 | 49.87 | 0.335 | 0.335 | 3.35 | 49.99 | 0 | 0 | 0 | 1.675 | 1.675 | 0 | 12 | 1 | 1 | 1.675 | 10 | 0 | 0
1438.3 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1438.35 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 2.6691 | 2.6691 | 0 | 12 | 1 | 1 | 2.6691 | 10 | 0 | 0
1438.4 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1438.45 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1438.5 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1438.55 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1438.6 | 49.84 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1438.65 | 49.84 | 49.79 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
1438.7 | 49.89 | 49.79 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
1438.75 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.12647 | 1.2647 | 5.6324 | 5.6324 | 0 | 12 | 1 | 1 | 5.6324 | 10 | 0 | 0
1438.8 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.145 | 1.45 | 5.725 | 5.725 | 0 | 12 | 1 | 1 | 5.725 | 10 | 0 | 0
1438.85 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.145 | 1.45 | 5.725 | 5.725 | 0 | 12 | 1 | 1 | 5.725 | 10 | 0 | 0
1438.9 | 49.96 | 49.79 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
1438.95 | 49.96 | 49.79 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
1439 | 50.02 | 49.79 | 1 | 1 | 10 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 4.9853 | 4.9853 | 0 | 12 | 1 | 1 | 4.9853 | 10 | 0 | 0
1439.05 | 50.02 | 49.79 | 1 | 1 | 10 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 4.9853 | 4.9853 | 0 | 12 | 1 | 1 | 4.9853 | 10 | 0 | 0
1439.1 | 50.03 | 49.79 | 1 | 1 | 10 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.9559 | 4.9559 | 0 | 12 | 1 | 1 | 4.9559 | 10 | 0 | 0
1439.15 | 50.03 | 49.84 | 0.62 | 0.9 | 9 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.4559 | 4.4559 | 0 | 12 | 1 | 1 | 4.4559 | 10 | 0 | 0
1439.2 | 50.02 | 49.84 | 0.62 | 0.8 | 8 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 3.9559 | 3.9559 | 0 | 12 | 1 | 1 | 3.9559 | 10 | 0 | 0
1439.25 | 50.02 | 49.89 | 0.145 | 0.7 | 7 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 3.4559 | 3.4559 | 0 | 12 | 1 | 1 | 3.4559 | 10 | 0 | 0
1439.3 | 50.08 | 49.89 | 0.145 | 0.6 | 6 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 2.8088 | 2.8088 | 0 | 12 | 1 | 1 | 2.8088 | 10 | 0 | 0
1439.35 | 50.08 | 49.89 | 0.145 | 0.5 | 5 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 2.3088 | 2.3088 | 0 | 12 | 1 | 1 | 2.3088 | 10 | 0 | 0
1439.4 | 50.01 | 49.89 | 0.145 | 0.4 | 4 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 1.8088 | 1.8088 | 0 | 12 | 1 | 1 | 1.8088 | 10 | 0 | 0
1439.45 | 50.01 | 49.96 | 0.014706 | 0.3 | 3 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 1.3088 | 1.3088 | 0 | 12 | 1 | 1 | 1.3088 | 10 | 0 | 0
1439.5 | 49.94 | 49.94 | 0.026471 | 0.2 | 2 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.80882 | 0.80882 | 0 | 12 | 1 | 1 | 0.80882 | 10 | 0 | 0
1439.55 | 49.94 | 49.94 | 0.026471 | 0.1 | 1 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.30882 | 0.30882 | 0 | 12 | 1 | 1 | 0.30882 | 10 | 0 | 0
1439.6 | 50 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
1439.65 | 50 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
1439.7 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
1439.75 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
1439.8 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1439.85 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1439.9 | 49.92 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1439.95 | 49.92 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
1440 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50.01 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1440.05 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1440.1 | 49.92 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1440.15 | 49.92 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1440.2 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1440.25 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1440.3 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1440.35 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1440.4 | 49.87 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1440.45 | 49.87 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1440.5 | 49.8 | 49.8 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1440.55 | 49.8 | 49.8 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1440.6 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1440.65 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1440.7 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1440.75 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1440.8 | 49.72 | 49.72 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1440.85 | 49.72 | 49.72 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1440.9 | 49.67 | 49.67 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1440.95 | 49.67 | 49.67 | 1 | 1 | 10 | 49.87 | 0.335 | 0.14412 | 1.4412 | 5.7206 | 5.7206 | 0 | 12 | 1 | 1 | 5.7206 | 10 | 0 | 0
1441 | 49.65 | 49.65 | 1 | 1 | 10 | 49.87 | 0.335 | 0.24412 | 2.4412 | 6.2206 | 6.2206 | 0 | 12 | 1 | 1 | 6.2206 | 10 | 0 | 0
1441.05 | 49.65 | 49.65 | 1 | 1 | 10 | 49.8 | 1 | 0.34412 | 3.4412 | 6.7206 | 6.7206 | 0 | 12 | 1 | 1 | 6.7206 | 10 | 0 | 0
1441.1 | 49.59 | 49.59 | 1 | 1 | 10 | 49.8 | 1 | 0.44412 | 4.4412 | 7.2206 | 7.2206 | 0 | 12 | 1 | 1 | 7.2206 | 10 | 0 | 0
1441.15 | 49.59 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.54412 | 5.4412 | 7.7206 | 7.7206 | 0 | 12 | 1 | 1 | 7.7206 | 10 | 0 | 0
1441.2 | 49.66 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.64412 | 6.4412 | 8.2206 | 8.2206 | 0 | 12 | 1 | 1 | 8.2206 | 10 | 0 | 0
1441.25 | 49.66 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.74412 | 7.4412 | 8.7206 | 8.7206 | 0 | 12 | 1 | 1 | 8.7206 | 10 | 0 | 0
1441.3 | 49.63 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.84412 | 8.4412 | 9.2206 | 9.2206 | 0 | 12 | 1 | 1 | 9.2206 | 10 | 0 | 0
1441.35 | 49.63 | 49.59 | 1 | 1 | 10 | 49.72 | 1 | 0.94412 | 9.4412 | 9.7206 | 9.7206 | 0 | 12 | 1 | 1 | 9.7206 | 10 | 0 | 0
1441.4 | 49.61 | 49.59 | 1 | 1 | 10 | 49.72 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1441.45 | 49.61 | 49.59 | 1 | 1 | 10 | 49.67 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1441.5 | 49.54 | 49.54 | 1 | 1 | 10 | 49.67 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1441.55 | 49.54 | 49.54 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1441.6 | 49.46 | 49.46 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1441.65 | 49.46 | 49.46 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1441.7 | 49.45 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1441.75 | 49.45 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1441.8 | 49.51 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1441.85 | 49.51 | 49.45 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1441.9 | 49.5 | 49.45 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1441.95 | 49.5 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1442 | 49.54 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1442.05 | 49.54 | 49.45 | 1 | 1 | 10 | 49.54 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1442.1 | 49.59 | 49.45 | 1 | 1 | 10 | 49.59 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1442.15 | 49.59 | 49.45 | 1 | 1 | 10 | 49.59 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1442.2 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1442.25 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1442.3 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1442.35 | 49.61 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1442.4 | 49.53 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1442.45 | 49.53 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1442.5 | 49.54 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1442.55 | 49.54 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1442.6 | 49.61 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1442.65 | 49.61 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1442.7 | 49.66 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1442.75 | 49.66 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1442.8 | 49.64 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1442.85 | 49.64 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1442.9 | 49.69 | 49.53 | 1 | 1 | 10 | 49.69 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1442.95 | 49.69 | 49.53 | 1 | 1 | 10 | 49.69 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1443 | 49.74 | 49.53 | 1 | 1 | 10 | 49.74 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1443.05 | 49.74 | 49.54 | 1 | 1 | 10 | 49.74 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1443.1 | 49.78 | 49.54 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1443.15 | 49.78 | 49.61 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1443.2 | 49.82 | 49.61 | 1 | 1 | 10 | 49.82 | 0.81 | 0.81 | 8.1 | 9.05 | 9.05 | 0 | 12 | 1 | 1 | 9.05 | 10 | 0 | 0
1443.25 | 49.82 | 49.64 | 1 | 1 | 10 | 49.82 | 0.81 | 0.81 | 8.1 | 9.05 | 9.05 | 0 | 12 | 1 | 1 | 9.05 | 10 | 0 | 0
1443.3 | 49.86 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
1443.35 | 49.86 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
1443.4 | 49.84 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
1443.45 | 49.84 | 49.69 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
1443.5 | 49.91 | 49.69 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1443.55 | 49.91 | 49.74 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1443.6 | 49.97 | 49.74 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1443.65 | 49.97 | 49.78 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1443.7 | 50.03 | 49.78 | 1 | 1 | 10 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.9559 | 4.9559 | 0 | 12 | 1 | 1 | 4.9559 | 10 | 0 | 0
1443.75 | 50.03 | 49.82 | 0.81 | 0.9 | 9 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.4559 | 4.4559 | 0 | 12 | 1 | 1 | 4.4559 | 10 | 0 | 0
1443.8 | 50.05 | 49.82 | 0.81 | 0.81 | 8.1 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 3.9471 | 3.9471 | 0 | 12 | 1 | 1 | 3.9471 | 10 | 0 | 0
1443.85 | 50.05 | 49.84 | 0.62 | 0.71 | 7.1 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 3.4471 | 3.4471 | 0 | 12 | 1 | 1 | 3.4471 | 10 | 0 | 0
1443.9 | 50.01 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
1443.95 | 50.01 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
1444 | 49.95 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
1444.05 | 49.95 | 49.91 | 0.044118 | 0.52 | 5.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.4971 | 2.4971 | 0 | 12 | 1 | 1 | 2.4971 | 10 | 0 | 0
1444.1 | 49.99 | 49.91 | 0.044118 | 0.42 | 4.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 1.9971 | 1.9971 | 0 | 12 | 1 | 1 | 1.9971 | 10 | 0 | 0
1444.15 | 49.99 | 49.95 | 0.020588 | 0.32 | 3.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 1.4971 | 1.4971 | 0 | 12 | 1 | 1 | 1.4971 | 10 | 0 | 0
1444.2 | 49.92 | 49.92 | 0.038235 | 0.22 | 2.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.99706 | 0.99706 | 0 | 12 | 1 | 1 | 0.99706 | 10 | 0 | 0
1444.25 | 49.92 | 49.92 | 0.038235 | 0.12 | 1.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.49706 | 0.49706 | 0 | 12 | 1 | 1 | 0.49706 | 10 | 0 | 0
1444.3 | 49.97 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1444.35 | 49.97 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1444.4 | 50.02 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1444.45 | 50.02 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.17647 | 0.17647 | 0 | 12 | 1 | 1 | 0.17647 | 10 | 0 | 0
1444.5 | 50.07 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1444.55 | 50.07 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1444.6 | 50.06 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1444.65 | 50.06 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1444.7 | 50.13 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
1444.75 | 50.13 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
1444.8 | 50.09 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
1444.85 | 50.09 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6309 | -1.6309 | 0 | 12 | 1 | 1 | -1.6309 | 10 | 0 | 0
1444.9 | 50.07 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6309 | -1.6309 | 0 | 12 | 1 | 1 | -1.6309 | 10 | 0 | 0
1444.95 | 50.07 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6897 | -1.6897 | 0 | 12 | 1 | 1 | -1.6897 | 10 | 0 | 0
1445 | 50.07 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6897 | -1.6897 | 0 | 12 | 1 | 1 | -1.6897 | 10 | 0 | 0
1445.05 | 50.07 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.13 | -0.335 | -0.335 | -3.35 | -1.8074 | -1.8074 | 0 | 12 | 1 | 1 | -1.8074 | 10 | 0 | 0
1445.1 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.13 | -0.335 | -0.335 | -3.35 | -1.7779 | -1.7779 | 0 | 12 | 1 | 1 | -1.7779 | 10 | 0 | 0
1445.15 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.13 | -0.335 | -0.335 | -3.35 | -1.7779 | -1.7779 | 0 | 12 | 1 | 1 | -1.7779 | 10 | 0 | 0
1445.2 | 50.01 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
1445.25 | 50.01 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
1445.3 | 50.07 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
1445.35 | 50.07 | 50.01 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.235 | -2.35 | -1.175 | -1.175 | 0 | 12 | 1 | 1 | -1.175 | 10 | 0 | 0
1445.4 | 50.05 | 50.01 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.135 | -1.35 | -0.675 | -0.675 | 0 | 12 | 1 | 1 | -0.675 | 10 | 0 | 0
1445.45 | 50.05 | 50.01 | 0 | 0 | 0 | 50.07 | -0.032353 | -0.035 | -0.35 | -0.175 | -0.175 | 0 | 12 | 1 | 1 | -0.175 | 10 | 0 | 0
1445.5 | 50.1 | 50.01 | 0 | 0 | 0 | 50.1 | -0.05 | -0.05 | -0.5 | -0.25 | -0.25 | 0 | 12 | 1 | 1 | -0.25 | 10 | 0 | 0
1445.55 | 50.1 | 50.01 | 0 | 0 | 0 | 50.1 | -0.05 | -0.05 | -0.5 | -0.25 | -0.25 | 0 | 12 | 1 | 1 | -0.25 | 10 | 0 | 0
1445.6 | 50.11 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1445.65 | 50.11 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1445.7 | 50.06 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1445.75 | 50.06 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1445.8 | 50.04 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1445.85 | 50.04 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1445.9 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1445.95 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1446 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1446.05 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1446.1 | 50.11 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1446.15 | 50.11 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1446.2 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1446.25 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1446.3 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1446.35 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1446.4 | 50.02 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.11 | -0.145 | -0.145 | -1.45 | -0.73971 | -0.73971 | 0 | 12 | 1 | 1 | -0.73971 | 10 | 0 | 0
1446.45 | 50.02 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.11 | -0.145 | -0.145 | -1.45 | -0.73971 | -0.73971 | 0 | 12 | 1 | 1 | -0.73971 | 10 | 0 | 0
1446.5 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1446.55 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1446.6 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1446.65 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1446.7 | 50.01 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1446.75 | 50.01 | 50 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.045 | -0.45 | -0.225 | -0.225 | 0 | 12 | 1 | 1 | -0.225 | 10 | 0 | 0
1446.8 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
1446.85 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
1446.9 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
1446.95 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1447 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.14706 | 0.14706 | 0 | 12 | 1 | 1 | 0.14706 | 10 | 0 | 0
1447.05 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1447.1 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1447.15 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1447.2 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1447.25 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1447.3 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1447.35 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1447.4 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1447.45 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1447.5 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1447.55 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1447.6 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1447.65 | 50 | 50 | 0 | 0 | 0 | 50.01 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1447.7 | 49.5 | 49.5 | 1 | 1 | 10 | 50.01 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1447.75 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1447.8 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1447.85 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1447.9 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1447.95 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1448 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1448.05 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1448.1 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1448.15 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1448.2 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1448.25 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.1 | 1 | 5.5 | 5.5 | 0 | 12 | 1 | 1 | 5.5 | 10 | 0 | 0
1448.3 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.2 | 2 | 6 | 6 | 0 | 12 | 1 | 1 | 6 | 10 | 0 | 0
1448.35 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.3 | 3 | 6.5 | 6.5 | 0 | 12 | 1 | 1 | 6.5 | 10 | 0 | 0
1448.4 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.4 | 4 | 7 | 7 | 0 | 12 | 1 | 1 | 7 | 10 | 0 | 0
1448.45 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.5 | 5 | 7.5 | 7.5 | 0 | 12 | 1 | 1 | 7.5 | 10 | 0 | 0
1448.5 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.6 | 6 | 8 | 8 | 0 | 12 | 1 | 1 | 8 | 10 | 0 | 0
1448.55 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.7 | 7 | 8.5 | 8.5 | 0 | 12 | 1 | 1 | 8.5 | 10 | 0 | 0
1448.6 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.8 | 8 | 9 | 9 | 0 | 12 | 1 | 1 | 9 | 10 | 0 | 0
1448.65 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.9 | 9 | 9.5 | 9.5 | 0 | 12 | 1 | 1 | 9.5 | 10 | 0 | 0
1448.7 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1448.75 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1448.8 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1448.85 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1448.9 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1448.95 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1449 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1449.05 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1449.1 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1449.15 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1449.2 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1449.25 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1449.3 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1449.35 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1449.4 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1449.45 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1449.5 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1449.55 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1449.6 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1449.65 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1449.7 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1449.75 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1449.8 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1449.85 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1449.9 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1449.95 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1450 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1450.05 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1450.1 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1450.15 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1450.2 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1450.25 | 50.5 | 50.5 | -1 | 0.9 | 9 | 50.5 | -1 | -1 | -10 | -0.5 | -0.5 | 0 | 12 | 1 | 1 | -0.5 | 10 | 0 | 0
1450.3 | 50.5 | 50.5 | -1 | 0.8 | 8 | 50.5 | -1 | -1 | -10 | -1 | -1 | 0 | 12 | 1 | 1 | -1 | 10 | 0 | 0
1450.35 | 50.5 | 50.5 | -1 | 0.7 | 7 | 50.5 | -1 | -1 | -10 | -1.5 | -1.5 | 0 | 12 | 1 | 1 | -1.5 | 10 | 0 | 0
1450.4 | 50.5 | 50.5 | -1 | 0.6 | 6 | 50.5 | -1 | -1 | -10 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
1450.45 | 50.5 | 50.5 | -1 | 0.5 | 5 | 50.5 | -1 | -1 | -10 | -2.5 | -2.5 | 0 | 12 | 1 | 1 | -2.5 | 10 | 0 | 0
1450.5 | 50.5 | 50.5 | -1 | 0.4 | 4 | 50.5 | -1 | -1 | -10 | -3 | -3 | 0 | 12 | 1 | 1 | -3 | 10 | 0 | 0
1450.55 | 50.5 | 50.5 | -1 | 0.3 | 3 | 50.5 | -1 | -1 | -10 | -3.5 | -3.5 | 0 | 12 | 1 | 1 | -3.5 | 10 | 0 | 0
1450.6 | 50.5 | 50.5 | -1 | 0.2 | 2 | 50.5 | -1 | -1 | -10 | -4 | -4 | 0 | 12 | 1 | 1 | -4 | 10 | 0 | 0
1450.65 | 50.5 | 50.5 | -1 | 0.1 | 1 | 50.5 | -1 | -1 | -10 | -4.5 | -4.5 | 0 | 12 | 1 | 1 | -4.5 | 10 | 0 | 0
1450.7 | 50.5 | 50.5 | -1 | 0 | 0 | 50.5 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1450.75 | 50.5 | 50.5 | -1 | -0.1 | -1 | 50.5 | -1 | -1 | -10 | -5.5 | -5.5 | 0 | 12 | 1 | 1 | -5.5 | 10 | 0 | 0
1450.8 | 50.5 | 50.5 | -1 | -0.2 | -2 | 50.5 | -1 | -1 | -10 | -6 | -6 | 0 | 12 | 1 | 1 | -6 | 10 | 0 | 0
1450.85 | 50.5 | 50.5 | -1 | -0.3 | -3 | 50.5 | -1 | -1 | -10 | -6.5 | -6.5 | 0 | 12 | 1 | 1 | -6.5 | 10 | 0 | 0
1450.9 | 50.5 | 50.5 | -1 | -0.4 | -4 | 50.5 | -1 | -1 | -10 | -7 | -7 | 0 | 12 | 1 | 1 | -7 | 10 | 0 | 0
1450.95 | 50.5 | 50.5 | -1 | -0.5 | -5 | 50.5 | -1 | -1 | -10 | -7.5 | -7.5 | 0 | 12 | 1 | 1 | -7.5 | 10 | 0 | 0
1451 | 50.5 | 50.5 | -1 | -0.6 | -6 | 50.5 | -1 | -1 | -10 | -8 | -8 | 0 | 12 | 1 | 1 | -8 | 10 | 0 | 0
1451.05 | 50.5 | 50.5 | -1 | -0.7 | -7 | 50.5 | -1 | -1 | -10 | -8.5 | -8.5 | 0 | 12 | 1 | 1 | -8.5 | 10 | 0 | 0
1451.1 | 50.5 | 50.5 | -1 | -0.8 | -8 | 50.5 | -1 | -1 | -10 | -9 | -9 | 0 | 12 | 1 | 1 | -9 | 10 | 0 | 0
1451.15 | 50.5 | 50.5 | -1 | -0.9 | -9 | 50.5 | -1 | -1 | -10 | -9.5 | -9.5 | 0 | 12 | 1 | 1 | -9.5 | 10 | 0 | 0
1451.2 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1451.25 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1451.3 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1451.35 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1451.4 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1451.45 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1451.5 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1451.55 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1451.6 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1451.65 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1451.7 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1451.75 | 50.47 | 50.47 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1451.8 | 50.45 | 50.45 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1451.85 | 50.42 | 50.42 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1451.9 | 50.4 | 50.4 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1451.95 | 50.37 | 50.37 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1452 | 50.35 | 50.35 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1452.05 | 50.32 | 50.32 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1452.1 | 50.29 | 50.29 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1452.15 | 50.27 | 50.27 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1452.2 | 50.24 | 50.24 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1452.25 | 50.22 | 50.22 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1452.3 | 50.19 | 50.19 | -0.905 | -0.905 | -9.05 | 50.47 | -1 | -1 | -10 | -9.525 | -9.525 | 0 | 12 | 1 | 1 | -9.525 | 10 | 0 | 0
1452.35 | 50.17 | 50.17 | -0.715 | -0.715 | -7.15 | 50.45 | -1 | -1 | -10 | -8.575 | -8.575 | 0 | 12 | 1 | 1 | -8.575 | 10 | 0 | 0
1452.4 | 50.14 | 50.14 | -0.43 | -0.43 | -4.3 | 50.42 | -1 | -1 | -10 | -7.15 | -7.15 | 0 | 12 | 1 | 1 | -7.15 | 10 | 0 | 0
1452.45 | 50.12 | 50.12 | -0.24 | -0.24 | -2.4 | 50.4 | -1 | -1 | -10 | -6.2 | -6.2 | 0 | 12 | 1 | 1 | -6.2 | 10 | 0 | 0
1452.5 | 50.09 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 50.37 | -1 | -1 | -10 | -5.2206 | -5.2206 | 0 | 12 | 1 | 1 | -5.2206 | 10 | 0 | 0
1452.55 | 50.06 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.35 | -1 | -1 | -10 | -5.1324 | -5.1324 | 0 | 12 | 1 | 1 | -5.1324 | 10 | 0 | 0
1452.6 | 50.04 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.32 | -1 | -1 | -10 | -5.0735 | -5.0735 | 0 | 12 | 1 | 1 | -5.0735 | 10 | 0 | 0
1452.65 | 50.01 | 50.01 | 0 | 0 | 0 | 50.29 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1452.7 | 49.99 | 49.99 | 0 | 0 | 0 | 50.27 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1452.75 | 49.96 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.24 | -1 | -1 | -10 | -4.9265 | -4.9265 | 0 | 12 | 1 | 1 | -4.9265 | 10 | 0 | 0
1452.8 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.22 | -1 | -1 | -10 | -4.8676 | -4.8676 | 0 | 12 | 1 | 1 | -4.8676 | 10 | 0 | 0
1452.85 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.19 | -0.905 | -0.905 | -9.05 | -4.3044 | -4.3044 | 0 | 12 | 1 | 1 | -4.3044 | 10 | 0 | 0
1452.9 | 49.88 | 49.88 | 0.24 | 0.24 | 2.4 | 50.17 | -0.715 | -0.805 | -8.05 | -2.825 | -2.825 | 0 | 12 | 1 | 1 | -2.825 | 10 | 0 | 0
1452.95 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.14 | -0.43 | -0.705 | -7.05 | -1.375 | -1.375 | 0 | 12 | 1 | 1 | -1.375 | 10 | 0 | 0
1453 | 49.83 | 49.83 | 0.715 | 0.715 | 7.15 | 50.12 | -0.24 | -0.605 | -6.05 | 0.55 | 0.55 | 0 | 12 | 1 | 1 | 0.55 | 10 | 0 | 0
1453.05 | 49.81 | 49.81 | 0.905 | 0.905 | 9.05 | 50.09 | -0.044118 | -0.505 | -5.05 | 2 | 2 | 0 | 12 | 1 | 1 | 2 | 10 | 0 | 0
1453.1 | 49.78 | 49.78 | 1 | 1 | 10 | 50.06 | -0.026471 | -0.405 | -4.05 | 2.975 | 2.975 | 0 | 12 | 1 | 1 | 2.975 | 10 | 0 | 0
1453.15 | 49.76 | 49.76 | 1 | 1 | 10 | 50.04 | -0.014706 | -0.305 | -3.05 | 3.475 | 3.475 | 0 | 12 | 1 | 1 | 3.475 | 10 | 0 | 0
1453.2 | 49.73 | 49.73 | 1 | 1 | 10 | 50.01 | 0 | -0.205 | -2.05 | 3.975 | 3.975 | 0 | 12 | 1 | 1 | 3.975 | 10 | 0 | 0
1453.25 | 49.71 | 49.71 | 1 | 1 | 10 | 49.99 | 0 | -0.105 | -1.05 | 4.475 | 4.475 | 0 | 12 | 1 | 1 | 4.475 | 10 | 0 | 0
1453.3 | 49.68 | 49.68 | 1 | 1 | 10 | 49.96 | 0.014706 | -0.005 | -0.05 | 4.975 | 4.975 | 0 | 12 | 1 | 1 | 4.975 | 10 | 0 | 0
1453.35 | 49.65 | 49.65 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
1453.4 | 49.63 | 49.63 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1453.45 | 49.6 | 49.6 | 1 | 1 | 10 | 49.88 | 0.24 | 0.14412 | 1.4412 | 5.7206 | 5.7206 | 0 | 12 | 1 | 1 | 5.7206 | 10 | 0 | 0
1453.5 | 49.58 | 49.58 | 1 | 1 | 10 | 49.86 | 0.43 | 0.24412 | 2.4412 | 6.2206 | 6.2206 | 0 | 12 | 1 | 1 | 6.2206 | 10 | 0 | 0
1453.55 | 49.55 | 49.55 | 1 | 1 | 10 | 49.83 | 0.715 | 0.34412 | 3.4412 | 6.7206 | 6.7206 | 0 | 12 | 1 | 1 | 6.7206 | 10 | 0 | 0
1453.6 | 49.53 | 49.53 | 1 | 1 | 10 | 49.81 | 0.905 | 0.44412 | 4.4412 | 7.2206 | 7.2206 | 0 | 12 | 1 | 1 | 7.2206 | 10 | 0 | 0
1453.65 | 49.5 | 49.5 | 1 | 1 | 10 | 49.78 | 1 | 0.54412 | 5.4412 | 7.7206 | 7.7206 | 0 | 12 | 1 | 1 | 7.7206 | 10 | 0 | 0
1453.7 | 49.5 | 49.5 | 1 | 1 | 10 | 49.76 | 1 | 0.64412 | 6.4412 | 8.2206 | 8.2206 | 0 | 12 | 1 | 1 | 8.2206 | 10 | 0 | 0
1453.75 | 49.53 | 49.5 | 1 | 1 | 10 | 49.73 | 1 | 0.74412 | 7.4412 | 8.7206 | 8.7206 | 0 | 12 | 1 | 1 | 8.7206 | 10 | 0 | 0
1453.8 | 49.55 | 49.5 | 1 | 1 | 10 | 49.71 | 1 | 0.84412 | 8.4412 | 9.2206 | 9.2206 | 0 | 12 | 1 | 1 | 9.2206 | 10 | 0 | 0
1453.85 | 49.58 | 49.5 | 1 | 1 | 10 | 49.68 | 1 | 0.94412 | 9.4412 | 9.7206 | 9.7206 | 0 | 12 | 1 | 1 | 9.7206 | 10 | 0 | 0
1453.9 | 49.6 | 49.5 | 1 | 1 | 10 | 49.65 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1453.95 | 49.63 | 49.5 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1454 | 49.65 | 49.5 | 1 | 1 | 10 | 49.65 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1454.05 | 49.68 | 49.5 | 1 | 1 | 10 | 49.68 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1454.1 | 49.71 | 49.5 | 1 | 1 | 10 | 49.71 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1454.15 | 49.73 | 49.5 | 1 | 1 | 10 | 49.73 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1454.2 | 49.76 | 49.5 | 1 | 1 | 10 | 49.76 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1454.25 | 49.78 | 49.5 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1454.3 | 49.81 | 49.53 | 1 | 1 | 10 | 49.81 | 0.905 | 0.905 | 9.05 | 9.525 | 9.525 | 0 | 12 | 1 | 1 | 9.525 | 10 | 0 | 0
1454.35 | 49.83 | 49.55 | 1 | 1 | 10 | 49.83 | 0.715 | 0.715 | 7.15 | 8.575 | 8.575 | 0 | 12 | 1 | 1 | 8.575 | 10 | 0 | 0
1454.4 | 49.86 | 49.58 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
1454.45 | 49.88 | 49.6 | 1 | 1 | 10 | 49.88 | 0.24 | 0.24 | 2.4 | 6.2 | 6.2 | 0 | 12 | 1 | 1 | 6.2 | 10 | 0 | 0
1454.5 | 49.91 | 49.63 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1454.55 | 49.94 | 49.65 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
1454.6 | 49.96 | 49.68 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
1454.65 | 49.99 | 49.71 | 1 | 1 | 10 | 49.99 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1454.7 | 50.01 | 49.73 | 1 | 1 | 10 | 50.01 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1454.75 | 50.04 | 49.76 | 1 | 1 | 10 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 4.9265 | 4.9265 | 0 | 12 | 1 | 1 | 4.9265 | 10 | 0 | 0
1454.8 | 50.06 | 49.78 | 1 | 1 | 10 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 4.8676 | 4.8676 | 0 | 12 | 1 | 1 | 4.8676 | 10 | 0 | 0
1454.85 | 50.09 | 49.81 | 0.905 | 0.905 | 9.05 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 4.3044 | 4.3044 | 0 | 12 | 1 | 1 | 4.3044 | 10 | 0 | 0
1454.9 | 50.12 | 49.83 | 0.715 | 0.805 | 8.05 | 50.12 | -0.24 | -0.24 | -2.4 | 2.825 | 2.825 | 0 | 12 | 1 | 1 | 2.825 | 10 | 0 | 0
1454.95 | 50.14 | 49.86 | 0.43 | 0.705 | 7.05 | 50.14 | -0.43 | -0.43 | -4.3 | 1.375 | 1.375 | 0 | 12 | 1 | 1 | 1.375 | 10 | 0 | 0
1455 | 50.17 | 49.88 | 0.24 | 0.605 | 6.05 | 50.17 | -0.715 | -0.715 | -7.15 | -0.55 | -0.55 | 0 | 12 | 1 | 1 | -0.55 | 10 | 0 | 0
1455.05 | 50.19 | 49.91 | 0.044118 | 0.505 | 5.05 | 50.19 | -0.905 | -0.905 | -9.05 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
1455.1 | 50.22 | 49.94 | 0.026471 | 0.405 | 4.05 | 50.22 | -1 | -1 | -10 | -2.975 | -2.975 | 0 | 12 | 1 | 1 | -2.975 | 10 | 0 | 0
1455.15 | 50.24 | 49.96 | 0.014706 | 0.305 | 3.05 | 50.24 | -1 | -1 | -10 | -3.475 | -3.475 | 0 | 12 | 1 | 1 | -3.475 | 10 | 0 | 0
1455.2 | 50.27 | 49.99 | 0 | 0.205 | 2.05 | 50.27 | -1 | -1 | -10 | -3.975 | -3.975 | 0 | 12 | 1 | 1 | -3.975 | 10 | 0 | 0
1455.25 | 50.29 | 50.01 | 0 | 0.105 | 1.05 | 50.29 | -1 | -1 | -10 | -4.475 | -4.475 | 0 | 12 | 1 | 1 | -4.475 | 10 | 0 | 0
1455.3 | 50.32 | 50.04 | -0.014706 | 0.005 | 0.05 | 50.32 | -1 | -1 | -10 | -4.975 | -4.975 | 0 | 12 | 1 | 1 | -4.975 | 10 | 0 | 0
1455.35 | 50.35 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.35 | -1 | -1 | -10 | -5.1324 | -5.1324 | 0 | 12 | 1 | 1 | -5.1324 | 10 | 0 | 0
1455.4 | 50.37 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 50.37 | -1 | -1 | -10 | -5.2206 | -5.2206 | 0 | 12 | 1 | 1 | -5.2206 | 10 | 0 | 0
1455.45 | 50.4 | 50.12 | -0.24 | -0.14412 | -1.4412 | 50.4 | -1 | -1 | -10 | -5.7206 | -5.7206 | 0 | 12 | 1 | 1 | -5.7206 | 10 | 0 | 0
1455.5 | 50.42 | 50.14 | -0.43 | -0.24412 | -2.4412 | 50.42 | -1 | -1 | -10 | -6.2206 | -6.2206 | 0 | 12 | 1 | 1 | -6.2206 | 10 | 0 | 0
1455.55 | 50.45 | 50.17 | -0.715 | -0.34412 | -3.4412 | 50.45 | -1 | -1 | -10 | -6.7206 | -6.7206 | 0 | 12 | 1 | 1 | -6.7206 | 10 | 0 | 0
1455.6 | 50.47 | 50.19 | -0.905 | -0.44412 | -4.4412 | 50.47 | -1 | -1 | -10 | -7.2206 | -7.2206 | 0 | 12 | 1 | 1 | -7.2206 | 10 | 0 | 0
1455.65 | 50.5 | 50.22 | -1 | -0.54412 | -5.4412 | 50.5 | -1 | -1 | -10 | -7.7206 | -7.7206 | 0 | 12 | 1 | 1 | -7.7206 | 10 | 0 | 0
1455.7 | 50.5 | 50.24 | -1 | -0.64412 | -6.4412 | 50.5 | -1 | -1 | -10 | -8.2206 | -8.2206 | 0 | 12 | 1 | 1 | -8.2206 | 10 | 0 | 0
1455.75 | 50.47 | 50.27 | -1 | -0.74412 | -7.4412 | 50.5 | -1 | -1 | -10 | -8.7206 | -8.7206 | 0 | 12 | 1 | 1 | -8.7206 | 10 | 0 | 0
1455.8 | 50.45 | 50.29 | -1 | -0.84412 | -8.4412 | 50.5 | -1 | -1 | -10 | -9.2206 | -9.2206 | 0 | 12 | 1 | 1 | -9.2206 | 10 | 0 | 0
1455.85 | 50.42 | 50.32 | -1 | -0.94412 | -9.4412 | 50.5 | -1 | -1 | -10 | -9.7206 | -9.7206 | 0 | 12 | 1 | 1 | -9.7206 | 10 | 0 | 0
1455.9 | 50.39 | 50.35 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1455.95 | 50.37 | 50.37 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1456 | 50.34 | 50.34 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1456.05 | 50.32 | 50.32 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1456.1 | 50.29 | 50.29 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1456.15 | 50.26 | 50.26 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1456.2 | 50.24 | 50.24 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1456.25 | 50.21 | 50.21 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1456.3 | 50.18 | 50.18 | -0.81 | -0.81 | -8.1 | 50.47 | -1 | -1 | -10 | -9.05 | -9.05 | 0 | 12 | 1 | 1 | -9.05 | 10 | 0 | 0
1456.35 | 50.16 | 50.16 | -0.62 | -0.62 | -6.2 | 50.45 | -1 | -1 | -10 | -8.1 | -8.1 | 0 | 12 | 1 | 1 | -8.1 | 10 | 0 | 0
1456.4 | 50.13 | 50.13 | -0.335 | -0.335 | -3.35 | 50.42 | -1 | -1 | -10 | -6.675 | -6.675 | 0 | 12 | 1 | 1 | -6.675 | 10 | 0 | 0
1456.45 | 50.11 | 50.11 | -0.145 | -0.145 | -1.45 | 50.39 | -1 | -1 | -10 | -5.725 | -5.725 | 0 | 12 | 1 | 1 | -5.725 | 10 | 0 | 0
1456.5 | 50.08 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 50.37 | -1 | -1 | -10 | -5.1912 | -5.1912 | 0 | 12 | 1 | 1 | -5.1912 | 10 | 0 | 0
1456.55 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.34 | -1 | -1 | -10 | -5.1029 | -5.1029 | 0 | 12 | 1 | 1 | -5.1029 | 10 | 0 | 0
1456.6 | 50.03 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 50.32 | -1 | -1 | -10 | -5.0441 | -5.0441 | 0 | 12 | 1 | 1 | -5.0441 | 10 | 0 | 0
1456.65 | 50 | 50 | 0 | 0 | 0 | 50.29 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1456.7 | 50 | 50 | 0 | 0 | 0 | 50.26 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1456.75 | 50 | 50 | 0 | 0 | 0 | 50.24 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1456.8 | 50 | 50 | 0 | 0 | 0 | 50.21 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1456.85 | 50 | 50 | 0 | 0 | 0 | 50.18 | -0.81 | -0.9 | -9 | -4.5 | -4.5 | 0 | 12 | 1 | 1 | -4.5 | 10 | 0 | 0
1456.9 | 50 | 50 | 0 | 0 | 0 | 50.16 | -0.62 | -0.8 | -8 | -4 | -4 | 0 | 12 | 1 | 1 | -4 | 10 | 0 | 0
1456.95 | 50 | 50 | 0 | 0 | 0 | 50.13 | -0.335 | -0.7 | -7 | -3.5 | -3.5 | 0 | 12 | 1 | 1 | -3.5 | 10 | 0 | 0
1457 | 50.01 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.6 | -6 | -3 | -3 | 0 | 12 | 1 | 1 | -3 | 10 | 0 | 0
1457.05 | 50.01 | 50 | 0 | 0 | 0 | 50.08 | -0.038235 | -0.5 | -5 | -2.5 | -2.5 | 0 | 12 | 1 | 1 | -2.5 | 10 | 0 | 0
1457.1 | 49.99 | 49.99 | 0 | 0 | 0 | 50.05 | -0.020588 | -0.4 | -4 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
1457.15 | 49.99 | 49.99 | 0 | 0 | 0 | 50.03 | -0.0088235 | -0.3 | -3 | -1.5 | -1.5 | 0 | 12 | 1 | 1 | -1.5 | 10 | 0 | 0
1457.2 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | -0.2 | -2 | -0.83824 | -0.83824 | 0 | 12 | 1 | 1 | -0.83824 | 10 | 0 | 0
1457.25 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | -0.1 | -1 | -0.33824 | -0.33824 | 0 | 12 | 1 | 1 | -0.33824 | 10 | 0 | 0
1457.3 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
1457.35 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
1457.4 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
1457.45 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
1457.5 | 49.89 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
1457.55 | 49.89 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
1457.6 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50.01 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1457.65 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1457.7 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1457.75 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 2.7868 | 2.7868 | 0 | 12 | 1 | 1 | 2.7868 | 10 | 0 | 0
1457.8 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 2.7868 | 2.7868 | 0 | 12 | 1 | 1 | 2.7868 | 10 | 0 | 0
1457.85 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 2.8456 | 2.8456 | 0 | 12 | 1 | 1 | 2.8456 | 10 | 0 | 0
1457.9 | 49.94 | 49.85 | 0.525 | 0.525 | 5.25 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 2.7574 | 2.7574 | 0 | 12 | 1 | 1 | 2.7574 | 10 | 0 | 0
1457.95 | 49.94 | 49.85 | 0.525 | 0.525 | 5.25 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 2.7574 | 2.7574 | 0 | 12 | 1 | 1 | 2.7574 | 10 | 0 | 0
1458 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1458.05 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1458.1 | 49.93 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1458.15 | 49.93 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1458.2 | 49.96 | 49.85 | 0.525 | 0.525 | 5.25 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 2.6985 | 2.6985 | 0 | 12 | 1 | 1 | 2.6985 | 10 | 0 | 0
1458.25 | 49.96 | 49.85 | 0.525 | 0.525 | 5.25 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 2.6985 | 2.6985 | 0 | 12 | 1 | 1 | 2.6985 | 10 | 0 | 0
1458.3 | 49.99 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1458.35 | 49.99 | 49.91 | 0.044118 | 0.425 | 4.25 | 49.99 | 0 | 0 | 0 | 2.125 | 2.125 | 0 | 12 | 1 | 1 | 2.125 | 10 | 0 | 0
1458.4 | 49.99 | 49.91 | 0.044118 | 0.325 | 3.25 | 49.99 | 0 | 0 | 0 | 1.625 | 1.625 | 0 | 12 | 1 | 1 | 1.625 | 10 | 0 | 0
1458.45 | 49.99 | 49.93 | 0.032353 | 0.225 | 2.25 | 49.99 | 0 | 0 | 0 | 1.125 | 1.125 | 0 | 12 | 1 | 1 | 1.125 | 10 | 0 | 0
1458.5 | 49.96 | 49.93 | 0.032353 | 0.125 | 1.25 | 49.99 | 0 | 0 | 0 | 0.625 | 0.625 | 0 | 12 | 1 | 1 | 0.625 | 10 | 0 | 0
1458.55 | 49.96 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 49.99 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1458.6 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1458.65 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1458.7 | 50.05 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.058824 | 0.058824 | 0 | 12 | 1 | 1 | 0.058824 | 10 | 0 | 0
1458.75 | 50.05 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
1458.8 | 49.97 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
1458.85 | 49.97 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
1458.9 | 49.92 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1458.95 | 49.92 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1459 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1459.05 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1459.1 | 49.94 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1459.15 | 49.94 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1459.2 | 50.01 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1459.25 | 50.01 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1459.3 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1459.35 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
1459.4 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
1459.45 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
1459.5 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
1459.55 | 49.95 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
1459.6 | 49.97 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
1459.65 | 49.97 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
1459.7 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
1459.75 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
1459.8 | 49.87 | 49.87 | 0.335 | 0.335 | 3.35 | 50.01 | 0 | 0 | 0 | 1.675 | 1.675 | 0 | 12 | 1 | 1 | 1.675 | 10 | 0 | 0
1459.85 | 49.87 | 49.87 | 0.335 | 0.335 | 3.35 | 49.99 | 0 | 0 | 0 | 1.675 | 1.675 | 0 | 12 | 1 | 1 | 1.675 | 10 | 0 | 0
1459.9 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1459.95 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 2.6691 | 2.6691 | 0 | 12 | 1 | 1 | 2.6691 | 10 | 0 | 0
1460 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1460.05 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1460.1 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1460.15 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1460.2 | 49.84 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1460.25 | 49.84 | 49.79 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
1460.3 | 49.89 | 49.79 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
1460.35 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.12647 | 1.2647 | 5.6324 | 5.6324 | 0 | 12 | 1 | 1 | 5.6324 | 10 | 0 | 0
1460.4 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.145 | 1.45 | 5.725 | 5.725 | 0 | 12 | 1 | 1 | 5.725 | 10 | 0 | 0
1460.45 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.145 | 1.45 | 5.725 | 5.725 | 0 | 12 | 1 | 1 | 5.725 | 10 | 0 | 0
1460.5 | 49.96 | 49.79 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
1460.55 | 49.96 | 49.79 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
1460.6 | 50.02 | 49.79 | 1 | 1 | 10 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 4.9853 | 4.9853 | 0 | 12 | 1 | 1 | 4.9853 | 10 | 0 | 0
1460.65 | 50.02 | 49.79 | 1 | 1 | 10 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 4.9853 | 4.9853 | 0 | 12 | 1 | 1 | 4.9853 | 10 | 0 | 0
1460.7 | 50.03 | 49.79 | 1 | 1 | 10 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.9559 | 4.9559 | 0 | 12 | 1 | 1 | 4.9559 | 10 | 0 | 0
1460.75 | 50.03 | 49.84 | 0.62 | 0.9 | 9 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.4559 | 4.4559 | 0 | 12 | 1 | 1 | 4.4559 | 10 | 0 | 0
1460.8 | 50.02 | 49.84 | 0.62 | 0.8 | 8 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 3.9559 | 3.9559 | 0 | 12 | 1 | 1 | 3.9559 | 10 | 0 | 0
1460.85 | 50.02 | 49.89 | 0.145 | 0.7 | 7 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 3.4559 | 3.4559 | 0 | 12 | 1 | 1 | 3.4559 | 10 | 0 | 0
1460.9 | 50.08 | 49.89 | 0.145 | 0.6 | 6 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 2.8088 | 2.8088 | 0 | 12 | 1 | 1 | 2.8088 | 10 | 0 | 0
1460.95 | 50.08 | 49.89 | 0.145 | 0.5 | 5 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 2.3088 | 2.3088 | 0 | 12 | 1 | 1 | 2.3088 | 10 | 0 | 0
1461 | 50.01 | 49.89 | 0.145 | 0.4 | 4 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 1.8088 | 1.8088 | 0 | 12 | 1 | 1 | 1.8088 | 10 | 0 | 0
1461.05 | 50.01 | 49.96 | 0.014706 | 0.3 | 3 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 1.3088 | 1.3088 | 0 | 12 | 1 | 1 | 1.3088 | 10 | 0 | 0
1461.1 | 49.94 | 49.94 | 0.026471 | 0.2 | 2 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.80882 | 0.80882 | 0 | 12 | 1 | 1 | 0.80882 | 10 | 0 | 0
1461.15 | 49.94 | 49.94 | 0.026471 | 0.1 | 1 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.30882 | 0.30882 | 0 | 12 | 1 | 1 | 0.30882 | 10 | 0 | 0
1461.2 | 50 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
1461.25 | 50 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
1461.3 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
1461.35 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
1461.4 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1461.45 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1461.5 | 49.92 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1461.55 | 49.92 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
1461.6 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50.01 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1461.65 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1461.7 | 49.92 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1461.75 | 49.92 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1461.8 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1461.85 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1461.9 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1461.95 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1462 | 49.87 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1462.05 | 49.87 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1462.1 | 49.8 | 49.8 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1462.15 | 49.8 | 49.8 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1462.2 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1462.25 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1462.3 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1462.35 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1462.4 | 49.72 | 49.72 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1462.45 | 49.72 | 49.72 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1462.5 | 49.67 | 49.67 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1462.55 | 49.67 | 49.67 | 1 | 1 | 10 | 49.87 | 0.335 | 0.14412 | 1.4412 | 5.7206 | 5.7206 | 0 | 12 | 1 | 1 | 5.7206 | 10 | 0 | 0
1462.6 | 49.65 | 49.65 | 1 | 1 | 10 | 49.87 | 0.335 | 0.24412 | 2.4412 | 6.2206 | 6.2206 | 0 | 12 | 1 | 1 | 6.2206 | 10 | 0 | 0
1462.65 | 49.65 | 49.65 | 1 | 1 | 10 | 49.8 | 1 | 0.34412 | 3.4412 | 6.7206 | 6.7206 | 0 | 12 | 1 | 1 | 6.7206 | 10 | 0 | 0
1462.7 | 49.59 | 49.59 | 1 | 1 | 10 | 49.8 | 1 | 0.44412 | 4.4412 | 7.2206 | 7.2206 | 0 | 12 | 1 | 1 | 7.2206 | 10 | 0 | 0
1462.75 | 49.59 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.54412 | 5.4412 | 7.7206 | 7.7206 | 0 | 12 | 1 | 1 | 7.7206 | 10 | 0 | 0
1462.8 | 49.66 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.64412 | 6.4412 | 8.2206 | 8.2206 | 0 | 12 | 1 | 1 | 8.2206 | 10 | 0 | 0
1462.85 | 49.66 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.74412 | 7.4412 | 8.7206 | 8.7206 | 0 | 12 | 1 | 1 | 8.7206 | 10 | 0 | 0
1462.9 | 49.63 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.84412 | 8.4412 | 9.2206 | 9.2206 | 0 | 12 | 1 | 1 | 9.2206 | 10 | 0 | 0
1462.95 | 49.63 | 49.59 | 1 | 1 | 10 | 49.72 | 1 | 0.94412 | 9.4412 | 9.7206 | 9.7206 | 0 | 12 | 1 | 1 | 9.7206 | 10 | 0 | 0
1463 | 49.61 | 49.59 | 1 | 1 | 10 | 49.72 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1463.05 | 49.61 | 49.59 | 1 | 1 | 10 | 49.67 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1463.1 | 49.54 | 49.54 | 1 | 1 | 10 | 49.67 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1463.15 | 49.54 | 49.54 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1463.2 | 49.46 | 49.46 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1463.25 | 49.46 | 49.46 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1463.3 | 49.45 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1463.35 | 49.45 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1463.4 | 49.51 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1463.45 | 49.51 | 49.45 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1463.5 | 49.5 | 49.45 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1463.55 | 49.5 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1463.6 | 49.54 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1463.65 | 49.54 | 49.45 | 1 | 1 | 10 | 49.54 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1463.7 | 49.59 | 49.45 | 1 | 1 | 10 | 49.59 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1463.75 | 49.59 | 49.45 | 1 | 1 | 10 | 49.59 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1463.8 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1463.85 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1463.9 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1463.95 | 49.61 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1464 | 49.53 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1464.05 | 49.53 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1464.1 | 49.54 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1464.15 | 49.54 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1464.2 | 49.61 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1464.25 | 49.61 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1464.3 | 49.66 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1464.35 | 49.66 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1464.4 | 49.64 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1464.45 | 49.64 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1464.5 | 49.69 | 49.53 | 1 | 1 | 10 | 49.69 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1464.55 | 49.69 | 49.53 | 1 | 1 | 10 | 49.69 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1464.6 | 49.74 | 49.53 | 1 | 1 | 10 | 49.74 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1464.65 | 49.74 | 49.54 | 1 | 1 | 10 | 49.74 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1464.7 | 49.78 | 49.54 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1464.75 | 49.78 | 49.61 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1464.8 | 49.82 | 49.61 | 1 | 1 | 10 | 49.82 | 0.81 | 0.81 | 8.1 | 9.05 | 9.05 | 0 | 12 | 1 | 1 | 9.05 | 10 | 0 | 0
1464.85 | 49.82 | 49.64 | 1 | 1 | 10 | 49.82 | 0.81 | 0.81 | 8.1 | 9.05 | 9.05 | 0 | 12 | 1 | 1 | 9.05 | 10 | 0 | 0
1464.9 | 49.86 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
1464.95 | 49.86 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
1465 | 49.84 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
1465.05 | 49.84 | 49.69 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
1465.1 | 49.91 | 49.69 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1465.15 | 49.91 | 49.74 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1465.2 | 49.97 | 49.74 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1465.25 | 49.97 | 49.78 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1465.3 | 50.03 | 49.78 | 1 | 1 | 10 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.9559 | 4.9559 | 0 | 12 | 1 | 1 | 4.9559 | 10 | 0 | 0
1465.35 | 50.03 | 49.82 | 0.81 | 0.9 | 9 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.4559 | 4.4559 | 0 | 12 | 1 | 1 | 4.4559 | 10 | 0 | 0
1465.4 | 50.05 | 49.82 | 0.81 | 0.81 | 8.1 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 3.9471 | 3.9471 | 0 | 12 | 1 | 1 | 3.9471 | 10 | 0 | 0
1465.45 | 50.05 | 49.84 | 0.62 | 0.71 | 7.1 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 3.4471 | 3.4471 | 0 | 12 | 1 | 1 | 3.4471 | 10 | 0 | 0
1465.5 | 50.01 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
1465.55 | 50.01 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
1465.6 | 49.95 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
1465.65 | 49.95 | 49.91 | 0.044118 | 0.52 | 5.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.4971 | 2.4971 | 0 | 12 | 1 | 1 | 2.4971 | 10 | 0 | 0
1465.7 | 49.99 | 49.91 | 0.044118 | 0.42 | 4.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 1.9971 | 1.9971 | 0 | 12 | 1 | 1 | 1.9971 | 10 | 0 | 0
1465.75 | 49.99 | 49.95 | 0.020588 | 0.32 | 3.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 1.4971 | 1.4971 | 0 | 12 | 1 | 1 | 1.4971 | 10 | 0 | 0
1465.8 | 49.92 | 49.92 | 0.038235 | 0.22 | 2.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.99706 | 0.99706 | 0 | 12 | 1 | 1 | 0.99706 | 10 | 0 | 0
1465.85 | 49.92 | 49.92 | 0.038235 | 0.12 | 1.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.49706 | 0.49706 | 0 | 12 | 1 | 1 | 0.49706 | 10 | 0 | 0
1465.9 | 49.97 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1465.95 | 49.97 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1466 | 50.02 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1466.05 | 50.02 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.17647 | 0.17647 | 0 | 12 | 1 | 1 | 0.17647 | 10 | 0 | 0
1466.1 | 50.07 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1466.15 | 50.07 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1466.2 | 50.06 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1466.25 | 50.06 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1466.3 | 50.13 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
1466.35 | 50.13 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
1466.4 | 50.09 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
1466.45 | 50.09 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6309 | -1.6309 | 0 | 12 | 1 | 1 | -1.6309 | 10 | 0 | 0
1466.5 | 50.07 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6309 | -1.6309 | 0 | 12 | 1 | 1 | -1.6309 | 10 | 0 | 0
1466.55 | 50.07 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6897 | -1.6897 | 0 | 12 | 1 | 1 | -1.6897 | 10 | 0 | 0
1466.6 | 50.07 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6897 | -1.6897 | 0 | 12 | 1 | 1 | -1.6897 | 10 | 0 | 0
1466.65 | 50.07 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.13 | -0.335 | -0.335 | -3.35 | -1.8074 | -1.8074 | 0 | 12 | 1 | 1 | -1.8074 | 10 | 0 | 0
1466.7 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.13 | -0.335 | -0.335 | -3.35 | -1.7779 | -1.7779 | 0 | 12 | 1 | 1 | -1.7779 | 10 | 0 | 0
1466.75 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.13 | -0.335 | -0.335 | -3.35 | -1.7779 | -1.7779 | 0 | 12 | 1 | 1 | -1.7779 | 10 | 0 | 0
1466.8 | 50.01 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
1466.85 | 50.01 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
1466.9 | 50.07 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
1466.95 | 50.07 | 50.01 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.235 | -2.35 | -1.175 | -1.175 | 0 | 12 | 1 | 1 | -1.175 | 10 | 0 | 0
1467 | 50.05 | 50.01 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.135 | -1.35 | -0.675 | -0.675 | 0 | 12 | 1 | 1 | -0.675 | 10 | 0 | 0
1467.05 | 50.05 | 50.01 | 0 | 0 | 0 | 50.07 | -0.032353 | -0.035 | -0.35 | -0.175 | -0.175 | 0 | 12 | 1 | 1 | -0.175 | 10 | 0 | 0
1467.1 | 50.1 | 50.01 | 0 | 0 | 0 | 50.1 | -0.05 | -0.05 | -0.5 | -0.25 | -0.25 | 0 | 12 | 1 | 1 | -0.25 | 10 | 0 | 0
1467.15 | 50.1 | 50.01 | 0 | 0 | 0 | 50.1 | -0.05 | -0.05 | -0.5 | -0.25 | -0.25 | 0 | 12 | 1 | 1 | -0.25 | 10 | 0 | 0
1467.2 | 50.11 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1467.25 | 50.11 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1467.3 | 50.06 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1467.35 | 50.06 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1467.4 | 50.04 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1467.45 | 50.04 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1467.5 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1467.55 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1467.6 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1467.65 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1467.7 | 50.11 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1467.75 | 50.11 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1467.8 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1467.85 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1467.9 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1467.95 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1468 | 50.02 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.11 | -0.145 | -0.145 | -1.45 | -0.73971 | -0.73971 | 0 | 12 | 1 | 1 | -0.73971 | 10 | 0 | 0
1468.05 | 50.02 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.11 | -0.145 | -0.145 | -1.45 | -0.73971 | -0.73971 | 0 | 12 | 1 | 1 | -0.73971 | 10 | 0 | 0
1468.1 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1468.15 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1468.2 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1468.25 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1468.3 | 50.01 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1468.35 | 50.01 | 50 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.045 | -0.45 | -0.225 | -0.225 | 0 | 12 | 1 | 1 | -0.225 | 10 | 0 | 0
1468.4 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
1468.45 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
1468.5 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
1468.55 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1468.6 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.14706 | 0.14706 | 0 | 12 | 1 | 1 | 0.14706 | 10 | 0 | 0
1468.65 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1468.7 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1468.75 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1468.8 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1468.85 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1468.9 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1468.95 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1469 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1469.05 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1469.1 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1469.15 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1469.2 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1469.25 | 50 | 50 | 0 | 0 | 0 | 50.01 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1469.3 | 49.5 | 49.5 | 1 | 1 | 10 | 50.01 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1469.35 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1469.4 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1469.45 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1469.5 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1469.55 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1469.6 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1469.65 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1469.7 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1469.75 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1469.8 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1469.85 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.1 | 1 | 5.5 | 5.5 | 0 | 12 | 1 | 1 | 5.5 | 10 | 0 | 0
1469.9 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.2 | 2 | 6 | 6 | 0 | 12 | 1 | 1 | 6 | 10 | 0 | 0
1469.95 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.3 | 3 | 6.5 | 6.5 | 0 | 12 | 1 | 1 | 6.5 | 10 | 0 | 0
1470 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.4 | 4 | 7 | 7 | 0 | 12 | 1 | 1 | 7 | 10 | 0 | 0
1470.05 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.5 | 5 | 7.5 | 7.5 | 0 | 12 | 1 | 1 | 7.5 | 10 | 0 | 0
1470.1 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.6 | 6 | 8 | 8 | 0 | 12 | 1 | 1 | 8 | 10 | 0 | 0
1470.15 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.7 | 7 | 8.5 | 8.5 | 0 | 12 | 1 | 1 | 8.5 | 10 | 0 | 0
1470.2 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.8 | 8 | 9 | 9 | 0 | 12 | 1 | 1 | 9 | 10 | 0 | 0
1470.25 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.9 | 9 | 9.5 | 9.5 | 0 | 12 | 1 | 1 | 9.5 | 10 | 0 | 0
1470.3 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1470.35 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1470.4 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1470.45 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1470.5 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1470.55 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1470.6 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1470.65 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1470.7 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1470.75 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1470.8 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1470.85 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1470.9 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1470.95 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1471 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1471.05 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1471.1 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1471.15 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1471.2 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1471.25 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1471.3 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1471.35 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1471.4 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1471.45 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1471.5 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1471.55 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1471.6 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1471.65 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1471.7 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1471.75 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1471.8 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1471.85 | 50.5 | 50.5 | -1 | 0.9 | 9 | 50.5 | -1 | -1 | -10 | -0.5 | -0.5 | 0 | 12 | 1 | 1 | -0.5 | 10 | 0 | 0
1471.9 | 50.5 | 50.5 | -1 | 0.8 | 8 | 50.5 | -1 | -1 | -10 | -1 | -1 | 0 | 12 | 1 | 1 | -1 | 10 | 0 | 0
1471.95 | 50.5 | 50.5 | -1 | 0.7 | 7 | 50.5 | -1 | -1 | -10 | -1.5 | -1.5 | 0 | 12 | 1 | 1 | -1.5 | 10 | 0 | 0
1472 | 50.5 | 50.5 | -1 | 0.6 | 6 | 50.5 | -1 | -1 | -10 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
1472.05 | 50.5 | 50.5 | -1 | 0.5 | 5 | 50.5 | -1 | -1 | -10 | -2.5 | -2.5 | 0 | 12 | 1 | 1 | -2.5 | 10 | 0 | 0
1472.1 | 50.5 | 50.5 | -1 | 0.4 | 4 | 50.5 | -1 | -1 | -10 | -3 | -3 | 0 | 12 | 1 | 1 | -3 | 10 | 0 | 0
1472.15 | 50.5 | 50.5 | -1 | 0.3 | 3 | 50.5 | -1 | -1 | -10 | -3.5 | -3.5 | 0 | 12 | 1 | 1 | -3.5 | 10 | 0 | 0
1472.2 | 50.5 | 50.5 | -1 | 0.2 | 2 | 50.5 | -1 | -1 | -10 | -4 | -4 | 0 | 12 | 1 | 1 | -4 | 10 | 0 | 0
1472.25 | 50.5 | 50.5 | -1 | 0.1 | 1 | 50.5 | -1 | -1 | -10 | -4.5 | -4.5 | 0 | 12 | 1 | 1 | -4.5 | 10 | 0 | 0
1472.3 | 50.5 | 50.5 | -1 | 0 | 0 | 50.5 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1472.35 | 50.5 | 50.5 | -1 | -0.1 | -1 | 50.5 | -1 | -1 | -10 | -5.5 | -5.5 | 0 | 12 | 1 | 1 | -5.5 | 10 | 0 | 0
1472.4 | 50.5 | 50.5 | -1 | -0.2 | -2 | 50.5 | -1 | -1 | -10 | -6 | -6 | 0 | 12 | 1 | 1 | -6 | 10 | 0 | 0
1472.45 | 50.5 | 50.5 | -1 | -0.3 | -3 | 50.5 | -1 | -1 | -10 | -6.5 | -6.5 | 0 | 12 | 1 | 1 | -6.5 | 10 | 0 | 0
1472.5 | 50.5 | 50.5 | -1 | -0.4 | -4 | 50.5 | -1 | -1 | -10 | -7 | -7 | 0 | 12 | 1 | 1 | -7 | 10 | 0 | 0
1472.55 | 50.5 | 50.5 | -1 | -0.5 | -5 | 50.5 | -1 | -1 | -10 | -7.5 | -7.5 | 0 | 12 | 1 | 1 | -7.5 | 10 | 0 | 0
1472.6 | 50.5 | 50.5 | -1 | -0.6 | -6 | 50.5 | -1 | -1 | -10 | -8 | -8 | 0 | 12 | 1 | 1 | -8 | 10 | 0 | 0
1472.65 | 50.5 | 50.5 | -1 | -0.7 | -7 | 50.5 | -1 | -1 | -10 | -8.5 | -8.5 | 0 | 12 | 1 | 1 | -8.5 | 10 | 0 | 0
1472.7 | 50.5 | 50.5 | -1 | -0.8 | -8 | 50.5 | -1 | -1 | -10 | -9 | -9 | 0 | 12 | 1 | 1 | -9 | 10 | 0 | 0
1472.75 | 50.5 | 50.5 | -1 | -0.9 | -9 | 50.5 | -1 | -1 | -10 | -9.5 | -9.5 | 0 | 12 | 1 | 1 | -9.5 | 10 | 0 | 0
1472.8 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1472.85 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1472.9 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1472.95 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1473 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1473.05 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1473.1 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1473.15 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1473.2 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1473.25 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1473.3 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1473.35 | 50.47 | 50.47 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1473.4 | 50.45 | 50.45 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1473.45 | 50.42 | 50.42 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1473.5 | 50.4 | 50.4 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1473.55 | 50.37 | 50.37 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1473.6 | 50.35 | 50.35 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1473.65 | 50.32 | 50.32 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1473.7 | 50.29 | 50.29 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1473.75 | 50.27 | 50.27 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1473.8 | 50.24 | 50.24 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1473.85 | 50.22 | 50.22 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1473.9 | 50.19 | 50.19 | -0.905 | -0.905 | -9.05 | 50.47 | -1 | -1 | -10 | -9.525 | -9.525 | 0 | 12 | 1 | 1 | -9.525 | 10 | 0 | 0
1473.95 | 50.17 | 50.17 | -0.715 | -0.715 | -7.15 | 50.45 | -1 | -1 | -10 | -8.575 | -8.575 | 0 | 12 | 1 | 1 | -8.575 | 10 | 0 | 0
1474 | 50.14 | 50.14 | -0.43 | -0.43 | -4.3 | 50.42 | -1 | -1 | -10 | -7.15 | -7.15 | 0 | 12 | 1 | 1 | -7.15 | 10 | 0 | 0
1474.05 | 50.12 | 50.12 | -0.24 | -0.24 | -2.4 | 50.4 | -1 | -1 | -10 | -6.2 | -6.2 | 0 | 12 | 1 | 1 | -6.2 | 10 | 0 | 0
1474.1 | 50.09 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 50.37 | -1 | -1 | -10 | -5.2206 | -5.2206 | 0 | 12 | 1 | 1 | -5.2206 | 10 | 0 | 0
1474.15 | 50.06 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.35 | -1 | -1 | -10 | -5.1324 | -5.1324 | 0 | 12 | 1 | 1 | -5.1324 | 10 | 0 | 0
1474.2 | 50.04 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.32 | -1 | -1 | -10 | -5.0735 | -5.0735 | 0 | 12 | 1 | 1 | -5.0735 | 10 | 0 | 0
1474.25 | 50.01 | 50.01 | 0 | 0 | 0 | 50.29 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1474.3 | 49.99 | 49.99 | 0 | 0 | 0 | 50.27 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1474.35 | 49.96 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.24 | -1 | -1 | -10 | -4.9265 | -4.9265 | 0 | 12 | 1 | 1 | -4.9265 | 10 | 0 | 0
1474.4 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.22 | -1 | -1 | -10 | -4.8676 | -4.8676 | 0 | 12 | 1 | 1 | -4.8676 | 10 | 0 | 0
1474.45 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.19 | -0.905 | -0.905 | -9.05 | -4.3044 | -4.3044 | 0 | 12 | 1 | 1 | -4.3044 | 10 | 0 | 0
1474.5 | 49.88 | 49.88 | 0.24 | 0.24 | 2.4 | 50.17 | -0.715 | -0.805 | -8.05 | -2.825 | -2.825 | 0 | 12 | 1 | 1 | -2.825 | 10 | 0 | 0
1474.55 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.14 | -0.43 | -0.705 | -7.05 | -1.375 | -1.375 | 0 | 12 | 1 | 1 | -1.375 | 10 | 0 | 0
1474.6 | 49.83 | 49.83 | 0.715 | 0.715 | 7.15 | 50.12 | -0.24 | -0.605 | -6.05 | 0.55 | 0.55 | 0 | 12 | 1 | 1 | 0.55 | 10 | 0 | 0
1474.65 | 49.81 | 49.81 | 0.905 | 0.905 | 9.05 | 50.09 | -0.044118 | -0.505 | -5.05 | 2 | 2 | 0 | 12 | 1 | 1 | 2 | 10 | 0 | 0
1474.7 | 49.78 | 49.78 | 1 | 1 | 10 | 50.06 | -0.026471 | -0.405 | -4.05 | 2.975 | 2.975 | 0 | 12 | 1 | 1 | 2.975 | 10 | 0 | 0
1474.75 | 49.76 | 49.76 | 1 | 1 | 10 | 50.04 | -0.014706 | -0.305 | -3.05 | 3.475 | 3.475 | 0 | 12 | 1 | 1 | 3.475 | 10 | 0 | 0
1474.8 | 49.73 | 49.73 | 1 | 1 | 10 | 50.01 | 0 | -0.205 | -2.05 | 3.975 | 3.975 | 0 | 12 | 1 | 1 | 3.975 | 10 | 0 | 0
1474.85 | 49.71 | 49.71 | 1 | 1 | 10 | 49.99 | 0 | -0.105 | -1.05 | 4.475 | 4.475 | 0 | 12 | 1 | 1 | 4.475 | 10 | 0 | 0
1474.9 | 49.68 | 49.68 | 1 | 1 | 10 | 49.96 | 0.014706 | -0.005 | -0.05 | 4.975 | 4.975 | 0 | 12 | 1 | 1 | 4.975 | 10 | 0 | 0
1474.95 | 49.65 | 49.65 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
1475 | 49.63 | 49.63 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1475.05 | 49.6 | 49.6 | 1 | 1 | 10 | 49.88 | 0.24 | 0.14412 | 1.4412 | 5.7206 | 5.7206 | 0 | 12 | 1 | 1 | 5.7206 | 10 | 0 | 0
1475.1 | 49.58 | 49.58 | 1 | 1 | 10 | 49.86 | 0.43 | 0.24412 | 2.4412 | 6.2206 | 6.2206 | 0 | 12 | 1 | 1 | 6.2206 | 10 | 0 | 0
1475.15 | 49.55 | 49.55 | 1 | 1 | 10 | 49.83 | 0.715 | 0.34412 | 3.4412 | 6.7206 | 6.7206 | 0 | 12 | 1 | 1 | 6.7206 | 10 | 0 | 0
1475.2 | 49.53 | 49.53 | 1 | 1 | 10 | 49.81 | 0.905 | 0.44412 | 4.4412 | 7.2206 | 7.2206 | 0 | 12 | 1 | 1 | 7.2206 | 10 | 0 | 0
1475.25 | 49.5 | 49.5 | 1 | 1 | 10 | 49.78 | 1 | 0.54412 | 5.4412 | 7.7206 | 7.7206 | 0 | 12 | 1 | 1 | 7.7206 | 10 | 0 | 0
1475.3 | 49.5 | 49.5 | 1 | 1 | 10 | 49.76 | 1 | 0.64412 | 6.4412 | 8.2206 | 8.2206 | 0 | 12 | 1 | 1 | 8.2206 | 10 | 0 | 0
1475.35 | 49.53 | 49.5 | 1 | 1 | 10 | 49.73 | 1 | 0.74412 | 7.4412 | 8.7206 | 8.7206 | 0 | 12 | 1 | 1 | 8.7206 | 10 | 0 | 0
1475.4 | 49.55 | 49.5 | 1 | 1 | 10 | 49.71 | 1 | 0.84412 | 8.4412 | 9.2206 | 9.2206 | 0 | 12 | 1 | 1 | 9.2206 | 10 | 0 | 0
1475.45 | 49.58 | 49.5 | 1 | 1 | 10 | 49.68 | 1 | 0.94412 | 9.4412 | 9.7206 | 9.7206 | 0 | 12 | 1 | 1 | 9.7206 | 10 | 0 | 0
1475.5 | 49.6 | 49.5 | 1 | 1 | 10 | 49.65 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1475.55 | 49.63 | 49.5 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1475.6 | 49.65 | 49.5 | 1 | 1 | 10 | 49.65 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1475.65 | 49.68 | 49.5 | 1 | 1 | 10 | 49.68 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1475.7 | 49.71 | 49.5 | 1 | 1 | 10 | 49.71 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1475.75 | 49.73 | 49.5 | 1 | 1 | 10 | 49.73 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1475.8 | 49.76 | 49.5 | 1 | 1 | 10 | 49.76 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1475.85 | 49.78 | 49.5 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1475.9 | 49.81 | 49.53 | 1 | 1 | 10 | 49.81 | 0.905 | 0.905 | 9.05 | 9.525 | 9.525 | 0 | 12 | 1 | 1 | 9.525 | 10 | 0 | 0
1475.95 | 49.83 | 49.55 | 1 | 1 | 10 | 49.83 | 0.715 | 0.715 | 7.15 | 8.575 | 8.575 | 0 | 12 | 1 | 1 | 8.575 | 10 | 0 | 0
1476 | 49.86 | 49.58 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
1476.05 | 49.88 | 49.6 | 1 | 1 | 10 | 49.88 | 0.24 | 0.24 | 2.4 | 6.2 | 6.2 | 0 | 12 | 1 | 1 | 6.2 | 10 | 0 | 0
1476.1 | 49.91 | 49.63 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1476.15 | 49.94 | 49.65 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
1476.2 | 49.96 | 49.68 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
1476.25 | 49.99 | 49.71 | 1 | 1 | 10 | 49.99 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1476.3 | 50.01 | 49.73 | 1 | 1 | 10 | 50.01 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1476.35 | 50.04 | 49.76 | 1 | 1 | 10 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 4.9265 | 4.9265 | 0 | 12 | 1 | 1 | 4.9265 | 10 | 0 | 0
1476.4 | 50.06 | 49.78 | 1 | 1 | 10 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 4.8676 | 4.8676 | 0 | 12 | 1 | 1 | 4.8676 | 10 | 0 | 0
1476.45 | 50.09 | 49.81 | 0.905 | 0.905 | 9.05 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 4.3044 | 4.3044 | 0 | 12 | 1 | 1 | 4.3044 | 10 | 0 | 0
1476.5 | 50.12 | 49.83 | 0.715 | 0.805 | 8.05 | 50.12 | -0.24 | -0.24 | -2.4 | 2.825 | 2.825 | 0 | 12 | 1 | 1 | 2.825 | 10 | 0 | 0
1476.55 | 50.14 | 49.86 | 0.43 | 0.705 | 7.05 | 50.14 | -0.43 | -0.43 | -4.3 | 1.375 | 1.375 | 0 | 12 | 1 | 1 | 1.375 | 10 | 0 | 0
1476.6 | 50.17 | 49.88 | 0.24 | 0.605 | 6.05 | 50.17 | -0.715 | -0.715 | -7.15 | -0.55 | -0.55 | 0 | 12 | 1 | 1 | -0.55 | 10 | 0 | 0
1476.65 | 50.19 | 49.91 | 0.044118 | 0.505 | 5.05 | 50.19 | -0.905 | -0.905 | -9.05 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
1476.7 | 50.22 | 49.94 | 0.026471 | 0.405 | 4.05 | 50.22 | -1 | -1 | -10 | -2.975 | -2.975 | 0 | 12 | 1 | 1 | -2.975 | 10 | 0 | 0
1476.75 | 50.24 | 49.96 | 0.014706 | 0.305 | 3.05 | 50.24 | -1 | -1 | -10 | -3.475 | -3.475 | 0 | 12 | 1 | 1 | -3.475 | 10 | 0 | 0
1476.8 | 50.27 | 49.99 | 0 | 0.205 | 2.05 | 50.27 | -1 | -1 | -10 | -3.975 | -3.975 | 0 | 12 | 1 | 1 | -3.975 | 10 | 0 | 0
1476.85 | 50.29 | 50.01 | 0 | 0.105 | 1.05 | 50.29 | -1 | -1 | -10 | -4.475 | -4.475 | 0 | 12 | 1 | 1 | -4.475 | 10 | 0 | 0
1476.9 | 50.32 | 50.04 | -0.014706 | 0.005 | 0.05 | 50.32 | -1 | -1 | -10 | -4.975 | -4.975 | 0 | 12 | 1 | 1 | -4.975 | 10 | 0 | 0
1476.95 | 50.35 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.35 | -1 | -1 | -10 | -5.1324 | -5.1324 | 0 | 12 | 1 | 1 | -5.1324 | 10 | 0 | 0
1477 | 50.37 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 50.37 | -1 | -1 | -10 | -5.2206 | -5.2206 | 0 | 12 | 1 | 1 | -5.2206 | 10 | 0 | 0
1477.05 | 50.4 | 50.12 | -0.24 | -0.14412 | -1.4412 | 50.4 | -1 | -1 | -10 | -5.7206 | -5.7206 | 0 | 12 | 1 | 1 | -5.7206 | 10 | 0 | 0
1477.1 | 50.42 | 50.14 | -0.43 | -0.24412 | -2.4412 | 50.42 | -1 | -1 | -10 | -6.2206 | -6.2206 | 0 | 12 | 1 | 1 | -6.2206 | 10 | 0 | 0
1477.15 | 50.45 | 50.17 | -0.715 | -0.34412 | -3.4412 | 50.45 | -1 | -1 | -10 | -6.7206 | -6.7206 | 0 | 12 | 1 | 1 | -6.7206 | 10 | 0 | 0
1477.2 | 50.47 | 50.19 | -0.905 | -0.44412 | -4.4412 | 50.47 | -1 | -1 | -10 | -7.2206 | -7.2206 | 0 | 12 | 1 | 1 | -7.2206 | 10 | 0 | 0
1477.25 | 50.5 | 50.22 | -1 | -0.54412 | -5.4412 | 50.5 | -1 | -1 | -10 | -7.7206 | -7.7206 | 0 | 12 | 1 | 1 | -7.7206 | 10 | 0 | 0
1477.3 | 50.5 | 50.24 | -1 | -0.64412 | -6.4412 | 50.5 | -1 | -1 | -10 | -8.2206 | -8.2206 | 0 | 12 | 1 | 1 | -8.2206 | 10 | 0 | 0
1477.35 | 50.47 | 50.27 | -1 | -0.74412 | -7.4412 | 50.5 | -1 | -1 | -10 | -8.7206 | -8.7206 | 0 | 12 | 1 | 1 | -8.7206 | 10 | 0 | 0
1477.4 | 50.45 | 50.29 | -1 | -0.84412 | -8.4412 | 50.5 | -1 | -1 | -10 | -9.2206 | -9.2206 | 0 | 12 | 1 | 1 | -9.2206 | 10 | 0 | 0
1477.45 | 50.42 | 50.32 | -1 | -0.94412 | -9.4412 | 50.5 | -1 | -1 | -10 | -9.7206 | -9.7206 | 0 | 12 | 1 | 1 | -9.7206 | 10 | 0 | 0
1477.5 | 50.39 | 50.35 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1477.55 | 50.37 | 50.37 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1477.6 | 50.34 | 50.34 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1477.65 | 50.32 | 50.32 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1477.7 | 50.29 | 50.29 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1477.75 | 50.26 | 50.26 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1477.8 | 50.24 | 50.24 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1477.85 | 50.21 | 50.21 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1477.9 | 50.18 | 50.18 | -0.81 | -0.81 | -8.1 | 50.47 | -1 | -1 | -10 | -9.05 | -9.05 | 0 | 12 | 1 | 1 | -9.05 | 10 | 0 | 0
1477.95 | 50.16 | 50.16 | -0.62 | -0.62 | -6.2 | 50.45 | -1 | -1 | -10 | -8.1 | -8.1 | 0 | 12 | 1 | 1 | -8.1 | 10 | 0 | 0
1478 | 50.13 | 50.13 | -0.335 | -0.335 | -3.35 | 50.42 | -1 | -1 | -10 | -6.675 | -6.675 | 0 | 12 | 1 | 1 | -6.675 | 10 | 0 | 0
1478.05 | 50.11 | 50.11 | -0.145 | -0.145 | -1.45 | 50.39 | -1 | -1 | -10 | -5.725 | -5.725 | 0 | 12 | 1 | 1 | -5.725 | 10 | 0 | 0
1478.1 | 50.08 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 50.37 | -1 | -1 | -10 | -5.1912 | -5.1912 | 0 | 12 | 1 | 1 | -5.1912 | 10 | 0 | 0
1478.15 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.34 | -1 | -1 | -10 | -5.1029 | -5.1029 | 0 | 12 | 1 | 1 | -5.1029 | 10 | 0 | 0
1478.2 | 50.03 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 50.32 | -1 | -1 | -10 | -5.0441 | -5.0441 | 0 | 12 | 1 | 1 | -5.0441 | 10 | 0 | 0
1478.25 | 50 | 50 | 0 | 0 | 0 | 50.29 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1478.3 | 50 | 50 | 0 | 0 | 0 | 50.26 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1478.35 | 50 | 50 | 0 | 0 | 0 | 50.24 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1478.4 | 50 | 50 | 0 | 0 | 0 | 50.21 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1478.45 | 50 | 50 | 0 | 0 | 0 | 50.18 | -0.81 | -0.9 | -9 | -4.5 | -4.5 | 0 | 12 | 1 | 1 | -4.5 | 10 | 0 | 0
1478.5 | 50 | 50 | 0 | 0 | 0 | 50.16 | -0.62 | -0.8 | -8 | -4 | -4 | 0 | 12 | 1 | 1 | -4 | 10 | 0 | 0
1478.55 | 50 | 50 | 0 | 0 | 0 | 50.13 | -0.335 | -0.7 | -7 | -3.5 | -3.5 | 0 | 12 | 1 | 1 | -3.5 | 10 | 0 | 0
1478.6 | 50.01 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.6 | -6 | -3 | -3 | 0 | 12 | 1 | 1 | -3 | 10 | 0 | 0
1478.65 | 50.01 | 50 | 0 | 0 | 0 | 50.08 | -0.038235 | -0.5 | -5 | -2.5 | -2.5 | 0 | 12 | 1 | 1 | -2.5 | 10 | 0 | 0
1478.7 | 49.99 | 49.99 | 0 | 0 | 0 | 50.05 | -0.020588 | -0.4 | -4 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
1478.75 | 49.99 | 49.99 | 0 | 0 | 0 | 50.03 | -0.0088235 | -0.3 | -3 | -1.5 | -1.5 | 0 | 12 | 1 | 1 | -1.5 | 10 | 0 | 0
1478.8 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | -0.2 | -2 | -0.83824 | -0.83824 | 0 | 12 | 1 | 1 | -0.83824 | 10 | 0 | 0
1478.85 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | -0.1 | -1 | -0.33824 | -0.33824 | 0 | 12 | 1 | 1 | -0.33824 | 10 | 0 | 0
1478.9 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
1478.95 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
1479 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
1479.05 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
1479.1 | 49.89 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
1479.15 | 49.89 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
1479.2 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50.01 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1479.25 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1479.3 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1479.35 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 2.7868 | 2.7868 | 0 | 12 | 1 | 1 | 2.7868 | 10 | 0 | 0
1479.4 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 2.7868 | 2.7868 | 0 | 12 | 1 | 1 | 2.7868 | 10 | 0 | 0
1479.45 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 2.8456 | 2.8456 | 0 | 12 | 1 | 1 | 2.8456 | 10 | 0 | 0
1479.5 | 49.94 | 49.85 | 0.525 | 0.525 | 5.25 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 2.7574 | 2.7574 | 0 | 12 | 1 | 1 | 2.7574 | 10 | 0 | 0
1479.55 | 49.94 | 49.85 | 0.525 | 0.525 | 5.25 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 2.7574 | 2.7574 | 0 | 12 | 1 | 1 | 2.7574 | 10 | 0 | 0
1479.6 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1479.65 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1479.7 | 49.93 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1479.75 | 49.93 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1479.8 | 49.96 | 49.85 | 0.525 | 0.525 | 5.25 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 2.6985 | 2.6985 | 0 | 12 | 1 | 1 | 2.6985 | 10 | 0 | 0
1479.85 | 49.96 | 49.85 | 0.525 | 0.525 | 5.25 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 2.6985 | 2.6985 | 0 | 12 | 1 | 1 | 2.6985 | 10 | 0 | 0
1479.9 | 49.99 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1479.95 | 49.99 | 49.91 | 0.044118 | 0.425 | 4.25 | 49.99 | 0 | 0 | 0 | 2.125 | 2.125 | 0 | 12 | 1 | 1 | 2.125 | 10 | 0 | 0
1480 | 49.99 | 49.91 | 0.044118 | 0.325 | 3.25 | 49.99 | 0 | 0 | 0 | 1.625 | 1.625 | 0 | 12 | 1 | 1 | 1.625 | 10 | 0 | 0
1480.05 | 49.99 | 49.93 | 0.032353 | 0.225 | 2.25 | 49.99 | 0 | 0 | 0 | 1.125 | 1.125 | 0 | 12 | 1 | 1 | 1.125 | 10 | 0 | 0
1480.1 | 49.96 | 49.93 | 0.032353 | 0.125 | 1.25 | 49.99 | 0 | 0 | 0 | 0.625 | 0.625 | 0 | 12 | 1 | 1 | 0.625 | 10 | 0 | 0
1480.15 | 49.96 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 49.99 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1480.2 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1480.25 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1480.3 | 50.05 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.058824 | 0.058824 | 0 | 12 | 1 | 1 | 0.058824 | 10 | 0 | 0
1480.35 | 50.05 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
1480.4 | 49.97 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
1480.45 | 49.97 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
1480.5 | 49.92 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1480.55 | 49.92 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1480.6 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1480.65 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1480.7 | 49.94 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1480.75 | 49.94 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1480.8 | 50.01 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1480.85 | 50.01 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1480.9 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1480.95 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
1481 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
1481.05 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
1481.1 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
1481.15 | 49.95 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
1481.2 | 49.97 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
1481.25 | 49.97 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
1481.3 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
1481.35 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
1481.4 | 49.87 | 49.87 | 0.335 | 0.335 | 3.35 | 50.01 | 0 | 0 | 0 | 1.675 | 1.675 | 0 | 12 | 1 | 1 | 1.675 | 10 | 0 | 0
1481.45 | 49.87 | 49.87 | 0.335 | 0.335 | 3.35 | 49.99 | 0 | 0 | 0 | 1.675 | 1.675 | 0 | 12 | 1 | 1 | 1.675 | 10 | 0 | 0
1481.5 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1481.55 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 2.6691 | 2.6691 | 0 | 12 | 1 | 1 | 2.6691 | 10 | 0 | 0
1481.6 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1481.65 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1481.7 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1481.75 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1481.8 | 49.84 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1481.85 | 49.84 | 49.79 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
1481.9 | 49.89 | 49.79 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
1481.95 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.12647 | 1.2647 | 5.6324 | 5.6324 | 0 | 12 | 1 | 1 | 5.6324 | 10 | 0 | 0
1482 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.145 | 1.45 | 5.725 | 5.725 | 0 | 12 | 1 | 1 | 5.725 | 10 | 0 | 0
1482.05 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.145 | 1.45 | 5.725 | 5.725 | 0 | 12 | 1 | 1 | 5.725 | 10 | 0 | 0
1482.1 | 49.96 | 49.79 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
1482.15 | 49.96 | 49.79 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
1482.2 | 50.02 | 49.79 | 1 | 1 | 10 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 4.9853 | 4.9853 | 0 | 12 | 1 | 1 | 4.9853 | 10 | 0 | 0
1482.25 | 50.02 | 49.79 | 1 | 1 | 10 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 4.9853 | 4.9853 | 0 | 12 | 1 | 1 | 4.9853 | 10 | 0 | 0
1482.3 | 50.03 | 49.79 | 1 | 1 | 10 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.9559 | 4.9559 | 0 | 12 | 1 | 1 | 4.9559 | 10 | 0 | 0
1482.35 | 50.03 | 49.84 | 0.62 | 0.9 | 9 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.4559 | 4.4559 | 0 | 12 | 1 | 1 | 4.4559 | 10 | 0 | 0
1482.4 | 50.02 | 49.84 | 0.62 | 0.8 | 8 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 3.9559 | 3.9559 | 0 | 12 | 1 | 1 | 3.9559 | 10 | 0 | 0
1482.45 | 50.02 | 49.89 | 0.145 | 0.7 | 7 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 3.4559 | 3.4559 | 0 | 12 | 1 | 1 | 3.4559 | 10 | 0 | 0
1482.5 | 50.08 | 49.89 | 0.145 | 0.6 | 6 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 2.8088 | 2.8088 | 0 | 12 | 1 | 1 | 2.8088 | 10 | 0 | 0
1482.55 | 50.08 | 49.89 | 0.145 | 0.5 | 5 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 2.3088 | 2.3088 | 0 | 12 | 1 | 1 | 2.3088 | 10 | 0 | 0
1482.6 | 50.01 | 49.89 | 0.145 | 0.4 | 4 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 1.8088 | 1.8088 | 0 | 12 | 1 | 1 | 1.8088 | 10 | 0 | 0
1482.65 | 50.01 | 49.96 | 0.014706 | 0.3 | 3 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 1.3088 | 1.3088 | 0 | 12 | 1 | 1 | 1.3088 | 10 | 0 | 0
1482.7 | 49.94 | 49.94 | 0.026471 | 0.2 | 2 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.80882 | 0.80882 | 0 | 12 | 1 | 1 | 0.80882 | 10 | 0 | 0
1482.75 | 49.94 | 49.94 | 0.026471 | 0.1 | 1 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.30882 | 0.30882 | 0 | 12 | 1 | 1 | 0.30882 | 10 | 0 | 0
1482.8 | 50 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
1482.85 | 50 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
1482.9 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
1482.95 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
1483 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1483.05 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1483.1 | 49.92 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1483.15 | 49.92 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
1483.2 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50.01 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1483.25 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1483.3 | 49.92 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1483.35 | 49.92 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1483.4 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1483.45 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1483.5 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1483.55 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1483.6 | 49.87 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1483.65 | 49.87 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1483.7 | 49.8 | 49.8 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1483.75 | 49.8 | 49.8 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1483.8 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1483.85 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1483.9 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1483.95 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1484 | 49.72 | 49.72 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1484.05 | 49.72 | 49.72 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1484.1 | 49.67 | 49.67 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1484.15 | 49.67 | 49.67 | 1 | 1 | 10 | 49.87 | 0.335 | 0.14412 | 1.4412 | 5.7206 | 5.7206 | 0 | 12 | 1 | 1 | 5.7206 | 10 | 0 | 0
1484.2 | 49.65 | 49.65 | 1 | 1 | 10 | 49.87 | 0.335 | 0.24412 | 2.4412 | 6.2206 | 6.2206 | 0 | 12 | 1 | 1 | 6.2206 | 10 | 0 | 0
1484.25 | 49.65 | 49.65 | 1 | 1 | 10 | 49.8 | 1 | 0.34412 | 3.4412 | 6.7206 | 6.7206 | 0 | 12 | 1 | 1 | 6.7206 | 10 | 0 | 0
1484.3 | 49.59 | 49.59 | 1 | 1 | 10 | 49.8 | 1 | 0.44412 | 4.4412 | 7.2206 | 7.2206 | 0 | 12 | 1 | 1 | 7.2206 | 10 | 0 | 0
1484.35 | 49.59 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.54412 | 5.4412 | 7.7206 | 7.7206 | 0 | 12 | 1 | 1 | 7.7206 | 10 | 0 | 0
1484.4 | 49.66 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.64412 | 6.4412 | 8.2206 | 8.2206 | 0 | 12 | 1 | 1 | 8.2206 | 10 | 0 | 0
1484.45 | 49.66 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.74412 | 7.4412 | 8.7206 | 8.7206 | 0 | 12 | 1 | 1 | 8.7206 | 10 | 0 | 0
1484.5 | 49.63 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.84412 | 8.4412 | 9.2206 | 9.2206 | 0 | 12 | 1 | 1 | 9.2206 | 10 | 0 | 0
1484.55 | 49.63 | 49.59 | 1 | 1 | 10 | 49.72 | 1 | 0.94412 | 9.4412 | 9.7206 | 9.7206 | 0 | 12 | 1 | 1 | 9.7206 | 10 | 0 | 0
1484.6 | 49.61 | 49.59 | 1 | 1 | 10 | 49.72 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1484.65 | 49.61 | 49.59 | 1 | 1 | 10 | 49.67 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1484.7 | 49.54 | 49.54 | 1 | 1 | 10 | 49.67 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1484.75 | 49.54 | 49.54 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1484.8 | 49.46 | 49.46 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1484.85 | 49.46 | 49.46 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1484.9 | 49.45 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1484.95 | 49.45 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1485 | 49.51 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1485.05 | 49.51 | 49.45 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1485.1 | 49.5 | 49.45 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1485.15 | 49.5 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1485.2 | 49.54 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1485.25 | 49.54 | 49.45 | 1 | 1 | 10 | 49.54 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1485.3 | 49.59 | 49.45 | 1 | 1 | 10 | 49.59 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1485.35 | 49.59 | 49.45 | 1 | 1 | 10 | 49.59 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1485.4 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1485.45 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1485.5 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1485.55 | 49.61 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1485.6 | 49.53 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1485.65 | 49.53 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1485.7 | 49.54 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1485.75 | 49.54 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1485.8 | 49.61 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1485.85 | 49.61 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1485.9 | 49.66 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1485.95 | 49.66 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1486 | 49.64 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1486.05 | 49.64 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1486.1 | 49.69 | 49.53 | 1 | 1 | 10 | 49.69 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1486.15 | 49.69 | 49.53 | 1 | 1 | 10 | 49.69 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1486.2 | 49.74 | 49.53 | 1 | 1 | 10 | 49.74 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1486.25 | 49.74 | 49.54 | 1 | 1 | 10 | 49.74 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1486.3 | 49.78 | 49.54 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1486.35 | 49.78 | 49.61 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1486.4 | 49.82 | 49.61 | 1 | 1 | 10 | 49.82 | 0.81 | 0.81 | 8.1 | 9.05 | 9.05 | 0 | 12 | 1 | 1 | 9.05 | 10 | 0 | 0
1486.45 | 49.82 | 49.64 | 1 | 1 | 10 | 49.82 | 0.81 | 0.81 | 8.1 | 9.05 | 9.05 | 0 | 12 | 1 | 1 | 9.05 | 10 | 0 | 0
1486.5 | 49.86 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
1486.55 | 49.86 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
1486.6 | 49.84 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
1486.65 | 49.84 | 49.69 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
1486.7 | 49.91 | 49.69 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1486.75 | 49.91 | 49.74 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1486.8 | 49.97 | 49.74 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1486.85 | 49.97 | 49.78 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1486.9 | 50.03 | 49.78 | 1 | 1 | 10 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.9559 | 4.9559 | 0 | 12 | 1 | 1 | 4.9559 | 10 | 0 | 0
1486.95 | 50.03 | 49.82 | 0.81 | 0.9 | 9 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.4559 | 4.4559 | 0 | 12 | 1 | 1 | 4.4559 | 10 | 0 | 0
1487 | 50.05 | 49.82 | 0.81 | 0.81 | 8.1 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 3.9471 | 3.9471 | 0 | 12 | 1 | 1 | 3.9471 | 10 | 0 | 0
1487.05 | 50.05 | 49.84 | 0.62 | 0.71 | 7.1 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 3.4471 | 3.4471 | 0 | 12 | 1 | 1 | 3.4471 | 10 | 0 | 0
1487.1 | 50.01 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
1487.15 | 50.01 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
1487.2 | 49.95 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
1487.25 | 49.95 | 49.91 | 0.044118 | 0.52 | 5.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.4971 | 2.4971 | 0 | 12 | 1 | 1 | 2.4971 | 10 | 0 | 0
1487.3 | 49.99 | 49.91 | 0.044118 | 0.42 | 4.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 1.9971 | 1.9971 | 0 | 12 | 1 | 1 | 1.9971 | 10 | 0 | 0
1487.35 | 49.99 | 49.95 | 0.020588 | 0.32 | 3.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 1.4971 | 1.4971 | 0 | 12 | 1 | 1 | 1.4971 | 10 | 0 | 0
1487.4 | 49.92 | 49.92 | 0.038235 | 0.22 | 2.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.99706 | 0.99706 | 0 | 12 | 1 | 1 | 0.99706 | 10 | 0 | 0
1487.45 | 49.92 | 49.92 | 0.038235 | 0.12 | 1.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.49706 | 0.49706 | 0 | 12 | 1 | 1 | 0.49706 | 10 | 0 | 0
1487.5 | 49.97 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1487.55 | 49.97 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1487.6 | 50.02 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1487.65 | 50.02 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.17647 | 0.17647 | 0 | 12 | 1 | 1 | 0.17647 | 10 | 0 | 0
1487.7 | 50.07 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1487.75 | 50.07 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1487.8 | 50.06 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1487.85 | 50.06 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1487.9 | 50.13 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
1487.95 | 50.13 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
1488 | 50.09 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
1488.05 | 50.09 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6309 | -1.6309 | 0 | 12 | 1 | 1 | -1.6309 | 10 | 0 | 0
1488.1 | 50.07 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6309 | -1.6309 | 0 | 12 | 1 | 1 | -1.6309 | 10 | 0 | 0
1488.15 | 50.07 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6897 | -1.6897 | 0 | 12 | 1 | 1 | -1.6897 | 10 | 0 | 0
1488.2 | 50.07 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6897 | -1.6897 | 0 | 12 | 1 | 1 | -1.6897 | 10 | 0 | 0
1488.25 | 50.07 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.13 | -0.335 | -0.335 | -3.35 | -1.8074 | -1.8074 | 0 | 12 | 1 | 1 | -1.8074 | 10 | 0 | 0
1488.3 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.13 | -0.335 | -0.335 | -3.35 | -1.7779 | -1.7779 | 0 | 12 | 1 | 1 | -1.7779 | 10 | 0 | 0
1488.35 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.13 | -0.335 | -0.335 | -3.35 | -1.7779 | -1.7779 | 0 | 12 | 1 | 1 | -1.7779 | 10 | 0 | 0
1488.4 | 50.01 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
1488.45 | 50.01 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
1488.5 | 50.07 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
1488.55 | 50.07 | 50.01 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.235 | -2.35 | -1.175 | -1.175 | 0 | 12 | 1 | 1 | -1.175 | 10 | 0 | 0
1488.6 | 50.05 | 50.01 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.135 | -1.35 | -0.675 | -0.675 | 0 | 12 | 1 | 1 | -0.675 | 10 | 0 | 0
1488.65 | 50.05 | 50.01 | 0 | 0 | 0 | 50.07 | -0.032353 | -0.035 | -0.35 | -0.175 | -0.175 | 0 | 12 | 1 | 1 | -0.175 | 10 | 0 | 0
1488.7 | 50.1 | 50.01 | 0 | 0 | 0 | 50.1 | -0.05 | -0.05 | -0.5 | -0.25 | -0.25 | 0 | 12 | 1 | 1 | -0.25 | 10 | 0 | 0
1488.75 | 50.1 | 50.01 | 0 | 0 | 0 | 50.1 | -0.05 | -0.05 | -0.5 | -0.25 | -0.25 | 0 | 12 | 1 | 1 | -0.25 | 10 | 0 | 0
1488.8 | 50.11 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1488.85 | 50.11 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1488.9 | 50.06 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1488.95 | 50.06 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1489 | 50.04 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1489.05 | 50.04 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1489.1 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1489.15 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1489.2 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1489.25 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1489.3 | 50.11 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1489.35 | 50.11 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1489.4 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1489.45 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1489.5 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1489.55 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1489.6 | 50.02 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.11 | -0.145 | -0.145 | -1.45 | -0.73971 | -0.73971 | 0 | 12 | 1 | 1 | -0.73971 | 10 | 0 | 0
1489.65 | 50.02 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.11 | -0.145 | -0.145 | -1.45 | -0.73971 | -0.73971 | 0 | 12 | 1 | 1 | -0.73971 | 10 | 0 | 0
1489.7 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1489.75 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1489.8 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1489.85 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1489.9 | 50.01 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1489.95 | 50.01 | 50 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.045 | -0.45 | -0.225 | -0.225 | 0 | 12 | 1 | 1 | -0.225 | 10 | 0 | 0
1490 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
1490.05 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
1490.1 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
1490.15 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1490.2 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.14706 | 0.14706 | 0 | 12 | 1 | 1 | 0.14706 | 10 | 0 | 0
1490.25 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1490.3 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1490.35 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1490.4 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1490.45 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1490.5 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1490.55 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1490.6 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1490.65 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1490.7 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1490.75 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1490.8 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1490.85 | 50 | 50 | 0 | 0 | 0 | 50.01 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1490.9 | 49.5 | 49.5 | 1 | 1 | 10 | 50.01 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1490.95 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1491 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1491.05 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1491.1 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1491.15 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1491.2 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1491.25 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1491.3 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1491.35 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1491.4 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1491.45 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.1 | 1 | 5.5 | 5.5 | 0 | 12 | 1 | 1 | 5.5 | 10 | 0 | 0
1491.5 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.2 | 2 | 6 | 6 | 0 | 12 | 1 | 1 | 6 | 10 | 0 | 0
1491.55 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.3 | 3 | 6.5 | 6.5 | 0 | 12 | 1 | 1 | 6.5 | 10 | 0 | 0
1491.6 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.4 | 4 | 7 | 7 | 0 | 12 | 1 | 1 | 7 | 10 | 0 | 0
1491.65 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.5 | 5 | 7.5 | 7.5 | 0 | 12 | 1 | 1 | 7.5 | 10 | 0 | 0
1491.7 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.6 | 6 | 8 | 8 | 0 | 12 | 1 | 1 | 8 | 10 | 0 | 0
1491.75 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.7 | 7 | 8.5 | 8.5 | 0 | 12 | 1 | 1 | 8.5 | 10 | 0 | 0
1491.8 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.8 | 8 | 9 | 9 | 0 | 12 | 1 | 1 | 9 | 10 | 0 | 0
1491.85 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.9 | 9 | 9.5 | 9.5 | 0 | 12 | 1 | 1 | 9.5 | 10 | 0 | 0
1491.9 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1491.95 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1492 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1492.05 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1492.1 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1492.15 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1492.2 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1492.25 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1492.3 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1492.35 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1492.4 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1492.45 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1492.5 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1492.55 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1492.6 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1492.65 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1492.7 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1492.75 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1492.8 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1492.85 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1492.9 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1492.95 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1493 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1493.05 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1493.1 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1493.15 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1493.2 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1493.25 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1493.3 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1493.35 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1493.4 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1493.45 | 50.5 | 50.5 | -1 | 0.9 | 9 | 50.5 | -1 | -1 | -10 | -0.5 | -0.5 | 0 | 12 | 1 | 1 | -0.5 | 10 | 0 | 0
1493.5 | 50.5 | 50.5 | -1 | 0.8 | 8 | 50.5 | -1 | -1 | -10 | -1 | -1 | 0 | 12 | 1 | 1 | -1 | 10 | 0 | 0
1493.55 | 50.5 | 50.5 | -1 | 0.7 | 7 | 50.5 | -1 | -1 | -10 | -1.5 | -1.5 | 0 | 12 | 1 | 1 | -1.5 | 10 | 0 | 0
1493.6 | 50.5 | 50.5 | -1 | 0.6 | 6 | 50.5 | -1 | -1 | -10 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
1493.65 | 50.5 | 50.5 | -1 | 0.5 | 5 | 50.5 | -1 | -1 | -10 | -2.5 | -2.5 | 0 | 12 | 1 | 1 | -2.5 | 10 | 0 | 0
1493.7 | 50.5 | 50.5 | -1 | 0.4 | 4 | 50.5 | -1 | -1 | -10 | -3 | -3 | 0 | 12 | 1 | 1 | -3 | 10 | 0 | 0
1493.75 | 50.5 | 50.5 | -1 | 0.3 | 3 | 50.5 | -1 | -1 | -10 | -3.5 | -3.5 | 0 | 12 | 1 | 1 | -3.5 | 10 | 0 | 0
1493.8 | 50.5 | 50.5 | -1 | 0.2 | 2 | 50.5 | -1 | -1 | -10 | -4 | -4 | 0 | 12 | 1 | 1 | -4 | 10 | 0 | 0
1493.85 | 50.5 | 50.5 | -1 | 0.1 | 1 | 50.5 | -1 | -1 | -10 | -4.5 | -4.5 | 0 | 12 | 1 | 1 | -4.5 | 10 | 0 | 0
1493.9 | 50.5 | 50.5 | -1 | 0 | 0 | 50.5 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1493.95 | 50.5 | 50.5 | -1 | -0.1 | -1 | 50.5 | -1 | -1 | -10 | -5.5 | -5.5 | 0 | 12 | 1 | 1 | -5.5 | 10 | 0 | 0
1494 | 50.5 | 50.5 | -1 | -0.2 | -2 | 50.5 | -1 | -1 | -10 | -6 | -6 | 0 | 12 | 1 | 1 | -6 | 10 | 0 | 0
1494.05 | 50.5 | 50.5 | -1 | -0.3 | -3 | 50.5 | -1 | -1 | -10 | -6.5 | -6.5 | 0 | 12 | 1 | 1 | -6.5 | 10 | 0 | 0
1494.1 | 50.5 | 50.5 | -1 | -0.4 | -4 | 50.5 | -1 | -1 | -10 | -7 | -7 | 0 | 12 | 1 | 1 | -7 | 10 | 0 | 0
1494.15 | 50.5 | 50.5 | -1 | -0.5 | -5 | 50.5 | -1 | -1 | -10 | -7.5 | -7.5 | 0 | 12 | 1 | 1 | -7.5 | 10 | 0 | 0
1494.2 | 50.5 | 50.5 | -1 | -0.6 | -6 | 50.5 | -1 | -1 | -10 | -8 | -8 | 0 | 12 | 1 | 1 | -8 | 10 | 0 | 0
1494.25 | 50.5 | 50.5 | -1 | -0.7 | -7 | 50.5 | -1 | -1 | -10 | -8.5 | -8.5 | 0 | 12 | 1 | 1 | -8.5 | 10 | 0 | 0
1494.3 | 50.5 | 50.5 | -1 | -0.8 | -8 | 50.5 | -1 | -1 | -10 | -9 | -9 | 0 | 12 | 1 | 1 | -9 | 10 | 0 | 0
1494.35 | 50.5 | 50.5 | -1 | -0.9 | -9 | 50.5 | -1 | -1 | -10 | -9.5 | -9.5 | 0 | 12 | 1 | 1 | -9.5 | 10 | 0 | 0
1494.4 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1494.45 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1494.5 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1494.55 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1494.6 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1494.65 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1494.7 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1494.75 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1494.8 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1494.85 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1494.9 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1494.95 | 50.47 | 50.47 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1495 | 50.45 | 50.45 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1495.05 | 50.42 | 50.42 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1495.1 | 50.4 | 50.4 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1495.15 | 50.37 | 50.37 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1495.2 | 50.35 | 50.35 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1495.25 | 50.32 | 50.32 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1495.3 | 50.29 | 50.29 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1495.35 | 50.27 | 50.27 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1495.4 | 50.24 | 50.24 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1495.45 | 50.22 | 50.22 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1495.5 | 50.19 | 50.19 | -0.905 | -0.905 | -9.05 | 50.47 | -1 | -1 | -10 | -9.525 | -9.525 | 0 | 12 | 1 | 1 | -9.525 | 10 | 0 | 0
1495.55 | 50.17 | 50.17 | -0.715 | -0.715 | -7.15 | 50.45 | -1 | -1 | -10 | -8.575 | -8.575 | 0 | 12 | 1 | 1 | -8.575 | 10 | 0 | 0
1495.6 | 50.14 | 50.14 | -0.43 | -0.43 | -4.3 | 50.42 | -1 | -1 | -10 | -7.15 | -7.15 | 0 | 12 | 1 | 1 | -7.15 | 10 | 0 | 0
1495.65 | 50.12 | 50.12 | -0.24 | -0.24 | -2.4 | 50.4 | -1 | -1 | -10 | -6.2 | -6.2 | 0 | 12 | 1 | 1 | -6.2 | 10 | 0 | 0
1495.7 | 50.09 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 50.37 | -1 | -1 | -10 | -5.2206 | -5.2206 | 0 | 12 | 1 | 1 | -5.2206 | 10 | 0 | 0
1495.75 | 50.06 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.35 | -1 | -1 | -10 | -5.1324 | -5.1324 | 0 | 12 | 1 | 1 | -5.1324 | 10 | 0 | 0
1495.8 | 50.04 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.32 | -1 | -1 | -10 | -5.0735 | -5.0735 | 0 | 12 | 1 | 1 | -5.0735 | 10 | 0 | 0
1495.85 | 50.01 | 50.01 | 0 | 0 | 0 | 50.29 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1495.9 | 49.99 | 49.99 | 0 | 0 | 0 | 50.27 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1495.95 | 49.96 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.24 | -1 | -1 | -10 | -4.9265 | -4.9265 | 0 | 12 | 1 | 1 | -4.9265 | 10 | 0 | 0
1496 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.22 | -1 | -1 | -10 | -4.8676 | -4.8676 | 0 | 12 | 1 | 1 | -4.8676 | 10 | 0 | 0
1496.05 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.19 | -0.905 | -0.905 | -9.05 | -4.3044 | -4.3044 | 0 | 12 | 1 | 1 | -4.3044 | 10 | 0 | 0
1496.1 | 49.88 | 49.88 | 0.24 | 0.24 | 2.4 | 50.17 | -0.715 | -0.805 | -8.05 | -2.825 | -2.825 | 0 | 12 | 1 | 1 | -2.825 | 10 | 0 | 0
1496.15 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.14 | -0.43 | -0.705 | -7.05 | -1.375 | -1.375 | 0 | 12 | 1 | 1 | -1.375 | 10 | 0 | 0
1496.2 | 49.83 | 49.83 | 0.715 | 0.715 | 7.15 | 50.12 | -0.24 | -0.605 | -6.05 | 0.55 | 0.55 | 0 | 12 | 1 | 1 | 0.55 | 10 | 0 | 0
1496.25 | 49.81 | 49.81 | 0.905 | 0.905 | 9.05 | 50.09 | -0.044118 | -0.505 | -5.05 | 2 | 2 | 0 | 12 | 1 | 1 | 2 | 10 | 0 | 0
1496.3 | 49.78 | 49.78 | 1 | 1 | 10 | 50.06 | -0.026471 | -0.405 | -4.05 | 2.975 | 2.975 | 0 | 12 | 1 | 1 | 2.975 | 10 | 0 | 0
1496.35 | 49.76 | 49.76 | 1 | 1 | 10 | 50.04 | -0.014706 | -0.305 | -3.05 | 3.475 | 3.475 | 0 | 12 | 1 | 1 | 3.475 | 10 | 0 | 0
1496.4 | 49.73 | 49.73 | 1 | 1 | 10 | 50.01 | 0 | -0.205 | -2.05 | 3.975 | 3.975 | 0 | 12 | 1 | 1 | 3.975 | 10 | 0 | 0
1496.45 | 49.71 | 49.71 | 1 | 1 | 10 | 49.99 | 0 | -0.105 | -1.05 | 4.475 | 4.475 | 0 | 12 | 1 | 1 | 4.475 | 10 | 0 | 0
1496.5 | 49.68 | 49.68 | 1 | 1 | 10 | 49.96 | 0.014706 | -0.005 | -0.05 | 4.975 | 4.975 | 0 | 12 | 1 | 1 | 4.975 | 10 | 0 | 0
1496.55 | 49.65 | 49.65 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
1496.6 | 49.63 | 49.63 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1496.65 | 49.6 | 49.6 | 1 | 1 | 10 | 49.88 | 0.24 | 0.14412 | 1.4412 | 5.7206 | 5.7206 | 0 | 12 | 1 | 1 | 5.7206 | 10 | 0 | 0
1496.7 | 49.58 | 49.58 | 1 | 1 | 10 | 49.86 | 0.43 | 0.24412 | 2.4412 | 6.2206 | 6.2206 | 0 | 12 | 1 | 1 | 6.2206 | 10 | 0 | 0
1496.75 | 49.55 | 49.55 | 1 | 1 | 10 | 49.83 | 0.715 | 0.34412 | 3.4412 | 6.7206 | 6.7206 | 0 | 12 | 1 | 1 | 6.7206 | 10 | 0 | 0
1496.8 | 49.53 | 49.53 | 1 | 1 | 10 | 49.81 | 0.905 | 0.44412 | 4.4412 | 7.2206 | 7.2206 | 0 | 12 | 1 | 1 | 7.2206 | 10 | 0 | 0
1496.85 | 49.5 | 49.5 | 1 | 1 | 10 | 49.78 | 1 | 0.54412 | 5.4412 | 7.7206 | 7.7206 | 0 | 12 | 1 | 1 | 7.7206 | 10 | 0 | 0
1496.9 | 49.5 | 49.5 | 1 | 1 | 10 | 49.76 | 1 | 0.64412 | 6.4412 | 8.2206 | 8.2206 | 0 | 12 | 1 | 1 | 8.2206 | 10 | 0 | 0
1496.95 | 49.53 | 49.5 | 1 | 1 | 10 | 49.73 | 1 | 0.74412 | 7.4412 | 8.7206 | 8.7206 | 0 | 12 | 1 | 1 | 8.7206 | 10 | 0 | 0
1497 | 49.55 | 49.5 | 1 | 1 | 10 | 49.71 | 1 | 0.84412 | 8.4412 | 9.2206 | 9.2206 | 0 | 12 | 1 | 1 | 9.2206 | 10 | 0 | 0
1497.05 | 49.58 | 49.5 | 1 | 1 | 10 | 49.68 | 1 | 0.94412 | 9.4412 | 9.7206 | 9.7206 | 0 | 12 | 1 | 1 | 9.7206 | 10 | 0 | 0
1497.1 | 49.6 | 49.5 | 1 | 1 | 10 | 49.65 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1497.15 | 49.63 | 49.5 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1497.2 | 49.65 | 49.5 | 1 | 1 | 10 | 49.65 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1497.25 | 49.68 | 49.5 | 1 | 1 | 10 | 49.68 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1497.3 | 49.71 | 49.5 | 1 | 1 | 10 | 49.71 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1497.35 | 49.73 | 49.5 | 1 | 1 | 10 | 49.73 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1497.4 | 49.76 | 49.5 | 1 | 1 | 10 | 49.76 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1497.45 | 49.78 | 49.5 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1497.5 | 49.81 | 49.53 | 1 | 1 | 10 | 49.81 | 0.905 | 0.905 | 9.05 | 9.525 | 9.525 | 0 | 12 | 1 | 1 | 9.525 | 10 | 0 | 0
1497.55 | 49.83 | 49.55 | 1 | 1 | 10 | 49.83 | 0.715 | 0.715 | 7.15 | 8.575 | 8.575 | 0 | 12 | 1 | 1 | 8.575 | 10 | 0 | 0
1497.6 | 49.86 | 49.58 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
1497.65 | 49.88 | 49.6 | 1 | 1 | 10 | 49.88 | 0.24 | 0.24 | 2.4 | 6.2 | 6.2 | 0 | 12 | 1 | 1 | 6.2 | 10 | 0 | 0
1497.7 | 49.91 | 49.63 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1497.75 | 49.94 | 49.65 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
1497.8 | 49.96 | 49.68 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
1497.85 | 49.99 | 49.71 | 1 | 1 | 10 | 49.99 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1497.9 | 50.01 | 49.73 | 1 | 1 | 10 | 50.01 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1497.95 | 50.04 | 49.76 | 1 | 1 | 10 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 4.9265 | 4.9265 | 0 | 12 | 1 | 1 | 4.9265 | 10 | 0 | 0
1498 | 50.06 | 49.78 | 1 | 1 | 10 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 4.8676 | 4.8676 | 0 | 12 | 1 | 1 | 4.8676 | 10 | 0 | 0
1498.05 | 50.09 | 49.81 | 0.905 | 0.905 | 9.05 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 4.3044 | 4.3044 | 0 | 12 | 1 | 1 | 4.3044 | 10 | 0 | 0
1498.1 | 50.12 | 49.83 | 0.715 | 0.805 | 8.05 | 50.12 | -0.24 | -0.24 | -2.4 | 2.825 | 2.825 | 0 | 12 | 1 | 1 | 2.825 | 10 | 0 | 0
1498.15 | 50.14 | 49.86 | 0.43 | 0.705 | 7.05 | 50.14 | -0.43 | -0.43 | -4.3 | 1.375 | 1.375 | 0 | 12 | 1 | 1 | 1.375 | 10 | 0 | 0
1498.2 | 50.17 | 49.88 | 0.24 | 0.605 | 6.05 | 50.17 | -0.715 | -0.715 | -7.15 | -0.55 | -0.55 | 0 | 12 | 1 | 1 | -0.55 | 10 | 0 | 0
1498.25 | 50.19 | 49.91 | 0.044118 | 0.505 | 5.05 | 50.19 | -0.905 | -0.905 | -9.05 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
1498.3 | 50.22 | 49.94 | 0.026471 | 0.405 | 4.05 | 50.22 | -1 | -1 | -10 | -2.975 | -2.975 | 0 | 12 | 1 | 1 | -2.975 | 10 | 0 | 0
1498.35 | 50.24 | 49.96 | 0.014706 | 0.305 | 3.05 | 50.24 | -1 | -1 | -10 | -3.475 | -3.475 | 0 | 12 | 1 | 1 | -3.475 | 10 | 0 | 0
1498.4 | 50.27 | 49.99 | 0 | 0.205 | 2.05 | 50.27 | -1 | -1 | -10 | -3.975 | -3.975 | 0 | 12 | 1 | 1 | -3.975 | 10 | 0 | 0
1498.45 | 50.29 | 50.01 | 0 | 0.105 | 1.05 | 50.29 | -1 | -1 | -10 | -4.475 | -4.475 | 0 | 12 | 1 | 1 | -4.475 | 10 | 0 | 0
1498.5 | 50.32 | 50.04 | -0.014706 | 0.005 | 0.05 | 50.32 | -1 | -1 | -10 | -4.975 | -4.975 | 0 | 12 | 1 | 1 | -4.975 | 10 | 0 | 0
1498.55 | 50.35 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.35 | -1 | -1 | -10 | -5.1324 | -5.1324 | 0 | 12 | 1 | 1 | -5.1324 | 10 | 0 | 0
1498.6 | 50.37 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 50.37 | -1 | -1 | -10 | -5.2206 | -5.2206 | 0 | 12 | 1 | 1 | -5.2206 | 10 | 0 | 0
1498.65 | 50.4 | 50.12 | -0.24 | -0.14412 | -1.4412 | 50.4 | -1 | -1 | -10 | -5.7206 | -5.7206 | 0 | 12 | 1 | 1 | -5.7206 | 10 | 0 | 0
1498.7 | 50.42 | 50.14 | -0.43 | -0.24412 | -2.4412 | 50.42 | -1 | -1 | -10 | -6.2206 | -6.2206 | 0 | 12 | 1 | 1 | -6.2206 | 10 | 0 | 0
1498.75 | 50.45 | 50.17 | -0.715 | -0.34412 | -3.4412 | 50.45 | -1 | -1 | -10 | -6.7206 | -6.7206 | 0 | 12 | 1 | 1 | -6.7206 | 10 | 0 | 0
1498.8 | 50.47 | 50.19 | -0.905 | -0.44412 | -4.4412 | 50.47 | -1 | -1 | -10 | -7.2206 | -7.2206 | 0 | 12 | 1 | 1 | -7.2206 | 10 | 0 | 0
1498.85 | 50.5 | 50.22 | -1 | -0.54412 | -5.4412 | 50.5 | -1 | -1 | -10 | -7.7206 | -7.7206 | 0 | 12 | 1 | 1 | -7.7206 | 10 | 0 | 0
1498.9 | 50.5 | 50.24 | -1 | -0.64412 | -6.4412 | 50.5 | -1 | -1 | -10 | -8.2206 | -8.2206 | 0 | 12 | 1 | 1 | -8.2206 | 10 | 0 | 0
1498.95 | 50.47 | 50.27 | -1 | -0.74412 | -7.4412 | 50.5 | -1 | -1 | -10 | -8.7206 | -8.7206 | 0 | 12 | 1 | 1 | -8.7206 | 10 | 0 | 0
1499 | 50.45 | 50.29 | -1 | -0.84412 | -8.4412 | 50.5 | -1 | -1 | -10 | -9.2206 | -9.2206 | 0 | 12 | 1 | 1 | -9.2206 | 10 | 0 | 0
1499.05 | 50.42 | 50.32 | -1 | -0.94412 | -9.4412 | 50.5 | -1 | -1 | -10 | -9.7206 | -9.7206 | 0 | 12 | 1 | 1 | -9.7206 | 10 | 0 | 0
1499.1 | 50.39 | 50.35 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1499.15 | 50.37 | 50.37 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1499.2 | 50.34 | 50.34 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1499.25 | 50.32 | 50.32 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1499.3 | 50.29 | 50.29 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1499.35 | 50.26 | 50.26 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1499.4 | 50.24 | 50.24 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1499.45 | 50.21 | 50.21 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1499.5 | 50.18 | 50.18 | -0.81 | -0.81 | -8.1 | 50.47 | -1 | -1 | -10 | -9.05 | -9.05 | 0 | 12 | 1 | 1 | -9.05 | 10 | 0 | 0
1499.55 | 50.16 | 50.16 | -0.62 | -0.62 | -6.2 | 50.45 | -1 | -1 | -10 | -8.1 | -8.1 | 0 | 12 | 1 | 1 | -8.1 | 10 | 0 | 0
1499.6 | 50.13 | 50.13 | -0.335 | -0.335 | -3.35 | 50.42 | -1 | -1 | -10 | -6.675 | -6.675 | 0 | 12 | 1 | 1 | -6.675 | 10 | 0 | 0
1499.65 | 50.11 | 50.11 | -0.145 | -0.145 | -1.45 | 50.39 | -1 | -1 | -10 | -5.725 | -5.725 | 0 | 12 | 1 | 1 | -5.725 | 10 | 0 | 0
1499.7 | 50.08 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 50.37 | -1 | -1 | -10 | -5.1912 | -5.1912 | 0 | 12 | 1 | 1 | -5.1912 | 10 | 0 | 0
1499.75 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.34 | -1 | -1 | -10 | -5.1029 | -5.1029 | 0 | 12 | 1 | 1 | -5.1029 | 10 | 0 | 0
1499.8 | 50.03 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 50.32 | -1 | -1 | -10 | -5.0441 | -5.0441 | 0 | 12 | 1 | 1 | -5.0441 | 10 | 0 | 0
1499.85 | 50 | 50 | 0 | 0 | 0 | 50.29 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1499.9 | 50 | 50 | 0 | 0 | 0 | 50.26 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1499.95 | 50 | 50 | 0 | 0 | 0 | 50.24 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1500 | 50 | 50 | 0 | 0 | 0 | 50.21 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1500.05 | 50 | 50 | 0 | 0 | 0 | 50.18 | -0.81 | -0.9 | -9 | -4.5 | -4.5 | 0 | 12 | 1 | 1 | -4.5 | 10 | 0 | 0
1500.1 | 50 | 50 | 0 | 0 | 0 | 50.16 | -0.62 | -0.8 | -8 | -4 | -4 | 0 | 12 | 1 | 1 | -4 | 10 | 0 | 0
1500.15 | 50 | 50 | 0 | 0 | 0 | 50.13 | -0.335 | -0.7 | -7 | -3.5 | -3.5 | 0 | 12 | 1 | 1 | -3.5 | 10 | 0 | 0
1500.2 | 50.01 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.6 | -6 | -3 | -3 | 0 | 12 | 1 | 1 | -3 | 10 | 0 | 0
1500.25 | 50.01 | 50 | 0 | 0 | 0 | 50.08 | -0.038235 | -0.5 | -5 | -2.5 | -2.5 | 0 | 12 | 1 | 1 | -2.5 | 10 | 0 | 0
1500.3 | 49.99 | 49.99 | 0 | 0 | 0 | 50.05 | -0.020588 | -0.4 | -4 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
1500.35 | 49.99 | 49.99 | 0 | 0 | 0 | 50.03 | -0.0088235 | -0.3 | -3 | -1.5 | -1.5 | 0 | 12 | 1 | 1 | -1.5 | 10 | 0 | 0
1500.4 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | -0.2 | -2 | -0.83824 | -0.83824 | 0 | 12 | 1 | 1 | -0.83824 | 10 | 0 | 0
1500.45 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | -0.1 | -1 | -0.33824 | -0.33824 | 0 | 12 | 1 | 1 | -0.33824 | 10 | 0 | 0
1500.5 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
1500.55 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
1500.6 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
1500.65 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
1500.7 | 49.89 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
1500.75 | 49.89 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
1500.8 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50.01 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1500.85 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1500.9 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1500.95 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 2.7868 | 2.7868 | 0 | 12 | 1 | 1 | 2.7868 | 10 | 0 | 0
1501 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 2.7868 | 2.7868 | 0 | 12 | 1 | 1 | 2.7868 | 10 | 0 | 0
1501.05 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 2.8456 | 2.8456 | 0 | 12 | 1 | 1 | 2.8456 | 10 | 0 | 0
1501.1 | 49.94 | 49.85 | 0.525 | 0.525 | 5.25 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 2.7574 | 2.7574 | 0 | 12 | 1 | 1 | 2.7574 | 10 | 0 | 0
1501.15 | 49.94 | 49.85 | 0.525 | 0.525 | 5.25 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 2.7574 | 2.7574 | 0 | 12 | 1 | 1 | 2.7574 | 10 | 0 | 0
1501.2 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1501.25 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1501.3 | 49.93 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1501.35 | 49.93 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1501.4 | 49.96 | 49.85 | 0.525 | 0.525 | 5.25 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 2.6985 | 2.6985 | 0 | 12 | 1 | 1 | 2.6985 | 10 | 0 | 0
1501.45 | 49.96 | 49.85 | 0.525 | 0.525 | 5.25 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 2.6985 | 2.6985 | 0 | 12 | 1 | 1 | 2.6985 | 10 | 0 | 0
1501.5 | 49.99 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1501.55 | 49.99 | 49.91 | 0.044118 | 0.425 | 4.25 | 49.99 | 0 | 0 | 0 | 2.125 | 2.125 | 0 | 12 | 1 | 1 | 2.125 | 10 | 0 | 0
1501.6 | 49.99 | 49.91 | 0.044118 | 0.325 | 3.25 | 49.99 | 0 | 0 | 0 | 1.625 | 1.625 | 0 | 12 | 1 | 1 | 1.625 | 10 | 0 | 0
1501.65 | 49.99 | 49.93 | 0.032353 | 0.225 | 2.25 | 49.99 | 0 | 0 | 0 | 1.125 | 1.125 | 0 | 12 | 1 | 1 | 1.125 | 10 | 0 | 0
1501.7 | 49.96 | 49.93 | 0.032353 | 0.125 | 1.25 | 49.99 | 0 | 0 | 0 | 0.625 | 0.625 | 0 | 12 | 1 | 1 | 0.625 | 10 | 0 | 0
1501.75 | 49.96 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 49.99 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1501.8 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1501.85 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1501.9 | 50.05 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.058824 | 0.058824 | 0 | 12 | 1 | 1 | 0.058824 | 10 | 0 | 0
1501.95 | 50.05 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
1502 | 49.97 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
1502.05 | 49.97 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
1502.1 | 49.92 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1502.15 | 49.92 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1502.2 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1502.25 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1502.3 | 49.94 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1502.35 | 49.94 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1502.4 | 50.01 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1502.45 | 50.01 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1502.5 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1502.55 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
1502.6 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
1502.65 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
1502.7 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
1502.75 | 49.95 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
1502.8 | 49.97 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
1502.85 | 49.97 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
1502.9 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
1502.95 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
1503 | 49.87 | 49.87 | 0.335 | 0.335 | 3.35 | 50.01 | 0 | 0 | 0 | 1.675 | 1.675 | 0 | 12 | 1 | 1 | 1.675 | 10 | 0 | 0
1503.05 | 49.87 | 49.87 | 0.335 | 0.335 | 3.35 | 49.99 | 0 | 0 | 0 | 1.675 | 1.675 | 0 | 12 | 1 | 1 | 1.675 | 10 | 0 | 0
1503.1 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1503.15 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 2.6691 | 2.6691 | 0 | 12 | 1 | 1 | 2.6691 | 10 | 0 | 0
1503.2 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1503.25 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1503.3 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1503.35 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1503.4 | 49.84 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1503.45 | 49.84 | 49.79 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
1503.5 | 49.89 | 49.79 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
1503.55 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.12647 | 1.2647 | 5.6324 | 5.6324 | 0 | 12 | 1 | 1 | 5.6324 | 10 | 0 | 0
1503.6 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.145 | 1.45 | 5.725 | 5.725 | 0 | 12 | 1 | 1 | 5.725 | 10 | 0 | 0
1503.65 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.145 | 1.45 | 5.725 | 5.725 | 0 | 12 | 1 | 1 | 5.725 | 10 | 0 | 0
1503.7 | 49.96 | 49.79 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
1503.75 | 49.96 | 49.79 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
1503.8 | 50.02 | 49.79 | 1 | 1 | 10 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 4.9853 | 4.9853 | 0 | 12 | 1 | 1 | 4.9853 | 10 | 0 | 0
1503.85 | 50.02 | 49.79 | 1 | 1 | 10 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 4.9853 | 4.9853 | 0 | 12 | 1 | 1 | 4.9853 | 10 | 0 | 0
1503.9 | 50.03 | 49.79 | 1 | 1 | 10 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.9559 | 4.9559 | 0 | 12 | 1 | 1 | 4.9559 | 10 | 0 | 0
1503.95 | 50.03 | 49.84 | 0.62 | 0.9 | 9 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.4559 | 4.4559 | 0 | 12 | 1 | 1 | 4.4559 | 10 | 0 | 0
1504 | 50.02 | 49.84 | 0.62 | 0.8 | 8 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 3.9559 | 3.9559 | 0 | 12 | 1 | 1 | 3.9559 | 10 | 0 | 0
1504.05 | 50.02 | 49.89 | 0.145 | 0.7 | 7 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 3.4559 | 3.4559 | 0 | 12 | 1 | 1 | 3.4559 | 10 | 0 | 0
1504.1 | 50.08 | 49.89 | 0.145 | 0.6 | 6 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 2.8088 | 2.8088 | 0 | 12 | 1 | 1 | 2.8088 | 10 | 0 | 0
1504.15 | 50.08 | 49.89 | 0.145 | 0.5 | 5 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 2.3088 | 2.3088 | 0 | 12 | 1 | 1 | 2.3088 | 10 | 0 | 0
1504.2 | 50.01 | 49.89 | 0.145 | 0.4 | 4 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 1.8088 | 1.8088 | 0 | 12 | 1 | 1 | 1.8088 | 10 | 0 | 0
1504.25 | 50.01 | 49.96 | 0.014706 | 0.3 | 3 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 1.3088 | 1.3088 | 0 | 12 | 1 | 1 | 1.3088 | 10 | 0 | 0
1504.3 | 49.94 | 49.94 | 0.026471 | 0.2 | 2 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.80882 | 0.80882 | 0 | 12 | 1 | 1 | 0.80882 | 10 | 0 | 0
1504.35 | 49.94 | 49.94 | 0.026471 | 0.1 | 1 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.30882 | 0.30882 | 0 | 12 | 1 | 1 | 0.30882 | 10 | 0 | 0
1504.4 | 50 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
1504.45 | 50 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
1504.5 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
1504.55 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
1504.6 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1504.65 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1504.7 | 49.92 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1504.75 | 49.92 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
1504.8 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50.01 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1504.85 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1504.9 | 49.92 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1504.95 | 49.92 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1505 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1505.05 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1505.1 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1505.15 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1505.2 | 49.87 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1505.25 | 49.87 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1505.3 | 49.8 | 49.8 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1505.35 | 49.8 | 49.8 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1505.4 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1505.45 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1505.5 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1505.55 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1505.6 | 49.72 | 49.72 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1505.65 | 49.72 | 49.72 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1505.7 | 49.67 | 49.67 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1505.75 | 49.67 | 49.67 | 1 | 1 | 10 | 49.87 | 0.335 | 0.14412 | 1.4412 | 5.7206 | 5.7206 | 0 | 12 | 1 | 1 | 5.7206 | 10 | 0 | 0
1505.8 | 49.65 | 49.65 | 1 | 1 | 10 | 49.87 | 0.335 | 0.24412 | 2.4412 | 6.2206 | 6.2206 | 0 | 12 | 1 | 1 | 6.2206 | 10 | 0 | 0
1505.85 | 49.65 | 49.65 | 1 | 1 | 10 | 49.8 | 1 | 0.34412 | 3.4412 | 6.7206 | 6.7206 | 0 | 12 | 1 | 1 | 6.7206 | 10 | 0 | 0
1505.9 | 49.59 | 49.59 | 1 | 1 | 10 | 49.8 | 1 | 0.44412 | 4.4412 | 7.2206 | 7.2206 | 0 | 12 | 1 | 1 | 7.2206 | 10 | 0 | 0
1505.95 | 49.59 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.54412 | 5.4412 | 7.7206 | 7.7206 | 0 | 12 | 1 | 1 | 7.7206 | 10 | 0 | 0
1506 | 49.66 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.64412 | 6.4412 | 8.2206 | 8.2206 | 0 | 12 | 1 | 1 | 8.2206 | 10 | 0 | 0
1506.05 | 49.66 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.74412 | 7.4412 | 8.7206 | 8.7206 | 0 | 12 | 1 | 1 | 8.7206 | 10 | 0 | 0
1506.1 | 49.63 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.84412 | 8.4412 | 9.2206 | 9.2206 | 0 | 12 | 1 | 1 | 9.2206 | 10 | 0 | 0
1506.15 | 49.63 | 49.59 | 1 | 1 | 10 | 49.72 | 1 | 0.94412 | 9.4412 | 9.7206 | 9.7206 | 0 | 12 | 1 | 1 | 9.7206 | 10 | 0 | 0
1506.2 | 49.61 | 49.59 | 1 | 1 | 10 | 49.72 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1506.25 | 49.61 | 49.59 | 1 | 1 | 10 | 49.67 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1506.3 | 49.54 | 49.54 | 1 | 1 | 10 | 49.67 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1506.35 | 49.54 | 49.54 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1506.4 | 49.46 | 49.46 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1506.45 | 49.46 | 49.46 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1506.5 | 49.45 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1506.55 | 49.45 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1506.6 | 49.51 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1506.65 | 49.51 | 49.45 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1506.7 | 49.5 | 49.45 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1506.75 | 49.5 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1506.8 | 49.54 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1506.85 | 49.54 | 49.45 | 1 | 1 | 10 | 49.54 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1506.9 | 49.59 | 49.45 | 1 | 1 | 10 | 49.59 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1506.95 | 49.59 | 49.45 | 1 | 1 | 10 | 49.59 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1507 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1507.05 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1507.1 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1507.15 | 49.61 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1507.2 | 49.53 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1507.25 | 49.53 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1507.3 | 49.54 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1507.35 | 49.54 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1507.4 | 49.61 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1507.45 | 49.61 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1507.5 | 49.66 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1507.55 | 49.66 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1507.6 | 49.64 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1507.65 | 49.64 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1507.7 | 49.69 | 49.53 | 1 | 1 | 10 | 49.69 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1507.75 | 49.69 | 49.53 | 1 | 1 | 10 | 49.69 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1507.8 | 49.74 | 49.53 | 1 | 1 | 10 | 49.74 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1507.85 | 49.74 | 49.54 | 1 | 1 | 10 | 49.74 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1507.9 | 49.78 | 49.54 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1507.95 | 49.78 | 49.61 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1508 | 49.82 | 49.61 | 1 | 1 | 10 | 49.82 | 0.81 | 0.81 | 8.1 | 9.05 | 9.05 | 0 | 12 | 1 | 1 | 9.05 | 10 | 0 | 0
1508.05 | 49.82 | 49.64 | 1 | 1 | 10 | 49.82 | 0.81 | 0.81 | 8.1 | 9.05 | 9.05 | 0 | 12 | 1 | 1 | 9.05 | 10 | 0 | 0
1508.1 | 49.86 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
1508.15 | 49.86 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
1508.2 | 49.84 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
1508.25 | 49.84 | 49.69 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
1508.3 | 49.91 | 49.69 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1508.35 | 49.91 | 49.74 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1508.4 | 49.97 | 49.74 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1508.45 | 49.97 | 49.78 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1508.5 | 50.03 | 49.78 | 1 | 1 | 10 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.9559 | 4.9559 | 0 | 12 | 1 | 1 | 4.9559 | 10 | 0 | 0
1508.55 | 50.03 | 49.82 | 0.81 | 0.9 | 9 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.4559 | 4.4559 | 0 | 12 | 1 | 1 | 4.4559 | 10 | 0 | 0
1508.6 | 50.05 | 49.82 | 0.81 | 0.81 | 8.1 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 3.9471 | 3.9471 | 0 | 12 | 1 | 1 | 3.9471 | 10 | 0 | 0
1508.65 | 50.05 | 49.84 | 0.62 | 0.71 | 7.1 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 3.4471 | 3.4471 | 0 | 12 | 1 | 1 | 3.4471 | 10 | 0 | 0
1508.7 | 50.01 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
1508.75 | 50.01 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
1508.8 | 49.95 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
1508.85 | 49.95 | 49.91 | 0.044118 | 0.52 | 5.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.4971 | 2.4971 | 0 | 12 | 1 | 1 | 2.4971 | 10 | 0 | 0
1508.9 | 49.99 | 49.91 | 0.044118 | 0.42 | 4.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 1.9971 | 1.9971 | 0 | 12 | 1 | 1 | 1.9971 | 10 | 0 | 0
1508.95 | 49.99 | 49.95 | 0.020588 | 0.32 | 3.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 1.4971 | 1.4971 | 0 | 12 | 1 | 1 | 1.4971 | 10 | 0 | 0
1509 | 49.92 | 49.92 | 0.038235 | 0.22 | 2.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.99706 | 0.99706 | 0 | 12 | 1 | 1 | 0.99706 | 10 | 0 | 0
1509.05 | 49.92 | 49.92 | 0.038235 | 0.12 | 1.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.49706 | 0.49706 | 0 | 12 | 1 | 1 | 0.49706 | 10 | 0 | 0
1509.1 | 49.97 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1509.15 | 49.97 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1509.2 | 50.02 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1509.25 | 50.02 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.17647 | 0.17647 | 0 | 12 | 1 | 1 | 0.17647 | 10 | 0 | 0
1509.3 | 50.07 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1509.35 | 50.07 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1509.4 | 50.06 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1509.45 | 50.06 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1509.5 | 50.13 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
1509.55 | 50.13 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
1509.6 | 50.09 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
1509.65 | 50.09 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6309 | -1.6309 | 0 | 12 | 1 | 1 | -1.6309 | 10 | 0 | 0
1509.7 | 50.07 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6309 | -1.6309 | 0 | 12 | 1 | 1 | -1.6309 | 10 | 0 | 0
1509.75 | 50.07 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6897 | -1.6897 | 0 | 12 | 1 | 1 | -1.6897 | 10 | 0 | 0
1509.8 | 50.07 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6897 | -1.6897 | 0 | 12 | 1 | 1 | -1.6897 | 10 | 0 | 0
1509.85 | 50.07 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.13 | -0.335 | -0.335 | -3.35 | -1.8074 | -1.8074 | 0 | 12 | 1 | 1 | -1.8074 | 10 | 0 | 0
1509.9 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.13 | -0.335 | -0.335 | -3.35 | -1.7779 | -1.7779 | 0 | 12 | 1 | 1 | -1.7779 | 10 | 0 | 0
1509.95 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.13 | -0.335 | -0.335 | -3.35 | -1.7779 | -1.7779 | 0 | 12 | 1 | 1 | -1.7779 | 10 | 0 | 0
1510 | 50.01 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
1510.05 | 50.01 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
1510.1 | 50.07 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
1510.15 | 50.07 | 50.01 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.235 | -2.35 | -1.175 | -1.175 | 0 | 12 | 1 | 1 | -1.175 | 10 | 0 | 0
1510.2 | 50.05 | 50.01 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.135 | -1.35 | -0.675 | -0.675 | 0 | 12 | 1 | 1 | -0.675 | 10 | 0 | 0
1510.25 | 50.05 | 50.01 | 0 | 0 | 0 | 50.07 | -0.032353 | -0.035 | -0.35 | -0.175 | -0.175 | 0 | 12 | 1 | 1 | -0.175 | 10 | 0 | 0
1510.3 | 50.1 | 50.01 | 0 | 0 | 0 | 50.1 | -0.05 | -0.05 | -0.5 | -0.25 | -0.25 | 0 | 12 | 1 | 1 | -0.25 | 10 | 0 | 0
1510.35 | 50.1 | 50.01 | 0 | 0 | 0 | 50.1 | -0.05 | -0.05 | -0.5 | -0.25 | -0.25 | 0 | 12 | 1 | 1 | -0.25 | 10 | 0 | 0
1510.4 | 50.11 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1510.45 | 50.11 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1510.5 | 50.06 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1510.55 | 50.06 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1510.6 | 50.04 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1510.65 | 50.04 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1510.7 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1510.75 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1510.8 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1510.85 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1510.9 | 50.11 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1510.95 | 50.11 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1511 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1511.05 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1511.1 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1511.15 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1511.2 | 50.02 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.11 | -0.145 | -0.145 | -1.45 | -0.73971 | -0.73971 | 0 | 12 | 1 | 1 | -0.73971 | 10 | 0 | 0
1511.25 | 50.02 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.11 | -0.145 | -0.145 | -1.45 | -0.73971 | -0.73971 | 0 | 12 | 1 | 1 | -0.73971 | 10 | 0 | 0
1511.3 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1511.35 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1511.4 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1511.45 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1511.5 | 50.01 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1511.55 | 50.01 | 50 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.045 | -0.45 | -0.225 | -0.225 | 0 | 12 | 1 | 1 | -0.225 | 10 | 0 | 0
1511.6 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
1511.65 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
1511.7 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
1511.75 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1511.8 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.14706 | 0.14706 | 0 | 12 | 1 | 1 | 0.14706 | 10 | 0 | 0
1511.85 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1511.9 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1511.95 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1512 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1512.05 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1512.1 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1512.15 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1512.2 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1512.25 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1512.3 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1512.35 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1512.4 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1512.45 | 50 | 50 | 0 | 0 | 0 | 50.01 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1512.5 | 49.5 | 49.5 | 1 | 1 | 10 | 50.01 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1512.55 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1512.6 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1512.65 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1512.7 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1512.75 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1512.8 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1512.85 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1512.9 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1512.95 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1513 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1513.05 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.1 | 1 | 5.5 | 5.5 | 0 | 12 | 1 | 1 | 5.5 | 10 | 0 | 0
1513.1 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.2 | 2 | 6 | 6 | 0 | 12 | 1 | 1 | 6 | 10 | 0 | 0
1513.15 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.3 | 3 | 6.5 | 6.5 | 0 | 12 | 1 | 1 | 6.5 | 10 | 0 | 0
1513.2 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.4 | 4 | 7 | 7 | 0 | 12 | 1 | 1 | 7 | 10 | 0 | 0
1513.25 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.5 | 5 | 7.5 | 7.5 | 0 | 12 | 1 | 1 | 7.5 | 10 | 0 | 0
1513.3 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.6 | 6 | 8 | 8 | 0 | 12 | 1 | 1 | 8 | 10 | 0 | 0
1513.35 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.7 | 7 | 8.5 | 8.5 | 0 | 12 | 1 | 1 | 8.5 | 10 | 0 | 0
1513.4 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.8 | 8 | 9 | 9 | 0 | 12 | 1 | 1 | 9 | 10 | 0 | 0
1513.45 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.9 | 9 | 9.5 | 9.5 | 0 | 12 | 1 | 1 | 9.5 | 10 | 0 | 0
1513.5 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1513.55 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1513.6 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1513.65 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1513.7 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1513.75 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1513.8 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1513.85 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1513.9 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1513.95 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1514 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1514.05 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1514.1 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1514.15 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1514.2 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1514.25 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1514.3 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1514.35 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1514.4 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1514.45 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1514.5 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1514.55 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1514.6 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1514.65 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1514.7 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1514.75 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1514.8 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1514.85 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1514.9 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1514.95 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1515 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1515.05 | 50.5 | 50.5 | -1 | 0.9 | 9 | 50.5 | -1 | -1 | -10 | -0.5 | -0.5 | 0 | 12 | 1 | 1 | -0.5 | 10 | 0 | 0
1515.1 | 50.5 | 50.5 | -1 | 0.8 | 8 | 50.5 | -1 | -1 | -10 | -1 | -1 | 0 | 12 | 1 | 1 | -1 | 10 | 0 | 0
1515.15 | 50.5 | 50.5 | -1 | 0.7 | 7 | 50.5 | -1 | -1 | -10 | -1.5 | -1.5 | 0 | 12 | 1 | 1 | -1.5 | 10 | 0 | 0
1515.2 | 50.5 | 50.5 | -1 | 0.6 | 6 | 50.5 | -1 | -1 | -10 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
1515.25 | 50.5 | 50.5 | -1 | 0.5 | 5 | 50.5 | -1 | -1 | -10 | -2.5 | -2.5 | 0 | 12 | 1 | 1 | -2.5 | 10 | 0 | 0
1515.3 | 50.5 | 50.5 | -1 | 0.4 | 4 | 50.5 | -1 | -1 | -10 | -3 | -3 | 0 | 12 | 1 | 1 | -3 | 10 | 0 | 0
1515.35 | 50.5 | 50.5 | -1 | 0.3 | 3 | 50.5 | -1 | -1 | -10 | -3.5 | -3.5 | 0 | 12 | 1 | 1 | -3.5 | 10 | 0 | 0
1515.4 | 50.5 | 50.5 | -1 | 0.2 | 2 | 50.5 | -1 | -1 | -10 | -4 | -4 | 0 | 12 | 1 | 1 | -4 | 10 | 0 | 0
1515.45 | 50.5 | 50.5 | -1 | 0.1 | 1 | 50.5 | -1 | -1 | -10 | -4.5 | -4.5 | 0 | 12 | 1 | 1 | -4.5 | 10 | 0 | 0
1515.5 | 50.5 | 50.5 | -1 | 0 | 0 | 50.5 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1515.55 | 50.5 | 50.5 | -1 | -0.1 | -1 | 50.5 | -1 | -1 | -10 | -5.5 | -5.5 | 0 | 12 | 1 | 1 | -5.5 | 10 | 0 | 0
1515.6 | 50.5 | 50.5 | -1 | -0.2 | -2 | 50.5 | -1 | -1 | -10 | -6 | -6 | 0 | 12 | 1 | 1 | -6 | 10 | 0 | 0
1515.65 | 50.5 | 50.5 | -1 | -0.3 | -3 | 50.5 | -1 | -1 | -10 | -6.5 | -6.5 | 0 | 12 | 1 | 1 | -6.5 | 10 | 0 | 0
1515.7 | 50.5 | 50.5 | -1 | -0.4 | -4 | 50.5 | -1 | -1 | -10 | -7 | -7 | 0 | 12 | 1 | 1 | -7 | 10 | 0 | 0
1515.75 | 50.5 | 50.5 | -1 | -0.5 | -5 | 50.5 | -1 | -1 | -10 | -7.5 | -7.5 | 0 | 12 | 1 | 1 | -7.5 | 10 | 0 | 0
1515.8 | 50.5 | 50.5 | -1 | -0.6 | -6 | 50.5 | -1 | -1 | -10 | -8 | -8 | 0 | 12 | 1 | 1 | -8 | 10 | 0 | 0
1515.85 | 50.5 | 50.5 | -1 | -0.7 | -7 | 50.5 | -1 | -1 | -10 | -8.5 | -8.5 | 0 | 12 | 1 | 1 | -8.5 | 10 | 0 | 0
1515.9 | 50.5 | 50.5 | -1 | -0.8 | -8 | 50.5 | -1 | -1 | -10 | -9 | -9 | 0 | 12 | 1 | 1 | -9 | 10 | 0 | 0
1515.95 | 50.5 | 50.5 | -1 | -0.9 | -9 | 50.5 | -1 | -1 | -10 | -9.5 | -9.5 | 0 | 12 | 1 | 1 | -9.5 | 10 | 0 | 0
1516 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1516.05 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1516.1 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1516.15 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1516.2 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1516.25 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1516.3 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1516.35 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1516.4 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1516.45 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1516.5 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1516.55 | 50.47 | 50.47 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1516.6 | 50.45 | 50.45 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1516.65 | 50.42 | 50.42 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1516.7 | 50.4 | 50.4 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1516.75 | 50.37 | 50.37 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1516.8 | 50.35 | 50.35 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1516.85 | 50.32 | 50.32 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1516.9 | 50.29 | 50.29 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1516.95 | 50.27 | 50.27 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1517 | 50.24 | 50.24 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1517.05 | 50.22 | 50.22 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1517.1 | 50.19 | 50.19 | -0.905 | -0.905 | -9.05 | 50.47 | -1 | -1 | -10 | -9.525 | -9.525 | 0 | 12 | 1 | 1 | -9.525 | 10 | 0 | 0
1517.15 | 50.17 | 50.17 | -0.715 | -0.715 | -7.15 | 50.45 | -1 | -1 | -10 | -8.575 | -8.575 | 0 | 12 | 1 | 1 | -8.575 | 10 | 0 | 0
1517.2 | 50.14 | 50.14 | -0.43 | -0.43 | -4.3 | 50.42 | -1 | -1 | -10 | -7.15 | -7.15 | 0 | 12 | 1 | 1 | -7.15 | 10 | 0 | 0
1517.25 | 50.12 | 50.12 | -0.24 | -0.24 | -2.4 | 50.4 | -1 | -1 | -10 | -6.2 | -6.2 | 0 | 12 | 1 | 1 | -6.2 | 10 | 0 | 0
1517.3 | 50.09 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 50.37 | -1 | -1 | -10 | -5.2206 | -5.2206 | 0 | 12 | 1 | 1 | -5.2206 | 10 | 0 | 0
1517.35 | 50.06 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.35 | -1 | -1 | -10 | -5.1324 | -5.1324 | 0 | 12 | 1 | 1 | -5.1324 | 10 | 0 | 0
1517.4 | 50.04 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.32 | -1 | -1 | -10 | -5.0735 | -5.0735 | 0 | 12 | 1 | 1 | -5.0735 | 10 | 0 | 0
1517.45 | 50.01 | 50.01 | 0 | 0 | 0 | 50.29 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1517.5 | 49.99 | 49.99 | 0 | 0 | 0 | 50.27 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1517.55 | 49.96 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.24 | -1 | -1 | -10 | -4.9265 | -4.9265 | 0 | 12 | 1 | 1 | -4.9265 | 10 | 0 | 0
1517.6 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.22 | -1 | -1 | -10 | -4.8676 | -4.8676 | 0 | 12 | 1 | 1 | -4.8676 | 10 | 0 | 0
1517.65 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.19 | -0.905 | -0.905 | -9.05 | -4.3044 | -4.3044 | 0 | 12 | 1 | 1 | -4.3044 | 10 | 0 | 0
1517.7 | 49.88 | 49.88 | 0.24 | 0.24 | 2.4 | 50.17 | -0.715 | -0.805 | -8.05 | -2.825 | -2.825 | 0 | 12 | 1 | 1 | -2.825 | 10 | 0 | 0
1517.75 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.14 | -0.43 | -0.705 | -7.05 | -1.375 | -1.375 | 0 | 12 | 1 | 1 | -1.375 | 10 | 0 | 0
1517.8 | 49.83 | 49.83 | 0.715 | 0.715 | 7.15 | 50.12 | -0.24 | -0.605 | -6.05 | 0.55 | 0.55 | 0 | 12 | 1 | 1 | 0.55 | 10 | 0 | 0
1517.85 | 49.81 | 49.81 | 0.905 | 0.905 | 9.05 | 50.09 | -0.044118 | -0.505 | -5.05 | 2 | 2 | 0 | 12 | 1 | 1 | 2 | 10 | 0 | 0
1517.9 | 49.78 | 49.78 | 1 | 1 | 10 | 50.06 | -0.026471 | -0.405 | -4.05 | 2.975 | 2.975 | 0 | 12 | 1 | 1 | 2.975 | 10 | 0 | 0
1517.95 | 49.76 | 49.76 | 1 | 1 | 10 | 50.04 | -0.014706 | -0.305 | -3.05 | 3.475 | 3.475 | 0 | 12 | 1 | 1 | 3.475 | 10 | 0 | 0
1518 | 49.73 | 49.73 | 1 | 1 | 10 | 50.01 | 0 | -0.205 | -2.05 | 3.975 | 3.975 | 0 | 12 | 1 | 1 | 3.975 | 10 | 0 | 0
1518.05 | 49.71 | 49.71 | 1 | 1 | 10 | 49.99 | 0 | -0.105 | -1.05 | 4.475 | 4.475 | 0 | 12 | 1 | 1 | 4.475 | 10 | 0 | 0
1518.1 | 49.68 | 49.68 | 1 | 1 | 10 | 49.96 | 0.014706 | -0.005 | -0.05 | 4.975 | 4.975 | 0 | 12 | 1 | 1 | 4.975 | 10 | 0 | 0
1518.15 | 49.65 | 49.65 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
1518.2 | 49.63 | 49.63 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1518.25 | 49.6 | 49.6 | 1 | 1 | 10 | 49.88 | 0.24 | 0.14412 | 1.4412 | 5.7206 | 5.7206 | 0 | 12 | 1 | 1 | 5.7206 | 10 | 0 | 0
1518.3 | 49.58 | 49.58 | 1 | 1 | 10 | 49.86 | 0.43 | 0.24412 | 2.4412 | 6.2206 | 6.2206 | 0 | 12 | 1 | 1 | 6.2206 | 10 | 0 | 0
1518.35 | 49.55 | 49.55 | 1 | 1 | 10 | 49.83 | 0.715 | 0.34412 | 3.4412 | 6.7206 | 6.7206 | 0 | 12 | 1 | 1 | 6.7206 | 10 | 0 | 0
1518.4 | 49.53 | 49.53 | 1 | 1 | 10 | 49.81 | 0.905 | 0.44412 | 4.4412 | 7.2206 | 7.2206 | 0 | 12 | 1 | 1 | 7.2206 | 10 | 0 | 0
1518.45 | 49.5 | 49.5 | 1 | 1 | 10 | 49.78 | 1 | 0.54412 | 5.4412 | 7.7206 | 7.7206 | 0 | 12 | 1 | 1 | 7.7206 | 10 | 0 | 0
1518.5 | 49.5 | 49.5 | 1 | 1 | 10 | 49.76 | 1 | 0.64412 | 6.4412 | 8.2206 | 8.2206 | 0 | 12 | 1 | 1 | 8.2206 | 10 | 0 | 0
1518.55 | 49.53 | 49.5 | 1 | 1 | 10 | 49.73 | 1 | 0.74412 | 7.4412 | 8.7206 | 8.7206 | 0 | 12 | 1 | 1 | 8.7206 | 10 | 0 | 0
1518.6 | 49.55 | 49.5 | 1 | 1 | 10 | 49.71 | 1 | 0.84412 | 8.4412 | 9.2206 | 9.2206 | 0 | 12 | 1 | 1 | 9.2206 | 10 | 0 | 0
1518.65 | 49.58 | 49.5 | 1 | 1 | 10 | 49.68 | 1 | 0.94412 | 9.4412 | 9.7206 | 9.7206 | 0 | 12 | 1 | 1 | 9.7206 | 10 | 0 | 0
1518.7 | 49.6 | 49.5 | 1 | 1 | 10 | 49.65 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1518.75 | 49.63 | 49.5 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1518.8 | 49.65 | 49.5 | 1 | 1 | 10 | 49.65 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1518.85 | 49.68 | 49.5 | 1 | 1 | 10 | 49.68 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1518.9 | 49.71 | 49.5 | 1 | 1 | 10 | 49.71 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1518.95 | 49.73 | 49.5 | 1 | 1 | 10 | 49.73 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1519 | 49.76 | 49.5 | 1 | 1 | 10 | 49.76 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1519.05 | 49.78 | 49.5 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1519.1 | 49.81 | 49.53 | 1 | 1 | 10 | 49.81 | 0.905 | 0.905 | 9.05 | 9.525 | 9.525 | 0 | 12 | 1 | 1 | 9.525 | 10 | 0 | 0
1519.15 | 49.83 | 49.55 | 1 | 1 | 10 | 49.83 | 0.715 | 0.715 | 7.15 | 8.575 | 8.575 | 0 | 12 | 1 | 1 | 8.575 | 10 | 0 | 0
1519.2 | 49.86 | 49.58 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
1519.25 | 49.88 | 49.6 | 1 | 1 | 10 | 49.88 | 0.24 | 0.24 | 2.4 | 6.2 | 6.2 | 0 | 12 | 1 | 1 | 6.2 | 10 | 0 | 0
1519.3 | 49.91 | 49.63 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1519.35 | 49.94 | 49.65 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
1519.4 | 49.96 | 49.68 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
1519.45 | 49.99 | 49.71 | 1 | 1 | 10 | 49.99 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1519.5 | 50.01 | 49.73 | 1 | 1 | 10 | 50.01 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1519.55 | 50.04 | 49.76 | 1 | 1 | 10 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 4.9265 | 4.9265 | 0 | 12 | 1 | 1 | 4.9265 | 10 | 0 | 0
1519.6 | 50.06 | 49.78 | 1 | 1 | 10 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 4.8676 | 4.8676 | 0 | 12 | 1 | 1 | 4.8676 | 10 | 0 | 0
1519.65 | 50.09 | 49.81 | 0.905 | 0.905 | 9.05 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 4.3044 | 4.3044 | 0 | 12 | 1 | 1 | 4.3044 | 10 | 0 | 0
1519.7 | 50.12 | 49.83 | 0.715 | 0.805 | 8.05 | 50.12 | -0.24 | -0.24 | -2.4 | 2.825 | 2.825 | 0 | 12 | 1 | 1 | 2.825 | 10 | 0 | 0
1519.75 | 50.14 | 49.86 | 0.43 | 0.705 | 7.05 | 50.14 | -0.43 | -0.43 | -4.3 | 1.375 | 1.375 | 0 | 12 | 1 | 1 | 1.375 | 10 | 0 | 0
1519.8 | 50.17 | 49.88 | 0.24 | 0.605 | 6.05 | 50.17 | -0.715 | -0.715 | -7.15 | -0.55 | -0.55 | 0 | 12 | 1 | 1 | -0.55 | 10 | 0 | 0
1519.85 | 50.19 | 49.91 | 0.044118 | 0.505 | 5.05 | 50.19 | -0.905 | -0.905 | -9.05 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
1519.9 | 50.22 | 49.94 | 0.026471 | 0.405 | 4.05 | 50.22 | -1 | -1 | -10 | -2.975 | -2.975 | 0 | 12 | 1 | 1 | -2.975 | 10 | 0 | 0
1519.95 | 50.24 | 49.96 | 0.014706 | 0.305 | 3.05 | 50.24 | -1 | -1 | -10 | -3.475 | -3.475 | 0 | 12 | 1 | 1 | -3.475 | 10 | 0 | 0
1520 | 50.27 | 49.99 | 0 | 0.205 | 2.05 | 50.27 | -1 | -1 | -10 | -3.975 | -3.975 | 0 | 12 | 1 | 1 | -3.975 | 10 | 0 | 0
1520.05 | 50.29 | 50.01 | 0 | 0.105 | 1.05 | 50.29 | -1 | -1 | -10 | -4.475 | -4.475 | 0 | 12 | 1 | 1 | -4.475 | 10 | 0 | 0
1520.1 | 50.32 | 50.04 | -0.014706 | 0.005 | 0.05 | 50.32 | -1 | -1 | -10 | -4.975 | -4.975 | 0 | 12 | 1 | 1 | -4.975 | 10 | 0 | 0
1520.15 | 50.35 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.35 | -1 | -1 | -10 | -5.1324 | -5.1324 | 0 | 12 | 1 | 1 | -5.1324 | 10 | 0 | 0
1520.2 | 50.37 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 50.37 | -1 | -1 | -10 | -5.2206 | -5.2206 | 0 | 12 | 1 | 1 | -5.2206 | 10 | 0 | 0
1520.25 | 50.4 | 50.12 | -0.24 | -0.14412 | -1.4412 | 50.4 | -1 | -1 | -10 | -5.7206 | -5.7206 | 0 | 12 | 1 | 1 | -5.7206 | 10 | 0 | 0
1520.3 | 50.42 | 50.14 | -0.43 | -0.24412 | -2.4412 | 50.42 | -1 | -1 | -10 | -6.2206 | -6.2206 | 0 | 12 | 1 | 1 | -6.2206 | 10 | 0 | 0
1520.35 | 50.45 | 50.17 | -0.715 | -0.34412 | -3.4412 | 50.45 | -1 | -1 | -10 | -6.7206 | -6.7206 | 0 | 12 | 1 | 1 | -6.7206 | 10 | 0 | 0
1520.4 | 50.47 | 50.19 | -0.905 | -0.44412 | -4.4412 | 50.47 | -1 | -1 | -10 | -7.2206 | -7.2206 | 0 | 12 | 1 | 1 | -7.2206 | 10 | 0 | 0
1520.45 | 50.5 | 50.22 | -1 | -0.54412 | -5.4412 | 50.5 | -1 | -1 | -10 | -7.7206 | -7.7206 | 0 | 12 | 1 | 1 | -7.7206 | 10 | 0 | 0
1520.5 | 50.5 | 50.24 | -1 | -0.64412 | -6.4412 | 50.5 | -1 | -1 | -10 | -8.2206 | -8.2206 | 0 | 12 | 1 | 1 | -8.2206 | 10 | 0 | 0
1520.55 | 50.47 | 50.27 | -1 | -0.74412 | -7.4412 | 50.5 | -1 | -1 | -10 | -8.7206 | -8.7206 | 0 | 12 | 1 | 1 | -8.7206 | 10 | 0 | 0
1520.6 | 50.45 | 50.29 | -1 | -0.84412 | -8.4412 | 50.5 | -1 | -1 | -10 | -9.2206 | -9.2206 | 0 | 12 | 1 | 1 | -9.2206 | 10 | 0 | 0
1520.65 | 50.42 | 50.32 | -1 | -0.94412 | -9.4412 | 50.5 | -1 | -1 | -10 | -9.7206 | -9.7206 | 0 | 12 | 1 | 1 | -9.7206 | 10 | 0 | 0
1520.7 | 50.39 | 50.35 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1520.75 | 50.37 | 50.37 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1520.8 | 50.34 | 50.34 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1520.85 | 50.32 | 50.32 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1520.9 | 50.29 | 50.29 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1520.95 | 50.26 | 50.26 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1521 | 50.24 | 50.24 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1521.05 | 50.21 | 50.21 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1521.1 | 50.18 | 50.18 | -0.81 | -0.81 | -8.1 | 50.47 | -1 | -1 | -10 | -9.05 | -9.05 | 0 | 12 | 1 | 1 | -9.05 | 10 | 0 | 0
1521.15 | 50.16 | 50.16 | -0.62 | -0.62 | -6.2 | 50.45 | -1 | -1 | -10 | -8.1 | -8.1 | 0 | 12 | 1 | 1 | -8.1 | 10 | 0 | 0
1521.2 | 50.13 | 50.13 | -0.335 | -0.335 | -3.35 | 50.42 | -1 | -1 | -10 | -6.675 | -6.675 | 0 | 12 | 1 | 1 | -6.675 | 10 | 0 | 0
1521.25 | 50.11 | 50.11 | -0.145 | -0.145 | -1.45 | 50.39 | -1 | -1 | -10 | -5.725 | -5.725 | 0 | 12 | 1 | 1 | -5.725 | 10 | 0 | 0
1521.3 | 50.08 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 50.37 | -1 | -1 | -10 | -5.1912 | -5.1912 | 0 | 12 | 1 | 1 | -5.1912 | 10 | 0 | 0
1521.35 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.34 | -1 | -1 | -10 | -5.1029 | -5.1029 | 0 | 12 | 1 | 1 | -5.1029 | 10 | 0 | 0
1521.4 | 50.03 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 50.32 | -1 | -1 | -10 | -5.0441 | -5.0441 | 0 | 12 | 1 | 1 | -5.0441 | 10 | 0 | 0
1521.45 | 50 | 50 | 0 | 0 | 0 | 50.29 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1521.5 | 50 | 50 | 0 | 0 | 0 | 50.26 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1521.55 | 50 | 50 | 0 | 0 | 0 | 50.24 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1521.6 | 50 | 50 | 0 | 0 | 0 | 50.21 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1521.65 | 50 | 50 | 0 | 0 | 0 | 50.18 | -0.81 | -0.9 | -9 | -4.5 | -4.5 | 0 | 12 | 1 | 1 | -4.5 | 10 | 0 | 0
1521.7 | 50 | 50 | 0 | 0 | 0 | 50.16 | -0.62 | -0.8 | -8 | -4 | -4 | 0 | 12 | 1 | 1 | -4 | 10 | 0 | 0
1521.75 | 50 | 50 | 0 | 0 | 0 | 50.13 | -0.335 | -0.7 | -7 | -3.5 | -3.5 | 0 | 12 | 1 | 1 | -3.5 | 10 | 0 | 0
1521.8 | 50.01 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.6 | -6 | -3 | -3 | 0 | 12 | 1 | 1 | -3 | 10 | 0 | 0
1521.85 | 50.01 | 50 | 0 | 0 | 0 | 50.08 | -0.038235 | -0.5 | -5 | -2.5 | -2.5 | 0 | 12 | 1 | 1 | -2.5 | 10 | 0 | 0
1521.9 | 49.99 | 49.99 | 0 | 0 | 0 | 50.05 | -0.020588 | -0.4 | -4 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
1521.95 | 49.99 | 49.99 | 0 | 0 | 0 | 50.03 | -0.0088235 | -0.3 | -3 | -1.5 | -1.5 | 0 | 12 | 1 | 1 | -1.5 | 10 | 0 | 0
1522 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | -0.2 | -2 | -0.83824 | -0.83824 | 0 | 12 | 1 | 1 | -0.83824 | 10 | 0 | 0
1522.05 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | -0.1 | -1 | -0.33824 | -0.33824 | 0 | 12 | 1 | 1 | -0.33824 | 10 | 0 | 0
1522.1 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
1522.15 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
1522.2 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
1522.25 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
1522.3 | 49.89 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
1522.35 | 49.89 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
1522.4 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50.01 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1522.45 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1522.5 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1522.55 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 2.7868 | 2.7868 | 0 | 12 | 1 | 1 | 2.7868 | 10 | 0 | 0
1522.6 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 2.7868 | 2.7868 | 0 | 12 | 1 | 1 | 2.7868 | 10 | 0 | 0
1522.65 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 2.8456 | 2.8456 | 0 | 12 | 1 | 1 | 2.8456 | 10 | 0 | 0
1522.7 | 49.94 | 49.85 | 0.525 | 0.525 | 5.25 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 2.7574 | 2.7574 | 0 | 12 | 1 | 1 | 2.7574 | 10 | 0 | 0
1522.75 | 49.94 | 49.85 | 0.525 | 0.525 | 5.25 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 2.7574 | 2.7574 | 0 | 12 | 1 | 1 | 2.7574 | 10 | 0 | 0
1522.8 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1522.85 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1522.9 | 49.93 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1522.95 | 49.93 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1523 | 49.96 | 49.85 | 0.525 | 0.525 | 5.25 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 2.6985 | 2.6985 | 0 | 12 | 1 | 1 | 2.6985 | 10 | 0 | 0
1523.05 | 49.96 | 49.85 | 0.525 | 0.525 | 5.25 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 2.6985 | 2.6985 | 0 | 12 | 1 | 1 | 2.6985 | 10 | 0 | 0
1523.1 | 49.99 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1523.15 | 49.99 | 49.91 | 0.044118 | 0.425 | 4.25 | 49.99 | 0 | 0 | 0 | 2.125 | 2.125 | 0 | 12 | 1 | 1 | 2.125 | 10 | 0 | 0
1523.2 | 49.99 | 49.91 | 0.044118 | 0.325 | 3.25 | 49.99 | 0 | 0 | 0 | 1.625 | 1.625 | 0 | 12 | 1 | 1 | 1.625 | 10 | 0 | 0
1523.25 | 49.99 | 49.93 | 0.032353 | 0.225 | 2.25 | 49.99 | 0 | 0 | 0 | 1.125 | 1.125 | 0 | 12 | 1 | 1 | 1.125 | 10 | 0 | 0
1523.3 | 49.96 | 49.93 | 0.032353 | 0.125 | 1.25 | 49.99 | 0 | 0 | 0 | 0.625 | 0.625 | 0 | 12 | 1 | 1 | 0.625 | 10 | 0 | 0
1523.35 | 49.96 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 49.99 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1523.4 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1523.45 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1523.5 | 50.05 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.058824 | 0.058824 | 0 | 12 | 1 | 1 | 0.058824 | 10 | 0 | 0
1523.55 | 50.05 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
1523.6 | 49.97 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
1523.65 | 49.97 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
1523.7 | 49.92 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1523.75 | 49.92 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1523.8 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1523.85 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1523.9 | 49.94 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1523.95 | 49.94 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1524 | 50.01 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1524.05 | 50.01 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1524.1 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1524.15 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
1524.2 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
1524.25 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
1524.3 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
1524.35 | 49.95 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
1524.4 | 49.97 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
1524.45 | 49.97 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
1524.5 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
1524.55 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
1524.6 | 49.87 | 49.87 | 0.335 | 0.335 | 3.35 | 50.01 | 0 | 0 | 0 | 1.675 | 1.675 | 0 | 12 | 1 | 1 | 1.675 | 10 | 0 | 0
1524.65 | 49.87 | 49.87 | 0.335 | 0.335 | 3.35 | 49.99 | 0 | 0 | 0 | 1.675 | 1.675 | 0 | 12 | 1 | 1 | 1.675 | 10 | 0 | 0
1524.7 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1524.75 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 2.6691 | 2.6691 | 0 | 12 | 1 | 1 | 2.6691 | 10 | 0 | 0
1524.8 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1524.85 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1524.9 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1524.95 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1525 | 49.84 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1525.05 | 49.84 | 49.79 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
1525.1 | 49.89 | 49.79 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
1525.15 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.12647 | 1.2647 | 5.6324 | 5.6324 | 0 | 12 | 1 | 1 | 5.6324 | 10 | 0 | 0
1525.2 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.145 | 1.45 | 5.725 | 5.725 | 0 | 12 | 1 | 1 | 5.725 | 10 | 0 | 0
1525.25 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.145 | 1.45 | 5.725 | 5.725 | 0 | 12 | 1 | 1 | 5.725 | 10 | 0 | 0
1525.3 | 49.96 | 49.79 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
1525.35 | 49.96 | 49.79 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
1525.4 | 50.02 | 49.79 | 1 | 1 | 10 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 4.9853 | 4.9853 | 0 | 12 | 1 | 1 | 4.9853 | 10 | 0 | 0
1525.45 | 50.02 | 49.79 | 1 | 1 | 10 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 4.9853 | 4.9853 | 0 | 12 | 1 | 1 | 4.9853 | 10 | 0 | 0
1525.5 | 50.03 | 49.79 | 1 | 1 | 10 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.9559 | 4.9559 | 0 | 12 | 1 | 1 | 4.9559 | 10 | 0 | 0
1525.55 | 50.03 | 49.84 | 0.62 | 0.9 | 9 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.4559 | 4.4559 | 0 | 12 | 1 | 1 | 4.4559 | 10 | 0 | 0
1525.6 | 50.02 | 49.84 | 0.62 | 0.8 | 8 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 3.9559 | 3.9559 | 0 | 12 | 1 | 1 | 3.9559 | 10 | 0 | 0
1525.65 | 50.02 | 49.89 | 0.145 | 0.7 | 7 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 3.4559 | 3.4559 | 0 | 12 | 1 | 1 | 3.4559 | 10 | 0 | 0
1525.7 | 50.08 | 49.89 | 0.145 | 0.6 | 6 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 2.8088 | 2.8088 | 0 | 12 | 1 | 1 | 2.8088 | 10 | 0 | 0
1525.75 | 50.08 | 49.89 | 0.145 | 0.5 | 5 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 2.3088 | 2.3088 | 0 | 12 | 1 | 1 | 2.3088 | 10 | 0 | 0
1525.8 | 50.01 | 49.89 | 0.145 | 0.4 | 4 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 1.8088 | 1.8088 | 0 | 12 | 1 | 1 | 1.8088 | 10 | 0 | 0
1525.85 | 50.01 | 49.96 | 0.014706 | 0.3 | 3 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 1.3088 | 1.3088 | 0 | 12 | 1 | 1 | 1.3088 | 10 | 0 | 0
1525.9 | 49.94 | 49.94 | 0.026471 | 0.2 | 2 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.80882 | 0.80882 | 0 | 12 | 1 | 1 | 0.80882 | 10 | 0 | 0
1525.95 | 49.94 | 49.94 | 0.026471 | 0.1 | 1 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.30882 | 0.30882 | 0 | 12 | 1 | 1 | 0.30882 | 10 | 0 | 0
1526 | 50 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
1526.05 | 50 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
1526.1 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
1526.15 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
1526.2 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1526.25 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1526.3 | 49.92 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1526.35 | 49.92 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
1526.4 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50.01 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1526.45 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1526.5 | 49.92 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1526.55 | 49.92 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1526.6 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1526.65 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1526.7 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1526.75 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1526.8 | 49.87 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1526.85 | 49.87 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1526.9 | 49.8 | 49.8 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1526.95 | 49.8 | 49.8 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1527 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1527.05 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1527.1 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1527.15 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1527.2 | 49.72 | 49.72 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1527.25 | 49.72 | 49.72 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1527.3 | 49.67 | 49.67 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1527.35 | 49.67 | 49.67 | 1 | 1 | 10 | 49.87 | 0.335 | 0.14412 | 1.4412 | 5.7206 | 5.7206 | 0 | 12 | 1 | 1 | 5.7206 | 10 | 0 | 0
1527.4 | 49.65 | 49.65 | 1 | 1 | 10 | 49.87 | 0.335 | 0.24412 | 2.4412 | 6.2206 | 6.2206 | 0 | 12 | 1 | 1 | 6.2206 | 10 | 0 | 0
1527.45 | 49.65 | 49.65 | 1 | 1 | 10 | 49.8 | 1 | 0.34412 | 3.4412 | 6.7206 | 6.7206 | 0 | 12 | 1 | 1 | 6.7206 | 10 | 0 | 0
1527.5 | 49.59 | 49.59 | 1 | 1 | 10 | 49.8 | 1 | 0.44412 | 4.4412 | 7.2206 | 7.2206 | 0 | 12 | 1 | 1 | 7.2206 | 10 | 0 | 0
1527.55 | 49.59 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.54412 | 5.4412 | 7.7206 | 7.7206 | 0 | 12 | 1 | 1 | 7.7206 | 10 | 0 | 0
1527.6 | 49.66 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.64412 | 6.4412 | 8.2206 | 8.2206 | 0 | 12 | 1 | 1 | 8.2206 | 10 | 0 | 0
1527.65 | 49.66 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.74412 | 7.4412 | 8.7206 | 8.7206 | 0 | 12 | 1 | 1 | 8.7206 | 10 | 0 | 0
1527.7 | 49.63 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.84412 | 8.4412 | 9.2206 | 9.2206 | 0 | 12 | 1 | 1 | 9.2206 | 10 | 0 | 0
1527.75 | 49.63 | 49.59 | 1 | 1 | 10 | 49.72 | 1 | 0.94412 | 9.4412 | 9.7206 | 9.7206 | 0 | 12 | 1 | 1 | 9.7206 | 10 | 0 | 0
1527.8 | 49.61 | 49.59 | 1 | 1 | 10 | 49.72 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1527.85 | 49.61 | 49.59 | 1 | 1 | 10 | 49.67 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1527.9 | 49.54 | 49.54 | 1 | 1 | 10 | 49.67 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1527.95 | 49.54 | 49.54 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1528 | 49.46 | 49.46 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1528.05 | 49.46 | 49.46 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1528.1 | 49.45 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1528.15 | 49.45 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1528.2 | 49.51 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1528.25 | 49.51 | 49.45 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1528.3 | 49.5 | 49.45 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1528.35 | 49.5 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1528.4 | 49.54 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1528.45 | 49.54 | 49.45 | 1 | 1 | 10 | 49.54 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1528.5 | 49.59 | 49.45 | 1 | 1 | 10 | 49.59 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1528.55 | 49.59 | 49.45 | 1 | 1 | 10 | 49.59 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1528.6 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1528.65 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1528.7 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1528.75 | 49.61 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1528.8 | 49.53 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1528.85 | 49.53 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1528.9 | 49.54 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1528.95 | 49.54 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1529 | 49.61 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1529.05 | 49.61 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1529.1 | 49.66 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1529.15 | 49.66 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1529.2 | 49.64 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1529.25 | 49.64 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1529.3 | 49.69 | 49.53 | 1 | 1 | 10 | 49.69 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1529.35 | 49.69 | 49.53 | 1 | 1 | 10 | 49.69 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1529.4 | 49.74 | 49.53 | 1 | 1 | 10 | 49.74 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1529.45 | 49.74 | 49.54 | 1 | 1 | 10 | 49.74 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1529.5 | 49.78 | 49.54 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1529.55 | 49.78 | 49.61 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1529.6 | 49.82 | 49.61 | 1 | 1 | 10 | 49.82 | 0.81 | 0.81 | 8.1 | 9.05 | 9.05 | 0 | 12 | 1 | 1 | 9.05 | 10 | 0 | 0
1529.65 | 49.82 | 49.64 | 1 | 1 | 10 | 49.82 | 0.81 | 0.81 | 8.1 | 9.05 | 9.05 | 0 | 12 | 1 | 1 | 9.05 | 10 | 0 | 0
1529.7 | 49.86 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
1529.75 | 49.86 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
1529.8 | 49.84 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
1529.85 | 49.84 | 49.69 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
1529.9 | 49.91 | 49.69 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1529.95 | 49.91 | 49.74 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1530 | 49.97 | 49.74 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1530.05 | 49.97 | 49.78 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1530.1 | 50.03 | 49.78 | 1 | 1 | 10 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.9559 | 4.9559 | 0 | 12 | 1 | 1 | 4.9559 | 10 | 0 | 0
1530.15 | 50.03 | 49.82 | 0.81 | 0.9 | 9 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.4559 | 4.4559 | 0 | 12 | 1 | 1 | 4.4559 | 10 | 0 | 0
1530.2 | 50.05 | 49.82 | 0.81 | 0.81 | 8.1 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 3.9471 | 3.9471 | 0 | 12 | 1 | 1 | 3.9471 | 10 | 0 | 0
1530.25 | 50.05 | 49.84 | 0.62 | 0.71 | 7.1 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 3.4471 | 3.4471 | 0 | 12 | 1 | 1 | 3.4471 | 10 | 0 | 0
1530.3 | 50.01 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
1530.35 | 50.01 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
1530.4 | 49.95 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
1530.45 | 49.95 | 49.91 | 0.044118 | 0.52 | 5.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.4971 | 2.4971 | 0 | 12 | 1 | 1 | 2.4971 | 10 | 0 | 0
1530.5 | 49.99 | 49.91 | 0.044118 | 0.42 | 4.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 1.9971 | 1.9971 | 0 | 12 | 1 | 1 | 1.9971 | 10 | 0 | 0
1530.55 | 49.99 | 49.95 | 0.020588 | 0.32 | 3.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 1.4971 | 1.4971 | 0 | 12 | 1 | 1 | 1.4971 | 10 | 0 | 0
1530.6 | 49.92 | 49.92 | 0.038235 | 0.22 | 2.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.99706 | 0.99706 | 0 | 12 | 1 | 1 | 0.99706 | 10 | 0 | 0
1530.65 | 49.92 | 49.92 | 0.038235 | 0.12 | 1.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.49706 | 0.49706 | 0 | 12 | 1 | 1 | 0.49706 | 10 | 0 | 0
1530.7 | 49.97 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1530.75 | 49.97 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1530.8 | 50.02 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1530.85 | 50.02 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.17647 | 0.17647 | 0 | 12 | 1 | 1 | 0.17647 | 10 | 0 | 0
1530.9 | 50.07 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1530.95 | 50.07 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1531 | 50.06 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1531.05 | 50.06 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1531.1 | 50.13 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
1531.15 | 50.13 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
1531.2 | 50.09 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
1531.25 | 50.09 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6309 | -1.6309 | 0 | 12 | 1 | 1 | -1.6309 | 10 | 0 | 0
1531.3 | 50.07 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6309 | -1.6309 | 0 | 12 | 1 | 1 | -1.6309 | 10 | 0 | 0
1531.35 | 50.07 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6897 | -1.6897 | 0 | 12 | 1 | 1 | -1.6897 | 10 | 0 | 0
1531.4 | 50.07 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6897 | -1.6897 | 0 | 12 | 1 | 1 | -1.6897 | 10 | 0 | 0
1531.45 | 50.07 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.13 | -0.335 | -0.335 | -3.35 | -1.8074 | -1.8074 | 0 | 12 | 1 | 1 | -1.8074 | 10 | 0 | 0
1531.5 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.13 | -0.335 | -0.335 | -3.35 | -1.7779 | -1.7779 | 0 | 12 | 1 | 1 | -1.7779 | 10 | 0 | 0
1531.55 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.13 | -0.335 | -0.335 | -3.35 | -1.7779 | -1.7779 | 0 | 12 | 1 | 1 | -1.7779 | 10 | 0 | 0
1531.6 | 50.01 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
1531.65 | 50.01 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
1531.7 | 50.07 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
1531.75 | 50.07 | 50.01 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.235 | -2.35 | -1.175 | -1.175 | 0 | 12 | 1 | 1 | -1.175 | 10 | 0 | 0
1531.8 | 50.05 | 50.01 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.135 | -1.35 | -0.675 | -0.675 | 0 | 12 | 1 | 1 | -0.675 | 10 | 0 | 0
1531.85 | 50.05 | 50.01 | 0 | 0 | 0 | 50.07 | -0.032353 | -0.035 | -0.35 | -0.175 | -0.175 | 0 | 12 | 1 | 1 | -0.175 | 10 | 0 | 0
1531.9 | 50.1 | 50.01 | 0 | 0 | 0 | 50.1 | -0.05 | -0.05 | -0.5 | -0.25 | -0.25 | 0 | 12 | 1 | 1 | -0.25 | 10 | 0 | 0
1531.95 | 50.1 | 50.01 | 0 | 0 | 0 | 50.1 | -0.05 | -0.05 | -0.5 | -0.25 | -0.25 | 0 | 12 | 1 | 1 | -0.25 | 10 | 0 | 0
1532 | 50.11 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1532.05 | 50.11 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1532.1 | 50.06 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1532.15 | 50.06 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1532.2 | 50.04 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1532.25 | 50.04 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1532.3 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1532.35 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1532.4 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1532.45 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1532.5 | 50.11 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1532.55 | 50.11 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1532.6 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1532.65 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1532.7 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1532.75 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1532.8 | 50.02 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.11 | -0.145 | -0.145 | -1.45 | -0.73971 | -0.73971 | 0 | 12 | 1 | 1 | -0.73971 | 10 | 0 | 0
1532.85 | 50.02 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.11 | -0.145 | -0.145 | -1.45 | -0.73971 | -0.73971 | 0 | 12 | 1 | 1 | -0.73971 | 10 | 0 | 0
1532.9 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1532.95 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1533 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1533.05 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1533.1 | 50.01 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1533.15 | 50.01 | 50 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.045 | -0.45 | -0.225 | -0.225 | 0 | 12 | 1 | 1 | -0.225 | 10 | 0 | 0
1533.2 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
1533.25 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
1533.3 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
1533.35 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1533.4 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.14706 | 0.14706 | 0 | 12 | 1 | 1 | 0.14706 | 10 | 0 | 0
1533.45 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1533.5 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1533.55 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1533.6 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1533.65 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1533.7 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1533.75 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1533.8 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1533.85 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1533.9 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1533.95 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1534 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1534.05 | 50 | 50 | 0 | 0 | 0 | 50.01 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1534.1 | 49.5 | 49.5 | 1 | 1 | 10 | 50.01 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1534.15 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1534.2 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1534.25 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1534.3 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1534.35 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1534.4 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1534.45 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1534.5 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1534.55 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1534.6 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1534.65 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.1 | 1 | 5.5 | 5.5 | 0 | 12 | 1 | 1 | 5.5 | 10 | 0 | 0
1534.7 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.2 | 2 | 6 | 6 | 0 | 12 | 1 | 1 | 6 | 10 | 0 | 0
1534.75 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.3 | 3 | 6.5 | 6.5 | 0 | 12 | 1 | 1 | 6.5 | 10 | 0 | 0
1534.8 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.4 | 4 | 7 | 7 | 0 | 12 | 1 | 1 | 7 | 10 | 0 | 0
1534.85 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.5 | 5 | 7.5 | 7.5 | 0 | 12 | 1 | 1 | 7.5 | 10 | 0 | 0
1534.9 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.6 | 6 | 8 | 8 | 0 | 12 | 1 | 1 | 8 | 10 | 0 | 0
1534.95 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.7 | 7 | 8.5 | 8.5 | 0 | 12 | 1 | 1 | 8.5 | 10 | 0 | 0
1535 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.8 | 8 | 9 | 9 | 0 | 12 | 1 | 1 | 9 | 10 | 0 | 0
1535.05 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.9 | 9 | 9.5 | 9.5 | 0 | 12 | 1 | 1 | 9.5 | 10 | 0 | 0
1535.1 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1535.15 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1535.2 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1535.25 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1535.3 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1535.35 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1535.4 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1535.45 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1535.5 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1535.55 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1535.6 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1535.65 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1535.7 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1535.75 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1535.8 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1535.85 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1535.9 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1535.95 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1536 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1536.05 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1536.1 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1536.15 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1536.2 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1536.25 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1536.3 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1536.35 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1536.4 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1536.45 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1536.5 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1536.55 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1536.6 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1536.65 | 50.5 | 50.5 | -1 | 0.9 | 9 | 50.5 | -1 | -1 | -10 | -0.5 | -0.5 | 0 | 12 | 1 | 1 | -0.5 | 10 | 0 | 0
1536.7 | 50.5 | 50.5 | -1 | 0.8 | 8 | 50.5 | -1 | -1 | -10 | -1 | -1 | 0 | 12 | 1 | 1 | -1 | 10 | 0 | 0
1536.75 | 50.5 | 50.5 | -1 | 0.7 | 7 | 50.5 | -1 | -1 | -10 | -1.5 | -1.5 | 0 | 12 | 1 | 1 | -1.5 | 10 | 0 | 0
1536.8 | 50.5 | 50.5 | -1 | 0.6 | 6 | 50.5 | -1 | -1 | -10 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
1536.85 | 50.5 | 50.5 | -1 | 0.5 | 5 | 50.5 | -1 | -1 | -10 | -2.5 | -2.5 | 0 | 12 | 1 | 1 | -2.5 | 10 | 0 | 0
1536.9 | 50.5 | 50.5 | -1 | 0.4 | 4 | 50.5 | -1 | -1 | -10 | -3 | -3 | 0 | 12 | 1 | 1 | -3 | 10 | 0 | 0
1536.95 | 50.5 | 50.5 | -1 | 0.3 | 3 | 50.5 | -1 | -1 | -10 | -3.5 | -3.5 | 0 | 12 | 1 | 1 | -3.5 | 10 | 0 | 0
1537 | 50.5 | 50.5 | -1 | 0.2 | 2 | 50.5 | -1 | -1 | -10 | -4 | -4 | 0 | 12 | 1 | 1 | -4 | 10 | 0 | 0
1537.05 | 50.5 | 50.5 | -1 | 0.1 | 1 | 50.5 | -1 | -1 | -10 | -4.5 | -4.5 | 0 | 12 | 1 | 1 | -4.5 | 10 | 0 | 0
1537.1 | 50.5 | 50.5 | -1 | 0 | 0 | 50.5 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1537.15 | 50.5 | 50.5 | -1 | -0.1 | -1 | 50.5 | -1 | -1 | -10 | -5.5 | -5.5 | 0 | 12 | 1 | 1 | -5.5 | 10 | 0 | 0
1537.2 | 50.5 | 50.5 | -1 | -0.2 | -2 | 50.5 | -1 | -1 | -10 | -6 | -6 | 0 | 12 | 1 | 1 | -6 | 10 | 0 | 0
1537.25 | 50.5 | 50.5 | -1 | -0.3 | -3 | 50.5 | -1 | -1 | -10 | -6.5 | -6.5 | 0 | 12 | 1 | 1 | -6.5 | 10 | 0 | 0
1537.3 | 50.5 | 50.5 | -1 | -0.4 | -4 | 50.5 | -1 | -1 | -10 | -7 | -7 | 0 | 12 | 1 | 1 | -7 | 10 | 0 | 0
1537.35 | 50.5 | 50.5 | -1 | -0.5 | -5 | 50.5 | -1 | -1 | -10 | -7.5 | -7.5 | 0 | 12 | 1 | 1 | -7.5 | 10 | 0 | 0
1537.4 | 50.5 | 50.5 | -1 | -0.6 | -6 | 50.5 | -1 | -1 | -10 | -8 | -8 | 0 | 12 | 1 | 1 | -8 | 10 | 0 | 0
1537.45 | 50.5 | 50.5 | -1 | -0.7 | -7 | 50.5 | -1 | -1 | -10 | -8.5 | -8.5 | 0 | 12 | 1 | 1 | -8.5 | 10 | 0 | 0
1537.5 | 50.5 | 50.5 | -1 | -0.8 | -8 | 50.5 | -1 | -1 | -10 | -9 | -9 | 0 | 12 | 1 | 1 | -9 | 10 | 0 | 0
1537.55 | 50.5 | 50.5 | -1 | -0.9 | -9 | 50.5 | -1 | -1 | -10 | -9.5 | -9.5 | 0 | 12 | 1 | 1 | -9.5 | 10 | 0 | 0
1537.6 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1537.65 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1537.7 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1537.75 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1537.8 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1537.85 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1537.9 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1537.95 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1538 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1538.05 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1538.1 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1538.15 | 50.47 | 50.47 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1538.2 | 50.45 | 50.45 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1538.25 | 50.42 | 50.42 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1538.3 | 50.4 | 50.4 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1538.35 | 50.37 | 50.37 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1538.4 | 50.35 | 50.35 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1538.45 | 50.32 | 50.32 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1538.5 | 50.29 | 50.29 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1538.55 | 50.27 | 50.27 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1538.6 | 50.24 | 50.24 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1538.65 | 50.22 | 50.22 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1538.7 | 50.19 | 50.19 | -0.905 | -0.905 | -9.05 | 50.47 | -1 | -1 | -10 | -9.525 | -9.525 | 0 | 12 | 1 | 1 | -9.525 | 10 | 0 | 0
1538.75 | 50.17 | 50.17 | -0.715 | -0.715 | -7.15 | 50.45 | -1 | -1 | -10 | -8.575 | -8.575 | 0 | 12 | 1 | 1 | -8.575 | 10 | 0 | 0
1538.8 | 50.14 | 50.14 | -0.43 | -0.43 | -4.3 | 50.42 | -1 | -1 | -10 | -7.15 | -7.15 | 0 | 12 | 1 | 1 | -7.15 | 10 | 0 | 0
1538.85 | 50.12 | 50.12 | -0.24 | -0.24 | -2.4 | 50.4 | -1 | -1 | -10 | -6.2 | -6.2 | 0 | 12 | 1 | 1 | -6.2 | 10 | 0 | 0
1538.9 | 50.09 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 50.37 | -1 | -1 | -10 | -5.2206 | -5.2206 | 0 | 12 | 1 | 1 | -5.2206 | 10 | 0 | 0
1538.95 | 50.06 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.35 | -1 | -1 | -10 | -5.1324 | -5.1324 | 0 | 12 | 1 | 1 | -5.1324 | 10 | 0 | 0
1539 | 50.04 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.32 | -1 | -1 | -10 | -5.0735 | -5.0735 | 0 | 12 | 1 | 1 | -5.0735 | 10 | 0 | 0
1539.05 | 50.01 | 50.01 | 0 | 0 | 0 | 50.29 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1539.1 | 49.99 | 49.99 | 0 | 0 | 0 | 50.27 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1539.15 | 49.96 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.24 | -1 | -1 | -10 | -4.9265 | -4.9265 | 0 | 12 | 1 | 1 | -4.9265 | 10 | 0 | 0
1539.2 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.22 | -1 | -1 | -10 | -4.8676 | -4.8676 | 0 | 12 | 1 | 1 | -4.8676 | 10 | 0 | 0
1539.25 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.19 | -0.905 | -0.905 | -9.05 | -4.3044 | -4.3044 | 0 | 12 | 1 | 1 | -4.3044 | 10 | 0 | 0
1539.3 | 49.88 | 49.88 | 0.24 | 0.24 | 2.4 | 50.17 | -0.715 | -0.805 | -8.05 | -2.825 | -2.825 | 0 | 12 | 1 | 1 | -2.825 | 10 | 0 | 0
1539.35 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.14 | -0.43 | -0.705 | -7.05 | -1.375 | -1.375 | 0 | 12 | 1 | 1 | -1.375 | 10 | 0 | 0
1539.4 | 49.83 | 49.83 | 0.715 | 0.715 | 7.15 | 50.12 | -0.24 | -0.605 | -6.05 | 0.55 | 0.55 | 0 | 12 | 1 | 1 | 0.55 | 10 | 0 | 0
1539.45 | 49.81 | 49.81 | 0.905 | 0.905 | 9.05 | 50.09 | -0.044118 | -0.505 | -5.05 | 2 | 2 | 0 | 12 | 1 | 1 | 2 | 10 | 0 | 0
1539.5 | 49.78 | 49.78 | 1 | 1 | 10 | 50.06 | -0.026471 | -0.405 | -4.05 | 2.975 | 2.975 | 0 | 12 | 1 | 1 | 2.975 | 10 | 0 | 0
1539.55 | 49.76 | 49.76 | 1 | 1 | 10 | 50.04 | -0.014706 | -0.305 | -3.05 | 3.475 | 3.475 | 0 | 12 | 1 | 1 | 3.475 | 10 | 0 | 0
1539.6 | 49.73 | 49.73 | 1 | 1 | 10 | 50.01 | 0 | -0.205 | -2.05 | 3.975 | 3.975 | 0 | 12 | 1 | 1 | 3.975 | 10 | 0 | 0
1539.65 | 49.71 | 49.71 | 1 | 1 | 10 | 49.99 | 0 | -0.105 | -1.05 | 4.475 | 4.475 | 0 | 12 | 1 | 1 | 4.475 | 10 | 0 | 0
1539.7 | 49.68 | 49.68 | 1 | 1 | 10 | 49.96 | 0.014706 | -0.005 | -0.05 | 4.975 | 4.975 | 0 | 12 | 1 | 1 | 4.975 | 10 | 0 | 0
1539.75 | 49.65 | 49.65 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
1539.8 | 49.63 | 49.63 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1539.85 | 49.6 | 49.6 | 1 | 1 | 10 | 49.88 | 0.24 | 0.14412 | 1.4412 | 5.7206 | 5.7206 | 0 | 12 | 1 | 1 | 5.7206 | 10 | 0 | 0
1539.9 | 49.58 | 49.58 | 1 | 1 | 10 | 49.86 | 0.43 | 0.24412 | 2.4412 | 6.2206 | 6.2206 | 0 | 12 | 1 | 1 | 6.2206 | 10 | 0 | 0
1539.95 | 49.55 | 49.55 | 1 | 1 | 10 | 49.83 | 0.715 | 0.34412 | 3.4412 | 6.7206 | 6.7206 | 0 | 12 | 1 | 1 | 6.7206 | 10 | 0 | 0
1540 | 49.53 | 49.53 | 1 | 1 | 10 | 49.81 | 0.905 | 0.44412 | 4.4412 | 7.2206 | 7.2206 | 0 | 12 | 1 | 1 | 7.2206 | 10 | 0 | 0
1540.05 | 49.5 | 49.5 | 1 | 1 | 10 | 49.78 | 1 | 0.54412 | 5.4412 | 7.7206 | 7.7206 | 0 | 12 | 1 | 1 | 7.7206 | 10 | 0 | 0
1540.1 | 49.5 | 49.5 | 1 | 1 | 10 | 49.76 | 1 | 0.64412 | 6.4412 | 8.2206 | 8.2206 | 0 | 12 | 1 | 1 | 8.2206 | 10 | 0 | 0
1540.15 | 49.53 | 49.5 | 1 | 1 | 10 | 49.73 | 1 | 0.74412 | 7.4412 | 8.7206 | 8.7206 | 0 | 12 | 1 | 1 | 8.7206 | 10 | 0 | 0
1540.2 | 49.55 | 49.5 | 1 | 1 | 10 | 49.71 | 1 | 0.84412 | 8.4412 | 9.2206 | 9.2206 | 0 | 12 | 1 | 1 | 9.2206 | 10 | 0 | 0
1540.25 | 49.58 | 49.5 | 1 | 1 | 10 | 49.68 | 1 | 0.94412 | 9.4412 | 9.7206 | 9.7206 | 0 | 12 | 1 | 1 | 9.7206 | 10 | 0 | 0
1540.3 | 49.6 | 49.5 | 1 | 1 | 10 | 49.65 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1540.35 | 49.63 | 49.5 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1540.4 | 49.65 | 49.5 | 1 | 1 | 10 | 49.65 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1540.45 | 49.68 | 49.5 | 1 | 1 | 10 | 49.68 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1540.5 | 49.71 | 49.5 | 1 | 1 | 10 | 49.71 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1540.55 | 49.73 | 49.5 | 1 | 1 | 10 | 49.73 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1540.6 | 49.76 | 49.5 | 1 | 1 | 10 | 49.76 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1540.65 | 49.78 | 49.5 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1540.7 | 49.81 | 49.53 | 1 | 1 | 10 | 49.81 | 0.905 | 0.905 | 9.05 | 9.525 | 9.525 | 0 | 12 | 1 | 1 | 9.525 | 10 | 0 | 0
1540.75 | 49.83 | 49.55 | 1 | 1 | 10 | 49.83 | 0.715 | 0.715 | 7.15 | 8.575 | 8.575 | 0 | 12 | 1 | 1 | 8.575 | 10 | 0 | 0
1540.8 | 49.86 | 49.58 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
1540.85 | 49.88 | 49.6 | 1 | 1 | 10 | 49.88 | 0.24 | 0.24 | 2.4 | 6.2 | 6.2 | 0 | 12 | 1 | 1 | 6.2 | 10 | 0 | 0
1540.9 | 49.91 | 49.63 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1540.95 | 49.94 | 49.65 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
1541 | 49.96 | 49.68 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
1541.05 | 49.99 | 49.71 | 1 | 1 | 10 | 49.99 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1541.1 | 50.01 | 49.73 | 1 | 1 | 10 | 50.01 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1541.15 | 50.04 | 49.76 | 1 | 1 | 10 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 4.9265 | 4.9265 | 0 | 12 | 1 | 1 | 4.9265 | 10 | 0 | 0
1541.2 | 50.06 | 49.78 | 1 | 1 | 10 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 4.8676 | 4.8676 | 0 | 12 | 1 | 1 | 4.8676 | 10 | 0 | 0
1541.25 | 50.09 | 49.81 | 0.905 | 0.905 | 9.05 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 4.3044 | 4.3044 | 0 | 12 | 1 | 1 | 4.3044 | 10 | 0 | 0
1541.3 | 50.12 | 49.83 | 0.715 | 0.805 | 8.05 | 50.12 | -0.24 | -0.24 | -2.4 | 2.825 | 2.825 | 0 | 12 | 1 | 1 | 2.825 | 10 | 0 | 0
1541.35 | 50.14 | 49.86 | 0.43 | 0.705 | 7.05 | 50.14 | -0.43 | -0.43 | -4.3 | 1.375 | 1.375 | 0 | 12 | 1 | 1 | 1.375 | 10 | 0 | 0
1541.4 | 50.17 | 49.88 | 0.24 | 0.605 | 6.05 | 50.17 | -0.715 | -0.715 | -7.15 | -0.55 | -0.55 | 0 | 12 | 1 | 1 | -0.55 | 10 | 0 | 0
1541.45 | 50.19 | 49.91 | 0.044118 | 0.505 | 5.05 | 50.19 | -0.905 | -0.905 | -9.05 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
1541.5 | 50.22 | 49.94 | 0.026471 | 0.405 | 4.05 | 50.22 | -1 | -1 | -10 | -2.975 | -2.975 | 0 | 12 | 1 | 1 | -2.975 | 10 | 0 | 0
1541.55 | 50.24 | 49.96 | 0.014706 | 0.305 | 3.05 | 50.24 | -1 | -1 | -10 | -3.475 | -3.475 | 0 | 12 | 1 | 1 | -3.475 | 10 | 0 | 0
1541.6 | 50.27 | 49.99 | 0 | 0.205 | 2.05 | 50.27 | -1 | -1 | -10 | -3.975 | -3.975 | 0 | 12 | 1 | 1 | -3.975 | 10 | 0 | 0
1541.65 | 50.29 | 50.01 | 0 | 0.105 | 1.05 | 50.29 | -1 | -1 | -10 | -4.475 | -4.475 | 0 | 12 | 1 | 1 | -4.475 | 10 | 0 | 0
1541.7 | 50.32 | 50.04 | -0.014706 | 0.005 | 0.05 | 50.32 | -1 | -1 | -10 | -4.975 | -4.975 | 0 | 12 | 1 | 1 | -4.975 | 10 | 0 | 0
1541.75 | 50.35 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.35 | -1 | -1 | -10 | -5.1324 | -5.1324 | 0 | 12 | 1 | 1 | -5.1324 | 10 | 0 | 0
1541.8 | 50.37 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 50.37 | -1 | -1 | -10 | -5.2206 | -5.2206 | 0 | 12 | 1 | 1 | -5.2206 | 10 | 0 | 0
1541.85 | 50.4 | 50.12 | -0.24 | -0.14412 | -1.4412 | 50.4 | -1 | -1 | -10 | -5.7206 | -5.7206 | 0 | 12 | 1 | 1 | -5.7206 | 10 | 0 | 0
1541.9 | 50.42 | 50.14 | -0.43 | -0.24412 | -2.4412 | 50.42 | -1 | -1 | -10 | -6.2206 | -6.2206 | 0 | 12 | 1 | 1 | -6.2206 | 10 | 0 | 0
1541.95 | 50.45 | 50.17 | -0.715 | -0.34412 | -3.4412 | 50.45 | -1 | -1 | -10 | -6.7206 | -6.7206 | 0 | 12 | 1 | 1 | -6.7206 | 10 | 0 | 0
1542 | 50.47 | 50.19 | -0.905 | -0.44412 | -4.4412 | 50.47 | -1 | -1 | -10 | -7.2206 | -7.2206 | 0 | 12 | 1 | 1 | -7.2206 | 10 | 0 | 0
1542.05 | 50.5 | 50.22 | -1 | -0.54412 | -5.4412 | 50.5 | -1 | -1 | -10 | -7.7206 | -7.7206 | 0 | 12 | 1 | 1 | -7.7206 | 10 | 0 | 0
1542.1 | 50.5 | 50.24 | -1 | -0.64412 | -6.4412 | 50.5 | -1 | -1 | -10 | -8.2206 | -8.2206 | 0 | 12 | 1 | 1 | -8.2206 | 10 | 0 | 0
1542.15 | 50.47 | 50.27 | -1 | -0.74412 | -7.4412 | 50.5 | -1 | -1 | -10 | -8.7206 | -8.7206 | 0 | 12 | 1 | 1 | -8.7206 | 10 | 0 | 0
1542.2 | 50.45 | 50.29 | -1 | -0.84412 | -8.4412 | 50.5 | -1 | -1 | -10 | -9.2206 | -9.2206 | 0 | 12 | 1 | 1 | -9.2206 | 10 | 0 | 0
1542.25 | 50.42 | 50.32 | -1 | -0.94412 | -9.4412 | 50.5 | -1 | -1 | -10 | -9.7206 | -9.7206 | 0 | 12 | 1 | 1 | -9.7206 | 10 | 0 | 0
1542.3 | 50.39 | 50.35 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1542.35 | 50.37 | 50.37 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1542.4 | 50.34 | 50.34 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1542.45 | 50.32 | 50.32 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1542.5 | 50.29 | 50.29 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1542.55 | 50.26 | 50.26 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1542.6 | 50.24 | 50.24 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1542.65 | 50.21 | 50.21 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1542.7 | 50.18 | 50.18 | -0.81 | -0.81 | -8.1 | 50.47 | -1 | -1 | -10 | -9.05 | -9.05 | 0 | 12 | 1 | 1 | -9.05 | 10 | 0 | 0
1542.75 | 50.16 | 50.16 | -0.62 | -0.62 | -6.2 | 50.45 | -1 | -1 | -10 | -8.1 | -8.1 | 0 | 12 | 1 | 1 | -8.1 | 10 | 0 | 0
1542.8 | 50.13 | 50.13 | -0.335 | -0.335 | -3.35 | 50.42 | -1 | -1 | -10 | -6.675 | -6.675 | 0 | 12 | 1 | 1 | -6.675 | 10 | 0 | 0
1542.85 | 50.11 | 50.11 | -0.145 | -0.145 | -1.45 | 50.39 | -1 | -1 | -10 | -5.725 | -5.725 | 0 | 12 | 1 | 1 | -5.725 | 10 | 0 | 0
1542.9 | 50.08 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 50.37 | -1 | -1 | -10 | -5.1912 | -5.1912 | 0 | 12 | 1 | 1 | -5.1912 | 10 | 0 | 0
1542.95 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.34 | -1 | -1 | -10 | -5.1029 | -5.1029 | 0 | 12 | 1 | 1 | -5.1029 | 10 | 0 | 0
1543 | 50.03 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 50.32 | -1 | -1 | -10 | -5.0441 | -5.0441 | 0 | 12 | 1 | 1 | -5.0441 | 10 | 0 | 0
1543.05 | 50 | 50 | 0 | 0 | 0 | 50.29 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1543.1 | 50 | 50 | 0 | 0 | 0 | 50.26 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1543.15 | 50 | 50 | 0 | 0 | 0 | 50.24 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1543.2 | 50 | 50 | 0 | 0 | 0 | 50.21 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1543.25 | 50 | 50 | 0 | 0 | 0 | 50.18 | -0.81 | -0.9 | -9 | -4.5 | -4.5 | 0 | 12 | 1 | 1 | -4.5 | 10 | 0 | 0
1543.3 | 50 | 50 | 0 | 0 | 0 | 50.16 | -0.62 | -0.8 | -8 | -4 | -4 | 0 | 12 | 1 | 1 | -4 | 10 | 0 | 0
1543.35 | 50 | 50 | 0 | 0 | 0 | 50.13 | -0.335 | -0.7 | -7 | -3.5 | -3.5 | 0 | 12 | 1 | 1 | -3.5 | 10 | 0 | 0
1543.4 | 50.01 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.6 | -6 | -3 | -3 | 0 | 12 | 1 | 1 | -3 | 10 | 0 | 0
1543.45 | 50.01 | 50 | 0 | 0 | 0 | 50.08 | -0.038235 | -0.5 | -5 | -2.5 | -2.5 | 0 | 12 | 1 | 1 | -2.5 | 10 | 0 | 0
1543.5 | 49.99 | 49.99 | 0 | 0 | 0 | 50.05 | -0.020588 | -0.4 | -4 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
1543.55 | 49.99 | 49.99 | 0 | 0 | 0 | 50.03 | -0.0088235 | -0.3 | -3 | -1.5 | -1.5 | 0 | 12 | 1 | 1 | -1.5 | 10 | 0 | 0
1543.6 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | -0.2 | -2 | -0.83824 | -0.83824 | 0 | 12 | 1 | 1 | -0.83824 | 10 | 0 | 0
1543.65 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | -0.1 | -1 | -0.33824 | -0.33824 | 0 | 12 | 1 | 1 | -0.33824 | 10 | 0 | 0
1543.7 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
1543.75 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
1543.8 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
1543.85 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
1543.9 | 49.89 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
1543.95 | 49.89 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
1544 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50.01 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1544.05 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1544.1 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1544.15 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 2.7868 | 2.7868 | 0 | 12 | 1 | 1 | 2.7868 | 10 | 0 | 0
1544.2 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 2.7868 | 2.7868 | 0 | 12 | 1 | 1 | 2.7868 | 10 | 0 | 0
1544.25 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 2.8456 | 2.8456 | 0 | 12 | 1 | 1 | 2.8456 | 10 | 0 | 0
1544.3 | 49.94 | 49.85 | 0.525 | 0.525 | 5.25 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 2.7574 | 2.7574 | 0 | 12 | 1 | 1 | 2.7574 | 10 | 0 | 0
1544.35 | 49.94 | 49.85 | 0.525 | 0.525 | 5.25 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 2.7574 | 2.7574 | 0 | 12 | 1 | 1 | 2.7574 | 10 | 0 | 0
1544.4 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1544.45 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1544.5 | 49.93 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1544.55 | 49.93 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1544.6 | 49.96 | 49.85 | 0.525 | 0.525 | 5.25 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 2.6985 | 2.6985 | 0 | 12 | 1 | 1 | 2.6985 | 10 | 0 | 0
1544.65 | 49.96 | 49.85 | 0.525 | 0.525 | 5.25 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 2.6985 | 2.6985 | 0 | 12 | 1 | 1 | 2.6985 | 10 | 0 | 0
1544.7 | 49.99 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1544.75 | 49.99 | 49.91 | 0.044118 | 0.425 | 4.25 | 49.99 | 0 | 0 | 0 | 2.125 | 2.125 | 0 | 12 | 1 | 1 | 2.125 | 10 | 0 | 0
1544.8 | 49.99 | 49.91 | 0.044118 | 0.325 | 3.25 | 49.99 | 0 | 0 | 0 | 1.625 | 1.625 | 0 | 12 | 1 | 1 | 1.625 | 10 | 0 | 0
1544.85 | 49.99 | 49.93 | 0.032353 | 0.225 | 2.25 | 49.99 | 0 | 0 | 0 | 1.125 | 1.125 | 0 | 12 | 1 | 1 | 1.125 | 10 | 0 | 0
1544.9 | 49.96 | 49.93 | 0.032353 | 0.125 | 1.25 | 49.99 | 0 | 0 | 0 | 0.625 | 0.625 | 0 | 12 | 1 | 1 | 0.625 | 10 | 0 | 0
1544.95 | 49.96 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 49.99 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1545 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1545.05 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1545.1 | 50.05 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.058824 | 0.058824 | 0 | 12 | 1 | 1 | 0.058824 | 10 | 0 | 0
1545.15 | 50.05 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
1545.2 | 49.97 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
1545.25 | 49.97 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
1545.3 | 49.92 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1545.35 | 49.92 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1545.4 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1545.45 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1545.5 | 49.94 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1545.55 | 49.94 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1545.6 | 50.01 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1545.65 | 50.01 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1545.7 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1545.75 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
1545.8 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
1545.85 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
1545.9 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
1545.95 | 49.95 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
1546 | 49.97 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
1546.05 | 49.97 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
1546.1 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
1546.15 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
1546.2 | 49.87 | 49.87 | 0.335 | 0.335 | 3.35 | 50.01 | 0 | 0 | 0 | 1.675 | 1.675 | 0 | 12 | 1 | 1 | 1.675 | 10 | 0 | 0
1546.25 | 49.87 | 49.87 | 0.335 | 0.335 | 3.35 | 49.99 | 0 | 0 | 0 | 1.675 | 1.675 | 0 | 12 | 1 | 1 | 1.675 | 10 | 0 | 0
1546.3 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1546.35 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 2.6691 | 2.6691 | 0 | 12 | 1 | 1 | 2.6691 | 10 | 0 | 0
1546.4 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1546.45 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1546.5 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1546.55 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1546.6 | 49.84 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1546.65 | 49.84 | 49.79 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
1546.7 | 49.89 | 49.79 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
1546.75 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.12647 | 1.2647 | 5.6324 | 5.6324 | 0 | 12 | 1 | 1 | 5.6324 | 10 | 0 | 0
1546.8 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.145 | 1.45 | 5.725 | 5.725 | 0 | 12 | 1 | 1 | 5.725 | 10 | 0 | 0
1546.85 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.145 | 1.45 | 5.725 | 5.725 | 0 | 12 | 1 | 1 | 5.725 | 10 | 0 | 0
1546.9 | 49.96 | 49.79 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
1546.95 | 49.96 | 49.79 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
1547 | 50.02 | 49.79 | 1 | 1 | 10 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 4.9853 | 4.9853 | 0 | 12 | 1 | 1 | 4.9853 | 10 | 0 | 0
1547.05 | 50.02 | 49.79 | 1 | 1 | 10 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 4.9853 | 4.9853 | 0 | 12 | 1 | 1 | 4.9853 | 10 | 0 | 0
1547.1 | 50.03 | 49.79 | 1 | 1 | 10 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.9559 | 4.9559 | 0 | 12 | 1 | 1 | 4.9559 | 10 | 0 | 0
1547.15 | 50.03 | 49.84 | 0.62 | 0.9 | 9 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.4559 | 4.4559 | 0 | 12 | 1 | 1 | 4.4559 | 10 | 0 | 0
1547.2 | 50.02 | 49.84 | 0.62 | 0.8 | 8 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 3.9559 | 3.9559 | 0 | 12 | 1 | 1 | 3.9559 | 10 | 0 | 0
1547.25 | 50.02 | 49.89 | 0.145 | 0.7 | 7 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 3.4559 | 3.4559 | 0 | 12 | 1 | 1 | 3.4559 | 10 | 0 | 0
1547.3 | 50.08 | 49.89 | 0.145 | 0.6 | 6 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 2.8088 | 2.8088 | 0 | 12 | 1 | 1 | 2.8088 | 10 | 0 | 0
1547.35 | 50.08 | 49.89 | 0.145 | 0.5 | 5 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 2.3088 | 2.3088 | 0 | 12 | 1 | 1 | 2.3088 | 10 | 0 | 0
1547.4 | 50.01 | 49.89 | 0.145 | 0.4 | 4 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 1.8088 | 1.8088 | 0 | 12 | 1 | 1 | 1.8088 | 10 | 0 | 0
1547.45 | 50.01 | 49.96 | 0.014706 | 0.3 | 3 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 1.3088 | 1.3088 | 0 | 12 | 1 | 1 | 1.3088 | 10 | 0 | 0
1547.5 | 49.94 | 49.94 | 0.026471 | 0.2 | 2 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.80882 | 0.80882 | 0 | 12 | 1 | 1 | 0.80882 | 10 | 0 | 0
1547.55 | 49.94 | 49.94 | 0.026471 | 0.1 | 1 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.30882 | 0.30882 | 0 | 12 | 1 | 1 | 0.30882 | 10 | 0 | 0
1547.6 | 50 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
1547.65 | 50 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
1547.7 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
1547.75 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
1547.8 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1547.85 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1547.9 | 49.92 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1547.95 | 49.92 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
1548 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50.01 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1548.05 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1548.1 | 49.92 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1548.15 | 49.92 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1548.2 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1548.25 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1548.3 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1548.35 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1548.4 | 49.87 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1548.45 | 49.87 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1548.5 | 49.8 | 49.8 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1548.55 | 49.8 | 49.8 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1548.6 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1548.65 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1548.7 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1548.75 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1548.8 | 49.72 | 49.72 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1548.85 | 49.72 | 49.72 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1548.9 | 49.67 | 49.67 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1548.95 | 49.67 | 49.67 | 1 | 1 | 10 | 49.87 | 0.335 | 0.14412 | 1.4412 | 5.7206 | 5.7206 | 0 | 12 | 1 | 1 | 5.7206 | 10 | 0 | 0
1549 | 49.65 | 49.65 | 1 | 1 | 10 | 49.87 | 0.335 | 0.24412 | 2.4412 | 6.2206 | 6.2206 | 0 | 12 | 1 | 1 | 6.2206 | 10 | 0 | 0
1549.05 | 49.65 | 49.65 | 1 | 1 | 10 | 49.8 | 1 | 0.34412 | 3.4412 | 6.7206 | 6.7206 | 0 | 12 | 1 | 1 | 6.7206 | 10 | 0 | 0
1549.1 | 49.59 | 49.59 | 1 | 1 | 10 | 49.8 | 1 | 0.44412 | 4.4412 | 7.2206 | 7.2206 | 0 | 12 | 1 | 1 | 7.2206 | 10 | 0 | 0
1549.15 | 49.59 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.54412 | 5.4412 | 7.7206 | 7.7206 | 0 | 12 | 1 | 1 | 7.7206 | 10 | 0 | 0
1549.2 | 49.66 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.64412 | 6.4412 | 8.2206 | 8.2206 | 0 | 12 | 1 | 1 | 8.2206 | 10 | 0 | 0
1549.25 | 49.66 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.74412 | 7.4412 | 8.7206 | 8.7206 | 0 | 12 | 1 | 1 | 8.7206 | 10 | 0 | 0
1549.3 | 49.63 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.84412 | 8.4412 | 9.2206 | 9.2206 | 0 | 12 | 1 | 1 | 9.2206 | 10 | 0 | 0
1549.35 | 49.63 | 49.59 | 1 | 1 | 10 | 49.72 | 1 | 0.94412 | 9.4412 | 9.7206 | 9.7206 | 0 | 12 | 1 | 1 | 9.7206 | 10 | 0 | 0
1549.4 | 49.61 | 49.59 | 1 | 1 | 10 | 49.72 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1549.45 | 49.61 | 49.59 | 1 | 1 | 10 | 49.67 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1549.5 | 49.54 | 49.54 | 1 | 1 | 10 | 49.67 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1549.55 | 49.54 | 49.54 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1549.6 | 49.46 | 49.46 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1549.65 | 49.46 | 49.46 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1549.7 | 49.45 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1549.75 | 49.45 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1549.8 | 49.51 | 49.45 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1549.85 | 49.51 | 49.45 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1549.9 | 49.5 | 49.45 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1549.95 | 49.5 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1550 | 49.54 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1550.05 | 49.54 | 49.45 | 1 | 1 | 10 | 49.54 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1550.1 | 49.59 | 49.45 | 1 | 1 | 10 | 49.59 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1550.15 | 49.59 | 49.45 | 1 | 1 | 10 | 49.59 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1550.2 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1550.25 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1550.3 | 49.61 | 49.45 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1550.35 | 49.61 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1550.4 | 49.53 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1550.45 | 49.53 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1550.5 | 49.54 | 49.5 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1550.55 | 49.54 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1550.6 | 49.61 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1550.65 | 49.61 | 49.53 | 1 | 1 | 10 | 49.61 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1550.7 | 49.66 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1550.75 | 49.66 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1550.8 | 49.64 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1550.85 | 49.64 | 49.53 | 1 | 1 | 10 | 49.66 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1550.9 | 49.69 | 49.53 | 1 | 1 | 10 | 49.69 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1550.95 | 49.69 | 49.53 | 1 | 1 | 10 | 49.69 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1551 | 49.74 | 49.53 | 1 | 1 | 10 | 49.74 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1551.05 | 49.74 | 49.54 | 1 | 1 | 10 | 49.74 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1551.1 | 49.78 | 49.54 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1551.15 | 49.78 | 49.61 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1551.2 | 49.82 | 49.61 | 1 | 1 | 10 | 49.82 | 0.81 | 0.81 | 8.1 | 9.05 | 9.05 | 0 | 12 | 1 | 1 | 9.05 | 10 | 0 | 0
1551.25 | 49.82 | 49.64 | 1 | 1 | 10 | 49.82 | 0.81 | 0.81 | 8.1 | 9.05 | 9.05 | 0 | 12 | 1 | 1 | 9.05 | 10 | 0 | 0
1551.3 | 49.86 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
1551.35 | 49.86 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
1551.4 | 49.84 | 49.64 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
1551.45 | 49.84 | 49.69 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
1551.5 | 49.91 | 49.69 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1551.55 | 49.91 | 49.74 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1551.6 | 49.97 | 49.74 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1551.65 | 49.97 | 49.78 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1551.7 | 50.03 | 49.78 | 1 | 1 | 10 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.9559 | 4.9559 | 0 | 12 | 1 | 1 | 4.9559 | 10 | 0 | 0
1551.75 | 50.03 | 49.82 | 0.81 | 0.9 | 9 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.4559 | 4.4559 | 0 | 12 | 1 | 1 | 4.4559 | 10 | 0 | 0
1551.8 | 50.05 | 49.82 | 0.81 | 0.81 | 8.1 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 3.9471 | 3.9471 | 0 | 12 | 1 | 1 | 3.9471 | 10 | 0 | 0
1551.85 | 50.05 | 49.84 | 0.62 | 0.71 | 7.1 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 3.4471 | 3.4471 | 0 | 12 | 1 | 1 | 3.4471 | 10 | 0 | 0
1551.9 | 50.01 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
1551.95 | 50.01 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
1552 | 49.95 | 49.84 | 0.62 | 0.62 | 6.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.9971 | 2.9971 | 0 | 12 | 1 | 1 | 2.9971 | 10 | 0 | 0
1552.05 | 49.95 | 49.91 | 0.044118 | 0.52 | 5.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 2.4971 | 2.4971 | 0 | 12 | 1 | 1 | 2.4971 | 10 | 0 | 0
1552.1 | 49.99 | 49.91 | 0.044118 | 0.42 | 4.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 1.9971 | 1.9971 | 0 | 12 | 1 | 1 | 1.9971 | 10 | 0 | 0
1552.15 | 49.99 | 49.95 | 0.020588 | 0.32 | 3.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 1.4971 | 1.4971 | 0 | 12 | 1 | 1 | 1.4971 | 10 | 0 | 0
1552.2 | 49.92 | 49.92 | 0.038235 | 0.22 | 2.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.99706 | 0.99706 | 0 | 12 | 1 | 1 | 0.99706 | 10 | 0 | 0
1552.25 | 49.92 | 49.92 | 0.038235 | 0.12 | 1.2 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.49706 | 0.49706 | 0 | 12 | 1 | 1 | 0.49706 | 10 | 0 | 0
1552.3 | 49.97 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1552.35 | 49.97 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1552.4 | 50.02 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1552.45 | 50.02 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.17647 | 0.17647 | 0 | 12 | 1 | 1 | 0.17647 | 10 | 0 | 0
1552.5 | 50.07 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1552.55 | 50.07 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1552.6 | 50.06 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1552.65 | 50.06 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.07 | -0.032353 | -0.032353 | -0.32353 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1552.7 | 50.13 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
1552.75 | 50.13 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
1552.8 | 50.09 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.4838 | -1.4838 | 0 | 12 | 1 | 1 | -1.4838 | 10 | 0 | 0
1552.85 | 50.09 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6309 | -1.6309 | 0 | 12 | 1 | 1 | -1.6309 | 10 | 0 | 0
1552.9 | 50.07 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6309 | -1.6309 | 0 | 12 | 1 | 1 | -1.6309 | 10 | 0 | 0
1552.95 | 50.07 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6897 | -1.6897 | 0 | 12 | 1 | 1 | -1.6897 | 10 | 0 | 0
1553 | 50.07 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.13 | -0.335 | -0.335 | -3.35 | -1.6897 | -1.6897 | 0 | 12 | 1 | 1 | -1.6897 | 10 | 0 | 0
1553.05 | 50.07 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.13 | -0.335 | -0.335 | -3.35 | -1.8074 | -1.8074 | 0 | 12 | 1 | 1 | -1.8074 | 10 | 0 | 0
1553.1 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.13 | -0.335 | -0.335 | -3.35 | -1.7779 | -1.7779 | 0 | 12 | 1 | 1 | -1.7779 | 10 | 0 | 0
1553.15 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.13 | -0.335 | -0.335 | -3.35 | -1.7779 | -1.7779 | 0 | 12 | 1 | 1 | -1.7779 | 10 | 0 | 0
1553.2 | 50.01 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
1553.25 | 50.01 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
1553.3 | 50.07 | 50.01 | 0 | 0 | 0 | 50.13 | -0.335 | -0.335 | -3.35 | -1.675 | -1.675 | 0 | 12 | 1 | 1 | -1.675 | 10 | 0 | 0
1553.35 | 50.07 | 50.01 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.235 | -2.35 | -1.175 | -1.175 | 0 | 12 | 1 | 1 | -1.175 | 10 | 0 | 0
1553.4 | 50.05 | 50.01 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.135 | -1.35 | -0.675 | -0.675 | 0 | 12 | 1 | 1 | -0.675 | 10 | 0 | 0
1553.45 | 50.05 | 50.01 | 0 | 0 | 0 | 50.07 | -0.032353 | -0.035 | -0.35 | -0.175 | -0.175 | 0 | 12 | 1 | 1 | -0.175 | 10 | 0 | 0
1553.5 | 50.1 | 50.01 | 0 | 0 | 0 | 50.1 | -0.05 | -0.05 | -0.5 | -0.25 | -0.25 | 0 | 12 | 1 | 1 | -0.25 | 10 | 0 | 0
1553.55 | 50.1 | 50.01 | 0 | 0 | 0 | 50.1 | -0.05 | -0.05 | -0.5 | -0.25 | -0.25 | 0 | 12 | 1 | 1 | -0.25 | 10 | 0 | 0
1553.6 | 50.11 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1553.65 | 50.11 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1553.7 | 50.06 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1553.75 | 50.06 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1553.8 | 50.04 | 50.01 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1553.85 | 50.04 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1553.9 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1553.95 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1554 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1554.05 | 50.07 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1554.1 | 50.11 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1554.15 | 50.11 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1554.2 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1554.25 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1554.3 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1554.35 | 50.09 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.11 | -0.145 | -0.145 | -1.45 | -0.79853 | -0.79853 | 0 | 12 | 1 | 1 | -0.79853 | 10 | 0 | 0
1554.4 | 50.02 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.11 | -0.145 | -0.145 | -1.45 | -0.73971 | -0.73971 | 0 | 12 | 1 | 1 | -0.73971 | 10 | 0 | 0
1554.45 | 50.02 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 50.11 | -0.145 | -0.145 | -1.45 | -0.73971 | -0.73971 | 0 | 12 | 1 | 1 | -0.73971 | 10 | 0 | 0
1554.5 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1554.55 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1554.6 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1554.65 | 50 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1554.7 | 50.01 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.145 | -1.45 | -0.725 | -0.725 | 0 | 12 | 1 | 1 | -0.725 | 10 | 0 | 0
1554.75 | 50.01 | 50 | 0 | 0 | 0 | 50.09 | -0.044118 | -0.045 | -0.45 | -0.225 | -0.225 | 0 | 12 | 1 | 1 | -0.225 | 10 | 0 | 0
1554.8 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
1554.85 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
1554.9 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.09 | -0.044118 | -0.044118 | -0.44118 | -0.17647 | -0.17647 | 0 | 12 | 1 | 1 | -0.17647 | 10 | 0 | 0
1554.95 | 49.97 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1555 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 0.14706 | 0.14706 | 0 | 12 | 1 | 1 | 0.14706 | 10 | 0 | 0
1555.05 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1555.1 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1555.15 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1555.2 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1555.25 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1555.3 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1555.35 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1555.4 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1555.45 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1555.5 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1555.55 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1555.6 | 50 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1555.65 | 50 | 50 | 0 | 0 | 0 | 50.01 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1555.7 | 49.5 | 49.5 | 1 | 1 | 10 | 50.01 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1555.75 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1555.8 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1555.85 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1555.9 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1555.95 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1556 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1556.05 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1556.1 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1556.15 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1556.2 | 49.5 | 49.5 | 1 | 1 | 10 | 50 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1556.25 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.1 | 1 | 5.5 | 5.5 | 0 | 12 | 1 | 1 | 5.5 | 10 | 0 | 0
1556.3 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.2 | 2 | 6 | 6 | 0 | 12 | 1 | 1 | 6 | 10 | 0 | 0
1556.35 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.3 | 3 | 6.5 | 6.5 | 0 | 12 | 1 | 1 | 6.5 | 10 | 0 | 0
1556.4 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.4 | 4 | 7 | 7 | 0 | 12 | 1 | 1 | 7 | 10 | 0 | 0
1556.45 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.5 | 5 | 7.5 | 7.5 | 0 | 12 | 1 | 1 | 7.5 | 10 | 0 | 0
1556.5 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.6 | 6 | 8 | 8 | 0 | 12 | 1 | 1 | 8 | 10 | 0 | 0
1556.55 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.7 | 7 | 8.5 | 8.5 | 0 | 12 | 1 | 1 | 8.5 | 10 | 0 | 0
1556.6 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.8 | 8 | 9 | 9 | 0 | 12 | 1 | 1 | 9 | 10 | 0 | 0
1556.65 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 0.9 | 9 | 9.5 | 9.5 | 0 | 12 | 1 | 1 | 9.5 | 10 | 0 | 0
1556.7 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1556.75 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1556.8 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1556.85 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1556.9 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1556.95 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1557 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1557.05 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1557.1 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1557.15 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1557.2 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1557.25 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1557.3 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1557.35 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1557.4 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1557.45 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1557.5 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1557.55 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1557.6 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1557.65 | 49.5 | 49.5 | 1 | 1 | 10 | 49.5 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1557.7 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1557.75 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1557.8 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1557.85 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1557.9 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1557.95 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1558 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1558.05 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1558.1 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1558.15 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1558.2 | 50.5 | 49.5 | 1 | 1 | 10 | 50.5 | -1 | -1 | -10 | 0 | 0 | 0 | 12 | 1 | 1 | 0 | 10 | 0 | 0
1558.25 | 50.5 | 50.5 | -1 | 0.9 | 9 | 50.5 | -1 | -1 | -10 | -0.5 | -0.5 | 0 | 12 | 1 | 1 | -0.5 | 10 | 0 | 0
1558.3 | 50.5 | 50.5 | -1 | 0.8 | 8 | 50.5 | -1 | -1 | -10 | -1 | -1 | 0 | 12 | 1 | 1 | -1 | 10 | 0 | 0
1558.35 | 50.5 | 50.5 | -1 | 0.7 | 7 | 50.5 | -1 | -1 | -10 | -1.5 | -1.5 | 0 | 12 | 1 | 1 | -1.5 | 10 | 0 | 0
1558.4 | 50.5 | 50.5 | -1 | 0.6 | 6 | 50.5 | -1 | -1 | -10 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
1558.45 | 50.5 | 50.5 | -1 | 0.5 | 5 | 50.5 | -1 | -1 | -10 | -2.5 | -2.5 | 0 | 12 | 1 | 1 | -2.5 | 10 | 0 | 0
1558.5 | 50.5 | 50.5 | -1 | 0.4 | 4 | 50.5 | -1 | -1 | -10 | -3 | -3 | 0 | 12 | 1 | 1 | -3 | 10 | 0 | 0
1558.55 | 50.5 | 50.5 | -1 | 0.3 | 3 | 50.5 | -1 | -1 | -10 | -3.5 | -3.5 | 0 | 12 | 1 | 1 | -3.5 | 10 | 0 | 0
1558.6 | 50.5 | 50.5 | -1 | 0.2 | 2 | 50.5 | -1 | -1 | -10 | -4 | -4 | 0 | 12 | 1 | 1 | -4 | 10 | 0 | 0
1558.65 | 50.5 | 50.5 | -1 | 0.1 | 1 | 50.5 | -1 | -1 | -10 | -4.5 | -4.5 | 0 | 12 | 1 | 1 | -4.5 | 10 | 0 | 0
1558.7 | 50.5 | 50.5 | -1 | 0 | 0 | 50.5 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1558.75 | 50.5 | 50.5 | -1 | -0.1 | -1 | 50.5 | -1 | -1 | -10 | -5.5 | -5.5 | 0 | 12 | 1 | 1 | -5.5 | 10 | 0 | 0
1558.8 | 50.5 | 50.5 | -1 | -0.2 | -2 | 50.5 | -1 | -1 | -10 | -6 | -6 | 0 | 12 | 1 | 1 | -6 | 10 | 0 | 0
1558.85 | 50.5 | 50.5 | -1 | -0.3 | -3 | 50.5 | -1 | -1 | -10 | -6.5 | -6.5 | 0 | 12 | 1 | 1 | -6.5 | 10 | 0 | 0
1558.9 | 50.5 | 50.5 | -1 | -0.4 | -4 | 50.5 | -1 | -1 | -10 | -7 | -7 | 0 | 12 | 1 | 1 | -7 | 10 | 0 | 0
1558.95 | 50.5 | 50.5 | -1 | -0.5 | -5 | 50.5 | -1 | -1 | -10 | -7.5 | -7.5 | 0 | 12 | 1 | 1 | -7.5 | 10 | 0 | 0
1559 | 50.5 | 50.5 | -1 | -0.6 | -6 | 50.5 | -1 | -1 | -10 | -8 | -8 | 0 | 12 | 1 | 1 | -8 | 10 | 0 | 0
1559.05 | 50.5 | 50.5 | -1 | -0.7 | -7 | 50.5 | -1 | -1 | -10 | -8.5 | -8.5 | 0 | 12 | 1 | 1 | -8.5 | 10 | 0 | 0
1559.1 | 50.5 | 50.5 | -1 | -0.8 | -8 | 50.5 | -1 | -1 | -10 | -9 | -9 | 0 | 12 | 1 | 1 | -9 | 10 | 0 | 0
1559.15 | 50.5 | 50.5 | -1 | -0.9 | -9 | 50.5 | -1 | -1 | -10 | -9.5 | -9.5 | 0 | 12 | 1 | 1 | -9.5 | 10 | 0 | 0
1559.2 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1559.25 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1559.3 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1559.35 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1559.4 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1559.45 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1559.5 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1559.55 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1559.6 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1559.65 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1559.7 | 50.5 | 50.5 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1559.75 | 50.47 | 50.47 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1559.8 | 50.45 | 50.45 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1559.85 | 50.42 | 50.42 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1559.9 | 50.4 | 50.4 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1559.95 | 50.37 | 50.37 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1560 | 50.35 | 50.35 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1560.05 | 50.32 | 50.32 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1560.1 | 50.29 | 50.29 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1560.15 | 50.27 | 50.27 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1560.2 | 50.24 | 50.24 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1560.25 | 50.22 | 50.22 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1560.3 | 50.19 | 50.19 | -0.905 | -0.905 | -9.05 | 50.47 | -1 | -1 | -10 | -9.525 | -9.525 | 0 | 12 | 1 | 1 | -9.525 | 10 | 0 | 0
1560.35 | 50.17 | 50.17 | -0.715 | -0.715 | -7.15 | 50.45 | -1 | -1 | -10 | -8.575 | -8.575 | 0 | 12 | 1 | 1 | -8.575 | 10 | 0 | 0
1560.4 | 50.14 | 50.14 | -0.43 | -0.43 | -4.3 | 50.42 | -1 | -1 | -10 | -7.15 | -7.15 | 0 | 12 | 1 | 1 | -7.15 | 10 | 0 | 0
1560.45 | 50.12 | 50.12 | -0.24 | -0.24 | -2.4 | 50.4 | -1 | -1 | -10 | -6.2 | -6.2 | 0 | 12 | 1 | 1 | -6.2 | 10 | 0 | 0
1560.5 | 50.09 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 50.37 | -1 | -1 | -10 | -5.2206 | -5.2206 | 0 | 12 | 1 | 1 | -5.2206 | 10 | 0 | 0
1560.55 | 50.06 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.35 | -1 | -1 | -10 | -5.1324 | -5.1324 | 0 | 12 | 1 | 1 | -5.1324 | 10 | 0 | 0
1560.6 | 50.04 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 50.32 | -1 | -1 | -10 | -5.0735 | -5.0735 | 0 | 12 | 1 | 1 | -5.0735 | 10 | 0 | 0
1560.65 | 50.01 | 50.01 | 0 | 0 | 0 | 50.29 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1560.7 | 49.99 | 49.99 | 0 | 0 | 0 | 50.27 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1560.75 | 49.96 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.24 | -1 | -1 | -10 | -4.9265 | -4.9265 | 0 | 12 | 1 | 1 | -4.9265 | 10 | 0 | 0
1560.8 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.22 | -1 | -1 | -10 | -4.8676 | -4.8676 | 0 | 12 | 1 | 1 | -4.8676 | 10 | 0 | 0
1560.85 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.19 | -0.905 | -0.905 | -9.05 | -4.3044 | -4.3044 | 0 | 12 | 1 | 1 | -4.3044 | 10 | 0 | 0
1560.9 | 49.88 | 49.88 | 0.24 | 0.24 | 2.4 | 50.17 | -0.715 | -0.805 | -8.05 | -2.825 | -2.825 | 0 | 12 | 1 | 1 | -2.825 | 10 | 0 | 0
1560.95 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.14 | -0.43 | -0.705 | -7.05 | -1.375 | -1.375 | 0 | 12 | 1 | 1 | -1.375 | 10 | 0 | 0
1561 | 49.83 | 49.83 | 0.715 | 0.715 | 7.15 | 50.12 | -0.24 | -0.605 | -6.05 | 0.55 | 0.55 | 0 | 12 | 1 | 1 | 0.55 | 10 | 0 | 0
1561.05 | 49.81 | 49.81 | 0.905 | 0.905 | 9.05 | 50.09 | -0.044118 | -0.505 | -5.05 | 2 | 2 | 0 | 12 | 1 | 1 | 2 | 10 | 0 | 0
1561.1 | 49.78 | 49.78 | 1 | 1 | 10 | 50.06 | -0.026471 | -0.405 | -4.05 | 2.975 | 2.975 | 0 | 12 | 1 | 1 | 2.975 | 10 | 0 | 0
1561.15 | 49.76 | 49.76 | 1 | 1 | 10 | 50.04 | -0.014706 | -0.305 | -3.05 | 3.475 | 3.475 | 0 | 12 | 1 | 1 | 3.475 | 10 | 0 | 0
1561.2 | 49.73 | 49.73 | 1 | 1 | 10 | 50.01 | 0 | -0.205 | -2.05 | 3.975 | 3.975 | 0 | 12 | 1 | 1 | 3.975 | 10 | 0 | 0
1561.25 | 49.71 | 49.71 | 1 | 1 | 10 | 49.99 | 0 | -0.105 | -1.05 | 4.475 | 4.475 | 0 | 12 | 1 | 1 | 4.475 | 10 | 0 | 0
1561.3 | 49.68 | 49.68 | 1 | 1 | 10 | 49.96 | 0.014706 | -0.005 | -0.05 | 4.975 | 4.975 | 0 | 12 | 1 | 1 | 4.975 | 10 | 0 | 0
1561.35 | 49.65 | 49.65 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
1561.4 | 49.63 | 49.63 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1561.45 | 49.6 | 49.6 | 1 | 1 | 10 | 49.88 | 0.24 | 0.14412 | 1.4412 | 5.7206 | 5.7206 | 0 | 12 | 1 | 1 | 5.7206 | 10 | 0 | 0
1561.5 | 49.58 | 49.58 | 1 | 1 | 10 | 49.86 | 0.43 | 0.24412 | 2.4412 | 6.2206 | 6.2206 | 0 | 12 | 1 | 1 | 6.2206 | 10 | 0 | 0
1561.55 | 49.55 | 49.55 | 1 | 1 | 10 | 49.83 | 0.715 | 0.34412 | 3.4412 | 6.7206 | 6.7206 | 0 | 12 | 1 | 1 | 6.7206 | 10 | 0 | 0
1561.6 | 49.53 | 49.53 | 1 | 1 | 10 | 49.81 | 0.905 | 0.44412 | 4.4412 | 7.2206 | 7.2206 | 0 | 12 | 1 | 1 | 7.2206 | 10 | 0 | 0
1561.65 | 49.5 | 49.5 | 1 | 1 | 10 | 49.78 | 1 | 0.54412 | 5.4412 | 7.7206 | 7.7206 | 0 | 12 | 1 | 1 | 7.7206 | 10 | 0 | 0
1561.7 | 49.5 | 49.5 | 1 | 1 | 10 | 49.76 | 1 | 0.64412 | 6.4412 | 8.2206 | 8.2206 | 0 | 12 | 1 | 1 | 8.2206 | 10 | 0 | 0
1561.75 | 49.53 | 49.5 | 1 | 1 | 10 | 49.73 | 1 | 0.74412 | 7.4412 | 8.7206 | 8.7206 | 0 | 12 | 1 | 1 | 8.7206 | 10 | 0 | 0
1561.8 | 49.55 | 49.5 | 1 | 1 | 10 | 49.71 | 1 | 0.84412 | 8.4412 | 9.2206 | 9.2206 | 0 | 12 | 1 | 1 | 9.2206 | 10 | 0 | 0
1561.85 | 49.58 | 49.5 | 1 | 1 | 10 | 49.68 | 1 | 0.94412 | 9.4412 | 9.7206 | 9.7206 | 0 | 12 | 1 | 1 | 9.7206 | 10 | 0 | 0
1561.9 | 49.6 | 49.5 | 1 | 1 | 10 | 49.65 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1561.95 | 49.63 | 49.5 | 1 | 1 | 10 | 49.63 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1562 | 49.65 | 49.5 | 1 | 1 | 10 | 49.65 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1562.05 | 49.68 | 49.5 | 1 | 1 | 10 | 49.68 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1562.1 | 49.71 | 49.5 | 1 | 1 | 10 | 49.71 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1562.15 | 49.73 | 49.5 | 1 | 1 | 10 | 49.73 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1562.2 | 49.76 | 49.5 | 1 | 1 | 10 | 49.76 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1562.25 | 49.78 | 49.5 | 1 | 1 | 10 | 49.78 | 1 | 1 | 10 | 10 | 10 | 0 | 12 | 1 | 1 | 10 | 10 | 0 | 0
1562.3 | 49.81 | 49.53 | 1 | 1 | 10 | 49.81 | 0.905 | 0.905 | 9.05 | 9.525 | 9.525 | 0 | 12 | 1 | 1 | 9.525 | 10 | 0 | 0
1562.35 | 49.83 | 49.55 | 1 | 1 | 10 | 49.83 | 0.715 | 0.715 | 7.15 | 8.575 | 8.575 | 0 | 12 | 1 | 1 | 8.575 | 10 | 0 | 0
1562.4 | 49.86 | 49.58 | 1 | 1 | 10 | 49.86 | 0.43 | 0.43 | 4.3 | 7.15 | 7.15 | 0 | 12 | 1 | 1 | 7.15 | 10 | 0 | 0
1562.45 | 49.88 | 49.6 | 1 | 1 | 10 | 49.88 | 0.24 | 0.24 | 2.4 | 6.2 | 6.2 | 0 | 12 | 1 | 1 | 6.2 | 10 | 0 | 0
1562.5 | 49.91 | 49.63 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1562.55 | 49.94 | 49.65 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
1562.6 | 49.96 | 49.68 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
1562.65 | 49.99 | 49.71 | 1 | 1 | 10 | 49.99 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1562.7 | 50.01 | 49.73 | 1 | 1 | 10 | 50.01 | 0 | 0 | 0 | 5 | 5 | 0 | 12 | 1 | 1 | 5 | 10 | 0 | 0
1562.75 | 50.04 | 49.76 | 1 | 1 | 10 | 50.04 | -0.014706 | -0.014706 | -0.14706 | 4.9265 | 4.9265 | 0 | 12 | 1 | 1 | 4.9265 | 10 | 0 | 0
1562.8 | 50.06 | 49.78 | 1 | 1 | 10 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 4.8676 | 4.8676 | 0 | 12 | 1 | 1 | 4.8676 | 10 | 0 | 0
1562.85 | 50.09 | 49.81 | 0.905 | 0.905 | 9.05 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 4.3044 | 4.3044 | 0 | 12 | 1 | 1 | 4.3044 | 10 | 0 | 0
1562.9 | 50.12 | 49.83 | 0.715 | 0.805 | 8.05 | 50.12 | -0.24 | -0.24 | -2.4 | 2.825 | 2.825 | 0 | 12 | 1 | 1 | 2.825 | 10 | 0 | 0
1562.95 | 50.14 | 49.86 | 0.43 | 0.705 | 7.05 | 50.14 | -0.43 | -0.43 | -4.3 | 1.375 | 1.375 | 0 | 12 | 1 | 1 | 1.375 | 10 | 0 | 0
1563 | 50.17 | 49.88 | 0.24 | 0.605 | 6.05 | 50.17 | -0.715 | -0.715 | -7.15 | -0.55 | -0.55 | 0 | 12 | 1 | 1 | -0.55 | 10 | 0 | 0
1563.05 | 50.19 | 49.91 | 0.044118 | 0.505 | 5.05 | 50.19 | -0.905 | -0.905 | -9.05 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
1563.1 | 50.22 | 49.94 | 0.026471 | 0.405 | 4.05 | 50.22 | -1 | -1 | -10 | -2.975 | -2.975 | 0 | 12 | 1 | 1 | -2.975 | 10 | 0 | 0
1563.15 | 50.24 | 49.96 | 0.014706 | 0.305 | 3.05 | 50.24 | -1 | -1 | -10 | -3.475 | -3.475 | 0 | 12 | 1 | 1 | -3.475 | 10 | 0 | 0
1563.2 | 50.27 | 49.99 | 0 | 0.205 | 2.05 | 50.27 | -1 | -1 | -10 | -3.975 | -3.975 | 0 | 12 | 1 | 1 | -3.975 | 10 | 0 | 0
1563.25 | 50.29 | 50.01 | 0 | 0.105 | 1.05 | 50.29 | -1 | -1 | -10 | -4.475 | -4.475 | 0 | 12 | 1 | 1 | -4.475 | 10 | 0 | 0
1563.3 | 50.32 | 50.04 | -0.014706 | 0.005 | 0.05 | 50.32 | -1 | -1 | -10 | -4.975 | -4.975 | 0 | 12 | 1 | 1 | -4.975 | 10 | 0 | 0
1563.35 | 50.35 | 50.06 | -0.026471 | -0.026471 | -0.26471 | 50.35 | -1 | -1 | -10 | -5.1324 | -5.1324 | 0 | 12 | 1 | 1 | -5.1324 | 10 | 0 | 0
1563.4 | 50.37 | 50.09 | -0.044118 | -0.044118 | -0.44118 | 50.37 | -1 | -1 | -10 | -5.2206 | -5.2206 | 0 | 12 | 1 | 1 | -5.2206 | 10 | 0 | 0
1563.45 | 50.4 | 50.12 | -0.24 | -0.14412 | -1.4412 | 50.4 | -1 | -1 | -10 | -5.7206 | -5.7206 | 0 | 12 | 1 | 1 | -5.7206 | 10 | 0 | 0
1563.5 | 50.42 | 50.14 | -0.43 | -0.24412 | -2.4412 | 50.42 | -1 | -1 | -10 | -6.2206 | -6.2206 | 0 | 12 | 1 | 1 | -6.2206 | 10 | 0 | 0
1563.55 | 50.45 | 50.17 | -0.715 | -0.34412 | -3.4412 | 50.45 | -1 | -1 | -10 | -6.7206 | -6.7206 | 0 | 12 | 1 | 1 | -6.7206 | 10 | 0 | 0
1563.6 | 50.47 | 50.19 | -0.905 | -0.44412 | -4.4412 | 50.47 | -1 | -1 | -10 | -7.2206 | -7.2206 | 0 | 12 | 1 | 1 | -7.2206 | 10 | 0 | 0
1563.65 | 50.5 | 50.22 | -1 | -0.54412 | -5.4412 | 50.5 | -1 | -1 | -10 | -7.7206 | -7.7206 | 0 | 12 | 1 | 1 | -7.7206 | 10 | 0 | 0
1563.7 | 50.5 | 50.24 | -1 | -0.64412 | -6.4412 | 50.5 | -1 | -1 | -10 | -8.2206 | -8.2206 | 0 | 12 | 1 | 1 | -8.2206 | 10 | 0 | 0
1563.75 | 50.47 | 50.27 | -1 | -0.74412 | -7.4412 | 50.5 | -1 | -1 | -10 | -8.7206 | -8.7206 | 0 | 12 | 1 | 1 | -8.7206 | 10 | 0 | 0
1563.8 | 50.45 | 50.29 | -1 | -0.84412 | -8.4412 | 50.5 | -1 | -1 | -10 | -9.2206 | -9.2206 | 0 | 12 | 1 | 1 | -9.2206 | 10 | 0 | 0
1563.85 | 50.42 | 50.32 | -1 | -0.94412 | -9.4412 | 50.5 | -1 | -1 | -10 | -9.7206 | -9.7206 | 0 | 12 | 1 | 1 | -9.7206 | 10 | 0 | 0
1563.9 | 50.39 | 50.35 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1563.95 | 50.37 | 50.37 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1564 | 50.34 | 50.34 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1564.05 | 50.32 | 50.32 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1564.1 | 50.29 | 50.29 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1564.15 | 50.26 | 50.26 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1564.2 | 50.24 | 50.24 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1564.25 | 50.21 | 50.21 | -1 | -1 | -10 | 50.5 | -1 | -1 | -10 | -10 | -10 | 0 | 12 | 1 | 1 | -10 | 10 | 0 | 0
1564.3 | 50.18 | 50.18 | -0.81 | -0.81 | -8.1 | 50.47 | -1 | -1 | -10 | -9.05 | -9.05 | 0 | 12 | 1 | 1 | -9.05 | 10 | 0 | 0
1564.35 | 50.16 | 50.16 | -0.62 | -0.62 | -6.2 | 50.45 | -1 | -1 | -10 | -8.1 | -8.1 | 0 | 12 | 1 | 1 | -8.1 | 10 | 0 | 0
1564.4 | 50.13 | 50.13 | -0.335 | -0.335 | -3.35 | 50.42 | -1 | -1 | -10 | -6.675 | -6.675 | 0 | 12 | 1 | 1 | -6.675 | 10 | 0 | 0
1564.45 | 50.11 | 50.11 | -0.145 | -0.145 | -1.45 | 50.39 | -1 | -1 | -10 | -5.725 | -5.725 | 0 | 12 | 1 | 1 | -5.725 | 10 | 0 | 0
1564.5 | 50.08 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 50.37 | -1 | -1 | -10 | -5.1912 | -5.1912 | 0 | 12 | 1 | 1 | -5.1912 | 10 | 0 | 0
1564.55 | 50.05 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 50.34 | -1 | -1 | -10 | -5.1029 | -5.1029 | 0 | 12 | 1 | 1 | -5.1029 | 10 | 0 | 0
1564.6 | 50.03 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 50.32 | -1 | -1 | -10 | -5.0441 | -5.0441 | 0 | 12 | 1 | 1 | -5.0441 | 10 | 0 | 0
1564.65 | 50 | 50 | 0 | 0 | 0 | 50.29 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1564.7 | 50 | 50 | 0 | 0 | 0 | 50.26 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1564.75 | 50 | 50 | 0 | 0 | 0 | 50.24 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1564.8 | 50 | 50 | 0 | 0 | 0 | 50.21 | -1 | -1 | -10 | -5 | -5 | 0 | 12 | 1 | 1 | -5 | 10 | 0 | 0
1564.85 | 50 | 50 | 0 | 0 | 0 | 50.18 | -0.81 | -0.9 | -9 | -4.5 | -4.5 | 0 | 12 | 1 | 1 | -4.5 | 10 | 0 | 0
1564.9 | 50 | 50 | 0 | 0 | 0 | 50.16 | -0.62 | -0.8 | -8 | -4 | -4 | 0 | 12 | 1 | 1 | -4 | 10 | 0 | 0
1564.95 | 50 | 50 | 0 | 0 | 0 | 50.13 | -0.335 | -0.7 | -7 | -3.5 | -3.5 | 0 | 12 | 1 | 1 | -3.5 | 10 | 0 | 0
1565 | 50.01 | 50 | 0 | 0 | 0 | 50.11 | -0.145 | -0.6 | -6 | -3 | -3 | 0 | 12 | 1 | 1 | -3 | 10 | 0 | 0
1565.05 | 50.01 | 50 | 0 | 0 | 0 | 50.08 | -0.038235 | -0.5 | -5 | -2.5 | -2.5 | 0 | 12 | 1 | 1 | -2.5 | 10 | 0 | 0
1565.1 | 49.99 | 49.99 | 0 | 0 | 0 | 50.05 | -0.020588 | -0.4 | -4 | -2 | -2 | 0 | 12 | 1 | 1 | -2 | 10 | 0 | 0
1565.15 | 49.99 | 49.99 | 0 | 0 | 0 | 50.03 | -0.0088235 | -0.3 | -3 | -1.5 | -1.5 | 0 | 12 | 1 | 1 | -1.5 | 10 | 0 | 0
1565.2 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | -0.2 | -2 | -0.83824 | -0.83824 | 0 | 12 | 1 | 1 | -0.83824 | 10 | 0 | 0
1565.25 | 49.93 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | -0.1 | -1 | -0.33824 | -0.33824 | 0 | 12 | 1 | 1 | -0.33824 | 10 | 0 | 0
1565.3 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
1565.35 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
1565.4 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
1565.45 | 49.86 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
1565.5 | 49.89 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
1565.55 | 49.89 | 49.86 | 0.43 | 0.43 | 4.3 | 50.01 | 0 | 0 | 0 | 2.15 | 2.15 | 0 | 12 | 1 | 1 | 2.15 | 10 | 0 | 0
1565.6 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50.01 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1565.65 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1565.7 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1565.75 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 2.7868 | 2.7868 | 0 | 12 | 1 | 1 | 2.7868 | 10 | 0 | 0
1565.8 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 2.7868 | 2.7868 | 0 | 12 | 1 | 1 | 2.7868 | 10 | 0 | 0
1565.85 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 2.8456 | 2.8456 | 0 | 12 | 1 | 1 | 2.8456 | 10 | 0 | 0
1565.9 | 49.94 | 49.85 | 0.525 | 0.525 | 5.25 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 2.7574 | 2.7574 | 0 | 12 | 1 | 1 | 2.7574 | 10 | 0 | 0
1565.95 | 49.94 | 49.85 | 0.525 | 0.525 | 5.25 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 2.7574 | 2.7574 | 0 | 12 | 1 | 1 | 2.7574 | 10 | 0 | 0
1566 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1566.05 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1566.1 | 49.93 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1566.15 | 49.93 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1566.2 | 49.96 | 49.85 | 0.525 | 0.525 | 5.25 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 2.6985 | 2.6985 | 0 | 12 | 1 | 1 | 2.6985 | 10 | 0 | 0
1566.25 | 49.96 | 49.85 | 0.525 | 0.525 | 5.25 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 2.6985 | 2.6985 | 0 | 12 | 1 | 1 | 2.6985 | 10 | 0 | 0
1566.3 | 49.99 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1566.35 | 49.99 | 49.91 | 0.044118 | 0.425 | 4.25 | 49.99 | 0 | 0 | 0 | 2.125 | 2.125 | 0 | 12 | 1 | 1 | 2.125 | 10 | 0 | 0
1566.4 | 49.99 | 49.91 | 0.044118 | 0.325 | 3.25 | 49.99 | 0 | 0 | 0 | 1.625 | 1.625 | 0 | 12 | 1 | 1 | 1.625 | 10 | 0 | 0
1566.45 | 49.99 | 49.93 | 0.032353 | 0.225 | 2.25 | 49.99 | 0 | 0 | 0 | 1.125 | 1.125 | 0 | 12 | 1 | 1 | 1.125 | 10 | 0 | 0
1566.5 | 49.96 | 49.93 | 0.032353 | 0.125 | 1.25 | 49.99 | 0 | 0 | 0 | 0.625 | 0.625 | 0 | 12 | 1 | 1 | 0.625 | 10 | 0 | 0
1566.55 | 49.96 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 49.99 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1566.6 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1566.65 | 50.01 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.01 | 0 | 0 | 0 | 0.16176 | 0.16176 | 0 | 12 | 1 | 1 | 0.16176 | 10 | 0 | 0
1566.7 | 50.05 | 49.93 | 0.032353 | 0.032353 | 0.32353 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.058824 | 0.058824 | 0 | 12 | 1 | 1 | 0.058824 | 10 | 0 | 0
1566.75 | 50.05 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
1566.8 | 49.97 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
1566.85 | 49.97 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 50.05 | -0.020588 | -0.020588 | -0.20588 | -0.029412 | -0.029412 | 0 | 12 | 1 | 1 | -0.029412 | 10 | 0 | 0
1566.9 | 49.92 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1566.95 | 49.92 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1567 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1567.05 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1567.1 | 49.94 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1567.15 | 49.94 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1567.2 | 50.01 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1567.25 | 50.01 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1567.3 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.05 | -0.020588 | -0.020588 | -0.20588 | 0.088235 | 0.088235 | 0 | 12 | 1 | 1 | 0.088235 | 10 | 0 | 0
1567.35 | 49.99 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
1567.4 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
1567.45 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
1567.5 | 49.95 | 49.92 | 0.038235 | 0.038235 | 0.38235 | 50.01 | 0 | 0 | 0 | 0.19118 | 0.19118 | 0 | 12 | 1 | 1 | 0.19118 | 10 | 0 | 0
1567.55 | 49.95 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
1567.6 | 49.97 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
1567.65 | 49.97 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
1567.7 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
1567.75 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.01 | 0 | 0 | 0 | 0.13235 | 0.13235 | 0 | 12 | 1 | 1 | 0.13235 | 10 | 0 | 0
1567.8 | 49.87 | 49.87 | 0.335 | 0.335 | 3.35 | 50.01 | 0 | 0 | 0 | 1.675 | 1.675 | 0 | 12 | 1 | 1 | 1.675 | 10 | 0 | 0
1567.85 | 49.87 | 49.87 | 0.335 | 0.335 | 3.35 | 49.99 | 0 | 0 | 0 | 1.675 | 1.675 | 0 | 12 | 1 | 1 | 1.675 | 10 | 0 | 0
1567.9 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.99 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1567.95 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 2.6691 | 2.6691 | 0 | 12 | 1 | 1 | 2.6691 | 10 | 0 | 0
1568 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1568.05 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1568.1 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1568.15 | 49.79 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1568.2 | 49.84 | 49.79 | 1 | 1 | 10 | 49.97 | 0.0088235 | 0.0088235 | 0.088235 | 5.0441 | 5.0441 | 0 | 12 | 1 | 1 | 5.0441 | 10 | 0 | 0
1568.25 | 49.84 | 49.79 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
1568.3 | 49.89 | 49.79 | 1 | 1 | 10 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 5.1324 | 5.1324 | 0 | 12 | 1 | 1 | 5.1324 | 10 | 0 | 0
1568.35 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.12647 | 1.2647 | 5.6324 | 5.6324 | 0 | 12 | 1 | 1 | 5.6324 | 10 | 0 | 0
1568.4 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.145 | 1.45 | 5.725 | 5.725 | 0 | 12 | 1 | 1 | 5.725 | 10 | 0 | 0
1568.45 | 49.89 | 49.79 | 1 | 1 | 10 | 49.89 | 0.145 | 0.145 | 1.45 | 5.725 | 5.725 | 0 | 12 | 1 | 1 | 5.725 | 10 | 0 | 0
1568.5 | 49.96 | 49.79 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
1568.55 | 49.96 | 49.79 | 1 | 1 | 10 | 49.96 | 0.014706 | 0.014706 | 0.14706 | 5.0735 | 5.0735 | 0 | 12 | 1 | 1 | 5.0735 | 10 | 0 | 0
1568.6 | 50.02 | 49.79 | 1 | 1 | 10 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 4.9853 | 4.9853 | 0 | 12 | 1 | 1 | 4.9853 | 10 | 0 | 0
1568.65 | 50.02 | 49.79 | 1 | 1 | 10 | 50.02 | -0.0029412 | -0.0029412 | -0.029412 | 4.9853 | 4.9853 | 0 | 12 | 1 | 1 | 4.9853 | 10 | 0 | 0
1568.7 | 50.03 | 49.79 | 1 | 1 | 10 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.9559 | 4.9559 | 0 | 12 | 1 | 1 | 4.9559 | 10 | 0 | 0
1568.75 | 50.03 | 49.84 | 0.62 | 0.9 | 9 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 4.4559 | 4.4559 | 0 | 12 | 1 | 1 | 4.4559 | 10 | 0 | 0
1568.8 | 50.02 | 49.84 | 0.62 | 0.8 | 8 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 3.9559 | 3.9559 | 0 | 12 | 1 | 1 | 3.9559 | 10 | 0 | 0
1568.85 | 50.02 | 49.89 | 0.145 | 0.7 | 7 | 50.03 | -0.0088235 | -0.0088235 | -0.088235 | 3.4559 | 3.4559 | 0 | 12 | 1 | 1 | 3.4559 | 10 | 0 | 0
1568.9 | 50.08 | 49.89 | 0.145 | 0.6 | 6 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 2.8088 | 2.8088 | 0 | 12 | 1 | 1 | 2.8088 | 10 | 0 | 0
1568.95 | 50.08 | 49.89 | 0.145 | 0.5 | 5 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 2.3088 | 2.3088 | 0 | 12 | 1 | 1 | 2.3088 | 10 | 0 | 0
1569 | 50.01 | 49.89 | 0.145 | 0.4 | 4 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 1.8088 | 1.8088 | 0 | 12 | 1 | 1 | 1.8088 | 10 | 0 | 0
1569.05 | 50.01 | 49.96 | 0.014706 | 0.3 | 3 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 1.3088 | 1.3088 | 0 | 12 | 1 | 1 | 1.3088 | 10 | 0 | 0
1569.1 | 49.94 | 49.94 | 0.026471 | 0.2 | 2 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.80882 | 0.80882 | 0 | 12 | 1 | 1 | 0.80882 | 10 | 0 | 0
1569.15 | 49.94 | 49.94 | 0.026471 | 0.1 | 1 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.30882 | 0.30882 | 0 | 12 | 1 | 1 | 0.30882 | 10 | 0 | 0
1569.2 | 50 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
1569.25 | 50 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
1569.3 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
1569.35 | 49.94 | 49.94 | 0.026471 | 0.026471 | 0.26471 | 50.08 | -0.038235 | -0.038235 | -0.38235 | -0.058824 | -0.058824 | 0 | 12 | 1 | 1 | -0.058824 | 10 | 0 | 0
1569.4 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1569.45 | 49.91 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1569.5 | 49.92 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.08 | -0.038235 | -0.038235 | -0.38235 | 0.029412 | 0.029412 | 0 | 12 | 1 | 1 | 0.029412 | 10 | 0 | 0
1569.55 | 49.92 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 50.01 | 0 | 0 | 0 | 0.22059 | 0.22059 | 0 | 12 | 1 | 1 | 0.22059 | 10 | 0 | 0
1569.6 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50.01 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1569.65 | 49.85 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1569.7 | 49.92 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1569.75 | 49.92 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1569.8 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 50 | 0 | 0 | 0 | 2.625 | 2.625 | 0 | 12 | 1 | 1 | 2.625 | 10 | 0 | 0
1569.85 | 49.95 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1569.9 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1569.95 | 49.91 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1570 | 49.87 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1570.05 | 49.87 | 49.85 | 0.525 | 0.525 | 5.25 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 2.7279 | 2.7279 | 0 | 12 | 1 | 1 | 2.7279 | 10 | 0 | 0
1570.1 | 49.8 | 49.8 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1570.15 | 49.8 | 49.8 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1570.2 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1570.25 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1570.3 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1570.35 | 49.74 | 49.74 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1570.4 | 49.72 | 49.72 | 1 | 1 | 10 | 49.95 | 0.020588 | 0.020588 | 0.20588 | 5.1029 | 5.1029 | 0 | 12 | 1 | 1 | 5.1029 | 10 | 0 | 0
1570.45 | 49.72 | 49.72 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1570.5 | 49.67 | 49.67 | 1 | 1 | 10 | 49.91 | 0.044118 | 0.044118 | 0.44118 | 5.2206 | 5.2206 | 0 | 12 | 1 | 1 | 5.2206 | 10 | 0 | 0
1570.55 | 49.67 | 49.67 | 1 | 1 | 10 | 49.87 | 0.335 | 0.14412 | 1.4412 | 5.7206 | 5.7206 | 0 | 12 | 1 | 1 | 5.7206 | 10 | 0 | 0
1570.6 | 49.65 | 49.65 | 1 | 1 | 10 | 49.87 | 0.335 | 0.24412 | 2.4412 | 6.2206 | 6.2206 | 0 | 12 | 1 | 1 | 6.2206 | 10 | 0 | 0
1570.65 | 49.65 | 49.65 | 1 | 1 | 10 | 49.8 | 1 | 0.34412 | 3.4412 | 6.7206 | 6.7206 | 0 | 12 | 1 | 1 | 6.7206 | 10 | 0 | 0
1570.7 | 49.59 | 49.59 | 1 | 1 | 10 | 49.8 | 1 | 0.44412 | 4.4412 | 7.2206 | 7.2206 | 0 | 12 | 1 | 1 | 7.2206 | 10 | 0 | 0
1570.75 | 49.59 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.54412 | 5.4412 | 7.7206 | 7.7206 | 0 | 12 | 1 | 1 | 7.7206 | 10 | 0 | 0
1570.8 | 49.66 | 49.59 | 1 | 1 | 10 | 49.74 | 1 | 0.64412 | 6.4412 | 8.2206 | 8.2206 | 0 | 12 | 1 | 1 | 8.2206 | 10 | 0 | 0