## Version
Date | Version | Details
2022-06-18 | 1 | This file only contains the indicative reporting associated with draft data for GC151 for June 2022. This file will be updated in June to reflect the full data set.
2022-07-19 | 2 | This file only contains the indicative reporting associated with data for GC151 for June 2022.
2022-09-07 | 3 | This file only contains the reporting associated with data for GC0105 & GC151 foor June 2022.

## Notes
Subject | Notes
RoCoF | RoCoF=(frequency_500ms - frequency_0ms)/500ms RoCoF is calculated using 500ms sliding window. Note that smaller losses will have less accurate ROCOF calculations The RoCoF figure in this report is from external service
System Inertia | Monitoring which transmission-connected generators are running and adding an estimate of inertia from embedded generation and demand
Data 'N/A' | N/A: data not applicable or potentially unreliable. For example, there maybe events when the loss of infeed or exfeed is not instantaneous (over long time period), the calculated RoCoF may not be indicative. For some events, during a disturbance the data may potentially be unreliable. NGESO will apply engineering judgement to determine whether the derived/calculated data is suitable for sharing.
MW trip/loss of all generation/ interconnection related to the incident | Positive sign: indicates a loss of infeed (e.g. generator or importing interconnector). Negative sign: indicates a loss of outfeed (e.g. exporting interconnector or loss of demand).

## Transmission Faults (GC0151)
Location | Network Operator | Date Time | Voltage Trace (Refer to sheet) | Notes
NANT | SHETL | 2022-06-01 18:40 |  | 132/11kV GT1
Kemsley | NGET | 2022-06-06 12:13 |  | X305 CB
Glenagnes | SHETL | 2022-06-09 23:06 |  | GT2
Ninfield | NGET | 2022-06-29 10:28 |  | DRC5 flash over

## System Incidents (GC0105)
|  |  | Date and time of the incident | System frequency trace (1-second interval) for the incident | System frequency immediately before the incident | System frequency immediately after the incident | Maximum/Minimum rate of change of frequency (RoCoF) of the incident | System inertia at the time of the incident | Where known, MW trip/loss of all generation/ interconnection related to the incident |  | Where known, MW trip/loss of all Embedded Generation(EG) related to the incident | Where known, MW trip/loss of all DNO demand related to the incident; | Transmission fault associated with the incident; | Any transient voltage dip (loss % and duration) at the local substation associated with the incident | Any other data to gain a clearer understanding of the incident and its potential implications
Reference | Name | Notes | Date Time | System Frequency (Refer to sheet) | Pre-Event Frequency (Hz) | Post-Event Frequency (Hz) | RoCoF (Hz/s) | System Inertia (GVAs) | Generation/Interconnection (MW) |  | EG (MW) | Demand (MW) | Transmission fault | Voltage Dip | Additional data
20220610-1 | NSL |  | 2022-06-10 02:07 | 20220610-1 | 50.092 | 50.315 | 0.12316 | 179 | NSL | -700
20220613-1 | HUMR.1 |  | 2022-06-13 08:41 | 20220613-1 | 49.986 | 49.774 | -0.042098 | 220 | HUMR.1 | 294.375
20220617-1 | KEAD-2 |  | 2022-06-17 13:57 | 20220617-1 | 50.034 | 49.748 | -0.071064 | 193 | KEAD-2 | 754
20220621-1 | MOYLE |  | 2022-06-21 10:55 | 20220621-1 | 49.9 | 50.033 | 0.030102 | 255 | MOYLE | -254.25
20220622-1 | CNQPS.4 |  | 2022-06-22 09:49 | 20220622-1 | 50.061 | 49.791 | -0.037311 | 262 | CNQPS.4 | 316.5
20220623-1 | MRWD.1 |  | 2022-06-23 11:11 | 20220623-1 | 50.071 | 49.829 | -0.028788 | 268 | MRWD.1 | 278.1
20220625-1 | CDCL-1 |  | 2022-06-25 04:54 | 20220625-1 | 49.981 | 49.848 | -0.034976 | 140 | CDCL-1 | 368
20220626-1 | HEYM27 |  | 2022-06-26 00:02 | 20220626-1 | 50.042 | 49.841 | -0.072101 | 174 | HEYM27 | 480.48
20220630-1 | EECL.1 |  | 2022-06-30 23:48 | 20220630-1 | 50.12 | 49.746 | -0.071051 | 255 | EECL.1 | 396.5625

## 20220610-1
In GMT |  |  | High resolution Incident data
Date | Time | Freq | time | freq
2022-06-10 | 1:07 | 50.097 | 2022-06-10 02:07 | 50.0968
2022-06-10 | 1:07 | 50.095 | 44722.0882 | 50.0968
2022-06-10 | 1:07 | 50.092 | 44722.0882 | 50.0967
2022-06-10 | 1:07 | 50.092 | 44722.0882 | 50.0967
2022-06-10 | 1:07 | 50.092 | 44722.0882 | 50.0968
2022-06-10 | 1:07 | 50.094 | 44722.0882 | 50.0968
2022-06-10 | 1:07 | 50.097 | 44722.0882 | 50.0968
2022-06-10 | 1:07 | 50.097 | 44722.0882 | 50.0968
2022-06-10 | 1:07 | 50.1 | 44722.0882 | 50.0968
2022-06-10 | 1:07 | 50.1 | 44722.0882 | 50.0967
2022-06-10 | 1:07 | 50.1 | 44722.0882 | 50.0967
2022-06-10 | 1:07 | 50.102 | 44722.0882 | 50.0966
2022-06-10 | 1:07 | 50.1 | 44722.0882 | 50.0966
2022-06-10 | 1:07 | 50.103 | 44722.0882 | 50.0965
2022-06-10 | 1:07 | 50.103 | 44722.0882 | 50.0965
2022-06-10 | 1:07 | 50.107 | 44722.0882 | 50.0964
2022-06-10 | 1:07 | 50.111 | 44722.0882 | 50.0964
2022-06-10 | 1:07 | 50.113 | 44722.0882 | 50.0964
2022-06-10 | 1:07 | 50.116 | 44722.0882 | 50.0964
2022-06-10 | 1:07 | 50.115 | 44722.0882 | 50.0964
2022-06-10 | 1:07 | 50.111 | 44722.0882 | 50.0963
2022-06-10 | 1:07 | 50.11 | 44722.0882 | 50.0962
2022-06-10 | 1:07 | 50.107 | 44722.0882 | 50.0961
2022-06-10 | 1:07 | 50.107 | 44722.0882 | 50.096
2022-06-10 | 1:07 | 50.101 | 44722.0882 | 50.0958
2022-06-10 | 1:07 | 50.099 | 44722.0882 | 50.0957
2022-06-10 | 1:07 | 50.095 | 44722.0882 | 50.0955
2022-06-10 | 1:07 | 50.094 | 44722.0882 | 50.0954
2022-06-10 | 1:07 | 50.092 | 44722.0882 | 50.0954
2022-06-10 | 1:07 | 50.095 | 44722.0882 | 50.0954
2022-06-10 | 1:08 | 50.169 | 44722.0882 | 50.0953
2022-06-10 | 1:08 | 50.245 | 44722.0882 | 50.0954
2022-06-10 | 1:08 | 50.297 | 44722.0882 | 50.0954
2022-06-10 | 1:08 | 50.315 | 44722.0882 | 50.0955
2022-06-10 | 1:08 | 50.315 | 44722.0882 | 50.0954
2022-06-10 | 1:08 | 50.31 | 44722.0882 | 50.0954
2022-06-10 | 1:08 | 50.305 | 44722.0882 | 50.0954
2022-06-10 | 1:08 | 50.298 | 44722.0882 | 50.0953
2022-06-10 | 1:08 | 50.296 | 44722.0882 | 50.0953
2022-06-10 | 1:08 | 50.296 | 44722.0882 | 50.0952
2022-06-10 | 1:08 | 50.295 | 44722.0882 | 50.0951
2022-06-10 | 1:08 | 50.296 | 44722.0882 | 50.095
2022-06-10 | 1:08 | 50.299 | 44722.0882 | 50.0949
2022-06-10 | 1:08 | 50.302 | 44722.0882 | 50.0948
2022-06-10 | 1:08 | 50.302 | 44722.0882 | 50.0947
2022-06-10 | 1:08 | 50.302 | 44722.0882 | 50.0947
2022-06-10 | 1:08 | 50.3 | 44722.0882 | 50.0947
2022-06-10 | 1:08 | 50.298 | 44722.0882 | 50.0946
2022-06-10 | 1:08 | 50.296 | 44722.0882 | 50.0946
2022-06-10 | 1:08 | 50.291 | 44722.0882 | 50.0946
2022-06-10 | 1:08 | 50.281 | 2022-06-10 02:07 | 50.0945
2022-06-10 | 1:08 | 50.271 | 44722.0882 | 50.0945
2022-06-10 | 1:08 | 50.263 | 44722.0882 | 50.0945
2022-06-10 | 1:08 | 50.257 | 44722.0882 | 50.0945
2022-06-10 | 1:08 | 50.255 | 44722.0882 | 50.0944
2022-06-10 | 1:08 | 50.251 | 44722.0882 | 50.0943
2022-06-10 | 1:08 | 50.25 | 44722.0882 | 50.0942
2022-06-10 | 1:08 | 50.25 | 44722.0882 | 50.0941
2022-06-10 | 1:08 | 50.25 | 44722.0882 | 50.0941
2022-06-10 | 1:08 | 50.25 | 44722.0882 | 50.0941
2022-06-10 | 1:08 | 50.251 | 44722.0882 | 50.0941
2022-06-10 | 1:08 | 50.251 | 44722.0882 | 50.0941
2022-06-10 | 1:08 | 50.251 | 44722.0882 | 50.0942
2022-06-10 | 1:08 | 50.25 | 44722.0882 | 50.0942
2022-06-10 | 1:08 | 50.25 | 44722.0882 | 50.0943
2022-06-10 | 1:08 | 50.251 | 44722.0882 | 50.0943
2022-06-10 | 1:08 | 50.251 | 44722.0882 | 50.0943
2022-06-10 | 1:08 | 50.251 | 44722.0882 | 50.0943
2022-06-10 | 1:08 | 50.249 | 44722.0882 | 50.0943
2022-06-10 | 1:08 | 50.248 | 44722.0882 | 50.0941
2022-06-10 | 1:08 | 50.249 | 44722.0882 | 50.094
2022-06-10 | 1:08 | 50.25 | 44722.0882 | 50.0938
2022-06-10 | 1:08 | 50.253 | 44722.0882 | 50.0936
2022-06-10 | 1:08 | 50.253 | 44722.0882 | 50.0935
2022-06-10 | 1:08 | 50.255 | 44722.0882 | 50.0934
2022-06-10 | 1:08 | 50.255 | 44722.0882 | 50.0934
2022-06-10 | 1:08 | 50.255 | 44722.0882 | 50.0934
2022-06-10 | 1:08 | 50.255 | 44722.0882 | 50.0935
2022-06-10 | 1:08 | 50.256 | 44722.0882 | 50.0936
2022-06-10 | 1:08 | 50.256 | 44722.0882 | 50.0937
2022-06-10 | 1:08 | 50.257 | 44722.0882 | 50.0938
2022-06-10 | 1:08 | 50.26 | 44722.0882 | 50.0939
2022-06-10 | 1:08 | 50.26 | 44722.0882 | 50.0939
2022-06-10 | 1:08 | 50.26 | 44722.0882 | 50.0939
2022-06-10 | 1:08 | 50.261 | 44722.0882 | 50.0939
2022-06-10 | 1:08 | 50.26 | 44722.0882 | 50.0939
2022-06-10 | 1:08 | 50.261 | 44722.0882 | 50.0938
2022-06-10 | 1:08 | 50.262 | 44722.0882 | 50.0937
2022-06-10 | 1:08 | 50.262 | 44722.0882 | 50.0936
2022-06-10 | 1:08 | 50.263 | 44722.0882 | 50.0935
2022-06-10 | 1:08 | 50.267 | 44722.0882 | 50.0933
2022-06-10 | 1:09 | 50.27 | 44722.0882 | 50.0932
2022-06-10 | 1:09 | 50.272 | 44722.0882 | 50.0931
2022-06-10 | 1:09 | 50.276 | 44722.0882 | 50.0931
2022-06-10 | 1:09 | 50.277 | 44722.0882 | 50.0931
2022-06-10 | 1:09 | 50.278 | 44722.0882 | 50.0932
2022-06-10 | 1:09 | 50.278 | 44722.0882 | 50.0932
2022-06-10 | 1:09 | 50.28 | 44722.0882 | 50.0932
2022-06-10 | 1:09 | 50.279 | 44722.0882 | 50.0933
2022-06-10 | 1:09 | 50.279 | 44722.0882 | 50.0934
2022-06-10 | 1:09 | 50.279 | 2022-06-10 02:07 | 50.0935
2022-06-10 | 1:09 | 50.279 | 44722.0882 | 50.0935
2022-06-10 | 1:09 | 50.281 | 44722.0882 | 50.0935
2022-06-10 | 1:09 | 50.283 | 44722.0882 | 50.0935
2022-06-10 | 1:09 | 50.284 | 44722.0882 | 50.0935
2022-06-10 | 1:09 | 50.284 | 44722.0882 | 50.0934
2022-06-10 | 1:09 | 50.282 | 44722.0882 | 50.0934
2022-06-10 | 1:09 | 50.281 | 44722.0882 | 50.0934
2022-06-10 | 1:09 | 50.279 | 44722.0882 | 50.0933
2022-06-10 | 1:09 | 50.279 | 44722.0882 | 50.0933
2022-06-10 | 1:09 | 50.281 | 44722.0882 | 50.0932
2022-06-10 | 1:09 | 50.283 | 44722.0882 | 50.0932
2022-06-10 | 1:09 | 50.284 | 44722.0882 | 50.0931
2022-06-10 | 1:09 | 50.285 | 44722.0882 | 50.0931
2022-06-10 | 1:09 | 50.284 | 44722.0882 | 50.0931
2022-06-10 | 1:09 | 50.284 | 44722.0882 | 50.093
2022-06-10 | 1:09 | 50.283 | 44722.0882 | 50.093
2022-06-10 | 1:09 | 50.283 | 44722.0882 | 50.093
2022-06-10 | 1:09 | 50.282 | 44722.0882 | 50.093
2022-06-10 | 1:09 | 50.284 | 44722.0882 | 50.0931
2022-06-10 | 1:09 | 50.284 | 44722.0882 | 50.0931
2022-06-10 | 1:09 | 50.284 | 44722.0882 | 50.0931
2022-06-10 | 1:09 | 50.285 | 44722.0882 | 50.093
2022-06-10 | 1:09 | 50.286 | 44722.0882 | 50.093
2022-06-10 | 1:09 | 50.285 | 44722.0882 | 50.093
2022-06-10 | 1:09 | 50.283 | 44722.0882 | 50.093
2022-06-10 | 1:09 | 50.275 | 44722.0882 | 50.093
2022-06-10 | 1:09 | 50.268 | 44722.0882 | 50.093
2022-06-10 | 1:09 | 50.264 | 44722.0882 | 50.093
2022-06-10 | 1:09 | 50.26 | 44722.0882 | 50.0929
2022-06-10 | 1:09 | 50.258 | 44722.0882 | 50.0929
2022-06-10 | 1:09 | 50.256 | 44722.0882 | 50.0929
2022-06-10 | 1:09 | 50.258 | 44722.0882 | 50.0929
2022-06-10 | 1:09 | 50.256 | 44722.0882 | 50.0929
2022-06-10 | 1:09 | 50.26 | 44722.0882 | 50.0929
2022-06-10 | 1:09 | 50.263 | 44722.0882 | 50.0929
2022-06-10 | 1:09 | 50.266 | 44722.0882 | 50.0929
2022-06-10 | 1:09 | 50.265 | 44722.0882 | 50.0929
2022-06-10 | 1:09 | 50.261 | 44722.0882 | 50.0929
2022-06-10 | 1:09 | 50.258 | 44722.0882 | 50.0929
2022-06-10 | 1:09 | 50.258 | 44722.0882 | 50.0929
2022-06-10 | 1:09 | 50.259 | 44722.0882 | 50.0929
2022-06-10 | 1:09 | 50.257 | 44722.0882 | 50.0929
2022-06-10 | 1:09 | 50.255 | 44722.0882 | 50.0929
2022-06-10 | 1:09 | 50.254 | 44722.0882 | 50.093
2022-06-10 | 1:09 | 50.252 | 44722.0882 | 50.0929
2022-06-10 | 1:09 | 50.252 | 44722.0882 | 50.0929
2022-06-10 | 1:09 | 50.249 | 44722.0882 | 50.0928
2022-06-10 | 1:09 | 50.248 | 44722.0882 | 50.0928
2022-06-10 | 1:09 | 50.25 | 44722.0882 | 50.0928
2022-06-10 | 1:10 | 50.253 | 2022-06-10 02:07 | 50.0928
2022-06-10 | 1:10 | 50.256 | 44722.0882 | 50.0928
2022-06-10 | 1:10 | 50.256 | 44722.0882 | 50.0928
2022-06-10 | 1:10 | 50.254 | 44722.0882 | 50.0928
2022-06-10 | 1:10 | 50.255 | 44722.0882 | 50.0928
2022-06-10 | 1:10 | 50.253 | 44722.0882 | 50.0927
2022-06-10 | 1:10 | 50.251 | 44722.0882 | 50.0927
2022-06-10 | 1:10 | 50.248 | 44722.0882 | 50.0927
2022-06-10 | 1:10 | 50.246 | 44722.0882 | 50.0926
2022-06-10 | 1:10 | 50.245 | 44722.0882 | 50.0926
2022-06-10 | 1:10 | 50.244 | 44722.0882 | 50.0925
2022-06-10 | 1:10 | 50.244 | 44722.0882 | 50.0925
2022-06-10 | 1:10 | 50.241 | 44722.0882 | 50.0925
2022-06-10 | 1:10 | 50.242 | 44722.0882 | 50.0925
2022-06-10 | 1:10 | 50.239 | 44722.0882 | 50.0925
2022-06-10 | 1:10 | 50.24 | 44722.0882 | 50.0925
2022-06-10 | 1:10 | 50.244 | 44722.0882 | 50.0926
2022-06-10 | 1:10 | 50.244 | 44722.0882 | 50.0927
2022-06-10 | 1:10 | 50.242 | 44722.0882 | 50.0927
2022-06-10 | 1:10 | 50.241 | 44722.0882 | 50.0928
2022-06-10 | 1:10 | 50.241 | 44722.0882 | 50.0928
2022-06-10 | 1:10 | 50.241 | 44722.0882 | 50.0929
2022-06-10 | 1:10 | 50.24 | 44722.0882 | 50.0929
2022-06-10 | 1:10 | 50.238 | 44722.0882 | 50.0929
2022-06-10 | 1:10 | 50.235 | 44722.0882 | 50.0929
2022-06-10 | 1:10 | 50.233 | 44722.0882 | 50.0929
2022-06-10 | 1:10 | 50.232 | 44722.0882 | 50.0929
2022-06-10 | 1:10 | 50.227 | 44722.0882 | 50.0929
2022-06-10 | 1:10 | 50.225 | 44722.0882 | 50.093
2022-06-10 | 1:10 | 50.226 | 44722.0882 | 50.093
2022-06-10 | 1:10 | 50.228 | 44722.0882 | 50.093
2022-06-10 | 1:10 | 50.227 | 44722.0882 | 50.0932
2022-06-10 | 1:10 | 50.224 | 44722.0882 | 50.0932
2022-06-10 | 1:10 | 50.223 | 44722.0882 | 50.0933
2022-06-10 | 1:10 | 50.221 | 44722.0882 | 50.0932
2022-06-10 | 1:10 | 50.22 | 44722.0882 | 50.0932
2022-06-10 | 1:10 | 50.219 | 44722.0882 | 50.0931
2022-06-10 | 1:10 | 50.22 | 44722.0882 | 50.0931
2022-06-10 | 1:10 | 50.22 | 44722.0882 | 50.093
2022-06-10 | 1:10 | 50.223 | 44722.0882 | 50.093
2022-06-10 | 1:10 | 50.223 | 44722.0882 | 50.093
2022-06-10 | 1:10 | 50.224 | 44722.0882 | 50.093
2022-06-10 | 1:10 | 50.221 | 44722.0882 | 50.0931
2022-06-10 | 1:10 | 50.219 | 44722.0882 | 50.0931
2022-06-10 | 1:10 | 50.217 | 44722.0882 | 50.0931
2022-06-10 | 1:10 | 50.215 | 44722.0882 | 50.0932
2022-06-10 | 1:10 | 50.213 | 44722.0882 | 50.0933
2022-06-10 | 1:10 | 50.212 | 44722.0882 | 50.0934
2022-06-10 | 1:10 | 50.211 | 44722.0882 | 50.0934
2022-06-10 | 1:10 | 50.211 | 44722.0882 | 50.0934
2022-06-10 | 1:10 | 50.207 | 2022-06-10 02:07 | 50.0934
2022-06-10 | 1:10 | 50.206 | 44722.0882 | 50.0934
2022-06-10 | 1:10 | 50.205 | 44722.0882 | 50.0933
2022-06-10 | 1:10 | 50.203 | 44722.0882 | 50.0932
2022-06-10 | 1:10 | 50.203 | 44722.0882 | 50.0932
2022-06-10 | 1:10 | 50.2 | 44722.0882 | 50.0932
2022-06-10 | 1:10 | 50.199 | 44722.0882 | 50.0931
2022-06-10 | 1:10 | 50.198 | 44722.0882 | 50.0931
2022-06-10 | 1:10 | 50.199 | 44722.0882 | 50.0931
2022-06-10 | 1:10 | 50.198 | 44722.0882 | 50.093
2022-06-10 | 1:10 | 50.197 | 44722.0882 | 50.093
2022-06-10 | 1:11 | 50.198 | 44722.0882 | 50.0931
2022-06-10 | 1:11 | 50.199 | 44722.0882 | 50.0931
2022-06-10 | 1:11 | 50.201 | 44722.0882 | 50.0932
2022-06-10 | 1:11 | 50.203 | 44722.0882 | 50.0933
2022-06-10 | 1:11 | 50.205 | 44722.0882 | 50.0933
2022-06-10 | 1:11 | 50.206 | 44722.0882 | 50.0933
2022-06-10 | 1:11 | 50.206 | 44722.0882 | 50.0933
2022-06-10 | 1:11 | 50.206 | 44722.0882 | 50.0933
2022-06-10 | 1:11 | 50.205 | 44722.0882 | 50.0932
2022-06-10 | 1:11 | 50.203 | 44722.0882 | 50.0932
2022-06-10 | 1:11 | 50.2 | 44722.0882 | 50.0931
2022-06-10 | 1:11 | 50.2 | 44722.0882 | 50.0931
2022-06-10 | 1:11 | 50.199 | 44722.0882 | 50.0931
2022-06-10 | 1:11 | 50.196 | 44722.0882 | 50.0931
2022-06-10 | 1:11 | 50.195 | 44722.0882 | 50.0931
2022-06-10 | 1:11 | 50.192 | 44722.0882 | 50.0932
2022-06-10 | 1:11 | 50.188 | 44722.0882 | 50.0933
2022-06-10 | 1:11 | 50.185 | 44722.0882 | 50.0934
2022-06-10 | 1:11 | 50.183 | 44722.0882 | 50.0935
2022-06-10 | 1:11 | 50.181 | 44722.0882 | 50.0936
2022-06-10 | 1:11 | 50.182 | 44722.0882 | 50.0937
2022-06-10 | 1:11 | 50.182 | 44722.0882 | 50.0937
2022-06-10 | 1:11 | 50.181 | 44722.0882 | 50.0938
2022-06-10 | 1:11 | 50.18 | 44722.0882 | 50.0939
2022-06-10 | 1:11 | 50.177 | 44722.0882 | 50.094
2022-06-10 | 1:11 | 50.176 | 44722.0882 | 50.0941
2022-06-10 | 1:11 | 50.173 | 44722.0882 | 50.0942
2022-06-10 | 1:11 | 50.156 | 44722.0882 | 50.0944
2022-06-10 | 1:11 | 50.164 | 44722.0882 | 50.0945
2022-06-10 | 1:11 | 50.159 | 44722.0883 | 50.0946
2022-06-10 | 1:11 | 50.151 | 44722.0883 | 50.0948
2022-06-10 | 1:11 | 50.147 | 44722.0883 | 50.0948
2022-06-10 | 1:11 | 50.143 | 44722.0883 | 50.0949
2022-06-10 | 1:11 | 50.143 | 44722.0883 | 50.095
2022-06-10 | 1:11 | 50.14 | 44722.0883 | 50.0951
2022-06-10 | 1:11 | 50.14 | 44722.0883 | 50.0951
2022-06-10 | 1:11 | 50.137 | 44722.0883 | 50.0952
2022-06-10 | 1:11 | 50.137 | 44722.0883 | 50.0953
2022-06-10 | 1:11 | 50.135 | 44722.0883 | 50.0953
2022-06-10 | 1:11 | 50.134 | 2022-06-10 02:07 | 50.0954
2022-06-10 | 1:11 | 50.129 | 44722.0883 | 50.0955
2022-06-10 | 1:11 | 50.124 | 44722.0883 | 50.0955
2022-06-10 | 1:11 | 50.118 | 44722.0883 | 50.0955
2022-06-10 | 1:11 | 50.113 | 44722.0883 | 50.0956
2022-06-10 | 1:11 | 50.108 | 44722.0883 | 50.0956
2022-06-10 | 1:11 | 50.104 | 44722.0883 | 50.0957
2022-06-10 | 1:11 | 50.101 | 44722.0883 | 50.0957
2022-06-10 | 1:11 | 50.101 | 44722.0883 | 50.0956
2022-06-10 | 1:11 | 50.103 | 44722.0883 | 50.0956
2022-06-10 | 1:11 | 50.101 | 44722.0883 | 50.0956
2022-06-10 | 1:11 | 50.1 | 44722.0883 | 50.0956
2022-06-10 | 1:11 | 50.101 | 44722.0883 | 50.0957
2022-06-10 | 1:11 | 50.101 | 44722.0883 | 50.0957
2022-06-10 | 1:11 | 50.098 | 44722.0883 | 50.0957
2022-06-10 | 1:11 | 50.093 | 44722.0883 | 50.0957
2022-06-10 | 1:11 | 50.088 | 44722.0883 | 50.0958
2022-06-10 | 1:11 | 50.084 | 44722.0883 | 50.0958
2022-06-10 | 1:11 | 50.083 | 44722.0883 | 50.0958
2022-06-10 | 1:11 | 50.082 | 44722.0883 | 50.0959
2022-06-10 | 1:12 | 50.081 | 44722.0883 | 50.0959
2022-06-10 | 1:12 | 50.078 | 44722.0883 | 50.096
2022-06-10 | 1:12 | 50.078 | 44722.0883 | 50.0961
2022-06-10 | 1:12 | 50.078 | 44722.0883 | 50.0962
2022-06-10 | 1:12 | 50.079 | 44722.0883 | 50.0963
2022-06-10 | 1:12 | 50.081 | 44722.0883 | 50.0964
2022-06-10 | 1:12 | 50.082 | 44722.0883 | 50.0964
2022-06-10 | 1:12 | 50.081 | 44722.0883 | 50.0965
2022-06-10 | 1:12 | 50.077 | 44722.0883 | 50.0965
2022-06-10 | 1:12 | 50.075 | 44722.0883 | 50.0964
2022-06-10 | 1:12 | 50.072 | 44722.0883 | 50.0964
2022-06-10 | 1:12 | 50.069 | 44722.0883 | 50.0963
2022-06-10 | 1:12 | 50.064 | 44722.0883 | 50.0963
2022-06-10 | 1:12 | 50.06 | 44722.0883 | 50.0963
2022-06-10 | 1:12 | 50.055 | 44722.0883 | 50.0963
2022-06-10 | 1:12 | 50.052 | 44722.0883 | 50.0964
2022-06-10 | 1:12 | 50.051 | 44722.0883 | 50.0965
2022-06-10 | 1:12 | 50.054 | 44722.0883 | 50.0966
2022-06-10 | 1:12 | 50.063 | 44722.0883 | 50.0967
2022-06-10 | 1:12 | 50.07 | 44722.0883 | 50.0968
2022-06-10 | 1:12 | 50.075 | 44722.0883 | 50.097
2022-06-10 | 1:12 | 50.078 | 44722.0883 | 50.0971
2022-06-10 | 1:12 | 50.078 | 44722.0883 | 50.0973
2022-06-10 | 1:12 | 50.08 | 44722.0883 | 50.0974
2022-06-10 | 1:12 | 50.08 | 44722.0883 | 50.0974
2022-06-10 | 1:12 | 50.078 | 44722.0883 | 50.0974
2022-06-10 | 1:12 | 50.077 | 44722.0883 | 50.0974
2022-06-10 | 1:12 | 50.074 | 44722.0883 | 50.0974
2022-06-10 | 1:12 | 50.074 | 44722.0883 | 50.0975
2022-06-10 | 1:12 | 50.074 | 44722.0883 | 50.0975
2022-06-10 | 1:12 | 50.075 | 2022-06-10 02:07 | 50.0976
2022-06-10 | 1:12 | 50.077 | 44722.0883 | 50.0975
2022-06-10 | 1:12 | 50.078 | 44722.0883 | 50.0976
2022-06-10 | 1:12 | 50.078 | 44722.0883 | 50.0976
2022-06-10 | 1:12 | 50.076 | 44722.0883 | 50.0976
2022-06-10 | 1:12 | 50.074 | 44722.0883 | 50.0976
2022-06-10 | 1:12 | 50.073 | 44722.0883 | 50.0977
2022-06-10 | 1:12 | 50.073 | 44722.0883 | 50.0977
2022-06-10 | 1:12 | 50.076 | 44722.0883 | 50.0978
2022-06-10 | 1:12 | 50.077 | 44722.0883 | 50.0978
2022-06-10 | 1:12 | 50.078 | 44722.0883 | 50.0979
2022-06-10 | 1:12 | 50.078 | 44722.0883 | 50.0979
2022-06-10 | 1:12 | 50.08 | 44722.0883 | 50.098
2022-06-10 | 1:12 | 50.081 | 44722.0883 | 50.098
2022-06-10 | 1:12 | 50.083 | 44722.0883 | 50.0981
2022-06-10 | 1:12 | 50.083 | 44722.0883 | 50.0982
2022-06-10 | 1:12 | 50.084 | 44722.0883 | 50.0982
2022-06-10 | 1:12 | 50.083 | 44722.0883 | 50.0982
2022-06-10 | 1:12 | 50.083 | 44722.0883 | 50.0982
2022-06-10 | 1:12 | 50.082 | 44722.0883 | 50.0982
2022-06-10 | 1:12 | 50.081 | 44722.0883 | 50.0982
2022-06-10 | 1:12 | 50.079 | 44722.0883 | 50.0982
2022-06-10 | 1:12 | 50.082 | 44722.0883 | 50.0981
2022-06-10 | 1:12 | 50.081 | 44722.0883 | 50.098
2022-06-10 | 1:12 | 50.079 | 44722.0883 | 50.098
2022-06-10 | 1:12 | 50.078 | 44722.0883 | 50.0979
2022-06-10 | 1:12 | 50.079 | 44722.0883 | 50.0978
2022-06-10 | 1:12 | 50.076 | 44722.0883 | 50.0977
2022-06-10 | 1:12 | 50.074 | 44722.0883 | 50.0977
2022-06-10 | 1:12 | 50.072 | 44722.0883 | 50.0977
2022-06-10 | 1:12 | 50.07 | 44722.0883 | 50.0977
2022-06-10 | 1:13 | 50.067 | 44722.0883 | 50.0978
2022-06-10 | 1:13 | 50.065 | 44722.0883 | 50.0979
2022-06-10 | 1:13 | 50.064 | 44722.0883 | 50.098
2022-06-10 | 1:13 | 50.063 | 44722.0883 | 50.0981
2022-06-10 | 1:13 | 50.064 | 44722.0883 | 50.0982
2022-06-10 | 1:13 | 50.065 | 44722.0883 | 50.0983
2022-06-10 | 1:13 | 50.067 | 44722.0883 | 50.0983
2022-06-10 | 1:13 | 50.068 | 44722.0883 | 50.0984
2022-06-10 | 1:13 | 50.068 | 44722.0883 | 50.0984
2022-06-10 | 1:13 | 50.068 | 44722.0883 | 50.0983
2022-06-10 | 1:13 | 50.067 | 44722.0883 | 50.0982
2022-06-10 | 1:13 | 50.063 | 44722.0883 | 50.0981
2022-06-10 | 1:13 | 50.058 | 44722.0883 | 50.098
2022-06-10 | 1:13 | 50.056 | 44722.0883 | 50.098
2022-06-10 | 1:13 | 50.053 | 44722.0883 | 50.0979
2022-06-10 | 1:13 | 50.048 | 44722.0883 | 50.0979
2022-06-10 | 1:13 | 50.046 | 44722.0883 | 50.0979
2022-06-10 | 1:13 | 50.043 | 44722.0883 | 50.098
2022-06-10 | 1:13 | 50.043 | 44722.0883 | 50.0981
2022-06-10 | 1:13 | 50.045 | 2022-06-10 02:07 | 50.0982
2022-06-10 | 1:13 | 50.046 | 44722.0883 | 50.0982
2022-06-10 | 1:13 | 50.044 | 44722.0883 | 50.0983
2022-06-10 | 1:13 | 50.044 | 44722.0883 | 50.0984
2022-06-10 | 1:13 | 50.044 | 44722.0883 | 50.0984
2022-06-10 | 1:13 | 50.044 | 44722.0883 | 50.0985
2022-06-10 | 1:13 | 50.044 | 44722.0883 | 50.0985
2022-06-10 | 1:13 | 50.04 | 44722.0883 | 50.0985
2022-06-10 | 1:13 | 50.037 | 44722.0883 | 50.0986
2022-06-10 | 1:13 | 50.034 | 44722.0883 | 50.0986
2022-06-10 | 1:13 | 50.034 | 44722.0883 | 50.0986
2022-06-10 | 1:13 | 50.032 | 44722.0883 | 50.0986
2022-06-10 | 1:13 | 50.032 | 44722.0883 | 50.0987
2022-06-10 | 1:13 | 50.032 | 44722.0883 | 50.0988
2022-06-10 | 1:13 | 50.034 | 44722.0883 | 50.0988
2022-06-10 | 1:13 | 50.037 | 44722.0883 | 50.0989
2022-06-10 | 1:13 | 50.039 | 44722.0883 | 50.0991
2022-06-10 | 1:13 | 50.038 | 44722.0883 | 50.0992
2022-06-10 | 1:13 | 50.038 | 44722.0883 | 50.0993
2022-06-10 | 1:13 | 50.038 | 44722.0883 | 50.0994
2022-06-10 | 1:13 | 50.036 | 44722.0883 | 50.0996
2022-06-10 | 1:13 | 50.034 | 44722.0883 | 50.0997
2022-06-10 | 1:13 | 50.031 | 44722.0883 | 50.0999
2022-06-10 | 1:13 | 50.027 | 44722.0883 | 50.0999
2022-06-10 | 1:13 | 50.023 | 44722.0883 | 50.1001
2022-06-10 | 1:13 | 50.02 | 44722.0883 | 50.1002
2022-06-10 | 1:13 | 50.019 | 44722.0883 | 50.1002
2022-06-10 | 1:13 | 50.02 | 44722.0883 | 50.1003
2022-06-10 | 1:13 | 50.019 | 44722.0883 | 50.1002
2022-06-10 | 1:13 | 50.02 | 44722.0883 | 50.1002
2022-06-10 | 1:13 | 50.02 | 44722.0883 | 50.1001
2022-06-10 | 1:13 | 50.024 | 44722.0883 | 50.1001
2022-06-10 | 1:13 | 50.027 | 44722.0883 | 50.1001
2022-06-10 | 1:13 | 50.028 | 44722.0883 | 50.1
2022-06-10 | 1:13 | 50.028 | 44722.0883 | 50.1001
2022-06-10 | 1:13 | 50.027 | 44722.0883 | 50.1001
2022-06-10 | 1:13 | 50.026 | 44722.0883 | 50.1002
2022-06-10 | 1:13 | 50.027 | 44722.0883 | 50.1002
2022-06-10 | 1:13 | 50.025 | 44722.0883 | 50.1002
2022-06-10 | 1:13 | 50.023 | 44722.0883 | 50.1003
2022-06-10 | 1:14 | 50.02 | 44722.0883 | 50.1003
2022-06-10 | 1:14 | 50.018 | 44722.0883 | 50.1003
2022-06-10 | 1:14 | 50.016 | 44722.0883 | 50.1003
2022-06-10 | 1:14 | 50.017 | 44722.0883 | 50.1004
2022-06-10 | 1:14 | 50.016 | 44722.0883 | 50.1005
2022-06-10 | 1:14 | 50.019 | 44722.0883 | 50.1005
2022-06-10 | 1:14 | 50.018 | 44722.0883 | 50.1005
2022-06-10 | 1:14 | 50.019 | 44722.0883 | 50.1005
2022-06-10 | 1:14 | 50.019 | 44722.0883 | 50.1005
2022-06-10 | 1:14 | 50.02 | 44722.0883 | 50.1006
2022-06-10 | 1:14 | 50.017 | 2022-06-10 02:07 | 50.1006
2022-06-10 | 1:14 | 50.016 | 44722.0883 | 50.1006
2022-06-10 | 1:14 | 50.012 | 44722.0883 | 50.1006
2022-06-10 | 1:14 | 50.014 | 44722.0883 | 50.1006
2022-06-10 | 1:14 | 50.013 | 44722.0883 | 50.1006
2022-06-10 | 1:14 | 50.013 | 44722.0883 | 50.1007
2022-06-10 | 1:14 | 50.015 | 44722.0883 | 50.1007
2022-06-10 | 1:14 | 50.016 | 44722.0883 | 50.1008
2022-06-10 | 1:14 | 50.015 | 44722.0883 | 50.1008
2022-06-10 | 1:14 | 50.013 | 44722.0883 | 50.1009
2022-06-10 | 1:14 | 50.014 | 44722.0883 | 50.101
2022-06-10 | 1:14 | 50.013 | 44722.0883 | 50.1011
2022-06-10 | 1:14 | 50.014 | 44722.0883 | 50.1011
2022-06-10 | 1:14 | 50.013 | 44722.0883 | 50.1011
2022-06-10 | 1:14 | 50.015 | 44722.0883 | 50.1011
2022-06-10 | 1:14 | 50.017 | 44722.0883 | 50.1011
2022-06-10 | 1:14 | 50.017 | 44722.0883 | 50.101
2022-06-10 | 1:14 | 50.02 | 44722.0883 | 50.1009
2022-06-10 | 1:14 | 50.022 | 44722.0883 | 50.1008
2022-06-10 | 1:14 | 50.023 | 44722.0883 | 50.1007
2022-06-10 | 1:14 | 50.025 | 44722.0883 | 50.1006
2022-06-10 | 1:14 | 50.023 | 44722.0883 | 50.1006
2022-06-10 | 1:14 | 50.024 | 44722.0883 | 50.1007
2022-06-10 | 1:14 | 50.023 | 44722.0883 | 50.1007
2022-06-10 | 1:14 | 50.024 | 44722.0883 | 50.1007
2022-06-10 | 1:14 | 50.024 | 44722.0883 | 50.1008
2022-06-10 | 1:14 | 50.023 | 44722.0883 | 50.1008
2022-06-10 | 1:14 | 50.022 | 44722.0883 | 50.1008
2022-06-10 | 1:14 | 50.019 | 44722.0883 | 50.1008
2022-06-10 | 1:14 | 50.017 | 44722.0883 | 50.1007
2022-06-10 | 1:14 | 50.017 | 44722.0883 | 50.1006
2022-06-10 | 1:14 | 50.018 | 44722.0883 | 50.1005
2022-06-10 | 1:14 | 50.019 | 44722.0883 | 50.1005
2022-06-10 | 1:14 | 50.02 | 44722.0883 | 50.1004
2022-06-10 | 1:14 | 50.02 | 44722.0883 | 50.1004
2022-06-10 | 1:14 | 50.02 | 44722.0883 | 50.1004
2022-06-10 | 1:14 | 50.019 | 44722.0883 | 50.1004
2022-06-10 | 1:14 | 50.019 | 44722.0883 | 50.1004
2022-06-10 | 1:14 | 50.018 | 44722.0883 | 50.1004
2022-06-10 | 1:14 | 50.018 | 44722.0883 | 50.1005
2022-06-10 | 1:14 | 50.019 | 44722.0883 | 50.1005
2022-06-10 | 1:14 | 50.02 | 44722.0883 | 50.1006
2022-06-10 | 1:14 | 50.021 | 44722.0883 | 50.1006
2022-06-10 | 1:14 | 50.023 | 44722.0883 | 50.1006
2022-06-10 | 1:14 | 50.024 | 44722.0883 | 50.1006
2022-06-10 | 1:14 | 50.024 | 44722.0883 | 50.1006
2022-06-10 | 1:14 | 50.024 | 44722.0883 | 50.1006
2022-06-10 | 1:14 | 50.022 | 44722.0883 | 50.1005
2022-06-10 | 1:14 | 50.02 | 44722.0883 | 50.1005
2022-06-10 | 1:14 | 50.015 | 44722.0883 | 50.1005
2022-06-10 | 1:14 | 50.011 | 2022-06-10 02:07 | 50.1004
2022-06-10 | 1:15 | 50.007 | 44722.0883 | 50.1003
2022-06-10 | 1:15 | 50.002 | 44722.0883 | 50.1003
2022-06-10 | 1:15 | 50.002 | 44722.0883 | 50.1003
2022-06-10 | 1:15 | 49.999 | 44722.0883 | 50.1004
2022-06-10 | 1:15 | 50.001 | 44722.0883 | 50.1005
2022-06-10 | 1:15 | 50.004 | 44722.0883 | 50.1005
2022-06-10 | 1:15 | 50.007 | 44722.0883 | 50.1005
2022-06-10 | 1:15 | 50.008 | 44722.0883 | 50.1005
2022-06-10 | 1:15 | 50.006 | 44722.0883 | 50.1005
2022-06-10 | 1:15 | 50.006 | 44722.0883 | 50.1004
2022-06-10 | 1:15 | 50.006 | 44722.0883 | 50.1004
2022-06-10 | 1:15 | 50.003 | 44722.0883 | 50.1004
2022-06-10 | 1:15 | 50 | 44722.0883 | 50.1004
2022-06-10 | 1:15 | 49.997 | 44722.0883 | 50.1004
2022-06-10 | 1:15 | 49.993 | 44722.0883 | 50.1004
2022-06-10 | 1:15 | 49.989 | 44722.0883 | 50.1004
2022-06-10 | 1:15 | 49.984 | 44722.0883 | 50.1005
2022-06-10 | 1:15 | 49.983 | 44722.0883 | 50.1006
2022-06-10 | 1:15 | 49.985 | 44722.0883 | 50.1006
2022-06-10 | 1:15 | 49.986 | 44722.0883 | 50.1006
2022-06-10 | 1:15 | 49.989 | 44722.0883 | 50.1006
2022-06-10 | 1:15 | 49.99 | 44722.0883 | 50.1006
2022-06-10 | 1:15 | 49.991 | 44722.0883 | 50.1006
2022-06-10 | 1:15 | 49.991 | 44722.0883 | 50.1005
2022-06-10 | 1:15 | 49.993 | 44722.0883 | 50.1005
2022-06-10 | 1:15 | 49.995 | 44722.0883 | 50.1005
2022-06-10 | 1:15 | 49.994 | 44722.0883 | 50.1005
2022-06-10 | 1:15 | 49.992 | 44722.0883 | 50.1004
2022-06-10 | 1:15 | 49.989 | 44722.0883 | 50.1004
2022-06-10 | 1:15 | 49.986 | 44722.0883 | 50.1004
2022-06-10 | 1:15 | 49.98 | 44722.0883 | 50.1004
2022-06-10 | 1:15 | 49.977 | 44722.0883 | 50.1004
2022-06-10 | 1:15 | 49.974 | 44722.0883 | 50.1004
2022-06-10 | 1:15 | 49.972 | 44722.0883 | 50.1005
2022-06-10 | 1:15 | 49.971 | 44722.0883 | 50.1005
2022-06-10 | 1:15 | 49.973 | 44722.0883 | 50.1006
2022-06-10 | 1:15 | 49.976 | 44722.0883 | 50.1006
2022-06-10 | 1:15 | 49.979 | 44722.0883 | 50.1006
2022-06-10 | 1:15 | 49.982 | 44722.0883 | 50.1007
2022-06-10 | 1:15 | 49.983 | 44722.0883 | 50.1007
2022-06-10 | 1:15 | 49.983 | 44722.0883 | 50.1007
2022-06-10 | 1:15 | 49.984 | 44722.0883 | 50.1007
2022-06-10 | 1:15 | 49.984 | 44722.0883 | 50.1006
2022-06-10 | 1:15 | 49.983 | 44722.0883 | 50.1006
2022-06-10 | 1:15 | 49.979 | 44722.0883 | 50.1007
2022-06-10 | 1:15 | 49.976 | 44722.0883 | 50.1007
2022-06-10 | 1:15 | 49.975 | 44722.0883 | 50.1007
2022-06-10 | 1:15 | 49.975 | 44722.0883 | 50.1008
2022-06-10 | 1:15 | 49.976 | 44722.0883 | 50.1008
2022-06-10 | 1:15 | 49.979 | 2022-06-10 02:07 | 50.1008
2022-06-10 | 1:15 | 49.981 | 44722.0883 | 50.1008
2022-06-10 | 1:15 | 49.983 | 44722.0883 | 50.1008
2022-06-10 | 1:15 | 49.984 | 44722.0883 | 50.1008
2022-06-10 | 1:15 | 49.986 | 44722.0883 | 50.1008
2022-06-10 | 1:15 | 49.985 | 44722.0883 | 50.1008
2022-06-10 | 1:15 | 49.984 | 44722.0883 | 50.1008
2022-06-10 | 1:15 | 49.985 | 44722.0883 | 50.1009
2022-06-10 | 1:15 | 49.988 | 44722.0883 | 50.1009
2022-06-10 | 1:15 | 49.988 | 44722.0883 | 50.1009
2022-06-10 | 1:16 | 49.993 | 44722.0883 | 50.1009
2022-06-10 | 1:16 | 49.995 | 44722.0883 | 50.101
2022-06-10 | 1:16 | 49.996 | 44722.0883 | 50.101
2022-06-10 | 1:16 | 49.995 | 44722.0883 | 50.1011
2022-06-10 | 1:16 | 49.995 | 44722.0883 | 50.1012
2022-06-10 | 1:16 | 49.994 | 44722.0883 | 50.1013
2022-06-10 | 1:16 | 49.997 | 44722.0883 | 50.1014
2022-06-10 | 1:16 | 49.998 | 44722.0883 | 50.1014
2022-06-10 | 1:16 | 50 | 44722.0883 | 50.1014
2022-06-10 | 1:16 | 50.002 | 44722.0883 | 50.1014
2022-06-10 | 1:16 | 50.002 | 44722.0883 | 50.1014
2022-06-10 | 1:16 | 50.003 | 44722.0883 | 50.1013
2022-06-10 | 1:16 | 50.001 | 44722.0883 | 50.1012
2022-06-10 | 1:16 | 49.998 | 44722.0883 | 50.1011
2022-06-10 | 1:16 | 49.997 | 44722.0883 | 50.101
2022-06-10 | 1:16 | 49.996 | 44722.0883 | 50.101
2022-06-10 | 1:16 | 49.995 | 44722.0883 | 50.101
2022-06-10 | 1:16 | 49.994 | 44722.0883 | 50.101
2022-06-10 | 1:16 | 49.993 | 44722.0883 | 50.1011
2022-06-10 | 1:16 | 49.994 | 44722.0883 | 50.1012
2022-06-10 | 1:16 | 49.994 | 44722.0883 | 50.1014
2022-06-10 | 1:16 | 49.994 | 44722.0883 | 50.1015
2022-06-10 | 1:16 | 49.997 | 44722.0883 | 50.1016
2022-06-10 | 1:16 | 50 | 44722.0883 | 50.1016
2022-06-10 | 1:16 | 50.005 | 44722.0883 | 50.1016
2022-06-10 | 1:16 | 50.007 | 44722.0883 | 50.1016
2022-06-10 | 1:16 | 50.011 | 44722.0883 | 50.1016
2022-06-10 | 1:16 | 50.013 | 44722.0883 | 50.1016
2022-06-10 | 1:16 | 50.014 | 44722.0883 | 50.1016
2022-06-10 | 1:16 | 50.014 | 44722.0883 | 50.1016
2022-06-10 | 1:16 | 50.012 | 44722.0883 | 50.1016
2022-06-10 | 1:16 | 50.011 | 44722.0883 | 50.1016
2022-06-10 | 1:16 | 50.01 | 44722.0883 | 50.1016
2022-06-10 | 1:16 | 50.01 | 44722.0883 | 50.1017
2022-06-10 | 1:16 | 50.011 | 44722.0883 | 50.1017
2022-06-10 | 1:16 | 50.011 | 44722.0883 | 50.1018
2022-06-10 | 1:16 | 50.007 | 44722.0883 | 50.1019
2022-06-10 | 1:16 | 50.002 | 44722.0883 | 50.1019
2022-06-10 | 1:16 | 49.996 | 44722.0883 | 50.102
2022-06-10 | 1:16 | 49.993 | 44722.0883 | 50.102
2022-06-10 | 1:16 | 49.986 | 2022-06-10 02:07 | 50.102
2022-06-10 | 1:16 | 49.979 | 44722.0883 | 50.102
2022-06-10 | 1:16 | 49.977 | 44722.0883 | 50.102
2022-06-10 | 1:16 | 49.977 | 44722.0883 | 50.1019
2022-06-10 | 1:16 | 49.978 | 44722.0883 | 50.1019
2022-06-10 | 1:16 | 49.983 | 44722.0883 | 50.1018
2022-06-10 | 1:16 | 49.985 | 44722.0883 | 50.1018
2022-06-10 | 1:16 | 49.987 | 44722.0883 | 50.1018
2022-06-10 | 1:16 | 49.991 | 44722.0883 | 50.1017
2022-06-10 | 1:16 | 49.994 | 44722.0883 | 50.1017
2022-06-10 | 1:16 | 49.997 | 44722.0883 | 50.1017
2022-06-10 | 1:16 | 49.997 | 44722.0883 | 50.1017
2022-06-10 | 1:16 | 49.996 | 44722.0883 | 50.1018
2022-06-10 | 1:16 | 49.993 | 44722.0883 | 50.1018
2022-06-10 | 1:16 | 49.988 | 44722.0883 | 50.1018
2022-06-10 | 1:16 | 49.985 | 44722.0883 | 50.1018
2022-06-10 | 1:16 | 49.981 | 44722.0883 | 50.1018
2022-06-10 | 1:16 | 49.982 | 44722.0883 | 50.1019
2022-06-10 | 1:16 | 49.982 | 44722.0883 | 50.1019
2022-06-10 | 1:16 | 49.983 | 44722.0883 | 50.1018
2022-06-10 | 1:16 | 49.984 | 44722.0883 | 50.1018
2022-06-10 | 1:17 | 49.984 | 44722.0883 | 50.1017
2022-06-10 | 1:17 | 49.983 | 44722.0883 | 50.1016
2022-06-10 | 1:17 | 49.981 | 44722.0883 | 50.1016
2022-06-10 | 1:17 | 49.981 | 44722.0883 | 50.1015
2022-06-10 | 1:17 | 49.981 | 44722.0883 | 50.1014
2022-06-10 | 1:17 | 49.979 | 44722.0883 | 50.1013
2022-06-10 | 1:17 | 49.978 | 44722.0883 | 50.1013
2022-06-10 | 1:17 | 49.977 | 44722.0883 | 50.1013
2022-06-10 | 1:17 | 49.976 | 44722.0883 | 50.1013
2022-06-10 | 1:17 | 49.977 | 44722.0883 | 50.1014
2022-06-10 | 1:17 | 49.976 | 44722.0883 | 50.1015
2022-06-10 | 1:17 | 49.978 | 44722.0883 | 50.1017
2022-06-10 | 1:17 | 49.982 | 44722.0883 | 50.1019
2022-06-10 | 1:17 | 49.983 | 44722.0883 | 50.102
2022-06-10 | 1:17 | 49.986 | 44722.0883 | 50.1021
2022-06-10 | 1:17 | 49.987 | 44722.0883 | 50.1021
2022-06-10 | 1:17 | 49.988 | 44722.0883 | 50.1021
2022-06-10 | 1:17 | 49.986 | 44722.0883 | 50.1021
2022-06-10 | 1:17 | 49.985 | 44722.0883 | 50.1021
2022-06-10 | 1:17 | 49.985 | 44722.0883 | 50.1021
2022-06-10 | 1:17 | 49.984 | 44722.0883 | 50.1022
2022-06-10 | 1:17 | 49.984 | 44722.0883 | 50.1022
2022-06-10 | 1:17 | 49.981 | 44722.0883 | 50.1022
2022-06-10 | 1:17 | 49.98 | 44722.0883 | 50.1022
2022-06-10 | 1:17 | 49.981 | 44722.0883 | 50.1021
2022-06-10 | 1:17 | 49.983 | 44722.0883 | 50.1021
2022-06-10 | 1:17 | 49.987 | 44722.0883 | 50.1021
2022-06-10 | 1:17 | 49.99 | 44722.0883 | 50.1021
2022-06-10 | 1:17 | 49.993 | 44722.0883 | 50.1021
2022-06-10 | 1:17 | 49.995 | 2022-06-10 02:07 | 50.1021
|  |  | 44722.0883 | 50.1021
|  |  | 44722.0883 | 50.1022
|  |  | 44722.0883 | 50.1023
|  |  | 44722.0883 | 50.1023
|  |  | 44722.0883 | 50.1024
|  |  | 44722.0883 | 50.1024
|  |  | 44722.0883 | 50.1024
|  |  | 44722.0883 | 50.1025
|  |  | 44722.0883 | 50.1025
|  |  | 44722.0883 | 50.1024
|  |  | 44722.0883 | 50.1024
|  |  | 44722.0883 | 50.1025
|  |  | 44722.0883 | 50.1024
|  |  | 44722.0883 | 50.1024
|  |  | 44722.0883 | 50.1024
|  |  | 44722.0883 | 50.1024
|  |  | 44722.0883 | 50.1024
|  |  | 44722.0883 | 50.1024
|  |  | 44722.0883 | 50.1024
|  |  | 44722.0883 | 50.1024
|  |  | 44722.0883 | 50.1023
|  |  | 44722.0883 | 50.1023
|  |  | 44722.0883 | 50.1022
|  |  | 44722.0883 | 50.1021
|  |  | 44722.0883 | 50.1021
|  |  | 44722.0883 | 50.1021
|  |  | 44722.0883 | 50.1021
|  |  | 44722.0883 | 50.1022
|  |  | 44722.0883 | 50.1023
|  |  | 44722.0883 | 50.1024
|  |  | 44722.0883 | 50.1024
|  |  | 44722.0883 | 50.1025
|  |  | 44722.0883 | 50.1025
|  |  | 44722.0883 | 50.1026
|  |  | 44722.0883 | 50.1026
|  |  | 44722.0883 | 50.1026
|  |  | 44722.0883 | 50.1026
|  |  | 44722.0883 | 50.1026
|  |  | 44722.0883 | 50.1026
|  |  | 44722.0883 | 50.1026
|  |  | 44722.0883 | 50.1025
|  |  | 44722.0883 | 50.1025
|  |  | 44722.0883 | 50.1025
|  |  | 44722.0883 | 50.1025
|  |  | 44722.0883 | 50.1025
|  |  | 44722.0883 | 50.1025
|  |  | 44722.0883 | 50.1026
|  |  | 44722.0883 | 50.1027
|  |  | 44722.0883 | 50.1028
|  |  | 2022-06-10 02:07 | 50.1029
|  |  | 44722.0883 | 50.103
|  |  | 44722.0883 | 50.1031
|  |  | 44722.0883 | 50.1032
|  |  | 44722.0883 | 50.1033
|  |  | 44722.0883 | 50.1033
|  |  | 44722.0883 | 50.1033
|  |  | 44722.0883 | 50.1033
|  |  | 44722.0883 | 50.1033
|  |  | 44722.0883 | 50.1033
|  |  | 44722.0883 | 50.1032
|  |  | 44722.0883 | 50.1032
|  |  | 44722.0883 | 50.1032
|  |  | 44722.0883 | 50.1032
|  |  | 44722.0883 | 50.1031
|  |  | 44722.0883 | 50.1032
|  |  | 44722.0883 | 50.1032
|  |  | 44722.0883 | 50.1032
|  |  | 44722.0883 | 50.1033
|  |  | 44722.0883 | 50.1033
|  |  | 44722.0883 | 50.1034
|  |  | 44722.0883 | 50.1034
|  |  | 44722.0883 | 50.1034
|  |  | 44722.0884 | 50.1035
|  |  | 44722.0884 | 50.1036
|  |  | 44722.0884 | 50.1036
|  |  | 44722.0884 | 50.1036
|  |  | 44722.0884 | 50.1036
|  |  | 44722.0884 | 50.1036
|  |  | 44722.0884 | 50.1036
|  |  | 44722.0884 | 50.1036
|  |  | 44722.0884 | 50.1037
|  |  | 44722.0884 | 50.1038
|  |  | 44722.0884 | 50.1039
|  |  | 44722.0884 | 50.104
|  |  | 44722.0884 | 50.1041
|  |  | 44722.0884 | 50.1042
|  |  | 44722.0884 | 50.1043
|  |  | 44722.0884 | 50.1044
|  |  | 44722.0884 | 50.1044
|  |  | 44722.0884 | 50.1043
|  |  | 44722.0884 | 50.1043
|  |  | 44722.0884 | 50.1044
|  |  | 44722.0884 | 50.1044
|  |  | 44722.0884 | 50.1045
|  |  | 44722.0884 | 50.1046
|  |  | 44722.0884 | 50.1047
|  |  | 44722.0884 | 50.1048
|  |  | 44722.0884 | 50.1049
|  |  | 44722.0884 | 50.1051
|  |  | 2022-06-10 02:07 | 50.1051
|  |  | 44722.0884 | 50.1052
|  |  | 44722.0884 | 50.1052
|  |  | 44722.0884 | 50.1051
|  |  | 44722.0884 | 50.1051
|  |  | 44722.0884 | 50.1051
|  |  | 44722.0884 | 50.105
|  |  | 44722.0884 | 50.105
|  |  | 44722.0884 | 50.105
|  |  | 44722.0884 | 50.1051
|  |  | 44722.0884 | 50.1052
|  |  | 44722.0884 | 50.1053
|  |  | 44722.0884 | 50.1054
|  |  | 44722.0884 | 50.1056
|  |  | 44722.0884 | 50.1057
|  |  | 44722.0884 | 50.1058
|  |  | 44722.0884 | 50.1058
|  |  | 44722.0884 | 50.1059
|  |  | 44722.0884 | 50.1059
|  |  | 44722.0884 | 50.1059
|  |  | 44722.0884 | 50.1059
|  |  | 44722.0884 | 50.106
|  |  | 44722.0884 | 50.1061
|  |  | 44722.0884 | 50.1061
|  |  | 44722.0884 | 50.1062
|  |  | 44722.0884 | 50.1063
|  |  | 44722.0884 | 50.1064
|  |  | 44722.0884 | 50.1066
|  |  | 44722.0884 | 50.1066
|  |  | 44722.0884 | 50.1067
|  |  | 44722.0884 | 50.1067
|  |  | 44722.0884 | 50.1068
|  |  | 44722.0884 | 50.1068
|  |  | 44722.0884 | 50.1068
|  |  | 44722.0884 | 50.1069
|  |  | 44722.0884 | 50.1069
|  |  | 44722.0884 | 50.1069
|  |  | 44722.0884 | 50.107
|  |  | 44722.0884 | 50.1071
|  |  | 44722.0884 | 50.1072
|  |  | 44722.0884 | 50.1073
|  |  | 44722.0884 | 50.1073
|  |  | 44722.0884 | 50.1073
|  |  | 44722.0884 | 50.1073
|  |  | 44722.0884 | 50.1074
|  |  | 44722.0884 | 50.1074
|  |  | 44722.0884 | 50.1075
|  |  | 44722.0884 | 50.1075
|  |  | 44722.0884 | 50.1075
|  |  | 44722.0884 | 50.1076
|  |  | 2022-06-10 02:07 | 50.1076
|  |  | 44722.0884 | 50.1077
|  |  | 44722.0884 | 50.1077
|  |  | 44722.0884 | 50.1077
|  |  | 44722.0884 | 50.1077
|  |  | 44722.0884 | 50.1077
|  |  | 44722.0884 | 50.1077
|  |  | 44722.0884 | 50.1078
|  |  | 44722.0884 | 50.1078
|  |  | 44722.0884 | 50.1079
|  |  | 44722.0884 | 50.1081
|  |  | 44722.0884 | 50.1082
|  |  | 44722.0884 | 50.1083
|  |  | 44722.0884 | 50.1084
|  |  | 44722.0884 | 50.1084
|  |  | 44722.0884 | 50.1085
|  |  | 44722.0884 | 50.1085
|  |  | 44722.0884 | 50.1086
|  |  | 44722.0884 | 50.1086
|  |  | 44722.0884 | 50.1087
|  |  | 44722.0884 | 50.1088
|  |  | 44722.0884 | 50.109
|  |  | 44722.0884 | 50.1091
|  |  | 44722.0884 | 50.1092
|  |  | 44722.0884 | 50.1094
|  |  | 44722.0884 | 50.1095
|  |  | 44722.0884 | 50.1097
|  |  | 44722.0884 | 50.1098
|  |  | 44722.0884 | 50.1099
|  |  | 44722.0884 | 50.1101
|  |  | 44722.0884 | 50.1101
|  |  | 44722.0884 | 50.1102
|  |  | 44722.0884 | 50.1103
|  |  | 44722.0884 | 50.1104
|  |  | 44722.0884 | 50.1104
|  |  | 44722.0884 | 50.1106
|  |  | 44722.0884 | 50.1106
|  |  | 44722.0884 | 50.1106
|  |  | 44722.0884 | 50.1106
|  |  | 44722.0884 | 50.1107
|  |  | 44722.0884 | 50.1109
|  |  | 44722.0884 | 50.1109
|  |  | 44722.0884 | 50.111
|  |  | 44722.0884 | 50.1111
|  |  | 44722.0884 | 50.1111
|  |  | 44722.0884 | 50.1111
|  |  | 44722.0884 | 50.1112
|  |  | 44722.0884 | 50.1112
|  |  | 44722.0884 | 50.1113
|  |  | 44722.0884 | 50.1114
|  |  | 2022-06-10 02:07 | 50.1115
|  |  | 44722.0884 | 50.1116
|  |  | 44722.0884 | 50.1117
|  |  | 44722.0884 | 50.1118
|  |  | 44722.0884 | 50.1119
|  |  | 44722.0884 | 50.1121
|  |  | 44722.0884 | 50.1121
|  |  | 44722.0884 | 50.1122
|  |  | 44722.0884 | 50.1122
|  |  | 44722.0884 | 50.1122
|  |  | 44722.0884 | 50.1122
|  |  | 44722.0884 | 50.1121
|  |  | 44722.0884 | 50.1121
|  |  | 44722.0884 | 50.1122
|  |  | 44722.0884 | 50.1123
|  |  | 44722.0884 | 50.1124
|  |  | 44722.0884 | 50.1125
|  |  | 44722.0884 | 50.1126
|  |  | 44722.0884 | 50.1127
|  |  | 44722.0884 | 50.1128
|  |  | 44722.0884 | 50.1129
|  |  | 44722.0884 | 50.113
|  |  | 44722.0884 | 50.113
|  |  | 44722.0884 | 50.113
|  |  | 44722.0884 | 50.113
|  |  | 44722.0884 | 50.1131
|  |  | 44722.0884 | 50.1131
|  |  | 44722.0884 | 50.1131
|  |  | 44722.0884 | 50.1132
|  |  | 44722.0884 | 50.1132
|  |  | 44722.0884 | 50.1133
|  |  | 44722.0884 | 50.1134
|  |  | 44722.0884 | 50.1136
|  |  | 44722.0884 | 50.1137
|  |  | 44722.0884 | 50.1137
|  |  | 44722.0884 | 50.1139
|  |  | 44722.0884 | 50.114
|  |  | 44722.0884 | 50.114
|  |  | 44722.0884 | 50.1141
|  |  | 44722.0884 | 50.1142
|  |  | 44722.0884 | 50.1141
|  |  | 44722.0884 | 50.1142
|  |  | 44722.0884 | 50.1143
|  |  | 44722.0884 | 50.1144
|  |  | 44722.0884 | 50.1145
|  |  | 44722.0884 | 50.1146
|  |  | 44722.0884 | 50.1147
|  |  | 44722.0884 | 50.1148
|  |  | 44722.0884 | 50.1149
|  |  | 44722.0884 | 50.1149
|  |  | 2022-06-10 02:07 | 50.1149
|  |  | 44722.0884 | 50.1148
|  |  | 44722.0884 | 50.1147
|  |  | 44722.0884 | 50.1147
|  |  | 44722.0884 | 50.1147
|  |  | 44722.0884 | 50.1147
|  |  | 44722.0884 | 50.1148
|  |  | 44722.0884 | 50.1149
|  |  | 44722.0884 | 50.1149
|  |  | 44722.0884 | 50.115
|  |  | 44722.0884 | 50.1151
|  |  | 44722.0884 | 50.1153
|  |  | 44722.0884 | 50.1154
|  |  | 44722.0884 | 50.1156
|  |  | 44722.0884 | 50.1156
|  |  | 44722.0884 | 50.1157
|  |  | 44722.0884 | 50.1156
|  |  | 44722.0884 | 50.1156
|  |  | 44722.0884 | 50.1157
|  |  | 44722.0884 | 50.1157
|  |  | 44722.0884 | 50.1157
|  |  | 44722.0884 | 50.1156
|  |  | 44722.0884 | 50.1156
|  |  | 44722.0884 | 50.1156
|  |  | 44722.0884 | 50.1156
|  |  | 44722.0884 | 50.1157
|  |  | 44722.0884 | 50.1158
|  |  | 44722.0884 | 50.1159
|  |  | 44722.0884 | 50.1161
|  |  | 44722.0884 | 50.1162
|  |  | 44722.0884 | 50.1163
|  |  | 44722.0884 | 50.1164
|  |  | 44722.0884 | 50.1166
|  |  | 44722.0884 | 50.1166
|  |  | 44722.0884 | 50.1166
|  |  | 44722.0884 | 50.1166
|  |  | 44722.0884 | 50.1166
|  |  | 44722.0884 | 50.1165
|  |  | 44722.0884 | 50.1164
|  |  | 44722.0884 | 50.1164
|  |  | 44722.0884 | 50.1163
|  |  | 44722.0884 | 50.1163
|  |  | 44722.0884 | 50.1163
|  |  | 44722.0884 | 50.1163
|  |  | 44722.0884 | 50.1163
|  |  | 44722.0884 | 50.1163
|  |  | 44722.0884 | 50.1164
|  |  | 44722.0884 | 50.1165
|  |  | 44722.0884 | 50.1166
|  |  | 44722.0884 | 50.1167
|  |  | 2022-06-10 02:07 | 50.1167
|  |  | 44722.0884 | 50.1167
|  |  | 44722.0884 | 50.1166
|  |  | 44722.0884 | 50.1166
|  |  | 44722.0884 | 50.1166
|  |  | 44722.0884 | 50.1165
|  |  | 44722.0884 | 50.1165
|  |  | 44722.0884 | 50.1164
|  |  | 44722.0884 | 50.1164
|  |  | 44722.0884 | 50.1164
|  |  | 44722.0884 | 50.1165
|  |  | 44722.0884 | 50.1165
|  |  | 44722.0884 | 50.1166
|  |  | 44722.0884 | 50.1167
|  |  | 44722.0884 | 50.1169
|  |  | 44722.0884 | 50.117
|  |  | 44722.0884 | 50.117
|  |  | 44722.0884 | 50.117
|  |  | 44722.0884 | 50.117
|  |  | 44722.0884 | 50.1168
|  |  | 44722.0884 | 50.1167
|  |  | 44722.0884 | 50.1165
|  |  | 44722.0884 | 50.1164
|  |  | 44722.0884 | 50.1162
|  |  | 44722.0884 | 50.116
|  |  | 44722.0884 | 50.1159
|  |  | 44722.0884 | 50.1158
|  |  | 44722.0884 | 50.1158
|  |  | 44722.0884 | 50.116
|  |  | 44722.0884 | 50.116
|  |  | 44722.0884 | 50.1161
|  |  | 44722.0884 | 50.1162
|  |  | 44722.0884 | 50.1162
|  |  | 44722.0884 | 50.1162
|  |  | 44722.0884 | 50.1161
|  |  | 44722.0884 | 50.116
|  |  | 44722.0884 | 50.1159
|  |  | 44722.0884 | 50.1158
|  |  | 44722.0884 | 50.1157
|  |  | 44722.0884 | 50.1156
|  |  | 44722.0884 | 50.1154
|  |  | 44722.0884 | 50.1154
|  |  | 44722.0884 | 50.1153
|  |  | 44722.0884 | 50.1151
|  |  | 44722.0884 | 50.1151
|  |  | 44722.0884 | 50.1151
|  |  | 44722.0884 | 50.1152
|  |  | 44722.0884 | 50.1152
|  |  | 44722.0884 | 50.1153
|  |  | 44722.0884 | 50.1153
|  |  | 2022-06-10 02:07 | 50.1153
|  |  | 44722.0884 | 50.1153
|  |  | 44722.0884 | 50.1152
|  |  | 44722.0884 | 50.1151
|  |  | 44722.0884 | 50.1149
|  |  | 44722.0884 | 50.1147
|  |  | 44722.0884 | 50.1145
|  |  | 44722.0884 | 50.1143
|  |  | 44722.0884 | 50.1141
|  |  | 44722.0884 | 50.114
|  |  | 44722.0884 | 50.1139
|  |  | 44722.0884 | 50.1138
|  |  | 44722.0884 | 50.1137
|  |  | 44722.0884 | 50.1137
|  |  | 44722.0884 | 50.1136
|  |  | 44722.0884 | 50.1136
|  |  | 44722.0884 | 50.1135
|  |  | 44722.0884 | 50.1134
|  |  | 44722.0884 | 50.1133
|  |  | 44722.0884 | 50.1132
|  |  | 44722.0884 | 50.1131
|  |  | 44722.0884 | 50.113
|  |  | 44722.0884 | 50.1128
|  |  | 44722.0884 | 50.1127
|  |  | 44722.0884 | 50.1126
|  |  | 44722.0884 | 50.1125
|  |  | 44722.0884 | 50.1124
|  |  | 44722.0884 | 50.1125
|  |  | 44722.0884 | 50.1125
|  |  | 44722.0884 | 50.1125
|  |  | 44722.0884 | 50.1125
|  |  | 44722.0884 | 50.1124
|  |  | 44722.0884 | 50.1123
|  |  | 44722.0884 | 50.1121
|  |  | 44722.0884 | 50.1119
|  |  | 44722.0884 | 50.1117
|  |  | 44722.0884 | 50.1115
|  |  | 44722.0884 | 50.1114
|  |  | 44722.0884 | 50.1114
|  |  | 44722.0884 | 50.1113
|  |  | 44722.0884 | 50.1114
|  |  | 44722.0884 | 50.1114
|  |  | 44722.0884 | 50.1116
|  |  | 44722.0884 | 50.1117
|  |  | 44722.0884 | 50.1117
|  |  | 44722.0884 | 50.1118
|  |  | 44722.0884 | 50.1117
|  |  | 44722.0884 | 50.1116
|  |  | 44722.0884 | 50.1115
|  |  | 44722.0884 | 50.1113
|  |  | 2022-06-10 02:07 | 50.1111
|  |  | 44722.0884 | 50.1109
|  |  | 44722.0884 | 50.1109
|  |  | 44722.0884 | 50.1108
|  |  | 44722.0884 | 50.1108
|  |  | 44722.0884 | 50.1107
|  |  | 44722.0884 | 50.1108
|  |  | 44722.0884 | 50.1108
|  |  | 44722.0884 | 50.1108
|  |  | 44722.0884 | 50.111
|  |  | 44722.0884 | 50.111
|  |  | 44722.0884 | 50.111
|  |  | 44722.0884 | 50.1109
|  |  | 44722.0884 | 50.1108
|  |  | 44722.0884 | 50.1107
|  |  | 44722.0884 | 50.1106
|  |  | 44722.0884 | 50.1105
|  |  | 44722.0884 | 50.1104
|  |  | 44722.0884 | 50.1104
|  |  | 44722.0884 | 50.1104
|  |  | 44722.0884 | 50.1104
|  |  | 44722.0884 | 50.1105
|  |  | 44722.0884 | 50.1105
|  |  | 44722.0884 | 50.1105
|  |  | 44722.0884 | 50.1105
|  |  | 44722.0884 | 50.1104
|  |  | 44722.0884 | 50.1103
|  |  | 44722.0884 | 50.1102
|  |  | 44722.0884 | 50.1101
|  |  | 44722.0884 | 50.1099
|  |  | 44722.0884 | 50.1098
|  |  | 44722.0884 | 50.1098
|  |  | 44722.0884 | 50.1098
|  |  | 44722.0884 | 50.1098
|  |  | 44722.0884 | 50.1098
|  |  | 44722.0884 | 50.1098
|  |  | 44722.0884 | 50.1099
|  |  | 44722.0884 | 50.1098
|  |  | 44722.0884 | 50.1098
|  |  | 44722.0884 | 50.1098
|  |  | 44722.0884 | 50.1097
|  |  | 44722.0884 | 50.1096
|  |  | 44722.0884 | 50.1095
|  |  | 44722.0884 | 50.1094
|  |  | 44722.0884 | 50.1093
|  |  | 44722.0884 | 50.1092
|  |  | 44722.0884 | 50.1092
|  |  | 44722.0884 | 50.1091
|  |  | 44722.0884 | 50.1091
|  |  | 44722.0884 | 50.1091
|  |  | 2022-06-10 02:07 | 50.1092
|  |  | 44722.0884 | 50.1093
|  |  | 44722.0884 | 50.1093
|  |  | 44722.0884 | 50.1094
|  |  | 44722.0884 | 50.1094
|  |  | 44722.0884 | 50.1095
|  |  | 44722.0884 | 50.1094
|  |  | 44722.0884 | 50.1094
|  |  | 44722.0884 | 50.1093
|  |  | 44722.0884 | 50.1092
|  |  | 44722.0884 | 50.1092
|  |  | 44722.0884 | 50.1091
|  |  | 44722.0884 | 50.1091
|  |  | 44722.0884 | 50.109
|  |  | 44722.0884 | 50.109
|  |  | 44722.0884 | 50.109
|  |  | 44722.0884 | 50.1089
|  |  | 44722.0884 | 50.1089
|  |  | 44722.0884 | 50.1088
|  |  | 44722.0884 | 50.1087
|  |  | 44722.0884 | 50.1087
|  |  | 44722.0884 | 50.1087
|  |  | 44722.0884 | 50.1086
|  |  | 44722.0884 | 50.1085
|  |  | 44722.0884 | 50.1084
|  |  | 44722.0884 | 50.1084
|  |  | 44722.0884 | 50.1084
|  |  | 44722.0884 | 50.1083
|  |  | 44722.0884 | 50.1084
|  |  | 44722.0884 | 50.1084
|  |  | 44722.0884 | 50.1083
|  |  | 44722.0884 | 50.1083
|  |  | 44722.0884 | 50.1083
|  |  | 44722.0884 | 50.1083
|  |  | 44722.0884 | 50.1084
|  |  | 44722.0884 | 50.1084
|  |  | 44722.0884 | 50.1084
|  |  | 44722.0884 | 50.1084
|  |  | 44722.0884 | 50.1085
|  |  | 44722.0884 | 50.1085
|  |  | 44722.0884 | 50.1085
|  |  | 44722.0884 | 50.1084
|  |  | 44722.0884 | 50.1083
|  |  | 44722.0884 | 50.1083
|  |  | 44722.0884 | 50.1082
|  |  | 44722.0884 | 50.1082
|  |  | 44722.0884 | 50.1082
|  |  | 44722.0884 | 50.1082
|  |  | 44722.0884 | 50.1082
|  |  | 44722.0884 | 50.1083
|  |  | 2022-06-10 02:07 | 50.1083
|  |  | 44722.0884 | 50.1083
|  |  | 44722.0884 | 50.1084
|  |  | 44722.0884 | 50.1084
|  |  | 44722.0885 | 50.1084
|  |  | 44722.0885 | 50.1084
|  |  | 44722.0885 | 50.1084
|  |  | 44722.0885 | 50.1084
|  |  | 44722.0885 | 50.1084
|  |  | 44722.0885 | 50.1083
|  |  | 44722.0885 | 50.1082
|  |  | 44722.0885 | 50.1082
|  |  | 44722.0885 | 50.1081
|  |  | 44722.0885 | 50.108
|  |  | 44722.0885 | 50.1079
|  |  | 44722.0885 | 50.1078
|  |  | 44722.0885 | 50.1078
|  |  | 44722.0885 | 50.1077
|  |  | 44722.0885 | 50.1077
|  |  | 44722.0885 | 50.1077
|  |  | 44722.0885 | 50.1077
|  |  | 44722.0885 | 50.1076
|  |  | 44722.0885 | 50.1077
|  |  | 44722.0885 | 50.1077
|  |  | 44722.0885 | 50.1078
|  |  | 44722.0885 | 50.1079
|  |  | 44722.0885 | 50.108
|  |  | 44722.0885 | 50.108
|  |  | 44722.0885 | 50.1079
|  |  | 44722.0885 | 50.1079
|  |  | 44722.0885 | 50.1079
|  |  | 44722.0885 | 50.1078
|  |  | 44722.0885 | 50.1078
|  |  | 44722.0885 | 50.1078
|  |  | 44722.0885 | 50.1078
|  |  | 44722.0885 | 50.1077
|  |  | 44722.0885 | 50.1077
|  |  | 44722.0885 | 50.1077
|  |  | 44722.0885 | 50.1076
|  |  | 44722.0885 | 50.1076
|  |  | 44722.0885 | 50.1076
|  |  | 44722.0885 | 50.1075
|  |  | 44722.0885 | 50.1074
|  |  | 44722.0885 | 50.1073
|  |  | 44722.0885 | 50.1072
|  |  | 44722.0885 | 50.1072
|  |  | 44722.0885 | 50.1071
|  |  | 44722.0885 | 50.107
|  |  | 44722.0885 | 50.107
|  |  | 44722.0885 | 50.107
|  |  | 2022-06-10 02:07 | 50.1071
|  |  | 44722.0885 | 50.1071
|  |  | 44722.0885 | 50.1071
|  |  | 44722.0885 | 50.107
|  |  | 44722.0885 | 50.1069
|  |  | 44722.0885 | 50.1068
|  |  | 44722.0885 | 50.1066
|  |  | 44722.0885 | 50.1065
|  |  | 44722.0885 | 50.1063
|  |  | 44722.0885 | 50.1062
|  |  | 44722.0885 | 50.1061
|  |  | 44722.0885 | 50.106
|  |  | 44722.0885 | 50.1059
|  |  | 44722.0885 | 50.1058
|  |  | 44722.0885 | 50.1057
|  |  | 44722.0885 | 50.1055
|  |  | 44722.0885 | 50.1054
|  |  | 44722.0885 | 50.1052
|  |  | 44722.0885 | 50.105
|  |  | 44722.0885 | 50.1048
|  |  | 44722.0885 | 50.1046
|  |  | 44722.0885 | 50.1045
|  |  | 44722.0885 | 50.1044
|  |  | 44722.0885 | 50.1043
|  |  | 44722.0885 | 50.1042
|  |  | 44722.0885 | 50.1041
|  |  | 44722.0885 | 50.104
|  |  | 44722.0885 | 50.104
|  |  | 44722.0885 | 50.1038
|  |  | 44722.0885 | 50.1037
|  |  | 44722.0885 | 50.1037
|  |  | 44722.0885 | 50.1037
|  |  | 44722.0885 | 50.1037
|  |  | 44722.0885 | 50.1036
|  |  | 44722.0885 | 50.1036
|  |  | 44722.0885 | 50.1035
|  |  | 44722.0885 | 50.1034
|  |  | 44722.0885 | 50.1033
|  |  | 44722.0885 | 50.1032
|  |  | 44722.0885 | 50.103
|  |  | 44722.0885 | 50.1029
|  |  | 44722.0885 | 50.1028
|  |  | 44722.0885 | 50.1027
|  |  | 44722.0885 | 50.1027
|  |  | 44722.0885 | 50.1026
|  |  | 44722.0885 | 50.1026
|  |  | 44722.0885 | 50.1026
|  |  | 44722.0885 | 50.1026
|  |  | 44722.0885 | 50.1026
|  |  | 44722.0885 | 50.1026
|  |  | 2022-06-10 02:07 | 50.1025
|  |  | 44722.0885 | 50.1024
|  |  | 44722.0885 | 50.1023
|  |  | 44722.0885 | 50.1022
|  |  | 44722.0885 | 50.102
|  |  | 44722.0885 | 50.1019
|  |  | 44722.0885 | 50.1018
|  |  | 44722.0885 | 50.1016
|  |  | 44722.0885 | 50.1015
|  |  | 44722.0885 | 50.1015
|  |  | 44722.0885 | 50.1014
|  |  | 44722.0885 | 50.1014
|  |  | 44722.0885 | 50.1014
|  |  | 44722.0885 | 50.1014
|  |  | 44722.0885 | 50.1014
|  |  | 44722.0885 | 50.1014
|  |  | 44722.0885 | 50.1013
|  |  | 44722.0885 | 50.1013
|  |  | 44722.0885 | 50.1012
|  |  | 44722.0885 | 50.1011
|  |  | 44722.0885 | 50.101
|  |  | 44722.0885 | 50.1009
|  |  | 44722.0885 | 50.1008
|  |  | 44722.0885 | 50.1006
|  |  | 44722.0885 | 50.1006
|  |  | 44722.0885 | 50.1004
|  |  | 44722.0885 | 50.1003
|  |  | 44722.0885 | 50.1002
|  |  | 44722.0885 | 50.1002
|  |  | 44722.0885 | 50.1001
|  |  | 44722.0885 | 50.1001
|  |  | 44722.0885 | 50.1001
|  |  | 44722.0885 | 50.1001
|  |  | 44722.0885 | 50.1001
|  |  | 44722.0885 | 50.1001
|  |  | 44722.0885 | 50.1001
|  |  | 44722.0885 | 50.1001
|  |  | 44722.0885 | 50.1001
|  |  | 44722.0885 | 50.1001
|  |  | 44722.0885 | 50.1
|  |  | 44722.0885 | 50.0999
|  |  | 44722.0885 | 50.0998
|  |  | 44722.0885 | 50.0998
|  |  | 44722.0885 | 50.0998
|  |  | 44722.0885 | 50.0998
|  |  | 44722.0885 | 50.0998
|  |  | 44722.0885 | 50.0997
|  |  | 44722.0885 | 50.0997
|  |  | 44722.0885 | 50.0997
|  |  | 44722.0885 | 50.0997
|  |  | 2022-06-10 02:07 | 50.0996
|  |  | 44722.0885 | 50.0995
|  |  | 44722.0885 | 50.0992
|  |  | 44722.0885 | 50.0991
|  |  | 44722.0885 | 50.0989
|  |  | 44722.0885 | 50.0988
|  |  | 44722.0885 | 50.0986
|  |  | 44722.0885 | 50.0985
|  |  | 44722.0885 | 50.0984
|  |  | 44722.0885 | 50.0984
|  |  | 44722.0885 | 50.0984
|  |  | 44722.0885 | 50.0984
|  |  | 44722.0885 | 50.0984
|  |  | 44722.0885 | 50.0985
|  |  | 44722.0885 | 50.0985
|  |  | 44722.0885 | 50.0984
|  |  | 44722.0885 | 50.0983
|  |  | 44722.0885 | 50.0982
|  |  | 44722.0885 | 50.098
|  |  | 44722.0885 | 50.0979
|  |  | 44722.0885 | 50.0977
|  |  | 44722.0885 | 50.0975
|  |  | 44722.0885 | 50.0974
|  |  | 44722.0885 | 50.0973
|  |  | 44722.0885 | 50.0972
|  |  | 44722.0885 | 50.0972
|  |  | 44722.0885 | 50.0971
|  |  | 44722.0885 | 50.0971
|  |  | 44722.0885 | 50.097
|  |  | 44722.0885 | 50.097
|  |  | 44722.0885 | 50.097
|  |  | 44722.0885 | 50.097
|  |  | 44722.0885 | 50.0969
|  |  | 44722.0885 | 50.0969
|  |  | 44722.0885 | 50.0968
|  |  | 44722.0885 | 50.0968
|  |  | 44722.0885 | 50.0967
|  |  | 44722.0885 | 50.0966
|  |  | 44722.0885 | 50.0965
|  |  | 44722.0885 | 50.0964
|  |  | 44722.0885 | 50.0964
|  |  | 44722.0885 | 50.0962
|  |  | 44722.0885 | 50.0962
|  |  | 44722.0885 | 50.0961
|  |  | 44722.0885 | 50.0961
|  |  | 44722.0885 | 50.0962
|  |  | 44722.0885 | 50.0962
|  |  | 44722.0885 | 50.0962
|  |  | 44722.0885 | 50.0963
|  |  | 44722.0885 | 50.0964
|  |  | 2022-06-10 02:07 | 50.0964
|  |  | 44722.0885 | 50.0963
|  |  | 44722.0885 | 50.0961
|  |  | 44722.0885 | 50.0959
|  |  | 44722.0885 | 50.0958
|  |  | 44722.0885 | 50.0956
|  |  | 44722.0885 | 50.0954
|  |  | 44722.0885 | 50.0953
|  |  | 44722.0885 | 50.0953
|  |  | 44722.0885 | 50.0952
|  |  | 44722.0885 | 50.0951
|  |  | 44722.0885 | 50.0951
|  |  | 44722.0885 | 50.0952
|  |  | 44722.0885 | 50.0952
|  |  | 44722.0885 | 50.0953
|  |  | 44722.0885 | 50.0953
|  |  | 44722.0885 | 50.0953
|  |  | 44722.0885 | 50.0953
|  |  | 44722.0885 | 50.0953
|  |  | 44722.0885 | 50.0952
|  |  | 44722.0885 | 50.0951
|  |  | 44722.0885 | 50.0949
|  |  | 44722.0885 | 50.0948
|  |  | 44722.0885 | 50.0946
|  |  | 44722.0885 | 50.0945
|  |  | 44722.0885 | 50.0944
|  |  | 44722.0885 | 50.0943
|  |  | 44722.0885 | 50.0943
|  |  | 44722.0885 | 50.0943
|  |  | 44722.0885 | 50.0943
|  |  | 44722.0885 | 50.0944
|  |  | 44722.0885 | 50.0944
|  |  | 44722.0885 | 50.0944
|  |  | 44722.0885 | 50.0944
|  |  | 44722.0885 | 50.0944
|  |  | 44722.0885 | 50.0943
|  |  | 44722.0885 | 50.0942
|  |  | 44722.0885 | 50.0942
|  |  | 44722.0885 | 50.094
|  |  | 44722.0885 | 50.094
|  |  | 44722.0885 | 50.0939
|  |  | 44722.0885 | 50.0939
|  |  | 44722.0885 | 50.0939
|  |  | 44722.0885 | 50.0939
|  |  | 44722.0885 | 50.0938
|  |  | 44722.0885 | 50.0938
|  |  | 44722.0885 | 50.0938
|  |  | 44722.0885 | 50.0939
|  |  | 44722.0885 | 50.0938
|  |  | 44722.0885 | 50.0938
|  |  | 2022-06-10 02:07 | 50.0937
|  |  | 44722.0885 | 50.0936
|  |  | 44722.0885 | 50.0934
|  |  | 44722.0885 | 50.0934
|  |  | 44722.0885 | 50.0934
|  |  | 44722.0885 | 50.0933
|  |  | 44722.0885 | 50.0932
|  |  | 44722.0885 | 50.0931
|  |  | 44722.0885 | 50.0931
|  |  | 44722.0885 | 50.0931
|  |  | 44722.0885 | 50.0931
|  |  | 44722.0885 | 50.0932
|  |  | 44722.0885 | 50.0933
|  |  | 44722.0885 | 50.0933
|  |  | 44722.0885 | 50.0933
|  |  | 44722.0885 | 50.0934
|  |  | 44722.0885 | 50.0934
|  |  | 44722.0885 | 50.0935
|  |  | 44722.0885 | 50.0935
|  |  | 44722.0885 | 50.0935
|  |  | 44722.0885 | 50.0935
|  |  | 44722.0885 | 50.0934
|  |  | 44722.0885 | 50.0933
|  |  | 44722.0885 | 50.0933
|  |  | 44722.0885 | 50.0933
|  |  | 44722.0885 | 50.0933
|  |  | 44722.0885 | 50.0933
|  |  | 44722.0885 | 50.0934
|  |  | 44722.0885 | 50.0934
|  |  | 44722.0885 | 50.0935
|  |  | 44722.0885 | 50.0936
|  |  | 44722.0885 | 50.0936
|  |  | 44722.0885 | 50.0937
|  |  | 44722.0885 | 50.0937
|  |  | 44722.0885 | 50.0937
|  |  | 44722.0885 | 50.0937
|  |  | 44722.0885 | 50.0936
|  |  | 44722.0885 | 50.0935
|  |  | 44722.0885 | 50.0935
|  |  | 44722.0885 | 50.0934
|  |  | 44722.0885 | 50.0933
|  |  | 44722.0885 | 50.0932
|  |  | 44722.0885 | 50.0931
|  |  | 44722.0885 | 50.0931
|  |  | 44722.0885 | 50.0931
|  |  | 44722.0885 | 50.0931
|  |  | 44722.0885 | 50.0931
|  |  | 44722.0885 | 50.0931
|  |  | 44722.0885 | 50.0931
|  |  | 44722.0885 | 50.0933
|  |  | 2022-06-10 02:07 | 50.0934
|  |  | 44722.0885 | 50.0934
|  |  | 44722.0885 | 50.0935
|  |  | 44722.0885 | 50.0935
|  |  | 44722.0885 | 50.0935
|  |  | 44722.0885 | 50.0935
|  |  | 44722.0885 | 50.0934
|  |  | 44722.0885 | 50.0933
|  |  | 44722.0885 | 50.0932
|  |  | 44722.0885 | 50.0932
|  |  | 44722.0885 | 50.0931
|  |  | 44722.0885 | 50.093
|  |  | 44722.0885 | 50.093
|  |  | 44722.0885 | 50.093
|  |  | 44722.0885 | 50.0931
|  |  | 44722.0885 | 50.0931
|  |  | 44722.0885 | 50.0932
|  |  | 44722.0885 | 50.0932
|  |  | 44722.0885 | 50.0933
|  |  | 44722.0885 | 50.0933
|  |  | 44722.0885 | 50.0934
|  |  | 44722.0885 | 50.0935
|  |  | 44722.0885 | 50.0935
|  |  | 44722.0885 | 50.0936
|  |  | 44722.0885 | 50.0937
|  |  | 44722.0885 | 50.0938
|  |  | 44722.0885 | 50.0939
|  |  | 44722.0885 | 50.094
|  |  | 44722.0885 | 50.094
|  |  | 44722.0885 | 50.0941
|  |  | 44722.0885 | 50.0941
|  |  | 44722.0885 | 50.0941
|  |  | 44722.0885 | 50.0941
|  |  | 44722.0885 | 50.094
|  |  | 44722.0885 | 50.094
|  |  | 44722.0885 | 50.094
|  |  | 44722.0885 | 50.0941
|  |  | 44722.0885 | 50.0941
|  |  | 44722.0885 | 50.0943
|  |  | 44722.0885 | 50.0944
|  |  | 44722.0885 | 50.0945
|  |  | 44722.0885 | 50.0946
|  |  | 44722.0885 | 50.0948
|  |  | 44722.0885 | 50.0949
|  |  | 44722.0885 | 50.095
|  |  | 44722.0885 | 50.095
|  |  | 44722.0885 | 50.0951
|  |  | 44722.0885 | 50.0951
|  |  | 44722.0885 | 50.0951
|  |  | 44722.0885 | 50.0951
|  |  | 2022-06-10 02:07 | 50.0952
|  |  | 44722.0885 | 50.0953
|  |  | 44722.0885 | 50.0955
|  |  | 44722.0885 | 50.0963
|  |  | 44722.0885 | 50.0977
|  |  | 44722.0885 | 50.1001
|  |  | 44722.0885 | 50.1035
|  |  | 44722.0885 | 50.108
|  |  | 44722.0885 | 50.1131
|  |  | 44722.0885 | 50.1184
|  |  | 44722.0885 | 50.1234
|  |  | 44722.0885 | 50.1277
|  |  | 44722.0885 | 50.1308
|  |  | 44722.0885 | 50.1327
|  |  | 44722.0885 | 50.1332
|  |  | 44722.0885 | 50.133
|  |  | 44722.0885 | 50.1323
|  |  | 44722.0885 | 50.1314
|  |  | 44722.0885 | 50.1307
|  |  | 44722.0885 | 50.1304
|  |  | 44722.0885 | 50.131
|  |  | 44722.0885 | 50.1325
|  |  | 44722.0885 | 50.1347
|  |  | 44722.0885 | 50.1376
|  |  | 44722.0885 | 50.1409
|  |  | 44722.0885 | 50.1441
|  |  | 44722.0885 | 50.1476
|  |  | 44722.0885 | 50.1507
|  |  | 44722.0885 | 50.1531
|  |  | 44722.0885 | 50.155
|  |  | 44722.0885 | 50.1564
|  |  | 44722.0885 | 50.1573
|  |  | 44722.0885 | 50.1576
|  |  | 44722.0885 | 50.1579
|  |  | 44722.0885 | 50.1583
|  |  | 44722.0885 | 50.1591
|  |  | 44722.0885 | 50.1597
|  |  | 44722.0885 | 50.1605
|  |  | 44722.0885 | 50.1616
|  |  | 44722.0885 | 50.1629
|  |  | 44722.0885 | 50.1643
|  |  | 44722.0885 | 50.1659
|  |  | 44722.0885 | 50.1675
|  |  | 44722.0885 | 50.1691
|  |  | 44722.0885 | 50.1706
|  |  | 44722.0885 | 50.1721
|  |  | 44722.0885 | 50.1734
|  |  | 44722.0885 | 50.1747
|  |  | 44722.0885 | 50.176
|  |  | 44722.0885 | 50.1773
|  |  | 2022-06-10 02:08 | 50.1786
|  |  | 44722.0885 | 50.1801
|  |  | 44722.0885 | 50.1814
|  |  | 44722.0885 | 50.1831
|  |  | 44722.0885 | 50.1847
|  |  | 44722.0885 | 50.1863
|  |  | 44722.0885 | 50.188
|  |  | 44722.0885 | 50.1896
|  |  | 44722.0885 | 50.1912
|  |  | 44722.0885 | 50.1929
|  |  | 44722.0885 | 50.1946
|  |  | 44722.0885 | 50.1964
|  |  | 44722.0885 | 50.1979
|  |  | 44722.0885 | 50.1996
|  |  | 44722.0885 | 50.2014
|  |  | 44722.0885 | 50.2032
|  |  | 44722.0885 | 50.205
|  |  | 44722.0885 | 50.2068
|  |  | 44722.0885 | 50.2086
|  |  | 44722.0885 | 50.2105
|  |  | 44722.0885 | 50.2123
|  |  | 44722.0885 | 50.214
|  |  | 44722.0885 | 50.2158
|  |  | 44722.0885 | 50.2177
|  |  | 44722.0885 | 50.2196
|  |  | 44722.0885 | 50.2214
|  |  | 44722.0885 | 50.2233
|  |  | 44722.0885 | 50.225
|  |  | 44722.0885 | 50.2267
|  |  | 44722.0885 | 50.2284
|  |  | 44722.0885 | 50.2301
|  |  | 44722.0885 | 50.2318
|  |  | 44722.0885 | 50.2335
|  |  | 44722.0885 | 50.2352
|  |  | 44722.0885 | 50.2369
|  |  | 44722.0885 | 50.2387
|  |  | 44722.0886 | 50.2405
|  |  | 44722.0886 | 50.2423
|  |  | 44722.0886 | 50.2441
|  |  | 44722.0886 | 50.2458
|  |  | 44722.0886 | 50.2475
|  |  | 44722.0886 | 50.2491
|  |  | 44722.0886 | 50.2506
|  |  | 44722.0886 | 50.252
|  |  | 44722.0886 | 50.2535
|  |  | 44722.0886 | 50.2549
|  |  | 44722.0886 | 50.2563
|  |  | 44722.0886 | 50.2577
|  |  | 44722.0886 | 50.2591
|  |  | 44722.0886 | 50.2604
|  |  | 2022-06-10 02:08 | 50.2618
|  |  | 44722.0886 | 50.2631
|  |  | 44722.0886 | 50.2644
|  |  | 44722.0886 | 50.2657
|  |  | 44722.0886 | 50.2668
|  |  | 44722.0886 | 50.2681
|  |  | 44722.0886 | 50.2691
|  |  | 44722.0886 | 50.27
|  |  | 44722.0886 | 50.2708
|  |  | 44722.0886 | 50.2717
|  |  | 44722.0886 | 50.2726
|  |  | 44722.0886 | 50.2735
|  |  | 44722.0886 | 50.2745
|  |  | 44722.0886 | 50.2754
|  |  | 44722.0886 | 50.2764
|  |  | 44722.0886 | 50.2774
|  |  | 44722.0886 | 50.2783
|  |  | 44722.0886 | 50.2792
|  |  | 44722.0886 | 50.2801
|  |  | 44722.0886 | 50.281
|  |  | 44722.0886 | 50.2818
|  |  | 44722.0886 | 50.2825
|  |  | 44722.0886 | 50.2831
|  |  | 44722.0886 | 50.2837
|  |  | 44722.0886 | 50.2843
|  |  | 44722.0886 | 50.285
|  |  | 44722.0886 | 50.2857
|  |  | 44722.0886 | 50.2863
|  |  | 44722.0886 | 50.2871
|  |  | 44722.0886 | 50.288
|  |  | 44722.0886 | 50.289
|  |  | 44722.0886 | 50.29
|  |  | 44722.0886 | 50.2912
|  |  | 44722.0886 | 50.2921
|  |  | 44722.0886 | 50.2931
|  |  | 44722.0886 | 50.294
|  |  | 44722.0886 | 50.2949
|  |  | 44722.0886 | 50.2957
|  |  | 44722.0886 | 50.2965
|  |  | 44722.0886 | 50.2972
|  |  | 44722.0886 | 50.2979
|  |  | 44722.0886 | 50.2985
|  |  | 44722.0886 | 50.299
|  |  | 44722.0886 | 50.2996
|  |  | 44722.0886 | 50.3002
|  |  | 44722.0886 | 50.3007
|  |  | 44722.0886 | 50.3011
|  |  | 44722.0886 | 50.3015
|  |  | 44722.0886 | 50.3019
|  |  | 44722.0886 | 50.3023
|  |  | 2022-06-10 02:08 | 50.3026
|  |  | 44722.0886 | 50.303
|  |  | 44722.0886 | 50.3034
|  |  | 44722.0886 | 50.3037
|  |  | 44722.0886 | 50.3042
|  |  | 44722.0886 | 50.3046
|  |  | 44722.0886 | 50.3051
|  |  | 44722.0886 | 50.3055
|  |  | 44722.0886 | 50.306
|  |  | 44722.0886 | 50.3064
|  |  | 44722.0886 | 50.3068
|  |  | 44722.0886 | 50.3071
|  |  | 44722.0886 | 50.3074
|  |  | 44722.0886 | 50.3078
|  |  | 44722.0886 | 50.3083
|  |  | 44722.0886 | 50.3087
|  |  | 44722.0886 | 50.3092
|  |  | 44722.0886 | 50.3098
|  |  | 44722.0886 | 50.3103
|  |  | 44722.0886 | 50.311
|  |  | 44722.0886 | 50.3116
|  |  | 44722.0886 | 50.3121
|  |  | 44722.0886 | 50.3127
|  |  | 44722.0886 | 50.3132
|  |  | 44722.0886 | 50.3136
|  |  | 44722.0886 | 50.314
|  |  | 44722.0886 | 50.3143
|  |  | 44722.0886 | 50.3147
|  |  | 44722.0886 | 50.3148
|  |  | 44722.0886 | 50.315
|  |  | 44722.0886 | 50.3153
|  |  | 44722.0886 | 50.3155
|  |  | 44722.0886 | 50.3158
|  |  | 44722.0886 | 50.316
|  |  | 44722.0886 | 50.316
|  |  | 44722.0886 | 50.3161
|  |  | 44722.0886 | 50.3163
|  |  | 44722.0886 | 50.3164
|  |  | 44722.0886 | 50.3166
|  |  | 44722.0886 | 50.3166
|  |  | 44722.0886 | 50.3166
|  |  | 44722.0886 | 50.3166
|  |  | 44722.0886 | 50.3167
|  |  | 44722.0886 | 50.3167
|  |  | 44722.0886 | 50.3168
|  |  | 44722.0886 | 50.3168
|  |  | 44722.0886 | 50.3169
|  |  | 44722.0886 | 50.317
|  |  | 44722.0886 | 50.3172
|  |  | 44722.0886 | 50.3172
|  |  | 2022-06-10 02:08 | 50.3173
|  |  | 44722.0886 | 50.3174
|  |  | 44722.0886 | 50.3177
|  |  | 44722.0886 | 50.3178
|  |  | 44722.0886 | 50.3179
|  |  | 44722.0886 | 50.3179
|  |  | 44722.0886 | 50.318
|  |  | 44722.0886 | 50.3181
|  |  | 44722.0886 | 50.3182
|  |  | 44722.0886 | 50.3183
|  |  | 44722.0886 | 50.3184
|  |  | 44722.0886 | 50.3185
|  |  | 44722.0886 | 50.3186
|  |  | 44722.0886 | 50.3186
|  |  | 44722.0886 | 50.3187
|  |  | 44722.0886 | 50.3187
|  |  | 44722.0886 | 50.3186
|  |  | 44722.0886 | 50.3185
|  |  | 44722.0886 | 50.3184
|  |  | 44722.0886 | 50.3183
|  |  | 44722.0886 | 50.3182
|  |  | 44722.0886 | 50.3181
|  |  | 44722.0886 | 50.3179
|  |  | 44722.0886 | 50.3179
|  |  | 44722.0886 | 50.3179
|  |  | 44722.0886 | 50.3177
|  |  | 44722.0886 | 50.3177
|  |  | 44722.0886 | 50.3176
|  |  | 44722.0886 | 50.3175
|  |  | 44722.0886 | 50.3174
|  |  | 44722.0886 | 50.3174
|  |  | 44722.0886 | 50.3173
|  |  | 44722.0886 | 50.3173
|  |  | 44722.0886 | 50.3172
|  |  | 44722.0886 | 50.3172
|  |  | 44722.0886 | 50.3171
|  |  | 44722.0886 | 50.3169
|  |  | 44722.0886 | 50.3168
|  |  | 44722.0886 | 50.3167
|  |  | 44722.0886 | 50.3166
|  |  | 44722.0886 | 50.3164
|  |  | 44722.0886 | 50.3163
|  |  | 44722.0886 | 50.3163
|  |  | 44722.0886 | 50.3162
|  |  | 44722.0886 | 50.3163
|  |  | 44722.0886 | 50.3163
|  |  | 44722.0886 | 50.3164
|  |  | 44722.0886 | 50.3166
|  |  | 44722.0886 | 50.3166
|  |  | 44722.0886 | 50.3167
|  |  | 2022-06-10 02:08 | 50.3166
|  |  | 44722.0886 | 50.3166
|  |  | 44722.0886 | 50.3165
|  |  | 44722.0886 | 50.3164
|  |  | 44722.0886 | 50.3163
|  |  | 44722.0886 | 50.3162
|  |  | 44722.0886 | 50.3162
|  |  | 44722.0886 | 50.3162
|  |  | 44722.0886 | 50.3162
|  |  | 44722.0886 | 50.3161
|  |  | 44722.0886 | 50.3161
|  |  | 44722.0886 | 50.3161
|  |  | 44722.0886 | 50.3161
|  |  | 44722.0886 | 50.316
|  |  | 44722.0886 | 50.3158
|  |  | 44722.0886 | 50.3155
|  |  | 44722.0886 | 50.3153
|  |  | 44722.0886 | 50.315
|  |  | 44722.0886 | 50.3149
|  |  | 44722.0886 | 50.3146
|  |  | 44722.0886 | 50.3144
|  |  | 44722.0886 | 50.3142
|  |  | 44722.0886 | 50.3141
|  |  | 44722.0886 | 50.314
|  |  | 44722.0886 | 50.3139
|  |  | 44722.0886 | 50.3138
|  |  | 44722.0886 | 50.3138
|  |  | 44722.0886 | 50.3137
|  |  | 44722.0886 | 50.3136
|  |  | 44722.0886 | 50.3135
|  |  | 44722.0886 | 50.3133
|  |  | 44722.0886 | 50.3131
|  |  | 44722.0886 | 50.3129
|  |  | 44722.0886 | 50.3127
|  |  | 44722.0886 | 50.3126
|  |  | 44722.0886 | 50.3124
|  |  | 44722.0886 | 50.3123
|  |  | 44722.0886 | 50.3122
|  |  | 44722.0886 | 50.3121
|  |  | 44722.0886 | 50.3121
|  |  | 44722.0886 | 50.3121
|  |  | 44722.0886 | 50.3121
|  |  | 44722.0886 | 50.3121
|  |  | 44722.0886 | 50.3121
|  |  | 44722.0886 | 50.3121
|  |  | 44722.0886 | 50.3121
|  |  | 44722.0886 | 50.3121
|  |  | 44722.0886 | 50.312
|  |  | 44722.0886 | 50.3119
|  |  | 44722.0886 | 50.3118
|  |  | 2022-06-10 02:08 | 50.3117
|  |  | 44722.0886 | 50.3116
|  |  | 44722.0886 | 50.3114
|  |  | 44722.0886 | 50.3113
|  |  | 44722.0886 | 50.3111
|  |  | 44722.0886 | 50.3108
|  |  | 44722.0886 | 50.3106
|  |  | 44722.0886 | 50.3103
|  |  | 44722.0886 | 50.31
|  |  | 44722.0886 | 50.3098
|  |  | 44722.0886 | 50.3096
|  |  | 44722.0886 | 50.3094
|  |  | 44722.0886 | 50.3094
|  |  | 44722.0886 | 50.3092
|  |  | 44722.0886 | 50.3091
|  |  | 44722.0886 | 50.309
|  |  | 44722.0886 | 50.309
|  |  | 44722.0886 | 50.3089
|  |  | 44722.0886 | 50.3088
|  |  | 44722.0886 | 50.3088
|  |  | 44722.0886 | 50.3087
|  |  | 44722.0886 | 50.3086
|  |  | 44722.0886 | 50.3084
|  |  | 44722.0886 | 50.3082
|  |  | 44722.0886 | 50.308
|  |  | 44722.0886 | 50.3078
|  |  | 44722.0886 | 50.3075
|  |  | 44722.0886 | 50.3073
|  |  | 44722.0886 | 50.307
|  |  | 44722.0886 | 50.3068
|  |  | 44722.0886 | 50.3066
|  |  | 44722.0886 | 50.3064
|  |  | 44722.0886 | 50.3063
|  |  | 44722.0886 | 50.3062
|  |  | 44722.0886 | 50.3062
|  |  | 44722.0886 | 50.3062
|  |  | 44722.0886 | 50.3061
|  |  | 44722.0886 | 50.3061
|  |  | 44722.0886 | 50.306
|  |  | 44722.0886 | 50.3059
|  |  | 44722.0886 | 50.3057
|  |  | 44722.0886 | 50.3056
|  |  | 44722.0886 | 50.3054
|  |  | 44722.0886 | 50.3052
|  |  | 44722.0886 | 50.305
|  |  | 44722.0886 | 50.3048
|  |  | 44722.0886 | 50.3046
|  |  | 44722.0886 | 50.3045
|  |  | 44722.0886 | 50.3044
|  |  | 44722.0886 | 50.3043
|  |  | 2022-06-10 02:08 | 50.3042
|  |  | 44722.0886 | 50.3041
|  |  | 44722.0886 | 50.304
|  |  | 44722.0886 | 50.3038
|  |  | 44722.0886 | 50.3037
|  |  | 44722.0886 | 50.3035
|  |  | 44722.0886 | 50.3033
|  |  | 44722.0886 | 50.3032
|  |  | 44722.0886 | 50.303
|  |  | 44722.0886 | 50.3028
|  |  | 44722.0886 | 50.3026
|  |  | 44722.0886 | 50.3025
|  |  | 44722.0886 | 50.3023
|  |  | 44722.0886 | 50.3021
|  |  | 44722.0886 | 50.3021
|  |  | 44722.0886 | 50.302
|  |  | 44722.0886 | 50.302
|  |  | 44722.0886 | 50.302
|  |  | 44722.0886 | 50.302
|  |  | 44722.0886 | 50.302
|  |  | 44722.0886 | 50.3019
|  |  | 44722.0886 | 50.3019
|  |  | 44722.0886 | 50.3018
|  |  | 44722.0886 | 50.3017
|  |  | 44722.0886 | 50.3016
|  |  | 44722.0886 | 50.3014
|  |  | 44722.0886 | 50.3013
|  |  | 44722.0886 | 50.3012
|  |  | 44722.0886 | 50.3011
|  |  | 44722.0886 | 50.301
|  |  | 44722.0886 | 50.3009
|  |  | 44722.0886 | 50.3008
|  |  | 44722.0886 | 50.3007
|  |  | 44722.0886 | 50.3005
|  |  | 44722.0886 | 50.3003
|  |  | 44722.0886 | 50.3001
|  |  | 44722.0886 | 50.3
|  |  | 44722.0886 | 50.2998
|  |  | 44722.0886 | 50.2996
|  |  | 44722.0886 | 50.2995
|  |  | 44722.0886 | 50.2993
|  |  | 44722.0886 | 50.2992
|  |  | 44722.0886 | 50.2991
|  |  | 44722.0886 | 50.299
|  |  | 44722.0886 | 50.299
|  |  | 44722.0886 | 50.2989
|  |  | 44722.0886 | 50.2989
|  |  | 44722.0886 | 50.2989
|  |  | 44722.0886 | 50.2989
|  |  | 44722.0886 | 50.2988
|  |  | 2022-06-10 02:08 | 50.2988
|  |  | 44722.0886 | 50.2986
|  |  | 44722.0886 | 50.2985
|  |  | 44722.0886 | 50.2984
|  |  | 44722.0886 | 50.2983
|  |  | 44722.0886 | 50.2982
|  |  | 44722.0886 | 50.2981
|  |  | 44722.0886 | 50.2981
|  |  | 44722.0886 | 50.2981
|  |  | 44722.0886 | 50.2981
|  |  | 44722.0886 | 50.2982
|  |  | 44722.0886 | 50.2982
|  |  | 44722.0886 | 50.2981
|  |  | 44722.0886 | 50.2981
|  |  | 44722.0886 | 50.2981
|  |  | 44722.0886 | 50.2981
|  |  | 44722.0886 | 50.2981
|  |  | 44722.0886 | 50.298
|  |  | 44722.0886 | 50.2979
|  |  | 44722.0886 | 50.2978
|  |  | 44722.0886 | 50.2978
|  |  | 44722.0886 | 50.2976
|  |  | 44722.0886 | 50.2975
|  |  | 44722.0886 | 50.2974
|  |  | 44722.0886 | 50.2972
|  |  | 44722.0886 | 50.2971
|  |  | 44722.0886 | 50.297
|  |  | 44722.0886 | 50.2969
|  |  | 44722.0886 | 50.2968
|  |  | 44722.0886 | 50.2967
|  |  | 44722.0886 | 50.2967
|  |  | 44722.0886 | 50.2967
|  |  | 44722.0886 | 50.2968
|  |  | 44722.0886 | 50.2968
|  |  | 44722.0886 | 50.2967
|  |  | 44722.0886 | 50.2966
|  |  | 44722.0886 | 50.2965
|  |  | 44722.0886 | 50.2964
|  |  | 44722.0886 | 50.2963
|  |  | 44722.0886 | 50.2963
|  |  | 44722.0886 | 50.2963
|  |  | 44722.0886 | 50.2963
|  |  | 44722.0886 | 50.2963
|  |  | 44722.0886 | 50.2963
|  |  | 44722.0886 | 50.2964
|  |  | 44722.0886 | 50.2964
|  |  | 44722.0886 | 50.2964
|  |  | 44722.0886 | 50.2963
|  |  | 44722.0886 | 50.2964
|  |  | 44722.0886 | 50.2963
|  |  | 2022-06-10 02:08 | 50.2963
|  |  | 44722.0886 | 50.2963
|  |  | 44722.0886 | 50.2963
|  |  | 44722.0886 | 50.2963
|  |  | 44722.0886 | 50.2963
|  |  | 44722.0886 | 50.2963
|  |  | 44722.0886 | 50.2963
|  |  | 44722.0886 | 50.2963
|  |  | 44722.0886 | 50.2963
|  |  | 44722.0886 | 50.2963
|  |  | 44722.0886 | 50.2963
|  |  | 44722.0886 | 50.2963
|  |  | 44722.0886 | 50.2964
|  |  | 44722.0886 | 50.2963
|  |  | 44722.0886 | 50.2963
|  |  | 44722.0886 | 50.2962
|  |  | 44722.0886 | 50.2961
|  |  | 44722.0886 | 50.2962
|  |  | 44722.0886 | 50.2962
|  |  | 44722.0886 | 50.2963
|  |  | 44722.0886 | 50.2964
|  |  | 44722.0886 | 50.2965
|  |  | 44722.0886 | 50.2966
|  |  | 44722.0886 | 50.2967
|  |  | 44722.0886 | 50.2967
|  |  | 44722.0886 | 50.2967
|  |  | 44722.0886 | 50.2967
|  |  | 44722.0886 | 50.2967
|  |  | 44722.0886 | 50.2967
|  |  | 44722.0886 | 50.2966
|  |  | 44722.0886 | 50.2966
|  |  | 44722.0886 | 50.2966
|  |  | 44722.0886 | 50.2966
|  |  | 44722.0886 | 50.2966
|  |  | 44722.0886 | 50.2967
|  |  | 44722.0886 | 50.2967
|  |  | 44722.0886 | 50.2966
|  |  | 44722.0886 | 50.2967
|  |  | 44722.0886 | 50.2967
|  |  | 44722.0886 | 50.2967
|  |  | 44722.0886 | 50.2966
|  |  | 44722.0886 | 50.2966
|  |  | 44722.0886 | 50.2966
|  |  | 44722.0886 | 50.2965
|  |  | 44722.0886 | 50.2965
|  |  | 44722.0886 | 50.2965
|  |  | 44722.0886 | 50.2966
|  |  | 44722.0886 | 50.2966
|  |  | 44722.0886 | 50.2966
|  |  | 44722.0886 | 50.2967
|  |  | 2022-06-10 02:08 | 50.2967
|  |  | 44722.0886 | 50.2966
|  |  | 44722.0886 | 50.2966
|  |  | 44722.0886 | 50.2965
|  |  | 44722.0886 | 50.2964
|  |  | 44722.0886 | 50.2963
|  |  | 44722.0886 | 50.2962
|  |  | 44722.0886 | 50.2961
|  |  | 44722.0886 | 50.2961
|  |  | 44722.0886 | 50.296
|  |  | 44722.0886 | 50.296
|  |  | 44722.0886 | 50.296
|  |  | 44722.0886 | 50.296
|  |  | 44722.0886 | 50.2959
|  |  | 44722.0886 | 50.2959
|  |  | 44722.0886 | 50.2959
|  |  | 44722.0886 | 50.2959
|  |  | 44722.0886 | 50.2958
|  |  | 44722.0886 | 50.2958
|  |  | 44722.0887 | 50.2958
|  |  | 44722.0887 | 50.2958
|  |  | 44722.0887 | 50.2958
|  |  | 44722.0887 | 50.2958
|  |  | 44722.0887 | 50.2958
|  |  | 44722.0887 | 50.2958
|  |  | 44722.0887 | 50.2958
|  |  | 44722.0887 | 50.2958
|  |  | 44722.0887 | 50.2959
|  |  | 44722.0887 | 50.2959
|  |  | 44722.0887 | 50.296
|  |  | 44722.0887 | 50.296
|  |  | 44722.0887 | 50.296
|  |  | 44722.0887 | 50.2959
|  |  | 44722.0887 | 50.2959
|  |  | 44722.0887 | 50.2959
|  |  | 44722.0887 | 50.2959
|  |  | 44722.0887 | 50.2959
|  |  | 44722.0887 | 50.2959
|  |  | 44722.0887 | 50.2959
|  |  | 44722.0887 | 50.2959
|  |  | 44722.0887 | 50.296
|  |  | 44722.0887 | 50.2961
|  |  | 44722.0887 | 50.2962
|  |  | 44722.0887 | 50.2962
|  |  | 44722.0887 | 50.2963
|  |  | 44722.0887 | 50.2964
|  |  | 44722.0887 | 50.2964
|  |  | 44722.0887 | 50.2964
|  |  | 44722.0887 | 50.2965
|  |  | 44722.0887 | 50.2964
|  |  | 2022-06-10 02:08 | 50.2964
|  |  | 44722.0887 | 50.2963
|  |  | 44722.0887 | 50.2962
|  |  | 44722.0887 | 50.2961
|  |  | 44722.0887 | 50.2961
|  |  | 44722.0887 | 50.296
|  |  | 44722.0887 | 50.296
|  |  | 44722.0887 | 50.2959
|  |  | 44722.0887 | 50.2959
|  |  | 44722.0887 | 50.296
|  |  | 44722.0887 | 50.2961
|  |  | 44722.0887 | 50.2962
|  |  | 44722.0887 | 50.2963
|  |  | 44722.0887 | 50.2963
|  |  | 44722.0887 | 50.2964
|  |  | 44722.0887 | 50.2965
|  |  | 44722.0887 | 50.2965
|  |  | 44722.0887 | 50.2965
|  |  | 44722.0887 | 50.2965
|  |  | 44722.0887 | 50.2966
|  |  | 44722.0887 | 50.2966
|  |  | 44722.0887 | 50.2966
|  |  | 44722.0887 | 50.2965
|  |  | 44722.0887 | 50.2965
|  |  | 44722.0887 | 50.2965
|  |  | 44722.0887 | 50.2966
|  |  | 44722.0887 | 50.2966
|  |  | 44722.0887 | 50.2966
|  |  | 44722.0887 | 50.2966
|  |  | 44722.0887 | 50.2967
|  |  | 44722.0887 | 50.2965
|  |  | 44722.0887 | 50.2965
|  |  | 44722.0887 | 50.2965
|  |  | 44722.0887 | 50.2964
|  |  | 44722.0887 | 50.2964
|  |  | 44722.0887 | 50.2964
|  |  | 44722.0887 | 50.2964
|  |  | 44722.0887 | 50.2965
|  |  | 44722.0887 | 50.2965
|  |  | 44722.0887 | 50.2968
|  |  | 44722.0887 | 50.2969
|  |  | 44722.0887 | 50.297
|  |  | 44722.0887 | 50.2971
|  |  | 44722.0887 | 50.2972
|  |  | 44722.0887 | 50.2973
|  |  | 44722.0887 | 50.2973
|  |  | 44722.0887 | 50.2973
|  |  | 44722.0887 | 50.2974
|  |  | 44722.0887 | 50.2974
|  |  | 44722.0887 | 50.2974
|  |  | 2022-06-10 02:08 | 50.2975
|  |  | 44722.0887 | 50.2975
|  |  | 44722.0887 | 50.2975
|  |  | 44722.0887 | 50.2974
|  |  | 44722.0887 | 50.2975
|  |  | 44722.0887 | 50.2975
|  |  | 44722.0887 | 50.2974
|  |  | 44722.0887 | 50.2974
|  |  | 44722.0887 | 50.2976
|  |  | 44722.0887 | 50.2977
|  |  | 44722.0887 | 50.2977
|  |  | 44722.0887 | 50.2978
|  |  | 44722.0887 | 50.2979
|  |  | 44722.0887 | 50.2979
|  |  | 44722.0887 | 50.2979
|  |  | 44722.0887 | 50.2978
|  |  | 44722.0887 | 50.2977
|  |  | 44722.0887 | 50.2977
|  |  | 44722.0887 | 50.2977
|  |  | 44722.0887 | 50.2977
|  |  | 44722.0887 | 50.2978
|  |  | 44722.0887 | 50.2979
|  |  | 44722.0887 | 50.298
|  |  | 44722.0887 | 50.2981
|  |  | 44722.0887 | 50.2982
|  |  | 44722.0887 | 50.2983
|  |  | 44722.0887 | 50.2984
|  |  | 44722.0887 | 50.2985
|  |  | 44722.0887 | 50.2985
|  |  | 44722.0887 | 50.2986
|  |  | 44722.0887 | 50.2988
|  |  | 44722.0887 | 50.2987
|  |  | 44722.0887 | 50.2987
|  |  | 44722.0887 | 50.2988
|  |  | 44722.0887 | 50.2988
|  |  | 44722.0887 | 50.2989
|  |  | 44722.0887 | 50.299
|  |  | 44722.0887 | 50.2992
|  |  | 44722.0887 | 50.2993
|  |  | 44722.0887 | 50.2995
|  |  | 44722.0887 | 50.2994
|  |  | 44722.0887 | 50.2997
|  |  | 44722.0887 | 50.2999
|  |  | 44722.0887 | 50.3
|  |  | 44722.0887 | 50.3001
|  |  | 44722.0887 | 50.3
|  |  | 44722.0887 | 50.3
|  |  | 44722.0887 | 50.3003
|  |  | 44722.0887 | 50.3004
|  |  | 44722.0887 | 50.3005
|  |  | 2022-06-10 02:08 | 50.3006
|  |  | 44722.0887 | 50.3008
|  |  | 44722.0887 | 50.3009
|  |  | 44722.0887 | 50.301
|  |  | 44722.0887 | 50.3012
|  |  | 44722.0887 | 50.3012
|  |  | 44722.0887 | 50.3013
|  |  | 44722.0887 | 50.3012
|  |  | 44722.0887 | 50.301
|  |  | 44722.0887 | 50.3011
|  |  | 44722.0887 | 50.301
|  |  | 44722.0887 | 50.301
|  |  | 44722.0887 | 50.3009
|  |  | 44722.0887 | 50.301
|  |  | 44722.0887 | 50.301
|  |  | 44722.0887 | 50.3011
|  |  | 44722.0887 | 50.3012
|  |  | 44722.0887 | 50.3013
|  |  | 44722.0887 | 50.3014
|  |  | 44722.0887 | 50.3016
|  |  | 44722.0887 | 50.3015
|  |  | 44722.0887 | 50.3015
|  |  | 44722.0887 | 50.3017
|  |  | 44722.0887 | 50.3017
|  |  | 44722.0887 | 50.3017
|  |  | 44722.0887 | 50.3016
|  |  | 44722.0887 | 50.3016
|  |  | 44722.0887 | 50.3016
|  |  | 44722.0887 | 50.3014
|  |  | 44722.0887 | 50.3015
|  |  | 44722.0887 | 50.3017
|  |  | 44722.0887 | 50.3017
|  |  | 44722.0887 | 50.3017
|  |  | 44722.0887 | 50.3017
|  |  | 44722.0887 | 50.3018
|  |  | 44722.0887 | 50.3019
|  |  | 44722.0887 | 50.302
|  |  | 44722.0887 | 50.3021
|  |  | 44722.0887 | 50.3021
|  |  | 44722.0887 | 50.3022
|  |  | 44722.0887 | 50.3023
|  |  | 44722.0887 | 50.3023
|  |  | 44722.0887 | 50.3024
|  |  | 44722.0887 | 50.3025
|  |  | 44722.0887 | 50.3025
|  |  | 44722.0887 | 50.3026
|  |  | 44722.0887 | 50.3027
|  |  | 44722.0887 | 50.3027
|  |  | 44722.0887 | 50.3028
|  |  | 44722.0887 | 50.3029
|  |  | 2022-06-10 02:08 | 50.303
|  |  | 44722.0887 | 50.3031
|  |  | 44722.0887 | 50.3031
|  |  | 44722.0887 | 50.3031
|  |  | 44722.0887 | 50.303
|  |  | 44722.0887 | 50.303
|  |  | 44722.0887 | 50.303
|  |  | 44722.0887 | 50.3029
|  |  | 44722.0887 | 50.303
|  |  | 44722.0887 | 50.303
|  |  | 44722.0887 | 50.303
|  |  | 44722.0887 | 50.3031
|  |  | 44722.0887 | 50.3031
|  |  | 44722.0887 | 50.3031
|  |  | 44722.0887 | 50.3031
|  |  | 44722.0887 | 50.3032
|  |  | 44722.0887 | 50.3032
|  |  | 44722.0887 | 50.3032
|  |  | 44722.0887 | 50.3031
|  |  | 44722.0887 | 50.3032
|  |  | 44722.0887 | 50.3031
|  |  | 44722.0887 | 50.3031
|  |  | 44722.0887 | 50.303
|  |  | 44722.0887 | 50.303
|  |  | 44722.0887 | 50.3029
|  |  | 44722.0887 | 50.3029
|  |  | 44722.0887 | 50.3029
|  |  | 44722.0887 | 50.3027
|  |  | 44722.0887 | 50.3027
|  |  | 44722.0887 | 50.3026
|  |  | 44722.0887 | 50.3027
|  |  | 44722.0887 | 50.3027
|  |  | 44722.0887 | 50.3028
|  |  | 44722.0887 | 50.3029
|  |  | 44722.0887 | 50.3029
|  |  | 44722.0887 | 50.303
|  |  | 44722.0887 | 50.3031
|  |  | 44722.0887 | 50.3031
|  |  | 44722.0887 | 50.3031
|  |  | 44722.0887 | 50.3032
|  |  | 44722.0887 | 50.3032
|  |  | 44722.0887 | 50.3032
|  |  | 44722.0887 | 50.3031
|  |  | 44722.0887 | 50.3031
|  |  | 44722.0887 | 50.303
|  |  | 44722.0887 | 50.303
|  |  | 44722.0887 | 50.303
|  |  | 44722.0887 | 50.3029
|  |  | 44722.0887 | 50.303
|  |  | 44722.0887 | 50.303
|  |  | 2022-06-10 02:08 | 50.303
|  |  | 44722.0887 | 50.303
|  |  | 44722.0887 | 50.303
|  |  | 44722.0887 | 50.303
|  |  | 44722.0887 | 50.3031
|  |  | 44722.0887 | 50.3031
|  |  | 44722.0887 | 50.3031
|  |  | 44722.0887 | 50.3031
|  |  | 44722.0887 | 50.3031
|  |  | 44722.0887 | 50.3031
|  |  | 44722.0887 | 50.3032
|  |  | 44722.0887 | 50.3031
|  |  | 44722.0887 | 50.3031
|  |  | 44722.0887 | 50.3032
|  |  | 44722.0887 | 50.3033
|  |  | 44722.0887 | 50.3032
|  |  | 44722.0887 | 50.3033
|  |  | 44722.0887 | 50.3034
|  |  | 44722.0887 | 50.3035
|  |  | 44722.0887 | 50.3036
|  |  | 44722.0887 | 50.3035
|  |  | 44722.0887 | 50.3035
|  |  | 44722.0887 | 50.3035
|  |  | 44722.0887 | 50.3035
|  |  | 44722.0887 | 50.3034
|  |  | 44722.0887 | 50.3033
|  |  | 44722.0887 | 50.3033
|  |  | 44722.0887 | 50.3032
|  |  | 44722.0887 | 50.3032
|  |  | 44722.0887 | 50.3032
|  |  | 44722.0887 | 50.3033
|  |  | 44722.0887 | 50.3033
|  |  | 44722.0887 | 50.3033
|  |  | 44722.0887 | 50.3034
|  |  | 44722.0887 | 50.3034
|  |  | 44722.0887 | 50.3034
|  |  | 44722.0887 | 50.3034
|  |  | 44722.0887 | 50.3034
|  |  | 44722.0887 | 50.3034
|  |  | 44722.0887 | 50.3033
|  |  | 44722.0887 | 50.3033
|  |  | 44722.0887 | 50.3034
|  |  | 44722.0887 | 50.3034
|  |  | 44722.0887 | 50.3034
|  |  | 44722.0887 | 50.3034
|  |  | 44722.0887 | 50.3033
|  |  | 44722.0887 | 50.3034
|  |  | 44722.0887 | 50.3034
|  |  | 44722.0887 | 50.3034
|  |  | 44722.0887 | 50.3034
|  |  | 2022-06-10 02:08 | 50.3033
|  |  | 44722.0887 | 50.3033
|  |  | 44722.0887 | 50.3033
|  |  | 44722.0887 | 50.3032
|  |  | 44722.0887 | 50.3031
|  |  | 44722.0887 | 50.3031
|  |  | 44722.0887 | 50.303
|  |  | 44722.0887 | 50.3028
|  |  | 44722.0887 | 50.3028
|  |  | 44722.0887 | 50.3027
|  |  | 44722.0887 | 50.3026
|  |  | 44722.0887 | 50.3025
|  |  | 44722.0887 | 50.3024
|  |  | 44722.0887 | 50.3024
|  |  | 44722.0887 | 50.3024
|  |  | 44722.0887 | 50.3023
|  |  | 44722.0887 | 50.3022
|  |  | 44722.0887 | 50.3022
|  |  | 44722.0887 | 50.3023
|  |  | 44722.0887 | 50.3023
|  |  | 44722.0887 | 50.3023
|  |  | 44722.0887 | 50.3023
|  |  | 44722.0887 | 50.3023
|  |  | 44722.0887 | 50.3023
|  |  | 44722.0887 | 50.3023
|  |  | 44722.0887 | 50.3023
|  |  | 44722.0887 | 50.3023
|  |  | 44722.0887 | 50.3023
|  |  | 44722.0887 | 50.3022
|  |  | 44722.0887 | 50.3022
|  |  | 44722.0887 | 50.3021
|  |  | 44722.0887 | 50.302
|  |  | 44722.0887 | 50.3019
|  |  | 44722.0887 | 50.3018
|  |  | 44722.0887 | 50.3018
|  |  | 44722.0887 | 50.3017
|  |  | 44722.0887 | 50.3017
|  |  | 44722.0887 | 50.3017
|  |  | 44722.0887 | 50.3017
|  |  | 44722.0887 | 50.3017
|  |  | 44722.0887 | 50.3016
|  |  | 44722.0887 | 50.3016
|  |  | 44722.0887 | 50.3016
|  |  | 44722.0887 | 50.3015
|  |  | 44722.0887 | 50.3015
|  |  | 44722.0887 | 50.3014
|  |  | 44722.0887 | 50.3014
|  |  | 44722.0887 | 50.3013
|  |  | 44722.0887 | 50.3012
|  |  | 44722.0887 | 50.3012
|  |  | 2022-06-10 02:08 | 50.3011
|  |  | 44722.0887 | 50.301
|  |  | 44722.0887 | 50.3009
|  |  | 44722.0887 | 50.3008
|  |  | 44722.0887 | 50.3008
|  |  | 44722.0887 | 50.3007
|  |  | 44722.0887 | 50.3007
|  |  | 44722.0887 | 50.3006
|  |  | 44722.0887 | 50.3006
|  |  | 44722.0887 | 50.3006
|  |  | 44722.0887 | 50.3006
|  |  | 44722.0887 | 50.3007
|  |  | 44722.0887 | 50.3007
|  |  | 44722.0887 | 50.3007
|  |  | 44722.0887 | 50.3006
|  |  | 44722.0887 | 50.3005
|  |  | 44722.0887 | 50.3004
|  |  | 44722.0887 | 50.3003
|  |  | 44722.0887 | 50.3003
|  |  | 44722.0887 | 50.3003
|  |  | 44722.0887 | 50.3002
|  |  | 44722.0887 | 50.3002
|  |  | 44722.0887 | 50.3002
|  |  | 44722.0887 | 50.3002
|  |  | 44722.0887 | 50.3002
|  |  | 44722.0887 | 50.3001
|  |  | 44722.0887 | 50.3
|  |  | 44722.0887 | 50.2998
|  |  | 44722.0887 | 50.2997
|  |  | 44722.0887 | 50.2996
|  |  | 44722.0887 | 50.2994
|  |  | 44722.0887 | 50.2993
|  |  | 44722.0887 | 50.2992
|  |  | 44722.0887 | 50.2991
|  |  | 44722.0887 | 50.299
|  |  | 44722.0887 | 50.299
|  |  | 44722.0887 | 50.299
|  |  | 44722.0887 | 50.2989
|  |  | 44722.0887 | 50.2988
|  |  | 44722.0887 | 50.2988
|  |  | 44722.0887 | 50.2988
|  |  | 44722.0887 | 50.2988
|  |  | 44722.0887 | 50.2988
|  |  | 44722.0887 | 50.2987
|  |  | 44722.0887 | 50.2986
|  |  | 44722.0887 | 50.2986
|  |  | 44722.0887 | 50.2985
|  |  | 44722.0887 | 50.2985
|  |  | 44722.0887 | 50.2985
|  |  | 44722.0887 | 50.2985
|  |  | 2022-06-10 02:08 | 50.2984
|  |  | 44722.0887 | 50.2983
|  |  | 44722.0887 | 50.2982
|  |  | 44722.0887 | 50.2982
|  |  | 44722.0887 | 50.2981
|  |  | 44722.0887 | 50.2981
|  |  | 44722.0887 | 50.298
|  |  | 44722.0887 | 50.298
|  |  | 44722.0887 | 50.298
|  |  | 44722.0887 | 50.298
|  |  | 44722.0887 | 50.298
|  |  | 44722.0887 | 50.298
|  |  | 44722.0887 | 50.298
|  |  | 44722.0887 | 50.298
|  |  | 44722.0887 | 50.2979
|  |  | 44722.0887 | 50.2979
|  |  | 44722.0887 | 50.2979
|  |  | 44722.0887 | 50.2978
|  |  | 44722.0887 | 50.2978
|  |  | 44722.0887 | 50.2977
|  |  | 44722.0887 | 50.2977
|  |  | 44722.0887 | 50.2976
|  |  | 44722.0887 | 50.2975
|  |  | 44722.0887 | 50.2974
|  |  | 44722.0887 | 50.2974
|  |  | 44722.0887 | 50.2974
|  |  | 44722.0887 | 50.2974
|  |  | 44722.0887 | 50.2974
|  |  | 44722.0887 | 50.2973
|  |  | 44722.0887 | 50.2973
|  |  | 44722.0887 | 50.2972
|  |  | 44722.0887 | 50.2972
|  |  | 44722.0887 | 50.2971
|  |  | 44722.0887 | 50.297
|  |  | 44722.0887 | 50.2968
|  |  | 44722.0887 | 50.2967
|  |  | 44722.0887 | 50.2966
|  |  | 44722.0887 | 50.2964
|  |  | 44722.0887 | 50.2963
|  |  | 44722.0887 | 50.2963
|  |  | 44722.0887 | 50.2962
|  |  | 44722.0887 | 50.2963
|  |  | 44722.0887 | 50.2963
|  |  | 44722.0887 | 50.2964
|  |  | 44722.0887 | 50.2965
|  |  | 44722.0887 | 50.2966
|  |  | 44722.0887 | 50.2966
|  |  | 44722.0887 | 50.2965
|  |  | 44722.0887 | 50.2965
|  |  | 44722.0887 | 50.2964
|  |  | 2022-06-10 02:08 | 50.2963
|  |  | 44722.0888 | 50.2963
|  |  | 44722.0888 | 50.2962
|  |  | 44722.0888 | 50.2961
|  |  | 44722.0888 | 50.2961
|  |  | 44722.0888 | 50.296
|  |  | 44722.0888 | 50.2959
|  |  | 44722.0888 | 50.2959
|  |  | 44722.0888 | 50.2958
|  |  | 44722.0888 | 50.2956
|  |  | 44722.0888 | 50.2956
|  |  | 44722.0888 | 50.2955
|  |  | 44722.0888 | 50.2953
|  |  | 44722.0888 | 50.2952
|  |  | 44722.0888 | 50.2951
|  |  | 44722.0888 | 50.295
|  |  | 44722.0888 | 50.2949
|  |  | 44722.0888 | 50.2948
|  |  | 44722.0888 | 50.2948
|  |  | 44722.0888 | 50.2947
|  |  | 44722.0888 | 50.2946
|  |  | 44722.0888 | 50.2945
|  |  | 44722.0888 | 50.2944
|  |  | 44722.0888 | 50.2943
|  |  | 44722.0888 | 50.2942
|  |  | 44722.0888 | 50.2942
|  |  | 44722.0888 | 50.2941
|  |  | 44722.0888 | 50.294
|  |  | 44722.0888 | 50.2939
|  |  | 44722.0888 | 50.2938
|  |  | 44722.0888 | 50.2936
|  |  | 44722.0888 | 50.2935
|  |  | 44722.0888 | 50.2934
|  |  | 44722.0888 | 50.2933
|  |  | 44722.0888 | 50.2932
|  |  | 44722.0888 | 50.2931
|  |  | 44722.0888 | 50.293
|  |  | 44722.0888 | 50.293
|  |  | 44722.0888 | 50.2929
|  |  | 44722.0888 | 50.2928
|  |  | 44722.0888 | 50.2928
|  |  | 44722.0888 | 50.2927
|  |  | 44722.0888 | 50.2927
|  |  | 44722.0888 | 50.2926
|  |  | 44722.0888 | 50.2925
|  |  | 44722.0888 | 50.2924
|  |  | 44722.0888 | 50.2923
|  |  | 44722.0888 | 50.2923
|  |  | 44722.0888 | 50.2922
|  |  | 44722.0888 | 50.292
|  |  | 2022-06-10 02:08 | 50.2919
|  |  | 44722.0888 | 50.2917
|  |  | 44722.0888 | 50.2915
|  |  | 44722.0888 | 50.2914
|  |  | 44722.0888 | 50.2912
|  |  | 44722.0888 | 50.291
|  |  | 44722.0888 | 50.2909
|  |  | 44722.0888 | 50.2908
|  |  | 44722.0888 | 50.2906
|  |  | 44722.0888 | 50.2905
|  |  | 44722.0888 | 50.2905
|  |  | 44722.0888 | 50.2904
|  |  | 44722.0888 | 50.2903
|  |  | 44722.0888 | 50.2902
|  |  | 44722.0888 | 50.2901
|  |  | 44722.0888 | 50.2899
|  |  | 44722.0888 | 50.2896
|  |  | 44722.0888 | 50.2894
|  |  | 44722.0888 | 50.2891
|  |  | 44722.0888 | 50.2888
|  |  | 44722.0888 | 50.2885
|  |  | 44722.0888 | 50.2882
|  |  | 44722.0888 | 50.2878
|  |  | 44722.0888 | 50.2875
|  |  | 44722.0888 | 50.2872
|  |  | 44722.0888 | 50.2869
|  |  | 44722.0888 | 50.2866
|  |  | 44722.0888 | 50.2863
|  |  | 44722.0888 | 50.2861
|  |  | 44722.0888 | 50.2858
|  |  | 44722.0888 | 50.2855
|  |  | 44722.0888 | 50.2852
|  |  | 44722.0888 | 50.285
|  |  | 44722.0888 | 50.2848
|  |  | 44722.0888 | 50.2847
|  |  | 44722.0888 | 50.2846
|  |  | 44722.0888 | 50.2845
|  |  | 44722.0888 | 50.2844
|  |  | 44722.0888 | 50.2842
|  |  | 44722.0888 | 50.284
|  |  | 44722.0888 | 50.2838
|  |  | 44722.0888 | 50.2835
|  |  | 44722.0888 | 50.2832
|  |  | 44722.0888 | 50.2829
|  |  | 44722.0888 | 50.2828
|  |  | 44722.0888 | 50.2825
|  |  | 44722.0888 | 50.2821
|  |  | 44722.0888 | 50.2818
|  |  | 44722.0888 | 50.2815
|  |  | 44722.0888 | 50.2813
|  |  | 2022-06-10 02:08 | 50.2812
|  |  | 44722.0888 | 50.281
|  |  | 44722.0888 | 50.2809
|  |  | 44722.0888 | 50.2809
|  |  | 44722.0888 | 50.2807
|  |  | 44722.0888 | 50.2805
|  |  | 44722.0888 | 50.2802
|  |  | 44722.0888 | 50.2798
|  |  | 44722.0888 | 50.2795
|  |  | 44722.0888 | 50.2792
|  |  | 44722.0888 | 50.2788
|  |  | 44722.0888 | 50.2785
|  |  | 44722.0888 | 50.2782
|  |  | 44722.0888 | 50.278
|  |  | 44722.0888 | 50.2778
|  |  | 44722.0888 | 50.2777
|  |  | 44722.0888 | 50.2775
|  |  | 44722.0888 | 50.2773
|  |  | 44722.0888 | 50.2771
|  |  | 44722.0888 | 50.2769
|  |  | 44722.0888 | 50.2767
|  |  | 44722.0888 | 50.2764
|  |  | 44722.0888 | 50.2762
|  |  | 44722.0888 | 50.276
|  |  | 44722.0888 | 50.2757
|  |  | 44722.0888 | 50.2754
|  |  | 44722.0888 | 50.2751
|  |  | 44722.0888 | 50.2749
|  |  | 44722.0888 | 50.2747
|  |  | 44722.0888 | 50.2745
|  |  | 44722.0888 | 50.2744
|  |  | 44722.0888 | 50.2742
|  |  | 44722.0888 | 50.2741
|  |  | 44722.0888 | 50.2739
|  |  | 44722.0888 | 50.2738
|  |  | 44722.0888 | 50.2736
|  |  | 44722.0888 | 50.2735
|  |  | 44722.0888 | 50.2733
|  |  | 44722.0888 | 50.2732
|  |  | 44722.0888 | 50.2729
|  |  | 44722.0888 | 50.2727
|  |  | 44722.0888 | 50.2724
|  |  | 44722.0888 | 50.2721
|  |  | 44722.0888 | 50.2718
|  |  | 44722.0888 | 50.2716
|  |  | 44722.0888 | 50.2713
|  |  | 44722.0888 | 50.2711
|  |  | 44722.0888 | 50.271
|  |  | 44722.0888 | 50.2708
|  |  | 44722.0888 | 50.2707
|  |  | 2022-06-10 02:08 | 50.2705
|  |  | 44722.0888 | 50.2703
|  |  | 44722.0888 | 50.2701
|  |  | 44722.0888 | 50.2699
|  |  | 44722.0888 | 50.2698
|  |  | 44722.0888 | 50.2697
|  |  | 44722.0888 | 50.2695
|  |  | 44722.0888 | 50.2694
|  |  | 44722.0888 | 50.2691
|  |  | 44722.0888 | 50.2689
|  |  | 44722.0888 | 50.2687
|  |  | 44722.0888 | 50.2685
|  |  | 44722.0888 | 50.2683
|  |  | 44722.0888 | 50.2681
|  |  | 44722.0888 | 50.2679
|  |  | 44722.0888 | 50.2677
|  |  | 44722.0888 | 50.2676
|  |  | 44722.0888 | 50.2674
|  |  | 44722.0888 | 50.2673
|  |  | 44722.0888 | 50.2671
|  |  | 44722.0888 | 50.2669
|  |  | 44722.0888 | 50.2668
|  |  | 44722.0888 | 50.2666
|  |  | 44722.0888 | 50.2664
|  |  | 44722.0888 | 50.2662
|  |  | 44722.0888 | 50.266
|  |  | 44722.0888 | 50.2658
|  |  | 44722.0888 | 50.2656
|  |  | 44722.0888 | 50.2654
|  |  | 44722.0888 | 50.2652
|  |  | 44722.0888 | 50.265
|  |  | 44722.0888 | 50.2648
|  |  | 44722.0888 | 50.2647
|  |  | 44722.0888 | 50.2646
|  |  | 44722.0888 | 50.2644
|  |  | 44722.0888 | 50.2644
|  |  | 44722.0888 | 50.2642
|  |  | 44722.0888 | 50.2641
|  |  | 44722.0888 | 50.2639
|  |  | 44722.0888 | 50.2638
|  |  | 44722.0888 | 50.2635
|  |  | 44722.0888 | 50.2634
|  |  | 44722.0888 | 50.2633
|  |  | 44722.0888 | 50.2632
|  |  | 44722.0888 | 50.2632
|  |  | 44722.0888 | 50.2631
|  |  | 44722.0888 | 50.263
|  |  | 44722.0888 | 50.2629
|  |  | 44722.0888 | 50.2628
|  |  | 44722.0888 | 50.2627
|  |  | 2022-06-10 02:08 | 50.2626
|  |  | 44722.0888 | 50.2625
|  |  | 44722.0888 | 50.2624
|  |  | 44722.0888 | 50.2623
|  |  | 44722.0888 | 50.2621
|  |  | 44722.0888 | 50.262
|  |  | 44722.0888 | 50.2618
|  |  | 44722.0888 | 50.2616
|  |  | 44722.0888 | 50.2614
|  |  | 44722.0888 | 50.2612
|  |  | 44722.0888 | 50.2611
|  |  | 44722.0888 | 50.2609
|  |  | 44722.0888 | 50.2607
|  |  | 44722.0888 | 50.2606
|  |  | 44722.0888 | 50.2605
|  |  | 44722.0888 | 50.2604
|  |  | 44722.0888 | 50.2603
|  |  | 44722.0888 | 50.2603
|  |  | 44722.0888 | 50.2602
|  |  | 44722.0888 | 50.2601
|  |  | 44722.0888 | 50.26
|  |  | 44722.0888 | 50.2599
|  |  | 44722.0888 | 50.2598
|  |  | 44722.0888 | 50.2597
|  |  | 44722.0888 | 50.2596
|  |  | 44722.0888 | 50.2595
|  |  | 44722.0888 | 50.2594
|  |  | 44722.0888 | 50.2593
|  |  | 44722.0888 | 50.2592
|  |  | 44722.0888 | 50.2591
|  |  | 44722.0888 | 50.2591
|  |  | 44722.0888 | 50.259
|  |  | 44722.0888 | 50.2589
|  |  | 44722.0888 | 50.2589
|  |  | 44722.0888 | 50.2589
|  |  | 44722.0888 | 50.2587
|  |  | 44722.0888 | 50.2587
|  |  | 44722.0888 | 50.2587
|  |  | 44722.0888 | 50.2586
|  |  | 44722.0888 | 50.2585
|  |  | 44722.0888 | 50.2584
|  |  | 44722.0888 | 50.2583
|  |  | 44722.0888 | 50.2582
|  |  | 44722.0888 | 50.2581
|  |  | 44722.0888 | 50.2581
|  |  | 44722.0888 | 50.2582
|  |  | 44722.0888 | 50.2582
|  |  | 44722.0888 | 50.2582
|  |  | 44722.0888 | 50.2582
|  |  | 44722.0888 | 50.2582
|  |  | 2022-06-10 02:08 | 50.2581
|  |  | 44722.0888 | 50.258
|  |  | 44722.0888 | 50.2579
|  |  | 44722.0888 | 50.2579
|  |  | 44722.0888 | 50.2578
|  |  | 44722.0888 | 50.2577
|  |  | 44722.0888 | 50.2577
|  |  | 44722.0888 | 50.2577
|  |  | 44722.0888 | 50.2576
|  |  | 44722.0888 | 50.2576
|  |  | 44722.0888 | 50.2576
|  |  | 44722.0888 | 50.2576
|  |  | 44722.0888 | 50.2576
|  |  | 44722.0888 | 50.2575
|  |  | 44722.0888 | 50.2575
|  |  | 44722.0888 | 50.2575
|  |  | 44722.0888 | 50.2574
|  |  | 44722.0888 | 50.2573
|  |  | 44722.0888 | 50.2571
|  |  | 44722.0888 | 50.257
|  |  | 44722.0888 | 50.2569
|  |  | 44722.0888 | 50.2568
|  |  | 44722.0888 | 50.2567
|  |  | 44722.0888 | 50.2566
|  |  | 44722.0888 | 50.2565
|  |  | 44722.0888 | 50.2564
|  |  | 44722.0888 | 50.2563
|  |  | 44722.0888 | 50.2562
|  |  | 44722.0888 | 50.2561
|  |  | 44722.0888 | 50.256
|  |  | 44722.0888 | 50.2559
|  |  | 44722.0888 | 50.2559
|  |  | 44722.0888 | 50.2558
|  |  | 44722.0888 | 50.2558
|  |  | 44722.0888 | 50.2558
|  |  | 44722.0888 | 50.2557
|  |  | 44722.0888 | 50.2557
|  |  | 44722.0888 | 50.2557
|  |  | 44722.0888 | 50.2556
|  |  | 44722.0888 | 50.2556
|  |  | 44722.0888 | 50.2556
|  |  | 44722.0888 | 50.2555
|  |  | 44722.0888 | 50.2554
|  |  | 44722.0888 | 50.2554
|  |  | 44722.0888 | 50.2553
|  |  | 44722.0888 | 50.2552
|  |  | 44722.0888 | 50.2552
|  |  | 44722.0888 | 50.2551
|  |  | 44722.0888 | 50.2551
|  |  | 44722.0888 | 50.255
|  |  | 2022-06-10 02:08 | 50.255
|  |  | 44722.0888 | 50.255
|  |  | 44722.0888 | 50.2549
|  |  | 44722.0888 | 50.2548
|  |  | 44722.0888 | 50.2548
|  |  | 44722.0888 | 50.2547
|  |  | 44722.0888 | 50.2547
|  |  | 44722.0888 | 50.2546
|  |  | 44722.0888 | 50.2546
|  |  | 44722.0888 | 50.2545
|  |  | 44722.0888 | 50.2545
|  |  | 44722.0888 | 50.2544
|  |  | 44722.0888 | 50.2544
|  |  | 44722.0888 | 50.2545
|  |  | 44722.0888 | 50.2544
|  |  | 44722.0888 | 50.2544
|  |  | 44722.0888 | 50.2543
|  |  | 44722.0888 | 50.2542
|  |  | 44722.0888 | 50.2541
|  |  | 44722.0888 | 50.2541
|  |  | 44722.0888 | 50.2539
|  |  | 44722.0888 | 50.2538
|  |  | 44722.0888 | 50.2537
|  |  | 44722.0888 | 50.2536
|  |  | 44722.0888 | 50.2535
|  |  | 44722.0888 | 50.2535
|  |  | 44722.0888 | 50.2534
|  |  | 44722.0888 | 50.2534
|  |  | 44722.0888 | 50.2533
|  |  | 44722.0888 | 50.2533
|  |  | 44722.0888 | 50.2531
|  |  | 44722.0888 | 50.253
|  |  | 44722.0888 | 50.253
|  |  | 44722.0888 | 50.2529
|  |  | 44722.0888 | 50.2529
|  |  | 44722.0888 | 50.2528
|  |  | 44722.0888 | 50.2528
|  |  | 44722.0888 | 50.2528
|  |  | 44722.0888 | 50.2528
|  |  | 44722.0888 | 50.2526
|  |  | 44722.0888 | 50.2524
|  |  | 44722.0888 | 50.2522
|  |  | 44722.0888 | 50.252
|  |  | 44722.0888 | 50.2518
|  |  | 44722.0888 | 50.2517
|  |  | 44722.0888 | 50.2515
|  |  | 44722.0888 | 50.2515
|  |  | 44722.0888 | 50.2515
|  |  | 44722.0888 | 50.2515
|  |  | 44722.0888 | 50.2515
|  |  | 2022-06-10 02:08 | 50.2516
|  |  | 44722.0888 | 50.2516
|  |  | 44722.0888 | 50.2516
|  |  | 44722.0888 | 50.2516
|  |  | 44722.0888 | 50.2516
|  |  | 44722.0888 | 50.2516
|  |  | 44722.0888 | 50.2515
|  |  | 44722.0888 | 50.2514
|  |  | 44722.0888 | 50.2513
|  |  | 44722.0888 | 50.2512
|  |  | 44722.0888 | 50.2511
|  |  | 44722.0888 | 50.251
|  |  | 44722.0888 | 50.2509
|  |  | 44722.0888 | 50.2509
|  |  | 44722.0888 | 50.2509
|  |  | 44722.0888 | 50.2509
|  |  | 44722.0888 | 50.251
|  |  | 44722.0888 | 50.251
|  |  | 44722.0888 | 50.251
|  |  | 44722.0888 | 50.251
|  |  | 44722.0888 | 50.251
|  |  | 44722.0888 | 50.251
|  |  | 44722.0888 | 50.251
|  |  | 44722.0888 | 50.2509
|  |  | 44722.0888 | 50.2509
|  |  | 44722.0888 | 50.2509
|  |  | 44722.0888 | 50.2508
|  |  | 44722.0888 | 50.2509
|  |  | 44722.0888 | 50.2509
|  |  | 44722.0888 | 50.2509
|  |  | 44722.0888 | 50.2509
|  |  | 44722.0888 | 50.251
|  |  | 44722.0888 | 50.251
|  |  | 44722.0888 | 50.2511
|  |  | 44722.0888 | 50.2512
|  |  | 44722.0888 | 50.2512
|  |  | 44722.0888 | 50.2513
|  |  | 44722.0888 | 50.2513
|  |  | 44722.0888 | 50.2512
|  |  | 44722.0888 | 50.2512
|  |  | 44722.0888 | 50.2511
|  |  | 44722.0888 | 50.251
|  |  | 44722.0888 | 50.2509
|  |  | 44722.0888 | 50.2508
|  |  | 44722.0888 | 50.2507
|  |  | 44722.0888 | 50.2506
|  |  | 44722.0888 | 50.2506
|  |  | 44722.0888 | 50.2506
|  |  | 44722.0888 | 50.2506
|  |  | 44722.0888 | 50.2506
|  |  | 2022-06-10 02:08 | 50.2507
|  |  | 44722.0888 | 50.2507
|  |  | 44722.0888 | 50.2507
|  |  | 44722.0888 | 50.2507
|  |  | 44722.0888 | 50.2507
|  |  | 44722.0888 | 50.2507
|  |  | 44722.0888 | 50.2507
|  |  | 44722.0888 | 50.2507
|  |  | 44722.0888 | 50.2506
|  |  | 44722.0888 | 50.2506
|  |  | 44722.0888 | 50.2506
|  |  | 44722.0888 | 50.2506
|  |  | 44722.0888 | 50.2506
|  |  | 44722.0888 | 50.2506
|  |  | 44722.0888 | 50.2506
|  |  | 44722.0888 | 50.2506
|  |  | 44722.0888 | 50.2505
|  |  | 44722.0888 | 50.2505
|  |  | 44722.0888 | 50.2504
|  |  | 44722.0888 | 50.2504
|  |  | 44722.0888 | 50.2504
|  |  | 44722.0888 | 50.2504
|  |  | 44722.0888 | 50.2503
|  |  | 44722.0888 | 50.2503
|  |  | 44722.0888 | 50.2504
|  |  | 44722.0888 | 50.2505
|  |  | 44722.0888 | 50.2505
|  |  | 44722.0888 | 50.2506
|  |  | 44722.0888 | 50.2506
|  |  | 44722.0888 | 50.2506
|  |  | 44722.0888 | 50.2505
|  |  | 44722.0888 | 50.2504
|  |  | 44722.0889 | 50.2503
|  |  | 44722.0889 | 50.2502
|  |  | 44722.0889 | 50.2501
|  |  | 44722.0889 | 50.25
|  |  | 44722.0889 | 50.25
|  |  | 44722.0889 | 50.25
|  |  | 44722.0889 | 50.25
|  |  | 44722.0889 | 50.25
|  |  | 44722.0889 | 50.25
|  |  | 44722.0889 | 50.2501
|  |  | 44722.0889 | 50.2502
|  |  | 44722.0889 | 50.2502
|  |  | 44722.0889 | 50.2503
|  |  | 44722.0889 | 50.2503
|  |  | 44722.0889 | 50.2502
|  |  | 44722.0889 | 50.2502
|  |  | 44722.0889 | 50.2502
|  |  | 44722.0889 | 50.2502
|  |  | 2022-06-10 02:08 | 50.2502
|  |  | 44722.0889 | 50.2502
|  |  | 44722.0889 | 50.2502
|  |  | 44722.0889 | 50.2502
|  |  | 44722.0889 | 50.2502
|  |  | 44722.0889 | 50.2502
|  |  | 44722.0889 | 50.2503
|  |  | 44722.0889 | 50.2503
|  |  | 44722.0889 | 50.2503
|  |  | 44722.0889 | 50.2503
|  |  | 44722.0889 | 50.2503
|  |  | 44722.0889 | 50.2503
|  |  | 44722.0889 | 50.2503
|  |  | 44722.0889 | 50.2503
|  |  | 44722.0889 | 50.2503
|  |  | 44722.0889 | 50.2503
|  |  | 44722.0889 | 50.2503
|  |  | 44722.0889 | 50.2503
|  |  | 44722.0889 | 50.2504
|  |  | 44722.0889 | 50.2504
|  |  | 44722.0889 | 50.2504
|  |  | 44722.0889 | 50.2504
|  |  | 44722.0889 | 50.2504
|  |  | 44722.0889 | 50.2503
|  |  | 44722.0889 | 50.2502
|  |  | 44722.0889 | 50.2502
|  |  | 44722.0889 | 50.2502
|  |  | 44722.0889 | 50.2502
|  |  | 44722.0889 | 50.2502
|  |  | 44722.0889 | 50.2502
|  |  | 44722.0889 | 50.2503
|  |  | 44722.0889 | 50.2503
|  |  | 44722.0889 | 50.2504
|  |  | 44722.0889 | 50.2504
|  |  | 44722.0889 | 50.2504
|  |  | 44722.0889 | 50.2505
|  |  | 44722.0889 | 50.2505
|  |  | 44722.0889 | 50.2504
|  |  | 44722.0889 | 50.2504
|  |  | 44722.0889 | 50.2504
|  |  | 44722.0889 | 50.2503
|  |  | 44722.0889 | 50.2503
|  |  | 44722.0889 | 50.2503
|  |  | 44722.0889 | 50.2503
|  |  | 44722.0889 | 50.2502
|  |  | 44722.0889 | 50.2502
|  |  | 44722.0889 | 50.2502
|  |  | 44722.0889 | 50.2502
|  |  | 44722.0889 | 50.2502
|  |  | 44722.0889 | 50.2503
|  |  | 2022-06-10 02:08 | 50.2503
|  |  | 44722.0889 | 50.2504
|  |  | 44722.0889 | 50.2504
|  |  | 44722.0889 | 50.2504
|  |  | 44722.0889 | 50.2505
|  |  | 44722.0889 | 50.2504
|  |  | 44722.0889 | 50.2504
|  |  | 44722.0889 | 50.2503
|  |  | 44722.0889 | 50.2502
|  |  | 44722.0889 | 50.2502
|  |  | 44722.0889 | 50.2502
|  |  | 44722.0889 | 50.2503
|  |  | 44722.0889 | 50.2502
|  |  | 44722.0889 | 50.2502
|  |  | 44722.0889 | 50.2502
|  |  | 44722.0889 | 50.2502
|  |  | 44722.0889 | 50.2502
|  |  | 44722.0889 | 50.2502
|  |  | 44722.0889 | 50.2503
|  |  | 44722.0889 | 50.2504
|  |  | 44722.0889 | 50.2505
|  |  | 44722.0889 | 50.2505
|  |  | 44722.0889 | 50.2505
|  |  | 44722.0889 | 50.2505
|  |  | 44722.0889 | 50.2505
|  |  | 44722.0889 | 50.2505
|  |  | 44722.0889 | 50.2505
|  |  | 44722.0889 | 50.2504
|  |  | 44722.0889 | 50.2504
|  |  | 44722.0889 | 50.2504
|  |  | 44722.0889 | 50.2504
|  |  | 44722.0889 | 50.2503
|  |  | 44722.0889 | 50.2502
|  |  | 44722.0889 | 50.2502
|  |  | 44722.0889 | 50.2502
|  |  | 44722.0889 | 50.2501
|  |  | 44722.0889 | 50.2501
|  |  | 44722.0889 | 50.25
|  |  | 44722.0889 | 50.2501
|  |  | 44722.0889 | 50.2501
|  |  | 44722.0889 | 50.2501
|  |  | 44722.0889 | 50.2501
|  |  | 44722.0889 | 50.2502
|  |  | 44722.0889 | 50.2503
|  |  | 44722.0889 | 50.2504
|  |  | 44722.0889 | 50.2506
|  |  | 44722.0889 | 50.2507
|  |  | 44722.0889 | 50.2507
|  |  | 44722.0889 | 50.2507
|  |  | 44722.0889 | 50.2507
|  |  | 2022-06-10 02:08 | 50.2508
|  |  | 44722.0889 | 50.2507
|  |  | 44722.0889 | 50.2506
|  |  | 44722.0889 | 50.2506
|  |  | 44722.0889 | 50.2506
|  |  | 44722.0889 | 50.2506
|  |  | 44722.0889 | 50.2507
|  |  | 44722.0889 | 50.2507
|  |  | 44722.0889 | 50.2508
|  |  | 44722.0889 | 50.251
|  |  | 44722.0889 | 50.2511
|  |  | 44722.0889 | 50.2512
|  |  | 44722.0889 | 50.2514
|  |  | 44722.0889 | 50.2514
|  |  | 44722.0889 | 50.2515
|  |  | 44722.0889 | 50.2515
|  |  | 44722.0889 | 50.2515
|  |  | 44722.0889 | 50.2514
|  |  | 44722.0889 | 50.2514
|  |  | 44722.0889 | 50.2514
|  |  | 44722.0889 | 50.2513
|  |  | 44722.0889 | 50.2513
|  |  | 44722.0889 | 50.2513
|  |  | 44722.0889 | 50.2514
|  |  | 44722.0889 | 50.2514
|  |  | 44722.0889 | 50.2515
|  |  | 44722.0889 | 50.2515
|  |  | 44722.0889 | 50.2515
|  |  | 44722.0889 | 50.2516
|  |  | 44722.0889 | 50.2516
|  |  | 44722.0889 | 50.2517
|  |  | 44722.0889 | 50.2517
|  |  | 44722.0889 | 50.2518
|  |  | 44722.0889 | 50.2518
|  |  | 44722.0889 | 50.2519
|  |  | 44722.0889 | 50.2519
|  |  | 44722.0889 | 50.2519
|  |  | 44722.0889 | 50.2519
|  |  | 44722.0889 | 50.252
|  |  | 44722.0889 | 50.252
|  |  | 44722.0889 | 50.252
|  |  | 44722.0889 | 50.252
|  |  | 44722.0889 | 50.252
|  |  | 44722.0889 | 50.252
|  |  | 44722.0889 | 50.252
|  |  | 44722.0889 | 50.252
|  |  | 44722.0889 | 50.2521
|  |  | 44722.0889 | 50.2522
|  |  | 44722.0889 | 50.2522
|  |  | 44722.0889 | 50.2523
|  |  | 2022-06-10 02:08 | 50.2524

## 20220613-1
In GMT |  |  | High resolution Incident data
Date | Time | Freq | time | freq
2022-06-13 | 7:40 | 49.966 | 2022-06-13 08:40 | 49.9679
2022-06-13 | 7:40 | 49.963 | 44725.3613 | 49.9679
2022-06-13 | 7:40 | 49.963 | 44725.3613 | 49.968
2022-06-13 | 7:40 | 49.962 | 44725.3613 | 49.968
2022-06-13 | 7:40 | 49.962 | 44725.3613 | 49.9681
2022-06-13 | 7:40 | 49.963 | 44725.3613 | 49.9682
2022-06-13 | 7:40 | 49.962 | 44725.3613 | 49.9683
2022-06-13 | 7:40 | 49.961 | 44725.3613 | 49.9684
2022-06-13 | 7:40 | 49.959 | 44725.3613 | 49.9685
2022-06-13 | 7:40 | 49.96 | 44725.3613 | 49.9685
2022-06-13 | 7:40 | 49.96 | 44725.3613 | 49.9686
2022-06-13 | 7:40 | 49.96 | 44725.3613 | 49.9686
2022-06-13 | 7:40 | 49.96 | 44725.3613 | 49.9687
2022-06-13 | 7:40 | 49.961 | 44725.3613 | 49.9687
2022-06-13 | 7:40 | 49.964 | 44725.3613 | 49.9687
2022-06-13 | 7:40 | 49.966 | 44725.3613 | 49.9687
2022-06-13 | 7:40 | 49.969 | 44725.3613 | 49.9687
2022-06-13 | 7:40 | 49.971 | 44725.3613 | 49.9687
2022-06-13 | 7:40 | 49.974 | 44725.3613 | 49.9687
2022-06-13 | 7:40 | 49.973 | 44725.3613 | 49.9688
2022-06-13 | 7:40 | 49.975 | 44725.3613 | 49.9689
2022-06-13 | 7:40 | 49.974 | 44725.3613 | 49.969
2022-06-13 | 7:40 | 49.974 | 44725.3613 | 49.9691
2022-06-13 | 7:40 | 49.975 | 44725.3613 | 49.9692
2022-06-13 | 7:40 | 49.976 | 44725.3613 | 49.9692
2022-06-13 | 7:40 | 49.977 | 44725.3613 | 49.9693
2022-06-13 | 7:40 | 49.979 | 44725.3613 | 49.9693
2022-06-13 | 7:40 | 49.979 | 44725.3613 | 49.9692
2022-06-13 | 7:40 | 49.981 | 44725.3613 | 49.9692
2022-06-13 | 7:40 | 49.983 | 44725.3613 | 49.9692
2022-06-13 | 7:41 | 49.985 | 44725.3613 | 49.9692
2022-06-13 | 7:41 | 49.986 | 44725.3613 | 49.9692
2022-06-13 | 7:41 | 49.987 | 44725.3613 | 49.9692
2022-06-13 | 7:41 | 49.986 | 44725.3613 | 49.9692
2022-06-13 | 7:41 | 49.983 | 44725.3613 | 49.9694
2022-06-13 | 7:41 | 49.983 | 44725.3613 | 49.9694
2022-06-13 | 7:41 | 49.981 | 44725.3613 | 49.9695
2022-06-13 | 7:41 | 49.979 | 44725.3613 | 49.9695
2022-06-13 | 7:41 | 49.977 | 44725.3613 | 49.9696
2022-06-13 | 7:41 | 49.974 | 44725.3613 | 49.9697
2022-06-13 | 7:41 | 49.97 | 44725.3613 | 49.9698
2022-06-13 | 7:41 | 49.967 | 44725.3613 | 49.9698
2022-06-13 | 7:41 | 49.965 | 44725.3613 | 49.9698
2022-06-13 | 7:41 | 49.963 | 44725.3613 | 49.9698
2022-06-13 | 7:41 | 49.962 | 44725.3613 | 49.9699
2022-06-13 | 7:41 | 49.957 | 44725.3613 | 49.9699
2022-06-13 | 7:41 | 49.955 | 44725.3613 | 49.9699
2022-06-13 | 7:41 | 49.927 | 44725.3613 | 49.97
2022-06-13 | 7:41 | 49.9 | 44725.3613 | 49.97
2022-06-13 | 7:41 | 49.882 | 44725.3613 | 49.9701
2022-06-13 | 7:41 | 49.865 | 2022-06-13 08:40 | 49.9702
2022-06-13 | 7:41 | 49.853 | 44725.3613 | 49.9702
2022-06-13 | 7:41 | 49.843 | 44725.3613 | 49.9703
2022-06-13 | 7:41 | 49.841 | 44725.3613 | 49.9704
2022-06-13 | 7:41 | 49.839 | 44725.3613 | 49.9704
2022-06-13 | 7:41 | 49.84 | 44725.3613 | 49.9705
2022-06-13 | 7:41 | 49.841 | 44725.3613 | 49.9705
2022-06-13 | 7:41 | 49.844 | 44725.3613 | 49.9706
2022-06-13 | 7:41 | 49.845 | 44725.3613 | 49.9707
2022-06-13 | 7:41 | 49.849 | 44725.3613 | 49.9708
2022-06-13 | 7:41 | 49.854 | 44725.3613 | 49.9708
2022-06-13 | 7:41 | 49.857 | 44725.3613 | 49.9709
2022-06-13 | 7:41 | 49.858 | 44725.3613 | 49.9709
2022-06-13 | 7:41 | 49.86 | 44725.3613 | 49.9708
2022-06-13 | 7:41 | 49.86 | 44725.3613 | 49.9709
2022-06-13 | 7:41 | 49.858 | 44725.3613 | 49.971
2022-06-13 | 7:41 | 49.856 | 44725.3613 | 49.971
2022-06-13 | 7:41 | 49.853 | 44725.3613 | 49.971
2022-06-13 | 7:41 | 49.85 | 44725.3613 | 49.971
2022-06-13 | 7:41 | 49.848 | 44725.3613 | 49.9709
2022-06-13 | 7:41 | 49.845 | 44725.3613 | 49.9709
2022-06-13 | 7:41 | 49.845 | 44725.3613 | 49.971
2022-06-13 | 7:41 | 49.846 | 44725.3613 | 49.971
2022-06-13 | 7:41 | 49.847 | 44725.3613 | 49.971
2022-06-13 | 7:41 | 49.848 | 44725.3613 | 49.971
2022-06-13 | 7:41 | 49.849 | 44725.3613 | 49.971
2022-06-13 | 7:41 | 49.851 | 44725.3613 | 49.971
2022-06-13 | 7:41 | 49.857 | 44725.3613 | 49.971
2022-06-13 | 7:41 | 49.86 | 44725.3613 | 49.971
2022-06-13 | 7:41 | 49.862 | 44725.3613 | 49.9711
2022-06-13 | 7:41 | 49.864 | 44725.3613 | 49.9711
2022-06-13 | 7:41 | 49.863 | 44725.3613 | 49.9712
2022-06-13 | 7:41 | 49.86 | 44725.3613 | 49.9713
2022-06-13 | 7:41 | 49.858 | 44725.3613 | 49.9713
2022-06-13 | 7:41 | 49.854 | 44725.3613 | 49.9714
2022-06-13 | 7:41 | 49.852 | 44725.3613 | 49.9714
2022-06-13 | 7:41 | 49.853 | 44725.3613 | 49.9714
2022-06-13 | 7:41 | 49.858 | 44725.3613 | 49.9714
2022-06-13 | 7:41 | 49.861 | 44725.3613 | 49.9714
2022-06-13 | 7:41 | 49.867 | 44725.3613 | 49.9714
2022-06-13 | 7:41 | 49.869 | 44725.3613 | 49.9713
2022-06-13 | 7:42 | 49.869 | 44725.3613 | 49.9714
2022-06-13 | 7:42 | 49.875 | 44725.3613 | 49.9713
2022-06-13 | 7:42 | 49.877 | 44725.3613 | 49.9714
2022-06-13 | 7:42 | 49.877 | 44725.3613 | 49.9714
2022-06-13 | 7:42 | 49.877 | 44725.3613 | 49.9714
2022-06-13 | 7:42 | 49.874 | 44725.3613 | 49.9715
2022-06-13 | 7:42 | 49.872 | 44725.3613 | 49.9715
2022-06-13 | 7:42 | 49.87 | 44725.3613 | 49.9715
2022-06-13 | 7:42 | 49.865 | 44725.3613 | 49.9716
2022-06-13 | 7:42 | 49.862 | 2022-06-13 08:40 | 49.9716
2022-06-13 | 7:42 | 49.859 | 44725.3613 | 49.9716
2022-06-13 | 7:42 | 49.856 | 44725.3613 | 49.9716
2022-06-13 | 7:42 | 49.855 | 44725.3613 | 49.9716
2022-06-13 | 7:42 | 49.853 | 44725.3613 | 49.9716
2022-06-13 | 7:42 | 49.85 | 44725.3613 | 49.9717
2022-06-13 | 7:42 | 49.848 | 44725.3613 | 49.9717
2022-06-13 | 7:42 | 49.847 | 44725.3613 | 49.9717
2022-06-13 | 7:42 | 49.848 | 44725.3613 | 49.9717
2022-06-13 | 7:42 | 49.85 | 44725.3613 | 49.9718
2022-06-13 | 7:42 | 49.852 | 44725.3613 | 49.9718
2022-06-13 | 7:42 | 49.854 | 44725.3613 | 49.9718
2022-06-13 | 7:42 | 49.856 | 44725.3613 | 49.9718
2022-06-13 | 7:42 | 49.859 | 44725.3613 | 49.9718
2022-06-13 | 7:42 | 49.864 | 44725.3613 | 49.9718
2022-06-13 | 7:42 | 49.866 | 44725.3613 | 49.9718
2022-06-13 | 7:42 | 49.867 | 44725.3613 | 49.9718
2022-06-13 | 7:42 | 49.87 | 44725.3613 | 49.9718
2022-06-13 | 7:42 | 49.87 | 44725.3613 | 49.9718
2022-06-13 | 7:42 | 49.87 | 44725.3613 | 49.9718
2022-06-13 | 7:42 | 49.866 | 44725.3613 | 49.9718
2022-06-13 | 7:42 | 49.86 | 44725.3613 | 49.9719
2022-06-13 | 7:42 | 49.856 | 44725.3613 | 49.9719
2022-06-13 | 7:42 | 49.853 | 44725.3613 | 49.972
2022-06-13 | 7:42 | 49.849 | 44725.3613 | 49.972
2022-06-13 | 7:42 | 49.844 | 44725.3613 | 49.9721
2022-06-13 | 7:42 | 49.841 | 44725.3613 | 49.9721
2022-06-13 | 7:42 | 49.839 | 44725.3613 | 49.9721
2022-06-13 | 7:42 | 49.836 | 44725.3613 | 49.9722
2022-06-13 | 7:42 | 49.832 | 44725.3613 | 49.9721
2022-06-13 | 7:42 | 49.83 | 44725.3613 | 49.9721
2022-06-13 | 7:42 | 49.826 | 44725.3613 | 49.9721
2022-06-13 | 7:42 | 49.823 | 44725.3613 | 49.9721
2022-06-13 | 7:42 | 49.822 | 44725.3613 | 49.972
2022-06-13 | 7:42 | 49.821 | 44725.3613 | 49.972
2022-06-13 | 7:42 | 49.823 | 44725.3613 | 49.972
2022-06-13 | 7:42 | 49.823 | 44725.3613 | 49.9721
2022-06-13 | 7:42 | 49.823 | 44725.3613 | 49.9721
2022-06-13 | 7:42 | 49.828 | 44725.3613 | 49.9722
2022-06-13 | 7:42 | 49.829 | 44725.3613 | 49.9722
2022-06-13 | 7:42 | 49.832 | 44725.3613 | 49.9723
2022-06-13 | 7:42 | 49.83 | 44725.3613 | 49.9723
2022-06-13 | 7:42 | 49.829 | 44725.3613 | 49.9724
2022-06-13 | 7:42 | 49.826 | 44725.3613 | 49.9724
2022-06-13 | 7:42 | 49.822 | 44725.3613 | 49.9724
2022-06-13 | 7:42 | 49.82 | 44725.3613 | 49.9725
2022-06-13 | 7:42 | 49.819 | 44725.3613 | 49.9725
2022-06-13 | 7:42 | 49.819 | 44725.3613 | 49.9725
2022-06-13 | 7:42 | 49.819 | 44725.3613 | 49.9725
2022-06-13 | 7:42 | 49.817 | 44725.3613 | 49.9725
2022-06-13 | 7:43 | 49.812 | 2022-06-13 08:40 | 49.9724
2022-06-13 | 7:43 | 49.807 | 44725.3613 | 49.9724
2022-06-13 | 7:43 | 49.804 | 44725.3613 | 49.9724
2022-06-13 | 7:43 | 49.797 | 44725.3613 | 49.9724
2022-06-13 | 7:43 | 49.795 | 44725.3613 | 49.9724
2022-06-13 | 7:43 | 49.793 | 44725.3613 | 49.9724
2022-06-13 | 7:43 | 49.789 | 44725.3613 | 49.9725
2022-06-13 | 7:43 | 49.788 | 44725.3613 | 49.9726
2022-06-13 | 7:43 | 49.79 | 44725.3613 | 49.9727
2022-06-13 | 7:43 | 49.792 | 44725.3613 | 49.9728
2022-06-13 | 7:43 | 49.792 | 44725.3613 | 49.9728
2022-06-13 | 7:43 | 49.794 | 44725.3613 | 49.9727
2022-06-13 | 7:43 | 49.797 | 44725.3613 | 49.9727
2022-06-13 | 7:43 | 49.797 | 44725.3613 | 49.9727
2022-06-13 | 7:43 | 49.799 | 44725.3613 | 49.9727
2022-06-13 | 7:43 | 49.799 | 44725.3613 | 49.9727
2022-06-13 | 7:43 | 49.801 | 44725.3613 | 49.9727
2022-06-13 | 7:43 | 49.802 | 44725.3613 | 49.9727
2022-06-13 | 7:43 | 49.804 | 44725.3613 | 49.9728
2022-06-13 | 7:43 | 49.802 | 44725.3613 | 49.9728
2022-06-13 | 7:43 | 49.805 | 44725.3613 | 49.9728
2022-06-13 | 7:43 | 49.806 | 44725.3613 | 49.9728
2022-06-13 | 7:43 | 49.808 | 44725.3613 | 49.9728
2022-06-13 | 7:43 | 49.809 | 44725.3613 | 49.9729
2022-06-13 | 7:43 | 49.811 | 44725.3613 | 49.9729
2022-06-13 | 7:43 | 49.812 | 44725.3613 | 49.9729
2022-06-13 | 7:43 | 49.81 | 44725.3613 | 49.973
2022-06-13 | 7:43 | 49.805 | 44725.3613 | 49.973
2022-06-13 | 7:43 | 49.798 | 44725.3613 | 49.973
2022-06-13 | 7:43 | 49.795 | 44725.3613 | 49.973
2022-06-13 | 7:43 | 49.793 | 44725.3613 | 49.973
2022-06-13 | 7:43 | 49.793 | 44725.3613 | 49.9731
2022-06-13 | 7:43 | 49.794 | 44725.3613 | 49.9731
2022-06-13 | 7:43 | 49.797 | 44725.3613 | 49.9731
2022-06-13 | 7:43 | 49.795 | 44725.3613 | 49.9731
2022-06-13 | 7:43 | 49.792 | 44725.3613 | 49.9731
2022-06-13 | 7:43 | 49.794 | 44725.3613 | 49.9731
2022-06-13 | 7:43 | 49.791 | 44725.3613 | 49.9731
2022-06-13 | 7:43 | 49.792 | 44725.3613 | 49.9731
2022-06-13 | 7:43 | 49.792 | 44725.3613 | 49.9731
2022-06-13 | 7:43 | 49.79 | 44725.3613 | 49.9732
2022-06-13 | 7:43 | 49.791 | 44725.3613 | 49.9731
2022-06-13 | 7:43 | 49.793 | 44725.3613 | 49.9732
2022-06-13 | 7:43 | 49.794 | 44725.3613 | 49.9732
2022-06-13 | 7:43 | 49.799 | 44725.3613 | 49.9732
2022-06-13 | 7:43 | 49.805 | 44725.3613 | 49.9732
2022-06-13 | 7:43 | 49.812 | 44725.3613 | 49.9732
2022-06-13 | 7:43 | 49.82 | 44725.3613 | 49.9732
2022-06-13 | 7:43 | 49.826 | 44725.3613 | 49.9733
2022-06-13 | 7:43 | 49.827 | 44725.3613 | 49.9733
2022-06-13 | 7:43 | 49.829 | 2022-06-13 08:40 | 49.9734
2022-06-13 | 7:43 | 49.827 | 44725.3613 | 49.9735
2022-06-13 | 7:43 | 49.829 | 44725.3613 | 49.9735
2022-06-13 | 7:43 | 49.829 | 44725.3613 | 49.9736
2022-06-13 | 7:43 | 49.829 | 44725.3613 | 49.9736
2022-06-13 | 7:43 | 49.828 | 44725.3613 | 49.9736
2022-06-13 | 7:43 | 49.827 | 44725.3613 | 49.9737
2022-06-13 | 7:43 | 49.825 | 44725.3613 | 49.9737
2022-06-13 | 7:43 | 49.828 | 44725.3613 | 49.9737
2022-06-13 | 7:43 | 49.828 | 44725.3613 | 49.9737
2022-06-13 | 7:44 | 49.829 | 44725.3613 | 49.9738
2022-06-13 | 7:44 | 49.831 | 44725.3613 | 49.9738
2022-06-13 | 7:44 | 49.832 | 44725.3613 | 49.9738
2022-06-13 | 7:44 | 49.835 | 44725.3613 | 49.9738
2022-06-13 | 7:44 | 49.837 | 44725.3613 | 49.9739
2022-06-13 | 7:44 | 49.837 | 44725.3613 | 49.9739
2022-06-13 | 7:44 | 49.839 | 44725.3613 | 49.974
2022-06-13 | 7:44 | 49.837 | 44725.3613 | 49.9739
2022-06-13 | 7:44 | 49.838 | 44725.3613 | 49.9739
2022-06-13 | 7:44 | 49.838 | 44725.3613 | 49.9739
2022-06-13 | 7:44 | 49.839 | 44725.3613 | 49.9739
2022-06-13 | 7:44 | 49.838 | 44725.3613 | 49.9739
2022-06-13 | 7:44 | 49.838 | 44725.3613 | 49.9739
2022-06-13 | 7:44 | 49.837 | 44725.3613 | 49.974
2022-06-13 | 7:44 | 49.838 | 44725.3613 | 49.974
2022-06-13 | 7:44 | 49.836 | 44725.3613 | 49.974
2022-06-13 | 7:44 | 49.834 | 44725.3613 | 49.974
2022-06-13 | 7:44 | 49.831 | 44725.3613 | 49.974
2022-06-13 | 7:44 | 49.828 | 44725.3613 | 49.9741
2022-06-13 | 7:44 | 49.826 | 44725.3613 | 49.9742
2022-06-13 | 7:44 | 49.824 | 44725.3613 | 49.9742
2022-06-13 | 7:44 | 49.823 | 44725.3613 | 49.9743
2022-06-13 | 7:44 | 49.824 | 44725.3613 | 49.9744
2022-06-13 | 7:44 | 49.823 | 44725.3613 | 49.9744
2022-06-13 | 7:44 | 49.822 | 44725.3613 | 49.9744
2022-06-13 | 7:44 | 49.825 | 44725.3613 | 49.9745
2022-06-13 | 7:44 | 49.83 | 44725.3613 | 49.9744
2022-06-13 | 7:44 | 49.834 | 44725.3613 | 49.9745
2022-06-13 | 7:44 | 49.837 | 44725.3613 | 49.9745
2022-06-13 | 7:44 | 49.841 | 44725.3613 | 49.9744
2022-06-13 | 7:44 | 49.841 | 44725.3613 | 49.9744
2022-06-13 | 7:44 | 49.839 | 44725.3613 | 49.9744
2022-06-13 | 7:44 | 49.836 | 44725.3613 | 49.9744
2022-06-13 | 7:44 | 49.831 | 44725.3613 | 49.9744
2022-06-13 | 7:44 | 49.829 | 44725.3613 | 49.9744
2022-06-13 | 7:44 | 49.825 | 44725.3613 | 49.9745
2022-06-13 | 7:44 | 49.823 | 44725.3613 | 49.9745
2022-06-13 | 7:44 | 49.817 | 44725.3613 | 49.9746
2022-06-13 | 7:44 | 49.813 | 44725.3613 | 49.9747
2022-06-13 | 7:44 | 49.808 | 44725.3613 | 49.9748
2022-06-13 | 7:44 | 49.808 | 2022-06-13 08:40 | 49.9748
2022-06-13 | 7:44 | 49.804 | 44725.3613 | 49.9749
2022-06-13 | 7:44 | 49.804 | 44725.3613 | 49.9749
2022-06-13 | 7:44 | 49.802 | 44725.3613 | 49.9749
2022-06-13 | 7:44 | 49.802 | 44725.3613 | 49.9749
2022-06-13 | 7:44 | 49.801 | 44725.3613 | 49.9748
2022-06-13 | 7:44 | 49.798 | 44725.3613 | 49.9747
2022-06-13 | 7:44 | 49.797 | 44725.3613 | 49.9747
2022-06-13 | 7:44 | 49.793 | 44725.3613 | 49.9747
2022-06-13 | 7:44 | 49.793 | 44725.3613 | 49.9746
2022-06-13 | 7:44 | 49.791 | 44725.3613 | 49.9747
2022-06-13 | 7:44 | 49.793 | 44725.3613 | 49.9747
2022-06-13 | 7:44 | 49.795 | 44725.3613 | 49.9747
2022-06-13 | 7:44 | 49.801 | 44725.3613 | 49.9746
2022-06-13 | 7:44 | 49.805 | 44725.3613 | 49.9746
2022-06-13 | 7:44 | 49.812 | 44725.3613 | 49.9745
2022-06-13 | 7:44 | 49.815 | 44725.3613 | 49.9745
2022-06-13 | 7:44 | 49.821 | 44725.3613 | 49.9745
2022-06-13 | 7:44 | 49.826 | 44725.3613 | 49.9744
2022-06-13 | 7:44 | 49.835 | 44725.3613 | 49.9744
2022-06-13 | 7:44 | 49.839 | 44725.3613 | 49.9743
2022-06-13 | 7:45 | 49.843 | 44725.3613 | 49.9743
2022-06-13 | 7:45 | 49.842 | 44725.3613 | 49.9743
2022-06-13 | 7:45 | 49.84 | 44725.3613 | 49.9743
2022-06-13 | 7:45 | 49.834 | 44725.3613 | 49.9743
2022-06-13 | 7:45 | 49.829 | 44725.3613 | 49.9744
2022-06-13 | 7:45 | 49.829 | 44725.3613 | 49.9744
2022-06-13 | 7:45 | 49.829 | 44725.3613 | 49.9744
2022-06-13 | 7:45 | 49.834 | 44725.3613 | 49.9744
2022-06-13 | 7:45 | 49.839 | 44725.3613 | 49.9744
2022-06-13 | 7:45 | 49.839 | 44725.3613 | 49.9744
2022-06-13 | 7:45 | 49.843 | 44725.3613 | 49.9744
2022-06-13 | 7:45 | 49.844 | 44725.3613 | 49.9744
2022-06-13 | 7:45 | 49.846 | 44725.3614 | 49.9744
2022-06-13 | 7:45 | 49.848 | 44725.3614 | 49.9744
2022-06-13 | 7:45 | 49.846 | 44725.3614 | 49.9743
2022-06-13 | 7:45 | 49.846 | 44725.3614 | 49.9742
2022-06-13 | 7:45 | 49.846 | 44725.3614 | 49.9742
2022-06-13 | 7:45 | 49.848 | 44725.3614 | 49.9741
2022-06-13 | 7:45 | 49.846 | 44725.3614 | 49.9741
2022-06-13 | 7:45 | 49.844 | 44725.3614 | 49.9741
2022-06-13 | 7:45 | 49.845 | 44725.3614 | 49.9741
2022-06-13 | 7:45 | 49.845 | 44725.3614 | 49.9742
2022-06-13 | 7:45 | 49.846 | 44725.3614 | 49.9742
2022-06-13 | 7:45 | 49.845 | 44725.3614 | 49.9742
2022-06-13 | 7:45 | 49.847 | 44725.3614 | 49.9743
2022-06-13 | 7:45 | 49.844 | 44725.3614 | 49.9743
2022-06-13 | 7:45 | 49.838 | 44725.3614 | 49.9743
2022-06-13 | 7:45 | 49.831 | 44725.3614 | 49.9743
2022-06-13 | 7:45 | 49.824 | 44725.3614 | 49.9742
2022-06-13 | 7:45 | 49.819 | 2022-06-13 08:40 | 49.9742
2022-06-13 | 7:45 | 49.813 | 44725.3614 | 49.9742
2022-06-13 | 7:45 | 49.807 | 44725.3614 | 49.9742
2022-06-13 | 7:45 | 49.803 | 44725.3614 | 49.9742
2022-06-13 | 7:45 | 49.804 | 44725.3614 | 49.9742
2022-06-13 | 7:45 | 49.807 | 44725.3614 | 49.9742
2022-06-13 | 7:45 | 49.809 | 44725.3614 | 49.9741
2022-06-13 | 7:45 | 49.81 | 44725.3614 | 49.9742
2022-06-13 | 7:45 | 49.813 | 44725.3614 | 49.9742
2022-06-13 | 7:45 | 49.817 | 44725.3614 | 49.9742
2022-06-13 | 7:45 | 49.823 | 44725.3614 | 49.9742
2022-06-13 | 7:45 | 49.83 | 44725.3614 | 49.9742
2022-06-13 | 7:45 | 49.834 | 44725.3614 | 49.9742
2022-06-13 | 7:45 | 49.832 | 44725.3614 | 49.9742
2022-06-13 | 7:45 | 49.828 | 44725.3614 | 49.9742
2022-06-13 | 7:45 | 49.82 | 44725.3614 | 49.9741
2022-06-13 | 7:45 | 49.811 | 44725.3614 | 49.9742
2022-06-13 | 7:45 | 49.802 | 44725.3614 | 49.9741
2022-06-13 | 7:45 | 49.794 | 44725.3614 | 49.974
2022-06-13 | 7:45 | 49.786 | 44725.3614 | 49.974
2022-06-13 | 7:45 | 49.78 | 44725.3614 | 49.974
2022-06-13 | 7:45 | 49.777 | 44725.3614 | 49.974
2022-06-13 | 7:45 | 49.777 | 44725.3614 | 49.974
2022-06-13 | 7:45 | 49.776 | 44725.3614 | 49.9741
2022-06-13 | 7:45 | 49.775 | 44725.3614 | 49.9741
2022-06-13 | 7:45 | 49.775 | 44725.3614 | 49.9741
2022-06-13 | 7:45 | 49.774 | 44725.3614 | 49.9742
2022-06-13 | 7:45 | 49.776 | 44725.3614 | 49.9742
2022-06-13 | 7:45 | 49.775 | 44725.3614 | 49.9742
2022-06-13 | 7:45 | 49.777 | 44725.3614 | 49.9742
2022-06-13 | 7:46 | 49.776 | 44725.3614 | 49.9743
2022-06-13 | 7:46 | 49.775 | 44725.3614 | 49.9743
2022-06-13 | 7:46 | 49.774 | 44725.3614 | 49.9743
2022-06-13 | 7:46 | 49.776 | 44725.3614 | 49.9744
2022-06-13 | 7:46 | 49.778 | 44725.3614 | 49.9744
2022-06-13 | 7:46 | 49.781 | 44725.3614 | 49.9745
2022-06-13 | 7:46 | 49.781 | 44725.3614 | 49.9745
2022-06-13 | 7:46 | 49.781 | 44725.3614 | 49.9746
2022-06-13 | 7:46 | 49.784 | 44725.3614 | 49.9747
2022-06-13 | 7:46 | 49.786 | 44725.3614 | 49.9747
2022-06-13 | 7:46 | 49.789 | 44725.3614 | 49.9747
2022-06-13 | 7:46 | 49.791 | 44725.3614 | 49.9747
2022-06-13 | 7:46 | 49.795 | 44725.3614 | 49.9747
2022-06-13 | 7:46 | 49.795 | 44725.3614 | 49.9747
2022-06-13 | 7:46 | 49.797 | 44725.3614 | 49.9747
2022-06-13 | 7:46 | 49.796 | 44725.3614 | 49.9746
2022-06-13 | 7:46 | 49.797 | 44725.3614 | 49.9746
2022-06-13 | 7:46 | 49.798 | 44725.3614 | 49.9746
2022-06-13 | 7:46 | 49.798 | 44725.3614 | 49.9746
2022-06-13 | 7:46 | 49.803 | 44725.3614 | 49.9746
2022-06-13 | 7:46 | 49.805 | 2022-06-13 08:40 | 49.9746
2022-06-13 | 7:46 | 49.808 | 44725.3614 | 49.9747
2022-06-13 | 7:46 | 49.813 | 44725.3614 | 49.9747
2022-06-13 | 7:46 | 49.819 | 44725.3614 | 49.9747
2022-06-13 | 7:46 | 49.829 | 44725.3614 | 49.9747
2022-06-13 | 7:46 | 49.835 | 44725.3614 | 49.9747
2022-06-13 | 7:46 | 49.841 | 44725.3614 | 49.9747
2022-06-13 | 7:46 | 49.843 | 44725.3614 | 49.9747
2022-06-13 | 7:46 | 49.845 | 44725.3614 | 49.9747
2022-06-13 | 7:46 | 49.843 | 44725.3614 | 49.9746
2022-06-13 | 7:46 | 49.841 | 44725.3614 | 49.9746
2022-06-13 | 7:46 | 49.837 | 44725.3614 | 49.9745
2022-06-13 | 7:46 | 49.832 | 44725.3614 | 49.9745
2022-06-13 | 7:46 | 49.829 | 44725.3614 | 49.9745
2022-06-13 | 7:46 | 49.824 | 44725.3614 | 49.9744
2022-06-13 | 7:46 | 49.822 | 44725.3614 | 49.9745
2022-06-13 | 7:46 | 49.82 | 44725.3614 | 49.9746
2022-06-13 | 7:46 | 49.819 | 44725.3614 | 49.9746
2022-06-13 | 7:46 | 49.818 | 44725.3614 | 49.9747
2022-06-13 | 7:46 | 49.818 | 44725.3614 | 49.9749
2022-06-13 | 7:46 | 49.821 | 44725.3614 | 49.9749
2022-06-13 | 7:46 | 49.822 | 44725.3614 | 49.975
2022-06-13 | 7:46 | 49.821 | 44725.3614 | 49.975
2022-06-13 | 7:46 | 49.82 | 44725.3614 | 49.975
2022-06-13 | 7:46 | 49.821 | 44725.3614 | 49.975
2022-06-13 | 7:46 | 49.821 | 44725.3614 | 49.975
2022-06-13 | 7:46 | 49.826 | 44725.3614 | 49.9751
2022-06-13 | 7:46 | 49.828 | 44725.3614 | 49.9752
2022-06-13 | 7:46 | 49.832 | 44725.3614 | 49.9753
2022-06-13 | 7:46 | 49.836 | 44725.3614 | 49.9754
2022-06-13 | 7:46 | 49.842 | 44725.3614 | 49.9755
2022-06-13 | 7:46 | 49.846 | 44725.3614 | 49.9756
2022-06-13 | 7:46 | 49.85 | 44725.3614 | 49.9756
2022-06-13 | 7:46 | 49.853 | 44725.3614 | 49.9757
2022-06-13 | 7:46 | 49.857 | 44725.3614 | 49.9757
2022-06-13 | 7:46 | 49.861 | 44725.3614 | 49.9757
2022-06-13 | 7:46 | 49.869 | 44725.3614 | 49.9757
2022-06-13 | 7:46 | 49.875 | 44725.3614 | 49.9757
2022-06-13 | 7:46 | 49.879 | 44725.3614 | 49.9757
2022-06-13 | 7:46 | 49.882 | 44725.3614 | 49.9757
2022-06-13 | 7:46 | 49.883 | 44725.3614 | 49.9758
2022-06-13 | 7:47 | 49.885 | 44725.3614 | 49.9758
2022-06-13 | 7:47 | 49.889 | 44725.3614 | 49.9758
2022-06-13 | 7:47 | 49.889 | 44725.3614 | 49.9759
2022-06-13 | 7:47 | 49.89 | 44725.3614 | 49.9759
2022-06-13 | 7:47 | 49.889 | 44725.3614 | 49.9759
2022-06-13 | 7:47 | 49.89 | 44725.3614 | 49.9759
2022-06-13 | 7:47 | 49.89 | 44725.3614 | 49.9759
2022-06-13 | 7:47 | 49.89 | 44725.3614 | 49.9759
2022-06-13 | 7:47 | 49.892 | 44725.3614 | 49.9759
2022-06-13 | 7:47 | 49.895 | 2022-06-13 08:40 | 49.9759
2022-06-13 | 7:47 | 49.896 | 44725.3614 | 49.9758
2022-06-13 | 7:47 | 49.898 | 44725.3614 | 49.9758
2022-06-13 | 7:47 | 49.9 | 44725.3614 | 49.9759
2022-06-13 | 7:47 | 49.902 | 44725.3614 | 49.9759
2022-06-13 | 7:47 | 49.906 | 44725.3614 | 49.9759
2022-06-13 | 7:47 | 49.908 | 44725.3614 | 49.9759
2022-06-13 | 7:47 | 49.909 | 44725.3614 | 49.9758
2022-06-13 | 7:47 | 49.912 | 44725.3614 | 49.9758
2022-06-13 | 7:47 | 49.915 | 44725.3614 | 49.9757
2022-06-13 | 7:47 | 49.917 | 44725.3614 | 49.9757
2022-06-13 | 7:47 | 49.918 | 44725.3614 | 49.9756
2022-06-13 | 7:47 | 49.919 | 44725.3614 | 49.9755
2022-06-13 | 7:47 | 49.919 | 44725.3614 | 49.9755
2022-06-13 | 7:47 | 49.92 | 44725.3614 | 49.9756
2022-06-13 | 7:47 | 49.924 | 44725.3614 | 49.9756
2022-06-13 | 7:47 | 49.925 | 44725.3614 | 49.9756
2022-06-13 | 7:47 | 49.927 | 44725.3614 | 49.9756
2022-06-13 | 7:47 | 49.928 | 44725.3614 | 49.9757
2022-06-13 | 7:47 | 49.926 | 44725.3614 | 49.9758
2022-06-13 | 7:47 | 49.922 | 44725.3614 | 49.9758
2022-06-13 | 7:47 | 49.915 | 44725.3614 | 49.9759
2022-06-13 | 7:47 | 49.91 | 44725.3614 | 49.9759
2022-06-13 | 7:47 | 49.905 | 44725.3614 | 49.9759
2022-06-13 | 7:47 | 49.904 | 44725.3614 | 49.9759
2022-06-13 | 7:47 | 49.902 | 44725.3614 | 49.9759
2022-06-13 | 7:47 | 49.901 | 44725.3614 | 49.976
2022-06-13 | 7:47 | 49.901 | 44725.3614 | 49.976
2022-06-13 | 7:47 | 49.905 | 44725.3614 | 49.976
2022-06-13 | 7:47 | 49.907 | 44725.3614 | 49.9761
2022-06-13 | 7:47 | 49.91 | 44725.3614 | 49.9762
2022-06-13 | 7:47 | 49.913 | 44725.3614 | 49.9762
2022-06-13 | 7:47 | 49.914 | 44725.3614 | 49.9763
2022-06-13 | 7:47 | 49.914 | 44725.3614 | 49.9764
2022-06-13 | 7:47 | 49.914 | 44725.3614 | 49.9764
2022-06-13 | 7:47 | 49.916 | 44725.3614 | 49.9764
2022-06-13 | 7:47 | 49.917 | 44725.3614 | 49.9765
2022-06-13 | 7:47 | 49.92 | 44725.3614 | 49.9765
2022-06-13 | 7:47 | 49.921 | 44725.3614 | 49.9765
2022-06-13 | 7:47 | 49.918 | 44725.3614 | 49.9766
2022-06-13 | 7:47 | 49.915 | 44725.3614 | 49.9766
2022-06-13 | 7:47 | 49.912 | 44725.3614 | 49.9767
2022-06-13 | 7:47 | 49.911 | 44725.3614 | 49.9768
2022-06-13 | 7:47 | 49.91 | 44725.3614 | 49.9768
2022-06-13 | 7:47 | 49.908 | 44725.3614 | 49.9769
2022-06-13 | 7:47 | 49.907 | 44725.3614 | 49.9769
2022-06-13 | 7:47 | 49.91 | 44725.3614 | 49.977
2022-06-13 | 7:47 | 49.91 | 44725.3614 | 49.977
2022-06-13 | 7:47 | 49.908 | 44725.3614 | 49.9771
2022-06-13 | 7:47 | 49.907 | 44725.3614 | 49.9772
2022-06-13 | 7:48 | 49.908 | 2022-06-13 08:40 | 49.9772
2022-06-13 | 7:48 | 49.907 | 44725.3614 | 49.9773
2022-06-13 | 7:48 | 49.91 | 44725.3614 | 49.9772
2022-06-13 | 7:48 | 49.912 | 44725.3614 | 49.9773
2022-06-13 | 7:48 | 49.914 | 44725.3614 | 49.9773
2022-06-13 | 7:48 | 49.915 | 44725.3614 | 49.9773
2022-06-13 | 7:48 | 49.919 | 44725.3614 | 49.9773
2022-06-13 | 7:48 | 49.923 | 44725.3614 | 49.9774
2022-06-13 | 7:48 | 49.928 | 44725.3614 | 49.9774
2022-06-13 | 7:48 | 49.931 | 44725.3614 | 49.9775
2022-06-13 | 7:48 | 49.934 | 44725.3614 | 49.9776
2022-06-13 | 7:48 | 49.936 | 44725.3614 | 49.9776
2022-06-13 | 7:48 | 49.936 | 44725.3614 | 49.9776
2022-06-13 | 7:48 | 49.938 | 44725.3614 | 49.9776
2022-06-13 | 7:48 | 49.938 | 44725.3614 | 49.9776
2022-06-13 | 7:48 | 49.939 | 44725.3614 | 49.9776
2022-06-13 | 7:48 | 49.939 | 44725.3614 | 49.9776
2022-06-13 | 7:48 | 49.937 | 44725.3614 | 49.9776
2022-06-13 | 7:48 | 49.935 | 44725.3614 | 49.9777
2022-06-13 | 7:48 | 49.935 | 44725.3614 | 49.9777
2022-06-13 | 7:48 | 49.934 | 44725.3614 | 49.9777
2022-06-13 | 7:48 | 49.931 | 44725.3614 | 49.9777
2022-06-13 | 7:48 | 49.929 | 44725.3614 | 49.9777
2022-06-13 | 7:48 | 49.928 | 44725.3614 | 49.9777
2022-06-13 | 7:48 | 49.931 | 44725.3614 | 49.9777
2022-06-13 | 7:48 | 49.934 | 44725.3614 | 49.9777
2022-06-13 | 7:48 | 49.937 | 44725.3614 | 49.9777
2022-06-13 | 7:48 | 49.939 | 44725.3614 | 49.9777
2022-06-13 | 7:48 | 49.941 | 44725.3614 | 49.9777
2022-06-13 | 7:48 | 49.944 | 44725.3614 | 49.9777
2022-06-13 | 7:48 | 49.944 | 44725.3614 | 49.9777
2022-06-13 | 7:48 | 49.94 | 44725.3614 | 49.9777
2022-06-13 | 7:48 | 49.935 | 44725.3614 | 49.9777
2022-06-13 | 7:48 | 49.929 | 44725.3614 | 49.9777
2022-06-13 | 7:48 | 49.923 | 44725.3614 | 49.9777
2022-06-13 | 7:48 | 49.92 | 44725.3614 | 49.9777
2022-06-13 | 7:48 | 49.918 | 44725.3614 | 49.9778
2022-06-13 | 7:48 | 49.916 | 44725.3614 | 49.9777
2022-06-13 | 7:48 | 49.914 | 44725.3614 | 49.9778
2022-06-13 | 7:48 | 49.912 | 44725.3614 | 49.9778
2022-06-13 | 7:48 | 49.907 | 44725.3614 | 49.9778
2022-06-13 | 7:48 | 49.904 | 44725.3614 | 49.9779
2022-06-13 | 7:48 | 49.902 | 44725.3614 | 49.9779
2022-06-13 | 7:48 | 49.902 | 44725.3614 | 49.9779
2022-06-13 | 7:48 | 49.903 | 44725.3614 | 49.978
2022-06-13 | 7:48 | 49.904 | 44725.3614 | 49.978
2022-06-13 | 7:48 | 49.908 | 44725.3614 | 49.9781
2022-06-13 | 7:48 | 49.91 | 44725.3614 | 49.9781
2022-06-13 | 7:48 | 49.913 | 44725.3614 | 49.9782
2022-06-13 | 7:48 | 49.914 | 44725.3614 | 49.9783
2022-06-13 | 7:48 | 49.912 | 2022-06-13 08:40 | 49.9783
2022-06-13 | 7:48 | 49.912 | 44725.3614 | 49.9784
2022-06-13 | 7:48 | 49.912 | 44725.3614 | 49.9785
2022-06-13 | 7:48 | 49.913 | 44725.3614 | 49.9785
2022-06-13 | 7:48 | 49.915 | 44725.3614 | 49.9786
2022-06-13 | 7:48 | 49.917 | 44725.3614 | 49.9787
2022-06-13 | 7:48 | 49.918 | 44725.3614 | 49.9788
2022-06-13 | 7:48 | 49.916 | 44725.3614 | 49.9788
2022-06-13 | 7:48 | 49.92 | 44725.3614 | 49.9788
2022-06-13 | 7:48 | 49.922 | 44725.3614 | 49.9787
2022-06-13 | 7:48 | 49.925 | 44725.3614 | 49.9787
2022-06-13 | 7:49 | 49.927 | 44725.3614 | 49.9787
2022-06-13 | 7:49 | 49.926 | 44725.3614 | 49.9787
2022-06-13 | 7:49 | 49.923 | 44725.3614 | 49.9788
2022-06-13 | 7:49 | 49.917 | 44725.3614 | 49.9788
2022-06-13 | 7:49 | 49.912 | 44725.3614 | 49.9789
2022-06-13 | 7:49 | 49.905 | 44725.3614 | 49.9789
2022-06-13 | 7:49 | 49.902 | 44725.3614 | 49.9789
2022-06-13 | 7:49 | 49.898 | 44725.3614 | 49.979
2022-06-13 | 7:49 | 49.896 | 44725.3614 | 49.979
2022-06-13 | 7:49 | 49.9 | 44725.3614 | 49.979
2022-06-13 | 7:49 | 49.903 | 44725.3614 | 49.979
2022-06-13 | 7:49 | 49.906 | 44725.3614 | 49.979
2022-06-13 | 7:49 | 49.912 | 44725.3614 | 49.979
2022-06-13 | 7:49 | 49.918 | 44725.3614 | 49.979
2022-06-13 | 7:49 | 49.925 | 44725.3614 | 49.979
2022-06-13 | 7:49 | 49.929 | 44725.3614 | 49.979
2022-06-13 | 7:49 | 49.932 | 44725.3614 | 49.9791
2022-06-13 | 7:49 | 49.93 | 44725.3614 | 49.9791
2022-06-13 | 7:49 | 49.927 | 44725.3614 | 49.9792
2022-06-13 | 7:49 | 49.924 | 44725.3614 | 49.9792
2022-06-13 | 7:49 | 49.922 | 44725.3614 | 49.9792
2022-06-13 | 7:49 | 49.92 | 44725.3614 | 49.9793
2022-06-13 | 7:49 | 49.919 | 44725.3614 | 49.9794
2022-06-13 | 7:49 | 49.917 | 44725.3614 | 49.9795
2022-06-13 | 7:49 | 49.914 | 44725.3614 | 49.9796
2022-06-13 | 7:49 | 49.914 | 44725.3614 | 49.9796
2022-06-13 | 7:49 | 49.912 | 44725.3614 | 49.9796
2022-06-13 | 7:49 | 49.912 | 44725.3614 | 49.9796
2022-06-13 | 7:49 | 49.911 | 44725.3614 | 49.9796
2022-06-13 | 7:49 | 49.909 | 44725.3614 | 49.9796
2022-06-13 | 7:49 | 49.907 | 44725.3614 | 49.9795
2022-06-13 | 7:49 | 49.905 | 44725.3614 | 49.9795
2022-06-13 | 7:49 | 49.905 | 44725.3614 | 49.9795
2022-06-13 | 7:49 | 49.906 | 44725.3614 | 49.9795
2022-06-13 | 7:49 | 49.906 | 44725.3614 | 49.9795
2022-06-13 | 7:49 | 49.905 | 44725.3614 | 49.9795
2022-06-13 | 7:49 | 49.904 | 44725.3614 | 49.9796
2022-06-13 | 7:49 | 49.902 | 44725.3614 | 49.9796
2022-06-13 | 7:49 | 49.899 | 44725.3614 | 49.9796
2022-06-13 | 7:49 | 49.9 | 2022-06-13 08:40 | 49.9796
2022-06-13 | 7:49 | 49.902 | 44725.3614 | 49.9795
2022-06-13 | 7:49 | 49.904 | 44725.3614 | 49.9795
2022-06-13 | 7:49 | 49.905 | 44725.3614 | 49.9795
2022-06-13 | 7:49 | 49.906 | 44725.3614 | 49.9795
2022-06-13 | 7:49 | 49.907 | 44725.3614 | 49.9794
2022-06-13 | 7:49 | 49.907 | 44725.3614 | 49.9794
2022-06-13 | 7:49 | 49.907 | 44725.3614 | 49.9794
2022-06-13 | 7:49 | 49.906 | 44725.3614 | 49.9793
2022-06-13 | 7:49 | 49.904 | 44725.3614 | 49.9793
2022-06-13 | 7:49 | 49.903 | 44725.3614 | 49.9793
2022-06-13 | 7:49 | 49.903 | 44725.3614 | 49.9793
2022-06-13 | 7:49 | 49.904 | 44725.3614 | 49.9793
2022-06-13 | 7:49 | 49.905 | 44725.3614 | 49.9793
2022-06-13 | 7:49 | 49.906 | 44725.3614 | 49.9793
2022-06-13 | 7:49 | 49.909 | 44725.3614 | 49.9793
2022-06-13 | 7:49 | 49.912 | 44725.3614 | 49.9794
2022-06-13 | 7:49 | 49.913 | 44725.3614 | 49.9794
2022-06-13 | 7:49 | 49.913 | 44725.3614 | 49.9794
2022-06-13 | 7:49 | 49.914 | 44725.3614 | 49.9794
2022-06-13 | 7:50 | 49.914 | 44725.3614 | 49.9795
2022-06-13 | 7:50 | 49.914 | 44725.3614 | 49.9795
2022-06-13 | 7:50 | 49.917 | 44725.3614 | 49.9796
2022-06-13 | 7:50 | 49.92 | 44725.3614 | 49.9796
2022-06-13 | 7:50 | 49.922 | 44725.3614 | 49.9797
2022-06-13 | 7:50 | 49.921 | 44725.3614 | 49.9797
2022-06-13 | 7:50 | 49.92 | 44725.3614 | 49.9798
2022-06-13 | 7:50 | 49.92 | 44725.3614 | 49.9798
2022-06-13 | 7:50 | 49.919 | 44725.3614 | 49.9798
2022-06-13 | 7:50 | 49.92 | 44725.3614 | 49.9799
2022-06-13 | 7:50 | 49.922 | 44725.3614 | 49.9799
2022-06-13 | 7:50 | 49.923 | 44725.3614 | 49.9799
2022-06-13 | 7:50 | 49.924 | 44725.3614 | 49.98
2022-06-13 | 7:50 | 49.923 | 44725.3614 | 49.98
2022-06-13 | 7:50 | 49.923 | 44725.3614 | 49.98
2022-06-13 | 7:50 | 49.921 | 44725.3614 | 49.98
2022-06-13 | 7:50 | 49.921 | 44725.3614 | 49.9801
2022-06-13 | 7:50 | 49.924 | 44725.3614 | 49.9801
2022-06-13 | 7:50 | 49.927 | 44725.3614 | 49.9802
2022-06-13 | 7:50 | 49.928 | 44725.3614 | 49.9803
2022-06-13 | 7:50 | 49.93 | 44725.3614 | 49.9803
2022-06-13 | 7:50 | 49.931 | 44725.3614 | 49.9803
2022-06-13 | 7:50 | 49.932 | 44725.3614 | 49.9803
2022-06-13 | 7:50 | 49.934 | 44725.3614 | 49.9804
2022-06-13 | 7:50 | 49.936 | 44725.3614 | 49.9804
2022-06-13 | 7:50 | 49.937 | 44725.3614 | 49.9804
2022-06-13 | 7:50 | 49.937 | 44725.3614 | 49.9804
2022-06-13 | 7:50 | 49.94 | 44725.3614 | 49.9804
2022-06-13 | 7:50 | 49.94 | 44725.3614 | 49.9804
2022-06-13 | 7:50 | 49.939 | 44725.3614 | 49.9804
2022-06-13 | 7:50 | 49.938 | 2022-06-13 08:40 | 49.9804
2022-06-13 | 7:50 | 49.934 | 44725.3614 | 49.9804
2022-06-13 | 7:50 | 49.933 | 44725.3614 | 49.9803
2022-06-13 | 7:50 | 49.932 | 44725.3614 | 49.9803
2022-06-13 | 7:50 | 49.933 | 44725.3614 | 49.9803
2022-06-13 | 7:50 | 49.932 | 44725.3614 | 49.9802
2022-06-13 | 7:50 | 49.931 | 44725.3614 | 49.9803
2022-06-13 | 7:50 | 49.928 | 44725.3614 | 49.9803
2022-06-13 | 7:50 | 49.925 | 44725.3614 | 49.9803
2022-06-13 | 7:50 | 49.922 | 44725.3614 | 49.9803
2022-06-13 | 7:50 | 49.919 | 44725.3614 | 49.9803
2022-06-13 | 7:50 | 49.915 | 44725.3614 | 49.9803
2022-06-13 | 7:50 | 49.91 | 44725.3614 | 49.9803
2022-06-13 | 7:50 | 49.907 | 44725.3614 | 49.9804
2022-06-13 | 7:50 | 49.906 | 44725.3614 | 49.9804
2022-06-13 | 7:50 | 49.907 | 44725.3614 | 49.9804
2022-06-13 | 7:50 | 49.909 | 44725.3614 | 49.9804
2022-06-13 | 7:50 | 49.91 | 44725.3614 | 49.9805
2022-06-13 | 7:50 | 49.908 | 44725.3614 | 49.9806
2022-06-13 | 7:50 | 49.905 | 44725.3614 | 49.9806
2022-06-13 | 7:50 | 49.898 | 44725.3614 | 49.9807
2022-06-13 | 7:50 | 49.889 | 44725.3614 | 49.9807
2022-06-13 | 7:50 | 49.882 | 44725.3614 | 49.9808
2022-06-13 | 7:50 | 49.878 | 44725.3614 | 49.9808
2022-06-13 | 7:50 | 49.874 | 44725.3614 | 49.9808
2022-06-13 | 7:50 | 49.871 | 44725.3614 | 49.9809
2022-06-13 | 7:50 | 49.867 | 44725.3614 | 49.9809
2022-06-13 | 7:50 | 49.864 | 44725.3614 | 49.9809
2022-06-13 | 7:50 | 49.864 | 44725.3614 | 49.9809
2022-06-13 | 7:50 | 49.864 | 44725.3614 | 49.981
2022-06-13 | 7:50 | 49.864 | 44725.3614 | 49.981
2022-06-13 | 7:51 | 49.867 | 44725.3614 | 49.981
2022-06-13 | 7:51 | 49.869 | 44725.3614 | 49.981
2022-06-13 | 7:51 | 49.871 | 44725.3614 | 49.9811
2022-06-13 | 7:51 | 49.873 | 44725.3614 | 49.981
2022-06-13 | 7:51 | 49.877 | 44725.3614 | 49.9811
2022-06-13 | 7:51 | 49.878 | 44725.3614 | 49.9811
2022-06-13 | 7:51 | 49.879 | 44725.3614 | 49.9811
2022-06-13 | 7:51 | 49.88 | 44725.3614 | 49.9811
2022-06-13 | 7:51 | 49.881 | 44725.3614 | 49.9811
2022-06-13 | 7:51 | 49.882 | 44725.3614 | 49.9811
2022-06-13 | 7:51 | 49.882 | 44725.3614 | 49.9812
2022-06-13 | 7:51 | 49.882 | 44725.3614 | 49.9812
2022-06-13 | 7:51 | 49.881 | 44725.3614 | 49.9813
2022-06-13 | 7:51 | 49.882 | 44725.3614 | 49.9814
2022-06-13 | 7:51 | 49.883 | 44725.3614 | 49.9814
2022-06-13 | 7:51 | 49.883 | 44725.3614 | 49.9815
2022-06-13 | 7:51 | 49.885 | 44725.3614 | 49.9816
2022-06-13 | 7:51 | 49.887 | 44725.3614 | 49.9816
2022-06-13 | 7:51 | 49.889 | 44725.3614 | 49.9816
2022-06-13 | 7:51 | 49.892 | 2022-06-13 08:40 | 49.9816
2022-06-13 | 7:51 | 49.893 | 44725.3614 | 49.9816
2022-06-13 | 7:51 | 49.894 | 44725.3614 | 49.9817
2022-06-13 | 7:51 | 49.894 | 44725.3614 | 49.9816
2022-06-13 | 7:51 | 49.892 | 44725.3614 | 49.9816
2022-06-13 | 7:51 | 49.889 | 44725.3614 | 49.9816
2022-06-13 | 7:51 | 49.884 | 44725.3614 | 49.9816
2022-06-13 | 7:51 | 49.881 | 44725.3614 | 49.9816
2022-06-13 | 7:51 | 49.877 | 44725.3614 | 49.9816
2022-06-13 | 7:51 | 49.876 | 44725.3614 | 49.9817
2022-06-13 | 7:51 | 49.876 | 44725.3614 | 49.9817
2022-06-13 | 7:51 | 49.877 | 44725.3614 | 49.9818
2022-06-13 | 7:51 | 49.875 | 44725.3614 | 49.9819
2022-06-13 | 7:51 | 49.873 | 44725.3614 | 49.982
2022-06-13 | 7:51 | 49.87 | 44725.3614 | 49.9821
2022-06-13 | 7:51 | 49.867 | 44725.3614 | 49.9822
2022-06-13 | 7:51 | 49.865 | 44725.3614 | 49.9823
2022-06-13 | 7:51 | 49.863 | 44725.3614 | 49.9823
2022-06-13 | 7:51 | 49.863 | 44725.3614 | 49.9823
2022-06-13 | 7:51 | 49.864 | 44725.3614 | 49.9824
2022-06-13 | 7:51 | 49.864 | 44725.3614 | 49.9823
2022-06-13 | 7:51 | 49.867 | 44725.3614 | 49.9823
2022-06-13 | 7:51 | 49.865 | 44725.3614 | 49.9823
2022-06-13 | 7:51 | 49.866 | 44725.3614 | 49.9823
2022-06-13 | 7:51 | 49.866 | 44725.3614 | 49.9823
2022-06-13 | 7:51 | 49.867 | 44725.3614 | 49.9823
2022-06-13 | 7:51 | 49.868 | 44725.3614 | 49.9823
2022-06-13 | 7:51 | 49.869 | 44725.3614 | 49.9824
2022-06-13 | 7:51 | 49.871 | 44725.3614 | 49.9824
2022-06-13 | 7:51 | 49.871 | 44725.3614 | 49.9825
2022-06-13 | 7:51 | 49.872 | 44725.3614 | 49.9826
2022-06-13 | 7:51 | 49.87 | 44725.3614 | 49.9826
2022-06-13 | 7:51 | 49.87 | 44725.3614 | 49.9827
2022-06-13 | 7:51 | 49.869 | 44725.3614 | 49.9827
2022-06-13 | 7:51 | 49.872 | 44725.3614 | 49.9827
2022-06-13 | 7:51 | 49.875 | 44725.3614 | 49.9828
2022-06-13 | 7:51 | 49.877 | 44725.3614 | 49.9829
2022-06-13 | 7:51 | 49.884 | 44725.3614 | 49.983
2022-06-13 | 7:51 | 49.889 | 44725.3614 | 49.983
2022-06-13 | 7:51 | 49.895 | 44725.3614 | 49.9831
2022-06-13 | 7:52 | 49.903 | 44725.3614 | 49.9831
2022-06-13 | 7:52 | 49.909 | 44725.3614 | 49.9832
2022-06-13 | 7:52 | 49.916 | 44725.3614 | 49.9833
2022-06-13 | 7:52 | 49.923 | 44725.3614 | 49.9833
2022-06-13 | 7:52 | 49.929 | 44725.3614 | 49.9833
2022-06-13 | 7:52 | 49.934 | 44725.3614 | 49.9834
2022-06-13 | 7:52 | 49.938 | 44725.3614 | 49.9834
2022-06-13 | 7:52 | 49.938 | 44725.3614 | 49.9835
2022-06-13 | 7:52 | 49.939 | 44725.3614 | 49.9835
2022-06-13 | 7:52 | 49.94 | 44725.3614 | 49.9835
2022-06-13 | 7:52 | 49.942 | 2022-06-13 08:40 | 49.9835
2022-06-13 | 7:52 | 49.942 | 44725.3614 | 49.9835
2022-06-13 | 7:52 | 49.942 | 44725.3614 | 49.9834
2022-06-13 | 7:52 | 49.943 | 44725.3614 | 49.9834
2022-06-13 | 7:52 | 49.943 | 44725.3614 | 49.9834
2022-06-13 | 7:52 | 49.944 | 44725.3614 | 49.9834
2022-06-13 | 7:52 | 49.944 | 44725.3614 | 49.9834
2022-06-13 | 7:52 | 49.947 | 44725.3614 | 49.9834
2022-06-13 | 7:52 | 49.951 | 44725.3614 | 49.9834
2022-06-13 | 7:52 | 49.955 | 44725.3614 | 49.9834
2022-06-13 | 7:52 | 49.961 | 44725.3614 | 49.9834
2022-06-13 | 7:52 | 49.962 | 44725.3614 | 49.9834
2022-06-13 | 7:52 | 49.964 | 44725.3614 | 49.9835
2022-06-13 | 7:52 | 49.966 | 44725.3614 | 49.9835
2022-06-13 | 7:52 | 49.966 | 44725.3614 | 49.9835
2022-06-13 | 7:52 | 49.965 | 44725.3615 | 49.9835
2022-06-13 | 7:52 | 49.964 | 44725.3615 | 49.9836
2022-06-13 | 7:52 | 49.964 | 44725.3615 | 49.9836
2022-06-13 | 7:52 | 49.965 | 44725.3615 | 49.9836
2022-06-13 | 7:52 | 49.962 | 44725.3615 | 49.9835
2022-06-13 | 7:52 | 49.96 | 44725.3615 | 49.9835
2022-06-13 | 7:52 | 49.956 | 44725.3615 | 49.9836
2022-06-13 | 7:52 | 49.953 | 44725.3615 | 49.9836
2022-06-13 | 7:52 | 49.952 | 44725.3615 | 49.9836
2022-06-13 | 7:52 | 49.948 | 44725.3615 | 49.9836
2022-06-13 | 7:52 | 49.944 | 44725.3615 | 49.9837
2022-06-13 | 7:52 | 49.939 | 44725.3615 | 49.9837
2022-06-13 | 7:52 | 49.936 | 44725.3615 | 49.9837
2022-06-13 | 7:52 | 49.936 | 44725.3615 | 49.9838
2022-06-13 | 7:52 | 49.937 | 44725.3615 | 49.9839
2022-06-13 | 7:52 | 49.938 | 44725.3615 | 49.9839
2022-06-13 | 7:52 | 49.939 | 44725.3615 | 49.984
2022-06-13 | 7:52 | 49.939 | 44725.3615 | 49.984
2022-06-13 | 7:52 | 49.942 | 44725.3615 | 49.984
2022-06-13 | 7:52 | 49.941 | 44725.3615 | 49.984
2022-06-13 | 7:52 | 49.944 | 44725.3615 | 49.984
2022-06-13 | 7:52 | 49.948 | 44725.3615 | 49.984
2022-06-13 | 7:52 | 49.952 | 44725.3615 | 49.9841
2022-06-13 | 7:52 | 49.955 | 44725.3615 | 49.9842
2022-06-13 | 7:52 | 49.958 | 44725.3615 | 49.9842
2022-06-13 | 7:52 | 49.959 | 44725.3615 | 49.9843
2022-06-13 | 7:52 | 49.956 | 44725.3615 | 49.9843
2022-06-13 | 7:52 | 49.954 | 44725.3615 | 49.9844
2022-06-13 | 7:52 | 49.952 | 44725.3615 | 49.9844
2022-06-13 | 7:52 | 49.952 | 44725.3615 | 49.9844
2022-06-13 | 7:52 | 49.949 | 44725.3615 | 49.9845
2022-06-13 | 7:52 | 49.948 | 44725.3615 | 49.9845
2022-06-13 | 7:52 | 49.95 | 44725.3615 | 49.9845
2022-06-13 | 7:52 | 49.951 | 44725.3615 | 49.9845
2022-06-13 | 7:52 | 49.951 | 44725.3615 | 49.9846
2022-06-13 | 7:52 | 49.95 | 2022-06-13 08:40 | 49.9847
2022-06-13 | 7:53 | 49.95 | 44725.3615 | 49.9848
2022-06-13 | 7:53 | 49.951 | 44725.3615 | 49.9849
2022-06-13 | 7:53 | 49.953 | 44725.3615 | 49.9851
2022-06-13 | 7:53 | 49.952 | 44725.3615 | 49.9852
2022-06-13 | 7:53 | 49.952 | 44725.3615 | 49.9853
2022-06-13 | 7:53 | 49.947 | 44725.3615 | 49.9854
2022-06-13 | 7:53 | 49.944 | 44725.3615 | 49.9855
2022-06-13 | 7:53 | 49.942 | 44725.3615 | 49.9855
2022-06-13 | 7:53 | 49.942 | 44725.3615 | 49.9856
2022-06-13 | 7:53 | 49.94 | 44725.3615 | 49.9856
2022-06-13 | 7:53 | 49.939 | 44725.3615 | 49.9856
2022-06-13 | 7:53 | 49.939 | 44725.3615 | 49.9856
2022-06-13 | 7:53 | 49.94 | 44725.3615 | 49.9856
2022-06-13 | 7:53 | 49.943 | 44725.3615 | 49.9856
2022-06-13 | 7:53 | 49.945 | 44725.3615 | 49.9856
2022-06-13 | 7:53 | 49.946 | 44725.3615 | 49.9856
2022-06-13 | 7:53 | 49.945 | 44725.3615 | 49.9857
2022-06-13 | 7:53 | 49.945 | 44725.3615 | 49.9857
2022-06-13 | 7:53 | 49.944 | 44725.3615 | 49.9857
2022-06-13 | 7:53 | 49.943 | 44725.3615 | 49.9858
2022-06-13 | 7:53 | 49.94 | 44725.3615 | 49.9858
2022-06-13 | 7:53 | 49.938 | 44725.3615 | 49.9859
2022-06-13 | 7:53 | 49.936 | 44725.3615 | 49.986
2022-06-13 | 7:53 | 49.936 | 44725.3615 | 49.9861
2022-06-13 | 7:53 | 49.935 | 44725.3615 | 49.9862
2022-06-13 | 7:53 | 49.933 | 44725.3615 | 49.9863
2022-06-13 | 7:53 | 49.933 | 44725.3615 | 49.9864
2022-06-13 | 7:53 | 49.934 | 44725.3615 | 49.9864
2022-06-13 | 7:53 | 49.935 | 44725.3615 | 49.9865
2022-06-13 | 7:53 | 49.935 | 44725.3615 | 49.9866
2022-06-13 | 7:53 | 49.936 | 44725.3615 | 49.9866
2022-06-13 | 7:53 | 49.935 | 44725.3615 | 49.9866
2022-06-13 | 7:53 | 49.935 | 44725.3615 | 49.9866
2022-06-13 | 7:53 | 49.936 | 44725.3615 | 49.9865
2022-06-13 | 7:53 | 49.937 | 44725.3615 | 49.9865
2022-06-13 | 7:53 | 49.937 | 44725.3615 | 49.9865
2022-06-13 | 7:53 | 49.938 | 44725.3615 | 49.9865
2022-06-13 | 7:53 | 49.939 | 44725.3615 | 49.9865
2022-06-13 | 7:53 | 49.94 | 44725.3615 | 49.9865
2022-06-13 | 7:53 | 49.939 | 44725.3615 | 49.9865
2022-06-13 | 7:53 | 49.942 | 44725.3615 | 49.9865
2022-06-13 | 7:53 | 49.945 | 44725.3615 | 49.9866
2022-06-13 | 7:53 | 49.945 | 44725.3615 | 49.9866
2022-06-13 | 7:53 | 49.947 | 44725.3615 | 49.9867
2022-06-13 | 7:53 | 49.948 | 44725.3615 | 49.9867
2022-06-13 | 7:53 | 49.952 | 44725.3615 | 49.9868
2022-06-13 | 7:53 | 49.952 | 44725.3615 | 49.9869
2022-06-13 | 7:53 | 49.951 | 44725.3615 | 49.9869
2022-06-13 | 7:53 | 49.95 | 44725.3615 | 49.9869
2022-06-13 | 7:53 | 49.946 | 2022-06-13 08:41 | 49.9869
2022-06-13 | 7:53 | 49.942 | 44725.3615 | 49.9869
2022-06-13 | 7:53 | 49.936 | 44725.3615 | 49.9869
2022-06-13 | 7:53 | 49.934 | 44725.3615 | 49.9868
2022-06-13 | 7:53 | 49.934 | 44725.3615 | 49.9868
2022-06-13 | 7:53 | 49.934 | 44725.3615 | 49.9867
2022-06-13 | 7:53 | 49.933 | 44725.3615 | 49.9866
2022-06-13 | 7:53 | 49.93 | 44725.3615 | 49.9865
2022-06-13 | 7:53 | 49.929 | 44725.3615 | 49.9864
2022-06-13 | 7:53 | 49.925 | 44725.3615 | 49.9864
2022-06-13 | 7:53 | 49.926 | 44725.3615 | 49.9864
2022-06-13 | 7:54 | 49.926 | 44725.3615 | 49.9864
2022-06-13 | 7:54 | 49.925 | 44725.3615 | 49.9865
2022-06-13 | 7:54 | 49.92 | 44725.3615 | 49.9865
2022-06-13 | 7:54 | 49.919 | 44725.3615 | 49.9865
2022-06-13 | 7:54 | 49.921 | 44725.3615 | 49.9866
2022-06-13 | 7:54 | 49.92 | 44725.3615 | 49.9866
2022-06-13 | 7:54 | 49.92 | 44725.3615 | 49.9866
2022-06-13 | 7:54 | 49.92 | 44725.3615 | 49.9866
2022-06-13 | 7:54 | 49.922 | 44725.3615 | 49.9867
2022-06-13 | 7:54 | 49.924 | 44725.3615 | 49.9866
2022-06-13 | 7:54 | 49.926 | 44725.3615 | 49.9867
2022-06-13 | 7:54 | 49.927 | 44725.3615 | 49.9867
2022-06-13 | 7:54 | 49.929 | 44725.3615 | 49.9868
2022-06-13 | 7:54 | 49.931 | 44725.3615 | 49.9868
2022-06-13 | 7:54 | 49.933 | 44725.3615 | 49.9869
2022-06-13 | 7:54 | 49.931 | 44725.3615 | 49.987
2022-06-13 | 7:54 | 49.931 | 44725.3615 | 49.987
2022-06-13 | 7:54 | 49.93 | 44725.3615 | 49.9871
2022-06-13 | 7:54 | 49.93 | 44725.3615 | 49.9872
2022-06-13 | 7:54 | 49.924 | 44725.3615 | 49.9872
2022-06-13 | 7:54 | 49.921 | 44725.3615 | 49.9872
2022-06-13 | 7:54 | 49.919 | 44725.3615 | 49.9872
2022-06-13 | 7:54 | 49.916 | 44725.3615 | 49.9872
2022-06-13 | 7:54 | 49.912 | 44725.3615 | 49.9871
2022-06-13 | 7:54 | 49.913 | 44725.3615 | 49.9871
2022-06-13 | 7:54 | 49.913 | 44725.3615 | 49.987
2022-06-13 | 7:54 | 49.915 | 44725.3615 | 49.987
2022-06-13 | 7:54 | 49.914 | 44725.3615 | 49.987
2022-06-13 | 7:54 | 49.912 | 44725.3615 | 49.9871
2022-06-13 | 7:54 | 49.913 | 44725.3615 | 49.9871
2022-06-13 | 7:54 | 49.911 | 44725.3615 | 49.9872
2022-06-13 | 7:54 | 49.911 | 44725.3615 | 49.9872
2022-06-13 | 7:54 | 49.911 | 44725.3615 | 49.9872
2022-06-13 | 7:54 | 49.912 | 44725.3615 | 49.9872
2022-06-13 | 7:54 | 49.911 | 44725.3615 | 49.9872
2022-06-13 | 7:54 | 49.911 | 44725.3615 | 49.9871
2022-06-13 | 7:54 | 49.912 | 44725.3615 | 49.9871
2022-06-13 | 7:54 | 49.916 | 44725.3615 | 49.987
2022-06-13 | 7:54 | 49.917 | 44725.3615 | 49.987
2022-06-13 | 7:54 | 49.914 | 2022-06-13 08:41 | 49.9869
2022-06-13 | 7:54 | 49.91 | 44725.3615 | 49.9868
2022-06-13 | 7:54 | 49.905 | 44725.3615 | 49.9868
2022-06-13 | 7:54 | 49.899 | 44725.3615 | 49.9867
2022-06-13 | 7:54 | 49.892 | 44725.3615 | 49.9867
2022-06-13 | 7:54 | 49.888 | 44725.3615 | 49.9867
2022-06-13 | 7:54 | 49.885 | 44725.3615 | 49.9867
2022-06-13 | 7:54 | 49.881 | 44725.3615 | 49.9868
2022-06-13 | 7:54 | 49.867 | 44725.3615 | 49.9867
2022-06-13 | 7:54 | 49.879 | 44725.3615 | 49.9868
2022-06-13 | 7:54 | 49.881 | 44725.3615 | 49.9868
2022-06-13 | 7:54 | 49.884 | 44725.3615 | 49.9868
2022-06-13 | 7:54 | 49.889 | 44725.3615 | 49.9868
2022-06-13 | 7:54 | 49.896 | 44725.3615 | 49.9868
2022-06-13 | 7:54 | 49.9 | 44725.3615 | 49.9869
2022-06-13 | 7:54 | 49.905 | 44725.3615 | 49.9869
2022-06-13 | 7:54 | 49.906 | 44725.3615 | 49.9869
2022-06-13 | 7:54 | 49.906 | 44725.3615 | 49.9869
2022-06-13 | 7:54 | 49.903 | 44725.3615 | 49.9868
2022-06-13 | 7:54 | 49.899 | 44725.3615 | 49.9868
2022-06-13 | 7:55 | 49.894 | 44725.3615 | 49.9868
2022-06-13 | 7:55 | 49.888 | 44725.3615 | 49.9868
2022-06-13 | 7:55 | 49.884 | 44725.3615 | 49.9867
2022-06-13 | 7:55 | 49.877 | 44725.3615 | 49.9868
2022-06-13 | 7:55 | 49.874 | 44725.3615 | 49.9868
2022-06-13 | 7:55 | 49.872 | 44725.3615 | 49.9868
2022-06-13 | 7:55 | 49.871 | 44725.3615 | 49.9869
2022-06-13 | 7:55 | 49.872 | 44725.3615 | 49.9869
2022-06-13 | 7:55 | 49.878 | 44725.3615 | 49.9869
2022-06-13 | 7:55 | 49.879 | 44725.3615 | 49.9869
2022-06-13 | 7:55 | 49.88 | 44725.3615 | 49.987
2022-06-13 | 7:55 | 49.88 | 44725.3615 | 49.987
2022-06-13 | 7:55 | 49.882 | 44725.3615 | 49.987
2022-06-13 | 7:55 | 49.882 | 44725.3615 | 49.9869
2022-06-13 | 7:55 | 49.885 | 44725.3615 | 49.9868
2022-06-13 | 7:55 | 49.888 | 44725.3615 | 49.9867
2022-06-13 | 7:55 | 49.889 | 44725.3615 | 49.9867
2022-06-13 | 7:55 | 49.891 | 44725.3615 | 49.9866
2022-06-13 | 7:55 | 49.89 | 44725.3615 | 49.9866
2022-06-13 | 7:55 | 49.891 | 44725.3615 | 49.9866
2022-06-13 | 7:55 | 49.89 | 44725.3615 | 49.9865
2022-06-13 | 7:55 | 49.89 | 44725.3615 | 49.9865
2022-06-13 | 7:55 | 49.891 | 44725.3615 | 49.9865
2022-06-13 | 7:55 | 49.893 | 44725.3615 | 49.9864
2022-06-13 | 7:55 | 49.896 | 44725.3615 | 49.9864
2022-06-13 | 7:55 | 49.895 | 44725.3615 | 49.9863
2022-06-13 | 7:55 | 49.895 | 44725.3615 | 49.9862
2022-06-13 | 7:55 | 49.896 | 44725.3615 | 49.9862
2022-06-13 | 7:55 | 49.894 | 44725.3615 | 49.9862
2022-06-13 | 7:55 | 49.893 | 44725.3615 | 49.9861
2022-06-13 | 7:55 | 49.89 | 2022-06-13 08:41 | 49.986
2022-06-13 | 7:55 | 49.89 | 44725.3615 | 49.9859
2022-06-13 | 7:55 | 49.89 | 44725.3615 | 49.9858
2022-06-13 | 7:55 | 49.889 | 44725.3615 | 49.9857
2022-06-13 | 7:55 | 49.89 | 44725.3615 | 49.9856
2022-06-13 | 7:55 | 49.891 | 44725.3615 | 49.9856
2022-06-13 | 7:55 | 49.891 | 44725.3615 | 49.9856
2022-06-13 | 7:55 | 49.89 | 44725.3615 | 49.9856
2022-06-13 | 7:55 | 49.888 | 44725.3615 | 49.9855
2022-06-13 | 7:55 | 49.884 | 44725.3615 | 49.9855
2022-06-13 | 7:55 | 49.882 | 44725.3615 | 49.9855
2022-06-13 | 7:55 | 49.879 | 44725.3615 | 49.9855
2022-06-13 | 7:55 | 49.875 | 44725.3615 | 49.9854
2022-06-13 | 7:55 | 49.873 | 44725.3615 | 49.9854
2022-06-13 | 7:55 | 49.87 | 44725.3615 | 49.9853
2022-06-13 | 7:55 | 49.869 | 44725.3615 | 49.9853
2022-06-13 | 7:55 | 49.868 | 44725.3615 | 49.9852
2022-06-13 | 7:55 | 49.868 | 44725.3615 | 49.9852
2022-06-13 | 7:55 | 49.868 | 44725.3615 | 49.9851
2022-06-13 | 7:55 | 49.869 | 44725.3615 | 49.9851
2022-06-13 | 7:55 | 49.872 | 44725.3615 | 49.985
2022-06-13 | 7:55 | 49.874 | 44725.3615 | 49.985
2022-06-13 | 7:55 | 49.876 | 44725.3615 | 49.985
2022-06-13 | 7:55 | 49.878 | 44725.3615 | 49.985
2022-06-13 | 7:55 | 49.882 | 44725.3615 | 49.985
2022-06-13 | 7:55 | 49.884 | 44725.3615 | 49.985
2022-06-13 | 7:55 | 49.887 | 44725.3615 | 49.985
2022-06-13 | 7:55 | 49.891 | 44725.3615 | 49.985
2022-06-13 | 7:55 | 49.896 | 44725.3615 | 49.9849
2022-06-13 | 7:55 | 49.9 | 44725.3615 | 49.9849
2022-06-13 | 7:55 | 49.903 | 44725.3615 | 49.9848
2022-06-13 | 7:56 | 49.907 | 44725.3615 | 49.9848
2022-06-13 | 7:56 | 49.909 | 44725.3615 | 49.9847
2022-06-13 | 7:56 | 49.909 | 44725.3615 | 49.9846
2022-06-13 | 7:56 | 49.907 | 44725.3615 | 49.9845
2022-06-13 | 7:56 | 49.906 | 44725.3615 | 49.9844
2022-06-13 | 7:56 | 49.905 | 44725.3615 | 49.9844
2022-06-13 | 7:56 | 49.904 | 44725.3615 | 49.9843
2022-06-13 | 7:56 | 49.904 | 44725.3615 | 49.9843
2022-06-13 | 7:56 | 49.904 | 44725.3615 | 49.9843
2022-06-13 | 7:56 | 49.902 | 44725.3615 | 49.9844
2022-06-13 | 7:56 | 49.899 | 44725.3615 | 49.9844
2022-06-13 | 7:56 | 49.898 | 44725.3615 | 49.9844
2022-06-13 | 7:56 | 49.896 | 44725.3615 | 49.9844
2022-06-13 | 7:56 | 49.898 | 44725.3615 | 49.9844
2022-06-13 | 7:56 | 49.897 | 44725.3615 | 49.9844
2022-06-13 | 7:56 | 49.896 | 44725.3615 | 49.9844
2022-06-13 | 7:56 | 49.895 | 44725.3615 | 49.9844
2022-06-13 | 7:56 | 49.894 | 44725.3615 | 49.9844
2022-06-13 | 7:56 | 49.893 | 44725.3615 | 49.9844
2022-06-13 | 7:56 | 49.891 | 2022-06-13 08:41 | 49.9843
2022-06-13 | 7:56 | 49.892 | 44725.3615 | 49.9843
2022-06-13 | 7:56 | 49.894 | 44725.3615 | 49.9843
2022-06-13 | 7:56 | 49.896 | 44725.3615 | 49.9843
2022-06-13 | 7:56 | 49.899 | 44725.3615 | 49.9844
2022-06-13 | 7:56 | 49.9 | 44725.3615 | 49.9844
2022-06-13 | 7:56 | 49.901 | 44725.3615 | 49.9844
2022-06-13 | 7:56 | 49.899 | 44725.3615 | 49.9843
2022-06-13 | 7:56 | 49.897 | 44725.3615 | 49.9842
2022-06-13 | 7:56 | 49.897 | 44725.3615 | 49.9841
2022-06-13 | 7:56 | 49.896 | 44725.3615 | 49.984
2022-06-13 | 7:56 | 49.894 | 44725.3615 | 49.9839
2022-06-13 | 7:56 | 49.892 | 44725.3615 | 49.9839
2022-06-13 | 7:56 | 49.892 | 44725.3615 | 49.9838
2022-06-13 | 7:56 | 49.892 | 44725.3615 | 49.9837
2022-06-13 | 7:56 | 49.893 | 44725.3615 | 49.9837
2022-06-13 | 7:56 | 49.894 | 44725.3615 | 49.9837
2022-06-13 | 7:56 | 49.893 | 44725.3615 | 49.9836
2022-06-13 | 7:56 | 49.89 | 44725.3615 | 49.9836
2022-06-13 | 7:56 | 49.888 | 44725.3615 | 49.9836
2022-06-13 | 7:56 | 49.885 | 44725.3615 | 49.9836
2022-06-13 | 7:56 | 49.882 | 44725.3615 | 49.9836
2022-06-13 | 7:56 | 49.879 | 44725.3615 | 49.9836
2022-06-13 | 7:56 | 49.881 | 44725.3615 | 49.9836
2022-06-13 | 7:56 | 49.876 | 44725.3615 | 49.9836
2022-06-13 | 7:56 | 49.875 | 44725.3615 | 49.9835
2022-06-13 | 7:56 | 49.875 | 44725.3615 | 49.9835
2022-06-13 | 7:56 | 49.875 | 44725.3615 | 49.9835
2022-06-13 | 7:56 | 49.875 | 44725.3615 | 49.9834
2022-06-13 | 7:56 | 49.878 | 44725.3615 | 49.9833
2022-06-13 | 7:56 | 49.879 | 44725.3615 | 49.9833
2022-06-13 | 7:56 | 49.879 | 44725.3615 | 49.9833
2022-06-13 | 7:56 | 49.877 | 44725.3615 | 49.9833
2022-06-13 | 7:56 | 49.877 | 44725.3615 | 49.9833
2022-06-13 | 7:56 | 49.877 | 44725.3615 | 49.9833
2022-06-13 | 7:56 | 49.874 | 44725.3615 | 49.9833
2022-06-13 | 7:56 | 49.872 | 44725.3615 | 49.9833
2022-06-13 | 7:56 | 49.867 | 44725.3615 | 49.9833
2022-06-13 | 7:56 | 49.863 | 44725.3615 | 49.9833
2022-06-13 | 7:56 | 49.855 | 44725.3615 | 49.9833
2022-06-13 | 7:57 | 49.852 | 44725.3615 | 49.9833
2022-06-13 | 7:57 | 49.849 | 44725.3615 | 49.9833
2022-06-13 | 7:57 | 49.846 | 44725.3615 | 49.9832
2022-06-13 | 7:57 | 49.842 | 44725.3615 | 49.9832
2022-06-13 | 7:57 | 49.842 | 44725.3615 | 49.9832
2022-06-13 | 7:57 | 49.845 | 44725.3615 | 49.9831
2022-06-13 | 7:57 | 49.85 | 44725.3615 | 49.9831
2022-06-13 | 7:57 | 49.852 | 44725.3615 | 49.9831
2022-06-13 | 7:57 | 49.853 | 44725.3615 | 49.983
2022-06-13 | 7:57 | 49.854 | 44725.3615 | 49.983
2022-06-13 | 7:57 | 49.856 | 2022-06-13 08:41 | 49.9829
2022-06-13 | 7:57 | 49.858 | 44725.3615 | 49.9829
2022-06-13 | 7:57 | 49.86 | 44725.3615 | 49.9829
2022-06-13 | 7:57 | 49.857 | 44725.3615 | 49.9828
2022-06-13 | 7:57 | 49.855 | 44725.3615 | 49.9828
2022-06-13 | 7:57 | 49.855 | 44725.3615 | 49.9828
2022-06-13 | 7:57 | 49.854 | 44725.3615 | 49.9828
2022-06-13 | 7:57 | 49.852 | 44725.3615 | 49.9828
2022-06-13 | 7:57 | 49.85 | 44725.3615 | 49.9828
2022-06-13 | 7:57 | 49.851 | 44725.3615 | 49.9828
2022-06-13 | 7:57 | 49.854 | 44725.3615 | 49.9828
2022-06-13 | 7:57 | 49.86 | 44725.3615 | 49.9828
2022-06-13 | 7:57 | 49.861 | 44725.3615 | 49.9827
2022-06-13 | 7:57 | 49.863 | 44725.3615 | 49.9827
2022-06-13 | 7:57 | 49.862 | 44725.3615 | 49.9826
2022-06-13 | 7:57 | 49.861 | 44725.3615 | 49.9826
2022-06-13 | 7:57 | 49.863 | 44725.3615 | 49.9825
2022-06-13 | 7:57 | 49.864 | 44725.3615 | 49.9825
2022-06-13 | 7:57 | 49.864 | 44725.3615 | 49.9825
2022-06-13 | 7:57 | 49.865 | 44725.3615 | 49.9825
2022-06-13 | 7:57 | 49.869 | 44725.3615 | 49.9825
2022-06-13 | 7:57 | 49.87 | 44725.3615 | 49.9825
2022-06-13 | 7:57 | 49.87 | 44725.3615 | 49.9824
2022-06-13 | 7:57 | 49.876 | 44725.3615 | 49.9824
2022-06-13 | 7:57 | 49.879 | 44725.3615 | 49.9824
2022-06-13 | 7:57 | 49.879 | 44725.3615 | 49.9824
2022-06-13 | 7:57 | 49.879 | 44725.3615 | 49.9824
2022-06-13 | 7:57 | 49.879 | 44725.3615 | 49.9824
2022-06-13 | 7:57 | 49.879 | 44725.3615 | 49.9824
2022-06-13 | 7:57 | 49.877 | 44725.3615 | 49.9824
2022-06-13 | 7:57 | 49.875 | 44725.3615 | 49.9824
2022-06-13 | 7:57 | 49.876 | 44725.3615 | 49.9824
2022-06-13 | 7:57 | 49.88 | 44725.3615 | 49.9824
2022-06-13 | 7:57 | 49.884 | 44725.3615 | 49.9824
2022-06-13 | 7:57 | 49.886 | 44725.3615 | 49.9824
2022-06-13 | 7:57 | 49.888 | 44725.3615 | 49.9824
2022-06-13 | 7:57 | 49.889 | 44725.3615 | 49.9824
2022-06-13 | 7:57 | 49.891 | 44725.3615 | 49.9824
2022-06-13 | 7:57 | 49.892 | 44725.3615 | 49.9824
2022-06-13 | 7:57 | 49.892 | 44725.3615 | 49.9824
2022-06-13 | 7:57 | 49.893 | 44725.3615 | 49.9823
2022-06-13 | 7:57 | 49.896 | 44725.3615 | 49.9822
2022-06-13 | 7:57 | 49.894 | 44725.3615 | 49.9821
2022-06-13 | 7:57 | 49.894 | 44725.3615 | 49.982
2022-06-13 | 7:57 | 49.892 | 44725.3615 | 49.982
2022-06-13 | 7:57 | 49.892 | 44725.3615 | 49.9819
2022-06-13 | 7:57 | 49.892 | 44725.3615 | 49.9818
2022-06-13 | 7:57 | 49.895 | 44725.3615 | 49.9817
2022-06-13 | 7:57 | 49.899 | 44725.3615 | 49.9817
2022-06-13 | 7:57 | 49.901 | 44725.3615 | 49.9817
2022-06-13 | 7:57 | 49.9 | 2022-06-13 08:41 | 49.9816
2022-06-13 | 7:58 | 49.9 | 44725.3615 | 49.9816
2022-06-13 | 7:58 | 49.901 | 44725.3615 | 49.9816
2022-06-13 | 7:58 | 49.901 | 44725.3615 | 49.9816
2022-06-13 | 7:58 | 49.898 | 44725.3615 | 49.9816
2022-06-13 | 7:58 | 49.897 | 44725.3615 | 49.9816
2022-06-13 | 7:58 | 49.896 | 44725.3615 | 49.9816
2022-06-13 | 7:58 | 49.897 | 44725.3615 | 49.9816
2022-06-13 | 7:58 | 49.899 | 44725.3615 | 49.9816
2022-06-13 | 7:58 | 49.9 | 44725.3615 | 49.9816
2022-06-13 | 7:58 | 49.906 | 44725.3615 | 49.9816
2022-06-13 | 7:58 | 49.911 | 44725.3615 | 49.9815
2022-06-13 | 7:58 | 49.915 | 44725.3615 | 49.9814
2022-06-13 | 7:58 | 49.919 | 44725.3615 | 49.9814
2022-06-13 | 7:58 | 49.923 | 44725.3615 | 49.9813
2022-06-13 | 7:58 | 49.927 | 44725.3615 | 49.9813
2022-06-13 | 7:58 | 49.929 | 44725.3615 | 49.9812
2022-06-13 | 7:58 | 49.931 | 44725.3615 | 49.9812
2022-06-13 | 7:58 | 49.931 | 44725.3615 | 49.9812
2022-06-13 | 7:58 | 49.928 | 44725.3615 | 49.9812
2022-06-13 | 7:58 | 49.928 | 44725.3615 | 49.9812
2022-06-13 | 7:58 | 49.927 | 44725.3615 | 49.9812
2022-06-13 | 7:58 | 49.922 | 44725.3615 | 49.9812
2022-06-13 | 7:58 | 49.918 | 44725.3615 | 49.9812
2022-06-13 | 7:58 | 49.915 | 44725.3615 | 49.9813
2022-06-13 | 7:58 | 49.913 | 44725.3615 | 49.9812
2022-06-13 | 7:58 | 49.908 | 44725.3615 | 49.9812
2022-06-13 | 7:58 | 49.903 | 44725.3615 | 49.9811
2022-06-13 | 7:58 | 49.899 | 44725.3615 | 49.9811
2022-06-13 | 7:58 | 49.897 | 44725.3615 | 49.981
2022-06-13 | 7:58 | 49.895 | 44725.3615 | 49.981
2022-06-13 | 7:58 | 49.89 | 44725.3615 | 49.981
2022-06-13 | 7:58 | 49.888 | 44725.3615 | 49.981
2022-06-13 | 7:58 | 49.888 | 44725.3615 | 49.9809
2022-06-13 | 7:58 | 49.888 | 44725.3615 | 49.9809
2022-06-13 | 7:58 | 49.889 | 44725.3615 | 49.9809
2022-06-13 | 7:58 | 49.895 | 44725.3615 | 49.9809
2022-06-13 | 7:58 | 49.904 | 44725.3615 | 49.981
2022-06-13 | 7:58 | 49.911 | 44725.3615 | 49.981
2022-06-13 | 7:58 | 49.916 | 44725.3615 | 49.9809
2022-06-13 | 7:58 | 49.92 | 44725.3615 | 49.9809
2022-06-13 | 7:58 | 49.922 | 44725.3615 | 49.9809
2022-06-13 | 7:58 | 49.923 | 44725.3615 | 49.9808
2022-06-13 | 7:58 | 49.923 | 44725.3615 | 49.9808
2022-06-13 | 7:58 | 49.919 | 44725.3615 | 49.9807
2022-06-13 | 7:58 | 49.916 | 44725.3615 | 49.9806
2022-06-13 | 7:58 | 49.913 | 44725.3615 | 49.9806
2022-06-13 | 7:58 | 49.908 | 44725.3615 | 49.9806
2022-06-13 | 7:58 | 49.906 | 44725.3615 | 49.9805
2022-06-13 | 7:58 | 49.903 | 44725.3615 | 49.9805
2022-06-13 | 7:58 | 49.906 | 2022-06-13 08:41 | 49.9805
2022-06-13 | 7:58 | 49.91 | 44725.3615 | 49.9805
2022-06-13 | 7:58 | 49.913 | 44725.3615 | 49.9805
2022-06-13 | 7:58 | 49.916 | 44725.3615 | 49.9805
2022-06-13 | 7:58 | 49.916 | 44725.3615 | 49.9805
2022-06-13 | 7:58 | 49.916 | 44725.3615 | 49.9805
2022-06-13 | 7:58 | 49.914 | 44725.3615 | 49.9805
2022-06-13 | 7:58 | 49.912 | 44725.3615 | 49.9805
2022-06-13 | 7:58 | 49.907 | 44725.3615 | 49.9804
2022-06-13 | 7:58 | 49.905 | 44725.3615 | 49.9803
2022-06-13 | 7:59 | 49.906 | 44725.3615 | 49.9802
2022-06-13 | 7:59 | 49.907 | 44725.3615 | 49.9801
2022-06-13 | 7:59 | 49.912 | 44725.3615 | 49.98
2022-06-13 | 7:59 | 49.914 | 44725.3615 | 49.9799
2022-06-13 | 7:59 | 49.92 | 44725.3615 | 49.9798
2022-06-13 | 7:59 | 49.921 | 44725.3615 | 49.9798
2022-06-13 | 7:59 | 49.926 | 44725.3615 | 49.9797
2022-06-13 | 7:59 | 49.926 | 44725.3615 | 49.9797
2022-06-13 | 7:59 | 49.931 | 44725.3615 | 49.9796
2022-06-13 | 7:59 | 49.932 | 44725.3615 | 49.9796
2022-06-13 | 7:59 | 49.935 | 44725.3615 | 49.9795
2022-06-13 | 7:59 | 49.937 | 44725.3615 | 49.9795
2022-06-13 | 7:59 | 49.934 | 44725.3615 | 49.9795
2022-06-13 | 7:59 | 49.934 | 44725.3615 | 49.9795
2022-06-13 | 7:59 | 49.93 | 44725.3615 | 49.9794
2022-06-13 | 7:59 | 49.928 | 44725.3615 | 49.9793
2022-06-13 | 7:59 | 49.924 | 44725.3615 | 49.9793
2022-06-13 | 7:59 | 49.92 | 44725.3615 | 49.9792
2022-06-13 | 7:59 | 49.92 | 44725.3615 | 49.9791
2022-06-13 | 7:59 | 49.917 | 44725.3615 | 49.979
2022-06-13 | 7:59 | 49.917 | 44725.3615 | 49.979
2022-06-13 | 7:59 | 49.92 | 44725.3615 | 49.9789
2022-06-13 | 7:59 | 49.919 | 44725.3615 | 49.9789
2022-06-13 | 7:59 | 49.921 | 44725.3615 | 49.9789
2022-06-13 | 7:59 | 49.923 | 44725.3615 | 49.9788
2022-06-13 | 7:59 | 49.923 | 44725.3615 | 49.9787
2022-06-13 | 7:59 | 49.923 | 44725.3615 | 49.9788
2022-06-13 | 7:59 | 49.926 | 44725.3615 | 49.9787
2022-06-13 | 7:59 | 49.93 | 44725.3615 | 49.9787
2022-06-13 | 7:59 | 49.933 | 44725.3615 | 49.9785
2022-06-13 | 7:59 | 49.933 | 44725.3615 | 49.9784
2022-06-13 | 7:59 | 49.928 | 44725.3615 | 49.9784
2022-06-13 | 7:59 | 49.927 | 44725.3615 | 49.9783
2022-06-13 | 7:59 | 49.924 | 44725.3615 | 49.9782
2022-06-13 | 7:59 | 49.922 | 44725.3615 | 49.9781
2022-06-13 | 7:59 | 49.919 | 44725.3615 | 49.978
2022-06-13 | 7:59 | 49.919 | 44725.3616 | 49.9779
2022-06-13 | 7:59 | 49.92 | 44725.3616 | 49.9779
2022-06-13 | 7:59 | 49.92 | 44725.3616 | 49.9778
2022-06-13 | 7:59 | 49.92 | 44725.3616 | 49.9778
2022-06-13 | 7:59 | 49.922 | 2022-06-13 08:41 | 49.9777
2022-06-13 | 7:59 | 49.92 | 44725.3616 | 49.9777
2022-06-13 | 7:59 | 49.92 | 44725.3616 | 49.9776
2022-06-13 | 7:59 | 49.92 | 44725.3616 | 49.9775
2022-06-13 | 7:59 | 49.921 | 44725.3616 | 49.9775
2022-06-13 | 7:59 | 49.925 | 44725.3616 | 49.9774
2022-06-13 | 7:59 | 49.927 | 44725.3616 | 49.9773
2022-06-13 | 7:59 | 49.93 | 44725.3616 | 49.9773
2022-06-13 | 7:59 | 49.933 | 44725.3616 | 49.9772
2022-06-13 | 7:59 | 49.936 | 44725.3616 | 49.9771
2022-06-13 | 7:59 | 49.939 | 44725.3616 | 49.9771
2022-06-13 | 7:59 | 49.938 | 44725.3616 | 49.977
2022-06-13 | 7:59 | 49.939 | 44725.3616 | 49.9769
2022-06-13 | 7:59 | 49.936 | 44725.3616 | 49.9769
2022-06-13 | 7:59 | 49.936 | 44725.3616 | 49.9769
2022-06-13 | 7:59 | 49.939 | 44725.3616 | 49.9768
2022-06-13 | 7:59 | 49.939 | 44725.3616 | 49.9767
2022-06-13 | 7:59 | 49.943 | 44725.3616 | 49.9766
2022-06-13 | 7:59 | 49.945 | 44725.3616 | 49.9765
2022-06-13 | 7:59 | 49.95 | 44725.3616 | 49.9764
2022-06-13 | 7:59 | 49.955 | 44725.3616 | 49.9763
2022-06-13 | 8:00 | 49.96 | 44725.3616 | 49.9762
2022-06-13 | 8:00 | 49.964 | 44725.3616 | 49.9762
2022-06-13 | 8:00 | 49.97 | 44725.3616 | 49.976
2022-06-13 | 8:00 | 49.976 | 44725.3616 | 49.976
2022-06-13 | 8:00 | 49.981 | 44725.3616 | 49.976
2022-06-13 | 8:00 | 49.983 | 44725.3616 | 49.9761
2022-06-13 | 8:00 | 49.983 | 44725.3616 | 49.976
2022-06-13 | 8:00 | 49.985 | 44725.3616 | 49.976
2022-06-13 | 8:00 | 49.987 | 44725.3616 | 49.976
2022-06-13 | 8:00 | 49.985 | 44725.3616 | 49.9759
2022-06-13 | 8:00 | 49.985 | 44725.3616 | 49.9758
2022-06-13 | 8:00 | 49.986 | 44725.3616 | 49.9757
2022-06-13 | 8:00 | 49.985 | 44725.3616 | 49.9756
2022-06-13 | 8:00 | 49.982 | 44725.3616 | 49.9754
2022-06-13 | 8:00 | 49.983 | 44725.3616 | 49.9753
2022-06-13 | 8:00 | 49.984 | 44725.3616 | 49.9752
2022-06-13 | 8:00 | 49.988 | 44725.3616 | 49.9751
2022-06-13 | 8:00 | 49.989 | 44725.3616 | 49.975
2022-06-13 | 8:00 | 49.989 | 44725.3616 | 49.9749
2022-06-13 | 8:00 | 49.99 | 44725.3616 | 49.9748
2022-06-13 | 8:00 | 49.988 | 44725.3616 | 49.9747
2022-06-13 | 8:00 | 49.989 | 44725.3616 | 49.9747
2022-06-13 | 8:00 | 49.99 | 44725.3616 | 49.9746
2022-06-13 | 8:00 | 49.995 | 44725.3616 | 49.9746
2022-06-13 | 8:00 | 49.997 | 44725.3616 | 49.9745
2022-06-13 | 8:00 | 49.998 | 44725.3616 | 49.9745
2022-06-13 | 8:00 | 49.998 | 44725.3616 | 49.9744
2022-06-13 | 8:00 | 49.997 | 44725.3616 | 49.9743
2022-06-13 | 8:00 | 49.995 | 44725.3616 | 49.9741
2022-06-13 | 8:00 | 49.995 | 2022-06-13 08:41 | 49.974
2022-06-13 | 8:00 | 49.992 | 44725.3616 | 49.9738
2022-06-13 | 8:00 | 49.989 | 44725.3616 | 49.9737
2022-06-13 | 8:00 | 49.986 | 44725.3616 | 49.9736
2022-06-13 | 8:00 | 49.984 | 44725.3616 | 49.9735
2022-06-13 | 8:00 | 49.983 | 44725.3616 | 49.9734
2022-06-13 | 8:00 | 49.981 | 44725.3616 | 49.9734
2022-06-13 | 8:00 | 49.98 | 44725.3616 | 49.9733
2022-06-13 | 8:00 | 49.982 | 44725.3616 | 49.9733
2022-06-13 | 8:00 | 49.98 | 44725.3616 | 49.9732
2022-06-13 | 8:00 | 49.978 | 44725.3616 | 49.9733
2022-06-13 | 8:00 | 49.975 | 44725.3616 | 49.9733
2022-06-13 | 8:00 | 49.969 | 44725.3616 | 49.9732
2022-06-13 | 8:00 | 49.966 | 44725.3616 | 49.9732
2022-06-13 | 8:00 | 49.962 | 44725.3616 | 49.9732
2022-06-13 | 8:00 | 49.96 | 44725.3616 | 49.9733
2022-06-13 | 8:00 | 49.958 | 44725.3616 | 49.9733
2022-06-13 | 8:00 | 49.958 | 44725.3616 | 49.9733
2022-06-13 | 8:00 | 49.958 | 44725.3616 | 49.9733
2022-06-13 | 8:00 | 49.958 | 44725.3616 | 49.9733
2022-06-13 | 8:00 | 49.96 | 44725.3616 | 49.9733
2022-06-13 | 8:00 | 49.96 | 44725.3616 | 49.9732
2022-06-13 | 8:00 | 49.966 | 44725.3616 | 49.9732
2022-06-13 | 8:00 | 49.974 | 44725.3616 | 49.9731
2022-06-13 | 8:00 | 49.981 | 44725.3616 | 49.973
2022-06-13 | 8:00 | 49.986 | 44725.3616 | 49.973
2022-06-13 | 8:00 | 49.986 | 44725.3616 | 49.9729
2022-06-13 | 8:00 | 49.985 | 44725.3616 | 49.9728
2022-06-13 | 8:00 | 49.985 | 44725.3616 | 49.9727
2022-06-13 | 8:00 | 49.985 | 44725.3616 | 49.9726
2022-06-13 | 8:01 | 49.988 | 44725.3616 | 49.9724
2022-06-13 | 8:01 | 49.991 | 44725.3616 | 49.9722
2022-06-13 | 8:01 | 49.99 | 44725.3616 | 49.972
2022-06-13 | 8:01 | 49.99 | 44725.3616 | 49.9718
2022-06-13 | 8:01 | 49.991 | 44725.3616 | 49.9717
2022-06-13 | 8:01 | 49.996 | 44725.3616 | 49.9715
2022-06-13 | 8:01 | 49.998 | 44725.3616 | 49.9714
2022-06-13 | 8:01 | 50 | 44725.3616 | 49.9712
2022-06-13 | 8:01 | 50.002 | 44725.3616 | 49.9711
2022-06-13 | 8:01 | 50 | 44725.3616 | 49.971
2022-06-13 | 8:01 | 50.001 | 44725.3616 | 49.9709
2022-06-13 | 8:01 | 50 | 44725.3616 | 49.9708
2022-06-13 | 8:01 | 50.005 | 44725.3616 | 49.9708
2022-06-13 | 8:01 | 50.005 | 44725.3616 | 49.9707
2022-06-13 | 8:01 | 50.008 | 44725.3616 | 49.9707
2022-06-13 | 8:01 | 50.01 | 44725.3616 | 49.9706
2022-06-13 | 8:01 | 50.013 | 44725.3616 | 49.9705
2022-06-13 | 8:01 | 50.011 | 44725.3616 | 49.9704
2022-06-13 | 8:01 | 50.013 | 44725.3616 | 49.9704
2022-06-13 | 8:01 | 50.01 | 44725.3616 | 49.9703
2022-06-13 | 8:01 | 50.01 | 2022-06-13 08:41 | 49.9702
2022-06-13 | 8:01 | 50.009 | 44725.3616 | 49.9701
2022-06-13 | 8:01 | 50.007 | 44725.3616 | 49.9701
2022-06-13 | 8:01 | 50.004 | 44725.3616 | 49.97
2022-06-13 | 8:01 | 50.001 | 44725.3616 | 49.97
2022-06-13 | 8:01 | 49.998 | 44725.3616 | 49.9699
2022-06-13 | 8:01 | 49.994 | 44725.3616 | 49.9699
2022-06-13 | 8:01 | 49.992 | 44725.3616 | 49.9698
2022-06-13 | 8:01 | 49.987 | 44725.3616 | 49.9698
2022-06-13 | 8:01 | 49.985 | 44725.3616 | 49.9697
2022-06-13 | 8:01 | 49.984 | 44725.3616 | 49.9697
2022-06-13 | 8:01 | 49.984 | 44725.3616 | 49.9697
2022-06-13 | 8:01 | 49.983 | 44725.3616 | 49.9697
2022-06-13 | 8:01 | 49.982 | 44725.3616 | 49.9697
2022-06-13 | 8:01 | 49.982 | 44725.3616 | 49.9697
2022-06-13 | 8:01 | 49.982 | 44725.3616 | 49.9696
2022-06-13 | 8:01 | 49.984 | 44725.3616 | 49.9696
2022-06-13 | 8:01 | 49.983 | 44725.3616 | 49.9695
2022-06-13 | 8:01 | 49.984 | 44725.3616 | 49.9694
2022-06-13 | 8:01 | 49.984 | 44725.3616 | 49.9693
2022-06-13 | 8:01 | 49.984 | 44725.3616 | 49.9692
2022-06-13 | 8:01 | 49.985 | 44725.3616 | 49.9691
2022-06-13 | 8:01 | 49.987 | 44725.3616 | 49.969
2022-06-13 | 8:01 | 49.992 | 44725.3616 | 49.9689
2022-06-13 | 8:01 | 49.995 | 44725.3616 | 49.9688
2022-06-13 | 8:01 | 50.001 | 44725.3616 | 49.9687
2022-06-13 | 8:01 | 50.004 | 44725.3616 | 49.9686
2022-06-13 | 8:01 | 50.009 | 44725.3616 | 49.9686
2022-06-13 | 8:01 | 50.013 | 44725.3616 | 49.9685
2022-06-13 | 8:01 | 50.018 | 44725.3616 | 49.9684
2022-06-13 | 8:01 | 50.02 | 44725.3616 | 49.9684
2022-06-13 | 8:01 | 50.021 | 44725.3616 | 49.9683
2022-06-13 | 8:01 | 50.024 | 44725.3616 | 49.9683
2022-06-13 | 8:01 | 50.024 | 44725.3616 | 49.9683
2022-06-13 | 8:01 | 50.025 | 44725.3616 | 49.9683
2022-06-13 | 8:01 | 50.027 | 44725.3616 | 49.9682
2022-06-13 | 8:01 | 50.034 | 44725.3616 | 49.9682
2022-06-13 | 8:01 | 50.038 | 44725.3616 | 49.9682
2022-06-13 | 8:01 | 50.043 | 44725.3616 | 49.9682
2022-06-13 | 8:01 | 50.047 | 44725.3616 | 49.9682
2022-06-13 | 8:01 | 50.051 | 44725.3616 | 49.9682
2022-06-13 | 8:02 | 50.053 | 44725.3616 | 49.9682
2022-06-13 | 8:02 | 50.054 | 44725.3616 | 49.9682
2022-06-13 | 8:02 | 50.056 | 44725.3616 | 49.9682
2022-06-13 | 8:02 | 50.059 | 44725.3616 | 49.9682
2022-06-13 | 8:02 | 50.06 | 44725.3616 | 49.9681
2022-06-13 | 8:02 | 50.059 | 44725.3616 | 49.9681
2022-06-13 | 8:02 | 50.058 | 44725.3616 | 49.9682
2022-06-13 | 8:02 | 50.059 | 44725.3616 | 49.9681
2022-06-13 | 8:02 | 50.059 | 44725.3616 | 49.968
2022-06-13 | 8:02 | 50.059 | 2022-06-13 08:41 | 49.968
2022-06-13 | 8:02 | 50.059 | 44725.3616 | 49.9679
2022-06-13 | 8:02 | 50.059 | 44725.3616 | 49.9678
2022-06-13 | 8:02 | 50.057 | 44725.3616 | 49.9678
2022-06-13 | 8:02 | 50.057 | 44725.3616 | 49.9677
2022-06-13 | 8:02 | 50.058 | 44725.3616 | 49.9677
2022-06-13 | 8:02 | 50.06 | 44725.3616 | 49.9677
2022-06-13 | 8:02 | 50.065 | 44725.3616 | 49.9676
2022-06-13 | 8:02 | 50.067 | 44725.3616 | 49.9676
2022-06-13 | 8:02 | 50.071 | 44725.3616 | 49.9675
2022-06-13 | 8:02 | 50.073 | 44725.3616 | 49.9675
2022-06-13 | 8:02 | 50.076 | 44725.3616 | 49.9674
2022-06-13 | 8:02 | 50.074 | 44725.3616 | 49.9673
2022-06-13 | 8:02 | 50.075 | 44725.3616 | 49.9673
2022-06-13 | 8:02 | 50.072 | 44725.3616 | 49.9673
2022-06-13 | 8:02 | 50.069 | 44725.3616 | 49.9673
2022-06-13 | 8:02 | 50.067 | 44725.3616 | 49.9672
2022-06-13 | 8:02 | 50.065 | 44725.3616 | 49.9672
2022-06-13 | 8:02 | 50.068 | 44725.3616 | 49.9672
2022-06-13 | 8:02 | 50.066 | 44725.3616 | 49.9671
2022-06-13 | 8:02 | 50.065 | 44725.3616 | 49.967
|  |  | 44725.3616 | 49.967
|  |  | 44725.3616 | 49.967
|  |  | 44725.3616 | 49.967
|  |  | 44725.3616 | 49.967
|  |  | 44725.3616 | 49.9671
|  |  | 44725.3616 | 49.967
|  |  | 44725.3616 | 49.9671
|  |  | 44725.3616 | 49.9671
|  |  | 44725.3616 | 49.9671
|  |  | 44725.3616 | 49.9671
|  |  | 44725.3616 | 49.9671
|  |  | 44725.3616 | 49.967
|  |  | 44725.3616 | 49.967
|  |  | 44725.3616 | 49.967
|  |  | 44725.3616 | 49.967
|  |  | 44725.3616 | 49.9669
|  |  | 44725.3616 | 49.9669
|  |  | 44725.3616 | 49.9669
|  |  | 44725.3616 | 49.9669
|  |  | 44725.3616 | 49.9669
|  |  | 44725.3616 | 49.9668
|  |  | 44725.3616 | 49.9668
|  |  | 44725.3616 | 49.9668
|  |  | 44725.3616 | 49.9667
|  |  | 44725.3616 | 49.9666
|  |  | 44725.3616 | 49.9666
|  |  | 44725.3616 | 49.9665
|  |  | 44725.3616 | 49.9664
|  |  | 44725.3616 | 49.9663
|  |  | 2022-06-13 08:41 | 49.9662
|  |  | 44725.3616 | 49.9662
|  |  | 44725.3616 | 49.9661
|  |  | 44725.3616 | 49.966
|  |  | 44725.3616 | 49.9659
|  |  | 44725.3616 | 49.9658
|  |  | 44725.3616 | 49.9657
|  |  | 44725.3616 | 49.9657
|  |  | 44725.3616 | 49.9656
|  |  | 44725.3616 | 49.9656
|  |  | 44725.3616 | 49.9656
|  |  | 44725.3616 | 49.9656
|  |  | 44725.3616 | 49.9656
|  |  | 44725.3616 | 49.9657
|  |  | 44725.3616 | 49.9657
|  |  | 44725.3616 | 49.9657
|  |  | 44725.3616 | 49.9657
|  |  | 44725.3616 | 49.9657
|  |  | 44725.3616 | 49.9657
|  |  | 44725.3616 | 49.9657
|  |  | 44725.3616 | 49.9657
|  |  | 44725.3616 | 49.9657
|  |  | 44725.3616 | 49.9657
|  |  | 44725.3616 | 49.9657
|  |  | 44725.3616 | 49.9657
|  |  | 44725.3616 | 49.9657
|  |  | 44725.3616 | 49.9657
|  |  | 44725.3616 | 49.9657
|  |  | 44725.3616 | 49.9657
|  |  | 44725.3616 | 49.9656
|  |  | 44725.3616 | 49.9656
|  |  | 44725.3616 | 49.9655
|  |  | 44725.3616 | 49.9653
|  |  | 44725.3616 | 49.9652
|  |  | 44725.3616 | 49.965
|  |  | 44725.3616 | 49.9648
|  |  | 44725.3616 | 49.9646
|  |  | 44725.3616 | 49.9645
|  |  | 44725.3616 | 49.9644
|  |  | 44725.3616 | 49.9643
|  |  | 44725.3616 | 49.9643
|  |  | 44725.3616 | 49.9643
|  |  | 44725.3616 | 49.9642
|  |  | 44725.3616 | 49.9641
|  |  | 44725.3616 | 49.9641
|  |  | 44725.3616 | 49.964
|  |  | 44725.3616 | 49.9639
|  |  | 44725.3616 | 49.9639
|  |  | 44725.3616 | 49.9638
|  |  | 44725.3616 | 49.9637
|  |  | 2022-06-13 08:41 | 49.9637
|  |  | 44725.3616 | 49.9637
|  |  | 44725.3616 | 49.9637
|  |  | 44725.3616 | 49.9638
|  |  | 44725.3616 | 49.9638
|  |  | 44725.3616 | 49.9638
|  |  | 44725.3616 | 49.9639
|  |  | 44725.3616 | 49.964
|  |  | 44725.3616 | 49.964
|  |  | 44725.3616 | 49.9641
|  |  | 44725.3616 | 49.9642
|  |  | 44725.3616 | 49.9643
|  |  | 44725.3616 | 49.9643
|  |  | 44725.3616 | 49.9643
|  |  | 44725.3616 | 49.9643
|  |  | 44725.3616 | 49.9643
|  |  | 44725.3616 | 49.9643
|  |  | 44725.3616 | 49.9642
|  |  | 44725.3616 | 49.9642
|  |  | 44725.3616 | 49.9641
|  |  | 44725.3616 | 49.964
|  |  | 44725.3616 | 49.9639
|  |  | 44725.3616 | 49.9638
|  |  | 44725.3616 | 49.9638
|  |  | 44725.3616 | 49.9637
|  |  | 44725.3616 | 49.9637
|  |  | 44725.3616 | 49.9636
|  |  | 44725.3616 | 49.9635
|  |  | 44725.3616 | 49.9634
|  |  | 44725.3616 | 49.9633
|  |  | 44725.3616 | 49.9632
|  |  | 44725.3616 | 49.9631
|  |  | 44725.3616 | 49.963
|  |  | 44725.3616 | 49.9628
|  |  | 44725.3616 | 49.9626
|  |  | 44725.3616 | 49.9625
|  |  | 44725.3616 | 49.9624
|  |  | 44725.3616 | 49.9622
|  |  | 44725.3616 | 49.962
|  |  | 44725.3616 | 49.9619
|  |  | 44725.3616 | 49.9618
|  |  | 44725.3616 | 49.9617
|  |  | 44725.3616 | 49.9616
|  |  | 44725.3616 | 49.9616
|  |  | 44725.3616 | 49.9616
|  |  | 44725.3616 | 49.9616
|  |  | 44725.3616 | 49.9617
|  |  | 44725.3616 | 49.9617
|  |  | 44725.3616 | 49.9618
|  |  | 44725.3616 | 49.9618
|  |  | 2022-06-13 08:41 | 49.9618
|  |  | 44725.3616 | 49.9618
|  |  | 44725.3616 | 49.9617
|  |  | 44725.3616 | 49.9617
|  |  | 44725.3616 | 49.9616
|  |  | 44725.3616 | 49.9615
|  |  | 44725.3616 | 49.9614
|  |  | 44725.3616 | 49.9614
|  |  | 44725.3616 | 49.9613
|  |  | 44725.3616 | 49.9612
|  |  | 44725.3616 | 49.961
|  |  | 44725.3616 | 49.9609
|  |  | 44725.3616 | 49.9608
|  |  | 44725.3616 | 49.9608
|  |  | 44725.3616 | 49.9607
|  |  | 44725.3616 | 49.9606
|  |  | 44725.3616 | 49.9606
|  |  | 44725.3616 | 49.9606
|  |  | 44725.3616 | 49.9605
|  |  | 44725.3616 | 49.9605
|  |  | 44725.3616 | 49.9605
|  |  | 44725.3616 | 49.9605
|  |  | 44725.3616 | 49.9605
|  |  | 44725.3616 | 49.9605
|  |  | 44725.3616 | 49.9605
|  |  | 44725.3616 | 49.9605
|  |  | 44725.3616 | 49.9604
|  |  | 44725.3616 | 49.9604
|  |  | 44725.3616 | 49.9603
|  |  | 44725.3616 | 49.9603
|  |  | 44725.3616 | 49.9603
|  |  | 44725.3616 | 49.9603
|  |  | 44725.3616 | 49.9603
|  |  | 44725.3616 | 49.9602
|  |  | 44725.3616 | 49.9602
|  |  | 44725.3616 | 49.9602
|  |  | 44725.3616 | 49.9602
|  |  | 44725.3616 | 49.9603
|  |  | 44725.3616 | 49.9602
|  |  | 44725.3616 | 49.9603
|  |  | 44725.3616 | 49.9603
|  |  | 44725.3616 | 49.9602
|  |  | 44725.3616 | 49.9601
|  |  | 44725.3616 | 49.9601
|  |  | 44725.3616 | 49.96
|  |  | 44725.3616 | 49.9598
|  |  | 44725.3616 | 49.9597
|  |  | 44725.3616 | 49.9597
|  |  | 44725.3616 | 49.9596
|  |  | 44725.3616 | 49.9596
|  |  | 2022-06-13 08:41 | 49.9594
|  |  | 44725.3616 | 49.9593
|  |  | 44725.3616 | 49.9593
|  |  | 44725.3616 | 49.9592
|  |  | 44725.3616 | 49.9591
|  |  | 44725.3616 | 49.9589
|  |  | 44725.3616 | 49.9588
|  |  | 44725.3616 | 49.9588
|  |  | 44725.3616 | 49.9587
|  |  | 44725.3616 | 49.9586
|  |  | 44725.3616 | 49.9586
|  |  | 44725.3616 | 49.9585
|  |  | 44725.3616 | 49.9584
|  |  | 44725.3616 | 49.9583
|  |  | 44725.3616 | 49.9582
|  |  | 44725.3616 | 49.9581
|  |  | 44725.3616 | 49.958
|  |  | 44725.3616 | 49.958
|  |  | 44725.3616 | 49.958
|  |  | 44725.3616 | 49.958
|  |  | 44725.3616 | 49.958
|  |  | 44725.3616 | 49.958
|  |  | 44725.3616 | 49.958
|  |  | 44725.3616 | 49.958
|  |  | 44725.3616 | 49.958
|  |  | 44725.3616 | 49.9579
|  |  | 44725.3616 | 49.9579
|  |  | 44725.3616 | 49.9579
|  |  | 44725.3616 | 49.9578
|  |  | 44725.3616 | 49.9578
|  |  | 44725.3616 | 49.9577
|  |  | 44725.3616 | 49.9577
|  |  | 44725.3616 | 49.9577
|  |  | 44725.3616 | 49.9577
|  |  | 44725.3616 | 49.9577
|  |  | 44725.3616 | 49.9577
|  |  | 44725.3616 | 49.9577
|  |  | 44725.3616 | 49.9577
|  |  | 44725.3616 | 49.9576
|  |  | 44725.3616 | 49.9575
|  |  | 44725.3616 | 49.9574
|  |  | 44725.3616 | 49.9574
|  |  | 44725.3616 | 49.9573
|  |  | 44725.3616 | 49.9572
|  |  | 44725.3616 | 49.9571
|  |  | 44725.3616 | 49.957
|  |  | 44725.3616 | 49.9569
|  |  | 44725.3616 | 49.9568
|  |  | 44725.3616 | 49.9566
|  |  | 44725.3616 | 49.9564
|  |  | 2022-06-13 08:41 | 49.9562
|  |  | 44725.3616 | 49.9559
|  |  | 44725.3616 | 49.9555
|  |  | 44725.3616 | 49.9551
|  |  | 44725.3616 | 49.9547
|  |  | 44725.3616 | 49.9541
|  |  | 44725.3616 | 49.9535
|  |  | 44725.3616 | 49.9529
|  |  | 44725.3616 | 49.9521
|  |  | 44725.3616 | 49.9513
|  |  | 44725.3616 | 49.9504
|  |  | 44725.3616 | 49.9496
|  |  | 44725.3616 | 49.9486
|  |  | 44725.3616 | 49.9477
|  |  | 44725.3616 | 49.9467
|  |  | 44725.3616 | 49.9457
|  |  | 44725.3616 | 49.9448
|  |  | 44725.3616 | 49.944
|  |  | 44725.3616 | 49.943
|  |  | 44725.3616 | 49.9421
|  |  | 44725.3616 | 49.9413
|  |  | 44725.3616 | 49.9403
|  |  | 44725.3616 | 49.9395
|  |  | 44725.3616 | 49.9387
|  |  | 44725.3616 | 49.9378
|  |  | 44725.3616 | 49.937
|  |  | 44725.3616 | 49.9362
|  |  | 44725.3616 | 49.9354
|  |  | 44725.3616 | 49.9348
|  |  | 44725.3617 | 49.9342
|  |  | 44725.3617 | 49.9337
|  |  | 44725.3617 | 49.9333
|  |  | 44725.3617 | 49.9328
|  |  | 44725.3617 | 49.9324
|  |  | 44725.3617 | 49.932
|  |  | 44725.3617 | 49.9313
|  |  | 44725.3617 | 49.9308
|  |  | 44725.3617 | 49.9302
|  |  | 44725.3617 | 49.9296
|  |  | 44725.3617 | 49.9289
|  |  | 44725.3617 | 49.9283
|  |  | 44725.3617 | 49.9278
|  |  | 44725.3617 | 49.9274
|  |  | 44725.3617 | 49.927
|  |  | 44725.3617 | 49.9267
|  |  | 44725.3617 | 49.9264
|  |  | 44725.3617 | 49.9262
|  |  | 44725.3617 | 49.926
|  |  | 44725.3617 | 49.926
|  |  | 44725.3617 | 49.9257
|  |  | 2022-06-13 08:41 | 49.9255
|  |  | 44725.3617 | 49.9251
|  |  | 44725.3617 | 49.9247
|  |  | 44725.3617 | 49.9243
|  |  | 44725.3617 | 49.9239
|  |  | 44725.3617 | 49.9235
|  |  | 44725.3617 | 49.923
|  |  | 44725.3617 | 49.9224
|  |  | 44725.3617 | 49.9219
|  |  | 44725.3617 | 49.9214
|  |  | 44725.3617 | 49.921
|  |  | 44725.3617 | 49.9206
|  |  | 44725.3617 | 49.92
|  |  | 44725.3617 | 49.9196
|  |  | 44725.3617 | 49.9191
|  |  | 44725.3617 | 49.9186
|  |  | 44725.3617 | 49.9181
|  |  | 44725.3617 | 49.9175
|  |  | 44725.3617 | 49.917
|  |  | 44725.3617 | 49.9165
|  |  | 44725.3617 | 49.9159
|  |  | 44725.3617 | 49.9153
|  |  | 44725.3617 | 49.9146
|  |  | 44725.3617 | 49.914
|  |  | 44725.3617 | 49.9133
|  |  | 44725.3617 | 49.9127
|  |  | 44725.3617 | 49.9121
|  |  | 44725.3617 | 49.9115
|  |  | 44725.3617 | 49.9109
|  |  | 44725.3617 | 49.9102
|  |  | 44725.3617 | 49.9096
|  |  | 44725.3617 | 49.9089
|  |  | 44725.3617 | 49.9083
|  |  | 44725.3617 | 49.9076
|  |  | 44725.3617 | 49.907
|  |  | 44725.3617 | 49.9064
|  |  | 44725.3617 | 49.9058
|  |  | 44725.3617 | 49.9052
|  |  | 44725.3617 | 49.9047
|  |  | 44725.3617 | 49.9041
|  |  | 44725.3617 | 49.9035
|  |  | 44725.3617 | 49.9029
|  |  | 44725.3617 | 49.9023
|  |  | 44725.3617 | 49.9017
|  |  | 44725.3617 | 49.9013
|  |  | 44725.3617 | 49.9008
|  |  | 44725.3617 | 49.9003
|  |  | 44725.3617 | 49.8998
|  |  | 44725.3617 | 49.8993
|  |  | 44725.3617 | 49.8989
|  |  | 2022-06-13 08:41 | 49.8984
|  |  | 44725.3617 | 49.898
|  |  | 44725.3617 | 49.8976
|  |  | 44725.3617 | 49.8972
|  |  | 44725.3617 | 49.8968
|  |  | 44725.3617 | 49.8964
|  |  | 44725.3617 | 49.896
|  |  | 44725.3617 | 49.8957
|  |  | 44725.3617 | 49.8954
|  |  | 44725.3617 | 49.895
|  |  | 44725.3617 | 49.8947
|  |  | 44725.3617 | 49.8944
|  |  | 44725.3617 | 49.8941
|  |  | 44725.3617 | 49.8938
|  |  | 44725.3617 | 49.8935
|  |  | 44725.3617 | 49.8932
|  |  | 44725.3617 | 49.8929
|  |  | 44725.3617 | 49.8925
|  |  | 44725.3617 | 49.8922
|  |  | 44725.3617 | 49.8919
|  |  | 44725.3617 | 49.8915
|  |  | 44725.3617 | 49.8912
|  |  | 44725.3617 | 49.8909
|  |  | 44725.3617 | 49.8906
|  |  | 44725.3617 | 49.8902
|  |  | 44725.3617 | 49.8899
|  |  | 44725.3617 | 49.8894
|  |  | 44725.3617 | 49.889
|  |  | 44725.3617 | 49.8886
|  |  | 44725.3617 | 49.8882
|  |  | 44725.3617 | 49.8878
|  |  | 44725.3617 | 49.8873
|  |  | 44725.3617 | 49.8869
|  |  | 44725.3617 | 49.8865
|  |  | 44725.3617 | 49.8862
|  |  | 44725.3617 | 49.8858
|  |  | 44725.3617 | 49.8854
|  |  | 44725.3617 | 49.8849
|  |  | 44725.3617 | 49.8844
|  |  | 44725.3617 | 49.8839
|  |  | 44725.3617 | 49.8835
|  |  | 44725.3617 | 49.883
|  |  | 44725.3617 | 49.8825
|  |  | 44725.3617 | 49.8821
|  |  | 44725.3617 | 49.8817
|  |  | 44725.3617 | 49.8813
|  |  | 44725.3617 | 49.8809
|  |  | 44725.3617 | 49.8805
|  |  | 44725.3617 | 49.88
|  |  | 44725.3617 | 49.8796
|  |  | 2022-06-13 08:41 | 49.8792
|  |  | 44725.3617 | 49.8788
|  |  | 44725.3617 | 49.8784
|  |  | 44725.3617 | 49.878
|  |  | 44725.3617 | 49.8776
|  |  | 44725.3617 | 49.8772
|  |  | 44725.3617 | 49.8769
|  |  | 44725.3617 | 49.8765
|  |  | 44725.3617 | 49.8761
|  |  | 44725.3617 | 49.8757
|  |  | 44725.3617 | 49.8753
|  |  | 44725.3617 | 49.8749
|  |  | 44725.3617 | 49.8745
|  |  | 44725.3617 | 49.874
|  |  | 44725.3617 | 49.8736
|  |  | 44725.3617 | 49.8732
|  |  | 44725.3617 | 49.8728
|  |  | 44725.3617 | 49.8723
|  |  | 44725.3617 | 49.8719
|  |  | 44725.3617 | 49.8715
|  |  | 44725.3617 | 49.871
|  |  | 44725.3617 | 49.8706
|  |  | 44725.3617 | 49.8702
|  |  | 44725.3617 | 49.8698
|  |  | 44725.3617 | 49.8694
|  |  | 44725.3617 | 49.869
|  |  | 44725.3617 | 49.8685
|  |  | 44725.3617 | 49.8681
|  |  | 44725.3617 | 49.8677
|  |  | 44725.3617 | 49.8673
|  |  | 44725.3617 | 49.8669
|  |  | 44725.3617 | 49.8665
|  |  | 44725.3617 | 49.8661
|  |  | 44725.3617 | 49.8657
|  |  | 44725.3617 | 49.8654
|  |  | 44725.3617 | 49.865
|  |  | 44725.3617 | 49.8647
|  |  | 44725.3617 | 49.8644
|  |  | 44725.3617 | 49.8641
|  |  | 44725.3617 | 49.8639
|  |  | 44725.3617 | 49.8636
|  |  | 44725.3617 | 49.8633
|  |  | 44725.3617 | 49.8629
|  |  | 44725.3617 | 49.8626
|  |  | 44725.3617 | 49.8622
|  |  | 44725.3617 | 49.8618
|  |  | 44725.3617 | 49.8615
|  |  | 44725.3617 | 49.8613
|  |  | 44725.3617 | 49.8611
|  |  | 44725.3617 | 49.8608
|  |  | 2022-06-13 08:41 | 49.8606
|  |  | 44725.3617 | 49.8604
|  |  | 44725.3617 | 49.8601
|  |  | 44725.3617 | 49.8599
|  |  | 44725.3617 | 49.8597
|  |  | 44725.3617 | 49.8595
|  |  | 44725.3617 | 49.8593
|  |  | 44725.3617 | 49.859
|  |  | 44725.3617 | 49.8588
|  |  | 44725.3617 | 49.8586
|  |  | 44725.3617 | 49.8583
|  |  | 44725.3617 | 49.858
|  |  | 44725.3617 | 49.8578
|  |  | 44725.3617 | 49.8575
|  |  | 44725.3617 | 49.8572
|  |  | 44725.3617 | 49.8569
|  |  | 44725.3617 | 49.8567
|  |  | 44725.3617 | 49.8565
|  |  | 44725.3617 | 49.8563
|  |  | 44725.3617 | 49.8561
|  |  | 44725.3617 | 49.856
|  |  | 44725.3617 | 49.8559
|  |  | 44725.3617 | 49.8558
|  |  | 44725.3617 | 49.8557
|  |  | 44725.3617 | 49.8556
|  |  | 44725.3617 | 49.8555
|  |  | 44725.3617 | 49.8553
|  |  | 44725.3617 | 49.8552
|  |  | 44725.3617 | 49.8551
|  |  | 44725.3617 | 49.8549
|  |  | 44725.3617 | 49.8548
|  |  | 44725.3617 | 49.8546
|  |  | 44725.3617 | 49.8544
|  |  | 44725.3617 | 49.8543
|  |  | 44725.3617 | 49.8541
|  |  | 44725.3617 | 49.8539
|  |  | 44725.3617 | 49.8537
|  |  | 44725.3617 | 49.8534
|  |  | 44725.3617 | 49.8532
|  |  | 44725.3617 | 49.853
|  |  | 44725.3617 | 49.8528
|  |  | 44725.3617 | 49.8525
|  |  | 44725.3617 | 49.8523
|  |  | 44725.3617 | 49.8521
|  |  | 44725.3617 | 49.852
|  |  | 44725.3617 | 49.8518
|  |  | 44725.3617 | 49.8516
|  |  | 44725.3617 | 49.8514
|  |  | 44725.3617 | 49.8512
|  |  | 44725.3617 | 49.8511
|  |  | 2022-06-13 08:41 | 49.8509
|  |  | 44725.3617 | 49.8507
|  |  | 44725.3617 | 49.8505
|  |  | 44725.3617 | 49.8504
|  |  | 44725.3617 | 49.8502
|  |  | 44725.3617 | 49.85
|  |  | 44725.3617 | 49.8498
|  |  | 44725.3617 | 49.8496
|  |  | 44725.3617 | 49.8495
|  |  | 44725.3617 | 49.8493
|  |  | 44725.3617 | 49.8491
|  |  | 44725.3617 | 49.849
|  |  | 44725.3617 | 49.8489
|  |  | 44725.3617 | 49.8487
|  |  | 44725.3617 | 49.8486
|  |  | 44725.3617 | 49.8485
|  |  | 44725.3617 | 49.8484
|  |  | 44725.3617 | 49.8483
|  |  | 44725.3617 | 49.8481
|  |  | 44725.3617 | 49.848
|  |  | 44725.3617 | 49.8479
|  |  | 44725.3617 | 49.8479
|  |  | 44725.3617 | 49.8478
|  |  | 44725.3617 | 49.8477
|  |  | 44725.3617 | 49.8476
|  |  | 44725.3617 | 49.8475
|  |  | 44725.3617 | 49.8473
|  |  | 44725.3617 | 49.8471
|  |  | 44725.3617 | 49.847
|  |  | 44725.3617 | 49.8468
|  |  | 44725.3617 | 49.8466
|  |  | 44725.3617 | 49.8465
|  |  | 44725.3617 | 49.8463
|  |  | 44725.3617 | 49.8462
|  |  | 44725.3617 | 49.8462
|  |  | 44725.3617 | 49.8461
|  |  | 44725.3617 | 49.846
|  |  | 44725.3617 | 49.846
|  |  | 44725.3617 | 49.8458
|  |  | 44725.3617 | 49.8457
|  |  | 44725.3617 | 49.8456
|  |  | 44725.3617 | 49.8455
|  |  | 44725.3617 | 49.8454
|  |  | 44725.3617 | 49.8453
|  |  | 44725.3617 | 49.8453
|  |  | 44725.3617 | 49.8452
|  |  | 44725.3617 | 49.8452
|  |  | 44725.3617 | 49.8452
|  |  | 44725.3617 | 49.8452
|  |  | 44725.3617 | 49.845
|  |  | 2022-06-13 08:41 | 49.845
|  |  | 44725.3617 | 49.8449
|  |  | 44725.3617 | 49.8448
|  |  | 44725.3617 | 49.8447
|  |  | 44725.3617 | 49.8446
|  |  | 44725.3617 | 49.8445
|  |  | 44725.3617 | 49.8444
|  |  | 44725.3617 | 49.8443
|  |  | 44725.3617 | 49.8442
|  |  | 44725.3617 | 49.8441
|  |  | 44725.3617 | 49.844
|  |  | 44725.3617 | 49.844
|  |  | 44725.3617 | 49.8439
|  |  | 44725.3617 | 49.8439
|  |  | 44725.3617 | 49.8439
|  |  | 44725.3617 | 49.8439
|  |  | 44725.3617 | 49.8439
|  |  | 44725.3617 | 49.8438
|  |  | 44725.3617 | 49.8437
|  |  | 44725.3617 | 49.8436
|  |  | 44725.3617 | 49.8435
|  |  | 44725.3617 | 49.8434
|  |  | 44725.3617 | 49.8434
|  |  | 44725.3617 | 49.8433
|  |  | 44725.3617 | 49.8432
|  |  | 44725.3617 | 49.8432
|  |  | 44725.3617 | 49.8431
|  |  | 44725.3617 | 49.843
|  |  | 44725.3617 | 49.843
|  |  | 44725.3617 | 49.8429
|  |  | 44725.3617 | 49.8429
|  |  | 44725.3617 | 49.8428
|  |  | 44725.3617 | 49.8428
|  |  | 44725.3617 | 49.8428
|  |  | 44725.3617 | 49.8427
|  |  | 44725.3617 | 49.8427
|  |  | 44725.3617 | 49.8427
|  |  | 44725.3617 | 49.8426
|  |  | 44725.3617 | 49.8425
|  |  | 44725.3617 | 49.8425
|  |  | 44725.3617 | 49.8424
|  |  | 44725.3617 | 49.8424
|  |  | 44725.3617 | 49.8423
|  |  | 44725.3617 | 49.8423
|  |  | 44725.3617 | 49.8423
|  |  | 44725.3617 | 49.8423
|  |  | 44725.3617 | 49.8423
|  |  | 44725.3617 | 49.8423
|  |  | 44725.3617 | 49.8422
|  |  | 44725.3617 | 49.8422
|  |  | 2022-06-13 08:41 | 49.8421
|  |  | 44725.3617 | 49.8421
|  |  | 44725.3617 | 49.842
|  |  | 44725.3617 | 49.842
|  |  | 44725.3617 | 49.8419
|  |  | 44725.3617 | 49.8418
|  |  | 44725.3617 | 49.8418
|  |  | 44725.3617 | 49.8418
|  |  | 44725.3617 | 49.8418
|  |  | 44725.3617 | 49.8417
|  |  | 44725.3617 | 49.8417
|  |  | 44725.3617 | 49.8417
|  |  | 44725.3617 | 49.8416
|  |  | 44725.3617 | 49.8415
|  |  | 44725.3617 | 49.8414
|  |  | 44725.3617 | 49.8413
|  |  | 44725.3617 | 49.8412
|  |  | 44725.3617 | 49.8411
|  |  | 44725.3617 | 49.841
|  |  | 44725.3617 | 49.8409
|  |  | 44725.3617 | 49.8408
|  |  | 44725.3617 | 49.8408
|  |  | 44725.3617 | 49.8408
|  |  | 44725.3617 | 49.8407
|  |  | 44725.3617 | 49.8406
|  |  | 44725.3617 | 49.8405
|  |  | 44725.3617 | 49.8404
|  |  | 44725.3617 | 49.8404
|  |  | 44725.3617 | 49.8404
|  |  | 44725.3617 | 49.8403
|  |  | 44725.3617 | 49.8403
|  |  | 44725.3617 | 49.8403
|  |  | 44725.3617 | 49.8403
|  |  | 44725.3617 | 49.8402
|  |  | 44725.3617 | 49.8402
|  |  | 44725.3617 | 49.8401
|  |  | 44725.3617 | 49.8401
|  |  | 44725.3617 | 49.84
|  |  | 44725.3617 | 49.8399
|  |  | 44725.3617 | 49.8398
|  |  | 44725.3617 | 49.8398
|  |  | 44725.3617 | 49.8398
|  |  | 44725.3617 | 49.8398
|  |  | 44725.3617 | 49.8398
|  |  | 44725.3617 | 49.8398
|  |  | 44725.3617 | 49.8398
|  |  | 44725.3617 | 49.8398
|  |  | 44725.3617 | 49.8399
|  |  | 44725.3617 | 49.8399
|  |  | 44725.3617 | 49.8399
|  |  | 2022-06-13 08:41 | 49.84
|  |  | 44725.3617 | 49.84
|  |  | 44725.3617 | 49.8401
|  |  | 44725.3617 | 49.8401
|  |  | 44725.3617 | 49.8401
|  |  | 44725.3617 | 49.8402
|  |  | 44725.3617 | 49.8403
|  |  | 44725.3617 | 49.8403
|  |  | 44725.3617 | 49.8404
|  |  | 44725.3617 | 49.8404
|  |  | 44725.3617 | 49.8404
|  |  | 44725.3617 | 49.8404
|  |  | 44725.3617 | 49.8404
|  |  | 44725.3617 | 49.8403
|  |  | 44725.3617 | 49.8403
|  |  | 44725.3617 | 49.8403
|  |  | 44725.3617 | 49.8402
|  |  | 44725.3617 | 49.8402
|  |  | 44725.3617 | 49.8402
|  |  | 44725.3617 | 49.8402
|  |  | 44725.3617 | 49.8402
|  |  | 44725.3617 | 49.8402
|  |  | 44725.3617 | 49.8402
|  |  | 44725.3617 | 49.8402
|  |  | 44725.3617 | 49.8402
|  |  | 44725.3617 | 49.8402
|  |  | 44725.3617 | 49.8402
|  |  | 44725.3617 | 49.8401
|  |  | 44725.3617 | 49.8401
|  |  | 44725.3617 | 49.8401
|  |  | 44725.3617 | 49.8401
|  |  | 44725.3617 | 49.84
|  |  | 44725.3617 | 49.8401
|  |  | 44725.3617 | 49.84
|  |  | 44725.3617 | 49.8399
|  |  | 44725.3617 | 49.8399
|  |  | 44725.3617 | 49.8398
|  |  | 44725.3617 | 49.8397
|  |  | 44725.3617 | 49.8397
|  |  | 44725.3617 | 49.8397
|  |  | 44725.3617 | 49.8396
|  |  | 44725.3617 | 49.8397
|  |  | 44725.3617 | 49.8396
|  |  | 44725.3617 | 49.8396
|  |  | 44725.3617 | 49.8396
|  |  | 44725.3617 | 49.8397
|  |  | 44725.3617 | 49.8398
|  |  | 44725.3617 | 49.8399
|  |  | 44725.3617 | 49.84
|  |  | 44725.3617 | 49.8401
|  |  | 2022-06-13 08:41 | 49.84
|  |  | 44725.3617 | 49.84
|  |  | 44725.3617 | 49.84
|  |  | 44725.3617 | 49.8399
|  |  | 44725.3617 | 49.84
|  |  | 44725.3617 | 49.84
|  |  | 44725.3617 | 49.84
|  |  | 44725.3617 | 49.8399
|  |  | 44725.3617 | 49.8399
|  |  | 44725.3617 | 49.8399
|  |  | 44725.3617 | 49.84
|  |  | 44725.3618 | 49.8401
|  |  | 44725.3618 | 49.8402
|  |  | 44725.3618 | 49.8402
|  |  | 44725.3618 | 49.8403
|  |  | 44725.3618 | 49.8404
|  |  | 44725.3618 | 49.8405
|  |  | 44725.3618 | 49.8405
|  |  | 44725.3618 | 49.8406
|  |  | 44725.3618 | 49.8406
|  |  | 44725.3618 | 49.8406
|  |  | 44725.3618 | 49.8406
|  |  | 44725.3618 | 49.8407
|  |  | 44725.3618 | 49.8407
|  |  | 44725.3618 | 49.8407
|  |  | 44725.3618 | 49.8408
|  |  | 44725.3618 | 49.8409
|  |  | 44725.3618 | 49.841
|  |  | 44725.3618 | 49.841
|  |  | 44725.3618 | 49.841
|  |  | 44725.3618 | 49.8411
|  |  | 44725.3618 | 49.8412
|  |  | 44725.3618 | 49.8413
|  |  | 44725.3618 | 49.8413
|  |  | 44725.3618 | 49.8413
|  |  | 44725.3618 | 49.8413
|  |  | 44725.3618 | 49.8412
|  |  | 44725.3618 | 49.8412
|  |  | 44725.3618 | 49.8411
|  |  | 44725.3618 | 49.841
|  |  | 44725.3618 | 49.8409
|  |  | 44725.3618 | 49.8409
|  |  | 44725.3618 | 49.841
|  |  | 44725.3618 | 49.8411
|  |  | 44725.3618 | 49.8411
|  |  | 44725.3618 | 49.8413
|  |  | 44725.3618 | 49.8414
|  |  | 44725.3618 | 49.8414
|  |  | 44725.3618 | 49.8415
|  |  | 44725.3618 | 49.8415
|  |  | 2022-06-13 08:41 | 49.8416
|  |  | 44725.3618 | 49.8416
|  |  | 44725.3618 | 49.8417
|  |  | 44725.3618 | 49.8417
|  |  | 44725.3618 | 49.8416
|  |  | 44725.3618 | 49.8417
|  |  | 44725.3618 | 49.8417
|  |  | 44725.3618 | 49.8417
|  |  | 44725.3618 | 49.8418
|  |  | 44725.3618 | 49.8419
|  |  | 44725.3618 | 49.8421
|  |  | 44725.3618 | 49.8422
|  |  | 44725.3618 | 49.8423
|  |  | 44725.3618 | 49.8423
|  |  | 44725.3618 | 49.8424
|  |  | 44725.3618 | 49.8424
|  |  | 44725.3618 | 49.8424
|  |  | 44725.3618 | 49.8425
|  |  | 44725.3618 | 49.8425
|  |  | 44725.3618 | 49.8425
|  |  | 44725.3618 | 49.8425
|  |  | 44725.3618 | 49.8426
|  |  | 44725.3618 | 49.8426
|  |  | 44725.3618 | 49.8427
|  |  | 44725.3618 | 49.8428
|  |  | 44725.3618 | 49.8429
|  |  | 44725.3618 | 49.843
|  |  | 44725.3618 | 49.8431
|  |  | 44725.3618 | 49.8432
|  |  | 44725.3618 | 49.8433
|  |  | 44725.3618 | 49.8434
|  |  | 44725.3618 | 49.8434
|  |  | 44725.3618 | 49.8434
|  |  | 44725.3618 | 49.8434
|  |  | 44725.3618 | 49.8434
|  |  | 44725.3618 | 49.8434
|  |  | 44725.3618 | 49.8434
|  |  | 44725.3618 | 49.8434
|  |  | 44725.3618 | 49.8435
|  |  | 44725.3618 | 49.8434
|  |  | 44725.3618 | 49.8435
|  |  | 44725.3618 | 49.8435
|  |  | 44725.3618 | 49.8435
|  |  | 44725.3618 | 49.8436
|  |  | 44725.3618 | 49.8436
|  |  | 44725.3618 | 49.8435
|  |  | 44725.3618 | 49.8435
|  |  | 44725.3618 | 49.8435
|  |  | 44725.3618 | 49.8434
|  |  | 44725.3618 | 49.8434
|  |  | 2022-06-13 08:41 | 49.8434
|  |  | 44725.3618 | 49.8435
|  |  | 44725.3618 | 49.8435
|  |  | 44725.3618 | 49.8436
|  |  | 44725.3618 | 49.8437
|  |  | 44725.3618 | 49.8438
|  |  | 44725.3618 | 49.8439
|  |  | 44725.3618 | 49.8439
|  |  | 44725.3618 | 49.844
|  |  | 44725.3618 | 49.844
|  |  | 44725.3618 | 49.8439
|  |  | 44725.3618 | 49.844
|  |  | 44725.3618 | 49.8439
|  |  | 44725.3618 | 49.8439
|  |  | 44725.3618 | 49.844
|  |  | 44725.3618 | 49.844
|  |  | 44725.3618 | 49.8441
|  |  | 44725.3618 | 49.8443
|  |  | 44725.3618 | 49.8444
|  |  | 44725.3618 | 49.8445
|  |  | 44725.3618 | 49.8447
|  |  | 44725.3618 | 49.8448
|  |  | 44725.3618 | 49.8449
|  |  | 44725.3618 | 49.8451
|  |  | 44725.3618 | 49.8452
|  |  | 44725.3618 | 49.8452
|  |  | 44725.3618 | 49.8453
|  |  | 44725.3618 | 49.8454
|  |  | 44725.3618 | 49.8454
|  |  | 44725.3618 | 49.8454
|  |  | 44725.3618 | 49.8455
|  |  | 44725.3618 | 49.8456
|  |  | 44725.3618 | 49.8457
|  |  | 44725.3618 | 49.8458
|  |  | 44725.3618 | 49.8459
|  |  | 44725.3618 | 49.8461
|  |  | 44725.3618 | 49.8462
|  |  | 44725.3618 | 49.8463
|  |  | 44725.3618 | 49.8464
|  |  | 44725.3618 | 49.8465
|  |  | 44725.3618 | 49.8465
|  |  | 44725.3618 | 49.8464
|  |  | 44725.3618 | 49.8464
|  |  | 44725.3618 | 49.8463
|  |  | 44725.3618 | 49.8463
|  |  | 44725.3618 | 49.8463
|  |  | 44725.3618 | 49.8463
|  |  | 44725.3618 | 49.8463
|  |  | 44725.3618 | 49.8463
|  |  | 44725.3618 | 49.8464
|  |  | 2022-06-13 08:41 | 49.8465
|  |  | 44725.3618 | 49.8466
|  |  | 44725.3618 | 49.8466
|  |  | 44725.3618 | 49.8468
|  |  | 44725.3618 | 49.8468
|  |  | 44725.3618 | 49.8469
|  |  | 44725.3618 | 49.847
|  |  | 44725.3618 | 49.847
|  |  | 44725.3618 | 49.8471
|  |  | 44725.3618 | 49.8472
|  |  | 44725.3618 | 49.8472
|  |  | 44725.3618 | 49.8473
|  |  | 44725.3618 | 49.8474
|  |  | 44725.3618 | 49.8474
|  |  | 44725.3618 | 49.8475
|  |  | 44725.3618 | 49.8477
|  |  | 44725.3618 | 49.8478
|  |  | 44725.3618 | 49.8479
|  |  | 44725.3618 | 49.848
|  |  | 44725.3618 | 49.8481
|  |  | 44725.3618 | 49.8482
|  |  | 44725.3618 | 49.8483
|  |  | 44725.3618 | 49.8484
|  |  | 44725.3618 | 49.8484
|  |  | 44725.3618 | 49.8485
|  |  | 44725.3618 | 49.8486
|  |  | 44725.3618 | 49.8487
|  |  | 44725.3618 | 49.8488
|  |  | 44725.3618 | 49.8489
|  |  | 44725.3618 | 49.849
|  |  | 44725.3618 | 49.8491
|  |  | 44725.3618 | 49.8493
|  |  | 44725.3618 | 49.8494
|  |  | 44725.3618 | 49.8496
|  |  | 44725.3618 | 49.8498
|  |  | 44725.3618 | 49.8499
|  |  | 44725.3618 | 49.85
|  |  | 44725.3618 | 49.8502
|  |  | 44725.3618 | 49.8503
|  |  | 44725.3618 | 49.8504
|  |  | 44725.3618 | 49.8506
|  |  | 44725.3618 | 49.8507
|  |  | 44725.3618 | 49.8509
|  |  | 44725.3618 | 49.851
|  |  | 44725.3618 | 49.8511
|  |  | 44725.3618 | 49.8513
|  |  | 44725.3618 | 49.8514
|  |  | 44725.3618 | 49.8515
|  |  | 44725.3618 | 49.8516
|  |  | 44725.3618 | 49.8518
|  |  | 2022-06-13 08:41 | 49.8519
|  |  | 44725.3618 | 49.852
|  |  | 44725.3618 | 49.8521
|  |  | 44725.3618 | 49.8522
|  |  | 44725.3618 | 49.8523
|  |  | 44725.3618 | 49.8525
|  |  | 44725.3618 | 49.8526
|  |  | 44725.3618 | 49.8527
|  |  | 44725.3618 | 49.8528
|  |  | 44725.3618 | 49.8529
|  |  | 44725.3618 | 49.853
|  |  | 44725.3618 | 49.8531
|  |  | 44725.3618 | 49.8531
|  |  | 44725.3618 | 49.8532
|  |  | 44725.3618 | 49.8532
|  |  | 44725.3618 | 49.8532
|  |  | 44725.3618 | 49.8533
|  |  | 44725.3618 | 49.8534
|  |  | 44725.3618 | 49.8534
|  |  | 44725.3618 | 49.8535
|  |  | 44725.3618 | 49.8537
|  |  | 44725.3618 | 49.8538
|  |  | 44725.3618 | 49.8539
|  |  | 44725.3618 | 49.854
|  |  | 44725.3618 | 49.8541
|  |  | 44725.3618 | 49.8542
|  |  | 44725.3618 | 49.8543
|  |  | 44725.3618 | 49.8544
|  |  | 44725.3618 | 49.8544
|  |  | 44725.3618 | 49.8544
|  |  | 44725.3618 | 49.8544
|  |  | 44725.3618 | 49.8545
|  |  | 44725.3618 | 49.8545
|  |  | 44725.3618 | 49.8545
|  |  | 44725.3618 | 49.8546
|  |  | 44725.3618 | 49.8546
|  |  | 44725.3618 | 49.8547
|  |  | 44725.3618 | 49.8548
|  |  | 44725.3618 | 49.8548
|  |  | 44725.3618 | 49.8549
|  |  | 44725.3618 | 49.855
|  |  | 44725.3618 | 49.8551
|  |  | 44725.3618 | 49.8552
|  |  | 44725.3618 | 49.8553
|  |  | 44725.3618 | 49.8553
|  |  | 44725.3618 | 49.8553
|  |  | 44725.3618 | 49.8554
|  |  | 44725.3618 | 49.8555
|  |  | 44725.3618 | 49.8556
|  |  | 44725.3618 | 49.8557
|  |  | 2022-06-13 08:41 | 49.8557
|  |  | 44725.3618 | 49.8557
|  |  | 44725.3618 | 49.8558
|  |  | 44725.3618 | 49.8558
|  |  | 44725.3618 | 49.8559
|  |  | 44725.3618 | 49.856
|  |  | 44725.3618 | 49.856
|  |  | 44725.3618 | 49.8561
|  |  | 44725.3618 | 49.8561
|  |  | 44725.3618 | 49.8561
|  |  | 44725.3618 | 49.8561
|  |  | 44725.3618 | 49.856
|  |  | 44725.3618 | 49.8561
|  |  | 44725.3618 | 49.8562
|  |  | 44725.3618 | 49.8563
|  |  | 44725.3618 | 49.8564
|  |  | 44725.3618 | 49.8566
|  |  | 44725.3618 | 49.8567
|  |  | 44725.3618 | 49.8568
|  |  | 44725.3618 | 49.857
|  |  | 44725.3618 | 49.857
|  |  | 44725.3618 | 49.8571
|  |  | 44725.3618 | 49.8571
|  |  | 44725.3618 | 49.8571
|  |  | 44725.3618 | 49.8571
|  |  | 44725.3618 | 49.8571
|  |  | 44725.3618 | 49.8571
|  |  | 44725.3618 | 49.857
|  |  | 44725.3618 | 49.857
|  |  | 44725.3618 | 49.8571
|  |  | 44725.3618 | 49.857
|  |  | 44725.3618 | 49.8571
|  |  | 44725.3618 | 49.8571
|  |  | 44725.3618 | 49.8572
|  |  | 44725.3618 | 49.8573
|  |  | 44725.3618 | 49.8573
|  |  | 44725.3618 | 49.8573
|  |  | 44725.3618 | 49.8573
|  |  | 44725.3618 | 49.8574
|  |  | 44725.3618 | 49.8574
|  |  | 44725.3618 | 49.8574
|  |  | 44725.3618 | 49.8574
|  |  | 44725.3618 | 49.8575
|  |  | 44725.3618 | 49.8575
|  |  | 44725.3618 | 49.8574
|  |  | 44725.3618 | 49.8574
|  |  | 44725.3618 | 49.8574
|  |  | 44725.3618 | 49.8574
|  |  | 44725.3618 | 49.8574
|  |  | 44725.3618 | 49.8575
|  |  | 2022-06-13 08:41 | 49.8576
|  |  | 44725.3618 | 49.8578
|  |  | 44725.3618 | 49.8578
|  |  | 44725.3618 | 49.8578
|  |  | 44725.3618 | 49.8578
|  |  | 44725.3618 | 49.8578
|  |  | 44725.3618 | 49.8578
|  |  | 44725.3618 | 49.8578
|  |  | 44725.3618 | 49.8579
|  |  | 44725.3618 | 49.8579
|  |  | 44725.3618 | 49.8579
|  |  | 44725.3618 | 49.8579
|  |  | 44725.3618 | 49.8578
|  |  | 44725.3618 | 49.8578
|  |  | 44725.3618 | 49.8579
|  |  | 44725.3618 | 49.858
|  |  | 44725.3618 | 49.8581
|  |  | 44725.3618 | 49.8582
|  |  | 44725.3618 | 49.8583
|  |  | 44725.3618 | 49.8583
|  |  | 44725.3618 | 49.8584
|  |  | 44725.3618 | 49.8584
|  |  | 44725.3618 | 49.8584
|  |  | 44725.3618 | 49.8583
|  |  | 44725.3618 | 49.8583
|  |  | 44725.3618 | 49.8583
|  |  | 44725.3618 | 49.8584
|  |  | 44725.3618 | 49.8585
|  |  | 44725.3618 | 49.8585
|  |  | 44725.3618 | 49.8585
|  |  | 44725.3618 | 49.8586
|  |  | 44725.3618 | 49.8587
|  |  | 44725.3618 | 49.8588
|  |  | 44725.3618 | 49.8588
|  |  | 44725.3618 | 49.8588
|  |  | 44725.3618 | 49.8588
|  |  | 44725.3618 | 49.8587
|  |  | 44725.3618 | 49.8587
|  |  | 44725.3618 | 49.8586
|  |  | 44725.3618 | 49.8587
|  |  | 44725.3618 | 49.8587
|  |  | 44725.3618 | 49.8586
|  |  | 44725.3618 | 49.8586
|  |  | 44725.3618 | 49.8586
|  |  | 44725.3618 | 49.8586
|  |  | 44725.3618 | 49.8585
|  |  | 44725.3618 | 49.8584
|  |  | 44725.3618 | 49.8585
|  |  | 44725.3618 | 49.8585
|  |  | 44725.3618 | 49.8585
|  |  | 2022-06-13 08:41 | 49.8586
|  |  | 44725.3618 | 49.8586
|  |  | 44725.3618 | 49.8586
|  |  | 44725.3618 | 49.8586
|  |  | 44725.3618 | 49.8586
|  |  | 44725.3618 | 49.8586
|  |  | 44725.3618 | 49.8587
|  |  | 44725.3618 | 49.8587
|  |  | 44725.3618 | 49.8587
|  |  | 44725.3618 | 49.8586
|  |  | 44725.3618 | 49.8586
|  |  | 44725.3618 | 49.8586
|  |  | 44725.3618 | 49.8585
|  |  | 44725.3618 | 49.8585
|  |  | 44725.3618 | 49.8585
|  |  | 44725.3618 | 49.8585
|  |  | 44725.3618 | 49.8587
|  |  | 44725.3618 | 49.8587
|  |  | 44725.3618 | 49.8588
|  |  | 44725.3618 | 49.8589
|  |  | 44725.3618 | 49.859
|  |  | 44725.3618 | 49.8591
|  |  | 44725.3618 | 49.8592
|  |  | 44725.3618 | 49.8592
|  |  | 44725.3618 | 49.8593
|  |  | 44725.3618 | 49.8593
|  |  | 44725.3618 | 49.8593
|  |  | 44725.3618 | 49.8594
|  |  | 44725.3618 | 49.8594
|  |  | 44725.3618 | 49.8593
|  |  | 44725.3618 | 49.8593
|  |  | 44725.3618 | 49.8592
|  |  | 44725.3618 | 49.8592
|  |  | 44725.3618 | 49.8592
|  |  | 44725.3618 | 49.8592
|  |  | 44725.3618 | 49.8592
|  |  | 44725.3618 | 49.8591
|  |  | 44725.3618 | 49.8591
|  |  | 44725.3618 | 49.8592
|  |  | 44725.3618 | 49.8593
|  |  | 44725.3618 | 49.8593
|  |  | 44725.3618 | 49.8594
|  |  | 44725.3618 | 49.8595
|  |  | 44725.3618 | 49.8595
|  |  | 44725.3618 | 49.8596
|  |  | 44725.3618 | 49.8596
|  |  | 44725.3618 | 49.8597
|  |  | 44725.3618 | 49.8598
|  |  | 44725.3618 | 49.8597
|  |  | 44725.3618 | 49.8596
|  |  | 2022-06-13 08:41 | 49.8596
|  |  | 44725.3618 | 49.8595
|  |  | 44725.3618 | 49.8595
|  |  | 44725.3618 | 49.8594
|  |  | 44725.3618 | 49.8594
|  |  | 44725.3618 | 49.8593
|  |  | 44725.3618 | 49.8593
|  |  | 44725.3618 | 49.8593
|  |  | 44725.3618 | 49.8593
|  |  | 44725.3618 | 49.8594
|  |  | 44725.3618 | 49.8595
|  |  | 44725.3618 | 49.8595
|  |  | 44725.3618 | 49.8596
|  |  | 44725.3618 | 49.8596
|  |  | 44725.3618 | 49.8597
|  |  | 44725.3618 | 49.8598
|  |  | 44725.3618 | 49.8597
|  |  | 44725.3618 | 49.8597
|  |  | 44725.3618 | 49.8596
|  |  | 44725.3618 | 49.8596
|  |  | 44725.3618 | 49.8596
|  |  | 44725.3618 | 49.8596
|  |  | 44725.3618 | 49.8596
|  |  | 44725.3618 | 49.8596
|  |  | 44725.3618 | 49.8596
|  |  | 44725.3618 | 49.8596
|  |  | 44725.3618 | 49.8596
|  |  | 44725.3618 | 49.8596
|  |  | 44725.3618 | 49.8596
|  |  | 44725.3618 | 49.8596
|  |  | 44725.3618 | 49.8597
|  |  | 44725.3618 | 49.8598
|  |  | 44725.3618 | 49.8599
|  |  | 44725.3618 | 49.8599
|  |  | 44725.3618 | 49.86
|  |  | 44725.3618 | 49.8601
|  |  | 44725.3618 | 49.8601
|  |  | 44725.3618 | 49.8602
|  |  | 44725.3618 | 49.8602
|  |  | 44725.3618 | 49.8603
|  |  | 44725.3618 | 49.8603
|  |  | 44725.3618 | 49.8604
|  |  | 44725.3619 | 49.8604
|  |  | 44725.3619 | 49.8604
|  |  | 44725.3619 | 49.8604
|  |  | 44725.3619 | 49.8604
|  |  | 44725.3619 | 49.8603
|  |  | 44725.3619 | 49.8603
|  |  | 44725.3619 | 49.8602
|  |  | 44725.3619 | 49.8602
|  |  | 2022-06-13 08:41 | 49.8602
|  |  | 44725.3619 | 49.8601
|  |  | 44725.3619 | 49.8601
|  |  | 44725.3619 | 49.8602
|  |  | 44725.3619 | 49.8602
|  |  | 44725.3619 | 49.8603
|  |  | 44725.3619 | 49.8603
|  |  | 44725.3619 | 49.8604
|  |  | 44725.3619 | 49.8604
|  |  | 44725.3619 | 49.8604
|  |  | 44725.3619 | 49.8605
|  |  | 44725.3619 | 49.8605
|  |  | 44725.3619 | 49.8604
|  |  | 44725.3619 | 49.8604
|  |  | 44725.3619 | 49.8604
|  |  | 44725.3619 | 49.8605
|  |  | 44725.3619 | 49.8605
|  |  | 44725.3619 | 49.8605
|  |  | 44725.3619 | 49.8605
|  |  | 44725.3619 | 49.8606
|  |  | 44725.3619 | 49.8605
|  |  | 44725.3619 | 49.8605
|  |  | 44725.3619 | 49.8605
|  |  | 44725.3619 | 49.8605
|  |  | 44725.3619 | 49.8605
|  |  | 44725.3619 | 49.8605
|  |  | 44725.3619 | 49.8605
|  |  | 44725.3619 | 49.8606
|  |  | 44725.3619 | 49.8606
|  |  | 44725.3619 | 49.8606
|  |  | 44725.3619 | 49.8607
|  |  | 44725.3619 | 49.8607
|  |  | 44725.3619 | 49.8607
|  |  | 44725.3619 | 49.8607
|  |  | 44725.3619 | 49.8607
|  |  | 44725.3619 | 49.8606
|  |  | 44725.3619 | 49.8606
|  |  | 44725.3619 | 49.8606
|  |  | 44725.3619 | 49.8606
|  |  | 44725.3619 | 49.8605
|  |  | 44725.3619 | 49.8604
|  |  | 44725.3619 | 49.8603
|  |  | 44725.3619 | 49.8602
|  |  | 44725.3619 | 49.8601
|  |  | 44725.3619 | 49.86
|  |  | 44725.3619 | 49.86
|  |  | 44725.3619 | 49.8599
|  |  | 44725.3619 | 49.8598
|  |  | 44725.3619 | 49.8597
|  |  | 44725.3619 | 49.8597
|  |  | 2022-06-13 08:41 | 49.8596
|  |  | 44725.3619 | 49.8595
|  |  | 44725.3619 | 49.8595
|  |  | 44725.3619 | 49.8594
|  |  | 44725.3619 | 49.8593
|  |  | 44725.3619 | 49.8594
|  |  | 44725.3619 | 49.8593
|  |  | 44725.3619 | 49.8593
|  |  | 44725.3619 | 49.8591
|  |  | 44725.3619 | 49.8592
|  |  | 44725.3619 | 49.8591
|  |  | 44725.3619 | 49.8591
|  |  | 44725.3619 | 49.859
|  |  | 44725.3619 | 49.8589
|  |  | 44725.3619 | 49.8589
|  |  | 44725.3619 | 49.8588
|  |  | 44725.3619 | 49.8587
|  |  | 44725.3619 | 49.8586
|  |  | 44725.3619 | 49.8585
|  |  | 44725.3619 | 49.8584
|  |  | 44725.3619 | 49.8584
|  |  | 44725.3619 | 49.8584
|  |  | 44725.3619 | 49.8584
|  |  | 44725.3619 | 49.8584
|  |  | 44725.3619 | 49.8583
|  |  | 44725.3619 | 49.8583
|  |  | 44725.3619 | 49.8583
|  |  | 44725.3619 | 49.8583
|  |  | 44725.3619 | 49.8583
|  |  | 44725.3619 | 49.8582
|  |  | 44725.3619 | 49.8582
|  |  | 44725.3619 | 49.8581
|  |  | 44725.3619 | 49.858
|  |  | 44725.3619 | 49.8579
|  |  | 44725.3619 | 49.8578
|  |  | 44725.3619 | 49.8577
|  |  | 44725.3619 | 49.8577
|  |  | 44725.3619 | 49.8577
|  |  | 44725.3619 | 49.8577
|  |  | 44725.3619 | 49.8577
|  |  | 44725.3619 | 49.8577
|  |  | 44725.3619 | 49.8577
|  |  | 44725.3619 | 49.8576
|  |  | 44725.3619 | 49.8576
|  |  | 44725.3619 | 49.8575
|  |  | 44725.3619 | 49.8574
|  |  | 44725.3619 | 49.8573
|  |  | 44725.3619 | 49.8572
|  |  | 44725.3619 | 49.8572
|  |  | 44725.3619 | 49.8571
|  |  | 2022-06-13 08:41 | 49.857
|  |  | 44725.3619 | 49.8569
|  |  | 44725.3619 | 49.8568
|  |  | 44725.3619 | 49.8568
|  |  | 44725.3619 | 49.8567
|  |  | 44725.3619 | 49.8567
|  |  | 44725.3619 | 49.8566
|  |  | 44725.3619 | 49.8566
|  |  | 44725.3619 | 49.8566
|  |  | 44725.3619 | 49.8565
|  |  | 44725.3619 | 49.8565
|  |  | 44725.3619 | 49.8565
|  |  | 44725.3619 | 49.8564
|  |  | 44725.3619 | 49.8564
|  |  | 44725.3619 | 49.8563
|  |  | 44725.3619 | 49.8562
|  |  | 44725.3619 | 49.8561
|  |  | 44725.3619 | 49.8561
|  |  | 44725.3619 | 49.856
|  |  | 44725.3619 | 49.8559
|  |  | 44725.3619 | 49.8559
|  |  | 44725.3619 | 49.8557
|  |  | 44725.3619 | 49.8557
|  |  | 44725.3619 | 49.8557
|  |  | 44725.3619 | 49.8556
|  |  | 44725.3619 | 49.8555
|  |  | 44725.3619 | 49.8554
|  |  | 44725.3619 | 49.8553
|  |  | 44725.3619 | 49.8552
|  |  | 44725.3619 | 49.8551
|  |  | 44725.3619 | 49.8551
|  |  | 44725.3619 | 49.8551
|  |  | 44725.3619 | 49.8551
|  |  | 44725.3619 | 49.8551
|  |  | 44725.3619 | 49.8551
|  |  | 44725.3619 | 49.855
|  |  | 44725.3619 | 49.8549
|  |  | 44725.3619 | 49.8548
|  |  | 44725.3619 | 49.8547
|  |  | 44725.3619 | 49.8547
|  |  | 44725.3619 | 49.8546
|  |  | 44725.3619 | 49.8545
|  |  | 44725.3619 | 49.8544
|  |  | 44725.3619 | 49.8543
|  |  | 44725.3619 | 49.8543
|  |  | 44725.3619 | 49.8542
|  |  | 44725.3619 | 49.8541
|  |  | 44725.3619 | 49.8541
|  |  | 44725.3619 | 49.854
|  |  | 44725.3619 | 49.854
|  |  | 2022-06-13 08:41 | 49.8541
|  |  | 44725.3619 | 49.8541
|  |  | 44725.3619 | 49.8541
|  |  | 44725.3619 | 49.854
|  |  | 44725.3619 | 49.8539
|  |  | 44725.3619 | 49.8538
|  |  | 44725.3619 | 49.8537
|  |  | 44725.3619 | 49.8537
|  |  | 44725.3619 | 49.8536
|  |  | 44725.3619 | 49.8535
|  |  | 44725.3619 | 49.8534
|  |  | 44725.3619 | 49.8533
|  |  | 44725.3619 | 49.8532
|  |  | 44725.3619 | 49.8531
|  |  | 44725.3619 | 49.8531
|  |  | 44725.3619 | 49.853
|  |  | 44725.3619 | 49.8529
|  |  | 44725.3619 | 49.8529
|  |  | 44725.3619 | 49.8528
|  |  | 44725.3619 | 49.8527
|  |  | 44725.3619 | 49.8526
|  |  | 44725.3619 | 49.8525
|  |  | 44725.3619 | 49.8525
|  |  | 44725.3619 | 49.8524
|  |  | 44725.3619 | 49.8524
|  |  | 44725.3619 | 49.8523
|  |  | 44725.3619 | 49.8523
|  |  | 44725.3619 | 49.8522
|  |  | 44725.3619 | 49.8521
|  |  | 44725.3619 | 49.852
|  |  | 44725.3619 | 49.8519
|  |  | 44725.3619 | 49.8517
|  |  | 44725.3619 | 49.8516
|  |  | 44725.3619 | 49.8515
|  |  | 44725.3619 | 49.8514
|  |  | 44725.3619 | 49.8514
|  |  | 44725.3619 | 49.8513
|  |  | 44725.3619 | 49.8513
|  |  | 44725.3619 | 49.8513
|  |  | 44725.3619 | 49.8513
|  |  | 44725.3619 | 49.8512
|  |  | 44725.3619 | 49.8512
|  |  | 44725.3619 | 49.8512
|  |  | 44725.3619 | 49.8512
|  |  | 44725.3619 | 49.8511
|  |  | 44725.3619 | 49.851
|  |  | 44725.3619 | 49.8509
|  |  | 44725.3619 | 49.8509
|  |  | 44725.3619 | 49.8508
|  |  | 44725.3619 | 49.8508
|  |  | 2022-06-13 08:41 | 49.8507
|  |  | 44725.3619 | 49.8507
|  |  | 44725.3619 | 49.8507
|  |  | 44725.3619 | 49.8507
|  |  | 44725.3619 | 49.8507
|  |  | 44725.3619 | 49.8506
|  |  | 44725.3619 | 49.8506
|  |  | 44725.3619 | 49.8505
|  |  | 44725.3619 | 49.8504
|  |  | 44725.3619 | 49.8503
|  |  | 44725.3619 | 49.8502
|  |  | 44725.3619 | 49.8502
|  |  | 44725.3619 | 49.8501
|  |  | 44725.3619 | 49.8501
|  |  | 44725.3619 | 49.85
|  |  | 44725.3619 | 49.8501
|  |  | 44725.3619 | 49.8501
|  |  | 44725.3619 | 49.8502
|  |  | 44725.3619 | 49.8502
|  |  | 44725.3619 | 49.8503
|  |  | 44725.3619 | 49.8503
|  |  | 44725.3619 | 49.8503
|  |  | 44725.3619 | 49.8503
|  |  | 44725.3619 | 49.8503
|  |  | 44725.3619 | 49.8502
|  |  | 44725.3619 | 49.8502
|  |  | 44725.3619 | 49.8501
|  |  | 44725.3619 | 49.8501
|  |  | 44725.3619 | 49.8501
|  |  | 44725.3619 | 49.8501
|  |  | 44725.3619 | 49.8502
|  |  | 44725.3619 | 49.8502
|  |  | 44725.3619 | 49.8502
|  |  | 44725.3619 | 49.8502
|  |  | 44725.3619 | 49.8502
|  |  | 44725.3619 | 49.8501
|  |  | 44725.3619 | 49.8501
|  |  | 44725.3619 | 49.85
|  |  | 44725.3619 | 49.8499
|  |  | 44725.3619 | 49.8498
|  |  | 44725.3619 | 49.8497
|  |  | 44725.3619 | 49.8496
|  |  | 44725.3619 | 49.8495
|  |  | 44725.3619 | 49.8495
|  |  | 44725.3619 | 49.8494
|  |  | 44725.3619 | 49.8493
|  |  | 44725.3619 | 49.8493
|  |  | 44725.3619 | 49.8493
|  |  | 44725.3619 | 49.8493
|  |  | 44725.3619 | 49.8492
|  |  | 2022-06-13 08:41 | 49.8491
|  |  | 44725.3619 | 49.8491
|  |  | 44725.3619 | 49.849
|  |  | 44725.3619 | 49.8489
|  |  | 44725.3619 | 49.8489
|  |  | 44725.3619 | 49.8488
|  |  | 44725.3619 | 49.8487
|  |  | 44725.3619 | 49.8486
|  |  | 44725.3619 | 49.8485
|  |  | 44725.3619 | 49.8485
|  |  | 44725.3619 | 49.8484
|  |  | 44725.3619 | 49.8483
|  |  | 44725.3619 | 49.8483
|  |  | 44725.3619 | 49.8482
|  |  | 44725.3619 | 49.8482
|  |  | 44725.3619 | 49.8481
|  |  | 44725.3619 | 49.848
|  |  | 44725.3619 | 49.8479
|  |  | 44725.3619 | 49.8478
|  |  | 44725.3619 | 49.8477
|  |  | 44725.3619 | 49.8476
|  |  | 44725.3619 | 49.8475
|  |  | 44725.3619 | 49.8474
|  |  | 44725.3619 | 49.8474
|  |  | 44725.3619 | 49.8473
|  |  | 44725.3619 | 49.8472
|  |  | 44725.3619 | 49.8472
|  |  | 44725.3619 | 49.8472
|  |  | 44725.3619 | 49.8472
|  |  | 44725.3619 | 49.8471
|  |  | 44725.3619 | 49.8471
|  |  | 44725.3619 | 49.847
|  |  | 44725.3619 | 49.8469
|  |  | 44725.3619 | 49.8469
|  |  | 44725.3619 | 49.8468
|  |  | 44725.3619 | 49.8467
|  |  | 44725.3619 | 49.8467
|  |  | 44725.3619 | 49.8466
|  |  | 44725.3619 | 49.8465
|  |  | 44725.3619 | 49.8464
|  |  | 44725.3619 | 49.8464
|  |  | 44725.3619 | 49.8463
|  |  | 44725.3619 | 49.8462
|  |  | 44725.3619 | 49.8461
|  |  | 44725.3619 | 49.8461
|  |  | 44725.3619 | 49.8461
|  |  | 44725.3619 | 49.8461
|  |  | 44725.3619 | 49.8461
|  |  | 44725.3619 | 49.8461
|  |  | 44725.3619 | 49.8461
|  |  | 2022-06-13 08:41 | 49.8461
|  |  | 44725.3619 | 49.8461
|  |  | 44725.3619 | 49.8461
|  |  | 44725.3619 | 49.8461
|  |  | 44725.3619 | 49.8461
|  |  | 44725.3619 | 49.846
|  |  | 44725.3619 | 49.846
|  |  | 44725.3619 | 49.8459
|  |  | 44725.3619 | 49.8459
|  |  | 44725.3619 | 49.8459
|  |  | 44725.3619 | 49.846
|  |  | 44725.3619 | 49.846
|  |  | 44725.3619 | 49.846
|  |  | 44725.3619 | 49.8459
|  |  | 44725.3619 | 49.8459
|  |  | 44725.3619 | 49.8459
|  |  | 44725.3619 | 49.8459
|  |  | 44725.3619 | 49.8459
|  |  | 44725.3619 | 49.8458
|  |  | 44725.3619 | 49.8458
|  |  | 44725.3619 | 49.8457
|  |  | 44725.3619 | 49.8456
|  |  | 44725.3619 | 49.8456
|  |  | 44725.3619 | 49.8456
|  |  | 44725.3619 | 49.8455
|  |  | 44725.3619 | 49.8455
|  |  | 44725.3619 | 49.8455
|  |  | 44725.3619 | 49.8455
|  |  | 44725.3619 | 49.8455
|  |  | 44725.3619 | 49.8457
|  |  | 44725.3619 | 49.8457
|  |  | 44725.3619 | 49.8458
|  |  | 44725.3619 | 49.8458
|  |  | 44725.3619 | 49.8459
|  |  | 44725.3619 | 49.846
|  |  | 44725.3619 | 49.8462
|  |  | 44725.3619 | 49.8463
|  |  | 44725.3619 | 49.8463
|  |  | 44725.3619 | 49.8463
|  |  | 44725.3619 | 49.8463
|  |  | 44725.3619 | 49.8463
|  |  | 44725.3619 | 49.8463
|  |  | 44725.3619 | 49.8463
|  |  | 44725.3619 | 49.8463
|  |  | 44725.3619 | 49.8463
|  |  | 44725.3619 | 49.8464
|  |  | 44725.3619 | 49.8464
|  |  | 44725.3619 | 49.8464
|  |  | 44725.3619 | 49.8464
|  |  | 44725.3619 | 49.8465
|  |  | 2022-06-13 08:41 | 49.8466
|  |  | 44725.3619 | 49.8466
|  |  | 44725.3619 | 49.8467
|  |  | 44725.3619 | 49.8468
|  |  | 44725.3619 | 49.847
|  |  | 44725.3619 | 49.847
|  |  | 44725.3619 | 49.8471
|  |  | 44725.3619 | 49.8471
|  |  | 44725.3619 | 49.847
|  |  | 44725.3619 | 49.8469
|  |  | 44725.3619 | 49.8468
|  |  | 44725.3619 | 49.8467
|  |  | 44725.3619 | 49.8467
|  |  | 44725.3619 | 49.8467
|  |  | 44725.3619 | 49.8467
|  |  | 44725.3619 | 49.8467
|  |  | 44725.3619 | 49.8468
|  |  | 44725.3619 | 49.8468
|  |  | 44725.3619 | 49.8469
|  |  | 44725.3619 | 49.8468
|  |  | 44725.3619 | 49.8468
|  |  | 44725.3619 | 49.8468
|  |  | 44725.3619 | 49.8468
|  |  | 44725.3619 | 49.8468
|  |  | 44725.3619 | 49.8468
|  |  | 44725.3619 | 49.8468
|  |  | 44725.3619 | 49.8468
|  |  | 44725.3619 | 49.8467
|  |  | 44725.3619 | 49.8467
|  |  | 44725.3619 | 49.8467
|  |  | 44725.3619 | 49.8466
|  |  | 44725.3619 | 49.8466
|  |  | 44725.3619 | 49.8466
|  |  | 44725.3619 | 49.8466
|  |  | 44725.3619 | 49.8466
|  |  | 44725.3619 | 49.8465
|  |  | 44725.3619 | 49.8465
|  |  | 44725.3619 | 49.8465
|  |  | 44725.3619 | 49.8465
|  |  | 44725.3619 | 49.8464
|  |  | 44725.3619 | 49.8464
|  |  | 44725.3619 | 49.8465
|  |  | 44725.3619 | 49.8465
|  |  | 44725.3619 | 49.8465
|  |  | 44725.3619 | 49.8465
|  |  | 44725.3619 | 49.8465
|  |  | 44725.3619 | 49.8465
|  |  | 44725.3619 | 49.8465
|  |  | 44725.3619 | 49.8465
|  |  | 44725.3619 | 49.8465
|  |  | 2022-06-13 08:41 | 49.8465
|  |  | 44725.3619 | 49.8465
|  |  | 44725.3619 | 49.8466
|  |  | 44725.3619 | 49.8466
|  |  | 44725.3619 | 49.8466
|  |  | 44725.3619 | 49.8466
|  |  | 44725.3619 | 49.8466
|  |  | 44725.3619 | 49.8467
|  |  | 44725.3619 | 49.8467
|  |  | 44725.3619 | 49.8467
|  |  | 44725.3619 | 49.8467
|  |  | 44725.3619 | 49.8467
|  |  | 44725.3619 | 49.8467
|  |  | 44725.3619 | 49.8468
|  |  | 44725.3619 | 49.8468
|  |  | 44725.3619 | 49.8468
|  |  | 44725.3619 | 49.8469
|  |  | 44725.3619 | 49.8469
|  |  | 44725.3619 | 49.8469
|  |  | 44725.3619 | 49.847
|  |  | 44725.3619 | 49.847
|  |  | 44725.3619 | 49.847
|  |  | 44725.3619 | 49.8471
|  |  | 44725.3619 | 49.8471
|  |  | 44725.3619 | 49.8471
|  |  | 44725.362 | 49.8471
|  |  | 44725.362 | 49.8471
|  |  | 44725.362 | 49.8472
|  |  | 44725.362 | 49.8472
|  |  | 44725.362 | 49.8472
|  |  | 44725.362 | 49.8472
|  |  | 44725.362 | 49.8473
|  |  | 44725.362 | 49.8473
|  |  | 44725.362 | 49.8473
|  |  | 44725.362 | 49.8473
|  |  | 44725.362 | 49.8473
|  |  | 44725.362 | 49.8473
|  |  | 44725.362 | 49.8472
|  |  | 44725.362 | 49.8472
|  |  | 44725.362 | 49.8472
|  |  | 44725.362 | 49.8472
|  |  | 44725.362 | 49.8472
|  |  | 44725.362 | 49.8471
|  |  | 44725.362 | 49.8471
|  |  | 44725.362 | 49.847
|  |  | 44725.362 | 49.847
|  |  | 44725.362 | 49.8471
|  |  | 44725.362 | 49.8471
|  |  | 44725.362 | 49.8471
|  |  | 44725.362 | 49.8471
|  |  | 2022-06-13 08:41 | 49.8471
|  |  | 44725.362 | 49.8472
|  |  | 44725.362 | 49.8473
|  |  | 44725.362 | 49.8473
|  |  | 44725.362 | 49.8474
|  |  | 44725.362 | 49.8474
|  |  | 44725.362 | 49.8474
|  |  | 44725.362 | 49.8474
|  |  | 44725.362 | 49.8474
|  |  | 44725.362 | 49.8473
|  |  | 44725.362 | 49.8473
|  |  | 44725.362 | 49.8472
|  |  | 44725.362 | 49.8471
|  |  | 44725.362 | 49.8471
|  |  | 44725.362 | 49.8471
|  |  | 44725.362 | 49.847
|  |  | 44725.362 | 49.847
|  |  | 44725.362 | 49.8471
|  |  | 44725.362 | 49.8472
|  |  | 44725.362 | 49.8472
|  |  | 44725.362 | 49.8472
|  |  | 44725.362 | 49.8473
|  |  | 44725.362 | 49.8474
|  |  | 44725.362 | 49.8474
|  |  | 44725.362 | 49.8475
|  |  | 44725.362 | 49.8475
|  |  | 44725.362 | 49.8475
|  |  | 44725.362 | 49.8475
|  |  | 44725.362 | 49.8475
|  |  | 44725.362 | 49.8475
|  |  | 44725.362 | 49.8476
|  |  | 44725.362 | 49.8476
|  |  | 44725.362 | 49.8476
|  |  | 44725.362 | 49.8476
|  |  | 44725.362 | 49.8476
|  |  | 44725.362 | 49.8476
|  |  | 44725.362 | 49.8477
|  |  | 44725.362 | 49.8477
|  |  | 44725.362 | 49.8476
|  |  | 44725.362 | 49.8476
|  |  | 44725.362 | 49.8476
|  |  | 44725.362 | 49.8476
|  |  | 44725.362 | 49.8475
|  |  | 44725.362 | 49.8476
|  |  | 44725.362 | 49.8475
|  |  | 44725.362 | 49.8475
|  |  | 44725.362 | 49.8475
|  |  | 44725.362 | 49.8475
|  |  | 44725.362 | 49.8475
|  |  | 44725.362 | 49.8475
|  |  | 2022-06-13 08:41 | 49.8475
|  |  | 44725.362 | 49.8474
|  |  | 44725.362 | 49.8474
|  |  | 44725.362 | 49.8473
|  |  | 44725.362 | 49.8473
|  |  | 44725.362 | 49.8473
|  |  | 44725.362 | 49.8473
|  |  | 44725.362 | 49.8474
|  |  | 44725.362 | 49.8474
|  |  | 44725.362 | 49.8474
|  |  | 44725.362 | 49.8474
|  |  | 44725.362 | 49.8474
|  |  | 44725.362 | 49.8474
|  |  | 44725.362 | 49.8474
|  |  | 44725.362 | 49.8474
|  |  | 44725.362 | 49.8474
|  |  | 44725.362 | 49.8474
|  |  | 44725.362 | 49.8474
|  |  | 44725.362 | 49.8475
|  |  | 44725.362 | 49.8475
|  |  | 44725.362 | 49.8475
|  |  | 44725.362 | 49.8476
|  |  | 44725.362 | 49.8476
|  |  | 44725.362 | 49.8477
|  |  | 44725.362 | 49.8477
|  |  | 44725.362 | 49.8478
|  |  | 44725.362 | 49.8478
|  |  | 44725.362 | 49.8479
|  |  | 44725.362 | 49.8479
|  |  | 44725.362 | 49.8479
|  |  | 44725.362 | 49.8479
|  |  | 44725.362 | 49.8479
|  |  | 44725.362 | 49.8479
|  |  | 44725.362 | 49.8479
|  |  | 44725.362 | 49.848
|  |  | 44725.362 | 49.8481
|  |  | 44725.362 | 49.8481
|  |  | 44725.362 | 49.8482
|  |  | 44725.362 | 49.8483
|  |  | 44725.362 | 49.8484
|  |  | 44725.362 | 49.8485
|  |  | 44725.362 | 49.8487
|  |  | 44725.362 | 49.8488
|  |  | 44725.362 | 49.8488
|  |  | 44725.362 | 49.8489
|  |  | 44725.362 | 49.8489
|  |  | 44725.362 | 49.8489
|  |  | 44725.362 | 49.8489
|  |  | 44725.362 | 49.8489
|  |  | 44725.362 | 49.8489
|  |  | 2022-06-13 08:41 | 49.8489

## 20220617-1
In GMT |  |  | High resolution Incident data
Date | Time | Freq | time | freq
2022-06-17 | 12:56 | 50.033 | 2022-06-17 13:57 | 50.0457
2022-06-17 | 12:56 | 50.033 | 44729.5809 | 50.0458
2022-06-17 | 12:56 | 50.038 | 44729.5809 | 50.0458
2022-06-17 | 12:56 | 50.037 | 44729.5809 | 50.0459
2022-06-17 | 12:56 | 50.035 | 44729.5809 | 50.0459
2022-06-17 | 12:56 | 50.035 | 44729.5809 | 50.046
2022-06-17 | 12:56 | 50.03 | 44729.5809 | 50.046
2022-06-17 | 12:56 | 50.03 | 44729.5809 | 50.0459
2022-06-17 | 12:56 | 50.034 | 44729.5809 | 50.046
2022-06-17 | 12:56 | 50.036 | 44729.5809 | 50.0459
2022-06-17 | 12:56 | 50.037 | 44729.5809 | 50.0459
2022-06-17 | 12:56 | 50.039 | 44729.5809 | 50.0458
2022-06-17 | 12:56 | 50.04 | 44729.5809 | 50.0458
2022-06-17 | 12:56 | 50.037 | 44729.5809 | 50.0457
2022-06-17 | 12:56 | 50.037 | 44729.5809 | 50.0457
2022-06-17 | 12:56 | 50.035 | 44729.5809 | 50.0458
2022-06-17 | 12:56 | 50.036 | 44729.5809 | 50.0458
2022-06-17 | 12:56 | 50.037 | 44729.5809 | 50.0458
2022-06-17 | 12:56 | 50.041 | 44729.5809 | 50.0458
2022-06-17 | 12:56 | 50.041 | 44729.5809 | 50.0459
2022-06-17 | 12:56 | 50.045 | 44729.5809 | 50.0459
2022-06-17 | 12:56 | 50.046 | 44729.5809 | 50.0459
2022-06-17 | 12:56 | 50.049 | 44729.5809 | 50.046
2022-06-17 | 12:56 | 50.052 | 44729.5809 | 50.0461
2022-06-17 | 12:56 | 50.052 | 44729.5809 | 50.0461
2022-06-17 | 12:56 | 50.049 | 44729.5809 | 50.0461
2022-06-17 | 12:56 | 50.047 | 44729.5809 | 50.046
2022-06-17 | 12:56 | 50.046 | 44729.5809 | 50.046
2022-06-17 | 12:56 | 50.044 | 44729.5809 | 50.046
2022-06-17 | 12:56 | 50.046 | 44729.5809 | 50.046
2022-06-17 | 12:56 | 50.045 | 44729.5809 | 50.046
2022-06-17 | 12:57 | 50.046 | 44729.5809 | 50.0459
2022-06-17 | 12:57 | 50.047 | 44729.5809 | 50.0459
2022-06-17 | 12:57 | 50.046 | 44729.5809 | 50.0459
2022-06-17 | 12:57 | 50.045 | 44729.5809 | 50.046
2022-06-17 | 12:57 | 50.039 | 44729.5809 | 50.046
2022-06-17 | 12:57 | 50.037 | 44729.5809 | 50.0461
2022-06-17 | 12:57 | 50.033 | 44729.5809 | 50.0461
2022-06-17 | 12:57 | 50.031 | 44729.5809 | 50.0461
2022-06-17 | 12:57 | 50.029 | 44729.5809 | 50.0461
2022-06-17 | 12:57 | 50.03 | 44729.5809 | 50.0461
2022-06-17 | 12:57 | 50.032 | 44729.5809 | 50.046
2022-06-17 | 12:57 | 50.033 | 44729.5809 | 50.046
2022-06-17 | 12:57 | 50.035 | 44729.5809 | 50.0459
2022-06-17 | 12:57 | 50.034 | 44729.5809 | 50.0459
2022-06-17 | 12:57 | 50.033 | 44729.5809 | 50.046
2022-06-17 | 12:57 | 50.034 | 44729.5809 | 50.046
2022-06-17 | 12:57 | 50.034 | 44729.5809 | 50.0461
2022-06-17 | 12:57 | 50.032 | 44729.5809 | 50.0462
2022-06-17 | 12:57 | 50.031 | 44729.5809 | 50.0463
2022-06-17 | 12:57 | 50.033 | 2022-06-17 13:57 | 50.0463
2022-06-17 | 12:57 | 50.031 | 44729.5809 | 50.0463
2022-06-17 | 12:57 | 50.028 | 44729.5809 | 50.0464
2022-06-17 | 12:57 | 50.028 | 44729.5809 | 50.0464
2022-06-17 | 12:57 | 50.031 | 44729.5809 | 50.0464
2022-06-17 | 12:57 | 50.029 | 44729.5809 | 50.0464
2022-06-17 | 12:57 | 49.978 | 44729.5809 | 50.0463
2022-06-17 | 12:57 | 49.92 | 44729.5809 | 50.0463
2022-06-17 | 12:57 | 49.874 | 44729.5809 | 50.0463
2022-06-17 | 12:57 | 49.835 | 44729.5809 | 50.0463
2022-06-17 | 12:57 | 49.794 | 44729.5809 | 50.0463
2022-06-17 | 12:57 | 49.767 | 44729.5809 | 50.0464
2022-06-17 | 12:57 | 49.761 | 44729.5809 | 50.0464
2022-06-17 | 12:57 | 49.761 | 44729.5809 | 50.0465
2022-06-17 | 12:57 | 49.759 | 44729.5809 | 50.0466
2022-06-17 | 12:57 | 49.757 | 44729.5809 | 50.0467
2022-06-17 | 12:57 | 49.759 | 44729.5809 | 50.0469
2022-06-17 | 12:57 | 49.759 | 44729.5809 | 50.047
2022-06-17 | 12:57 | 49.755 | 44729.5809 | 50.0471
2022-06-17 | 12:57 | 49.753 | 44729.5809 | 50.0472
2022-06-17 | 12:57 | 49.75 | 44729.5809 | 50.0473
2022-06-17 | 12:57 | 49.748 | 44729.5809 | 50.0474
2022-06-17 | 12:57 | 49.748 | 44729.5809 | 50.0475
2022-06-17 | 12:57 | 49.752 | 44729.5809 | 50.0475
2022-06-17 | 12:57 | 49.755 | 44729.5809 | 50.0475
2022-06-17 | 12:57 | 49.757 | 44729.5809 | 50.0475
2022-06-17 | 12:57 | 49.759 | 44729.5809 | 50.0474
2022-06-17 | 12:57 | 49.757 | 44729.5809 | 50.0474
2022-06-17 | 12:57 | 49.757 | 44729.5809 | 50.0473
2022-06-17 | 12:57 | 49.759 | 44729.5809 | 50.0472
2022-06-17 | 12:57 | 49.761 | 44729.5809 | 50.0471
2022-06-17 | 12:57 | 49.761 | 44729.5809 | 50.047
2022-06-17 | 12:57 | 49.76 | 44729.5809 | 50.047
2022-06-17 | 12:57 | 49.758 | 44729.5809 | 50.047
2022-06-17 | 12:57 | 49.755 | 44729.5809 | 50.047
2022-06-17 | 12:57 | 49.752 | 44729.5809 | 50.047
2022-06-17 | 12:57 | 49.752 | 44729.5809 | 50.047
2022-06-17 | 12:57 | 49.752 | 44729.5809 | 50.0471
2022-06-17 | 12:57 | 49.755 | 44729.5809 | 50.0471
2022-06-17 | 12:57 | 49.757 | 44729.5809 | 50.0472
2022-06-17 | 12:58 | 49.757 | 44729.5809 | 50.0472
2022-06-17 | 12:58 | 49.758 | 44729.5809 | 50.0473
2022-06-17 | 12:58 | 49.757 | 44729.5809 | 50.0473
2022-06-17 | 12:58 | 49.759 | 44729.5809 | 50.0474
2022-06-17 | 12:58 | 49.762 | 44729.5809 | 50.0475
2022-06-17 | 12:58 | 49.761 | 44729.5809 | 50.0474
2022-06-17 | 12:58 | 49.763 | 44729.5809 | 50.0475
2022-06-17 | 12:58 | 49.765 | 44729.5809 | 50.0475
2022-06-17 | 12:58 | 49.765 | 44729.5809 | 50.0475
2022-06-17 | 12:58 | 49.767 | 44729.5809 | 50.0476
2022-06-17 | 12:58 | 49.768 | 2022-06-17 13:57 | 50.0476
2022-06-17 | 12:58 | 49.768 | 44729.5809 | 50.0475
2022-06-17 | 12:58 | 49.768 | 44729.5809 | 50.0475
2022-06-17 | 12:58 | 49.767 | 44729.5809 | 50.0475
2022-06-17 | 12:58 | 49.766 | 44729.5809 | 50.0474
2022-06-17 | 12:58 | 49.765 | 44729.5809 | 50.0474
2022-06-17 | 12:58 | 49.769 | 44729.5809 | 50.0474
2022-06-17 | 12:58 | 49.769 | 44729.5809 | 50.0474
2022-06-17 | 12:58 | 49.765 | 44729.5809 | 50.0474
2022-06-17 | 12:58 | 49.763 | 44729.5809 | 50.0474
2022-06-17 | 12:58 | 49.762 | 44729.5809 | 50.0475
2022-06-17 | 12:58 | 49.765 | 44729.5809 | 50.0476
2022-06-17 | 12:58 | 49.765 | 44729.5809 | 50.0477
2022-06-17 | 12:58 | 49.768 | 44729.5809 | 50.0478
2022-06-17 | 12:58 | 49.771 | 44729.5809 | 50.0479
2022-06-17 | 12:58 | 49.77 | 44729.5809 | 50.048
2022-06-17 | 12:58 | 49.767 | 44729.5809 | 50.0481
2022-06-17 | 12:58 | 49.765 | 44729.5809 | 50.0482
2022-06-17 | 12:58 | 49.761 | 44729.5809 | 50.0482
2022-06-17 | 12:58 | 49.759 | 44729.5809 | 50.0483
2022-06-17 | 12:58 | 49.762 | 44729.5809 | 50.0483
2022-06-17 | 12:58 | 49.756 | 44729.5809 | 50.0483
2022-06-17 | 12:58 | 49.757 | 44729.5809 | 50.0483
2022-06-17 | 12:58 | 49.757 | 44729.5809 | 50.0482
2022-06-17 | 12:58 | 49.758 | 44729.5809 | 50.0482
2022-06-17 | 12:58 | 49.757 | 44729.5809 | 50.0483
2022-06-17 | 12:58 | 49.761 | 44729.5809 | 50.0483
2022-06-17 | 12:58 | 49.762 | 44729.5809 | 50.0482
2022-06-17 | 12:58 | 49.76 | 44729.5809 | 50.0483
2022-06-17 | 12:58 | 49.758 | 44729.5809 | 50.0483
2022-06-17 | 12:58 | 49.757 | 44729.5809 | 50.0483
2022-06-17 | 12:58 | 49.756 | 44729.5809 | 50.0483
2022-06-17 | 12:58 | 49.753 | 44729.5809 | 50.0482
2022-06-17 | 12:58 | 49.75 | 44729.5809 | 50.0482
2022-06-17 | 12:58 | 49.748 | 44729.5809 | 50.0481
2022-06-17 | 12:58 | 49.747 | 44729.5809 | 50.048
2022-06-17 | 12:58 | 49.748 | 44729.5809 | 50.0478
2022-06-17 | 12:58 | 49.751 | 44729.5809 | 50.0478
2022-06-17 | 12:58 | 49.752 | 44729.5809 | 50.0477
2022-06-17 | 12:58 | 49.753 | 44729.5809 | 50.0477
2022-06-17 | 12:58 | 49.755 | 44729.5809 | 50.0477
2022-06-17 | 12:58 | 49.756 | 44729.5809 | 50.0477
2022-06-17 | 12:58 | 49.759 | 44729.5809 | 50.0477
2022-06-17 | 12:58 | 49.762 | 44729.5809 | 50.0477
2022-06-17 | 12:58 | 49.767 | 44729.5809 | 50.0477
2022-06-17 | 12:58 | 49.773 | 44729.5809 | 50.0477
2022-06-17 | 12:58 | 49.78 | 44729.5809 | 50.0476
2022-06-17 | 12:58 | 49.785 | 44729.5809 | 50.0476
2022-06-17 | 12:58 | 49.789 | 44729.5809 | 50.0475
2022-06-17 | 12:58 | 49.795 | 44729.5809 | 50.0473
2022-06-17 | 12:58 | 49.801 | 2022-06-17 13:57 | 50.0471
2022-06-17 | 12:59 | 49.808 | 44729.5809 | 50.047
2022-06-17 | 12:59 | 49.813 | 44729.5809 | 50.0469
2022-06-17 | 12:59 | 49.818 | 44729.5809 | 50.0468
2022-06-17 | 12:59 | 49.82 | 44729.5809 | 50.0468
2022-06-17 | 12:59 | 49.821 | 44729.5809 | 50.0467
2022-06-17 | 12:59 | 49.822 | 44729.5809 | 50.0466
2022-06-17 | 12:59 | 49.822 | 44729.5809 | 50.0465
2022-06-17 | 12:59 | 49.824 | 44729.5809 | 50.0464
2022-06-17 | 12:59 | 49.821 | 44729.5809 | 50.0463
2022-06-17 | 12:59 | 49.818 | 44729.5809 | 50.0462
2022-06-17 | 12:59 | 49.819 | 44729.5809 | 50.0461
2022-06-17 | 12:59 | 49.82 | 44729.5809 | 50.046
2022-06-17 | 12:59 | 49.824 | 44729.5809 | 50.0459
2022-06-17 | 12:59 | 49.828 | 44729.5809 | 50.0459
2022-06-17 | 12:59 | 49.826 | 44729.5809 | 50.0459
2022-06-17 | 12:59 | 49.827 | 44729.5809 | 50.046
2022-06-17 | 12:59 | 49.829 | 44729.5809 | 50.046
2022-06-17 | 12:59 | 49.832 | 44729.5809 | 50.0459
2022-06-17 | 12:59 | 49.834 | 44729.5809 | 50.0458
2022-06-17 | 12:59 | 49.836 | 44729.5809 | 50.0457
2022-06-17 | 12:59 | 49.838 | 44729.5809 | 50.0457
2022-06-17 | 12:59 | 49.84 | 44729.5809 | 50.0456
2022-06-17 | 12:59 | 49.84 | 44729.5809 | 50.0455
2022-06-17 | 12:59 | 49.84 | 44729.5809 | 50.0454
2022-06-17 | 12:59 | 49.84 | 44729.5809 | 50.0453
2022-06-17 | 12:59 | 49.841 | 44729.5809 | 50.0452
2022-06-17 | 12:59 | 49.842 | 44729.5809 | 50.0452
2022-06-17 | 12:59 | 49.844 | 44729.5809 | 50.0453
2022-06-17 | 12:59 | 49.848 | 44729.5809 | 50.0453
2022-06-17 | 12:59 | 49.854 | 44729.5809 | 50.0454
2022-06-17 | 12:59 | 49.857 | 44729.5809 | 50.0455
2022-06-17 | 12:59 | 49.855 | 44729.5809 | 50.0455
2022-06-17 | 12:59 | 49.849 | 44729.5809 | 50.0454
2022-06-17 | 12:59 | 49.845 | 44729.5809 | 50.0454
2022-06-17 | 12:59 | 49.84 | 44729.5809 | 50.0454
2022-06-17 | 12:59 | 49.84 | 44729.5809 | 50.0452
2022-06-17 | 12:59 | 49.839 | 44729.5809 | 50.0452
2022-06-17 | 12:59 | 49.838 | 44729.5809 | 50.0451
2022-06-17 | 12:59 | 49.839 | 44729.5809 | 50.045
2022-06-17 | 12:59 | 49.841 | 44729.5809 | 50.0448
2022-06-17 | 12:59 | 49.846 | 44729.5809 | 50.0446
2022-06-17 | 12:59 | 49.849 | 44729.5809 | 50.0444
2022-06-17 | 12:59 | 49.85 | 44729.5809 | 50.0444
2022-06-17 | 12:59 | 49.851 | 44729.5809 | 50.0443
2022-06-17 | 12:59 | 49.854 | 44729.5809 | 50.0442
2022-06-17 | 12:59 | 49.854 | 44729.5809 | 50.0442
2022-06-17 | 12:59 | 49.857 | 44729.5809 | 50.0442
2022-06-17 | 12:59 | 49.856 | 44729.5809 | 50.0441
2022-06-17 | 12:59 | 49.855 | 44729.5809 | 50.0441
2022-06-17 | 12:59 | 49.856 | 2022-06-17 13:57 | 50.0439
2022-06-17 | 12:59 | 49.855 | 44729.5809 | 50.0438
2022-06-17 | 12:59 | 49.854 | 44729.5809 | 50.0437
2022-06-17 | 12:59 | 49.857 | 44729.5809 | 50.0436
2022-06-17 | 12:59 | 49.859 | 44729.581 | 50.0434
2022-06-17 | 12:59 | 49.86 | 44729.581 | 50.0432
2022-06-17 | 12:59 | 49.859 | 44729.581 | 50.043
2022-06-17 | 12:59 | 49.86 | 44729.581 | 50.0428
2022-06-17 | 12:59 | 49.858 | 44729.581 | 50.0426
2022-06-17 | 12:59 | 49.863 | 44729.581 | 50.0425
2022-06-17 | 13:00 | 49.862 | 44729.581 | 50.0424
2022-06-17 | 13:00 | 49.863 | 44729.581 | 50.0423
2022-06-17 | 13:00 | 49.862 | 44729.581 | 50.0423
2022-06-17 | 13:00 | 49.86 | 44729.581 | 50.0423
2022-06-17 | 13:00 | 49.858 | 44729.581 | 50.0423
2022-06-17 | 13:00 | 49.857 | 44729.581 | 50.0423
2022-06-17 | 13:00 | 49.855 | 44729.581 | 50.0423
2022-06-17 | 13:00 | 49.855 | 44729.581 | 50.0423
2022-06-17 | 13:00 | 49.852 | 44729.581 | 50.0422
2022-06-17 | 13:00 | 49.851 | 44729.581 | 50.0421
2022-06-17 | 13:00 | 49.851 | 44729.581 | 50.042
2022-06-17 | 13:00 | 49.851 | 44729.581 | 50.0418
2022-06-17 | 13:00 | 49.856 | 44729.581 | 50.0417
2022-06-17 | 13:00 | 49.858 | 44729.581 | 50.0415
2022-06-17 | 13:00 | 49.857 | 44729.581 | 50.0414
2022-06-17 | 13:00 | 49.863 | 44729.581 | 50.0415
2022-06-17 | 13:00 | 49.865 | 44729.581 | 50.0414
2022-06-17 | 13:00 | 49.867 | 44729.581 | 50.0413
2022-06-17 | 13:00 | 49.867 | 44729.581 | 50.0413
2022-06-17 | 13:00 | 49.866 | 44729.581 | 50.0413
2022-06-17 | 13:00 | 49.864 | 44729.581 | 50.0412
2022-06-17 | 13:00 | 49.862 | 44729.581 | 50.0411
2022-06-17 | 13:00 | 49.862 | 44729.581 | 50.041
2022-06-17 | 13:00 | 49.861 | 44729.581 | 50.0409
2022-06-17 | 13:00 | 49.86 | 44729.581 | 50.0408
2022-06-17 | 13:00 | 49.86 | 44729.581 | 50.0407
2022-06-17 | 13:00 | 49.86 | 44729.581 | 50.0406
2022-06-17 | 13:00 | 49.862 | 44729.581 | 50.0404
2022-06-17 | 13:00 | 49.858 | 44729.581 | 50.0403
2022-06-17 | 13:00 | 49.863 | 44729.581 | 50.0403
2022-06-17 | 13:00 | 49.859 | 44729.581 | 50.0402
2022-06-17 | 13:00 | 49.856 | 44729.581 | 50.0402
2022-06-17 | 13:00 | 49.851 | 44729.581 | 50.0402
2022-06-17 | 13:00 | 49.849 | 44729.581 | 50.0402
2022-06-17 | 13:00 | 49.85 | 44729.581 | 50.0401
2022-06-17 | 13:00 | 49.854 | 44729.581 | 50.0401
2022-06-17 | 13:00 | 49.854 | 44729.581 | 50.04
2022-06-17 | 13:00 | 49.855 | 44729.581 | 50.0399
2022-06-17 | 13:00 | 49.856 | 44729.581 | 50.0398
2022-06-17 | 13:00 | 49.857 | 44729.581 | 50.0396
2022-06-17 | 13:00 | 49.858 | 2022-06-17 13:57 | 50.0395
2022-06-17 | 13:00 | 49.862 | 44729.581 | 50.0394
2022-06-17 | 13:00 | 49.863 | 44729.581 | 50.0393
2022-06-17 | 13:00 | 49.865 | 44729.581 | 50.0393
2022-06-17 | 13:00 | 49.865 | 44729.581 | 50.0392
2022-06-17 | 13:00 | 49.864 | 44729.581 | 50.0391
2022-06-17 | 13:00 | 49.867 | 44729.581 | 50.0392
2022-06-17 | 13:00 | 49.865 | 44729.581 | 50.0391
2022-06-17 | 13:00 | 49.867 | 44729.581 | 50.0391
2022-06-17 | 13:00 | 49.87 | 44729.581 | 50.0391
2022-06-17 | 13:00 | 49.875 | 44729.581 | 50.0391
2022-06-17 | 13:00 | 49.881 | 44729.581 | 50.039
2022-06-17 | 13:00 | 49.883 | 44729.581 | 50.0389
2022-06-17 | 13:00 | 49.889 | 44729.581 | 50.0389
2022-06-17 | 13:00 | 49.888 | 44729.581 | 50.0389
2022-06-17 | 13:00 | 49.886 | 44729.581 | 50.0388
2022-06-17 | 13:00 | 49.885 | 44729.581 | 50.0388
2022-06-17 | 13:00 | 49.882 | 44729.581 | 50.0387
2022-06-17 | 13:00 | 49.879 | 44729.581 | 50.0387
2022-06-17 | 13:00 | 49.882 | 44729.581 | 50.0386
2022-06-17 | 13:01 | 49.881 | 44729.581 | 50.0385
2022-06-17 | 13:01 | 49.881 | 44729.581 | 50.0385
2022-06-17 | 13:01 | 49.884 | 44729.581 | 50.0385
2022-06-17 | 13:01 | 49.883 | 44729.581 | 50.0384
2022-06-17 | 13:01 | 49.882 | 44729.581 | 50.0384
2022-06-17 | 13:01 | 49.882 | 44729.581 | 50.0383
2022-06-17 | 13:01 | 49.885 | 44729.581 | 50.0382
2022-06-17 | 13:01 | 49.884 | 44729.581 | 50.0381
2022-06-17 | 13:01 | 49.881 | 44729.581 | 50.038
2022-06-17 | 13:01 | 49.881 | 44729.581 | 50.0381
2022-06-17 | 13:01 | 49.878 | 44729.581 | 50.0381
2022-06-17 | 13:01 | 49.879 | 44729.581 | 50.0382
2022-06-17 | 13:01 | 49.885 | 44729.581 | 50.0382
2022-06-17 | 13:01 | 49.891 | 44729.581 | 50.0383
2022-06-17 | 13:01 | 49.895 | 44729.581 | 50.0383
2022-06-17 | 13:01 | 49.896 | 44729.581 | 50.0382
2022-06-17 | 13:01 | 49.898 | 44729.581 | 50.0382
2022-06-17 | 13:01 | 49.898 | 44729.581 | 50.0382
2022-06-17 | 13:01 | 49.898 | 44729.581 | 50.0381
2022-06-17 | 13:01 | 49.899 | 44729.581 | 50.0381
2022-06-17 | 13:01 | 49.9 | 44729.581 | 50.038
2022-06-17 | 13:01 | 49.899 | 44729.581 | 50.038
2022-06-17 | 13:01 | 49.898 | 44729.581 | 50.0379
2022-06-17 | 13:01 | 49.896 | 44729.581 | 50.0379
2022-06-17 | 13:01 | 49.897 | 44729.581 | 50.0378
2022-06-17 | 13:01 | 49.895 | 44729.581 | 50.0377
2022-06-17 | 13:01 | 49.894 | 44729.581 | 50.0377
2022-06-17 | 13:01 | 49.895 | 44729.581 | 50.0377
2022-06-17 | 13:01 | 49.9 | 44729.581 | 50.0377
2022-06-17 | 13:01 | 49.901 | 44729.581 | 50.0376
2022-06-17 | 13:01 | 49.905 | 2022-06-17 13:57 | 50.0375
2022-06-17 | 13:01 | 49.905 | 44729.581 | 50.0374
2022-06-17 | 13:01 | 49.907 | 44729.581 | 50.0373
2022-06-17 | 13:01 | 49.908 | 44729.581 | 50.0372
2022-06-17 | 13:01 | 49.911 | 44729.581 | 50.0371
2022-06-17 | 13:01 | 49.917 | 44729.581 | 50.0369
2022-06-17 | 13:01 | 49.923 | 44729.581 | 50.0368
2022-06-17 | 13:01 | 49.927 | 44729.581 | 50.0367
2022-06-17 | 13:01 | 49.926 | 44729.581 | 50.0366
2022-06-17 | 13:01 | 49.929 | 44729.581 | 50.0366
2022-06-17 | 13:01 | 49.93 | 44729.581 | 50.0365
2022-06-17 | 13:01 | 49.932 | 44729.581 | 50.0365
2022-06-17 | 13:01 | 49.933 | 44729.581 | 50.0365
2022-06-17 | 13:01 | 49.934 | 44729.581 | 50.0365
2022-06-17 | 13:01 | 49.932 | 44729.581 | 50.0366
2022-06-17 | 13:01 | 49.933 | 44729.581 | 50.0365
2022-06-17 | 13:01 | 49.932 | 44729.581 | 50.0365
2022-06-17 | 13:01 | 49.935 | 44729.581 | 50.0364
2022-06-17 | 13:01 | 49.939 | 44729.581 | 50.0363
2022-06-17 | 13:01 | 49.941 | 44729.581 | 50.0363
2022-06-17 | 13:01 | 49.941 | 44729.581 | 50.0362
2022-06-17 | 13:01 | 49.945 | 44729.581 | 50.0361
2022-06-17 | 13:01 | 49.947 | 44729.581 | 50.036
2022-06-17 | 13:01 | 49.945 | 44729.581 | 50.036
2022-06-17 | 13:01 | 49.95 | 44729.581 | 50.036
2022-06-17 | 13:01 | 49.949 | 44729.581 | 50.0359
2022-06-17 | 13:01 | 49.949 | 44729.581 | 50.0359
2022-06-17 | 13:01 | 49.948 | 44729.581 | 50.0359
2022-06-17 | 13:01 | 49.949 | 44729.581 | 50.0358
2022-06-17 | 13:01 | 49.947 | 44729.581 | 50.0358
2022-06-17 | 13:01 | 49.949 | 44729.581 | 50.0357
2022-06-17 | 13:02 | 49.954 | 44729.581 | 50.0357
2022-06-17 | 13:02 | 49.955 | 44729.581 | 50.0356
2022-06-17 | 13:02 | 49.956 | 44729.581 | 50.0356
2022-06-17 | 13:02 | 49.955 | 44729.581 | 50.0355
2022-06-17 | 13:02 | 49.956 | 44729.581 | 50.0354
2022-06-17 | 13:02 | 49.953 | 44729.581 | 50.0354
2022-06-17 | 13:02 | 49.95 | 44729.581 | 50.0353
2022-06-17 | 13:02 | 49.952 | 44729.581 | 50.0352
2022-06-17 | 13:02 | 49.953 | 44729.581 | 50.0353
2022-06-17 | 13:02 | 49.95 | 44729.581 | 50.0352
2022-06-17 | 13:02 | 49.949 | 44729.581 | 50.0351
2022-06-17 | 13:02 | 49.948 | 44729.581 | 50.0351
2022-06-17 | 13:02 | 49.947 | 44729.581 | 50.035
2022-06-17 | 13:02 | 49.948 | 44729.581 | 50.035
2022-06-17 | 13:02 | 49.949 | 44729.581 | 50.035
2022-06-17 | 13:02 | 49.954 | 44729.581 | 50.0349
2022-06-17 | 13:02 | 49.954 | 44729.581 | 50.0348
2022-06-17 | 13:02 | 49.952 | 44729.581 | 50.0347
2022-06-17 | 13:02 | 49.952 | 44729.581 | 50.0346
2022-06-17 | 13:02 | 49.951 | 2022-06-17 13:57 | 50.0346
2022-06-17 | 13:02 | 49.951 | 44729.581 | 50.0346
2022-06-17 | 13:02 | 49.947 | 44729.581 | 50.0346
2022-06-17 | 13:02 | 49.946 | 44729.581 | 50.0345
2022-06-17 | 13:02 | 49.945 | 44729.581 | 50.0345
2022-06-17 | 13:02 | 49.944 | 44729.581 | 50.0343
2022-06-17 | 13:02 | 49.942 | 44729.581 | 50.0343
2022-06-17 | 13:02 | 49.942 | 44729.581 | 50.0342
2022-06-17 | 13:02 | 49.94 | 44729.581 | 50.0341
2022-06-17 | 13:02 | 49.943 | 44729.581 | 50.034
2022-06-17 | 13:02 | 49.943 | 44729.581 | 50.034
2022-06-17 | 13:02 | 49.944 | 44729.581 | 50.0339
2022-06-17 | 13:02 | 49.942 | 44729.581 | 50.0338
2022-06-17 | 13:02 | 49.942 | 44729.581 | 50.0337
2022-06-17 | 13:02 | 49.944 | 44729.581 | 50.0336
2022-06-17 | 13:02 | 49.947 | 44729.581 | 50.0336
2022-06-17 | 13:02 | 49.948 | 44729.581 | 50.0336
2022-06-17 | 13:02 | 49.951 | 44729.581 | 50.0336
2022-06-17 | 13:02 | 49.952 | 44729.581 | 50.0335
2022-06-17 | 13:02 | 49.952 | 44729.581 | 50.0334
2022-06-17 | 13:02 | 49.953 | 44729.581 | 50.0333
2022-06-17 | 13:02 | 49.956 | 44729.581 | 50.0333
2022-06-17 | 13:02 | 49.96 | 44729.581 | 50.0332
2022-06-17 | 13:02 | 49.958 | 44729.581 | 50.0331
2022-06-17 | 13:02 | 49.959 | 44729.581 | 50.033
2022-06-17 | 13:02 | 49.963 | 44729.581 | 50.0329
2022-06-17 | 13:02 | 49.966 | 44729.581 | 50.0327
2022-06-17 | 13:02 | 49.968 | 44729.581 | 50.0326
2022-06-17 | 13:02 | 49.969 | 44729.581 | 50.0325
2022-06-17 | 13:02 | 49.97 | 44729.581 | 50.0324
2022-06-17 | 13:02 | 49.963 | 44729.581 | 50.0323
2022-06-17 | 13:02 | 49.959 | 44729.581 | 50.0323
2022-06-17 | 13:02 | 49.953 | 44729.581 | 50.0322
2022-06-17 | 13:02 | 49.951 | 44729.581 | 50.0322
2022-06-17 | 13:02 | 49.948 | 44729.581 | 50.0322
2022-06-17 | 13:02 | 49.95 | 44729.581 | 50.0323
2022-06-17 | 13:02 | 49.952 | 44729.581 | 50.0322
2022-06-17 | 13:02 | 49.955 | 44729.581 | 50.0321
2022-06-17 | 13:02 | 49.957 | 44729.581 | 50.032
2022-06-17 | 13:02 | 49.957 | 44729.581 | 50.0319
2022-06-17 | 13:03 | 49.953 | 44729.581 | 50.0319
2022-06-17 | 13:03 | 49.95 | 44729.581 | 50.0318
2022-06-17 | 13:03 | 49.942 | 44729.581 | 50.0318
2022-06-17 | 13:03 | 49.94 | 44729.581 | 50.0318
2022-06-17 | 13:03 | 49.936 | 44729.581 | 50.0316
2022-06-17 | 13:03 | 49.935 | 44729.581 | 50.0315
2022-06-17 | 13:03 | 49.934 | 44729.581 | 50.0314
2022-06-17 | 13:03 | 49.943 | 44729.581 | 50.0313
2022-06-17 | 13:03 | 49.947 | 44729.581 | 50.0313
2022-06-17 | 13:03 | 49.953 | 44729.581 | 50.0313
2022-06-17 | 13:03 | 49.96 | 2022-06-17 13:57 | 50.0313
2022-06-17 | 13:03 | 49.962 | 44729.581 | 50.0314
2022-06-17 | 13:03 | 49.965 | 44729.581 | 50.0314
2022-06-17 | 13:03 | 49.969 | 44729.581 | 50.0313
2022-06-17 | 13:03 | 49.973 | 44729.581 | 50.0312
2022-06-17 | 13:03 | 49.976 | 44729.581 | 50.0311
2022-06-17 | 13:03 | 49.975 | 44729.581 | 50.031
2022-06-17 | 13:03 | 49.974 | 44729.581 | 50.0309
2022-06-17 | 13:03 | 49.974 | 44729.581 | 50.0309
2022-06-17 | 13:03 | 49.971 | 44729.581 | 50.0309
2022-06-17 | 13:03 | 49.97 | 44729.581 | 50.0309
2022-06-17 | 13:03 | 49.973 | 44729.581 | 50.031
2022-06-17 | 13:03 | 49.975 | 44729.581 | 50.0312
2022-06-17 | 13:03 | 49.983 | 44729.581 | 50.0313
2022-06-17 | 13:03 | 49.987 | 44729.581 | 50.0313
2022-06-17 | 13:03 | 49.989 | 44729.581 | 50.0313
2022-06-17 | 13:03 | 49.992 | 44729.581 | 50.0313
2022-06-17 | 13:03 | 49.994 | 44729.581 | 50.0312
2022-06-17 | 13:03 | 49.992 | 44729.581 | 50.0311
2022-06-17 | 13:03 | 49.993 | 44729.581 | 50.0309
2022-06-17 | 13:03 | 49.994 | 44729.581 | 50.0309
2022-06-17 | 13:03 | 49.992 | 44729.581 | 50.0308
2022-06-17 | 13:03 | 49.988 | 44729.581 | 50.0307
2022-06-17 | 13:03 | 49.989 | 44729.581 | 50.0307
2022-06-17 | 13:03 | 49.991 | 44729.581 | 50.0308
2022-06-17 | 13:03 | 49.995 | 44729.581 | 50.0309
2022-06-17 | 13:03 | 49.999 | 44729.581 | 50.031
2022-06-17 | 13:03 | 50.002 | 44729.581 | 50.031
2022-06-17 | 13:03 | 50.002 | 44729.581 | 50.0311
2022-06-17 | 13:03 | 50.002 | 44729.581 | 50.0311
2022-06-17 | 13:03 | 50 | 44729.581 | 50.0311
2022-06-17 | 13:03 | 49.998 | 44729.581 | 50.0311
2022-06-17 | 13:03 | 49.996 | 44729.581 | 50.031
2022-06-17 | 13:03 | 49.992 | 44729.581 | 50.0308
2022-06-17 | 13:03 | 49.985 | 44729.581 | 50.0308
2022-06-17 | 13:03 | 49.981 | 44729.581 | 50.0307
2022-06-17 | 13:03 | 49.978 | 44729.581 | 50.0307
2022-06-17 | 13:03 | 49.979 | 44729.581 | 50.0306
2022-06-17 | 13:03 | 49.981 | 44729.581 | 50.0306
2022-06-17 | 13:03 | 49.987 | 44729.581 | 50.0307
2022-06-17 | 13:03 | 49.994 | 44729.581 | 50.0307
2022-06-17 | 13:03 | 49.996 | 44729.581 | 50.0308
2022-06-17 | 13:03 | 50.001 | 44729.581 | 50.0308
2022-06-17 | 13:03 | 50.006 | 44729.581 | 50.0309
2022-06-17 | 13:03 | 50.012 | 44729.581 | 50.0309
2022-06-17 | 13:03 | 50.016 | 44729.581 | 50.031
2022-06-17 | 13:03 | 50.018 | 44729.581 | 50.031
2022-06-17 | 13:03 | 50.019 | 44729.581 | 50.031
2022-06-17 | 13:03 | 50.019 | 44729.581 | 50.0309
2022-06-17 | 13:03 | 50.016 | 44729.581 | 50.0308
2022-06-17 | 13:03 | 50.016 | 2022-06-17 13:57 | 50.0308
2022-06-17 | 13:04 | 50.017 | 44729.581 | 50.0308
2022-06-17 | 13:04 | 50.016 | 44729.581 | 50.0307
2022-06-17 | 13:04 | 50.018 | 44729.581 | 50.0307
2022-06-17 | 13:04 | 50.019 | 44729.581 | 50.0307
2022-06-17 | 13:04 | 50.019 | 44729.581 | 50.0307
2022-06-17 | 13:04 | 50.025 | 44729.581 | 50.0307
2022-06-17 | 13:04 | 50.035 | 44729.581 | 50.0307
2022-06-17 | 13:04 | 50.043 | 44729.581 | 50.0307
2022-06-17 | 13:04 | 50.05 | 44729.581 | 50.0307
2022-06-17 | 13:04 | 50.051 | 44729.581 | 50.0307
2022-06-17 | 13:04 | 50.05 | 44729.581 | 50.0307
2022-06-17 | 13:04 | 50.048 | 44729.581 | 50.0307
2022-06-17 | 13:04 | 50.047 | 44729.581 | 50.0307
2022-06-17 | 13:04 | 50.047 | 44729.581 | 50.0307
2022-06-17 | 13:04 | 50.043 | 44729.581 | 50.0307
2022-06-17 | 13:04 | 50.04 | 44729.581 | 50.0308
2022-06-17 | 13:04 | 50.037 | 44729.581 | 50.0308
2022-06-17 | 13:04 | 50.028 | 44729.581 | 50.0308
2022-06-17 | 13:04 | 50.015 | 44729.581 | 50.0308
2022-06-17 | 13:04 | 49.998 | 44729.581 | 50.0308
2022-06-17 | 13:04 | 49.983 | 44729.581 | 50.0309
2022-06-17 | 13:04 | 49.975 | 44729.581 | 50.0308
2022-06-17 | 13:04 | 49.966 | 44729.581 | 50.0308
2022-06-17 | 13:04 | 49.958 | 44729.581 | 50.0307
2022-06-17 | 13:04 | 49.951 | 44729.581 | 50.0307
2022-06-17 | 13:04 | 49.946 | 44729.581 | 50.0307
2022-06-17 | 13:04 | 49.945 | 44729.581 | 50.0307
2022-06-17 | 13:04 | 49.943 | 44729.581 | 50.0308
2022-06-17 | 13:04 | 49.94 | 44729.581 | 50.0308
2022-06-17 | 13:04 | 49.94 | 44729.581 | 50.0308
|  |  | 44729.581 | 50.0308
|  |  | 44729.581 | 50.0309
|  |  | 44729.581 | 50.031
|  |  | 44729.581 | 50.031
|  |  | 44729.581 | 50.0311
|  |  | 44729.581 | 50.0311
|  |  | 44729.581 | 50.0311
|  |  | 44729.581 | 50.0312
|  |  | 44729.581 | 50.0313
|  |  | 44729.581 | 50.0314
|  |  | 44729.581 | 50.0315
|  |  | 44729.581 | 50.0316
|  |  | 44729.581 | 50.0317
|  |  | 44729.581 | 50.0318
|  |  | 44729.581 | 50.0318
|  |  | 44729.581 | 50.0319
|  |  | 44729.581 | 50.0318
|  |  | 44729.581 | 50.0318
|  |  | 44729.581 | 50.0318
|  |  | 2022-06-17 13:57 | 50.0317
|  |  | 44729.581 | 50.0317
|  |  | 44729.581 | 50.0316
|  |  | 44729.581 | 50.0316
|  |  | 44729.581 | 50.0316
|  |  | 44729.581 | 50.0316
|  |  | 44729.581 | 50.0316
|  |  | 44729.581 | 50.0317
|  |  | 44729.581 | 50.0318
|  |  | 44729.581 | 50.0318
|  |  | 44729.581 | 50.0319
|  |  | 44729.581 | 50.0319
|  |  | 44729.581 | 50.032
|  |  | 44729.581 | 50.0319
|  |  | 44729.581 | 50.0319
|  |  | 44729.581 | 50.0318
|  |  | 44729.581 | 50.0317
|  |  | 44729.581 | 50.0317
|  |  | 44729.581 | 50.0316
|  |  | 44729.581 | 50.0315
|  |  | 44729.581 | 50.0315
|  |  | 44729.581 | 50.0315
|  |  | 44729.581 | 50.0315
|  |  | 44729.581 | 50.0316
|  |  | 44729.581 | 50.0315
|  |  | 44729.581 | 50.0316
|  |  | 44729.581 | 50.0316
|  |  | 44729.581 | 50.0316
|  |  | 44729.581 | 50.0316
|  |  | 44729.581 | 50.0317
|  |  | 44729.581 | 50.0318
|  |  | 44729.581 | 50.0319
|  |  | 44729.581 | 50.032
|  |  | 44729.581 | 50.0321
|  |  | 44729.581 | 50.0322
|  |  | 44729.581 | 50.0322
|  |  | 44729.581 | 50.0322
|  |  | 44729.581 | 50.0322
|  |  | 44729.581 | 50.0322
|  |  | 44729.581 | 50.0321
|  |  | 44729.581 | 50.032
|  |  | 44729.581 | 50.0319
|  |  | 44729.581 | 50.0318
|  |  | 44729.581 | 50.0318
|  |  | 44729.581 | 50.0318
|  |  | 44729.581 | 50.0318
|  |  | 44729.581 | 50.0317
|  |  | 44729.581 | 50.0317
|  |  | 44729.581 | 50.0318
|  |  | 44729.581 | 50.032
|  |  | 2022-06-17 13:57 | 50.0321
|  |  | 44729.581 | 50.0323
|  |  | 44729.581 | 50.0325
|  |  | 44729.581 | 50.0326
|  |  | 44729.581 | 50.0327
|  |  | 44729.581 | 50.0328
|  |  | 44729.581 | 50.0328
|  |  | 44729.581 | 50.0327
|  |  | 44729.581 | 50.0326
|  |  | 44729.581 | 50.0326
|  |  | 44729.581 | 50.0326
|  |  | 44729.581 | 50.0325
|  |  | 44729.581 | 50.0326
|  |  | 44729.581 | 50.0326
|  |  | 44729.581 | 50.0327
|  |  | 44729.581 | 50.0327
|  |  | 44729.581 | 50.0328
|  |  | 44729.581 | 50.0328
|  |  | 44729.581 | 50.0329
|  |  | 44729.581 | 50.0329
|  |  | 44729.581 | 50.0329
|  |  | 44729.581 | 50.0329
|  |  | 44729.581 | 50.033
|  |  | 44729.581 | 50.033
|  |  | 44729.581 | 50.0331
|  |  | 44729.581 | 50.0333
|  |  | 44729.581 | 50.0334
|  |  | 44729.581 | 50.0334
|  |  | 44729.581 | 50.0335
|  |  | 44729.581 | 50.0335
|  |  | 44729.581 | 50.0335
|  |  | 44729.581 | 50.0335
|  |  | 44729.581 | 50.0335
|  |  | 44729.581 | 50.0334
|  |  | 44729.581 | 50.0334
|  |  | 44729.581 | 50.0335
|  |  | 44729.581 | 50.0335
|  |  | 44729.581 | 50.0336
|  |  | 44729.581 | 50.0337
|  |  | 44729.581 | 50.0338
|  |  | 44729.581 | 50.0339
|  |  | 44729.581 | 50.034
|  |  | 44729.581 | 50.0341
|  |  | 44729.581 | 50.0342
|  |  | 44729.581 | 50.0342
|  |  | 44729.581 | 50.0343
|  |  | 44729.581 | 50.0343
|  |  | 44729.581 | 50.0342
|  |  | 44729.581 | 50.0342
|  |  | 44729.581 | 50.0343
|  |  | 2022-06-17 13:57 | 50.0343
|  |  | 44729.581 | 50.0343
|  |  | 44729.581 | 50.0344
|  |  | 44729.581 | 50.0344
|  |  | 44729.581 | 50.0346
|  |  | 44729.581 | 50.0347
|  |  | 44729.581 | 50.0348
|  |  | 44729.581 | 50.0348
|  |  | 44729.581 | 50.035
|  |  | 44729.581 | 50.035
|  |  | 44729.581 | 50.0351
|  |  | 44729.581 | 50.0352
|  |  | 44729.581 | 50.0352
|  |  | 44729.581 | 50.0352
|  |  | 44729.581 | 50.0351
|  |  | 44729.581 | 50.0351
|  |  | 44729.581 | 50.0351
|  |  | 44729.581 | 50.035
|  |  | 44729.581 | 50.0351
|  |  | 44729.581 | 50.0351
|  |  | 44729.581 | 50.0351
|  |  | 44729.581 | 50.0351
|  |  | 44729.581 | 50.0352
|  |  | 44729.581 | 50.0352
|  |  | 44729.581 | 50.0352
|  |  | 44729.581 | 50.0352
|  |  | 44729.581 | 50.0354
|  |  | 44729.581 | 50.0354
|  |  | 44729.581 | 50.0353
|  |  | 44729.581 | 50.0353
|  |  | 44729.581 | 50.0351
|  |  | 44729.581 | 50.0351
|  |  | 44729.581 | 50.035
|  |  | 44729.581 | 50.0349
|  |  | 44729.581 | 50.0348
|  |  | 44729.581 | 50.0348
|  |  | 44729.5811 | 50.0349
|  |  | 44729.5811 | 50.0349
|  |  | 44729.5811 | 50.0349
|  |  | 44729.5811 | 50.035
|  |  | 44729.5811 | 50.035
|  |  | 44729.5811 | 50.0351
|  |  | 44729.5811 | 50.0351
|  |  | 44729.5811 | 50.0351
|  |  | 44729.5811 | 50.0351
|  |  | 44729.5811 | 50.0351
|  |  | 44729.5811 | 50.035
|  |  | 44729.5811 | 50.035
|  |  | 44729.5811 | 50.035
|  |  | 44729.5811 | 50.035
|  |  | 2022-06-17 13:57 | 50.035
|  |  | 44729.5811 | 50.035
|  |  | 44729.5811 | 50.0351
|  |  | 44729.5811 | 50.0351
|  |  | 44729.5811 | 50.0351
|  |  | 44729.5811 | 50.0352
|  |  | 44729.5811 | 50.0352
|  |  | 44729.5811 | 50.0352
|  |  | 44729.5811 | 50.0353
|  |  | 44729.5811 | 50.0353
|  |  | 44729.5811 | 50.0353
|  |  | 44729.5811 | 50.0353
|  |  | 44729.5811 | 50.0353
|  |  | 44729.5811 | 50.0353
|  |  | 44729.5811 | 50.0354
|  |  | 44729.5811 | 50.0354
|  |  | 44729.5811 | 50.0354
|  |  | 44729.5811 | 50.0354
|  |  | 44729.5811 | 50.0354
|  |  | 44729.5811 | 50.0353
|  |  | 44729.5811 | 50.0354
|  |  | 44729.5811 | 50.0354
|  |  | 44729.5811 | 50.0353
|  |  | 44729.5811 | 50.0353
|  |  | 44729.5811 | 50.0352
|  |  | 44729.5811 | 50.0352
|  |  | 44729.5811 | 50.0353
|  |  | 44729.5811 | 50.0353
|  |  | 44729.5811 | 50.0354
|  |  | 44729.5811 | 50.0355
|  |  | 44729.5811 | 50.0355
|  |  | 44729.5811 | 50.0355
|  |  | 44729.5811 | 50.0354
|  |  | 44729.5811 | 50.0354
|  |  | 44729.5811 | 50.0352
|  |  | 44729.5811 | 50.0351
|  |  | 44729.5811 | 50.035
|  |  | 44729.5811 | 50.0348
|  |  | 44729.5811 | 50.0347
|  |  | 44729.5811 | 50.0346
|  |  | 44729.5811 | 50.0345
|  |  | 44729.5811 | 50.0344
|  |  | 44729.5811 | 50.0344
|  |  | 44729.5811 | 50.0344
|  |  | 44729.5811 | 50.0344
|  |  | 44729.5811 | 50.0344
|  |  | 44729.5811 | 50.0344
|  |  | 44729.5811 | 50.0343
|  |  | 44729.5811 | 50.0344
|  |  | 44729.5811 | 50.0343
|  |  | 2022-06-17 13:57 | 50.0341
|  |  | 44729.5811 | 50.034
|  |  | 44729.5811 | 50.0339
|  |  | 44729.5811 | 50.0338
|  |  | 44729.5811 | 50.0338
|  |  | 44729.5811 | 50.0338
|  |  | 44729.5811 | 50.0339
|  |  | 44729.5811 | 50.034
|  |  | 44729.5811 | 50.0341
|  |  | 44729.5811 | 50.0342
|  |  | 44729.5811 | 50.0344
|  |  | 44729.5811 | 50.0344
|  |  | 44729.5811 | 50.0344
|  |  | 44729.5811 | 50.0344
|  |  | 44729.5811 | 50.0344
|  |  | 44729.5811 | 50.0343
|  |  | 44729.5811 | 50.0342
|  |  | 44729.5811 | 50.0342
|  |  | 44729.5811 | 50.0341
|  |  | 44729.5811 | 50.034
|  |  | 44729.5811 | 50.0338
|  |  | 44729.5811 | 50.0337
|  |  | 44729.5811 | 50.0337
|  |  | 44729.5811 | 50.0338
|  |  | 44729.5811 | 50.0338
|  |  | 44729.5811 | 50.0339
|  |  | 44729.5811 | 50.034
|  |  | 44729.5811 | 50.0341
|  |  | 44729.5811 | 50.0342
|  |  | 44729.5811 | 50.0343
|  |  | 44729.5811 | 50.0344
|  |  | 44729.5811 | 50.0345
|  |  | 44729.5811 | 50.0345
|  |  | 44729.5811 | 50.0345
|  |  | 44729.5811 | 50.0344
|  |  | 44729.5811 | 50.0342
|  |  | 44729.5811 | 50.0341
|  |  | 44729.5811 | 50.0341
|  |  | 44729.5811 | 50.034
|  |  | 44729.5811 | 50.034
|  |  | 44729.5811 | 50.0341
|  |  | 44729.5811 | 50.034
|  |  | 44729.5811 | 50.034
|  |  | 44729.5811 | 50.0339
|  |  | 44729.5811 | 50.0338
|  |  | 44729.5811 | 50.0338
|  |  | 44729.5811 | 50.0338
|  |  | 44729.5811 | 50.0337
|  |  | 44729.5811 | 50.0336
|  |  | 44729.5811 | 50.0335
|  |  | 2022-06-17 13:57 | 50.0335
|  |  | 44729.5811 | 50.0334
|  |  | 44729.5811 | 50.0334
|  |  | 44729.5811 | 50.0334
|  |  | 44729.5811 | 50.0334
|  |  | 44729.5811 | 50.0334
|  |  | 44729.5811 | 50.0334
|  |  | 44729.5811 | 50.0335
|  |  | 44729.5811 | 50.0335
|  |  | 44729.5811 | 50.0335
|  |  | 44729.5811 | 50.0336
|  |  | 44729.5811 | 50.0336
|  |  | 44729.5811 | 50.0336
|  |  | 44729.5811 | 50.0337
|  |  | 44729.5811 | 50.0337
|  |  | 44729.5811 | 50.0337
|  |  | 44729.5811 | 50.0337
|  |  | 44729.5811 | 50.0337
|  |  | 44729.5811 | 50.0337
|  |  | 44729.5811 | 50.0337
|  |  | 44729.5811 | 50.0337
|  |  | 44729.5811 | 50.0338
|  |  | 44729.5811 | 50.0339
|  |  | 44729.5811 | 50.034
|  |  | 44729.5811 | 50.0341
|  |  | 44729.5811 | 50.0342
|  |  | 44729.5811 | 50.0341
|  |  | 44729.5811 | 50.0341
|  |  | 44729.5811 | 50.0342
|  |  | 44729.5811 | 50.0342
|  |  | 44729.5811 | 50.0343
|  |  | 44729.5811 | 50.0343
|  |  | 44729.5811 | 50.0343
|  |  | 44729.5811 | 50.0343
|  |  | 44729.5811 | 50.0342
|  |  | 44729.5811 | 50.0341
|  |  | 44729.5811 | 50.0341
|  |  | 44729.5811 | 50.0341
|  |  | 44729.5811 | 50.0341
|  |  | 44729.5811 | 50.034
|  |  | 44729.5811 | 50.0341
|  |  | 44729.5811 | 50.0342
|  |  | 44729.5811 | 50.0343
|  |  | 44729.5811 | 50.0343
|  |  | 44729.5811 | 50.0344
|  |  | 44729.5811 | 50.0344
|  |  | 44729.5811 | 50.0345
|  |  | 44729.5811 | 50.0345
|  |  | 44729.5811 | 50.0345
|  |  | 44729.5811 | 50.0345
|  |  | 2022-06-17 13:57 | 50.0345
|  |  | 44729.5811 | 50.0344
|  |  | 44729.5811 | 50.0344
|  |  | 44729.5811 | 50.0343
|  |  | 44729.5811 | 50.0342
|  |  | 44729.5811 | 50.0342
|  |  | 44729.5811 | 50.0341
|  |  | 44729.5811 | 50.034
|  |  | 44729.5811 | 50.034
|  |  | 44729.5811 | 50.0339
|  |  | 44729.5811 | 50.0339
|  |  | 44729.5811 | 50.0338
|  |  | 44729.5811 | 50.0338
|  |  | 44729.5811 | 50.0338
|  |  | 44729.5811 | 50.0337
|  |  | 44729.5811 | 50.0336
|  |  | 44729.5811 | 50.0335
|  |  | 44729.5811 | 50.0334
|  |  | 44729.5811 | 50.0333
|  |  | 44729.5811 | 50.0333
|  |  | 44729.5811 | 50.0335
|  |  | 44729.5811 | 50.0335
|  |  | 44729.5811 | 50.0335
|  |  | 44729.5811 | 50.0333
|  |  | 44729.5811 | 50.0333
|  |  | 44729.5811 | 50.0333
|  |  | 44729.5811 | 50.0332
|  |  | 44729.5811 | 50.0331
|  |  | 44729.5811 | 50.033
|  |  | 44729.5811 | 50.0331
|  |  | 44729.5811 | 50.033
|  |  | 44729.5811 | 50.033
|  |  | 44729.5811 | 50.0329
|  |  | 44729.5811 | 50.0329
|  |  | 44729.5811 | 50.0328
|  |  | 44729.5811 | 50.0328
|  |  | 44729.5811 | 50.0327
|  |  | 44729.5811 | 50.0327
|  |  | 44729.5811 | 50.0327
|  |  | 44729.5811 | 50.0327
|  |  | 44729.5811 | 50.0325
|  |  | 44729.5811 | 50.0326
|  |  | 44729.5811 | 50.0326
|  |  | 44729.5811 | 50.0327
|  |  | 44729.5811 | 50.0327
|  |  | 44729.5811 | 50.0328
|  |  | 44729.5811 | 50.0329
|  |  | 44729.5811 | 50.0329
|  |  | 44729.5811 | 50.0329
|  |  | 44729.5811 | 50.0329
|  |  | 2022-06-17 13:57 | 50.0326
|  |  | 44729.5811 | 50.0326
|  |  | 44729.5811 | 50.0325
|  |  | 44729.5811 | 50.0324
|  |  | 44729.5811 | 50.0324
|  |  | 44729.5811 | 50.0324
|  |  | 44729.5811 | 50.0325
|  |  | 44729.5811 | 50.0326
|  |  | 44729.5811 | 50.0326
|  |  | 44729.5811 | 50.0326
|  |  | 44729.5811 | 50.0327
|  |  | 44729.5811 | 50.0328
|  |  | 44729.5811 | 50.0329
|  |  | 44729.5811 | 50.0329
|  |  | 44729.5811 | 50.033
|  |  | 44729.5811 | 50.0331
|  |  | 44729.5811 | 50.0332
|  |  | 44729.5811 | 50.0332
|  |  | 44729.5811 | 50.0332
|  |  | 44729.5811 | 50.0332
|  |  | 44729.5811 | 50.0331
|  |  | 44729.5811 | 50.033
|  |  | 44729.5811 | 50.0329
|  |  | 44729.5811 | 50.0328
|  |  | 44729.5811 | 50.0327
|  |  | 44729.5811 | 50.0327
|  |  | 44729.5811 | 50.0327
|  |  | 44729.5811 | 50.0328
|  |  | 44729.5811 | 50.033
|  |  | 44729.5811 | 50.033
|  |  | 44729.5811 | 50.0331
|  |  | 44729.5811 | 50.0333
|  |  | 44729.5811 | 50.0333
|  |  | 44729.5811 | 50.0332
|  |  | 44729.5811 | 50.0331
|  |  | 44729.5811 | 50.0331
|  |  | 44729.5811 | 50.0331
|  |  | 44729.5811 | 50.0331
|  |  | 44729.5811 | 50.0331
|  |  | 44729.5811 | 50.0331
|  |  | 44729.5811 | 50.0332
|  |  | 44729.5811 | 50.0331
|  |  | 44729.5811 | 50.0331
|  |  | 44729.5811 | 50.033
|  |  | 44729.5811 | 50.033
|  |  | 44729.5811 | 50.033
|  |  | 44729.5811 | 50.0331
|  |  | 44729.5811 | 50.0332
|  |  | 44729.5811 | 50.0333
|  |  | 44729.5811 | 50.0333
|  |  | 2022-06-17 13:57 | 50.0334
|  |  | 44729.5811 | 50.0335
|  |  | 44729.5811 | 50.0336
|  |  | 44729.5811 | 50.0337
|  |  | 44729.5811 | 50.0336
|  |  | 44729.5811 | 50.0336
|  |  | 44729.5811 | 50.0337
|  |  | 44729.5811 | 50.0337
|  |  | 44729.5811 | 50.0337
|  |  | 44729.5811 | 50.0337
|  |  | 44729.5811 | 50.0336
|  |  | 44729.5811 | 50.0336
|  |  | 44729.5811 | 50.0336
|  |  | 44729.5811 | 50.0336
|  |  | 44729.5811 | 50.0336
|  |  | 44729.5811 | 50.0336
|  |  | 44729.5811 | 50.0335
|  |  | 44729.5811 | 50.0335
|  |  | 44729.5811 | 50.0335
|  |  | 44729.5811 | 50.0336
|  |  | 44729.5811 | 50.0337
|  |  | 44729.5811 | 50.0338
|  |  | 44729.5811 | 50.0339
|  |  | 44729.5811 | 50.0339
|  |  | 44729.5811 | 50.0338
|  |  | 44729.5811 | 50.0337
|  |  | 44729.5811 | 50.0336
|  |  | 44729.5811 | 50.0334
|  |  | 44729.5811 | 50.0333
|  |  | 44729.5811 | 50.0331
|  |  | 44729.5811 | 50.0331
|  |  | 44729.5811 | 50.0331
|  |  | 44729.5811 | 50.0332
|  |  | 44729.5811 | 50.0334
|  |  | 44729.5811 | 50.0335
|  |  | 44729.5811 | 50.0337
|  |  | 44729.5811 | 50.0337
|  |  | 44729.5811 | 50.0338
|  |  | 44729.5811 | 50.0338
|  |  | 44729.5811 | 50.0338
|  |  | 44729.5811 | 50.0337
|  |  | 44729.5811 | 50.0336
|  |  | 44729.5811 | 50.0334
|  |  | 44729.5811 | 50.0332
|  |  | 44729.5811 | 50.0331
|  |  | 44729.5811 | 50.0329
|  |  | 44729.5811 | 50.0328
|  |  | 44729.5811 | 50.0328
|  |  | 44729.5811 | 50.0327
|  |  | 44729.5811 | 50.0328
|  |  | 2022-06-17 13:57 | 50.0328
|  |  | 44729.5811 | 50.0328
|  |  | 44729.5811 | 50.0329
|  |  | 44729.5811 | 50.0329
|  |  | 44729.5811 | 50.0329
|  |  | 44729.5811 | 50.0329
|  |  | 44729.5811 | 50.0329
|  |  | 44729.5811 | 50.0328
|  |  | 44729.5811 | 50.0328
|  |  | 44729.5811 | 50.0328
|  |  | 44729.5811 | 50.0328
|  |  | 44729.5811 | 50.0328
|  |  | 44729.5811 | 50.0328
|  |  | 44729.5811 | 50.0328
|  |  | 44729.5811 | 50.0329
|  |  | 44729.5811 | 50.0329
|  |  | 44729.5811 | 50.0329
|  |  | 44729.5811 | 50.0329
|  |  | 44729.5811 | 50.0328
|  |  | 44729.5811 | 50.0328
|  |  | 44729.5811 | 50.0328
|  |  | 44729.5811 | 50.0328
|  |  | 44729.5811 | 50.0328
|  |  | 44729.5811 | 50.0328
|  |  | 44729.5811 | 50.0328
|  |  | 44729.5811 | 50.0329
|  |  | 44729.5811 | 50.0328
|  |  | 44729.5811 | 50.0327
|  |  | 44729.5811 | 50.0326
|  |  | 44729.5811 | 50.0325
|  |  | 44729.5811 | 50.0324
|  |  | 44729.5811 | 50.0323
|  |  | 44729.5811 | 50.0323
|  |  | 44729.5811 | 50.0322
|  |  | 44729.5811 | 50.0322
|  |  | 44729.5811 | 50.0322
|  |  | 44729.5811 | 50.0322
|  |  | 44729.5811 | 50.0321
|  |  | 44729.5811 | 50.0321
|  |  | 44729.5811 | 50.032
|  |  | 44729.5811 | 50.0318
|  |  | 44729.5811 | 50.0317
|  |  | 44729.5811 | 50.0316
|  |  | 44729.5811 | 50.0315
|  |  | 44729.5811 | 50.0315
|  |  | 44729.5811 | 50.0314
|  |  | 44729.5811 | 50.0313
|  |  | 44729.5811 | 50.0313
|  |  | 44729.5811 | 50.0314
|  |  | 44729.5811 | 50.0314
|  |  | 2022-06-17 13:57 | 50.0314
|  |  | 44729.5811 | 50.0315
|  |  | 44729.5811 | 50.0315
|  |  | 44729.5811 | 50.0314
|  |  | 44729.5811 | 50.0314
|  |  | 44729.5811 | 50.0313
|  |  | 44729.5811 | 50.0313
|  |  | 44729.5811 | 50.0312
|  |  | 44729.5811 | 50.0312
|  |  | 44729.5811 | 50.0312
|  |  | 44729.5811 | 50.0312
|  |  | 44729.5811 | 50.0313
|  |  | 44729.5811 | 50.0313
|  |  | 44729.5811 | 50.0313
|  |  | 44729.5811 | 50.0313
|  |  | 44729.5811 | 50.0312
|  |  | 44729.5811 | 50.0312
|  |  | 44729.5811 | 50.0311
|  |  | 44729.5811 | 50.031
|  |  | 44729.5811 | 50.0309
|  |  | 44729.5811 | 50.0308
|  |  | 44729.5811 | 50.0307
|  |  | 44729.5811 | 50.0307
|  |  | 44729.5811 | 50.0307
|  |  | 44729.5811 | 50.0308
|  |  | 44729.5811 | 50.0309
|  |  | 44729.5811 | 50.0311
|  |  | 44729.5811 | 50.0313
|  |  | 44729.5811 | 50.0314
|  |  | 44729.5811 | 50.0316
|  |  | 44729.5811 | 50.0318
|  |  | 44729.5811 | 50.0318
|  |  | 44729.5811 | 50.0317
|  |  | 44729.5811 | 50.0315
|  |  | 44729.5811 | 50.0314
|  |  | 44729.5811 | 50.0312
|  |  | 44729.5811 | 50.0311
|  |  | 44729.5811 | 50.031
|  |  | 44729.5811 | 50.0309
|  |  | 44729.5811 | 50.0309
|  |  | 44729.5811 | 50.031
|  |  | 44729.5811 | 50.031
|  |  | 44729.5811 | 50.031
|  |  | 44729.5811 | 50.0311
|  |  | 44729.5811 | 50.0312
|  |  | 44729.5811 | 50.0312
|  |  | 44729.5811 | 50.031
|  |  | 44729.5811 | 50.0309
|  |  | 44729.5811 | 50.0308
|  |  | 44729.5811 | 50.0307
|  |  | 2022-06-17 13:57 | 50.0306
|  |  | 44729.5811 | 50.0305
|  |  | 44729.5811 | 50.0304
|  |  | 44729.5811 | 50.0303
|  |  | 44729.5811 | 50.0302
|  |  | 44729.5811 | 50.0302
|  |  | 44729.5811 | 50.0303
|  |  | 44729.5811 | 50.0303
|  |  | 44729.5811 | 50.0303
|  |  | 44729.5811 | 50.0303
|  |  | 44729.5811 | 50.0302
|  |  | 44729.5811 | 50.0301
|  |  | 44729.5811 | 50.03
|  |  | 44729.5811 | 50.0299
|  |  | 44729.5811 | 50.0299
|  |  | 44729.5811 | 50.0298
|  |  | 44729.5811 | 50.0298
|  |  | 44729.5811 | 50.0297
|  |  | 44729.5811 | 50.0295
|  |  | 44729.5812 | 50.0294
|  |  | 44729.5812 | 50.0294
|  |  | 44729.5812 | 50.0293
|  |  | 44729.5812 | 50.0293
|  |  | 44729.5812 | 50.0292
|  |  | 44729.5812 | 50.0292
|  |  | 44729.5812 | 50.0292
|  |  | 44729.5812 | 50.0293
|  |  | 44729.5812 | 50.0294
|  |  | 44729.5812 | 50.0295
|  |  | 44729.5812 | 50.0296
|  |  | 44729.5812 | 50.0297
|  |  | 44729.5812 | 50.0298
|  |  | 44729.5812 | 50.0298
|  |  | 44729.5812 | 50.0298
|  |  | 44729.5812 | 50.0297
|  |  | 44729.5812 | 50.0297
|  |  | 44729.5812 | 50.0296
|  |  | 44729.5812 | 50.0296
|  |  | 44729.5812 | 50.0295
|  |  | 44729.5812 | 50.0295
|  |  | 44729.5812 | 50.0294
|  |  | 44729.5812 | 50.0294
|  |  | 44729.5812 | 50.0293
|  |  | 44729.5812 | 50.0293
|  |  | 44729.5812 | 50.0293
|  |  | 44729.5812 | 50.0293
|  |  | 44729.5812 | 50.0293
|  |  | 44729.5812 | 50.0293
|  |  | 44729.5812 | 50.0293
|  |  | 44729.5812 | 50.0293
|  |  | 2022-06-17 13:57 | 50.0294
|  |  | 44729.5812 | 50.0294
|  |  | 44729.5812 | 50.0295
|  |  | 44729.5812 | 50.0295
|  |  | 44729.5812 | 50.0293
|  |  | 44729.5812 | 50.0292
|  |  | 44729.5812 | 50.029
|  |  | 44729.5812 | 50.0289
|  |  | 44729.5812 | 50.0287
|  |  | 44729.5812 | 50.0285
|  |  | 44729.5812 | 50.0284
|  |  | 44729.5812 | 50.0283
|  |  | 44729.5812 | 50.0282
|  |  | 44729.5812 | 50.0283
|  |  | 44729.5812 | 50.0283
|  |  | 44729.5812 | 50.0283
|  |  | 44729.5812 | 50.0284
|  |  | 44729.5812 | 50.0284
|  |  | 44729.5812 | 50.0285
|  |  | 44729.5812 | 50.0285
|  |  | 44729.5812 | 50.0285
|  |  | 44729.5812 | 50.0285
|  |  | 44729.5812 | 50.0285
|  |  | 44729.5812 | 50.0284
|  |  | 44729.5812 | 50.0282
|  |  | 44729.5812 | 50.0282
|  |  | 44729.5812 | 50.0282
|  |  | 44729.5812 | 50.0281
|  |  | 44729.5812 | 50.0281
|  |  | 44729.5812 | 50.0281
|  |  | 44729.5812 | 50.0281
|  |  | 44729.5812 | 50.0282
|  |  | 44729.5812 | 50.0281
|  |  | 44729.5812 | 50.0282
|  |  | 44729.5812 | 50.0282
|  |  | 44729.5812 | 50.0282
|  |  | 44729.5812 | 50.0282
|  |  | 44729.5812 | 50.0283
|  |  | 44729.5812 | 50.0283
|  |  | 44729.5812 | 50.0283
|  |  | 44729.5812 | 50.0283
|  |  | 44729.5812 | 50.0283
|  |  | 44729.5812 | 50.0283
|  |  | 44729.5812 | 50.0284
|  |  | 44729.5812 | 50.0285
|  |  | 44729.5812 | 50.0286
|  |  | 44729.5812 | 50.0287
|  |  | 44729.5812 | 50.0288
|  |  | 44729.5812 | 50.0289
|  |  | 44729.5812 | 50.0288
|  |  | 2022-06-17 13:57 | 50.0288
|  |  | 44729.5812 | 50.0288
|  |  | 44729.5812 | 50.0288
|  |  | 44729.5812 | 50.0287
|  |  | 44729.5812 | 50.0286
|  |  | 44729.5812 | 50.0286
|  |  | 44729.5812 | 50.0286
|  |  | 44729.5812 | 50.0286
|  |  | 44729.5812 | 50.0286
|  |  | 44729.5812 | 50.0286
|  |  | 44729.5812 | 50.0286
|  |  | 44729.5812 | 50.0287
|  |  | 44729.5812 | 50.0287
|  |  | 44729.5812 | 50.0288
|  |  | 44729.5812 | 50.0289
|  |  | 44729.5812 | 50.0289
|  |  | 44729.5812 | 50.029
|  |  | 44729.5812 | 50.0289
|  |  | 44729.5812 | 50.0289
|  |  | 44729.5812 | 50.0289
|  |  | 44729.5812 | 50.0288
|  |  | 44729.5812 | 50.0288
|  |  | 44729.5812 | 50.0287
|  |  | 44729.5812 | 50.0286
|  |  | 44729.5812 | 50.0286
|  |  | 44729.5812 | 50.0287
|  |  | 44729.5812 | 50.0287
|  |  | 44729.5812 | 50.0288
|  |  | 44729.5812 | 50.0289
|  |  | 44729.5812 | 50.0291
|  |  | 44729.5812 | 50.0293
|  |  | 44729.5812 | 50.0293
|  |  | 44729.5812 | 50.0294
|  |  | 44729.5812 | 50.0296
|  |  | 44729.5812 | 50.0295
|  |  | 44729.5812 | 50.0294
|  |  | 44729.5812 | 50.0293
|  |  | 44729.5812 | 50.0291
|  |  | 44729.5812 | 50.0289
|  |  | 44729.5812 | 50.0288
|  |  | 44729.5812 | 50.0288
|  |  | 44729.5812 | 50.0288
|  |  | 44729.5812 | 50.0288
|  |  | 44729.5812 | 50.029
|  |  | 44729.5812 | 50.0291
|  |  | 44729.5812 | 50.0292
|  |  | 44729.5812 | 50.0294
|  |  | 44729.5812 | 50.0295
|  |  | 44729.5812 | 50.0296
|  |  | 44729.5812 | 50.0297
|  |  | 2022-06-17 13:57 | 50.0297
|  |  | 44729.5812 | 50.0297
|  |  | 44729.5812 | 50.0298
|  |  | 44729.5812 | 50.0298
|  |  | 44729.5812 | 50.0298
|  |  | 44729.5812 | 50.0298
|  |  | 44729.5812 | 50.0298
|  |  | 44729.5812 | 50.0298
|  |  | 44729.5812 | 50.0297
|  |  | 44729.5812 | 50.0297
|  |  | 44729.5812 | 50.0296
|  |  | 44729.5812 | 50.0297
|  |  | 44729.5812 | 50.0297
|  |  | 44729.5812 | 50.0298
|  |  | 44729.5812 | 50.0298
|  |  | 44729.5812 | 50.0297
|  |  | 44729.5812 | 50.0298
|  |  | 44729.5812 | 50.0298
|  |  | 44729.5812 | 50.0298
|  |  | 44729.5812 | 50.0298
|  |  | 44729.5812 | 50.0297
|  |  | 44729.5812 | 50.0296
|  |  | 44729.5812 | 50.0296
|  |  | 44729.5812 | 50.0295
|  |  | 44729.5812 | 50.0295
|  |  | 44729.5812 | 50.0295
|  |  | 44729.5812 | 50.0296
|  |  | 44729.5812 | 50.0296
|  |  | 44729.5812 | 50.0296
|  |  | 44729.5812 | 50.0296
|  |  | 44729.5812 | 50.0296
|  |  | 44729.5812 | 50.0297
|  |  | 44729.5812 | 50.0297
|  |  | 44729.5812 | 50.0296
|  |  | 44729.5812 | 50.0296
|  |  | 44729.5812 | 50.0296
|  |  | 44729.5812 | 50.0295
|  |  | 44729.5812 | 50.0295
|  |  | 44729.5812 | 50.0294
|  |  | 44729.5812 | 50.0294
|  |  | 44729.5812 | 50.0293
|  |  | 44729.5812 | 50.0293
|  |  | 44729.5812 | 50.0292
|  |  | 44729.5812 | 50.0292
|  |  | 44729.5812 | 50.0291
|  |  | 44729.5812 | 50.0292
|  |  | 44729.5812 | 50.0292
|  |  | 44729.5812 | 50.0292
|  |  | 44729.5812 | 50.0292
|  |  | 44729.5812 | 50.0292
|  |  | 2022-06-17 13:57 | 50.0291
|  |  | 44729.5812 | 50.0291
|  |  | 44729.5812 | 50.029
|  |  | 44729.5812 | 50.0289
|  |  | 44729.5812 | 50.0288
|  |  | 44729.5812 | 50.0288
|  |  | 44729.5812 | 50.0287
|  |  | 44729.5812 | 50.0286
|  |  | 44729.5812 | 50.0285
|  |  | 44729.5812 | 50.0283
|  |  | 44729.5812 | 50.0281
|  |  | 44729.5812 | 50.0276
|  |  | 44729.5812 | 50.0267
|  |  | 44729.5812 | 50.0254
|  |  | 44729.5812 | 50.0238
|  |  | 44729.5812 | 50.022
|  |  | 44729.5812 | 50.0201
|  |  | 44729.5812 | 50.0184
|  |  | 44729.5812 | 50.0168
|  |  | 44729.5812 | 50.0155
|  |  | 44729.5812 | 50.0145
|  |  | 44729.5812 | 50.0138
|  |  | 44729.5812 | 50.0133
|  |  | 44729.5812 | 50.0128
|  |  | 44729.5812 | 50.0123
|  |  | 44729.5812 | 50.0116
|  |  | 44729.5812 | 50.0106
|  |  | 44729.5812 | 50.0095
|  |  | 44729.5812 | 50.008
|  |  | 44729.5812 | 50.0064
|  |  | 44729.5812 | 50.0047
|  |  | 44729.5812 | 50.0028
|  |  | 44729.5812 | 50.0007
|  |  | 44729.5812 | 49.9989
|  |  | 44729.5812 | 49.9973
|  |  | 44729.5812 | 49.9955
|  |  | 44729.5812 | 49.994
|  |  | 44729.5812 | 49.9926
|  |  | 44729.5812 | 49.9913
|  |  | 44729.5812 | 49.9901
|  |  | 44729.5812 | 49.989
|  |  | 44729.5812 | 49.9879
|  |  | 44729.5812 | 49.9868
|  |  | 44729.5812 | 49.9856
|  |  | 44729.5812 | 49.9844
|  |  | 44729.5812 | 49.9831
|  |  | 44729.5812 | 49.9818
|  |  | 44729.5812 | 49.9806
|  |  | 44729.5812 | 49.9794
|  |  | 44729.5812 | 49.9782
|  |  | 2022-06-17 13:57 | 49.977
|  |  | 44729.5812 | 49.9759
|  |  | 44729.5812 | 49.9748
|  |  | 44729.5812 | 49.9738
|  |  | 44729.5812 | 49.9726
|  |  | 44729.5812 | 49.9715
|  |  | 44729.5812 | 49.9706
|  |  | 44729.5812 | 49.9696
|  |  | 44729.5812 | 49.9685
|  |  | 44729.5812 | 49.9674
|  |  | 44729.5812 | 49.9663
|  |  | 44729.5812 | 49.9651
|  |  | 44729.5812 | 49.964
|  |  | 44729.5812 | 49.9629
|  |  | 44729.5812 | 49.9618
|  |  | 44729.5812 | 49.9607
|  |  | 44729.5812 | 49.9597
|  |  | 44729.5812 | 49.9587
|  |  | 44729.5812 | 49.9576
|  |  | 44729.5812 | 49.9565
|  |  | 44729.5812 | 49.9554
|  |  | 44729.5812 | 49.9542
|  |  | 44729.5812 | 49.953
|  |  | 44729.5812 | 49.9518
|  |  | 44729.5812 | 49.9505
|  |  | 44729.5812 | 49.9491
|  |  | 44729.5812 | 49.9478
|  |  | 44729.5812 | 49.9465
|  |  | 44729.5812 | 49.9452
|  |  | 44729.5812 | 49.9439
|  |  | 44729.5812 | 49.9425
|  |  | 44729.5812 | 49.9412
|  |  | 44729.5812 | 49.9399
|  |  | 44729.5812 | 49.9386
|  |  | 44729.5812 | 49.9373
|  |  | 44729.5812 | 49.936
|  |  | 44729.5812 | 49.9347
|  |  | 44729.5812 | 49.9333
|  |  | 44729.5812 | 49.932
|  |  | 44729.5812 | 49.9307
|  |  | 44729.5812 | 49.9293
|  |  | 44729.5812 | 49.928
|  |  | 44729.5812 | 49.9267
|  |  | 44729.5812 | 49.9255
|  |  | 44729.5812 | 49.9241
|  |  | 44729.5812 | 49.9228
|  |  | 44729.5812 | 49.9215
|  |  | 44729.5812 | 49.9202
|  |  | 44729.5812 | 49.9189
|  |  | 44729.5812 | 49.9176
|  |  | 2022-06-17 13:57 | 49.9164
|  |  | 44729.5812 | 49.9152
|  |  | 44729.5812 | 49.9141
|  |  | 44729.5812 | 49.913
|  |  | 44729.5812 | 49.9119
|  |  | 44729.5812 | 49.9108
|  |  | 44729.5812 | 49.9098
|  |  | 44729.5812 | 49.9087
|  |  | 44729.5812 | 49.9077
|  |  | 44729.5812 | 49.9067
|  |  | 44729.5812 | 49.9057
|  |  | 44729.5812 | 49.9049
|  |  | 44729.5812 | 49.904
|  |  | 44729.5812 | 49.9031
|  |  | 44729.5812 | 49.9022
|  |  | 44729.5812 | 49.9013
|  |  | 44729.5812 | 49.9005
|  |  | 44729.5812 | 49.8996
|  |  | 44729.5812 | 49.8988
|  |  | 44729.5812 | 49.898
|  |  | 44729.5812 | 49.8971
|  |  | 44729.5812 | 49.8962
|  |  | 44729.5812 | 49.8955
|  |  | 44729.5812 | 49.8946
|  |  | 44729.5812 | 49.8937
|  |  | 44729.5812 | 49.8929
|  |  | 44729.5812 | 49.8921
|  |  | 44729.5812 | 49.8913
|  |  | 44729.5812 | 49.8904
|  |  | 44729.5812 | 49.8896
|  |  | 44729.5812 | 49.8889
|  |  | 44729.5812 | 49.8881
|  |  | 44729.5812 | 49.8874
|  |  | 44729.5812 | 49.8866
|  |  | 44729.5812 | 49.8859
|  |  | 44729.5812 | 49.885
|  |  | 44729.5812 | 49.8842
|  |  | 44729.5812 | 49.8834
|  |  | 44729.5812 | 49.8826
|  |  | 44729.5812 | 49.8818
|  |  | 44729.5812 | 49.8809
|  |  | 44729.5812 | 49.8802
|  |  | 44729.5812 | 49.8795
|  |  | 44729.5812 | 49.8787
|  |  | 44729.5812 | 49.878
|  |  | 44729.5812 | 49.8773
|  |  | 44729.5812 | 49.8765
|  |  | 44729.5812 | 49.8758
|  |  | 44729.5812 | 49.8752
|  |  | 44729.5812 | 49.8745
|  |  | 2022-06-17 13:57 | 49.8738
|  |  | 44729.5812 | 49.873
|  |  | 44729.5812 | 49.8723
|  |  | 44729.5812 | 49.8716
|  |  | 44729.5812 | 49.871
|  |  | 44729.5812 | 49.8703
|  |  | 44729.5812 | 49.8696
|  |  | 44729.5812 | 49.869
|  |  | 44729.5812 | 49.8683
|  |  | 44729.5812 | 49.8675
|  |  | 44729.5812 | 49.8668
|  |  | 44729.5812 | 49.8662
|  |  | 44729.5812 | 49.8657
|  |  | 44729.5812 | 49.8651
|  |  | 44729.5812 | 49.8646
|  |  | 44729.5812 | 49.864
|  |  | 44729.5812 | 49.8634
|  |  | 44729.5812 | 49.8628
|  |  | 44729.5812 | 49.8622
|  |  | 44729.5812 | 49.8616
|  |  | 44729.5812 | 49.861
|  |  | 44729.5812 | 49.8603
|  |  | 44729.5812 | 49.8598
|  |  | 44729.5812 | 49.8592
|  |  | 44729.5812 | 49.8586
|  |  | 44729.5812 | 49.858
|  |  | 44729.5812 | 49.8574
|  |  | 44729.5812 | 49.8566
|  |  | 44729.5812 | 49.856
|  |  | 44729.5812 | 49.8552
|  |  | 44729.5812 | 49.8543
|  |  | 44729.5812 | 49.8532
|  |  | 44729.5812 | 49.852
|  |  | 44729.5812 | 49.8508
|  |  | 44729.5812 | 49.8495
|  |  | 44729.5812 | 49.8483
|  |  | 44729.5812 | 49.8473
|  |  | 44729.5812 | 49.8463
|  |  | 44729.5812 | 49.8454
|  |  | 44729.5812 | 49.8446
|  |  | 44729.5812 | 49.8439
|  |  | 44729.5812 | 49.8431
|  |  | 44729.5812 | 49.8423
|  |  | 44729.5812 | 49.8415
|  |  | 44729.5812 | 49.8405
|  |  | 44729.5812 | 49.8395
|  |  | 44729.5812 | 49.8385
|  |  | 44729.5812 | 49.8374
|  |  | 44729.5812 | 49.8364
|  |  | 44729.5812 | 49.8351
|  |  | 2022-06-17 13:57 | 49.8339
|  |  | 44729.5812 | 49.8328
|  |  | 44729.5812 | 49.8317
|  |  | 44729.5812 | 49.8306
|  |  | 44729.5812 | 49.8296
|  |  | 44729.5812 | 49.8288
|  |  | 44729.5812 | 49.8279
|  |  | 44729.5812 | 49.8271
|  |  | 44729.5812 | 49.8262
|  |  | 44729.5812 | 49.8254
|  |  | 44729.5812 | 49.8245
|  |  | 44729.5812 | 49.8235
|  |  | 44729.5812 | 49.8224
|  |  | 44729.5812 | 49.8213
|  |  | 44729.5812 | 49.8203
|  |  | 44729.5812 | 49.8192
|  |  | 44729.5812 | 49.8182
|  |  | 44729.5812 | 49.8171
|  |  | 44729.5812 | 49.8163
|  |  | 44729.5812 | 49.8155
|  |  | 44729.5812 | 49.8147
|  |  | 44729.5812 | 49.8142
|  |  | 44729.5812 | 49.8137
|  |  | 44729.5812 | 49.813
|  |  | 44729.5812 | 49.8124
|  |  | 44729.5812 | 49.8117
|  |  | 44729.5812 | 49.811
|  |  | 44729.5812 | 49.8102
|  |  | 44729.5812 | 49.8094
|  |  | 44729.5812 | 49.8086
|  |  | 44729.5812 | 49.8079
|  |  | 44729.5812 | 49.807
|  |  | 44729.5812 | 49.8063
|  |  | 44729.5812 | 49.8056
|  |  | 44729.5812 | 49.8049
|  |  | 44729.5812 | 49.8042
|  |  | 44729.5812 | 49.8035
|  |  | 44729.5812 | 49.8027
|  |  | 44729.5812 | 49.8019
|  |  | 44729.5812 | 49.8011
|  |  | 44729.5812 | 49.8003
|  |  | 44729.5812 | 49.7995
|  |  | 44729.5812 | 49.7987
|  |  | 44729.5812 | 49.798
|  |  | 44729.5812 | 49.7972
|  |  | 44729.5812 | 49.7965
|  |  | 44729.5812 | 49.7959
|  |  | 44729.5812 | 49.7952
|  |  | 44729.5812 | 49.7946
|  |  | 44729.5812 | 49.7941
|  |  | 2022-06-17 13:57 | 49.7934
|  |  | 44729.5813 | 49.7927
|  |  | 44729.5813 | 49.7921
|  |  | 44729.5813 | 49.7912
|  |  | 44729.5813 | 49.7904
|  |  | 44729.5813 | 49.7896
|  |  | 44729.5813 | 49.7887
|  |  | 44729.5813 | 49.7879
|  |  | 44729.5813 | 49.787
|  |  | 44729.5813 | 49.7862
|  |  | 44729.5813 | 49.7854
|  |  | 44729.5813 | 49.7847
|  |  | 44729.5813 | 49.7841
|  |  | 44729.5813 | 49.7835
|  |  | 44729.5813 | 49.783
|  |  | 44729.5813 | 49.7826
|  |  | 44729.5813 | 49.7822
|  |  | 44729.5813 | 49.7817
|  |  | 44729.5813 | 49.7813
|  |  | 44729.5813 | 49.7808
|  |  | 44729.5813 | 49.7802
|  |  | 44729.5813 | 49.7796
|  |  | 44729.5813 | 49.779
|  |  | 44729.5813 | 49.7784
|  |  | 44729.5813 | 49.7778
|  |  | 44729.5813 | 49.7773
|  |  | 44729.5813 | 49.7768
|  |  | 44729.5813 | 49.7762
|  |  | 44729.5813 | 49.7757
|  |  | 44729.5813 | 49.7753
|  |  | 44729.5813 | 49.7748
|  |  | 44729.5813 | 49.7743
|  |  | 44729.5813 | 49.7739
|  |  | 44729.5813 | 49.7736
|  |  | 44729.5813 | 49.7733
|  |  | 44729.5813 | 49.7731
|  |  | 44729.5813 | 49.7729
|  |  | 44729.5813 | 49.7726
|  |  | 44729.5813 | 49.7724
|  |  | 44729.5813 | 49.7721
|  |  | 44729.5813 | 49.7718
|  |  | 44729.5813 | 49.7715
|  |  | 44729.5813 | 49.7711
|  |  | 44729.5813 | 49.7706
|  |  | 44729.5813 | 49.7702
|  |  | 44729.5813 | 49.7698
|  |  | 44729.5813 | 49.7694
|  |  | 44729.5813 | 49.7691
|  |  | 44729.5813 | 49.7688
|  |  | 44729.5813 | 49.7686
|  |  | 2022-06-17 13:57 | 49.7684
|  |  | 44729.5813 | 49.7682
|  |  | 44729.5813 | 49.768
|  |  | 44729.5813 | 49.7678
|  |  | 44729.5813 | 49.7676
|  |  | 44729.5813 | 49.7675
|  |  | 44729.5813 | 49.7673
|  |  | 44729.5813 | 49.767
|  |  | 44729.5813 | 49.7668
|  |  | 44729.5813 | 49.7664
|  |  | 44729.5813 | 49.7661
|  |  | 44729.5813 | 49.7658
|  |  | 44729.5813 | 49.7655
|  |  | 44729.5813 | 49.7653
|  |  | 44729.5813 | 49.765
|  |  | 44729.5813 | 49.7649
|  |  | 44729.5813 | 49.7648
|  |  | 44729.5813 | 49.7646
|  |  | 44729.5813 | 49.7646
|  |  | 44729.5813 | 49.7645
|  |  | 44729.5813 | 49.7644
|  |  | 44729.5813 | 49.7643
|  |  | 44729.5813 | 49.7642
|  |  | 44729.5813 | 49.764
|  |  | 44729.5813 | 49.7638
|  |  | 44729.5813 | 49.7636
|  |  | 44729.5813 | 49.7634
|  |  | 44729.5813 | 49.7632
|  |  | 44729.5813 | 49.7631
|  |  | 44729.5813 | 49.7629
|  |  | 44729.5813 | 49.7628
|  |  | 44729.5813 | 49.7627
|  |  | 44729.5813 | 49.7626
|  |  | 44729.5813 | 49.7625
|  |  | 44729.5813 | 49.7624
|  |  | 44729.5813 | 49.7623
|  |  | 44729.5813 | 49.7622
|  |  | 44729.5813 | 49.7621
|  |  | 44729.5813 | 49.762
|  |  | 44729.5813 | 49.7619
|  |  | 44729.5813 | 49.7617
|  |  | 44729.5813 | 49.7616
|  |  | 44729.5813 | 49.7614
|  |  | 44729.5813 | 49.7612
|  |  | 44729.5813 | 49.761
|  |  | 44729.5813 | 49.7609
|  |  | 44729.5813 | 49.7608
|  |  | 44729.5813 | 49.7607
|  |  | 44729.5813 | 49.7606
|  |  | 44729.5813 | 49.7606
|  |  | 2022-06-17 13:57 | 49.7605
|  |  | 44729.5813 | 49.7604
|  |  | 44729.5813 | 49.7604
|  |  | 44729.5813 | 49.7604
|  |  | 44729.5813 | 49.7604
|  |  | 44729.5813 | 49.7603
|  |  | 44729.5813 | 49.7602
|  |  | 44729.5813 | 49.7601
|  |  | 44729.5813 | 49.76
|  |  | 44729.5813 | 49.7599
|  |  | 44729.5813 | 49.7598
|  |  | 44729.5813 | 49.7597
|  |  | 44729.5813 | 49.7596
|  |  | 44729.5813 | 49.7596
|  |  | 44729.5813 | 49.7595
|  |  | 44729.5813 | 49.7596
|  |  | 44729.5813 | 49.7597
|  |  | 44729.5813 | 49.7597
|  |  | 44729.5813 | 49.7598
|  |  | 44729.5813 | 49.7599
|  |  | 44729.5813 | 49.7601
|  |  | 44729.5813 | 49.7601
|  |  | 44729.5813 | 49.7601
|  |  | 44729.5813 | 49.7601
|  |  | 44729.5813 | 49.76
|  |  | 44729.5813 | 49.76
|  |  | 44729.5813 | 49.76
|  |  | 44729.5813 | 49.7601
|  |  | 44729.5813 | 49.7601
|  |  | 44729.5813 | 49.7601
|  |  | 44729.5813 | 49.7602
|  |  | 44729.5813 | 49.7603
|  |  | 44729.5813 | 49.7603
|  |  | 44729.5813 | 49.7603
|  |  | 44729.5813 | 49.7604
|  |  | 44729.5813 | 49.7604
|  |  | 44729.5813 | 49.7604
|  |  | 44729.5813 | 49.7604
|  |  | 44729.5813 | 49.7604
|  |  | 44729.5813 | 49.7603
|  |  | 44729.5813 | 49.7602
|  |  | 44729.5813 | 49.76
|  |  | 44729.5813 | 49.7599
|  |  | 44729.5813 | 49.7599
|  |  | 44729.5813 | 49.7599
|  |  | 44729.5813 | 49.7598
|  |  | 44729.5813 | 49.7597
|  |  | 44729.5813 | 49.7597
|  |  | 44729.5813 | 49.7597
|  |  | 44729.5813 | 49.7598
|  |  | 2022-06-17 13:57 | 49.7598
|  |  | 44729.5813 | 49.7598
|  |  | 44729.5813 | 49.7599
|  |  | 44729.5813 | 49.7599
|  |  | 44729.5813 | 49.7599
|  |  | 44729.5813 | 49.7598
|  |  | 44729.5813 | 49.7598
|  |  | 44729.5813 | 49.7597
|  |  | 44729.5813 | 49.7596
|  |  | 44729.5813 | 49.7596
|  |  | 44729.5813 | 49.7594
|  |  | 44729.5813 | 49.7594
|  |  | 44729.5813 | 49.7593
|  |  | 44729.5813 | 49.7592
|  |  | 44729.5813 | 49.7592
|  |  | 44729.5813 | 49.7591
|  |  | 44729.5813 | 49.759
|  |  | 44729.5813 | 49.7591
|  |  | 44729.5813 | 49.759
|  |  | 44729.5813 | 49.759
|  |  | 44729.5813 | 49.7589
|  |  | 44729.5813 | 49.7589
|  |  | 44729.5813 | 49.7588
|  |  | 44729.5813 | 49.7589
|  |  | 44729.5813 | 49.759
|  |  | 44729.5813 | 49.759
|  |  | 44729.5813 | 49.7591
|  |  | 44729.5813 | 49.7592
|  |  | 44729.5813 | 49.7592
|  |  | 44729.5813 | 49.7592
|  |  | 44729.5813 | 49.7592
|  |  | 44729.5813 | 49.759
|  |  | 44729.5813 | 49.7589
|  |  | 44729.5813 | 49.7588
|  |  | 44729.5813 | 49.7587
|  |  | 44729.5813 | 49.7586
|  |  | 44729.5813 | 49.7586
|  |  | 44729.5813 | 49.7587
|  |  | 44729.5813 | 49.7588
|  |  | 44729.5813 | 49.7588
|  |  | 44729.5813 | 49.7589
|  |  | 44729.5813 | 49.7591
|  |  | 44729.5813 | 49.7592
|  |  | 44729.5813 | 49.7592
|  |  | 44729.5813 | 49.7591
|  |  | 44729.5813 | 49.759
|  |  | 44729.5813 | 49.7589
|  |  | 44729.5813 | 49.7587
|  |  | 44729.5813 | 49.7587
|  |  | 44729.5813 | 49.7586
|  |  | 2022-06-17 13:57 | 49.7586
|  |  | 44729.5813 | 49.7587
|  |  | 44729.5813 | 49.7588
|  |  | 44729.5813 | 49.7588
|  |  | 44729.5813 | 49.7588
|  |  | 44729.5813 | 49.7587
|  |  | 44729.5813 | 49.7586
|  |  | 44729.5813 | 49.7585
|  |  | 44729.5813 | 49.7584
|  |  | 44729.5813 | 49.7582
|  |  | 44729.5813 | 49.7581
|  |  | 44729.5813 | 49.7579
|  |  | 44729.5813 | 49.7579
|  |  | 44729.5813 | 49.7579
|  |  | 44729.5813 | 49.7579
|  |  | 44729.5813 | 49.758
|  |  | 44729.5813 | 49.7581
|  |  | 44729.5813 | 49.7582
|  |  | 44729.5813 | 49.7582
|  |  | 44729.5813 | 49.7582
|  |  | 44729.5813 | 49.7581
|  |  | 44729.5813 | 49.7581
|  |  | 44729.5813 | 49.758
|  |  | 44729.5813 | 49.7579
|  |  | 44729.5813 | 49.7579
|  |  | 44729.5813 | 49.7579
|  |  | 44729.5813 | 49.758
|  |  | 44729.5813 | 49.758
|  |  | 44729.5813 | 49.7581
|  |  | 44729.5813 | 49.7582
|  |  | 44729.5813 | 49.7582
|  |  | 44729.5813 | 49.7582
|  |  | 44729.5813 | 49.7582
|  |  | 44729.5813 | 49.7581
|  |  | 44729.5813 | 49.7579
|  |  | 44729.5813 | 49.7578
|  |  | 44729.5813 | 49.7576
|  |  | 44729.5813 | 49.7576
|  |  | 44729.5813 | 49.7575
|  |  | 44729.5813 | 49.7575
|  |  | 44729.5813 | 49.7576
|  |  | 44729.5813 | 49.7577
|  |  | 44729.5813 | 49.7579
|  |  | 44729.5813 | 49.7579
|  |  | 44729.5813 | 49.7581
|  |  | 44729.5813 | 49.7582
|  |  | 44729.5813 | 49.7582
|  |  | 44729.5813 | 49.7583
|  |  | 44729.5813 | 49.7582
|  |  | 44729.5813 | 49.7582
|  |  | 2022-06-17 13:57 | 49.7581
|  |  | 44729.5813 | 49.7581
|  |  | 44729.5813 | 49.7581
|  |  | 44729.5813 | 49.7581
|  |  | 44729.5813 | 49.7581
|  |  | 44729.5813 | 49.7581
|  |  | 44729.5813 | 49.758
|  |  | 44729.5813 | 49.758
|  |  | 44729.5813 | 49.7579
|  |  | 44729.5813 | 49.7579
|  |  | 44729.5813 | 49.7579
|  |  | 44729.5813 | 49.7579
|  |  | 44729.5813 | 49.7579
|  |  | 44729.5813 | 49.7579
|  |  | 44729.5813 | 49.7579
|  |  | 44729.5813 | 49.7579
|  |  | 44729.5813 | 49.758
|  |  | 44729.5813 | 49.758
|  |  | 44729.5813 | 49.7581
|  |  | 44729.5813 | 49.7581
|  |  | 44729.5813 | 49.7582
|  |  | 44729.5813 | 49.7583
|  |  | 44729.5813 | 49.7583
|  |  | 44729.5813 | 49.7584
|  |  | 44729.5813 | 49.7584
|  |  | 44729.5813 | 49.7584
|  |  | 44729.5813 | 49.7584
|  |  | 44729.5813 | 49.7583
|  |  | 44729.5813 | 49.7581
|  |  | 44729.5813 | 49.758
|  |  | 44729.5813 | 49.758
|  |  | 44729.5813 | 49.758
|  |  | 44729.5813 | 49.758
|  |  | 44729.5813 | 49.7581
|  |  | 44729.5813 | 49.7581
|  |  | 44729.5813 | 49.7581
|  |  | 44729.5813 | 49.7582
|  |  | 44729.5813 | 49.7583
|  |  | 44729.5813 | 49.7583
|  |  | 44729.5813 | 49.7583
|  |  | 44729.5813 | 49.7584
|  |  | 44729.5813 | 49.7583
|  |  | 44729.5813 | 49.7582
|  |  | 44729.5813 | 49.7582
|  |  | 44729.5813 | 49.7581
|  |  | 44729.5813 | 49.7581
|  |  | 44729.5813 | 49.7581
|  |  | 44729.5813 | 49.7581
|  |  | 44729.5813 | 49.7582
|  |  | 44729.5813 | 49.7582
|  |  | 2022-06-17 13:57 | 49.7583
|  |  | 44729.5813 | 49.7584
|  |  | 44729.5813 | 49.7585
|  |  | 44729.5813 | 49.7586
|  |  | 44729.5813 | 49.7586
|  |  | 44729.5813 | 49.7587
|  |  | 44729.5813 | 49.7586
|  |  | 44729.5813 | 49.7585
|  |  | 44729.5813 | 49.7583
|  |  | 44729.5813 | 49.7582
|  |  | 44729.5813 | 49.758
|  |  | 44729.5813 | 49.758
|  |  | 44729.5813 | 49.7579
|  |  | 44729.5813 | 49.7578
|  |  | 44729.5813 | 49.7577
|  |  | 44729.5813 | 49.7578
|  |  | 44729.5813 | 49.7578
|  |  | 44729.5813 | 49.7578
|  |  | 44729.5813 | 49.7579
|  |  | 44729.5813 | 49.7579
|  |  | 44729.5813 | 49.7579
|  |  | 44729.5813 | 49.7579
|  |  | 44729.5813 | 49.7579
|  |  | 44729.5813 | 49.7579
|  |  | 44729.5813 | 49.7578
|  |  | 44729.5813 | 49.7578
|  |  | 44729.5813 | 49.7579
|  |  | 44729.5813 | 49.7578
|  |  | 44729.5813 | 49.7578
|  |  | 44729.5813 | 49.7577
|  |  | 44729.5813 | 49.7576
|  |  | 44729.5813 | 49.7576
|  |  | 44729.5813 | 49.7575
|  |  | 44729.5813 | 49.7574
|  |  | 44729.5813 | 49.7572
|  |  | 44729.5813 | 49.7571
|  |  | 44729.5813 | 49.7571
|  |  | 44729.5813 | 49.757
|  |  | 44729.5813 | 49.757
|  |  | 44729.5813 | 49.757
|  |  | 44729.5813 | 49.7571
|  |  | 44729.5813 | 49.7571
|  |  | 44729.5813 | 49.7572
|  |  | 44729.5813 | 49.7573
|  |  | 44729.5813 | 49.7573
|  |  | 44729.5813 | 49.7573
|  |  | 44729.5813 | 49.7573
|  |  | 44729.5813 | 49.7571
|  |  | 44729.5813 | 49.757
|  |  | 44729.5813 | 49.7569
|  |  | 2022-06-17 13:57 | 49.7568
|  |  | 44729.5813 | 49.7567
|  |  | 44729.5813 | 49.7566
|  |  | 44729.5813 | 49.7565
|  |  | 44729.5813 | 49.7565
|  |  | 44729.5813 | 49.7565
|  |  | 44729.5813 | 49.7565
|  |  | 44729.5813 | 49.7565
|  |  | 44729.5813 | 49.7566
|  |  | 44729.5813 | 49.7567
|  |  | 44729.5813 | 49.7568
|  |  | 44729.5813 | 49.7568
|  |  | 44729.5813 | 49.7568
|  |  | 44729.5813 | 49.7569
|  |  | 44729.5813 | 49.7569
|  |  | 44729.5813 | 49.7568
|  |  | 44729.5813 | 49.7567
|  |  | 44729.5813 | 49.7565
|  |  | 44729.5813 | 49.7563
|  |  | 44729.5813 | 49.7562
|  |  | 44729.5813 | 49.7561
|  |  | 44729.5813 | 49.756
|  |  | 44729.5813 | 49.7559
|  |  | 44729.5813 | 49.7559
|  |  | 44729.5813 | 49.7558
|  |  | 44729.5813 | 49.7559
|  |  | 44729.5813 | 49.7559
|  |  | 44729.5813 | 49.7559
|  |  | 44729.5813 | 49.7559
|  |  | 44729.5813 | 49.7559
|  |  | 44729.5813 | 49.7558
|  |  | 44729.5813 | 49.7557
|  |  | 44729.5813 | 49.7556
|  |  | 44729.5813 | 49.7555
|  |  | 44729.5813 | 49.7554
|  |  | 44729.5813 | 49.7553
|  |  | 44729.5813 | 49.7553
|  |  | 44729.5813 | 49.7553
|  |  | 44729.5813 | 49.7553
|  |  | 44729.5813 | 49.7554
|  |  | 44729.5813 | 49.7554
|  |  | 44729.5813 | 49.7555
|  |  | 44729.5813 | 49.7555
|  |  | 44729.5813 | 49.7555
|  |  | 44729.5813 | 49.7555
|  |  | 44729.5813 | 49.7555
|  |  | 44729.5813 | 49.7555
|  |  | 44729.5813 | 49.7555
|  |  | 44729.5813 | 49.7555
|  |  | 44729.5813 | 49.7555
|  |  | 2022-06-17 13:57 | 49.7555
|  |  | 44729.5813 | 49.7556
|  |  | 44729.5813 | 49.7556
|  |  | 44729.5813 | 49.7556
|  |  | 44729.5813 | 49.7556
|  |  | 44729.5813 | 49.7555
|  |  | 44729.5813 | 49.7554
|  |  | 44729.5813 | 49.7553
|  |  | 44729.5813 | 49.7552
|  |  | 44729.5813 | 49.7552
|  |  | 44729.5813 | 49.7551
|  |  | 44729.5813 | 49.7551
|  |  | 44729.5813 | 49.755
|  |  | 44729.5813 | 49.755
|  |  | 44729.5813 | 49.755
|  |  | 44729.5813 | 49.755
|  |  | 44729.5813 | 49.755
|  |  | 44729.5813 | 49.755
|  |  | 44729.5813 | 49.7551
|  |  | 44729.5813 | 49.755
|  |  | 44729.5813 | 49.755
|  |  | 44729.5813 | 49.7549
|  |  | 44729.5813 | 49.7549
|  |  | 44729.5813 | 49.7548
|  |  | 44729.5813 | 49.7546
|  |  | 44729.5813 | 49.7544
|  |  | 44729.5813 | 49.7542
|  |  | 44729.5813 | 49.754
|  |  | 44729.5813 | 49.7538
|  |  | 44729.5813 | 49.7536
|  |  | 44729.5813 | 49.7536
|  |  | 44729.5813 | 49.7536
|  |  | 44729.5814 | 49.7535
|  |  | 44729.5814 | 49.7535
|  |  | 44729.5814 | 49.7536
|  |  | 44729.5814 | 49.7535
|  |  | 44729.5814 | 49.7535
|  |  | 44729.5814 | 49.7535
|  |  | 44729.5814 | 49.7534
|  |  | 44729.5814 | 49.7532
|  |  | 44729.5814 | 49.7531
|  |  | 44729.5814 | 49.753
|  |  | 44729.5814 | 49.7528
|  |  | 44729.5814 | 49.7528
|  |  | 44729.5814 | 49.7527
|  |  | 44729.5814 | 49.7527
|  |  | 44729.5814 | 49.7527
|  |  | 44729.5814 | 49.7526
|  |  | 44729.5814 | 49.7526
|  |  | 44729.5814 | 49.7526
|  |  | 2022-06-17 13:57 | 49.7525
|  |  | 44729.5814 | 49.7524
|  |  | 44729.5814 | 49.7523
|  |  | 44729.5814 | 49.7522
|  |  | 44729.5814 | 49.7522
|  |  | 44729.5814 | 49.752
|  |  | 44729.5814 | 49.7519
|  |  | 44729.5814 | 49.7518
|  |  | 44729.5814 | 49.7517
|  |  | 44729.5814 | 49.7516
|  |  | 44729.5814 | 49.7515
|  |  | 44729.5814 | 49.7515
|  |  | 44729.5814 | 49.7515
|  |  | 44729.5814 | 49.7515
|  |  | 44729.5814 | 49.7516
|  |  | 44729.5814 | 49.7516
|  |  | 44729.5814 | 49.7516
|  |  | 44729.5814 | 49.7515
|  |  | 44729.5814 | 49.7514
|  |  | 44729.5814 | 49.7512
|  |  | 44729.5814 | 49.7509
|  |  | 44729.5814 | 49.7507
|  |  | 44729.5814 | 49.7504
|  |  | 44729.5814 | 49.7503
|  |  | 44729.5814 | 49.7502
|  |  | 44729.5814 | 49.7501
|  |  | 44729.5814 | 49.7501
|  |  | 44729.5814 | 49.7501
|  |  | 44729.5814 | 49.7502
|  |  | 44729.5814 | 49.7502
|  |  | 44729.5814 | 49.7502
|  |  | 44729.5814 | 49.7501
|  |  | 44729.5814 | 49.7501
|  |  | 44729.5814 | 49.75
|  |  | 44729.5814 | 49.7498
|  |  | 44729.5814 | 49.7497
|  |  | 44729.5814 | 49.7495
|  |  | 44729.5814 | 49.7493
|  |  | 44729.5814 | 49.7492
|  |  | 44729.5814 | 49.749
|  |  | 44729.5814 | 49.7489
|  |  | 44729.5814 | 49.7488
|  |  | 44729.5814 | 49.7487
|  |  | 44729.5814 | 49.7487
|  |  | 44729.5814 | 49.7486
|  |  | 44729.5814 | 49.7486
|  |  | 44729.5814 | 49.7485
|  |  | 44729.5814 | 49.7485
|  |  | 44729.5814 | 49.7485
|  |  | 44729.5814 | 49.7485
|  |  | 2022-06-17 13:57 | 49.7485
|  |  | 44729.5814 | 49.7483
|  |  | 44729.5814 | 49.7482
|  |  | 44729.5814 | 49.7482
|  |  | 44729.5814 | 49.7481
|  |  | 44729.5814 | 49.748
|  |  | 44729.5814 | 49.7479
|  |  | 44729.5814 | 49.7479
|  |  | 44729.5814 | 49.7478
|  |  | 44729.5814 | 49.7478
|  |  | 44729.5814 | 49.7478
|  |  | 44729.5814 | 49.7478
|  |  | 44729.5814 | 49.7479
|  |  | 44729.5814 | 49.7479
|  |  | 44729.5814 | 49.748
|  |  | 44729.5814 | 49.748
|  |  | 44729.5814 | 49.748
|  |  | 44729.5814 | 49.748
|  |  | 44729.5814 | 49.748
|  |  | 44729.5814 | 49.748
|  |  | 44729.5814 | 49.7481
|  |  | 44729.5814 | 49.7481
|  |  | 44729.5814 | 49.7481
|  |  | 44729.5814 | 49.748
|  |  | 44729.5814 | 49.748
|  |  | 44729.5814 | 49.748
|  |  | 44729.5814 | 49.748
|  |  | 44729.5814 | 49.748
|  |  | 44729.5814 | 49.7479
|  |  | 44729.5814 | 49.7479
|  |  | 44729.5814 | 49.7479
|  |  | 44729.5814 | 49.748
|  |  | 44729.5814 | 49.748
|  |  | 44729.5814 | 49.748
|  |  | 44729.5814 | 49.748
|  |  | 44729.5814 | 49.748
|  |  | 44729.5814 | 49.748
|  |  | 44729.5814 | 49.7479
|  |  | 44729.5814 | 49.7479
|  |  | 44729.5814 | 49.7479
|  |  | 44729.5814 | 49.748
|  |  | 44729.5814 | 49.7481
|  |  | 44729.5814 | 49.7482
|  |  | 44729.5814 | 49.7483
|  |  | 44729.5814 | 49.7485
|  |  | 44729.5814 | 49.7486
|  |  | 44729.5814 | 49.7488
|  |  | 44729.5814 | 49.7488
|  |  | 44729.5814 | 49.7489
|  |  | 44729.5814 | 49.7488
|  |  | 2022-06-17 13:57 | 49.7488
|  |  | 44729.5814 | 49.7488
|  |  | 44729.5814 | 49.7489
|  |  | 44729.5814 | 49.7488
|  |  | 44729.5814 | 49.7489
|  |  | 44729.5814 | 49.7489
|  |  | 44729.5814 | 49.7489
|  |  | 44729.5814 | 49.7489
|  |  | 44729.5814 | 49.749
|  |  | 44729.5814 | 49.749
|  |  | 44729.5814 | 49.749
|  |  | 44729.5814 | 49.749
|  |  | 44729.5814 | 49.749
|  |  | 44729.5814 | 49.749
|  |  | 44729.5814 | 49.7491
|  |  | 44729.5814 | 49.7492
|  |  | 44729.5814 | 49.7492
|  |  | 44729.5814 | 49.7493
|  |  | 44729.5814 | 49.7493
|  |  | 44729.5814 | 49.7494
|  |  | 44729.5814 | 49.7494
|  |  | 44729.5814 | 49.7494
|  |  | 44729.5814 | 49.7494
|  |  | 44729.5814 | 49.7496
|  |  | 44729.5814 | 49.7496
|  |  | 44729.5814 | 49.7495
|  |  | 44729.5814 | 49.7495
|  |  | 44729.5814 | 49.7494
|  |  | 44729.5814 | 49.7493
|  |  | 44729.5814 | 49.7493
|  |  | 44729.5814 | 49.7493
|  |  | 44729.5814 | 49.7493
|  |  | 44729.5814 | 49.7493
|  |  | 44729.5814 | 49.7494
|  |  | 44729.5814 | 49.7496
|  |  | 44729.5814 | 49.7499
|  |  | 44729.5814 | 49.75
|  |  | 44729.5814 | 49.7502
|  |  | 44729.5814 | 49.7503
|  |  | 44729.5814 | 49.7503
|  |  | 44729.5814 | 49.7502
|  |  | 44729.5814 | 49.75
|  |  | 44729.5814 | 49.7498
|  |  | 44729.5814 | 49.7497
|  |  | 44729.5814 | 49.7497
|  |  | 44729.5814 | 49.7496
|  |  | 44729.5814 | 49.7496
|  |  | 44729.5814 | 49.7498
|  |  | 44729.5814 | 49.7499
|  |  | 44729.5814 | 49.7501
|  |  | 2022-06-17 13:57 | 49.7503
|  |  | 44729.5814 | 49.7504
|  |  | 44729.5814 | 49.7505
|  |  | 44729.5814 | 49.7506
|  |  | 44729.5814 | 49.7507
|  |  | 44729.5814 | 49.7507
|  |  | 44729.5814 | 49.7507
|  |  | 44729.5814 | 49.7508
|  |  | 44729.5814 | 49.7508
|  |  | 44729.5814 | 49.7507
|  |  | 44729.5814 | 49.7507
|  |  | 44729.5814 | 49.7506
|  |  | 44729.5814 | 49.7505
|  |  | 44729.5814 | 49.7505
|  |  | 44729.5814 | 49.7504
|  |  | 44729.5814 | 49.7504
|  |  | 44729.5814 | 49.7504
|  |  | 44729.5814 | 49.7504
|  |  | 44729.5814 | 49.7504
|  |  | 44729.5814 | 49.7504
|  |  | 44729.5814 | 49.7506
|  |  | 44729.5814 | 49.7507
|  |  | 44729.5814 | 49.7508
|  |  | 44729.5814 | 49.7509
|  |  | 44729.5814 | 49.751
|  |  | 44729.5814 | 49.7511
|  |  | 44729.5814 | 49.7512
|  |  | 44729.5814 | 49.7512
|  |  | 44729.5814 | 49.7512
|  |  | 44729.5814 | 49.7511
|  |  | 44729.5814 | 49.7511
|  |  | 44729.5814 | 49.7511
|  |  | 44729.5814 | 49.7509
|  |  | 44729.5814 | 49.7509
|  |  | 44729.5814 | 49.751
|  |  | 44729.5814 | 49.751
|  |  | 44729.5814 | 49.7511
|  |  | 44729.5814 | 49.7512
|  |  | 44729.5814 | 49.7513
|  |  | 44729.5814 | 49.7515
|  |  | 44729.5814 | 49.7516
|  |  | 44729.5814 | 49.7517
|  |  | 44729.5814 | 49.7518
|  |  | 44729.5814 | 49.7519
|  |  | 44729.5814 | 49.7521
|  |  | 44729.5814 | 49.7522
|  |  | 44729.5814 | 49.7523
|  |  | 44729.5814 | 49.7523
|  |  | 44729.5814 | 49.7524
|  |  | 44729.5814 | 49.7525
|  |  | 2022-06-17 13:57 | 49.7525
|  |  | 44729.5814 | 49.7525
|  |  | 44729.5814 | 49.7526
|  |  | 44729.5814 | 49.7526
|  |  | 44729.5814 | 49.7528
|  |  | 44729.5814 | 49.7529
|  |  | 44729.5814 | 49.7529
|  |  | 44729.5814 | 49.753
|  |  | 44729.5814 | 49.7531
|  |  | 44729.5814 | 49.7532
|  |  | 44729.5814 | 49.7532
|  |  | 44729.5814 | 49.7533
|  |  | 44729.5814 | 49.7533
|  |  | 44729.5814 | 49.7533
|  |  | 44729.5814 | 49.7533
|  |  | 44729.5814 | 49.7533
|  |  | 44729.5814 | 49.7533
|  |  | 44729.5814 | 49.7533
|  |  | 44729.5814 | 49.7534
|  |  | 44729.5814 | 49.7535
|  |  | 44729.5814 | 49.7535
|  |  | 44729.5814 | 49.7537
|  |  | 44729.5814 | 49.7538
|  |  | 44729.5814 | 49.754
|  |  | 44729.5814 | 49.7541
|  |  | 44729.5814 | 49.7542
|  |  | 44729.5814 | 49.7543
|  |  | 44729.5814 | 49.7544
|  |  | 44729.5814 | 49.7544
|  |  | 44729.5814 | 49.7543
|  |  | 44729.5814 | 49.7544
|  |  | 44729.5814 | 49.7545
|  |  | 44729.5814 | 49.7546
|  |  | 44729.5814 | 49.7547
|  |  | 44729.5814 | 49.7548
|  |  | 44729.5814 | 49.7548
|  |  | 44729.5814 | 49.755
|  |  | 44729.5814 | 49.755
|  |  | 44729.5814 | 49.7551
|  |  | 44729.5814 | 49.7553
|  |  | 44729.5814 | 49.7554
|  |  | 44729.5814 | 49.7555
|  |  | 44729.5814 | 49.7556
|  |  | 44729.5814 | 49.7556
|  |  | 44729.5814 | 49.7555
|  |  | 44729.5814 | 49.7555
|  |  | 44729.5814 | 49.7555
|  |  | 44729.5814 | 49.7554
|  |  | 44729.5814 | 49.7554
|  |  | 44729.5814 | 49.7555
|  |  | 2022-06-17 13:57 | 49.7555
|  |  | 44729.5814 | 49.7557
|  |  | 44729.5814 | 49.7559
|  |  | 44729.5814 | 49.7561
|  |  | 44729.5814 | 49.7562
|  |  | 44729.5814 | 49.7564
|  |  | 44729.5814 | 49.7566
|  |  | 44729.5814 | 49.7567
|  |  | 44729.5814 | 49.7568
|  |  | 44729.5814 | 49.7569
|  |  | 44729.5814 | 49.7569
|  |  | 44729.5814 | 49.7569
|  |  | 44729.5814 | 49.757
|  |  | 44729.5814 | 49.757
|  |  | 44729.5814 | 49.7571
|  |  | 44729.5814 | 49.7571
|  |  | 44729.5814 | 49.7571
|  |  | 44729.5814 | 49.7571
|  |  | 44729.5814 | 49.7571
|  |  | 44729.5814 | 49.7572
|  |  | 44729.5814 | 49.7573
|  |  | 44729.5814 | 49.7574
|  |  | 44729.5814 | 49.7574
|  |  | 44729.5814 | 49.7575
|  |  | 44729.5814 | 49.7575
|  |  | 44729.5814 | 49.7576
|  |  | 44729.5814 | 49.7577
|  |  | 44729.5814 | 49.7578
|  |  | 44729.5814 | 49.7578
|  |  | 44729.5814 | 49.7579
|  |  | 44729.5814 | 49.758
|  |  | 44729.5814 | 49.7579
|  |  | 44729.5814 | 49.7579
|  |  | 44729.5814 | 49.758
|  |  | 44729.5814 | 49.758
|  |  | 44729.5814 | 49.7579
|  |  | 44729.5814 | 49.7579
|  |  | 44729.5814 | 49.7578
|  |  | 44729.5814 | 49.7578
|  |  | 44729.5814 | 49.7578
|  |  | 44729.5814 | 49.7579
|  |  | 44729.5814 | 49.7579
|  |  | 44729.5814 | 49.7579
|  |  | 44729.5814 | 49.758
|  |  | 44729.5814 | 49.758
|  |  | 44729.5814 | 49.758
|  |  | 44729.5814 | 49.7581
|  |  | 44729.5814 | 49.7581
|  |  | 44729.5814 | 49.7582
|  |  | 44729.5814 | 49.7582
|  |  | 2022-06-17 13:57 | 49.7582
|  |  | 44729.5814 | 49.7583
|  |  | 44729.5814 | 49.7584
|  |  | 44729.5814 | 49.7584
|  |  | 44729.5814 | 49.7583
|  |  | 44729.5814 | 49.7583
|  |  | 44729.5814 | 49.7583
|  |  | 44729.5814 | 49.7583
|  |  | 44729.5814 | 49.7583
|  |  | 44729.5814 | 49.7583
|  |  | 44729.5814 | 49.7584
|  |  | 44729.5814 | 49.7585
|  |  | 44729.5814 | 49.7585
|  |  | 44729.5814 | 49.7585
|  |  | 44729.5814 | 49.7585
|  |  | 44729.5814 | 49.7583
|  |  | 44729.5814 | 49.7583
|  |  | 44729.5814 | 49.7582
|  |  | 44729.5814 | 49.7581
|  |  | 44729.5814 | 49.7581
|  |  | 44729.5814 | 49.758
|  |  | 44729.5814 | 49.758
|  |  | 44729.5814 | 49.7579
|  |  | 44729.5814 | 49.7579
|  |  | 44729.5814 | 49.7579
|  |  | 44729.5814 | 49.758
|  |  | 44729.5814 | 49.7581
|  |  | 44729.5814 | 49.7581
|  |  | 44729.5814 | 49.758
|  |  | 44729.5814 | 49.758
|  |  | 44729.5814 | 49.758
|  |  | 44729.5814 | 49.7579
|  |  | 44729.5814 | 49.7578
|  |  | 44729.5814 | 49.7577
|  |  | 44729.5814 | 49.7577
|  |  | 44729.5814 | 49.7576
|  |  | 44729.5814 | 49.7576
|  |  | 44729.5814 | 49.7577
|  |  | 44729.5814 | 49.7578
|  |  | 44729.5814 | 49.7578
|  |  | 44729.5814 | 49.7579
|  |  | 44729.5814 | 49.758
|  |  | 44729.5814 | 49.7581
|  |  | 44729.5814 | 49.7582
|  |  | 44729.5814 | 49.7583
|  |  | 44729.5814 | 49.7584
|  |  | 44729.5814 | 49.7583
|  |  | 44729.5814 | 49.7581
|  |  | 44729.5814 | 49.7582
|  |  | 44729.5814 | 49.7582
|  |  | 2022-06-17 13:57 | 49.7582
|  |  | 44729.5814 | 49.7581
|  |  | 44729.5814 | 49.7581
|  |  | 44729.5814 | 49.7581
|  |  | 44729.5814 | 49.758
|  |  | 44729.5814 | 49.7581
|  |  | 44729.5814 | 49.7581
|  |  | 44729.5814 | 49.7581
|  |  | 44729.5814 | 49.7581
|  |  | 44729.5814 | 49.7582
|  |  | 44729.5814 | 49.7583
|  |  | 44729.5814 | 49.7583
|  |  | 44729.5814 | 49.7584
|  |  | 44729.5814 | 49.7585
|  |  | 44729.5814 | 49.7585
|  |  | 44729.5814 | 49.7586
|  |  | 44729.5814 | 49.7587
|  |  | 44729.5814 | 49.7588
|  |  | 44729.5814 | 49.7588
|  |  | 44729.5814 | 49.759
|  |  | 44729.5814 | 49.7589
|  |  | 44729.5814 | 49.759
|  |  | 44729.5814 | 49.759
|  |  | 44729.5814 | 49.759
|  |  | 44729.5814 | 49.759
|  |  | 44729.5814 | 49.759
|  |  | 44729.5814 | 49.759
|  |  | 44729.5814 | 49.7589
|  |  | 44729.5814 | 49.7589
|  |  | 44729.5814 | 49.7588
|  |  | 44729.5814 | 49.7586
|  |  | 44729.5814 | 49.7586
|  |  | 44729.5814 | 49.7585
|  |  | 44729.5814 | 49.7585
|  |  | 44729.5814 | 49.7585
|  |  | 44729.5814 | 49.7585
|  |  | 44729.5814 | 49.7585
|  |  | 44729.5814 | 49.7586
|  |  | 44729.5814 | 49.7586
|  |  | 44729.5814 | 49.7586
|  |  | 44729.5814 | 49.7586
|  |  | 44729.5814 | 49.7584
|  |  | 44729.5814 | 49.7584
|  |  | 44729.5814 | 49.7582
|  |  | 44729.5814 | 49.7581
|  |  | 44729.5814 | 49.7579
|  |  | 44729.5814 | 49.7579
|  |  | 44729.5814 | 49.7579
|  |  | 44729.5814 | 49.7579
|  |  | 44729.5814 | 49.7579
|  |  | 2022-06-17 13:57 | 49.7579
|  |  | 44729.5814 | 49.758
|  |  | 44729.5814 | 49.7581
|  |  | 44729.5814 | 49.7582
|  |  | 44729.5814 | 49.7583
|  |  | 44729.5814 | 49.7584
|  |  | 44729.5814 | 49.7584
|  |  | 44729.5814 | 49.7584
|  |  | 44729.5814 | 49.7584
|  |  | 44729.5814 | 49.7583
|  |  | 44729.5814 | 49.7583
|  |  | 44729.5814 | 49.7582
|  |  | 44729.5814 | 49.7582
|  |  | 44729.5814 | 49.7581
|  |  | 44729.5814 | 49.7581
|  |  | 44729.5815 | 49.758
|  |  | 44729.5815 | 49.7581
|  |  | 44729.5815 | 49.7581
|  |  | 44729.5815 | 49.7582
|  |  | 44729.5815 | 49.7583
|  |  | 44729.5815 | 49.7584
|  |  | 44729.5815 | 49.7585
|  |  | 44729.5815 | 49.7585
|  |  | 44729.5815 | 49.7586
|  |  | 44729.5815 | 49.7586
|  |  | 44729.5815 | 49.7586
|  |  | 44729.5815 | 49.7586
|  |  | 44729.5815 | 49.7585
|  |  | 44729.5815 | 49.7585
|  |  | 44729.5815 | 49.7585
|  |  | 44729.5815 | 49.7585
|  |  | 44729.5815 | 49.7584
|  |  | 44729.5815 | 49.7584
|  |  | 44729.5815 | 49.7584
|  |  | 44729.5815 | 49.7584
|  |  | 44729.5815 | 49.7583
|  |  | 44729.5815 | 49.7583
|  |  | 44729.5815 | 49.7582
|  |  | 44729.5815 | 49.7582
|  |  | 44729.5815 | 49.7582
|  |  | 44729.5815 | 49.7582
|  |  | 44729.5815 | 49.7582
|  |  | 44729.5815 | 49.7582
|  |  | 44729.5815 | 49.7583
|  |  | 44729.5815 | 49.7583
|  |  | 44729.5815 | 49.7583
|  |  | 44729.5815 | 49.7583
|  |  | 44729.5815 | 49.7583
|  |  | 44729.5815 | 49.7583
|  |  | 44729.5815 | 49.7583
|  |  | 2022-06-17 13:57 | 49.7584
|  |  | 44729.5815 | 49.7584
|  |  | 44729.5815 | 49.7585
|  |  | 44729.5815 | 49.7586
|  |  | 44729.5815 | 49.7587
|  |  | 44729.5815 | 49.7589
|  |  | 44729.5815 | 49.759
|  |  | 44729.5815 | 49.7591
|  |  | 44729.5815 | 49.7592
|  |  | 44729.5815 | 49.7593
|  |  | 44729.5815 | 49.7593
|  |  | 44729.5815 | 49.7593
|  |  | 44729.5815 | 49.7593
|  |  | 44729.5815 | 49.7593
|  |  | 44729.5815 | 49.7593
|  |  | 44729.5815 | 49.7593
|  |  | 44729.5815 | 49.7593
|  |  | 44729.5815 | 49.7594
|  |  | 44729.5815 | 49.7595
|  |  | 44729.5815 | 49.7596
|  |  | 44729.5815 | 49.7596
|  |  | 44729.5815 | 49.7596
|  |  | 44729.5815 | 49.7596
|  |  | 44729.5815 | 49.7595
|  |  | 44729.5815 | 49.7595
|  |  | 44729.5815 | 49.7593
|  |  | 44729.5815 | 49.7592
|  |  | 44729.5815 | 49.7591
|  |  | 44729.5815 | 49.7591
|  |  | 44729.5815 | 49.7591
|  |  | 44729.5815 | 49.7593
|  |  | 44729.5815 | 49.7593
|  |  | 44729.5815 | 49.7593
|  |  | 44729.5815 | 49.7594
|  |  | 44729.5815 | 49.7594
|  |  | 44729.5815 | 49.7593
|  |  | 44729.5815 | 49.7593
|  |  | 44729.5815 | 49.7593
|  |  | 44729.5815 | 49.7592
|  |  | 44729.5815 | 49.7593
|  |  | 44729.5815 | 49.7593
|  |  | 44729.5815 | 49.7592
|  |  | 44729.5815 | 49.7591
|  |  | 44729.5815 | 49.7588
|  |  | 44729.5815 | 49.7588
|  |  | 44729.5815 | 49.7588
|  |  | 44729.5815 | 49.7588
|  |  | 44729.5815 | 49.7588
|  |  | 44729.5815 | 49.7588
|  |  | 44729.5815 | 49.7589
|  |  | 2022-06-17 13:57 | 49.759
|  |  | 44729.5815 | 49.7589
|  |  | 44729.5815 | 49.7589
|  |  | 44729.5815 | 49.7589
|  |  | 44729.5815 | 49.7589
|  |  | 44729.5815 | 49.7588
|  |  | 44729.5815 | 49.7588
|  |  | 44729.5815 | 49.7588
|  |  | 44729.5815 | 49.7588
|  |  | 44729.5815 | 49.7589
|  |  | 44729.5815 | 49.7589
|  |  | 44729.5815 | 49.759
|  |  | 44729.5815 | 49.7591
|  |  | 44729.5815 | 49.7592
|  |  | 44729.5815 | 49.7594
|  |  | 44729.5815 | 49.7596
|  |  | 44729.5815 | 49.7597
|  |  | 44729.5815 | 49.7598
|  |  | 44729.5815 | 49.76
|  |  | 44729.5815 | 49.76
|  |  | 44729.5815 | 49.76
|  |  | 44729.5815 | 49.7599
|  |  | 44729.5815 | 49.7599
|  |  | 44729.5815 | 49.7598
|  |  | 44729.5815 | 49.7598
|  |  | 44729.5815 | 49.7598
|  |  | 44729.5815 | 49.7597
|  |  | 44729.5815 | 49.7597
|  |  | 44729.5815 | 49.7597
|  |  | 44729.5815 | 49.7597
|  |  | 44729.5815 | 49.7597
|  |  | 44729.5815 | 49.7598
|  |  | 44729.5815 | 49.7599
|  |  | 44729.5815 | 49.7599
|  |  | 44729.5815 | 49.76
|  |  | 44729.5815 | 49.76
|  |  | 44729.5815 | 49.7601
|  |  | 44729.5815 | 49.7602
|  |  | 44729.5815 | 49.7603
|  |  | 44729.5815 | 49.7603
|  |  | 44729.5815 | 49.7603
|  |  | 44729.5815 | 49.7603
|  |  | 44729.5815 | 49.7603
|  |  | 44729.5815 | 49.7603
|  |  | 44729.5815 | 49.7603
|  |  | 44729.5815 | 49.7604
|  |  | 44729.5815 | 49.7604
|  |  | 44729.5815 | 49.7605
|  |  | 44729.5815 | 49.7605
|  |  | 44729.5815 | 49.7606
|  |  | 2022-06-17 13:57 | 49.7606
|  |  | 44729.5815 | 49.7606
|  |  | 44729.5815 | 49.7607
|  |  | 44729.5815 | 49.7607
|  |  | 44729.5815 | 49.7607
|  |  | 44729.5815 | 49.7607
|  |  | 44729.5815 | 49.7606
|  |  | 44729.5815 | 49.7607
|  |  | 44729.5815 | 49.7607
|  |  | 44729.5815 | 49.7608
|  |  | 44729.5815 | 49.761
|  |  | 44729.5815 | 49.7611
|  |  | 44729.5815 | 49.7612
|  |  | 44729.5815 | 49.7614
|  |  | 44729.5815 | 49.7615
|  |  | 44729.5815 | 49.7617
|  |  | 44729.5815 | 49.7618
|  |  | 44729.5815 | 49.7618
|  |  | 44729.5815 | 49.7618
|  |  | 44729.5815 | 49.7617
|  |  | 44729.5815 | 49.7617
|  |  | 44729.5815 | 49.7616
|  |  | 44729.5815 | 49.7616
|  |  | 44729.5815 | 49.7616
|  |  | 44729.5815 | 49.7616
|  |  | 44729.5815 | 49.7616
|  |  | 44729.5815 | 49.7616
|  |  | 44729.5815 | 49.7617
|  |  | 44729.5815 | 49.7618
|  |  | 44729.5815 | 49.762
|  |  | 44729.5815 | 49.762
|  |  | 44729.5815 | 49.7621
|  |  | 44729.5815 | 49.7622
|  |  | 44729.5815 | 49.7623
|  |  | 44729.5815 | 49.7623
|  |  | 44729.5815 | 49.7623
|  |  | 44729.5815 | 49.7623
|  |  | 44729.5815 | 49.7622
|  |  | 44729.5815 | 49.7621
|  |  | 44729.5815 | 49.7621
|  |  | 44729.5815 | 49.7621
|  |  | 44729.5815 | 49.7621
|  |  | 44729.5815 | 49.7621
|  |  | 44729.5815 | 49.7621
|  |  | 44729.5815 | 49.7622
|  |  | 44729.5815 | 49.7622
|  |  | 44729.5815 | 49.7621
|  |  | 44729.5815 | 49.7621
|  |  | 44729.5815 | 49.7621
|  |  | 44729.5815 | 49.7621
|  |  | 2022-06-17 13:57 | 49.7621
|  |  | 44729.5815 | 49.7621
|  |  | 44729.5815 | 49.7621
|  |  | 44729.5815 | 49.7621
|  |  | 44729.5815 | 49.7621
|  |  | 44729.5815 | 49.7621
|  |  | 44729.5815 | 49.7621
|  |  | 44729.5815 | 49.762
|  |  | 44729.5815 | 49.762
|  |  | 44729.5815 | 49.762
|  |  | 44729.5815 | 49.762
|  |  | 44729.5815 | 49.7621
|  |  | 44729.5815 | 49.762
|  |  | 44729.5815 | 49.762
|  |  | 44729.5815 | 49.762
|  |  | 44729.5815 | 49.762
|  |  | 44729.5815 | 49.762
|  |  | 44729.5815 | 49.7619
|  |  | 44729.5815 | 49.7618
|  |  | 44729.5815 | 49.7617
|  |  | 44729.5815 | 49.7617
|  |  | 44729.5815 | 49.7616
|  |  | 44729.5815 | 49.7615
|  |  | 44729.5815 | 49.7614
|  |  | 44729.5815 | 49.7614
|  |  | 44729.5815 | 49.7614
|  |  | 44729.5815 | 49.7613
|  |  | 44729.5815 | 49.7613
|  |  | 44729.5815 | 49.7613
|  |  | 44729.5815 | 49.7613
|  |  | 44729.5815 | 49.7613
|  |  | 44729.5815 | 49.7614
|  |  | 44729.5815 | 49.7614
|  |  | 44729.5815 | 49.7614
|  |  | 44729.5815 | 49.7614
|  |  | 44729.5815 | 49.7614
|  |  | 44729.5815 | 49.7613
|  |  | 44729.5815 | 49.7612
|  |  | 44729.5815 | 49.7611
|  |  | 44729.5815 | 49.7611
|  |  | 44729.5815 | 49.7611
|  |  | 44729.5815 | 49.7611
|  |  | 44729.5815 | 49.7611
|  |  | 44729.5815 | 49.7611
|  |  | 44729.5815 | 49.761
|  |  | 44729.5815 | 49.761
|  |  | 44729.5815 | 49.7609
|  |  | 44729.5815 | 49.761
|  |  | 44729.5815 | 49.7609
|  |  | 44729.5815 | 49.7609
|  |  | 2022-06-17 13:57 | 49.7608
|  |  | 44729.5815 | 49.7608
|  |  | 44729.5815 | 49.7608
|  |  | 44729.5815 | 49.7608
|  |  | 44729.5815 | 49.7608
|  |  | 44729.5815 | 49.7608
|  |  | 44729.5815 | 49.7608
|  |  | 44729.5815 | 49.7607
|  |  | 44729.5815 | 49.7606
|  |  | 44729.5815 | 49.7603
|  |  | 44729.5815 | 49.7602
|  |  | 44729.5815 | 49.7602
|  |  | 44729.5815 | 49.7601
|  |  | 44729.5815 | 49.7601
|  |  | 44729.5815 | 49.7601
|  |  | 44729.5815 | 49.7601
|  |  | 44729.5815 | 49.7601
|  |  | 44729.5815 | 49.7601
|  |  | 44729.5815 | 49.7601
|  |  | 44729.5815 | 49.7601
|  |  | 44729.5815 | 49.7601
|  |  | 44729.5815 | 49.7601
|  |  | 44729.5815 | 49.7601
|  |  | 44729.5815 | 49.76
|  |  | 44729.5815 | 49.7601
|  |  | 44729.5815 | 49.76
|  |  | 44729.5815 | 49.76
|  |  | 44729.5815 | 49.7599
|  |  | 44729.5815 | 49.7599
|  |  | 44729.5815 | 49.7597
|  |  | 44729.5815 | 49.7597
|  |  | 44729.5815 | 49.7596
|  |  | 44729.5815 | 49.7596
|  |  | 44729.5815 | 49.7595
|  |  | 44729.5815 | 49.7595
|  |  | 44729.5815 | 49.7594
|  |  | 44729.5815 | 49.7594
|  |  | 44729.5815 | 49.7594
|  |  | 44729.5815 | 49.7594
|  |  | 44729.5815 | 49.7593
|  |  | 44729.5815 | 49.7592
|  |  | 44729.5815 | 49.7591
|  |  | 44729.5815 | 49.759
|  |  | 44729.5815 | 49.7589
|  |  | 44729.5815 | 49.7588
|  |  | 44729.5815 | 49.7587
|  |  | 44729.5815 | 49.7586
|  |  | 44729.5815 | 49.7584
|  |  | 44729.5815 | 49.7584
|  |  | 44729.5815 | 49.7583
|  |  | 2022-06-17 13:57 | 49.7582
|  |  | 44729.5815 | 49.7582
|  |  | 44729.5815 | 49.7581
|  |  | 44729.5815 | 49.758
|  |  | 44729.5815 | 49.7579
|  |  | 44729.5815 | 49.7578
|  |  | 44729.5815 | 49.7577
|  |  | 44729.5815 | 49.7576
|  |  | 44729.5815 | 49.7575
|  |  | 44729.5815 | 49.7574
|  |  | 44729.5815 | 49.7573
|  |  | 44729.5815 | 49.7573
|  |  | 44729.5815 | 49.7572
|  |  | 44729.5815 | 49.7572
|  |  | 44729.5815 | 49.7572
|  |  | 44729.5815 | 49.7572
|  |  | 44729.5815 | 49.7573
|  |  | 44729.5815 | 49.7574
|  |  | 44729.5815 | 49.7574
|  |  | 44729.5815 | 49.7574
|  |  | 44729.5815 | 49.7574
|  |  | 44729.5815 | 49.7573
|  |  | 44729.5815 | 49.7572
|  |  | 44729.5815 | 49.7571
|  |  | 44729.5815 | 49.7571
|  |  | 44729.5815 | 49.7569
|  |  | 44729.5815 | 49.7569
|  |  | 44729.5815 | 49.757
|  |  | 44729.5815 | 49.757
|  |  | 44729.5815 | 49.757
|  |  | 44729.5815 | 49.757
|  |  | 44729.5815 | 49.757
|  |  | 44729.5815 | 49.7569
|  |  | 44729.5815 | 49.7568
|  |  | 44729.5815 | 49.7568
|  |  | 44729.5815 | 49.7567
|  |  | 44729.5815 | 49.7566
|  |  | 44729.5815 | 49.7565
|  |  | 44729.5815 | 49.7565
|  |  | 44729.5815 | 49.7564
|  |  | 44729.5815 | 49.7564
|  |  | 44729.5815 | 49.7564
|  |  | 44729.5815 | 49.7565
|  |  | 44729.5815 | 49.7565
|  |  | 44729.5815 | 49.7565
|  |  | 44729.5815 | 49.7564
|  |  | 44729.5815 | 49.7563
|  |  | 44729.5815 | 49.7561
|  |  | 44729.5815 | 49.7559
|  |  | 44729.5815 | 49.7556
|  |  | 2022-06-17 13:57 | 49.7554
|  |  | 44729.5815 | 49.7552
|  |  | 44729.5815 | 49.7552
|  |  | 44729.5815 | 49.7551
|  |  | 44729.5815 | 49.7552
|  |  | 44729.5815 | 49.7553
|  |  | 44729.5815 | 49.7555
|  |  | 44729.5815 | 49.7557
|  |  | 44729.5815 | 49.7559
|  |  | 44729.5815 | 49.7561
|  |  | 44729.5815 | 49.7561
|  |  | 44729.5815 | 49.7561
|  |  | 44729.5815 | 49.7559
|  |  | 44729.5815 | 49.7556
|  |  | 44729.5815 | 49.7554
|  |  | 44729.5815 | 49.7551
|  |  | 44729.5815 | 49.7549
|  |  | 44729.5815 | 49.7548
|  |  | 44729.5815 | 49.7547
|  |  | 44729.5815 | 49.7548
|  |  | 44729.5815 | 49.7548
|  |  | 44729.5815 | 49.7549
|  |  | 44729.5815 | 49.7551
|  |  | 44729.5815 | 49.7553
|  |  | 44729.5815 | 49.7555
|  |  | 44729.5815 | 49.7556
|  |  | 44729.5815 | 49.7555
|  |  | 44729.5815 | 49.7554
|  |  | 44729.5815 | 49.7553
|  |  | 44729.5815 | 49.755
|  |  | 44729.5815 | 49.7548
|  |  | 44729.5815 | 49.7546
|  |  | 44729.5815 | 49.7544
|  |  | 44729.5815 | 49.7543
|  |  | 44729.5815 | 49.7542
|  |  | 44729.5815 | 49.7541
|  |  | 44729.5815 | 49.7542
|  |  | 44729.5815 | 49.7542
|  |  | 44729.5815 | 49.7541
|  |  | 44729.5815 | 49.754
|  |  | 44729.5815 | 49.7539
|  |  | 44729.5815 | 49.7538
|  |  | 44729.5815 | 49.7536
|  |  | 44729.5815 | 49.7535
|  |  | 44729.5815 | 49.7533
|  |  | 44729.5815 | 49.7533
|  |  | 44729.5815 | 49.7532
|  |  | 44729.5815 | 49.7532
|  |  | 44729.5815 | 49.7532
|  |  | 44729.5815 | 49.7532
|  |  | 2022-06-17 13:57 | 49.7533
|  |  | 44729.5815 | 49.7533
|  |  | 44729.5815 | 49.7534
|  |  | 44729.5815 | 49.7534
|  |  | 44729.5815 | 49.7534
|  |  | 44729.5815 | 49.7534
|  |  | 44729.5815 | 49.7533
|  |  | 44729.5815 | 49.7533
|  |  | 44729.5815 | 49.7532
|  |  | 44729.5815 | 49.7532
|  |  | 44729.5815 | 49.7531
|  |  | 44729.5815 | 49.753
|  |  | 44729.5815 | 49.753
|  |  | 44729.5815 | 49.7531
|  |  | 44729.5815 | 49.753
|  |  | 44729.5815 | 49.753
|  |  | 44729.5815 | 49.753
|  |  | 44729.5815 | 49.753
|  |  | 44729.5815 | 49.753
|  |  | 44729.5815 | 49.753
|  |  | 44729.5815 | 49.753
|  |  | 44729.5815 | 49.7529
|  |  | 44729.5815 | 49.7528
|  |  | 44729.5815 | 49.7527
|  |  | 44729.5815 | 49.7527
|  |  | 44729.5815 | 49.7526
|  |  | 44729.5815 | 49.7527
|  |  | 44729.5815 | 49.7527
|  |  | 44729.5815 | 49.7526
|  |  | 44729.5815 | 49.7526
|  |  | 44729.5815 | 49.7526
|  |  | 44729.5815 | 49.7525
|  |  | 44729.5815 | 49.7526
|  |  | 44729.5815 | 49.7527
|  |  | 44729.5815 | 49.7525
|  |  | 44729.5815 | 49.7524
|  |  | 44729.5815 | 49.7522
|  |  | 44729.5815 | 49.7521
|  |  | 44729.5815 | 49.7519
|  |  | 44729.5815 | 49.7517
|  |  | 44729.5815 | 49.7517
|  |  | 44729.5815 | 49.7515
|  |  | 44729.5815 | 49.7514
|  |  | 44729.5815 | 49.7515
|  |  | 44729.5815 | 49.7515
|  |  | 44729.5815 | 49.7515
|  |  | 44729.5816 | 49.7516
|  |  | 44729.5816 | 49.7516
|  |  | 44729.5816 | 49.7517
|  |  | 44729.5816 | 49.7518
|  |  | 2022-06-17 13:57 | 49.7518
|  |  | 44729.5816 | 49.7518
|  |  | 44729.5816 | 49.7518
|  |  | 44729.5816 | 49.7518
|  |  | 44729.5816 | 49.7517
|  |  | 44729.5816 | 49.7517
|  |  | 44729.5816 | 49.7517
|  |  | 44729.5816 | 49.7517
|  |  | 44729.5816 | 49.7517
|  |  | 44729.5816 | 49.7516
|  |  | 44729.5816 | 49.7516
|  |  | 44729.5816 | 49.7516
|  |  | 44729.5816 | 49.7516
|  |  | 44729.5816 | 49.7516
|  |  | 44729.5816 | 49.7515
|  |  | 44729.5816 | 49.7515
|  |  | 44729.5816 | 49.7516
|  |  | 44729.5816 | 49.7516
|  |  | 44729.5816 | 49.7516
|  |  | 44729.5816 | 49.7517
|  |  | 44729.5816 | 49.7516
|  |  | 44729.5816 | 49.7517
|  |  | 44729.5816 | 49.7517
|  |  | 44729.5816 | 49.7518
|  |  | 44729.5816 | 49.7519
|  |  | 44729.5816 | 49.7519
|  |  | 44729.5816 | 49.7519
|  |  | 44729.5816 | 49.7519
|  |  | 44729.5816 | 49.7518
|  |  | 44729.5816 | 49.7518
|  |  | 44729.5816 | 49.7518
|  |  | 44729.5816 | 49.7517
|  |  | 44729.5816 | 49.7517
|  |  | 44729.5816 | 49.7517
|  |  | 44729.5816 | 49.7517
|  |  | 44729.5816 | 49.7518
|  |  | 44729.5816 | 49.7519
|  |  | 44729.5816 | 49.752
|  |  | 44729.5816 | 49.7522
|  |  | 44729.5816 | 49.7523
|  |  | 44729.5816 | 49.7524
|  |  | 44729.5816 | 49.7524
|  |  | 44729.5816 | 49.7525
|  |  | 44729.5816 | 49.7525
|  |  | 44729.5816 | 49.7524
|  |  | 44729.5816 | 49.7524
|  |  | 44729.5816 | 49.7524
|  |  | 44729.5816 | 49.7523
|  |  | 44729.5816 | 49.7523
|  |  | 44729.5816 | 49.7523
|  |  | 2022-06-17 13:57 | 49.7524
|  |  | 44729.5816 | 49.7525
|  |  | 44729.5816 | 49.7526
|  |  | 44729.5816 | 49.7526
|  |  | 44729.5816 | 49.7527
|  |  | 44729.5816 | 49.7527
|  |  | 44729.5816 | 49.7527
|  |  | 44729.5816 | 49.7527
|  |  | 44729.5816 | 49.7527
|  |  | 44729.5816 | 49.7527
|  |  | 44729.5816 | 49.7528
|  |  | 44729.5816 | 49.7529
|  |  | 44729.5816 | 49.7531
|  |  | 44729.5816 | 49.7531
|  |  | 44729.5816 | 49.7533
|  |  | 44729.5816 | 49.7535
|  |  | 44729.5816 | 49.7536
|  |  | 44729.5816 | 49.7538
|  |  | 44729.5816 | 49.7539
|  |  | 44729.5816 | 49.7541
|  |  | 44729.5816 | 49.7542
|  |  | 44729.5816 | 49.7543
|  |  | 44729.5816 | 49.7544
|  |  | 44729.5816 | 49.7545
|  |  | 44729.5816 | 49.7545
|  |  | 44729.5816 | 49.7545
|  |  | 44729.5816 | 49.7545
|  |  | 44729.5816 | 49.7545
|  |  | 44729.5816 | 49.7546
|  |  | 44729.5816 | 49.7547
|  |  | 44729.5816 | 49.7549
|  |  | 44729.5816 | 49.755
|  |  | 44729.5816 | 49.7552
|  |  | 44729.5816 | 49.7553
|  |  | 44729.5816 | 49.7554
|  |  | 44729.5816 | 49.7555
|  |  | 44729.5816 | 49.7556
|  |  | 44729.5816 | 49.7556
|  |  | 44729.5816 | 49.7557
|  |  | 44729.5816 | 49.7557
|  |  | 44729.5816 | 49.7556
|  |  | 44729.5816 | 49.7558
|  |  | 44729.5816 | 49.7559
|  |  | 44729.5816 | 49.756
|  |  | 44729.5816 | 49.7562
|  |  | 44729.5816 | 49.7563
|  |  | 44729.5816 | 49.7563
|  |  | 44729.5816 | 49.7563
|  |  | 44729.5816 | 49.7563
|  |  | 44729.5816 | 49.7563
|  |  | 2022-06-17 13:57 | 49.7564
|  |  | 44729.5816 | 49.7564
|  |  | 44729.5816 | 49.7565
|  |  | 44729.5816 | 49.7565
|  |  | 44729.5816 | 49.7566
|  |  | 44729.5816 | 49.7567
|  |  | 44729.5816 | 49.7568
|  |  | 44729.5816 | 49.7568
|  |  | 44729.5816 | 49.7568
|  |  | 44729.5816 | 49.7568
|  |  | 44729.5816 | 49.7568
|  |  | 44729.5816 | 49.7568
|  |  | 44729.5816 | 49.7568
|  |  | 44729.5816 | 49.7569
|  |  | 44729.5816 | 49.7569
|  |  | 44729.5816 | 49.7569
|  |  | 44729.5816 | 49.757
|  |  | 44729.5816 | 49.757
|  |  | 44729.5816 | 49.7572
|  |  | 44729.5816 | 49.7573
|  |  | 44729.5816 | 49.7575
|  |  | 44729.5816 | 49.7576
|  |  | 44729.5816 | 49.7577
|  |  | 44729.5816 | 49.7578
|  |  | 44729.5816 | 49.7579
|  |  | 44729.5816 | 49.7579
|  |  | 44729.5816 | 49.758
|  |  | 44729.5816 | 49.758
|  |  | 44729.5816 | 49.7579
|  |  | 44729.5816 | 49.7579
|  |  | 44729.5816 | 49.7578
|  |  | 44729.5816 | 49.7577
|  |  | 44729.5816 | 49.7576
|  |  | 44729.5816 | 49.7576
|  |  | 44729.5816 | 49.7575
|  |  | 44729.5816 | 49.7576
|  |  | 44729.5816 | 49.7577
|  |  | 44729.5816 | 49.7578
|  |  | 44729.5816 | 49.7579
|  |  | 44729.5816 | 49.758
|  |  | 44729.5816 | 49.758
|  |  | 44729.5816 | 49.7582
|  |  | 44729.5816 | 49.7582
|  |  | 44729.5816 | 49.7583
|  |  | 44729.5816 | 49.7583
|  |  | 44729.5816 | 49.7583
|  |  | 44729.5816 | 49.7584
|  |  | 44729.5816 | 49.7585
|  |  | 44729.5816 | 49.7586
|  |  | 44729.5816 | 49.7587
|  |  | 2022-06-17 13:57 | 49.7588
|  |  | 44729.5816 | 49.7589
|  |  | 44729.5816 | 49.759
|  |  | 44729.5816 | 49.759
|  |  | 44729.5816 | 49.759
|  |  | 44729.5816 | 49.759
|  |  | 44729.5816 | 49.7589
|  |  | 44729.5816 | 49.7589
|  |  | 44729.5816 | 49.7588
|  |  | 44729.5816 | 49.7587
|  |  | 44729.5816 | 49.7587
|  |  | 44729.5816 | 49.7587
|  |  | 44729.5816 | 49.7586
|  |  | 44729.5816 | 49.7587
|  |  | 44729.5816 | 49.7587
|  |  | 44729.5816 | 49.7587
|  |  | 44729.5816 | 49.7587
|  |  | 44729.5816 | 49.7588
|  |  | 44729.5816 | 49.7588
|  |  | 44729.5816 | 49.7588
|  |  | 44729.5816 | 49.7588
|  |  | 44729.5816 | 49.7588
|  |  | 44729.5816 | 49.7588
|  |  | 44729.5816 | 49.7587
|  |  | 44729.5816 | 49.7586
|  |  | 44729.5816 | 49.7585
|  |  | 44729.5816 | 49.7585
|  |  | 44729.5816 | 49.7584
|  |  | 44729.5816 | 49.7583
|  |  | 44729.5816 | 49.7582
|  |  | 44729.5816 | 49.7581
|  |  | 44729.5816 | 49.7581
|  |  | 44729.5816 | 49.7581
|  |  | 44729.5816 | 49.7582
|  |  | 44729.5816 | 49.7582
|  |  | 44729.5816 | 49.7582
|  |  | 44729.5816 | 49.7583
|  |  | 44729.5816 | 49.7583
|  |  | 44729.5816 | 49.7583
|  |  | 44729.5816 | 49.7583
|  |  | 44729.5816 | 49.7583
|  |  | 44729.5816 | 49.7583
|  |  | 44729.5816 | 49.7583
|  |  | 44729.5816 | 49.7583
|  |  | 44729.5816 | 49.7583
|  |  | 44729.5816 | 49.7584
|  |  | 44729.5816 | 49.7583
|  |  | 44729.5816 | 49.7584
|  |  | 44729.5816 | 49.7585
|  |  | 44729.5816 | 49.7585
|  |  | 2022-06-17 13:57 | 49.7586

## 20220621-1
In GMT |  |  | High resolution Incident data
Date | Time | Freq | time | freq
2022-06-21 | 9:53 | 49.925 | 2022-06-21 10:54 | 49.9009
2022-06-21 | 9:53 | 49.924 | 44733.4543 | 49.901
2022-06-21 | 9:53 | 49.923 | 44733.4543 | 49.9011
2022-06-21 | 9:53 | 49.922 | 44733.4543 | 49.9012
2022-06-21 | 9:53 | 49.922 | 44733.4543 | 49.9013
2022-06-21 | 9:53 | 49.925 | 44733.4543 | 49.9014
2022-06-21 | 9:53 | 49.924 | 44733.4543 | 49.9014
2022-06-21 | 9:53 | 49.927 | 44733.4543 | 49.9015
2022-06-21 | 9:53 | 49.929 | 44733.4543 | 49.9015
2022-06-21 | 9:53 | 49.931 | 44733.4543 | 49.9015
2022-06-21 | 9:53 | 49.932 | 44733.4543 | 49.9015
2022-06-21 | 9:53 | 49.932 | 44733.4543 | 49.9015
2022-06-21 | 9:53 | 49.932 | 44733.4543 | 49.9015
2022-06-21 | 9:53 | 49.932 | 44733.4543 | 49.9015
2022-06-21 | 9:53 | 49.931 | 44733.4543 | 49.9015
2022-06-21 | 9:53 | 49.93 | 44733.4543 | 49.9016
2022-06-21 | 9:53 | 49.928 | 44733.4543 | 49.9017
2022-06-21 | 9:53 | 49.928 | 44733.4543 | 49.9017
2022-06-21 | 9:53 | 49.928 | 44733.4543 | 49.9019
2022-06-21 | 9:53 | 49.928 | 44733.4543 | 49.9019
2022-06-21 | 9:53 | 49.926 | 44733.4543 | 49.9019
2022-06-21 | 9:53 | 49.925 | 44733.4543 | 49.9019
2022-06-21 | 9:53 | 49.926 | 44733.4543 | 49.902
2022-06-21 | 9:53 | 49.927 | 44733.4543 | 49.902
2022-06-21 | 9:53 | 49.925 | 44733.4543 | 49.902
2022-06-21 | 9:53 | 49.927 | 44733.4543 | 49.902
2022-06-21 | 9:53 | 49.926 | 44733.4543 | 49.902
2022-06-21 | 9:53 | 49.925 | 44733.4543 | 49.9021
2022-06-21 | 9:53 | 49.925 | 44733.4543 | 49.9022
2022-06-21 | 9:53 | 49.924 | 44733.4543 | 49.9022
2022-06-21 | 9:54 | 49.923 | 44733.4543 | 49.9023
2022-06-21 | 9:54 | 49.922 | 44733.4543 | 49.9023
2022-06-21 | 9:54 | 49.92 | 44733.4543 | 49.9024
2022-06-21 | 9:54 | 49.919 | 44733.4543 | 49.9024
2022-06-21 | 9:54 | 49.917 | 44733.4543 | 49.9025
2022-06-21 | 9:54 | 49.918 | 44733.4543 | 49.9024
2022-06-21 | 9:54 | 49.921 | 44733.4543 | 49.9025
2022-06-21 | 9:54 | 49.92 | 44733.4543 | 49.9025
2022-06-21 | 9:54 | 49.922 | 44733.4543 | 49.9026
2022-06-21 | 9:54 | 49.922 | 44733.4543 | 49.9026
2022-06-21 | 9:54 | 49.922 | 44733.4543 | 49.9027
2022-06-21 | 9:54 | 49.924 | 44733.4543 | 49.9027
2022-06-21 | 9:54 | 49.925 | 44733.4543 | 49.9027
2022-06-21 | 9:54 | 49.925 | 44733.4544 | 49.9027
2022-06-21 | 9:54 | 49.924 | 44733.4544 | 49.9027
2022-06-21 | 9:54 | 49.922 | 44733.4544 | 49.9027
2022-06-21 | 9:54 | 49.922 | 44733.4544 | 49.9027
2022-06-21 | 9:54 | 49.921 | 44733.4544 | 49.9028
2022-06-21 | 9:54 | 49.924 | 44733.4544 | 49.9028
2022-06-21 | 9:54 | 49.924 | 44733.4544 | 49.9028
2022-06-21 | 9:54 | 49.923 | 2022-06-21 10:54 | 49.9028
2022-06-21 | 9:54 | 49.923 | 44733.4544 | 49.9028
2022-06-21 | 9:54 | 49.924 | 44733.4544 | 49.9028
2022-06-21 | 9:54 | 49.923 | 44733.4544 | 49.9029
2022-06-21 | 9:54 | 49.925 | 44733.4544 | 49.9029
2022-06-21 | 9:54 | 49.924 | 44733.4544 | 49.9029
2022-06-21 | 9:54 | 49.925 | 44733.4544 | 49.9029
2022-06-21 | 9:54 | 49.924 | 44733.4544 | 49.9029
2022-06-21 | 9:54 | 49.922 | 44733.4544 | 49.9029
2022-06-21 | 9:54 | 49.92 | 44733.4544 | 49.9029
2022-06-21 | 9:54 | 49.917 | 44733.4544 | 49.9029
2022-06-21 | 9:54 | 49.911 | 44733.4544 | 49.9028
2022-06-21 | 9:54 | 49.906 | 44733.4544 | 49.9028
2022-06-21 | 9:54 | 49.902 | 44733.4544 | 49.9028
2022-06-21 | 9:54 | 49.899 | 44733.4544 | 49.9028
2022-06-21 | 9:54 | 49.9 | 44733.4544 | 49.9028
2022-06-21 | 9:54 | 49.898 | 44733.4544 | 49.9028
2022-06-21 | 9:54 | 49.897 | 44733.4544 | 49.9028
2022-06-21 | 9:54 | 49.897 | 44733.4544 | 49.9028
2022-06-21 | 9:54 | 49.897 | 44733.4544 | 49.9028
2022-06-21 | 9:54 | 49.894 | 44733.4544 | 49.9028
2022-06-21 | 9:54 | 49.895 | 44733.4544 | 49.9028
2022-06-21 | 9:54 | 49.894 | 44733.4544 | 49.9028
2022-06-21 | 9:54 | 49.896 | 44733.4544 | 49.9028
2022-06-21 | 9:54 | 49.899 | 44733.4544 | 49.9028
2022-06-21 | 9:54 | 49.901 | 44733.4544 | 49.9028
2022-06-21 | 9:54 | 49.902 | 44733.4544 | 49.9028
2022-06-21 | 9:54 | 49.903 | 44733.4544 | 49.9028
2022-06-21 | 9:54 | 49.901 | 44733.4544 | 49.9029
2022-06-21 | 9:54 | 49.9 | 44733.4544 | 49.9029
2022-06-21 | 9:54 | 49.9 | 44733.4544 | 49.9028
2022-06-21 | 9:54 | 49.899 | 44733.4544 | 49.9028
2022-06-21 | 9:54 | 49.9 | 44733.4544 | 49.9028
2022-06-21 | 9:54 | 49.9 | 44733.4544 | 49.9028
2022-06-21 | 9:54 | 49.899 | 44733.4544 | 49.9027
2022-06-21 | 9:54 | 49.899 | 44733.4544 | 49.9027
2022-06-21 | 9:54 | 49.899 | 44733.4544 | 49.9027
2022-06-21 | 9:54 | 49.899 | 44733.4544 | 49.9027
2022-06-21 | 9:54 | 49.901 | 44733.4544 | 49.9027
2022-06-21 | 9:54 | 49.903 | 44733.4544 | 49.9028
2022-06-21 | 9:54 | 49.904 | 44733.4544 | 49.9029
2022-06-21 | 9:55 | 49.902 | 44733.4544 | 49.9028
2022-06-21 | 9:55 | 49.9 | 44733.4544 | 49.9028
2022-06-21 | 9:55 | 49.9 | 44733.4544 | 49.9028
2022-06-21 | 9:55 | 49.902 | 44733.4544 | 49.9028
2022-06-21 | 9:55 | 49.902 | 44733.4544 | 49.9027
2022-06-21 | 9:55 | 49.904 | 44733.4544 | 49.9027
2022-06-21 | 9:55 | 49.905 | 44733.4544 | 49.9026
2022-06-21 | 9:55 | 49.908 | 44733.4544 | 49.9026
2022-06-21 | 9:55 | 49.912 | 44733.4544 | 49.9025
2022-06-21 | 9:55 | 49.936 | 2022-06-21 10:54 | 49.9025
2022-06-21 | 9:55 | 49.955 | 44733.4544 | 49.9025
2022-06-21 | 9:55 | 49.97 | 44733.4544 | 49.9026
2022-06-21 | 9:55 | 49.983 | 44733.4544 | 49.9027
2022-06-21 | 9:55 | 49.991 | 44733.4544 | 49.9028
2022-06-21 | 9:55 | 49.999 | 44733.4544 | 49.9028
2022-06-21 | 9:55 | 50.006 | 44733.4544 | 49.9028
2022-06-21 | 9:55 | 50.012 | 44733.4544 | 49.9028
2022-06-21 | 9:55 | 50.016 | 44733.4544 | 49.9028
2022-06-21 | 9:55 | 50.021 | 44733.4544 | 49.9028
2022-06-21 | 9:55 | 50.025 | 44733.4544 | 49.9028
2022-06-21 | 9:55 | 50.025 | 44733.4544 | 49.9028
2022-06-21 | 9:55 | 50.029 | 44733.4544 | 49.9027
2022-06-21 | 9:55 | 50.033 | 44733.4544 | 49.9026
2022-06-21 | 9:55 | 50.031 | 44733.4544 | 49.9026
2022-06-21 | 9:55 | 50.031 | 44733.4544 | 49.9025
2022-06-21 | 9:55 | 50.031 | 44733.4544 | 49.9025
2022-06-21 | 9:55 | 50.032 | 44733.4544 | 49.9025
2022-06-21 | 9:55 | 50.032 | 44733.4544 | 49.9024
2022-06-21 | 9:55 | 50.03 | 44733.4544 | 49.9025
2022-06-21 | 9:55 | 50.03 | 44733.4544 | 49.9025
2022-06-21 | 9:55 | 50.027 | 44733.4544 | 49.9025
2022-06-21 | 9:55 | 50.028 | 44733.4544 | 49.9025
2022-06-21 | 9:55 | 50.025 | 44733.4544 | 49.9024
2022-06-21 | 9:55 | 50.025 | 44733.4544 | 49.9024
2022-06-21 | 9:55 | 50.024 | 44733.4544 | 49.9024
2022-06-21 | 9:55 | 50.023 | 44733.4544 | 49.9024
2022-06-21 | 9:55 | 50.023 | 44733.4544 | 49.9024
2022-06-21 | 9:55 | 50.023 | 44733.4544 | 49.9024
2022-06-21 | 9:55 | 50.026 | 44733.4544 | 49.9024
2022-06-21 | 9:55 | 50.027 | 44733.4544 | 49.9024
2022-06-21 | 9:55 | 50.028 | 44733.4544 | 49.9023
2022-06-21 | 9:55 | 50.028 | 44733.4544 | 49.9022
2022-06-21 | 9:55 | 50.03 | 44733.4544 | 49.9022
2022-06-21 | 9:55 | 50.028 | 44733.4544 | 49.9022
2022-06-21 | 9:55 | 50.029 | 44733.4544 | 49.9022
2022-06-21 | 9:55 | 50.032 | 44733.4544 | 49.9021
2022-06-21 | 9:55 | 50.032 | 44733.4544 | 49.9021
2022-06-21 | 9:55 | 50.035 | 44733.4544 | 49.902
2022-06-21 | 9:55 | 50.035 | 44733.4544 | 49.902
2022-06-21 | 9:55 | 50.036 | 44733.4544 | 49.902
2022-06-21 | 9:55 | 50.035 | 44733.4544 | 49.902
2022-06-21 | 9:55 | 50.034 | 44733.4544 | 49.9019
2022-06-21 | 9:55 | 50.031 | 44733.4544 | 49.9019
2022-06-21 | 9:55 | 50.031 | 44733.4544 | 49.902
2022-06-21 | 9:55 | 50.032 | 44733.4544 | 49.902
2022-06-21 | 9:55 | 50.031 | 44733.4544 | 49.902
2022-06-21 | 9:55 | 50.032 | 44733.4544 | 49.902
2022-06-21 | 9:55 | 50.034 | 44733.4544 | 49.902
2022-06-21 | 9:55 | 50.036 | 44733.4544 | 49.9021
2022-06-21 | 9:56 | 50.037 | 2022-06-21 10:54 | 49.9021
2022-06-21 | 9:56 | 50.037 | 44733.4544 | 49.9021
2022-06-21 | 9:56 | 50.036 | 44733.4544 | 49.9022
2022-06-21 | 9:56 | 50.033 | 44733.4544 | 49.9023
2022-06-21 | 9:56 | 50.033 | 44733.4544 | 49.9023
2022-06-21 | 9:56 | 50.033 | 44733.4544 | 49.9024
2022-06-21 | 9:56 | 50.034 | 44733.4544 | 49.9024
2022-06-21 | 9:56 | 50.035 | 44733.4544 | 49.9024
2022-06-21 | 9:56 | 50.037 | 44733.4544 | 49.9023
2022-06-21 | 9:56 | 50.038 | 44733.4544 | 49.9023
2022-06-21 | 9:56 | 50.039 | 44733.4544 | 49.9022
2022-06-21 | 9:56 | 50.038 | 44733.4544 | 49.9021
2022-06-21 | 9:56 | 50.037 | 44733.4544 | 49.902
2022-06-21 | 9:56 | 50.04 | 44733.4544 | 49.9019
2022-06-21 | 9:56 | 50.038 | 44733.4544 | 49.9018
2022-06-21 | 9:56 | 50.036 | 44733.4544 | 49.9018
2022-06-21 | 9:56 | 50.035 | 44733.4544 | 49.9018
2022-06-21 | 9:56 | 50.036 | 44733.4544 | 49.9019
2022-06-21 | 9:56 | 50.033 | 44733.4544 | 49.9019
2022-06-21 | 9:56 | 50.034 | 44733.4544 | 49.9019
2022-06-21 | 9:56 | 50.032 | 44733.4544 | 49.902
2022-06-21 | 9:56 | 50.03 | 44733.4544 | 49.902
2022-06-21 | 9:56 | 50.029 | 44733.4544 | 49.902
2022-06-21 | 9:56 | 50.028 | 44733.4544 | 49.9019
2022-06-21 | 9:56 | 50.027 | 44733.4544 | 49.9019
2022-06-21 | 9:56 | 50.026 | 44733.4544 | 49.9019
2022-06-21 | 9:56 | 50.024 | 44733.4544 | 49.9018
2022-06-21 | 9:56 | 50.022 | 44733.4544 | 49.9018
2022-06-21 | 9:56 | 50.022 | 44733.4544 | 49.9017
2022-06-21 | 9:56 | 50.021 | 44733.4544 | 49.9016
2022-06-21 | 9:56 | 50.019 | 44733.4544 | 49.9016
2022-06-21 | 9:56 | 50.016 | 44733.4544 | 49.9015
2022-06-21 | 9:56 | 50.014 | 44733.4544 | 49.9015
2022-06-21 | 9:56 | 50.015 | 44733.4544 | 49.9014
2022-06-21 | 9:56 | 50.017 | 44733.4544 | 49.9014
2022-06-21 | 9:56 | 50.02 | 44733.4544 | 49.9013
2022-06-21 | 9:56 | 50.022 | 44733.4544 | 49.9013
2022-06-21 | 9:56 | 50.023 | 44733.4544 | 49.9013
2022-06-21 | 9:56 | 50.024 | 44733.4544 | 49.9013
2022-06-21 | 9:56 | 50.025 | 44733.4544 | 49.9012
2022-06-21 | 9:56 | 50.029 | 44733.4544 | 49.9012
2022-06-21 | 9:56 | 50.03 | 44733.4544 | 49.9012
2022-06-21 | 9:56 | 50.032 | 44733.4544 | 49.9012
2022-06-21 | 9:56 | 50.032 | 44733.4544 | 49.9012
2022-06-21 | 9:56 | 50.03 | 44733.4544 | 49.9012
2022-06-21 | 9:56 | 50.028 | 44733.4544 | 49.9011
2022-06-21 | 9:56 | 50.028 | 44733.4544 | 49.9012
2022-06-21 | 9:56 | 50.028 | 44733.4544 | 49.9012
2022-06-21 | 9:56 | 50.027 | 44733.4544 | 49.9012
2022-06-21 | 9:56 | 50.026 | 44733.4544 | 49.9012
2022-06-21 | 9:56 | 50.027 | 2022-06-21 10:54 | 49.9012
2022-06-21 | 9:56 | 50.027 | 44733.4544 | 49.9012
2022-06-21 | 9:56 | 50.028 | 44733.4544 | 49.9012
2022-06-21 | 9:56 | 50.026 | 44733.4544 | 49.9012
2022-06-21 | 9:56 | 50.025 | 44733.4544 | 49.9012
2022-06-21 | 9:56 | 50.026 | 44733.4544 | 49.9012
2022-06-21 | 9:56 | 50.027 | 44733.4544 | 49.9011
2022-06-21 | 9:56 | 50.03 | 44733.4544 | 49.901
2022-06-21 | 9:56 | 50.031 | 44733.4544 | 49.901
2022-06-21 | 9:56 | 50.032 | 44733.4544 | 49.901
2022-06-21 | 9:56 | 50.031 | 44733.4544 | 49.9009
2022-06-21 | 9:57 | 50.032 | 44733.4544 | 49.901
2022-06-21 | 9:57 | 50.032 | 44733.4544 | 49.901
2022-06-21 | 9:57 | 50.032 | 44733.4544 | 49.901
2022-06-21 | 9:57 | 50.032 | 44733.4544 | 49.901
2022-06-21 | 9:57 | 50.031 | 44733.4544 | 49.9011
2022-06-21 | 9:57 | 50.032 | 44733.4544 | 49.9011
2022-06-21 | 9:57 | 50.031 | 44733.4544 | 49.9011
2022-06-21 | 9:57 | 50.032 | 44733.4544 | 49.9011
2022-06-21 | 9:57 | 50.031 | 44733.4544 | 49.9011
2022-06-21 | 9:57 | 50.031 | 44733.4544 | 49.901
2022-06-21 | 9:57 | 50.033 | 44733.4544 | 49.901
2022-06-21 | 9:57 | 50.033 | 44733.4544 | 49.901
2022-06-21 | 9:57 | 50.032 | 44733.4544 | 49.9009
2022-06-21 | 9:57 | 50.031 | 44733.4544 | 49.9008
2022-06-21 | 9:57 | 50.029 | 44733.4544 | 49.9008
2022-06-21 | 9:57 | 50.029 | 44733.4544 | 49.9008
2022-06-21 | 9:57 | 50.027 | 44733.4544 | 49.9009
2022-06-21 | 9:57 | 50.027 | 44733.4544 | 49.9009
2022-06-21 | 9:57 | 50.026 | 44733.4544 | 49.901
2022-06-21 | 9:57 | 50.026 | 44733.4544 | 49.901
2022-06-21 | 9:57 | 50.026 | 44733.4544 | 49.901
2022-06-21 | 9:57 | 50.027 | 44733.4544 | 49.901
2022-06-21 | 9:57 | 50.029 | 44733.4544 | 49.901
2022-06-21 | 9:57 | 50.03 | 44733.4544 | 49.9009
2022-06-21 | 9:57 | 50.031 | 44733.4544 | 49.9009
2022-06-21 | 9:57 | 50.032 | 44733.4544 | 49.9009
2022-06-21 | 9:57 | 50.033 | 44733.4544 | 49.9008
2022-06-21 | 9:57 | 50.033 | 44733.4544 | 49.9008
2022-06-21 | 9:57 | 50.034 | 44733.4544 | 49.9008
2022-06-21 | 9:57 | 50.034 | 44733.4544 | 49.9007
|  |  | 44733.4544 | 49.9007
|  |  | 44733.4544 | 49.9006
|  |  | 44733.4544 | 49.9006
|  |  | 44733.4544 | 49.9005
|  |  | 44733.4544 | 49.9005
|  |  | 44733.4544 | 49.9005
|  |  | 44733.4544 | 49.9004
|  |  | 44733.4544 | 49.9004
|  |  | 44733.4544 | 49.9004
|  |  | 2022-06-21 10:54 | 49.9003
|  |  | 44733.4544 | 49.9003
|  |  | 44733.4544 | 49.9003
|  |  | 44733.4544 | 49.9003
|  |  | 44733.4544 | 49.9004
|  |  | 44733.4544 | 49.9004
|  |  | 44733.4544 | 49.9004
|  |  | 44733.4544 | 49.9004
|  |  | 44733.4544 | 49.9003
|  |  | 44733.4544 | 49.9003
|  |  | 44733.4544 | 49.9002
|  |  | 44733.4544 | 49.9001
|  |  | 44733.4544 | 49.9
|  |  | 44733.4544 | 49.9
|  |  | 44733.4544 | 49.8999
|  |  | 44733.4544 | 49.8999
|  |  | 44733.4544 | 49.8998
|  |  | 44733.4544 | 49.8998
|  |  | 44733.4544 | 49.8998
|  |  | 44733.4544 | 49.8998
|  |  | 44733.4544 | 49.8998
|  |  | 44733.4544 | 49.8997
|  |  | 44733.4544 | 49.8997
|  |  | 44733.4544 | 49.8996
|  |  | 44733.4544 | 49.8996
|  |  | 44733.4544 | 49.8997
|  |  | 44733.4544 | 49.8997
|  |  | 44733.4544 | 49.8997
|  |  | 44733.4544 | 49.8997
|  |  | 44733.4544 | 49.8996
|  |  | 44733.4544 | 49.8996
|  |  | 44733.4544 | 49.8995
|  |  | 44733.4544 | 49.8995
|  |  | 44733.4544 | 49.8996
|  |  | 44733.4544 | 49.8995
|  |  | 44733.4544 | 49.8995
|  |  | 44733.4544 | 49.8995
|  |  | 44733.4544 | 49.8995
|  |  | 44733.4544 | 49.8994
|  |  | 44733.4544 | 49.8995
|  |  | 44733.4544 | 49.8995
|  |  | 44733.4544 | 49.8995
|  |  | 44733.4544 | 49.8996
|  |  | 44733.4544 | 49.8996
|  |  | 44733.4544 | 49.8997
|  |  | 44733.4544 | 49.8997
|  |  | 44733.4544 | 49.8998
|  |  | 44733.4544 | 49.8998
|  |  | 44733.4544 | 49.8998
|  |  | 44733.4544 | 49.8998
|  |  | 2022-06-21 10:54 | 49.8998
|  |  | 44733.4544 | 49.8999
|  |  | 44733.4544 | 49.8999
|  |  | 44733.4544 | 49.8998
|  |  | 44733.4544 | 49.8998
|  |  | 44733.4544 | 49.8998
|  |  | 44733.4544 | 49.8998
|  |  | 44733.4544 | 49.8997
|  |  | 44733.4544 | 49.8997
|  |  | 44733.4544 | 49.8997
|  |  | 44733.4544 | 49.8997
|  |  | 44733.4544 | 49.8997
|  |  | 44733.4544 | 49.8998
|  |  | 44733.4544 | 49.8998
|  |  | 44733.4544 | 49.8999
|  |  | 44733.4544 | 49.8999
|  |  | 44733.4544 | 49.9
|  |  | 44733.4544 | 49.9
|  |  | 44733.4544 | 49.9
|  |  | 44733.4544 | 49.9
|  |  | 44733.4544 | 49.9
|  |  | 44733.4544 | 49.9
|  |  | 44733.4544 | 49.8999
|  |  | 44733.4544 | 49.8999
|  |  | 44733.4544 | 49.8999
|  |  | 44733.4544 | 49.8999
|  |  | 44733.4544 | 49.8999
|  |  | 44733.4544 | 49.9
|  |  | 44733.4544 | 49.9001
|  |  | 44733.4544 | 49.9001
|  |  | 44733.4544 | 49.9001
|  |  | 44733.4544 | 49.9001
|  |  | 44733.4544 | 49.9001
|  |  | 44733.4544 | 49.9001
|  |  | 44733.4544 | 49.9
|  |  | 44733.4544 | 49.8999
|  |  | 44733.4544 | 49.8999
|  |  | 44733.4544 | 49.8999
|  |  | 44733.4544 | 49.8999
|  |  | 44733.4544 | 49.8999
|  |  | 44733.4544 | 49.8999
|  |  | 44733.4544 | 49.8999
|  |  | 44733.4544 | 49.8999
|  |  | 44733.4544 | 49.9
|  |  | 44733.4544 | 49.9
|  |  | 44733.4544 | 49.9
|  |  | 44733.4544 | 49.9
|  |  | 44733.4544 | 49.9
|  |  | 44733.4544 | 49.8999
|  |  | 44733.4544 | 49.8999
|  |  | 2022-06-21 10:54 | 49.8999
|  |  | 44733.4544 | 49.8998
|  |  | 44733.4544 | 49.8997
|  |  | 44733.4544 | 49.8997
|  |  | 44733.4544 | 49.8996
|  |  | 44733.4544 | 49.8996
|  |  | 44733.4544 | 49.8996
|  |  | 44733.4544 | 49.8997
|  |  | 44733.4544 | 49.8997
|  |  | 44733.4544 | 49.8997
|  |  | 44733.4544 | 49.8997
|  |  | 44733.4544 | 49.8997
|  |  | 44733.4544 | 49.8997
|  |  | 44733.4544 | 49.8997
|  |  | 44733.4544 | 49.8998
|  |  | 44733.4544 | 49.8998
|  |  | 44733.4544 | 49.8998
|  |  | 44733.4544 | 49.8998
|  |  | 44733.4544 | 49.8999
|  |  | 44733.4544 | 49.8999
|  |  | 44733.4544 | 49.9
|  |  | 44733.4544 | 49.9
|  |  | 44733.4544 | 49.9001
|  |  | 44733.4544 | 49.9002
|  |  | 44733.4544 | 49.9003
|  |  | 44733.4544 | 49.9004
|  |  | 44733.4544 | 49.9004
|  |  | 44733.4544 | 49.9005
|  |  | 44733.4544 | 49.9005
|  |  | 44733.4544 | 49.9005
|  |  | 44733.4544 | 49.9005
|  |  | 44733.4544 | 49.9005
|  |  | 44733.4544 | 49.9006
|  |  | 44733.4544 | 49.9006
|  |  | 44733.4544 | 49.9005
|  |  | 44733.4544 | 49.9005
|  |  | 44733.4544 | 49.9005
|  |  | 44733.4544 | 49.9006
|  |  | 44733.4544 | 49.9007
|  |  | 44733.4544 | 49.9008
|  |  | 44733.4544 | 49.9007
|  |  | 44733.4544 | 49.9007
|  |  | 44733.4544 | 49.9006
|  |  | 44733.4544 | 49.9006
|  |  | 44733.4544 | 49.9006
|  |  | 44733.4544 | 49.9006
|  |  | 44733.4544 | 49.9006
|  |  | 44733.4544 | 49.9006
|  |  | 44733.4544 | 49.9006
|  |  | 44733.4544 | 49.9006
|  |  | 2022-06-21 10:54 | 49.9006
|  |  | 44733.4544 | 49.9006
|  |  | 44733.4544 | 49.9006
|  |  | 44733.4544 | 49.9006
|  |  | 44733.4544 | 49.9007
|  |  | 44733.4544 | 49.9007
|  |  | 44733.4544 | 49.9006
|  |  | 44733.4544 | 49.9006
|  |  | 44733.4544 | 49.9006
|  |  | 44733.4544 | 49.9005
|  |  | 44733.4544 | 49.9006
|  |  | 44733.4544 | 49.9005
|  |  | 44733.4544 | 49.9005
|  |  | 44733.4544 | 49.9004
|  |  | 44733.4544 | 49.9004
|  |  | 44733.4544 | 49.9005
|  |  | 44733.4544 | 49.9005
|  |  | 44733.4544 | 49.9005
|  |  | 44733.4544 | 49.9006
|  |  | 44733.4544 | 49.9006
|  |  | 44733.4544 | 49.9007
|  |  | 44733.4544 | 49.9008
|  |  | 44733.4544 | 49.9008
|  |  | 44733.4544 | 49.9008
|  |  | 44733.4544 | 49.9008
|  |  | 44733.4544 | 49.9008
|  |  | 44733.4544 | 49.9008
|  |  | 44733.4544 | 49.9007
|  |  | 44733.4544 | 49.9007
|  |  | 44733.4544 | 49.9006
|  |  | 44733.4544 | 49.9006
|  |  | 44733.4544 | 49.9005
|  |  | 44733.4544 | 49.9005
|  |  | 44733.4544 | 49.9005
|  |  | 44733.4544 | 49.9005
|  |  | 44733.4544 | 49.9006
|  |  | 44733.4544 | 49.9006
|  |  | 44733.4544 | 49.9007
|  |  | 44733.4544 | 49.9007
|  |  | 44733.4544 | 49.9008
|  |  | 44733.4544 | 49.9008
|  |  | 44733.4544 | 49.9008
|  |  | 44733.4544 | 49.9008
|  |  | 44733.4544 | 49.9007
|  |  | 44733.4544 | 49.9007
|  |  | 44733.4544 | 49.9007
|  |  | 44733.4544 | 49.9006
|  |  | 44733.4544 | 49.9006
|  |  | 44733.4544 | 49.9006
|  |  | 44733.4544 | 49.9006
|  |  | 2022-06-21 10:54 | 49.9006
|  |  | 44733.4544 | 49.9006
|  |  | 44733.4544 | 49.9007
|  |  | 44733.4544 | 49.9008
|  |  | 44733.4544 | 49.9007
|  |  | 44733.4544 | 49.9008
|  |  | 44733.4544 | 49.9009
|  |  | 44733.4544 | 49.9009
|  |  | 44733.4544 | 49.901
|  |  | 44733.4544 | 49.901
|  |  | 44733.4544 | 49.901
|  |  | 44733.4544 | 49.9009
|  |  | 44733.4544 | 49.9009
|  |  | 44733.4544 | 49.9009
|  |  | 44733.4544 | 49.9009
|  |  | 44733.4544 | 49.9008
|  |  | 44733.4544 | 49.9009
|  |  | 44733.4544 | 49.9009
|  |  | 44733.4544 | 49.9008
|  |  | 44733.4544 | 49.9009
|  |  | 44733.4544 | 49.9009
|  |  | 44733.4544 | 49.9008
|  |  | 44733.4544 | 49.9008
|  |  | 44733.4544 | 49.9008
|  |  | 44733.4544 | 49.9008
|  |  | 44733.4545 | 49.9008
|  |  | 44733.4545 | 49.9008
|  |  | 44733.4545 | 49.9007
|  |  | 44733.4545 | 49.9007
|  |  | 44733.4545 | 49.9007
|  |  | 44733.4545 | 49.9007
|  |  | 44733.4545 | 49.9007
|  |  | 44733.4545 | 49.9007
|  |  | 44733.4545 | 49.9007
|  |  | 44733.4545 | 49.9007
|  |  | 44733.4545 | 49.9007
|  |  | 44733.4545 | 49.9007
|  |  | 44733.4545 | 49.9006
|  |  | 44733.4545 | 49.9006
|  |  | 44733.4545 | 49.9006
|  |  | 44733.4545 | 49.9006
|  |  | 44733.4545 | 49.9006
|  |  | 44733.4545 | 49.9006
|  |  | 44733.4545 | 49.9006
|  |  | 44733.4545 | 49.9007
|  |  | 44733.4545 | 49.9007
|  |  | 44733.4545 | 49.9007
|  |  | 44733.4545 | 49.9007
|  |  | 44733.4545 | 49.9007
|  |  | 44733.4545 | 49.9007
|  |  | 2022-06-21 10:54 | 49.9007
|  |  | 44733.4545 | 49.9006
|  |  | 44733.4545 | 49.9006
|  |  | 44733.4545 | 49.9006
|  |  | 44733.4545 | 49.9005
|  |  | 44733.4545 | 49.9005
|  |  | 44733.4545 | 49.9005
|  |  | 44733.4545 | 49.9005
|  |  | 44733.4545 | 49.9005
|  |  | 44733.4545 | 49.9006
|  |  | 44733.4545 | 49.9006
|  |  | 44733.4545 | 49.9006
|  |  | 44733.4545 | 49.9006
|  |  | 44733.4545 | 49.9006
|  |  | 44733.4545 | 49.9007
|  |  | 44733.4545 | 49.9007
|  |  | 44733.4545 | 49.9007
|  |  | 44733.4545 | 49.9006
|  |  | 44733.4545 | 49.9006
|  |  | 44733.4545 | 49.9007
|  |  | 44733.4545 | 49.9008
|  |  | 44733.4545 | 49.9008
|  |  | 44733.4545 | 49.9008
|  |  | 44733.4545 | 49.9009
|  |  | 44733.4545 | 49.9009
|  |  | 44733.4545 | 49.9009
|  |  | 44733.4545 | 49.9009
|  |  | 44733.4545 | 49.901
|  |  | 44733.4545 | 49.901
|  |  | 44733.4545 | 49.901
|  |  | 44733.4545 | 49.901
|  |  | 44733.4545 | 49.901
|  |  | 44733.4545 | 49.901
|  |  | 44733.4545 | 49.901
|  |  | 44733.4545 | 49.901
|  |  | 44733.4545 | 49.9011
|  |  | 44733.4545 | 49.9011
|  |  | 44733.4545 | 49.9011
|  |  | 44733.4545 | 49.9011
|  |  | 44733.4545 | 49.9011
|  |  | 44733.4545 | 49.9011
|  |  | 44733.4545 | 49.9011
|  |  | 44733.4545 | 49.901
|  |  | 44733.4545 | 49.901
|  |  | 44733.4545 | 49.901
|  |  | 44733.4545 | 49.901
|  |  | 44733.4545 | 49.901
|  |  | 44733.4545 | 49.901
|  |  | 44733.4545 | 49.9011
|  |  | 44733.4545 | 49.9011
|  |  | 2022-06-21 10:54 | 49.9011
|  |  | 44733.4545 | 49.9011
|  |  | 44733.4545 | 49.9011
|  |  | 44733.4545 | 49.9011
|  |  | 44733.4545 | 49.9011
|  |  | 44733.4545 | 49.9011
|  |  | 44733.4545 | 49.9011
|  |  | 44733.4545 | 49.9011
|  |  | 44733.4545 | 49.9011
|  |  | 44733.4545 | 49.9011
|  |  | 44733.4545 | 49.901
|  |  | 44733.4545 | 49.901
|  |  | 44733.4545 | 49.901
|  |  | 44733.4545 | 49.9009
|  |  | 44733.4545 | 49.9009
|  |  | 44733.4545 | 49.9009
|  |  | 44733.4545 | 49.9009
|  |  | 44733.4545 | 49.901
|  |  | 44733.4545 | 49.901
|  |  | 44733.4545 | 49.9011
|  |  | 44733.4545 | 49.9011
|  |  | 44733.4545 | 49.901
|  |  | 44733.4545 | 49.9009
|  |  | 44733.4545 | 49.9009
|  |  | 44733.4545 | 49.9009
|  |  | 44733.4545 | 49.9009
|  |  | 44733.4545 | 49.9008
|  |  | 44733.4545 | 49.9008
|  |  | 44733.4545 | 49.9008
|  |  | 44733.4545 | 49.9007
|  |  | 44733.4545 | 49.9007
|  |  | 44733.4545 | 49.9007
|  |  | 44733.4545 | 49.9008
|  |  | 44733.4545 | 49.9008
|  |  | 44733.4545 | 49.9009
|  |  | 44733.4545 | 49.9009
|  |  | 44733.4545 | 49.901
|  |  | 44733.4545 | 49.901
|  |  | 44733.4545 | 49.901
|  |  | 44733.4545 | 49.901
|  |  | 44733.4545 | 49.9011
|  |  | 44733.4545 | 49.9011
|  |  | 44733.4545 | 49.9012
|  |  | 44733.4545 | 49.9013
|  |  | 44733.4545 | 49.9013
|  |  | 44733.4545 | 49.9014
|  |  | 44733.4545 | 49.9014
|  |  | 44733.4545 | 49.9014
|  |  | 44733.4545 | 49.9014
|  |  | 44733.4545 | 49.9014
|  |  | 2022-06-21 10:54 | 49.9013
|  |  | 44733.4545 | 49.9013
|  |  | 44733.4545 | 49.9013
|  |  | 44733.4545 | 49.9012
|  |  | 44733.4545 | 49.9012
|  |  | 44733.4545 | 49.9012
|  |  | 44733.4545 | 49.9012
|  |  | 44733.4545 | 49.9012
|  |  | 44733.4545 | 49.9012
|  |  | 44733.4545 | 49.9013
|  |  | 44733.4545 | 49.9013
|  |  | 44733.4545 | 49.9013
|  |  | 44733.4545 | 49.9013
|  |  | 44733.4545 | 49.9014
|  |  | 44733.4545 | 49.9014
|  |  | 44733.4545 | 49.9014
|  |  | 44733.4545 | 49.9014
|  |  | 44733.4545 | 49.9014
|  |  | 44733.4545 | 49.9014
|  |  | 44733.4545 | 49.9014
|  |  | 44733.4545 | 49.9014
|  |  | 44733.4545 | 49.9014
|  |  | 44733.4545 | 49.9015
|  |  | 44733.4545 | 49.9015
|  |  | 44733.4545 | 49.9016
|  |  | 44733.4545 | 49.9016
|  |  | 44733.4545 | 49.9016
|  |  | 44733.4545 | 49.9017
|  |  | 44733.4545 | 49.9016
|  |  | 44733.4545 | 49.9017
|  |  | 44733.4545 | 49.9017
|  |  | 44733.4545 | 49.9017
|  |  | 44733.4545 | 49.9018
|  |  | 44733.4545 | 49.9019
|  |  | 44733.4545 | 49.9019
|  |  | 44733.4545 | 49.902
|  |  | 44733.4545 | 49.902
|  |  | 44733.4545 | 49.9021
|  |  | 44733.4545 | 49.9021
|  |  | 44733.4545 | 49.9022
|  |  | 44733.4545 | 49.9022
|  |  | 44733.4545 | 49.9022
|  |  | 44733.4545 | 49.9022
|  |  | 44733.4545 | 49.9021
|  |  | 44733.4545 | 49.9021
|  |  | 44733.4545 | 49.9021
|  |  | 44733.4545 | 49.9021
|  |  | 44733.4545 | 49.9021
|  |  | 44733.4545 | 49.9021
|  |  | 44733.4545 | 49.9021
|  |  | 2022-06-21 10:54 | 49.9021
|  |  | 44733.4545 | 49.9021
|  |  | 44733.4545 | 49.9022
|  |  | 44733.4545 | 49.9022
|  |  | 44733.4545 | 49.9023
|  |  | 44733.4545 | 49.9022
|  |  | 44733.4545 | 49.9022
|  |  | 44733.4545 | 49.9022
|  |  | 44733.4545 | 49.9022
|  |  | 44733.4545 | 49.9022
|  |  | 44733.4545 | 49.9023
|  |  | 44733.4545 | 49.9023
|  |  | 44733.4545 | 49.9022
|  |  | 44733.4545 | 49.9022
|  |  | 44733.4545 | 49.9022
|  |  | 44733.4545 | 49.9023
|  |  | 44733.4545 | 49.9025
|  |  | 44733.4545 | 49.9026
|  |  | 44733.4545 | 49.9027
|  |  | 44733.4545 | 49.9028
|  |  | 44733.4545 | 49.9028
|  |  | 44733.4545 | 49.9028
|  |  | 44733.4545 | 49.9028
|  |  | 44733.4545 | 49.9028
|  |  | 44733.4545 | 49.9028
|  |  | 44733.4545 | 49.9027
|  |  | 44733.4545 | 49.9026
|  |  | 44733.4545 | 49.9026
|  |  | 44733.4545 | 49.9026
|  |  | 44733.4545 | 49.9025
|  |  | 44733.4545 | 49.9025
|  |  | 44733.4545 | 49.9025
|  |  | 44733.4545 | 49.9026
|  |  | 44733.4545 | 49.9026
|  |  | 44733.4545 | 49.9027
|  |  | 44733.4545 | 49.9028
|  |  | 44733.4545 | 49.9029
|  |  | 44733.4545 | 49.9028
|  |  | 44733.4545 | 49.9029
|  |  | 44733.4545 | 49.903
|  |  | 44733.4545 | 49.903
|  |  | 44733.4545 | 49.903
|  |  | 44733.4545 | 49.9031
|  |  | 44733.4545 | 49.903
|  |  | 44733.4545 | 49.903
|  |  | 44733.4545 | 49.903
|  |  | 44733.4545 | 49.903
|  |  | 44733.4545 | 49.903
|  |  | 44733.4545 | 49.903
|  |  | 44733.4545 | 49.903
|  |  | 2022-06-21 10:54 | 49.903
|  |  | 44733.4545 | 49.903
|  |  | 44733.4545 | 49.903
|  |  | 44733.4545 | 49.903
|  |  | 44733.4545 | 49.903
|  |  | 44733.4545 | 49.903
|  |  | 44733.4545 | 49.903
|  |  | 44733.4545 | 49.903
|  |  | 44733.4545 | 49.903
|  |  | 44733.4545 | 49.903
|  |  | 44733.4545 | 49.9031
|  |  | 44733.4545 | 49.9031
|  |  | 44733.4545 | 49.9031
|  |  | 44733.4545 | 49.9031
|  |  | 44733.4545 | 49.903
|  |  | 44733.4545 | 49.903
|  |  | 44733.4545 | 49.903
|  |  | 44733.4545 | 49.903
|  |  | 44733.4545 | 49.9029
|  |  | 44733.4545 | 49.903
|  |  | 44733.4545 | 49.903
|  |  | 44733.4545 | 49.9031
|  |  | 44733.4545 | 49.9032
|  |  | 44733.4545 | 49.9032
|  |  | 44733.4545 | 49.9032
|  |  | 44733.4545 | 49.9032
|  |  | 44733.4545 | 49.9032
|  |  | 44733.4545 | 49.9032
|  |  | 44733.4545 | 49.9033
|  |  | 44733.4545 | 49.9032
|  |  | 44733.4545 | 49.9032
|  |  | 44733.4545 | 49.9032
|  |  | 44733.4545 | 49.9032
|  |  | 44733.4545 | 49.9032
|  |  | 44733.4545 | 49.9032
|  |  | 44733.4545 | 49.9031
|  |  | 44733.4545 | 49.9031
|  |  | 44733.4545 | 49.9031
|  |  | 44733.4545 | 49.9031
|  |  | 44733.4545 | 49.9031
|  |  | 44733.4545 | 49.9031
|  |  | 44733.4545 | 49.9031
|  |  | 44733.4545 | 49.903
|  |  | 44733.4545 | 49.903
|  |  | 44733.4545 | 49.9031
|  |  | 44733.4545 | 49.9031
|  |  | 44733.4545 | 49.9032
|  |  | 44733.4545 | 49.9031
|  |  | 44733.4545 | 49.9031
|  |  | 44733.4545 | 49.9031
|  |  | 2022-06-21 10:55 | 49.903
|  |  | 44733.4545 | 49.903
|  |  | 44733.4545 | 49.903
|  |  | 44733.4545 | 49.9029
|  |  | 44733.4545 | 49.9028
|  |  | 44733.4545 | 49.9029
|  |  | 44733.4545 | 49.9029
|  |  | 44733.4545 | 49.9029
|  |  | 44733.4545 | 49.9029
|  |  | 44733.4545 | 49.9028
|  |  | 44733.4545 | 49.9028
|  |  | 44733.4545 | 49.9028
|  |  | 44733.4545 | 49.9027
|  |  | 44733.4545 | 49.9028
|  |  | 44733.4545 | 49.9028
|  |  | 44733.4545 | 49.9028
|  |  | 44733.4545 | 49.9027
|  |  | 44733.4545 | 49.9027
|  |  | 44733.4545 | 49.9027
|  |  | 44733.4545 | 49.9027
|  |  | 44733.4545 | 49.9027
|  |  | 44733.4545 | 49.9026
|  |  | 44733.4545 | 49.9026
|  |  | 44733.4545 | 49.9025
|  |  | 44733.4545 | 49.9024
|  |  | 44733.4545 | 49.9024
|  |  | 44733.4545 | 49.9023
|  |  | 44733.4545 | 49.9023
|  |  | 44733.4545 | 49.9023
|  |  | 44733.4545 | 49.9023
|  |  | 44733.4545 | 49.9023
|  |  | 44733.4545 | 49.9023
|  |  | 44733.4545 | 49.9023
|  |  | 44733.4545 | 49.9022
|  |  | 44733.4545 | 49.9022
|  |  | 44733.4545 | 49.9022
|  |  | 44733.4545 | 49.9022
|  |  | 44733.4545 | 49.9022
|  |  | 44733.4545 | 49.9021
|  |  | 44733.4545 | 49.9021
|  |  | 44733.4545 | 49.9021
|  |  | 44733.4545 | 49.902
|  |  | 44733.4545 | 49.902
|  |  | 44733.4545 | 49.902
|  |  | 44733.4545 | 49.902
|  |  | 44733.4545 | 49.902
|  |  | 44733.4545 | 49.902
|  |  | 44733.4545 | 49.902
|  |  | 44733.4545 | 49.902
|  |  | 44733.4545 | 49.9021
|  |  | 2022-06-21 10:55 | 49.9021
|  |  | 44733.4545 | 49.9022
|  |  | 44733.4545 | 49.9022
|  |  | 44733.4545 | 49.9022
|  |  | 44733.4545 | 49.9022
|  |  | 44733.4545 | 49.9021
|  |  | 44733.4545 | 49.9021
|  |  | 44733.4545 | 49.9021
|  |  | 44733.4545 | 49.9021
|  |  | 44733.4545 | 49.9021
|  |  | 44733.4545 | 49.9021
|  |  | 44733.4545 | 49.9021
|  |  | 44733.4545 | 49.902
|  |  | 44733.4545 | 49.902
|  |  | 44733.4545 | 49.9019
|  |  | 44733.4545 | 49.9019
|  |  | 44733.4545 | 49.9018
|  |  | 44733.4545 | 49.9018
|  |  | 44733.4545 | 49.9019
|  |  | 44733.4545 | 49.9019
|  |  | 44733.4545 | 49.9019
|  |  | 44733.4545 | 49.9019
|  |  | 44733.4545 | 49.9019
|  |  | 44733.4545 | 49.902
|  |  | 44733.4545 | 49.902
|  |  | 44733.4545 | 49.9019
|  |  | 44733.4545 | 49.9019
|  |  | 44733.4545 | 49.9019
|  |  | 44733.4545 | 49.9018
|  |  | 44733.4545 | 49.9018
|  |  | 44733.4545 | 49.9017
|  |  | 44733.4545 | 49.9016
|  |  | 44733.4545 | 49.9016
|  |  | 44733.4545 | 49.9016
|  |  | 44733.4545 | 49.9015
|  |  | 44733.4545 | 49.9015
|  |  | 44733.4545 | 49.9015
|  |  | 44733.4545 | 49.9016
|  |  | 44733.4545 | 49.9016
|  |  | 44733.4545 | 49.9016
|  |  | 44733.4545 | 49.9016
|  |  | 44733.4545 | 49.9015
|  |  | 44733.4545 | 49.9016
|  |  | 44733.4545 | 49.9016
|  |  | 44733.4545 | 49.9016
|  |  | 44733.4545 | 49.9016
|  |  | 44733.4545 | 49.9016
|  |  | 44733.4545 | 49.9016
|  |  | 44733.4545 | 49.9016
|  |  | 44733.4545 | 49.9015
|  |  | 2022-06-21 10:55 | 49.9015
|  |  | 44733.4545 | 49.9015
|  |  | 44733.4545 | 49.9015
|  |  | 44733.4545 | 49.9014
|  |  | 44733.4545 | 49.9014
|  |  | 44733.4545 | 49.9015
|  |  | 44733.4545 | 49.9015
|  |  | 44733.4545 | 49.9016
|  |  | 44733.4545 | 49.9016
|  |  | 44733.4545 | 49.9017
|  |  | 44733.4545 | 49.9018
|  |  | 44733.4545 | 49.9017
|  |  | 44733.4545 | 49.9018
|  |  | 44733.4545 | 49.9017
|  |  | 44733.4545 | 49.9016
|  |  | 44733.4545 | 49.9015
|  |  | 44733.4545 | 49.9015
|  |  | 44733.4545 | 49.9014
|  |  | 44733.4545 | 49.9014
|  |  | 44733.4545 | 49.9014
|  |  | 44733.4545 | 49.9015
|  |  | 44733.4545 | 49.9015
|  |  | 44733.4545 | 49.9015
|  |  | 44733.4545 | 49.9015
|  |  | 44733.4545 | 49.9016
|  |  | 44733.4545 | 49.9018
|  |  | 44733.4545 | 49.9018
|  |  | 44733.4545 | 49.9019
|  |  | 44733.4545 | 49.9019
|  |  | 44733.4545 | 49.9018
|  |  | 44733.4545 | 49.9018
|  |  | 44733.4545 | 49.9018
|  |  | 44733.4545 | 49.9017
|  |  | 44733.4545 | 49.9017
|  |  | 44733.4545 | 49.9017
|  |  | 44733.4545 | 49.9017
|  |  | 44733.4545 | 49.9017
|  |  | 44733.4545 | 49.9017
|  |  | 44733.4545 | 49.9016
|  |  | 44733.4545 | 49.9016
|  |  | 44733.4545 | 49.9016
|  |  | 44733.4545 | 49.9017
|  |  | 44733.4545 | 49.9017
|  |  | 44733.4545 | 49.9018
|  |  | 44733.4545 | 49.9018
|  |  | 44733.4545 | 49.9019
|  |  | 44733.4545 | 49.9019
|  |  | 44733.4545 | 49.9019
|  |  | 44733.4545 | 49.9019
|  |  | 44733.4545 | 49.9019
|  |  | 2022-06-21 10:55 | 49.9018
|  |  | 44733.4545 | 49.9018
|  |  | 44733.4545 | 49.9017
|  |  | 44733.4545 | 49.9018
|  |  | 44733.4545 | 49.9017
|  |  | 44733.4545 | 49.9017
|  |  | 44733.4546 | 49.9017
|  |  | 44733.4546 | 49.9017
|  |  | 44733.4546 | 49.9018
|  |  | 44733.4546 | 49.9018
|  |  | 44733.4546 | 49.9019
|  |  | 44733.4546 | 49.902
|  |  | 44733.4546 | 49.902
|  |  | 44733.4546 | 49.902
|  |  | 44733.4546 | 49.902
|  |  | 44733.4546 | 49.902
|  |  | 44733.4546 | 49.9019
|  |  | 44733.4546 | 49.9019
|  |  | 44733.4546 | 49.9019
|  |  | 44733.4546 | 49.9019
|  |  | 44733.4546 | 49.9019
|  |  | 44733.4546 | 49.9019
|  |  | 44733.4546 | 49.902
|  |  | 44733.4546 | 49.902
|  |  | 44733.4546 | 49.902
|  |  | 44733.4546 | 49.9021
|  |  | 44733.4546 | 49.902
|  |  | 44733.4546 | 49.902
|  |  | 44733.4546 | 49.9021
|  |  | 44733.4546 | 49.902
|  |  | 44733.4546 | 49.902
|  |  | 44733.4546 | 49.9019
|  |  | 44733.4546 | 49.9019
|  |  | 44733.4546 | 49.9018
|  |  | 44733.4546 | 49.9018
|  |  | 44733.4546 | 49.9018
|  |  | 44733.4546 | 49.9018
|  |  | 44733.4546 | 49.9019
|  |  | 44733.4546 | 49.9019
|  |  | 44733.4546 | 49.902
|  |  | 44733.4546 | 49.902
|  |  | 44733.4546 | 49.902
|  |  | 44733.4546 | 49.902
|  |  | 44733.4546 | 49.902
|  |  | 44733.4546 | 49.902
|  |  | 44733.4546 | 49.902
|  |  | 44733.4546 | 49.9019
|  |  | 44733.4546 | 49.9019
|  |  | 44733.4546 | 49.9019
|  |  | 44733.4546 | 49.9019
|  |  | 2022-06-21 10:55 | 49.9018
|  |  | 44733.4546 | 49.9019
|  |  | 44733.4546 | 49.9019
|  |  | 44733.4546 | 49.9018
|  |  | 44733.4546 | 49.9019
|  |  | 44733.4546 | 49.902
|  |  | 44733.4546 | 49.902
|  |  | 44733.4546 | 49.9019
|  |  | 44733.4546 | 49.9019
|  |  | 44733.4546 | 49.9018
|  |  | 44733.4546 | 49.9018
|  |  | 44733.4546 | 49.9017
|  |  | 44733.4546 | 49.9017
|  |  | 44733.4546 | 49.9016
|  |  | 44733.4546 | 49.9016
|  |  | 44733.4546 | 49.9016
|  |  | 44733.4546 | 49.9017
|  |  | 44733.4546 | 49.9017
|  |  | 44733.4546 | 49.9018
|  |  | 44733.4546 | 49.9018
|  |  | 44733.4546 | 49.9018
|  |  | 44733.4546 | 49.9018
|  |  | 44733.4546 | 49.9019
|  |  | 44733.4546 | 49.9019
|  |  | 44733.4546 | 49.9019
|  |  | 44733.4546 | 49.9018
|  |  | 44733.4546 | 49.9018
|  |  | 44733.4546 | 49.9018
|  |  | 44733.4546 | 49.9018
|  |  | 44733.4546 | 49.9018
|  |  | 44733.4546 | 49.9018
|  |  | 44733.4546 | 49.9018
|  |  | 44733.4546 | 49.9019
|  |  | 44733.4546 | 49.9019
|  |  | 44733.4546 | 49.902
|  |  | 44733.4546 | 49.902
|  |  | 44733.4546 | 49.9021
|  |  | 44733.4546 | 49.9021
|  |  | 44733.4546 | 49.9021
|  |  | 44733.4546 | 49.9021
|  |  | 44733.4546 | 49.902
|  |  | 44733.4546 | 49.902
|  |  | 44733.4546 | 49.9018
|  |  | 44733.4546 | 49.9019
|  |  | 44733.4546 | 49.9019
|  |  | 44733.4546 | 49.9019
|  |  | 44733.4546 | 49.902
|  |  | 44733.4546 | 49.9021
|  |  | 44733.4546 | 49.9022
|  |  | 44733.4546 | 49.9021
|  |  | 2022-06-21 10:55 | 49.9022
|  |  | 44733.4546 | 49.9023
|  |  | 44733.4546 | 49.9023
|  |  | 44733.4546 | 49.9023
|  |  | 44733.4546 | 49.9024
|  |  | 44733.4546 | 49.9024
|  |  | 44733.4546 | 49.9024
|  |  | 44733.4546 | 49.9024
|  |  | 44733.4546 | 49.9024
|  |  | 44733.4546 | 49.9024
|  |  | 44733.4546 | 49.9024
|  |  | 44733.4546 | 49.9025
|  |  | 44733.4546 | 49.9026
|  |  | 44733.4546 | 49.9026
|  |  | 44733.4546 | 49.9026
|  |  | 44733.4546 | 49.9027
|  |  | 44733.4546 | 49.9028
|  |  | 44733.4546 | 49.9027
|  |  | 44733.4546 | 49.9028
|  |  | 44733.4546 | 49.9028
|  |  | 44733.4546 | 49.9027
|  |  | 44733.4546 | 49.9027
|  |  | 44733.4546 | 49.9027
|  |  | 44733.4546 | 49.9027
|  |  | 44733.4546 | 49.9027
|  |  | 44733.4546 | 49.9027
|  |  | 44733.4546 | 49.9028
|  |  | 44733.4546 | 49.9028
|  |  | 44733.4546 | 49.9028
|  |  | 44733.4546 | 49.9029
|  |  | 44733.4546 | 49.903
|  |  | 44733.4546 | 49.903
|  |  | 44733.4546 | 49.9031
|  |  | 44733.4546 | 49.9031
|  |  | 44733.4546 | 49.9032
|  |  | 44733.4546 | 49.9032
|  |  | 44733.4546 | 49.9032
|  |  | 44733.4546 | 49.9032
|  |  | 44733.4546 | 49.9033
|  |  | 44733.4546 | 49.9033
|  |  | 44733.4546 | 49.9033
|  |  | 44733.4546 | 49.9034
|  |  | 44733.4546 | 49.9034
|  |  | 44733.4546 | 49.9034
|  |  | 44733.4546 | 49.9034
|  |  | 44733.4546 | 49.9035
|  |  | 44733.4546 | 49.9035
|  |  | 44733.4546 | 49.9036
|  |  | 44733.4546 | 49.9035
|  |  | 44733.4546 | 49.9036
|  |  | 2022-06-21 10:55 | 49.9036
|  |  | 44733.4546 | 49.9037
|  |  | 44733.4546 | 49.9037
|  |  | 44733.4546 | 49.9038
|  |  | 44733.4546 | 49.9038
|  |  | 44733.4546 | 49.9039
|  |  | 44733.4546 | 49.9039
|  |  | 44733.4546 | 49.9039
|  |  | 44733.4546 | 49.9039
|  |  | 44733.4546 | 49.904
|  |  | 44733.4546 | 49.9041
|  |  | 44733.4546 | 49.904
|  |  | 44733.4546 | 49.9041
|  |  | 44733.4546 | 49.9041
|  |  | 44733.4546 | 49.9041
|  |  | 44733.4546 | 49.9041
|  |  | 44733.4546 | 49.9041
|  |  | 44733.4546 | 49.9041
|  |  | 44733.4546 | 49.9041
|  |  | 44733.4546 | 49.9041
|  |  | 44733.4546 | 49.9042
|  |  | 44733.4546 | 49.9042
|  |  | 44733.4546 | 49.9043
|  |  | 44733.4546 | 49.9043
|  |  | 44733.4546 | 49.9044
|  |  | 44733.4546 | 49.9045
|  |  | 44733.4546 | 49.9046
|  |  | 44733.4546 | 49.9047
|  |  | 44733.4546 | 49.9047
|  |  | 44733.4546 | 49.9047
|  |  | 44733.4546 | 49.9048
|  |  | 44733.4546 | 49.9049
|  |  | 44733.4546 | 49.9049
|  |  | 44733.4546 | 49.9049
|  |  | 44733.4546 | 49.905
|  |  | 44733.4546 | 49.905
|  |  | 44733.4546 | 49.9051
|  |  | 44733.4546 | 49.9052
|  |  | 44733.4546 | 49.9052
|  |  | 44733.4546 | 49.9053
|  |  | 44733.4546 | 49.9053
|  |  | 44733.4546 | 49.9054
|  |  | 44733.4546 | 49.9054
|  |  | 44733.4546 | 49.9055
|  |  | 44733.4546 | 49.9055
|  |  | 44733.4546 | 49.9055
|  |  | 44733.4546 | 49.9055
|  |  | 44733.4546 | 49.9056
|  |  | 44733.4546 | 49.9057
|  |  | 44733.4546 | 49.9057
|  |  | 2022-06-21 10:55 | 49.9057
|  |  | 44733.4546 | 49.9057
|  |  | 44733.4546 | 49.9057
|  |  | 44733.4546 | 49.9058
|  |  | 44733.4546 | 49.9057
|  |  | 44733.4546 | 49.9058
|  |  | 44733.4546 | 49.9058
|  |  | 44733.4546 | 49.9059
|  |  | 44733.4546 | 49.9059
|  |  | 44733.4546 | 49.9059
|  |  | 44733.4546 | 49.9059
|  |  | 44733.4546 | 49.9059
|  |  | 44733.4546 | 49.906
|  |  | 44733.4546 | 49.906
|  |  | 44733.4546 | 49.906
|  |  | 44733.4546 | 49.906
|  |  | 44733.4546 | 49.9061
|  |  | 44733.4546 | 49.9061
|  |  | 44733.4546 | 49.9061
|  |  | 44733.4546 | 49.9061
|  |  | 44733.4546 | 49.9061
|  |  | 44733.4546 | 49.9061
|  |  | 44733.4546 | 49.906
|  |  | 44733.4546 | 49.9061
|  |  | 44733.4546 | 49.9061
|  |  | 44733.4546 | 49.9061
|  |  | 44733.4546 | 49.9062
|  |  | 44733.4546 | 49.9062
|  |  | 44733.4546 | 49.9063
|  |  | 44733.4546 | 49.9064
|  |  | 44733.4546 | 49.9064
|  |  | 44733.4546 | 49.9065
|  |  | 44733.4546 | 49.9065
|  |  | 44733.4546 | 49.9065
|  |  | 44733.4546 | 49.9065
|  |  | 44733.4546 | 49.9066
|  |  | 44733.4546 | 49.9066
|  |  | 44733.4546 | 49.9066
|  |  | 44733.4546 | 49.9066
|  |  | 44733.4546 | 49.9066
|  |  | 44733.4546 | 49.9067
|  |  | 44733.4546 | 49.9067
|  |  | 44733.4546 | 49.9068
|  |  | 44733.4546 | 49.9069
|  |  | 44733.4546 | 49.907
|  |  | 44733.4546 | 49.907
|  |  | 44733.4546 | 49.9071
|  |  | 44733.4546 | 49.9072
|  |  | 44733.4546 | 49.9073
|  |  | 44733.4546 | 49.9073
|  |  | 2022-06-21 10:55 | 49.9074
|  |  | 44733.4546 | 49.9074
|  |  | 44733.4546 | 49.9074
|  |  | 44733.4546 | 49.9074
|  |  | 44733.4546 | 49.9074
|  |  | 44733.4546 | 49.9074
|  |  | 44733.4546 | 49.9073
|  |  | 44733.4546 | 49.9074
|  |  | 44733.4546 | 49.9074
|  |  | 44733.4546 | 49.9074
|  |  | 44733.4546 | 49.9074
|  |  | 44733.4546 | 49.9074
|  |  | 44733.4546 | 49.9074
|  |  | 44733.4546 | 49.9074
|  |  | 44733.4546 | 49.9074
|  |  | 44733.4546 | 49.9075
|  |  | 44733.4546 | 49.9075
|  |  | 44733.4546 | 49.9074
|  |  | 44733.4546 | 49.9074
|  |  | 44733.4546 | 49.9074
|  |  | 44733.4546 | 49.9073
|  |  | 44733.4546 | 49.9073
|  |  | 44733.4546 | 49.9073
|  |  | 44733.4546 | 49.9073
|  |  | 44733.4546 | 49.9073
|  |  | 44733.4546 | 49.9074
|  |  | 44733.4546 | 49.9074
|  |  | 44733.4546 | 49.9075
|  |  | 44733.4546 | 49.9078
|  |  | 44733.4546 | 49.9085
|  |  | 44733.4546 | 49.9095
|  |  | 44733.4546 | 49.9107
|  |  | 44733.4546 | 49.9127
|  |  | 44733.4546 | 49.9146
|  |  | 44733.4546 | 49.9164
|  |  | 44733.4546 | 49.918
|  |  | 44733.4546 | 49.9197
|  |  | 44733.4546 | 49.9199
|  |  | 44733.4546 | 49.9201
|  |  | 44733.4546 | 49.92
|  |  | 44733.4546 | 49.9195
|  |  | 44733.4546 | 49.919
|  |  | 44733.4546 | 49.9183
|  |  | 44733.4546 | 49.9183
|  |  | 44733.4546 | 49.9182
|  |  | 44733.4546 | 49.9184
|  |  | 44733.4546 | 49.9188
|  |  | 44733.4546 | 49.9194
|  |  | 44733.4546 | 49.9201
|  |  | 44733.4546 | 49.9209
|  |  | 2022-06-21 10:55 | 49.9215
|  |  | 44733.4546 | 49.9221
|  |  | 44733.4546 | 49.9225
|  |  | 44733.4546 | 49.9228
|  |  | 44733.4546 | 49.923
|  |  | 44733.4546 | 49.9231
|  |  | 44733.4546 | 49.9232
|  |  | 44733.4546 | 49.9232
|  |  | 44733.4546 | 49.9231
|  |  | 44733.4546 | 49.9231
|  |  | 44733.4546 | 49.9231
|  |  | 44733.4546 | 49.9232
|  |  | 44733.4546 | 49.9232
|  |  | 44733.4546 | 49.9233
|  |  | 44733.4546 | 49.9234
|  |  | 44733.4546 | 49.9236
|  |  | 44733.4546 | 49.9238
|  |  | 44733.4546 | 49.9241
|  |  | 44733.4546 | 49.9243
|  |  | 44733.4546 | 49.9246
|  |  | 44733.4546 | 49.9249
|  |  | 44733.4546 | 49.9251
|  |  | 44733.4546 | 49.9253
|  |  | 44733.4546 | 49.9255
|  |  | 44733.4546 | 49.9257
|  |  | 44733.4546 | 49.9259
|  |  | 44733.4546 | 49.926
|  |  | 44733.4546 | 49.9262
|  |  | 44733.4546 | 49.9264
|  |  | 44733.4546 | 49.9266
|  |  | 44733.4546 | 49.9269
|  |  | 44733.4546 | 49.9272
|  |  | 44733.4546 | 49.9274
|  |  | 44733.4546 | 49.9277
|  |  | 44733.4546 | 49.928
|  |  | 44733.4546 | 49.9283
|  |  | 44733.4546 | 49.9286
|  |  | 44733.4546 | 49.929
|  |  | 44733.4546 | 49.9295
|  |  | 44733.4546 | 49.9301
|  |  | 44733.4546 | 49.9307
|  |  | 44733.4546 | 49.9311
|  |  | 44733.4546 | 49.9315
|  |  | 44733.4546 | 49.9319
|  |  | 44733.4546 | 49.9325
|  |  | 44733.4546 | 49.933
|  |  | 44733.4546 | 49.9337
|  |  | 44733.4546 | 49.9343
|  |  | 44733.4546 | 49.9348
|  |  | 44733.4546 | 49.9354
|  |  | 2022-06-21 10:55 | 49.9361
|  |  | 44733.4546 | 49.9366
|  |  | 44733.4546 | 49.9373
|  |  | 44733.4546 | 49.9379
|  |  | 44733.4546 | 49.9385
|  |  | 44733.4546 | 49.9392
|  |  | 44733.4546 | 49.9398
|  |  | 44733.4546 | 49.9404
|  |  | 44733.4546 | 49.941
|  |  | 44733.4546 | 49.9417
|  |  | 44733.4546 | 49.9424
|  |  | 44733.4546 | 49.943
|  |  | 44733.4546 | 49.9437
|  |  | 44733.4546 | 49.9443
|  |  | 44733.4546 | 49.9448
|  |  | 44733.4546 | 49.9454
|  |  | 44733.4546 | 49.946
|  |  | 44733.4546 | 49.9465
|  |  | 44733.4546 | 49.947
|  |  | 44733.4546 | 49.9474
|  |  | 44733.4546 | 49.9478
|  |  | 44733.4546 | 49.9482
|  |  | 44733.4546 | 49.9485
|  |  | 44733.4546 | 49.9489
|  |  | 44733.4546 | 49.9492
|  |  | 44733.4546 | 49.9495
|  |  | 44733.4546 | 49.9497
|  |  | 44733.4546 | 49.95
|  |  | 44733.4546 | 49.9503
|  |  | 44733.4546 | 49.9505
|  |  | 44733.4546 | 49.9507
|  |  | 44733.4546 | 49.951
|  |  | 44733.4546 | 49.9512
|  |  | 44733.4546 | 49.9515
|  |  | 44733.4546 | 49.9517
|  |  | 44733.4546 | 49.9519
|  |  | 44733.4546 | 49.9521
|  |  | 44733.4546 | 49.9523
|  |  | 44733.4546 | 49.9524
|  |  | 44733.4546 | 49.9526
|  |  | 44733.4546 | 49.9527
|  |  | 44733.4546 | 49.9529
|  |  | 44733.4546 | 49.9532
|  |  | 44733.4546 | 49.9534
|  |  | 44733.4546 | 49.9536
|  |  | 44733.4546 | 49.9539
|  |  | 44733.4546 | 49.9542
|  |  | 44733.4546 | 49.9545
|  |  | 44733.4546 | 49.9548
|  |  | 44733.4546 | 49.9551
|  |  | 2022-06-21 10:55 | 49.9554
|  |  | 44733.4546 | 49.9557
|  |  | 44733.4546 | 49.956
|  |  | 44733.4546 | 49.9564
|  |  | 44733.4546 | 49.9567
|  |  | 44733.4546 | 49.957
|  |  | 44733.4546 | 49.9574
|  |  | 44733.4546 | 49.9577
|  |  | 44733.4546 | 49.9581
|  |  | 44733.4546 | 49.9584
|  |  | 44733.4546 | 49.9588
|  |  | 44733.4546 | 49.9592
|  |  | 44733.4546 | 49.9595
|  |  | 44733.4546 | 49.9598
|  |  | 44733.4546 | 49.9602
|  |  | 44733.4546 | 49.9606
|  |  | 44733.4546 | 49.9609
|  |  | 44733.4546 | 49.9613
|  |  | 44733.4546 | 49.9617
|  |  | 44733.4546 | 49.9622
|  |  | 44733.4546 | 49.9626
|  |  | 44733.4546 | 49.963
|  |  | 44733.4546 | 49.9634
|  |  | 44733.4546 | 49.9638
|  |  | 44733.4546 | 49.9641
|  |  | 44733.4546 | 49.9645
|  |  | 44733.4546 | 49.9648
|  |  | 44733.4546 | 49.9651
|  |  | 44733.4546 | 49.9655
|  |  | 44733.4546 | 49.9658
|  |  | 44733.4546 | 49.9662
|  |  | 44733.4546 | 49.9665
|  |  | 44733.4546 | 49.9668
|  |  | 44733.4546 | 49.9671
|  |  | 44733.4546 | 49.9674
|  |  | 44733.4546 | 49.9678
|  |  | 44733.4546 | 49.9681
|  |  | 44733.4546 | 49.9684
|  |  | 44733.4546 | 49.9687
|  |  | 44733.4547 | 49.9691
|  |  | 44733.4547 | 49.9693
|  |  | 44733.4547 | 49.9696
|  |  | 44733.4547 | 49.9699
|  |  | 44733.4547 | 49.9701
|  |  | 44733.4547 | 49.9703
|  |  | 44733.4547 | 49.9705
|  |  | 44733.4547 | 49.9707
|  |  | 44733.4547 | 49.9709
|  |  | 44733.4547 | 49.9711
|  |  | 44733.4547 | 49.9713
|  |  | 2022-06-21 10:55 | 49.9716
|  |  | 44733.4547 | 49.9718
|  |  | 44733.4547 | 49.9721
|  |  | 44733.4547 | 49.9724
|  |  | 44733.4547 | 49.9726
|  |  | 44733.4547 | 49.9729
|  |  | 44733.4547 | 49.9731
|  |  | 44733.4547 | 49.9733
|  |  | 44733.4547 | 49.9736
|  |  | 44733.4547 | 49.9739
|  |  | 44733.4547 | 49.9741
|  |  | 44733.4547 | 49.9744
|  |  | 44733.4547 | 49.9746
|  |  | 44733.4547 | 49.9747
|  |  | 44733.4547 | 49.9749
|  |  | 44733.4547 | 49.9752
|  |  | 44733.4547 | 49.9754
|  |  | 44733.4547 | 49.9756
|  |  | 44733.4547 | 49.9758
|  |  | 44733.4547 | 49.9761
|  |  | 44733.4547 | 49.9764
|  |  | 44733.4547 | 49.9767
|  |  | 44733.4547 | 49.977
|  |  | 44733.4547 | 49.9773
|  |  | 44733.4547 | 49.9777
|  |  | 44733.4547 | 49.978
|  |  | 44733.4547 | 49.9783
|  |  | 44733.4547 | 49.9785
|  |  | 44733.4547 | 49.9787
|  |  | 44733.4547 | 49.9789
|  |  | 44733.4547 | 49.9791
|  |  | 44733.4547 | 49.9794
|  |  | 44733.4547 | 49.9797
|  |  | 44733.4547 | 49.9799
|  |  | 44733.4547 | 49.9802
|  |  | 44733.4547 | 49.9805
|  |  | 44733.4547 | 49.9807
|  |  | 44733.4547 | 49.9809
|  |  | 44733.4547 | 49.9811
|  |  | 44733.4547 | 49.9813
|  |  | 44733.4547 | 49.9815
|  |  | 44733.4547 | 49.9817
|  |  | 44733.4547 | 49.9818
|  |  | 44733.4547 | 49.9819
|  |  | 44733.4547 | 49.982
|  |  | 44733.4547 | 49.9822
|  |  | 44733.4547 | 49.9824
|  |  | 44733.4547 | 49.9827
|  |  | 44733.4547 | 49.983
|  |  | 44733.4547 | 49.9832
|  |  | 2022-06-21 10:55 | 49.9835
|  |  | 44733.4547 | 49.9837
|  |  | 44733.4547 | 49.9839
|  |  | 44733.4547 | 49.9841
|  |  | 44733.4547 | 49.9843
|  |  | 44733.4547 | 49.9844
|  |  | 44733.4547 | 49.9846
|  |  | 44733.4547 | 49.9847
|  |  | 44733.4547 | 49.9848
|  |  | 44733.4547 | 49.985
|  |  | 44733.4547 | 49.9852
|  |  | 44733.4547 | 49.9854
|  |  | 44733.4547 | 49.9856
|  |  | 44733.4547 | 49.9858
|  |  | 44733.4547 | 49.986
|  |  | 44733.4547 | 49.9862
|  |  | 44733.4547 | 49.9863
|  |  | 44733.4547 | 49.9864
|  |  | 44733.4547 | 49.9866
|  |  | 44733.4547 | 49.9867
|  |  | 44733.4547 | 49.9869
|  |  | 44733.4547 | 49.987
|  |  | 44733.4547 | 49.9872
|  |  | 44733.4547 | 49.9874
|  |  | 44733.4547 | 49.9876
|  |  | 44733.4547 | 49.9878
|  |  | 44733.4547 | 49.988
|  |  | 44733.4547 | 49.9882
|  |  | 44733.4547 | 49.9883
|  |  | 44733.4547 | 49.9886
|  |  | 44733.4547 | 49.9888
|  |  | 44733.4547 | 49.9889
|  |  | 44733.4547 | 49.989
|  |  | 44733.4547 | 49.9891
|  |  | 44733.4547 | 49.9893
|  |  | 44733.4547 | 49.9894
|  |  | 44733.4547 | 49.9896
|  |  | 44733.4547 | 49.9898
|  |  | 44733.4547 | 49.99
|  |  | 44733.4547 | 49.9901
|  |  | 44733.4547 | 49.9903
|  |  | 44733.4547 | 49.9906
|  |  | 44733.4547 | 49.9908
|  |  | 44733.4547 | 49.991
|  |  | 44733.4547 | 49.9912
|  |  | 44733.4547 | 49.9913
|  |  | 44733.4547 | 49.9915
|  |  | 44733.4547 | 49.9917
|  |  | 44733.4547 | 49.9919
|  |  | 44733.4547 | 49.9921
|  |  | 2022-06-21 10:55 | 49.9923
|  |  | 44733.4547 | 49.9926
|  |  | 44733.4547 | 49.9928
|  |  | 44733.4547 | 49.993
|  |  | 44733.4547 | 49.9931
|  |  | 44733.4547 | 49.9933
|  |  | 44733.4547 | 49.9934
|  |  | 44733.4547 | 49.9936
|  |  | 44733.4547 | 49.9938
|  |  | 44733.4547 | 49.994
|  |  | 44733.4547 | 49.9941
|  |  | 44733.4547 | 49.9942
|  |  | 44733.4547 | 49.9944
|  |  | 44733.4547 | 49.9945
|  |  | 44733.4547 | 49.9947
|  |  | 44733.4547 | 49.9948
|  |  | 44733.4547 | 49.995
|  |  | 44733.4547 | 49.9951
|  |  | 44733.4547 | 49.9953
|  |  | 44733.4547 | 49.9955
|  |  | 44733.4547 | 49.9957
|  |  | 44733.4547 | 49.9959
|  |  | 44733.4547 | 49.9961
|  |  | 44733.4547 | 49.9962
|  |  | 44733.4547 | 49.9965
|  |  | 44733.4547 | 49.9966
|  |  | 44733.4547 | 49.9968
|  |  | 44733.4547 | 49.997
|  |  | 44733.4547 | 49.9972
|  |  | 44733.4547 | 49.9973
|  |  | 44733.4547 | 49.9974
|  |  | 44733.4547 | 49.9975
|  |  | 44733.4547 | 49.9976
|  |  | 44733.4547 | 49.9977
|  |  | 44733.4547 | 49.9979
|  |  | 44733.4547 | 49.9981
|  |  | 44733.4547 | 49.9982
|  |  | 44733.4547 | 49.9984
|  |  | 44733.4547 | 49.9986
|  |  | 44733.4547 | 49.9988
|  |  | 44733.4547 | 49.9989
|  |  | 44733.4547 | 49.9991
|  |  | 44733.4547 | 49.9992
|  |  | 44733.4547 | 49.9994
|  |  | 44733.4547 | 49.9995
|  |  | 44733.4547 | 49.9996
|  |  | 44733.4547 | 49.9998
|  |  | 44733.4547 | 49.9999
|  |  | 44733.4547 | 50
|  |  | 44733.4547 | 50.0001
|  |  | 2022-06-21 10:55 | 50.0001
|  |  | 44733.4547 | 50.0003
|  |  | 44733.4547 | 50.0003
|  |  | 44733.4547 | 50.0004
|  |  | 44733.4547 | 50.0005
|  |  | 44733.4547 | 50.0007
|  |  | 44733.4547 | 50.0009
|  |  | 44733.4547 | 50.0011
|  |  | 44733.4547 | 50.0012
|  |  | 44733.4547 | 50.0014
|  |  | 44733.4547 | 50.0015
|  |  | 44733.4547 | 50.0017
|  |  | 44733.4547 | 50.0018
|  |  | 44733.4547 | 50.002
|  |  | 44733.4547 | 50.0021
|  |  | 44733.4547 | 50.0024
|  |  | 44733.4547 | 50.0025
|  |  | 44733.4547 | 50.0026
|  |  | 44733.4547 | 50.0026
|  |  | 44733.4547 | 50.0027
|  |  | 44733.4547 | 50.0028
|  |  | 44733.4547 | 50.0028
|  |  | 44733.4547 | 50.0029
|  |  | 44733.4547 | 50.0031
|  |  | 44733.4547 | 50.0033
|  |  | 44733.4547 | 50.0035
|  |  | 44733.4547 | 50.0036
|  |  | 44733.4547 | 50.0038
|  |  | 44733.4547 | 50.0039
|  |  | 44733.4547 | 50.0041
|  |  | 44733.4547 | 50.0043
|  |  | 44733.4547 | 50.0044
|  |  | 44733.4547 | 50.0045
|  |  | 44733.4547 | 50.0046
|  |  | 44733.4547 | 50.0047
|  |  | 44733.4547 | 50.0049
|  |  | 44733.4547 | 50.005
|  |  | 44733.4547 | 50.005
|  |  | 44733.4547 | 50.0052
|  |  | 44733.4547 | 50.0054
|  |  | 44733.4547 | 50.0057
|  |  | 44733.4547 | 50.0059
|  |  | 44733.4547 | 50.0061
|  |  | 44733.4547 | 50.0063
|  |  | 44733.4547 | 50.0064
|  |  | 44733.4547 | 50.0066
|  |  | 44733.4547 | 50.0068
|  |  | 44733.4547 | 50.0069
|  |  | 44733.4547 | 50.007
|  |  | 44733.4547 | 50.007
|  |  | 2022-06-21 10:55 | 50.0071
|  |  | 44733.4547 | 50.0072
|  |  | 44733.4547 | 50.0073
|  |  | 44733.4547 | 50.0074
|  |  | 44733.4547 | 50.0076
|  |  | 44733.4547 | 50.0077
|  |  | 44733.4547 | 50.0079
|  |  | 44733.4547 | 50.008
|  |  | 44733.4547 | 50.0082
|  |  | 44733.4547 | 50.0083
|  |  | 44733.4547 | 50.0084
|  |  | 44733.4547 | 50.0085
|  |  | 44733.4547 | 50.0086
|  |  | 44733.4547 | 50.0087
|  |  | 44733.4547 | 50.0088
|  |  | 44733.4547 | 50.0089
|  |  | 44733.4547 | 50.009
|  |  | 44733.4547 | 50.009
|  |  | 44733.4547 | 50.0092
|  |  | 44733.4547 | 50.0093
|  |  | 44733.4547 | 50.0094
|  |  | 44733.4547 | 50.0095
|  |  | 44733.4547 | 50.0095
|  |  | 44733.4547 | 50.0096
|  |  | 44733.4547 | 50.0097
|  |  | 44733.4547 | 50.0098
|  |  | 44733.4547 | 50.0099
|  |  | 44733.4547 | 50.0099
|  |  | 44733.4547 | 50.01
|  |  | 44733.4547 | 50.0102
|  |  | 44733.4547 | 50.0103
|  |  | 44733.4547 | 50.0104
|  |  | 44733.4547 | 50.0105
|  |  | 44733.4547 | 50.0106
|  |  | 44733.4547 | 50.0107
|  |  | 44733.4547 | 50.0108
|  |  | 44733.4547 | 50.0109
|  |  | 44733.4547 | 50.011
|  |  | 44733.4547 | 50.0111
|  |  | 44733.4547 | 50.0112
|  |  | 44733.4547 | 50.0113
|  |  | 44733.4547 | 50.0114
|  |  | 44733.4547 | 50.0115
|  |  | 44733.4547 | 50.0116
|  |  | 44733.4547 | 50.0116
|  |  | 44733.4547 | 50.0118
|  |  | 44733.4547 | 50.0119
|  |  | 44733.4547 | 50.0121
|  |  | 44733.4547 | 50.0122
|  |  | 44733.4547 | 50.0123
|  |  | 2022-06-21 10:55 | 50.0125
|  |  | 44733.4547 | 50.0127
|  |  | 44733.4547 | 50.0128
|  |  | 44733.4547 | 50.0129
|  |  | 44733.4547 | 50.0129
|  |  | 44733.4547 | 50.013
|  |  | 44733.4547 | 50.013
|  |  | 44733.4547 | 50.0131
|  |  | 44733.4547 | 50.0132
|  |  | 44733.4547 | 50.0133
|  |  | 44733.4547 | 50.0134
|  |  | 44733.4547 | 50.0135
|  |  | 44733.4547 | 50.0137
|  |  | 44733.4547 | 50.0138
|  |  | 44733.4547 | 50.0138
|  |  | 44733.4547 | 50.014
|  |  | 44733.4547 | 50.0141
|  |  | 44733.4547 | 50.0142
|  |  | 44733.4547 | 50.0144
|  |  | 44733.4547 | 50.0145
|  |  | 44733.4547 | 50.0145
|  |  | 44733.4547 | 50.0146
|  |  | 44733.4547 | 50.0147
|  |  | 44733.4547 | 50.0147
|  |  | 44733.4547 | 50.0149
|  |  | 44733.4547 | 50.015
|  |  | 44733.4547 | 50.015
|  |  | 44733.4547 | 50.0151
|  |  | 44733.4547 | 50.0152
|  |  | 44733.4547 | 50.0153
|  |  | 44733.4547 | 50.0153
|  |  | 44733.4547 | 50.0155
|  |  | 44733.4547 | 50.0155
|  |  | 44733.4547 | 50.0156
|  |  | 44733.4547 | 50.0156
|  |  | 44733.4547 | 50.0157
|  |  | 44733.4547 | 50.0158
|  |  | 44733.4547 | 50.0158
|  |  | 44733.4547 | 50.0158
|  |  | 44733.4547 | 50.0159
|  |  | 44733.4547 | 50.0161
|  |  | 44733.4547 | 50.0161
|  |  | 44733.4547 | 50.0163
|  |  | 44733.4547 | 50.0164
|  |  | 44733.4547 | 50.0165
|  |  | 44733.4547 | 50.0167
|  |  | 44733.4547 | 50.0168
|  |  | 44733.4547 | 50.0169
|  |  | 44733.4547 | 50.0171
|  |  | 44733.4547 | 50.0171
|  |  | 2022-06-21 10:55 | 50.0172
|  |  | 44733.4547 | 50.0173
|  |  | 44733.4547 | 50.0173
|  |  | 44733.4547 | 50.0174
|  |  | 44733.4547 | 50.0174
|  |  | 44733.4547 | 50.0175
|  |  | 44733.4547 | 50.0176
|  |  | 44733.4547 | 50.0176
|  |  | 44733.4547 | 50.0177
|  |  | 44733.4547 | 50.0178
|  |  | 44733.4547 | 50.0179
|  |  | 44733.4547 | 50.0181
|  |  | 44733.4547 | 50.0181
|  |  | 44733.4547 | 50.0182
|  |  | 44733.4547 | 50.0183
|  |  | 44733.4547 | 50.0184
|  |  | 44733.4547 | 50.0185
|  |  | 44733.4547 | 50.0186
|  |  | 44733.4547 | 50.0188
|  |  | 44733.4547 | 50.0188
|  |  | 44733.4547 | 50.019
|  |  | 44733.4547 | 50.0192
|  |  | 44733.4547 | 50.0193
|  |  | 44733.4547 | 50.0194
|  |  | 44733.4547 | 50.0195
|  |  | 44733.4547 | 50.0195
|  |  | 44733.4547 | 50.0196
|  |  | 44733.4547 | 50.0197
|  |  | 44733.4547 | 50.0198
|  |  | 44733.4547 | 50.0199
|  |  | 44733.4547 | 50.0199
|  |  | 44733.4547 | 50.0201
|  |  | 44733.4547 | 50.0201
|  |  | 44733.4547 | 50.0203
|  |  | 44733.4547 | 50.0205
|  |  | 44733.4547 | 50.0206
|  |  | 44733.4547 | 50.0207
|  |  | 44733.4547 | 50.0208
|  |  | 44733.4547 | 50.0208
|  |  | 44733.4547 | 50.0208
|  |  | 44733.4547 | 50.021
|  |  | 44733.4547 | 50.021
|  |  | 44733.4547 | 50.021
|  |  | 44733.4547 | 50.021
|  |  | 44733.4547 | 50.0211
|  |  | 44733.4547 | 50.0212
|  |  | 44733.4547 | 50.0216
|  |  | 44733.4547 | 50.0216
|  |  | 44733.4547 | 50.0217
|  |  | 44733.4547 | 50.0218
|  |  | 2022-06-21 10:55 | 50.0219
|  |  | 44733.4547 | 50.022
|  |  | 44733.4547 | 50.0221
|  |  | 44733.4547 | 50.0222
|  |  | 44733.4547 | 50.0223
|  |  | 44733.4547 | 50.0224
|  |  | 44733.4547 | 50.0225
|  |  | 44733.4547 | 50.0226
|  |  | 44733.4547 | 50.0227
|  |  | 44733.4547 | 50.0228
|  |  | 44733.4547 | 50.0228
|  |  | 44733.4547 | 50.0228
|  |  | 44733.4547 | 50.0229
|  |  | 44733.4547 | 50.0228
|  |  | 44733.4547 | 50.0229
|  |  | 44733.4547 | 50.0229
|  |  | 44733.4547 | 50.0229
|  |  | 44733.4547 | 50.0228
|  |  | 44733.4547 | 50.0229
|  |  | 44733.4547 | 50.023
|  |  | 44733.4547 | 50.023
|  |  | 44733.4547 | 50.0231
|  |  | 44733.4547 | 50.0231
|  |  | 44733.4547 | 50.0232
|  |  | 44733.4547 | 50.0233
|  |  | 44733.4547 | 50.0234
|  |  | 44733.4547 | 50.0235
|  |  | 44733.4547 | 50.0236
|  |  | 44733.4547 | 50.0236
|  |  | 44733.4547 | 50.0237
|  |  | 44733.4547 | 50.0237
|  |  | 44733.4547 | 50.0238
|  |  | 44733.4547 | 50.0238
|  |  | 44733.4547 | 50.0239
|  |  | 44733.4547 | 50.0239
|  |  | 44733.4547 | 50.0239
|  |  | 44733.4547 | 50.0239
|  |  | 44733.4547 | 50.024
|  |  | 44733.4547 | 50.0241
|  |  | 44733.4547 | 50.0241
|  |  | 44733.4547 | 50.0242
|  |  | 44733.4547 | 50.0243
|  |  | 44733.4547 | 50.0243
|  |  | 44733.4547 | 50.0244
|  |  | 44733.4547 | 50.0244
|  |  | 44733.4547 | 50.0245
|  |  | 44733.4547 | 50.0245
|  |  | 44733.4547 | 50.0245
|  |  | 44733.4547 | 50.0245
|  |  | 44733.4547 | 50.0245
|  |  | 2022-06-21 10:55 | 50.0245
|  |  | 44733.4547 | 50.0245
|  |  | 44733.4547 | 50.0245
|  |  | 44733.4547 | 50.0245
|  |  | 44733.4547 | 50.0245
|  |  | 44733.4547 | 50.0245
|  |  | 44733.4547 | 50.0245
|  |  | 44733.4547 | 50.0246
|  |  | 44733.4547 | 50.0247
|  |  | 44733.4547 | 50.0248
|  |  | 44733.4547 | 50.0248
|  |  | 44733.4547 | 50.0249
|  |  | 44733.4547 | 50.0249
|  |  | 44733.4547 | 50.025
|  |  | 44733.4547 | 50.0251
|  |  | 44733.4547 | 50.0251
|  |  | 44733.4547 | 50.0253
|  |  | 44733.4547 | 50.0253
|  |  | 44733.4547 | 50.0252
|  |  | 44733.4547 | 50.0253
|  |  | 44733.4547 | 50.0253
|  |  | 44733.4548 | 50.0254
|  |  | 44733.4548 | 50.0254
|  |  | 44733.4548 | 50.0255
|  |  | 44733.4548 | 50.0255
|  |  | 44733.4548 | 50.0256
|  |  | 44733.4548 | 50.0256
|  |  | 44733.4548 | 50.0257
|  |  | 44733.4548 | 50.0258
|  |  | 44733.4548 | 50.0259
|  |  | 44733.4548 | 50.026
|  |  | 44733.4548 | 50.026
|  |  | 44733.4548 | 50.026
|  |  | 44733.4548 | 50.026
|  |  | 44733.4548 | 50.0261
|  |  | 44733.4548 | 50.0261
|  |  | 44733.4548 | 50.0262
|  |  | 44733.4548 | 50.0263
|  |  | 44733.4548 | 50.0264
|  |  | 44733.4548 | 50.0265
|  |  | 44733.4548 | 50.0266
|  |  | 44733.4548 | 50.0266
|  |  | 44733.4548 | 50.0267
|  |  | 44733.4548 | 50.0268
|  |  | 44733.4548 | 50.0269
|  |  | 44733.4548 | 50.0269
|  |  | 44733.4548 | 50.027
|  |  | 44733.4548 | 50.0271
|  |  | 44733.4548 | 50.0272
|  |  | 44733.4548 | 50.0274
|  |  | 2022-06-21 10:55 | 50.0275
|  |  | 44733.4548 | 50.0275
|  |  | 44733.4548 | 50.0275
|  |  | 44733.4548 | 50.0276
|  |  | 44733.4548 | 50.0276
|  |  | 44733.4548 | 50.0277
|  |  | 44733.4548 | 50.0278
|  |  | 44733.4548 | 50.0279
|  |  | 44733.4548 | 50.028
|  |  | 44733.4548 | 50.0282
|  |  | 44733.4548 | 50.0283
|  |  | 44733.4548 | 50.0283
|  |  | 44733.4548 | 50.0284
|  |  | 44733.4548 | 50.0284
|  |  | 44733.4548 | 50.0285
|  |  | 44733.4548 | 50.0285
|  |  | 44733.4548 | 50.0285
|  |  | 44733.4548 | 50.0286
|  |  | 44733.4548 | 50.0286
|  |  | 44733.4548 | 50.0286
|  |  | 44733.4548 | 50.0288
|  |  | 44733.4548 | 50.0289
|  |  | 44733.4548 | 50.0291
|  |  | 44733.4548 | 50.0291
|  |  | 44733.4548 | 50.0292
|  |  | 44733.4548 | 50.0292
|  |  | 44733.4548 | 50.0293
|  |  | 44733.4548 | 50.0293
|  |  | 44733.4548 | 50.0294
|  |  | 44733.4548 | 50.0294
|  |  | 44733.4548 | 50.0294
|  |  | 44733.4548 | 50.0293
|  |  | 44733.4548 | 50.0293
|  |  | 44733.4548 | 50.0293
|  |  | 44733.4548 | 50.0293
|  |  | 44733.4548 | 50.0293
|  |  | 44733.4548 | 50.0294
|  |  | 44733.4548 | 50.0294
|  |  | 44733.4548 | 50.0295
|  |  | 44733.4548 | 50.0295
|  |  | 44733.4548 | 50.0296
|  |  | 44733.4548 | 50.0297
|  |  | 44733.4548 | 50.0297
|  |  | 44733.4548 | 50.0298
|  |  | 44733.4548 | 50.0299
|  |  | 44733.4548 | 50.03
|  |  | 44733.4548 | 50.0301
|  |  | 44733.4548 | 50.0302
|  |  | 44733.4548 | 50.0303
|  |  | 44733.4548 | 50.0303
|  |  | 2022-06-21 10:55 | 50.0303
|  |  | 44733.4548 | 50.0303
|  |  | 44733.4548 | 50.0304
|  |  | 44733.4548 | 50.0305
|  |  | 44733.4548 | 50.0305
|  |  | 44733.4548 | 50.0305
|  |  | 44733.4548 | 50.0306
|  |  | 44733.4548 | 50.0307
|  |  | 44733.4548 | 50.0307
|  |  | 44733.4548 | 50.0308
|  |  | 44733.4548 | 50.0309
|  |  | 44733.4548 | 50.0309
|  |  | 44733.4548 | 50.031
|  |  | 44733.4548 | 50.031
|  |  | 44733.4548 | 50.031
|  |  | 44733.4548 | 50.031
|  |  | 44733.4548 | 50.031
|  |  | 44733.4548 | 50.0311
|  |  | 44733.4548 | 50.0312
|  |  | 44733.4548 | 50.0314
|  |  | 44733.4548 | 50.0315
|  |  | 44733.4548 | 50.0316
|  |  | 44733.4548 | 50.0317
|  |  | 44733.4548 | 50.0318
|  |  | 44733.4548 | 50.0318
|  |  | 44733.4548 | 50.0319
|  |  | 44733.4548 | 50.0319
|  |  | 44733.4548 | 50.0319
|  |  | 44733.4548 | 50.0319
|  |  | 44733.4548 | 50.032
|  |  | 44733.4548 | 50.032
|  |  | 44733.4548 | 50.032
|  |  | 44733.4548 | 50.032
|  |  | 44733.4548 | 50.0321
|  |  | 44733.4548 | 50.0321
|  |  | 44733.4548 | 50.0322
|  |  | 44733.4548 | 50.0323
|  |  | 44733.4548 | 50.0323
|  |  | 44733.4548 | 50.0323
|  |  | 44733.4548 | 50.0323
|  |  | 44733.4548 | 50.0323
|  |  | 44733.4548 | 50.0323
|  |  | 44733.4548 | 50.0323
|  |  | 44733.4548 | 50.0322
|  |  | 44733.4548 | 50.0322
|  |  | 44733.4548 | 50.0322
|  |  | 44733.4548 | 50.0322
|  |  | 44733.4548 | 50.0322
|  |  | 44733.4548 | 50.0323
|  |  | 44733.4548 | 50.0323
|  |  | 2022-06-21 10:55 | 50.0323
|  |  | 44733.4548 | 50.0323
|  |  | 44733.4548 | 50.0324
|  |  | 44733.4548 | 50.0324
|  |  | 44733.4548 | 50.0324
|  |  | 44733.4548 | 50.0324
|  |  | 44733.4548 | 50.0324
|  |  | 44733.4548 | 50.0324
|  |  | 44733.4548 | 50.0325
|  |  | 44733.4548 | 50.0326
|  |  | 44733.4548 | 50.0327
|  |  | 44733.4548 | 50.0327
|  |  | 44733.4548 | 50.0328
|  |  | 44733.4548 | 50.0328
|  |  | 44733.4548 | 50.0328
|  |  | 44733.4548 | 50.0328
|  |  | 44733.4548 | 50.0327
|  |  | 44733.4548 | 50.0327
|  |  | 44733.4548 | 50.0327
|  |  | 44733.4548 | 50.0327
|  |  | 44733.4548 | 50.0327
|  |  | 44733.4548 | 50.0327
|  |  | 44733.4548 | 50.0327
|  |  | 44733.4548 | 50.0327
|  |  | 44733.4548 | 50.0327
|  |  | 44733.4548 | 50.0327
|  |  | 44733.4548 | 50.0327
|  |  | 44733.4548 | 50.0327
|  |  | 44733.4548 | 50.0327
|  |  | 44733.4548 | 50.0326
|  |  | 44733.4548 | 50.0327
|  |  | 44733.4548 | 50.0327
|  |  | 44733.4548 | 50.0327
|  |  | 44733.4548 | 50.0327
|  |  | 44733.4548 | 50.0327
|  |  | 44733.4548 | 50.0326
|  |  | 44733.4548 | 50.0326
|  |  | 44733.4548 | 50.0327
|  |  | 44733.4548 | 50.0327
|  |  | 44733.4548 | 50.0327
|  |  | 44733.4548 | 50.0327
|  |  | 44733.4548 | 50.0328
|  |  | 44733.4548 | 50.0328
|  |  | 44733.4548 | 50.0328
|  |  | 44733.4548 | 50.0328
|  |  | 44733.4548 | 50.0327
|  |  | 44733.4548 | 50.0327
|  |  | 44733.4548 | 50.0327
|  |  | 44733.4548 | 50.0328
|  |  | 44733.4548 | 50.0327
|  |  | 2022-06-21 10:55 | 50.0327
|  |  | 44733.4548 | 50.0327
|  |  | 44733.4548 | 50.0327
|  |  | 44733.4548 | 50.0327
|  |  | 44733.4548 | 50.0328
|  |  | 44733.4548 | 50.0328
|  |  | 44733.4548 | 50.0329
|  |  | 44733.4548 | 50.0329
|  |  | 44733.4548 | 50.0328
|  |  | 44733.4548 | 50.0328
|  |  | 44733.4548 | 50.0328
|  |  | 44733.4548 | 50.0328
|  |  | 44733.4548 | 50.0328
|  |  | 44733.4548 | 50.0328
|  |  | 44733.4548 | 50.0328
|  |  | 44733.4548 | 50.0328
|  |  | 44733.4548 | 50.0328
|  |  | 44733.4548 | 50.0328
|  |  | 44733.4548 | 50.0328
|  |  | 44733.4548 | 50.0328
|  |  | 44733.4548 | 50.0328
|  |  | 44733.4548 | 50.0328
|  |  | 44733.4548 | 50.0329
|  |  | 44733.4548 | 50.0329
|  |  | 44733.4548 | 50.0328
|  |  | 44733.4548 | 50.0327
|  |  | 44733.4548 | 50.0327
|  |  | 44733.4548 | 50.0327
|  |  | 44733.4548 | 50.0327
|  |  | 44733.4548 | 50.0326
|  |  | 44733.4548 | 50.0326
|  |  | 44733.4548 | 50.0326
|  |  | 44733.4548 | 50.0327
|  |  | 44733.4548 | 50.0328
|  |  | 44733.4548 | 50.0329
|  |  | 44733.4548 | 50.033
|  |  | 44733.4548 | 50.033
|  |  | 44733.4548 | 50.033
|  |  | 44733.4548 | 50.033
|  |  | 44733.4548 | 50.033
|  |  | 44733.4548 | 50.0329
|  |  | 44733.4548 | 50.0329
|  |  | 44733.4548 | 50.0328
|  |  | 44733.4548 | 50.0328
|  |  | 44733.4548 | 50.0327
|  |  | 44733.4548 | 50.0327
|  |  | 44733.4548 | 50.0328
|  |  | 44733.4548 | 50.0328
|  |  | 44733.4548 | 50.0329
|  |  | 44733.4548 | 50.033
|  |  | 2022-06-21 10:55 | 50.033
|  |  | 44733.4548 | 50.0331
|  |  | 44733.4548 | 50.0332
|  |  | 44733.4548 | 50.0332
|  |  | 44733.4548 | 50.0332
|  |  | 44733.4548 | 50.0332
|  |  | 44733.4548 | 50.0331
|  |  | 44733.4548 | 50.033
|  |  | 44733.4548 | 50.0331
|  |  | 44733.4548 | 50.0331
|  |  | 44733.4548 | 50.0331
|  |  | 44733.4548 | 50.0331
|  |  | 44733.4548 | 50.0332
|  |  | 44733.4548 | 50.0332
|  |  | 44733.4548 | 50.0331
|  |  | 44733.4548 | 50.0332
|  |  | 44733.4548 | 50.0331
|  |  | 44733.4548 | 50.033
|  |  | 44733.4548 | 50.033
|  |  | 44733.4548 | 50.033
|  |  | 44733.4548 | 50.033
|  |  | 44733.4548 | 50.0331
|  |  | 44733.4548 | 50.0331
|  |  | 44733.4548 | 50.0333
|  |  | 44733.4548 | 50.0333
|  |  | 44733.4548 | 50.0334
|  |  | 44733.4548 | 50.0333
|  |  | 44733.4548 | 50.0332
|  |  | 44733.4548 | 50.0332
|  |  | 44733.4548 | 50.0332
|  |  | 44733.4548 | 50.0331
|  |  | 44733.4548 | 50.0331
|  |  | 44733.4548 | 50.0331
|  |  | 44733.4548 | 50.0331
|  |  | 44733.4548 | 50.0331
|  |  | 44733.4548 | 50.0331
|  |  | 44733.4548 | 50.0331
|  |  | 44733.4548 | 50.033
|  |  | 44733.4548 | 50.0331
|  |  | 44733.4548 | 50.0331
|  |  | 44733.4548 | 50.033
|  |  | 44733.4548 | 50.033
|  |  | 44733.4548 | 50.0329
|  |  | 44733.4548 | 50.0329
|  |  | 44733.4548 | 50.0328
|  |  | 44733.4548 | 50.0328
|  |  | 44733.4548 | 50.0328
|  |  | 44733.4548 | 50.0328
|  |  | 44733.4548 | 50.0329
|  |  | 44733.4548 | 50.0328
|  |  | 2022-06-21 10:55 | 50.0328
|  |  | 44733.4548 | 50.0329
|  |  | 44733.4548 | 50.033
|  |  | 44733.4548 | 50.0331
|  |  | 44733.4548 | 50.0331
|  |  | 44733.4548 | 50.0332
|  |  | 44733.4548 | 50.0332
|  |  | 44733.4548 | 50.0332
|  |  | 44733.4548 | 50.0331
|  |  | 44733.4548 | 50.0331
|  |  | 44733.4548 | 50.033
|  |  | 44733.4548 | 50.0329
|  |  | 44733.4548 | 50.0328
|  |  | 44733.4548 | 50.0327
|  |  | 44733.4548 | 50.0327
|  |  | 44733.4548 | 50.0326
|  |  | 44733.4548 | 50.0326
|  |  | 44733.4548 | 50.0327
|  |  | 44733.4548 | 50.0327
|  |  | 44733.4548 | 50.0328
|  |  | 44733.4548 | 50.0329
|  |  | 44733.4548 | 50.0329
|  |  | 44733.4548 | 50.033
|  |  | 44733.4548 | 50.0331
|  |  | 44733.4548 | 50.0331
|  |  | 44733.4548 | 50.0331
|  |  | 44733.4548 | 50.0332
|  |  | 44733.4548 | 50.0331
|  |  | 44733.4548 | 50.0331
|  |  | 44733.4548 | 50.0331
|  |  | 44733.4548 | 50.033
|  |  | 44733.4548 | 50.033
|  |  | 44733.4548 | 50.0329
|  |  | 44733.4548 | 50.0328
|  |  | 44733.4548 | 50.0328
|  |  | 44733.4548 | 50.0328
|  |  | 44733.4548 | 50.0328
|  |  | 44733.4548 | 50.0328
|  |  | 44733.4548 | 50.0328
|  |  | 44733.4548 | 50.0329
|  |  | 44733.4548 | 50.0329
|  |  | 44733.4548 | 50.0329
|  |  | 44733.4548 | 50.0329
|  |  | 44733.4548 | 50.0329
|  |  | 44733.4548 | 50.0329
|  |  | 44733.4548 | 50.0329
|  |  | 44733.4548 | 50.0329
|  |  | 44733.4548 | 50.0329
|  |  | 44733.4548 | 50.033
|  |  | 44733.4548 | 50.033
|  |  | 2022-06-21 10:55 | 50.0331
|  |  | 44733.4548 | 50.0331
|  |  | 44733.4548 | 50.0331
|  |  | 44733.4548 | 50.0331
|  |  | 44733.4548 | 50.033
|  |  | 44733.4548 | 50.0329
|  |  | 44733.4548 | 50.0328
|  |  | 44733.4548 | 50.0327
|  |  | 44733.4548 | 50.0327
|  |  | 44733.4548 | 50.0326
|  |  | 44733.4548 | 50.0326
|  |  | 44733.4548 | 50.0325
|  |  | 44733.4548 | 50.0325
|  |  | 44733.4548 | 50.0326
|  |  | 44733.4548 | 50.0326
|  |  | 44733.4548 | 50.0327
|  |  | 44733.4548 | 50.0328
|  |  | 44733.4548 | 50.0328
|  |  | 44733.4548 | 50.0329
|  |  | 44733.4548 | 50.0329
|  |  | 44733.4548 | 50.0329
|  |  | 44733.4548 | 50.0329
|  |  | 44733.4548 | 50.0328
|  |  | 44733.4548 | 50.0327
|  |  | 44733.4548 | 50.0327
|  |  | 44733.4548 | 50.0326
|  |  | 44733.4548 | 50.0326
|  |  | 44733.4548 | 50.0325
|  |  | 44733.4548 | 50.0326
|  |  | 44733.4548 | 50.0326
|  |  | 44733.4548 | 50.0326
|  |  | 44733.4548 | 50.0327
|  |  | 44733.4548 | 50.0327
|  |  | 44733.4548 | 50.0328
|  |  | 44733.4548 | 50.0328
|  |  | 44733.4548 | 50.0328
|  |  | 44733.4548 | 50.0329
|  |  | 44733.4548 | 50.0329
|  |  | 44733.4548 | 50.0329
|  |  | 44733.4548 | 50.0328
|  |  | 44733.4548 | 50.0328
|  |  | 44733.4548 | 50.0328
|  |  | 44733.4548 | 50.0329
|  |  | 44733.4548 | 50.0329
|  |  | 44733.4548 | 50.0329
|  |  | 44733.4548 | 50.0329
|  |  | 44733.4548 | 50.0328
|  |  | 44733.4548 | 50.0329
|  |  | 44733.4548 | 50.0329
|  |  | 44733.4548 | 50.0329
|  |  | 2022-06-21 10:55 | 50.0328
|  |  | 44733.4548 | 50.0329
|  |  | 44733.4548 | 50.0329
|  |  | 44733.4548 | 50.0329
|  |  | 44733.4548 | 50.0329
|  |  | 44733.4548 | 50.0328
|  |  | 44733.4548 | 50.0328
|  |  | 44733.4548 | 50.0328
|  |  | 44733.4548 | 50.0328
|  |  | 44733.4548 | 50.0328
|  |  | 44733.4548 | 50.0327
|  |  | 44733.4548 | 50.0327
|  |  | 44733.4548 | 50.0327
|  |  | 44733.4548 | 50.0326
|  |  | 44733.4548 | 50.0326
|  |  | 44733.4548 | 50.0326
|  |  | 44733.4548 | 50.0327
|  |  | 44733.4548 | 50.0327
|  |  | 44733.4548 | 50.0328
|  |  | 44733.4548 | 50.0328
|  |  | 44733.4548 | 50.0329
|  |  | 44733.4548 | 50.0329
|  |  | 44733.4548 | 50.0329
|  |  | 44733.4548 | 50.0329
|  |  | 44733.4548 | 50.0329
|  |  | 44733.4548 | 50.0328
|  |  | 44733.4548 | 50.0328
|  |  | 44733.4548 | 50.0327
|  |  | 44733.4548 | 50.0326
|  |  | 44733.4548 | 50.0326
|  |  | 44733.4548 | 50.0325
|  |  | 44733.4548 | 50.0324
|  |  | 44733.4548 | 50.0324
|  |  | 44733.4548 | 50.0324
|  |  | 44733.4548 | 50.0324
|  |  | 44733.4548 | 50.0324
|  |  | 44733.4548 | 50.0324
|  |  | 44733.4548 | 50.0324
|  |  | 44733.4548 | 50.0324
|  |  | 44733.4548 | 50.0323
|  |  | 44733.4548 | 50.0323
|  |  | 44733.4548 | 50.0323
|  |  | 44733.4548 | 50.0322
|  |  | 44733.4548 | 50.0321
|  |  | 44733.4548 | 50.032
|  |  | 44733.4548 | 50.0319
|  |  | 44733.4548 | 50.0319
|  |  | 44733.4548 | 50.0318
|  |  | 44733.4548 | 50.0318
|  |  | 44733.4548 | 50.0319
|  |  | 2022-06-21 10:55 | 50.0319
|  |  | 44733.4548 | 50.0319
|  |  | 44733.4549 | 50.0319
|  |  | 44733.4549 | 50.0319
|  |  | 44733.4549 | 50.0319
|  |  | 44733.4549 | 50.0319
|  |  | 44733.4549 | 50.0319
|  |  | 44733.4549 | 50.0318
|  |  | 44733.4549 | 50.0318
|  |  | 44733.4549 | 50.0317
|  |  | 44733.4549 | 50.0316
|  |  | 44733.4549 | 50.0315
|  |  | 44733.4549 | 50.0313
|  |  | 44733.4549 | 50.0313
|  |  | 44733.4549 | 50.0312
|  |  | 44733.4549 | 50.0312
|  |  | 44733.4549 | 50.0311
|  |  | 44733.4549 | 50.0311
|  |  | 44733.4549 | 50.0311
|  |  | 44733.4549 | 50.0311
|  |  | 44733.4549 | 50.0311
|  |  | 44733.4549 | 50.0311
|  |  | 44733.4549 | 50.0311
|  |  | 44733.4549 | 50.0312
|  |  | 44733.4549 | 50.0312
|  |  | 44733.4549 | 50.0312
|  |  | 44733.4549 | 50.0312
|  |  | 44733.4549 | 50.0313
|  |  | 44733.4549 | 50.0313
|  |  | 44733.4549 | 50.0312
|  |  | 44733.4549 | 50.0312
|  |  | 44733.4549 | 50.0311
|  |  | 44733.4549 | 50.0311
|  |  | 44733.4549 | 50.031
|  |  | 44733.4549 | 50.0309
|  |  | 44733.4549 | 50.0309
|  |  | 44733.4549 | 50.0308
|  |  | 44733.4549 | 50.0308
|  |  | 44733.4549 | 50.0308
|  |  | 44733.4549 | 50.0308
|  |  | 44733.4549 | 50.0307
|  |  | 44733.4549 | 50.0307
|  |  | 44733.4549 | 50.0307
|  |  | 44733.4549 | 50.0307
|  |  | 44733.4549 | 50.0307
|  |  | 44733.4549 | 50.0307
|  |  | 44733.4549 | 50.0307
|  |  | 44733.4549 | 50.0307
|  |  | 44733.4549 | 50.0306
|  |  | 44733.4549 | 50.0306
|  |  | 2022-06-21 10:55 | 50.0306
|  |  | 44733.4549 | 50.0305
|  |  | 44733.4549 | 50.0305
|  |  | 44733.4549 | 50.0304
|  |  | 44733.4549 | 50.0303
|  |  | 44733.4549 | 50.0301
|  |  | 44733.4549 | 50.03
|  |  | 44733.4549 | 50.0299
|  |  | 44733.4549 | 50.0298
|  |  | 44733.4549 | 50.0297
|  |  | 44733.4549 | 50.0296
|  |  | 44733.4549 | 50.0296
|  |  | 44733.4549 | 50.0296
|  |  | 44733.4549 | 50.0298
|  |  | 44733.4549 | 50.0299
|  |  | 44733.4549 | 50.0299
|  |  | 44733.4549 | 50.03
|  |  | 44733.4549 | 50.0299
|  |  | 44733.4549 | 50.03
|  |  | 44733.4549 | 50.03
|  |  | 44733.4549 | 50.0299
|  |  | 44733.4549 | 50.0298
|  |  | 44733.4549 | 50.0297
|  |  | 44733.4549 | 50.0296
|  |  | 44733.4549 | 50.0295
|  |  | 44733.4549 | 50.0294
|  |  | 44733.4549 | 50.0293
|  |  | 44733.4549 | 50.0292
|  |  | 44733.4549 | 50.0292
|  |  | 44733.4549 | 50.0292
|  |  | 44733.4549 | 50.0292
|  |  | 44733.4549 | 50.0292
|  |  | 44733.4549 | 50.0292
|  |  | 44733.4549 | 50.0292
|  |  | 44733.4549 | 50.0291
|  |  | 44733.4549 | 50.0291
|  |  | 44733.4549 | 50.029
|  |  | 44733.4549 | 50.029
|  |  | 44733.4549 | 50.0289
|  |  | 44733.4549 | 50.0288
|  |  | 44733.4549 | 50.0287
|  |  | 44733.4549 | 50.0286
|  |  | 44733.4549 | 50.0285
|  |  | 44733.4549 | 50.0285
|  |  | 44733.4549 | 50.0284
|  |  | 44733.4549 | 50.0284
|  |  | 44733.4549 | 50.0284
|  |  | 44733.4549 | 50.0284
|  |  | 44733.4549 | 50.0284
|  |  | 44733.4549 | 50.0284
|  |  | 2022-06-21 10:55 | 50.0284
|  |  | 44733.4549 | 50.0283
|  |  | 44733.4549 | 50.0283
|  |  | 44733.4549 | 50.0283
|  |  | 44733.4549 | 50.0282
|  |  | 44733.4549 | 50.0281
|  |  | 44733.4549 | 50.0281
|  |  | 44733.4549 | 50.028
|  |  | 44733.4549 | 50.028
|  |  | 44733.4549 | 50.028
|  |  | 44733.4549 | 50.0279
|  |  | 44733.4549 | 50.0279
|  |  | 44733.4549 | 50.0278
|  |  | 44733.4549 | 50.0278
|  |  | 44733.4549 | 50.0277
|  |  | 44733.4549 | 50.0277
|  |  | 44733.4549 | 50.0277
|  |  | 44733.4549 | 50.0278
|  |  | 44733.4549 | 50.0277
|  |  | 44733.4549 | 50.0278
|  |  | 44733.4549 | 50.0278
|  |  | 44733.4549 | 50.0278
|  |  | 44733.4549 | 50.0279
|  |  | 44733.4549 | 50.0278
|  |  | 44733.4549 | 50.0277
|  |  | 44733.4549 | 50.0277
|  |  | 44733.4549 | 50.0277
|  |  | 44733.4549 | 50.0277
|  |  | 44733.4549 | 50.0276
|  |  | 44733.4549 | 50.0275
|  |  | 44733.4549 | 50.0275
|  |  | 44733.4549 | 50.0275
|  |  | 44733.4549 | 50.0274
|  |  | 44733.4549 | 50.0274
|  |  | 44733.4549 | 50.0274
|  |  | 44733.4549 | 50.0274
|  |  | 44733.4549 | 50.0274
|  |  | 44733.4549 | 50.0274
|  |  | 44733.4549 | 50.0274
|  |  | 44733.4549 | 50.0273
|  |  | 44733.4549 | 50.0273
|  |  | 44733.4549 | 50.0273
|  |  | 44733.4549 | 50.0272
|  |  | 44733.4549 | 50.0272
|  |  | 44733.4549 | 50.0272
|  |  | 44733.4549 | 50.0272
|  |  | 44733.4549 | 50.0272
|  |  | 44733.4549 | 50.0271
|  |  | 44733.4549 | 50.0271
|  |  | 44733.4549 | 50.027
|  |  | 2022-06-21 10:55 | 50.027
|  |  | 44733.4549 | 50.0269
|  |  | 44733.4549 | 50.0269
|  |  | 44733.4549 | 50.0269
|  |  | 44733.4549 | 50.0268
|  |  | 44733.4549 | 50.0268
|  |  | 44733.4549 | 50.0268
|  |  | 44733.4549 | 50.0268
|  |  | 44733.4549 | 50.0268
|  |  | 44733.4549 | 50.0268
|  |  | 44733.4549 | 50.0268
|  |  | 44733.4549 | 50.0267
|  |  | 44733.4549 | 50.0267
|  |  | 44733.4549 | 50.0266
|  |  | 44733.4549 | 50.0265
|  |  | 44733.4549 | 50.0265
|  |  | 44733.4549 | 50.0264
|  |  | 44733.4549 | 50.0265
|  |  | 44733.4549 | 50.0265
|  |  | 44733.4549 | 50.0265
|  |  | 44733.4549 | 50.0266
|  |  | 44733.4549 | 50.0266
|  |  | 44733.4549 | 50.0266
|  |  | 44733.4549 | 50.0266
|  |  | 44733.4549 | 50.0266
|  |  | 44733.4549 | 50.0265
|  |  | 44733.4549 | 50.0264
|  |  | 44733.4549 | 50.0264
|  |  | 44733.4549 | 50.0263
|  |  | 44733.4549 | 50.0263
|  |  | 44733.4549 | 50.0263
|  |  | 44733.4549 | 50.0263
|  |  | 44733.4549 | 50.0263
|  |  | 44733.4549 | 50.0264
|  |  | 44733.4549 | 50.0263
|  |  | 44733.4549 | 50.0263
|  |  | 44733.4549 | 50.0263
|  |  | 44733.4549 | 50.0263
|  |  | 44733.4549 | 50.0262
|  |  | 44733.4549 | 50.0262
|  |  | 44733.4549 | 50.0261
|  |  | 44733.4549 | 50.026
|  |  | 44733.4549 | 50.0259
|  |  | 44733.4549 | 50.0258
|  |  | 44733.4549 | 50.0258
|  |  | 44733.4549 | 50.0257
|  |  | 44733.4549 | 50.0257
|  |  | 44733.4549 | 50.0259
|  |  | 44733.4549 | 50.026
|  |  | 44733.4549 | 50.0261
|  |  | 2022-06-21 10:55 | 50.0261
|  |  | 44733.4549 | 50.0262
|  |  | 44733.4549 | 50.0261
|  |  | 44733.4549 | 50.0261
|  |  | 44733.4549 | 50.0261
|  |  | 44733.4549 | 50.026
|  |  | 44733.4549 | 50.0259
|  |  | 44733.4549 | 50.0259
|  |  | 44733.4549 | 50.0258
|  |  | 44733.4549 | 50.0258
|  |  | 44733.4549 | 50.0258
|  |  | 44733.4549 | 50.0258
|  |  | 44733.4549 | 50.0259
|  |  | 44733.4549 | 50.0259
|  |  | 44733.4549 | 50.0258
|  |  | 44733.4549 | 50.0258
|  |  | 44733.4549 | 50.0257
|  |  | 44733.4549 | 50.0257
|  |  | 44733.4549 | 50.0257
|  |  | 44733.4549 | 50.0257
|  |  | 44733.4549 | 50.0256
|  |  | 44733.4549 | 50.0256
|  |  | 44733.4549 | 50.0256
|  |  | 44733.4549 | 50.0256
|  |  | 44733.4549 | 50.0257
|  |  | 44733.4549 | 50.0256
|  |  | 44733.4549 | 50.0256
|  |  | 44733.4549 | 50.0256
|  |  | 44733.4549 | 50.0256
|  |  | 44733.4549 | 50.0255
|  |  | 44733.4549 | 50.0254
|  |  | 44733.4549 | 50.0254
|  |  | 44733.4549 | 50.0254
|  |  | 44733.4549 | 50.0254
|  |  | 44733.4549 | 50.0254
|  |  | 44733.4549 | 50.0254
|  |  | 44733.4549 | 50.0254
|  |  | 44733.4549 | 50.0254
|  |  | 44733.4549 | 50.0254
|  |  | 44733.4549 | 50.0254
|  |  | 44733.4549 | 50.0253
|  |  | 44733.4549 | 50.0253
|  |  | 44733.4549 | 50.0253
|  |  | 44733.4549 | 50.0253
|  |  | 44733.4549 | 50.0252
|  |  | 44733.4549 | 50.0252
|  |  | 44733.4549 | 50.0251
|  |  | 44733.4549 | 50.0251
|  |  | 44733.4549 | 50.0251
|  |  | 44733.4549 | 50.0251
|  |  | 2022-06-21 10:55 | 50.0251
|  |  | 44733.4549 | 50.025
|  |  | 44733.4549 | 50.025
|  |  | 44733.4549 | 50.0251
|  |  | 44733.4549 | 50.025
|  |  | 44733.4549 | 50.025
|  |  | 44733.4549 | 50.025
|  |  | 44733.4549 | 50.025
|  |  | 44733.4549 | 50.0249
|  |  | 44733.4549 | 50.0249
|  |  | 44733.4549 | 50.0249
|  |  | 44733.4549 | 50.0249
|  |  | 44733.4549 | 50.0249
|  |  | 44733.4549 | 50.0249
|  |  | 44733.4549 | 50.0249
|  |  | 44733.4549 | 50.025
|  |  | 44733.4549 | 50.0249
|  |  | 44733.4549 | 50.0249
|  |  | 44733.4549 | 50.0248
|  |  | 44733.4549 | 50.0247
|  |  | 44733.4549 | 50.0247
|  |  | 44733.4549 | 50.0246
|  |  | 44733.4549 | 50.0246
|  |  | 44733.4549 | 50.0246
|  |  | 44733.4549 | 50.0246
|  |  | 44733.4549 | 50.0247
|  |  | 44733.4549 | 50.0247
|  |  | 44733.4549 | 50.0247
|  |  | 44733.4549 | 50.0247
|  |  | 44733.4549 | 50.0247
|  |  | 44733.4549 | 50.0247
|  |  | 44733.4549 | 50.0246
|  |  | 44733.4549 | 50.0246
|  |  | 44733.4549 | 50.0245
|  |  | 44733.4549 | 50.0244
|  |  | 44733.4549 | 50.0244
|  |  | 44733.4549 | 50.0243
|  |  | 44733.4549 | 50.0243
|  |  | 44733.4549 | 50.0243
|  |  | 44733.4549 | 50.0243
|  |  | 44733.4549 | 50.0243
|  |  | 44733.4549 | 50.0243
|  |  | 44733.4549 | 50.0243
|  |  | 44733.4549 | 50.0243
|  |  | 44733.4549 | 50.0243
|  |  | 44733.4549 | 50.0243
|  |  | 44733.4549 | 50.0242
|  |  | 44733.4549 | 50.0242
|  |  | 44733.4549 | 50.0242
|  |  | 44733.4549 | 50.0241
|  |  | 2022-06-21 10:55 | 50.0242
|  |  | 44733.4549 | 50.0242
|  |  | 44733.4549 | 50.0242
|  |  | 44733.4549 | 50.0242
|  |  | 44733.4549 | 50.0242
|  |  | 44733.4549 | 50.0242
|  |  | 44733.4549 | 50.0242
|  |  | 44733.4549 | 50.0242
|  |  | 44733.4549 | 50.0242
|  |  | 44733.4549 | 50.0241
|  |  | 44733.4549 | 50.0241
|  |  | 44733.4549 | 50.0241
|  |  | 44733.4549 | 50.0241
|  |  | 44733.4549 | 50.024
|  |  | 44733.4549 | 50.024
|  |  | 44733.4549 | 50.024
|  |  | 44733.4549 | 50.024
|  |  | 44733.4549 | 50.024
|  |  | 44733.4549 | 50.0239
|  |  | 44733.4549 | 50.0239
|  |  | 44733.4549 | 50.0239
|  |  | 44733.4549 | 50.0239
|  |  | 44733.4549 | 50.0239
|  |  | 44733.4549 | 50.024
|  |  | 44733.4549 | 50.024
|  |  | 44733.4549 | 50.024
|  |  | 44733.4549 | 50.0241
|  |  | 44733.4549 | 50.024
|  |  | 44733.4549 | 50.024
|  |  | 44733.4549 | 50.024
|  |  | 44733.4549 | 50.024
|  |  | 44733.4549 | 50.024
|  |  | 44733.4549 | 50.024
|  |  | 44733.4549 | 50.024
|  |  | 44733.4549 | 50.024
|  |  | 44733.4549 | 50.0239
|  |  | 44733.4549 | 50.0239
|  |  | 44733.4549 | 50.0239
|  |  | 44733.4549 | 50.0238
|  |  | 44733.4549 | 50.0237
|  |  | 44733.4549 | 50.0237
|  |  | 44733.4549 | 50.0237
|  |  | 44733.4549 | 50.0236
|  |  | 44733.4549 | 50.0236
|  |  | 44733.4549 | 50.0235
|  |  | 44733.4549 | 50.0235
|  |  | 44733.4549 | 50.0236
|  |  | 44733.4549 | 50.0236
|  |  | 44733.4549 | 50.0236
|  |  | 44733.4549 | 50.0236
|  |  | 2022-06-21 10:55 | 50.0238
|  |  | 44733.4549 | 50.0238
|  |  | 44733.4549 | 50.0238
|  |  | 44733.4549 | 50.0238
|  |  | 44733.4549 | 50.0238
|  |  | 44733.4549 | 50.0239
|  |  | 44733.4549 | 50.0238
|  |  | 44733.4549 | 50.0238
|  |  | 44733.4549 | 50.0238
|  |  | 44733.4549 | 50.0238
|  |  | 44733.4549 | 50.0238
|  |  | 44733.4549 | 50.0237
|  |  | 44733.4549 | 50.0237
|  |  | 44733.4549 | 50.0236
|  |  | 44733.4549 | 50.0236
|  |  | 44733.4549 | 50.0236
|  |  | 44733.4549 | 50.0236
|  |  | 44733.4549 | 50.0236
|  |  | 44733.4549 | 50.0236
|  |  | 44733.4549 | 50.0236
|  |  | 44733.4549 | 50.0237
|  |  | 44733.4549 | 50.0237
|  |  | 44733.4549 | 50.0238
|  |  | 44733.4549 | 50.0238
|  |  | 44733.4549 | 50.0239
|  |  | 44733.4549 | 50.0239
|  |  | 44733.4549 | 50.0239
|  |  | 44733.4549 | 50.0239
|  |  | 44733.4549 | 50.0239
|  |  | 44733.4549 | 50.024
|  |  | 44733.4549 | 50.024
|  |  | 44733.4549 | 50.024
|  |  | 44733.4549 | 50.024
|  |  | 44733.4549 | 50.0239
|  |  | 44733.4549 | 50.0239
|  |  | 44733.4549 | 50.0239
|  |  | 44733.4549 | 50.0239
|  |  | 44733.4549 | 50.0239
|  |  | 44733.4549 | 50.0239
|  |  | 44733.4549 | 50.0239
|  |  | 44733.4549 | 50.0239
|  |  | 44733.4549 | 50.0239
|  |  | 44733.4549 | 50.0239
|  |  | 44733.4549 | 50.0239
|  |  | 44733.4549 | 50.0239
|  |  | 44733.4549 | 50.0239
|  |  | 44733.4549 | 50.0239
|  |  | 44733.4549 | 50.0239
|  |  | 44733.4549 | 50.0239
|  |  | 44733.4549 | 50.024
|  |  | 2022-06-21 10:55 | 50.024
|  |  | 44733.4549 | 50.024
|  |  | 44733.4549 | 50.024
|  |  | 44733.4549 | 50.024
|  |  | 44733.4549 | 50.024
|  |  | 44733.4549 | 50.0241
|  |  | 44733.4549 | 50.0241
|  |  | 44733.4549 | 50.0241
|  |  | 44733.4549 | 50.0241
|  |  | 44733.4549 | 50.0241
|  |  | 44733.4549 | 50.024
|  |  | 44733.4549 | 50.024
|  |  | 44733.4549 | 50.024
|  |  | 44733.4549 | 50.024
|  |  | 44733.4549 | 50.0241
|  |  | 44733.4549 | 50.0241
|  |  | 44733.4549 | 50.0241
|  |  | 44733.4549 | 50.0242
|  |  | 44733.4549 | 50.0242
|  |  | 44733.4549 | 50.0243
|  |  | 44733.4549 | 50.0243
|  |  | 44733.4549 | 50.0244
|  |  | 44733.4549 | 50.0244
|  |  | 44733.4549 | 50.0244
|  |  | 44733.4549 | 50.0244
|  |  | 44733.4549 | 50.0244
|  |  | 44733.4549 | 50.0244
|  |  | 44733.4549 | 50.0244
|  |  | 44733.4549 | 50.0244
|  |  | 44733.4549 | 50.0243
|  |  | 44733.4549 | 50.0243
|  |  | 44733.4549 | 50.0242
|  |  | 44733.4549 | 50.0242
|  |  | 44733.4549 | 50.0242
|  |  | 44733.4549 | 50.0242
|  |  | 44733.455 | 50.0242
|  |  | 44733.455 | 50.0243
|  |  | 44733.455 | 50.0244
|  |  | 44733.455 | 50.0245
|  |  | 44733.455 | 50.0246
|  |  | 44733.455 | 50.0247
|  |  | 44733.455 | 50.0247
|  |  | 44733.455 | 50.0248
|  |  | 44733.455 | 50.0247
|  |  | 44733.455 | 50.0247
|  |  | 44733.455 | 50.0246
|  |  | 44733.455 | 50.0246
|  |  | 44733.455 | 50.0246
|  |  | 44733.455 | 50.0246
|  |  | 44733.455 | 50.0246
|  |  | 2022-06-21 10:55 | 50.0246
|  |  | 44733.455 | 50.0246
|  |  | 44733.455 | 50.0247
|  |  | 44733.455 | 50.0247
|  |  | 44733.455 | 50.0246
|  |  | 44733.455 | 50.0246
|  |  | 44733.455 | 50.0246
|  |  | 44733.455 | 50.0246
|  |  | 44733.455 | 50.0245
|  |  | 44733.455 | 50.0245
|  |  | 44733.455 | 50.0245
|  |  | 44733.455 | 50.0246
|  |  | 44733.455 | 50.0246
|  |  | 44733.455 | 50.0247
|  |  | 44733.455 | 50.0248
|  |  | 44733.455 | 50.0249
|  |  | 44733.455 | 50.025
|  |  | 44733.455 | 50.0251
|  |  | 44733.455 | 50.0252
|  |  | 44733.455 | 50.0253
|  |  | 44733.455 | 50.0253
|  |  | 44733.455 | 50.0253
|  |  | 44733.455 | 50.0252
|  |  | 44733.455 | 50.0252
|  |  | 44733.455 | 50.0252
|  |  | 44733.455 | 50.0252
|  |  | 44733.455 | 50.0252
|  |  | 44733.455 | 50.0252
|  |  | 44733.455 | 50.0252
|  |  | 44733.455 | 50.0252
|  |  | 44733.455 | 50.0252
|  |  | 44733.455 | 50.0253
|  |  | 44733.455 | 50.0253
|  |  | 44733.455 | 50.0254
|  |  | 44733.455 | 50.0254
|  |  | 44733.455 | 50.0254
|  |  | 44733.455 | 50.0255
|  |  | 44733.455 | 50.0256
|  |  | 44733.455 | 50.0257
|  |  | 44733.455 | 50.0257
|  |  | 44733.455 | 50.0258
|  |  | 44733.455 | 50.0259
|  |  | 44733.455 | 50.026
|  |  | 44733.455 | 50.0261
|  |  | 44733.455 | 50.0262
|  |  | 44733.455 | 50.0262
|  |  | 44733.455 | 50.0262
|  |  | 44733.455 | 50.0262
|  |  | 44733.455 | 50.0262
|  |  | 44733.455 | 50.0261
|  |  | 2022-06-21 10:55 | 50.0262
|  |  | 44733.455 | 50.0262
|  |  | 44733.455 | 50.0262
|  |  | 44733.455 | 50.0263
|  |  | 44733.455 | 50.0263
|  |  | 44733.455 | 50.0264
|  |  | 44733.455 | 50.0264
|  |  | 44733.455 | 50.0265
|  |  | 44733.455 | 50.0267
|  |  | 44733.455 | 50.0268
|  |  | 44733.455 | 50.0269
|  |  | 44733.455 | 50.027
|  |  | 44733.455 | 50.027
|  |  | 44733.455 | 50.0271
|  |  | 44733.455 | 50.0271
|  |  | 44733.455 | 50.0271
|  |  | 44733.455 | 50.0271
|  |  | 44733.455 | 50.0271
|  |  | 44733.455 | 50.0272
|  |  | 44733.455 | 50.0272
|  |  | 44733.455 | 50.0272
|  |  | 44733.455 | 50.0272
|  |  | 44733.455 | 50.0272
|  |  | 44733.455 | 50.0272
|  |  | 44733.455 | 50.0273
|  |  | 44733.455 | 50.0273
|  |  | 44733.455 | 50.0274
|  |  | 44733.455 | 50.0276
|  |  | 44733.455 | 50.0277
|  |  | 44733.455 | 50.0278
|  |  | 44733.455 | 50.0279
|  |  | 44733.455 | 50.0279
|  |  | 44733.455 | 50.028
|  |  | 44733.455 | 50.0279
|  |  | 44733.455 | 50.0279
|  |  | 44733.455 | 50.0278
|  |  | 44733.455 | 50.0278
|  |  | 44733.455 | 50.0277
|  |  | 44733.455 | 50.0277
|  |  | 44733.455 | 50.0277
|  |  | 44733.455 | 50.0278
|  |  | 44733.455 | 50.0278
|  |  | 44733.455 | 50.0279
|  |  | 44733.455 | 50.028
|  |  | 44733.455 | 50.0281
|  |  | 44733.455 | 50.028
|  |  | 44733.455 | 50.028
|  |  | 44733.455 | 50.0279
|  |  | 44733.455 | 50.0278
|  |  | 44733.455 | 50.0277
|  |  | 2022-06-21 10:55 | 50.0276
|  |  | 44733.455 | 50.0276
|  |  | 44733.455 | 50.0276
|  |  | 44733.455 | 50.0277
|  |  | 44733.455 | 50.0278
|  |  | 44733.455 | 50.0279
|  |  | 44733.455 | 50.028
|  |  | 44733.455 | 50.0281
|  |  | 44733.455 | 50.0282
|  |  | 44733.455 | 50.0282
|  |  | 44733.455 | 50.0282
|  |  | 44733.455 | 50.0282
|  |  | 44733.455 | 50.0281
|  |  | 44733.455 | 50.028
|  |  | 44733.455 | 50.028
|  |  | 44733.455 | 50.0279
|  |  | 44733.455 | 50.0279
|  |  | 44733.455 | 50.028
|  |  | 44733.455 | 50.0281
|  |  | 44733.455 | 50.0282
|  |  | 44733.455 | 50.0283
|  |  | 44733.455 | 50.0284
|  |  | 44733.455 | 50.0285
|  |  | 44733.455 | 50.0286
|  |  | 44733.455 | 50.0286
|  |  | 44733.455 | 50.0287
|  |  | 44733.455 | 50.0287
|  |  | 44733.455 | 50.0287
|  |  | 44733.455 | 50.0287
|  |  | 44733.455 | 50.0286
|  |  | 44733.455 | 50.0286
|  |  | 44733.455 | 50.0286
|  |  | 44733.455 | 50.0286
|  |  | 44733.455 | 50.0287
|  |  | 44733.455 | 50.0287
|  |  | 44733.455 | 50.0287
|  |  | 44733.455 | 50.0288
|  |  | 44733.455 | 50.0288
|  |  | 44733.455 | 50.0289
|  |  | 44733.455 | 50.0289
|  |  | 44733.455 | 50.0289
|  |  | 44733.455 | 50.0289
|  |  | 44733.455 | 50.029
|  |  | 44733.455 | 50.029
|  |  | 44733.455 | 50.029
|  |  | 44733.455 | 50.029
|  |  | 44733.455 | 50.029
|  |  | 44733.455 | 50.0291
|  |  | 44733.455 | 50.0291
|  |  | 44733.455 | 50.0292
|  |  | 2022-06-21 10:55 | 50.0293
|  |  | 44733.455 | 50.0293
|  |  | 44733.455 | 50.0294
|  |  | 44733.455 | 50.0295
|  |  | 44733.455 | 50.0295
|  |  | 44733.455 | 50.0295
|  |  | 44733.455 | 50.0295
|  |  | 44733.455 | 50.0295
|  |  | 44733.455 | 50.0295
|  |  | 44733.455 | 50.0295
|  |  | 44733.455 | 50.0295
|  |  | 44733.455 | 50.0295
|  |  | 44733.455 | 50.0296
|  |  | 44733.455 | 50.0297
|  |  | 44733.455 | 50.0298
|  |  | 44733.455 | 50.0299
|  |  | 44733.455 | 50.03
|  |  | 44733.455 | 50.03
|  |  | 44733.455 | 50.03
|  |  | 44733.455 | 50.03
|  |  | 44733.455 | 50.0299
|  |  | 44733.455 | 50.0299
|  |  | 44733.455 | 50.0298
|  |  | 44733.455 | 50.0297
|  |  | 44733.455 | 50.0297
|  |  | 44733.455 | 50.0296
|  |  | 44733.455 | 50.0297
|  |  | 44733.455 | 50.0297
|  |  | 44733.455 | 50.0297
|  |  | 44733.455 | 50.0297
|  |  | 44733.455 | 50.0296
|  |  | 44733.455 | 50.0296
|  |  | 44733.455 | 50.0295
|  |  | 44733.455 | 50.0295
|  |  | 44733.455 | 50.0295
|  |  | 44733.455 | 50.0295
|  |  | 44733.455 | 50.0294
|  |  | 44733.455 | 50.0294
|  |  | 44733.455 | 50.0294
|  |  | 44733.455 | 50.0294
|  |  | 44733.455 | 50.0294
|  |  | 44733.455 | 50.0294
|  |  | 44733.455 | 50.0295
|  |  | 44733.455 | 50.0295
|  |  | 44733.455 | 50.0296
|  |  | 44733.455 | 50.0297
|  |  | 44733.455 | 50.0297
|  |  | 44733.455 | 50.0297
|  |  | 44733.455 | 50.0297
|  |  | 44733.455 | 50.0297
|  |  | 2022-06-21 10:55 | 50.0297
|  |  | 44733.455 | 50.0297
|  |  | 44733.455 | 50.0297
|  |  | 44733.455 | 50.0296
|  |  | 44733.455 | 50.0295
|  |  | 44733.455 | 50.0295
|  |  | 44733.455 | 50.0295
|  |  | 44733.455 | 50.0295
|  |  | 44733.455 | 50.0295
|  |  | 44733.455 | 50.0296
|  |  | 44733.455 | 50.0295
|  |  | 44733.455 | 50.0296
|  |  | 44733.455 | 50.0296
|  |  | 44733.455 | 50.0297
|  |  | 44733.455 | 50.0297
|  |  | 44733.455 | 50.0298
|  |  | 44733.455 | 50.0298
|  |  | 44733.455 | 50.0297
|  |  | 44733.455 | 50.0298
|  |  | 44733.455 | 50.0297
|  |  | 44733.455 | 50.0297
|  |  | 44733.455 | 50.0296
|  |  | 44733.455 | 50.0296
|  |  | 44733.455 | 50.0296
|  |  | 44733.455 | 50.0296
|  |  | 44733.455 | 50.0296
|  |  | 44733.455 | 50.0295
|  |  | 44733.455 | 50.0295
|  |  | 44733.455 | 50.0295
|  |  | 44733.455 | 50.0296
|  |  | 44733.455 | 50.0297
|  |  | 44733.455 | 50.0297
|  |  | 44733.455 | 50.0297
|  |  | 44733.455 | 50.0298
|  |  | 44733.455 | 50.0298
|  |  | 44733.455 | 50.0299
|  |  | 44733.455 | 50.0299
|  |  | 44733.455 | 50.03
|  |  | 44733.455 | 50.0299
|  |  | 44733.455 | 50.0299
|  |  | 44733.455 | 50.0299
|  |  | 44733.455 | 50.0298
|  |  | 44733.455 | 50.0298
|  |  | 44733.455 | 50.0297
|  |  | 44733.455 | 50.0297
|  |  | 44733.455 | 50.0297
|  |  | 44733.455 | 50.0296
|  |  | 44733.455 | 50.0296
|  |  | 44733.455 | 50.0297
|  |  | 44733.455 | 50.0297
|  |  | 2022-06-21 10:55 | 50.0297
|  |  | 44733.455 | 50.0298
|  |  | 44733.455 | 50.0298
|  |  | 44733.455 | 50.0299
|  |  | 44733.455 | 50.0299
|  |  | 44733.455 | 50.03
|  |  | 44733.455 | 50.03
|  |  | 44733.455 | 50.03
|  |  | 44733.455 | 50.0299
|  |  | 44733.455 | 50.0299
|  |  | 44733.455 | 50.0298
|  |  | 44733.455 | 50.0297
|  |  | 44733.455 | 50.0297
|  |  | 44733.455 | 50.0296
|  |  | 44733.455 | 50.0296
|  |  | 44733.455 | 50.0295
|  |  | 44733.455 | 50.0295
|  |  | 44733.455 | 50.0295
|  |  | 44733.455 | 50.0295
|  |  | 44733.455 | 50.0295
|  |  | 44733.455 | 50.0296
|  |  | 44733.455 | 50.0296
|  |  | 44733.455 | 50.0296
|  |  | 44733.455 | 50.0296
|  |  | 44733.455 | 50.0296
|  |  | 44733.455 | 50.0296
|  |  | 44733.455 | 50.0296
|  |  | 44733.455 | 50.0296
|  |  | 44733.455 | 50.0296
|  |  | 44733.455 | 50.0296
|  |  | 44733.455 | 50.0296
|  |  | 44733.455 | 50.0296
|  |  | 44733.455 | 50.0296
|  |  | 44733.455 | 50.0295
|  |  | 44733.455 | 50.0296
|  |  | 44733.455 | 50.0296
|  |  | 44733.455 | 50.0296
|  |  | 44733.455 | 50.0296
|  |  | 44733.455 | 50.0296
|  |  | 44733.455 | 50.0296
|  |  | 44733.455 | 50.0296
|  |  | 44733.455 | 50.0295
|  |  | 44733.455 | 50.0294
|  |  | 44733.455 | 50.0294
|  |  | 44733.455 | 50.0294
|  |  | 44733.455 | 50.0294
|  |  | 44733.455 | 50.0294
|  |  | 44733.455 | 50.0295
|  |  | 44733.455 | 50.0295
|  |  | 44733.455 | 50.0295
|  |  | 2022-06-21 10:55 | 50.0295
|  |  | 44733.455 | 50.0296
|  |  | 44733.455 | 50.0296
|  |  | 44733.455 | 50.0296
|  |  | 44733.455 | 50.0297
|  |  | 44733.455 | 50.0297
|  |  | 44733.455 | 50.0298
|  |  | 44733.455 | 50.0298
|  |  | 44733.455 | 50.0298
|  |  | 44733.455 | 50.0299
|  |  | 44733.455 | 50.0298
|  |  | 44733.455 | 50.0297
|  |  | 44733.455 | 50.0297
|  |  | 44733.455 | 50.0297
|  |  | 44733.455 | 50.0296
|  |  | 44733.455 | 50.0296
|  |  | 44733.455 | 50.0296
|  |  | 44733.455 | 50.0296
|  |  | 44733.455 | 50.0296
|  |  | 44733.455 | 50.0296
|  |  | 44733.455 | 50.0297
|  |  | 44733.455 | 50.0297
|  |  | 44733.455 | 50.0298
|  |  | 44733.455 | 50.0299
|  |  | 44733.455 | 50.0299
|  |  | 44733.455 | 50.03
|  |  | 44733.455 | 50.03
|  |  | 44733.455 | 50.03
|  |  | 44733.455 | 50.0301
|  |  | 44733.455 | 50.0301
|  |  | 44733.455 | 50.0301
|  |  | 44733.455 | 50.03
|  |  | 44733.455 | 50.03
|  |  | 44733.455 | 50.03
|  |  | 44733.455 | 50.0299
|  |  | 44733.455 | 50.0299
|  |  | 44733.455 | 50.0299
|  |  | 44733.455 | 50.0299
|  |  | 44733.455 | 50.0299
|  |  | 44733.455 | 50.03
|  |  | 44733.455 | 50.03
|  |  | 44733.455 | 50.0301
|  |  | 44733.455 | 50.0301
|  |  | 44733.455 | 50.0301
|  |  | 44733.455 | 50.0301
|  |  | 44733.455 | 50.0302
|  |  | 44733.455 | 50.0303
|  |  | 44733.455 | 50.0303
|  |  | 44733.455 | 50.0303
|  |  | 44733.455 | 50.0304
|  |  | 2022-06-21 10:55 | 50.0305

## 20220622-1
GMT |  |  | High resolution Incident data
Date | Time | Freq | time | freq
2022-06-22 | 8:48 | 50.031 | 2022-06-22 09:48 | 50.0323
2022-06-22 | 8:48 | 50.027 | 44734.4085 | 50.0323
2022-06-22 | 8:48 | 50.023 | 44734.4085 | 50.0323
2022-06-22 | 8:48 | 50.022 | 44734.4085 | 50.0323
2022-06-22 | 8:48 | 50.023 | 44734.4085 | 50.0322
2022-06-22 | 8:48 | 50.024 | 44734.4085 | 50.0322
2022-06-22 | 8:48 | 50.026 | 44734.4085 | 50.0322
2022-06-22 | 8:48 | 50.03 | 44734.4085 | 50.0322
2022-06-22 | 8:48 | 50.033 | 44734.4085 | 50.0322
2022-06-22 | 8:48 | 50.034 | 44734.4085 | 50.0321
2022-06-22 | 8:48 | 50.036 | 44734.4085 | 50.0321
2022-06-22 | 8:48 | 50.035 | 44734.4085 | 50.0321
2022-06-22 | 8:48 | 50.035 | 44734.4085 | 50.032
2022-06-22 | 8:48 | 50.033 | 44734.4085 | 50.032
2022-06-22 | 8:48 | 50.032 | 44734.4085 | 50.0319
2022-06-22 | 8:48 | 50.032 | 44734.4085 | 50.0318
2022-06-22 | 8:48 | 50.03 | 44734.4085 | 50.0317
2022-06-22 | 8:48 | 50.029 | 44734.4085 | 50.0317
2022-06-22 | 8:48 | 50.03 | 44734.4085 | 50.0315
2022-06-22 | 8:48 | 50.031 | 44734.4085 | 50.0315
2022-06-22 | 8:48 | 50.035 | 44734.4085 | 50.0314
2022-06-22 | 8:48 | 50.036 | 44734.4085 | 50.0314
2022-06-22 | 8:48 | 50.038 | 44734.4085 | 50.0313
2022-06-22 | 8:48 | 50.039 | 44734.4085 | 50.0313
2022-06-22 | 8:48 | 50.039 | 44734.4085 | 50.0312
2022-06-22 | 8:48 | 50.043 | 44734.4085 | 50.0311
2022-06-22 | 8:48 | 50.044 | 44734.4085 | 50.031
2022-06-22 | 8:48 | 50.047 | 44734.4085 | 50.031
2022-06-22 | 8:48 | 50.048 | 44734.4085 | 50.031
2022-06-22 | 8:48 | 50.049 | 44734.4085 | 50.031
2022-06-22 | 8:49 | 50.049 | 44734.4085 | 50.0309
2022-06-22 | 8:49 | 50.053 | 44734.4085 | 50.031
2022-06-22 | 8:49 | 50.055 | 44734.4085 | 50.031
2022-06-22 | 8:49 | 50.06 | 44734.4085 | 50.0309
2022-06-22 | 8:49 | 50.06 | 44734.4085 | 50.0309
2022-06-22 | 8:49 | 50.063 | 44734.4085 | 50.0308
2022-06-22 | 8:49 | 50.062 | 44734.4085 | 50.0308
2022-06-22 | 8:49 | 50.061 | 44734.4085 | 50.0309
2022-06-22 | 8:49 | 50.059 | 44734.4085 | 50.0309
2022-06-22 | 8:49 | 50.058 | 44734.4085 | 50.0309
2022-06-22 | 8:49 | 50.05 | 44734.4085 | 50.0309
2022-06-22 | 8:49 | 50.023 | 44734.4085 | 50.0309
2022-06-22 | 8:49 | 49.989 | 44734.4085 | 50.0309
2022-06-22 | 8:49 | 49.967 | 44734.4085 | 50.0308
2022-06-22 | 8:49 | 49.945 | 44734.4085 | 50.0308
2022-06-22 | 8:49 | 49.937 | 44734.4085 | 50.0308
2022-06-22 | 8:49 | 49.926 | 44734.4085 | 50.0308
2022-06-22 | 8:49 | 49.918 | 44734.4085 | 50.0308
2022-06-22 | 8:49 | 49.91 | 44734.4085 | 50.0308
2022-06-22 | 8:49 | 49.906 | 44734.4085 | 50.0308
2022-06-22 | 8:49 | 49.907 | 2022-06-22 09:48 | 50.0308
2022-06-22 | 8:49 | 49.907 | 44734.4085 | 50.0308
2022-06-22 | 8:49 | 49.907 | 44734.4085 | 50.0307
2022-06-22 | 8:49 | 49.911 | 44734.4085 | 50.0307
2022-06-22 | 8:49 | 49.914 | 44734.4085 | 50.0307
2022-06-22 | 8:49 | 49.919 | 44734.4085 | 50.0307
2022-06-22 | 8:49 | 49.918 | 44734.4085 | 50.0306
2022-06-22 | 8:49 | 49.922 | 44734.4085 | 50.0306
2022-06-22 | 8:49 | 49.92 | 44734.4085 | 50.0305
2022-06-22 | 8:49 | 49.922 | 44734.4085 | 50.0305
2022-06-22 | 8:49 | 49.926 | 44734.4085 | 50.0305
2022-06-22 | 8:49 | 49.926 | 44734.4085 | 50.0305
2022-06-22 | 8:49 | 49.925 | 44734.4085 | 50.0304
2022-06-22 | 8:49 | 49.927 | 44734.4085 | 50.0305
2022-06-22 | 8:49 | 49.925 | 44734.4085 | 50.0305
2022-06-22 | 8:49 | 49.924 | 44734.4085 | 50.0304
2022-06-22 | 8:49 | 49.921 | 44734.4085 | 50.0305
2022-06-22 | 8:49 | 49.917 | 44734.4085 | 50.0305
2022-06-22 | 8:49 | 49.912 | 44734.4085 | 50.0305
2022-06-22 | 8:49 | 49.909 | 44734.4085 | 50.0306
2022-06-22 | 8:49 | 49.905 | 44734.4085 | 50.0306
2022-06-22 | 8:49 | 49.903 | 44734.4085 | 50.0306
2022-06-22 | 8:49 | 49.903 | 44734.4085 | 50.0306
2022-06-22 | 8:49 | 49.904 | 44734.4085 | 50.0305
2022-06-22 | 8:49 | 49.905 | 44734.4085 | 50.0305
2022-06-22 | 8:49 | 49.906 | 44734.4085 | 50.0303
2022-06-22 | 8:49 | 49.906 | 44734.4085 | 50.0302
2022-06-22 | 8:49 | 49.906 | 44734.4085 | 50.0302
2022-06-22 | 8:49 | 49.905 | 44734.4085 | 50.0301
2022-06-22 | 8:49 | 49.906 | 44734.4085 | 50.0301
2022-06-22 | 8:49 | 49.905 | 44734.4085 | 50.0301
2022-06-22 | 8:49 | 49.906 | 44734.4085 | 50.0301
2022-06-22 | 8:49 | 49.904 | 44734.4085 | 50.0301
2022-06-22 | 8:49 | 49.898 | 44734.4085 | 50.0301
2022-06-22 | 8:49 | 49.893 | 44734.4085 | 50.0301
2022-06-22 | 8:49 | 49.887 | 44734.4085 | 50.0301
2022-06-22 | 8:49 | 49.885 | 44734.4085 | 50.0301
2022-06-22 | 8:49 | 49.883 | 44734.4085 | 50.03
2022-06-22 | 8:49 | 49.884 | 44734.4085 | 50.03
2022-06-22 | 8:49 | 49.887 | 44734.4085 | 50.03
2022-06-22 | 8:49 | 49.893 | 44734.4085 | 50.0299
2022-06-22 | 8:50 | 49.898 | 44734.4085 | 50.0299
2022-06-22 | 8:50 | 49.902 | 44734.4085 | 50.0299
2022-06-22 | 8:50 | 49.905 | 44734.4085 | 50.03
2022-06-22 | 8:50 | 49.909 | 44734.4085 | 50.03
2022-06-22 | 8:50 | 49.914 | 44734.4085 | 50.03
2022-06-22 | 8:50 | 49.921 | 44734.4085 | 50.03
2022-06-22 | 8:50 | 49.927 | 44734.4085 | 50.0301
2022-06-22 | 8:50 | 49.931 | 44734.4085 | 50.0301
2022-06-22 | 8:50 | 49.932 | 44734.4085 | 50.03
2022-06-22 | 8:50 | 49.931 | 2022-06-22 09:48 | 50.0301
2022-06-22 | 8:50 | 49.927 | 44734.4085 | 50.0301
2022-06-22 | 8:50 | 49.925 | 44734.4085 | 50.0301
2022-06-22 | 8:50 | 49.921 | 44734.4085 | 50.0301
2022-06-22 | 8:50 | 49.919 | 44734.4085 | 50.03
2022-06-22 | 8:50 | 49.916 | 44734.4085 | 50.03
2022-06-22 | 8:50 | 49.91 | 44734.4085 | 50.03
2022-06-22 | 8:50 | 49.907 | 44734.4085 | 50.0299
2022-06-22 | 8:50 | 49.907 | 44734.4085 | 50.0299
2022-06-22 | 8:50 | 49.906 | 44734.4085 | 50.0299
2022-06-22 | 8:50 | 49.907 | 44734.4085 | 50.0299
2022-06-22 | 8:50 | 49.908 | 44734.4085 | 50.0299
2022-06-22 | 8:50 | 49.91 | 44734.4085 | 50.03
2022-06-22 | 8:50 | 49.914 | 44734.4085 | 50.03
2022-06-22 | 8:50 | 49.916 | 44734.4085 | 50.03
2022-06-22 | 8:50 | 49.917 | 44734.4085 | 50.0301
2022-06-22 | 8:50 | 49.918 | 44734.4085 | 50.0301
2022-06-22 | 8:50 | 49.918 | 44734.4085 | 50.0301
2022-06-22 | 8:50 | 49.917 | 44734.4085 | 50.0301
2022-06-22 | 8:50 | 49.918 | 44734.4085 | 50.0301
2022-06-22 | 8:50 | 49.918 | 44734.4085 | 50.0301
2022-06-22 | 8:50 | 49.917 | 44734.4085 | 50.0302
2022-06-22 | 8:50 | 49.919 | 44734.4085 | 50.0301
2022-06-22 | 8:50 | 49.917 | 44734.4085 | 50.0301
2022-06-22 | 8:50 | 49.915 | 44734.4085 | 50.0301
2022-06-22 | 8:50 | 49.915 | 44734.4085 | 50.0301
2022-06-22 | 8:50 | 49.913 | 44734.4085 | 50.0301
2022-06-22 | 8:50 | 49.91 | 44734.4085 | 50.0301
2022-06-22 | 8:50 | 49.91 | 44734.4085 | 50.0301
2022-06-22 | 8:50 | 49.91 | 44734.4085 | 50.0302
2022-06-22 | 8:50 | 49.908 | 44734.4085 | 50.0302
2022-06-22 | 8:50 | 49.907 | 44734.4085 | 50.0302
2022-06-22 | 8:50 | 49.904 | 44734.4085 | 50.0302
2022-06-22 | 8:50 | 49.904 | 44734.4085 | 50.0302
2022-06-22 | 8:50 | 49.903 | 44734.4085 | 50.0302
2022-06-22 | 8:50 | 49.903 | 44734.4085 | 50.0302
2022-06-22 | 8:50 | 49.903 | 44734.4085 | 50.0302
2022-06-22 | 8:50 | 49.901 | 44734.4085 | 50.0302
2022-06-22 | 8:50 | 49.9 | 44734.4085 | 50.0302
2022-06-22 | 8:50 | 49.898 | 44734.4085 | 50.0303
2022-06-22 | 8:50 | 49.898 | 44734.4085 | 50.0304
2022-06-22 | 8:50 | 49.9 | 44734.4085 | 50.0304
2022-06-22 | 8:50 | 49.899 | 44734.4085 | 50.0305
2022-06-22 | 8:50 | 49.897 | 44734.4085 | 50.0306
2022-06-22 | 8:50 | 49.896 | 44734.4085 | 50.0307
2022-06-22 | 8:50 | 49.894 | 44734.4085 | 50.0307
2022-06-22 | 8:50 | 49.897 | 44734.4085 | 50.0307
2022-06-22 | 8:50 | 49.898 | 44734.4085 | 50.0307
2022-06-22 | 8:50 | 49.899 | 44734.4085 | 50.0307
2022-06-22 | 8:50 | 49.898 | 44734.4085 | 50.0307
2022-06-22 | 8:51 | 49.897 | 2022-06-22 09:48 | 50.0307
2022-06-22 | 8:51 | 49.897 | 44734.4085 | 50.0307
2022-06-22 | 8:51 | 49.896 | 44734.4085 | 50.0307
2022-06-22 | 8:51 | 49.896 | 44734.4085 | 50.0307
2022-06-22 | 8:51 | 49.896 | 44734.4085 | 50.0308
2022-06-22 | 8:51 | 49.895 | 44734.4085 | 50.0308
2022-06-22 | 8:51 | 49.895 | 44734.4085 | 50.0309
2022-06-22 | 8:51 | 49.894 | 44734.4085 | 50.031
2022-06-22 | 8:51 | 49.896 | 44734.4085 | 50.031
2022-06-22 | 8:51 | 49.899 | 44734.4085 | 50.031
2022-06-22 | 8:51 | 49.9 | 44734.4085 | 50.0311
2022-06-22 | 8:51 | 49.901 | 44734.4085 | 50.0312
2022-06-22 | 8:51 | 49.899 | 44734.4085 | 50.0313
2022-06-22 | 8:51 | 49.899 | 44734.4085 | 50.0314
2022-06-22 | 8:51 | 49.899 | 44734.4085 | 50.0314
2022-06-22 | 8:51 | 49.899 | 44734.4085 | 50.0315
2022-06-22 | 8:51 | 49.899 | 44734.4085 | 50.0316
2022-06-22 | 8:51 | 49.899 | 44734.4085 | 50.0316
2022-06-22 | 8:51 | 49.9 | 44734.4085 | 50.0317
2022-06-22 | 8:51 | 49.898 | 44734.4085 | 50.0317
2022-06-22 | 8:51 | 49.895 | 44734.4085 | 50.0318
2022-06-22 | 8:51 | 49.891 | 44734.4085 | 50.0318
2022-06-22 | 8:51 | 49.888 | 44734.4085 | 50.0319
2022-06-22 | 8:51 | 49.887 | 44734.4085 | 50.0319
2022-06-22 | 8:51 | 49.886 | 44734.4085 | 50.0319
2022-06-22 | 8:51 | 49.887 | 44734.4085 | 50.0319
2022-06-22 | 8:51 | 49.888 | 44734.4085 | 50.032
2022-06-22 | 8:51 | 49.89 | 44734.4085 | 50.032
2022-06-22 | 8:51 | 49.89 | 44734.4085 | 50.0322
2022-06-22 | 8:51 | 49.894 | 44734.4085 | 50.0323
2022-06-22 | 8:51 | 49.898 | 44734.4085 | 50.0323
2022-06-22 | 8:51 | 49.901 | 44734.4085 | 50.0325
2022-06-22 | 8:51 | 49.903 | 44734.4085 | 50.0326
2022-06-22 | 8:51 | 49.905 | 44734.4085 | 50.0327
2022-06-22 | 8:51 | 49.909 | 44734.4085 | 50.0328
2022-06-22 | 8:51 | 49.91 | 44734.4085 | 50.0328
2022-06-22 | 8:51 | 49.911 | 44734.4086 | 50.0328
2022-06-22 | 8:51 | 49.911 | 44734.4086 | 50.0329
2022-06-22 | 8:51 | 49.911 | 44734.4086 | 50.0329
2022-06-22 | 8:51 | 49.91 | 44734.4086 | 50.0329
2022-06-22 | 8:51 | 49.907 | 44734.4086 | 50.0329
2022-06-22 | 8:51 | 49.905 | 44734.4086 | 50.033
2022-06-22 | 8:51 | 49.902 | 44734.4086 | 50.033
2022-06-22 | 8:51 | 49.901 | 44734.4086 | 50.033
2022-06-22 | 8:51 | 49.899 | 44734.4086 | 50.0331
2022-06-22 | 8:51 | 49.899 | 44734.4086 | 50.0331
2022-06-22 | 8:51 | 49.898 | 44734.4086 | 50.0331
2022-06-22 | 8:51 | 49.897 | 44734.4086 | 50.0331
2022-06-22 | 8:51 | 49.898 | 44734.4086 | 50.0331
2022-06-22 | 8:51 | 49.897 | 44734.4086 | 50.0331
2022-06-22 | 8:51 | 49.894 | 2022-06-22 09:48 | 50.0331
2022-06-22 | 8:51 | 49.894 | 44734.4086 | 50.0331
2022-06-22 | 8:51 | 49.892 | 44734.4086 | 50.0331
2022-06-22 | 8:51 | 49.891 | 44734.4086 | 50.0331
2022-06-22 | 8:51 | 49.891 | 44734.4086 | 50.0332
2022-06-22 | 8:51 | 49.893 | 44734.4086 | 50.0332
2022-06-22 | 8:51 | 49.894 | 44734.4086 | 50.0333
2022-06-22 | 8:51 | 49.896 | 44734.4086 | 50.0333
2022-06-22 | 8:51 | 49.897 | 44734.4086 | 50.0333
2022-06-22 | 8:51 | 49.897 | 44734.4086 | 50.0334
2022-06-22 | 8:51 | 49.895 | 44734.4086 | 50.0334
2022-06-22 | 8:52 | 49.896 | 44734.4086 | 50.0335
2022-06-22 | 8:52 | 49.897 | 44734.4086 | 50.0335
2022-06-22 | 8:52 | 49.898 | 44734.4086 | 50.0336
2022-06-22 | 8:52 | 49.898 | 44734.4086 | 50.0337
2022-06-22 | 8:52 | 49.9 | 44734.4086 | 50.0337
2022-06-22 | 8:52 | 49.9 | 44734.4086 | 50.0338
2022-06-22 | 8:52 | 49.901 | 44734.4086 | 50.0338
2022-06-22 | 8:52 | 49.901 | 44734.4086 | 50.0339
2022-06-22 | 8:52 | 49.901 | 44734.4086 | 50.034
2022-06-22 | 8:52 | 49.898 | 44734.4086 | 50.034
2022-06-22 | 8:52 | 49.899 | 44734.4086 | 50.0341
2022-06-22 | 8:52 | 49.896 | 44734.4086 | 50.0342
2022-06-22 | 8:52 | 49.896 | 44734.4086 | 50.0343
2022-06-22 | 8:52 | 49.894 | 44734.4086 | 50.0343
2022-06-22 | 8:52 | 49.895 | 44734.4086 | 50.0344
2022-06-22 | 8:52 | 49.896 | 44734.4086 | 50.0345
2022-06-22 | 8:52 | 49.896 | 44734.4086 | 50.0345
2022-06-22 | 8:52 | 49.897 | 44734.4086 | 50.0346
2022-06-22 | 8:52 | 49.896 | 44734.4086 | 50.0347
2022-06-22 | 8:52 | 49.897 | 44734.4086 | 50.0348
2022-06-22 | 8:52 | 49.894 | 44734.4086 | 50.0348
2022-06-22 | 8:52 | 49.893 | 44734.4086 | 50.0349
2022-06-22 | 8:52 | 49.892 | 44734.4086 | 50.0349
2022-06-22 | 8:52 | 49.893 | 44734.4086 | 50.035
2022-06-22 | 8:52 | 49.893 | 44734.4086 | 50.0351
2022-06-22 | 8:52 | 49.891 | 44734.4086 | 50.0351
2022-06-22 | 8:52 | 49.89 | 44734.4086 | 50.0352
2022-06-22 | 8:52 | 49.893 | 44734.4086 | 50.0352
2022-06-22 | 8:52 | 49.891 | 44734.4086 | 50.0352
2022-06-22 | 8:52 | 49.888 | 44734.4086 | 50.0353
2022-06-22 | 8:52 | 49.881 | 44734.4086 | 50.0353
2022-06-22 | 8:52 | 49.876 | 44734.4086 | 50.0353
2022-06-22 | 8:52 | 49.872 | 44734.4086 | 50.0354
2022-06-22 | 8:52 | 49.874 | 44734.4086 | 50.0355
2022-06-22 | 8:52 | 49.872 | 44734.4086 | 50.0356
2022-06-22 | 8:52 | 49.873 | 44734.4086 | 50.0357
2022-06-22 | 8:52 | 49.872 | 44734.4086 | 50.0357
2022-06-22 | 8:52 | 49.871 | 44734.4086 | 50.0358
2022-06-22 | 8:52 | 49.869 | 44734.4086 | 50.0358
2022-06-22 | 8:52 | 49.867 | 2022-06-22 09:48 | 50.0359
2022-06-22 | 8:52 | 49.863 | 44734.4086 | 50.0359
2022-06-22 | 8:52 | 49.861 | 44734.4086 | 50.0359
2022-06-22 | 8:52 | 49.86 | 44734.4086 | 50.0359
2022-06-22 | 8:52 | 49.856 | 44734.4086 | 50.036
2022-06-22 | 8:52 | 49.855 | 44734.4086 | 50.036
2022-06-22 | 8:52 | 49.852 | 44734.4086 | 50.0361
2022-06-22 | 8:52 | 49.849 | 44734.4086 | 50.0361
2022-06-22 | 8:52 | 49.845 | 44734.4086 | 50.0362
2022-06-22 | 8:52 | 49.842 | 44734.4086 | 50.0362
2022-06-22 | 8:52 | 49.836 | 44734.4086 | 50.0363
2022-06-22 | 8:52 | 49.834 | 44734.4086 | 50.0363
2022-06-22 | 8:52 | 49.833 | 44734.4086 | 50.0363
2022-06-22 | 8:52 | 49.831 | 44734.4086 | 50.0364
2022-06-22 | 8:52 | 49.83 | 44734.4086 | 50.0364
2022-06-22 | 8:52 | 49.829 | 44734.4086 | 50.0364
2022-06-22 | 8:52 | 49.828 | 44734.4086 | 50.0364
2022-06-22 | 8:52 | 49.824 | 44734.4086 | 50.0364
2022-06-22 | 8:52 | 49.824 | 44734.4086 | 50.0364
2022-06-22 | 8:52 | 49.821 | 44734.4086 | 50.0364
2022-06-22 | 8:53 | 49.821 | 44734.4086 | 50.0364
2022-06-22 | 8:53 | 49.819 | 44734.4086 | 50.0365
2022-06-22 | 8:53 | 49.818 | 44734.4086 | 50.0365
2022-06-22 | 8:53 | 49.817 | 44734.4086 | 50.0366
2022-06-22 | 8:53 | 49.815 | 44734.4086 | 50.0366
2022-06-22 | 8:53 | 49.817 | 44734.4086 | 50.0367
2022-06-22 | 8:53 | 49.816 | 44734.4086 | 50.0369
2022-06-22 | 8:53 | 49.821 | 44734.4086 | 50.037
2022-06-22 | 8:53 | 49.823 | 44734.4086 | 50.037
2022-06-22 | 8:53 | 49.827 | 44734.4086 | 50.0371
2022-06-22 | 8:53 | 49.827 | 44734.4086 | 50.0371
2022-06-22 | 8:53 | 49.83 | 44734.4086 | 50.0372
2022-06-22 | 8:53 | 49.83 | 44734.4086 | 50.0373
2022-06-22 | 8:53 | 49.831 | 44734.4086 | 50.0373
2022-06-22 | 8:53 | 49.832 | 44734.4086 | 50.0373
2022-06-22 | 8:53 | 49.83 | 44734.4086 | 50.0374
2022-06-22 | 8:53 | 49.826 | 44734.4086 | 50.0374
2022-06-22 | 8:53 | 49.82 | 44734.4086 | 50.0374
2022-06-22 | 8:53 | 49.816 | 44734.4086 | 50.0375
2022-06-22 | 8:53 | 49.814 | 44734.4086 | 50.0375
2022-06-22 | 8:53 | 49.81 | 44734.4086 | 50.0375
2022-06-22 | 8:53 | 49.809 | 44734.4086 | 50.0376
2022-06-22 | 8:53 | 49.808 | 44734.4086 | 50.0376
2022-06-22 | 8:53 | 49.804 | 44734.4086 | 50.0377
2022-06-22 | 8:53 | 49.802 | 44734.4086 | 50.0378
2022-06-22 | 8:53 | 49.798 | 44734.4086 | 50.0379
2022-06-22 | 8:53 | 49.795 | 44734.4086 | 50.038
2022-06-22 | 8:53 | 49.794 | 44734.4086 | 50.038
2022-06-22 | 8:53 | 49.793 | 44734.4086 | 50.038
2022-06-22 | 8:53 | 49.793 | 44734.4086 | 50.038
2022-06-22 | 8:53 | 49.791 | 2022-06-22 09:48 | 50.0379
2022-06-22 | 8:53 | 49.791 | 44734.4086 | 50.0378
2022-06-22 | 8:53 | 49.792 | 44734.4086 | 50.0378
2022-06-22 | 8:53 | 49.795 | 44734.4086 | 50.0378
2022-06-22 | 8:53 | 49.797 | 44734.4086 | 50.0377
2022-06-22 | 8:53 | 49.797 | 44734.4086 | 50.0378
2022-06-22 | 8:53 | 49.797 | 44734.4086 | 50.0378
2022-06-22 | 8:53 | 49.795 | 44734.4086 | 50.0378
2022-06-22 | 8:53 | 49.794 | 44734.4086 | 50.0379
2022-06-22 | 8:53 | 49.793 | 44734.4086 | 50.0379
2022-06-22 | 8:53 | 49.793 | 44734.4086 | 50.038
2022-06-22 | 8:53 | 49.793 | 44734.4086 | 50.038
2022-06-22 | 8:53 | 49.793 | 44734.4086 | 50.038
2022-06-22 | 8:53 | 49.792 | 44734.4086 | 50.038
2022-06-22 | 8:53 | 49.792 | 44734.4086 | 50.038
2022-06-22 | 8:53 | 49.794 | 44734.4086 | 50.038
2022-06-22 | 8:53 | 49.793 | 44734.4086 | 50.038
2022-06-22 | 8:53 | 49.795 | 44734.4086 | 50.0379
2022-06-22 | 8:53 | 49.795 | 44734.4086 | 50.038
2022-06-22 | 8:53 | 49.797 | 44734.4086 | 50.038
2022-06-22 | 8:53 | 49.798 | 44734.4086 | 50.0381
2022-06-22 | 8:53 | 49.8 | 44734.4086 | 50.0381
2022-06-22 | 8:53 | 49.8 | 44734.4086 | 50.0381
2022-06-22 | 8:53 | 49.802 | 44734.4086 | 50.0382
2022-06-22 | 8:53 | 49.802 | 44734.4086 | 50.0381
2022-06-22 | 8:53 | 49.804 | 44734.4086 | 50.0381
2022-06-22 | 8:53 | 49.805 | 44734.4086 | 50.0381
2022-06-22 | 8:53 | 49.804 | 44734.4086 | 50.0381
2022-06-22 | 8:53 | 49.806 | 44734.4086 | 50.038
2022-06-22 | 8:53 | 49.807 | 44734.4086 | 50.038
2022-06-22 | 8:53 | 49.808 | 44734.4086 | 50.0381
2022-06-22 | 8:54 | 49.81 | 44734.4086 | 50.0381
2022-06-22 | 8:54 | 49.81 | 44734.4086 | 50.0382
2022-06-22 | 8:54 | 49.812 | 44734.4086 | 50.0382
2022-06-22 | 8:54 | 49.811 | 44734.4086 | 50.0382
2022-06-22 | 8:54 | 49.815 | 44734.4086 | 50.0382
2022-06-22 | 8:54 | 49.818 | 44734.4086 | 50.0382
2022-06-22 | 8:54 | 49.822 | 44734.4086 | 50.0383
2022-06-22 | 8:54 | 49.827 | 44734.4086 | 50.0383
2022-06-22 | 8:54 | 49.83 | 44734.4086 | 50.0384
2022-06-22 | 8:54 | 49.834 | 44734.4086 | 50.0385
2022-06-22 | 8:54 | 49.84 | 44734.4086 | 50.0386
2022-06-22 | 8:54 | 49.84 | 44734.4086 | 50.0387
2022-06-22 | 8:54 | 49.844 | 44734.4086 | 50.0388
2022-06-22 | 8:54 | 49.845 | 44734.4086 | 50.0389
2022-06-22 | 8:54 | 49.844 | 44734.4086 | 50.0389
2022-06-22 | 8:54 | 49.844 | 44734.4086 | 50.0391
2022-06-22 | 8:54 | 49.841 | 44734.4086 | 50.0392
2022-06-22 | 8:54 | 49.843 | 44734.4086 | 50.0393
2022-06-22 | 8:54 | 49.844 | 44734.4086 | 50.0393
2022-06-22 | 8:54 | 49.846 | 2022-06-22 09:48 | 50.0394
2022-06-22 | 8:54 | 49.846 | 44734.4086 | 50.0394
2022-06-22 | 8:54 | 49.847 | 44734.4086 | 50.0394
2022-06-22 | 8:54 | 49.847 | 44734.4086 | 50.0395
2022-06-22 | 8:54 | 49.847 | 44734.4086 | 50.0395
2022-06-22 | 8:54 | 49.845 | 44734.4086 | 50.0396
2022-06-22 | 8:54 | 49.843 | 44734.4086 | 50.0396
2022-06-22 | 8:54 | 49.839 | 44734.4086 | 50.0396
2022-06-22 | 8:54 | 49.836 | 44734.4086 | 50.0396
2022-06-22 | 8:54 | 49.832 | 44734.4086 | 50.0396
2022-06-22 | 8:54 | 49.829 | 44734.4086 | 50.0396
2022-06-22 | 8:54 | 49.825 | 44734.4086 | 50.0396
2022-06-22 | 8:54 | 49.824 | 44734.4086 | 50.0397
2022-06-22 | 8:54 | 49.821 | 44734.4086 | 50.0396
2022-06-22 | 8:54 | 49.818 | 44734.4086 | 50.0396
2022-06-22 | 8:54 | 49.815 | 44734.4086 | 50.0396
2022-06-22 | 8:54 | 49.814 | 44734.4086 | 50.0397
2022-06-22 | 8:54 | 49.816 | 44734.4086 | 50.0397
2022-06-22 | 8:54 | 49.815 | 44734.4086 | 50.0397
2022-06-22 | 8:54 | 49.816 | 44734.4086 | 50.0397
2022-06-22 | 8:54 | 49.818 | 44734.4086 | 50.0398
2022-06-22 | 8:54 | 49.819 | 44734.4086 | 50.0398
2022-06-22 | 8:54 | 49.822 | 44734.4086 | 50.0399
2022-06-22 | 8:54 | 49.822 | 44734.4086 | 50.0399
2022-06-22 | 8:54 | 49.82 | 44734.4086 | 50.0398
2022-06-22 | 8:54 | 49.82 | 44734.4086 | 50.0398
2022-06-22 | 8:54 | 49.82 | 44734.4086 | 50.0398
2022-06-22 | 8:54 | 49.82 | 44734.4086 | 50.0398
2022-06-22 | 8:54 | 49.822 | 44734.4086 | 50.0399
2022-06-22 | 8:54 | 49.824 | 44734.4086 | 50.0399
2022-06-22 | 8:54 | 49.829 | 44734.4086 | 50.04
2022-06-22 | 8:54 | 49.834 | 44734.4086 | 50.0401
2022-06-22 | 8:54 | 49.838 | 44734.4086 | 50.04
2022-06-22 | 8:54 | 49.84 | 44734.4086 | 50.0399
2022-06-22 | 8:54 | 49.842 | 44734.4086 | 50.0399
2022-06-22 | 8:54 | 49.844 | 44734.4086 | 50.0398
2022-06-22 | 8:54 | 49.844 | 44734.4086 | 50.0399
2022-06-22 | 8:54 | 49.843 | 44734.4086 | 50.0399
2022-06-22 | 8:54 | 49.844 | 44734.4086 | 50.0399
2022-06-22 | 8:54 | 49.844 | 44734.4086 | 50.0399
2022-06-22 | 8:55 | 49.845 | 44734.4086 | 50.04
2022-06-22 | 8:55 | 49.847 | 44734.4086 | 50.04
2022-06-22 | 8:55 | 49.847 | 44734.4086 | 50.04
2022-06-22 | 8:55 | 49.85 | 44734.4086 | 50.0401
2022-06-22 | 8:55 | 49.852 | 44734.4086 | 50.0401
2022-06-22 | 8:55 | 49.854 | 44734.4086 | 50.0401
2022-06-22 | 8:55 | 49.855 | 44734.4086 | 50.0401
2022-06-22 | 8:55 | 49.855 | 44734.4086 | 50.0401
2022-06-22 | 8:55 | 49.855 | 44734.4086 | 50.04
2022-06-22 | 8:55 | 49.855 | 44734.4086 | 50.0399
2022-06-22 | 8:55 | 49.855 | 2022-06-22 09:48 | 50.0399
2022-06-22 | 8:55 | 49.855 | 44734.4086 | 50.0398
2022-06-22 | 8:55 | 49.856 | 44734.4086 | 50.0398
2022-06-22 | 8:55 | 49.854 | 44734.4086 | 50.0397
2022-06-22 | 8:55 | 49.854 | 44734.4086 | 50.0397
2022-06-22 | 8:55 | 49.858 | 44734.4086 | 50.0397
2022-06-22 | 8:55 | 49.862 | 44734.4086 | 50.0398
2022-06-22 | 8:55 | 49.865 | 44734.4086 | 50.0398
2022-06-22 | 8:55 | 49.866 | 44734.4086 | 50.0399
2022-06-22 | 8:55 | 49.869 | 44734.4086 | 50.0399
2022-06-22 | 8:55 | 49.869 | 44734.4086 | 50.04
2022-06-22 | 8:55 | 49.869 | 44734.4086 | 50.0401
2022-06-22 | 8:55 | 49.873 | 44734.4086 | 50.0402
2022-06-22 | 8:55 | 49.873 | 44734.4086 | 50.0402
2022-06-22 | 8:55 | 49.873 | 44734.4086 | 50.0403
2022-06-22 | 8:55 | 49.874 | 44734.4086 | 50.0403
2022-06-22 | 8:55 | 49.874 | 44734.4086 | 50.0403
2022-06-22 | 8:55 | 49.873 | 44734.4086 | 50.0403
2022-06-22 | 8:55 | 49.872 | 44734.4086 | 50.0403
2022-06-22 | 8:55 | 49.87 | 44734.4086 | 50.0403
2022-06-22 | 8:55 | 49.867 | 44734.4086 | 50.0403
2022-06-22 | 8:55 | 49.863 | 44734.4086 | 50.0404
2022-06-22 | 8:55 | 49.86 | 44734.4086 | 50.0405
2022-06-22 | 8:55 | 49.857 | 44734.4086 | 50.0404
2022-06-22 | 8:55 | 49.855 | 44734.4086 | 50.0404
2022-06-22 | 8:55 | 49.854 | 44734.4086 | 50.0404
2022-06-22 | 8:55 | 49.851 | 44734.4086 | 50.0404
2022-06-22 | 8:55 | 49.847 | 44734.4086 | 50.0404
2022-06-22 | 8:55 | 49.844 | 44734.4086 | 50.0404
2022-06-22 | 8:55 | 49.841 | 44734.4086 | 50.0404
2022-06-22 | 8:55 | 49.838 | 44734.4086 | 50.0404
2022-06-22 | 8:55 | 49.836 | 44734.4086 | 50.0404
2022-06-22 | 8:55 | 49.836 | 44734.4086 | 50.0404
2022-06-22 | 8:55 | 49.837 | 44734.4086 | 50.0404
2022-06-22 | 8:55 | 49.839 | 44734.4086 | 50.0405
2022-06-22 | 8:55 | 49.84 | 44734.4086 | 50.0405
2022-06-22 | 8:55 | 49.838 | 44734.4086 | 50.0406
2022-06-22 | 8:55 | 49.838 | 44734.4086 | 50.0406
2022-06-22 | 8:55 | 49.838 | 44734.4086 | 50.0407
2022-06-22 | 8:55 | 49.841 | 44734.4086 | 50.0407
2022-06-22 | 8:55 | 49.846 | 44734.4086 | 50.0408
2022-06-22 | 8:55 | 49.851 | 44734.4086 | 50.0409
2022-06-22 | 8:55 | 49.855 | 44734.4086 | 50.0408
2022-06-22 | 8:55 | 49.859 | 44734.4086 | 50.0408
2022-06-22 | 8:55 | 49.863 | 44734.4086 | 50.041
2022-06-22 | 8:55 | 49.865 | 44734.4086 | 50.041
2022-06-22 | 8:55 | 49.865 | 44734.4086 | 50.041
2022-06-22 | 8:55 | 49.867 | 44734.4086 | 50.0409
2022-06-22 | 8:55 | 49.866 | 44734.4086 | 50.0408
2022-06-22 | 8:55 | 49.866 | 44734.4086 | 50.0408
2022-06-22 | 8:56 | 49.867 | 2022-06-22 09:48 | 50.0408
2022-06-22 | 8:56 | 49.865 | 44734.4086 | 50.0409
2022-06-22 | 8:56 | 49.865 | 44734.4086 | 50.041
2022-06-22 | 8:56 | 49.862 | 44734.4086 | 50.041
2022-06-22 | 8:56 | 49.861 | 44734.4086 | 50.0411
2022-06-22 | 8:56 | 49.857 | 44734.4086 | 50.0411
2022-06-22 | 8:56 | 49.854 | 44734.4086 | 50.0412
2022-06-22 | 8:56 | 49.853 | 44734.4086 | 50.0412
2022-06-22 | 8:56 | 49.849 | 44734.4086 | 50.0412
2022-06-22 | 8:56 | 49.849 | 44734.4086 | 50.0413
2022-06-22 | 8:56 | 49.845 | 44734.4086 | 50.0413
2022-06-22 | 8:56 | 49.845 | 44734.4086 | 50.0413
2022-06-22 | 8:56 | 49.841 | 44734.4086 | 50.0414
2022-06-22 | 8:56 | 49.839 | 44734.4086 | 50.0415
2022-06-22 | 8:56 | 49.838 | 44734.4086 | 50.0416
2022-06-22 | 8:56 | 49.836 | 44734.4086 | 50.0417
2022-06-22 | 8:56 | 49.831 | 44734.4086 | 50.0418
2022-06-22 | 8:56 | 49.83 | 44734.4086 | 50.0419
2022-06-22 | 8:56 | 49.829 | 44734.4086 | 50.042
2022-06-22 | 8:56 | 49.827 | 44734.4086 | 50.042
2022-06-22 | 8:56 | 49.826 | 44734.4086 | 50.042
2022-06-22 | 8:56 | 49.826 | 44734.4086 | 50.042
2022-06-22 | 8:56 | 49.828 | 44734.4086 | 50.0421
2022-06-22 | 8:56 | 49.828 | 44734.4086 | 50.042
2022-06-22 | 8:56 | 49.828 | 44734.4086 | 50.042
2022-06-22 | 8:56 | 49.827 | 44734.4086 | 50.0421
2022-06-22 | 8:56 | 49.826 | 44734.4086 | 50.0422
2022-06-22 | 8:56 | 49.828 | 44734.4086 | 50.0422
2022-06-22 | 8:56 | 49.83 | 44734.4086 | 50.0423
2022-06-22 | 8:56 | 49.831 | 44734.4086 | 50.0424
2022-06-22 | 8:56 | 49.829 | 44734.4086 | 50.0425
2022-06-22 | 8:56 | 49.829 | 44734.4086 | 50.0425
2022-06-22 | 8:56 | 49.827 | 44734.4086 | 50.0426
2022-06-22 | 8:56 | 49.826 | 44734.4086 | 50.0427
2022-06-22 | 8:56 | 49.822 | 44734.4086 | 50.0428
2022-06-22 | 8:56 | 49.82 | 44734.4086 | 50.0428
2022-06-22 | 8:56 | 49.816 | 44734.4086 | 50.0428
2022-06-22 | 8:56 | 49.813 | 44734.4086 | 50.0428
2022-06-22 | 8:56 | 49.814 | 44734.4086 | 50.0428
2022-06-22 | 8:56 | 49.814 | 44734.4086 | 50.0429
2022-06-22 | 8:56 | 49.812 | 44734.4086 | 50.0429
2022-06-22 | 8:56 | 49.812 | 44734.4086 | 50.043
2022-06-22 | 8:56 | 49.81 | 44734.4086 | 50.043
2022-06-22 | 8:56 | 49.811 | 44734.4086 | 50.043
2022-06-22 | 8:56 | 49.813 | 44734.4086 | 50.0431
2022-06-22 | 8:56 | 49.815 | 44734.4086 | 50.0431
2022-06-22 | 8:56 | 49.819 | 44734.4086 | 50.0432
2022-06-22 | 8:56 | 49.823 | 44734.4086 | 50.0432
2022-06-22 | 8:56 | 49.826 | 44734.4086 | 50.0432
2022-06-22 | 8:56 | 49.828 | 44734.4086 | 50.0432
2022-06-22 | 8:56 | 49.832 | 2022-06-22 09:48 | 50.0432
2022-06-22 | 8:56 | 49.834 | 44734.4086 | 50.0433
2022-06-22 | 8:56 | 49.836 | 44734.4086 | 50.0434
2022-06-22 | 8:56 | 49.835 | 44734.4086 | 50.0434
2022-06-22 | 8:56 | 49.833 | 44734.4086 | 50.0435
2022-06-22 | 8:56 | 49.834 | 44734.4086 | 50.0435
2022-06-22 | 8:56 | 49.837 | 44734.4086 | 50.0436
2022-06-22 | 8:56 | 49.84 | 44734.4086 | 50.0436
2022-06-22 | 8:56 | 49.844 | 44734.4086 | 50.0436
2022-06-22 | 8:56 | 49.846 | 44734.4086 | 50.0436
2022-06-22 | 8:56 | 49.848 | 44734.4086 | 50.0436
2022-06-22 | 8:57 | 49.851 | 44734.4086 | 50.0436
2022-06-22 | 8:57 | 49.852 | 44734.4086 | 50.0436
2022-06-22 | 8:57 | 49.855 | 44734.4086 | 50.0437
2022-06-22 | 8:57 | 49.857 | 44734.4086 | 50.0438
2022-06-22 | 8:57 | 49.858 | 44734.4086 | 50.0439
2022-06-22 | 8:57 | 49.859 | 44734.4086 | 50.044
2022-06-22 | 8:57 | 49.859 | 44734.4086 | 50.044
2022-06-22 | 8:57 | 49.858 | 44734.4086 | 50.044
2022-06-22 | 8:57 | 49.857 | 44734.4086 | 50.0441
2022-06-22 | 8:57 | 49.858 | 44734.4086 | 50.0441
2022-06-22 | 8:57 | 49.861 | 44734.4086 | 50.0442
2022-06-22 | 8:57 | 49.862 | 44734.4086 | 50.0443
2022-06-22 | 8:57 | 49.864 | 44734.4086 | 50.0444
2022-06-22 | 8:57 | 49.867 | 44734.4086 | 50.0445
2022-06-22 | 8:57 | 49.867 | 44734.4086 | 50.0445
2022-06-22 | 8:57 | 49.866 | 44734.4086 | 50.0446
2022-06-22 | 8:57 | 49.866 | 44734.4086 | 50.0446
2022-06-22 | 8:57 | 49.867 | 44734.4086 | 50.0447
2022-06-22 | 8:57 | 49.869 | 44734.4086 | 50.0447
2022-06-22 | 8:57 | 49.869 | 44734.4086 | 50.0447
2022-06-22 | 8:57 | 49.871 | 44734.4086 | 50.0447
2022-06-22 | 8:57 | 49.872 | 44734.4086 | 50.0447
2022-06-22 | 8:57 | 49.873 | 44734.4086 | 50.0447
2022-06-22 | 8:57 | 49.871 | 44734.4086 | 50.0447
2022-06-22 | 8:57 | 49.873 | 44734.4086 | 50.0448
2022-06-22 | 8:57 | 49.874 | 44734.4086 | 50.0448
2022-06-22 | 8:57 | 49.874 | 44734.4086 | 50.0449
2022-06-22 | 8:57 | 49.874 | 44734.4086 | 50.0451
2022-06-22 | 8:57 | 49.876 | 44734.4086 | 50.0451
2022-06-22 | 8:57 | 49.877 | 44734.4086 | 50.0453
2022-06-22 | 8:57 | 49.879 | 44734.4086 | 50.0454
2022-06-22 | 8:57 | 49.88 | 44734.4086 | 50.0455
2022-06-22 | 8:57 | 49.881 | 44734.4086 | 50.0456
2022-06-22 | 8:57 | 49.881 | 44734.4086 | 50.0457
2022-06-22 | 8:57 | 49.883 | 44734.4086 | 50.0457
2022-06-22 | 8:57 | 49.884 | 44734.4086 | 50.0458
2022-06-22 | 8:57 | 49.885 | 44734.4086 | 50.0458
2022-06-22 | 8:57 | 49.886 | 44734.4086 | 50.0458
2022-06-22 | 8:57 | 49.883 | 44734.4086 | 50.0458
2022-06-22 | 8:57 | 49.883 | 2022-06-22 09:48 | 50.0458
2022-06-22 | 8:57 | 49.882 | 44734.4086 | 50.046
2022-06-22 | 8:57 | 49.881 | 44734.4086 | 50.0458
2022-06-22 | 8:57 | 49.88 | 44734.4086 | 50.0458
2022-06-22 | 8:57 | 49.881 | 44734.4086 | 50.0459
2022-06-22 | 8:57 | 49.882 | 44734.4086 | 50.0459
2022-06-22 | 8:57 | 49.883 | 44734.4086 | 50.0459
2022-06-22 | 8:57 | 49.883 | 44734.4086 | 50.0459
2022-06-22 | 8:57 | 49.883 | 44734.4086 | 50.046
2022-06-22 | 8:57 | 49.883 | 44734.4086 | 50.0461
2022-06-22 | 8:57 | 49.881 | 44734.4086 | 50.0461
2022-06-22 | 8:57 | 49.882 | 44734.4086 | 50.0462
2022-06-22 | 8:57 | 49.884 | 44734.4086 | 50.0463
2022-06-22 | 8:57 | 49.888 | 44734.4086 | 50.0463
2022-06-22 | 8:57 | 49.888 | 44734.4086 | 50.0463
2022-06-22 | 8:57 | 49.888 | 44734.4086 | 50.0463
2022-06-22 | 8:57 | 49.888 | 44734.4086 | 50.0463
2022-06-22 | 8:57 | 49.89 | 44734.4086 | 50.0462
2022-06-22 | 8:57 | 49.893 | 44734.4086 | 50.0462
2022-06-22 | 8:57 | 49.897 | 44734.4086 | 50.0462
2022-06-22 | 8:58 | 49.9 | 44734.4086 | 50.0463
2022-06-22 | 8:58 | 49.903 | 44734.4086 | 50.0463
2022-06-22 | 8:58 | 49.904 | 44734.4086 | 50.0463
2022-06-22 | 8:58 | 49.906 | 44734.4086 | 50.0463
2022-06-22 | 8:58 | 49.908 | 44734.4086 | 50.0463
2022-06-22 | 8:58 | 49.91 | 44734.4086 | 50.0464
2022-06-22 | 8:58 | 49.914 | 44734.4086 | 50.0465
2022-06-22 | 8:58 | 49.917 | 44734.4086 | 50.0466
2022-06-22 | 8:58 | 49.917 | 44734.4086 | 50.0467
2022-06-22 | 8:58 | 49.919 | 44734.4086 | 50.0467
2022-06-22 | 8:58 | 49.922 | 44734.4086 | 50.0468
2022-06-22 | 8:58 | 49.926 | 44734.4086 | 50.0468
2022-06-22 | 8:58 | 49.928 | 44734.4086 | 50.0469
2022-06-22 | 8:58 | 49.93 | 44734.4086 | 50.0469
2022-06-22 | 8:58 | 49.931 | 44734.4086 | 50.0469
2022-06-22 | 8:58 | 49.932 | 44734.4086 | 50.0469
2022-06-22 | 8:58 | 49.933 | 44734.4086 | 50.0469
2022-06-22 | 8:58 | 49.937 | 44734.4086 | 50.0468
2022-06-22 | 8:58 | 49.94 | 44734.4086 | 50.0469
2022-06-22 | 8:58 | 49.942 | 44734.4086 | 50.047
2022-06-22 | 8:58 | 49.943 | 44734.4086 | 50.0471
2022-06-22 | 8:58 | 49.944 | 44734.4086 | 50.0471
2022-06-22 | 8:58 | 49.945 | 44734.4086 | 50.0473
2022-06-22 | 8:58 | 49.95 | 44734.4086 | 50.0474
2022-06-22 | 8:58 | 49.951 | 44734.4086 | 50.0475
2022-06-22 | 8:58 | 49.954 | 44734.4086 | 50.0475
2022-06-22 | 8:58 | 49.957 | 44734.4086 | 50.0476
2022-06-22 | 8:58 | 49.958 | 44734.4086 | 50.0476
2022-06-22 | 8:58 | 49.957 | 44734.4086 | 50.0476
2022-06-22 | 8:58 | 49.955 | 44734.4086 | 50.0476
2022-06-22 | 8:58 | 49.952 | 2022-06-22 09:48 | 50.0477
2022-06-22 | 8:58 | 49.948 | 44734.4086 | 50.0477
2022-06-22 | 8:58 | 49.946 | 44734.4086 | 50.0477
2022-06-22 | 8:58 | 49.945 | 44734.4086 | 50.0477
2022-06-22 | 8:58 | 49.943 | 44734.4086 | 50.0478
2022-06-22 | 8:58 | 49.941 | 44734.4086 | 50.0478
2022-06-22 | 8:58 | 49.938 | 44734.4086 | 50.0479
2022-06-22 | 8:58 | 49.933 | 44734.4086 | 50.048
2022-06-22 | 8:58 | 49.929 | 44734.4086 | 50.048
2022-06-22 | 8:58 | 49.924 | 44734.4086 | 50.0481
2022-06-22 | 8:58 | 49.92 | 44734.4086 | 50.0481
2022-06-22 | 8:58 | 49.917 | 44734.4086 | 50.0481
2022-06-22 | 8:58 | 49.914 | 44734.4086 | 50.048
2022-06-22 | 8:58 | 49.911 | 44734.4086 | 50.048
2022-06-22 | 8:58 | 49.912 | 44734.4086 | 50.048
2022-06-22 | 8:58 | 49.911 | 44734.4086 | 50.0479
2022-06-22 | 8:58 | 49.912 | 44734.4086 | 50.0479
2022-06-22 | 8:58 | 49.912 | 44734.4086 | 50.0478
2022-06-22 | 8:58 | 49.913 | 44734.4086 | 50.0478
2022-06-22 | 8:58 | 49.914 | 44734.4087 | 50.0479
2022-06-22 | 8:58 | 49.914 | 44734.4087 | 50.0479
2022-06-22 | 8:58 | 49.917 | 44734.4087 | 50.0479
2022-06-22 | 8:58 | 49.919 | 44734.4087 | 50.048
2022-06-22 | 8:58 | 49.918 | 44734.4087 | 50.048
2022-06-22 | 8:58 | 49.916 | 44734.4087 | 50.0481
2022-06-22 | 8:58 | 49.914 | 44734.4087 | 50.0483
2022-06-22 | 8:58 | 49.912 | 44734.4087 | 50.0483
2022-06-22 | 8:58 | 49.909 | 44734.4087 | 50.0483
2022-06-22 | 8:58 | 49.905 | 44734.4087 | 50.0482
2022-06-22 | 8:58 | 49.902 | 44734.4087 | 50.0482
2022-06-22 | 8:58 | 49.899 | 44734.4087 | 50.0481
2022-06-22 | 8:59 | 49.897 | 44734.4087 | 50.0481
2022-06-22 | 8:59 | 49.899 | 44734.4087 | 50.048
2022-06-22 | 8:59 | 49.899 | 44734.4087 | 50.0481
2022-06-22 | 8:59 | 49.9 | 44734.4087 | 50.0481
2022-06-22 | 8:59 | 49.901 | 44734.4087 | 50.0481
2022-06-22 | 8:59 | 49.902 | 44734.4087 | 50.0482
2022-06-22 | 8:59 | 49.902 | 44734.4087 | 50.0482
2022-06-22 | 8:59 | 49.901 | 44734.4087 | 50.0483
2022-06-22 | 8:59 | 49.898 | 44734.4087 | 50.0483
2022-06-22 | 8:59 | 49.894 | 44734.4087 | 50.0484
2022-06-22 | 8:59 | 49.89 | 44734.4087 | 50.0484
2022-06-22 | 8:59 | 49.886 | 44734.4087 | 50.0485
2022-06-22 | 8:59 | 49.884 | 44734.4087 | 50.0485
2022-06-22 | 8:59 | 49.882 | 44734.4087 | 50.0485
2022-06-22 | 8:59 | 49.879 | 44734.4087 | 50.0484
2022-06-22 | 8:59 | 49.879 | 44734.4087 | 50.0484
2022-06-22 | 8:59 | 49.88 | 44734.4087 | 50.0484
2022-06-22 | 8:59 | 49.878 | 44734.4087 | 50.0483
2022-06-22 | 8:59 | 49.877 | 44734.4087 | 50.0482
2022-06-22 | 8:59 | 49.878 | 2022-06-22 09:48 | 50.0482
2022-06-22 | 8:59 | 49.878 | 44734.4087 | 50.0483
2022-06-22 | 8:59 | 49.88 | 44734.4087 | 50.0484
2022-06-22 | 8:59 | 49.88 | 44734.4087 | 50.0484
2022-06-22 | 8:59 | 49.883 | 44734.4087 | 50.0486
2022-06-22 | 8:59 | 49.885 | 44734.4087 | 50.0487
2022-06-22 | 8:59 | 49.885 | 44734.4087 | 50.0488
2022-06-22 | 8:59 | 49.889 | 44734.4087 | 50.0488
2022-06-22 | 8:59 | 49.89 | 44734.4087 | 50.0488
2022-06-22 | 8:59 | 49.892 | 44734.4087 | 50.0489
2022-06-22 | 8:59 | 49.893 | 44734.4087 | 50.049
2022-06-22 | 8:59 | 49.896 | 44734.4087 | 50.049
2022-06-22 | 8:59 | 49.898 | 44734.4087 | 50.049
2022-06-22 | 8:59 | 49.898 | 44734.4087 | 50.049
2022-06-22 | 8:59 | 49.899 | 44734.4087 | 50.049
2022-06-22 | 8:59 | 49.897 | 44734.4087 | 50.049
2022-06-22 | 8:59 | 49.898 | 44734.4087 | 50.049
2022-06-22 | 8:59 | 49.901 | 44734.4087 | 50.049
2022-06-22 | 8:59 | 49.904 | 44734.4087 | 50.049
2022-06-22 | 8:59 | 49.905 | 44734.4087 | 50.0491
2022-06-22 | 8:59 | 49.91 | 44734.4087 | 50.0491
2022-06-22 | 8:59 | 49.911 | 44734.4087 | 50.0491
2022-06-22 | 8:59 | 49.91 | 44734.4087 | 50.0491
2022-06-22 | 8:59 | 49.907 | 44734.4087 | 50.0491
2022-06-22 | 8:59 | 49.904 | 44734.4087 | 50.0492
2022-06-22 | 8:59 | 49.905 | 44734.4087 | 50.0493
2022-06-22 | 8:59 | 49.904 | 44734.4087 | 50.0492
2022-06-22 | 8:59 | 49.904 | 44734.4087 | 50.0492
2022-06-22 | 8:59 | 49.902 | 44734.4087 | 50.0493
2022-06-22 | 8:59 | 49.905 | 44734.4087 | 50.0492
2022-06-22 | 8:59 | 49.902 | 44734.4087 | 50.0492
2022-06-22 | 8:59 | 49.901 | 44734.4087 | 50.0493
2022-06-22 | 8:59 | 49.904 | 44734.4087 | 50.0493
2022-06-22 | 8:59 | 49.906 | 44734.4087 | 50.0492
2022-06-22 | 8:59 | 49.907 | 44734.4087 | 50.0492
2022-06-22 | 8:59 | 49.908 | 44734.4087 | 50.0492
2022-06-22 | 8:59 | 49.91 | 44734.4087 | 50.0493
2022-06-22 | 8:59 | 49.915 | 44734.4087 | 50.0493
2022-06-22 | 8:59 | 49.918 | 44734.4087 | 50.0493
2022-06-22 | 8:59 | 49.921 | 44734.4087 | 50.0494
2022-06-22 | 9:00 | 49.922 | 44734.4087 | 50.0494
2022-06-22 | 9:00 | 49.923 | 44734.4087 | 50.0493
2022-06-22 | 9:00 | 49.922 | 44734.4087 | 50.0493
2022-06-22 | 9:00 | 49.92 | 44734.4087 | 50.0493
2022-06-22 | 9:00 | 49.919 | 44734.4087 | 50.0493
2022-06-22 | 9:00 | 49.917 | 44734.4087 | 50.0493
2022-06-22 | 9:00 | 49.918 | 44734.4087 | 50.0493
2022-06-22 | 9:00 | 49.919 | 44734.4087 | 50.0493
2022-06-22 | 9:00 | 49.918 | 44734.4087 | 50.0493
2022-06-22 | 9:00 | 49.921 | 44734.4087 | 50.0493
2022-06-22 | 9:00 | 49.922 | 2022-06-22 09:48 | 50.0492
2022-06-22 | 9:00 | 49.923 | 44734.4087 | 50.0492
2022-06-22 | 9:00 | 49.924 | 44734.4087 | 50.0492
2022-06-22 | 9:00 | 49.924 | 44734.4087 | 50.0492
2022-06-22 | 9:00 | 49.928 | 44734.4087 | 50.0493
2022-06-22 | 9:00 | 49.928 | 44734.4087 | 50.0493
2022-06-22 | 9:00 | 49.931 | 44734.4087 | 50.0493
2022-06-22 | 9:00 | 49.934 | 44734.4087 | 50.0494
2022-06-22 | 9:00 | 49.94 | 44734.4087 | 50.0494
2022-06-22 | 9:00 | 49.944 | 44734.4087 | 50.0495
2022-06-22 | 9:00 | 49.946 | 44734.4087 | 50.0495
2022-06-22 | 9:00 | 49.951 | 44734.4087 | 50.0495
2022-06-22 | 9:00 | 49.953 | 44734.4087 | 50.0495
2022-06-22 | 9:00 | 49.954 | 44734.4087 | 50.0495
2022-06-22 | 9:00 | 49.954 | 44734.4087 | 50.0495
2022-06-22 | 9:00 | 49.955 | 44734.4087 | 50.0497
2022-06-22 | 9:00 | 49.957 | 44734.4087 | 50.0497
2022-06-22 | 9:00 | 49.957 | 44734.4087 | 50.0497
2022-06-22 | 9:00 | 49.959 | 44734.4087 | 50.0497
2022-06-22 | 9:00 | 49.965 | 44734.4087 | 50.0498
2022-06-22 | 9:00 | 49.965 | 44734.4087 | 50.0498
2022-06-22 | 9:00 | 49.967 | 44734.4087 | 50.0499
2022-06-22 | 9:00 | 49.965 | 44734.4087 | 50.0499
2022-06-22 | 9:00 | 49.964 | 44734.4087 | 50.05
2022-06-22 | 9:00 | 49.966 | 44734.4087 | 50.0501
2022-06-22 | 9:00 | 49.967 | 44734.4087 | 50.0501
2022-06-22 | 9:00 | 49.968 | 44734.4087 | 50.0502
2022-06-22 | 9:00 | 49.972 | 44734.4087 | 50.0502
2022-06-22 | 9:00 | 49.977 | 44734.4087 | 50.0503
2022-06-22 | 9:00 | 49.98 | 44734.4087 | 50.0503
2022-06-22 | 9:00 | 49.985 | 44734.4087 | 50.0503
2022-06-22 | 9:00 | 49.989 | 44734.4087 | 50.0504
2022-06-22 | 9:00 | 49.991 | 44734.4087 | 50.0505
2022-06-22 | 9:00 | 49.994 | 44734.4087 | 50.0505
2022-06-22 | 9:00 | 49.997 | 44734.4087 | 50.0505
2022-06-22 | 9:00 | 50.001 | 44734.4087 | 50.0506
2022-06-22 | 9:00 | 50.005 | 44734.4087 | 50.0506
2022-06-22 | 9:00 | 50.01 | 44734.4087 | 50.0507
2022-06-22 | 9:00 | 50.017 | 44734.4087 | 50.0507
2022-06-22 | 9:00 | 50.021 | 44734.4087 | 50.0508
2022-06-22 | 9:00 | 50.025 | 44734.4087 | 50.0508
2022-06-22 | 9:00 | 50.026 | 44734.4087 | 50.0509
2022-06-22 | 9:00 | 50.028 | 44734.4087 | 50.0509
2022-06-22 | 9:00 | 50.029 | 44734.4087 | 50.0509
2022-06-22 | 9:00 | 50.03 | 44734.4087 | 50.051
2022-06-22 | 9:00 | 50.028 | 44734.4087 | 50.051
2022-06-22 | 9:00 | 50.029 | 44734.4087 | 50.0511
2022-06-22 | 9:00 | 50.028 | 44734.4087 | 50.0512
2022-06-22 | 9:00 | 50.026 | 44734.4087 | 50.0513
2022-06-22 | 9:00 | 50.025 | 44734.4087 | 50.0514
2022-06-22 | 9:00 | 50.02 | 2022-06-22 09:49 | 50.0515
2022-06-22 | 9:01 | 50.021 | 44734.4087 | 50.0515
2022-06-22 | 9:01 | 50.021 | 44734.4087 | 50.0515
2022-06-22 | 9:01 | 50.025 | 44734.4087 | 50.0516
2022-06-22 | 9:01 | 50.028 | 44734.4087 | 50.0516
2022-06-22 | 9:01 | 50.032 | 44734.4087 | 50.0517
2022-06-22 | 9:01 | 50.035 | 44734.4087 | 50.0517
2022-06-22 | 9:01 | 50.038 | 44734.4087 | 50.0517
2022-06-22 | 9:01 | 50.039 | 44734.4087 | 50.0518
2022-06-22 | 9:01 | 50.039 | 44734.4087 | 50.0519
2022-06-22 | 9:01 | 50.041 | 44734.4087 | 50.052
2022-06-22 | 9:01 | 50.04 | 44734.4087 | 50.052
2022-06-22 | 9:01 | 50.04 | 44734.4087 | 50.052
2022-06-22 | 9:01 | 50.045 | 44734.4087 | 50.0521
2022-06-22 | 9:01 | 50.049 | 44734.4087 | 50.0521
2022-06-22 | 9:01 | 50.052 | 44734.4087 | 50.0522
2022-06-22 | 9:01 | 50.056 | 44734.4087 | 50.0523
2022-06-22 | 9:01 | 50.058 | 44734.4087 | 50.0523
2022-06-22 | 9:01 | 50.06 | 44734.4087 | 50.0524
2022-06-22 | 9:01 | 50.06 | 44734.4087 | 50.0524
2022-06-22 | 9:01 | 50.055 | 44734.4087 | 50.0525
2022-06-22 | 9:01 | 50.054 | 44734.4087 | 50.0525
2022-06-22 | 9:01 | 50.05 | 44734.4087 | 50.0525
2022-06-22 | 9:01 | 50.048 | 44734.4087 | 50.0526
2022-06-22 | 9:01 | 50.048 | 44734.4087 | 50.0526
2022-06-22 | 9:01 | 50.05 | 44734.4087 | 50.0526
2022-06-22 | 9:01 | 50.055 | 44734.4087 | 50.0526
2022-06-22 | 9:01 | 50.056 | 44734.4087 | 50.0526
2022-06-22 | 9:01 | 50.062 | 44734.4087 | 50.0526
2022-06-22 | 9:01 | 50.063 | 44734.4087 | 50.0526
2022-06-22 | 9:01 | 50.061 | 44734.4087 | 50.0527
2022-06-22 | 9:01 | 50.057 | 44734.4087 | 50.0527
2022-06-22 | 9:01 | 50.056 | 44734.4087 | 50.0528
2022-06-22 | 9:01 | 50.055 | 44734.4087 | 50.0528
2022-06-22 | 9:01 | 50.058 | 44734.4087 | 50.0529
2022-06-22 | 9:01 | 50.058 | 44734.4087 | 50.0529
2022-06-22 | 9:01 | 50.059 | 44734.4087 | 50.053
2022-06-22 | 9:01 | 50.061 | 44734.4087 | 50.053
2022-06-22 | 9:01 | 50.06 | 44734.4087 | 50.0531
2022-06-22 | 9:01 | 50.061 | 44734.4087 | 50.0532
2022-06-22 | 9:01 | 50.063 | 44734.4087 | 50.0532
2022-06-22 | 9:01 | 50.059 | 44734.4087 | 50.0533
2022-06-22 | 9:01 | 50.058 | 44734.4087 | 50.0534
2022-06-22 | 9:01 | 50.056 | 44734.4087 | 50.0535
2022-06-22 | 9:01 | 50.052 | 44734.4087 | 50.0536
2022-06-22 | 9:01 | 50.048 | 44734.4087 | 50.0536
2022-06-22 | 9:01 | 50.045 | 44734.4087 | 50.0537
2022-06-22 | 9:01 | 50.042 | 44734.4087 | 50.0538
2022-06-22 | 9:01 | 50.038 | 44734.4087 | 50.0538
2022-06-22 | 9:01 | 50.035 | 44734.4087 | 50.0539
2022-06-22 | 9:01 | 50.034 | 2022-06-22 09:49 | 50.054
2022-06-22 | 9:01 | 50.033 | 44734.4087 | 50.0541
2022-06-22 | 9:01 | 50.033 | 44734.4087 | 50.0542
2022-06-22 | 9:01 | 50.031 | 44734.4087 | 50.0543
2022-06-22 | 9:01 | 50.03 | 44734.4087 | 50.0545
2022-06-22 | 9:01 | 50.029 | 44734.4087 | 50.0547
2022-06-22 | 9:01 | 50.029 | 44734.4087 | 50.0548
2022-06-22 | 9:01 | 50.029 | 44734.4087 | 50.0549
2022-06-22 | 9:01 | 50.029 | 44734.4087 | 50.055
2022-06-22 | 9:01 | 50.029 | 44734.4087 | 50.0551
2022-06-22 | 9:02 | 50.032 | 44734.4087 | 50.0551
2022-06-22 | 9:02 | 50.034 | 44734.4087 | 50.0552
2022-06-22 | 9:02 | 50.032 | 44734.4087 | 50.0552
2022-06-22 | 9:02 | 50.031 | 44734.4087 | 50.0553
2022-06-22 | 9:02 | 50.034 | 44734.4087 | 50.0554
2022-06-22 | 9:02 | 50.033 | 44734.4087 | 50.0555
2022-06-22 | 9:02 | 50.036 | 44734.4087 | 50.0555
2022-06-22 | 9:02 | 50.036 | 44734.4087 | 50.0556
2022-06-22 | 9:02 | 50.037 | 44734.4087 | 50.0557
2022-06-22 | 9:02 | 50.038 | 44734.4087 | 50.0558
2022-06-22 | 9:02 | 50.04 | 44734.4087 | 50.0559
2022-06-22 | 9:02 | 50.04 | 44734.4087 | 50.0559
2022-06-22 | 9:02 | 50.04 | 44734.4087 | 50.0559
2022-06-22 | 9:02 | 50.039 | 44734.4087 | 50.056
2022-06-22 | 9:02 | 50.038 | 44734.4087 | 50.056
2022-06-22 | 9:02 | 50.036 | 44734.4087 | 50.0561
2022-06-22 | 9:02 | 50.035 | 44734.4087 | 50.0561
2022-06-22 | 9:02 | 50.032 | 44734.4087 | 50.0561
2022-06-22 | 9:02 | 50.027 | 44734.4087 | 50.0561
2022-06-22 | 9:02 | 50.026 | 44734.4087 | 50.0562
2022-06-22 | 9:02 | 50.025 | 44734.4087 | 50.0563
2022-06-22 | 9:02 | 50.026 | 44734.4087 | 50.0564
2022-06-22 | 9:02 | 50.024 | 44734.4087 | 50.0565
2022-06-22 | 9:02 | 50.023 | 44734.4087 | 50.0565
2022-06-22 | 9:02 | 50.024 | 44734.4087 | 50.0566
2022-06-22 | 9:02 | 50.025 | 44734.4087 | 50.0567
2022-06-22 | 9:02 | 50.025 | 44734.4087 | 50.0567
2022-06-22 | 9:02 | 50.025 | 44734.4087 | 50.0568
2022-06-22 | 9:02 | 50.03 | 44734.4087 | 50.0568
2022-06-22 | 9:02 | 50.032 | 44734.4087 | 50.0569
2022-06-22 | 9:02 | 50.032 | 44734.4087 | 50.0569
2022-06-22 | 9:02 | 50.035 | 44734.4087 | 50.0569
2022-06-22 | 9:02 | 50.036 | 44734.4087 | 50.0569
2022-06-22 | 9:02 | 50.04 | 44734.4087 | 50.0569
2022-06-22 | 9:02 | 50.043 | 44734.4087 | 50.0568
2022-06-22 | 9:02 | 50.045 | 44734.4087 | 50.0568
2022-06-22 | 9:02 | 50.044 | 44734.4087 | 50.0569
2022-06-22 | 9:02 | 50.047 | 44734.4087 | 50.0568
2022-06-22 | 9:02 | 50.045 | 44734.4087 | 50.0568
2022-06-22 | 9:02 | 50.042 | 44734.4087 | 50.0569
2022-06-22 | 9:02 | 50.041 | 2022-06-22 09:49 | 50.057
2022-06-22 | 9:02 | 50.038 | 44734.4087 | 50.0571
2022-06-22 | 9:02 | 50.032 | 44734.4087 | 50.0573
2022-06-22 | 9:02 | 50.026 | 44734.4087 | 50.0574
2022-06-22 | 9:02 | 50.021 | 44734.4087 | 50.0576
2022-06-22 | 9:02 | 50.014 | 44734.4087 | 50.0577
2022-06-22 | 9:02 | 50.013 | 44734.4087 | 50.0578
2022-06-22 | 9:02 | 50.012 | 44734.4087 | 50.0578
2022-06-22 | 9:02 | 50.01 | 44734.4087 | 50.0579
2022-06-22 | 9:02 | 50.011 | 44734.4087 | 50.0579
2022-06-22 | 9:02 | 50.015 | 44734.4087 | 50.058
2022-06-22 | 9:02 | 50.017 | 44734.4087 | 50.058
2022-06-22 | 9:02 | 50.021 | 44734.4087 | 50.058
2022-06-22 | 9:02 | 50.029 | 44734.4087 | 50.0581
2022-06-22 | 9:02 | 50.036 | 44734.4087 | 50.0581
2022-06-22 | 9:02 | 50.041 | 44734.4087 | 50.0582
2022-06-22 | 9:02 | 50.044 | 44734.4087 | 50.0582
2022-06-22 | 9:02 | 50.045 | 44734.4087 | 50.0583
2022-06-22 | 9:02 | 50.047 | 44734.4087 | 50.0584
2022-06-22 | 9:02 | 50.045 | 44734.4087 | 50.0585
2022-06-22 | 9:02 | 50.042 | 44734.4087 | 50.0586
2022-06-22 | 9:03 | 50.039 | 44734.4087 | 50.0587
2022-06-22 | 9:03 | 50.035 | 44734.4087 | 50.0588
2022-06-22 | 9:03 | 50.03 | 44734.4087 | 50.0589
2022-06-22 | 9:03 | 50.027 | 44734.4087 | 50.059
2022-06-22 | 9:03 | 50.025 | 44734.4087 | 50.0591
2022-06-22 | 9:03 | 50.023 | 44734.4087 | 50.0592
2022-06-22 | 9:03 | 50.021 | 44734.4087 | 50.0592
2022-06-22 | 9:03 | 50.02 | 44734.4087 | 50.0592
2022-06-22 | 9:03 | 50.018 | 44734.4087 | 50.0592
2022-06-22 | 9:03 | 50.018 | 44734.4087 | 50.0592
2022-06-22 | 9:03 | 50.017 | 44734.4087 | 50.0593
2022-06-22 | 9:03 | 50.014 | 44734.4087 | 50.0593
2022-06-22 | 9:03 | 50.016 | 44734.4087 | 50.0593
2022-06-22 | 9:03 | 50.014 | 44734.4087 | 50.0594
2022-06-22 | 9:03 | 50.013 | 44734.4087 | 50.0594
2022-06-22 | 9:03 | 50.013 | 44734.4087 | 50.0594
2022-06-22 | 9:03 | 50.009 | 44734.4087 | 50.0594
2022-06-22 | 9:03 | 50.007 | 44734.4087 | 50.0595
2022-06-22 | 9:03 | 50.006 | 44734.4087 | 50.0595
2022-06-22 | 9:03 | 50.005 | 44734.4087 | 50.0595
2022-06-22 | 9:03 | 50.007 | 44734.4087 | 50.0595
2022-06-22 | 9:03 | 50.008 | 44734.4087 | 50.0596
2022-06-22 | 9:03 | 50.008 | 44734.4087 | 50.0596
2022-06-22 | 9:03 | 50.008 | 44734.4087 | 50.0596
2022-06-22 | 9:03 | 50.009 | 44734.4087 | 50.0595
2022-06-22 | 9:03 | 50.007 | 44734.4087 | 50.0595
2022-06-22 | 9:03 | 50.008 | 44734.4087 | 50.0595
2022-06-22 | 9:03 | 50.007 | 44734.4087 | 50.0595
2022-06-22 | 9:03 | 50.005 | 44734.4087 | 50.0595
2022-06-22 | 9:03 | 50.003 | 2022-06-22 09:49 | 50.0595
|  |  | 44734.4087 | 50.0595
|  |  | 44734.4087 | 50.0595
|  |  | 44734.4087 | 50.0596
|  |  | 44734.4087 | 50.0596
|  |  | 44734.4087 | 50.0597
|  |  | 44734.4087 | 50.0597
|  |  | 44734.4087 | 50.0598
|  |  | 44734.4087 | 50.0599
|  |  | 44734.4087 | 50.06
|  |  | 44734.4087 | 50.06
|  |  | 44734.4087 | 50.06
|  |  | 44734.4087 | 50.0601
|  |  | 44734.4087 | 50.0601
|  |  | 44734.4087 | 50.0601
|  |  | 44734.4087 | 50.0601
|  |  | 44734.4087 | 50.0601
|  |  | 44734.4087 | 50.0601
|  |  | 44734.4087 | 50.0602
|  |  | 44734.4087 | 50.0602
|  |  | 44734.4087 | 50.0602
|  |  | 44734.4087 | 50.0602
|  |  | 44734.4087 | 50.0603
|  |  | 44734.4087 | 50.0603
|  |  | 44734.4087 | 50.0603
|  |  | 44734.4087 | 50.0604
|  |  | 44734.4087 | 50.0605
|  |  | 44734.4087 | 50.0606
|  |  | 44734.4087 | 50.0607
|  |  | 44734.4087 | 50.0608
|  |  | 44734.4087 | 50.0609
|  |  | 44734.4087 | 50.061
|  |  | 44734.4087 | 50.0611
|  |  | 44734.4087 | 50.0611
|  |  | 44734.4087 | 50.0612
|  |  | 44734.4087 | 50.0612
|  |  | 44734.4087 | 50.0612
|  |  | 44734.4087 | 50.0612
|  |  | 44734.4087 | 50.0613
|  |  | 44734.4087 | 50.0613
|  |  | 44734.4087 | 50.0613
|  |  | 44734.4087 | 50.0613
|  |  | 44734.4087 | 50.0614
|  |  | 44734.4087 | 50.0614
|  |  | 44734.4087 | 50.0614
|  |  | 44734.4087 | 50.0614
|  |  | 44734.4087 | 50.0614
|  |  | 44734.4087 | 50.0614
|  |  | 44734.4087 | 50.0614
|  |  | 44734.4087 | 50.0615
|  |  | 2022-06-22 09:49 | 50.0615
|  |  | 44734.4087 | 50.0615
|  |  | 44734.4087 | 50.0615
|  |  | 44734.4087 | 50.0614
|  |  | 44734.4087 | 50.0614
|  |  | 44734.4087 | 50.0614
|  |  | 44734.4087 | 50.0613
|  |  | 44734.4087 | 50.0613
|  |  | 44734.4087 | 50.0613
|  |  | 44734.4087 | 50.0613
|  |  | 44734.4087 | 50.0613
|  |  | 44734.4087 | 50.0613
|  |  | 44734.4087 | 50.0613
|  |  | 44734.4087 | 50.0614
|  |  | 44734.4087 | 50.0615
|  |  | 44734.4087 | 50.0616
|  |  | 44734.4087 | 50.0617
|  |  | 44734.4087 | 50.0618
|  |  | 44734.4087 | 50.0619
|  |  | 44734.4087 | 50.0619
|  |  | 44734.4087 | 50.0621
|  |  | 44734.4087 | 50.0621
|  |  | 44734.4087 | 50.0621
|  |  | 44734.4087 | 50.0621
|  |  | 44734.4087 | 50.0621
|  |  | 44734.4087 | 50.0621
|  |  | 44734.4087 | 50.0622
|  |  | 44734.4087 | 50.0622
|  |  | 44734.4087 | 50.0622
|  |  | 44734.4087 | 50.0622
|  |  | 44734.4087 | 50.0623
|  |  | 44734.4087 | 50.0624
|  |  | 44734.4087 | 50.0624
|  |  | 44734.4087 | 50.0625
|  |  | 44734.4087 | 50.0626
|  |  | 44734.4087 | 50.0627
|  |  | 44734.4087 | 50.0628
|  |  | 44734.4087 | 50.0629
|  |  | 44734.4087 | 50.063
|  |  | 44734.4087 | 50.0631
|  |  | 44734.4087 | 50.0631
|  |  | 44734.4087 | 50.0632
|  |  | 44734.4087 | 50.0633
|  |  | 44734.4087 | 50.0632
|  |  | 44734.4087 | 50.0632
|  |  | 44734.4087 | 50.0631
|  |  | 44734.4087 | 50.063
|  |  | 44734.4087 | 50.0629
|  |  | 44734.4087 | 50.0628
|  |  | 44734.4087 | 50.0627
|  |  | 2022-06-22 09:49 | 50.0627
|  |  | 44734.4087 | 50.0626
|  |  | 44734.4087 | 50.0626
|  |  | 44734.4087 | 50.0627
|  |  | 44734.4087 | 50.0627
|  |  | 44734.4087 | 50.0628
|  |  | 44734.4087 | 50.0629
|  |  | 44734.4087 | 50.063
|  |  | 44734.4087 | 50.063
|  |  | 44734.4087 | 50.0631
|  |  | 44734.4087 | 50.0631
|  |  | 44734.4087 | 50.0632
|  |  | 44734.4087 | 50.0631
|  |  | 44734.4087 | 50.0631
|  |  | 44734.4087 | 50.063
|  |  | 44734.4087 | 50.063
|  |  | 44734.4087 | 50.0629
|  |  | 44734.4087 | 50.0628
|  |  | 44734.4087 | 50.0628
|  |  | 44734.4087 | 50.0628
|  |  | 44734.4087 | 50.0628
|  |  | 44734.4087 | 50.0628
|  |  | 44734.4087 | 50.0629
|  |  | 44734.4087 | 50.0628
|  |  | 44734.4087 | 50.0628
|  |  | 44734.4087 | 50.0629
|  |  | 44734.4087 | 50.063
|  |  | 44734.4087 | 50.063
|  |  | 44734.4087 | 50.063
|  |  | 44734.4087 | 50.063
|  |  | 44734.4087 | 50.0629
|  |  | 44734.4087 | 50.0629
|  |  | 44734.4087 | 50.0629
|  |  | 44734.4087 | 50.0628
|  |  | 44734.4087 | 50.0628
|  |  | 44734.4087 | 50.0628
|  |  | 44734.4087 | 50.0628
|  |  | 44734.4087 | 50.0628
|  |  | 44734.4087 | 50.0628
|  |  | 44734.4087 | 50.0628
|  |  | 44734.4087 | 50.0628
|  |  | 44734.4087 | 50.0628
|  |  | 44734.4087 | 50.0628
|  |  | 44734.4087 | 50.0628
|  |  | 44734.4087 | 50.0628
|  |  | 44734.4087 | 50.0628
|  |  | 44734.4087 | 50.0627
|  |  | 44734.4087 | 50.0626
|  |  | 44734.4087 | 50.0626
|  |  | 44734.4087 | 50.0626
|  |  | 2022-06-22 09:49 | 50.0626
|  |  | 44734.4088 | 50.0627
|  |  | 44734.4088 | 50.0627
|  |  | 44734.4088 | 50.0627
|  |  | 44734.4088 | 50.0627
|  |  | 44734.4088 | 50.0626
|  |  | 44734.4088 | 50.0626
|  |  | 44734.4088 | 50.0625
|  |  | 44734.4088 | 50.0625
|  |  | 44734.4088 | 50.0625
|  |  | 44734.4088 | 50.0624
|  |  | 44734.4088 | 50.0625
|  |  | 44734.4088 | 50.0624
|  |  | 44734.4088 | 50.0623
|  |  | 44734.4088 | 50.0622
|  |  | 44734.4088 | 50.0622
|  |  | 44734.4088 | 50.0621
|  |  | 44734.4088 | 50.062
|  |  | 44734.4088 | 50.062
|  |  | 44734.4088 | 50.062
|  |  | 44734.4088 | 50.062
|  |  | 44734.4088 | 50.062
|  |  | 44734.4088 | 50.062
|  |  | 44734.4088 | 50.062
|  |  | 44734.4088 | 50.062
|  |  | 44734.4088 | 50.0621
|  |  | 44734.4088 | 50.0621
|  |  | 44734.4088 | 50.0622
|  |  | 44734.4088 | 50.062
|  |  | 44734.4088 | 50.062
|  |  | 44734.4088 | 50.0621
|  |  | 44734.4088 | 50.062
|  |  | 44734.4088 | 50.062
|  |  | 44734.4088 | 50.0619
|  |  | 44734.4088 | 50.0618
|  |  | 44734.4088 | 50.0618
|  |  | 44734.4088 | 50.0617
|  |  | 44734.4088 | 50.0616
|  |  | 44734.4088 | 50.0615
|  |  | 44734.4088 | 50.0615
|  |  | 44734.4088 | 50.0615
|  |  | 44734.4088 | 50.0616
|  |  | 44734.4088 | 50.0616
|  |  | 44734.4088 | 50.0616
|  |  | 44734.4088 | 50.0616
|  |  | 44734.4088 | 50.0616
|  |  | 44734.4088 | 50.0616
|  |  | 44734.4088 | 50.0616
|  |  | 44734.4088 | 50.0615
|  |  | 44734.4088 | 50.0614
|  |  | 2022-06-22 09:49 | 50.0614
|  |  | 44734.4088 | 50.0613
|  |  | 44734.4088 | 50.0613
|  |  | 44734.4088 | 50.0613
|  |  | 44734.4088 | 50.0614
|  |  | 44734.4088 | 50.0614
|  |  | 44734.4088 | 50.0615
|  |  | 44734.4088 | 50.0615
|  |  | 44734.4088 | 50.0614
|  |  | 44734.4088 | 50.0614
|  |  | 44734.4088 | 50.0614
|  |  | 44734.4088 | 50.0614
|  |  | 44734.4088 | 50.0614
|  |  | 44734.4088 | 50.0614
|  |  | 44734.4088 | 50.0614
|  |  | 44734.4088 | 50.0614
|  |  | 44734.4088 | 50.0614
|  |  | 44734.4088 | 50.0614
|  |  | 44734.4088 | 50.0613
|  |  | 44734.4088 | 50.0613
|  |  | 44734.4088 | 50.0613
|  |  | 44734.4088 | 50.0611
|  |  | 44734.4088 | 50.061
|  |  | 44734.4088 | 50.061
|  |  | 44734.4088 | 50.0609
|  |  | 44734.4088 | 50.0609
|  |  | 44734.4088 | 50.0608
|  |  | 44734.4088 | 50.0608
|  |  | 44734.4088 | 50.0608
|  |  | 44734.4088 | 50.0608
|  |  | 44734.4088 | 50.0608
|  |  | 44734.4088 | 50.0608
|  |  | 44734.4088 | 50.0607
|  |  | 44734.4088 | 50.0606
|  |  | 44734.4088 | 50.0605
|  |  | 44734.4088 | 50.0604
|  |  | 44734.4088 | 50.0604
|  |  | 44734.4088 | 50.0603
|  |  | 44734.4088 | 50.0603
|  |  | 44734.4088 | 50.0604
|  |  | 44734.4088 | 50.0604
|  |  | 44734.4088 | 50.0604
|  |  | 44734.4088 | 50.0603
|  |  | 44734.4088 | 50.0603
|  |  | 44734.4088 | 50.0602
|  |  | 44734.4088 | 50.0601
|  |  | 44734.4088 | 50.0601
|  |  | 44734.4088 | 50.06
|  |  | 44734.4088 | 50.0599
|  |  | 44734.4088 | 50.0598
|  |  | 2022-06-22 09:49 | 50.0597
|  |  | 44734.4088 | 50.0597
|  |  | 44734.4088 | 50.0596
|  |  | 44734.4088 | 50.0595
|  |  | 44734.4088 | 50.0595
|  |  | 44734.4088 | 50.0595
|  |  | 44734.4088 | 50.0593
|  |  | 44734.4088 | 50.0593
|  |  | 44734.4088 | 50.0594
|  |  | 44734.4088 | 50.0594
|  |  | 44734.4088 | 50.0594
|  |  | 44734.4088 | 50.0594
|  |  | 44734.4088 | 50.0594
|  |  | 44734.4088 | 50.0594
|  |  | 44734.4088 | 50.0595
|  |  | 44734.4088 | 50.0594
|  |  | 44734.4088 | 50.0594
|  |  | 44734.4088 | 50.0594
|  |  | 44734.4088 | 50.0594
|  |  | 44734.4088 | 50.0594
|  |  | 44734.4088 | 50.0593
|  |  | 44734.4088 | 50.0593
|  |  | 44734.4088 | 50.0593
|  |  | 44734.4088 | 50.0591
|  |  | 44734.4088 | 50.0591
|  |  | 44734.4088 | 50.0591
|  |  | 44734.4088 | 50.0592
|  |  | 44734.4088 | 50.0593
|  |  | 44734.4088 | 50.0592
|  |  | 44734.4088 | 50.0593
|  |  | 44734.4088 | 50.0593
|  |  | 44734.4088 | 50.0592
|  |  | 44734.4088 | 50.0592
|  |  | 44734.4088 | 50.0591
|  |  | 44734.4088 | 50.0591
|  |  | 44734.4088 | 50.0589
|  |  | 44734.4088 | 50.0588
|  |  | 44734.4088 | 50.0588
|  |  | 44734.4088 | 50.0587
|  |  | 44734.4088 | 50.0587
|  |  | 44734.4088 | 50.0587
|  |  | 44734.4088 | 50.0588
|  |  | 44734.4088 | 50.0588
|  |  | 44734.4088 | 50.0588
|  |  | 44734.4088 | 50.0589
|  |  | 44734.4088 | 50.0589
|  |  | 44734.4088 | 50.0589
|  |  | 44734.4088 | 50.0589
|  |  | 44734.4088 | 50.0589
|  |  | 44734.4088 | 50.059
|  |  | 2022-06-22 09:49 | 50.059
|  |  | 44734.4088 | 50.0589
|  |  | 44734.4088 | 50.0589
|  |  | 44734.4088 | 50.0589
|  |  | 44734.4088 | 50.0588
|  |  | 44734.4088 | 50.0588
|  |  | 44734.4088 | 50.0587
|  |  | 44734.4088 | 50.0587
|  |  | 44734.4088 | 50.0586
|  |  | 44734.4088 | 50.0586
|  |  | 44734.4088 | 50.0585
|  |  | 44734.4088 | 50.0585
|  |  | 44734.4088 | 50.0585
|  |  | 44734.4088 | 50.0584
|  |  | 44734.4088 | 50.0584
|  |  | 44734.4088 | 50.0584
|  |  | 44734.4088 | 50.0583
|  |  | 44734.4088 | 50.0583
|  |  | 44734.4088 | 50.0582
|  |  | 44734.4088 | 50.058
|  |  | 44734.4088 | 50.0579
|  |  | 44734.4088 | 50.0577
|  |  | 44734.4088 | 50.0575
|  |  | 44734.4088 | 50.0573
|  |  | 44734.4088 | 50.0571
|  |  | 44734.4088 | 50.0569
|  |  | 44734.4088 | 50.0568
|  |  | 44734.4088 | 50.0566
|  |  | 44734.4088 | 50.0563
|  |  | 44734.4088 | 50.0561
|  |  | 44734.4088 | 50.0559
|  |  | 44734.4088 | 50.0557
|  |  | 44734.4088 | 50.0556
|  |  | 44734.4088 | 50.0554
|  |  | 44734.4088 | 50.0552
|  |  | 44734.4088 | 50.0551
|  |  | 44734.4088 | 50.0549
|  |  | 44734.4088 | 50.0546
|  |  | 44734.4088 | 50.0544
|  |  | 44734.4088 | 50.0541
|  |  | 44734.4088 | 50.0538
|  |  | 44734.4088 | 50.0535
|  |  | 44734.4088 | 50.0532
|  |  | 44734.4088 | 50.0529
|  |  | 44734.4088 | 50.0527
|  |  | 44734.4088 | 50.0524
|  |  | 44734.4088 | 50.0521
|  |  | 44734.4088 | 50.0519
|  |  | 44734.4088 | 50.0516
|  |  | 44734.4088 | 50.0513
|  |  | 2022-06-22 09:49 | 50.0511
|  |  | 44734.4088 | 50.0507
|  |  | 44734.4088 | 50.0503
|  |  | 44734.4088 | 50.0498
|  |  | 44734.4088 | 50.0492
|  |  | 44734.4088 | 50.0486
|  |  | 44734.4088 | 50.048
|  |  | 44734.4088 | 50.0473
|  |  | 44734.4088 | 50.0466
|  |  | 44734.4088 | 50.0459
|  |  | 44734.4088 | 50.0451
|  |  | 44734.4088 | 50.0444
|  |  | 44734.4088 | 50.0437
|  |  | 44734.4088 | 50.043
|  |  | 44734.4088 | 50.0422
|  |  | 44734.4088 | 50.0415
|  |  | 44734.4088 | 50.0408
|  |  | 44734.4088 | 50.0401
|  |  | 44734.4088 | 50.039
|  |  | 44734.4088 | 50.0383
|  |  | 44734.4088 | 50.0375
|  |  | 44734.4088 | 50.0368
|  |  | 44734.4088 | 50.0361
|  |  | 44734.4088 | 50.0353
|  |  | 44734.4088 | 50.0346
|  |  | 44734.4088 | 50.0338
|  |  | 44734.4088 | 50.0331
|  |  | 44734.4088 | 50.0323
|  |  | 44734.4088 | 50.0316
|  |  | 44734.4088 | 50.0309
|  |  | 44734.4088 | 50.03
|  |  | 44734.4088 | 50.0293
|  |  | 44734.4088 | 50.0287
|  |  | 44734.4088 | 50.0281
|  |  | 44734.4088 | 50.0275
|  |  | 44734.4088 | 50.027
|  |  | 44734.4088 | 50.0264
|  |  | 44734.4088 | 50.0259
|  |  | 44734.4088 | 50.0254
|  |  | 44734.4088 | 50.0252
|  |  | 44734.4088 | 50.0248
|  |  | 44734.4088 | 50.0242
|  |  | 44734.4088 | 50.0238
|  |  | 44734.4088 | 50.0233
|  |  | 44734.4088 | 50.0227
|  |  | 44734.4088 | 50.0222
|  |  | 44734.4088 | 50.0217
|  |  | 44734.4088 | 50.0212
|  |  | 44734.4088 | 50.0206
|  |  | 44734.4088 | 50.0202
|  |  | 2022-06-22 09:49 | 50.0196
|  |  | 44734.4088 | 50.019
|  |  | 44734.4088 | 50.0184
|  |  | 44734.4088 | 50.0178
|  |  | 44734.4088 | 50.0172
|  |  | 44734.4088 | 50.0166
|  |  | 44734.4088 | 50.016
|  |  | 44734.4088 | 50.0153
|  |  | 44734.4088 | 50.0147
|  |  | 44734.4088 | 50.014
|  |  | 44734.4088 | 50.0134
|  |  | 44734.4088 | 50.0127
|  |  | 44734.4088 | 50.0121
|  |  | 44734.4088 | 50.0114
|  |  | 44734.4088 | 50.0107
|  |  | 44734.4088 | 50.01
|  |  | 44734.4088 | 50.0093
|  |  | 44734.4088 | 50.0085
|  |  | 44734.4088 | 50.0078
|  |  | 44734.4088 | 50.0072
|  |  | 44734.4088 | 50.0065
|  |  | 44734.4088 | 50.0058
|  |  | 44734.4088 | 50.0051
|  |  | 44734.4088 | 50.0043
|  |  | 44734.4088 | 50.0036
|  |  | 44734.4088 | 50.0029
|  |  | 44734.4088 | 50.0022
|  |  | 44734.4088 | 50.0015
|  |  | 44734.4088 | 50.0008
|  |  | 44734.4088 | 50.0002
|  |  | 44734.4088 | 49.9996
|  |  | 44734.4088 | 49.999
|  |  | 44734.4088 | 49.9984
|  |  | 44734.4088 | 49.9979
|  |  | 44734.4088 | 49.9973
|  |  | 44734.4088 | 49.9967
|  |  | 44734.4088 | 49.9961
|  |  | 44734.4088 | 49.9955
|  |  | 44734.4088 | 49.995
|  |  | 44734.4088 | 49.9944
|  |  | 44734.4088 | 49.9938
|  |  | 44734.4088 | 49.9932
|  |  | 44734.4088 | 49.9927
|  |  | 44734.4088 | 49.9922
|  |  | 44734.4088 | 49.9916
|  |  | 44734.4088 | 49.991
|  |  | 44734.4088 | 49.9905
|  |  | 44734.4088 | 49.9899
|  |  | 44734.4088 | 49.9894
|  |  | 44734.4088 | 49.9888
|  |  | 2022-06-22 09:49 | 49.9882
|  |  | 44734.4088 | 49.9876
|  |  | 44734.4088 | 49.987
|  |  | 44734.4088 | 49.9864
|  |  | 44734.4088 | 49.9858
|  |  | 44734.4088 | 49.9854
|  |  | 44734.4088 | 49.9848
|  |  | 44734.4088 | 49.9843
|  |  | 44734.4088 | 49.9838
|  |  | 44734.4088 | 49.9833
|  |  | 44734.4088 | 49.9828
|  |  | 44734.4088 | 49.9823
|  |  | 44734.4088 | 49.9818
|  |  | 44734.4088 | 49.9813
|  |  | 44734.4088 | 49.9809
|  |  | 44734.4088 | 49.9804
|  |  | 44734.4088 | 49.9799
|  |  | 44734.4088 | 49.9795
|  |  | 44734.4088 | 49.9791
|  |  | 44734.4088 | 49.9787
|  |  | 44734.4088 | 49.9782
|  |  | 44734.4088 | 49.9776
|  |  | 44734.4088 | 49.9771
|  |  | 44734.4088 | 49.9766
|  |  | 44734.4088 | 49.9761
|  |  | 44734.4088 | 49.9756
|  |  | 44734.4088 | 49.9751
|  |  | 44734.4088 | 49.9746
|  |  | 44734.4088 | 49.9741
|  |  | 44734.4088 | 49.9737
|  |  | 44734.4088 | 49.9732
|  |  | 44734.4088 | 49.9726
|  |  | 44734.4088 | 49.9721
|  |  | 44734.4088 | 49.9716
|  |  | 44734.4088 | 49.9712
|  |  | 44734.4088 | 49.9707
|  |  | 44734.4088 | 49.9702
|  |  | 44734.4088 | 49.9697
|  |  | 44734.4088 | 49.9692
|  |  | 44734.4088 | 49.9687
|  |  | 44734.4088 | 49.9682
|  |  | 44734.4088 | 49.9677
|  |  | 44734.4088 | 49.9672
|  |  | 44734.4088 | 49.9667
|  |  | 44734.4088 | 49.9661
|  |  | 44734.4088 | 49.9656
|  |  | 44734.4088 | 49.965
|  |  | 44734.4088 | 49.9645
|  |  | 44734.4088 | 49.9639
|  |  | 44734.4088 | 49.9633
|  |  | 2022-06-22 09:49 | 49.9628
|  |  | 44734.4088 | 49.9623
|  |  | 44734.4088 | 49.9618
|  |  | 44734.4088 | 49.9613
|  |  | 44734.4088 | 49.9609
|  |  | 44734.4088 | 49.9605
|  |  | 44734.4088 | 49.9601
|  |  | 44734.4088 | 49.9598
|  |  | 44734.4088 | 49.9596
|  |  | 44734.4088 | 49.9593
|  |  | 44734.4088 | 49.9591
|  |  | 44734.4088 | 49.9588
|  |  | 44734.4088 | 49.9585
|  |  | 44734.4088 | 49.9582
|  |  | 44734.4088 | 49.9579
|  |  | 44734.4088 | 49.9576
|  |  | 44734.4088 | 49.9572
|  |  | 44734.4088 | 49.9569
|  |  | 44734.4088 | 49.9565
|  |  | 44734.4088 | 49.9561
|  |  | 44734.4088 | 49.9558
|  |  | 44734.4088 | 49.9555
|  |  | 44734.4088 | 49.9553
|  |  | 44734.4088 | 49.955
|  |  | 44734.4088 | 49.9548
|  |  | 44734.4088 | 49.9546
|  |  | 44734.4088 | 49.9543
|  |  | 44734.4088 | 49.9541
|  |  | 44734.4088 | 49.9538
|  |  | 44734.4088 | 49.9536
|  |  | 44734.4088 | 49.9533
|  |  | 44734.4088 | 49.953
|  |  | 44734.4088 | 49.9527
|  |  | 44734.4088 | 49.9523
|  |  | 44734.4088 | 49.9519
|  |  | 44734.4088 | 49.9515
|  |  | 44734.4088 | 49.9511
|  |  | 44734.4088 | 49.9507
|  |  | 44734.4088 | 49.9503
|  |  | 44734.4088 | 49.9499
|  |  | 44734.4088 | 49.9496
|  |  | 44734.4088 | 49.9492
|  |  | 44734.4088 | 49.9489
|  |  | 44734.4088 | 49.9485
|  |  | 44734.4088 | 49.9481
|  |  | 44734.4088 | 49.9478
|  |  | 44734.4088 | 49.9474
|  |  | 44734.4088 | 49.9471
|  |  | 44734.4088 | 49.9466
|  |  | 44734.4088 | 49.9462
|  |  | 2022-06-22 09:49 | 49.9459
|  |  | 44734.4088 | 49.9455
|  |  | 44734.4088 | 49.9451
|  |  | 44734.4088 | 49.9449
|  |  | 44734.4088 | 49.9446
|  |  | 44734.4088 | 49.9444
|  |  | 44734.4088 | 49.9441
|  |  | 44734.4088 | 49.9439
|  |  | 44734.4088 | 49.9437
|  |  | 44734.4088 | 49.9435
|  |  | 44734.4088 | 49.9433
|  |  | 44734.4088 | 49.943
|  |  | 44734.4088 | 49.9429
|  |  | 44734.4088 | 49.9427
|  |  | 44734.4088 | 49.9425
|  |  | 44734.4088 | 49.9423
|  |  | 44734.4088 | 49.9421
|  |  | 44734.4088 | 49.9418
|  |  | 44734.4088 | 49.9416
|  |  | 44734.4088 | 49.9413
|  |  | 44734.4088 | 49.941
|  |  | 44734.4088 | 49.9408
|  |  | 44734.4088 | 49.9406
|  |  | 44734.4088 | 49.9403
|  |  | 44734.4088 | 49.9401
|  |  | 44734.4088 | 49.9399
|  |  | 44734.4088 | 49.9397
|  |  | 44734.4088 | 49.9395
|  |  | 44734.4088 | 49.9393
|  |  | 44734.4088 | 49.939
|  |  | 44734.4088 | 49.9389
|  |  | 44734.4088 | 49.9386
|  |  | 44734.4088 | 49.9384
|  |  | 44734.4089 | 49.9381
|  |  | 44734.4089 | 49.9378
|  |  | 44734.4089 | 49.9375
|  |  | 44734.4089 | 49.9373
|  |  | 44734.4089 | 49.937
|  |  | 44734.4089 | 49.9368
|  |  | 44734.4089 | 49.9365
|  |  | 44734.4089 | 49.9364
|  |  | 44734.4089 | 49.9362
|  |  | 44734.4089 | 49.936
|  |  | 44734.4089 | 49.9359
|  |  | 44734.4089 | 49.9357
|  |  | 44734.4089 | 49.9354
|  |  | 44734.4089 | 49.9352
|  |  | 44734.4089 | 49.9349
|  |  | 44734.4089 | 49.9347
|  |  | 44734.4089 | 49.9345
|  |  | 2022-06-22 09:49 | 49.9343
|  |  | 44734.4089 | 49.9341
|  |  | 44734.4089 | 49.9338
|  |  | 44734.4089 | 49.9336
|  |  | 44734.4089 | 49.9334
|  |  | 44734.4089 | 49.9331
|  |  | 44734.4089 | 49.9329
|  |  | 44734.4089 | 49.9327
|  |  | 44734.4089 | 49.9326
|  |  | 44734.4089 | 49.9324
|  |  | 44734.4089 | 49.9322
|  |  | 44734.4089 | 49.932
|  |  | 44734.4089 | 49.9319
|  |  | 44734.4089 | 49.9317
|  |  | 44734.4089 | 49.9315
|  |  | 44734.4089 | 49.9313
|  |  | 44734.4089 | 49.9312
|  |  | 44734.4089 | 49.931
|  |  | 44734.4089 | 49.9309
|  |  | 44734.4089 | 49.9307
|  |  | 44734.4089 | 49.9304
|  |  | 44734.4089 | 49.9302
|  |  | 44734.4089 | 49.93
|  |  | 44734.4089 | 49.9298
|  |  | 44734.4089 | 49.9296
|  |  | 44734.4089 | 49.9293
|  |  | 44734.4089 | 49.9292
|  |  | 44734.4089 | 49.929
|  |  | 44734.4089 | 49.9287
|  |  | 44734.4089 | 49.9285
|  |  | 44734.4089 | 49.9283
|  |  | 44734.4089 | 49.9281
|  |  | 44734.4089 | 49.928
|  |  | 44734.4089 | 49.9278
|  |  | 44734.4089 | 49.9276
|  |  | 44734.4089 | 49.9274
|  |  | 44734.4089 | 49.9273
|  |  | 44734.4089 | 49.9271
|  |  | 44734.4089 | 49.9269
|  |  | 44734.4089 | 49.9266
|  |  | 44734.4089 | 49.9265
|  |  | 44734.4089 | 49.9263
|  |  | 44734.4089 | 49.9261
|  |  | 44734.4089 | 49.9259
|  |  | 44734.4089 | 49.9256
|  |  | 44734.4089 | 49.9255
|  |  | 44734.4089 | 49.9252
|  |  | 44734.4089 | 49.9251
|  |  | 44734.4089 | 49.9249
|  |  | 44734.4089 | 49.9247
|  |  | 2022-06-22 09:49 | 49.9245
|  |  | 44734.4089 | 49.9243
|  |  | 44734.4089 | 49.9241
|  |  | 44734.4089 | 49.9239
|  |  | 44734.4089 | 49.9238
|  |  | 44734.4089 | 49.9236
|  |  | 44734.4089 | 49.9234
|  |  | 44734.4089 | 49.9232
|  |  | 44734.4089 | 49.9231
|  |  | 44734.4089 | 49.9229
|  |  | 44734.4089 | 49.9227
|  |  | 44734.4089 | 49.9224
|  |  | 44734.4089 | 49.9222
|  |  | 44734.4089 | 49.922
|  |  | 44734.4089 | 49.9217
|  |  | 44734.4089 | 49.9215
|  |  | 44734.4089 | 49.9213
|  |  | 44734.4089 | 49.9211
|  |  | 44734.4089 | 49.9209
|  |  | 44734.4089 | 49.9207
|  |  | 44734.4089 | 49.9206
|  |  | 44734.4089 | 49.9204
|  |  | 44734.4089 | 49.9203
|  |  | 44734.4089 | 49.9202
|  |  | 44734.4089 | 49.92
|  |  | 44734.4089 | 49.9198
|  |  | 44734.4089 | 49.9197
|  |  | 44734.4089 | 49.9195
|  |  | 44734.4089 | 49.9194
|  |  | 44734.4089 | 49.9192
|  |  | 44734.4089 | 49.919
|  |  | 44734.4089 | 49.9188
|  |  | 44734.4089 | 49.9186
|  |  | 44734.4089 | 49.9185
|  |  | 44734.4089 | 49.9184
|  |  | 44734.4089 | 49.9183
|  |  | 44734.4089 | 49.9182
|  |  | 44734.4089 | 49.9181
|  |  | 44734.4089 | 49.918
|  |  | 44734.4089 | 49.9179
|  |  | 44734.4089 | 49.9179
|  |  | 44734.4089 | 49.9178
|  |  | 44734.4089 | 49.9177
|  |  | 44734.4089 | 49.9175
|  |  | 44734.4089 | 49.9173
|  |  | 44734.4089 | 49.9171
|  |  | 44734.4089 | 49.9169
|  |  | 44734.4089 | 49.9168
|  |  | 44734.4089 | 49.9166
|  |  | 44734.4089 | 49.9164
|  |  | 2022-06-22 09:49 | 49.9162
|  |  | 44734.4089 | 49.916
|  |  | 44734.4089 | 49.9158
|  |  | 44734.4089 | 49.9157
|  |  | 44734.4089 | 49.9156
|  |  | 44734.4089 | 49.9154
|  |  | 44734.4089 | 49.9153
|  |  | 44734.4089 | 49.9152
|  |  | 44734.4089 | 49.9151
|  |  | 44734.4089 | 49.9149
|  |  | 44734.4089 | 49.9148
|  |  | 44734.4089 | 49.9146
|  |  | 44734.4089 | 49.9144
|  |  | 44734.4089 | 49.9142
|  |  | 44734.4089 | 49.914
|  |  | 44734.4089 | 49.9138
|  |  | 44734.4089 | 49.9137
|  |  | 44734.4089 | 49.9135
|  |  | 44734.4089 | 49.9134
|  |  | 44734.4089 | 49.9132
|  |  | 44734.4089 | 49.9131
|  |  | 44734.4089 | 49.913
|  |  | 44734.4089 | 49.9129
|  |  | 44734.4089 | 49.9128
|  |  | 44734.4089 | 49.9127
|  |  | 44734.4089 | 49.9126
|  |  | 44734.4089 | 49.9125
|  |  | 44734.4089 | 49.9124
|  |  | 44734.4089 | 49.9123
|  |  | 44734.4089 | 49.9122
|  |  | 44734.4089 | 49.9122
|  |  | 44734.4089 | 49.9121
|  |  | 44734.4089 | 49.912
|  |  | 44734.4089 | 49.9119
|  |  | 44734.4089 | 49.9119
|  |  | 44734.4089 | 49.9118
|  |  | 44734.4089 | 49.9117
|  |  | 44734.4089 | 49.9117
|  |  | 44734.4089 | 49.9116
|  |  | 44734.4089 | 49.9116
|  |  | 44734.4089 | 49.9115
|  |  | 44734.4089 | 49.9114
|  |  | 44734.4089 | 49.9114
|  |  | 44734.4089 | 49.9113
|  |  | 44734.4089 | 49.9113
|  |  | 44734.4089 | 49.9112
|  |  | 44734.4089 | 49.9111
|  |  | 44734.4089 | 49.911
|  |  | 44734.4089 | 49.9108
|  |  | 44734.4089 | 49.9108
|  |  | 2022-06-22 09:49 | 49.9107
|  |  | 44734.4089 | 49.9106
|  |  | 44734.4089 | 49.9105
|  |  | 44734.4089 | 49.9105
|  |  | 44734.4089 | 49.9104
|  |  | 44734.4089 | 49.9103
|  |  | 44734.4089 | 49.9102
|  |  | 44734.4089 | 49.9101
|  |  | 44734.4089 | 49.91
|  |  | 44734.4089 | 49.9099
|  |  | 44734.4089 | 49.9099
|  |  | 44734.4089 | 49.9098
|  |  | 44734.4089 | 49.9097
|  |  | 44734.4089 | 49.9097
|  |  | 44734.4089 | 49.9096
|  |  | 44734.4089 | 49.9095
|  |  | 44734.4089 | 49.9094
|  |  | 44734.4089 | 49.9094
|  |  | 44734.4089 | 49.9093
|  |  | 44734.4089 | 49.9092
|  |  | 44734.4089 | 49.9091
|  |  | 44734.4089 | 49.9091
|  |  | 44734.4089 | 49.909
|  |  | 44734.4089 | 49.9089
|  |  | 44734.4089 | 49.9088
|  |  | 44734.4089 | 49.9088
|  |  | 44734.4089 | 49.9087
|  |  | 44734.4089 | 49.9086
|  |  | 44734.4089 | 49.9085
|  |  | 44734.4089 | 49.9085
|  |  | 44734.4089 | 49.9084
|  |  | 44734.4089 | 49.9084
|  |  | 44734.4089 | 49.9084
|  |  | 44734.4089 | 49.9083
|  |  | 44734.4089 | 49.9082
|  |  | 44734.4089 | 49.9081
|  |  | 44734.4089 | 49.908
|  |  | 44734.4089 | 49.908
|  |  | 44734.4089 | 49.9079
|  |  | 44734.4089 | 49.908
|  |  | 44734.4089 | 49.908
|  |  | 44734.4089 | 49.9079
|  |  | 44734.4089 | 49.9079
|  |  | 44734.4089 | 49.9079
|  |  | 44734.4089 | 49.9078
|  |  | 44734.4089 | 49.9077
|  |  | 44734.4089 | 49.9076
|  |  | 44734.4089 | 49.9075
|  |  | 44734.4089 | 49.9075
|  |  | 44734.4089 | 49.9075
|  |  | 2022-06-22 09:49 | 49.9074
|  |  | 44734.4089 | 49.9073
|  |  | 44734.4089 | 49.9073
|  |  | 44734.4089 | 49.9073
|  |  | 44734.4089 | 49.9073
|  |  | 44734.4089 | 49.9074
|  |  | 44734.4089 | 49.9074
|  |  | 44734.4089 | 49.9074
|  |  | 44734.4089 | 49.9074
|  |  | 44734.4089 | 49.9074
|  |  | 44734.4089 | 49.9074
|  |  | 44734.4089 | 49.9074
|  |  | 44734.4089 | 49.9073
|  |  | 44734.4089 | 49.9073
|  |  | 44734.4089 | 49.9073
|  |  | 44734.4089 | 49.9073
|  |  | 44734.4089 | 49.9073
|  |  | 44734.4089 | 49.9073
|  |  | 44734.4089 | 49.9073
|  |  | 44734.4089 | 49.9073
|  |  | 44734.4089 | 49.9073
|  |  | 44734.4089 | 49.9073
|  |  | 44734.4089 | 49.9073
|  |  | 44734.4089 | 49.9073
|  |  | 44734.4089 | 49.9073
|  |  | 44734.4089 | 49.9072
|  |  | 44734.4089 | 49.9072
|  |  | 44734.4089 | 49.9072
|  |  | 44734.4089 | 49.9071
|  |  | 44734.4089 | 49.9071
|  |  | 44734.4089 | 49.9071
|  |  | 44734.4089 | 49.9071
|  |  | 44734.4089 | 49.9071
|  |  | 44734.4089 | 49.9071
|  |  | 44734.4089 | 49.9071
|  |  | 44734.4089 | 49.9071
|  |  | 44734.4089 | 49.9071
|  |  | 44734.4089 | 49.9071
|  |  | 44734.4089 | 49.9071
|  |  | 44734.4089 | 49.9071
|  |  | 44734.4089 | 49.9072
|  |  | 44734.4089 | 49.9072
|  |  | 44734.4089 | 49.9071
|  |  | 44734.4089 | 49.9071
|  |  | 44734.4089 | 49.9071
|  |  | 44734.4089 | 49.907
|  |  | 44734.4089 | 49.9071
|  |  | 44734.4089 | 49.907
|  |  | 44734.4089 | 49.907
|  |  | 44734.4089 | 49.907
|  |  | 2022-06-22 09:49 | 49.907
|  |  | 44734.4089 | 49.9069
|  |  | 44734.4089 | 49.9069
|  |  | 44734.4089 | 49.907
|  |  | 44734.4089 | 49.907
|  |  | 44734.4089 | 49.907
|  |  | 44734.4089 | 49.9071
|  |  | 44734.4089 | 49.9071
|  |  | 44734.4089 | 49.9071
|  |  | 44734.4089 | 49.9072
|  |  | 44734.4089 | 49.9072
|  |  | 44734.4089 | 49.9073
|  |  | 44734.4089 | 49.9074
|  |  | 44734.4089 | 49.9075
|  |  | 44734.4089 | 49.9075
|  |  | 44734.4089 | 49.9075
|  |  | 44734.4089 | 49.9076
|  |  | 44734.4089 | 49.9075
|  |  | 44734.4089 | 49.9075
|  |  | 44734.4089 | 49.9075
|  |  | 44734.4089 | 49.9075
|  |  | 44734.4089 | 49.9076
|  |  | 44734.4089 | 49.9076
|  |  | 44734.4089 | 49.9077
|  |  | 44734.4089 | 49.9076
|  |  | 44734.4089 | 49.9076
|  |  | 44734.4089 | 49.9076
|  |  | 44734.4089 | 49.9076
|  |  | 44734.4089 | 49.9076
|  |  | 44734.4089 | 49.9076
|  |  | 44734.4089 | 49.9077
|  |  | 44734.4089 | 49.9077
|  |  | 44734.4089 | 49.9078
|  |  | 44734.4089 | 49.9077
|  |  | 44734.4089 | 49.9077
|  |  | 44734.4089 | 49.9077
|  |  | 44734.4089 | 49.9077
|  |  | 44734.4089 | 49.9077
|  |  | 44734.4089 | 49.9077
|  |  | 44734.4089 | 49.9077
|  |  | 44734.4089 | 49.9077
|  |  | 44734.4089 | 49.9077
|  |  | 44734.4089 | 49.9077
|  |  | 44734.4089 | 49.9078
|  |  | 44734.4089 | 49.9078
|  |  | 44734.4089 | 49.9078
|  |  | 44734.4089 | 49.9079
|  |  | 44734.4089 | 49.908
|  |  | 44734.4089 | 49.908
|  |  | 44734.4089 | 49.908
|  |  | 2022-06-22 09:49 | 49.9081
|  |  | 44734.4089 | 49.9081
|  |  | 44734.4089 | 49.9082
|  |  | 44734.4089 | 49.9083
|  |  | 44734.4089 | 49.9083
|  |  | 44734.4089 | 49.9083
|  |  | 44734.4089 | 49.9082
|  |  | 44734.4089 | 49.9083
|  |  | 44734.4089 | 49.9082
|  |  | 44734.4089 | 49.9082
|  |  | 44734.4089 | 49.9082
|  |  | 44734.4089 | 49.9082
|  |  | 44734.4089 | 49.9082
|  |  | 44734.4089 | 49.9083
|  |  | 44734.4089 | 49.9083
|  |  | 44734.4089 | 49.9084
|  |  | 44734.4089 | 49.9084
|  |  | 44734.4089 | 49.9084
|  |  | 44734.4089 | 49.9085
|  |  | 44734.4089 | 49.9086
|  |  | 44734.4089 | 49.9086
|  |  | 44734.4089 | 49.9086
|  |  | 44734.4089 | 49.9086
|  |  | 44734.4089 | 49.9086
|  |  | 44734.4089 | 49.9086
|  |  | 44734.4089 | 49.9086
|  |  | 44734.4089 | 49.9086
|  |  | 44734.4089 | 49.9086
|  |  | 44734.4089 | 49.9087
|  |  | 44734.4089 | 49.9087
|  |  | 44734.4089 | 49.9088
|  |  | 44734.4089 | 49.9089
|  |  | 44734.4089 | 49.9089
|  |  | 44734.4089 | 49.909
|  |  | 44734.4089 | 49.909
|  |  | 44734.4089 | 49.9091
|  |  | 44734.4089 | 49.9091
|  |  | 44734.4089 | 49.9092
|  |  | 44734.4089 | 49.9092
|  |  | 44734.4089 | 49.9093
|  |  | 44734.4089 | 49.9093
|  |  | 44734.4089 | 49.9094
|  |  | 44734.4089 | 49.9095
|  |  | 44734.4089 | 49.9095
|  |  | 44734.4089 | 49.9096
|  |  | 44734.4089 | 49.9097
|  |  | 44734.4089 | 49.9097
|  |  | 44734.4089 | 49.9098
|  |  | 44734.4089 | 49.9098
|  |  | 44734.4089 | 49.9098
|  |  | 2022-06-22 09:49 | 49.9099
|  |  | 44734.4089 | 49.9099
|  |  | 44734.4089 | 49.9099
|  |  | 44734.4089 | 49.91
|  |  | 44734.4089 | 49.9101
|  |  | 44734.4089 | 49.9102
|  |  | 44734.4089 | 49.9102
|  |  | 44734.4089 | 49.9102
|  |  | 44734.4089 | 49.9103
|  |  | 44734.4089 | 49.9103
|  |  | 44734.4089 | 49.9103
|  |  | 44734.4089 | 49.9104
|  |  | 44734.4089 | 49.9104
|  |  | 44734.4089 | 49.9104
|  |  | 44734.4089 | 49.9104
|  |  | 44734.4089 | 49.9105
|  |  | 44734.4089 | 49.9105
|  |  | 44734.4089 | 49.9105
|  |  | 44734.4089 | 49.9104
|  |  | 44734.4089 | 49.9104
|  |  | 44734.4089 | 49.9105
|  |  | 44734.4089 | 49.9105
|  |  | 44734.4089 | 49.9107
|  |  | 44734.4089 | 49.9107
|  |  | 44734.4089 | 49.9108
|  |  | 44734.4089 | 49.9108
|  |  | 44734.4089 | 49.9107
|  |  | 44734.4089 | 49.9108
|  |  | 44734.4089 | 49.9108
|  |  | 44734.4089 | 49.9109
|  |  | 44734.4089 | 49.911
|  |  | 44734.4089 | 49.911
|  |  | 44734.4089 | 49.911
|  |  | 44734.4089 | 49.911
|  |  | 44734.4089 | 49.9111
|  |  | 44734.4089 | 49.9111
|  |  | 44734.4089 | 49.9111
|  |  | 44734.4089 | 49.9112
|  |  | 44734.4089 | 49.9112
|  |  | 44734.4089 | 49.9113
|  |  | 44734.4089 | 49.9113
|  |  | 44734.4089 | 49.9115
|  |  | 44734.4089 | 49.9116
|  |  | 44734.4089 | 49.9117
|  |  | 44734.4089 | 49.9117
|  |  | 44734.4089 | 49.9118
|  |  | 44734.4089 | 49.9119
|  |  | 44734.4089 | 49.912
|  |  | 44734.4089 | 49.9121
|  |  | 44734.4089 | 49.9122
|  |  | 2022-06-22 09:49 | 49.9123
|  |  | 44734.4089 | 49.9123
|  |  | 44734.4089 | 49.9124
|  |  | 44734.4089 | 49.9125
|  |  | 44734.4089 | 49.9126
|  |  | 44734.4089 | 49.9127
|  |  | 44734.4089 | 49.9127
|  |  | 44734.4089 | 49.9128
|  |  | 44734.4089 | 49.9129
|  |  | 44734.4089 | 49.913
|  |  | 44734.4089 | 49.9132
|  |  | 44734.4089 | 49.9133
|  |  | 44734.4089 | 49.9133
|  |  | 44734.4089 | 49.9134
|  |  | 44734.4089 | 49.9135
|  |  | 44734.409 | 49.9135
|  |  | 44734.409 | 49.9136
|  |  | 44734.409 | 49.9137
|  |  | 44734.409 | 49.9138
|  |  | 44734.409 | 49.9138
|  |  | 44734.409 | 49.9138
|  |  | 44734.409 | 49.914
|  |  | 44734.409 | 49.914
|  |  | 44734.409 | 49.9141
|  |  | 44734.409 | 49.9142
|  |  | 44734.409 | 49.9142
|  |  | 44734.409 | 49.9143
|  |  | 44734.409 | 49.9144
|  |  | 44734.409 | 49.9144
|  |  | 44734.409 | 49.9144
|  |  | 44734.409 | 49.9145
|  |  | 44734.409 | 49.9145
|  |  | 44734.409 | 49.9146
|  |  | 44734.409 | 49.9146
|  |  | 44734.409 | 49.9146
|  |  | 44734.409 | 49.9148
|  |  | 44734.409 | 49.9149
|  |  | 44734.409 | 49.915
|  |  | 44734.409 | 49.9152
|  |  | 44734.409 | 49.9153
|  |  | 44734.409 | 49.9154
|  |  | 44734.409 | 49.9155
|  |  | 44734.409 | 49.9155
|  |  | 44734.409 | 49.9156
|  |  | 44734.409 | 49.9156
|  |  | 44734.409 | 49.9156
|  |  | 44734.409 | 49.9156
|  |  | 44734.409 | 49.9156
|  |  | 44734.409 | 49.9156
|  |  | 44734.409 | 49.9156
|  |  | 2022-06-22 09:49 | 49.9157
|  |  | 44734.409 | 49.9158
|  |  | 44734.409 | 49.9159
|  |  | 44734.409 | 49.916
|  |  | 44734.409 | 49.9161
|  |  | 44734.409 | 49.9162
|  |  | 44734.409 | 49.9162
|  |  | 44734.409 | 49.9163
|  |  | 44734.409 | 49.9164
|  |  | 44734.409 | 49.9164
|  |  | 44734.409 | 49.9164
|  |  | 44734.409 | 49.9165
|  |  | 44734.409 | 49.9165
|  |  | 44734.409 | 49.9166
|  |  | 44734.409 | 49.9166
|  |  | 44734.409 | 49.9167
|  |  | 44734.409 | 49.9168
|  |  | 44734.409 | 49.9168
|  |  | 44734.409 | 49.9169
|  |  | 44734.409 | 49.917
|  |  | 44734.409 | 49.9171
|  |  | 44734.409 | 49.9171
|  |  | 44734.409 | 49.9172
|  |  | 44734.409 | 49.9173
|  |  | 44734.409 | 49.9173
|  |  | 44734.409 | 49.9174
|  |  | 44734.409 | 49.9175
|  |  | 44734.409 | 49.9175
|  |  | 44734.409 | 49.9175
|  |  | 44734.409 | 49.9175
|  |  | 44734.409 | 49.9176
|  |  | 44734.409 | 49.9177
|  |  | 44734.409 | 49.9177
|  |  | 44734.409 | 49.9179
|  |  | 44734.409 | 49.9179
|  |  | 44734.409 | 49.918
|  |  | 44734.409 | 49.9182
|  |  | 44734.409 | 49.9183
|  |  | 44734.409 | 49.9185
|  |  | 44734.409 | 49.9186
|  |  | 44734.409 | 49.9187
|  |  | 44734.409 | 49.9187
|  |  | 44734.409 | 49.9187
|  |  | 44734.409 | 49.9187
|  |  | 44734.409 | 49.9187
|  |  | 44734.409 | 49.9186
|  |  | 44734.409 | 49.9186
|  |  | 44734.409 | 49.9185
|  |  | 44734.409 | 49.9185
|  |  | 44734.409 | 49.9185
|  |  | 2022-06-22 09:49 | 49.9186
|  |  | 44734.409 | 49.9186
|  |  | 44734.409 | 49.9187
|  |  | 44734.409 | 49.9187
|  |  | 44734.409 | 49.9188
|  |  | 44734.409 | 49.9188
|  |  | 44734.409 | 49.9188
|  |  | 44734.409 | 49.9189
|  |  | 44734.409 | 49.9189
|  |  | 44734.409 | 49.9189
|  |  | 44734.409 | 49.9188
|  |  | 44734.409 | 49.9188
|  |  | 44734.409 | 49.9188
|  |  | 44734.409 | 49.9187
|  |  | 44734.409 | 49.9187
|  |  | 44734.409 | 49.9187
|  |  | 44734.409 | 49.9187
|  |  | 44734.409 | 49.9189
|  |  | 44734.409 | 49.919
|  |  | 44734.409 | 49.9191
|  |  | 44734.409 | 49.9193
|  |  | 44734.409 | 49.9194
|  |  | 44734.409 | 49.9194
|  |  | 44734.409 | 49.9195
|  |  | 44734.409 | 49.9196
|  |  | 44734.409 | 49.9196
|  |  | 44734.409 | 49.9197
|  |  | 44734.409 | 49.9197
|  |  | 44734.409 | 49.9198
|  |  | 44734.409 | 49.9198
|  |  | 44734.409 | 49.9198
|  |  | 44734.409 | 49.9198
|  |  | 44734.409 | 49.9198
|  |  | 44734.409 | 49.9198
|  |  | 44734.409 | 49.9199
|  |  | 44734.409 | 49.92
|  |  | 44734.409 | 49.92
|  |  | 44734.409 | 49.9201
|  |  | 44734.409 | 49.9201
|  |  | 44734.409 | 49.9202
|  |  | 44734.409 | 49.9202
|  |  | 44734.409 | 49.9203
|  |  | 44734.409 | 49.9203
|  |  | 44734.409 | 49.9204
|  |  | 44734.409 | 49.9204
|  |  | 44734.409 | 49.9204
|  |  | 44734.409 | 49.9204
|  |  | 44734.409 | 49.9205
|  |  | 44734.409 | 49.9205
|  |  | 44734.409 | 49.9205
|  |  | 2022-06-22 09:49 | 49.9205
|  |  | 44734.409 | 49.9205
|  |  | 44734.409 | 49.9204
|  |  | 44734.409 | 49.9204
|  |  | 44734.409 | 49.9204
|  |  | 44734.409 | 49.9204
|  |  | 44734.409 | 49.9205
|  |  | 44734.409 | 49.9206
|  |  | 44734.409 | 49.9206
|  |  | 44734.409 | 49.9207
|  |  | 44734.409 | 49.9207
|  |  | 44734.409 | 49.9208
|  |  | 44734.409 | 49.9208
|  |  | 44734.409 | 49.9208
|  |  | 44734.409 | 49.9208
|  |  | 44734.409 | 49.9208
|  |  | 44734.409 | 49.9207
|  |  | 44734.409 | 49.9207
|  |  | 44734.409 | 49.9207
|  |  | 44734.409 | 49.9207
|  |  | 44734.409 | 49.9208
|  |  | 44734.409 | 49.9208
|  |  | 44734.409 | 49.9209
|  |  | 44734.409 | 49.9209
|  |  | 44734.409 | 49.9211
|  |  | 44734.409 | 49.9212
|  |  | 44734.409 | 49.9213
|  |  | 44734.409 | 49.9213
|  |  | 44734.409 | 49.9213
|  |  | 44734.409 | 49.9213
|  |  | 44734.409 | 49.9213
|  |  | 44734.409 | 49.9213
|  |  | 44734.409 | 49.9213
|  |  | 44734.409 | 49.9212
|  |  | 44734.409 | 49.9212
|  |  | 44734.409 | 49.9212
|  |  | 44734.409 | 49.9212
|  |  | 44734.409 | 49.9211
|  |  | 44734.409 | 49.9211
|  |  | 44734.409 | 49.9211
|  |  | 44734.409 | 49.9211
|  |  | 44734.409 | 49.9212
|  |  | 44734.409 | 49.9212
|  |  | 44734.409 | 49.9212
|  |  | 44734.409 | 49.9213
|  |  | 44734.409 | 49.9213
|  |  | 44734.409 | 49.9213
|  |  | 44734.409 | 49.9213
|  |  | 44734.409 | 49.9213
|  |  | 44734.409 | 49.9214
|  |  | 2022-06-22 09:49 | 49.9213
|  |  | 44734.409 | 49.9213
|  |  | 44734.409 | 49.9213
|  |  | 44734.409 | 49.9214
|  |  | 44734.409 | 49.9213
|  |  | 44734.409 | 49.9214
|  |  | 44734.409 | 49.9214
|  |  | 44734.409 | 49.9214
|  |  | 44734.409 | 49.9214
|  |  | 44734.409 | 49.9214
|  |  | 44734.409 | 49.9214
|  |  | 44734.409 | 49.9215
|  |  | 44734.409 | 49.9215
|  |  | 44734.409 | 49.9215
|  |  | 44734.409 | 49.9216
|  |  | 44734.409 | 49.9217
|  |  | 44734.409 | 49.9217
|  |  | 44734.409 | 49.9217
|  |  | 44734.409 | 49.9218
|  |  | 44734.409 | 49.9218
|  |  | 44734.409 | 49.9217
|  |  | 44734.409 | 49.9217
|  |  | 44734.409 | 49.9216
|  |  | 44734.409 | 49.9215
|  |  | 44734.409 | 49.9215
|  |  | 44734.409 | 49.9214
|  |  | 44734.409 | 49.9214
|  |  | 44734.409 | 49.9213
|  |  | 44734.409 | 49.9213
|  |  | 44734.409 | 49.9213
|  |  | 44734.409 | 49.9214
|  |  | 44734.409 | 49.9214
|  |  | 44734.409 | 49.9214
|  |  | 44734.409 | 49.9214
|  |  | 44734.409 | 49.9214
|  |  | 44734.409 | 49.9213
|  |  | 44734.409 | 49.9213
|  |  | 44734.409 | 49.9213
|  |  | 44734.409 | 49.9213
|  |  | 44734.409 | 49.9213
|  |  | 44734.409 | 49.9213
|  |  | 44734.409 | 49.9214
|  |  | 44734.409 | 49.9214
|  |  | 44734.409 | 49.9215
|  |  | 44734.409 | 49.9216
|  |  | 44734.409 | 49.9216
|  |  | 44734.409 | 49.9217
|  |  | 44734.409 | 49.9216
|  |  | 44734.409 | 49.9216
|  |  | 44734.409 | 49.9216
|  |  | 2022-06-22 09:49 | 49.9215
|  |  | 44734.409 | 49.9215
|  |  | 44734.409 | 49.9214
|  |  | 44734.409 | 49.9215
|  |  | 44734.409 | 49.9215
|  |  | 44734.409 | 49.9215
|  |  | 44734.409 | 49.9216
|  |  | 44734.409 | 49.9216
|  |  | 44734.409 | 49.9217
|  |  | 44734.409 | 49.9218
|  |  | 44734.409 | 49.9219
|  |  | 44734.409 | 49.922
|  |  | 44734.409 | 49.9221
|  |  | 44734.409 | 49.9222
|  |  | 44734.409 | 49.9222
|  |  | 44734.409 | 49.9222
|  |  | 44734.409 | 49.9222
|  |  | 44734.409 | 49.9223
|  |  | 44734.409 | 49.9223
|  |  | 44734.409 | 49.9223
|  |  | 44734.409 | 49.9223
|  |  | 44734.409 | 49.9224
|  |  | 44734.409 | 49.9224
|  |  | 44734.409 | 49.9225
|  |  | 44734.409 | 49.9226
|  |  | 44734.409 | 49.9226
|  |  | 44734.409 | 49.9227
|  |  | 44734.409 | 49.9228
|  |  | 44734.409 | 49.9228
|  |  | 44734.409 | 49.9229
|  |  | 44734.409 | 49.9229
|  |  | 44734.409 | 49.9229
|  |  | 44734.409 | 49.923
|  |  | 44734.409 | 49.9231
|  |  | 44734.409 | 49.9231
|  |  | 44734.409 | 49.9233
|  |  | 44734.409 | 49.9234
|  |  | 44734.409 | 49.9234
|  |  | 44734.409 | 49.9235
|  |  | 44734.409 | 49.9235
|  |  | 44734.409 | 49.9235
|  |  | 44734.409 | 49.9235
|  |  | 44734.409 | 49.9235
|  |  | 44734.409 | 49.9236
|  |  | 44734.409 | 49.9236
|  |  | 44734.409 | 49.9236
|  |  | 44734.409 | 49.9236
|  |  | 44734.409 | 49.9237
|  |  | 44734.409 | 49.9237
|  |  | 44734.409 | 49.9238
|  |  | 2022-06-22 09:49 | 49.9239
|  |  | 44734.409 | 49.9239
|  |  | 44734.409 | 49.924
|  |  | 44734.409 | 49.9241
|  |  | 44734.409 | 49.9241
|  |  | 44734.409 | 49.9242
|  |  | 44734.409 | 49.9243
|  |  | 44734.409 | 49.9244
|  |  | 44734.409 | 49.9245
|  |  | 44734.409 | 49.9246
|  |  | 44734.409 | 49.9247
|  |  | 44734.409 | 49.9247
|  |  | 44734.409 | 49.9248
|  |  | 44734.409 | 49.9248
|  |  | 44734.409 | 49.9248
|  |  | 44734.409 | 49.9248
|  |  | 44734.409 | 49.9247
|  |  | 44734.409 | 49.9248
|  |  | 44734.409 | 49.9248
|  |  | 44734.409 | 49.9247
|  |  | 44734.409 | 49.9248
|  |  | 44734.409 | 49.9248
|  |  | 44734.409 | 49.9248
|  |  | 44734.409 | 49.9249
|  |  | 44734.409 | 49.9251
|  |  | 44734.409 | 49.9252
|  |  | 44734.409 | 49.9252
|  |  | 44734.409 | 49.9253
|  |  | 44734.409 | 49.9253
|  |  | 44734.409 | 49.9253
|  |  | 44734.409 | 49.9254
|  |  | 44734.409 | 49.9254
|  |  | 44734.409 | 49.9255
|  |  | 44734.409 | 49.9254
|  |  | 44734.409 | 49.9255
|  |  | 44734.409 | 49.9256
|  |  | 44734.409 | 49.9257
|  |  | 44734.409 | 49.9258
|  |  | 44734.409 | 49.9258
|  |  | 44734.409 | 49.9259
|  |  | 44734.409 | 49.9259
|  |  | 44734.409 | 49.926
|  |  | 44734.409 | 49.9261
|  |  | 44734.409 | 49.9261
|  |  | 44734.409 | 49.9262
|  |  | 44734.409 | 49.9262
|  |  | 44734.409 | 49.9262
|  |  | 44734.409 | 49.9263
|  |  | 44734.409 | 49.9263
|  |  | 44734.409 | 49.9263
|  |  | 2022-06-22 09:49 | 49.9264
|  |  | 44734.409 | 49.9264
|  |  | 44734.409 | 49.9265
|  |  | 44734.409 | 49.9265
|  |  | 44734.409 | 49.9265
|  |  | 44734.409 | 49.9265
|  |  | 44734.409 | 49.9264
|  |  | 44734.409 | 49.9264
|  |  | 44734.409 | 49.9262
|  |  | 44734.409 | 49.9262
|  |  | 44734.409 | 49.9262
|  |  | 44734.409 | 49.9263
|  |  | 44734.409 | 49.9263
|  |  | 44734.409 | 49.9263
|  |  | 44734.409 | 49.9264
|  |  | 44734.409 | 49.9265
|  |  | 44734.409 | 49.9266
|  |  | 44734.409 | 49.9266
|  |  | 44734.409 | 49.9267
|  |  | 44734.409 | 49.9267
|  |  | 44734.409 | 49.9267
|  |  | 44734.409 | 49.9266
|  |  | 44734.409 | 49.9266
|  |  | 44734.409 | 49.9265
|  |  | 44734.409 | 49.9265
|  |  | 44734.409 | 49.9265
|  |  | 44734.409 | 49.9265
|  |  | 44734.409 | 49.9266
|  |  | 44734.409 | 49.9266
|  |  | 44734.409 | 49.9267
|  |  | 44734.409 | 49.9267
|  |  | 44734.409 | 49.9267
|  |  | 44734.409 | 49.9268
|  |  | 44734.409 | 49.9268
|  |  | 44734.409 | 49.9268
|  |  | 44734.409 | 49.9268
|  |  | 44734.409 | 49.9268
|  |  | 44734.409 | 49.9267
|  |  | 44734.409 | 49.9267
|  |  | 44734.409 | 49.9266
|  |  | 44734.409 | 49.9266
|  |  | 44734.409 | 49.9265
|  |  | 44734.409 | 49.9264
|  |  | 44734.409 | 49.9263
|  |  | 44734.409 | 49.9263
|  |  | 44734.409 | 49.9262
|  |  | 44734.409 | 49.9262
|  |  | 44734.409 | 49.9262
|  |  | 44734.409 | 49.9263
|  |  | 44734.409 | 49.9263
|  |  | 2022-06-22 09:49 | 49.9263
|  |  | 44734.409 | 49.9263
|  |  | 44734.409 | 49.9264
|  |  | 44734.409 | 49.9265
|  |  | 44734.409 | 49.9265
|  |  | 44734.409 | 49.9265
|  |  | 44734.409 | 49.9264
|  |  | 44734.409 | 49.9265
|  |  | 44734.409 | 49.9265
|  |  | 44734.409 | 49.9264
|  |  | 44734.409 | 49.9264
|  |  | 44734.409 | 49.9264
|  |  | 44734.409 | 49.9263
|  |  | 44734.409 | 49.9263
|  |  | 44734.409 | 49.9262
|  |  | 44734.409 | 49.9262
|  |  | 44734.409 | 49.9262
|  |  | 44734.409 | 49.9262
|  |  | 44734.409 | 49.9262
|  |  | 44734.409 | 49.9262
|  |  | 44734.409 | 49.9263
|  |  | 44734.409 | 49.9263
|  |  | 44734.409 | 49.9263
|  |  | 44734.409 | 49.9264
|  |  | 44734.409 | 49.9265
|  |  | 44734.409 | 49.9265
|  |  | 44734.409 | 49.9266
|  |  | 44734.409 | 49.9266
|  |  | 44734.409 | 49.9266
|  |  | 44734.409 | 49.9266
|  |  | 44734.409 | 49.9265
|  |  | 44734.409 | 49.9265
|  |  | 44734.409 | 49.9264
|  |  | 44734.409 | 49.9263
|  |  | 44734.409 | 49.9263
|  |  | 44734.409 | 49.9263
|  |  | 44734.409 | 49.9263
|  |  | 44734.409 | 49.9263
|  |  | 44734.409 | 49.9264
|  |  | 44734.409 | 49.9264
|  |  | 44734.409 | 49.9264
|  |  | 44734.409 | 49.9265
|  |  | 44734.409 | 49.9265
|  |  | 44734.409 | 49.9265
|  |  | 44734.409 | 49.9264
|  |  | 44734.409 | 49.9264
|  |  | 44734.4091 | 49.9263
|  |  | 44734.4091 | 49.9263
|  |  | 44734.4091 | 49.9263
|  |  | 44734.4091 | 49.9264
|  |  | 2022-06-22 09:49 | 49.9264
|  |  | 44734.4091 | 49.9264
|  |  | 44734.4091 | 49.9265
|  |  | 44734.4091 | 49.9266
|  |  | 44734.4091 | 49.9266
|  |  | 44734.4091 | 49.9266
|  |  | 44734.4091 | 49.9266
|  |  | 44734.4091 | 49.9266
|  |  | 44734.4091 | 49.9266
|  |  | 44734.4091 | 49.9266
|  |  | 44734.4091 | 49.9266
|  |  | 44734.4091 | 49.9266
|  |  | 44734.4091 | 49.9265
|  |  | 44734.4091 | 49.9265
|  |  | 44734.4091 | 49.9264
|  |  | 44734.4091 | 49.9264
|  |  | 44734.4091 | 49.9264
|  |  | 44734.4091 | 49.9263
|  |  | 44734.4091 | 49.9263
|  |  | 44734.4091 | 49.9263
|  |  | 44734.4091 | 49.9264
|  |  | 44734.4091 | 49.9263
|  |  | 44734.4091 | 49.9264
|  |  | 44734.4091 | 49.9264
|  |  | 44734.4091 | 49.9264
|  |  | 44734.4091 | 49.9263
|  |  | 44734.4091 | 49.9263
|  |  | 44734.4091 | 49.9262
|  |  | 44734.4091 | 49.9262
|  |  | 44734.4091 | 49.9262
|  |  | 44734.4091 | 49.9262
|  |  | 44734.4091 | 49.9262
|  |  | 44734.4091 | 49.9263
|  |  | 44734.4091 | 49.9263
|  |  | 44734.4091 | 49.9263
|  |  | 44734.4091 | 49.9264
|  |  | 44734.4091 | 49.9264
|  |  | 44734.4091 | 49.9264
|  |  | 44734.4091 | 49.9264
|  |  | 44734.4091 | 49.9264
|  |  | 44734.4091 | 49.9264
|  |  | 44734.4091 | 49.9265
|  |  | 44734.4091 | 49.9265
|  |  | 44734.4091 | 49.9266
|  |  | 44734.4091 | 49.9266
|  |  | 44734.4091 | 49.9267
|  |  | 44734.4091 | 49.9268
|  |  | 44734.4091 | 49.9268
|  |  | 44734.4091 | 49.9268
|  |  | 44734.4091 | 49.9268
|  |  | 2022-06-22 09:49 | 49.9268
|  |  | 44734.4091 | 49.9268
|  |  | 44734.4091 | 49.9268
|  |  | 44734.4091 | 49.9269
|  |  | 44734.4091 | 49.9268
|  |  | 44734.4091 | 49.9268
|  |  | 44734.4091 | 49.9267
|  |  | 44734.4091 | 49.9266
|  |  | 44734.4091 | 49.9266
|  |  | 44734.4091 | 49.9266
|  |  | 44734.4091 | 49.9267
|  |  | 44734.4091 | 49.9267
|  |  | 44734.4091 | 49.9267
|  |  | 44734.4091 | 49.9267
|  |  | 44734.4091 | 49.9266
|  |  | 44734.4091 | 49.9266
|  |  | 44734.4091 | 49.9266
|  |  | 44734.4091 | 49.9266
|  |  | 44734.4091 | 49.9266
|  |  | 44734.4091 | 49.9266
|  |  | 44734.4091 | 49.9266
|  |  | 44734.4091 | 49.9265
|  |  | 44734.4091 | 49.9265
|  |  | 44734.4091 | 49.9265
|  |  | 44734.4091 | 49.9265
|  |  | 44734.4091 | 49.9265
|  |  | 44734.4091 | 49.9265
|  |  | 44734.4091 | 49.9265
|  |  | 44734.4091 | 49.9265
|  |  | 44734.4091 | 49.9264
|  |  | 44734.4091 | 49.9264
|  |  | 44734.4091 | 49.9263
|  |  | 44734.4091 | 49.9263
|  |  | 44734.4091 | 49.9262
|  |  | 44734.4091 | 49.9262
|  |  | 44734.4091 | 49.9262
|  |  | 44734.4091 | 49.9263
|  |  | 44734.4091 | 49.9262
|  |  | 44734.4091 | 49.9262
|  |  | 44734.4091 | 49.9263
|  |  | 44734.4091 | 49.9263
|  |  | 44734.4091 | 49.9263
|  |  | 44734.4091 | 49.9263
|  |  | 44734.4091 | 49.9263
|  |  | 44734.4091 | 49.9263
|  |  | 44734.4091 | 49.9262
|  |  | 44734.4091 | 49.9262
|  |  | 44734.4091 | 49.9262
|  |  | 44734.4091 | 49.9262
|  |  | 44734.4091 | 49.9262
|  |  | 2022-06-22 09:49 | 49.9262
|  |  | 44734.4091 | 49.9261
|  |  | 44734.4091 | 49.9259
|  |  | 44734.4091 | 49.9259
|  |  | 44734.4091 | 49.9259
|  |  | 44734.4091 | 49.9259
|  |  | 44734.4091 | 49.926
|  |  | 44734.4091 | 49.926
|  |  | 44734.4091 | 49.9261
|  |  | 44734.4091 | 49.9261
|  |  | 44734.4091 | 49.9261
|  |  | 44734.4091 | 49.9261
|  |  | 44734.4091 | 49.926
|  |  | 44734.4091 | 49.9259
|  |  | 44734.4091 | 49.9258
|  |  | 44734.4091 | 49.9257
|  |  | 44734.4091 | 49.9257
|  |  | 44734.4091 | 49.9257
|  |  | 44734.4091 | 49.9257
|  |  | 44734.4091 | 49.9257
|  |  | 44734.4091 | 49.9256
|  |  | 44734.4091 | 49.9255
|  |  | 44734.4091 | 49.9255
|  |  | 44734.4091 | 49.9256
|  |  | 44734.4091 | 49.9256
|  |  | 44734.4091 | 49.9256
|  |  | 44734.4091 | 49.9255
|  |  | 44734.4091 | 49.9254
|  |  | 44734.4091 | 49.9254
|  |  | 44734.4091 | 49.9253
|  |  | 44734.4091 | 49.9252
|  |  | 44734.4091 | 49.9251
|  |  | 44734.4091 | 49.9251
|  |  | 44734.4091 | 49.9251
|  |  | 44734.4091 | 49.925
|  |  | 44734.4091 | 49.925
|  |  | 44734.4091 | 49.9249
|  |  | 44734.4091 | 49.9249
|  |  | 44734.4091 | 49.9249
|  |  | 44734.4091 | 49.9248
|  |  | 44734.4091 | 49.9248
|  |  | 44734.4091 | 49.9248
|  |  | 44734.4091 | 49.9247
|  |  | 44734.4091 | 49.9246
|  |  | 44734.4091 | 49.9245
|  |  | 44734.4091 | 49.9244
|  |  | 44734.4091 | 49.9244
|  |  | 44734.4091 | 49.9243
|  |  | 44734.4091 | 49.9242
|  |  | 44734.4091 | 49.9241
|  |  | 2022-06-22 09:49 | 49.924
|  |  | 44734.4091 | 49.924
|  |  | 44734.4091 | 49.9239
|  |  | 44734.4091 | 49.9238
|  |  | 44734.4091 | 49.9236
|  |  | 44734.4091 | 49.9235
|  |  | 44734.4091 | 49.9235
|  |  | 44734.4091 | 49.9234
|  |  | 44734.4091 | 49.9233
|  |  | 44734.4091 | 49.9233
|  |  | 44734.4091 | 49.9232
|  |  | 44734.4091 | 49.9232
|  |  | 44734.4091 | 49.9231
|  |  | 44734.4091 | 49.9231
|  |  | 44734.4091 | 49.9231
|  |  | 44734.4091 | 49.9231
|  |  | 44734.4091 | 49.923
|  |  | 44734.4091 | 49.923
|  |  | 44734.4091 | 49.9229
|  |  | 44734.4091 | 49.9228
|  |  | 44734.4091 | 49.9227
|  |  | 44734.4091 | 49.9226
|  |  | 44734.4091 | 49.9225
|  |  | 44734.4091 | 49.9224
|  |  | 44734.4091 | 49.9223
|  |  | 44734.4091 | 49.9222
|  |  | 44734.4091 | 49.9222
|  |  | 44734.4091 | 49.9221
|  |  | 44734.4091 | 49.9221
|  |  | 44734.4091 | 49.922
|  |  | 44734.4091 | 49.922
|  |  | 44734.4091 | 49.9219
|  |  | 44734.4091 | 49.9219
|  |  | 44734.4091 | 49.9218
|  |  | 44734.4091 | 49.9217
|  |  | 44734.4091 | 49.9216
|  |  | 44734.4091 | 49.9215
|  |  | 44734.4091 | 49.9214
|  |  | 44734.4091 | 49.9213
|  |  | 44734.4091 | 49.9213
|  |  | 44734.4091 | 49.9212
|  |  | 44734.4091 | 49.9211
|  |  | 44734.4091 | 49.9211
|  |  | 44734.4091 | 49.9209
|  |  | 44734.4091 | 49.9208
|  |  | 44734.4091 | 49.9208
|  |  | 44734.4091 | 49.9207
|  |  | 44734.4091 | 49.9206
|  |  | 44734.4091 | 49.9206
|  |  | 44734.4091 | 49.9205
|  |  | 2022-06-22 09:49 | 49.9205
|  |  | 44734.4091 | 49.9204
|  |  | 44734.4091 | 49.9205
|  |  | 44734.4091 | 49.9203
|  |  | 44734.4091 | 49.9202
|  |  | 44734.4091 | 49.9201
|  |  | 44734.4091 | 49.9201
|  |  | 44734.4091 | 49.92
|  |  | 44734.4091 | 49.9199
|  |  | 44734.4091 | 49.9198
|  |  | 44734.4091 | 49.9197
|  |  | 44734.4091 | 49.9197
|  |  | 44734.4091 | 49.9196
|  |  | 44734.4091 | 49.9195
|  |  | 44734.4091 | 49.9195
|  |  | 44734.4091 | 49.9194
|  |  | 44734.4091 | 49.9194
|  |  | 44734.4091 | 49.9193
|  |  | 44734.4091 | 49.9193
|  |  | 44734.4091 | 49.9192
|  |  | 44734.4091 | 49.9192
|  |  | 44734.4091 | 49.9191
|  |  | 44734.4091 | 49.919
|  |  | 44734.4091 | 49.9189
|  |  | 44734.4091 | 49.9188
|  |  | 44734.4091 | 49.9188
|  |  | 44734.4091 | 49.9186
|  |  | 44734.4091 | 49.9186
|  |  | 44734.4091 | 49.9184
|  |  | 44734.4091 | 49.9183
|  |  | 44734.4091 | 49.9183
|  |  | 44734.4091 | 49.9181
|  |  | 44734.4091 | 49.9181
|  |  | 44734.4091 | 49.918
|  |  | 44734.4091 | 49.9179
|  |  | 44734.4091 | 49.9178
|  |  | 44734.4091 | 49.9178
|  |  | 44734.4091 | 49.9178
|  |  | 44734.4091 | 49.9177
|  |  | 44734.4091 | 49.9176
|  |  | 44734.4091 | 49.9175
|  |  | 44734.4091 | 49.9176
|  |  | 44734.4091 | 49.9176
|  |  | 44734.4091 | 49.9175
|  |  | 44734.4091 | 49.9174
|  |  | 44734.4091 | 49.9173
|  |  | 44734.4091 | 49.9171
|  |  | 44734.4091 | 49.917
|  |  | 44734.4091 | 49.9168
|  |  | 44734.4091 | 49.9167
|  |  | 2022-06-22 09:49 | 49.9165
|  |  | 44734.4091 | 49.9164
|  |  | 44734.4091 | 49.9164
|  |  | 44734.4091 | 49.9163
|  |  | 44734.4091 | 49.9162
|  |  | 44734.4091 | 49.9162
|  |  | 44734.4091 | 49.9162
|  |  | 44734.4091 | 49.9162
|  |  | 44734.4091 | 49.9161
|  |  | 44734.4091 | 49.9161
|  |  | 44734.4091 | 49.916
|  |  | 44734.4091 | 49.916
|  |  | 44734.4091 | 49.9159
|  |  | 44734.4091 | 49.9158
|  |  | 44734.4091 | 49.9157
|  |  | 44734.4091 | 49.9156
|  |  | 44734.4091 | 49.9155
|  |  | 44734.4091 | 49.9155
|  |  | 44734.4091 | 49.9153
|  |  | 44734.4091 | 49.9152
|  |  | 44734.4091 | 49.9152
|  |  | 44734.4091 | 49.9151
|  |  | 44734.4091 | 49.915
|  |  | 44734.4091 | 49.9149
|  |  | 44734.4091 | 49.9149
|  |  | 44734.4091 | 49.9148
|  |  | 44734.4091 | 49.9148
|  |  | 44734.4091 | 49.9147
|  |  | 44734.4091 | 49.9147
|  |  | 44734.4091 | 49.9145
|  |  | 44734.4091 | 49.9145
|  |  | 44734.4091 | 49.9144
|  |  | 44734.4091 | 49.9144
|  |  | 44734.4091 | 49.9143
|  |  | 44734.4091 | 49.9143
|  |  | 44734.4091 | 49.9142
|  |  | 44734.4091 | 49.9141
|  |  | 44734.4091 | 49.914
|  |  | 44734.4091 | 49.9139
|  |  | 44734.4091 | 49.9138
|  |  | 44734.4091 | 49.9137
|  |  | 44734.4091 | 49.9136
|  |  | 44734.4091 | 49.9135
|  |  | 44734.4091 | 49.9133
|  |  | 44734.4091 | 49.9132
|  |  | 44734.4091 | 49.9131
|  |  | 44734.4091 | 49.913
|  |  | 44734.4091 | 49.9129
|  |  | 44734.4091 | 49.9128
|  |  | 44734.4091 | 49.9128
|  |  | 2022-06-22 09:49 | 49.9127
|  |  | 44734.4091 | 49.9127
|  |  | 44734.4091 | 49.9126
|  |  | 44734.4091 | 49.9125
|  |  | 44734.4091 | 49.9125
|  |  | 44734.4091 | 49.9125
|  |  | 44734.4091 | 49.9124
|  |  | 44734.4091 | 49.9123
|  |  | 44734.4091 | 49.9122
|  |  | 44734.4091 | 49.9122
|  |  | 44734.4091 | 49.9121
|  |  | 44734.4091 | 49.9121
|  |  | 44734.4091 | 49.912
|  |  | 44734.4091 | 49.9119
|  |  | 44734.4091 | 49.9119
|  |  | 44734.4091 | 49.9118
|  |  | 44734.4091 | 49.9117
|  |  | 44734.4091 | 49.9116
|  |  | 44734.4091 | 49.9116
|  |  | 44734.4091 | 49.9115
|  |  | 44734.4091 | 49.9115
|  |  | 44734.4091 | 49.9114
|  |  | 44734.4091 | 49.9114
|  |  | 44734.4091 | 49.9114
|  |  | 44734.4091 | 49.9113
|  |  | 44734.4091 | 49.9113
|  |  | 44734.4091 | 49.9112
|  |  | 44734.4091 | 49.9111
|  |  | 44734.4091 | 49.9111
|  |  | 44734.4091 | 49.911
|  |  | 44734.4091 | 49.9109
|  |  | 44734.4091 | 49.9108
|  |  | 44734.4091 | 49.9108
|  |  | 44734.4091 | 49.9107
|  |  | 44734.4091 | 49.9106
|  |  | 44734.4091 | 49.9106
|  |  | 44734.4091 | 49.9105
|  |  | 44734.4091 | 49.9105
|  |  | 44734.4091 | 49.9104
|  |  | 44734.4091 | 49.9103
|  |  | 44734.4091 | 49.9103
|  |  | 44734.4091 | 49.9103
|  |  | 44734.4091 | 49.9102
|  |  | 44734.4091 | 49.9102
|  |  | 44734.4091 | 49.9101
|  |  | 44734.4091 | 49.9101
|  |  | 44734.4091 | 49.91
|  |  | 44734.4091 | 49.9099
|  |  | 44734.4091 | 49.9098
|  |  | 44734.4091 | 49.9097
|  |  | 2022-06-22 09:49 | 49.9096
|  |  | 44734.4091 | 49.9096
|  |  | 44734.4091 | 49.9095
|  |  | 44734.4091 | 49.9093
|  |  | 44734.4091 | 49.9092
|  |  | 44734.4091 | 49.9092
|  |  | 44734.4091 | 49.9091
|  |  | 44734.4091 | 49.909
|  |  | 44734.4091 | 49.9089
|  |  | 44734.4091 | 49.9088
|  |  | 44734.4091 | 49.9088
|  |  | 44734.4091 | 49.9087
|  |  | 44734.4091 | 49.9086
|  |  | 44734.4091 | 49.9085
|  |  | 44734.4091 | 49.9084
|  |  | 44734.4091 | 49.9083
|  |  | 44734.4091 | 49.9082
|  |  | 44734.4091 | 49.9081
|  |  | 44734.4091 | 49.908
|  |  | 44734.4091 | 49.9079
|  |  | 44734.4091 | 49.9078
|  |  | 44734.4091 | 49.9076
|  |  | 44734.4091 | 49.9076
|  |  | 44734.4091 | 49.9075
|  |  | 44734.4091 | 49.9074
|  |  | 44734.4091 | 49.9073
|  |  | 44734.4091 | 49.9072
|  |  | 44734.4091 | 49.9071
|  |  | 44734.4091 | 49.9071
|  |  | 44734.4091 | 49.907
|  |  | 44734.4091 | 49.907
|  |  | 44734.4091 | 49.907
|  |  | 44734.4091 | 49.907
|  |  | 44734.4091 | 49.907
|  |  | 44734.4091 | 49.9069
|  |  | 44734.4091 | 49.9069
|  |  | 44734.4091 | 49.9068
|  |  | 44734.4091 | 49.9067
|  |  | 44734.4091 | 49.9067
|  |  | 44734.4091 | 49.9067
|  |  | 44734.4091 | 49.9067
|  |  | 44734.4091 | 49.9066
|  |  | 44734.4091 | 49.9066
|  |  | 44734.4091 | 49.9066
|  |  | 44734.4091 | 49.9066
|  |  | 44734.4091 | 49.9066
|  |  | 44734.4091 | 49.9065
|  |  | 44734.4091 | 49.9065
|  |  | 44734.4091 | 49.9064
|  |  | 44734.4091 | 49.9063
|  |  | 2022-06-22 09:49 | 49.9062
|  |  | 44734.4091 | 49.9062
|  |  | 44734.4091 | 49.9061
|  |  | 44734.4091 | 49.906
|  |  | 44734.4091 | 49.9059
|  |  | 44734.4091 | 49.9059
|  |  | 44734.4091 | 49.9058
|  |  | 44734.4091 | 49.9057
|  |  | 44734.4091 | 49.9056
|  |  | 44734.4091 | 49.9056
|  |  | 44734.4091 | 49.9055
|  |  | 44734.4091 | 49.9054
|  |  | 44734.4091 | 49.9054
|  |  | 44734.4091 | 49.9053
|  |  | 44734.4091 | 49.9053
|  |  | 44734.4091 | 49.9053
|  |  | 44734.4091 | 49.9052
|  |  | 44734.4091 | 49.9051
|  |  | 44734.4091 | 49.9051
|  |  | 44734.4091 | 49.905
|  |  | 44734.4091 | 49.905
|  |  | 44734.4091 | 49.9049
|  |  | 44734.4091 | 49.9049
|  |  | 44734.4091 | 49.9048
|  |  | 44734.4091 | 49.9049
|  |  | 44734.4091 | 49.9048
|  |  | 44734.4091 | 49.9047
|  |  | 44734.4091 | 49.9047
|  |  | 44734.4091 | 49.9047
|  |  | 44734.4092 | 49.9047
|  |  | 44734.4092 | 49.9047
|  |  | 44734.4092 | 49.9047
|  |  | 44734.4092 | 49.9046
|  |  | 44734.4092 | 49.9045
|  |  | 44734.4092 | 49.9044
|  |  | 44734.4092 | 49.9044
|  |  | 44734.4092 | 49.9044
|  |  | 44734.4092 | 49.9043
|  |  | 44734.4092 | 49.9043
|  |  | 44734.4092 | 49.9043
|  |  | 44734.4092 | 49.9043
|  |  | 44734.4092 | 49.9042
|  |  | 44734.4092 | 49.9042
|  |  | 44734.4092 | 49.9041
|  |  | 44734.4092 | 49.9041
|  |  | 44734.4092 | 49.904
|  |  | 44734.4092 | 49.904
|  |  | 44734.4092 | 49.904
|  |  | 44734.4092 | 49.904
|  |  | 44734.4092 | 49.904
|  |  | 2022-06-22 09:49 | 49.904
|  |  | 44734.4092 | 49.9041
|  |  | 44734.4092 | 49.9041
|  |  | 44734.4092 | 49.9041
|  |  | 44734.4092 | 49.9041
|  |  | 44734.4092 | 49.904
|  |  | 44734.4092 | 49.904
|  |  | 44734.4092 | 49.904
|  |  | 44734.4092 | 49.9039
|  |  | 44734.4092 | 49.9039
|  |  | 44734.4092 | 49.9039
|  |  | 44734.4092 | 49.904
|  |  | 44734.4092 | 49.904
|  |  | 44734.4092 | 49.9041
|  |  | 44734.4092 | 49.9041
|  |  | 44734.4092 | 49.9041
|  |  | 44734.4092 | 49.904
|  |  | 44734.4092 | 49.904
|  |  | 44734.4092 | 49.904
|  |  | 44734.4092 | 49.9039
|  |  | 44734.4092 | 49.9039
|  |  | 44734.4092 | 49.904
|  |  | 44734.4092 | 49.904
|  |  | 44734.4092 | 49.9039
|  |  | 44734.4092 | 49.9038
|  |  | 44734.4092 | 49.9038
|  |  | 44734.4092 | 49.9037
|  |  | 44734.4092 | 49.9037
|  |  | 44734.4092 | 49.9037
|  |  | 44734.4092 | 49.9036
|  |  | 44734.4092 | 49.9036
|  |  | 44734.4092 | 49.9036
|  |  | 44734.4092 | 49.9036
|  |  | 44734.4092 | 49.9036
|  |  | 44734.4092 | 49.9036
|  |  | 44734.4092 | 49.9036
|  |  | 44734.4092 | 49.9036
|  |  | 44734.4092 | 49.9037
|  |  | 44734.4092 | 49.9037
|  |  | 44734.4092 | 49.9037
|  |  | 44734.4092 | 49.9037
|  |  | 44734.4092 | 49.9038
|  |  | 44734.4092 | 49.9038
|  |  | 44734.4092 | 49.9038
|  |  | 44734.4092 | 49.9038
|  |  | 44734.4092 | 49.9038
|  |  | 44734.4092 | 49.9037
|  |  | 44734.4092 | 49.9038
|  |  | 44734.4092 | 49.9038
|  |  | 44734.4092 | 49.9039
|  |  | 2022-06-22 09:49 | 49.9039
|  |  | 44734.4092 | 49.9039
|  |  | 44734.4092 | 49.904
|  |  | 44734.4092 | 49.904
|  |  | 44734.4092 | 49.9041
|  |  | 44734.4092 | 49.904
|  |  | 44734.4092 | 49.904
|  |  | 44734.4092 | 49.904
|  |  | 44734.4092 | 49.904
|  |  | 44734.4092 | 49.9041
|  |  | 44734.4092 | 49.9041
|  |  | 44734.4092 | 49.9041
|  |  | 44734.4092 | 49.9042
|  |  | 44734.4092 | 49.9042
|  |  | 44734.4092 | 49.9042
|  |  | 44734.4092 | 49.9042
|  |  | 44734.4092 | 49.9042
|  |  | 44734.4092 | 49.9043
|  |  | 44734.4092 | 49.9044
|  |  | 44734.4092 | 49.9044
|  |  | 44734.4092 | 49.9044
|  |  | 44734.4092 | 49.9045
|  |  | 44734.4092 | 49.9045
|  |  | 44734.4092 | 49.9046
|  |  | 44734.4092 | 49.9046
|  |  | 44734.4092 | 49.9047
|  |  | 44734.4092 | 49.9047
|  |  | 44734.4092 | 49.9047
|  |  | 44734.4092 | 49.9048
|  |  | 44734.4092 | 49.9049
|  |  | 44734.4092 | 49.905
|  |  | 44734.4092 | 49.9049
|  |  | 44734.4092 | 49.9049
|  |  | 44734.4092 | 49.905
|  |  | 44734.4092 | 49.905
|  |  | 44734.4092 | 49.905
|  |  | 44734.4092 | 49.9051
|  |  | 44734.4092 | 49.9051
|  |  | 44734.4092 | 49.9051
|  |  | 44734.4092 | 49.9052
|  |  | 44734.4092 | 49.9052
|  |  | 44734.4092 | 49.9053
|  |  | 44734.4092 | 49.9054
|  |  | 44734.4092 | 49.9054
|  |  | 44734.4092 | 49.9055
|  |  | 44734.4092 | 49.9056
|  |  | 44734.4092 | 49.9056
|  |  | 44734.4092 | 49.9057
|  |  | 44734.4092 | 49.9057
|  |  | 44734.4092 | 49.9058
|  |  | 2022-06-22 09:49 | 49.9058
|  |  | 44734.4092 | 49.9058
|  |  | 44734.4092 | 49.9057
|  |  | 44734.4092 | 49.9057
|  |  | 44734.4092 | 49.9057
|  |  | 44734.4092 | 49.9057
|  |  | 44734.4092 | 49.9057
|  |  | 44734.4092 | 49.9057
|  |  | 44734.4092 | 49.9058
|  |  | 44734.4092 | 49.9058
|  |  | 44734.4092 | 49.9058
|  |  | 44734.4092 | 49.9059
|  |  | 44734.4092 | 49.9059
|  |  | 44734.4092 | 49.9059
|  |  | 44734.4092 | 49.9059
|  |  | 44734.4092 | 49.906
|  |  | 44734.4092 | 49.9059
|  |  | 44734.4092 | 49.9059
|  |  | 44734.4092 | 49.9059
|  |  | 44734.4092 | 49.906
|  |  | 44734.4092 | 49.906
|  |  | 44734.4092 | 49.9061
|  |  | 44734.4092 | 49.9062
|  |  | 44734.4092 | 49.9062
|  |  | 44734.4092 | 49.9063
|  |  | 44734.4092 | 49.9063
|  |  | 44734.4092 | 49.9063
|  |  | 44734.4092 | 49.9063
|  |  | 44734.4092 | 49.9063
|  |  | 44734.4092 | 49.9064
|  |  | 44734.4092 | 49.9064
|  |  | 44734.4092 | 49.9064
|  |  | 44734.4092 | 49.9065
|  |  | 44734.4092 | 49.9065
|  |  | 44734.4092 | 49.9066
|  |  | 44734.4092 | 49.9067
|  |  | 44734.4092 | 49.9067
|  |  | 44734.4092 | 49.9067
|  |  | 44734.4092 | 49.9068
|  |  | 44734.4092 | 49.9068
|  |  | 44734.4092 | 49.9068
|  |  | 44734.4092 | 49.9068
|  |  | 44734.4092 | 49.9068
|  |  | 44734.4092 | 49.9068
|  |  | 44734.4092 | 49.9068
|  |  | 44734.4092 | 49.9068
|  |  | 44734.4092 | 49.9069
|  |  | 44734.4092 | 49.9069
|  |  | 44734.4092 | 49.9069
|  |  | 44734.4092 | 49.9069
|  |  | 2022-06-22 09:49 | 49.907
|  |  | 44734.4092 | 49.907
|  |  | 44734.4092 | 49.9071
|  |  | 44734.4092 | 49.9071
|  |  | 44734.4092 | 49.9072
|  |  | 44734.4092 | 49.9073
|  |  | 44734.4092 | 49.9073
|  |  | 44734.4092 | 49.9073
|  |  | 44734.4092 | 49.9072
|  |  | 44734.4092 | 49.9072
|  |  | 44734.4092 | 49.9072
|  |  | 44734.4092 | 49.9072
|  |  | 44734.4092 | 49.9072
|  |  | 44734.4092 | 49.9072
|  |  | 44734.4092 | 49.9073
|  |  | 44734.4092 | 49.9074
|  |  | 44734.4092 | 49.9075
|  |  | 44734.4092 | 49.9075
|  |  | 44734.4092 | 49.9075
|  |  | 44734.4092 | 49.9075
|  |  | 44734.4092 | 49.9075
|  |  | 44734.4092 | 49.9075
|  |  | 44734.4092 | 49.9075
|  |  | 44734.4092 | 49.9075
|  |  | 44734.4092 | 49.9075
|  |  | 44734.4092 | 49.9075
|  |  | 44734.4092 | 49.9074
|  |  | 44734.4092 | 49.9074
|  |  | 44734.4092 | 49.9073
|  |  | 44734.4092 | 49.9073
|  |  | 44734.4092 | 49.9073
|  |  | 44734.4092 | 49.9073
|  |  | 44734.4092 | 49.9073
|  |  | 44734.4092 | 49.9073
|  |  | 44734.4092 | 49.9073
|  |  | 44734.4092 | 49.9073
|  |  | 44734.4092 | 49.9072
|  |  | 44734.4092 | 49.9072
|  |  | 44734.4092 | 49.9071
|  |  | 44734.4092 | 49.9071
|  |  | 44734.4092 | 49.907
|  |  | 44734.4092 | 49.907
|  |  | 44734.4092 | 49.907
|  |  | 44734.4092 | 49.907
|  |  | 44734.4092 | 49.907
|  |  | 44734.4092 | 49.9071
|  |  | 44734.4092 | 49.9071
|  |  | 44734.4092 | 49.907
|  |  | 44734.4092 | 49.907
|  |  | 44734.4092 | 49.9069
|  |  | 2022-06-22 09:49 | 49.9069

## 20220623-1
In GMT |  |  | High resolution Incident data
Date | Time | Freq | time | freq
2022-06-23 | 10:10 | 50.044 | 2022-06-23 11:10 | 50.0701
2022-06-23 | 10:10 | 50.044 | 44735.4656 | 50.0701
2022-06-23 | 10:10 | 50.046 | 44735.4656 | 50.0701
2022-06-23 | 10:10 | 50.046 | 44735.4656 | 50.0702
2022-06-23 | 10:10 | 50.046 | 44735.4656 | 50.0701
2022-06-23 | 10:10 | 50.047 | 44735.4656 | 50.0702
2022-06-23 | 10:10 | 50.049 | 44735.4656 | 50.0701
2022-06-23 | 10:10 | 50.05 | 44735.4656 | 50.0702
2022-06-23 | 10:10 | 50.052 | 44735.4656 | 50.0701
2022-06-23 | 10:10 | 50.054 | 44735.4656 | 50.07
2022-06-23 | 10:10 | 50.057 | 44735.4656 | 50.07
2022-06-23 | 10:10 | 50.059 | 44735.4656 | 50.07
2022-06-23 | 10:10 | 50.062 | 44735.4656 | 50.07
2022-06-23 | 10:10 | 50.062 | 44735.4656 | 50.07
2022-06-23 | 10:10 | 50.064 | 44735.4656 | 50.0701
2022-06-23 | 10:10 | 50.063 | 44735.4656 | 50.0702
2022-06-23 | 10:10 | 50.063 | 44735.4656 | 50.0702
2022-06-23 | 10:10 | 50.062 | 44735.4656 | 50.0703
2022-06-23 | 10:10 | 50.062 | 44735.4656 | 50.0703
2022-06-23 | 10:10 | 50.06 | 44735.4656 | 50.0703
2022-06-23 | 10:10 | 50.058 | 44735.4656 | 50.0704
2022-06-23 | 10:10 | 50.059 | 44735.4656 | 50.0703
2022-06-23 | 10:10 | 50.062 | 44735.4656 | 50.0702
2022-06-23 | 10:10 | 50.064 | 44735.4656 | 50.0702
2022-06-23 | 10:10 | 50.065 | 44735.4656 | 50.0702
2022-06-23 | 10:10 | 50.063 | 44735.4656 | 50.0701
2022-06-23 | 10:10 | 50.064 | 44735.4656 | 50.0701
2022-06-23 | 10:10 | 50.066 | 44735.4656 | 50.0701
2022-06-23 | 10:10 | 50.068 | 44735.4656 | 50.0701
2022-06-23 | 10:10 | 50.068 | 44735.4656 | 50.0701
2022-06-23 | 10:10 | 50.069 | 44735.4656 | 50.0702
2022-06-23 | 10:11 | 50.069 | 44735.4656 | 50.0703
2022-06-23 | 10:11 | 50.07 | 44735.4656 | 50.0704
2022-06-23 | 10:11 | 50.071 | 44735.4656 | 50.0704
2022-06-23 | 10:11 | 50.072 | 44735.4656 | 50.0705
2022-06-23 | 10:11 | 50.071 | 44735.4656 | 50.0706
2022-06-23 | 10:11 | 50.072 | 44735.4656 | 50.0706
2022-06-23 | 10:11 | 50.072 | 44735.4656 | 50.0706
2022-06-23 | 10:11 | 50.072 | 44735.4656 | 50.0706
2022-06-23 | 10:11 | 50.071 | 44735.4656 | 50.0706
2022-06-23 | 10:11 | 50.068 | 44735.4656 | 50.0705
2022-06-23 | 10:11 | 50.065 | 44735.4656 | 50.0704
2022-06-23 | 10:11 | 50.065 | 44735.4656 | 50.0704
2022-06-23 | 10:11 | 50.062 | 44735.4656 | 50.0704
2022-06-23 | 10:11 | 50.06 | 44735.4656 | 50.0704
2022-06-23 | 10:11 | 50.057 | 44735.4656 | 50.0703
2022-06-23 | 10:11 | 50.055 | 44735.4656 | 50.0703
2022-06-23 | 10:11 | 50.055 | 44735.4656 | 50.0704
2022-06-23 | 10:11 | 50.054 | 44735.4656 | 50.0704
2022-06-23 | 10:11 | 50.054 | 44735.4656 | 50.0705
2022-06-23 | 10:11 | 50.055 | 2022-06-23 11:11 | 50.0705
2022-06-23 | 10:11 | 50.053 | 44735.4656 | 50.0706
2022-06-23 | 10:11 | 50.037 | 44735.4656 | 50.0706
2022-06-23 | 10:11 | 50.026 | 44735.4656 | 50.0707
2022-06-23 | 10:11 | 50.006 | 44735.4656 | 50.0707
2022-06-23 | 10:11 | 49.987 | 44735.4656 | 50.0706
2022-06-23 | 10:11 | 49.977 | 44735.4656 | 50.0706
2022-06-23 | 10:11 | 49.97 | 44735.4656 | 50.0706
2022-06-23 | 10:11 | 49.966 | 44735.4656 | 50.0706
2022-06-23 | 10:11 | 49.96 | 44735.4656 | 50.0705
2022-06-23 | 10:11 | 49.957 | 44735.4656 | 50.0704
2022-06-23 | 10:11 | 49.955 | 44735.4656 | 50.0705
2022-06-23 | 10:11 | 49.949 | 44735.4656 | 50.0705
2022-06-23 | 10:11 | 49.946 | 44735.4656 | 50.0705
2022-06-23 | 10:11 | 49.942 | 44735.4656 | 50.0704
2022-06-23 | 10:11 | 49.937 | 44735.4656 | 50.0704
2022-06-23 | 10:11 | 49.937 | 44735.4656 | 50.0704
2022-06-23 | 10:11 | 49.936 | 44735.4656 | 50.0704
2022-06-23 | 10:11 | 49.937 | 44735.4656 | 50.0704
2022-06-23 | 10:11 | 49.938 | 44735.4656 | 50.0704
2022-06-23 | 10:11 | 49.942 | 44735.4656 | 50.0704
2022-06-23 | 10:11 | 49.942 | 44735.4656 | 50.0704
2022-06-23 | 10:11 | 49.944 | 44735.4656 | 50.0705
2022-06-23 | 10:11 | 49.944 | 44735.4656 | 50.0705
2022-06-23 | 10:11 | 49.945 | 44735.4656 | 50.0705
2022-06-23 | 10:11 | 49.943 | 44735.4656 | 50.0705
2022-06-23 | 10:11 | 49.942 | 44735.4656 | 50.0706
2022-06-23 | 10:11 | 49.941 | 44735.4656 | 50.0707
2022-06-23 | 10:11 | 49.94 | 44735.4656 | 50.0708
2022-06-23 | 10:11 | 49.941 | 44735.4656 | 50.0709
2022-06-23 | 10:11 | 49.941 | 44735.4656 | 50.071
2022-06-23 | 10:11 | 49.936 | 44735.4656 | 50.0711
2022-06-23 | 10:11 | 49.936 | 44735.4656 | 50.0712
2022-06-23 | 10:11 | 49.935 | 44735.4656 | 50.0712
2022-06-23 | 10:11 | 49.934 | 44735.4656 | 50.0713
2022-06-23 | 10:11 | 49.936 | 44735.4656 | 50.0713
2022-06-23 | 10:11 | 49.94 | 44735.4656 | 50.0714
2022-06-23 | 10:11 | 49.941 | 44735.4656 | 50.0714
2022-06-23 | 10:11 | 49.943 | 44735.4656 | 50.0715
2022-06-23 | 10:11 | 49.945 | 44735.4656 | 50.0715
2022-06-23 | 10:12 | 49.946 | 44735.4656 | 50.0716
2022-06-23 | 10:12 | 49.947 | 44735.4656 | 50.0717
2022-06-23 | 10:12 | 49.948 | 44735.4656 | 50.0717
2022-06-23 | 10:12 | 49.946 | 44735.4656 | 50.0718
2022-06-23 | 10:12 | 49.945 | 44735.4656 | 50.0719
2022-06-23 | 10:12 | 49.943 | 44735.4656 | 50.0719
2022-06-23 | 10:12 | 49.939 | 44735.4656 | 50.0719
2022-06-23 | 10:12 | 49.934 | 44735.4656 | 50.0718
2022-06-23 | 10:12 | 49.931 | 44735.4656 | 50.0719
2022-06-23 | 10:12 | 49.929 | 44735.4656 | 50.0718
2022-06-23 | 10:12 | 49.927 | 2022-06-23 11:11 | 50.0718
2022-06-23 | 10:12 | 49.924 | 44735.4656 | 50.0717
2022-06-23 | 10:12 | 49.923 | 44735.4656 | 50.0717
2022-06-23 | 10:12 | 49.921 | 44735.4656 | 50.0717
2022-06-23 | 10:12 | 49.919 | 44735.4656 | 50.0717
2022-06-23 | 10:12 | 49.918 | 44735.4656 | 50.0717
2022-06-23 | 10:12 | 49.915 | 44735.4656 | 50.0717
2022-06-23 | 10:12 | 49.916 | 44735.4656 | 50.0717
2022-06-23 | 10:12 | 49.915 | 44735.4656 | 50.0718
2022-06-23 | 10:12 | 49.916 | 44735.4657 | 50.072
2022-06-23 | 10:12 | 49.917 | 44735.4657 | 50.0719
2022-06-23 | 10:12 | 49.917 | 44735.4657 | 50.072
2022-06-23 | 10:12 | 49.92 | 44735.4657 | 50.072
2022-06-23 | 10:12 | 49.921 | 44735.4657 | 50.0721
2022-06-23 | 10:12 | 49.922 | 44735.4657 | 50.0721
2022-06-23 | 10:12 | 49.926 | 44735.4657 | 50.0722
2022-06-23 | 10:12 | 49.93 | 44735.4657 | 50.0722
2022-06-23 | 10:12 | 49.931 | 44735.4657 | 50.0722
2022-06-23 | 10:12 | 49.931 | 44735.4657 | 50.0722
2022-06-23 | 10:12 | 49.932 | 44735.4657 | 50.0722
2022-06-23 | 10:12 | 49.933 | 44735.4657 | 50.0722
2022-06-23 | 10:12 | 49.933 | 44735.4657 | 50.0721
2022-06-23 | 10:12 | 49.928 | 44735.4657 | 50.0721
2022-06-23 | 10:12 | 49.928 | 44735.4657 | 50.0721
2022-06-23 | 10:12 | 49.926 | 44735.4657 | 50.0721
2022-06-23 | 10:12 | 49.924 | 44735.4657 | 50.0721
2022-06-23 | 10:12 | 49.922 | 44735.4657 | 50.0721
2022-06-23 | 10:12 | 49.924 | 44735.4657 | 50.0722
2022-06-23 | 10:12 | 49.926 | 44735.4657 | 50.0722
2022-06-23 | 10:12 | 49.925 | 44735.4657 | 50.0722
2022-06-23 | 10:12 | 49.927 | 44735.4657 | 50.0723
2022-06-23 | 10:12 | 49.929 | 44735.4657 | 50.0724
2022-06-23 | 10:12 | 49.931 | 44735.4657 | 50.0724
2022-06-23 | 10:12 | 49.933 | 44735.4657 | 50.0725
2022-06-23 | 10:12 | 49.933 | 44735.4657 | 50.0726
2022-06-23 | 10:12 | 49.935 | 44735.4657 | 50.0726
2022-06-23 | 10:12 | 49.935 | 44735.4657 | 50.0727
2022-06-23 | 10:12 | 49.937 | 44735.4657 | 50.0727
2022-06-23 | 10:12 | 49.936 | 44735.4657 | 50.0727
2022-06-23 | 10:12 | 49.938 | 44735.4657 | 50.0728
2022-06-23 | 10:12 | 49.941 | 44735.4657 | 50.0728
2022-06-23 | 10:12 | 49.94 | 44735.4657 | 50.0727
2022-06-23 | 10:12 | 49.94 | 44735.4657 | 50.0727
2022-06-23 | 10:12 | 49.938 | 44735.4657 | 50.0727
2022-06-23 | 10:12 | 49.938 | 44735.4657 | 50.0727
2022-06-23 | 10:12 | 49.937 | 44735.4657 | 50.0726
2022-06-23 | 10:12 | 49.937 | 44735.4657 | 50.0726
2022-06-23 | 10:12 | 49.938 | 44735.4657 | 50.0725
2022-06-23 | 10:12 | 49.938 | 44735.4657 | 50.0726
2022-06-23 | 10:12 | 49.939 | 44735.4657 | 50.0725
2022-06-23 | 10:12 | 49.938 | 2022-06-23 11:11 | 50.0725
2022-06-23 | 10:13 | 49.938 | 44735.4657 | 50.0726
2022-06-23 | 10:13 | 49.939 | 44735.4657 | 50.0727
2022-06-23 | 10:13 | 49.943 | 44735.4657 | 50.0728
2022-06-23 | 10:13 | 49.942 | 44735.4657 | 50.0729
2022-06-23 | 10:13 | 49.941 | 44735.4657 | 50.073
2022-06-23 | 10:13 | 49.943 | 44735.4657 | 50.073
2022-06-23 | 10:13 | 49.941 | 44735.4657 | 50.073
2022-06-23 | 10:13 | 49.944 | 44735.4657 | 50.073
2022-06-23 | 10:13 | 49.943 | 44735.4657 | 50.0729
2022-06-23 | 10:13 | 49.944 | 44735.4657 | 50.0729
2022-06-23 | 10:13 | 49.942 | 44735.4657 | 50.0729
2022-06-23 | 10:13 | 49.942 | 44735.4657 | 50.0728
2022-06-23 | 10:13 | 49.944 | 44735.4657 | 50.0728
2022-06-23 | 10:13 | 49.94 | 44735.4657 | 50.0728
2022-06-23 | 10:13 | 49.943 | 44735.4657 | 50.0728
2022-06-23 | 10:13 | 49.943 | 44735.4657 | 50.0727
2022-06-23 | 10:13 | 49.944 | 44735.4657 | 50.0728
2022-06-23 | 10:13 | 49.944 | 44735.4657 | 50.0729
2022-06-23 | 10:13 | 49.943 | 44735.4657 | 50.0729
2022-06-23 | 10:13 | 49.942 | 44735.4657 | 50.073
2022-06-23 | 10:13 | 49.942 | 44735.4657 | 50.073
2022-06-23 | 10:13 | 49.94 | 44735.4657 | 50.073
2022-06-23 | 10:13 | 49.941 | 44735.4657 | 50.073
2022-06-23 | 10:13 | 49.941 | 44735.4657 | 50.0729
2022-06-23 | 10:13 | 49.94 | 44735.4657 | 50.0729
2022-06-23 | 10:13 | 49.938 | 44735.4657 | 50.0728
2022-06-23 | 10:13 | 49.933 | 44735.4657 | 50.0728
2022-06-23 | 10:13 | 49.929 | 44735.4657 | 50.0728
2022-06-23 | 10:13 | 49.928 | 44735.4657 | 50.0727
2022-06-23 | 10:13 | 49.926 | 44735.4657 | 50.0728
2022-06-23 | 10:13 | 49.924 | 44735.4657 | 50.0727
2022-06-23 | 10:13 | 49.921 | 44735.4657 | 50.0727
2022-06-23 | 10:13 | 49.921 | 44735.4657 | 50.0727
2022-06-23 | 10:13 | 49.922 | 44735.4657 | 50.0728
2022-06-23 | 10:13 | 49.921 | 44735.4657 | 50.0728
2022-06-23 | 10:13 | 49.921 | 44735.4657 | 50.0729
2022-06-23 | 10:13 | 49.922 | 44735.4657 | 50.0729
2022-06-23 | 10:13 | 49.921 | 44735.4657 | 50.0729
2022-06-23 | 10:13 | 49.921 | 44735.4657 | 50.0729
2022-06-23 | 10:13 | 49.919 | 44735.4657 | 50.0729
2022-06-23 | 10:13 | 49.917 | 44735.4657 | 50.0729
2022-06-23 | 10:13 | 49.914 | 44735.4657 | 50.0728
2022-06-23 | 10:13 | 49.914 | 44735.4657 | 50.0728
2022-06-23 | 10:13 | 49.913 | 44735.4657 | 50.0727
2022-06-23 | 10:13 | 49.913 | 44735.4657 | 50.0727
2022-06-23 | 10:13 | 49.911 | 44735.4657 | 50.0726
2022-06-23 | 10:13 | 49.909 | 44735.4657 | 50.0726
2022-06-23 | 10:13 | 49.909 | 44735.4657 | 50.0726
2022-06-23 | 10:13 | 49.91 | 44735.4657 | 50.0725
2022-06-23 | 10:13 | 49.908 | 2022-06-23 11:11 | 50.0725
2022-06-23 | 10:13 | 49.91 | 44735.4657 | 50.0725
2022-06-23 | 10:13 | 49.908 | 44735.4657 | 50.0725
2022-06-23 | 10:13 | 49.906 | 44735.4657 | 50.0725
2022-06-23 | 10:13 | 49.907 | 44735.4657 | 50.0725
2022-06-23 | 10:13 | 49.908 | 44735.4657 | 50.0725
2022-06-23 | 10:13 | 49.906 | 44735.4657 | 50.0724
2022-06-23 | 10:13 | 49.908 | 44735.4657 | 50.0724
2022-06-23 | 10:13 | 49.905 | 44735.4657 | 50.0724
2022-06-23 | 10:13 | 49.906 | 44735.4657 | 50.0724
2022-06-23 | 10:14 | 49.905 | 44735.4657 | 50.0724
2022-06-23 | 10:14 | 49.904 | 44735.4657 | 50.0724
2022-06-23 | 10:14 | 49.905 | 44735.4657 | 50.0725
2022-06-23 | 10:14 | 49.903 | 44735.4657 | 50.0726
2022-06-23 | 10:14 | 49.906 | 44735.4657 | 50.0726
2022-06-23 | 10:14 | 49.904 | 44735.4657 | 50.0725
2022-06-23 | 10:14 | 49.905 | 44735.4657 | 50.0725
2022-06-23 | 10:14 | 49.903 | 44735.4657 | 50.0725
2022-06-23 | 10:14 | 49.904 | 44735.4657 | 50.0725
2022-06-23 | 10:14 | 49.902 | 44735.4657 | 50.0725
2022-06-23 | 10:14 | 49.906 | 44735.4657 | 50.0724
2022-06-23 | 10:14 | 49.907 | 44735.4657 | 50.0724
2022-06-23 | 10:14 | 49.91 | 44735.4657 | 50.0724
2022-06-23 | 10:14 | 49.914 | 44735.4657 | 50.0724
2022-06-23 | 10:14 | 49.914 | 44735.4657 | 50.0724
2022-06-23 | 10:14 | 49.918 | 44735.4657 | 50.0724
2022-06-23 | 10:14 | 49.918 | 44735.4657 | 50.0724
2022-06-23 | 10:14 | 49.921 | 44735.4657 | 50.0724
2022-06-23 | 10:14 | 49.921 | 44735.4657 | 50.0725
2022-06-23 | 10:14 | 49.918 | 44735.4657 | 50.0725
2022-06-23 | 10:14 | 49.918 | 44735.4657 | 50.0725
2022-06-23 | 10:14 | 49.917 | 44735.4657 | 50.0725
2022-06-23 | 10:14 | 49.917 | 44735.4657 | 50.0725
2022-06-23 | 10:14 | 49.918 | 44735.4657 | 50.0724
2022-06-23 | 10:14 | 49.918 | 44735.4657 | 50.0724
2022-06-23 | 10:14 | 49.921 | 44735.4657 | 50.0723
2022-06-23 | 10:14 | 49.923 | 44735.4657 | 50.0723
2022-06-23 | 10:14 | 49.926 | 44735.4657 | 50.0723
2022-06-23 | 10:14 | 49.928 | 44735.4657 | 50.0724
2022-06-23 | 10:14 | 49.929 | 44735.4657 | 50.0723
2022-06-23 | 10:14 | 49.929 | 44735.4657 | 50.0723
2022-06-23 | 10:14 | 49.929 | 44735.4657 | 50.0723
2022-06-23 | 10:14 | 49.926 | 44735.4657 | 50.0724
2022-06-23 | 10:14 | 49.922 | 44735.4657 | 50.0724
2022-06-23 | 10:14 | 49.921 | 44735.4657 | 50.0725
2022-06-23 | 10:14 | 49.922 | 44735.4657 | 50.0725
2022-06-23 | 10:14 | 49.92 | 44735.4657 | 50.0726
2022-06-23 | 10:14 | 49.919 | 44735.4657 | 50.0726
2022-06-23 | 10:14 | 49.916 | 44735.4657 | 50.0726
2022-06-23 | 10:14 | 49.915 | 44735.4657 | 50.0726
2022-06-23 | 10:14 | 49.915 | 2022-06-23 11:11 | 50.0726
2022-06-23 | 10:14 | 49.917 | 44735.4657 | 50.0726
2022-06-23 | 10:14 | 49.918 | 44735.4657 | 50.0727
2022-06-23 | 10:14 | 49.919 | 44735.4657 | 50.0727
2022-06-23 | 10:14 | 49.92 | 44735.4657 | 50.0728
2022-06-23 | 10:14 | 49.924 | 44735.4657 | 50.0729
2022-06-23 | 10:14 | 49.928 | 44735.4657 | 50.0729
2022-06-23 | 10:14 | 49.929 | 44735.4657 | 50.0729
2022-06-23 | 10:14 | 49.932 | 44735.4657 | 50.0729
2022-06-23 | 10:14 | 49.934 | 44735.4657 | 50.0729
2022-06-23 | 10:14 | 49.935 | 44735.4657 | 50.0729
2022-06-23 | 10:14 | 49.939 | 44735.4657 | 50.0728
2022-06-23 | 10:14 | 49.94 | 44735.4657 | 50.0728
2022-06-23 | 10:14 | 49.939 | 44735.4657 | 50.0728
2022-06-23 | 10:14 | 49.935 | 44735.4657 | 50.0728
2022-06-23 | 10:14 | 49.933 | 44735.4657 | 50.0727
2022-06-23 | 10:14 | 49.932 | 44735.4657 | 50.0726
2022-06-23 | 10:14 | 49.93 | 44735.4657 | 50.0726
2022-06-23 | 10:14 | 49.931 | 44735.4657 | 50.0726
2022-06-23 | 10:14 | 49.933 | 44735.4657 | 50.0726
2022-06-23 | 10:14 | 49.933 | 44735.4657 | 50.0725
2022-06-23 | 10:15 | 49.932 | 44735.4657 | 50.0725
2022-06-23 | 10:15 | 49.934 | 44735.4657 | 50.0725
2022-06-23 | 10:15 | 49.935 | 44735.4657 | 50.0725
2022-06-23 | 10:15 | 49.936 | 44735.4657 | 50.0725
2022-06-23 | 10:15 | 49.934 | 44735.4657 | 50.0725
2022-06-23 | 10:15 | 49.933 | 44735.4657 | 50.0725
2022-06-23 | 10:15 | 49.933 | 44735.4657 | 50.0725
2022-06-23 | 10:15 | 49.933 | 44735.4657 | 50.0726
2022-06-23 | 10:15 | 49.933 | 44735.4657 | 50.0727
2022-06-23 | 10:15 | 49.932 | 44735.4657 | 50.0727
2022-06-23 | 10:15 | 49.932 | 44735.4657 | 50.0727
2022-06-23 | 10:15 | 49.93 | 44735.4657 | 50.0728
2022-06-23 | 10:15 | 49.933 | 44735.4657 | 50.0728
2022-06-23 | 10:15 | 49.934 | 44735.4657 | 50.0728
2022-06-23 | 10:15 | 49.935 | 44735.4657 | 50.0729
2022-06-23 | 10:15 | 49.937 | 44735.4657 | 50.0729
2022-06-23 | 10:15 | 49.936 | 44735.4657 | 50.073
2022-06-23 | 10:15 | 49.936 | 44735.4657 | 50.073
2022-06-23 | 10:15 | 49.937 | 44735.4657 | 50.073
2022-06-23 | 10:15 | 49.937 | 44735.4657 | 50.0731
2022-06-23 | 10:15 | 49.938 | 44735.4657 | 50.0731
2022-06-23 | 10:15 | 49.938 | 44735.4657 | 50.0731
2022-06-23 | 10:15 | 49.939 | 44735.4657 | 50.0731
2022-06-23 | 10:15 | 49.94 | 44735.4657 | 50.0731
2022-06-23 | 10:15 | 49.94 | 44735.4657 | 50.0731
2022-06-23 | 10:15 | 49.938 | 44735.4657 | 50.0731
2022-06-23 | 10:15 | 49.937 | 44735.4657 | 50.0731
2022-06-23 | 10:15 | 49.935 | 44735.4657 | 50.0731
2022-06-23 | 10:15 | 49.935 | 44735.4657 | 50.0731
2022-06-23 | 10:15 | 49.934 | 2022-06-23 11:11 | 50.0731
2022-06-23 | 10:15 | 49.931 | 44735.4657 | 50.0732
2022-06-23 | 10:15 | 49.926 | 44735.4657 | 50.0732
2022-06-23 | 10:15 | 49.924 | 44735.4657 | 50.0732
2022-06-23 | 10:15 | 49.922 | 44735.4657 | 50.0733
2022-06-23 | 10:15 | 49.922 | 44735.4657 | 50.0733
2022-06-23 | 10:15 | 49.921 | 44735.4657 | 50.0734
2022-06-23 | 10:15 | 49.918 | 44735.4657 | 50.0734
2022-06-23 | 10:15 | 49.916 | 44735.4657 | 50.0735
2022-06-23 | 10:15 | 49.915 | 44735.4657 | 50.0735
2022-06-23 | 10:15 | 49.917 | 44735.4657 | 50.0735
2022-06-23 | 10:15 | 49.919 | 44735.4657 | 50.0735
2022-06-23 | 10:15 | 49.922 | 44735.4657 | 50.0734
2022-06-23 | 10:15 | 49.924 | 44735.4657 | 50.0734
2022-06-23 | 10:15 | 49.926 | 44735.4657 | 50.0734
2022-06-23 | 10:15 | 49.922 | 44735.4657 | 50.0735
2022-06-23 | 10:15 | 49.92 | 44735.4657 | 50.0735
2022-06-23 | 10:15 | 49.919 | 44735.4657 | 50.0737
2022-06-23 | 10:15 | 49.919 | 44735.4657 | 50.0737
2022-06-23 | 10:15 | 49.913 | 44735.4657 | 50.0738
2022-06-23 | 10:15 | 49.912 | 44735.4657 | 50.0738
2022-06-23 | 10:15 | 49.913 | 44735.4657 | 50.0739
2022-06-23 | 10:15 | 49.913 | 44735.4657 | 50.0739
2022-06-23 | 10:15 | 49.911 | 44735.4657 | 50.074
2022-06-23 | 10:15 | 49.912 | 44735.4657 | 50.074
2022-06-23 | 10:15 | 49.914 | 44735.4657 | 50.0739
2022-06-23 | 10:15 | 49.916 | 44735.4657 | 50.0739
2022-06-23 | 10:15 | 49.914 | 44735.4657 | 50.0739
2022-06-23 | 10:15 | 49.913 | 44735.4657 | 50.0739
2022-06-23 | 10:15 | 49.912 | 44735.4657 | 50.0738
2022-06-23 | 10:16 | 49.914 | 44735.4657 | 50.0739
2022-06-23 | 10:16 | 49.916 | 44735.4657 | 50.0739
2022-06-23 | 10:16 | 49.916 | 44735.4657 | 50.0739
2022-06-23 | 10:16 | 49.916 | 44735.4657 | 50.0739
2022-06-23 | 10:16 | 49.916 | 44735.4657 | 50.074
2022-06-23 | 10:16 | 49.916 | 44735.4657 | 50.074
2022-06-23 | 10:16 | 49.918 | 44735.4657 | 50.074
2022-06-23 | 10:16 | 49.921 | 44735.4657 | 50.074
2022-06-23 | 10:16 | 49.925 | 44735.4657 | 50.074
2022-06-23 | 10:16 | 49.929 | 44735.4657 | 50.074
2022-06-23 | 10:16 | 49.931 | 44735.4657 | 50.074
2022-06-23 | 10:16 | 49.936 | 44735.4657 | 50.0741
2022-06-23 | 10:16 | 49.938 | 44735.4657 | 50.0741
2022-06-23 | 10:16 | 49.94 | 44735.4657 | 50.0741
2022-06-23 | 10:16 | 49.939 | 44735.4657 | 50.0741
2022-06-23 | 10:16 | 49.939 | 44735.4657 | 50.0741
2022-06-23 | 10:16 | 49.938 | 44735.4657 | 50.0741
2022-06-23 | 10:16 | 49.933 | 44735.4657 | 50.0741
2022-06-23 | 10:16 | 49.928 | 44735.4657 | 50.0741
2022-06-23 | 10:16 | 49.925 | 44735.4657 | 50.0741
2022-06-23 | 10:16 | 49.922 | 2022-06-23 11:11 | 50.0741
2022-06-23 | 10:16 | 49.917 | 44735.4657 | 50.0741
2022-06-23 | 10:16 | 49.915 | 44735.4657 | 50.0741
2022-06-23 | 10:16 | 49.915 | 44735.4657 | 50.0741
2022-06-23 | 10:16 | 49.912 | 44735.4657 | 50.0741
2022-06-23 | 10:16 | 49.91 | 44735.4657 | 50.0741
2022-06-23 | 10:16 | 49.91 | 44735.4657 | 50.0741
2022-06-23 | 10:16 | 49.908 | 44735.4657 | 50.0741
2022-06-23 | 10:16 | 49.908 | 44735.4657 | 50.0741
2022-06-23 | 10:16 | 49.908 | 44735.4657 | 50.0741
2022-06-23 | 10:16 | 49.907 | 44735.4657 | 50.0741
2022-06-23 | 10:16 | 49.91 | 44735.4657 | 50.0741
2022-06-23 | 10:16 | 49.912 | 44735.4657 | 50.0741
2022-06-23 | 10:16 | 49.913 | 44735.4657 | 50.074
2022-06-23 | 10:16 | 49.915 | 44735.4657 | 50.0741
2022-06-23 | 10:16 | 49.917 | 44735.4657 | 50.0741
2022-06-23 | 10:16 | 49.921 | 44735.4657 | 50.0741
2022-06-23 | 10:16 | 49.921 | 44735.4657 | 50.0742
2022-06-23 | 10:16 | 49.925 | 44735.4657 | 50.0742
2022-06-23 | 10:16 | 49.928 | 44735.4657 | 50.0742
2022-06-23 | 10:16 | 49.928 | 44735.4657 | 50.0742
2022-06-23 | 10:16 | 49.926 | 44735.4657 | 50.0741
2022-06-23 | 10:16 | 49.925 | 44735.4657 | 50.074
2022-06-23 | 10:16 | 49.925 | 44735.4657 | 50.0739
2022-06-23 | 10:16 | 49.926 | 44735.4657 | 50.0739
2022-06-23 | 10:16 | 49.925 | 44735.4657 | 50.0739
2022-06-23 | 10:16 | 49.925 | 44735.4657 | 50.0739
2022-06-23 | 10:16 | 49.924 | 44735.4657 | 50.0738
2022-06-23 | 10:16 | 49.926 | 44735.4657 | 50.0738
2022-06-23 | 10:16 | 49.926 | 44735.4657 | 50.0737
2022-06-23 | 10:16 | 49.928 | 44735.4657 | 50.0736
2022-06-23 | 10:16 | 49.932 | 44735.4657 | 50.0735
2022-06-23 | 10:16 | 49.933 | 44735.4657 | 50.0735
2022-06-23 | 10:16 | 49.935 | 44735.4657 | 50.0734
2022-06-23 | 10:16 | 49.939 | 44735.4657 | 50.0734
2022-06-23 | 10:16 | 49.939 | 44735.4657 | 50.0734
2022-06-23 | 10:16 | 49.939 | 44735.4657 | 50.0735
2022-06-23 | 10:16 | 49.937 | 44735.4657 | 50.0735
2022-06-23 | 10:16 | 49.937 | 44735.4657 | 50.0736
2022-06-23 | 10:16 | 49.937 | 44735.4657 | 50.0736
2022-06-23 | 10:16 | 49.936 | 44735.4657 | 50.0737
2022-06-23 | 10:17 | 49.937 | 44735.4657 | 50.0737
2022-06-23 | 10:17 | 49.938 | 44735.4657 | 50.0737
2022-06-23 | 10:17 | 49.938 | 44735.4657 | 50.0738
2022-06-23 | 10:17 | 49.94 | 44735.4657 | 50.0738
2022-06-23 | 10:17 | 49.941 | 44735.4657 | 50.0738
2022-06-23 | 10:17 | 49.942 | 44735.4657 | 50.0739
2022-06-23 | 10:17 | 49.944 | 44735.4657 | 50.0739
2022-06-23 | 10:17 | 49.945 | 44735.4657 | 50.0739
2022-06-23 | 10:17 | 49.945 | 44735.4657 | 50.0739
2022-06-23 | 10:17 | 49.941 | 2022-06-23 11:11 | 50.0739
2022-06-23 | 10:17 | 49.94 | 44735.4657 | 50.0738
2022-06-23 | 10:17 | 49.94 | 44735.4657 | 50.0738
2022-06-23 | 10:17 | 49.935 | 44735.4657 | 50.0737
2022-06-23 | 10:17 | 49.933 | 44735.4657 | 50.0737
2022-06-23 | 10:17 | 49.93 | 44735.4657 | 50.0737
2022-06-23 | 10:17 | 49.928 | 44735.4657 | 50.0737
2022-06-23 | 10:17 | 49.928 | 44735.4657 | 50.0737
2022-06-23 | 10:17 | 49.925 | 44735.4657 | 50.0737
2022-06-23 | 10:17 | 49.926 | 44735.4657 | 50.0737
2022-06-23 | 10:17 | 49.924 | 44735.4657 | 50.0737
2022-06-23 | 10:17 | 49.927 | 44735.4657 | 50.0738
2022-06-23 | 10:17 | 49.927 | 44735.4657 | 50.0738
2022-06-23 | 10:17 | 49.926 | 44735.4657 | 50.0738
2022-06-23 | 10:17 | 49.926 | 44735.4657 | 50.0737
2022-06-23 | 10:17 | 49.923 | 44735.4657 | 50.0737
2022-06-23 | 10:17 | 49.924 | 44735.4657 | 50.0737
2022-06-23 | 10:17 | 49.922 | 44735.4657 | 50.0736
2022-06-23 | 10:17 | 49.925 | 44735.4657 | 50.0735
2022-06-23 | 10:17 | 49.923 | 44735.4657 | 50.0735
2022-06-23 | 10:17 | 49.924 | 44735.4657 | 50.0734
2022-06-23 | 10:17 | 49.92 | 44735.4657 | 50.0734
2022-06-23 | 10:17 | 49.919 | 44735.4657 | 50.0734
2022-06-23 | 10:17 | 49.917 | 44735.4657 | 50.0733
2022-06-23 | 10:17 | 49.919 | 44735.4657 | 50.0732
2022-06-23 | 10:17 | 49.921 | 44735.4657 | 50.0732
2022-06-23 | 10:17 | 49.922 | 44735.4657 | 50.073
2022-06-23 | 10:17 | 49.922 | 44735.4657 | 50.073
2022-06-23 | 10:17 | 49.923 | 44735.4657 | 50.0729
2022-06-23 | 10:17 | 49.92 | 44735.4657 | 50.0728
2022-06-23 | 10:17 | 49.922 | 44735.4657 | 50.0728
2022-06-23 | 10:17 | 49.919 | 44735.4657 | 50.0727
2022-06-23 | 10:17 | 49.919 | 44735.4657 | 50.0726
2022-06-23 | 10:17 | 49.917 | 44735.4657 | 50.0724
2022-06-23 | 10:17 | 49.919 | 44735.4657 | 50.0724
2022-06-23 | 10:17 | 49.924 | 44735.4657 | 50.0723
2022-06-23 | 10:17 | 49.923 | 44735.4657 | 50.0722
2022-06-23 | 10:17 | 49.927 | 44735.4657 | 50.0721
2022-06-23 | 10:17 | 49.93 | 44735.4657 | 50.0721
2022-06-23 | 10:17 | 49.933 | 44735.4657 | 50.072
2022-06-23 | 10:17 | 49.937 | 44735.4657 | 50.072
2022-06-23 | 10:17 | 49.941 | 44735.4657 | 50.072
2022-06-23 | 10:17 | 49.941 | 44735.4657 | 50.072
2022-06-23 | 10:17 | 49.944 | 44735.4657 | 50.072
2022-06-23 | 10:17 | 49.944 | 44735.4657 | 50.072
2022-06-23 | 10:17 | 49.943 | 44735.4657 | 50.072
2022-06-23 | 10:17 | 49.942 | 44735.4657 | 50.072
2022-06-23 | 10:17 | 49.944 | 44735.4657 | 50.072
2022-06-23 | 10:17 | 49.943 | 44735.4657 | 50.072
2022-06-23 | 10:17 | 49.942 | 44735.4657 | 50.0719
2022-06-23 | 10:17 | 49.94 | 2022-06-23 11:11 | 50.0719
2022-06-23 | 10:18 | 49.939 | 44735.4657 | 50.0718
2022-06-23 | 10:18 | 49.936 | 44735.4657 | 50.0718
2022-06-23 | 10:18 | 49.936 | 44735.4657 | 50.0717
2022-06-23 | 10:18 | 49.938 | 44735.4657 | 50.0717
2022-06-23 | 10:18 | 49.937 | 44735.4657 | 50.0716
2022-06-23 | 10:18 | 49.939 | 44735.4657 | 50.0716
2022-06-23 | 10:18 | 49.941 | 44735.4657 | 50.0716
2022-06-23 | 10:18 | 49.94 | 44735.4657 | 50.0715
2022-06-23 | 10:18 | 49.938 | 44735.4657 | 50.0715
2022-06-23 | 10:18 | 49.936 | 44735.4657 | 50.0715
2022-06-23 | 10:18 | 49.938 | 44735.4657 | 50.0716
2022-06-23 | 10:18 | 49.938 | 44735.4657 | 50.0716
2022-06-23 | 10:18 | 49.939 | 44735.4657 | 50.0716
2022-06-23 | 10:18 | 49.939 | 44735.4657 | 50.0716
2022-06-23 | 10:18 | 49.937 | 44735.4657 | 50.0716
2022-06-23 | 10:18 | 49.938 | 44735.4657 | 50.0717
2022-06-23 | 10:18 | 49.936 | 44735.4657 | 50.0717
2022-06-23 | 10:18 | 49.936 | 44735.4657 | 50.0716
2022-06-23 | 10:18 | 49.938 | 44735.4657 | 50.0716
2022-06-23 | 10:18 | 49.936 | 44735.4657 | 50.0716
2022-06-23 | 10:18 | 49.939 | 44735.4657 | 50.0715
2022-06-23 | 10:18 | 49.938 | 44735.4657 | 50.0714
2022-06-23 | 10:18 | 49.94 | 44735.4657 | 50.0713
2022-06-23 | 10:18 | 49.941 | 44735.4657 | 50.0713
2022-06-23 | 10:18 | 49.942 | 44735.4657 | 50.0712
2022-06-23 | 10:18 | 49.945 | 44735.4657 | 50.0712
2022-06-23 | 10:18 | 49.946 | 44735.4657 | 50.0712
2022-06-23 | 10:18 | 49.947 | 44735.4657 | 50.0711
2022-06-23 | 10:18 | 49.947 | 44735.4657 | 50.0712
2022-06-23 | 10:18 | 49.945 | 44735.4657 | 50.0712
2022-06-23 | 10:18 | 49.945 | 44735.4657 | 50.0711
2022-06-23 | 10:18 | 49.943 | 44735.4657 | 50.0711
2022-06-23 | 10:18 | 49.945 | 44735.4657 | 50.0711
2022-06-23 | 10:18 | 49.944 | 44735.4657 | 50.071
2022-06-23 | 10:18 | 49.946 | 44735.4657 | 50.0711
2022-06-23 | 10:18 | 49.944 | 44735.4657 | 50.071
2022-06-23 | 10:18 | 49.945 | 44735.4657 | 50.0709
2022-06-23 | 10:18 | 49.942 | 44735.4657 | 50.0709
2022-06-23 | 10:18 | 49.943 | 44735.4657 | 50.0709
2022-06-23 | 10:18 | 49.939 | 44735.4657 | 50.0708
2022-06-23 | 10:18 | 49.94 | 44735.4657 | 50.0707
2022-06-23 | 10:18 | 49.936 | 44735.4657 | 50.0707
2022-06-23 | 10:18 | 49.938 | 44735.4657 | 50.0706
2022-06-23 | 10:18 | 49.939 | 44735.4657 | 50.0705
2022-06-23 | 10:18 | 49.94 | 44735.4657 | 50.0704
2022-06-23 | 10:18 | 49.943 | 44735.4657 | 50.0704
2022-06-23 | 10:18 | 49.942 | 44735.4657 | 50.0703
2022-06-23 | 10:18 | 49.943 | 44735.4657 | 50.0702
2022-06-23 | 10:18 | 49.943 | 44735.4657 | 50.0702
2022-06-23 | 10:18 | 49.942 | 2022-06-23 11:11 | 50.0701
2022-06-23 | 10:18 | 49.94 | 44735.4657 | 50.0701
2022-06-23 | 10:18 | 49.94 | 44735.4657 | 50.0701
2022-06-23 | 10:18 | 49.938 | 44735.4657 | 50.0701
2022-06-23 | 10:18 | 49.938 | 44735.4657 | 50.07
2022-06-23 | 10:18 | 49.938 | 44735.4657 | 50.0698
2022-06-23 | 10:18 | 49.938 | 44735.4657 | 50.0697
2022-06-23 | 10:18 | 49.935 | 44735.4657 | 50.0696
2022-06-23 | 10:18 | 49.936 | 44735.4657 | 50.0696
2022-06-23 | 10:18 | 49.933 | 44735.4657 | 50.0695
2022-06-23 | 10:19 | 49.933 | 44735.4657 | 50.0695
2022-06-23 | 10:19 | 49.933 | 44735.4657 | 50.0694
2022-06-23 | 10:19 | 49.935 | 44735.4657 | 50.0693
2022-06-23 | 10:19 | 49.936 | 44735.4657 | 50.0693
2022-06-23 | 10:19 | 49.936 | 44735.4657 | 50.0693
2022-06-23 | 10:19 | 49.937 | 44735.4657 | 50.0692
2022-06-23 | 10:19 | 49.936 | 44735.4657 | 50.0692
2022-06-23 | 10:19 | 49.939 | 44735.4657 | 50.0691
2022-06-23 | 10:19 | 49.938 | 44735.4657 | 50.0691
2022-06-23 | 10:19 | 49.941 | 44735.4657 | 50.069
2022-06-23 | 10:19 | 49.94 | 44735.4657 | 50.069
2022-06-23 | 10:19 | 49.939 | 44735.4657 | 50.0689
2022-06-23 | 10:19 | 49.938 | 44735.4657 | 50.0689
2022-06-23 | 10:19 | 49.937 | 44735.4657 | 50.0689
2022-06-23 | 10:19 | 49.937 | 44735.4657 | 50.0688
2022-06-23 | 10:19 | 49.935 | 44735.4657 | 50.0687
2022-06-23 | 10:19 | 49.933 | 44735.4657 | 50.0686
2022-06-23 | 10:19 | 49.929 | 44735.4657 | 50.0685
2022-06-23 | 10:19 | 49.926 | 44735.4657 | 50.0685
2022-06-23 | 10:19 | 49.921 | 44735.4657 | 50.0684
2022-06-23 | 10:19 | 49.922 | 44735.4657 | 50.0684
2022-06-23 | 10:19 | 49.917 | 44735.4657 | 50.0684
2022-06-23 | 10:19 | 49.917 | 44735.4657 | 50.0683
2022-06-23 | 10:19 | 49.915 | 44735.4657 | 50.0682
2022-06-23 | 10:19 | 49.918 | 44735.4657 | 50.0682
2022-06-23 | 10:19 | 49.916 | 44735.4657 | 50.0681
2022-06-23 | 10:19 | 49.916 | 44735.4657 | 50.068
2022-06-23 | 10:19 | 49.915 | 44735.4657 | 50.068
2022-06-23 | 10:19 | 49.913 | 44735.4657 | 50.0679
2022-06-23 | 10:19 | 49.911 | 44735.4657 | 50.0678
2022-06-23 | 10:19 | 49.909 | 44735.4658 | 50.0677
2022-06-23 | 10:19 | 49.905 | 44735.4658 | 50.0676
2022-06-23 | 10:19 | 49.903 | 44735.4658 | 50.0676
2022-06-23 | 10:19 | 49.904 | 44735.4658 | 50.0676
2022-06-23 | 10:19 | 49.901 | 44735.4658 | 50.0675
2022-06-23 | 10:19 | 49.899 | 44735.4658 | 50.0674
2022-06-23 | 10:19 | 49.9 | 44735.4658 | 50.0674
2022-06-23 | 10:19 | 49.899 | 44735.4658 | 50.0674
2022-06-23 | 10:19 | 49.898 | 44735.4658 | 50.0674
2022-06-23 | 10:19 | 49.9 | 44735.4658 | 50.0674
2022-06-23 | 10:19 | 49.901 | 2022-06-23 11:11 | 50.0673
2022-06-23 | 10:19 | 49.901 | 44735.4658 | 50.0673
2022-06-23 | 10:19 | 49.903 | 44735.4658 | 50.0672
2022-06-23 | 10:19 | 49.901 | 44735.4658 | 50.0671
2022-06-23 | 10:19 | 49.903 | 44735.4658 | 50.0671
2022-06-23 | 10:19 | 49.907 | 44735.4658 | 50.0671
2022-06-23 | 10:19 | 49.907 | 44735.4658 | 50.0671
2022-06-23 | 10:19 | 49.909 | 44735.4658 | 50.067
2022-06-23 | 10:19 | 49.906 | 44735.4658 | 50.067
2022-06-23 | 10:19 | 49.902 | 44735.4658 | 50.067
2022-06-23 | 10:19 | 49.901 | 44735.4658 | 50.067
2022-06-23 | 10:19 | 49.899 | 44735.4658 | 50.0669
2022-06-23 | 10:19 | 49.898 | 44735.4658 | 50.0669
2022-06-23 | 10:19 | 49.9 | 44735.4658 | 50.0669
2022-06-23 | 10:19 | 49.897 | 44735.4658 | 50.0669
2022-06-23 | 10:19 | 49.895 | 44735.4658 | 50.0669
2022-06-23 | 10:19 | 49.895 | 44735.4658 | 50.0668
2022-06-23 | 10:19 | 49.891 | 44735.4658 | 50.0668
2022-06-23 | 10:19 | 49.891 | 44735.4658 | 50.0668
2022-06-23 | 10:19 | 49.887 | 44735.4658 | 50.0668
2022-06-23 | 10:19 | 49.886 | 44735.4658 | 50.0667
2022-06-23 | 10:20 | 49.883 | 44735.4658 | 50.0666
2022-06-23 | 10:20 | 49.882 | 44735.4658 | 50.0666
2022-06-23 | 10:20 | 49.881 | 44735.4658 | 50.0665
2022-06-23 | 10:20 | 49.881 | 44735.4658 | 50.0665
2022-06-23 | 10:20 | 49.881 | 44735.4658 | 50.0664
2022-06-23 | 10:20 | 49.881 | 44735.4658 | 50.0663
2022-06-23 | 10:20 | 49.881 | 44735.4658 | 50.0663
2022-06-23 | 10:20 | 49.882 | 44735.4658 | 50.0663
2022-06-23 | 10:20 | 49.882 | 44735.4658 | 50.0662
2022-06-23 | 10:20 | 49.886 | 44735.4658 | 50.0662
2022-06-23 | 10:20 | 49.888 | 44735.4658 | 50.0662
2022-06-23 | 10:20 | 49.894 | 44735.4658 | 50.0661
2022-06-23 | 10:20 | 49.896 | 44735.4658 | 50.0661
2022-06-23 | 10:20 | 49.899 | 44735.4658 | 50.0661
2022-06-23 | 10:20 | 49.899 | 44735.4658 | 50.0661
2022-06-23 | 10:20 | 49.901 | 44735.4658 | 50.066
2022-06-23 | 10:20 | 49.898 | 44735.4658 | 50.066
2022-06-23 | 10:20 | 49.897 | 44735.4658 | 50.066
2022-06-23 | 10:20 | 49.896 | 44735.4658 | 50.0659
2022-06-23 | 10:20 | 49.897 | 44735.4658 | 50.0659
2022-06-23 | 10:20 | 49.897 | 44735.4658 | 50.0658
2022-06-23 | 10:20 | 49.899 | 44735.4658 | 50.0657
2022-06-23 | 10:20 | 49.901 | 44735.4658 | 50.0657
2022-06-23 | 10:20 | 49.9 | 44735.4658 | 50.0657
2022-06-23 | 10:20 | 49.899 | 44735.4658 | 50.0656
2022-06-23 | 10:20 | 49.901 | 44735.4658 | 50.0655
2022-06-23 | 10:20 | 49.898 | 44735.4658 | 50.0654
2022-06-23 | 10:20 | 49.897 | 44735.4658 | 50.0653
2022-06-23 | 10:20 | 49.896 | 44735.4658 | 50.0653
2022-06-23 | 10:20 | 49.898 | 2022-06-23 11:11 | 50.0653
2022-06-23 | 10:20 | 49.898 | 44735.4658 | 50.0652
2022-06-23 | 10:20 | 49.896 | 44735.4658 | 50.0653
2022-06-23 | 10:20 | 49.894 | 44735.4658 | 50.0653
2022-06-23 | 10:20 | 49.896 | 44735.4658 | 50.0653
2022-06-23 | 10:20 | 49.897 | 44735.4658 | 50.0654
2022-06-23 | 10:20 | 49.897 | 44735.4658 | 50.0654
2022-06-23 | 10:20 | 49.899 | 44735.4658 | 50.0654
2022-06-23 | 10:20 | 49.902 | 44735.4658 | 50.0653
2022-06-23 | 10:20 | 49.904 | 44735.4658 | 50.0653
2022-06-23 | 10:20 | 49.906 | 44735.4658 | 50.0652
2022-06-23 | 10:20 | 49.907 | 44735.4658 | 50.0651
2022-06-23 | 10:20 | 49.91 | 44735.4658 | 50.0651
2022-06-23 | 10:20 | 49.911 | 44735.4658 | 50.065
2022-06-23 | 10:20 | 49.912 | 44735.4658 | 50.065
2022-06-23 | 10:20 | 49.912 | 44735.4658 | 50.065
2022-06-23 | 10:20 | 49.91 | 44735.4658 | 50.065
2022-06-23 | 10:20 | 49.91 | 44735.4658 | 50.065
2022-06-23 | 10:20 | 49.908 | 44735.4658 | 50.0649
2022-06-23 | 10:20 | 49.911 | 44735.4658 | 50.065
2022-06-23 | 10:20 | 49.911 | 44735.4658 | 50.0649
2022-06-23 | 10:20 | 49.911 | 44735.4658 | 50.0649
2022-06-23 | 10:20 | 49.913 | 44735.4658 | 50.0648
2022-06-23 | 10:20 | 49.913 | 44735.4658 | 50.0646
2022-06-23 | 10:20 | 49.912 | 44735.4658 | 50.0645
2022-06-23 | 10:20 | 49.913 | 44735.4658 | 50.0646
2022-06-23 | 10:20 | 49.911 | 44735.4658 | 50.0646
2022-06-23 | 10:20 | 49.911 | 44735.4658 | 50.0645
2022-06-23 | 10:20 | 49.908 | 44735.4658 | 50.0644
2022-06-23 | 10:20 | 49.911 | 44735.4658 | 50.0644
2022-06-23 | 10:21 | 49.907 | 44735.4658 | 50.0643
2022-06-23 | 10:21 | 49.906 | 44735.4658 | 50.0642
2022-06-23 | 10:21 | 49.901 | 44735.4658 | 50.0642
2022-06-23 | 10:21 | 49.898 | 44735.4658 | 50.0641
2022-06-23 | 10:21 | 49.894 | 44735.4658 | 50.0641
2022-06-23 | 10:21 | 49.892 | 44735.4658 | 50.064
2022-06-23 | 10:21 | 49.892 | 44735.4658 | 50.064
2022-06-23 | 10:21 | 49.892 | 44735.4658 | 50.0639
2022-06-23 | 10:21 | 49.893 | 44735.4658 | 50.0639
2022-06-23 | 10:21 | 49.894 | 44735.4658 | 50.0639
2022-06-23 | 10:21 | 49.895 | 44735.4658 | 50.0638
2022-06-23 | 10:21 | 49.897 | 44735.4658 | 50.0638
2022-06-23 | 10:21 | 49.898 | 44735.4658 | 50.0637
2022-06-23 | 10:21 | 49.897 | 44735.4658 | 50.0637
2022-06-23 | 10:21 | 49.897 | 44735.4658 | 50.0636
2022-06-23 | 10:21 | 49.896 | 44735.4658 | 50.0636
2022-06-23 | 10:21 | 49.893 | 44735.4658 | 50.0635
2022-06-23 | 10:21 | 49.893 | 44735.4658 | 50.0634
2022-06-23 | 10:21 | 49.892 | 44735.4658 | 50.0633
2022-06-23 | 10:21 | 49.893 | 44735.4658 | 50.0632
2022-06-23 | 10:21 | 49.893 | 2022-06-23 11:11 | 50.0631
2022-06-23 | 10:21 | 49.892 | 44735.4658 | 50.063
2022-06-23 | 10:21 | 49.888 | 44735.4658 | 50.0629
2022-06-23 | 10:21 | 49.888 | 44735.4658 | 50.0628
2022-06-23 | 10:21 | 49.889 | 44735.4658 | 50.0627
2022-06-23 | 10:21 | 49.89 | 44735.4658 | 50.0626
2022-06-23 | 10:21 | 49.89 | 44735.4658 | 50.0625
2022-06-23 | 10:21 | 49.89 | 44735.4658 | 50.0625
2022-06-23 | 10:21 | 49.89 | 44735.4658 | 50.0626
2022-06-23 | 10:21 | 49.89 | 44735.4658 | 50.0625
2022-06-23 | 10:21 | 49.885 | 44735.4658 | 50.0624
2022-06-23 | 10:21 | 49.879 | 44735.4658 | 50.0624
2022-06-23 | 10:21 | 49.873 | 44735.4658 | 50.0623
2022-06-23 | 10:21 | 49.868 | 44735.4658 | 50.0623
2022-06-23 | 10:21 | 49.864 | 44735.4658 | 50.0623
2022-06-23 | 10:21 | 49.861 | 44735.4658 | 50.0622
2022-06-23 | 10:21 | 49.859 | 44735.4658 | 50.0622
2022-06-23 | 10:21 | 49.86 | 44735.4658 | 50.0622
2022-06-23 | 10:21 | 49.861 | 44735.4658 | 50.0622
2022-06-23 | 10:21 | 49.86 | 44735.4658 | 50.0622
2022-06-23 | 10:21 | 49.862 | 44735.4658 | 50.0621
2022-06-23 | 10:21 | 49.863 | 44735.4658 | 50.062
2022-06-23 | 10:21 | 49.865 | 44735.4658 | 50.0621
2022-06-23 | 10:21 | 49.865 | 44735.4658 | 50.062
2022-06-23 | 10:21 | 49.867 | 44735.4658 | 50.062
2022-06-23 | 10:21 | 49.869 | 44735.4658 | 50.062
2022-06-23 | 10:21 | 49.87 | 44735.4658 | 50.0619
2022-06-23 | 10:21 | 49.87 | 44735.4658 | 50.0619
2022-06-23 | 10:21 | 49.869 | 44735.4658 | 50.0618
2022-06-23 | 10:21 | 49.869 | 44735.4658 | 50.0617
2022-06-23 | 10:21 | 49.87 | 44735.4658 | 50.0617
2022-06-23 | 10:21 | 49.872 | 44735.4658 | 50.0616
2022-06-23 | 10:21 | 49.873 | 44735.4658 | 50.0615
2022-06-23 | 10:21 | 49.874 | 44735.4658 | 50.0615
2022-06-23 | 10:21 | 49.877 | 44735.4658 | 50.0614
2022-06-23 | 10:21 | 49.88 | 44735.4658 | 50.0614
2022-06-23 | 10:21 | 49.882 | 44735.4658 | 50.0613
2022-06-23 | 10:21 | 49.883 | 44735.4658 | 50.0613
2022-06-23 | 10:21 | 49.885 | 44735.4658 | 50.0612
2022-06-23 | 10:21 | 49.887 | 44735.4658 | 50.0612
2022-06-23 | 10:21 | 49.889 | 44735.4658 | 50.0611
2022-06-23 | 10:22 | 49.889 | 44735.4658 | 50.0611
2022-06-23 | 10:22 | 49.891 | 44735.4658 | 50.0611
2022-06-23 | 10:22 | 49.892 | 44735.4658 | 50.0611
2022-06-23 | 10:22 | 49.895 | 44735.4658 | 50.061
2022-06-23 | 10:22 | 49.898 | 44735.4658 | 50.0609
2022-06-23 | 10:22 | 49.899 | 44735.4658 | 50.0609
2022-06-23 | 10:22 | 49.902 | 44735.4658 | 50.0608
2022-06-23 | 10:22 | 49.905 | 44735.4658 | 50.0607
2022-06-23 | 10:22 | 49.905 | 44735.4658 | 50.0607
2022-06-23 | 10:22 | 49.906 | 2022-06-23 11:11 | 50.0606
2022-06-23 | 10:22 | 49.908 | 44735.4658 | 50.0604
2022-06-23 | 10:22 | 49.908 | 44735.4658 | 50.0604
2022-06-23 | 10:22 | 49.906 | 44735.4658 | 50.0604
2022-06-23 | 10:22 | 49.902 | 44735.4658 | 50.0603
2022-06-23 | 10:22 | 49.9 | 44735.4658 | 50.0604
2022-06-23 | 10:22 | 49.897 | 44735.4658 | 50.0604
2022-06-23 | 10:22 | 49.894 | 44735.4658 | 50.0604
2022-06-23 | 10:22 | 49.89 | 44735.4658 | 50.0604
2022-06-23 | 10:22 | 49.886 | 44735.4658 | 50.0604
2022-06-23 | 10:22 | 49.883 | 44735.4658 | 50.0603
2022-06-23 | 10:22 | 49.882 | 44735.4658 | 50.0603
2022-06-23 | 10:22 | 49.881 | 44735.4658 | 50.0602
2022-06-23 | 10:22 | 49.88 | 44735.4658 | 50.0601
2022-06-23 | 10:22 | 49.88 | 44735.4658 | 50.06
2022-06-23 | 10:22 | 49.882 | 44735.4658 | 50.06
2022-06-23 | 10:22 | 49.887 | 44735.4658 | 50.0599
2022-06-23 | 10:22 | 49.89 | 44735.4658 | 50.0598
2022-06-23 | 10:22 | 49.893 | 44735.4658 | 50.0598
2022-06-23 | 10:22 | 49.898 | 44735.4658 | 50.0597
2022-06-23 | 10:22 | 49.902 | 44735.4658 | 50.0597
2022-06-23 | 10:22 | 49.902 | 44735.4658 | 50.0596
2022-06-23 | 10:22 | 49.904 | 44735.4658 | 50.0596
2022-06-23 | 10:22 | 49.906 | 44735.4658 | 50.0595
2022-06-23 | 10:22 | 49.907 | 44735.4658 | 50.0594
2022-06-23 | 10:22 | 49.906 | 44735.4658 | 50.0594
2022-06-23 | 10:22 | 49.905 | 44735.4658 | 50.0593
2022-06-23 | 10:22 | 49.9 | 44735.4658 | 50.0592
2022-06-23 | 10:22 | 49.897 | 44735.4658 | 50.0592
2022-06-23 | 10:22 | 49.894 | 44735.4658 | 50.0591
2022-06-23 | 10:22 | 49.891 | 44735.4658 | 50.059
2022-06-23 | 10:22 | 49.893 | 44735.4658 | 50.059
2022-06-23 | 10:22 | 49.891 | 44735.4658 | 50.0589
2022-06-23 | 10:22 | 49.891 | 44735.4658 | 50.0589
2022-06-23 | 10:22 | 49.891 | 44735.4658 | 50.0589
2022-06-23 | 10:22 | 49.893 | 44735.4658 | 50.0588
2022-06-23 | 10:22 | 49.894 | 44735.4658 | 50.0588
2022-06-23 | 10:22 | 49.895 | 44735.4658 | 50.0587
2022-06-23 | 10:22 | 49.897 | 44735.4658 | 50.0587
2022-06-23 | 10:22 | 49.898 | 44735.4658 | 50.0587
2022-06-23 | 10:22 | 49.898 | 44735.4658 | 50.0588
2022-06-23 | 10:22 | 49.894 | 44735.4658 | 50.0588
2022-06-23 | 10:22 | 49.895 | 44735.4658 | 50.0588
2022-06-23 | 10:22 | 49.897 | 44735.4658 | 50.0588
2022-06-23 | 10:22 | 49.895 | 44735.4658 | 50.0587
2022-06-23 | 10:22 | 49.894 | 44735.4658 | 50.0586
2022-06-23 | 10:22 | 49.893 | 44735.4658 | 50.0585
2022-06-23 | 10:22 | 49.891 | 44735.4658 | 50.0584
2022-06-23 | 10:22 | 49.89 | 44735.4658 | 50.0584
2022-06-23 | 10:22 | 49.89 | 44735.4658 | 50.0583
2022-06-23 | 10:23 | 49.891 | 2022-06-23 11:11 | 50.0582
2022-06-23 | 10:23 | 49.891 | 44735.4658 | 50.0582
2022-06-23 | 10:23 | 49.892 | 44735.4658 | 50.0581
2022-06-23 | 10:23 | 49.895 | 44735.4658 | 50.0582
2022-06-23 | 10:23 | 49.897 | 44735.4658 | 50.0582
2022-06-23 | 10:23 | 49.897 | 44735.4658 | 50.0582
2022-06-23 | 10:23 | 49.899 | 44735.4658 | 50.0582
2022-06-23 | 10:23 | 49.9 | 44735.4658 | 50.0582
2022-06-23 | 10:23 | 49.899 | 44735.4658 | 50.0582
2022-06-23 | 10:23 | 49.895 | 44735.4658 | 50.0582
2022-06-23 | 10:23 | 49.899 | 44735.4658 | 50.0582
2022-06-23 | 10:23 | 49.9 | 44735.4658 | 50.0582
2022-06-23 | 10:23 | 49.897 | 44735.4658 | 50.0582
2022-06-23 | 10:23 | 49.896 | 44735.4658 | 50.0581
2022-06-23 | 10:23 | 49.896 | 44735.4658 | 50.0581
2022-06-23 | 10:23 | 49.894 | 44735.4658 | 50.058
2022-06-23 | 10:23 | 49.894 | 44735.4658 | 50.0579
2022-06-23 | 10:23 | 49.896 | 44735.4658 | 50.0579
2022-06-23 | 10:23 | 49.896 | 44735.4658 | 50.0578
2022-06-23 | 10:23 | 49.898 | 44735.4658 | 50.0578
2022-06-23 | 10:23 | 49.9 | 44735.4658 | 50.0577
2022-06-23 | 10:23 | 49.902 | 44735.4658 | 50.0576
2022-06-23 | 10:23 | 49.902 | 44735.4658 | 50.0575
2022-06-23 | 10:23 | 49.902 | 44735.4658 | 50.0574
2022-06-23 | 10:23 | 49.903 | 44735.4658 | 50.0574
2022-06-23 | 10:23 | 49.904 | 44735.4658 | 50.0574
2022-06-23 | 10:23 | 49.903 | 44735.4658 | 50.0573
2022-06-23 | 10:23 | 49.903 | 44735.4658 | 50.0572
2022-06-23 | 10:23 | 49.902 | 44735.4658 | 50.0572
2022-06-23 | 10:23 | 49.899 | 44735.4658 | 50.0572
2022-06-23 | 10:23 | 49.897 | 44735.4658 | 50.0571
2022-06-23 | 10:23 | 49.894 | 44735.4658 | 50.057
2022-06-23 | 10:23 | 49.89 | 44735.4658 | 50.057
2022-06-23 | 10:23 | 49.887 | 44735.4658 | 50.057
2022-06-23 | 10:23 | 49.886 | 44735.4658 | 50.0569
2022-06-23 | 10:23 | 49.884 | 44735.4658 | 50.0568
2022-06-23 | 10:23 | 49.885 | 44735.4658 | 50.0568
2022-06-23 | 10:23 | 49.883 | 44735.4658 | 50.0567
2022-06-23 | 10:23 | 49.883 | 44735.4658 | 50.0566
2022-06-23 | 10:23 | 49.885 | 44735.4658 | 50.0565
2022-06-23 | 10:23 | 49.885 | 44735.4658 | 50.0565
2022-06-23 | 10:23 | 49.885 | 44735.4658 | 50.0564
2022-06-23 | 10:23 | 49.886 | 44735.4658 | 50.0563
2022-06-23 | 10:23 | 49.886 | 44735.4658 | 50.0563
2022-06-23 | 10:23 | 49.883 | 44735.4658 | 50.0563
2022-06-23 | 10:23 | 49.881 | 44735.4658 | 50.0561
2022-06-23 | 10:23 | 49.879 | 44735.4658 | 50.0561
2022-06-23 | 10:23 | 49.879 | 44735.4658 | 50.056
2022-06-23 | 10:23 | 49.879 | 44735.4658 | 50.056
2022-06-23 | 10:23 | 49.88 | 44735.4658 | 50.056
2022-06-23 | 10:23 | 49.881 | 2022-06-23 11:11 | 50.056
2022-06-23 | 10:23 | 49.881 | 44735.4658 | 50.0559
2022-06-23 | 10:23 | 49.883 | 44735.4658 | 50.0559
2022-06-23 | 10:23 | 49.885 | 44735.4658 | 50.0559
2022-06-23 | 10:23 | 49.889 | 44735.4658 | 50.0558
2022-06-23 | 10:23 | 49.892 | 44735.4658 | 50.0557
2022-06-23 | 10:23 | 49.895 | 44735.4658 | 50.0557
2022-06-23 | 10:23 | 49.895 | 44735.4658 | 50.0557
2022-06-23 | 10:23 | 49.896 | 44735.4658 | 50.0558
2022-06-23 | 10:23 | 49.897 | 44735.4658 | 50.0559
2022-06-23 | 10:23 | 49.897 | 44735.4658 | 50.0559
2022-06-23 | 10:24 | 49.895 | 44735.4658 | 50.056
2022-06-23 | 10:24 | 49.894 | 44735.4658 | 50.0561
2022-06-23 | 10:24 | 49.892 | 44735.4658 | 50.0561
2022-06-23 | 10:24 | 49.892 | 44735.4658 | 50.056
2022-06-23 | 10:24 | 49.891 | 44735.4658 | 50.0559
2022-06-23 | 10:24 | 49.89 | 44735.4658 | 50.0559
2022-06-23 | 10:24 | 49.891 | 44735.4658 | 50.0559
2022-06-23 | 10:24 | 49.893 | 44735.4658 | 50.0558
2022-06-23 | 10:24 | 49.895 | 44735.4658 | 50.0557
2022-06-23 | 10:24 | 49.9 | 44735.4658 | 50.0557
2022-06-23 | 10:24 | 49.902 | 44735.4658 | 50.0557
2022-06-23 | 10:24 | 49.904 | 44735.4658 | 50.0557
2022-06-23 | 10:24 | 49.904 | 44735.4658 | 50.0557
2022-06-23 | 10:24 | 49.905 | 44735.4658 | 50.0558
2022-06-23 | 10:24 | 49.905 | 44735.4658 | 50.0558
2022-06-23 | 10:24 | 49.903 | 44735.4658 | 50.0558
2022-06-23 | 10:24 | 49.901 | 44735.4658 | 50.0558
2022-06-23 | 10:24 | 49.899 | 44735.4658 | 50.0558
2022-06-23 | 10:24 | 49.899 | 44735.4658 | 50.0559
2022-06-23 | 10:24 | 49.901 | 44735.4658 | 50.0558
2022-06-23 | 10:24 | 49.902 | 44735.4658 | 50.0558
2022-06-23 | 10:24 | 49.903 | 44735.4658 | 50.0558
2022-06-23 | 10:24 | 49.902 | 44735.4658 | 50.0557
2022-06-23 | 10:24 | 49.9 | 44735.4658 | 50.0557
2022-06-23 | 10:24 | 49.902 | 44735.4658 | 50.0556
2022-06-23 | 10:24 | 49.901 | 44735.4658 | 50.0556
2022-06-23 | 10:24 | 49.899 | 44735.4658 | 50.0556
2022-06-23 | 10:24 | 49.899 | 44735.4658 | 50.0556
2022-06-23 | 10:24 | 49.901 | 44735.4658 | 50.0556
2022-06-23 | 10:24 | 49.902 | 44735.4658 | 50.0556
2022-06-23 | 10:24 | 49.904 | 44735.4658 | 50.0557
2022-06-23 | 10:24 | 49.903 | 44735.4658 | 50.0557
2022-06-23 | 10:24 | 49.902 | 44735.4658 | 50.0558
2022-06-23 | 10:24 | 49.899 | 44735.4658 | 50.0558
2022-06-23 | 10:24 | 49.897 | 44735.4658 | 50.0558
2022-06-23 | 10:24 | 49.895 | 44735.4658 | 50.0558
2022-06-23 | 10:24 | 49.892 | 44735.4658 | 50.0558
2022-06-23 | 10:24 | 49.887 | 44735.4658 | 50.0557
2022-06-23 | 10:24 | 49.884 | 44735.4658 | 50.0557
2022-06-23 | 10:24 | 49.878 | 2022-06-23 11:11 | 50.0556
2022-06-23 | 10:24 | 49.875 | 44735.4658 | 50.0556
2022-06-23 | 10:24 | 49.875 | 44735.4658 | 50.0555
2022-06-23 | 10:24 | 49.875 | 44735.4658 | 50.0555
2022-06-23 | 10:24 | 49.876 | 44735.4658 | 50.0554
2022-06-23 | 10:24 | 49.879 | 44735.4658 | 50.0554
2022-06-23 | 10:24 | 49.879 | 44735.4658 | 50.0553
2022-06-23 | 10:24 | 49.877 | 44735.4658 | 50.0553
2022-06-23 | 10:24 | 49.879 | 44735.4658 | 50.0552
2022-06-23 | 10:24 | 49.881 | 44735.4658 | 50.0552
2022-06-23 | 10:24 | 49.88 | 44735.4658 | 50.0552
2022-06-23 | 10:24 | 49.88 | 44735.4658 | 50.0551
2022-06-23 | 10:24 | 49.88 | 44735.4658 | 50.0551
2022-06-23 | 10:24 | 49.878 | 44735.4658 | 50.055
2022-06-23 | 10:24 | 49.879 | 44735.4658 | 50.0551
2022-06-23 | 10:24 | 49.879 | 44735.4658 | 50.0551
2022-06-23 | 10:24 | 49.879 | 44735.4658 | 50.055
2022-06-23 | 10:24 | 49.879 | 44735.4658 | 50.055
2022-06-23 | 10:24 | 49.879 | 44735.4658 | 50.055
2022-06-23 | 10:24 | 49.88 | 44735.4658 | 50.055
2022-06-23 | 10:25 | 49.881 | 44735.4658 | 50.055
2022-06-23 | 10:25 | 49.883 | 44735.4658 | 50.0551
2022-06-23 | 10:25 | 49.885 | 44735.4658 | 50.0553
2022-06-23 | 10:25 | 49.885 | 44735.4658 | 50.0553
2022-06-23 | 10:25 | 49.886 | 44735.4658 | 50.0553
2022-06-23 | 10:25 | 49.887 | 44735.4658 | 50.0552
2022-06-23 | 10:25 | 49.887 | 44735.4658 | 50.0552
2022-06-23 | 10:25 | 49.886 | 44735.4658 | 50.0552
2022-06-23 | 10:25 | 49.886 | 44735.4658 | 50.0552
2022-06-23 | 10:25 | 49.886 | 44735.4658 | 50.0552
2022-06-23 | 10:25 | 49.885 | 44735.4658 | 50.0552
2022-06-23 | 10:25 | 49.883 | 44735.4658 | 50.0552
2022-06-23 | 10:25 | 49.881 | 44735.4658 | 50.0552
2022-06-23 | 10:25 | 49.88 | 44735.4658 | 50.0552
2022-06-23 | 10:25 | 49.881 | 44735.4658 | 50.0553
2022-06-23 | 10:25 | 49.886 | 44735.4658 | 50.0553
2022-06-23 | 10:25 | 49.891 | 44735.4658 | 50.0552
2022-06-23 | 10:25 | 49.894 | 44735.4658 | 50.0552
2022-06-23 | 10:25 | 49.897 | 44735.4658 | 50.0552
2022-06-23 | 10:25 | 49.897 | 44735.4658 | 50.0551
2022-06-23 | 10:25 | 49.9 | 44735.4658 | 50.0551
2022-06-23 | 10:25 | 49.901 | 44735.4658 | 50.0551
2022-06-23 | 10:25 | 49.903 | 44735.4658 | 50.0551
2022-06-23 | 10:25 | 49.907 | 44735.4658 | 50.055
2022-06-23 | 10:25 | 49.91 | 44735.4658 | 50.0552
2022-06-23 | 10:25 | 49.913 | 44735.4658 | 50.0549
2022-06-23 | 10:25 | 49.915 | 44735.4658 | 50.0549
2022-06-23 | 10:25 | 49.917 | 44735.4658 | 50.0549
2022-06-23 | 10:25 | 49.92 | 44735.4658 | 50.0549
2022-06-23 | 10:25 | 49.921 | 44735.4658 | 50.0548
2022-06-23 | 10:25 | 49.921 | 2022-06-23 11:11 | 50.0548
2022-06-23 | 10:25 | 49.921 | 44735.4658 | 50.0548
2022-06-23 | 10:25 | 49.92 | 44735.4658 | 50.0548
2022-06-23 | 10:25 | 49.919 | 44735.4658 | 50.0548
2022-06-23 | 10:25 | 49.918 | 44735.4658 | 50.0548
2022-06-23 | 10:25 | 49.915 | 44735.4658 | 50.0548
2022-06-23 | 10:25 | 49.913 | 44735.4658 | 50.0548
2022-06-23 | 10:25 | 49.912 | 44735.4658 | 50.0548
2022-06-23 | 10:25 | 49.912 | 44735.4658 | 50.0548
2022-06-23 | 10:25 | 49.912 | 44735.4658 | 50.0548
2022-06-23 | 10:25 | 49.912 | 44735.4658 | 50.0549
2022-06-23 | 10:25 | 49.913 | 44735.4658 | 50.0549
2022-06-23 | 10:25 | 49.914 | 44735.4658 | 50.055
2022-06-23 | 10:25 | 49.915 | 44735.4658 | 50.0549
2022-06-23 | 10:25 | 49.915 | 44735.4658 | 50.055
2022-06-23 | 10:25 | 49.912 | 44735.4658 | 50.055
2022-06-23 | 10:25 | 49.91 | 44735.4658 | 50.0551
2022-06-23 | 10:25 | 49.908 | 44735.4658 | 50.0551
2022-06-23 | 10:25 | 49.907 | 44735.4658 | 50.0551
2022-06-23 | 10:25 | 49.904 | 44735.4658 | 50.0552
2022-06-23 | 10:25 | 49.901 | 44735.4658 | 50.0551
2022-06-23 | 10:25 | 49.898 | 44735.4658 | 50.0551
2022-06-23 | 10:25 | 49.898 | 44735.4658 | 50.0551
2022-06-23 | 10:25 | 49.898 | 44735.4658 | 50.0553
2022-06-23 | 10:25 | 49.899 | 44735.4658 | 50.0552
2022-06-23 | 10:25 | 49.899 | 44735.4658 | 50.0552
2022-06-23 | 10:25 | 49.898 | 44735.4658 | 50.0551
2022-06-23 | 10:25 | 49.898 | 44735.4658 | 50.0551
2022-06-23 | 10:25 | 49.898 | 44735.4658 | 50.0551
2022-06-23 | 10:25 | 49.898 | 44735.4658 | 50.0551
2022-06-23 | 10:26 | 49.9 | 44735.4658 | 50.0552
2022-06-23 | 10:26 | 49.902 | 44735.4658 | 50.0552
2022-06-23 | 10:26 | 49.904 | 44735.4658 | 50.0552
2022-06-23 | 10:26 | 49.906 | 44735.4658 | 50.0552
2022-06-23 | 10:26 | 49.904 | 44735.4658 | 50.0552
2022-06-23 | 10:26 | 49.904 | 44735.4658 | 50.0553
2022-06-23 | 10:26 | 49.902 | 44735.4658 | 50.0552
2022-06-23 | 10:26 | 49.901 | 44735.4658 | 50.0551
2022-06-23 | 10:26 | 49.901 | 44735.4658 | 50.055
2022-06-23 | 10:26 | 49.901 | 44735.4658 | 50.0549
2022-06-23 | 10:26 | 49.902 | 44735.4658 | 50.0548
2022-06-23 | 10:26 | 49.903 | 44735.4658 | 50.0547
2022-06-23 | 10:26 | 49.905 | 44735.4658 | 50.0547
2022-06-23 | 10:26 | 49.906 | 44735.4658 | 50.0547
2022-06-23 | 10:26 | 49.909 | 44735.4658 | 50.0546
2022-06-23 | 10:26 | 49.909 | 44735.4658 | 50.0547
2022-06-23 | 10:26 | 49.911 | 44735.4658 | 50.0546
2022-06-23 | 10:26 | 49.911 | 44735.4658 | 50.0547
2022-06-23 | 10:26 | 49.911 | 44735.4658 | 50.0547
2022-06-23 | 10:26 | 49.911 | 44735.4658 | 50.055
2022-06-23 | 10:26 | 49.912 | 2022-06-23 11:11 | 50.0551
2022-06-23 | 10:26 | 49.913 | 44735.4658 | 50.0551
2022-06-23 | 10:26 | 49.914 | 44735.4658 | 50.0551
2022-06-23 | 10:26 | 49.918 | 44735.4658 | 50.0552
2022-06-23 | 10:26 | 49.921 | 44735.4658 | 50.055
2022-06-23 | 10:26 | 49.925 | 44735.4658 | 50.055
2022-06-23 | 10:26 | 49.927 | 44735.4658 | 50.0551
2022-06-23 | 10:26 | 49.926 | 44735.4658 | 50.0551
2022-06-23 | 10:26 | 49.925 | 44735.4658 | 50.0551
2022-06-23 | 10:26 | 49.924 | 44735.4658 | 50.0551
2022-06-23 | 10:26 | 49.922 | 44735.4658 | 50.0551
2022-06-23 | 10:26 | 49.922 | 44735.4658 | 50.0551
2022-06-23 | 10:26 | 49.921 | 44735.4658 | 50.0551
2022-06-23 | 10:26 | 49.921 | 44735.4658 | 50.0552
2022-06-23 | 10:26 | 49.92 | 44735.4658 | 50.0552
2022-06-23 | 10:26 | 49.92 | 44735.4658 | 50.0552
2022-06-23 | 10:26 | 49.918 | 44735.4658 | 50.0551
2022-06-23 | 10:26 | 49.918 | 44735.4658 | 50.055
2022-06-23 | 10:26 | 49.917 | 44735.4658 | 50.0549
2022-06-23 | 10:26 | 49.916 | 44735.4658 | 50.0551
2022-06-23 | 10:26 | 49.915 | 44735.4658 | 50.055
2022-06-23 | 10:26 | 49.917 | 44735.4658 | 50.055
2022-06-23 | 10:26 | 49.917 | 44735.4659 | 50.0548
2022-06-23 | 10:26 | 49.917 | 44735.4659 | 50.0547
2022-06-23 | 10:26 | 49.917 | 44735.4659 | 50.0547
2022-06-23 | 10:26 | 49.914 | 44735.4659 | 50.0546
2022-06-23 | 10:26 | 49.913 | 44735.4659 | 50.0546
2022-06-23 | 10:26 | 49.912 | 44735.4659 | 50.0545
2022-06-23 | 10:26 | 49.912 | 44735.4659 | 50.0545
2022-06-23 | 10:26 | 49.913 | 44735.4659 | 50.0544
2022-06-23 | 10:26 | 49.916 | 44735.4659 | 50.0544
2022-06-23 | 10:26 | 49.918 | 44735.4659 | 50.0545
2022-06-23 | 10:26 | 49.922 | 44735.4659 | 50.0545
2022-06-23 | 10:26 | 49.921 | 44735.4659 | 50.0545
2022-06-23 | 10:26 | 49.923 | 44735.4659 | 50.0544
2022-06-23 | 10:26 | 49.924 | 44735.4659 | 50.0544
2022-06-23 | 10:26 | 49.926 | 44735.4659 | 50.0544
2022-06-23 | 10:26 | 49.93 | 44735.4659 | 50.0544
2022-06-23 | 10:26 | 49.933 | 44735.4659 | 50.0544
2022-06-23 | 10:26 | 49.936 | 44735.4659 | 50.0545
2022-06-23 | 10:26 | 49.937 | 44735.4659 | 50.0545
2022-06-23 | 10:27 | 49.938 | 44735.4659 | 50.0544
2022-06-23 | 10:27 | 49.939 | 44735.4659 | 50.0544
2022-06-23 | 10:27 | 49.939 | 44735.4659 | 50.0544
2022-06-23 | 10:27 | 49.94 | 44735.4659 | 50.0544
2022-06-23 | 10:27 | 49.94 | 44735.4659 | 50.0543
2022-06-23 | 10:27 | 49.941 | 44735.4659 | 50.0543
2022-06-23 | 10:27 | 49.94 | 44735.4659 | 50.0543
2022-06-23 | 10:27 | 49.942 | 44735.4659 | 50.0542
2022-06-23 | 10:27 | 49.942 | 44735.4659 | 50.0542
2022-06-23 | 10:27 | 49.942 | 2022-06-23 11:11 | 50.0542
2022-06-23 | 10:27 | 49.941 | 44735.4659 | 50.0542
2022-06-23 | 10:27 | 49.937 | 44735.4659 | 50.0542
2022-06-23 | 10:27 | 49.937 | 44735.4659 | 50.0542
2022-06-23 | 10:27 | 49.935 | 44735.4659 | 50.0543
2022-06-23 | 10:27 | 49.934 | 44735.4659 | 50.0543
2022-06-23 | 10:27 | 49.933 | 44735.4659 | 50.0543
2022-06-23 | 10:27 | 49.933 | 44735.4659 | 50.0543
2022-06-23 | 10:27 | 49.931 | 44735.4659 | 50.0543
2022-06-23 | 10:27 | 49.929 | 44735.4659 | 50.0542
2022-06-23 | 10:27 | 49.927 | 44735.4659 | 50.0543
2022-06-23 | 10:27 | 49.925 | 44735.4659 | 50.0543
2022-06-23 | 10:27 | 49.922 | 44735.4659 | 50.0543
2022-06-23 | 10:27 | 49.922 | 44735.4659 | 50.0544
2022-06-23 | 10:27 | 49.92 | 44735.4659 | 50.0544
2022-06-23 | 10:27 | 49.92 | 44735.4659 | 50.0545
2022-06-23 | 10:27 | 49.921 | 44735.4659 | 50.0545
2022-06-23 | 10:27 | 49.921 | 44735.4659 | 50.0545
2022-06-23 | 10:27 | 49.925 | 44735.4659 | 50.0545
2022-06-23 | 10:27 | 49.924 | 44735.4659 | 50.0545
2022-06-23 | 10:27 | 49.924 | 44735.4659 | 50.0545
2022-06-23 | 10:27 | 49.921 | 44735.4659 | 50.0544
2022-06-23 | 10:27 | 49.918 | 44735.4659 | 50.0543
2022-06-23 | 10:27 | 49.915 | 44735.4659 | 50.0543
2022-06-23 | 10:27 | 49.911 | 44735.4659 | 50.0541
2022-06-23 | 10:27 | 49.907 | 44735.4659 | 50.0541
2022-06-23 | 10:27 | 49.903 | 44735.4659 | 50.054
2022-06-23 | 10:27 | 49.903 | 44735.4659 | 50.054
2022-06-23 | 10:27 | 49.904 | 44735.4659 | 50.054
2022-06-23 | 10:27 | 49.906 | 44735.4659 | 50.0539
2022-06-23 | 10:27 | 49.906 | 44735.4659 | 50.0539
2022-06-23 | 10:27 | 49.904 | 44735.4659 | 50.0539
2022-06-23 | 10:27 | 49.903 | 44735.4659 | 50.0538
2022-06-23 | 10:27 | 49.899 | 44735.4659 | 50.0538
2022-06-23 | 10:27 | 49.895 | 44735.4659 | 50.0538
2022-06-23 | 10:27 | 49.893 | 44735.4659 | 50.0538
2022-06-23 | 10:27 | 49.887 | 44735.4659 | 50.0538
2022-06-23 | 10:27 | 49.883 | 44735.4659 | 50.0537
2022-06-23 | 10:27 | 49.883 | 44735.4659 | 50.0537
2022-06-23 | 10:27 | 49.881 | 44735.4659 | 50.0536
2022-06-23 | 10:27 | 49.881 | 44735.4659 | 50.0536
2022-06-23 | 10:27 | 49.881 | 44735.4659 | 50.0536
2022-06-23 | 10:27 | 49.881 | 44735.4659 | 50.0535
2022-06-23 | 10:27 | 49.882 | 44735.4659 | 50.0535
2022-06-23 | 10:27 | 49.884 | 44735.4659 | 50.0535
2022-06-23 | 10:27 | 49.885 | 44735.4659 | 50.0535
2022-06-23 | 10:27 | 49.885 | 44735.4659 | 50.0534
2022-06-23 | 10:27 | 49.885 | 44735.4659 | 50.0533
2022-06-23 | 10:27 | 49.884 | 44735.4659 | 50.0532
2022-06-23 | 10:27 | 49.884 | 44735.4659 | 50.0532
2022-06-23 | 10:28 | 49.885 | 2022-06-23 11:11 | 50.0531
2022-06-23 | 10:28 | 49.887 | 44735.4659 | 50.053
2022-06-23 | 10:28 | 49.887 | 44735.4659 | 50.053
2022-06-23 | 10:28 | 49.889 | 44735.4659 | 50.053
2022-06-23 | 10:28 | 49.893 | 44735.4659 | 50.0529
2022-06-23 | 10:28 | 49.894 | 44735.4659 | 50.0529
2022-06-23 | 10:28 | 49.892 | 44735.4659 | 50.0527
2022-06-23 | 10:28 | 49.891 | 44735.4659 | 50.0526
2022-06-23 | 10:28 | 49.891 | 44735.4659 | 50.0525
2022-06-23 | 10:28 | 49.891 | 44735.4659 | 50.0525
2022-06-23 | 10:28 | 49.891 | 44735.4659 | 50.0525
2022-06-23 | 10:28 | 49.893 | 44735.4659 | 50.0525
2022-06-23 | 10:28 | 49.896 | 44735.4659 | 50.0525
2022-06-23 | 10:28 | 49.898 | 44735.4659 | 50.0525
2022-06-23 | 10:28 | 49.898 | 44735.4659 | 50.0525
2022-06-23 | 10:28 | 49.899 | 44735.4659 | 50.0525
2022-06-23 | 10:28 | 49.903 | 44735.4659 | 50.0525
2022-06-23 | 10:28 | 49.908 | 44735.4659 | 50.0525
2022-06-23 | 10:28 | 49.912 | 44735.4659 | 50.0525
2022-06-23 | 10:28 | 49.915 | 44735.4659 | 50.0524
2022-06-23 | 10:28 | 49.918 | 44735.4659 | 50.0524
2022-06-23 | 10:28 | 49.921 | 44735.4659 | 50.0524
2022-06-23 | 10:28 | 49.923 | 44735.4659 | 50.0523
2022-06-23 | 10:28 | 49.927 | 44735.4659 | 50.0522
2022-06-23 | 10:28 | 49.931 | 44735.4659 | 50.0522
2022-06-23 | 10:28 | 49.933 | 44735.4659 | 50.0521
2022-06-23 | 10:28 | 49.936 | 44735.4659 | 50.0521
2022-06-23 | 10:28 | 49.935 | 44735.4659 | 50.0521
2022-06-23 | 10:28 | 49.935 | 44735.4659 | 50.0521
2022-06-23 | 10:28 | 49.932 | 44735.4659 | 50.0521
2022-06-23 | 10:28 | 49.929 | 44735.4659 | 50.0521
2022-06-23 | 10:28 | 49.924 | 44735.4659 | 50.0521
2022-06-23 | 10:28 | 49.922 | 44735.4659 | 50.052
2022-06-23 | 10:28 | 49.92 | 44735.4659 | 50.052
2022-06-23 | 10:28 | 49.918 | 44735.4659 | 50.052
2022-06-23 | 10:28 | 49.918 | 44735.4659 | 50.0519
2022-06-23 | 10:28 | 49.918 | 44735.4659 | 50.0519
2022-06-23 | 10:28 | 49.919 | 44735.4659 | 50.052
2022-06-23 | 10:28 | 49.921 | 44735.4659 | 50.052
2022-06-23 | 10:28 | 49.921 | 44735.4659 | 50.052
2022-06-23 | 10:28 | 49.92 | 44735.4659 | 50.0519
2022-06-23 | 10:28 | 49.918 | 44735.4659 | 50.0519
2022-06-23 | 10:28 | 49.917 | 44735.4659 | 50.0518
2022-06-23 | 10:28 | 49.914 | 44735.4659 | 50.0517
2022-06-23 | 10:28 | 49.911 | 44735.4659 | 50.0515
2022-06-23 | 10:28 | 49.909 | 44735.4659 | 50.0513
2022-06-23 | 10:28 | 49.904 | 44735.4659 | 50.0509
2022-06-23 | 10:28 | 49.902 | 44735.4659 | 50.0505
2022-06-23 | 10:28 | 49.901 | 44735.4659 | 50.05
2022-06-23 | 10:28 | 49.899 | 44735.4659 | 50.0495
2022-06-23 | 10:28 | 49.899 | 2022-06-23 11:11 | 50.0489
2022-06-23 | 10:28 | 49.901 | 44735.4659 | 50.0485
2022-06-23 | 10:28 | 49.902 | 44735.4659 | 50.048
2022-06-23 | 10:28 | 49.903 | 44735.4659 | 50.0477
2022-06-23 | 10:28 | 49.901 | 44735.4659 | 50.0474
2022-06-23 | 10:28 | 49.899 | 44735.4659 | 50.0472
2022-06-23 | 10:28 | 49.898 | 44735.4659 | 50.0471
2022-06-23 | 10:28 | 49.899 | 44735.4659 | 50.047
2022-06-23 | 10:28 | 49.897 | 44735.4659 | 50.0468
2022-06-23 | 10:28 | 49.894 | 44735.4659 | 50.0467
2022-06-23 | 10:28 | 49.892 | 44735.4659 | 50.0464
2022-06-23 | 10:29 | 49.889 | 44735.4659 | 50.046
2022-06-23 | 10:29 | 49.885 | 44735.4659 | 50.0456
2022-06-23 | 10:29 | 49.882 | 44735.4659 | 50.0452
2022-06-23 | 10:29 | 49.881 | 44735.4659 | 50.0447
2022-06-23 | 10:29 | 49.88 | 44735.4659 | 50.0442
2022-06-23 | 10:29 | 49.876 | 44735.4659 | 50.0437
2022-06-23 | 10:29 | 49.872 | 44735.4659 | 50.0432
2022-06-23 | 10:29 | 49.87 | 44735.4659 | 50.0427
2022-06-23 | 10:29 | 49.866 | 44735.4659 | 50.0422
2022-06-23 | 10:29 | 49.863 | 44735.4659 | 50.0417
2022-06-23 | 10:29 | 49.863 | 44735.4659 | 50.0412
2022-06-23 | 10:29 | 49.865 | 44735.4659 | 50.0407
2022-06-23 | 10:29 | 49.863 | 44735.4659 | 50.0402
2022-06-23 | 10:29 | 49.86 | 44735.4659 | 50.0398
2022-06-23 | 10:29 | 49.857 | 44735.4659 | 50.0393
2022-06-23 | 10:29 | 49.854 | 44735.4659 | 50.0388
2022-06-23 | 10:29 | 49.849 | 44735.4659 | 50.0384
2022-06-23 | 10:29 | 49.849 | 44735.4659 | 50.038
2022-06-23 | 10:29 | 49.847 | 44735.4659 | 50.0375
2022-06-23 | 10:29 | 49.847 | 44735.4659 | 50.0368
2022-06-23 | 10:29 | 49.847 | 44735.4659 | 50.0361
2022-06-23 | 10:29 | 49.849 | 44735.4659 | 50.0355
2022-06-23 | 10:29 | 49.851 | 44735.4659 | 50.0349
2022-06-23 | 10:29 | 49.853 | 44735.4659 | 50.0342
2022-06-23 | 10:29 | 49.851 | 44735.4659 | 50.0336
2022-06-23 | 10:29 | 49.851 | 44735.4659 | 50.0331
2022-06-23 | 10:29 | 49.85 | 44735.4659 | 50.0324
2022-06-23 | 10:29 | 49.848 | 44735.4659 | 50.0319
2022-06-23 | 10:29 | 49.846 | 44735.4659 | 50.0313
2022-06-23 | 10:29 | 49.839 | 44735.4659 | 50.0307
2022-06-23 | 10:29 | 49.835 | 44735.4659 | 50.0302
2022-06-23 | 10:29 | 49.835 | 44735.4659 | 50.0296
2022-06-23 | 10:29 | 49.834 | 44735.4659 | 50.0291
2022-06-23 | 10:29 | 49.834 | 44735.4659 | 50.0285
2022-06-23 | 10:29 | 49.835 | 44735.4659 | 50.028
2022-06-23 | 10:29 | 49.835 | 44735.4659 | 50.0274
2022-06-23 | 10:29 | 49.834 | 44735.4659 | 50.0268
2022-06-23 | 10:29 | 49.835 | 44735.4659 | 50.0263
2022-06-23 | 10:29 | 49.835 | 44735.4659 | 50.0257
2022-06-23 | 10:29 | 49.837 | 2022-06-23 11:11 | 50.0252
2022-06-23 | 10:29 | 49.835 | 44735.4659 | 50.0246
2022-06-23 | 10:29 | 49.831 | 44735.4659 | 50.0241
2022-06-23 | 10:29 | 49.831 | 44735.4659 | 50.0236
2022-06-23 | 10:29 | 49.829 | 44735.4659 | 50.0231
2022-06-23 | 10:29 | 49.828 | 44735.4659 | 50.0226
2022-06-23 | 10:29 | 49.829 | 44735.4659 | 50.0221
2022-06-23 | 10:29 | 49.83 | 44735.4659 | 50.0217
2022-06-23 | 10:29 | 49.829 | 44735.4659 | 50.0212
2022-06-23 | 10:29 | 49.831 | 44735.4659 | 50.0208
2022-06-23 | 10:29 | 49.834 | 44735.4659 | 50.0205
2022-06-23 | 10:29 | 49.836 | 44735.4659 | 50.0201
2022-06-23 | 10:29 | 49.841 | 44735.4659 | 50.0199
2022-06-23 | 10:29 | 49.843 | 44735.4659 | 50.0195
2022-06-23 | 10:29 | 49.848 | 44735.4659 | 50.0191
2022-06-23 | 10:29 | 49.852 | 44735.4659 | 50.0188
2022-06-23 | 10:29 | 49.856 | 44735.4659 | 50.0183
2022-06-23 | 10:29 | 49.859 | 44735.4659 | 50.018
2022-06-23 | 10:29 | 49.859 | 44735.4659 | 50.0176
2022-06-23 | 10:29 | 49.863 | 44735.4659 | 50.0172
2022-06-23 | 10:30 | 49.87 | 44735.4659 | 50.0167
2022-06-23 | 10:30 | 49.875 | 44735.4659 | 50.0163
2022-06-23 | 10:30 | 49.884 | 44735.4659 | 50.0159
2022-06-23 | 10:30 | 49.891 | 44735.4659 | 50.0155
2022-06-23 | 10:30 | 49.898 | 44735.4659 | 50.0151
2022-06-23 | 10:30 | 49.905 | 44735.4659 | 50.0147
2022-06-23 | 10:30 | 49.911 | 44735.4659 | 50.0143
2022-06-23 | 10:30 | 49.915 | 44735.4659 | 50.014
2022-06-23 | 10:30 | 49.917 | 44735.4659 | 50.0137
2022-06-23 | 10:30 | 49.919 | 44735.4659 | 50.0133
2022-06-23 | 10:30 | 49.921 | 44735.4659 | 50.013
2022-06-23 | 10:30 | 49.923 | 44735.4659 | 50.0127
2022-06-23 | 10:30 | 49.925 | 44735.4659 | 50.0123
2022-06-23 | 10:30 | 49.93 | 44735.4659 | 50.012
2022-06-23 | 10:30 | 49.935 | 44735.4659 | 50.0116
2022-06-23 | 10:30 | 49.94 | 44735.4659 | 50.0114
2022-06-23 | 10:30 | 49.945 | 44735.4659 | 50.011
2022-06-23 | 10:30 | 49.947 | 44735.4659 | 50.0107
2022-06-23 | 10:30 | 49.95 | 44735.4659 | 50.0103
2022-06-23 | 10:30 | 49.951 | 44735.4659 | 50.0099
2022-06-23 | 10:30 | 49.953 | 44735.4659 | 50.0095
2022-06-23 | 10:30 | 49.948 | 44735.4659 | 50.0091
2022-06-23 | 10:30 | 49.947 | 44735.4659 | 50.0087
2022-06-23 | 10:30 | 49.948 | 44735.4659 | 50.0083
2022-06-23 | 10:30 | 49.946 | 44735.4659 | 50.0079
2022-06-23 | 10:30 | 49.947 | 44735.4659 | 50.0075
2022-06-23 | 10:30 | 49.948 | 44735.4659 | 50.0071
2022-06-23 | 10:30 | 49.95 | 44735.4659 | 50.0066
2022-06-23 | 10:30 | 49.951 | 44735.4659 | 50.0063
2022-06-23 | 10:30 | 49.952 | 44735.4659 | 50.0058
2022-06-23 | 10:30 | 49.953 | 2022-06-23 11:11 | 50.0055
2022-06-23 | 10:30 | 49.952 | 44735.4659 | 50.0051
2022-06-23 | 10:30 | 49.95 | 44735.4659 | 50.0046
2022-06-23 | 10:30 | 49.949 | 44735.4659 | 50.0042
2022-06-23 | 10:30 | 49.949 | 44735.4659 | 50.0038
2022-06-23 | 10:30 | 49.948 | 44735.4659 | 50.0034
2022-06-23 | 10:30 | 49.948 | 44735.4659 | 50.003
2022-06-23 | 10:30 | 49.948 | 44735.4659 | 50.0026
2022-06-23 | 10:30 | 49.946 | 44735.4659 | 50.0021
2022-06-23 | 10:30 | 49.946 | 44735.4659 | 50.0017
2022-06-23 | 10:30 | 49.946 | 44735.4659 | 50.0013
2022-06-23 | 10:30 | 49.944 | 44735.4659 | 50.0008
2022-06-23 | 10:30 | 49.943 | 44735.4659 | 50.0003
2022-06-23 | 10:30 | 49.942 | 44735.4659 | 49.9999
2022-06-23 | 10:30 | 49.941 | 44735.4659 | 49.9994
2022-06-23 | 10:30 | 49.94 | 44735.4659 | 49.999
2022-06-23 | 10:30 | 49.941 | 44735.4659 | 49.9984
2022-06-23 | 10:30 | 49.941 | 44735.4659 | 49.998
2022-06-23 | 10:30 | 49.943 | 44735.4659 | 49.9976
2022-06-23 | 10:30 | 49.943 | 44735.4659 | 49.9972
2022-06-23 | 10:30 | 49.943 | 44735.4659 | 49.9968
2022-06-23 | 10:30 | 49.941 | 44735.4659 | 49.9964
2022-06-23 | 10:30 | 49.942 | 44735.4659 | 49.996
2022-06-23 | 10:30 | 49.94 | 44735.4659 | 49.9957
2022-06-23 | 10:30 | 49.939 | 44735.4659 | 49.9954
2022-06-23 | 10:30 | 49.938 | 44735.4659 | 49.9949
2022-06-23 | 10:30 | 49.938 | 44735.4659 | 49.9946
2022-06-23 | 10:30 | 49.938 | 44735.4659 | 49.9942
2022-06-23 | 10:30 | 49.939 | 44735.4659 | 49.9938
2022-06-23 | 10:30 | 49.938 | 44735.4659 | 49.9935
2022-06-23 | 10:30 | 49.936 | 44735.4659 | 49.9932
2022-06-23 | 10:31 | 49.937 | 44735.4659 | 49.9928
2022-06-23 | 10:31 | 49.934 | 44735.4659 | 49.9925
2022-06-23 | 10:31 | 49.934 | 44735.4659 | 49.9922
2022-06-23 | 10:31 | 49.932 | 44735.4659 | 49.9919
2022-06-23 | 10:31 | 49.933 | 44735.4659 | 49.9916
2022-06-23 | 10:31 | 49.934 | 44735.4659 | 49.9913
2022-06-23 | 10:31 | 49.932 | 44735.4659 | 49.9908
2022-06-23 | 10:31 | 49.932 | 44735.4659 | 49.9905
2022-06-23 | 10:31 | 49.934 | 44735.4659 | 49.9902
2022-06-23 | 10:31 | 49.935 | 44735.4659 | 49.99
2022-06-23 | 10:31 | 49.936 | 44735.4659 | 49.9896
2022-06-23 | 10:31 | 49.935 | 44735.4659 | 49.9893
2022-06-23 | 10:31 | 49.935 | 44735.4659 | 49.9889
2022-06-23 | 10:31 | 49.935 | 44735.4659 | 49.9886
2022-06-23 | 10:31 | 49.933 | 44735.4659 | 49.9883
2022-06-23 | 10:31 | 49.933 | 44735.4659 | 49.988
2022-06-23 | 10:31 | 49.932 | 44735.4659 | 49.9878
2022-06-23 | 10:31 | 49.93 | 44735.4659 | 49.9876
2022-06-23 | 10:31 | 49.93 | 44735.4659 | 49.9874
2022-06-23 | 10:31 | 49.927 | 2022-06-23 11:11 | 49.9872
2022-06-23 | 10:31 | 49.926 | 44735.4659 | 49.987
2022-06-23 | 10:31 | 49.926 | 44735.4659 | 49.9867
2022-06-23 | 10:31 | 49.927 | 44735.4659 | 49.9865
2022-06-23 | 10:31 | 49.929 | 44735.4659 | 49.9862
2022-06-23 | 10:31 | 49.93 | 44735.4659 | 49.9859
2022-06-23 | 10:31 | 49.933 | 44735.4659 | 49.9857
2022-06-23 | 10:31 | 49.934 | 44735.4659 | 49.9854
2022-06-23 | 10:31 | 49.933 | 44735.4659 | 49.9851
2022-06-23 | 10:31 | 49.933 | 44735.4659 | 49.9848
2022-06-23 | 10:31 | 49.935 | 44735.4659 | 49.9846
2022-06-23 | 10:31 | 49.934 | 44735.4659 | 49.9842
2022-06-23 | 10:31 | 49.933 | 44735.4659 | 49.984
2022-06-23 | 10:31 | 49.933 | 44735.4659 | 49.9837
2022-06-23 | 10:31 | 49.932 | 44735.4659 | 49.9835
2022-06-23 | 10:31 | 49.926 | 44735.4659 | 49.9833
2022-06-23 | 10:31 | 49.926 | 44735.4659 | 49.983
2022-06-23 | 10:31 | 49.924 | 44735.4659 | 49.9828
2022-06-23 | 10:31 | 49.924 | 44735.4659 | 49.9825
2022-06-23 | 10:31 | 49.924 | 44735.4659 | 49.9822
2022-06-23 | 10:31 | 49.926 | 44735.4659 | 49.982
2022-06-23 | 10:31 | 49.928 | 44735.4659 | 49.9818
2022-06-23 | 10:31 | 49.929 | 44735.4659 | 49.9817
2022-06-23 | 10:31 | 49.93 | 44735.4659 | 49.9816
2022-06-23 | 10:31 | 49.935 | 44735.4659 | 49.9815
2022-06-23 | 10:31 | 49.937 | 44735.4659 | 49.9813
2022-06-23 | 10:31 | 49.935 | 44735.4659 | 49.9812
2022-06-23 | 10:31 | 49.936 | 44735.4659 | 49.981
2022-06-23 | 10:31 | 49.933 | 44735.4659 | 49.9808
2022-06-23 | 10:31 | 49.93 | 44735.4659 | 49.9807
2022-06-23 | 10:31 | 49.929 | 44735.4659 | 49.9804
2022-06-23 | 10:31 | 49.93 | 44735.4659 | 49.9802
2022-06-23 | 10:31 | 49.93 | 44735.4659 | 49.98
2022-06-23 | 10:31 | 49.931 | 44735.4659 | 49.9798
2022-06-23 | 10:31 | 49.929 | 44735.4659 | 49.9796
2022-06-23 | 10:31 | 49.928 | 44735.4659 | 49.9795
2022-06-23 | 10:31 | 49.927 | 44735.4659 | 49.9793
2022-06-23 | 10:31 | 49.925 | 44735.4659 | 49.9791
2022-06-23 | 10:31 | 49.925 | 44735.4659 | 49.9789
2022-06-23 | 10:31 | 49.925 | 44735.4659 | 49.9787
2022-06-23 | 10:32 | 49.927 | 44735.4659 | 49.9786
2022-06-23 | 10:32 | 49.929 | 44735.4659 | 49.9784
2022-06-23 | 10:32 | 49.93 | 44735.4659 | 49.9782
2022-06-23 | 10:32 | 49.932 | 44735.4659 | 49.978
2022-06-23 | 10:32 | 49.933 | 44735.4659 | 49.9779
2022-06-23 | 10:32 | 49.936 | 44735.4659 | 49.9777
2022-06-23 | 10:32 | 49.938 | 44735.4659 | 49.9775
2022-06-23 | 10:32 | 49.938 | 44735.4659 | 49.9774
2022-06-23 | 10:32 | 49.938 | 44735.4659 | 49.9773
2022-06-23 | 10:32 | 49.938 | 44735.4659 | 49.9771
2022-06-23 | 10:32 | 49.94 | 2022-06-23 11:11 | 49.977
2022-06-23 | 10:32 | 49.942 | 44735.4659 | 49.9768
2022-06-23 | 10:32 | 49.943 | 44735.4659 | 49.9767
2022-06-23 | 10:32 | 49.946 | 44735.4659 | 49.9765
2022-06-23 | 10:32 | 49.948 | 44735.4659 | 49.9763
2022-06-23 | 10:32 | 49.949 | 44735.4659 | 49.9762
2022-06-23 | 10:32 | 49.952 | 44735.4659 | 49.976
2022-06-23 | 10:32 | 49.952 | 44735.4659 | 49.9759
2022-06-23 | 10:32 | 49.951 | 44735.4659 | 49.9757
2022-06-23 | 10:32 | 49.95 | 44735.4659 | 49.9756
2022-06-23 | 10:32 | 49.95 | 44735.4659 | 49.9755
2022-06-23 | 10:32 | 49.949 | 44735.4659 | 49.9754
2022-06-23 | 10:32 | 49.947 | 44735.4659 | 49.9753
2022-06-23 | 10:32 | 49.944 | 44735.4659 | 49.9752
2022-06-23 | 10:32 | 49.941 | 44735.4659 | 49.975
2022-06-23 | 10:32 | 49.939 | 44735.4659 | 49.9749
2022-06-23 | 10:32 | 49.94 | 44735.4659 | 49.9748
2022-06-23 | 10:32 | 49.942 | 44735.4659 | 49.9747
2022-06-23 | 10:32 | 49.942 | 44735.4659 | 49.9746
2022-06-23 | 10:32 | 49.941 | 44735.4659 | 49.9745
2022-06-23 | 10:32 | 49.94 | 44735.4659 | 49.9743
2022-06-23 | 10:32 | 49.939 | 44735.4659 | 49.9742
2022-06-23 | 10:32 | 49.938 | 44735.4659 | 49.974
2022-06-23 | 10:32 | 49.941 | 44735.4659 | 49.9739
2022-06-23 | 10:32 | 49.941 | 44735.4659 | 49.9737
2022-06-23 | 10:32 | 49.941 | 44735.4659 | 49.9736
2022-06-23 | 10:32 | 49.942 | 44735.4659 | 49.9735
2022-06-23 | 10:32 | 49.943 | 44735.4659 | 49.9733
2022-06-23 | 10:32 | 49.944 | 44735.4659 | 49.9732
2022-06-23 | 10:32 | 49.944 | 44735.4659 | 49.9731
2022-06-23 | 10:32 | 49.944 | 44735.4659 | 49.9729
2022-06-23 | 10:32 | 49.946 | 44735.4659 | 49.9728
2022-06-23 | 10:32 | 49.948 | 44735.4659 | 49.9726
2022-06-23 | 10:32 | 49.949 | 44735.4659 | 49.9724
2022-06-23 | 10:32 | 49.95 | 44735.4659 | 49.9723
2022-06-23 | 10:32 | 49.952 | 44735.4659 | 49.9722
2022-06-23 | 10:32 | 49.954 | 44735.4659 | 49.9721
2022-06-23 | 10:32 | 49.956 | 44735.4659 | 49.972
2022-06-23 | 10:32 | 49.958 | 44735.4659 | 49.9719
2022-06-23 | 10:32 | 49.957 | 44735.4659 | 49.9718
2022-06-23 | 10:32 | 49.956 | 44735.4659 | 49.9717
2022-06-23 | 10:32 | 49.955 | 44735.4659 | 49.9715
2022-06-23 | 10:32 | 49.954 | 44735.4659 | 49.9714
2022-06-23 | 10:32 | 49.95 | 44735.4659 | 49.9712
2022-06-23 | 10:32 | 49.947 | 44735.4659 | 49.971
2022-06-23 | 10:32 | 49.944 | 44735.4659 | 49.9708
2022-06-23 | 10:32 | 49.941 | 44735.4659 | 49.9706
2022-06-23 | 10:32 | 49.941 | 44735.4659 | 49.9705
2022-06-23 | 10:32 | 49.941 | 44735.4659 | 49.9703
2022-06-23 | 10:32 | 49.941 | 44735.4659 | 49.9702
2022-06-23 | 10:32 | 49.94 | 2022-06-23 11:11 | 49.9701
2022-06-23 | 10:33 | 49.938 | 44735.4659 | 49.97
2022-06-23 | 10:33 | 49.935 | 44735.4659 | 49.97
2022-06-23 | 10:33 | 49.933 | 44735.4659 | 49.9698
2022-06-23 | 10:33 | 49.931 | 44735.4659 | 49.9697
2022-06-23 | 10:33 | 49.931 | 44735.4659 | 49.9695
2022-06-23 | 10:33 | 49.929 | 44735.4659 | 49.9693
2022-06-23 | 10:33 | 49.928 | 44735.4659 | 49.9692
2022-06-23 | 10:33 | 49.929 | 44735.4659 | 49.969
2022-06-23 | 10:33 | 49.927 | 44735.4659 | 49.9688
2022-06-23 | 10:33 | 49.927 | 44735.4659 | 49.9687
2022-06-23 | 10:33 | 49.93 | 44735.4659 | 49.9686
2022-06-23 | 10:33 | 49.933 | 44735.4659 | 49.9685
2022-06-23 | 10:33 | 49.934 | 44735.4659 | 49.9684
2022-06-23 | 10:33 | 49.936 | 44735.4659 | 49.9683
2022-06-23 | 10:33 | 49.934 | 44735.4659 | 49.9682
2022-06-23 | 10:33 | 49.934 | 44735.4659 | 49.9682
2022-06-23 | 10:33 | 49.933 | 44735.4659 | 49.9682
2022-06-23 | 10:33 | 49.931 | 44735.4659 | 49.9681
2022-06-23 | 10:33 | 49.93 | 44735.4659 | 49.968
2022-06-23 | 10:33 | 49.928 | 44735.4659 | 49.9679
2022-06-23 | 10:33 | 49.925 | 44735.4659 | 49.9678
2022-06-23 | 10:33 | 49.923 | 44735.4659 | 49.9676
2022-06-23 | 10:33 | 49.921 | 44735.4659 | 49.9675
2022-06-23 | 10:33 | 49.92 | 44735.4659 | 49.9674
2022-06-23 | 10:33 | 49.918 | 44735.4659 | 49.9673
2022-06-23 | 10:33 | 49.915 | 44735.4659 | 49.9671
2022-06-23 | 10:33 | 49.913 | 44735.4659 | 49.967
2022-06-23 | 10:33 | 49.912 | 44735.4659 | 49.967
2022-06-23 | 10:33 | 49.913 | 44735.4659 | 49.9669
2022-06-23 | 10:33 | 49.912 | 44735.4659 | 49.9669
2022-06-23 | 10:33 | 49.911 | 44735.4659 | 49.9669
2022-06-23 | 10:33 | 49.909 | 44735.4659 | 49.9669
2022-06-23 | 10:33 | 49.908 | 44735.4659 | 49.9668
2022-06-23 | 10:33 | 49.908 | 44735.4659 | 49.9668
2022-06-23 | 10:33 | 49.909 | 44735.4659 | 49.9667
2022-06-23 | 10:33 | 49.912 | 44735.4659 | 49.9667
2022-06-23 | 10:33 | 49.915 | 44735.4659 | 49.9666
2022-06-23 | 10:33 | 49.918 | 44735.4659 | 49.9666
2022-06-23 | 10:33 | 49.92 | 44735.4659 | 49.9665
2022-06-23 | 10:33 | 49.921 | 44735.4659 | 49.9664
2022-06-23 | 10:33 | 49.92 | 44735.4659 | 49.9663
2022-06-23 | 10:33 | 49.922 | 44735.4659 | 49.9662
2022-06-23 | 10:33 | 49.923 | 44735.4659 | 49.9661
2022-06-23 | 10:33 | 49.925 | 44735.4659 | 49.9661
2022-06-23 | 10:33 | 49.926 | 44735.4659 | 49.966
2022-06-23 | 10:33 | 49.925 | 44735.4659 | 49.966
2022-06-23 | 10:33 | 49.924 | 44735.4659 | 49.9659
2022-06-23 | 10:33 | 49.924 | 44735.4659 | 49.9659
2022-06-23 | 10:33 | 49.923 | 44735.4659 | 49.9659
2022-06-23 | 10:33 | 49.922 | 2022-06-23 11:11 | 49.9658
2022-06-23 | 10:33 | 49.918 | 44735.4659 | 49.9658
2022-06-23 | 10:33 | 49.914 | 44735.4659 | 49.9657
2022-06-23 | 10:33 | 49.911 | 44735.4659 | 49.9656
2022-06-23 | 10:33 | 49.906 | 44735.4659 | 49.9656
2022-06-23 | 10:33 | 49.902 | 44735.466 | 49.9655
2022-06-23 | 10:33 | 49.9 | 44735.466 | 49.9655
2022-06-23 | 10:33 | 49.897 | 44735.466 | 49.9654
2022-06-23 | 10:33 | 49.896 | 44735.466 | 49.9653
2022-06-23 | 10:33 | 49.898 | 44735.466 | 49.9652
2022-06-23 | 10:34 | 49.899 | 44735.466 | 49.9652
2022-06-23 | 10:34 | 49.9 | 44735.466 | 49.9651
2022-06-23 | 10:34 | 49.901 | 44735.466 | 49.965
2022-06-23 | 10:34 | 49.901 | 44735.466 | 49.965
2022-06-23 | 10:34 | 49.901 | 44735.466 | 49.9649
2022-06-23 | 10:34 | 49.901 | 44735.466 | 49.9648
2022-06-23 | 10:34 | 49.903 | 44735.466 | 49.9648
2022-06-23 | 10:34 | 49.904 | 44735.466 | 49.9647
2022-06-23 | 10:34 | 49.904 | 44735.466 | 49.9646
2022-06-23 | 10:34 | 49.906 | 44735.466 | 49.9645
2022-06-23 | 10:34 | 49.907 | 44735.466 | 49.9645
2022-06-23 | 10:34 | 49.906 | 44735.466 | 49.9643
2022-06-23 | 10:34 | 49.909 | 44735.466 | 49.9643
2022-06-23 | 10:34 | 49.911 | 44735.466 | 49.9643
2022-06-23 | 10:34 | 49.911 | 44735.466 | 49.9643
2022-06-23 | 10:34 | 49.911 | 44735.466 | 49.9643
2022-06-23 | 10:34 | 49.909 | 44735.466 | 49.9642
2022-06-23 | 10:34 | 49.909 | 44735.466 | 49.9642
2022-06-23 | 10:34 | 49.909 | 44735.466 | 49.964
2022-06-23 | 10:34 | 49.908 | 44735.466 | 49.9639
2022-06-23 | 10:34 | 49.907 | 44735.466 | 49.9638
2022-06-23 | 10:34 | 49.908 | 44735.466 | 49.9636
2022-06-23 | 10:34 | 49.909 | 44735.466 | 49.9635
2022-06-23 | 10:34 | 49.91 | 44735.466 | 49.9634
2022-06-23 | 10:34 | 49.909 | 44735.466 | 49.9634
2022-06-23 | 10:34 | 49.911 | 44735.466 | 49.9634
2022-06-23 | 10:34 | 49.915 | 44735.466 | 49.9633
2022-06-23 | 10:34 | 49.918 | 44735.466 | 49.9633
2022-06-23 | 10:34 | 49.918 | 44735.466 | 49.9633
2022-06-23 | 10:34 | 49.917 | 44735.466 | 49.9632
2022-06-23 | 10:34 | 49.917 | 44735.466 | 49.9632
2022-06-23 | 10:34 | 49.912 | 44735.466 | 49.9631
2022-06-23 | 10:34 | 49.908 | 44735.466 | 49.9629
2022-06-23 | 10:34 | 49.903 | 44735.466 | 49.9628
2022-06-23 | 10:34 | 49.898 | 44735.466 | 49.9627
2022-06-23 | 10:34 | 49.894 | 44735.466 | 49.9627
2022-06-23 | 10:34 | 49.891 | 44735.466 | 49.9626
2022-06-23 | 10:34 | 49.888 | 44735.466 | 49.9625
2022-06-23 | 10:34 | 49.886 | 44735.466 | 49.9624
2022-06-23 | 10:34 | 49.883 | 44735.466 | 49.9624
2022-06-23 | 10:34 | 49.883 | 2022-06-23 11:11 | 49.9623
2022-06-23 | 10:34 | 49.883 | 44735.466 | 49.9622
2022-06-23 | 10:34 | 49.884 | 44735.466 | 49.9621
2022-06-23 | 10:34 | 49.883 | 44735.466 | 49.962
2022-06-23 | 10:34 | 49.883 | 44735.466 | 49.962
2022-06-23 | 10:34 | 49.885 | 44735.466 | 49.9619
2022-06-23 | 10:34 | 49.884 | 44735.466 | 49.9617
2022-06-23 | 10:34 | 49.884 | 44735.466 | 49.9616
2022-06-23 | 10:34 | 49.884 | 44735.466 | 49.9615
2022-06-23 | 10:34 | 49.884 | 44735.466 | 49.9615
2022-06-23 | 10:34 | 49.884 | 44735.466 | 49.9614
2022-06-23 | 10:34 | 49.882 | 44735.466 | 49.9613
2022-06-23 | 10:34 | 49.883 | 44735.466 | 49.9612
2022-06-23 | 10:34 | 49.883 | 44735.466 | 49.9612
2022-06-23 | 10:34 | 49.885 | 44735.466 | 49.9611
2022-06-23 | 10:34 | 49.887 | 44735.466 | 49.9611
2022-06-23 | 10:34 | 49.888 | 44735.466 | 49.961
2022-06-23 | 10:34 | 49.891 | 44735.466 | 49.961
2022-06-23 | 10:34 | 49.89 | 44735.466 | 49.9609
2022-06-23 | 10:34 | 49.896 | 44735.466 | 49.9608
2022-06-23 | 10:34 | 49.896 | 44735.466 | 49.9608
2022-06-23 | 10:35 | 49.897 | 44735.466 | 49.9607
2022-06-23 | 10:35 | 49.894 | 44735.466 | 49.9606
2022-06-23 | 10:35 | 49.895 | 44735.466 | 49.9605
2022-06-23 | 10:35 | 49.892 | 44735.466 | 49.9604
2022-06-23 | 10:35 | 49.888 | 44735.466 | 49.9603
2022-06-23 | 10:35 | 49.887 | 44735.466 | 49.9603
2022-06-23 | 10:35 | 49.887 | 44735.466 | 49.9602
2022-06-23 | 10:35 | 49.889 | 44735.466 | 49.9601
2022-06-23 | 10:35 | 49.888 | 44735.466 | 49.96
2022-06-23 | 10:35 | 49.892 | 44735.466 | 49.9599
2022-06-23 | 10:35 | 49.891 | 44735.466 | 49.9598
2022-06-23 | 10:35 | 49.889 | 44735.466 | 49.9597
2022-06-23 | 10:35 | 49.888 | 44735.466 | 49.9596
2022-06-23 | 10:35 | 49.887 | 44735.466 | 49.9595
2022-06-23 | 10:35 | 49.886 | 44735.466 | 49.9595
2022-06-23 | 10:35 | 49.884 | 44735.466 | 49.9594
2022-06-23 | 10:35 | 49.883 | 44735.466 | 49.9594
2022-06-23 | 10:35 | 49.881 | 44735.466 | 49.9594
2022-06-23 | 10:35 | 49.879 | 44735.466 | 49.9594
2022-06-23 | 10:35 | 49.877 | 44735.466 | 49.9593
2022-06-23 | 10:35 | 49.876 | 44735.466 | 49.9593
2022-06-23 | 10:35 | 49.876 | 44735.466 | 49.9591
2022-06-23 | 10:35 | 49.875 | 44735.466 | 49.9591
2022-06-23 | 10:35 | 49.878 | 44735.466 | 49.959
2022-06-23 | 10:35 | 49.878 | 44735.466 | 49.959
2022-06-23 | 10:35 | 49.879 | 44735.466 | 49.9589
2022-06-23 | 10:35 | 49.878 | 44735.466 | 49.9589
2022-06-23 | 10:35 | 49.876 | 44735.466 | 49.9588
2022-06-23 | 10:35 | 49.874 | 44735.466 | 49.9587
2022-06-23 | 10:35 | 49.872 | 2022-06-23 11:11 | 49.9586
2022-06-23 | 10:35 | 49.869 | 44735.466 | 49.9585
2022-06-23 | 10:35 | 49.867 | 44735.466 | 49.9584
2022-06-23 | 10:35 | 49.866 | 44735.466 | 49.9583
2022-06-23 | 10:35 | 49.867 | 44735.466 | 49.9582
2022-06-23 | 10:35 | 49.864 | 44735.466 | 49.9581
2022-06-23 | 10:35 | 49.866 | 44735.466 | 49.9579
2022-06-23 | 10:35 | 49.866 | 44735.466 | 49.9578
2022-06-23 | 10:35 | 49.868 | 44735.466 | 49.9576
2022-06-23 | 10:35 | 49.869 | 44735.466 | 49.9576
2022-06-23 | 10:35 | 49.872 | 44735.466 | 49.9575
2022-06-23 | 10:35 | 49.872 | 44735.466 | 49.9574
2022-06-23 | 10:35 | 49.872 | 44735.466 | 49.9573
2022-06-23 | 10:35 | 49.873 | 44735.466 | 49.9574
2022-06-23 | 10:35 | 49.877 | 44735.466 | 49.9573
2022-06-23 | 10:35 | 49.879 | 44735.466 | 49.9573
2022-06-23 | 10:35 | 49.883 | 44735.466 | 49.9573
2022-06-23 | 10:35 | 49.887 | 44735.466 | 49.9573
2022-06-23 | 10:35 | 49.891 | 44735.466 | 49.9573
2022-06-23 | 10:35 | 49.895 | 44735.466 | 49.9572
2022-06-23 | 10:35 | 49.894 | 44735.466 | 49.9571
2022-06-23 | 10:35 | 49.894 | 44735.466 | 49.957
2022-06-23 | 10:35 | 49.895 | 44735.466 | 49.9569
2022-06-23 | 10:35 | 49.893 | 44735.466 | 49.9568
2022-06-23 | 10:35 | 49.889 | 44735.466 | 49.9567
2022-06-23 | 10:35 | 49.887 | 44735.466 | 49.9565
2022-06-23 | 10:35 | 49.884 | 44735.466 | 49.9565
2022-06-23 | 10:35 | 49.882 | 44735.466 | 49.9564
2022-06-23 | 10:35 | 49.881 | 44735.466 | 49.9563
2022-06-23 | 10:35 | 49.879 | 44735.466 | 49.9561
2022-06-23 | 10:35 | 49.877 | 44735.466 | 49.956
2022-06-23 | 10:36 | 49.877 | 44735.466 | 49.956
2022-06-23 | 10:36 | 49.874 | 44735.466 | 49.9558
2022-06-23 | 10:36 | 49.873 | 44735.466 | 49.9558
2022-06-23 | 10:36 | 49.871 | 44735.466 | 49.9557
2022-06-23 | 10:36 | 49.87 | 44735.466 | 49.9556
2022-06-23 | 10:36 | 49.869 | 44735.466 | 49.9555
2022-06-23 | 10:36 | 49.867 | 44735.466 | 49.9555
2022-06-23 | 10:36 | 49.869 | 44735.466 | 49.9554
2022-06-23 | 10:36 | 49.868 | 44735.466 | 49.9554
2022-06-23 | 10:36 | 49.871 | 44735.466 | 49.9553
2022-06-23 | 10:36 | 49.869 | 44735.466 | 49.9552
2022-06-23 | 10:36 | 49.871 | 44735.466 | 49.9552
2022-06-23 | 10:36 | 49.871 | 44735.466 | 49.9551
2022-06-23 | 10:36 | 49.872 | 44735.466 | 49.955
2022-06-23 | 10:36 | 49.87 | 44735.466 | 49.9549
2022-06-23 | 10:36 | 49.872 | 44735.466 | 49.9548
2022-06-23 | 10:36 | 49.874 | 44735.466 | 49.9547
2022-06-23 | 10:36 | 49.877 | 44735.466 | 49.9546
2022-06-23 | 10:36 | 49.878 | 44735.466 | 49.9545
2022-06-23 | 10:36 | 49.879 | 2022-06-23 11:11 | 49.9544
2022-06-23 | 10:36 | 49.882 | 44735.466 | 49.9544
2022-06-23 | 10:36 | 49.883 | 44735.466 | 49.9543
2022-06-23 | 10:36 | 49.883 | 44735.466 | 49.9543
2022-06-23 | 10:36 | 49.886 | 44735.466 | 49.9542
2022-06-23 | 10:36 | 49.89 | 44735.466 | 49.9542
2022-06-23 | 10:36 | 49.892 | 44735.466 | 49.9541
2022-06-23 | 10:36 | 49.894 | 44735.466 | 49.9541
2022-06-23 | 10:36 | 49.898 | 44735.466 | 49.954
2022-06-23 | 10:36 | 49.9 | 44735.466 | 49.954
2022-06-23 | 10:36 | 49.902 | 44735.466 | 49.9539
2022-06-23 | 10:36 | 49.901 | 44735.466 | 49.9539
2022-06-23 | 10:36 | 49.9 | 44735.466 | 49.9538
2022-06-23 | 10:36 | 49.899 | 44735.466 | 49.9537
2022-06-23 | 10:36 | 49.9 | 44735.466 | 49.9536
2022-06-23 | 10:36 | 49.901 | 44735.466 | 49.9535
2022-06-23 | 10:36 | 49.902 | 44735.466 | 49.9535
2022-06-23 | 10:36 | 49.901 | 44735.466 | 49.9533
2022-06-23 | 10:36 | 49.9 | 44735.466 | 49.9532
2022-06-23 | 10:36 | 49.901 | 44735.466 | 49.9531
2022-06-23 | 10:36 | 49.898 | 44735.466 | 49.953
2022-06-23 | 10:36 | 49.899 | 44735.466 | 49.9528
2022-06-23 | 10:36 | 49.898 | 44735.466 | 49.9527
2022-06-23 | 10:36 | 49.895 | 44735.466 | 49.9526
2022-06-23 | 10:36 | 49.895 | 44735.466 | 49.9526
2022-06-23 | 10:36 | 49.892 | 44735.466 | 49.9525
2022-06-23 | 10:36 | 49.893 | 44735.466 | 49.9525
2022-06-23 | 10:36 | 49.892 | 44735.466 | 49.9524
2022-06-23 | 10:36 | 49.891 | 44735.466 | 49.9524
2022-06-23 | 10:36 | 49.889 | 44735.466 | 49.9524
2022-06-23 | 10:36 | 49.888 | 44735.466 | 49.9523
2022-06-23 | 10:36 | 49.888 | 44735.466 | 49.9523
2022-06-23 | 10:36 | 49.886 | 44735.466 | 49.9522
2022-06-23 | 10:36 | 49.885 | 44735.466 | 49.9522
2022-06-23 | 10:36 | 49.885 | 44735.466 | 49.9521
2022-06-23 | 10:36 | 49.884 | 44735.466 | 49.9521
2022-06-23 | 10:36 | 49.885 | 44735.466 | 49.9521
2022-06-23 | 10:36 | 49.885 | 44735.466 | 49.952
2022-06-23 | 10:36 | 49.885 | 44735.466 | 49.9519
2022-06-23 | 10:36 | 49.889 | 44735.466 | 49.9518
2022-06-23 | 10:37 | 49.89 | 44735.466 | 49.9516
2022-06-23 | 10:37 | 49.891 | 44735.466 | 49.9515
2022-06-23 | 10:37 | 49.894 | 44735.466 | 49.9514
2022-06-23 | 10:37 | 49.895 | 44735.466 | 49.9512
2022-06-23 | 10:37 | 49.898 | 44735.466 | 49.9512
2022-06-23 | 10:37 | 49.897 | 44735.466 | 49.9511
2022-06-23 | 10:37 | 49.901 | 44735.466 | 49.9511
2022-06-23 | 10:37 | 49.903 | 44735.466 | 49.951
2022-06-23 | 10:37 | 49.908 | 44735.466 | 49.951
2022-06-23 | 10:37 | 49.91 | 44735.466 | 49.9509
2022-06-23 | 10:37 | 49.914 | 2022-06-23 11:11 | 49.9509
2022-06-23 | 10:37 | 49.917 | 44735.466 | 49.9509
2022-06-23 | 10:37 | 49.921 | 44735.466 | 49.9508
2022-06-23 | 10:37 | 49.923 | 44735.466 | 49.9508
2022-06-23 | 10:37 | 49.928 | 44735.466 | 49.9507
2022-06-23 | 10:37 | 49.93 | 44735.466 | 49.9506
2022-06-23 | 10:37 | 49.932 | 44735.466 | 49.9506
2022-06-23 | 10:37 | 49.932 | 44735.466 | 49.9505
2022-06-23 | 10:37 | 49.933 | 44735.466 | 49.9504
2022-06-23 | 10:37 | 49.933 | 44735.466 | 49.9503
2022-06-23 | 10:37 | 49.933 | 44735.466 | 49.9502
2022-06-23 | 10:37 | 49.933 | 44735.466 | 49.9501
2022-06-23 | 10:37 | 49.934 | 44735.466 | 49.95
2022-06-23 | 10:37 | 49.934 | 44735.466 | 49.9499
2022-06-23 | 10:37 | 49.938 | 44735.466 | 49.9498
2022-06-23 | 10:37 | 49.936 | 44735.466 | 49.9498
2022-06-23 | 10:37 | 49.935 | 44735.466 | 49.9497
2022-06-23 | 10:37 | 49.934 | 44735.466 | 49.9496
2022-06-23 | 10:37 | 49.933 | 44735.466 | 49.9496
2022-06-23 | 10:37 | 49.931 | 44735.466 | 49.9496
2022-06-23 | 10:37 | 49.929 | 44735.466 | 49.9495
2022-06-23 | 10:37 | 49.925 | 44735.466 | 49.9494
2022-06-23 | 10:37 | 49.923 | 44735.466 | 49.9493
2022-06-23 | 10:37 | 49.921 | 44735.466 | 49.9492
2022-06-23 | 10:37 | 49.917 | 44735.466 | 49.949
2022-06-23 | 10:37 | 49.917 | 44735.466 | 49.9488
2022-06-23 | 10:37 | 49.917 | 44735.466 | 49.9486
2022-06-23 | 10:37 | 49.916 | 44735.466 | 49.9485
2022-06-23 | 10:37 | 49.916 | 44735.466 | 49.9484
2022-06-23 | 10:37 | 49.915 | 44735.466 | 49.9483
2022-06-23 | 10:37 | 49.914 | 44735.466 | 49.9482
2022-06-23 | 10:37 | 49.913 | 44735.466 | 49.9482
2022-06-23 | 10:37 | 49.912 | 44735.466 | 49.948
2022-06-23 | 10:37 | 49.914 | 44735.466 | 49.948
2022-06-23 | 10:37 | 49.918 | 44735.466 | 49.948
2022-06-23 | 10:37 | 49.919 | 44735.466 | 49.9479
2022-06-23 | 10:37 | 49.923 | 44735.466 | 49.9478
2022-06-23 | 10:37 | 49.923 | 44735.466 | 49.9478
2022-06-23 | 10:37 | 49.923 | 44735.466 | 49.9477
2022-06-23 | 10:37 | 49.924 | 44735.466 | 49.9476
2022-06-23 | 10:37 | 49.925 | 44735.466 | 49.9475
2022-06-23 | 10:37 | 49.924 | 44735.466 | 49.9474
2022-06-23 | 10:37 | 49.925 | 44735.466 | 49.9473
2022-06-23 | 10:37 | 49.927 | 44735.466 | 49.9473
2022-06-23 | 10:37 | 49.926 | 44735.466 | 49.9472
2022-06-23 | 10:37 | 49.928 | 44735.466 | 49.9471
2022-06-23 | 10:37 | 49.931 | 44735.466 | 49.947
2022-06-23 | 10:37 | 49.931 | 44735.466 | 49.9469
2022-06-23 | 10:37 | 49.933 | 44735.466 | 49.9468
2022-06-23 | 10:37 | 49.936 | 44735.466 | 49.9467
2022-06-23 | 10:37 | 49.941 | 2022-06-23 11:11 | 49.9465
2022-06-23 | 10:38 | 49.942 | 44735.466 | 49.9464
2022-06-23 | 10:38 | 49.947 | 44735.466 | 49.9463
2022-06-23 | 10:38 | 49.948 | 44735.466 | 49.9462
2022-06-23 | 10:38 | 49.95 | 44735.466 | 49.9461
2022-06-23 | 10:38 | 49.95 | 44735.466 | 49.946
2022-06-23 | 10:38 | 49.952 | 44735.466 | 49.9459
2022-06-23 | 10:38 | 49.95 | 44735.466 | 49.9459
2022-06-23 | 10:38 | 49.953 | 44735.466 | 49.9458
2022-06-23 | 10:38 | 49.95 | 44735.466 | 49.9457
2022-06-23 | 10:38 | 49.953 | 44735.466 | 49.9456
2022-06-23 | 10:38 | 49.954 | 44735.466 | 49.9455
2022-06-23 | 10:38 | 49.955 | 44735.466 | 49.9455
2022-06-23 | 10:38 | 49.958 | 44735.466 | 49.9454
2022-06-23 | 10:38 | 49.958 | 44735.466 | 49.9452
2022-06-23 | 10:38 | 49.957 | 44735.466 | 49.9451
2022-06-23 | 10:38 | 49.956 | 44735.466 | 49.9449
2022-06-23 | 10:38 | 49.959 | 44735.466 | 49.9448
2022-06-23 | 10:38 | 49.96 | 44735.466 | 49.9447
2022-06-23 | 10:38 | 49.96 | 44735.466 | 49.9446
2022-06-23 | 10:38 | 49.959 | 44735.466 | 49.9445
2022-06-23 | 10:38 | 49.958 | 44735.466 | 49.9444
2022-06-23 | 10:38 | 49.957 | 44735.466 | 49.9443
2022-06-23 | 10:38 | 49.956 | 44735.466 | 49.9442
2022-06-23 | 10:38 | 49.958 | 44735.466 | 49.9442
2022-06-23 | 10:38 | 49.957 | 44735.466 | 49.9441
2022-06-23 | 10:38 | 49.96 | 44735.466 | 49.9441
2022-06-23 | 10:38 | 49.958 | 44735.466 | 49.944
2022-06-23 | 10:38 | 49.957 | 44735.466 | 49.944
2022-06-23 | 10:38 | 49.955 | 44735.466 | 49.9439
2022-06-23 | 10:38 | 49.955 | 44735.466 | 49.9439
2022-06-23 | 10:38 | 49.954 | 44735.466 | 49.9438
2022-06-23 | 10:38 | 49.951 | 44735.466 | 49.9437
2022-06-23 | 10:38 | 49.95 | 44735.466 | 49.9435
2022-06-23 | 10:38 | 49.945 | 44735.466 | 49.9434
2022-06-23 | 10:38 | 49.936 | 44735.466 | 49.9433
2022-06-23 | 10:38 | 49.927 | 44735.466 | 49.9432
2022-06-23 | 10:38 | 49.919 | 44735.466 | 49.9431
2022-06-23 | 10:38 | 49.908 | 44735.466 | 49.9432
2022-06-23 | 10:38 | 49.897 | 44735.466 | 49.9431
2022-06-23 | 10:38 | 49.888 | 44735.466 | 49.943
2022-06-23 | 10:38 | 49.877 | 44735.466 | 49.9429
2022-06-23 | 10:38 | 49.87 | 44735.466 | 49.9427
2022-06-23 | 10:38 | 49.866 | 44735.466 | 49.9426
2022-06-23 | 10:38 | 49.864 | 44735.466 | 49.9425
2022-06-23 | 10:38 | 49.857 | 44735.466 | 49.9424
2022-06-23 | 10:38 | 49.856 | 44735.466 | 49.9424
2022-06-23 | 10:38 | 49.856 | 44735.466 | 49.9423
2022-06-23 | 10:38 | 49.856 | 44735.466 | 49.9423
2022-06-23 | 10:38 | 49.855 | 44735.466 | 49.9422
2022-06-23 | 10:38 | 49.856 | 2022-06-23 11:11 | 49.9421
2022-06-23 | 10:38 | 49.855 | 44735.466 | 49.942
2022-06-23 | 10:38 | 49.856 | 44735.466 | 49.9419
2022-06-23 | 10:38 | 49.857 | 44735.466 | 49.9418
2022-06-23 | 10:38 | 49.857 | 44735.466 | 49.9418
2022-06-23 | 10:38 | 49.859 | 44735.466 | 49.9417
2022-06-23 | 10:38 | 49.86 | 44735.466 | 49.9416
2022-06-23 | 10:38 | 49.86 | 44735.466 | 49.9415
2022-06-23 | 10:38 | 49.863 | 44735.466 | 49.9415
2022-06-23 | 10:38 | 49.865 | 44735.466 | 49.9414
2022-06-23 | 10:39 | 49.867 | 44735.466 | 49.9414
2022-06-23 | 10:39 | 49.869 | 44735.466 | 49.9413
2022-06-23 | 10:39 | 49.872 | 44735.466 | 49.9412
2022-06-23 | 10:39 | 49.875 | 44735.466 | 49.9411
2022-06-23 | 10:39 | 49.877 | 44735.466 | 49.9411
2022-06-23 | 10:39 | 49.88 | 44735.466 | 49.941
2022-06-23 | 10:39 | 49.885 | 44735.466 | 49.941
2022-06-23 | 10:39 | 49.889 | 44735.466 | 49.9409
2022-06-23 | 10:39 | 49.892 | 44735.466 | 49.9408
2022-06-23 | 10:39 | 49.894 | 44735.466 | 49.9408
2022-06-23 | 10:39 | 49.895 | 44735.466 | 49.9408
2022-06-23 | 10:39 | 49.897 | 44735.466 | 49.9408
2022-06-23 | 10:39 | 49.898 | 44735.466 | 49.9407
2022-06-23 | 10:39 | 49.9 | 44735.466 | 49.9407
2022-06-23 | 10:39 | 49.901 | 44735.466 | 49.9406
2022-06-23 | 10:39 | 49.902 | 44735.466 | 49.9406
2022-06-23 | 10:39 | 49.903 | 44735.466 | 49.9405
2022-06-23 | 10:39 | 49.903 | 44735.466 | 49.9405
2022-06-23 | 10:39 | 49.903 | 44735.466 | 49.9405
2022-06-23 | 10:39 | 49.899 | 44735.466 | 49.9405
2022-06-23 | 10:39 | 49.903 | 44735.466 | 49.9404
2022-06-23 | 10:39 | 49.902 | 44735.466 | 49.9404
2022-06-23 | 10:39 | 49.906 | 44735.466 | 49.9403
2022-06-23 | 10:39 | 49.904 | 44735.466 | 49.9403
2022-06-23 | 10:39 | 49.906 | 44735.466 | 49.9401
2022-06-23 | 10:39 | 49.904 | 44735.466 | 49.9401
2022-06-23 | 10:39 | 49.903 | 44735.466 | 49.94
2022-06-23 | 10:39 | 49.902 | 44735.466 | 49.9399
2022-06-23 | 10:39 | 49.9 | 44735.466 | 49.9399
2022-06-23 | 10:39 | 49.895 | 44735.466 | 49.9397
2022-06-23 | 10:39 | 49.892 | 44735.466 | 49.9397
2022-06-23 | 10:39 | 49.887 | 44735.466 | 49.9397
2022-06-23 | 10:39 | 49.887 | 44735.466 | 49.9397
2022-06-23 | 10:39 | 49.887 | 44735.466 | 49.9396
2022-06-23 | 10:39 | 49.889 | 44735.466 | 49.9396
2022-06-23 | 10:39 | 49.891 | 44735.466 | 49.9396
2022-06-23 | 10:39 | 49.891 | 44735.466 | 49.9395
2022-06-23 | 10:39 | 49.893 | 44735.466 | 49.9395
2022-06-23 | 10:39 | 49.892 | 44735.466 | 49.9394
2022-06-23 | 10:39 | 49.893 | 44735.466 | 49.9393
2022-06-23 | 10:39 | 49.893 | 2022-06-23 11:11 | 49.9393
2022-06-23 | 10:39 | 49.895 | 44735.466 | 49.9392
2022-06-23 | 10:39 | 49.894 | 44735.466 | 49.9391
2022-06-23 | 10:39 | 49.895 | 44735.466 | 49.9391
2022-06-23 | 10:39 | 49.897 | 44735.466 | 49.939
2022-06-23 | 10:39 | 49.898 | 44735.466 | 49.939
2022-06-23 | 10:39 | 49.899 | 44735.466 | 49.9389
2022-06-23 | 10:39 | 49.898 | 44735.466 | 49.9389
2022-06-23 | 10:39 | 49.899 | 44735.466 | 49.9389
2022-06-23 | 10:39 | 49.898 | 44735.466 | 49.9389
2022-06-23 | 10:39 | 49.897 | 44735.466 | 49.9389
2022-06-23 | 10:39 | 49.898 | 44735.466 | 49.9388
2022-06-23 | 10:39 | 49.899 | 44735.466 | 49.9388
2022-06-23 | 10:39 | 49.902 | 44735.466 | 49.9388
2022-06-23 | 10:39 | 49.905 | 44735.466 | 49.9388
2022-06-23 | 10:39 | 49.905 | 44735.466 | 49.9387
2022-06-23 | 10:39 | 49.906 | 44735.466 | 49.9387
2022-06-23 | 10:39 | 49.904 | 44735.466 | 49.9386
2022-06-23 | 10:39 | 49.902 | 44735.466 | 49.9386
2022-06-23 | 10:39 | 49.9 | 44735.466 | 49.9385
2022-06-23 | 10:39 | 49.897 | 44735.466 | 49.9384
2022-06-23 | 10:40 | 49.897 | 44735.466 | 49.9384
2022-06-23 | 10:40 | 49.897 | 44735.466 | 49.9384
2022-06-23 | 10:40 | 49.897 | 44735.466 | 49.9384
2022-06-23 | 10:40 | 49.897 | 44735.466 | 49.9384
2022-06-23 | 10:40 | 49.897 | 44735.466 | 49.9384
2022-06-23 | 10:40 | 49.895 | 44735.466 | 49.9383
2022-06-23 | 10:40 | 49.895 | 44735.466 | 49.9383
2022-06-23 | 10:40 | 49.895 | 44735.466 | 49.9383
2022-06-23 | 10:40 | 49.894 | 44735.466 | 49.9382
2022-06-23 | 10:40 | 49.896 | 44735.466 | 49.9381
2022-06-23 | 10:40 | 49.898 | 44735.466 | 49.9381
2022-06-23 | 10:40 | 49.898 | 44735.466 | 49.938
2022-06-23 | 10:40 | 49.896 | 44735.466 | 49.938
2022-06-23 | 10:40 | 49.898 | 44735.466 | 49.938
2022-06-23 | 10:40 | 49.899 | 44735.466 | 49.9379
2022-06-23 | 10:40 | 49.901 | 44735.466 | 49.9379
2022-06-23 | 10:40 | 49.903 | 44735.466 | 49.938
2022-06-23 | 10:40 | 49.903 | 44735.466 | 49.938
2022-06-23 | 10:40 | 49.907 | 44735.466 | 49.9379
2022-06-23 | 10:40 | 49.906 | 44735.466 | 49.9379
2022-06-23 | 10:40 | 49.907 | 44735.466 | 49.9379
2022-06-23 | 10:40 | 49.907 | 44735.466 | 49.9379
2022-06-23 | 10:40 | 49.906 | 44735.466 | 49.9379
2022-06-23 | 10:40 | 49.908 | 44735.466 | 49.9378
2022-06-23 | 10:40 | 49.907 | 44735.466 | 49.9378
2022-06-23 | 10:40 | 49.909 | 44735.466 | 49.9378
2022-06-23 | 10:40 | 49.91 | 44735.466 | 49.9377
2022-06-23 | 10:40 | 49.909 | 44735.466 | 49.9377
2022-06-23 | 10:40 | 49.91 | 44735.466 | 49.9377
2022-06-23 | 10:40 | 49.909 | 2022-06-23 11:11 | 49.9377
2022-06-23 | 10:40 | 49.909 | 44735.466 | 49.9377
2022-06-23 | 10:40 | 49.909 | 44735.466 | 49.9377
2022-06-23 | 10:40 | 49.907 | 44735.466 | 49.9377
2022-06-23 | 10:40 | 49.908 | 44735.466 | 49.9377
2022-06-23 | 10:40 | 49.908 | 44735.466 | 49.9376
2022-06-23 | 10:40 | 49.91 | 44735.466 | 49.9375
2022-06-23 | 10:40 | 49.909 | 44735.466 | 49.9377
2022-06-23 | 10:40 | 49.909 | 44735.466 | 49.9377
2022-06-23 | 10:40 | 49.906 | 44735.466 | 49.9376
2022-06-23 | 10:40 | 49.906 | 44735.466 | 49.9376
2022-06-23 | 10:40 | 49.904 | 44735.466 | 49.9375
2022-06-23 | 10:40 | 49.906 | 44735.466 | 49.9375
2022-06-23 | 10:40 | 49.903 | 44735.466 | 49.9374
2022-06-23 | 10:40 | 49.903 | 44735.466 | 49.9375
2022-06-23 | 10:40 | 49.901 | 44735.466 | 49.9374
2022-06-23 | 10:40 | 49.9 | 44735.466 | 49.9374
2022-06-23 | 10:40 | 49.902 | 44735.466 | 49.9373
2022-06-23 | 10:40 | 49.904 | 44735.466 | 49.9373
2022-06-23 | 10:40 | 49.904 | 44735.466 | 49.9372
2022-06-23 | 10:40 | 49.902 | 44735.466 | 49.9371
2022-06-23 | 10:40 | 49.901 | 44735.466 | 49.937
2022-06-23 | 10:40 | 49.901 | 44735.466 | 49.937
2022-06-23 | 10:40 | 49.901 | 44735.466 | 49.9369
2022-06-23 | 10:40 | 49.898 | 44735.466 | 49.9368
2022-06-23 | 10:40 | 49.897 | 44735.466 | 49.9368
2022-06-23 | 10:40 | 49.895 | 44735.466 | 49.9368
2022-06-23 | 10:40 | 49.894 | 44735.466 | 49.9368
2022-06-23 | 10:40 | 49.895 | 44735.466 | 49.9369
2022-06-23 | 10:40 | 49.893 | 44735.466 | 49.9369
2022-06-23 | 10:41 | 49.892 | 44735.466 | 49.9369
2022-06-23 | 10:41 | 49.892 | 44735.466 | 49.9369
2022-06-23 | 10:41 | 49.895 | 44735.466 | 49.9369
2022-06-23 | 10:41 | 49.893 | 44735.466 | 49.9369
2022-06-23 | 10:41 | 49.895 | 44735.466 | 49.9367
2022-06-23 | 10:41 | 49.897 | 44735.466 | 49.9367
2022-06-23 | 10:41 | 49.899 | 44735.4661 | 49.9366
2022-06-23 | 10:41 | 49.902 | 44735.4661 | 49.9366
2022-06-23 | 10:41 | 49.9 | 44735.4661 | 49.9366
2022-06-23 | 10:41 | 49.904 | 44735.4661 | 49.9365
2022-06-23 | 10:41 | 49.904 | 44735.4661 | 49.9366
2022-06-23 | 10:41 | 49.906 | 44735.4661 | 49.9366
2022-06-23 | 10:41 | 49.906 | 44735.4661 | 49.9366
2022-06-23 | 10:41 | 49.908 | 44735.4661 | 49.9366
2022-06-23 | 10:41 | 49.913 | 44735.4661 | 49.9366
2022-06-23 | 10:41 | 49.913 | 44735.4661 | 49.9366
2022-06-23 | 10:41 | 49.914 | 44735.4661 | 49.9366
2022-06-23 | 10:41 | 49.915 | 44735.4661 | 49.9366
2022-06-23 | 10:41 | 49.913 | 44735.4661 | 49.9366
2022-06-23 | 10:41 | 49.912 | 44735.4661 | 49.9366
2022-06-23 | 10:41 | 49.914 | 2022-06-23 11:11 | 49.9366
2022-06-23 | 10:41 | 49.914 | 44735.4661 | 49.9366
2022-06-23 | 10:41 | 49.916 | 44735.4661 | 49.9367
2022-06-23 | 10:41 | 49.916 | 44735.4661 | 49.9367
2022-06-23 | 10:41 | 49.917 | 44735.4661 | 49.9368
2022-06-23 | 10:41 | 49.916 | 44735.4661 | 49.9368
2022-06-23 | 10:41 | 49.917 | 44735.4661 | 49.9368
2022-06-23 | 10:41 | 49.916 | 44735.4661 | 49.9368
2022-06-23 | 10:41 | 49.916 | 44735.4661 | 49.9369
2022-06-23 | 10:41 | 49.916 | 44735.4661 | 49.9367
2022-06-23 | 10:41 | 49.915 | 44735.4661 | 49.9368
2022-06-23 | 10:41 | 49.913 | 44735.4661 | 49.9366
2022-06-23 | 10:41 | 49.911 | 44735.4661 | 49.9366
2022-06-23 | 10:41 | 49.908 | 44735.4661 | 49.9366
2022-06-23 | 10:41 | 49.908 | 44735.4661 | 49.9366
2022-06-23 | 10:41 | 49.907 | 44735.4661 | 49.9367
2022-06-23 | 10:41 | 49.907 | 44735.4661 | 49.9366
2022-06-23 | 10:41 | 49.909 | 44735.4661 | 49.9366
2022-06-23 | 10:41 | 49.912 | 44735.4661 | 49.9366
2022-06-23 | 10:41 | 49.913 | 44735.4661 | 49.9366
2022-06-23 | 10:41 | 49.916 | 44735.4661 | 49.9365
2022-06-23 | 10:41 | 49.919 | 44735.4661 | 49.9365
2022-06-23 | 10:41 | 49.919 | 44735.4661 | 49.9365
2022-06-23 | 10:41 | 49.92 | 44735.4661 | 49.9365
2022-06-23 | 10:41 | 49.919 | 44735.4661 | 49.9365
2022-06-23 | 10:41 | 49.92 | 44735.4661 | 49.9365
2022-06-23 | 10:41 | 49.92 | 44735.4661 | 49.9366
2022-06-23 | 10:41 | 49.92 | 44735.4661 | 49.9366
2022-06-23 | 10:41 | 49.919 | 44735.4661 | 49.9366
2022-06-23 | 10:41 | 49.918 | 44735.4661 | 49.9367
2022-06-23 | 10:41 | 49.917 | 44735.4661 | 49.9366
2022-06-23 | 10:41 | 49.915 | 44735.4661 | 49.9366
2022-06-23 | 10:41 | 49.911 | 44735.4661 | 49.9366
2022-06-23 | 10:41 | 49.91 | 44735.4661 | 49.9366
2022-06-23 | 10:41 | 49.909 | 44735.4661 | 49.9366
2022-06-23 | 10:41 | 49.907 | 44735.4661 | 49.9366
2022-06-23 | 10:41 | 49.911 | 44735.4661 | 49.9367
2022-06-23 | 10:41 | 49.912 | 44735.4661 | 49.9367
2022-06-23 | 10:41 | 49.916 | 44735.4661 | 49.9368
2022-06-23 | 10:41 | 49.921 | 44735.4661 | 49.9369
2022-06-23 | 10:41 | 49.922 | 44735.4661 | 49.9369
2022-06-23 | 10:42 | 49.925 | 44735.4661 | 49.9369
2022-06-23 | 10:42 | 49.926 | 44735.4661 | 49.9369
2022-06-23 | 10:42 | 49.929 | 44735.4661 | 49.937
2022-06-23 | 10:42 | 49.929 | 44735.4661 | 49.937
2022-06-23 | 10:42 | 49.931 | 44735.4661 | 49.937
2022-06-23 | 10:42 | 49.928 | 44735.4661 | 49.9369
2022-06-23 | 10:42 | 49.926 | 44735.4661 | 49.9368
2022-06-23 | 10:42 | 49.927 | 44735.4661 | 49.9368
2022-06-23 | 10:42 | 49.926 | 44735.4661 | 49.9369
2022-06-23 | 10:42 | 49.926 | 2022-06-23 11:11 | 49.9369
2022-06-23 | 10:42 | 49.929 | 44735.4661 | 49.937
2022-06-23 | 10:42 | 49.93 | 44735.4661 | 49.9371
2022-06-23 | 10:42 | 49.933 | 44735.4661 | 49.9371
2022-06-23 | 10:42 | 49.934 | 44735.4661 | 49.9372
2022-06-23 | 10:42 | 49.933 | 44735.4661 | 49.9373
2022-06-23 | 10:42 | 49.933 | 44735.4661 | 49.9374
2022-06-23 | 10:42 | 49.932 | 44735.4661 | 49.9374
2022-06-23 | 10:42 | 49.93 | 44735.4661 | 49.9374
2022-06-23 | 10:42 | 49.926 | 44735.4661 | 49.9375
2022-06-23 | 10:42 | 49.924 | 44735.4661 | 49.9374
2022-06-23 | 10:42 | 49.921 | 44735.4661 | 49.9375
2022-06-23 | 10:42 | 49.922 | 44735.4661 | 49.9375
2022-06-23 | 10:42 | 49.922 | 44735.4661 | 49.9375
2022-06-23 | 10:42 | 49.921 | 44735.4661 | 49.9374
2022-06-23 | 10:42 | 49.922 | 44735.4661 | 49.9374
2022-06-23 | 10:42 | 49.922 | 44735.4661 | 49.9374
2022-06-23 | 10:42 | 49.924 | 44735.4661 | 49.9373
2022-06-23 | 10:42 | 49.924 | 44735.4661 | 49.9373
2022-06-23 | 10:42 | 49.926 | 44735.4661 | 49.9374
2022-06-23 | 10:42 | 49.925 | 44735.4661 | 49.9374
2022-06-23 | 10:42 | 49.925 | 44735.4661 | 49.9374
2022-06-23 | 10:42 | 49.929 | 44735.4661 | 49.9374
2022-06-23 | 10:42 | 49.931 | 44735.4661 | 49.9375
2022-06-23 | 10:42 | 49.931 | 44735.4661 | 49.9376
2022-06-23 | 10:42 | 49.934 | 44735.4661 | 49.9376
2022-06-23 | 10:42 | 49.935 | 44735.4661 | 49.9377
2022-06-23 | 10:42 | 49.932 | 44735.4661 | 49.9378
2022-06-23 | 10:42 | 49.93 | 44735.4661 | 49.9379
2022-06-23 | 10:42 | 49.93 | 44735.4661 | 49.938
2022-06-23 | 10:42 | 49.932 | 44735.4661 | 49.9379
2022-06-23 | 10:42 | 49.936 | 44735.4661 | 49.9379
2022-06-23 | 10:42 | 49.938 | 44735.4661 | 49.9379
2022-06-23 | 10:42 | 49.94 | 44735.4661 | 49.9379
2022-06-23 | 10:42 | 49.946 | 44735.4661 | 49.9379
2022-06-23 | 10:42 | 49.95 | 44735.4661 | 49.938
2022-06-23 | 10:42 | 49.954 | 44735.4661 | 49.938
2022-06-23 | 10:42 | 49.954 | 44735.4661 | 49.938
2022-06-23 | 10:42 | 49.957 | 44735.4661 | 49.9381
2022-06-23 | 10:42 | 49.958 | 44735.4661 | 49.9382
2022-06-23 | 10:42 | 49.961 | 44735.4661 | 49.9382
2022-06-23 | 10:42 | 49.961 | 44735.4661 | 49.9383
2022-06-23 | 10:42 | 49.963 | 44735.4661 | 49.9384
2022-06-23 | 10:42 | 49.964 | 44735.4661 | 49.9384
2022-06-23 | 10:42 | 49.965 | 44735.4661 | 49.9385
2022-06-23 | 10:42 | 49.969 | 44735.4661 | 49.9386
2022-06-23 | 10:42 | 49.97 | 44735.4661 | 49.9386
2022-06-23 | 10:42 | 49.97 | 44735.4661 | 49.9387
2022-06-23 | 10:42 | 49.968 | 44735.4661 | 49.9387
2022-06-23 | 10:42 | 49.965 | 44735.4661 | 49.9388
2022-06-23 | 10:43 | 49.965 | 2022-06-23 11:11 | 49.939
2022-06-23 | 10:43 | 49.967 | 44735.4661 | 49.939
2022-06-23 | 10:43 | 49.967 | 44735.4661 | 49.939
2022-06-23 | 10:43 | 49.964 | 44735.4661 | 49.9391
2022-06-23 | 10:43 | 49.957 | 44735.4661 | 49.9391
2022-06-23 | 10:43 | 49.953 | 44735.4661 | 49.9392
2022-06-23 | 10:43 | 49.948 | 44735.4661 | 49.9393
2022-06-23 | 10:43 | 49.945 | 44735.4661 | 49.9393
2022-06-23 | 10:43 | 49.94 | 44735.4661 | 49.9393
2022-06-23 | 10:43 | 49.936 | 44735.4661 | 49.9394
2022-06-23 | 10:43 | 49.931 | 44735.4661 | 49.9395
2022-06-23 | 10:43 | 49.924 | 44735.4661 | 49.9395
2022-06-23 | 10:43 | 49.923 | 44735.4661 | 49.9396
2022-06-23 | 10:43 | 49.918 | 44735.4661 | 49.9396
2022-06-23 | 10:43 | 49.915 | 44735.4661 | 49.9397
2022-06-23 | 10:43 | 49.913 | 44735.4661 | 49.9397
2022-06-23 | 10:43 | 49.909 | 44735.4661 | 49.9397
2022-06-23 | 10:43 | 49.91 | 44735.4661 | 49.9398
2022-06-23 | 10:43 | 49.911 | 44735.4661 | 49.9398
2022-06-23 | 10:43 | 49.91 | 44735.4661 | 49.9399
2022-06-23 | 10:43 | 49.91 | 44735.4661 | 49.9399
2022-06-23 | 10:43 | 49.908 | 44735.4661 | 49.9399
2022-06-23 | 10:43 | 49.908 | 44735.4661 | 49.94
2022-06-23 | 10:43 | 49.908 | 44735.4661 | 49.94
2022-06-23 | 10:43 | 49.912 | 44735.4661 | 49.9401
2022-06-23 | 10:43 | 49.915 | 44735.4661 | 49.9401
2022-06-23 | 10:43 | 49.913 | 44735.4661 | 49.94
2022-06-23 | 10:43 | 49.918 | 44735.4661 | 49.9401
2022-06-23 | 10:43 | 49.918 | 44735.4661 | 49.9401
2022-06-23 | 10:43 | 49.921 | 44735.4661 | 49.9401
2022-06-23 | 10:43 | 49.919 | 44735.4661 | 49.9402
2022-06-23 | 10:43 | 49.917 | 44735.4661 | 49.9403
2022-06-23 | 10:43 | 49.911 | 44735.4661 | 49.9404
2022-06-23 | 10:43 | 49.908 | 44735.4661 | 49.9405
2022-06-23 | 10:43 | 49.906 | 44735.4661 | 49.9406
2022-06-23 | 10:43 | 49.901 | 44735.4661 | 49.9407
2022-06-23 | 10:43 | 49.897 | 44735.4661 | 49.9408
2022-06-23 | 10:43 | 49.895 | 44735.4661 | 49.9409
2022-06-23 | 10:43 | 49.894 | 44735.4661 | 49.941
2022-06-23 | 10:43 | 49.892 | 44735.4661 | 49.9411
2022-06-23 | 10:43 | 49.892 | 44735.4661 | 49.9411
2022-06-23 | 10:43 | 49.889 | 44735.4661 | 49.9411
2022-06-23 | 10:43 | 49.89 | 44735.4661 | 49.9412
2022-06-23 | 10:43 | 49.89 | 44735.4661 | 49.9412
2022-06-23 | 10:43 | 49.892 | 44735.4661 | 49.9412
2022-06-23 | 10:43 | 49.891 | 44735.4661 | 49.9413
2022-06-23 | 10:43 | 49.893 | 44735.4661 | 49.9414
2022-06-23 | 10:43 | 49.894 | 44735.4661 | 49.9414
2022-06-23 | 10:43 | 49.895 | 44735.4661 | 49.9415
2022-06-23 | 10:43 | 49.897 | 44735.4661 | 49.9416
2022-06-23 | 10:43 | 49.9 | 2022-06-23 11:11 | 49.9416
2022-06-23 | 10:43 | 49.902 | 44735.4661 | 49.9417
2022-06-23 | 10:43 | 49.9 | 44735.4661 | 49.9417
2022-06-23 | 10:43 | 49.901 | 44735.4661 | 49.9419
2022-06-23 | 10:43 | 49.903 | 44735.4661 | 49.9419
2022-06-23 | 10:43 | 49.902 | 44735.4661 | 49.9418
2022-06-23 | 10:43 | 49.903 | 44735.4661 | 49.9418
2022-06-23 | 10:43 | 49.906 | 44735.4661 | 49.9419
2022-06-23 | 10:43 | 49.908 | 44735.4661 | 49.9419
2022-06-23 | 10:43 | 49.909 | 44735.4661 | 49.9419
2022-06-23 | 10:44 | 49.91 | 44735.4661 | 49.9419
2022-06-23 | 10:44 | 49.91 | 44735.4661 | 49.942
2022-06-23 | 10:44 | 49.91 | 44735.4661 | 49.9421
2022-06-23 | 10:44 | 49.91 | 44735.4661 | 49.9422
2022-06-23 | 10:44 | 49.909 | 44735.4661 | 49.9425
2022-06-23 | 10:44 | 49.907 | 44735.4661 | 49.9426
2022-06-23 | 10:44 | 49.905 | 44735.4661 | 49.9426
2022-06-23 | 10:44 | 49.901 | 44735.4661 | 49.9426
2022-06-23 | 10:44 | 49.899 | 44735.4661 | 49.9428
2022-06-23 | 10:44 | 49.898 | 44735.4661 | 49.9428
2022-06-23 | 10:44 | 49.897 | 44735.4661 | 49.9429
2022-06-23 | 10:44 | 49.897 | 44735.4661 | 49.9429
2022-06-23 | 10:44 | 49.897 | 44735.4661 | 49.9429
2022-06-23 | 10:44 | 49.897 | 44735.4661 | 49.9429
2022-06-23 | 10:44 | 49.898 | 44735.4661 | 49.943
2022-06-23 | 10:44 | 49.899 | 44735.4661 | 49.943
2022-06-23 | 10:44 | 49.9 | 44735.4661 | 49.943
2022-06-23 | 10:44 | 49.901 | 44735.4661 | 49.943
2022-06-23 | 10:44 | 49.904 | 44735.4661 | 49.943
2022-06-23 | 10:44 | 49.906 | 44735.4661 | 49.9429
2022-06-23 | 10:44 | 49.905 | 44735.4661 | 49.943
2022-06-23 | 10:44 | 49.906 | 44735.4661 | 49.943
2022-06-23 | 10:44 | 49.907 | 44735.4661 | 49.943
2022-06-23 | 10:44 | 49.908 | 44735.4661 | 49.9429
2022-06-23 | 10:44 | 49.91 | 44735.4661 | 49.9429
2022-06-23 | 10:44 | 49.913 | 44735.4661 | 49.943
2022-06-23 | 10:44 | 49.915 | 44735.4661 | 49.943
2022-06-23 | 10:44 | 49.916 | 44735.4661 | 49.943
2022-06-23 | 10:44 | 49.918 | 44735.4661 | 49.9431
2022-06-23 | 10:44 | 49.92 | 44735.4661 | 49.943
2022-06-23 | 10:44 | 49.922 | 44735.4661 | 49.943
2022-06-23 | 10:44 | 49.919 | 44735.4661 | 49.943
2022-06-23 | 10:44 | 49.917 | 44735.4661 | 49.9429
2022-06-23 | 10:44 | 49.917 | 44735.4661 | 49.9429
2022-06-23 | 10:44 | 49.92 | 44735.4661 | 49.9429
2022-06-23 | 10:44 | 49.924 | 44735.4661 | 49.9429
2022-06-23 | 10:44 | 49.924 | 44735.4661 | 49.9429
2022-06-23 | 10:44 | 49.922 | 44735.4661 | 49.9429
2022-06-23 | 10:44 | 49.921 | 44735.4661 | 49.9431
2022-06-23 | 10:44 | 49.918 | 44735.4661 | 49.9431
2022-06-23 | 10:44 | 49.915 | 2022-06-23 11:11 | 49.9431
2022-06-23 | 10:44 | 49.914 | 44735.4661 | 49.9431
2022-06-23 | 10:44 | 49.911 | 44735.4661 | 49.9432
2022-06-23 | 10:44 | 49.91 | 44735.4661 | 49.9431
2022-06-23 | 10:44 | 49.911 | 44735.4661 | 49.9431
2022-06-23 | 10:44 | 49.91 | 44735.4661 | 49.9432
2022-06-23 | 10:44 | 49.907 | 44735.4661 | 49.9433
2022-06-23 | 10:44 | 49.904 | 44735.4661 | 49.9433
2022-06-23 | 10:44 | 49.903 | 44735.4661 | 49.9434
2022-06-23 | 10:44 | 49.901 | 44735.4661 | 49.9434
2022-06-23 | 10:44 | 49.9 | 44735.4661 | 49.9434
2022-06-23 | 10:44 | 49.901 | 44735.4661 | 49.9433
2022-06-23 | 10:44 | 49.901 | 44735.4661 | 49.9434
2022-06-23 | 10:44 | 49.901 | 44735.4661 | 49.9433
2022-06-23 | 10:44 | 49.902 | 44735.4661 | 49.9433
2022-06-23 | 10:44 | 49.9 | 44735.4661 | 49.9433
2022-06-23 | 10:44 | 49.903 | 44735.4661 | 49.9433
2022-06-23 | 10:44 | 49.903 | 44735.4661 | 49.9433
2022-06-23 | 10:44 | 49.906 | 44735.4661 | 49.9433
2022-06-23 | 10:44 | 49.907 | 44735.4661 | 49.9434
2022-06-23 | 10:44 | 49.908 | 44735.4661 | 49.9435
2022-06-23 | 10:45 | 49.909 | 44735.4661 | 49.9435
2022-06-23 | 10:45 | 49.909 | 44735.4661 | 49.9435
2022-06-23 | 10:45 | 49.91 | 44735.4661 | 49.9435
2022-06-23 | 10:45 | 49.912 | 44735.4661 | 49.9435
2022-06-23 | 10:45 | 49.911 | 44735.4661 | 49.9435
2022-06-23 | 10:45 | 49.913 | 44735.4661 | 49.9435
2022-06-23 | 10:45 | 49.913 | 44735.4661 | 49.9435
2022-06-23 | 10:45 | 49.912 | 44735.4661 | 49.9435
2022-06-23 | 10:45 | 49.911 | 44735.4661 | 49.9435
2022-06-23 | 10:45 | 49.913 | 44735.4661 | 49.9436
2022-06-23 | 10:45 | 49.912 | 44735.4661 | 49.9436
2022-06-23 | 10:45 | 49.911 | 44735.4661 | 49.9436
2022-06-23 | 10:45 | 49.911 | 44735.4661 | 49.9437
2022-06-23 | 10:45 | 49.909 | 44735.4661 | 49.9437
2022-06-23 | 10:45 | 49.91 | 44735.4661 | 49.9437
2022-06-23 | 10:45 | 49.911 | 44735.4661 | 49.9438
2022-06-23 | 10:45 | 49.91 | 44735.4661 | 49.9438
2022-06-23 | 10:45 | 49.91 | 44735.4661 | 49.9438
2022-06-23 | 10:45 | 49.91 | 44735.4661 | 49.9438
2022-06-23 | 10:45 | 49.909 | 44735.4661 | 49.9438
2022-06-23 | 10:45 | 49.905 | 44735.4661 | 49.9438
2022-06-23 | 10:45 | 49.901 | 44735.4661 | 49.9438
2022-06-23 | 10:45 | 49.899 | 44735.4661 | 49.9439
2022-06-23 | 10:45 | 49.9 | 44735.4661 | 49.9438
2022-06-23 | 10:45 | 49.896 | 44735.4661 | 49.9438
2022-06-23 | 10:45 | 49.893 | 44735.4661 | 49.9438
2022-06-23 | 10:45 | 49.893 | 44735.4661 | 49.9438
2022-06-23 | 10:45 | 49.895 | 44735.4661 | 49.9438
2022-06-23 | 10:45 | 49.894 | 44735.4661 | 49.9438
2022-06-23 | 10:45 | 49.896 | 2022-06-23 11:11 | 49.9438
2022-06-23 | 10:45 | 49.895 | 44735.4661 | 49.9438
2022-06-23 | 10:45 | 49.898 | 44735.4661 | 49.9438
2022-06-23 | 10:45 | 49.899 | 44735.4661 | 49.9438
2022-06-23 | 10:45 | 49.901 | 44735.4661 | 49.9439
2022-06-23 | 10:45 | 49.902 | 44735.4661 | 49.9439
2022-06-23 | 10:45 | 49.906 | 44735.4661 | 49.944
2022-06-23 | 10:45 | 49.905 | 44735.4661 | 49.9441
2022-06-23 | 10:45 | 49.908 | 44735.4661 | 49.9441
2022-06-23 | 10:45 | 49.908 | 44735.4661 | 49.9441
2022-06-23 | 10:45 | 49.911 | 44735.4661 | 49.9441
2022-06-23 | 10:45 | 49.911 | 44735.4661 | 49.9441
2022-06-23 | 10:45 | 49.912 | 44735.4661 | 49.944
2022-06-23 | 10:45 | 49.914 | 44735.4661 | 49.944
2022-06-23 | 10:45 | 49.912 | 44735.4661 | 49.9439
2022-06-23 | 10:45 | 49.912 | 44735.4661 | 49.9439
2022-06-23 | 10:45 | 49.913 | 44735.4661 | 49.9438
2022-06-23 | 10:45 | 49.912 | 44735.4661 | 49.9438
2022-06-23 | 10:45 | 49.912 | 44735.4661 | 49.9438
2022-06-23 | 10:45 | 49.91 | 44735.4661 | 49.9438
2022-06-23 | 10:45 | 49.906 | 44735.4661 | 49.9437
2022-06-23 | 10:45 | 49.906 | 44735.4661 | 49.9437
2022-06-23 | 10:45 | 49.907 | 44735.4661 | 49.9437
2022-06-23 | 10:45 | 49.905 | 44735.4661 | 49.9439
2022-06-23 | 10:45 | 49.904 | 44735.4661 | 49.9439
2022-06-23 | 10:45 | 49.904 | 44735.4661 | 49.944
2022-06-23 | 10:45 | 49.901 | 44735.4661 | 49.944
2022-06-23 | 10:45 | 49.9 | 44735.4661 | 49.9441
2022-06-23 | 10:45 | 49.9 | 44735.4661 | 49.9441
2022-06-23 | 10:45 | 49.898 | 44735.4661 | 49.9441
2022-06-23 | 10:46 | 49.895 | 44735.4661 | 49.9441
2022-06-23 | 10:46 | 49.894 | 44735.4661 | 49.9441
2022-06-23 | 10:46 | 49.892 | 44735.4661 | 49.944
2022-06-23 | 10:46 | 49.89 | 44735.4661 | 49.9439
2022-06-23 | 10:46 | 49.889 | 44735.4661 | 49.9439
2022-06-23 | 10:46 | 49.886 | 44735.4661 | 49.944
2022-06-23 | 10:46 | 49.884 | 44735.4661 | 49.944
2022-06-23 | 10:46 | 49.884 | 44735.4661 | 49.9442
2022-06-23 | 10:46 | 49.887 | 44735.4661 | 49.9442
2022-06-23 | 10:46 | 49.889 | 44735.4661 | 49.9442
2022-06-23 | 10:46 | 49.892 | 44735.4661 | 49.9442
2022-06-23 | 10:46 | 49.894 | 44735.4661 | 49.9442
2022-06-23 | 10:46 | 49.895 | 44735.4661 | 49.9442
2022-06-23 | 10:46 | 49.896 | 44735.4661 | 49.9442
2022-06-23 | 10:46 | 49.897 | 44735.4661 | 49.9443
2022-06-23 | 10:46 | 49.896 | 44735.4661 | 49.9443
2022-06-23 | 10:46 | 49.895 | 44735.4661 | 49.9442
2022-06-23 | 10:46 | 49.894 | 44735.4661 | 49.9442
2022-06-23 | 10:46 | 49.896 | 44735.4661 | 49.9441
2022-06-23 | 10:46 | 49.895 | 44735.4661 | 49.9441
2022-06-23 | 10:46 | 49.897 | 2022-06-23 11:11 | 49.9442
2022-06-23 | 10:46 | 49.896 | 44735.4661 | 49.9441
2022-06-23 | 10:46 | 49.896 | 44735.4661 | 49.9441
2022-06-23 | 10:46 | 49.899 | 44735.4661 | 49.9441
2022-06-23 | 10:46 | 49.898 | 44735.4661 | 49.9441
2022-06-23 | 10:46 | 49.901 | 44735.4661 | 49.9441
2022-06-23 | 10:46 | 49.898 | 44735.4661 | 49.9442
2022-06-23 | 10:46 | 49.898 | 44735.4661 | 49.9443
2022-06-23 | 10:46 | 49.899 | 44735.4661 | 49.9443
2022-06-23 | 10:46 | 49.9 | 44735.4661 | 49.9443
2022-06-23 | 10:46 | 49.902 | 44735.4661 | 49.9443
2022-06-23 | 10:46 | 49.9 | 44735.4661 | 49.9443
2022-06-23 | 10:46 | 49.898 | 44735.4661 | 49.9442
2022-06-23 | 10:46 | 49.9 | 44735.4661 | 49.9441
2022-06-23 | 10:46 | 49.901 | 44735.4661 | 49.9441
2022-06-23 | 10:46 | 49.902 | 44735.4661 | 49.9441
2022-06-23 | 10:46 | 49.904 | 44735.4661 | 49.9441
2022-06-23 | 10:46 | 49.904 | 44735.4661 | 49.9441
2022-06-23 | 10:46 | 49.905 | 44735.4661 | 49.9441
2022-06-23 | 10:46 | 49.906 | 44735.4661 | 49.9441
2022-06-23 | 10:46 | 49.906 | 44735.4661 | 49.9441
2022-06-23 | 10:46 | 49.908 | 44735.4661 | 49.9441
2022-06-23 | 10:46 | 49.907 | 44735.4661 | 49.9441
2022-06-23 | 10:46 | 49.907 | 44735.4661 | 49.9441
2022-06-23 | 10:46 | 49.907 | 44735.4661 | 49.9442
2022-06-23 | 10:46 | 49.906 | 44735.4661 | 49.9442
2022-06-23 | 10:46 | 49.906 | 44735.4661 | 49.9442
2022-06-23 | 10:46 | 49.904 | 44735.4661 | 49.9442
2022-06-23 | 10:46 | 49.903 | 44735.4661 | 49.9442
2022-06-23 | 10:46 | 49.9 | 44735.4661 | 49.9442
2022-06-23 | 10:46 | 49.9 | 44735.4661 | 49.9442
2022-06-23 | 10:46 | 49.9 | 44735.4661 | 49.9441
2022-06-23 | 10:46 | 49.898 | 44735.4661 | 49.9441
2022-06-23 | 10:46 | 49.897 | 44735.4661 | 49.9441
2022-06-23 | 10:46 | 49.895 | 44735.4661 | 49.9441
2022-06-23 | 10:46 | 49.894 | 44735.4661 | 49.9441
2022-06-23 | 10:46 | 49.891 | 44735.4661 | 49.944
2022-06-23 | 10:46 | 49.887 | 44735.4661 | 49.944
2022-06-23 | 10:46 | 49.884 | 44735.4661 | 49.944
2022-06-23 | 10:46 | 49.881 | 44735.4661 | 49.9441
2022-06-23 | 10:46 | 49.879 | 44735.4661 | 49.944
2022-06-23 | 10:47 | 49.879 | 44735.4661 | 49.944
2022-06-23 | 10:47 | 49.882 | 44735.4661 | 49.9441
2022-06-23 | 10:47 | 49.884 | 44735.4661 | 49.9441
2022-06-23 | 10:47 | 49.887 | 44735.4661 | 49.9441
2022-06-23 | 10:47 | 49.889 | 44735.4661 | 49.9441
2022-06-23 | 10:47 | 49.893 | 44735.4661 | 49.9441
2022-06-23 | 10:47 | 49.897 | 44735.4661 | 49.9442
2022-06-23 | 10:47 | 49.9 | 44735.4661 | 49.9442
2022-06-23 | 10:47 | 49.904 | 44735.4661 | 49.9442
2022-06-23 | 10:47 | 49.907 | 2022-06-23 11:11 | 49.9442
2022-06-23 | 10:47 | 49.908 | 44735.4661 | 49.9443
2022-06-23 | 10:47 | 49.91 | 44735.4661 | 49.9442
2022-06-23 | 10:47 | 49.909 | 44735.4661 | 49.9441
2022-06-23 | 10:47 | 49.907 | 44735.4661 | 49.9441
2022-06-23 | 10:47 | 49.906 | 44735.4661 | 49.9441
2022-06-23 | 10:47 | 49.903 | 44735.4661 | 49.944
2022-06-23 | 10:47 | 49.901 | 44735.4661 | 49.944
2022-06-23 | 10:47 | 49.898 | 44735.4661 | 49.944
2022-06-23 | 10:47 | 49.897 | 44735.4661 | 49.944
2022-06-23 | 10:47 | 49.895 | 44735.4661 | 49.9439
2022-06-23 | 10:47 | 49.893 | 44735.4661 | 49.9439
2022-06-23 | 10:47 | 49.891 | 44735.4661 | 49.9439
2022-06-23 | 10:47 | 49.891 | 44735.4661 | 49.9438
2022-06-23 | 10:47 | 49.891 | 44735.4661 | 49.9438
2022-06-23 | 10:47 | 49.894 | 44735.4661 | 49.9438
2022-06-23 | 10:47 | 49.897 | 44735.4661 | 49.9438
2022-06-23 | 10:47 | 49.901 | 44735.4661 | 49.9437
2022-06-23 | 10:47 | 49.901 | 44735.4661 | 49.9438
2022-06-23 | 10:47 | 49.903 | 44735.4661 | 49.9438
2022-06-23 | 10:47 | 49.904 | 44735.4661 | 49.9437
2022-06-23 | 10:47 | 49.905 | 44735.4661 | 49.9437
2022-06-23 | 10:47 | 49.906 | 44735.4661 | 49.9437
2022-06-23 | 10:47 | 49.908 | 44735.4661 | 49.9437
2022-06-23 | 10:47 | 49.909 | 44735.4661 | 49.9438
2022-06-23 | 10:47 | 49.909 | 44735.4661 | 49.9438
2022-06-23 | 10:47 | 49.909 | 44735.4661 | 49.9438
2022-06-23 | 10:47 | 49.911 | 44735.4661 | 49.9438
2022-06-23 | 10:47 | 49.914 | 44735.4661 | 49.9437
2022-06-23 | 10:47 | 49.915 | 44735.4661 | 49.9437
2022-06-23 | 10:47 | 49.918 | 44735.4661 | 49.9436
2022-06-23 | 10:47 | 49.919 | 44735.4661 | 49.9435
2022-06-23 | 10:47 | 49.92 | 44735.4661 | 49.9435
2022-06-23 | 10:47 | 49.92 | 44735.4661 | 49.9434
2022-06-23 | 10:47 | 49.921 | 44735.4661 | 49.9433
2022-06-23 | 10:47 | 49.92 | 44735.4661 | 49.9433
2022-06-23 | 10:47 | 49.922 | 44735.4661 | 49.9433
2022-06-23 | 10:47 | 49.923 | 44735.4661 | 49.9432
2022-06-23 | 10:47 | 49.925 | 44735.4661 | 49.9433
2022-06-23 | 10:47 | 49.924 | 44735.4661 | 49.9433
2022-06-23 | 10:47 | 49.923 | 44735.4661 | 49.9433
2022-06-23 | 10:47 | 49.923 | 44735.4661 | 49.9434
2022-06-23 | 10:47 | 49.923 | 44735.4661 | 49.9434
2022-06-23 | 10:47 | 49.921 | 44735.4661 | 49.9434
2022-06-23 | 10:47 | 49.919 | 44735.4661 | 49.9435
2022-06-23 | 10:47 | 49.917 | 44735.4661 | 49.9435
2022-06-23 | 10:47 | 49.919 | 44735.4661 | 49.9435
2022-06-23 | 10:47 | 49.919 | 44735.4661 | 49.9435
2022-06-23 | 10:47 | 49.92 | 44735.4661 | 49.9434
2022-06-23 | 10:47 | 49.918 | 44735.4661 | 49.9434
2022-06-23 | 10:48 | 49.919 | 2022-06-23 11:11 | 49.9433
2022-06-23 | 10:48 | 49.918 | 44735.4661 | 49.9433
2022-06-23 | 10:48 | 49.917 | 44735.4661 | 49.9433
2022-06-23 | 10:48 | 49.914 | 44735.4661 | 49.9434
2022-06-23 | 10:48 | 49.913 | 44735.4661 | 49.9434
2022-06-23 | 10:48 | 49.912 | 44735.4661 | 49.9434
2022-06-23 | 10:48 | 49.913 | 44735.4661 | 49.9435
2022-06-23 | 10:48 | 49.913 | 44735.4661 | 49.9435
2022-06-23 | 10:48 | 49.915 | 44735.4661 | 49.9435
2022-06-23 | 10:48 | 49.915 | 44735.4661 | 49.9435
2022-06-23 | 10:48 | 49.916 | 44735.4661 | 49.9435
2022-06-23 | 10:48 | 49.915 | 44735.4661 | 49.9434
2022-06-23 | 10:48 | 49.917 | 44735.4661 | 49.9433
2022-06-23 | 10:48 | 49.918 | 44735.4661 | 49.9434
2022-06-23 | 10:48 | 49.919 | 44735.4661 | 49.9433
2022-06-23 | 10:48 | 49.917 | 44735.4661 | 49.9433
2022-06-23 | 10:48 | 49.918 | 44735.4661 | 49.9434
2022-06-23 | 10:48 | 49.916 | 44735.4661 | 49.9434
2022-06-23 | 10:48 | 49.915 | 44735.4662 | 49.9435
2022-06-23 | 10:48 | 49.914 | 44735.4662 | 49.9435
2022-06-23 | 10:48 | 49.912 | 44735.4662 | 49.9436
2022-06-23 | 10:48 | 49.912 | 44735.4662 | 49.9436
2022-06-23 | 10:48 | 49.912 | 44735.4662 | 49.9437
2022-06-23 | 10:48 | 49.912 | 44735.4662 | 49.9436
2022-06-23 | 10:48 | 49.911 | 44735.4662 | 49.9437
2022-06-23 | 10:48 | 49.913 | 44735.4662 | 49.9437
2022-06-23 | 10:48 | 49.913 | 44735.4662 | 49.9437
2022-06-23 | 10:48 | 49.911 | 44735.4662 | 49.9437
2022-06-23 | 10:48 | 49.911 | 44735.4662 | 49.9437
2022-06-23 | 10:48 | 49.91 | 44735.4662 | 49.9437
2022-06-23 | 10:48 | 49.911 | 44735.4662 | 49.9436
2022-06-23 | 10:48 | 49.913 | 44735.4662 | 49.9436
2022-06-23 | 10:48 | 49.914 | 44735.4662 | 49.9436
2022-06-23 | 10:48 | 49.916 | 44735.4662 | 49.9436
2022-06-23 | 10:48 | 49.915 | 44735.4662 | 49.9437
2022-06-23 | 10:48 | 49.919 | 44735.4662 | 49.9437
2022-06-23 | 10:48 | 49.921 | 44735.4662 | 49.9436
2022-06-23 | 10:48 | 49.922 | 44735.4662 | 49.9436
2022-06-23 | 10:48 | 49.923 | 44735.4662 | 49.9436
2022-06-23 | 10:48 | 49.924 | 44735.4662 | 49.9436
2022-06-23 | 10:48 | 49.926 | 44735.4662 | 49.9436
2022-06-23 | 10:48 | 49.927 | 44735.4662 | 49.9436
2022-06-23 | 10:48 | 49.929 | 44735.4662 | 49.9436
2022-06-23 | 10:48 | 49.932 | 44735.4662 | 49.9435
2022-06-23 | 10:48 | 49.935 | 44735.4662 | 49.9435
2022-06-23 | 10:48 | 49.936 | 44735.4662 | 49.9434
2022-06-23 | 10:48 | 49.938 | 44735.4662 | 49.9434
2022-06-23 | 10:48 | 49.94 | 44735.4662 | 49.9434
2022-06-23 | 10:48 | 49.942 | 44735.4662 | 49.9434
2022-06-23 | 10:48 | 49.945 | 44735.4662 | 49.9434
2022-06-23 | 10:48 | 49.946 | 2022-06-23 11:11 | 49.9434
2022-06-23 | 10:48 | 49.947 | 44735.4662 | 49.9434
2022-06-23 | 10:48 | 49.949 | 44735.4662 | 49.9433
2022-06-23 | 10:48 | 49.949 | 44735.4662 | 49.9433
2022-06-23 | 10:48 | 49.95 | 44735.4662 | 49.9433
2022-06-23 | 10:48 | 49.951 | 44735.4662 | 49.9432
2022-06-23 | 10:48 | 49.954 | 44735.4662 | 49.9433
2022-06-23 | 10:48 | 49.956 | 44735.4662 | 49.9433
2022-06-23 | 10:48 | 49.957 | 44735.4662 | 49.9433
2022-06-23 | 10:48 | 49.956 | 44735.4662 | 49.9433
2022-06-23 | 10:48 | 49.957 | 44735.4662 | 49.9433
2022-06-23 | 10:49 | 49.956 | 44735.4662 | 49.9433
2022-06-23 | 10:49 | 49.954 | 44735.4662 | 49.9433
2022-06-23 | 10:49 | 49.953 | 44735.4662 | 49.9433
2022-06-23 | 10:49 | 49.954 | 44735.4662 | 49.9433
2022-06-23 | 10:49 | 49.952 | 44735.4662 | 49.9433
2022-06-23 | 10:49 | 49.95 | 44735.4662 | 49.9433
2022-06-23 | 10:49 | 49.948 | 44735.4662 | 49.9434
2022-06-23 | 10:49 | 49.946 | 44735.4662 | 49.9434
2022-06-23 | 10:49 | 49.944 | 44735.4662 | 49.9433
2022-06-23 | 10:49 | 49.945 | 44735.4662 | 49.9433
2022-06-23 | 10:49 | 49.945 | 44735.4662 | 49.9433
2022-06-23 | 10:49 | 49.945 | 44735.4662 | 49.9433
2022-06-23 | 10:49 | 49.946 | 44735.4662 | 49.9432
2022-06-23 | 10:49 | 49.947 | 44735.4662 | 49.9432
2022-06-23 | 10:49 | 49.945 | 44735.4662 | 49.9432
2022-06-23 | 10:49 | 49.943 | 44735.4662 | 49.9431
2022-06-23 | 10:49 | 49.942 | 44735.4662 | 49.9431
2022-06-23 | 10:49 | 49.94 | 44735.4662 | 49.9431
2022-06-23 | 10:49 | 49.938 | 44735.4662 | 49.9431
2022-06-23 | 10:49 | 49.936 | 44735.4662 | 49.9431
2022-06-23 | 10:49 | 49.936 | 44735.4662 | 49.9432
2022-06-23 | 10:49 | 49.933 | 44735.4662 | 49.9432
2022-06-23 | 10:49 | 49.929 | 44735.4662 | 49.9432
2022-06-23 | 10:49 | 49.926 | 44735.4662 | 49.9433
2022-06-23 | 10:49 | 49.924 | 44735.4662 | 49.9433
2022-06-23 | 10:49 | 49.922 | 44735.4662 | 49.9433
2022-06-23 | 10:49 | 49.919 | 44735.4662 | 49.9433
2022-06-23 | 10:49 | 49.919 | 44735.4662 | 49.9434
2022-06-23 | 10:49 | 49.92 | 44735.4662 | 49.9434
2022-06-23 | 10:49 | 49.92 | 44735.4662 | 49.9434
2022-06-23 | 10:49 | 49.918 | 44735.4662 | 49.9434
2022-06-23 | 10:49 | 49.918 | 44735.4662 | 49.9434
2022-06-23 | 10:49 | 49.916 | 44735.4662 | 49.9435
2022-06-23 | 10:49 | 49.917 | 44735.4662 | 49.9435
2022-06-23 | 10:49 | 49.917 | 44735.4662 | 49.9436
2022-06-23 | 10:49 | 49.919 | 44735.4662 | 49.9436
2022-06-23 | 10:49 | 49.922 | 44735.4662 | 49.9436
2022-06-23 | 10:49 | 49.926 | 44735.4662 | 49.9436
2022-06-23 | 10:49 | 49.928 | 44735.4662 | 49.9436
2022-06-23 | 10:49 | 49.929 | 2022-06-23 11:11 | 49.9437
2022-06-23 | 10:49 | 49.931 | 44735.4662 | 49.9437
2022-06-23 | 10:49 | 49.932 | 44735.4662 | 49.9437
2022-06-23 | 10:49 | 49.931 | 44735.4662 | 49.9436
2022-06-23 | 10:49 | 49.932 | 44735.4662 | 49.9436
2022-06-23 | 10:49 | 49.931 | 44735.4662 | 49.9436
2022-06-23 | 10:49 | 49.928 | 44735.4662 | 49.9436
2022-06-23 | 10:49 | 49.928 | 44735.4662 | 49.9435
2022-06-23 | 10:49 | 49.928 | 44735.4662 | 49.9435
2022-06-23 | 10:49 | 49.927 | 44735.4662 | 49.9434
2022-06-23 | 10:49 | 49.926 | 44735.4662 | 49.9433
2022-06-23 | 10:49 | 49.925 | 44735.4662 | 49.9432
2022-06-23 | 10:49 | 49.924 | 44735.4662 | 49.9431
2022-06-23 | 10:49 | 49.924 | 44735.4662 | 49.943
2022-06-23 | 10:49 | 49.923 | 44735.4662 | 49.943
2022-06-23 | 10:49 | 49.926 | 44735.4662 | 49.9429
2022-06-23 | 10:49 | 49.928 | 44735.4662 | 49.943
2022-06-23 | 10:49 | 49.93 | 44735.4662 | 49.943
2022-06-23 | 10:49 | 49.931 | 44735.4662 | 49.943
2022-06-23 | 10:49 | 49.931 | 44735.4662 | 49.943
2022-06-23 | 10:50 | 49.933 | 44735.4662 | 49.943
2022-06-23 | 10:50 | 49.932 | 44735.4662 | 49.9429
2022-06-23 | 10:50 | 49.933 | 44735.4662 | 49.9429
2022-06-23 | 10:50 | 49.934 | 44735.4662 | 49.9429
2022-06-23 | 10:50 | 49.934 | 44735.4662 | 49.9428
2022-06-23 | 10:50 | 49.935 | 44735.4662 | 49.9428
2022-06-23 | 10:50 | 49.934 | 44735.4662 | 49.9426
2022-06-23 | 10:50 | 49.935 | 44735.4662 | 49.9426
2022-06-23 | 10:50 | 49.937 | 44735.4662 | 49.9426
2022-06-23 | 10:50 | 49.94 | 44735.4662 | 49.9427
2022-06-23 | 10:50 | 49.939 | 44735.4662 | 49.9427
2022-06-23 | 10:50 | 49.938 | 44735.4662 | 49.9427
2022-06-23 | 10:50 | 49.938 | 44735.4662 | 49.9428
2022-06-23 | 10:50 | 49.938 | 44735.4662 | 49.9428
2022-06-23 | 10:50 | 49.936 | 44735.4662 | 49.9427
2022-06-23 | 10:50 | 49.934 | 44735.4662 | 49.9427
2022-06-23 | 10:50 | 49.932 | 44735.4662 | 49.9427
2022-06-23 | 10:50 | 49.932 | 44735.4662 | 49.9427
2022-06-23 | 10:50 | 49.932 | 44735.4662 | 49.9426
2022-06-23 | 10:50 | 49.931 | 44735.4662 | 49.9425
2022-06-23 | 10:50 | 49.933 | 44735.4662 | 49.9425
2022-06-23 | 10:50 | 49.933 | 44735.4662 | 49.9424
2022-06-23 | 10:50 | 49.935 | 44735.4662 | 49.9424
2022-06-23 | 10:50 | 49.935 | 44735.4662 | 49.9425
2022-06-23 | 10:50 | 49.934 | 44735.4662 | 49.9425
2022-06-23 | 10:50 | 49.935 | 44735.4662 | 49.9425
2022-06-23 | 10:50 | 49.936 | 44735.4662 | 49.9425
2022-06-23 | 10:50 | 49.938 | 44735.4662 | 49.9426
2022-06-23 | 10:50 | 49.941 | 44735.4662 | 49.9426
2022-06-23 | 10:50 | 49.943 | 44735.4662 | 49.9427
2022-06-23 | 10:50 | 49.944 | 2022-06-23 11:11 | 49.9427
2022-06-23 | 10:50 | 49.942 | 44735.4662 | 49.9427
2022-06-23 | 10:50 | 49.941 | 44735.4662 | 49.9427
2022-06-23 | 10:50 | 49.941 | 44735.4662 | 49.9427
2022-06-23 | 10:50 | 49.94 | 44735.4662 | 49.9426
2022-06-23 | 10:50 | 49.941 | 44735.4662 | 49.9426
2022-06-23 | 10:50 | 49.942 | 44735.4662 | 49.9425
2022-06-23 | 10:50 | 49.942 | 44735.4662 | 49.9425
2022-06-23 | 10:50 | 49.944 | 44735.4662 | 49.9424
2022-06-23 | 10:50 | 49.946 | 44735.4662 | 49.9424
2022-06-23 | 10:50 | 49.948 | 44735.4662 | 49.9423
2022-06-23 | 10:50 | 49.947 | 44735.4662 | 49.9423
2022-06-23 | 10:50 | 49.948 | 44735.4662 | 49.9423
2022-06-23 | 10:50 | 49.945 | 44735.4662 | 49.9423
2022-06-23 | 10:50 | 49.945 | 44735.4662 | 49.9423
2022-06-23 | 10:50 | 49.943 | 44735.4662 | 49.9423
2022-06-23 | 10:50 | 49.94 | 44735.4662 | 49.9422
2022-06-23 | 10:50 | 49.942 | 44735.4662 | 49.9422
2022-06-23 | 10:50 | 49.943 | 44735.4662 | 49.9422
2022-06-23 | 10:50 | 49.943 | 44735.4662 | 49.9421
2022-06-23 | 10:50 | 49.943 | 44735.4662 | 49.942
2022-06-23 | 10:50 | 49.942 | 44735.4662 | 49.942
2022-06-23 | 10:50 | 49.941 | 44735.4662 | 49.942
2022-06-23 | 10:50 | 49.942 | 44735.4662 | 49.942
2022-06-23 | 10:50 | 49.938 | 44735.4662 | 49.942
2022-06-23 | 10:50 | 49.938 | 44735.4662 | 49.942
2022-06-23 | 10:50 | 49.937 | 44735.4662 | 49.942
2022-06-23 | 10:50 | 49.934 | 44735.4662 | 49.942
2022-06-23 | 10:50 | 49.932 | 44735.4662 | 49.942
2022-06-23 | 10:50 | 49.934 | 44735.4662 | 49.942
2022-06-23 | 10:50 | 49.933 | 44735.4662 | 49.942
2022-06-23 | 10:51 | 49.935 | 44735.4662 | 49.942
2022-06-23 | 10:51 | 49.936 | 44735.4662 | 49.942
2022-06-23 | 10:51 | 49.937 | 44735.4662 | 49.9419
2022-06-23 | 10:51 | 49.937 | 44735.4662 | 49.9419
2022-06-23 | 10:51 | 49.94 | 44735.4662 | 49.9419
2022-06-23 | 10:51 | 49.941 | 44735.4662 | 49.9419
2022-06-23 | 10:51 | 49.943 | 44735.4662 | 49.9419
2022-06-23 | 10:51 | 49.944 | 44735.4662 | 49.9418
2022-06-23 | 10:51 | 49.949 | 44735.4662 | 49.9418
2022-06-23 | 10:51 | 49.949 | 44735.4662 | 49.9418
2022-06-23 | 10:51 | 49.949 | 44735.4662 | 49.9417
2022-06-23 | 10:51 | 49.949 | 44735.4662 | 49.9418
2022-06-23 | 10:51 | 49.949 | 44735.4662 | 49.9418
2022-06-23 | 10:51 | 49.95 | 44735.4662 | 49.9417
2022-06-23 | 10:51 | 49.952 | 44735.4662 | 49.9417
2022-06-23 | 10:51 | 49.951 | 44735.4662 | 49.9417
2022-06-23 | 10:51 | 49.95 | 44735.4662 | 49.9416
2022-06-23 | 10:51 | 49.949 | 44735.4662 | 49.9415
2022-06-23 | 10:51 | 49.949 | 44735.4662 | 49.9415
2022-06-23 | 10:51 | 49.947 | 2022-06-23 11:11 | 49.9415
2022-06-23 | 10:51 | 49.948 | 44735.4662 | 49.9415
2022-06-23 | 10:51 | 49.947 | 44735.4662 | 49.9416
2022-06-23 | 10:51 | 49.946 | 44735.4662 | 49.9415
2022-06-23 | 10:51 | 49.946 | 44735.4662 | 49.9415
2022-06-23 | 10:51 | 49.945 | 44735.4662 | 49.9415
2022-06-23 | 10:51 | 49.943 | 44735.4662 | 49.9414
2022-06-23 | 10:51 | 49.943 | 44735.4662 | 49.9415
2022-06-23 | 10:51 | 49.941 | 44735.4662 | 49.9414
2022-06-23 | 10:51 | 49.938 | 44735.4662 | 49.9414
2022-06-23 | 10:51 | 49.937 | 44735.4662 | 49.9413
2022-06-23 | 10:51 | 49.935 | 44735.4662 | 49.9413
2022-06-23 | 10:51 | 49.932 | 44735.4662 | 49.9413
2022-06-23 | 10:51 | 49.93 | 44735.4662 | 49.9412
2022-06-23 | 10:51 | 49.929 | 44735.4662 | 49.9412
2022-06-23 | 10:51 | 49.929 | 44735.4662 | 49.9412
2022-06-23 | 10:51 | 49.923 | 44735.4662 | 49.9412
2022-06-23 | 10:51 | 49.923 | 44735.4662 | 49.9412
2022-06-23 | 10:51 | 49.919 | 44735.4662 | 49.9412
2022-06-23 | 10:51 | 49.918 | 44735.4662 | 49.9412
2022-06-23 | 10:51 | 49.919 | 44735.4662 | 49.9411
2022-06-23 | 10:51 | 49.917 | 44735.4662 | 49.9411
2022-06-23 | 10:51 | 49.917 | 44735.4662 | 49.9411
2022-06-23 | 10:51 | 49.915 | 44735.4662 | 49.9411
2022-06-23 | 10:51 | 49.915 | 44735.4662 | 49.9411
2022-06-23 | 10:51 | 49.915 | 44735.4662 | 49.9411
2022-06-23 | 10:51 | 49.916 | 44735.4662 | 49.9411
2022-06-23 | 10:51 | 49.917 | 44735.4662 | 49.941
2022-06-23 | 10:51 | 49.918 | 44735.4662 | 49.9409
2022-06-23 | 10:51 | 49.919 | 44735.4662 | 49.9408
2022-06-23 | 10:51 | 49.921 | 44735.4662 | 49.9408
2022-06-23 | 10:51 | 49.921 | 44735.4662 | 49.9407
2022-06-23 | 10:51 | 49.923 | 44735.4662 | 49.9406
2022-06-23 | 10:51 | 49.923 | 44735.4662 | 49.9404
2022-06-23 | 10:51 | 49.924 | 44735.4662 | 49.9403
2022-06-23 | 10:51 | 49.923 | 44735.4662 | 49.9403
2022-06-23 | 10:51 | 49.923 | 44735.4662 | 49.9402
2022-06-23 | 10:51 | 49.925 | 44735.4662 | 49.9401
2022-06-23 | 10:51 | 49.925 | 44735.4662 | 49.94
2022-06-23 | 10:51 | 49.926 | 44735.4662 | 49.9399
2022-06-23 | 10:52 | 49.93 | 44735.4662 | 49.9399
2022-06-23 | 10:52 | 49.932 | 44735.4662 | 49.9398
2022-06-23 | 10:52 | 49.937 | 44735.4662 | 49.9398
2022-06-23 | 10:52 | 49.938 | 44735.4662 | 49.9397
2022-06-23 | 10:52 | 49.939 | 44735.4662 | 49.9397
2022-06-23 | 10:52 | 49.939 | 44735.4662 | 49.9396
2022-06-23 | 10:52 | 49.939 | 44735.4662 | 49.9395
2022-06-23 | 10:52 | 49.939 | 44735.4662 | 49.9395
2022-06-23 | 10:52 | 49.94 | 44735.4662 | 49.9395
2022-06-23 | 10:52 | 49.941 | 44735.4662 | 49.9394
2022-06-23 | 10:52 | 49.942 | 2022-06-23 11:11 | 49.9394
2022-06-23 | 10:52 | 49.946 | 44735.4662 | 49.9393
2022-06-23 | 10:52 | 49.949 | 44735.4662 | 49.9392
2022-06-23 | 10:52 | 49.95 | 44735.4662 | 49.9391
2022-06-23 | 10:52 | 49.953 | 44735.4662 | 49.939
2022-06-23 | 10:52 | 49.957 | 44735.4662 | 49.939
2022-06-23 | 10:52 | 49.956 | 44735.4662 | 49.939
2022-06-23 | 10:52 | 49.957 | 44735.4662 | 49.9389
2022-06-23 | 10:52 | 49.956 | 44735.4662 | 49.939
2022-06-23 | 10:52 | 49.956 | 44735.4662 | 49.9391
2022-06-23 | 10:52 | 49.953 | 44735.4662 | 49.9391
2022-06-23 | 10:52 | 49.95 | 44735.4662 | 49.939
2022-06-23 | 10:52 | 49.948 | 44735.4662 | 49.9389
2022-06-23 | 10:52 | 49.946 | 44735.4662 | 49.9388
2022-06-23 | 10:52 | 49.946 | 44735.4662 | 49.9387
2022-06-23 | 10:52 | 49.947 | 44735.4662 | 49.9386
2022-06-23 | 10:52 | 49.951 | 44735.4662 | 49.9385
2022-06-23 | 10:52 | 49.951 | 44735.4662 | 49.9385
2022-06-23 | 10:52 | 49.954 | 44735.4662 | 49.9384
2022-06-23 | 10:52 | 49.955 | 44735.4662 | 49.9383
2022-06-23 | 10:52 | 49.953 | 44735.4662 | 49.9382
2022-06-23 | 10:52 | 49.952 | 44735.4662 | 49.9382
2022-06-23 | 10:52 | 49.951 | 44735.4662 | 49.9381
2022-06-23 | 10:52 | 49.953 | 44735.4662 | 49.9381
2022-06-23 | 10:52 | 49.955 | 44735.4662 | 49.9381
2022-06-23 | 10:52 | 49.957 | 44735.4662 | 49.938
2022-06-23 | 10:52 | 49.956 | 44735.4662 | 49.938
2022-06-23 | 10:52 | 49.957 | 44735.4662 | 49.938
2022-06-23 | 10:52 | 49.956 | 44735.4662 | 49.9379
2022-06-23 | 10:52 | 49.958 | 44735.4662 | 49.9379
2022-06-23 | 10:52 | 49.955 | 44735.4662 | 49.9379
2022-06-23 | 10:52 | 49.954 | 44735.4662 | 49.9379
2022-06-23 | 10:52 | 49.952 | 44735.4662 | 49.9379
2022-06-23 | 10:52 | 49.951 | 44735.4662 | 49.9379
2022-06-23 | 10:52 | 49.95 | 44735.4662 | 49.9378
2022-06-23 | 10:52 | 49.947 | 44735.4662 | 49.9379
2022-06-23 | 10:52 | 49.946 | 44735.4662 | 49.9378
2022-06-23 | 10:52 | 49.944 | 44735.4662 | 49.9378
2022-06-23 | 10:52 | 49.942 | 44735.4662 | 49.9378
2022-06-23 | 10:52 | 49.942 | 44735.4662 | 49.9377
2022-06-23 | 10:52 | 49.938 | 44735.4662 | 49.9376
2022-06-23 | 10:52 | 49.936 | 44735.4662 | 49.9376
2022-06-23 | 10:52 | 49.937 | 44735.4662 | 49.9376
2022-06-23 | 10:52 | 49.936 | 44735.4662 | 49.9376
2022-06-23 | 10:52 | 49.935 | 44735.4662 | 49.9376
2022-06-23 | 10:52 | 49.939 | 44735.4662 | 49.9376
2022-06-23 | 10:52 | 49.938 | 44735.4662 | 49.9375
2022-06-23 | 10:52 | 49.938 | 44735.4662 | 49.9375
2022-06-23 | 10:52 | 49.938 | 44735.4662 | 49.9375
2022-06-23 | 10:52 | 49.937 | 44735.4662 | 49.9374
2022-06-23 | 10:52 | 49.937 | 2022-06-23 11:11 | 49.9373
2022-06-23 | 10:53 | 49.938 | 44735.4662 | 49.9372
2022-06-23 | 10:53 | 49.941 | 44735.4662 | 49.9372
2022-06-23 | 10:53 | 49.944 | 44735.4662 | 49.9372
2022-06-23 | 10:53 | 49.946 | 44735.4662 | 49.9371
2022-06-23 | 10:53 | 49.948 | 44735.4662 | 49.937
2022-06-23 | 10:53 | 49.952 | 44735.4662 | 49.9371
2022-06-23 | 10:53 | 49.952 | 44735.4662 | 49.937
2022-06-23 | 10:53 | 49.952 | 44735.4662 | 49.937
2022-06-23 | 10:53 | 49.954 | 44735.4662 | 49.937
2022-06-23 | 10:53 | 49.953 | 44735.4662 | 49.9369
2022-06-23 | 10:53 | 49.954 | 44735.4662 | 49.9367
2022-06-23 | 10:53 | 49.953 | 44735.4662 | 49.9365
2022-06-23 | 10:53 | 49.953 | 44735.4662 | 49.9365
2022-06-23 | 10:53 | 49.956 | 44735.4662 | 49.9364
2022-06-23 | 10:53 | 49.958 | 44735.4662 | 49.9363
2022-06-23 | 10:53 | 49.956 | 44735.4662 | 49.9363
2022-06-23 | 10:53 | 49.956 | 44735.4662 | 49.9362
2022-06-23 | 10:53 | 49.954 | 44735.4662 | 49.9361
2022-06-23 | 10:53 | 49.952 | 44735.4662 | 49.9361
2022-06-23 | 10:53 | 49.954 | 44735.4662 | 49.9361
2022-06-23 | 10:53 | 49.953 | 44735.4662 | 49.9361
2022-06-23 | 10:53 | 49.953 | 44735.4662 | 49.9361
2022-06-23 | 10:53 | 49.953 | 44735.4662 | 49.9361
2022-06-23 | 10:53 | 49.952 | 44735.4662 | 49.9361
2022-06-23 | 10:53 | 49.953 | 44735.4662 | 49.9361
2022-06-23 | 10:53 | 49.954 | 44735.4662 | 49.9361
2022-06-23 | 10:53 | 49.953 | 44735.4662 | 49.9361
2022-06-23 | 10:53 | 49.955 | 44735.4662 | 49.936
2022-06-23 | 10:53 | 49.954 | 44735.4662 | 49.936
2022-06-23 | 10:53 | 49.954 | 44735.4662 | 49.936
2022-06-23 | 10:53 | 49.954 | 44735.4662 | 49.936
2022-06-23 | 10:53 | 49.95 | 44735.4662 | 49.936
2022-06-23 | 10:53 | 49.95 | 44735.4662 | 49.9359
2022-06-23 | 10:53 | 49.948 | 44735.4662 | 49.936
2022-06-23 | 10:53 | 49.945 | 44735.4662 | 49.9359
2022-06-23 | 10:53 | 49.944 | 44735.4662 | 49.936
2022-06-23 | 10:53 | 49.941 | 44735.4662 | 49.936
2022-06-23 | 10:53 | 49.939 | 44735.4662 | 49.936
2022-06-23 | 10:53 | 49.937 | 44735.4662 | 49.936
2022-06-23 | 10:53 | 49.936 | 44735.4662 | 49.9361
2022-06-23 | 10:53 | 49.932 | 44735.4662 | 49.9361
2022-06-23 | 10:53 | 49.932 | 44735.4662 | 49.9361
2022-06-23 | 10:53 | 49.933 | 44735.4662 | 49.9361
2022-06-23 | 10:53 | 49.931 | 44735.4662 | 49.9361
2022-06-23 | 10:53 | 49.93 | 44735.4662 | 49.936
2022-06-23 | 10:53 | 49.93 | 44735.4662 | 49.936
2022-06-23 | 10:53 | 49.927 | 44735.4662 | 49.936
2022-06-23 | 10:53 | 49.927 | 44735.4662 | 49.9359
2022-06-23 | 10:53 | 49.926 | 44735.4662 | 49.9358
2022-06-23 | 10:53 | 49.924 | 2022-06-23 11:11 | 49.9358
2022-06-23 | 10:53 | 49.922 | 44735.4662 | 49.9358
2022-06-23 | 10:53 | 49.92 | 44735.4662 | 49.9358
2022-06-23 | 10:53 | 49.918 | 44735.4662 | 49.9358
2022-06-23 | 10:53 | 49.916 | 44735.4662 | 49.9358
2022-06-23 | 10:53 | 49.919 | 44735.4662 | 49.9358
2022-06-23 | 10:53 | 49.921 | 44735.4662 | 49.9357
2022-06-23 | 10:53 | 49.923 | 44735.4662 | 49.9357
2022-06-23 | 10:53 | 49.924 | 44735.4662 | 49.9357
2022-06-23 | 10:53 | 49.926 | 44735.4662 | 49.9357
2022-06-23 | 10:54 | 49.927 | 44735.4662 | 49.9357
2022-06-23 | 10:54 | 49.93 | 44735.4662 | 49.9357
2022-06-23 | 10:54 | 49.933 | 44735.4662 | 49.9357
2022-06-23 | 10:54 | 49.935 | 44735.4662 | 49.9357
2022-06-23 | 10:54 | 49.936 | 44735.4662 | 49.9357
2022-06-23 | 10:54 | 49.938 | 44735.4662 | 49.9356
2022-06-23 | 10:54 | 49.94 | 44735.4662 | 49.9356
2022-06-23 | 10:54 | 49.942 | 44735.4662 | 49.9356
2022-06-23 | 10:54 | 49.941 | 44735.4662 | 49.9356
2022-06-23 | 10:54 | 49.941 | 44735.4662 | 49.9355
2022-06-23 | 10:54 | 49.941 | 44735.4662 | 49.9356
2022-06-23 | 10:54 | 49.942 | 44735.4662 | 49.9356
2022-06-23 | 10:54 | 49.942 | 44735.4662 | 49.9355
2022-06-23 | 10:54 | 49.942 | 44735.4662 | 49.9355
2022-06-23 | 10:54 | 49.943 | 44735.4662 | 49.9355
2022-06-23 | 10:54 | 49.942 | 44735.4662 | 49.9354
2022-06-23 | 10:54 | 49.942 | 44735.4662 | 49.9354
2022-06-23 | 10:54 | 49.941 | 44735.4662 | 49.9353
2022-06-23 | 10:54 | 49.937 | 44735.4662 | 49.9353
2022-06-23 | 10:54 | 49.933 | 44735.4662 | 49.9353
2022-06-23 | 10:54 | 49.929 | 44735.4662 | 49.9352
2022-06-23 | 10:54 | 49.924 | 44735.4662 | 49.9352
2022-06-23 | 10:54 | 49.919 | 44735.4662 | 49.9352
2022-06-23 | 10:54 | 49.914 | 44735.4662 | 49.9351
2022-06-23 | 10:54 | 49.91 | 44735.4662 | 49.9351
2022-06-23 | 10:54 | 49.909 | 44735.4662 | 49.9351
2022-06-23 | 10:54 | 49.909 | 44735.4662 | 49.9351
2022-06-23 | 10:54 | 49.911 | 44735.4662 | 49.9351
2022-06-23 | 10:54 | 49.914 | 44735.4662 | 49.9351
2022-06-23 | 10:54 | 49.917 | 44735.4662 | 49.9351
2022-06-23 | 10:54 | 49.92 | 44735.4662 | 49.9352
2022-06-23 | 10:54 | 49.922 | 44735.4662 | 49.9351
2022-06-23 | 10:54 | 49.926 | 44735.4662 | 49.9351
2022-06-23 | 10:54 | 49.928 | 44735.4662 | 49.9351
2022-06-23 | 10:54 | 49.933 | 44735.4662 | 49.9352
2022-06-23 | 10:54 | 49.937 | 44735.4662 | 49.9351
2022-06-23 | 10:54 | 49.941 | 44735.4662 | 49.9351
2022-06-23 | 10:54 | 49.944 | 44735.4662 | 49.9351
2022-06-23 | 10:54 | 49.945 | 44735.4662 | 49.9352
2022-06-23 | 10:54 | 49.945 | 44735.4662 | 49.9352
2022-06-23 | 10:54 | 49.944 | 2022-06-23 11:11 | 49.9352
2022-06-23 | 10:54 | 49.945 | 44735.4662 | 49.9352
2022-06-23 | 10:54 | 49.947 | 44735.4662 | 49.9352
2022-06-23 | 10:54 | 49.948 | 44735.4662 | 49.9353
2022-06-23 | 10:54 | 49.948 | 44735.4662 | 49.9353
2022-06-23 | 10:54 | 49.948 | 44735.4662 | 49.9354
2022-06-23 | 10:54 | 49.947 | 44735.4662 | 49.9354
2022-06-23 | 10:54 | 49.949 | 44735.4662 | 49.9355
2022-06-23 | 10:54 | 49.948 | 44735.4662 | 49.9355
2022-06-23 | 10:54 | 49.947 | 44735.4662 | 49.9355
2022-06-23 | 10:54 | 49.947 | 44735.4662 | 49.9356
2022-06-23 | 10:54 | 49.949 | 44735.4662 | 49.9356
2022-06-23 | 10:54 | 49.949 | 44735.4662 | 49.9356
2022-06-23 | 10:54 | 49.949 | 44735.4662 | 49.9356
2022-06-23 | 10:54 | 49.948 | 44735.4662 | 49.9356
2022-06-23 | 10:54 | 49.947 | 44735.4662 | 49.9356
2022-06-23 | 10:54 | 49.946 | 44735.4662 | 49.9356
2022-06-23 | 10:54 | 49.944 | 44735.4662 | 49.9357
2022-06-23 | 10:54 | 49.942 | 44735.4662 | 49.9357
2022-06-23 | 10:54 | 49.942 | 44735.4662 | 49.9358
2022-06-23 | 10:55 | 49.94 | 44735.4662 | 49.9357
2022-06-23 | 10:55 | 49.938 | 44735.4662 | 49.9358
2022-06-23 | 10:55 | 49.936 | 44735.4662 | 49.9357
2022-06-23 | 10:55 | 49.935 | 44735.4662 | 49.9357
2022-06-23 | 10:55 | 49.937 | 44735.4662 | 49.9357
2022-06-23 | 10:55 | 49.938 | 44735.4662 | 49.9356
2022-06-23 | 10:55 | 49.939 | 44735.4662 | 49.9356
2022-06-23 | 10:55 | 49.937 | 44735.4662 | 49.9356
2022-06-23 | 10:55 | 49.935 | 44735.4662 | 49.9356
2022-06-23 | 10:55 | 49.934 | 44735.4662 | 49.9356
2022-06-23 | 10:55 | 49.935 | 44735.4662 | 49.9357
2022-06-23 | 10:55 | 49.936 | 44735.4662 | 49.9357
2022-06-23 | 10:55 | 49.937 | 44735.4662 | 49.9357
2022-06-23 | 10:55 | 49.938 | 44735.4662 | 49.9358
2022-06-23 | 10:55 | 49.941 | 44735.4662 | 49.9359
2022-06-23 | 10:55 | 49.943 | 44735.4662 | 49.936
2022-06-23 | 10:55 | 49.943 | 44735.4662 | 49.936
2022-06-23 | 10:55 | 49.947 | 44735.4662 | 49.936
2022-06-23 | 10:55 | 49.948 | 44735.4662 | 49.9361
2022-06-23 | 10:55 | 49.95 | 44735.4662 | 49.9362
2022-06-23 | 10:55 | 49.949 | 44735.4662 | 49.9362
2022-06-23 | 10:55 | 49.949 | 44735.4662 | 49.9362
2022-06-23 | 10:55 | 49.95 | 44735.4662 | 49.9362
2022-06-23 | 10:55 | 49.948 | 44735.4662 | 49.9362
2022-06-23 | 10:55 | 49.949 | 44735.4662 | 49.9362
2022-06-23 | 10:55 | 49.947 | 44735.4662 | 49.9362
2022-06-23 | 10:55 | 49.947 | 44735.4662 | 49.9362
2022-06-23 | 10:55 | 49.946 | 44735.4662 | 49.9363
2022-06-23 | 10:55 | 49.945 | 44735.4662 | 49.9364
2022-06-23 | 10:55 | 49.946 | 44735.4662 | 49.9364
2022-06-23 | 10:55 | 49.947 | 2022-06-23 11:11 | 49.9364
|  |  | 44735.4663 | 49.9365
|  |  | 44735.4663 | 49.9366
|  |  | 44735.4663 | 49.9367
|  |  | 44735.4663 | 49.9367
|  |  | 44735.4663 | 49.9366
|  |  | 44735.4663 | 49.9367
|  |  | 44735.4663 | 49.9366
|  |  | 44735.4663 | 49.9366
|  |  | 44735.4663 | 49.9366
|  |  | 44735.4663 | 49.9367
|  |  | 44735.4663 | 49.9367
|  |  | 44735.4663 | 49.9367
|  |  | 44735.4663 | 49.9368
|  |  | 44735.4663 | 49.9368
|  |  | 44735.4663 | 49.9369
|  |  | 44735.4663 | 49.937
|  |  | 44735.4663 | 49.9371
|  |  | 44735.4663 | 49.9371
|  |  | 44735.4663 | 49.9372
|  |  | 44735.4663 | 49.9373
|  |  | 44735.4663 | 49.9373
|  |  | 44735.4663 | 49.9373
|  |  | 44735.4663 | 49.9373
|  |  | 44735.4663 | 49.9374
|  |  | 44735.4663 | 49.9374
|  |  | 44735.4663 | 49.9374
|  |  | 44735.4663 | 49.9375
|  |  | 44735.4663 | 49.9376
|  |  | 44735.4663 | 49.9377
|  |  | 44735.4663 | 49.9378
|  |  | 44735.4663 | 49.9379
|  |  | 44735.4663 | 49.938
|  |  | 44735.4663 | 49.9381
|  |  | 44735.4663 | 49.9381
|  |  | 44735.4663 | 49.9382
|  |  | 44735.4663 | 49.9383
|  |  | 44735.4663 | 49.9383
|  |  | 44735.4663 | 49.9383
|  |  | 44735.4663 | 49.9383
|  |  | 44735.4663 | 49.9384
|  |  | 44735.4663 | 49.9385
|  |  | 44735.4663 | 49.9386
|  |  | 44735.4663 | 49.9387
|  |  | 44735.4663 | 49.9388
|  |  | 44735.4663 | 49.9388
|  |  | 44735.4663 | 49.9389
|  |  | 44735.4663 | 49.9389
|  |  | 44735.4663 | 49.9389
|  |  | 44735.4663 | 49.9389
|  |  | 2022-06-23 11:11 | 49.939
|  |  | 44735.4663 | 49.939
|  |  | 44735.4663 | 49.939
|  |  | 44735.4663 | 49.9391
|  |  | 44735.4663 | 49.9391
|  |  | 44735.4663 | 49.9391
|  |  | 44735.4663 | 49.9392
|  |  | 44735.4663 | 49.9392
|  |  | 44735.4663 | 49.9392
|  |  | 44735.4663 | 49.9392
|  |  | 44735.4663 | 49.9392
|  |  | 44735.4663 | 49.9393
|  |  | 44735.4663 | 49.9392
|  |  | 44735.4663 | 49.9393
|  |  | 44735.4663 | 49.9393
|  |  | 44735.4663 | 49.9393
|  |  | 44735.4663 | 49.9394
|  |  | 44735.4663 | 49.9395
|  |  | 44735.4663 | 49.9395
|  |  | 44735.4663 | 49.9396
|  |  | 44735.4663 | 49.9396
|  |  | 44735.4663 | 49.9397
|  |  | 44735.4663 | 49.9398
|  |  | 44735.4663 | 49.9398
|  |  | 44735.4663 | 49.9399
|  |  | 44735.4663 | 49.94
|  |  | 44735.4663 | 49.94
|  |  | 44735.4663 | 49.9401
|  |  | 44735.4663 | 49.9401
|  |  | 44735.4663 | 49.9401
|  |  | 44735.4663 | 49.9401
|  |  | 44735.4663 | 49.9402
|  |  | 44735.4663 | 49.9403
|  |  | 44735.4663 | 49.9403
|  |  | 44735.4663 | 49.9403
|  |  | 44735.4663 | 49.9404
|  |  | 44735.4663 | 49.9403
|  |  | 44735.4663 | 49.9403
|  |  | 44735.4663 | 49.9403
|  |  | 44735.4663 | 49.9404
|  |  | 44735.4663 | 49.9405
|  |  | 44735.4663 | 49.9405
|  |  | 44735.4663 | 49.9406
|  |  | 44735.4663 | 49.9406
|  |  | 44735.4663 | 49.9408
|  |  | 44735.4663 | 49.9409
|  |  | 44735.4663 | 49.941
|  |  | 44735.4663 | 49.9412
|  |  | 44735.4663 | 49.9413
|  |  | 44735.4663 | 49.9413
|  |  | 2022-06-23 11:11 | 49.9415
|  |  | 44735.4663 | 49.9415
|  |  | 44735.4663 | 49.9416
|  |  | 44735.4663 | 49.9417
|  |  | 44735.4663 | 49.9418
|  |  | 44735.4663 | 49.9419
|  |  | 44735.4663 | 49.9419
|  |  | 44735.4663 | 49.942
|  |  | 44735.4663 | 49.942
|  |  | 44735.4663 | 49.9421
|  |  | 44735.4663 | 49.9422
|  |  | 44735.4663 | 49.9423
|  |  | 44735.4663 | 49.9425
|  |  | 44735.4663 | 49.9426
|  |  | 44735.4663 | 49.9427
|  |  | 44735.4663 | 49.9428
|  |  | 44735.4663 | 49.9429
|  |  | 44735.4663 | 49.943
|  |  | 44735.4663 | 49.9431
|  |  | 44735.4663 | 49.9431
|  |  | 44735.4663 | 49.9431
|  |  | 44735.4663 | 49.9431
|  |  | 44735.4663 | 49.943
|  |  | 44735.4663 | 49.9429
|  |  | 44735.4663 | 49.9429
|  |  | 44735.4663 | 49.9429
|  |  | 44735.4663 | 49.9429
|  |  | 44735.4663 | 49.943
|  |  | 44735.4663 | 49.943
|  |  | 44735.4663 | 49.943
|  |  | 44735.4663 | 49.9431
|  |  | 44735.4663 | 49.9431
|  |  | 44735.4663 | 49.9431
|  |  | 44735.4663 | 49.9432
|  |  | 44735.4663 | 49.9432
|  |  | 44735.4663 | 49.9432
|  |  | 44735.4663 | 49.9432
|  |  | 44735.4663 | 49.9432
|  |  | 44735.4663 | 49.9433
|  |  | 44735.4663 | 49.9433
|  |  | 44735.4663 | 49.9433
|  |  | 44735.4663 | 49.9433
|  |  | 44735.4663 | 49.9432
|  |  | 44735.4663 | 49.9432
|  |  | 44735.4663 | 49.9433
|  |  | 44735.4663 | 49.9433
|  |  | 44735.4663 | 49.9433
|  |  | 44735.4663 | 49.9433
|  |  | 44735.4663 | 49.9433
|  |  | 44735.4663 | 49.9434
|  |  | 2022-06-23 11:11 | 49.9434
|  |  | 44735.4663 | 49.9435
|  |  | 44735.4663 | 49.9435
|  |  | 44735.4663 | 49.9436
|  |  | 44735.4663 | 49.9436
|  |  | 44735.4663 | 49.9437
|  |  | 44735.4663 | 49.9437
|  |  | 44735.4663 | 49.9437
|  |  | 44735.4663 | 49.9437
|  |  | 44735.4663 | 49.9437
|  |  | 44735.4663 | 49.9436
|  |  | 44735.4663 | 49.9436
|  |  | 44735.4663 | 49.9436
|  |  | 44735.4663 | 49.9437
|  |  | 44735.4663 | 49.9435
|  |  | 44735.4663 | 49.9436
|  |  | 44735.4663 | 49.9437
|  |  | 44735.4663 | 49.9437
|  |  | 44735.4663 | 49.9438
|  |  | 44735.4663 | 49.9439
|  |  | 44735.4663 | 49.9439
|  |  | 44735.4663 | 49.9439
|  |  | 44735.4663 | 49.944
|  |  | 44735.4663 | 49.9441
|  |  | 44735.4663 | 49.9441
|  |  | 44735.4663 | 49.9441
|  |  | 44735.4663 | 49.9441
|  |  | 44735.4663 | 49.9442
|  |  | 44735.4663 | 49.9442
|  |  | 44735.4663 | 49.9442
|  |  | 44735.4663 | 49.9442
|  |  | 44735.4663 | 49.9441
|  |  | 44735.4663 | 49.9441
|  |  | 44735.4663 | 49.9441
|  |  | 44735.4663 | 49.9441
|  |  | 44735.4663 | 49.9441
|  |  | 44735.4663 | 49.9441
|  |  | 44735.4663 | 49.9441
|  |  | 44735.4663 | 49.9441
|  |  | 44735.4663 | 49.9442
|  |  | 44735.4663 | 49.9442
|  |  | 44735.4663 | 49.9442
|  |  | 44735.4663 | 49.9442
|  |  | 44735.4663 | 49.9442
|  |  | 44735.4663 | 49.9442
|  |  | 44735.4663 | 49.9442
|  |  | 44735.4663 | 49.9442
|  |  | 44735.4663 | 49.9442
|  |  | 44735.4663 | 49.9443
|  |  | 44735.4663 | 49.9443
|  |  | 2022-06-23 11:11 | 49.9444
|  |  | 44735.4663 | 49.9444
|  |  | 44735.4663 | 49.9444
|  |  | 44735.4663 | 49.9444
|  |  | 44735.4663 | 49.9444
|  |  | 44735.4663 | 49.9444
|  |  | 44735.4663 | 49.9445
|  |  | 44735.4663 | 49.9445
|  |  | 44735.4663 | 49.9445
|  |  | 44735.4663 | 49.9446
|  |  | 44735.4663 | 49.9446
|  |  | 44735.4663 | 49.9447
|  |  | 44735.4663 | 49.9447
|  |  | 44735.4663 | 49.9447
|  |  | 44735.4663 | 49.9447
|  |  | 44735.4663 | 49.9448
|  |  | 44735.4663 | 49.9448
|  |  | 44735.4663 | 49.9449
|  |  | 44735.4663 | 49.9449
|  |  | 44735.4663 | 49.945
|  |  | 44735.4663 | 49.945
|  |  | 44735.4663 | 49.945
|  |  | 44735.4663 | 49.9451
|  |  | 44735.4663 | 49.9451
|  |  | 44735.4663 | 49.9451
|  |  | 44735.4663 | 49.9451
|  |  | 44735.4663 | 49.9451
|  |  | 44735.4663 | 49.9451
|  |  | 44735.4663 | 49.9451
|  |  | 44735.4663 | 49.9451
|  |  | 44735.4663 | 49.9451
|  |  | 44735.4663 | 49.9451
|  |  | 44735.4663 | 49.9452
|  |  | 44735.4663 | 49.9453
|  |  | 44735.4663 | 49.9453
|  |  | 44735.4663 | 49.9454
|  |  | 44735.4663 | 49.9454
|  |  | 44735.4663 | 49.9454
|  |  | 44735.4663 | 49.9455
|  |  | 44735.4663 | 49.9455
|  |  | 44735.4663 | 49.9456
|  |  | 44735.4663 | 49.9456
|  |  | 44735.4663 | 49.9456
|  |  | 44735.4663 | 49.9456
|  |  | 44735.4663 | 49.9456
|  |  | 44735.4663 | 49.9456
|  |  | 44735.4663 | 49.9457
|  |  | 44735.4663 | 49.9457
|  |  | 44735.4663 | 49.9458
|  |  | 44735.4663 | 49.9459
|  |  | 2022-06-23 11:11 | 49.9459
|  |  | 44735.4663 | 49.946
|  |  | 44735.4663 | 49.946
|  |  | 44735.4663 | 49.9461
|  |  | 44735.4663 | 49.9461
|  |  | 44735.4663 | 49.9461
|  |  | 44735.4663 | 49.9461
|  |  | 44735.4663 | 49.9461
|  |  | 44735.4663 | 49.946
|  |  | 44735.4663 | 49.9461
|  |  | 44735.4663 | 49.946
|  |  | 44735.4663 | 49.946
|  |  | 44735.4663 | 49.946
|  |  | 44735.4663 | 49.9459
|  |  | 44735.4663 | 49.9459
|  |  | 44735.4663 | 49.9459
|  |  | 44735.4663 | 49.9458
|  |  | 44735.4663 | 49.9458
|  |  | 44735.4663 | 49.9458
|  |  | 44735.4663 | 49.9458
|  |  | 44735.4663 | 49.9458
|  |  | 44735.4663 | 49.9459
|  |  | 44735.4663 | 49.9459
|  |  | 44735.4663 | 49.9459
|  |  | 44735.4663 | 49.9459
|  |  | 44735.4663 | 49.9459
|  |  | 44735.4663 | 49.9459
|  |  | 44735.4663 | 49.9459
|  |  | 44735.4663 | 49.9459
|  |  | 44735.4663 | 49.9459
|  |  | 44735.4663 | 49.9459
|  |  | 44735.4663 | 49.946
|  |  | 44735.4663 | 49.946
|  |  | 44735.4663 | 49.9461
|  |  | 44735.4663 | 49.9461
|  |  | 44735.4663 | 49.9462
|  |  | 44735.4663 | 49.9463
|  |  | 44735.4663 | 49.9464
|  |  | 44735.4663 | 49.9464
|  |  | 44735.4663 | 49.9465
|  |  | 44735.4663 | 49.9466
|  |  | 44735.4663 | 49.9467
|  |  | 44735.4663 | 49.9467
|  |  | 44735.4663 | 49.9467
|  |  | 44735.4663 | 49.9468
|  |  | 44735.4663 | 49.9468
|  |  | 44735.4663 | 49.9468
|  |  | 44735.4663 | 49.9468
|  |  | 44735.4663 | 49.9468
|  |  | 44735.4663 | 49.9468
|  |  | 2022-06-23 11:11 | 49.9468

## 20220625-1
In GMT |  |  | High resolution Incident data
Date | Time | Freq | time | freq
2022-06-25 | 3:54 | 49.977 | 2022-06-25 04:54 | 49.9783
2022-06-25 | 3:54 | 49.979 | 44737.2042 | 49.9783
2022-06-25 | 3:54 | 49.975 | 44737.2042 | 49.9784
2022-06-25 | 3:54 | 49.976 | 44737.2042 | 49.9784
2022-06-25 | 3:54 | 49.974 | 44737.2042 | 49.9784
2022-06-25 | 3:54 | 49.973 | 44737.2042 | 49.9784
2022-06-25 | 3:54 | 49.974 | 44737.2042 | 49.9784
2022-06-25 | 3:54 | 49.976 | 44737.2042 | 49.9783
2022-06-25 | 3:54 | 49.977 | 44737.2042 | 49.9782
2022-06-25 | 3:54 | 49.979 | 44737.2042 | 49.9781
2022-06-25 | 3:54 | 49.982 | 44737.2042 | 49.9779
2022-06-25 | 3:54 | 49.984 | 44737.2042 | 49.9778
2022-06-25 | 3:54 | 49.986 | 44737.2042 | 49.9777
2022-06-25 | 3:54 | 49.986 | 44737.2042 | 49.9777
2022-06-25 | 3:54 | 49.986 | 44737.2042 | 49.9777
2022-06-25 | 3:54 | 49.985 | 44737.2042 | 49.9777
2022-06-25 | 3:54 | 49.985 | 44737.2042 | 49.9777
2022-06-25 | 3:54 | 49.983 | 44737.2042 | 49.9778
2022-06-25 | 3:54 | 49.981 | 44737.2042 | 49.9779
2022-06-25 | 3:54 | 49.979 | 44737.2042 | 49.978
2022-06-25 | 3:54 | 49.979 | 44737.2042 | 49.978
2022-06-25 | 3:54 | 49.977 | 44737.2042 | 49.9781
2022-06-25 | 3:54 | 49.977 | 44737.2042 | 49.9781
2022-06-25 | 3:54 | 49.975 | 44737.2042 | 49.9781
2022-06-25 | 3:54 | 49.978 | 44737.2042 | 49.9781
2022-06-25 | 3:54 | 49.976 | 44737.2042 | 49.978
2022-06-25 | 3:54 | 49.978 | 44737.2042 | 49.978
2022-06-25 | 3:54 | 49.978 | 44737.2042 | 49.978
2022-06-25 | 3:54 | 49.98 | 44737.2042 | 49.978
2022-06-25 | 3:54 | 49.979 | 44737.2042 | 49.978
2022-06-25 | 3:54 | 49.98 | 44737.2042 | 49.978
2022-06-25 | 3:55 | 49.982 | 44737.2042 | 49.978
2022-06-25 | 3:55 | 49.982 | 44737.2042 | 49.978
2022-06-25 | 3:55 | 49.982 | 44737.2042 | 49.9781
2022-06-25 | 3:55 | 49.982 | 44737.2042 | 49.9781
2022-06-25 | 3:55 | 49.981 | 44737.2042 | 49.9781
2022-06-25 | 3:55 | 49.978 | 44737.2042 | 49.9781
2022-06-25 | 3:55 | 49.959 | 44737.2042 | 49.9781
2022-06-25 | 3:55 | 49.93 | 44737.2042 | 49.9781
2022-06-25 | 3:55 | 49.911 | 44737.2042 | 49.9781
2022-06-25 | 3:55 | 49.903 | 44737.2042 | 49.9781
2022-06-25 | 3:55 | 49.902 | 44737.2042 | 49.9781
2022-06-25 | 3:55 | 49.904 | 44737.2042 | 49.978
2022-06-25 | 3:55 | 49.906 | 44737.2042 | 49.978
2022-06-25 | 3:55 | 49.907 | 44737.2042 | 49.978
2022-06-25 | 3:55 | 49.906 | 44737.2042 | 49.978
2022-06-25 | 3:55 | 49.905 | 44737.2042 | 49.978
2022-06-25 | 3:55 | 49.904 | 44737.2042 | 49.9781
2022-06-25 | 3:55 | 49.905 | 44737.2042 | 49.9781
2022-06-25 | 3:55 | 49.904 | 44737.2042 | 49.9781
2022-06-25 | 3:55 | 49.903 | 2022-06-25 04:54 | 49.9781
2022-06-25 | 3:55 | 49.901 | 44737.2042 | 49.9782
2022-06-25 | 3:55 | 49.899 | 44737.2042 | 49.9782
2022-06-25 | 3:55 | 49.898 | 44737.2042 | 49.9782
2022-06-25 | 3:55 | 49.898 | 44737.2042 | 49.9781
2022-06-25 | 3:55 | 49.897 | 44737.2042 | 49.9781
2022-06-25 | 3:55 | 49.899 | 44737.2042 | 49.9781
2022-06-25 | 3:55 | 49.899 | 44737.2042 | 49.9781
2022-06-25 | 3:55 | 49.898 | 44737.2042 | 49.9781
2022-06-25 | 3:55 | 49.897 | 44737.2042 | 49.9782
2022-06-25 | 3:55 | 49.897 | 44737.2042 | 49.9782
2022-06-25 | 3:55 | 49.894 | 44737.2042 | 49.9782
2022-06-25 | 3:55 | 49.889 | 44737.2042 | 49.9782
2022-06-25 | 3:55 | 49.888 | 44737.2042 | 49.9782
2022-06-25 | 3:55 | 49.886 | 44737.2042 | 49.9783
2022-06-25 | 3:55 | 49.885 | 44737.2042 | 49.9783
2022-06-25 | 3:55 | 49.888 | 44737.2042 | 49.9783
2022-06-25 | 3:55 | 49.889 | 44737.2042 | 49.9783
2022-06-25 | 3:55 | 49.891 | 44737.2042 | 49.9783
2022-06-25 | 3:55 | 49.893 | 44737.2042 | 49.9783
2022-06-25 | 3:55 | 49.896 | 44737.2042 | 49.9783
2022-06-25 | 3:55 | 49.894 | 44737.2042 | 49.9782
2022-06-25 | 3:55 | 49.894 | 44737.2042 | 49.9781
2022-06-25 | 3:55 | 49.892 | 44737.2042 | 49.9781
2022-06-25 | 3:55 | 49.891 | 44737.2042 | 49.9781
2022-06-25 | 3:55 | 49.882 | 44737.2042 | 49.978
2022-06-25 | 3:55 | 49.876 | 44737.2042 | 49.978
2022-06-25 | 3:55 | 49.865 | 44737.2042 | 49.978
2022-06-25 | 3:55 | 49.862 | 44737.2042 | 49.9779
2022-06-25 | 3:55 | 49.858 | 44737.2042 | 49.978
2022-06-25 | 3:55 | 49.86 | 44737.2042 | 49.978
2022-06-25 | 3:55 | 49.859 | 44737.2042 | 49.9781
2022-06-25 | 3:55 | 49.855 | 44737.2042 | 49.9781
2022-06-25 | 3:55 | 49.855 | 44737.2042 | 49.9781
2022-06-25 | 3:55 | 49.854 | 44737.2042 | 49.9782
2022-06-25 | 3:55 | 49.852 | 44737.2042 | 49.9782
2022-06-25 | 3:55 | 49.855 | 44737.2042 | 49.9782
2022-06-25 | 3:55 | 49.853 | 44737.2042 | 49.9782
2022-06-25 | 3:55 | 49.848 | 44737.2042 | 49.9782
2022-06-25 | 3:55 | 49.849 | 44737.2042 | 49.9782
2022-06-25 | 3:56 | 49.854 | 44737.2042 | 49.9781
2022-06-25 | 3:56 | 49.855 | 44737.2042 | 49.978
2022-06-25 | 3:56 | 49.854 | 44737.2042 | 49.978
2022-06-25 | 3:56 | 49.852 | 44737.2042 | 49.9779
2022-06-25 | 3:56 | 49.851 | 44737.2042 | 49.9778
2022-06-25 | 3:56 | 49.85 | 44737.2042 | 49.9778
2022-06-25 | 3:56 | 49.849 | 44737.2042 | 49.9777
2022-06-25 | 3:56 | 49.851 | 44737.2042 | 49.9777
2022-06-25 | 3:56 | 49.85 | 44737.2042 | 49.9776
2022-06-25 | 3:56 | 49.853 | 44737.2042 | 49.9776
2022-06-25 | 3:56 | 49.853 | 2022-06-25 04:54 | 49.9776
2022-06-25 | 3:56 | 49.855 | 44737.2042 | 49.9777
2022-06-25 | 3:56 | 49.854 | 44737.2042 | 49.9777
2022-06-25 | 3:56 | 49.857 | 44737.2042 | 49.9777
2022-06-25 | 3:56 | 49.858 | 44737.2042 | 49.9777
2022-06-25 | 3:56 | 49.857 | 44737.2042 | 49.9776
2022-06-25 | 3:56 | 49.856 | 44737.2042 | 49.9776
2022-06-25 | 3:56 | 49.855 | 44737.2042 | 49.9775
2022-06-25 | 3:56 | 49.854 | 44737.2042 | 49.9775
2022-06-25 | 3:56 | 49.856 | 44737.2042 | 49.9774
2022-06-25 | 3:56 | 49.856 | 44737.2042 | 49.9774
2022-06-25 | 3:56 | 49.857 | 44737.2042 | 49.9773
2022-06-25 | 3:56 | 49.857 | 44737.2042 | 49.9772
2022-06-25 | 3:56 | 49.857 | 44737.2042 | 49.9772
2022-06-25 | 3:56 | 49.856 | 44737.2042 | 49.9772
2022-06-25 | 3:56 | 49.857 | 44737.2042 | 49.9772
2022-06-25 | 3:56 | 49.856 | 44737.2042 | 49.9772
2022-06-25 | 3:56 | 49.855 | 44737.2042 | 49.9772
2022-06-25 | 3:56 | 49.855 | 44737.2042 | 49.9772
2022-06-25 | 3:56 | 49.854 | 44737.2042 | 49.9772
2022-06-25 | 3:56 | 49.853 | 44737.2042 | 49.9773
2022-06-25 | 3:56 | 49.853 | 44737.2042 | 49.9772
2022-06-25 | 3:56 | 49.854 | 44737.2042 | 49.9772
2022-06-25 | 3:56 | 49.856 | 44737.2042 | 49.9771
2022-06-25 | 3:56 | 49.857 | 44737.2042 | 49.977
2022-06-25 | 3:56 | 49.859 | 44737.2042 | 49.9769
2022-06-25 | 3:56 | 49.857 | 44737.2042 | 49.9767
2022-06-25 | 3:56 | 49.856 | 44737.2042 | 49.9766
2022-06-25 | 3:56 | 49.856 | 44737.2042 | 49.9765
2022-06-25 | 3:56 | 49.854 | 44737.2042 | 49.9765
2022-06-25 | 3:56 | 49.853 | 44737.2042 | 49.9765
2022-06-25 | 3:56 | 49.853 | 44737.2042 | 49.9766
2022-06-25 | 3:56 | 49.852 | 44737.2042 | 49.9766
2022-06-25 | 3:56 | 49.851 | 44737.2042 | 49.9767
2022-06-25 | 3:56 | 49.85 | 44737.2042 | 49.9767
2022-06-25 | 3:56 | 49.85 | 44737.2042 | 49.9768
2022-06-25 | 3:56 | 49.851 | 44737.2042 | 49.9767
2022-06-25 | 3:56 | 49.851 | 44737.2042 | 49.9767
2022-06-25 | 3:56 | 49.851 | 44737.2042 | 49.9766
2022-06-25 | 3:56 | 49.852 | 44737.2042 | 49.9765
2022-06-25 | 3:56 | 49.852 | 44737.2042 | 49.9763
2022-06-25 | 3:56 | 49.854 | 44737.2042 | 49.9762
2022-06-25 | 3:56 | 49.854 | 44737.2042 | 49.9761
2022-06-25 | 3:56 | 49.855 | 44737.2042 | 49.976
2022-06-25 | 3:56 | 49.856 | 44737.2042 | 49.9759
2022-06-25 | 3:56 | 49.858 | 44737.2042 | 49.9759
2022-06-25 | 3:56 | 49.858 | 44737.2042 | 49.9759
2022-06-25 | 3:56 | 49.859 | 44737.2042 | 49.9759
2022-06-25 | 3:56 | 49.86 | 44737.2042 | 49.9758
2022-06-25 | 3:56 | 49.861 | 44737.2042 | 49.9758
2022-06-25 | 3:56 | 49.865 | 2022-06-25 04:54 | 49.9757
2022-06-25 | 3:57 | 49.871 | 44737.2042 | 49.9757
2022-06-25 | 3:57 | 49.878 | 44737.2042 | 49.9756
2022-06-25 | 3:57 | 49.885 | 44737.2042 | 49.9755
2022-06-25 | 3:57 | 49.891 | 44737.2042 | 49.9755
2022-06-25 | 3:57 | 49.897 | 44737.2042 | 49.9754
2022-06-25 | 3:57 | 49.904 | 44737.2042 | 49.9754
2022-06-25 | 3:57 | 49.912 | 44737.2042 | 49.9753
2022-06-25 | 3:57 | 49.918 | 44737.2042 | 49.9753
2022-06-25 | 3:57 | 49.924 | 44737.2042 | 49.9753
2022-06-25 | 3:57 | 49.93 | 44737.2042 | 49.9752
2022-06-25 | 3:57 | 49.934 | 44737.2042 | 49.9752
2022-06-25 | 3:57 | 49.935 | 44737.2042 | 49.9752
2022-06-25 | 3:57 | 49.938 | 44737.2042 | 49.9751
2022-06-25 | 3:57 | 49.941 | 44737.2042 | 49.9749
2022-06-25 | 3:57 | 49.94 | 44737.2042 | 49.975
2022-06-25 | 3:57 | 49.939 | 44737.2042 | 49.9749
2022-06-25 | 3:57 | 49.938 | 44737.2042 | 49.9748
2022-06-25 | 3:57 | 49.938 | 44737.2042 | 49.9747
2022-06-25 | 3:57 | 49.938 | 44737.2042 | 49.9747
2022-06-25 | 3:57 | 49.935 | 44737.2042 | 49.9747
2022-06-25 | 3:57 | 49.932 | 44737.2042 | 49.9747
2022-06-25 | 3:57 | 49.929 | 44737.2042 | 49.9746
2022-06-25 | 3:57 | 49.927 | 44737.2042 | 49.9747
2022-06-25 | 3:57 | 49.928 | 44737.2042 | 49.9746
2022-06-25 | 3:57 | 49.93 | 44737.2042 | 49.9746
2022-06-25 | 3:57 | 49.931 | 44737.2042 | 49.9746
2022-06-25 | 3:57 | 49.931 | 44737.2042 | 49.9746
2022-06-25 | 3:57 | 49.929 | 44737.2042 | 49.9745
2022-06-25 | 3:57 | 49.93 | 44737.2042 | 49.9744
2022-06-25 | 3:57 | 49.93 | 44737.2042 | 49.9744
2022-06-25 | 3:57 | 49.933 | 44737.2042 | 49.9743
2022-06-25 | 3:57 | 49.937 | 44737.2042 | 49.9742
2022-06-25 | 3:57 | 49.943 | 44737.2042 | 49.9742
2022-06-25 | 3:57 | 49.948 | 44737.2042 | 49.9741
2022-06-25 | 3:57 | 49.95 | 44737.2042 | 49.9741
2022-06-25 | 3:57 | 49.951 | 44737.2042 | 49.9741
2022-06-25 | 3:57 | 49.954 | 44737.2042 | 49.9741
2022-06-25 | 3:57 | 49.955 | 44737.2042 | 49.9741
2022-06-25 | 3:57 | 49.958 | 44737.2042 | 49.9741
2022-06-25 | 3:57 | 49.958 | 44737.2042 | 49.9741
2022-06-25 | 3:57 | 49.96 | 44737.2042 | 49.9741
2022-06-25 | 3:57 | 49.958 | 44737.2042 | 49.9741
2022-06-25 | 3:57 | 49.957 | 44737.2042 | 49.974
2022-06-25 | 3:57 | 49.956 | 44737.2042 | 49.974
2022-06-25 | 3:57 | 49.954 | 44737.2042 | 49.974
2022-06-25 | 3:57 | 49.951 | 44737.2042 | 49.9739
2022-06-25 | 3:57 | 49.948 | 44737.2042 | 49.9739
2022-06-25 | 3:57 | 49.946 | 44737.2042 | 49.9738
2022-06-25 | 3:57 | 49.945 | 44737.2042 | 49.9738
2022-06-25 | 3:57 | 49.946 | 2022-06-25 04:54 | 49.9738
2022-06-25 | 3:57 | 49.948 | 44737.2042 | 49.9738
2022-06-25 | 3:57 | 49.95 | 44737.2042 | 49.9738
2022-06-25 | 3:57 | 49.951 | 44737.2042 | 49.9738
2022-06-25 | 3:57 | 49.952 | 44737.2042 | 49.9738
2022-06-25 | 3:57 | 49.954 | 44737.2042 | 49.9738
2022-06-25 | 3:57 | 49.955 | 44737.2042 | 49.9738
2022-06-25 | 3:57 | 49.954 | 44737.2042 | 49.9738
2022-06-25 | 3:57 | 49.953 | 44737.2042 | 49.9737
2022-06-25 | 3:57 | 49.953 | 44737.2042 | 49.9737
2022-06-25 | 3:58 | 49.953 | 44737.2042 | 49.9737
2022-06-25 | 3:58 | 49.951 | 44737.2042 | 49.9737
2022-06-25 | 3:58 | 49.952 | 44737.2042 | 49.9737
2022-06-25 | 3:58 | 49.952 | 44737.2042 | 49.9737
2022-06-25 | 3:58 | 49.95 | 44737.2042 | 49.9737
2022-06-25 | 3:58 | 49.949 | 44737.2042 | 49.9737
2022-06-25 | 3:58 | 49.948 | 44737.2042 | 49.9738
2022-06-25 | 3:58 | 49.948 | 44737.2042 | 49.9738
2022-06-25 | 3:58 | 49.947 | 44737.2042 | 49.9739
2022-06-25 | 3:58 | 49.947 | 44737.2042 | 49.9739
2022-06-25 | 3:58 | 49.945 | 44737.2042 | 49.9739
2022-06-25 | 3:58 | 49.945 | 44737.2042 | 49.9739
2022-06-25 | 3:58 | 49.948 | 44737.2042 | 49.9739
2022-06-25 | 3:58 | 49.948 | 44737.2042 | 49.9739
2022-06-25 | 3:58 | 49.95 | 44737.2042 | 49.9739
2022-06-25 | 3:58 | 49.952 | 44737.2042 | 49.9739
2022-06-25 | 3:58 | 49.951 | 44737.2042 | 49.9739
2022-06-25 | 3:58 | 49.954 | 44737.2042 | 49.9739
2022-06-25 | 3:58 | 49.956 | 44737.2042 | 49.9739
2022-06-25 | 3:58 | 49.957 | 44737.2042 | 49.9739
2022-06-25 | 3:58 | 49.958 | 44737.2042 | 49.9739
2022-06-25 | 3:58 | 49.957 | 44737.2042 | 49.9739
2022-06-25 | 3:58 | 49.957 | 44737.2042 | 49.974
2022-06-25 | 3:58 | 49.958 | 44737.2042 | 49.974
2022-06-25 | 3:58 | 49.959 | 44737.2042 | 49.974
2022-06-25 | 3:58 | 49.962 | 44737.2042 | 49.9741
2022-06-25 | 3:58 | 49.964 | 44737.2042 | 49.9741
2022-06-25 | 3:58 | 49.963 | 44737.2042 | 49.9741
2022-06-25 | 3:58 | 49.963 | 44737.2042 | 49.9741
2022-06-25 | 3:58 | 49.963 | 44737.2042 | 49.9741
2022-06-25 | 3:58 | 49.964 | 44737.2042 | 49.9741
2022-06-25 | 3:58 | 49.962 | 44737.2042 | 49.9742
2022-06-25 | 3:58 | 49.959 | 44737.2042 | 49.9742
2022-06-25 | 3:58 | 49.954 | 44737.2042 | 49.9743
2022-06-25 | 3:58 | 49.952 | 44737.2042 | 49.9743
2022-06-25 | 3:58 | 49.951 | 44737.2042 | 49.9744
2022-06-25 | 3:58 | 49.946 | 44737.2042 | 49.9744
2022-06-25 | 3:58 | 49.943 | 44737.2042 | 49.9743
2022-06-25 | 3:58 | 49.939 | 44737.2042 | 49.9743
2022-06-25 | 3:58 | 49.936 | 44737.2042 | 49.9743
2022-06-25 | 3:58 | 49.934 | 2022-06-25 04:54 | 49.9743
2022-06-25 | 3:58 | 49.933 | 44737.2042 | 49.9743
2022-06-25 | 3:58 | 49.934 | 44737.2042 | 49.9743
2022-06-25 | 3:58 | 49.936 | 44737.2042 | 49.9743
2022-06-25 | 3:58 | 49.935 | 44737.2042 | 49.9744
2022-06-25 | 3:58 | 49.937 | 44737.2042 | 49.9744
2022-06-25 | 3:58 | 49.936 | 44737.2042 | 49.9744
2022-06-25 | 3:58 | 49.933 | 44737.2042 | 49.9744
2022-06-25 | 3:58 | 49.931 | 44737.2042 | 49.9744
2022-06-25 | 3:58 | 49.932 | 44737.2042 | 49.9744
2022-06-25 | 3:58 | 49.933 | 44737.2042 | 49.9743
2022-06-25 | 3:58 | 49.933 | 44737.2042 | 49.9743
2022-06-25 | 3:58 | 49.933 | 44737.2042 | 49.9744
2022-06-25 | 3:58 | 49.937 | 44737.2042 | 49.9744
2022-06-25 | 3:58 | 49.937 | 44737.2042 | 49.9744
2022-06-25 | 3:58 | 49.942 | 44737.2042 | 49.9743
2022-06-25 | 3:58 | 49.941 | 44737.2042 | 49.9743
2022-06-25 | 3:58 | 49.946 | 44737.2042 | 49.9743
2022-06-25 | 3:58 | 49.945 | 44737.2042 | 49.9743
2022-06-25 | 3:58 | 49.946 | 44737.2042 | 49.9743
2022-06-25 | 3:58 | 49.945 | 44737.2042 | 49.9742
2022-06-25 | 3:59 | 49.942 | 44737.2042 | 49.9743
2022-06-25 | 3:59 | 49.941 | 44737.2042 | 49.9743
2022-06-25 | 3:59 | 49.942 | 44737.2042 | 49.9744
2022-06-25 | 3:59 | 49.942 | 44737.2042 | 49.9744
2022-06-25 | 3:59 | 49.942 | 44737.2042 | 49.9745
2022-06-25 | 3:59 | 49.942 | 44737.2042 | 49.9745
2022-06-25 | 3:59 | 49.938 | 44737.2042 | 49.9746
2022-06-25 | 3:59 | 49.937 | 44737.2042 | 49.9745
2022-06-25 | 3:59 | 49.936 | 44737.2042 | 49.9745
2022-06-25 | 3:59 | 49.937 | 44737.2042 | 49.9744
2022-06-25 | 3:59 | 49.936 | 44737.2042 | 49.9744
2022-06-25 | 3:59 | 49.938 | 44737.2042 | 49.9744
2022-06-25 | 3:59 | 49.936 | 44737.2042 | 49.9744
2022-06-25 | 3:59 | 49.939 | 44737.2042 | 49.9744
2022-06-25 | 3:59 | 49.938 | 44737.2042 | 49.9744
2022-06-25 | 3:59 | 49.939 | 44737.2042 | 49.9744
2022-06-25 | 3:59 | 49.939 | 44737.2042 | 49.9745
2022-06-25 | 3:59 | 49.94 | 44737.2042 | 49.9746
2022-06-25 | 3:59 | 49.941 | 44737.2042 | 49.9747
2022-06-25 | 3:59 | 49.941 | 44737.2042 | 49.9748
2022-06-25 | 3:59 | 49.94 | 44737.2042 | 49.9749
2022-06-25 | 3:59 | 49.94 | 44737.2042 | 49.975
2022-06-25 | 3:59 | 49.939 | 44737.2042 | 49.9751
2022-06-25 | 3:59 | 49.94 | 44737.2042 | 49.9752
2022-06-25 | 3:59 | 49.939 | 44737.2042 | 49.9752
2022-06-25 | 3:59 | 49.937 | 44737.2042 | 49.9753
2022-06-25 | 3:59 | 49.938 | 44737.2042 | 49.9753
2022-06-25 | 3:59 | 49.938 | 44737.2042 | 49.9753
2022-06-25 | 3:59 | 49.937 | 44737.2042 | 49.9753
2022-06-25 | 3:59 | 49.937 | 2022-06-25 04:54 | 49.9753
2022-06-25 | 3:59 | 49.935 | 44737.2042 | 49.9753
2022-06-25 | 3:59 | 49.933 | 44737.2042 | 49.9753
2022-06-25 | 3:59 | 49.933 | 44737.2042 | 49.9753
2022-06-25 | 3:59 | 49.934 | 44737.2042 | 49.9754
2022-06-25 | 3:59 | 49.936 | 44737.2042 | 49.9754
2022-06-25 | 3:59 | 49.937 | 44737.2042 | 49.9754
2022-06-25 | 3:59 | 49.939 | 44737.2042 | 49.9755
2022-06-25 | 3:59 | 49.94 | 44737.2042 | 49.9755
2022-06-25 | 3:59 | 49.939 | 44737.2042 | 49.9755
2022-06-25 | 3:59 | 49.937 | 44737.2042 | 49.9755
2022-06-25 | 3:59 | 49.937 | 44737.2042 | 49.9756
2022-06-25 | 3:59 | 49.936 | 44737.2042 | 49.9756
2022-06-25 | 3:59 | 49.937 | 44737.2042 | 49.9756
2022-06-25 | 3:59 | 49.937 | 44737.2042 | 49.9756
2022-06-25 | 3:59 | 49.936 | 44737.2042 | 49.9756
2022-06-25 | 3:59 | 49.937 | 44737.2042 | 49.9757
2022-06-25 | 3:59 | 49.934 | 44737.2042 | 49.9756
2022-06-25 | 3:59 | 49.935 | 44737.2042 | 49.9756
2022-06-25 | 3:59 | 49.933 | 44737.2042 | 49.9755
2022-06-25 | 3:59 | 49.933 | 44737.2042 | 49.9755
2022-06-25 | 3:59 | 49.933 | 44737.2042 | 49.9756
2022-06-25 | 3:59 | 49.932 | 44737.2042 | 49.9757
2022-06-25 | 3:59 | 49.931 | 44737.2042 | 49.9758
2022-06-25 | 3:59 | 49.932 | 44737.2042 | 49.9759
2022-06-25 | 3:59 | 49.932 | 44737.2042 | 49.9759
2022-06-25 | 3:59 | 49.931 | 44737.2042 | 49.9759
2022-06-25 | 3:59 | 49.933 | 44737.2042 | 49.9759
2022-06-25 | 3:59 | 49.931 | 44737.2042 | 49.976
2022-06-25 | 3:59 | 49.931 | 44737.2042 | 49.976
2022-06-25 | 3:59 | 49.932 | 44737.2042 | 49.976
2022-06-25 | 4:00 | 49.93 | 44737.2042 | 49.976
2022-06-25 | 4:00 | 49.929 | 44737.2042 | 49.9761
2022-06-25 | 4:00 | 49.93 | 44737.2042 | 49.9762
2022-06-25 | 4:00 | 49.93 | 44737.2042 | 49.9762
2022-06-25 | 4:00 | 49.927 | 44737.2042 | 49.9763
2022-06-25 | 4:00 | 49.927 | 44737.2042 | 49.9763
2022-06-25 | 4:00 | 49.927 | 44737.2042 | 49.9763
2022-06-25 | 4:00 | 49.925 | 44737.2042 | 49.9764
2022-06-25 | 4:00 | 49.924 | 44737.2042 | 49.9765
2022-06-25 | 4:00 | 49.922 | 44737.2042 | 49.9765
2022-06-25 | 4:00 | 49.921 | 44737.2042 | 49.9766
2022-06-25 | 4:00 | 49.922 | 44737.2042 | 49.9767
2022-06-25 | 4:00 | 49.92 | 44737.2042 | 49.9768
2022-06-25 | 4:00 | 49.923 | 44737.2042 | 49.9769
2022-06-25 | 4:00 | 49.922 | 44737.2042 | 49.977
2022-06-25 | 4:00 | 49.922 | 44737.2042 | 49.9771
2022-06-25 | 4:00 | 49.92 | 44737.2042 | 49.9771
2022-06-25 | 4:00 | 49.92 | 44737.2042 | 49.9771
2022-06-25 | 4:00 | 49.919 | 44737.2042 | 49.9772
2022-06-25 | 4:00 | 49.92 | 2022-06-25 04:54 | 49.9771
2022-06-25 | 4:00 | 49.92 | 44737.2042 | 49.9771
2022-06-25 | 4:00 | 49.92 | 44737.2042 | 49.9771
2022-06-25 | 4:00 | 49.919 | 44737.2042 | 49.9771
2022-06-25 | 4:00 | 49.921 | 44737.2042 | 49.9772
2022-06-25 | 4:00 | 49.922 | 44737.2042 | 49.9772
2022-06-25 | 4:00 | 49.919 | 44737.2042 | 49.9772
2022-06-25 | 4:00 | 49.92 | 44737.2042 | 49.9773
2022-06-25 | 4:00 | 49.919 | 44737.2042 | 49.9773
2022-06-25 | 4:00 | 49.916 | 44737.2042 | 49.9774
2022-06-25 | 4:00 | 49.915 | 44737.2043 | 49.9775
2022-06-25 | 4:00 | 49.91 | 44737.2043 | 49.9775
2022-06-25 | 4:00 | 49.904 | 44737.2043 | 49.9775
2022-06-25 | 4:00 | 49.9 | 44737.2043 | 49.9775
2022-06-25 | 4:00 | 49.898 | 44737.2043 | 49.9775
2022-06-25 | 4:00 | 49.896 | 44737.2043 | 49.9775
2022-06-25 | 4:00 | 49.895 | 44737.2043 | 49.9776
2022-06-25 | 4:00 | 49.895 | 44737.2043 | 49.9776
2022-06-25 | 4:00 | 49.894 | 44737.2043 | 49.9776
2022-06-25 | 4:00 | 49.895 | 44737.2043 | 49.9776
2022-06-25 | 4:00 | 49.895 | 44737.2043 | 49.9777
2022-06-25 | 4:00 | 49.896 | 44737.2043 | 49.9777
2022-06-25 | 4:00 | 49.896 | 44737.2043 | 49.9777
2022-06-25 | 4:00 | 49.9 | 44737.2043 | 49.9777
2022-06-25 | 4:00 | 49.901 | 44737.2043 | 49.9776
2022-06-25 | 4:00 | 49.902 | 44737.2043 | 49.9777
2022-06-25 | 4:00 | 49.906 | 44737.2043 | 49.9776
2022-06-25 | 4:00 | 49.906 | 44737.2043 | 49.9776
2022-06-25 | 4:00 | 49.908 | 44737.2043 | 49.9776
2022-06-25 | 4:00 | 49.909 | 44737.2043 | 49.9776
2022-06-25 | 4:00 | 49.912 | 44737.2043 | 49.9776
2022-06-25 | 4:00 | 49.912 | 44737.2043 | 49.9776
2022-06-25 | 4:00 | 49.91 | 44737.2043 | 49.9776
2022-06-25 | 4:00 | 49.909 | 44737.2043 | 49.9776
2022-06-25 | 4:00 | 49.909 | 44737.2043 | 49.9776
2022-06-25 | 4:00 | 49.907 | 44737.2043 | 49.9776
2022-06-25 | 4:00 | 49.905 | 44737.2043 | 49.9777
2022-06-25 | 4:00 | 49.904 | 44737.2043 | 49.9777
2022-06-25 | 4:00 | 49.904 | 44737.2043 | 49.9777
2022-06-25 | 4:00 | 49.903 | 44737.2043 | 49.9778
2022-06-25 | 4:01 | 49.903 | 44737.2043 | 49.9778
2022-06-25 | 4:01 | 49.902 | 44737.2043 | 49.9779
2022-06-25 | 4:01 | 49.9 | 44737.2043 | 49.978
2022-06-25 | 4:01 | 49.897 | 44737.2043 | 49.9781
2022-06-25 | 4:01 | 49.895 | 44737.2043 | 49.9782
2022-06-25 | 4:01 | 49.893 | 44737.2043 | 49.9783
2022-06-25 | 4:01 | 49.892 | 44737.2043 | 49.9783
2022-06-25 | 4:01 | 49.892 | 44737.2043 | 49.9783
2022-06-25 | 4:01 | 49.893 | 44737.2043 | 49.9783
2022-06-25 | 4:01 | 49.89 | 44737.2043 | 49.9783
2022-06-25 | 4:01 | 49.891 | 2022-06-25 04:54 | 49.9783
2022-06-25 | 4:01 | 49.891 | 44737.2043 | 49.9784
2022-06-25 | 4:01 | 49.889 | 44737.2043 | 49.9784
2022-06-25 | 4:01 | 49.885 | 44737.2043 | 49.9784
2022-06-25 | 4:01 | 49.886 | 44737.2043 | 49.9785
2022-06-25 | 4:01 | 49.883 | 44737.2043 | 49.9785
2022-06-25 | 4:01 | 49.882 | 44737.2043 | 49.9786
2022-06-25 | 4:01 | 49.881 | 44737.2043 | 49.9786
2022-06-25 | 4:01 | 49.879 | 44737.2043 | 49.9786
2022-06-25 | 4:01 | 49.879 | 44737.2043 | 49.9787
2022-06-25 | 4:01 | 49.878 | 44737.2043 | 49.9788
2022-06-25 | 4:01 | 49.879 | 44737.2043 | 49.9789
2022-06-25 | 4:01 | 49.88 | 44737.2043 | 49.9789
2022-06-25 | 4:01 | 49.88 | 44737.2043 | 49.9789
2022-06-25 | 4:01 | 49.88 | 44737.2043 | 49.979
2022-06-25 | 4:01 | 49.881 | 44737.2043 | 49.9791
2022-06-25 | 4:01 | 49.88 | 44737.2043 | 49.9791
2022-06-25 | 4:01 | 49.877 | 44737.2043 | 49.9791
2022-06-25 | 4:01 | 49.873 | 44737.2043 | 49.9792
2022-06-25 | 4:01 | 49.872 | 44737.2043 | 49.9792
2022-06-25 | 4:01 | 49.871 | 44737.2043 | 49.9792
2022-06-25 | 4:01 | 49.864 | 44737.2043 | 49.9792
2022-06-25 | 4:01 | 49.862 | 44737.2043 | 49.9792
2022-06-25 | 4:01 | 49.858 | 44737.2043 | 49.9792
2022-06-25 | 4:01 | 49.856 | 44737.2043 | 49.9792
2022-06-25 | 4:01 | 49.855 | 44737.2043 | 49.9793
2022-06-25 | 4:01 | 49.857 | 44737.2043 | 49.9793
2022-06-25 | 4:01 | 49.858 | 44737.2043 | 49.9793
2022-06-25 | 4:01 | 49.858 | 44737.2043 | 49.9794
2022-06-25 | 4:01 | 49.857 | 44737.2043 | 49.9795
2022-06-25 | 4:01 | 49.857 | 44737.2043 | 49.9796
2022-06-25 | 4:01 | 49.856 | 44737.2043 | 49.9797
2022-06-25 | 4:01 | 49.856 | 44737.2043 | 49.9797
2022-06-25 | 4:01 | 49.855 | 44737.2043 | 49.9798
2022-06-25 | 4:01 | 49.855 | 44737.2043 | 49.9798
2022-06-25 | 4:01 | 49.857 | 44737.2043 | 49.9798
2022-06-25 | 4:01 | 49.858 | 44737.2043 | 49.9798
2022-06-25 | 4:01 | 49.857 | 44737.2043 | 49.9798
2022-06-25 | 4:01 | 49.854 | 44737.2043 | 49.9798
2022-06-25 | 4:01 | 49.851 | 44737.2043 | 49.9798
2022-06-25 | 4:01 | 49.851 | 44737.2043 | 49.9798
2022-06-25 | 4:01 | 49.852 | 44737.2043 | 49.9798
2022-06-25 | 4:01 | 49.855 | 44737.2043 | 49.9798
2022-06-25 | 4:01 | 49.857 | 44737.2043 | 49.9798
2022-06-25 | 4:01 | 49.857 | 44737.2043 | 49.9798
2022-06-25 | 4:01 | 49.863 | 44737.2043 | 49.9799
2022-06-25 | 4:01 | 49.868 | 44737.2043 | 49.98
2022-06-25 | 4:01 | 49.871 | 44737.2043 | 49.9801
2022-06-25 | 4:01 | 49.873 | 44737.2043 | 49.9802
2022-06-25 | 4:01 | 49.874 | 44737.2043 | 49.9803
2022-06-25 | 4:01 | 49.875 | 2022-06-25 04:54 | 49.9803
2022-06-25 | 4:02 | 49.875 | 44737.2043 | 49.9804
2022-06-25 | 4:02 | 49.875 | 44737.2043 | 49.9805
2022-06-25 | 4:02 | 49.875 | 44737.2043 | 49.9805
2022-06-25 | 4:02 | 49.875 | 44737.2043 | 49.9805
2022-06-25 | 4:02 | 49.873 | 44737.2043 | 49.9805
2022-06-25 | 4:02 | 49.872 | 44737.2043 | 49.9806
2022-06-25 | 4:02 | 49.871 | 44737.2043 | 49.9806
2022-06-25 | 4:02 | 49.871 | 44737.2043 | 49.9806
2022-06-25 | 4:02 | 49.874 | 44737.2043 | 49.9807
2022-06-25 | 4:02 | 49.875 | 44737.2043 | 49.9808
2022-06-25 | 4:02 | 49.876 | 44737.2043 | 49.9809
2022-06-25 | 4:02 | 49.879 | 44737.2043 | 49.981
2022-06-25 | 4:02 | 49.878 | 44737.2043 | 49.9811
2022-06-25 | 4:02 | 49.877 | 44737.2043 | 49.9813
2022-06-25 | 4:02 | 49.875 | 44737.2043 | 49.9813
2022-06-25 | 4:02 | 49.875 | 44737.2043 | 49.9814
2022-06-25 | 4:02 | 49.877 | 44737.2043 | 49.9815
2022-06-25 | 4:02 | 49.876 | 44737.2043 | 49.9816
2022-06-25 | 4:02 | 49.877 | 44737.2043 | 49.9817
2022-06-25 | 4:02 | 49.877 | 44737.2043 | 49.9818
2022-06-25 | 4:02 | 49.876 | 44737.2043 | 49.9819
2022-06-25 | 4:02 | 49.875 | 44737.2043 | 49.9819
2022-06-25 | 4:02 | 49.874 | 44737.2043 | 49.982
2022-06-25 | 4:02 | 49.872 | 44737.2043 | 49.982
2022-06-25 | 4:02 | 49.87 | 44737.2043 | 49.982
2022-06-25 | 4:02 | 49.87 | 44737.2043 | 49.982
2022-06-25 | 4:02 | 49.87 | 44737.2043 | 49.982
2022-06-25 | 4:02 | 49.866 | 44737.2043 | 49.982
2022-06-25 | 4:02 | 49.863 | 44737.2043 | 49.982
2022-06-25 | 4:02 | 49.861 | 44737.2043 | 49.982
2022-06-25 | 4:02 | 49.86 | 44737.2043 | 49.9821
2022-06-25 | 4:02 | 49.858 | 44737.2043 | 49.9821
2022-06-25 | 4:02 | 49.858 | 44737.2043 | 49.9821
2022-06-25 | 4:02 | 49.86 | 44737.2043 | 49.9821
2022-06-25 | 4:02 | 49.858 | 44737.2043 | 49.982
2022-06-25 | 4:02 | 49.859 | 44737.2043 | 49.982
2022-06-25 | 4:02 | 49.859 | 44737.2043 | 49.982
2022-06-25 | 4:02 | 49.859 | 44737.2043 | 49.982
2022-06-25 | 4:02 | 49.857 | 44737.2043 | 49.9821
2022-06-25 | 4:02 | 49.858 | 44737.2043 | 49.9821
2022-06-25 | 4:02 | 49.856 | 44737.2043 | 49.9821
2022-06-25 | 4:02 | 49.855 | 44737.2043 | 49.9822
2022-06-25 | 4:02 | 49.856 | 44737.2043 | 49.9822
2022-06-25 | 4:02 | 49.856 | 44737.2043 | 49.9823
2022-06-25 | 4:02 | 49.857 | 44737.2043 | 49.9824
2022-06-25 | 4:02 | 49.857 | 44737.2043 | 49.9824
2022-06-25 | 4:02 | 49.857 | 44737.2043 | 49.9824
2022-06-25 | 4:02 | 49.859 | 44737.2043 | 49.9825
2022-06-25 | 4:02 | 49.858 | 44737.2043 | 49.9826
2022-06-25 | 4:02 | 49.859 | 2022-06-25 04:54 | 49.9826
2022-06-25 | 4:02 | 49.86 | 44737.2043 | 49.9827
2022-06-25 | 4:02 | 49.857 | 44737.2043 | 49.9827
2022-06-25 | 4:02 | 49.858 | 44737.2043 | 49.9828
2022-06-25 | 4:02 | 49.857 | 44737.2043 | 49.9828
2022-06-25 | 4:02 | 49.853 | 44737.2043 | 49.9828
2022-06-25 | 4:02 | 49.851 | 44737.2043 | 49.9829
2022-06-25 | 4:02 | 49.849 | 44737.2043 | 49.9829
2022-06-25 | 4:02 | 49.849 | 44737.2043 | 49.983
2022-06-25 | 4:02 | 49.847 | 44737.2043 | 49.983
2022-06-25 | 4:03 | 49.847 | 44737.2043 | 49.9831
2022-06-25 | 4:03 | 49.848 | 44737.2043 | 49.9831
2022-06-25 | 4:03 | 49.846 | 44737.2043 | 49.9832
2022-06-25 | 4:03 | 49.846 | 44737.2043 | 49.9833
2022-06-25 | 4:03 | 49.846 | 44737.2043 | 49.9834
2022-06-25 | 4:03 | 49.845 | 44737.2043 | 49.9836
2022-06-25 | 4:03 | 49.845 | 44737.2043 | 49.9837
2022-06-25 | 4:03 | 49.846 | 44737.2043 | 49.9838
2022-06-25 | 4:03 | 49.845 | 44737.2043 | 49.984
2022-06-25 | 4:03 | 49.844 | 44737.2043 | 49.9841
2022-06-25 | 4:03 | 49.843 | 44737.2043 | 49.9842
2022-06-25 | 4:03 | 49.841 | 44737.2043 | 49.9842
2022-06-25 | 4:03 | 49.838 | 44737.2043 | 49.9843
2022-06-25 | 4:03 | 49.835 | 44737.2043 | 49.9843
2022-06-25 | 4:03 | 49.832 | 44737.2043 | 49.9843
2022-06-25 | 4:03 | 49.83 | 44737.2043 | 49.9842
2022-06-25 | 4:03 | 49.829 | 44737.2043 | 49.9842
2022-06-25 | 4:03 | 49.836 | 44737.2043 | 49.9842
2022-06-25 | 4:03 | 49.838 | 44737.2043 | 49.9842
2022-06-25 | 4:03 | 49.843 | 44737.2043 | 49.9843
2022-06-25 | 4:03 | 49.844 | 44737.2043 | 49.9844
2022-06-25 | 4:03 | 49.846 | 44737.2043 | 49.9845
2022-06-25 | 4:03 | 49.845 | 44737.2043 | 49.9846
2022-06-25 | 4:03 | 49.845 | 44737.2043 | 49.9848
2022-06-25 | 4:03 | 49.843 | 44737.2043 | 49.9849
2022-06-25 | 4:03 | 49.843 | 44737.2043 | 49.985
2022-06-25 | 4:03 | 49.844 | 44737.2043 | 49.9851
2022-06-25 | 4:03 | 49.842 | 44737.2043 | 49.9851
2022-06-25 | 4:03 | 49.841 | 44737.2043 | 49.9851
2022-06-25 | 4:03 | 49.839 | 44737.2043 | 49.9852
2022-06-25 | 4:03 | 49.84 | 44737.2043 | 49.9852
2022-06-25 | 4:03 | 49.838 | 44737.2043 | 49.9851
2022-06-25 | 4:03 | 49.835 | 44737.2043 | 49.9851
2022-06-25 | 4:03 | 49.834 | 44737.2043 | 49.9852
2022-06-25 | 4:03 | 49.831 | 44737.2043 | 49.9852
2022-06-25 | 4:03 | 49.832 | 44737.2043 | 49.9852
2022-06-25 | 4:03 | 49.828 | 44737.2043 | 49.9852
2022-06-25 | 4:03 | 49.825 | 44737.2043 | 49.9852
2022-06-25 | 4:03 | 49.82 | 44737.2043 | 49.9852
2022-06-25 | 4:03 | 49.818 | 44737.2043 | 49.9852
2022-06-25 | 4:03 | 49.817 | 2022-06-25 04:54 | 49.9853
2022-06-25 | 4:03 | 49.816 | 44737.2043 | 49.9853
2022-06-25 | 4:03 | 49.815 | 44737.2043 | 49.9854
2022-06-25 | 4:03 | 49.815 | 44737.2043 | 49.9855
2022-06-25 | 4:03 | 49.817 | 44737.2043 | 49.9855
2022-06-25 | 4:03 | 49.817 | 44737.2043 | 49.9855
2022-06-25 | 4:03 | 49.819 | 44737.2043 | 49.9856
2022-06-25 | 4:03 | 49.821 | 44737.2043 | 49.9857
2022-06-25 | 4:03 | 49.823 | 44737.2043 | 49.9857
2022-06-25 | 4:03 | 49.823 | 44737.2043 | 49.9857
2022-06-25 | 4:03 | 49.826 | 44737.2043 | 49.9858
2022-06-25 | 4:03 | 49.826 | 44737.2043 | 49.9858
2022-06-25 | 4:03 | 49.827 | 44737.2043 | 49.9859
2022-06-25 | 4:03 | 49.825 | 44737.2043 | 49.9859
2022-06-25 | 4:03 | 49.824 | 44737.2043 | 49.986
2022-06-25 | 4:03 | 49.824 | 44737.2043 | 49.986
2022-06-25 | 4:03 | 49.824 | 44737.2043 | 49.986
2022-06-25 | 4:03 | 49.824 | 44737.2043 | 49.9861
2022-06-25 | 4:03 | 49.827 | 44737.2043 | 49.9861
2022-06-25 | 4:03 | 49.828 | 44737.2043 | 49.9862
2022-06-25 | 4:03 | 49.831 | 44737.2043 | 49.9862
2022-06-25 | 4:04 | 49.838 | 44737.2043 | 49.9863
2022-06-25 | 4:04 | 49.842 | 44737.2043 | 49.9863
2022-06-25 | 4:04 | 49.851 | 44737.2043 | 49.9864
2022-06-25 | 4:04 | 49.858 | 44737.2043 | 49.9864
2022-06-25 | 4:04 | 49.864 | 44737.2043 | 49.9865
2022-06-25 | 4:04 | 49.872 | 44737.2043 | 49.9865
2022-06-25 | 4:04 | 49.883 | 44737.2043 | 49.9866
2022-06-25 | 4:04 | 49.895 | 44737.2043 | 49.9867
2022-06-25 | 4:04 | 49.905 | 44737.2043 | 49.9867
2022-06-25 | 4:04 | 49.911 | 44737.2043 | 49.9868
2022-06-25 | 4:04 | 49.917 | 44737.2043 | 49.9868
2022-06-25 | 4:04 | 49.921 | 44737.2043 | 49.9868
2022-06-25 | 4:04 | 49.92 | 44737.2043 | 49.9868
2022-06-25 | 4:04 | 49.921 | 44737.2043 | 49.9868
2022-06-25 | 4:04 | 49.925 | 44737.2043 | 49.9869
2022-06-25 | 4:04 | 49.927 | 44737.2043 | 49.987
2022-06-25 | 4:04 | 49.929 | 44737.2043 | 49.987
2022-06-25 | 4:04 | 49.932 | 44737.2043 | 49.987
2022-06-25 | 4:04 | 49.933 | 44737.2043 | 49.9871
2022-06-25 | 4:04 | 49.933 | 44737.2043 | 49.9871
2022-06-25 | 4:04 | 49.934 | 44737.2043 | 49.9872
2022-06-25 | 4:04 | 49.932 | 44737.2043 | 49.9873
2022-06-25 | 4:04 | 49.932 | 44737.2043 | 49.9873
2022-06-25 | 4:04 | 49.931 | 44737.2043 | 49.9873
2022-06-25 | 4:04 | 49.928 | 44737.2043 | 49.9874
2022-06-25 | 4:04 | 49.927 | 44737.2043 | 49.9873
2022-06-25 | 4:04 | 49.926 | 44737.2043 | 49.9873
2022-06-25 | 4:04 | 49.926 | 44737.2043 | 49.9873
2022-06-25 | 4:04 | 49.926 | 44737.2043 | 49.9873
2022-06-25 | 4:04 | 49.927 | 2022-06-25 04:54 | 49.9873
2022-06-25 | 4:04 | 49.928 | 44737.2043 | 49.9872
2022-06-25 | 4:04 | 49.931 | 44737.2043 | 49.9871
2022-06-25 | 4:04 | 49.933 | 44737.2043 | 49.9871
2022-06-25 | 4:04 | 49.934 | 44737.2043 | 49.9871
2022-06-25 | 4:04 | 49.936 | 44737.2043 | 49.9871
2022-06-25 | 4:04 | 49.938 | 44737.2043 | 49.9871
2022-06-25 | 4:04 | 49.938 | 44737.2043 | 49.9871
2022-06-25 | 4:04 | 49.94 | 44737.2043 | 49.9871
2022-06-25 | 4:04 | 49.939 | 44737.2043 | 49.9872
2022-06-25 | 4:04 | 49.941 | 44737.2043 | 49.9872
2022-06-25 | 4:04 | 49.941 | 44737.2043 | 49.9872
2022-06-25 | 4:04 | 49.942 | 44737.2043 | 49.9872
2022-06-25 | 4:04 | 49.942 | 44737.2043 | 49.9872
2022-06-25 | 4:04 | 49.943 | 44737.2043 | 49.9872
2022-06-25 | 4:04 | 49.944 | 44737.2043 | 49.9872
2022-06-25 | 4:04 | 49.946 | 44737.2043 | 49.9871
2022-06-25 | 4:04 | 49.947 | 44737.2043 | 49.9871
2022-06-25 | 4:04 | 49.95 | 44737.2043 | 49.987
2022-06-25 | 4:04 | 49.954 | 44737.2043 | 49.987
2022-06-25 | 4:04 | 49.953 | 44737.2043 | 49.987
2022-06-25 | 4:04 | 49.951 | 44737.2043 | 49.9869
2022-06-25 | 4:04 | 49.951 | 44737.2043 | 49.9869
2022-06-25 | 4:04 | 49.95 | 44737.2043 | 49.9869
2022-06-25 | 4:04 | 49.948 | 44737.2043 | 49.9869
2022-06-25 | 4:04 | 49.947 | 44737.2043 | 49.9868
2022-06-25 | 4:04 | 49.947 | 44737.2043 | 49.9868
2022-06-25 | 4:04 | 49.947 | 44737.2043 | 49.9868
2022-06-25 | 4:04 | 49.949 | 44737.2043 | 49.9868
2022-06-25 | 4:04 | 49.949 | 44737.2043 | 49.9867
2022-06-25 | 4:05 | 49.952 | 44737.2043 | 49.9867
2022-06-25 | 4:05 | 49.952 | 44737.2043 | 49.9866
2022-06-25 | 4:05 | 49.953 | 44737.2043 | 49.9866
2022-06-25 | 4:05 | 49.954 | 44737.2043 | 49.9867
2022-06-25 | 4:05 | 49.955 | 44737.2043 | 49.9867
2022-06-25 | 4:05 | 49.958 | 44737.2043 | 49.9867
2022-06-25 | 4:05 | 49.958 | 44737.2043 | 49.9868
2022-06-25 | 4:05 | 49.96 | 44737.2043 | 49.9868
2022-06-25 | 4:05 | 49.96 | 44737.2043 | 49.9867
2022-06-25 | 4:05 | 49.959 | 44737.2043 | 49.9867
2022-06-25 | 4:05 | 49.961 | 44737.2043 | 49.9867
2022-06-25 | 4:05 | 49.958 | 44737.2043 | 49.9866
2022-06-25 | 4:05 | 49.96 | 44737.2043 | 49.9865
2022-06-25 | 4:05 | 49.957 | 44737.2043 | 49.9865
2022-06-25 | 4:05 | 49.956 | 44737.2043 | 49.9864
2022-06-25 | 4:05 | 49.956 | 44737.2043 | 49.9864
2022-06-25 | 4:05 | 49.956 | 44737.2043 | 49.9864
2022-06-25 | 4:05 | 49.955 | 44737.2043 | 49.9864
2022-06-25 | 4:05 | 49.956 | 44737.2043 | 49.9865
2022-06-25 | 4:05 | 49.957 | 44737.2043 | 49.9865
2022-06-25 | 4:05 | 49.957 | 2022-06-25 04:54 | 49.9865
2022-06-25 | 4:05 | 49.956 | 44737.2043 | 49.9865
2022-06-25 | 4:05 | 49.956 | 44737.2043 | 49.9865
2022-06-25 | 4:05 | 49.957 | 44737.2043 | 49.9865
2022-06-25 | 4:05 | 49.958 | 44737.2043 | 49.9864
2022-06-25 | 4:05 | 49.958 | 44737.2043 | 49.9863
2022-06-25 | 4:05 | 49.959 | 44737.2043 | 49.9863
2022-06-25 | 4:05 | 49.96 | 44737.2043 | 49.9862
2022-06-25 | 4:05 | 49.96 | 44737.2043 | 49.9863
2022-06-25 | 4:05 | 49.961 | 44737.2043 | 49.9863
2022-06-25 | 4:05 | 49.962 | 44737.2043 | 49.9862
2022-06-25 | 4:05 | 49.961 | 44737.2043 | 49.9863
2022-06-25 | 4:05 | 49.962 | 44737.2043 | 49.9863
2022-06-25 | 4:05 | 49.962 | 44737.2043 | 49.9863
2022-06-25 | 4:05 | 49.964 | 44737.2043 | 49.9863
2022-06-25 | 4:05 | 49.966 | 44737.2043 | 49.9863
2022-06-25 | 4:05 | 49.967 | 44737.2043 | 49.9863
2022-06-25 | 4:05 | 49.97 | 44737.2043 | 49.9863
2022-06-25 | 4:05 | 49.971 | 44737.2043 | 49.9862
2022-06-25 | 4:05 | 49.97 | 44737.2043 | 49.9862
2022-06-25 | 4:05 | 49.97 | 44737.2043 | 49.9862
2022-06-25 | 4:05 | 49.97 | 44737.2043 | 49.9862
2022-06-25 | 4:05 | 49.969 | 44737.2043 | 49.9862
2022-06-25 | 4:05 | 49.972 | 44737.2043 | 49.9861
2022-06-25 | 4:05 | 49.973 | 44737.2043 | 49.9861
2022-06-25 | 4:05 | 49.974 | 44737.2043 | 49.9861
2022-06-25 | 4:05 | 49.975 | 44737.2043 | 49.9861
2022-06-25 | 4:05 | 49.978 | 44737.2043 | 49.9861
2022-06-25 | 4:05 | 49.982 | 44737.2043 | 49.9861
2022-06-25 | 4:05 | 49.985 | 44737.2043 | 49.9861
2022-06-25 | 4:05 | 49.985 | 44737.2043 | 49.9861
2022-06-25 | 4:05 | 49.987 | 44737.2043 | 49.9861
2022-06-25 | 4:05 | 49.991 | 44737.2043 | 49.9861
2022-06-25 | 4:05 | 49.992 | 44737.2043 | 49.9861
2022-06-25 | 4:05 | 49.993 | 44737.2043 | 49.9861
2022-06-25 | 4:05 | 49.994 | 44737.2043 | 49.986
2022-06-25 | 4:05 | 49.997 | 44737.2043 | 49.986
2022-06-25 | 4:05 | 50.001 | 44737.2043 | 49.9859
2022-06-25 | 4:05 | 50.002 | 44737.2043 | 49.9859
2022-06-25 | 4:05 | 50.004 | 44737.2043 | 49.9858
2022-06-25 | 4:05 | 50.006 | 44737.2043 | 49.9858
2022-06-25 | 4:06 | 50.006 | 44737.2043 | 49.9857
2022-06-25 | 4:06 | 50.01 | 44737.2043 | 49.9857
2022-06-25 | 4:06 | 50.013 | 44737.2043 | 49.9858
2022-06-25 | 4:06 | 50.016 | 44737.2043 | 49.9858
2022-06-25 | 4:06 | 50.018 | 44737.2043 | 49.9858
2022-06-25 | 4:06 | 50.019 | 44737.2043 | 49.9859
2022-06-25 | 4:06 | 50.019 | 44737.2043 | 49.9858
2022-06-25 | 4:06 | 50.022 | 44737.2043 | 49.9858
2022-06-25 | 4:06 | 50.019 | 44737.2043 | 49.9858
2022-06-25 | 4:06 | 50.019 | 2022-06-25 04:54 | 49.9858
2022-06-25 | 4:06 | 50.02 | 44737.2043 | 49.9857
2022-06-25 | 4:06 | 50.018 | 44737.2043 | 49.9857
2022-06-25 | 4:06 | 50.017 | 44737.2043 | 49.9857
2022-06-25 | 4:06 | 50.016 | 44737.2043 | 49.9856
2022-06-25 | 4:06 | 50.015 | 44737.2043 | 49.9856
2022-06-25 | 4:06 | 50.013 | 44737.2043 | 49.9856
2022-06-25 | 4:06 | 50.011 | 44737.2043 | 49.9855
2022-06-25 | 4:06 | 50.01 | 44737.2043 | 49.9855
2022-06-25 | 4:06 | 50.011 | 44737.2043 | 49.9854
2022-06-25 | 4:06 | 50.012 | 44737.2043 | 49.9854
2022-06-25 | 4:06 | 50.012 | 44737.2043 | 49.9853
2022-06-25 | 4:06 | 50.013 | 44737.2043 | 49.9853
2022-06-25 | 4:06 | 50.014 | 44737.2043 | 49.9853
2022-06-25 | 4:06 | 50.011 | 44737.2043 | 49.9853
2022-06-25 | 4:06 | 50.01 | 44737.2043 | 49.9853
2022-06-25 | 4:06 | 50.011 | 44737.2043 | 49.9853
2022-06-25 | 4:06 | 50.012 | 44737.2043 | 49.9853
2022-06-25 | 4:06 | 50.013 | 44737.2043 | 49.9853
2022-06-25 | 4:06 | 50.012 | 44737.2043 | 49.9853
2022-06-25 | 4:06 | 50.014 | 44737.2043 | 49.9852
|  |  | 44737.2043 | 49.9852
|  |  | 44737.2043 | 49.9852
|  |  | 44737.2043 | 49.9851
|  |  | 44737.2043 | 49.985
|  |  | 44737.2043 | 49.985
|  |  | 44737.2043 | 49.9849
|  |  | 44737.2043 | 49.9849
|  |  | 44737.2043 | 49.9849
|  |  | 44737.2043 | 49.9849
|  |  | 44737.2043 | 49.9849
|  |  | 44737.2043 | 49.9849
|  |  | 44737.2043 | 49.9849
|  |  | 44737.2043 | 49.9849
|  |  | 44737.2043 | 49.9848
|  |  | 44737.2043 | 49.9848
|  |  | 44737.2043 | 49.9848
|  |  | 44737.2043 | 49.9848
|  |  | 44737.2043 | 49.9848
|  |  | 44737.2043 | 49.9849
|  |  | 44737.2043 | 49.9849
|  |  | 44737.2043 | 49.9849
|  |  | 44737.2043 | 49.985
|  |  | 44737.2043 | 49.985
|  |  | 44737.2043 | 49.985
|  |  | 44737.2043 | 49.985
|  |  | 44737.2043 | 49.985
|  |  | 44737.2043 | 49.985
|  |  | 44737.2043 | 49.985
|  |  | 44737.2043 | 49.985
|  |  | 2022-06-25 04:54 | 49.985
|  |  | 44737.2043 | 49.9849
|  |  | 44737.2043 | 49.9849
|  |  | 44737.2043 | 49.9849
|  |  | 44737.2043 | 49.9849
|  |  | 44737.2043 | 49.9849
|  |  | 44737.2043 | 49.9849
|  |  | 44737.2043 | 49.9848
|  |  | 44737.2043 | 49.9848
|  |  | 44737.2043 | 49.9848
|  |  | 44737.2043 | 49.9848
|  |  | 44737.2043 | 49.9847
|  |  | 44737.2043 | 49.9847
|  |  | 44737.2043 | 49.9847
|  |  | 44737.2043 | 49.9847
|  |  | 44737.2043 | 49.9847
|  |  | 44737.2043 | 49.9847
|  |  | 44737.2043 | 49.9847
|  |  | 44737.2043 | 49.9847
|  |  | 44737.2043 | 49.9848
|  |  | 44737.2043 | 49.9847
|  |  | 44737.2043 | 49.9846
|  |  | 44737.2043 | 49.9846
|  |  | 44737.2043 | 49.9845
|  |  | 44737.2043 | 49.9845
|  |  | 44737.2043 | 49.9845
|  |  | 44737.2043 | 49.9845
|  |  | 44737.2043 | 49.9844
|  |  | 44737.2043 | 49.9844
|  |  | 44737.2043 | 49.9845
|  |  | 44737.2043 | 49.9844
|  |  | 44737.2043 | 49.9844
|  |  | 44737.2043 | 49.9844
|  |  | 44737.2043 | 49.9844
|  |  | 44737.2043 | 49.9843
|  |  | 44737.2043 | 49.9843
|  |  | 44737.2043 | 49.9842
|  |  | 44737.2043 | 49.9842
|  |  | 44737.2043 | 49.9841
|  |  | 44737.2043 | 49.9841
|  |  | 44737.2043 | 49.9841
|  |  | 44737.2043 | 49.9841
|  |  | 44737.2043 | 49.9842
|  |  | 44737.2044 | 49.9842
|  |  | 44737.2044 | 49.9843
|  |  | 44737.2044 | 49.9843
|  |  | 44737.2044 | 49.9843
|  |  | 44737.2044 | 49.9844
|  |  | 44737.2044 | 49.9844
|  |  | 44737.2044 | 49.9844
|  |  | 2022-06-25 04:54 | 49.9845
|  |  | 44737.2044 | 49.9845
|  |  | 44737.2044 | 49.9845
|  |  | 44737.2044 | 49.9845
|  |  | 44737.2044 | 49.9845
|  |  | 44737.2044 | 49.9845
|  |  | 44737.2044 | 49.9844
|  |  | 44737.2044 | 49.9843
|  |  | 44737.2044 | 49.9843
|  |  | 44737.2044 | 49.9843
|  |  | 44737.2044 | 49.9842
|  |  | 44737.2044 | 49.9842
|  |  | 44737.2044 | 49.9842
|  |  | 44737.2044 | 49.9841
|  |  | 44737.2044 | 49.9841
|  |  | 44737.2044 | 49.9841
|  |  | 44737.2044 | 49.9841
|  |  | 44737.2044 | 49.984
|  |  | 44737.2044 | 49.984
|  |  | 44737.2044 | 49.984
|  |  | 44737.2044 | 49.9839
|  |  | 44737.2044 | 49.9839
|  |  | 44737.2044 | 49.9839
|  |  | 44737.2044 | 49.9839
|  |  | 44737.2044 | 49.9839
|  |  | 44737.2044 | 49.9839
|  |  | 44737.2044 | 49.9838
|  |  | 44737.2044 | 49.9838
|  |  | 44737.2044 | 49.9838
|  |  | 44737.2044 | 49.9837
|  |  | 44737.2044 | 49.9837
|  |  | 44737.2044 | 49.9836
|  |  | 44737.2044 | 49.9836
|  |  | 44737.2044 | 49.9836
|  |  | 44737.2044 | 49.9835
|  |  | 44737.2044 | 49.9835
|  |  | 44737.2044 | 49.9835
|  |  | 44737.2044 | 49.9835
|  |  | 44737.2044 | 49.9835
|  |  | 44737.2044 | 49.9835
|  |  | 44737.2044 | 49.9835
|  |  | 44737.2044 | 49.9835
|  |  | 44737.2044 | 49.9835
|  |  | 44737.2044 | 49.9835
|  |  | 44737.2044 | 49.9836
|  |  | 44737.2044 | 49.9836
|  |  | 44737.2044 | 49.9835
|  |  | 44737.2044 | 49.9835
|  |  | 44737.2044 | 49.9835
|  |  | 44737.2044 | 49.9834
|  |  | 2022-06-25 04:54 | 49.9834
|  |  | 44737.2044 | 49.9833
|  |  | 44737.2044 | 49.9833
|  |  | 44737.2044 | 49.9833
|  |  | 44737.2044 | 49.9832
|  |  | 44737.2044 | 49.9832
|  |  | 44737.2044 | 49.9832
|  |  | 44737.2044 | 49.9832
|  |  | 44737.2044 | 49.9831
|  |  | 44737.2044 | 49.9831
|  |  | 44737.2044 | 49.983
|  |  | 44737.2044 | 49.983
|  |  | 44737.2044 | 49.9829
|  |  | 44737.2044 | 49.9828
|  |  | 44737.2044 | 49.9827
|  |  | 44737.2044 | 49.9827
|  |  | 44737.2044 | 49.9826
|  |  | 44737.2044 | 49.9826
|  |  | 44737.2044 | 49.9825
|  |  | 44737.2044 | 49.9825
|  |  | 44737.2044 | 49.9825
|  |  | 44737.2044 | 49.9824
|  |  | 44737.2044 | 49.9824
|  |  | 44737.2044 | 49.9823
|  |  | 44737.2044 | 49.9822
|  |  | 44737.2044 | 49.9821
|  |  | 44737.2044 | 49.9821
|  |  | 44737.2044 | 49.982
|  |  | 44737.2044 | 49.982
|  |  | 44737.2044 | 49.9819
|  |  | 44737.2044 | 49.9819
|  |  | 44737.2044 | 49.9818
|  |  | 44737.2044 | 49.9818
|  |  | 44737.2044 | 49.9817
|  |  | 44737.2044 | 49.9816
|  |  | 44737.2044 | 49.9815
|  |  | 44737.2044 | 49.9815
|  |  | 44737.2044 | 49.9813
|  |  | 44737.2044 | 49.9813
|  |  | 44737.2044 | 49.9812
|  |  | 44737.2044 | 49.9812
|  |  | 44737.2044 | 49.9812
|  |  | 44737.2044 | 49.9813
|  |  | 44737.2044 | 49.9813
|  |  | 44737.2044 | 49.9813
|  |  | 44737.2044 | 49.9813
|  |  | 44737.2044 | 49.9814
|  |  | 44737.2044 | 49.9814
|  |  | 44737.2044 | 49.9814
|  |  | 44737.2044 | 49.9814
|  |  | 2022-06-25 04:54 | 49.9814
|  |  | 44737.2044 | 49.9813
|  |  | 44737.2044 | 49.9813
|  |  | 44737.2044 | 49.9812
|  |  | 44737.2044 | 49.9811
|  |  | 44737.2044 | 49.9811
|  |  | 44737.2044 | 49.9811
|  |  | 44737.2044 | 49.9811
|  |  | 44737.2044 | 49.9811
|  |  | 44737.2044 | 49.9811
|  |  | 44737.2044 | 49.9811
|  |  | 44737.2044 | 49.9811
|  |  | 44737.2044 | 49.9811
|  |  | 44737.2044 | 49.9811
|  |  | 44737.2044 | 49.9811
|  |  | 44737.2044 | 49.981
|  |  | 44737.2044 | 49.981
|  |  | 44737.2044 | 49.9809
|  |  | 44737.2044 | 49.9808
|  |  | 44737.2044 | 49.9808
|  |  | 44737.2044 | 49.9807
|  |  | 44737.2044 | 49.9807
|  |  | 44737.2044 | 49.9807
|  |  | 44737.2044 | 49.9806
|  |  | 44737.2044 | 49.9806
|  |  | 44737.2044 | 49.9806
|  |  | 44737.2044 | 49.9805
|  |  | 44737.2044 | 49.9805
|  |  | 44737.2044 | 49.9805
|  |  | 44737.2044 | 49.9805
|  |  | 44737.2044 | 49.9806
|  |  | 44737.2044 | 49.9806
|  |  | 44737.2044 | 49.9806
|  |  | 44737.2044 | 49.9806
|  |  | 44737.2044 | 49.9806
|  |  | 44737.2044 | 49.9806
|  |  | 44737.2044 | 49.9805
|  |  | 44737.2044 | 49.9805
|  |  | 44737.2044 | 49.9805
|  |  | 44737.2044 | 49.9804
|  |  | 44737.2044 | 49.9803
|  |  | 44737.2044 | 49.9803
|  |  | 44737.2044 | 49.9802
|  |  | 44737.2044 | 49.9802
|  |  | 44737.2044 | 49.9801
|  |  | 44737.2044 | 49.9801
|  |  | 44737.2044 | 49.9801
|  |  | 44737.2044 | 49.9801
|  |  | 44737.2044 | 49.9801
|  |  | 44737.2044 | 49.9801
|  |  | 2022-06-25 04:54 | 49.9802
|  |  | 44737.2044 | 49.9802
|  |  | 44737.2044 | 49.9801
|  |  | 44737.2044 | 49.9802
|  |  | 44737.2044 | 49.9802
|  |  | 44737.2044 | 49.9802
|  |  | 44737.2044 | 49.9802
|  |  | 44737.2044 | 49.9802
|  |  | 44737.2044 | 49.9802
|  |  | 44737.2044 | 49.9803
|  |  | 44737.2044 | 49.9802
|  |  | 44737.2044 | 49.9802
|  |  | 44737.2044 | 49.9801
|  |  | 44737.2044 | 49.98
|  |  | 44737.2044 | 49.98
|  |  | 44737.2044 | 49.98
|  |  | 44737.2044 | 49.98
|  |  | 44737.2044 | 49.9799
|  |  | 44737.2044 | 49.9799
|  |  | 44737.2044 | 49.9799
|  |  | 44737.2044 | 49.9798
|  |  | 44737.2044 | 49.9797
|  |  | 44737.2044 | 49.9797
|  |  | 44737.2044 | 49.9796
|  |  | 44737.2044 | 49.9795
|  |  | 44737.2044 | 49.9794
|  |  | 44737.2044 | 49.9794
|  |  | 44737.2044 | 49.9793
|  |  | 44737.2044 | 49.9793
|  |  | 44737.2044 | 49.9793
|  |  | 44737.2044 | 49.9793
|  |  | 44737.2044 | 49.9793
|  |  | 44737.2044 | 49.9794
|  |  | 44737.2044 | 49.9793
|  |  | 44737.2044 | 49.9793
|  |  | 44737.2044 | 49.9793
|  |  | 44737.2044 | 49.9793
|  |  | 44737.2044 | 49.9792
|  |  | 44737.2044 | 49.9792
|  |  | 44737.2044 | 49.9791
|  |  | 44737.2044 | 49.9789
|  |  | 44737.2044 | 49.9788
|  |  | 44737.2044 | 49.9788
|  |  | 44737.2044 | 49.9788
|  |  | 44737.2044 | 49.9788
|  |  | 44737.2044 | 49.9789
|  |  | 44737.2044 | 49.9789
|  |  | 44737.2044 | 49.9789
|  |  | 44737.2044 | 49.979
|  |  | 44737.2044 | 49.979
|  |  | 2022-06-25 04:54 | 49.979
|  |  | 44737.2044 | 49.979
|  |  | 44737.2044 | 49.979
|  |  | 44737.2044 | 49.9789
|  |  | 44737.2044 | 49.9788
|  |  | 44737.2044 | 49.9787
|  |  | 44737.2044 | 49.9787
|  |  | 44737.2044 | 49.9786
|  |  | 44737.2044 | 49.9785
|  |  | 44737.2044 | 49.9785
|  |  | 44737.2044 | 49.9784
|  |  | 44737.2044 | 49.9784
|  |  | 44737.2044 | 49.9783
|  |  | 44737.2044 | 49.9784
|  |  | 44737.2044 | 49.9784
|  |  | 44737.2044 | 49.9784
|  |  | 44737.2044 | 49.9784
|  |  | 44737.2044 | 49.9785
|  |  | 44737.2044 | 49.9785
|  |  | 44737.2044 | 49.9785
|  |  | 44737.2044 | 49.9785
|  |  | 44737.2044 | 49.9784
|  |  | 44737.2044 | 49.9784
|  |  | 44737.2044 | 49.9783
|  |  | 44737.2044 | 49.9782
|  |  | 44737.2044 | 49.9782
|  |  | 44737.2044 | 49.9781
|  |  | 44737.2044 | 49.9781
|  |  | 44737.2044 | 49.9781
|  |  | 44737.2044 | 49.9781
|  |  | 44737.2044 | 49.9781
|  |  | 44737.2044 | 49.9781
|  |  | 44737.2044 | 49.9781
|  |  | 44737.2044 | 49.9782
|  |  | 44737.2044 | 49.9782
|  |  | 44737.2044 | 49.9782
|  |  | 44737.2044 | 49.9782
|  |  | 44737.2044 | 49.9782
|  |  | 44737.2044 | 49.978
|  |  | 44737.2044 | 49.9779
|  |  | 44737.2044 | 49.9778
|  |  | 44737.2044 | 49.9777
|  |  | 44737.2044 | 49.9777
|  |  | 44737.2044 | 49.9776
|  |  | 44737.2044 | 49.9776
|  |  | 44737.2044 | 49.9776
|  |  | 44737.2044 | 49.9776
|  |  | 44737.2044 | 49.9776
|  |  | 44737.2044 | 49.9777
|  |  | 44737.2044 | 49.9778
|  |  | 2022-06-25 04:54 | 49.9779
|  |  | 44737.2044 | 49.978
|  |  | 44737.2044 | 49.978
|  |  | 44737.2044 | 49.978
|  |  | 44737.2044 | 49.978
|  |  | 44737.2044 | 49.978
|  |  | 44737.2044 | 49.978
|  |  | 44737.2044 | 49.9779
|  |  | 44737.2044 | 49.9779
|  |  | 44737.2044 | 49.9778
|  |  | 44737.2044 | 49.9777
|  |  | 44737.2044 | 49.9777
|  |  | 44737.2044 | 49.9776
|  |  | 44737.2044 | 49.9776
|  |  | 44737.2044 | 49.9776
|  |  | 44737.2044 | 49.9775
|  |  | 44737.2044 | 49.9775
|  |  | 44737.2044 | 49.9776
|  |  | 44737.2044 | 49.9776
|  |  | 44737.2044 | 49.9776
|  |  | 44737.2044 | 49.9776
|  |  | 44737.2044 | 49.9776
|  |  | 44737.2044 | 49.9776
|  |  | 44737.2044 | 49.9776
|  |  | 44737.2044 | 49.9775
|  |  | 44737.2044 | 49.9775
|  |  | 44737.2044 | 49.9775
|  |  | 44737.2044 | 49.9774
|  |  | 44737.2044 | 49.9774
|  |  | 44737.2044 | 49.9774
|  |  | 44737.2044 | 49.9774
|  |  | 44737.2044 | 49.9774
|  |  | 44737.2044 | 49.9775
|  |  | 44737.2044 | 49.9774
|  |  | 44737.2044 | 49.9774
|  |  | 44737.2044 | 49.9774
|  |  | 44737.2044 | 49.9774
|  |  | 44737.2044 | 49.9774
|  |  | 44737.2044 | 49.9774
|  |  | 44737.2044 | 49.9773
|  |  | 44737.2044 | 49.9772
|  |  | 44737.2044 | 49.9772
|  |  | 44737.2044 | 49.9772
|  |  | 44737.2044 | 49.9772
|  |  | 44737.2044 | 49.9772
|  |  | 44737.2044 | 49.9771
|  |  | 44737.2044 | 49.9771
|  |  | 44737.2044 | 49.9771
|  |  | 44737.2044 | 49.977
|  |  | 44737.2044 | 49.977
|  |  | 2022-06-25 04:54 | 49.977
|  |  | 44737.2044 | 49.977
|  |  | 44737.2044 | 49.9769
|  |  | 44737.2044 | 49.977
|  |  | 44737.2044 | 49.977
|  |  | 44737.2044 | 49.977
|  |  | 44737.2044 | 49.9769
|  |  | 44737.2044 | 49.9769
|  |  | 44737.2044 | 49.9769
|  |  | 44737.2044 | 49.9769
|  |  | 44737.2044 | 49.9769
|  |  | 44737.2044 | 49.9769
|  |  | 44737.2044 | 49.977
|  |  | 44737.2044 | 49.9771
|  |  | 44737.2044 | 49.9771
|  |  | 44737.2044 | 49.9772
|  |  | 44737.2044 | 49.9772
|  |  | 44737.2044 | 49.9772
|  |  | 44737.2044 | 49.9772
|  |  | 44737.2044 | 49.9772
|  |  | 44737.2044 | 49.9772
|  |  | 44737.2044 | 49.9772
|  |  | 44737.2044 | 49.9772
|  |  | 44737.2044 | 49.9771
|  |  | 44737.2044 | 49.9771
|  |  | 44737.2044 | 49.9771
|  |  | 44737.2044 | 49.9771
|  |  | 44737.2044 | 49.9771
|  |  | 44737.2044 | 49.9771
|  |  | 44737.2044 | 49.9771
|  |  | 44737.2044 | 49.9771
|  |  | 44737.2044 | 49.9772
|  |  | 44737.2044 | 49.9772
|  |  | 44737.2044 | 49.9772
|  |  | 44737.2044 | 49.9772
|  |  | 44737.2044 | 49.9772
|  |  | 44737.2044 | 49.9772
|  |  | 44737.2044 | 49.9772
|  |  | 44737.2044 | 49.9772
|  |  | 44737.2044 | 49.9772
|  |  | 44737.2044 | 49.9772
|  |  | 44737.2044 | 49.9772
|  |  | 44737.2044 | 49.9772
|  |  | 44737.2044 | 49.9772
|  |  | 44737.2044 | 49.9771
|  |  | 44737.2044 | 49.977
|  |  | 44737.2044 | 49.977
|  |  | 44737.2044 | 49.9769
|  |  | 44737.2044 | 49.9769
|  |  | 44737.2044 | 49.9769
|  |  | 2022-06-25 04:54 | 49.9769
|  |  | 44737.2044 | 49.9769
|  |  | 44737.2044 | 49.9769
|  |  | 44737.2044 | 49.977
|  |  | 44737.2044 | 49.977
|  |  | 44737.2044 | 49.977
|  |  | 44737.2044 | 49.9771
|  |  | 44737.2044 | 49.9771
|  |  | 44737.2044 | 49.9771
|  |  | 44737.2044 | 49.9771
|  |  | 44737.2044 | 49.977
|  |  | 44737.2044 | 49.9769
|  |  | 44737.2044 | 49.9769
|  |  | 44737.2044 | 49.9769
|  |  | 44737.2044 | 49.9769
|  |  | 44737.2044 | 49.9768
|  |  | 44737.2044 | 49.9769
|  |  | 44737.2044 | 49.9768
|  |  | 44737.2044 | 49.9769
|  |  | 44737.2044 | 49.9769
|  |  | 44737.2044 | 49.9769
|  |  | 44737.2044 | 49.9769
|  |  | 44737.2044 | 49.9768
|  |  | 44737.2044 | 49.9768
|  |  | 44737.2044 | 49.9769
|  |  | 44737.2044 | 49.9769
|  |  | 44737.2044 | 49.977
|  |  | 44737.2044 | 49.977
|  |  | 44737.2044 | 49.9771
|  |  | 44737.2044 | 49.9771
|  |  | 44737.2044 | 49.9772
|  |  | 44737.2044 | 49.9772
|  |  | 44737.2044 | 49.9772
|  |  | 44737.2044 | 49.9772
|  |  | 44737.2044 | 49.9772
|  |  | 44737.2044 | 49.9772
|  |  | 44737.2044 | 49.9772
|  |  | 44737.2044 | 49.9773
|  |  | 44737.2044 | 49.9773
|  |  | 44737.2044 | 49.9773
|  |  | 44737.2044 | 49.9773
|  |  | 44737.2044 | 49.9773
|  |  | 44737.2044 | 49.9773
|  |  | 44737.2044 | 49.9773
|  |  | 44737.2044 | 49.9773
|  |  | 44737.2044 | 49.9773
|  |  | 44737.2044 | 49.9773
|  |  | 44737.2044 | 49.9773
|  |  | 44737.2044 | 49.9773
|  |  | 44737.2044 | 49.9772
|  |  | 2022-06-25 04:54 | 49.9773
|  |  | 44737.2044 | 49.9773
|  |  | 44737.2044 | 49.9773
|  |  | 44737.2044 | 49.9773
|  |  | 44737.2044 | 49.9773
|  |  | 44737.2044 | 49.9773
|  |  | 44737.2044 | 49.9774
|  |  | 44737.2044 | 49.9774
|  |  | 44737.2044 | 49.9774
|  |  | 44737.2044 | 49.9774
|  |  | 44737.2044 | 49.9773
|  |  | 44737.2044 | 49.9773
|  |  | 44737.2044 | 49.9773
|  |  | 44737.2044 | 49.9773
|  |  | 44737.2044 | 49.9773
|  |  | 44737.2044 | 49.9773
|  |  | 44737.2044 | 49.9774
|  |  | 44737.2044 | 49.9774
|  |  | 44737.2044 | 49.9774
|  |  | 44737.2044 | 49.9774
|  |  | 44737.2044 | 49.9775
|  |  | 44737.2044 | 49.9775
|  |  | 44737.2044 | 49.9776
|  |  | 44737.2044 | 49.9775
|  |  | 44737.2044 | 49.9775
|  |  | 44737.2045 | 49.9776
|  |  | 44737.2045 | 49.9776
|  |  | 44737.2045 | 49.9776
|  |  | 44737.2045 | 49.9776
|  |  | 44737.2045 | 49.9777
|  |  | 44737.2045 | 49.9777
|  |  | 44737.2045 | 49.9778
|  |  | 44737.2045 | 49.9778
|  |  | 44737.2045 | 49.9778
|  |  | 44737.2045 | 49.9778
|  |  | 44737.2045 | 49.9778
|  |  | 44737.2045 | 49.9779
|  |  | 44737.2045 | 49.9779
|  |  | 44737.2045 | 49.9779
|  |  | 44737.2045 | 49.9779
|  |  | 44737.2045 | 49.9779
|  |  | 44737.2045 | 49.9779
|  |  | 44737.2045 | 49.9779
|  |  | 44737.2045 | 49.9779
|  |  | 44737.2045 | 49.9779
|  |  | 44737.2045 | 49.9778
|  |  | 44737.2045 | 49.9778
|  |  | 44737.2045 | 49.9778
|  |  | 44737.2045 | 49.9777
|  |  | 44737.2045 | 49.9777
|  |  | 2022-06-25 04:54 | 49.9778
|  |  | 44737.2045 | 49.9778
|  |  | 44737.2045 | 49.9778
|  |  | 44737.2045 | 49.9779
|  |  | 44737.2045 | 49.978
|  |  | 44737.2045 | 49.978
|  |  | 44737.2045 | 49.978
|  |  | 44737.2045 | 49.978
|  |  | 44737.2045 | 49.9781
|  |  | 44737.2045 | 49.978
|  |  | 44737.2045 | 49.9781
|  |  | 44737.2045 | 49.9781
|  |  | 44737.2045 | 49.9781
|  |  | 44737.2045 | 49.9782
|  |  | 44737.2045 | 49.9782
|  |  | 44737.2045 | 49.9782
|  |  | 44737.2045 | 49.9782
|  |  | 44737.2045 | 49.9782
|  |  | 44737.2045 | 49.9782
|  |  | 44737.2045 | 49.9782
|  |  | 44737.2045 | 49.9782
|  |  | 44737.2045 | 49.9782
|  |  | 44737.2045 | 49.9782
|  |  | 44737.2045 | 49.9783
|  |  | 44737.2045 | 49.9783
|  |  | 44737.2045 | 49.9784
|  |  | 44737.2045 | 49.9784
|  |  | 44737.2045 | 49.9784
|  |  | 44737.2045 | 49.9785
|  |  | 44737.2045 | 49.9785
|  |  | 44737.2045 | 49.9785
|  |  | 44737.2045 | 49.9785
|  |  | 44737.2045 | 49.9785
|  |  | 44737.2045 | 49.9784
|  |  | 44737.2045 | 49.9784
|  |  | 44737.2045 | 49.9783
|  |  | 44737.2045 | 49.9783
|  |  | 44737.2045 | 49.9783
|  |  | 44737.2045 | 49.9782
|  |  | 44737.2045 | 49.9782
|  |  | 44737.2045 | 49.9782
|  |  | 44737.2045 | 49.9783
|  |  | 44737.2045 | 49.9783
|  |  | 44737.2045 | 49.9784
|  |  | 44737.2045 | 49.9784
|  |  | 44737.2045 | 49.9784
|  |  | 44737.2045 | 49.9785
|  |  | 44737.2045 | 49.9784
|  |  | 44737.2045 | 49.9785
|  |  | 44737.2045 | 49.9785
|  |  | 2022-06-25 04:54 | 49.9785
|  |  | 44737.2045 | 49.9785
|  |  | 44737.2045 | 49.9785
|  |  | 44737.2045 | 49.9785
|  |  | 44737.2045 | 49.9785
|  |  | 44737.2045 | 49.9786
|  |  | 44737.2045 | 49.9786
|  |  | 44737.2045 | 49.9787
|  |  | 44737.2045 | 49.9787
|  |  | 44737.2045 | 49.9788
|  |  | 44737.2045 | 49.9789
|  |  | 44737.2045 | 49.9789
|  |  | 44737.2045 | 49.9789
|  |  | 44737.2045 | 49.979
|  |  | 44737.2045 | 49.979
|  |  | 44737.2045 | 49.979
|  |  | 44737.2045 | 49.9791
|  |  | 44737.2045 | 49.9791
|  |  | 44737.2045 | 49.9791
|  |  | 44737.2045 | 49.9792
|  |  | 44737.2045 | 49.9792
|  |  | 44737.2045 | 49.9792
|  |  | 44737.2045 | 49.9793
|  |  | 44737.2045 | 49.9793
|  |  | 44737.2045 | 49.9793
|  |  | 44737.2045 | 49.9793
|  |  | 44737.2045 | 49.9793
|  |  | 44737.2045 | 49.9793
|  |  | 44737.2045 | 49.9794
|  |  | 44737.2045 | 49.9794
|  |  | 44737.2045 | 49.9795
|  |  | 44737.2045 | 49.9796
|  |  | 44737.2045 | 49.9796
|  |  | 44737.2045 | 49.9796
|  |  | 44737.2045 | 49.9796
|  |  | 44737.2045 | 49.9796
|  |  | 44737.2045 | 49.9796
|  |  | 44737.2045 | 49.9795
|  |  | 44737.2045 | 49.9796
|  |  | 44737.2045 | 49.9796
|  |  | 44737.2045 | 49.9796
|  |  | 44737.2045 | 49.9796
|  |  | 44737.2045 | 49.9797
|  |  | 44737.2045 | 49.9797
|  |  | 44737.2045 | 49.9798
|  |  | 44737.2045 | 49.9798
|  |  | 44737.2045 | 49.9798
|  |  | 44737.2045 | 49.9798
|  |  | 44737.2045 | 49.9798
|  |  | 44737.2045 | 49.9797
|  |  | 2022-06-25 04:54 | 49.9797
|  |  | 44737.2045 | 49.9797
|  |  | 44737.2045 | 49.9797
|  |  | 44737.2045 | 49.9797
|  |  | 44737.2045 | 49.9796
|  |  | 44737.2045 | 49.9796
|  |  | 44737.2045 | 49.9796
|  |  | 44737.2045 | 49.9796
|  |  | 44737.2045 | 49.9797
|  |  | 44737.2045 | 49.9797
|  |  | 44737.2045 | 49.9798
|  |  | 44737.2045 | 49.9798
|  |  | 44737.2045 | 49.9798
|  |  | 44737.2045 | 49.9798
|  |  | 44737.2045 | 49.9798
|  |  | 44737.2045 | 49.9799
|  |  | 44737.2045 | 49.9799
|  |  | 44737.2045 | 49.9799
|  |  | 44737.2045 | 49.9799
|  |  | 44737.2045 | 49.9799
|  |  | 44737.2045 | 49.9799
|  |  | 44737.2045 | 49.98
|  |  | 44737.2045 | 49.98
|  |  | 44737.2045 | 49.98
|  |  | 44737.2045 | 49.9801
|  |  | 44737.2045 | 49.9801
|  |  | 44737.2045 | 49.9801
|  |  | 44737.2045 | 49.9802
|  |  | 44737.2045 | 49.9802
|  |  | 44737.2045 | 49.9803
|  |  | 44737.2045 | 49.9803
|  |  | 44737.2045 | 49.9803
|  |  | 44737.2045 | 49.9803
|  |  | 44737.2045 | 49.9803
|  |  | 44737.2045 | 49.9803
|  |  | 44737.2045 | 49.9802
|  |  | 44737.2045 | 49.9802
|  |  | 44737.2045 | 49.9802
|  |  | 44737.2045 | 49.9802
|  |  | 44737.2045 | 49.9802
|  |  | 44737.2045 | 49.9801
|  |  | 44737.2045 | 49.9802
|  |  | 44737.2045 | 49.9802
|  |  | 44737.2045 | 49.9802
|  |  | 44737.2045 | 49.9802
|  |  | 44737.2045 | 49.9802
|  |  | 44737.2045 | 49.9801
|  |  | 44737.2045 | 49.9802
|  |  | 44737.2045 | 49.9802
|  |  | 44737.2045 | 49.9802
|  |  | 2022-06-25 04:54 | 49.9803
|  |  | 44737.2045 | 49.9803
|  |  | 44737.2045 | 49.9804
|  |  | 44737.2045 | 49.9804
|  |  | 44737.2045 | 49.9803
|  |  | 44737.2045 | 49.9803
|  |  | 44737.2045 | 49.9803
|  |  | 44737.2045 | 49.9803
|  |  | 44737.2045 | 49.9803
|  |  | 44737.2045 | 49.9803
|  |  | 44737.2045 | 49.9803
|  |  | 44737.2045 | 49.9803
|  |  | 44737.2045 | 49.9804
|  |  | 44737.2045 | 49.9803
|  |  | 44737.2045 | 49.9803
|  |  | 44737.2045 | 49.9802
|  |  | 44737.2045 | 49.9803
|  |  | 44737.2045 | 49.9804
|  |  | 44737.2045 | 49.9804
|  |  | 44737.2045 | 49.9803
|  |  | 44737.2045 | 49.9803
|  |  | 44737.2045 | 49.9803
|  |  | 44737.2045 | 49.9803
|  |  | 44737.2045 | 49.9803
|  |  | 44737.2045 | 49.9803
|  |  | 44737.2045 | 49.9803
|  |  | 44737.2045 | 49.9804
|  |  | 44737.2045 | 49.9804
|  |  | 44737.2045 | 49.9804
|  |  | 44737.2045 | 49.9805
|  |  | 44737.2045 | 49.9805
|  |  | 44737.2045 | 49.9806
|  |  | 44737.2045 | 49.9806
|  |  | 44737.2045 | 49.9806
|  |  | 44737.2045 | 49.9806
|  |  | 44737.2045 | 49.9806
|  |  | 44737.2045 | 49.9806
|  |  | 44737.2045 | 49.9805
|  |  | 44737.2045 | 49.9805
|  |  | 44737.2045 | 49.9805
|  |  | 44737.2045 | 49.9805
|  |  | 44737.2045 | 49.9806
|  |  | 44737.2045 | 49.9806
|  |  | 44737.2045 | 49.9806
|  |  | 44737.2045 | 49.9806
|  |  | 44737.2045 | 49.9806
|  |  | 44737.2045 | 49.9806
|  |  | 44737.2045 | 49.9806
|  |  | 44737.2045 | 49.9805
|  |  | 44737.2045 | 49.9805
|  |  | 2022-06-25 04:54 | 49.9805
|  |  | 44737.2045 | 49.9806
|  |  | 44737.2045 | 49.9806
|  |  | 44737.2045 | 49.9806
|  |  | 44737.2045 | 49.9805
|  |  | 44737.2045 | 49.9806
|  |  | 44737.2045 | 49.9806
|  |  | 44737.2045 | 49.9806
|  |  | 44737.2045 | 49.9806
|  |  | 44737.2045 | 49.9807
|  |  | 44737.2045 | 49.9807
|  |  | 44737.2045 | 49.9807
|  |  | 44737.2045 | 49.9808
|  |  | 44737.2045 | 49.9808
|  |  | 44737.2045 | 49.9809
|  |  | 44737.2045 | 49.9809
|  |  | 44737.2045 | 49.981
|  |  | 44737.2045 | 49.981
|  |  | 44737.2045 | 49.981
|  |  | 44737.2045 | 49.981
|  |  | 44737.2045 | 49.981
|  |  | 44737.2045 | 49.981
|  |  | 44737.2045 | 49.981
|  |  | 44737.2045 | 49.981
|  |  | 44737.2045 | 49.981
|  |  | 44737.2045 | 49.9809
|  |  | 44737.2045 | 49.9809
|  |  | 44737.2045 | 49.9809
|  |  | 44737.2045 | 49.9808
|  |  | 44737.2045 | 49.9809
|  |  | 44737.2045 | 49.9809
|  |  | 44737.2045 | 49.9809
|  |  | 44737.2045 | 49.9809
|  |  | 44737.2045 | 49.9809
|  |  | 44737.2045 | 49.9809
|  |  | 44737.2045 | 49.9809
|  |  | 44737.2045 | 49.9809
|  |  | 44737.2045 | 49.9809
|  |  | 44737.2045 | 49.9809
|  |  | 44737.2045 | 49.981
|  |  | 44737.2045 | 49.981
|  |  | 44737.2045 | 49.9811
|  |  | 44737.2045 | 49.9811
|  |  | 44737.2045 | 49.9811
|  |  | 44737.2045 | 49.9811
|  |  | 44737.2045 | 49.9811
|  |  | 44737.2045 | 49.9811
|  |  | 44737.2045 | 49.9811
|  |  | 44737.2045 | 49.9811
|  |  | 44737.2045 | 49.9811
|  |  | 2022-06-25 04:55 | 49.9811
|  |  | 44737.2045 | 49.9812
|  |  | 44737.2045 | 49.9812
|  |  | 44737.2045 | 49.9812
|  |  | 44737.2045 | 49.9813
|  |  | 44737.2045 | 49.9813
|  |  | 44737.2045 | 49.9813
|  |  | 44737.2045 | 49.9813
|  |  | 44737.2045 | 49.9814
|  |  | 44737.2045 | 49.9814
|  |  | 44737.2045 | 49.9814
|  |  | 44737.2045 | 49.9814
|  |  | 44737.2045 | 49.9815
|  |  | 44737.2045 | 49.9815
|  |  | 44737.2045 | 49.9816
|  |  | 44737.2045 | 49.9816
|  |  | 44737.2045 | 49.9817
|  |  | 44737.2045 | 49.9817
|  |  | 44737.2045 | 49.9817
|  |  | 44737.2045 | 49.9818
|  |  | 44737.2045 | 49.9818
|  |  | 44737.2045 | 49.9819
|  |  | 44737.2045 | 49.9819
|  |  | 44737.2045 | 49.9819
|  |  | 44737.2045 | 49.9819
|  |  | 44737.2045 | 49.982
|  |  | 44737.2045 | 49.982
|  |  | 44737.2045 | 49.9821
|  |  | 44737.2045 | 49.9821
|  |  | 44737.2045 | 49.9821
|  |  | 44737.2045 | 49.9821
|  |  | 44737.2045 | 49.9822
|  |  | 44737.2045 | 49.9822
|  |  | 44737.2045 | 49.9822
|  |  | 44737.2045 | 49.9823
|  |  | 44737.2045 | 49.9823
|  |  | 44737.2045 | 49.9823
|  |  | 44737.2045 | 49.9822
|  |  | 44737.2045 | 49.9822
|  |  | 44737.2045 | 49.9822
|  |  | 44737.2045 | 49.9822
|  |  | 44737.2045 | 49.9822
|  |  | 44737.2045 | 49.9823
|  |  | 44737.2045 | 49.9823
|  |  | 44737.2045 | 49.9823
|  |  | 44737.2045 | 49.9824
|  |  | 44737.2045 | 49.9824
|  |  | 44737.2045 | 49.9825
|  |  | 44737.2045 | 49.9825
|  |  | 44737.2045 | 49.9825
|  |  | 2022-06-25 04:55 | 49.9825
|  |  | 44737.2045 | 49.9825
|  |  | 44737.2045 | 49.9825
|  |  | 44737.2045 | 49.9825
|  |  | 44737.2045 | 49.9824
|  |  | 44737.2045 | 49.9824
|  |  | 44737.2045 | 49.9825
|  |  | 44737.2045 | 49.9825
|  |  | 44737.2045 | 49.9825
|  |  | 44737.2045 | 49.9826
|  |  | 44737.2045 | 49.9825
|  |  | 44737.2045 | 49.9826
|  |  | 44737.2045 | 49.9827
|  |  | 44737.2045 | 49.9827
|  |  | 44737.2045 | 49.9827
|  |  | 44737.2045 | 49.9826
|  |  | 44737.2045 | 49.9826
|  |  | 44737.2045 | 49.9826
|  |  | 44737.2045 | 49.9826
|  |  | 44737.2045 | 49.9826
|  |  | 44737.2045 | 49.9826
|  |  | 44737.2045 | 49.9827
|  |  | 44737.2045 | 49.9827
|  |  | 44737.2045 | 49.9828
|  |  | 44737.2045 | 49.9829
|  |  | 44737.2045 | 49.9829
|  |  | 44737.2045 | 49.983
|  |  | 44737.2045 | 49.983
|  |  | 44737.2045 | 49.983
|  |  | 44737.2045 | 49.9829
|  |  | 44737.2045 | 49.9829
|  |  | 44737.2045 | 49.9829
|  |  | 44737.2045 | 49.9829
|  |  | 44737.2045 | 49.9828
|  |  | 44737.2045 | 49.9828
|  |  | 44737.2045 | 49.9828
|  |  | 44737.2045 | 49.9829
|  |  | 44737.2045 | 49.9828
|  |  | 44737.2045 | 49.9829
|  |  | 44737.2045 | 49.9829
|  |  | 44737.2045 | 49.9829
|  |  | 44737.2045 | 49.9829
|  |  | 44737.2045 | 49.9829
|  |  | 44737.2045 | 49.9829
|  |  | 44737.2045 | 49.9828
|  |  | 44737.2045 | 49.9828
|  |  | 44737.2045 | 49.9828
|  |  | 44737.2045 | 49.9828
|  |  | 44737.2045 | 49.9829
|  |  | 44737.2045 | 49.983
|  |  | 2022-06-25 04:55 | 49.983
|  |  | 44737.2045 | 49.983
|  |  | 44737.2045 | 49.983
|  |  | 44737.2045 | 49.983
|  |  | 44737.2045 | 49.983
|  |  | 44737.2045 | 49.9829
|  |  | 44737.2045 | 49.9829
|  |  | 44737.2045 | 49.9829
|  |  | 44737.2045 | 49.9828
|  |  | 44737.2045 | 49.9829
|  |  | 44737.2045 | 49.9829
|  |  | 44737.2045 | 49.9829
|  |  | 44737.2045 | 49.983
|  |  | 44737.2045 | 49.9831
|  |  | 44737.2045 | 49.9832
|  |  | 44737.2045 | 49.9832
|  |  | 44737.2045 | 49.9833
|  |  | 44737.2045 | 49.9832
|  |  | 44737.2045 | 49.9832
|  |  | 44737.2045 | 49.9831
|  |  | 44737.2045 | 49.9831
|  |  | 44737.2045 | 49.983
|  |  | 44737.2045 | 49.9829
|  |  | 44737.2045 | 49.9829
|  |  | 44737.2045 | 49.9829
|  |  | 44737.2045 | 49.9829
|  |  | 44737.2045 | 49.9829
|  |  | 44737.2045 | 49.9829
|  |  | 44737.2045 | 49.983
|  |  | 44737.2045 | 49.983
|  |  | 44737.2045 | 49.983
|  |  | 44737.2045 | 49.983
|  |  | 44737.2045 | 49.983
|  |  | 44737.2045 | 49.9829
|  |  | 44737.2045 | 49.9829
|  |  | 44737.2045 | 49.9829
|  |  | 44737.2045 | 49.9829
|  |  | 44737.2045 | 49.9828
|  |  | 44737.2045 | 49.9829
|  |  | 44737.2045 | 49.9829
|  |  | 44737.2045 | 49.9829
|  |  | 44737.2045 | 49.9829
|  |  | 44737.2045 | 49.9829
|  |  | 44737.2045 | 49.983
|  |  | 44737.2045 | 49.983
|  |  | 44737.2045 | 49.983
|  |  | 44737.2045 | 49.983
|  |  | 44737.2045 | 49.983
|  |  | 44737.2045 | 49.9831
|  |  | 44737.2045 | 49.9831
|  |  | 2022-06-25 04:55 | 49.983
|  |  | 44737.2045 | 49.9831
|  |  | 44737.2045 | 49.9831
|  |  | 44737.2045 | 49.9831
|  |  | 44737.2045 | 49.9831
|  |  | 44737.2045 | 49.9831
|  |  | 44737.2046 | 49.983
|  |  | 44737.2046 | 49.983
|  |  | 44737.2046 | 49.9829
|  |  | 44737.2046 | 49.9829
|  |  | 44737.2046 | 49.9829
|  |  | 44737.2046 | 49.9828
|  |  | 44737.2046 | 49.9828
|  |  | 44737.2046 | 49.9828
|  |  | 44737.2046 | 49.9828
|  |  | 44737.2046 | 49.9828
|  |  | 44737.2046 | 49.9828
|  |  | 44737.2046 | 49.9828
|  |  | 44737.2046 | 49.9828
|  |  | 44737.2046 | 49.9829
|  |  | 44737.2046 | 49.9829
|  |  | 44737.2046 | 49.983
|  |  | 44737.2046 | 49.983
|  |  | 44737.2046 | 49.983
|  |  | 44737.2046 | 49.9831
|  |  | 44737.2046 | 49.9831
|  |  | 44737.2046 | 49.983
|  |  | 44737.2046 | 49.983
|  |  | 44737.2046 | 49.9829
|  |  | 44737.2046 | 49.9829
|  |  | 44737.2046 | 49.9829
|  |  | 44737.2046 | 49.9828
|  |  | 44737.2046 | 49.9828
|  |  | 44737.2046 | 49.9828
|  |  | 44737.2046 | 49.9828
|  |  | 44737.2046 | 49.9828
|  |  | 44737.2046 | 49.9829
|  |  | 44737.2046 | 49.9829
|  |  | 44737.2046 | 49.9829
|  |  | 44737.2046 | 49.9829
|  |  | 44737.2046 | 49.9829
|  |  | 44737.2046 | 49.9829
|  |  | 44737.2046 | 49.9828
|  |  | 44737.2046 | 49.9828
|  |  | 44737.2046 | 49.9827
|  |  | 44737.2046 | 49.9826
|  |  | 44737.2046 | 49.9826
|  |  | 44737.2046 | 49.9825
|  |  | 44737.2046 | 49.9825
|  |  | 44737.2046 | 49.9825
|  |  | 2022-06-25 04:55 | 49.9825
|  |  | 44737.2046 | 49.9826
|  |  | 44737.2046 | 49.9826
|  |  | 44737.2046 | 49.9826
|  |  | 44737.2046 | 49.9827
|  |  | 44737.2046 | 49.9827
|  |  | 44737.2046 | 49.9827
|  |  | 44737.2046 | 49.9826
|  |  | 44737.2046 | 49.9826
|  |  | 44737.2046 | 49.9825
|  |  | 44737.2046 | 49.9825
|  |  | 44737.2046 | 49.9825
|  |  | 44737.2046 | 49.9824
|  |  | 44737.2046 | 49.9824
|  |  | 44737.2046 | 49.9824
|  |  | 44737.2046 | 49.9824
|  |  | 44737.2046 | 49.9824
|  |  | 44737.2046 | 49.9824
|  |  | 44737.2046 | 49.9825
|  |  | 44737.2046 | 49.9825
|  |  | 44737.2046 | 49.9825
|  |  | 44737.2046 | 49.9825
|  |  | 44737.2046 | 49.9824
|  |  | 44737.2046 | 49.9823
|  |  | 44737.2046 | 49.9823
|  |  | 44737.2046 | 49.9822
|  |  | 44737.2046 | 49.9821
|  |  | 44737.2046 | 49.982
|  |  | 44737.2046 | 49.9819
|  |  | 44737.2046 | 49.9819
|  |  | 44737.2046 | 49.9818
|  |  | 44737.2046 | 49.9818
|  |  | 44737.2046 | 49.9817
|  |  | 44737.2046 | 49.9816
|  |  | 44737.2046 | 49.9816
|  |  | 44737.2046 | 49.9815
|  |  | 44737.2046 | 49.9815
|  |  | 44737.2046 | 49.9815
|  |  | 44737.2046 | 49.9815
|  |  | 44737.2046 | 49.9815
|  |  | 44737.2046 | 49.9816
|  |  | 44737.2046 | 49.9816
|  |  | 44737.2046 | 49.9816
|  |  | 44737.2046 | 49.9816
|  |  | 44737.2046 | 49.9815
|  |  | 44737.2046 | 49.9814
|  |  | 44737.2046 | 49.9812
|  |  | 44737.2046 | 49.9811
|  |  | 44737.2046 | 49.9811
|  |  | 44737.2046 | 49.9809
|  |  | 2022-06-25 04:55 | 49.9809
|  |  | 44737.2046 | 49.9809
|  |  | 44737.2046 | 49.9809
|  |  | 44737.2046 | 49.9809
|  |  | 44737.2046 | 49.9809
|  |  | 44737.2046 | 49.9808
|  |  | 44737.2046 | 49.9808
|  |  | 44737.2046 | 49.9808
|  |  | 44737.2046 | 49.9808
|  |  | 44737.2046 | 49.9807
|  |  | 44737.2046 | 49.9807
|  |  | 44737.2046 | 49.9806
|  |  | 44737.2046 | 49.9805
|  |  | 44737.2046 | 49.9805
|  |  | 44737.2046 | 49.9805
|  |  | 44737.2046 | 49.9804
|  |  | 44737.2046 | 49.9805
|  |  | 44737.2046 | 49.9805
|  |  | 44737.2046 | 49.9805
|  |  | 44737.2046 | 49.9806
|  |  | 44737.2046 | 49.9807
|  |  | 44737.2046 | 49.9806
|  |  | 44737.2046 | 49.9806
|  |  | 44737.2046 | 49.9807
|  |  | 44737.2046 | 49.9806
|  |  | 44737.2046 | 49.9806
|  |  | 44737.2046 | 49.9805
|  |  | 44737.2046 | 49.9805
|  |  | 44737.2046 | 49.9804
|  |  | 44737.2046 | 49.9803
|  |  | 44737.2046 | 49.9803
|  |  | 44737.2046 | 49.9802
|  |  | 44737.2046 | 49.9801
|  |  | 44737.2046 | 49.98
|  |  | 44737.2046 | 49.98
|  |  | 44737.2046 | 49.9799
|  |  | 44737.2046 | 49.9799
|  |  | 44737.2046 | 49.9798
|  |  | 44737.2046 | 49.9797
|  |  | 44737.2046 | 49.9796
|  |  | 44737.2046 | 49.9796
|  |  | 44737.2046 | 49.9795
|  |  | 44737.2046 | 49.9795
|  |  | 44737.2046 | 49.9795
|  |  | 44737.2046 | 49.9796
|  |  | 44737.2046 | 49.9796
|  |  | 44737.2046 | 49.9796
|  |  | 44737.2046 | 49.9796
|  |  | 44737.2046 | 49.9796
|  |  | 44737.2046 | 49.9795
|  |  | 2022-06-25 04:55 | 49.9795
|  |  | 44737.2046 | 49.9795
|  |  | 44737.2046 | 49.9794
|  |  | 44737.2046 | 49.9793
|  |  | 44737.2046 | 49.9793
|  |  | 44737.2046 | 49.9793
|  |  | 44737.2046 | 49.9793
|  |  | 44737.2046 | 49.9793
|  |  | 44737.2046 | 49.9794
|  |  | 44737.2046 | 49.9793
|  |  | 44737.2046 | 49.9793
|  |  | 44737.2046 | 49.9792
|  |  | 44737.2046 | 49.979
|  |  | 44737.2046 | 49.9787
|  |  | 44737.2046 | 49.9782
|  |  | 44737.2046 | 49.9774
|  |  | 44737.2046 | 49.9766
|  |  | 44737.2046 | 49.9756
|  |  | 44737.2046 | 49.9747
|  |  | 44737.2046 | 49.9738
|  |  | 44737.2046 | 49.9732
|  |  | 44737.2046 | 49.9727
|  |  | 44737.2046 | 49.9723
|  |  | 44737.2046 | 49.972
|  |  | 44737.2046 | 49.9718
|  |  | 44737.2046 | 49.9716
|  |  | 44737.2046 | 49.9715
|  |  | 44737.2046 | 49.9711
|  |  | 44737.2046 | 49.9707
|  |  | 44737.2046 | 49.9701
|  |  | 44737.2046 | 49.9694
|  |  | 44737.2046 | 49.9686
|  |  | 44737.2046 | 49.9677
|  |  | 44737.2046 | 49.9668
|  |  | 44737.2046 | 49.9659
|  |  | 44737.2046 | 49.965
|  |  | 44737.2046 | 49.9641
|  |  | 44737.2046 | 49.9633
|  |  | 44737.2046 | 49.9626
|  |  | 44737.2046 | 49.9619
|  |  | 44737.2046 | 49.9612
|  |  | 44737.2046 | 49.9607
|  |  | 44737.2046 | 49.9601
|  |  | 44737.2046 | 49.9595
|  |  | 44737.2046 | 49.9588
|  |  | 44737.2046 | 49.9582
|  |  | 44737.2046 | 49.9575
|  |  | 44737.2046 | 49.9568
|  |  | 44737.2046 | 49.9562
|  |  | 44737.2046 | 49.9555
|  |  | 2022-06-25 04:55 | 49.9549
|  |  | 44737.2046 | 49.9543
|  |  | 44737.2046 | 49.9537
|  |  | 44737.2046 | 49.9532
|  |  | 44737.2046 | 49.9526
|  |  | 44737.2046 | 49.952
|  |  | 44737.2046 | 49.9514
|  |  | 44737.2046 | 49.9508
|  |  | 44737.2046 | 49.9503
|  |  | 44737.2046 | 49.9497
|  |  | 44737.2046 | 49.9491
|  |  | 44737.2046 | 49.9486
|  |  | 44737.2046 | 49.9481
|  |  | 44737.2046 | 49.9476
|  |  | 44737.2046 | 49.9471
|  |  | 44737.2046 | 49.9466
|  |  | 44737.2046 | 49.9461
|  |  | 44737.2046 | 49.9456
|  |  | 44737.2046 | 49.945
|  |  | 44737.2046 | 49.9445
|  |  | 44737.2046 | 49.944
|  |  | 44737.2046 | 49.9435
|  |  | 44737.2046 | 49.943
|  |  | 44737.2046 | 49.9425
|  |  | 44737.2046 | 49.942
|  |  | 44737.2046 | 49.9415
|  |  | 44737.2046 | 49.941
|  |  | 44737.2046 | 49.9404
|  |  | 44737.2046 | 49.9398
|  |  | 44737.2046 | 49.9392
|  |  | 44737.2046 | 49.9386
|  |  | 44737.2046 | 49.9381
|  |  | 44737.2046 | 49.9375
|  |  | 44737.2046 | 49.9369
|  |  | 44737.2046 | 49.9364
|  |  | 44737.2046 | 49.9358
|  |  | 44737.2046 | 49.9352
|  |  | 44737.2046 | 49.9346
|  |  | 44737.2046 | 49.934
|  |  | 44737.2046 | 49.9335
|  |  | 44737.2046 | 49.9329
|  |  | 44737.2046 | 49.9325
|  |  | 44737.2046 | 49.932
|  |  | 44737.2046 | 49.9314
|  |  | 44737.2046 | 49.9309
|  |  | 44737.2046 | 49.9303
|  |  | 44737.2046 | 49.9298
|  |  | 44737.2046 | 49.9293
|  |  | 44737.2046 | 49.9288
|  |  | 44737.2046 | 49.9283
|  |  | 2022-06-25 04:55 | 49.9278
|  |  | 44737.2046 | 49.9274
|  |  | 44737.2046 | 49.9268
|  |  | 44737.2046 | 49.9263
|  |  | 44737.2046 | 49.9259
|  |  | 44737.2046 | 49.9254
|  |  | 44737.2046 | 49.9249
|  |  | 44737.2046 | 49.9245
|  |  | 44737.2046 | 49.924
|  |  | 44737.2046 | 49.9235
|  |  | 44737.2046 | 49.9231
|  |  | 44737.2046 | 49.9227
|  |  | 44737.2046 | 49.9224
|  |  | 44737.2046 | 49.9221
|  |  | 44737.2046 | 49.9217
|  |  | 44737.2046 | 49.9214
|  |  | 44737.2046 | 49.9211
|  |  | 44737.2046 | 49.9208
|  |  | 44737.2046 | 49.9204
|  |  | 44737.2046 | 49.9201
|  |  | 44737.2046 | 49.9198
|  |  | 44737.2046 | 49.9195
|  |  | 44737.2046 | 49.9191
|  |  | 44737.2046 | 49.9188
|  |  | 44737.2046 | 49.9184
|  |  | 44737.2046 | 49.918
|  |  | 44737.2046 | 49.9177
|  |  | 44737.2046 | 49.9173
|  |  | 44737.2046 | 49.917
|  |  | 44737.2046 | 49.9166
|  |  | 44737.2046 | 49.9163
|  |  | 44737.2046 | 49.9161
|  |  | 44737.2046 | 49.9158
|  |  | 44737.2046 | 49.9155
|  |  | 44737.2046 | 49.9153
|  |  | 44737.2046 | 49.915
|  |  | 44737.2046 | 49.9147
|  |  | 44737.2046 | 49.9144
|  |  | 44737.2046 | 49.9141
|  |  | 44737.2046 | 49.9138
|  |  | 44737.2046 | 49.9135
|  |  | 44737.2046 | 49.9132
|  |  | 44737.2046 | 49.9129
|  |  | 44737.2046 | 49.9127
|  |  | 44737.2046 | 49.9124
|  |  | 44737.2046 | 49.9121
|  |  | 44737.2046 | 49.9118
|  |  | 44737.2046 | 49.9116
|  |  | 44737.2046 | 49.9114
|  |  | 44737.2046 | 49.9111
|  |  | 2022-06-25 04:55 | 49.9109
|  |  | 44737.2046 | 49.9108
|  |  | 44737.2046 | 49.9106
|  |  | 44737.2046 | 49.9104
|  |  | 44737.2046 | 49.9102
|  |  | 44737.2046 | 49.91
|  |  | 44737.2046 | 49.9098
|  |  | 44737.2046 | 49.9096
|  |  | 44737.2046 | 49.9094
|  |  | 44737.2046 | 49.9092
|  |  | 44737.2046 | 49.9089
|  |  | 44737.2046 | 49.9087
|  |  | 44737.2046 | 49.9085
|  |  | 44737.2046 | 49.9082
|  |  | 44737.2046 | 49.908
|  |  | 44737.2046 | 49.9078
|  |  | 44737.2046 | 49.9077
|  |  | 44737.2046 | 49.9075
|  |  | 44737.2046 | 49.9073
|  |  | 44737.2046 | 49.9071
|  |  | 44737.2046 | 49.907
|  |  | 44737.2046 | 49.9069
|  |  | 44737.2046 | 49.9067
|  |  | 44737.2046 | 49.9065
|  |  | 44737.2046 | 49.9063
|  |  | 44737.2046 | 49.9061
|  |  | 44737.2046 | 49.9059
|  |  | 44737.2046 | 49.9057
|  |  | 44737.2046 | 49.9055
|  |  | 44737.2046 | 49.9054
|  |  | 44737.2046 | 49.9052
|  |  | 44737.2046 | 49.9051
|  |  | 44737.2046 | 49.905
|  |  | 44737.2046 | 49.9049
|  |  | 44737.2046 | 49.9048
|  |  | 44737.2046 | 49.9046
|  |  | 44737.2046 | 49.9045
|  |  | 44737.2046 | 49.9044
|  |  | 44737.2046 | 49.9043
|  |  | 44737.2046 | 49.9043
|  |  | 44737.2046 | 49.9042
|  |  | 44737.2046 | 49.9042
|  |  | 44737.2046 | 49.9041
|  |  | 44737.2046 | 49.9041
|  |  | 44737.2046 | 49.904
|  |  | 44737.2046 | 49.904
|  |  | 44737.2046 | 49.904
|  |  | 44737.2046 | 49.9039
|  |  | 44737.2046 | 49.9039
|  |  | 44737.2046 | 49.9039
|  |  | 2022-06-25 04:55 | 49.9039
|  |  | 44737.2046 | 49.9039
|  |  | 44737.2046 | 49.9039
|  |  | 44737.2046 | 49.9039
|  |  | 44737.2046 | 49.9039
|  |  | 44737.2046 | 49.9038
|  |  | 44737.2046 | 49.9037
|  |  | 44737.2046 | 49.9037
|  |  | 44737.2046 | 49.9037
|  |  | 44737.2046 | 49.9037
|  |  | 44737.2046 | 49.9037
|  |  | 44737.2046 | 49.9037
|  |  | 44737.2046 | 49.9037
|  |  | 44737.2046 | 49.9037
|  |  | 44737.2046 | 49.9037
|  |  | 44737.2046 | 49.9038
|  |  | 44737.2046 | 49.9037
|  |  | 44737.2046 | 49.9037
|  |  | 44737.2046 | 49.9037
|  |  | 44737.2046 | 49.9037
|  |  | 44737.2046 | 49.9037
|  |  | 44737.2046 | 49.9036
|  |  | 44737.2046 | 49.9035
|  |  | 44737.2046 | 49.9034
|  |  | 44737.2046 | 49.9033
|  |  | 44737.2046 | 49.9033
|  |  | 44737.2046 | 49.9034
|  |  | 44737.2046 | 49.9034
|  |  | 44737.2046 | 49.9033
|  |  | 44737.2046 | 49.9034
|  |  | 44737.2046 | 49.9034
|  |  | 44737.2046 | 49.9035
|  |  | 44737.2046 | 49.9035
|  |  | 44737.2046 | 49.9036
|  |  | 44737.2046 | 49.9036
|  |  | 44737.2046 | 49.9035
|  |  | 44737.2046 | 49.9035
|  |  | 44737.2046 | 49.9034
|  |  | 44737.2046 | 49.9034
|  |  | 44737.2046 | 49.9034
|  |  | 44737.2046 | 49.9034
|  |  | 44737.2046 | 49.9035
|  |  | 44737.2046 | 49.9035
|  |  | 44737.2046 | 49.9035
|  |  | 44737.2046 | 49.9036
|  |  | 44737.2046 | 49.9035
|  |  | 44737.2046 | 49.9035
|  |  | 44737.2046 | 49.9036
|  |  | 44737.2046 | 49.9035
|  |  | 44737.2046 | 49.9037
|  |  | 2022-06-25 04:55 | 49.9037
|  |  | 44737.2046 | 49.9037
|  |  | 44737.2046 | 49.9038
|  |  | 44737.2046 | 49.9039
|  |  | 44737.2046 | 49.9039
|  |  | 44737.2046 | 49.9039
|  |  | 44737.2046 | 49.904
|  |  | 44737.2046 | 49.904
|  |  | 44737.2046 | 49.9041
|  |  | 44737.2046 | 49.9041
|  |  | 44737.2046 | 49.9042
|  |  | 44737.2046 | 49.9042
|  |  | 44737.2046 | 49.9042
|  |  | 44737.2046 | 49.9043
|  |  | 44737.2046 | 49.9043
|  |  | 44737.2046 | 49.9044
|  |  | 44737.2046 | 49.9044
|  |  | 44737.2046 | 49.9044
|  |  | 44737.2046 | 49.9045
|  |  | 44737.2046 | 49.9046
|  |  | 44737.2046 | 49.9046
|  |  | 44737.2046 | 49.9047
|  |  | 44737.2046 | 49.9048
|  |  | 44737.2046 | 49.9049
|  |  | 44737.2046 | 49.9049
|  |  | 44737.2046 | 49.9049
|  |  | 44737.2046 | 49.9049
|  |  | 44737.2046 | 49.9049
|  |  | 44737.2046 | 49.9048
|  |  | 44737.2046 | 49.9048
|  |  | 44737.2046 | 49.9048
|  |  | 44737.2046 | 49.9048
|  |  | 44737.2046 | 49.9048
|  |  | 44737.2046 | 49.9048
|  |  | 44737.2046 | 49.9049
|  |  | 44737.2046 | 49.9049
|  |  | 44737.2046 | 49.905
|  |  | 44737.2046 | 49.9051
|  |  | 44737.2046 | 49.9051
|  |  | 44737.2047 | 49.9051
|  |  | 44737.2047 | 49.9052
|  |  | 44737.2047 | 49.9051
|  |  | 44737.2047 | 49.9052
|  |  | 44737.2047 | 49.9051
|  |  | 44737.2047 | 49.9051
|  |  | 44737.2047 | 49.9051
|  |  | 44737.2047 | 49.9052
|  |  | 44737.2047 | 49.9052
|  |  | 44737.2047 | 49.9053
|  |  | 44737.2047 | 49.9053
|  |  | 2022-06-25 04:55 | 49.9054
|  |  | 44737.2047 | 49.9054
|  |  | 44737.2047 | 49.9055
|  |  | 44737.2047 | 49.9055
|  |  | 44737.2047 | 49.9054
|  |  | 44737.2047 | 49.9054
|  |  | 44737.2047 | 49.9053
|  |  | 44737.2047 | 49.9053
|  |  | 44737.2047 | 49.9052
|  |  | 44737.2047 | 49.9053
|  |  | 44737.2047 | 49.9053
|  |  | 44737.2047 | 49.9054
|  |  | 44737.2047 | 49.9055
|  |  | 44737.2047 | 49.9056
|  |  | 44737.2047 | 49.9056
|  |  | 44737.2047 | 49.9057
|  |  | 44737.2047 | 49.9058
|  |  | 44737.2047 | 49.9058
|  |  | 44737.2047 | 49.906
|  |  | 44737.2047 | 49.906
|  |  | 44737.2047 | 49.906
|  |  | 44737.2047 | 49.906
|  |  | 44737.2047 | 49.906
|  |  | 44737.2047 | 49.906
|  |  | 44737.2047 | 49.9061
|  |  | 44737.2047 | 49.9062
|  |  | 44737.2047 | 49.9063
|  |  | 44737.2047 | 49.9063
|  |  | 44737.2047 | 49.9064
|  |  | 44737.2047 | 49.9064
|  |  | 44737.2047 | 49.9065
|  |  | 44737.2047 | 49.9065
|  |  | 44737.2047 | 49.9065
|  |  | 44737.2047 | 49.9065
|  |  | 44737.2047 | 49.9065
|  |  | 44737.2047 | 49.9065
|  |  | 44737.2047 | 49.9065
|  |  | 44737.2047 | 49.9065
|  |  | 44737.2047 | 49.9065
|  |  | 44737.2047 | 49.9065
|  |  | 44737.2047 | 49.9065
|  |  | 44737.2047 | 49.9065
|  |  | 44737.2047 | 49.9066
|  |  | 44737.2047 | 49.9065
|  |  | 44737.2047 | 49.9065
|  |  | 44737.2047 | 49.9066
|  |  | 44737.2047 | 49.9066
|  |  | 44737.2047 | 49.9066
|  |  | 44737.2047 | 49.9067
|  |  | 44737.2047 | 49.9067
|  |  | 2022-06-25 04:55 | 49.9067
|  |  | 44737.2047 | 49.9068
|  |  | 44737.2047 | 49.9069
|  |  | 44737.2047 | 49.9069
|  |  | 44737.2047 | 49.9069
|  |  | 44737.2047 | 49.9069
|  |  | 44737.2047 | 49.9069
|  |  | 44737.2047 | 49.907
|  |  | 44737.2047 | 49.907
|  |  | 44737.2047 | 49.9071
|  |  | 44737.2047 | 49.9071
|  |  | 44737.2047 | 49.9071
|  |  | 44737.2047 | 49.9071
|  |  | 44737.2047 | 49.9072
|  |  | 44737.2047 | 49.9072
|  |  | 44737.2047 | 49.9072
|  |  | 44737.2047 | 49.9072
|  |  | 44737.2047 | 49.9071
|  |  | 44737.2047 | 49.9071
|  |  | 44737.2047 | 49.907
|  |  | 44737.2047 | 49.907
|  |  | 44737.2047 | 49.9069
|  |  | 44737.2047 | 49.9069
|  |  | 44737.2047 | 49.9069
|  |  | 44737.2047 | 49.9069
|  |  | 44737.2047 | 49.9069
|  |  | 44737.2047 | 49.9069
|  |  | 44737.2047 | 49.9069
|  |  | 44737.2047 | 49.907
|  |  | 44737.2047 | 49.907
|  |  | 44737.2047 | 49.9071
|  |  | 44737.2047 | 49.9071
|  |  | 44737.2047 | 49.9071
|  |  | 44737.2047 | 49.9071
|  |  | 44737.2047 | 49.907
|  |  | 44737.2047 | 49.907
|  |  | 44737.2047 | 49.9069
|  |  | 44737.2047 | 49.9069
|  |  | 44737.2047 | 49.9068
|  |  | 44737.2047 | 49.9068
|  |  | 44737.2047 | 49.9068
|  |  | 44737.2047 | 49.9068
|  |  | 44737.2047 | 49.9068
|  |  | 44737.2047 | 49.9069
|  |  | 44737.2047 | 49.9069
|  |  | 44737.2047 | 49.9068
|  |  | 44737.2047 | 49.9068
|  |  | 44737.2047 | 49.9068
|  |  | 44737.2047 | 49.9067
|  |  | 44737.2047 | 49.9067
|  |  | 2022-06-25 04:55 | 49.9067
|  |  | 44737.2047 | 49.9066
|  |  | 44737.2047 | 49.9065
|  |  | 44737.2047 | 49.9065
|  |  | 44737.2047 | 49.9065
|  |  | 44737.2047 | 49.9065
|  |  | 44737.2047 | 49.9065
|  |  | 44737.2047 | 49.9065
|  |  | 44737.2047 | 49.9066
|  |  | 44737.2047 | 49.9065
|  |  | 44737.2047 | 49.9065
|  |  | 44737.2047 | 49.9065
|  |  | 44737.2047 | 49.9064
|  |  | 44737.2047 | 49.9063
|  |  | 44737.2047 | 49.9063
|  |  | 44737.2047 | 49.9063
|  |  | 44737.2047 | 49.9063
|  |  | 44737.2047 | 49.9063
|  |  | 44737.2047 | 49.9064
|  |  | 44737.2047 | 49.9064
|  |  | 44737.2047 | 49.9065
|  |  | 44737.2047 | 49.9066
|  |  | 44737.2047 | 49.9066
|  |  | 44737.2047 | 49.9067
|  |  | 44737.2047 | 49.9067
|  |  | 44737.2047 | 49.9067
|  |  | 44737.2047 | 49.9067
|  |  | 44737.2047 | 49.9067
|  |  | 44737.2047 | 49.9067
|  |  | 44737.2047 | 49.9067
|  |  | 44737.2047 | 49.9067
|  |  | 44737.2047 | 49.9067
|  |  | 44737.2047 | 49.9067
|  |  | 44737.2047 | 49.9067
|  |  | 44737.2047 | 49.9067
|  |  | 44737.2047 | 49.9068
|  |  | 44737.2047 | 49.9068
|  |  | 44737.2047 | 49.9068
|  |  | 44737.2047 | 49.9068
|  |  | 44737.2047 | 49.9069
|  |  | 44737.2047 | 49.9068
|  |  | 44737.2047 | 49.9069
|  |  | 44737.2047 | 49.9069
|  |  | 44737.2047 | 49.9069
|  |  | 44737.2047 | 49.9069
|  |  | 44737.2047 | 49.9069
|  |  | 44737.2047 | 49.9069
|  |  | 44737.2047 | 49.9068
|  |  | 44737.2047 | 49.9067
|  |  | 44737.2047 | 49.9066
|  |  | 2022-06-25 04:55 | 49.9065
|  |  | 44737.2047 | 49.9065
|  |  | 44737.2047 | 49.9064
|  |  | 44737.2047 | 49.9064
|  |  | 44737.2047 | 49.9064
|  |  | 44737.2047 | 49.9064
|  |  | 44737.2047 | 49.9064
|  |  | 44737.2047 | 49.9064
|  |  | 44737.2047 | 49.9064
|  |  | 44737.2047 | 49.9064
|  |  | 44737.2047 | 49.9063
|  |  | 44737.2047 | 49.9063
|  |  | 44737.2047 | 49.9064
|  |  | 44737.2047 | 49.9064
|  |  | 44737.2047 | 49.9065
|  |  | 44737.2047 | 49.9065
|  |  | 44737.2047 | 49.9065
|  |  | 44737.2047 | 49.9065
|  |  | 44737.2047 | 49.9064
|  |  | 44737.2047 | 49.9064
|  |  | 44737.2047 | 49.9063
|  |  | 44737.2047 | 49.9063
|  |  | 44737.2047 | 49.9063
|  |  | 44737.2047 | 49.9063
|  |  | 44737.2047 | 49.9064
|  |  | 44737.2047 | 49.9064
|  |  | 44737.2047 | 49.9065
|  |  | 44737.2047 | 49.9066
|  |  | 44737.2047 | 49.9067
|  |  | 44737.2047 | 49.9068
|  |  | 44737.2047 | 49.9068
|  |  | 44737.2047 | 49.9067
|  |  | 44737.2047 | 49.9067
|  |  | 44737.2047 | 49.9067
|  |  | 44737.2047 | 49.9066
|  |  | 44737.2047 | 49.9066
|  |  | 44737.2047 | 49.9066
|  |  | 44737.2047 | 49.9066
|  |  | 44737.2047 | 49.9066
|  |  | 44737.2047 | 49.9066
|  |  | 44737.2047 | 49.9066
|  |  | 44737.2047 | 49.9067
|  |  | 44737.2047 | 49.9067
|  |  | 44737.2047 | 49.9067
|  |  | 44737.2047 | 49.9067
|  |  | 44737.2047 | 49.9066
|  |  | 44737.2047 | 49.9066
|  |  | 44737.2047 | 49.9065
|  |  | 44737.2047 | 49.9064
|  |  | 44737.2047 | 49.9064
|  |  | 2022-06-25 04:55 | 49.9064
|  |  | 44737.2047 | 49.9064
|  |  | 44737.2047 | 49.9064
|  |  | 44737.2047 | 49.9064
|  |  | 44737.2047 | 49.9064
|  |  | 44737.2047 | 49.9064
|  |  | 44737.2047 | 49.9064
|  |  | 44737.2047 | 49.9063
|  |  | 44737.2047 | 49.9063
|  |  | 44737.2047 | 49.9062
|  |  | 44737.2047 | 49.9061
|  |  | 44737.2047 | 49.906
|  |  | 44737.2047 | 49.906
|  |  | 44737.2047 | 49.9059
|  |  | 44737.2047 | 49.9059
|  |  | 44737.2047 | 49.9058
|  |  | 44737.2047 | 49.9058
|  |  | 44737.2047 | 49.9058
|  |  | 44737.2047 | 49.9058
|  |  | 44737.2047 | 49.9059
|  |  | 44737.2047 | 49.9059
|  |  | 44737.2047 | 49.9059
|  |  | 44737.2047 | 49.9059
|  |  | 44737.2047 | 49.9058
|  |  | 44737.2047 | 49.9058
|  |  | 44737.2047 | 49.9058
|  |  | 44737.2047 | 49.9057
|  |  | 44737.2047 | 49.9056
|  |  | 44737.2047 | 49.9056
|  |  | 44737.2047 | 49.9056
|  |  | 44737.2047 | 49.9056
|  |  | 44737.2047 | 49.9056
|  |  | 44737.2047 | 49.9057
|  |  | 44737.2047 | 49.9057
|  |  | 44737.2047 | 49.9058
|  |  | 44737.2047 | 49.9058
|  |  | 44737.2047 | 49.9058
|  |  | 44737.2047 | 49.9057
|  |  | 44737.2047 | 49.9057
|  |  | 44737.2047 | 49.9056
|  |  | 44737.2047 | 49.9056
|  |  | 44737.2047 | 49.9055
|  |  | 44737.2047 | 49.9055
|  |  | 44737.2047 | 49.9055
|  |  | 44737.2047 | 49.9055
|  |  | 44737.2047 | 49.9055
|  |  | 44737.2047 | 49.9055
|  |  | 44737.2047 | 49.9055
|  |  | 44737.2047 | 49.9055
|  |  | 44737.2047 | 49.9055
|  |  | 2022-06-25 04:55 | 49.9054
|  |  | 44737.2047 | 49.9054
|  |  | 44737.2047 | 49.9054
|  |  | 44737.2047 | 49.9054
|  |  | 44737.2047 | 49.9055
|  |  | 44737.2047 | 49.9054
|  |  | 44737.2047 | 49.9054
|  |  | 44737.2047 | 49.9055
|  |  | 44737.2047 | 49.9055
|  |  | 44737.2047 | 49.9056
|  |  | 44737.2047 | 49.9057
|  |  | 44737.2047 | 49.9056
|  |  | 44737.2047 | 49.9056
|  |  | 44737.2047 | 49.9055
|  |  | 44737.2047 | 49.9055
|  |  | 44737.2047 | 49.9055
|  |  | 44737.2047 | 49.9054
|  |  | 44737.2047 | 49.9055
|  |  | 44737.2047 | 49.9055
|  |  | 44737.2047 | 49.9054
|  |  | 44737.2047 | 49.9053
|  |  | 44737.2047 | 49.9053
|  |  | 44737.2047 | 49.9053
|  |  | 44737.2047 | 49.9052
|  |  | 44737.2047 | 49.9053
|  |  | 44737.2047 | 49.9052
|  |  | 44737.2047 | 49.9053
|  |  | 44737.2047 | 49.9053
|  |  | 44737.2047 | 49.9053
|  |  | 44737.2047 | 49.9053
|  |  | 44737.2047 | 49.9053
|  |  | 44737.2047 | 49.9053
|  |  | 44737.2047 | 49.9053
|  |  | 44737.2047 | 49.9052
|  |  | 44737.2047 | 49.9051
|  |  | 44737.2047 | 49.9051
|  |  | 44737.2047 | 49.905
|  |  | 44737.2047 | 49.905
|  |  | 44737.2047 | 49.905
|  |  | 44737.2047 | 49.905
|  |  | 44737.2047 | 49.9049
|  |  | 44737.2047 | 49.905
|  |  | 44737.2047 | 49.905
|  |  | 44737.2047 | 49.905
|  |  | 44737.2047 | 49.905
|  |  | 44737.2047 | 49.9051
|  |  | 44737.2047 | 49.9051
|  |  | 44737.2047 | 49.9051
|  |  | 44737.2047 | 49.9051
|  |  | 44737.2047 | 49.9051
|  |  | 2022-06-25 04:55 | 49.9051
|  |  | 44737.2047 | 49.9051
|  |  | 44737.2047 | 49.905
|  |  | 44737.2047 | 49.9051
|  |  | 44737.2047 | 49.905
|  |  | 44737.2047 | 49.905
|  |  | 44737.2047 | 49.905
|  |  | 44737.2047 | 49.905
|  |  | 44737.2047 | 49.905
|  |  | 44737.2047 | 49.905
|  |  | 44737.2047 | 49.905
|  |  | 44737.2047 | 49.9049
|  |  | 44737.2047 | 49.9048
|  |  | 44737.2047 | 49.9048
|  |  | 44737.2047 | 49.9047
|  |  | 44737.2047 | 49.9047
|  |  | 44737.2047 | 49.9047
|  |  | 44737.2047 | 49.9047
|  |  | 44737.2047 | 49.9047
|  |  | 44737.2047 | 49.9047
|  |  | 44737.2047 | 49.9048
|  |  | 44737.2047 | 49.9048
|  |  | 44737.2047 | 49.9048
|  |  | 44737.2047 | 49.9048
|  |  | 44737.2047 | 49.9049
|  |  | 44737.2047 | 49.9049
|  |  | 44737.2047 | 49.9049
|  |  | 44737.2047 | 49.9049
|  |  | 44737.2047 | 49.9049
|  |  | 44737.2047 | 49.9048
|  |  | 44737.2047 | 49.9048
|  |  | 44737.2047 | 49.9048
|  |  | 44737.2047 | 49.9048
|  |  | 44737.2047 | 49.9048
|  |  | 44737.2047 | 49.9048
|  |  | 44737.2047 | 49.9048
|  |  | 44737.2047 | 49.9049
|  |  | 44737.2047 | 49.9049
|  |  | 44737.2047 | 49.9048
|  |  | 44737.2047 | 49.9048
|  |  | 44737.2047 | 49.9048
|  |  | 44737.2047 | 49.9048
|  |  | 44737.2047 | 49.9048
|  |  | 44737.2047 | 49.9047
|  |  | 44737.2047 | 49.9047
|  |  | 44737.2047 | 49.9047
|  |  | 44737.2047 | 49.9047
|  |  | 44737.2047 | 49.9047
|  |  | 44737.2047 | 49.9046
|  |  | 44737.2047 | 49.9046
|  |  | 2022-06-25 04:55 | 49.9046
|  |  | 44737.2047 | 49.9046
|  |  | 44737.2047 | 49.9045
|  |  | 44737.2047 | 49.9045
|  |  | 44737.2047 | 49.9045
|  |  | 44737.2047 | 49.9044
|  |  | 44737.2047 | 49.9044
|  |  | 44737.2047 | 49.9043
|  |  | 44737.2047 | 49.9042
|  |  | 44737.2047 | 49.9041
|  |  | 44737.2047 | 49.9041
|  |  | 44737.2047 | 49.904
|  |  | 44737.2047 | 49.904
|  |  | 44737.2047 | 49.9039
|  |  | 44737.2047 | 49.9039
|  |  | 44737.2047 | 49.9039
|  |  | 44737.2047 | 49.9039
|  |  | 44737.2047 | 49.9038
|  |  | 44737.2047 | 49.9038
|  |  | 44737.2047 | 49.9037
|  |  | 44737.2047 | 49.9037
|  |  | 44737.2047 | 49.9037
|  |  | 44737.2047 | 49.9036
|  |  | 44737.2047 | 49.9036
|  |  | 44737.2047 | 49.9036
|  |  | 44737.2047 | 49.9035
|  |  | 44737.2047 | 49.9034
|  |  | 44737.2047 | 49.9033
|  |  | 44737.2047 | 49.9033
|  |  | 44737.2047 | 49.9032
|  |  | 44737.2047 | 49.9032
|  |  | 44737.2047 | 49.9032
|  |  | 44737.2047 | 49.9031
|  |  | 44737.2047 | 49.9031
|  |  | 44737.2047 | 49.9031
|  |  | 44737.2047 | 49.9031
|  |  | 44737.2047 | 49.9031
|  |  | 44737.2047 | 49.9031
|  |  | 44737.2047 | 49.9031
|  |  | 44737.2047 | 49.903
|  |  | 44737.2047 | 49.903
|  |  | 44737.2047 | 49.9029
|  |  | 44737.2047 | 49.9029
|  |  | 44737.2047 | 49.9028
|  |  | 44737.2047 | 49.9028
|  |  | 44737.2047 | 49.9027
|  |  | 44737.2047 | 49.9027
|  |  | 44737.2047 | 49.9027
|  |  | 44737.2047 | 49.9026
|  |  | 44737.2047 | 49.9026
|  |  | 2022-06-25 04:55 | 49.9026
|  |  | 44737.2047 | 49.9025
|  |  | 44737.2047 | 49.9025
|  |  | 44737.2047 | 49.9025
|  |  | 44737.2047 | 49.9024
|  |  | 44737.2047 | 49.9024
|  |  | 44737.2047 | 49.9024
|  |  | 44737.2047 | 49.9023
|  |  | 44737.2047 | 49.9023
|  |  | 44737.2047 | 49.9022
|  |  | 44737.2047 | 49.9021
|  |  | 44737.2047 | 49.9021
|  |  | 44737.2047 | 49.902
|  |  | 44737.2047 | 49.902
|  |  | 44737.2047 | 49.9019
|  |  | 44737.2047 | 49.9019
|  |  | 44737.2047 | 49.9019
|  |  | 44737.2047 | 49.9019
|  |  | 44737.2047 | 49.9019
|  |  | 44737.2047 | 49.9019
|  |  | 44737.2047 | 49.9018
|  |  | 44737.2048 | 49.9018
|  |  | 44737.2048 | 49.9018
|  |  | 44737.2048 | 49.9017
|  |  | 44737.2048 | 49.9017
|  |  | 44737.2048 | 49.9016
|  |  | 44737.2048 | 49.9016
|  |  | 44737.2048 | 49.9015
|  |  | 44737.2048 | 49.9014
|  |  | 44737.2048 | 49.9014
|  |  | 44737.2048 | 49.9012
|  |  | 44737.2048 | 49.9011
|  |  | 44737.2048 | 49.9011
|  |  | 44737.2048 | 49.9011
|  |  | 44737.2048 | 49.9011
|  |  | 44737.2048 | 49.9011
|  |  | 44737.2048 | 49.9011
|  |  | 44737.2048 | 49.9012
|  |  | 44737.2048 | 49.9012
|  |  | 44737.2048 | 49.9012
|  |  | 44737.2048 | 49.9012
|  |  | 44737.2048 | 49.9012
|  |  | 44737.2048 | 49.9012
|  |  | 44737.2048 | 49.9012
|  |  | 44737.2048 | 49.9012
|  |  | 44737.2048 | 49.9011
|  |  | 44737.2048 | 49.9011
|  |  | 44737.2048 | 49.9011
|  |  | 44737.2048 | 49.901
|  |  | 44737.2048 | 49.901
|  |  | 2022-06-25 04:55 | 49.901
|  |  | 44737.2048 | 49.901
|  |  | 44737.2048 | 49.901
|  |  | 44737.2048 | 49.901
|  |  | 44737.2048 | 49.9009
|  |  | 44737.2048 | 49.9009
|  |  | 44737.2048 | 49.9008
|  |  | 44737.2048 | 49.9008
|  |  | 44737.2048 | 49.9008
|  |  | 44737.2048 | 49.9007
|  |  | 44737.2048 | 49.9007
|  |  | 44737.2048 | 49.9007
|  |  | 44737.2048 | 49.9007
|  |  | 44737.2048 | 49.9007
|  |  | 44737.2048 | 49.9007
|  |  | 44737.2048 | 49.9007
|  |  | 44737.2048 | 49.9008
|  |  | 44737.2048 | 49.9008
|  |  | 44737.2048 | 49.9008
|  |  | 44737.2048 | 49.9008
|  |  | 44737.2048 | 49.9008
|  |  | 44737.2048 | 49.9007
|  |  | 44737.2048 | 49.9007
|  |  | 44737.2048 | 49.9007
|  |  | 44737.2048 | 49.9007
|  |  | 44737.2048 | 49.9007
|  |  | 44737.2048 | 49.9007
|  |  | 44737.2048 | 49.9007
|  |  | 44737.2048 | 49.9007
|  |  | 44737.2048 | 49.9006
|  |  | 44737.2048 | 49.9006
|  |  | 44737.2048 | 49.9005
|  |  | 44737.2048 | 49.9005
|  |  | 44737.2048 | 49.9004
|  |  | 44737.2048 | 49.9004
|  |  | 44737.2048 | 49.9003
|  |  | 44737.2048 | 49.9004
|  |  | 44737.2048 | 49.9004
|  |  | 44737.2048 | 49.9004
|  |  | 44737.2048 | 49.9004
|  |  | 44737.2048 | 49.9004
|  |  | 44737.2048 | 49.9003
|  |  | 44737.2048 | 49.9003
|  |  | 44737.2048 | 49.9002
|  |  | 44737.2048 | 49.9002
|  |  | 44737.2048 | 49.9001
|  |  | 44737.2048 | 49.9001
|  |  | 44737.2048 | 49.9001
|  |  | 44737.2048 | 49.9001
|  |  | 44737.2048 | 49.9001
|  |  | 2022-06-25 04:55 | 49.9001
|  |  | 44737.2048 | 49.9
|  |  | 44737.2048 | 49.9
|  |  | 44737.2048 | 49.9
|  |  | 44737.2048 | 49.9
|  |  | 44737.2048 | 49.9
|  |  | 44737.2048 | 49.9
|  |  | 44737.2048 | 49.9
|  |  | 44737.2048 | 49.9
|  |  | 44737.2048 | 49.9001
|  |  | 44737.2048 | 49.9
|  |  | 44737.2048 | 49.8999
|  |  | 44737.2048 | 49.8998
|  |  | 44737.2048 | 49.8998
|  |  | 44737.2048 | 49.8997
|  |  | 44737.2048 | 49.8997
|  |  | 44737.2048 | 49.8996
|  |  | 44737.2048 | 49.8996
|  |  | 44737.2048 | 49.8997
|  |  | 44737.2048 | 49.8997
|  |  | 44737.2048 | 49.8997
|  |  | 44737.2048 | 49.8997
|  |  | 44737.2048 | 49.8997
|  |  | 44737.2048 | 49.8997
|  |  | 44737.2048 | 49.8997
|  |  | 44737.2048 | 49.8997
|  |  | 44737.2048 | 49.8996
|  |  | 44737.2048 | 49.8995
|  |  | 44737.2048 | 49.8995
|  |  | 44737.2048 | 49.8994
|  |  | 44737.2048 | 49.8993
|  |  | 44737.2048 | 49.8992
|  |  | 44737.2048 | 49.8991
|  |  | 44737.2048 | 49.899
|  |  | 44737.2048 | 49.899
|  |  | 44737.2048 | 49.899
|  |  | 44737.2048 | 49.899
|  |  | 44737.2048 | 49.899
|  |  | 44737.2048 | 49.899
|  |  | 44737.2048 | 49.899
|  |  | 44737.2048 | 49.8989
|  |  | 44737.2048 | 49.8989
|  |  | 44737.2048 | 49.8989
|  |  | 44737.2048 | 49.8988
|  |  | 44737.2048 | 49.8987
|  |  | 44737.2048 | 49.8986
|  |  | 44737.2048 | 49.8985
|  |  | 44737.2048 | 49.8984
|  |  | 44737.2048 | 49.8984
|  |  | 44737.2048 | 49.8984
|  |  | 2022-06-25 04:55 | 49.8985
|  |  | 44737.2048 | 49.8986
|  |  | 44737.2048 | 49.8987
|  |  | 44737.2048 | 49.8988
|  |  | 44737.2048 | 49.8988
|  |  | 44737.2048 | 49.8989
|  |  | 44737.2048 | 49.8989
|  |  | 44737.2048 | 49.8989
|  |  | 44737.2048 | 49.8989
|  |  | 44737.2048 | 49.8989
|  |  | 44737.2048 | 49.8989
|  |  | 44737.2048 | 49.8988
|  |  | 44737.2048 | 49.8987
|  |  | 44737.2048 | 49.8987
|  |  | 44737.2048 | 49.8986
|  |  | 44737.2048 | 49.8986
|  |  | 44737.2048 | 49.8985
|  |  | 44737.2048 | 49.8985
|  |  | 44737.2048 | 49.8984
|  |  | 44737.2048 | 49.8984
|  |  | 44737.2048 | 49.8983
|  |  | 44737.2048 | 49.8983
|  |  | 44737.2048 | 49.8983
|  |  | 44737.2048 | 49.8982
|  |  | 44737.2048 | 49.8982
|  |  | 44737.2048 | 49.8982
|  |  | 44737.2048 | 49.8981
|  |  | 44737.2048 | 49.898
|  |  | 44737.2048 | 49.898
|  |  | 44737.2048 | 49.8979
|  |  | 44737.2048 | 49.8979
|  |  | 44737.2048 | 49.8979
|  |  | 44737.2048 | 49.8978
|  |  | 44737.2048 | 49.8979
|  |  | 44737.2048 | 49.8979
|  |  | 44737.2048 | 49.8979
|  |  | 44737.2048 | 49.8979
|  |  | 44737.2048 | 49.898
|  |  | 44737.2048 | 49.8979
|  |  | 44737.2048 | 49.8979
|  |  | 44737.2048 | 49.8979
|  |  | 44737.2048 | 49.8979
|  |  | 44737.2048 | 49.898
|  |  | 44737.2048 | 49.8979
|  |  | 44737.2048 | 49.8979
|  |  | 44737.2048 | 49.8978
|  |  | 44737.2048 | 49.8978
|  |  | 44737.2048 | 49.8979
|  |  | 44737.2048 | 49.8979
|  |  | 44737.2048 | 49.898
|  |  | 2022-06-25 04:55 | 49.898
|  |  | 44737.2048 | 49.8981
|  |  | 44737.2048 | 49.8981
|  |  | 44737.2048 | 49.8982
|  |  | 44737.2048 | 49.8983
|  |  | 44737.2048 | 49.8983
|  |  | 44737.2048 | 49.8983
|  |  | 44737.2048 | 49.8982
|  |  | 44737.2048 | 49.8982
|  |  | 44737.2048 | 49.8981
|  |  | 44737.2048 | 49.8981
|  |  | 44737.2048 | 49.8981
|  |  | 44737.2048 | 49.8981
|  |  | 44737.2048 | 49.8981
|  |  | 44737.2048 | 49.8981
|  |  | 44737.2048 | 49.8982
|  |  | 44737.2048 | 49.8983
|  |  | 44737.2048 | 49.8983
|  |  | 44737.2048 | 49.8983
|  |  | 44737.2048 | 49.8984
|  |  | 44737.2048 | 49.8984
|  |  | 44737.2048 | 49.8984
|  |  | 44737.2048 | 49.8983
|  |  | 44737.2048 | 49.8983
|  |  | 44737.2048 | 49.8983
|  |  | 44737.2048 | 49.8983
|  |  | 44737.2048 | 49.8982
|  |  | 44737.2048 | 49.8982
|  |  | 44737.2048 | 49.8982
|  |  | 44737.2048 | 49.8982
|  |  | 44737.2048 | 49.8982
|  |  | 44737.2048 | 49.8982
|  |  | 44737.2048 | 49.8982
|  |  | 44737.2048 | 49.8983
|  |  | 44737.2048 | 49.8983
|  |  | 44737.2048 | 49.8984
|  |  | 44737.2048 | 49.8984
|  |  | 44737.2048 | 49.8984
|  |  | 44737.2048 | 49.8984
|  |  | 44737.2048 | 49.8984
|  |  | 44737.2048 | 49.8984
|  |  | 44737.2048 | 49.8984
|  |  | 44737.2048 | 49.8983
|  |  | 44737.2048 | 49.8983
|  |  | 44737.2048 | 49.8982
|  |  | 44737.2048 | 49.8982
|  |  | 44737.2048 | 49.8983
|  |  | 44737.2048 | 49.8983
|  |  | 44737.2048 | 49.8983
|  |  | 44737.2048 | 49.8984
|  |  | 2022-06-25 04:55 | 49.8984
|  |  | 44737.2048 | 49.8985
|  |  | 44737.2048 | 49.8986
|  |  | 44737.2048 | 49.8987
|  |  | 44737.2048 | 49.8987
|  |  | 44737.2048 | 49.8988
|  |  | 44737.2048 | 49.8989
|  |  | 44737.2048 | 49.8989
|  |  | 44737.2048 | 49.899
|  |  | 44737.2048 | 49.899
|  |  | 44737.2048 | 49.899
|  |  | 44737.2048 | 49.899
|  |  | 44737.2048 | 49.899
|  |  | 44737.2048 | 49.899
|  |  | 44737.2048 | 49.899
|  |  | 44737.2048 | 49.899
|  |  | 44737.2048 | 49.899
|  |  | 44737.2048 | 49.899
|  |  | 44737.2048 | 49.899
|  |  | 44737.2048 | 49.899
|  |  | 44737.2048 | 49.899
|  |  | 44737.2048 | 49.8991
|  |  | 44737.2048 | 49.8991
|  |  | 44737.2048 | 49.899
|  |  | 44737.2048 | 49.899
|  |  | 44737.2048 | 49.8991
|  |  | 44737.2048 | 49.8991
|  |  | 44737.2048 | 49.8991
|  |  | 44737.2048 | 49.8992
|  |  | 44737.2048 | 49.8993
|  |  | 44737.2048 | 49.8993
|  |  | 44737.2048 | 49.8994
|  |  | 44737.2048 | 49.8994
|  |  | 44737.2048 | 49.8993
|  |  | 44737.2048 | 49.8993
|  |  | 44737.2048 | 49.8993
|  |  | 44737.2048 | 49.8993
|  |  | 44737.2048 | 49.8992
|  |  | 44737.2048 | 49.8992
|  |  | 44737.2048 | 49.8992
|  |  | 44737.2048 | 49.8992
|  |  | 44737.2048 | 49.8992
|  |  | 44737.2048 | 49.8993
|  |  | 44737.2048 | 49.8993
|  |  | 44737.2048 | 49.8994
|  |  | 44737.2048 | 49.8995
|  |  | 44737.2048 | 49.8995
|  |  | 44737.2048 | 49.8996
|  |  | 44737.2048 | 49.8996
|  |  | 44737.2048 | 49.8996
|  |  | 2022-06-25 04:55 | 49.8996
|  |  | 44737.2048 | 49.8996
|  |  | 44737.2048 | 49.8996
|  |  | 44737.2048 | 49.8996
|  |  | 44737.2048 | 49.8996
|  |  | 44737.2048 | 49.8996
|  |  | 44737.2048 | 49.8996
|  |  | 44737.2048 | 49.8995
|  |  | 44737.2048 | 49.8995
|  |  | 44737.2048 | 49.8995
|  |  | 44737.2048 | 49.8995
|  |  | 44737.2048 | 49.8995
|  |  | 44737.2048 | 49.8995
|  |  | 44737.2048 | 49.8995
|  |  | 44737.2048 | 49.8995
|  |  | 44737.2048 | 49.8995
|  |  | 44737.2048 | 49.8995
|  |  | 44737.2048 | 49.8995
|  |  | 44737.2048 | 49.8996
|  |  | 44737.2048 | 49.8996
|  |  | 44737.2048 | 49.8996
|  |  | 44737.2048 | 49.8996
|  |  | 44737.2048 | 49.8996
|  |  | 44737.2048 | 49.8997
|  |  | 44737.2048 | 49.8997
|  |  | 44737.2048 | 49.8997
|  |  | 44737.2048 | 49.8997
|  |  | 44737.2048 | 49.8997
|  |  | 44737.2048 | 49.8997
|  |  | 44737.2048 | 49.8996
|  |  | 44737.2048 | 49.8997
|  |  | 44737.2048 | 49.8997
|  |  | 44737.2048 | 49.8997
|  |  | 44737.2048 | 49.8997
|  |  | 44737.2048 | 49.8997
|  |  | 44737.2048 | 49.8997
|  |  | 44737.2048 | 49.8997
|  |  | 44737.2048 | 49.8997
|  |  | 44737.2048 | 49.8998
|  |  | 44737.2048 | 49.8998
|  |  | 44737.2048 | 49.8998
|  |  | 44737.2048 | 49.8999
|  |  | 44737.2048 | 49.8999
|  |  | 44737.2048 | 49.8999
|  |  | 44737.2048 | 49.8998
|  |  | 44737.2048 | 49.8997
|  |  | 44737.2048 | 49.8997
|  |  | 44737.2048 | 49.8996
|  |  | 44737.2048 | 49.8996
|  |  | 44737.2048 | 49.8996
|  |  | 2022-06-25 04:55 | 49.8996
|  |  | 44737.2048 | 49.8996
|  |  | 44737.2048 | 49.8996
|  |  | 44737.2048 | 49.8996
|  |  | 44737.2048 | 49.8996
|  |  | 44737.2048 | 49.8997
|  |  | 44737.2048 | 49.8997
|  |  | 44737.2048 | 49.8997
|  |  | 44737.2048 | 49.8997
|  |  | 44737.2048 | 49.8997
|  |  | 44737.2048 | 49.8996
|  |  | 44737.2048 | 49.8996
|  |  | 44737.2048 | 49.8995
|  |  | 44737.2048 | 49.8994
|  |  | 44737.2048 | 49.8994
|  |  | 44737.2048 | 49.8993
|  |  | 44737.2048 | 49.8992
|  |  | 44737.2048 | 49.8992
|  |  | 44737.2048 | 49.8992
|  |  | 44737.2048 | 49.8992
|  |  | 44737.2048 | 49.8991
|  |  | 44737.2048 | 49.8991
|  |  | 44737.2048 | 49.8991
|  |  | 44737.2048 | 49.8991
|  |  | 44737.2048 | 49.8991
|  |  | 44737.2048 | 49.8991
|  |  | 44737.2048 | 49.899
|  |  | 44737.2048 | 49.899
|  |  | 44737.2048 | 49.899
|  |  | 44737.2048 | 49.899
|  |  | 44737.2048 | 49.899
|  |  | 44737.2048 | 49.899
|  |  | 44737.2048 | 49.899
|  |  | 44737.2048 | 49.8989
|  |  | 44737.2048 | 49.8989
|  |  | 44737.2048 | 49.8989
|  |  | 44737.2048 | 49.8988
|  |  | 44737.2048 | 49.8988
|  |  | 44737.2048 | 49.8988
|  |  | 44737.2048 | 49.8988
|  |  | 44737.2048 | 49.8988
|  |  | 44737.2048 | 49.8989
|  |  | 44737.2048 | 49.8989
|  |  | 44737.2048 | 49.899
|  |  | 44737.2048 | 49.899
|  |  | 44737.2048 | 49.899
|  |  | 44737.2048 | 49.899
|  |  | 44737.2048 | 49.899
|  |  | 44737.2048 | 49.8989
|  |  | 44737.2048 | 49.8989
|  |  | 2022-06-25 04:55 | 49.8989
|  |  | 44737.2048 | 49.8989
|  |  | 44737.2048 | 49.8988
|  |  | 44737.2048 | 49.8988
|  |  | 44737.2048 | 49.8988
|  |  | 44737.2048 | 49.8989
|  |  | 44737.2048 | 49.899
|  |  | 44737.2048 | 49.899
|  |  | 44737.2048 | 49.899
|  |  | 44737.2048 | 49.899
|  |  | 44737.2048 | 49.8989
|  |  | 44737.2048 | 49.8989
|  |  | 44737.2048 | 49.8988
|  |  | 44737.2048 | 49.8987
|  |  | 44737.2048 | 49.8987
|  |  | 44737.2048 | 49.8986
|  |  | 44737.2048 | 49.8985
|  |  | 44737.2048 | 49.8985
|  |  | 44737.2048 | 49.8984
|  |  | 44737.2048 | 49.8984
|  |  | 44737.2048 | 49.8984
|  |  | 44737.2048 | 49.8983
|  |  | 44737.2048 | 49.8983
|  |  | 44737.2048 | 49.8983
|  |  | 44737.2048 | 49.8982
|  |  | 44737.2048 | 49.8982
|  |  | 44737.2048 | 49.8981
|  |  | 44737.2048 | 49.8981
|  |  | 44737.2048 | 49.898
|  |  | 44737.2048 | 49.898
|  |  | 44737.2048 | 49.8979
|  |  | 44737.2048 | 49.8979
|  |  | 44737.2048 | 49.8978
|  |  | 44737.2048 | 49.8978
|  |  | 44737.2048 | 49.8979
|  |  | 44737.2048 | 49.8979
|  |  | 44737.2048 | 49.8979
|  |  | 44737.2048 | 49.8979
|  |  | 44737.2048 | 49.898
|  |  | 44737.2048 | 49.898
|  |  | 44737.2048 | 49.898
|  |  | 44737.2048 | 49.8979
|  |  | 44737.2048 | 49.8979
|  |  | 44737.2048 | 49.8978
|  |  | 44737.2048 | 49.8978
|  |  | 44737.2048 | 49.8977
|  |  | 44737.2048 | 49.8976
|  |  | 44737.2048 | 49.8976
|  |  | 44737.2048 | 49.8976
|  |  | 44737.2048 | 49.8976
|  |  | 2022-06-25 04:55 | 49.8976
|  |  | 44737.2048 | 49.8976
|  |  | 44737.2049 | 49.8976
|  |  | 44737.2049 | 49.8977
|  |  | 44737.2049 | 49.8977
|  |  | 44737.2049 | 49.8977
|  |  | 44737.2049 | 49.8977
|  |  | 44737.2049 | 49.8978
|  |  | 44737.2049 | 49.8978
|  |  | 44737.2049 | 49.8978
|  |  | 44737.2049 | 49.8978
|  |  | 44737.2049 | 49.8978
|  |  | 44737.2049 | 49.8978
|  |  | 44737.2049 | 49.8978
|  |  | 44737.2049 | 49.8977
|  |  | 44737.2049 | 49.8976
|  |  | 44737.2049 | 49.8976
|  |  | 44737.2049 | 49.8975
|  |  | 44737.2049 | 49.8975
|  |  | 44737.2049 | 49.8974
|  |  | 44737.2049 | 49.8973
|  |  | 44737.2049 | 49.8973
|  |  | 44737.2049 | 49.8973
|  |  | 44737.2049 | 49.8972
|  |  | 44737.2049 | 49.8972
|  |  | 44737.2049 | 49.8972
|  |  | 44737.2049 | 49.8971
|  |  | 44737.2049 | 49.8971
|  |  | 44737.2049 | 49.8971
|  |  | 44737.2049 | 49.897
|  |  | 44737.2049 | 49.897
|  |  | 44737.2049 | 49.8969
|  |  | 44737.2049 | 49.8969
|  |  | 44737.2049 | 49.8969
|  |  | 44737.2049 | 49.8968
|  |  | 44737.2049 | 49.8968
|  |  | 44737.2049 | 49.8967
|  |  | 44737.2049 | 49.8967
|  |  | 44737.2049 | 49.8968
|  |  | 44737.2049 | 49.8968
|  |  | 44737.2049 | 49.8968
|  |  | 44737.2049 | 49.8968
|  |  | 44737.2049 | 49.8968
|  |  | 44737.2049 | 49.8968
|  |  | 44737.2049 | 49.8967
|  |  | 44737.2049 | 49.8967
|  |  | 44737.2049 | 49.8966
|  |  | 44737.2049 | 49.8966
|  |  | 44737.2049 | 49.8966
|  |  | 44737.2049 | 49.8966
|  |  | 2022-06-25 04:55 | 49.8965

## 20220626-1
In GMT |  |  | High resolution Incident data
Date | Time | Freq | time | freq
2022-06-25 | 23:01 | 50.028 | 2022-06-26 00:01 | 50.0403
2022-06-25 | 23:01 | 50.028 | 44738.0009 | 50.0404
2022-06-25 | 23:01 | 50.029 | 44738.0009 | 50.0405
2022-06-25 | 23:01 | 50.032 | 44738.0009 | 50.0406
2022-06-25 | 23:01 | 50.034 | 44738.0009 | 50.0405
2022-06-25 | 23:01 | 50.037 | 44738.0009 | 50.0405
2022-06-25 | 23:01 | 50.039 | 44738.0009 | 50.0405
2022-06-25 | 23:01 | 50.039 | 44738.0009 | 50.0404
2022-06-25 | 23:01 | 50.039 | 44738.0009 | 50.0403
2022-06-25 | 23:01 | 50.04 | 44738.0009 | 50.0402
2022-06-25 | 23:01 | 50.038 | 44738.0009 | 50.0402
2022-06-25 | 23:01 | 50.038 | 44738.0009 | 50.0402
2022-06-25 | 23:01 | 50.036 | 44738.0009 | 50.0403
2022-06-25 | 23:01 | 50.037 | 44738.0009 | 50.0404
2022-06-25 | 23:01 | 50.034 | 44738.0009 | 50.0406
2022-06-25 | 23:01 | 50.033 | 44738.0009 | 50.0408
2022-06-25 | 23:01 | 50.034 | 44738.0009 | 50.041
2022-06-25 | 23:01 | 50.035 | 44738.0009 | 50.0411
2022-06-25 | 23:01 | 50.037 | 44738.0009 | 50.0413
2022-06-25 | 23:01 | 50.039 | 44738.0009 | 50.0414
2022-06-25 | 23:01 | 50.038 | 44738.0009 | 50.0415
2022-06-25 | 23:01 | 50.041 | 44738.0009 | 50.0415
2022-06-25 | 23:01 | 50.042 | 44738.0009 | 50.0415
2022-06-25 | 23:01 | 50.039 | 44738.0009 | 50.0415
2022-06-25 | 23:01 | 50.038 | 44738.0009 | 50.0415
2022-06-25 | 23:01 | 50.034 | 44738.0009 | 50.0414
2022-06-25 | 23:01 | 50.033 | 44738.0009 | 50.0414
2022-06-25 | 23:01 | 50.03 | 44738.0009 | 50.0414
2022-06-25 | 23:01 | 50.031 | 44738.0009 | 50.0414
2022-06-25 | 23:01 | 50.03 | 44738.0009 | 50.0414
2022-06-25 | 23:02 | 50.032 | 44738.0009 | 50.0415
2022-06-25 | 23:02 | 50.034 | 44738.0009 | 50.0416
2022-06-25 | 23:02 | 50.035 | 44738.0009 | 50.0417
2022-06-25 | 23:02 | 50.034 | 44738.0009 | 50.0418
2022-06-25 | 23:02 | 50.035 | 44738.0009 | 50.0419
2022-06-25 | 23:02 | 50.032 | 44738.0009 | 50.042
2022-06-25 | 23:02 | 50.031 | 44738.0009 | 50.0421
2022-06-25 | 23:02 | 50.03 | 44738.0009 | 50.0421
2022-06-25 | 23:02 | 50.028 | 44738.0009 | 50.0421
2022-06-25 | 23:02 | 50.028 | 44738.0009 | 50.0421
2022-06-25 | 23:02 | 50.029 | 44738.0009 | 50.0421
2022-06-25 | 23:02 | 50.028 | 44738.0009 | 50.0421
2022-06-25 | 23:02 | 50.028 | 44738.0009 | 50.0422
2022-06-25 | 23:02 | 50.029 | 44738.0009 | 50.0423
2022-06-25 | 23:02 | 50.03 | 44738.0009 | 50.0424
2022-06-25 | 23:02 | 50.03 | 44738.0009 | 50.0424
2022-06-25 | 23:02 | 50.029 | 44738.0009 | 50.0425
2022-06-25 | 23:02 | 50.027 | 44738.0009 | 50.0426
2022-06-25 | 23:02 | 50.023 | 44738.0009 | 50.0427
2022-06-25 | 23:02 | 50.019 | 44738.0009 | 50.0427
2022-06-25 | 23:02 | 49.994 | 2022-06-26 00:01 | 50.0427
2022-06-25 | 23:02 | 49.945 | 44738.0009 | 50.0427
2022-06-25 | 23:02 | 49.891 | 44738.0009 | 50.0427
2022-06-25 | 23:02 | 49.86 | 44738.0009 | 50.0426
2022-06-25 | 23:02 | 49.844 | 44738.0009 | 50.0426
2022-06-25 | 23:02 | 49.841 | 44738.0009 | 50.0426
2022-06-25 | 23:02 | 49.845 | 44738.0009 | 50.0427
2022-06-25 | 23:02 | 49.853 | 44738.0009 | 50.0428
2022-06-25 | 23:02 | 49.864 | 44738.0009 | 50.0428
2022-06-25 | 23:02 | 49.87 | 44738.0009 | 50.0429
2022-06-25 | 23:02 | 49.876 | 44738.0009 | 50.043
2022-06-25 | 23:02 | 49.874 | 44738.0009 | 50.043
2022-06-25 | 23:02 | 49.874 | 44738.0009 | 50.0431
2022-06-25 | 23:02 | 49.875 | 44738.0009 | 50.043
2022-06-25 | 23:02 | 49.872 | 44738.0009 | 50.043
2022-06-25 | 23:02 | 49.871 | 44738.0009 | 50.0429
2022-06-25 | 23:02 | 49.868 | 44738.0009 | 50.0429
2022-06-25 | 23:02 | 49.868 | 44738.0009 | 50.0429
2022-06-25 | 23:02 | 49.867 | 44738.0009 | 50.0429
2022-06-25 | 23:02 | 49.867 | 44738.0009 | 50.0429
2022-06-25 | 23:02 | 49.866 | 44738.0009 | 50.043
2022-06-25 | 23:02 | 49.866 | 44738.0009 | 50.043
2022-06-25 | 23:02 | 49.867 | 44738.0009 | 50.043
2022-06-25 | 23:02 | 49.867 | 44738.0009 | 50.043
2022-06-25 | 23:02 | 49.868 | 44738.0009 | 50.043
2022-06-25 | 23:02 | 49.87 | 44738.0009 | 50.0429
2022-06-25 | 23:02 | 49.875 | 44738.0009 | 50.0428
2022-06-25 | 23:02 | 49.876 | 44738.0009 | 50.0428
2022-06-25 | 23:02 | 49.879 | 44738.0009 | 50.0427
2022-06-25 | 23:02 | 49.882 | 44738.0009 | 50.0427
2022-06-25 | 23:02 | 49.882 | 44738.0009 | 50.0427
2022-06-25 | 23:02 | 49.886 | 44738.0009 | 50.0428
2022-06-25 | 23:02 | 49.885 | 44738.0009 | 50.0428
2022-06-25 | 23:02 | 49.882 | 44738.0009 | 50.0428
2022-06-25 | 23:02 | 49.878 | 44738.0009 | 50.0429
2022-06-25 | 23:02 | 49.877 | 44738.0009 | 50.0429
2022-06-25 | 23:02 | 49.873 | 44738.0009 | 50.0429
2022-06-25 | 23:02 | 49.873 | 44738.0009 | 50.0428
2022-06-25 | 23:02 | 49.87 | 44738.0009 | 50.0428
2022-06-25 | 23:02 | 49.872 | 44738.0009 | 50.0427
2022-06-25 | 23:03 | 49.871 | 44738.0009 | 50.0426
2022-06-25 | 23:03 | 49.869 | 44738.0009 | 50.0425
2022-06-25 | 23:03 | 49.868 | 44738.0009 | 50.0425
2022-06-25 | 23:03 | 49.866 | 44738.0009 | 50.0424
2022-06-25 | 23:03 | 49.865 | 44738.0009 | 50.0424
2022-06-25 | 23:03 | 49.862 | 44738.0009 | 50.0424
2022-06-25 | 23:03 | 49.862 | 44738.0009 | 50.0424
2022-06-25 | 23:03 | 49.863 | 44738.0009 | 50.0424
2022-06-25 | 23:03 | 49.864 | 44738.0009 | 50.0424
2022-06-25 | 23:03 | 49.865 | 44738.0009 | 50.0424
2022-06-25 | 23:03 | 49.865 | 2022-06-26 00:01 | 50.0424
2022-06-25 | 23:03 | 49.865 | 44738.0009 | 50.0423
2022-06-25 | 23:03 | 49.865 | 44738.0009 | 50.0423
2022-06-25 | 23:03 | 49.866 | 44738.0009 | 50.0423
2022-06-25 | 23:03 | 49.866 | 44738.001 | 50.0422
2022-06-25 | 23:03 | 49.87 | 44738.001 | 50.0422
2022-06-25 | 23:03 | 49.87 | 44738.001 | 50.0422
2022-06-25 | 23:03 | 49.873 | 44738.001 | 50.0422
2022-06-25 | 23:03 | 49.876 | 44738.001 | 50.0423
2022-06-25 | 23:03 | 49.875 | 44738.001 | 50.0423
2022-06-25 | 23:03 | 49.877 | 44738.001 | 50.0423
2022-06-25 | 23:03 | 49.875 | 44738.001 | 50.0423
2022-06-25 | 23:03 | 49.877 | 44738.001 | 50.0422
2022-06-25 | 23:03 | 49.88 | 44738.001 | 50.0422
2022-06-25 | 23:03 | 49.881 | 44738.001 | 50.0421
2022-06-25 | 23:03 | 49.878 | 44738.001 | 50.0421
2022-06-25 | 23:03 | 49.875 | 44738.001 | 50.042
2022-06-25 | 23:03 | 49.874 | 44738.001 | 50.042
2022-06-25 | 23:03 | 49.87 | 44738.001 | 50.0421
2022-06-25 | 23:03 | 49.869 | 44738.001 | 50.0421
2022-06-25 | 23:03 | 49.868 | 44738.001 | 50.0421
2022-06-25 | 23:03 | 49.866 | 44738.001 | 50.0421
2022-06-25 | 23:03 | 49.868 | 44738.001 | 50.0419
2022-06-25 | 23:03 | 49.865 | 44738.001 | 50.0419
2022-06-25 | 23:03 | 49.866 | 44738.001 | 50.0418
2022-06-25 | 23:03 | 49.866 | 44738.001 | 50.0418
2022-06-25 | 23:03 | 49.867 | 44738.001 | 50.0417
2022-06-25 | 23:03 | 49.865 | 44738.001 | 50.0417
2022-06-25 | 23:03 | 49.866 | 44738.001 | 50.0416
2022-06-25 | 23:03 | 49.863 | 44738.001 | 50.0415
2022-06-25 | 23:03 | 49.863 | 44738.001 | 50.0414
2022-06-25 | 23:03 | 49.865 | 44738.001 | 50.0414
2022-06-25 | 23:03 | 49.868 | 44738.001 | 50.0412
2022-06-25 | 23:03 | 49.869 | 44738.001 | 50.0412
2022-06-25 | 23:03 | 49.866 | 44738.001 | 50.0411
2022-06-25 | 23:03 | 49.866 | 44738.001 | 50.0411
2022-06-25 | 23:03 | 49.865 | 44738.001 | 50.0411
2022-06-25 | 23:03 | 49.863 | 44738.001 | 50.041
2022-06-25 | 23:03 | 49.862 | 44738.001 | 50.041
2022-06-25 | 23:03 | 49.863 | 44738.001 | 50.041
2022-06-25 | 23:03 | 49.86 | 44738.001 | 50.0409
2022-06-25 | 23:03 | 49.861 | 44738.001 | 50.0408
2022-06-25 | 23:03 | 49.863 | 44738.001 | 50.0408
2022-06-25 | 23:03 | 49.865 | 44738.001 | 50.0406
2022-06-25 | 23:03 | 49.866 | 44738.001 | 50.0405
2022-06-25 | 23:03 | 49.87 | 44738.001 | 50.0403
2022-06-25 | 23:03 | 49.872 | 44738.001 | 50.0401
2022-06-25 | 23:03 | 49.873 | 44738.001 | 50.0399
2022-06-25 | 23:03 | 49.872 | 44738.001 | 50.0398
2022-06-25 | 23:03 | 49.871 | 44738.001 | 50.0396
2022-06-25 | 23:04 | 49.871 | 2022-06-26 00:01 | 50.0395
2022-06-25 | 23:04 | 49.872 | 44738.001 | 50.0395
2022-06-25 | 23:04 | 49.874 | 44738.001 | 50.0394
2022-06-25 | 23:04 | 49.876 | 44738.001 | 50.0394
2022-06-25 | 23:04 | 49.878 | 44738.001 | 50.0393
2022-06-25 | 23:04 | 49.879 | 44738.001 | 50.0393
2022-06-25 | 23:04 | 49.881 | 44738.001 | 50.0393
2022-06-25 | 23:04 | 49.883 | 44738.001 | 50.0393
2022-06-25 | 23:04 | 49.889 | 44738.001 | 50.0393
2022-06-25 | 23:04 | 49.898 | 44738.001 | 50.0393
2022-06-25 | 23:04 | 49.9 | 44738.001 | 50.0392
2022-06-25 | 23:04 | 49.906 | 44738.001 | 50.0393
2022-06-25 | 23:04 | 49.909 | 44738.001 | 50.0392
2022-06-25 | 23:04 | 49.909 | 44738.001 | 50.0392
2022-06-25 | 23:04 | 49.912 | 44738.001 | 50.0392
2022-06-25 | 23:04 | 49.914 | 44738.001 | 50.0391
2022-06-25 | 23:04 | 49.915 | 44738.001 | 50.039
2022-06-25 | 23:04 | 49.915 | 44738.001 | 50.0389
2022-06-25 | 23:04 | 49.913 | 44738.001 | 50.0389
2022-06-25 | 23:04 | 49.911 | 44738.001 | 50.0388
2022-06-25 | 23:04 | 49.91 | 44738.001 | 50.0388
2022-06-25 | 23:04 | 49.91 | 44738.001 | 50.0387
2022-06-25 | 23:04 | 49.91 | 44738.001 | 50.0387
2022-06-25 | 23:04 | 49.911 | 44738.001 | 50.0387
2022-06-25 | 23:04 | 49.912 | 44738.001 | 50.0387
2022-06-25 | 23:04 | 49.913 | 44738.001 | 50.0387
2022-06-25 | 23:04 | 49.915 | 44738.001 | 50.0387
2022-06-25 | 23:04 | 49.916 | 44738.001 | 50.0386
2022-06-25 | 23:04 | 49.916 | 44738.001 | 50.0386
2022-06-25 | 23:04 | 49.918 | 44738.001 | 50.0387
2022-06-25 | 23:04 | 49.919 | 44738.001 | 50.0387
2022-06-25 | 23:04 | 49.92 | 44738.001 | 50.0387
2022-06-25 | 23:04 | 49.921 | 44738.001 | 50.0387
2022-06-25 | 23:04 | 49.922 | 44738.001 | 50.0387
2022-06-25 | 23:04 | 49.923 | 44738.001 | 50.0386
2022-06-25 | 23:04 | 49.922 | 44738.001 | 50.0386
2022-06-25 | 23:04 | 49.92 | 44738.001 | 50.0384
2022-06-25 | 23:04 | 49.918 | 44738.001 | 50.0383
2022-06-25 | 23:04 | 49.917 | 44738.001 | 50.0382
2022-06-25 | 23:04 | 49.919 | 44738.001 | 50.0379
2022-06-25 | 23:04 | 49.918 | 44738.001 | 50.0378
2022-06-25 | 23:04 | 49.92 | 44738.001 | 50.0377
2022-06-25 | 23:04 | 49.918 | 44738.001 | 50.0377
2022-06-25 | 23:04 | 49.919 | 44738.001 | 50.0376
2022-06-25 | 23:04 | 49.917 | 44738.001 | 50.0376
2022-06-25 | 23:04 | 49.92 | 44738.001 | 50.0376
2022-06-25 | 23:04 | 49.921 | 44738.001 | 50.0376
2022-06-25 | 23:04 | 49.922 | 44738.001 | 50.0376
2022-06-25 | 23:04 | 49.922 | 44738.001 | 50.0376
2022-06-25 | 23:04 | 49.925 | 44738.001 | 50.0376
2022-06-25 | 23:04 | 49.926 | 2022-06-26 00:01 | 50.0375
2022-06-25 | 23:04 | 49.926 | 44738.001 | 50.0375
2022-06-25 | 23:04 | 49.922 | 44738.001 | 50.0374
2022-06-25 | 23:04 | 49.921 | 44738.001 | 50.0373
2022-06-25 | 23:04 | 49.92 | 44738.001 | 50.0373
2022-06-25 | 23:04 | 49.921 | 44738.001 | 50.0373
2022-06-25 | 23:04 | 49.923 | 44738.001 | 50.0372
2022-06-25 | 23:04 | 49.925 | 44738.001 | 50.0372
2022-06-25 | 23:04 | 49.927 | 44738.001 | 50.0371
2022-06-25 | 23:04 | 49.929 | 44738.001 | 50.037
2022-06-25 | 23:04 | 49.93 | 44738.001 | 50.037
2022-06-25 | 23:05 | 49.928 | 44738.001 | 50.0369
2022-06-25 | 23:05 | 49.927 | 44738.001 | 50.0368
2022-06-25 | 23:05 | 49.922 | 44738.001 | 50.0367
2022-06-25 | 23:05 | 49.922 | 44738.001 | 50.0367
2022-06-25 | 23:05 | 49.923 | 44738.001 | 50.0366
2022-06-25 | 23:05 | 49.926 | 44738.001 | 50.0366
2022-06-25 | 23:05 | 49.93 | 44738.001 | 50.0366
2022-06-25 | 23:05 | 49.931 | 44738.001 | 50.0367
2022-06-25 | 23:05 | 49.933 | 44738.001 | 50.0367
2022-06-25 | 23:05 | 49.936 | 44738.001 | 50.0367
2022-06-25 | 23:05 | 49.937 | 44738.001 | 50.0368
2022-06-25 | 23:05 | 49.938 | 44738.001 | 50.0367
2022-06-25 | 23:05 | 49.94 | 44738.001 | 50.0367
2022-06-25 | 23:05 | 49.939 | 44738.001 | 50.0366
2022-06-25 | 23:05 | 49.939 | 44738.001 | 50.0365
2022-06-25 | 23:05 | 49.94 | 44738.001 | 50.0364
2022-06-25 | 23:05 | 49.94 | 44738.001 | 50.0364
2022-06-25 | 23:05 | 49.938 | 44738.001 | 50.0363
2022-06-25 | 23:05 | 49.937 | 44738.001 | 50.0363
2022-06-25 | 23:05 | 49.934 | 44738.001 | 50.0363
2022-06-25 | 23:05 | 49.933 | 44738.001 | 50.0363
2022-06-25 | 23:05 | 49.934 | 44738.001 | 50.0363
2022-06-25 | 23:05 | 49.935 | 44738.001 | 50.0363
2022-06-25 | 23:05 | 49.939 | 44738.001 | 50.0363
2022-06-25 | 23:05 | 49.944 | 44738.001 | 50.0363
2022-06-25 | 23:05 | 49.947 | 44738.001 | 50.0363
2022-06-25 | 23:05 | 49.95 | 44738.001 | 50.0363
2022-06-25 | 23:05 | 49.952 | 44738.001 | 50.0363
2022-06-25 | 23:05 | 49.954 | 44738.001 | 50.0363
2022-06-25 | 23:05 | 49.953 | 44738.001 | 50.0363
2022-06-25 | 23:05 | 49.952 | 44738.001 | 50.0363
2022-06-25 | 23:05 | 49.95 | 44738.001 | 50.0362
2022-06-25 | 23:05 | 49.947 | 44738.001 | 50.0362
2022-06-25 | 23:05 | 49.945 | 44738.001 | 50.0361
2022-06-25 | 23:05 | 49.942 | 44738.001 | 50.0361
2022-06-25 | 23:05 | 49.941 | 44738.001 | 50.036
2022-06-25 | 23:05 | 49.939 | 44738.001 | 50.036
2022-06-25 | 23:05 | 49.938 | 44738.001 | 50.0359
2022-06-25 | 23:05 | 49.937 | 44738.001 | 50.0359
2022-06-25 | 23:05 | 49.938 | 2022-06-26 00:01 | 50.0359
2022-06-25 | 23:05 | 49.937 | 44738.001 | 50.0359
2022-06-25 | 23:05 | 49.937 | 44738.001 | 50.0358
2022-06-25 | 23:05 | 49.938 | 44738.001 | 50.0358
2022-06-25 | 23:05 | 49.938 | 44738.001 | 50.0358
2022-06-25 | 23:05 | 49.939 | 44738.001 | 50.0357
2022-06-25 | 23:05 | 49.941 | 44738.001 | 50.0357
2022-06-25 | 23:05 | 49.941 | 44738.001 | 50.0357
2022-06-25 | 23:05 | 49.943 | 44738.001 | 50.0356
2022-06-25 | 23:05 | 49.942 | 44738.001 | 50.0356
2022-06-25 | 23:05 | 49.942 | 44738.001 | 50.0356
2022-06-25 | 23:05 | 49.942 | 44738.001 | 50.0356
2022-06-25 | 23:05 | 49.94 | 44738.001 | 50.0355
2022-06-25 | 23:05 | 49.94 | 44738.001 | 50.0354
2022-06-25 | 23:05 | 49.939 | 44738.001 | 50.0354
2022-06-25 | 23:05 | 49.942 | 44738.001 | 50.0353
2022-06-25 | 23:05 | 49.943 | 44738.001 | 50.0353
2022-06-25 | 23:05 | 49.943 | 44738.001 | 50.0352
2022-06-25 | 23:05 | 49.944 | 44738.001 | 50.0351
2022-06-25 | 23:05 | 49.943 | 44738.001 | 50.0351
2022-06-25 | 23:06 | 49.943 | 44738.001 | 50.035
2022-06-25 | 23:06 | 49.944 | 44738.001 | 50.035
2022-06-25 | 23:06 | 49.943 | 44738.001 | 50.035
2022-06-25 | 23:06 | 49.944 | 44738.001 | 50.0349
2022-06-25 | 23:06 | 49.946 | 44738.001 | 50.0349
2022-06-25 | 23:06 | 49.947 | 44738.001 | 50.0348
2022-06-25 | 23:06 | 49.951 | 44738.001 | 50.0347
2022-06-25 | 23:06 | 49.951 | 44738.001 | 50.0346
2022-06-25 | 23:06 | 49.953 | 44738.001 | 50.0345
2022-06-25 | 23:06 | 49.952 | 44738.001 | 50.0344
2022-06-25 | 23:06 | 49.951 | 44738.001 | 50.0343
2022-06-25 | 23:06 | 49.949 | 44738.001 | 50.0342
2022-06-25 | 23:06 | 49.948 | 44738.001 | 50.0342
2022-06-25 | 23:06 | 49.945 | 44738.001 | 50.0341
2022-06-25 | 23:06 | 49.946 | 44738.001 | 50.034
2022-06-25 | 23:06 | 49.942 | 44738.001 | 50.0339
2022-06-25 | 23:06 | 49.944 | 44738.001 | 50.0338
2022-06-25 | 23:06 | 49.943 | 44738.001 | 50.0337
2022-06-25 | 23:06 | 49.941 | 44738.001 | 50.0336
2022-06-25 | 23:06 | 49.945 | 44738.001 | 50.0335
2022-06-25 | 23:06 | 49.943 | 44738.001 | 50.0335
2022-06-25 | 23:06 | 49.941 | 44738.001 | 50.0334
2022-06-25 | 23:06 | 49.941 | 44738.001 | 50.0334
2022-06-25 | 23:06 | 49.939 | 44738.001 | 50.0334
2022-06-25 | 23:06 | 49.94 | 44738.001 | 50.0334
2022-06-25 | 23:06 | 49.941 | 44738.001 | 50.0334
2022-06-25 | 23:06 | 49.944 | 44738.001 | 50.0334
2022-06-25 | 23:06 | 49.948 | 44738.001 | 50.0334
2022-06-25 | 23:06 | 49.951 | 44738.001 | 50.0333
2022-06-25 | 23:06 | 49.953 | 44738.001 | 50.0332
2022-06-25 | 23:06 | 49.952 | 2022-06-26 00:01 | 50.033
2022-06-25 | 23:06 | 49.951 | 44738.001 | 50.0329
2022-06-25 | 23:06 | 49.949 | 44738.001 | 50.0328
2022-06-25 | 23:06 | 49.947 | 44738.001 | 50.0327
2022-06-25 | 23:06 | 49.946 | 44738.001 | 50.0327
2022-06-25 | 23:06 | 49.948 | 44738.001 | 50.0327
2022-06-25 | 23:06 | 49.949 | 44738.001 | 50.0327
2022-06-25 | 23:06 | 49.949 | 44738.001 | 50.0326
2022-06-25 | 23:06 | 49.952 | 44738.001 | 50.0326
2022-06-25 | 23:06 | 49.953 | 44738.001 | 50.0326
2022-06-25 | 23:06 | 49.953 | 44738.001 | 50.0326
2022-06-25 | 23:06 | 49.953 | 44738.001 | 50.0325
2022-06-25 | 23:06 | 49.954 | 44738.001 | 50.0324
2022-06-25 | 23:06 | 49.953 | 44738.001 | 50.0324
2022-06-25 | 23:06 | 49.955 | 44738.001 | 50.0323
2022-06-25 | 23:06 | 49.954 | 44738.001 | 50.0323
2022-06-25 | 23:06 | 49.955 | 44738.001 | 50.0322
2022-06-25 | 23:06 | 49.952 | 44738.001 | 50.0322
2022-06-25 | 23:06 | 49.953 | 44738.001 | 50.0322
2022-06-25 | 23:06 | 49.953 | 44738.001 | 50.0322
2022-06-25 | 23:06 | 49.952 | 44738.001 | 50.0321
2022-06-25 | 23:06 | 49.952 | 44738.001 | 50.0321
2022-06-25 | 23:06 | 49.951 | 44738.001 | 50.032
2022-06-25 | 23:06 | 49.952 | 44738.001 | 50.0319
2022-06-25 | 23:06 | 49.953 | 44738.001 | 50.0318
2022-06-25 | 23:06 | 49.954 | 44738.001 | 50.0318
2022-06-25 | 23:06 | 49.962 | 44738.001 | 50.0317
2022-06-25 | 23:06 | 49.973 | 44738.001 | 50.0317
2022-06-25 | 23:06 | 49.98 | 44738.001 | 50.0317
2022-06-25 | 23:06 | 49.983 | 44738.001 | 50.0317
2022-06-25 | 23:06 | 49.986 | 44738.001 | 50.0316
2022-06-25 | 23:07 | 49.985 | 44738.001 | 50.0316
2022-06-25 | 23:07 | 49.984 | 44738.001 | 50.0316
2022-06-25 | 23:07 | 49.981 | 44738.001 | 50.0317
2022-06-25 | 23:07 | 49.981 | 44738.001 | 50.0316
2022-06-25 | 23:07 | 49.981 | 44738.001 | 50.0316
2022-06-25 | 23:07 | 49.981 | 44738.001 | 50.0316
2022-06-25 | 23:07 | 49.983 | 44738.001 | 50.0316
2022-06-25 | 23:07 | 49.984 | 44738.001 | 50.0315
2022-06-25 | 23:07 | 49.984 | 44738.001 | 50.0315
2022-06-25 | 23:07 | 49.985 | 44738.001 | 50.0314
2022-06-25 | 23:07 | 49.983 | 44738.001 | 50.0313
2022-06-25 | 23:07 | 49.984 | 44738.001 | 50.0313
2022-06-25 | 23:07 | 49.984 | 44738.001 | 50.0312
2022-06-25 | 23:07 | 49.985 | 44738.001 | 50.0312
2022-06-25 | 23:07 | 49.983 | 44738.001 | 50.0312
2022-06-25 | 23:07 | 49.983 | 44738.001 | 50.0311
2022-06-25 | 23:07 | 49.984 | 44738.001 | 50.0311
2022-06-25 | 23:07 | 49.984 | 44738.001 | 50.031
2022-06-25 | 23:07 | 49.985 | 44738.001 | 50.031
2022-06-25 | 23:07 | 49.988 | 2022-06-26 00:01 | 50.0309
2022-06-25 | 23:07 | 49.986 | 44738.001 | 50.0309
2022-06-25 | 23:07 | 49.989 | 44738.001 | 50.0308
2022-06-25 | 23:07 | 49.989 | 44738.001 | 50.0308
2022-06-25 | 23:07 | 49.993 | 44738.001 | 50.0308
2022-06-25 | 23:07 | 49.992 | 44738.001 | 50.0307
2022-06-25 | 23:07 | 49.995 | 44738.001 | 50.0307
2022-06-25 | 23:07 | 49.995 | 44738.001 | 50.0307
2022-06-25 | 23:07 | 49.994 | 44738.001 | 50.0307
2022-06-25 | 23:07 | 49.993 | 44738.001 | 50.0307
2022-06-25 | 23:07 | 49.995 | 44738.001 | 50.0307
2022-06-25 | 23:07 | 49.992 | 44738.001 | 50.0306
2022-06-25 | 23:07 | 49.988 | 44738.001 | 50.0306
2022-06-25 | 23:07 | 49.986 | 44738.001 | 50.0306
2022-06-25 | 23:07 | 49.986 | 44738.001 | 50.0305
2022-06-25 | 23:07 | 49.985 | 44738.001 | 50.0304
2022-06-25 | 23:07 | 49.986 | 44738.001 | 50.0304
2022-06-25 | 23:07 | 49.987 | 44738.001 | 50.0304
2022-06-25 | 23:07 | 49.988 | 44738.001 | 50.0304
2022-06-25 | 23:07 | 49.987 | 44738.001 | 50.0305
2022-06-25 | 23:07 | 49.988 | 44738.001 | 50.0305
2022-06-25 | 23:07 | 49.988 | 44738.001 | 50.0305
2022-06-25 | 23:07 | 49.986 | 44738.001 | 50.0306
2022-06-25 | 23:07 | 49.984 | 44738.001 | 50.0306
2022-06-25 | 23:07 | 49.983 | 44738.001 | 50.0306
2022-06-25 | 23:07 | 49.985 | 44738.001 | 50.0306
2022-06-25 | 23:07 | 49.986 | 44738.001 | 50.0306
2022-06-25 | 23:07 | 49.988 | 44738.001 | 50.0306
2022-06-25 | 23:07 | 49.989 | 44738.001 | 50.0306
2022-06-25 | 23:07 | 49.991 | 44738.001 | 50.0305
2022-06-25 | 23:07 | 49.992 | 44738.001 | 50.0304
2022-06-25 | 23:07 | 49.994 | 44738.001 | 50.0303
2022-06-25 | 23:07 | 49.997 | 44738.001 | 50.0303
2022-06-25 | 23:07 | 49.998 | 44738.001 | 50.0303
2022-06-25 | 23:07 | 49.997 | 44738.001 | 50.0303
2022-06-25 | 23:07 | 49.995 | 44738.001 | 50.0304
2022-06-25 | 23:07 | 49.995 | 44738.001 | 50.0304
2022-06-25 | 23:07 | 49.994 | 44738.001 | 50.0305
2022-06-25 | 23:07 | 49.993 | 44738.001 | 50.0306
2022-06-25 | 23:07 | 49.991 | 44738.001 | 50.0307
2022-06-25 | 23:08 | 49.99 | 44738.001 | 50.0308
2022-06-25 | 23:08 | 49.987 | 44738.001 | 50.0308
2022-06-25 | 23:08 | 49.984 | 44738.001 | 50.0309
2022-06-25 | 23:08 | 49.981 | 44738.001 | 50.0309
2022-06-25 | 23:08 | 49.978 | 44738.001 | 50.0309
2022-06-25 | 23:08 | 49.978 | 44738.001 | 50.0309
2022-06-25 | 23:08 | 49.979 | 44738.001 | 50.0309
2022-06-25 | 23:08 | 49.981 | 44738.001 | 50.0308
2022-06-25 | 23:08 | 49.986 | 44738.001 | 50.0307
2022-06-25 | 23:08 | 49.987 | 44738.001 | 50.0307
2022-06-25 | 23:08 | 49.991 | 2022-06-26 00:01 | 50.0308
2022-06-25 | 23:08 | 49.994 | 44738.001 | 50.0308
2022-06-25 | 23:08 | 49.998 | 44738.001 | 50.0309
2022-06-25 | 23:08 | 50 | 44738.001 | 50.0309
2022-06-25 | 23:08 | 50.002 | 44738.001 | 50.031
2022-06-25 | 23:08 | 50.006 | 44738.001 | 50.031
2022-06-25 | 23:08 | 50.008 | 44738.001 | 50.0311
2022-06-25 | 23:08 | 50.006 | 44738.001 | 50.0311
2022-06-25 | 23:08 | 50.005 | 44738.001 | 50.0312
2022-06-25 | 23:08 | 50.004 | 44738.001 | 50.0312
2022-06-25 | 23:08 | 50 | 44738.001 | 50.0312
2022-06-25 | 23:08 | 49.998 | 44738.001 | 50.0311
2022-06-25 | 23:08 | 49.998 | 44738.001 | 50.031
2022-06-25 | 23:08 | 49.996 | 44738.001 | 50.0309
2022-06-25 | 23:08 | 49.995 | 44738.001 | 50.0309
2022-06-25 | 23:08 | 49.996 | 44738.001 | 50.0308
2022-06-25 | 23:08 | 49.994 | 44738.001 | 50.0307
2022-06-25 | 23:08 | 49.994 | 44738.001 | 50.0307
2022-06-25 | 23:08 | 49.995 | 44738.001 | 50.0308
2022-06-25 | 23:08 | 49.998 | 44738.001 | 50.0309
2022-06-25 | 23:08 | 49.998 | 44738.001 | 50.031
2022-06-25 | 23:08 | 50.003 | 44738.001 | 50.031
2022-06-25 | 23:08 | 50.004 | 44738.001 | 50.0311
2022-06-25 | 23:08 | 50.006 | 44738.001 | 50.031
2022-06-25 | 23:08 | 50.009 | 44738.001 | 50.031
2022-06-25 | 23:08 | 50.011 | 44738.001 | 50.0309
2022-06-25 | 23:08 | 50.012 | 44738.001 | 50.0309
2022-06-25 | 23:08 | 50.014 | 44738.001 | 50.0308
2022-06-25 | 23:08 | 50.017 | 44738.001 | 50.0307
2022-06-25 | 23:08 | 50.017 | 44738.001 | 50.0307
2022-06-25 | 23:08 | 50.017 | 44738.001 | 50.0308
2022-06-25 | 23:08 | 50.017 | 44738.001 | 50.0308
2022-06-25 | 23:08 | 50.016 | 44738.001 | 50.0309
2022-06-25 | 23:08 | 50.016 | 44738.001 | 50.031
2022-06-25 | 23:08 | 50.017 | 44738.001 | 50.031
2022-06-25 | 23:08 | 50.015 | 44738.001 | 50.0311
2022-06-25 | 23:08 | 50.017 | 44738.001 | 50.0312
2022-06-25 | 23:08 | 50.016 | 44738.001 | 50.0312
2022-06-25 | 23:08 | 50.014 | 44738.001 | 50.0312
2022-06-25 | 23:08 | 50.009 | 44738.001 | 50.0311
2022-06-25 | 23:08 | 50.005 | 44738.001 | 50.0311
2022-06-25 | 23:08 | 50 | 44738.001 | 50.0311
2022-06-25 | 23:08 | 49.995 | 44738.001 | 50.031
2022-06-25 | 23:08 | 49.992 | 44738.001 | 50.031
2022-06-25 | 23:08 | 49.99 | 44738.001 | 50.031
2022-06-25 | 23:08 | 49.983 | 44738.001 | 50.0311
2022-06-25 | 23:08 | 49.982 | 44738.001 | 50.0312
2022-06-25 | 23:08 | 49.981 | 44738.001 | 50.0313
2022-06-25 | 23:08 | 49.983 | 44738.001 | 50.0314
2022-06-25 | 23:08 | 49.985 | 44738.001 | 50.0314
2022-06-25 | 23:08 | 49.985 | 2022-06-26 00:01 | 50.0315
2022-06-25 | 23:09 | 49.984 | 44738.001 | 50.0316
2022-06-25 | 23:09 | 49.985 | 44738.001 | 50.0316
2022-06-25 | 23:09 | 49.985 | 44738.001 | 50.0316
2022-06-25 | 23:09 | 49.987 | 44738.001 | 50.0317
2022-06-25 | 23:09 | 49.985 | 44738.001 | 50.0317
2022-06-25 | 23:09 | 49.982 | 44738.001 | 50.0318
2022-06-25 | 23:09 | 49.977 | 44738.001 | 50.0318
2022-06-25 | 23:09 | 49.97 | 44738.001 | 50.0319
2022-06-25 | 23:09 | 49.965 | 44738.001 | 50.032
2022-06-25 | 23:09 | 49.958 | 44738.001 | 50.032
2022-06-25 | 23:09 | 49.955 | 44738.001 | 50.032
2022-06-25 | 23:09 | 49.953 | 44738.001 | 50.0321
2022-06-25 | 23:09 | 49.95 | 44738.001 | 50.0321
2022-06-25 | 23:09 | 49.948 | 44738.001 | 50.0321
2022-06-25 | 23:09 | 49.941 | 44738.001 | 50.0321
2022-06-25 | 23:09 | 49.938 | 44738.001 | 50.0322
2022-06-25 | 23:09 | 49.933 | 44738.001 | 50.0323
2022-06-25 | 23:09 | 49.933 | 44738.001 | 50.0323
2022-06-25 | 23:09 | 49.933 | 44738.001 | 50.0323
2022-06-25 | 23:09 | 49.93 | 44738.001 | 50.0323
2022-06-25 | 23:09 | 49.929 | 44738.001 | 50.0323
2022-06-25 | 23:09 | 49.929 | 44738.001 | 50.0324
2022-06-25 | 23:09 | 49.929 | 44738.001 | 50.0324
2022-06-25 | 23:09 | 49.928 | 44738.001 | 50.0323
2022-06-25 | 23:09 | 49.928 | 44738.001 | 50.0323
2022-06-25 | 23:09 | 49.93 | 44738.001 | 50.0323
2022-06-25 | 23:09 | 49.929 | 44738.001 | 50.0323
2022-06-25 | 23:09 | 49.93 | 44738.001 | 50.0323
2022-06-25 | 23:09 | 49.931 | 44738.001 | 50.0324
2022-06-25 | 23:09 | 49.932 | 44738.001 | 50.0324
2022-06-25 | 23:09 | 49.932 | 44738.001 | 50.0325
2022-06-25 | 23:09 | 49.929 | 44738.001 | 50.0326
2022-06-25 | 23:09 | 49.931 | 44738.001 | 50.0326
2022-06-25 | 23:09 | 49.931 | 44738.001 | 50.0327
2022-06-25 | 23:09 | 49.932 | 44738.001 | 50.0328
2022-06-25 | 23:09 | 49.932 | 44738.001 | 50.0329
2022-06-25 | 23:09 | 49.932 | 44738.001 | 50.033
2022-06-25 | 23:09 | 49.931 | 44738.001 | 50.033
2022-06-25 | 23:09 | 49.929 | 44738.001 | 50.033
2022-06-25 | 23:09 | 49.93 | 44738.001 | 50.0329
2022-06-25 | 23:09 | 49.931 | 44738.001 | 50.0329
2022-06-25 | 23:09 | 49.932 | 44738.001 | 50.0329
2022-06-25 | 23:09 | 49.937 | 44738.001 | 50.0329
2022-06-25 | 23:09 | 49.94 | 44738.001 | 50.033
2022-06-25 | 23:09 | 49.942 | 44738.001 | 50.0331
2022-06-25 | 23:09 | 49.944 | 44738.001 | 50.0332
2022-06-25 | 23:09 | 49.945 | 44738.001 | 50.0333
2022-06-25 | 23:09 | 49.944 | 44738.001 | 50.0334
2022-06-25 | 23:09 | 49.942 | 44738.001 | 50.0335
2022-06-25 | 23:09 | 49.942 | 2022-06-26 00:02 | 50.0335
2022-06-25 | 23:09 | 49.942 | 44738.001 | 50.0336
2022-06-25 | 23:09 | 49.938 | 44738.001 | 50.0336
2022-06-25 | 23:09 | 49.939 | 44738.001 | 50.0336
2022-06-25 | 23:09 | 49.936 | 44738.001 | 50.0336
2022-06-25 | 23:09 | 49.939 | 44738.001 | 50.0335
2022-06-25 | 23:09 | 49.937 | 44738.001 | 50.0335
2022-06-25 | 23:09 | 49.935 | 44738.001 | 50.0334
2022-06-25 | 23:09 | 49.937 | 44738.001 | 50.0334
2022-06-25 | 23:09 | 49.936 | 44738.001 | 50.0334
2022-06-25 | 23:10 | 49.936 | 44738.001 | 50.0333
2022-06-25 | 23:10 | 49.935 | 44738.001 | 50.0334
2022-06-25 | 23:10 | 49.937 | 44738.001 | 50.0335
2022-06-25 | 23:10 | 49.936 | 44738.001 | 50.0336
2022-06-25 | 23:10 | 49.936 | 44738.001 | 50.0336
2022-06-25 | 23:10 | 49.935 | 44738.001 | 50.0337
2022-06-25 | 23:10 | 49.937 | 44738.001 | 50.0338
2022-06-25 | 23:10 | 49.938 | 44738.001 | 50.0339
2022-06-25 | 23:10 | 49.94 | 44738.001 | 50.0339
2022-06-25 | 23:10 | 49.94 | 44738.001 | 50.0339
2022-06-25 | 23:10 | 49.942 | 44738.001 | 50.0338
2022-06-25 | 23:10 | 49.943 | 44738.001 | 50.0337
2022-06-25 | 23:10 | 49.944 | 44738.001 | 50.0336
2022-06-25 | 23:10 | 49.949 | 44738.001 | 50.0336
2022-06-25 | 23:10 | 49.949 | 44738.001 | 50.0335
2022-06-25 | 23:10 | 49.952 | 44738.001 | 50.0335
2022-06-25 | 23:10 | 49.953 | 44738.001 | 50.0335
2022-06-25 | 23:10 | 49.952 | 44738.001 | 50.0336
2022-06-25 | 23:10 | 49.95 | 44738.001 | 50.0337
2022-06-25 | 23:10 | 49.954 | 44738.001 | 50.0338
2022-06-25 | 23:10 | 49.954 | 44738.001 | 50.0339
2022-06-25 | 23:10 | 49.956 | 44738.001 | 50.034
2022-06-25 | 23:10 | 49.954 | 44738.001 | 50.0341
2022-06-25 | 23:10 | 49.953 | 44738.001 | 50.0341
2022-06-25 | 23:10 | 49.955 | 44738.001 | 50.0341
2022-06-25 | 23:10 | 49.954 | 44738.001 | 50.034
2022-06-25 | 23:10 | 49.956 | 44738.001 | 50.034
2022-06-25 | 23:10 | 49.956 | 44738.0011 | 50.034
2022-06-25 | 23:10 | 49.956 | 44738.0011 | 50.034
2022-06-25 | 23:10 | 49.953 | 44738.0011 | 50.034
2022-06-25 | 23:10 | 49.951 | 44738.0011 | 50.034
2022-06-25 | 23:10 | 49.947 | 44738.0011 | 50.0341
2022-06-25 | 23:10 | 49.944 | 44738.0011 | 50.0341
2022-06-25 | 23:10 | 49.942 | 44738.0011 | 50.0341
2022-06-25 | 23:10 | 49.943 | 44738.0011 | 50.0342
2022-06-25 | 23:10 | 49.943 | 44738.0011 | 50.0342
2022-06-25 | 23:10 | 49.945 | 44738.0011 | 50.0343
2022-06-25 | 23:10 | 49.944 | 44738.0011 | 50.0343
2022-06-25 | 23:10 | 49.943 | 44738.0011 | 50.0343
2022-06-25 | 23:10 | 49.944 | 44738.0011 | 50.0344
2022-06-25 | 23:10 | 49.944 | 2022-06-26 00:02 | 50.0344
2022-06-25 | 23:10 | 49.944 | 44738.0011 | 50.0343
2022-06-25 | 23:10 | 49.943 | 44738.0011 | 50.0343
2022-06-25 | 23:10 | 49.943 | 44738.0011 | 50.0343
2022-06-25 | 23:10 | 49.944 | 44738.0011 | 50.0342
2022-06-25 | 23:10 | 49.944 | 44738.0011 | 50.0343
2022-06-25 | 23:10 | 49.946 | 44738.0011 | 50.0343
2022-06-25 | 23:10 | 49.946 | 44738.0011 | 50.0344
2022-06-25 | 23:10 | 49.945 | 44738.0011 | 50.0344
2022-06-25 | 23:10 | 49.944 | 44738.0011 | 50.0344
2022-06-25 | 23:10 | 49.945 | 44738.0011 | 50.0345
2022-06-25 | 23:10 | 49.944 | 44738.0011 | 50.0345
2022-06-25 | 23:10 | 49.945 | 44738.0011 | 50.0345
2022-06-25 | 23:10 | 49.945 | 44738.0011 | 50.0345
2022-06-25 | 23:10 | 49.943 | 44738.0011 | 50.0344
2022-06-25 | 23:10 | 49.944 | 44738.0011 | 50.0344
2022-06-25 | 23:10 | 49.946 | 44738.0011 | 50.0344
2022-06-25 | 23:10 | 49.947 | 44738.0011 | 50.0343
2022-06-25 | 23:10 | 49.947 | 44738.0011 | 50.0344
2022-06-25 | 23:10 | 49.948 | 44738.0011 | 50.0344
2022-06-25 | 23:10 | 49.949 | 44738.0011 | 50.0344
2022-06-25 | 23:11 | 49.948 | 44738.0011 | 50.0345
2022-06-25 | 23:11 | 49.949 | 44738.0011 | 50.0345
2022-06-25 | 23:11 | 49.947 | 44738.0011 | 50.0346
2022-06-25 | 23:11 | 49.948 | 44738.0011 | 50.0346
2022-06-25 | 23:11 | 49.948 | 44738.0011 | 50.0346
2022-06-25 | 23:11 | 49.947 | 44738.0011 | 50.0346
2022-06-25 | 23:11 | 49.945 | 44738.0011 | 50.0346
2022-06-25 | 23:11 | 49.945 | 44738.0011 | 50.0346
2022-06-25 | 23:11 | 49.944 | 44738.0011 | 50.0346
2022-06-25 | 23:11 | 49.944 | 44738.0011 | 50.0346
2022-06-25 | 23:11 | 49.945 | 44738.0011 | 50.0346
2022-06-25 | 23:11 | 49.945 | 44738.0011 | 50.0346
2022-06-25 | 23:11 | 49.947 | 44738.0011 | 50.0346
2022-06-25 | 23:11 | 49.949 | 44738.0011 | 50.0346
2022-06-25 | 23:11 | 49.949 | 44738.0011 | 50.0346
2022-06-25 | 23:11 | 49.95 | 44738.0011 | 50.0346
2022-06-25 | 23:11 | 49.951 | 44738.0011 | 50.0346
2022-06-25 | 23:11 | 49.952 | 44738.0011 | 50.0346
2022-06-25 | 23:11 | 49.95 | 44738.0011 | 50.0347
2022-06-25 | 23:11 | 49.948 | 44738.0011 | 50.0347
2022-06-25 | 23:11 | 49.947 | 44738.0011 | 50.0348
2022-06-25 | 23:11 | 49.946 | 44738.0011 | 50.0349
2022-06-25 | 23:11 | 49.944 | 44738.0011 | 50.0349
2022-06-25 | 23:11 | 49.945 | 44738.0011 | 50.0349
2022-06-25 | 23:11 | 49.944 | 44738.0011 | 50.035
2022-06-25 | 23:11 | 49.946 | 44738.0011 | 50.035
2022-06-25 | 23:11 | 49.942 | 44738.0011 | 50.035
2022-06-25 | 23:11 | 49.941 | 44738.0011 | 50.035
2022-06-25 | 23:11 | 49.94 | 44738.0011 | 50.0351
2022-06-25 | 23:11 | 49.94 | 2022-06-26 00:02 | 50.0351
|  |  | 44738.0011 | 50.0351
|  |  | 44738.0011 | 50.0352
|  |  | 44738.0011 | 50.0352
|  |  | 44738.0011 | 50.0352
|  |  | 44738.0011 | 50.0352
|  |  | 44738.0011 | 50.0351
|  |  | 44738.0011 | 50.0351
|  |  | 44738.0011 | 50.0351
|  |  | 44738.0011 | 50.0351
|  |  | 44738.0011 | 50.0351
|  |  | 44738.0011 | 50.0352
|  |  | 44738.0011 | 50.0352
|  |  | 44738.0011 | 50.0353
|  |  | 44738.0011 | 50.0354
|  |  | 44738.0011 | 50.0355
|  |  | 44738.0011 | 50.0356
|  |  | 44738.0011 | 50.0357
|  |  | 44738.0011 | 50.0358
|  |  | 44738.0011 | 50.0357
|  |  | 44738.0011 | 50.0357
|  |  | 44738.0011 | 50.0357
|  |  | 44738.0011 | 50.0356
|  |  | 44738.0011 | 50.0355
|  |  | 44738.0011 | 50.0355
|  |  | 44738.0011 | 50.0354
|  |  | 44738.0011 | 50.0354
|  |  | 44738.0011 | 50.0354
|  |  | 44738.0011 | 50.0354
|  |  | 44738.0011 | 50.0354
|  |  | 44738.0011 | 50.0354
|  |  | 44738.0011 | 50.0354
|  |  | 44738.0011 | 50.0354
|  |  | 44738.0011 | 50.0355
|  |  | 44738.0011 | 50.0355
|  |  | 44738.0011 | 50.0355
|  |  | 44738.0011 | 50.0355
|  |  | 44738.0011 | 50.0354
|  |  | 44738.0011 | 50.0354
|  |  | 44738.0011 | 50.0353
|  |  | 44738.0011 | 50.0351
|  |  | 44738.0011 | 50.0351
|  |  | 44738.0011 | 50.035
|  |  | 44738.0011 | 50.0349
|  |  | 44738.0011 | 50.0348
|  |  | 44738.0011 | 50.0348
|  |  | 44738.0011 | 50.0348
|  |  | 44738.0011 | 50.0348
|  |  | 44738.0011 | 50.0348
|  |  | 44738.0011 | 50.0348
|  |  | 2022-06-26 00:02 | 50.0348
|  |  | 44738.0011 | 50.0348
|  |  | 44738.0011 | 50.0349
|  |  | 44738.0011 | 50.0349
|  |  | 44738.0011 | 50.0348
|  |  | 44738.0011 | 50.0348
|  |  | 44738.0011 | 50.0348
|  |  | 44738.0011 | 50.0347
|  |  | 44738.0011 | 50.0347
|  |  | 44738.0011 | 50.0346
|  |  | 44738.0011 | 50.0345
|  |  | 44738.0011 | 50.0345
|  |  | 44738.0011 | 50.0344
|  |  | 44738.0011 | 50.0344
|  |  | 44738.0011 | 50.0344
|  |  | 44738.0011 | 50.0344
|  |  | 44738.0011 | 50.0345
|  |  | 44738.0011 | 50.0345
|  |  | 44738.0011 | 50.0347
|  |  | 44738.0011 | 50.0348
|  |  | 44738.0011 | 50.0349
|  |  | 44738.0011 | 50.0349
|  |  | 44738.0011 | 50.035
|  |  | 44738.0011 | 50.035
|  |  | 44738.0011 | 50.035
|  |  | 44738.0011 | 50.035
|  |  | 44738.0011 | 50.035
|  |  | 44738.0011 | 50.0349
|  |  | 44738.0011 | 50.0349
|  |  | 44738.0011 | 50.0348
|  |  | 44738.0011 | 50.0347
|  |  | 44738.0011 | 50.0347
|  |  | 44738.0011 | 50.0347
|  |  | 44738.0011 | 50.0348
|  |  | 44738.0011 | 50.0347
|  |  | 44738.0011 | 50.0347
|  |  | 44738.0011 | 50.0347
|  |  | 44738.0011 | 50.0347
|  |  | 44738.0011 | 50.0347
|  |  | 44738.0011 | 50.0347
|  |  | 44738.0011 | 50.0346
|  |  | 44738.0011 | 50.0347
|  |  | 44738.0011 | 50.0347
|  |  | 44738.0011 | 50.0348
|  |  | 44738.0011 | 50.0349
|  |  | 44738.0011 | 50.0349
|  |  | 44738.0011 | 50.035
|  |  | 44738.0011 | 50.035
|  |  | 44738.0011 | 50.035
|  |  | 44738.0011 | 50.0349
|  |  | 2022-06-26 00:02 | 50.0349
|  |  | 44738.0011 | 50.0348
|  |  | 44738.0011 | 50.0348
|  |  | 44738.0011 | 50.0347
|  |  | 44738.0011 | 50.0345
|  |  | 44738.0011 | 50.0344
|  |  | 44738.0011 | 50.0344
|  |  | 44738.0011 | 50.0344
|  |  | 44738.0011 | 50.0344
|  |  | 44738.0011 | 50.0344
|  |  | 44738.0011 | 50.0344
|  |  | 44738.0011 | 50.0345
|  |  | 44738.0011 | 50.0346
|  |  | 44738.0011 | 50.0347
|  |  | 44738.0011 | 50.0348
|  |  | 44738.0011 | 50.0348
|  |  | 44738.0011 | 50.0348
|  |  | 44738.0011 | 50.0348
|  |  | 44738.0011 | 50.0348
|  |  | 44738.0011 | 50.0347
|  |  | 44738.0011 | 50.0346
|  |  | 44738.0011 | 50.0346
|  |  | 44738.0011 | 50.0344
|  |  | 44738.0011 | 50.0343
|  |  | 44738.0011 | 50.0342
|  |  | 44738.0011 | 50.0341
|  |  | 44738.0011 | 50.034
|  |  | 44738.0011 | 50.0339
|  |  | 44738.0011 | 50.0338
|  |  | 44738.0011 | 50.0338
|  |  | 44738.0011 | 50.0338
|  |  | 44738.0011 | 50.0338
|  |  | 44738.0011 | 50.0339
|  |  | 44738.0011 | 50.034
|  |  | 44738.0011 | 50.034
|  |  | 44738.0011 | 50.034
|  |  | 44738.0011 | 50.0341
|  |  | 44738.0011 | 50.0341
|  |  | 44738.0011 | 50.034
|  |  | 44738.0011 | 50.0339
|  |  | 44738.0011 | 50.0338
|  |  | 44738.0011 | 50.0336
|  |  | 44738.0011 | 50.0336
|  |  | 44738.0011 | 50.0335
|  |  | 44738.0011 | 50.0334
|  |  | 44738.0011 | 50.0334
|  |  | 44738.0011 | 50.0334
|  |  | 44738.0011 | 50.0334
|  |  | 44738.0011 | 50.0334
|  |  | 44738.0011 | 50.0334
|  |  | 2022-06-26 00:02 | 50.0333
|  |  | 44738.0011 | 50.0333
|  |  | 44738.0011 | 50.0333
|  |  | 44738.0011 | 50.0333
|  |  | 44738.0011 | 50.0333
|  |  | 44738.0011 | 50.0333
|  |  | 44738.0011 | 50.0333
|  |  | 44738.0011 | 50.0333
|  |  | 44738.0011 | 50.0332
|  |  | 44738.0011 | 50.0331
|  |  | 44738.0011 | 50.0331
|  |  | 44738.0011 | 50.033
|  |  | 44738.0011 | 50.0329
|  |  | 44738.0011 | 50.0328
|  |  | 44738.0011 | 50.0327
|  |  | 44738.0011 | 50.0326
|  |  | 44738.0011 | 50.0325
|  |  | 44738.0011 | 50.0324
|  |  | 44738.0011 | 50.0324
|  |  | 44738.0011 | 50.0324
|  |  | 44738.0011 | 50.0325
|  |  | 44738.0011 | 50.0325
|  |  | 44738.0011 | 50.0325
|  |  | 44738.0011 | 50.0326
|  |  | 44738.0011 | 50.0326
|  |  | 44738.0011 | 50.0326
|  |  | 44738.0011 | 50.0325
|  |  | 44738.0011 | 50.0324
|  |  | 44738.0011 | 50.0324
|  |  | 44738.0011 | 50.0323
|  |  | 44738.0011 | 50.0322
|  |  | 44738.0011 | 50.0321
|  |  | 44738.0011 | 50.032
|  |  | 44738.0011 | 50.0319
|  |  | 44738.0011 | 50.0318
|  |  | 44738.0011 | 50.0317
|  |  | 44738.0011 | 50.0317
|  |  | 44738.0011 | 50.0317
|  |  | 44738.0011 | 50.0316
|  |  | 44738.0011 | 50.0316
|  |  | 44738.0011 | 50.0316
|  |  | 44738.0011 | 50.0316
|  |  | 44738.0011 | 50.0317
|  |  | 44738.0011 | 50.0317
|  |  | 44738.0011 | 50.0317
|  |  | 44738.0011 | 50.0316
|  |  | 44738.0011 | 50.0316
|  |  | 44738.0011 | 50.0315
|  |  | 44738.0011 | 50.0315
|  |  | 44738.0011 | 50.0314
|  |  | 2022-06-26 00:02 | 50.0314
|  |  | 44738.0011 | 50.0313
|  |  | 44738.0011 | 50.0313
|  |  | 44738.0011 | 50.0313
|  |  | 44738.0011 | 50.0313
|  |  | 44738.0011 | 50.0313
|  |  | 44738.0011 | 50.0313
|  |  | 44738.0011 | 50.0313
|  |  | 44738.0011 | 50.0313
|  |  | 44738.0011 | 50.0313
|  |  | 44738.0011 | 50.0313
|  |  | 44738.0011 | 50.0313
|  |  | 44738.0011 | 50.0312
|  |  | 44738.0011 | 50.0311
|  |  | 44738.0011 | 50.031
|  |  | 44738.0011 | 50.0309
|  |  | 44738.0011 | 50.0308
|  |  | 44738.0011 | 50.0307
|  |  | 44738.0011 | 50.0307
|  |  | 44738.0011 | 50.0306
|  |  | 44738.0011 | 50.0305
|  |  | 44738.0011 | 50.0304
|  |  | 44738.0011 | 50.0303
|  |  | 44738.0011 | 50.0303
|  |  | 44738.0011 | 50.0303
|  |  | 44738.0011 | 50.0302
|  |  | 44738.0011 | 50.0303
|  |  | 44738.0011 | 50.0303
|  |  | 44738.0011 | 50.0302
|  |  | 44738.0011 | 50.0302
|  |  | 44738.0011 | 50.0302
|  |  | 44738.0011 | 50.0301
|  |  | 44738.0011 | 50.0299
|  |  | 44738.0011 | 50.0298
|  |  | 44738.0011 | 50.0297
|  |  | 44738.0011 | 50.0297
|  |  | 44738.0011 | 50.0296
|  |  | 44738.0011 | 50.0296
|  |  | 44738.0011 | 50.0296
|  |  | 44738.0011 | 50.0297
|  |  | 44738.0011 | 50.0298
|  |  | 44738.0011 | 50.0298
|  |  | 44738.0011 | 50.0298
|  |  | 44738.0011 | 50.0299
|  |  | 44738.0011 | 50.0299
|  |  | 44738.0011 | 50.0298
|  |  | 44738.0011 | 50.0298
|  |  | 44738.0011 | 50.0298
|  |  | 44738.0011 | 50.0296
|  |  | 44738.0011 | 50.0296
|  |  | 2022-06-26 00:02 | 50.0295
|  |  | 44738.0011 | 50.0295
|  |  | 44738.0011 | 50.0294
|  |  | 44738.0011 | 50.0294
|  |  | 44738.0011 | 50.0294
|  |  | 44738.0011 | 50.0295
|  |  | 44738.0011 | 50.0296
|  |  | 44738.0011 | 50.0297
|  |  | 44738.0011 | 50.0299
|  |  | 44738.0011 | 50.03
|  |  | 44738.0011 | 50.0301
|  |  | 44738.0011 | 50.0301
|  |  | 44738.0011 | 50.0302
|  |  | 44738.0011 | 50.0301
|  |  | 44738.0011 | 50.0301
|  |  | 44738.0011 | 50.0299
|  |  | 44738.0011 | 50.0299
|  |  | 44738.0011 | 50.0298
|  |  | 44738.0011 | 50.0297
|  |  | 44738.0011 | 50.0296
|  |  | 44738.0011 | 50.0296
|  |  | 44738.0011 | 50.0296
|  |  | 44738.0011 | 50.0295
|  |  | 44738.0011 | 50.0296
|  |  | 44738.0011 | 50.0296
|  |  | 44738.0011 | 50.0296
|  |  | 44738.0011 | 50.0296
|  |  | 44738.0011 | 50.0296
|  |  | 44738.0011 | 50.0295
|  |  | 44738.0011 | 50.0295
|  |  | 44738.0011 | 50.0294
|  |  | 44738.0011 | 50.0294
|  |  | 44738.0011 | 50.0293
|  |  | 44738.0011 | 50.0292
|  |  | 44738.0011 | 50.0291
|  |  | 44738.0011 | 50.0291
|  |  | 44738.0011 | 50.029
|  |  | 44738.0011 | 50.0291
|  |  | 44738.0011 | 50.0291
|  |  | 44738.0011 | 50.0292
|  |  | 44738.0011 | 50.0293
|  |  | 44738.0011 | 50.0293
|  |  | 44738.0011 | 50.0293
|  |  | 44738.0011 | 50.0293
|  |  | 44738.0011 | 50.0293
|  |  | 44738.0011 | 50.0293
|  |  | 44738.0011 | 50.0292
|  |  | 44738.0011 | 50.0291
|  |  | 44738.0011 | 50.029
|  |  | 44738.0011 | 50.0288
|  |  | 2022-06-26 00:02 | 50.0287
|  |  | 44738.0011 | 50.0286
|  |  | 44738.0011 | 50.0286
|  |  | 44738.0011 | 50.0286
|  |  | 44738.0011 | 50.0286
|  |  | 44738.0011 | 50.0286
|  |  | 44738.0011 | 50.0287
|  |  | 44738.0011 | 50.0289
|  |  | 44738.0011 | 50.029
|  |  | 44738.0011 | 50.029
|  |  | 44738.0011 | 50.0289
|  |  | 44738.0011 | 50.0289
|  |  | 44738.0011 | 50.0289
|  |  | 44738.0011 | 50.0289
|  |  | 44738.0011 | 50.0289
|  |  | 44738.0011 | 50.0288
|  |  | 44738.0011 | 50.0288
|  |  | 44738.0011 | 50.0288
|  |  | 44738.0011 | 50.0288
|  |  | 44738.0011 | 50.0289
|  |  | 44738.0011 | 50.029
|  |  | 44738.0011 | 50.0291
|  |  | 44738.0011 | 50.0292
|  |  | 44738.0011 | 50.0292
|  |  | 44738.0011 | 50.0292
|  |  | 44738.0011 | 50.0293
|  |  | 44738.0011 | 50.0292
|  |  | 44738.0011 | 50.029
|  |  | 44738.0011 | 50.0289
|  |  | 44738.0011 | 50.0287
|  |  | 44738.0011 | 50.0287
|  |  | 44738.0011 | 50.0287
|  |  | 44738.0011 | 50.0287
|  |  | 44738.0011 | 50.0287
|  |  | 44738.0011 | 50.0288
|  |  | 44738.0011 | 50.0288
|  |  | 44738.0011 | 50.0289
|  |  | 44738.0011 | 50.0289
|  |  | 44738.0011 | 50.0288
|  |  | 44738.0011 | 50.0288
|  |  | 44738.0011 | 50.0287
|  |  | 44738.0011 | 50.0286
|  |  | 44738.0011 | 50.0285
|  |  | 44738.0011 | 50.0285
|  |  | 44738.0011 | 50.0285
|  |  | 44738.0011 | 50.0285
|  |  | 44738.0011 | 50.0285
|  |  | 44738.0011 | 50.0286
|  |  | 44738.0011 | 50.0286
|  |  | 44738.0011 | 50.0286
|  |  | 2022-06-26 00:02 | 50.0286
|  |  | 44738.0011 | 50.0286
|  |  | 44738.0011 | 50.0286
|  |  | 44738.0011 | 50.0286
|  |  | 44738.0011 | 50.0286
|  |  | 44738.0011 | 50.0285
|  |  | 44738.0011 | 50.0284
|  |  | 44738.0011 | 50.0284
|  |  | 44738.0011 | 50.0284
|  |  | 44738.0011 | 50.0284
|  |  | 44738.0011 | 50.0284
|  |  | 44738.0011 | 50.0283
|  |  | 44738.0011 | 50.0283
|  |  | 44738.0011 | 50.0283
|  |  | 44738.0011 | 50.0284
|  |  | 44738.0011 | 50.0283
|  |  | 44738.0011 | 50.0284
|  |  | 44738.0011 | 50.0284
|  |  | 44738.0011 | 50.0284
|  |  | 44738.0012 | 50.0285
|  |  | 44738.0012 | 50.0284
|  |  | 44738.0012 | 50.0284
|  |  | 44738.0012 | 50.0283
|  |  | 44738.0012 | 50.0283
|  |  | 44738.0012 | 50.0283
|  |  | 44738.0012 | 50.0283
|  |  | 44738.0012 | 50.0283
|  |  | 44738.0012 | 50.0283
|  |  | 44738.0012 | 50.0284
|  |  | 44738.0012 | 50.0284
|  |  | 44738.0012 | 50.0284
|  |  | 44738.0012 | 50.0284
|  |  | 44738.0012 | 50.0284
|  |  | 44738.0012 | 50.0284
|  |  | 44738.0012 | 50.0283
|  |  | 44738.0012 | 50.0283
|  |  | 44738.0012 | 50.0282
|  |  | 44738.0012 | 50.0282
|  |  | 44738.0012 | 50.0282
|  |  | 44738.0012 | 50.0281
|  |  | 44738.0012 | 50.0282
|  |  | 44738.0012 | 50.0283
|  |  | 44738.0012 | 50.0284
|  |  | 44738.0012 | 50.0285
|  |  | 44738.0012 | 50.0285
|  |  | 44738.0012 | 50.0286
|  |  | 44738.0012 | 50.0286
|  |  | 44738.0012 | 50.0286
|  |  | 44738.0012 | 50.0285
|  |  | 44738.0012 | 50.0284
|  |  | 2022-06-26 00:02 | 50.0283
|  |  | 44738.0012 | 50.0283
|  |  | 44738.0012 | 50.0282
|  |  | 44738.0012 | 50.0281
|  |  | 44738.0012 | 50.0281
|  |  | 44738.0012 | 50.0281
|  |  | 44738.0012 | 50.0282
|  |  | 44738.0012 | 50.0282
|  |  | 44738.0012 | 50.0283
|  |  | 44738.0012 | 50.0283
|  |  | 44738.0012 | 50.0284
|  |  | 44738.0012 | 50.0284
|  |  | 44738.0012 | 50.0285
|  |  | 44738.0012 | 50.0285
|  |  | 44738.0012 | 50.0285
|  |  | 44738.0012 | 50.0286
|  |  | 44738.0012 | 50.0286
|  |  | 44738.0012 | 50.0288
|  |  | 44738.0012 | 50.0288
|  |  | 44738.0012 | 50.0289
|  |  | 44738.0012 | 50.0289
|  |  | 44738.0012 | 50.0289
|  |  | 44738.0012 | 50.029
|  |  | 44738.0012 | 50.029
|  |  | 44738.0012 | 50.0289
|  |  | 44738.0012 | 50.0288
|  |  | 44738.0012 | 50.0288
|  |  | 44738.0012 | 50.0288
|  |  | 44738.0012 | 50.0287
|  |  | 44738.0012 | 50.0287
|  |  | 44738.0012 | 50.0287
|  |  | 44738.0012 | 50.0288
|  |  | 44738.0012 | 50.0288
|  |  | 44738.0012 | 50.0289
|  |  | 44738.0012 | 50.0289
|  |  | 44738.0012 | 50.029
|  |  | 44738.0012 | 50.029
|  |  | 44738.0012 | 50.029
|  |  | 44738.0012 | 50.029
|  |  | 44738.0012 | 50.029
|  |  | 44738.0012 | 50.0291
|  |  | 44738.0012 | 50.0291
|  |  | 44738.0012 | 50.0291
|  |  | 44738.0012 | 50.0292
|  |  | 44738.0012 | 50.0292
|  |  | 44738.0012 | 50.0293
|  |  | 44738.0012 | 50.0293
|  |  | 44738.0012 | 50.0293
|  |  | 44738.0012 | 50.0293
|  |  | 44738.0012 | 50.0293
|  |  | 2022-06-26 00:02 | 50.0292
|  |  | 44738.0012 | 50.0292
|  |  | 44738.0012 | 50.0291
|  |  | 44738.0012 | 50.0291
|  |  | 44738.0012 | 50.0291
|  |  | 44738.0012 | 50.029
|  |  | 44738.0012 | 50.0291
|  |  | 44738.0012 | 50.0291
|  |  | 44738.0012 | 50.0291
|  |  | 44738.0012 | 50.0291
|  |  | 44738.0012 | 50.0292
|  |  | 44738.0012 | 50.0292
|  |  | 44738.0012 | 50.0292
|  |  | 44738.0012 | 50.0292
|  |  | 44738.0012 | 50.0292
|  |  | 44738.0012 | 50.0292
|  |  | 44738.0012 | 50.0292
|  |  | 44738.0012 | 50.0292
|  |  | 44738.0012 | 50.0293
|  |  | 44738.0012 | 50.0293
|  |  | 44738.0012 | 50.0293
|  |  | 44738.0012 | 50.0293
|  |  | 44738.0012 | 50.0293
|  |  | 44738.0012 | 50.0293
|  |  | 44738.0012 | 50.0293
|  |  | 44738.0012 | 50.0293
|  |  | 44738.0012 | 50.0293
|  |  | 44738.0012 | 50.0293
|  |  | 44738.0012 | 50.0293
|  |  | 44738.0012 | 50.0294
|  |  | 44738.0012 | 50.0294
|  |  | 44738.0012 | 50.0295
|  |  | 44738.0012 | 50.0295
|  |  | 44738.0012 | 50.0296
|  |  | 44738.0012 | 50.0296
|  |  | 44738.0012 | 50.0297
|  |  | 44738.0012 | 50.0297
|  |  | 44738.0012 | 50.0297
|  |  | 44738.0012 | 50.0297
|  |  | 44738.0012 | 50.0297
|  |  | 44738.0012 | 50.0296
|  |  | 44738.0012 | 50.0296
|  |  | 44738.0012 | 50.0295
|  |  | 44738.0012 | 50.0295
|  |  | 44738.0012 | 50.0295
|  |  | 44738.0012 | 50.0295
|  |  | 44738.0012 | 50.0295
|  |  | 44738.0012 | 50.0295
|  |  | 44738.0012 | 50.0296
|  |  | 44738.0012 | 50.0296
|  |  | 2022-06-26 00:02 | 50.0296
|  |  | 44738.0012 | 50.0296
|  |  | 44738.0012 | 50.0296
|  |  | 44738.0012 | 50.0296
|  |  | 44738.0012 | 50.0296
|  |  | 44738.0012 | 50.0296
|  |  | 44738.0012 | 50.0296
|  |  | 44738.0012 | 50.0295
|  |  | 44738.0012 | 50.0295
|  |  | 44738.0012 | 50.0295
|  |  | 44738.0012 | 50.0295
|  |  | 44738.0012 | 50.0295
|  |  | 44738.0012 | 50.0295
|  |  | 44738.0012 | 50.0295
|  |  | 44738.0012 | 50.0296
|  |  | 44738.0012 | 50.0296
|  |  | 44738.0012 | 50.0296
|  |  | 44738.0012 | 50.0297
|  |  | 44738.0012 | 50.0297
|  |  | 44738.0012 | 50.0297
|  |  | 44738.0012 | 50.0297
|  |  | 44738.0012 | 50.0298
|  |  | 44738.0012 | 50.0298
|  |  | 44738.0012 | 50.0298
|  |  | 44738.0012 | 50.0298
|  |  | 44738.0012 | 50.0299
|  |  | 44738.0012 | 50.0299
|  |  | 44738.0012 | 50.0299
|  |  | 44738.0012 | 50.03
|  |  | 44738.0012 | 50.03
|  |  | 44738.0012 | 50.03
|  |  | 44738.0012 | 50.0299
|  |  | 44738.0012 | 50.0299
|  |  | 44738.0012 | 50.0299
|  |  | 44738.0012 | 50.0298
|  |  | 44738.0012 | 50.0298
|  |  | 44738.0012 | 50.0298
|  |  | 44738.0012 | 50.0298
|  |  | 44738.0012 | 50.0298
|  |  | 44738.0012 | 50.0298
|  |  | 44738.0012 | 50.0298
|  |  | 44738.0012 | 50.0298
|  |  | 44738.0012 | 50.0298
|  |  | 44738.0012 | 50.0298
|  |  | 44738.0012 | 50.0298
|  |  | 44738.0012 | 50.0298
|  |  | 44738.0012 | 50.0299
|  |  | 44738.0012 | 50.0299
|  |  | 44738.0012 | 50.0298
|  |  | 44738.0012 | 50.0298
|  |  | 2022-06-26 00:02 | 50.0297
|  |  | 44738.0012 | 50.0298
|  |  | 44738.0012 | 50.0297
|  |  | 44738.0012 | 50.0297
|  |  | 44738.0012 | 50.0297
|  |  | 44738.0012 | 50.0298
|  |  | 44738.0012 | 50.0298
|  |  | 44738.0012 | 50.0299
|  |  | 44738.0012 | 50.0299
|  |  | 44738.0012 | 50.0299
|  |  | 44738.0012 | 50.03
|  |  | 44738.0012 | 50.0301
|  |  | 44738.0012 | 50.0301
|  |  | 44738.0012 | 50.0301
|  |  | 44738.0012 | 50.0302
|  |  | 44738.0012 | 50.0302
|  |  | 44738.0012 | 50.0302
|  |  | 44738.0012 | 50.0301
|  |  | 44738.0012 | 50.0302
|  |  | 44738.0012 | 50.0302
|  |  | 44738.0012 | 50.0302
|  |  | 44738.0012 | 50.0302
|  |  | 44738.0012 | 50.0303
|  |  | 44738.0012 | 50.0303
|  |  | 44738.0012 | 50.0304
|  |  | 44738.0012 | 50.0303
|  |  | 44738.0012 | 50.0304
|  |  | 44738.0012 | 50.0304
|  |  | 44738.0012 | 50.0305
|  |  | 44738.0012 | 50.0305
|  |  | 44738.0012 | 50.0306
|  |  | 44738.0012 | 50.0306
|  |  | 44738.0012 | 50.0306
|  |  | 44738.0012 | 50.0307
|  |  | 44738.0012 | 50.0307
|  |  | 44738.0012 | 50.0306
|  |  | 44738.0012 | 50.0306
|  |  | 44738.0012 | 50.0305
|  |  | 44738.0012 | 50.0305
|  |  | 44738.0012 | 50.0305
|  |  | 44738.0012 | 50.0305
|  |  | 44738.0012 | 50.0306
|  |  | 44738.0012 | 50.0306
|  |  | 44738.0012 | 50.0307
|  |  | 44738.0012 | 50.0307
|  |  | 44738.0012 | 50.0308
|  |  | 44738.0012 | 50.0309
|  |  | 44738.0012 | 50.0309
|  |  | 44738.0012 | 50.031
|  |  | 44738.0012 | 50.031
|  |  | 2022-06-26 00:02 | 50.031
|  |  | 44738.0012 | 50.031
|  |  | 44738.0012 | 50.031
|  |  | 44738.0012 | 50.0309
|  |  | 44738.0012 | 50.0309
|  |  | 44738.0012 | 50.0308
|  |  | 44738.0012 | 50.0307
|  |  | 44738.0012 | 50.0307
|  |  | 44738.0012 | 50.0306
|  |  | 44738.0012 | 50.0306
|  |  | 44738.0012 | 50.0305
|  |  | 44738.0012 | 50.0305
|  |  | 44738.0012 | 50.0305
|  |  | 44738.0012 | 50.0306
|  |  | 44738.0012 | 50.0307
|  |  | 44738.0012 | 50.0308
|  |  | 44738.0012 | 50.0309
|  |  | 44738.0012 | 50.031
|  |  | 44738.0012 | 50.031
|  |  | 44738.0012 | 50.031
|  |  | 44738.0012 | 50.031
|  |  | 44738.0012 | 50.0309
|  |  | 44738.0012 | 50.0309
|  |  | 44738.0012 | 50.0308
|  |  | 44738.0012 | 50.0307
|  |  | 44738.0012 | 50.0307
|  |  | 44738.0012 | 50.0307
|  |  | 44738.0012 | 50.0308
|  |  | 44738.0012 | 50.0308
|  |  | 44738.0012 | 50.0309
|  |  | 44738.0012 | 50.031
|  |  | 44738.0012 | 50.031
|  |  | 44738.0012 | 50.0311
|  |  | 44738.0012 | 50.0311
|  |  | 44738.0012 | 50.0311
|  |  | 44738.0012 | 50.031
|  |  | 44738.0012 | 50.0311
|  |  | 44738.0012 | 50.031
|  |  | 44738.0012 | 50.031
|  |  | 44738.0012 | 50.031
|  |  | 44738.0012 | 50.031
|  |  | 44738.0012 | 50.0311
|  |  | 44738.0012 | 50.0311
|  |  | 44738.0012 | 50.0311
|  |  | 44738.0012 | 50.0311
|  |  | 44738.0012 | 50.0311
|  |  | 44738.0012 | 50.0311
|  |  | 44738.0012 | 50.0311
|  |  | 44738.0012 | 50.031
|  |  | 44738.0012 | 50.031
|  |  | 2022-06-26 00:02 | 50.0309
|  |  | 44738.0012 | 50.0309
|  |  | 44738.0012 | 50.0309
|  |  | 44738.0012 | 50.0309
|  |  | 44738.0012 | 50.0309
|  |  | 44738.0012 | 50.0309
|  |  | 44738.0012 | 50.0309
|  |  | 44738.0012 | 50.031
|  |  | 44738.0012 | 50.031
|  |  | 44738.0012 | 50.0311
|  |  | 44738.0012 | 50.0311
|  |  | 44738.0012 | 50.0312
|  |  | 44738.0012 | 50.0312
|  |  | 44738.0012 | 50.0312
|  |  | 44738.0012 | 50.0312
|  |  | 44738.0012 | 50.0312
|  |  | 44738.0012 | 50.0311
|  |  | 44738.0012 | 50.0311
|  |  | 44738.0012 | 50.031
|  |  | 44738.0012 | 50.031
|  |  | 44738.0012 | 50.0309
|  |  | 44738.0012 | 50.0309
|  |  | 44738.0012 | 50.0309
|  |  | 44738.0012 | 50.0308
|  |  | 44738.0012 | 50.0308
|  |  | 44738.0012 | 50.0308
|  |  | 44738.0012 | 50.0308
|  |  | 44738.0012 | 50.0308
|  |  | 44738.0012 | 50.0307
|  |  | 44738.0012 | 50.0307
|  |  | 44738.0012 | 50.0307
|  |  | 44738.0012 | 50.0306
|  |  | 44738.0012 | 50.0306
|  |  | 44738.0012 | 50.0306
|  |  | 44738.0012 | 50.0306
|  |  | 44738.0012 | 50.0305
|  |  | 44738.0012 | 50.0305
|  |  | 44738.0012 | 50.0305
|  |  | 44738.0012 | 50.0304
|  |  | 44738.0012 | 50.0304
|  |  | 44738.0012 | 50.0304
|  |  | 44738.0012 | 50.0304
|  |  | 44738.0012 | 50.0303
|  |  | 44738.0012 | 50.0303
|  |  | 44738.0012 | 50.0303
|  |  | 44738.0012 | 50.0302
|  |  | 44738.0012 | 50.0302
|  |  | 44738.0012 | 50.0302
|  |  | 44738.0012 | 50.0301
|  |  | 44738.0012 | 50.0301
|  |  | 2022-06-26 00:02 | 50.03
|  |  | 44738.0012 | 50.0299
|  |  | 44738.0012 | 50.0298
|  |  | 44738.0012 | 50.0298
|  |  | 44738.0012 | 50.0297
|  |  | 44738.0012 | 50.0296
|  |  | 44738.0012 | 50.0296
|  |  | 44738.0012 | 50.0295
|  |  | 44738.0012 | 50.0295
|  |  | 44738.0012 | 50.0294
|  |  | 44738.0012 | 50.0294
|  |  | 44738.0012 | 50.0294
|  |  | 44738.0012 | 50.0294
|  |  | 44738.0012 | 50.0295
|  |  | 44738.0012 | 50.0295
|  |  | 44738.0012 | 50.0295
|  |  | 44738.0012 | 50.0295
|  |  | 44738.0012 | 50.0296
|  |  | 44738.0012 | 50.0296
|  |  | 44738.0012 | 50.0295
|  |  | 44738.0012 | 50.0295
|  |  | 44738.0012 | 50.0294
|  |  | 44738.0012 | 50.0293
|  |  | 44738.0012 | 50.0292
|  |  | 44738.0012 | 50.0291
|  |  | 44738.0012 | 50.029
|  |  | 44738.0012 | 50.0289
|  |  | 44738.0012 | 50.0288
|  |  | 44738.0012 | 50.0288
|  |  | 44738.0012 | 50.0288
|  |  | 44738.0012 | 50.0288
|  |  | 44738.0012 | 50.0287
|  |  | 44738.0012 | 50.0287
|  |  | 44738.0012 | 50.0287
|  |  | 44738.0012 | 50.0286
|  |  | 44738.0012 | 50.0286
|  |  | 44738.0012 | 50.0285
|  |  | 44738.0012 | 50.0285
|  |  | 44738.0012 | 50.0284
|  |  | 44738.0012 | 50.0284
|  |  | 44738.0012 | 50.0283
|  |  | 44738.0012 | 50.0282
|  |  | 44738.0012 | 50.0281
|  |  | 44738.0012 | 50.028
|  |  | 44738.0012 | 50.0279
|  |  | 44738.0012 | 50.0278
|  |  | 44738.0012 | 50.0278
|  |  | 44738.0012 | 50.0277
|  |  | 44738.0012 | 50.0276
|  |  | 44738.0012 | 50.0275
|  |  | 2022-06-26 00:02 | 50.0275
|  |  | 44738.0012 | 50.0275
|  |  | 44738.0012 | 50.0274
|  |  | 44738.0012 | 50.0274
|  |  | 44738.0012 | 50.0273
|  |  | 44738.0012 | 50.0272
|  |  | 44738.0012 | 50.027
|  |  | 44738.0012 | 50.0269
|  |  | 44738.0012 | 50.0268
|  |  | 44738.0012 | 50.0267
|  |  | 44738.0012 | 50.0266
|  |  | 44738.0012 | 50.0266
|  |  | 44738.0012 | 50.0266
|  |  | 44738.0012 | 50.0267
|  |  | 44738.0012 | 50.0267
|  |  | 44738.0012 | 50.0266
|  |  | 44738.0012 | 50.0265
|  |  | 44738.0012 | 50.0264
|  |  | 44738.0012 | 50.0263
|  |  | 44738.0012 | 50.0261
|  |  | 44738.0012 | 50.0259
|  |  | 44738.0012 | 50.0257
|  |  | 44738.0012 | 50.0256
|  |  | 44738.0012 | 50.0254
|  |  | 44738.0012 | 50.0253
|  |  | 44738.0012 | 50.0252
|  |  | 44738.0012 | 50.0251
|  |  | 44738.0012 | 50.025
|  |  | 44738.0012 | 50.025
|  |  | 44738.0012 | 50.0249
|  |  | 44738.0012 | 50.0249
|  |  | 44738.0012 | 50.0248
|  |  | 44738.0012 | 50.0247
|  |  | 44738.0012 | 50.0246
|  |  | 44738.0012 | 50.0245
|  |  | 44738.0012 | 50.0244
|  |  | 44738.0012 | 50.0243
|  |  | 44738.0012 | 50.0242
|  |  | 44738.0012 | 50.0242
|  |  | 44738.0012 | 50.0241
|  |  | 44738.0012 | 50.0241
|  |  | 44738.0012 | 50.024
|  |  | 44738.0012 | 50.0239
|  |  | 44738.0012 | 50.0239
|  |  | 44738.0012 | 50.0238
|  |  | 44738.0012 | 50.0238
|  |  | 44738.0012 | 50.0238
|  |  | 44738.0012 | 50.0238
|  |  | 44738.0012 | 50.0238
|  |  | 44738.0012 | 50.0238
|  |  | 2022-06-26 00:02 | 50.0239
|  |  | 44738.0013 | 50.0239
|  |  | 44738.0013 | 50.0238
|  |  | 44738.0013 | 50.0238
|  |  | 44738.0013 | 50.0237
|  |  | 44738.0013 | 50.0237
|  |  | 44738.0013 | 50.0237
|  |  | 44738.0013 | 50.0236
|  |  | 44738.0013 | 50.0236
|  |  | 44738.0013 | 50.0235
|  |  | 44738.0013 | 50.0234
|  |  | 44738.0013 | 50.0234
|  |  | 44738.0013 | 50.0233
|  |  | 44738.0013 | 50.0232
|  |  | 44738.0013 | 50.0231
|  |  | 44738.0013 | 50.0231
|  |  | 44738.0013 | 50.023
|  |  | 44738.0013 | 50.0229
|  |  | 44738.0013 | 50.0229
|  |  | 44738.0013 | 50.0228
|  |  | 44738.0013 | 50.0227
|  |  | 44738.0013 | 50.0226
|  |  | 44738.0013 | 50.0225
|  |  | 44738.0013 | 50.0224
|  |  | 44738.0013 | 50.0223
|  |  | 44738.0013 | 50.0222
|  |  | 44738.0013 | 50.0221
|  |  | 44738.0013 | 50.022
|  |  | 44738.0013 | 50.0219
|  |  | 44738.0013 | 50.0217
|  |  | 44738.0013 | 50.0216
|  |  | 44738.0013 | 50.0215
|  |  | 44738.0013 | 50.0214
|  |  | 44738.0013 | 50.0213
|  |  | 44738.0013 | 50.0212
|  |  | 44738.0013 | 50.0211
|  |  | 44738.0013 | 50.0209
|  |  | 44738.0013 | 50.0208
|  |  | 44738.0013 | 50.0207
|  |  | 44738.0013 | 50.0206
|  |  | 44738.0013 | 50.0205
|  |  | 44738.0013 | 50.0205
|  |  | 44738.0013 | 50.0205
|  |  | 44738.0013 | 50.0204
|  |  | 44738.0013 | 50.0204
|  |  | 44738.0013 | 50.0203
|  |  | 44738.0013 | 50.0202
|  |  | 44738.0013 | 50.0202
|  |  | 44738.0013 | 50.0201
|  |  | 44738.0013 | 50.02
|  |  | 2022-06-26 00:02 | 50.0199
|  |  | 44738.0013 | 50.0199
|  |  | 44738.0013 | 50.02
|  |  | 44738.0013 | 50.0202
|  |  | 44738.0013 | 50.0203
|  |  | 44738.0013 | 50.0205
|  |  | 44738.0013 | 50.0207
|  |  | 44738.0013 | 50.0208
|  |  | 44738.0013 | 50.021
|  |  | 44738.0013 | 50.0211
|  |  | 44738.0013 | 50.0212
|  |  | 44738.0013 | 50.0212
|  |  | 44738.0013 | 50.0212
|  |  | 44738.0013 | 50.0212
|  |  | 44738.0013 | 50.0212
|  |  | 44738.0013 | 50.0212
|  |  | 44738.0013 | 50.0213
|  |  | 44738.0013 | 50.0214
|  |  | 44738.0013 | 50.0215
|  |  | 44738.0013 | 50.0216
|  |  | 44738.0013 | 50.0217
|  |  | 44738.0013 | 50.0217
|  |  | 44738.0013 | 50.0218
|  |  | 44738.0013 | 50.0217
|  |  | 44738.0013 | 50.0217
|  |  | 44738.0013 | 50.0217
|  |  | 44738.0013 | 50.0215
|  |  | 44738.0013 | 50.0212
|  |  | 44738.0013 | 50.0208
|  |  | 44738.0013 | 50.0202
|  |  | 44738.0013 | 50.0193
|  |  | 44738.0013 | 50.0184
|  |  | 44738.0013 | 50.0173
|  |  | 44738.0013 | 50.0161
|  |  | 44738.0013 | 50.0148
|  |  | 44738.0013 | 50.0133
|  |  | 44738.0013 | 50.0117
|  |  | 44738.0013 | 50.01
|  |  | 44738.0013 | 50.0084
|  |  | 44738.0013 | 50.0066
|  |  | 44738.0013 | 50.0049
|  |  | 44738.0013 | 50.0031
|  |  | 44738.0013 | 50.0014
|  |  | 44738.0013 | 49.9997
|  |  | 44738.0013 | 49.998
|  |  | 44738.0013 | 49.9965
|  |  | 44738.0013 | 49.9949
|  |  | 44738.0013 | 49.9934
|  |  | 44738.0013 | 49.9918
|  |  | 44738.0013 | 49.9902
|  |  | 2022-06-26 00:02 | 49.9889
|  |  | 44738.0013 | 49.9875
|  |  | 44738.0013 | 49.9863
|  |  | 44738.0013 | 49.9852
|  |  | 44738.0013 | 49.9842
|  |  | 44738.0013 | 49.9833
|  |  | 44738.0013 | 49.9825
|  |  | 44738.0013 | 49.9818
|  |  | 44738.0013 | 49.9811
|  |  | 44738.0013 | 49.9802
|  |  | 44738.0013 | 49.9799
|  |  | 44738.0013 | 49.9794
|  |  | 44738.0013 | 49.9789
|  |  | 44738.0013 | 49.9784
|  |  | 44738.0013 | 49.9779
|  |  | 44738.0013 | 49.9774
|  |  | 44738.0013 | 49.9768
|  |  | 44738.0013 | 49.9762
|  |  | 44738.0013 | 49.9755
|  |  | 44738.0013 | 49.9748
|  |  | 44738.0013 | 49.9741
|  |  | 44738.0013 | 49.9735
|  |  | 44738.0013 | 49.9727
|  |  | 44738.0013 | 49.9719
|  |  | 44738.0013 | 49.9709
|  |  | 44738.0013 | 49.9699
|  |  | 44738.0013 | 49.9688
|  |  | 44738.0013 | 49.9676
|  |  | 44738.0013 | 49.9662
|  |  | 44738.0013 | 49.9651
|  |  | 44738.0013 | 49.9637
|  |  | 44738.0013 | 49.9623
|  |  | 44738.0013 | 49.9608
|  |  | 44738.0013 | 49.9593
|  |  | 44738.0013 | 49.9577
|  |  | 44738.0013 | 49.9562
|  |  | 44738.0013 | 49.9543
|  |  | 44738.0013 | 49.9527
|  |  | 44738.0013 | 49.9511
|  |  | 44738.0013 | 49.9495
|  |  | 44738.0013 | 49.9478
|  |  | 44738.0013 | 49.9464
|  |  | 44738.0013 | 49.9451
|  |  | 44738.0013 | 49.9437
|  |  | 44738.0013 | 49.9425
|  |  | 44738.0013 | 49.9413
|  |  | 44738.0013 | 49.9402
|  |  | 44738.0013 | 49.939
|  |  | 44738.0013 | 49.9377
|  |  | 44738.0013 | 49.9363
|  |  | 2022-06-26 00:02 | 49.9351
|  |  | 44738.0013 | 49.9339
|  |  | 44738.0013 | 49.9327
|  |  | 44738.0013 | 49.9315
|  |  | 44738.0013 | 49.9304
|  |  | 44738.0013 | 49.9293
|  |  | 44738.0013 | 49.9283
|  |  | 44738.0013 | 49.9272
|  |  | 44738.0013 | 49.9263
|  |  | 44738.0013 | 49.9253
|  |  | 44738.0013 | 49.9244
|  |  | 44738.0013 | 49.9234
|  |  | 44738.0013 | 49.9224
|  |  | 44738.0013 | 49.9213
|  |  | 44738.0013 | 49.9202
|  |  | 44738.0013 | 49.9189
|  |  | 44738.0013 | 49.9177
|  |  | 44738.0013 | 49.9165
|  |  | 44738.0013 | 49.9153
|  |  | 44738.0013 | 49.914
|  |  | 44738.0013 | 49.9129
|  |  | 44738.0013 | 49.9118
|  |  | 44738.0013 | 49.9106
|  |  | 44738.0013 | 49.9094
|  |  | 44738.0013 | 49.9083
|  |  | 44738.0013 | 49.9071
|  |  | 44738.0013 | 49.9059
|  |  | 44738.0013 | 49.9046
|  |  | 44738.0013 | 49.9033
|  |  | 44738.0013 | 49.9022
|  |  | 44738.0013 | 49.9011
|  |  | 44738.0013 | 49.8999
|  |  | 44738.0013 | 49.8988
|  |  | 44738.0013 | 49.8979
|  |  | 44738.0013 | 49.8969
|  |  | 44738.0013 | 49.8961
|  |  | 44738.0013 | 49.8953
|  |  | 44738.0013 | 49.8945
|  |  | 44738.0013 | 49.8939
|  |  | 44738.0013 | 49.8931
|  |  | 44738.0013 | 49.8924
|  |  | 44738.0013 | 49.8917
|  |  | 44738.0013 | 49.8909
|  |  | 44738.0013 | 49.8903
|  |  | 44738.0013 | 49.8897
|  |  | 44738.0013 | 49.8891
|  |  | 44738.0013 | 49.8886
|  |  | 44738.0013 | 49.888
|  |  | 44738.0013 | 49.8876
|  |  | 44738.0013 | 49.8872
|  |  | 2022-06-26 00:02 | 49.8867
|  |  | 44738.0013 | 49.8862
|  |  | 44738.0013 | 49.8857
|  |  | 44738.0013 | 49.885
|  |  | 44738.0013 | 49.8843
|  |  | 44738.0013 | 49.8836
|  |  | 44738.0013 | 49.8828
|  |  | 44738.0013 | 49.882
|  |  | 44738.0013 | 49.8812
|  |  | 44738.0013 | 49.8804
|  |  | 44738.0013 | 49.8796
|  |  | 44738.0013 | 49.8788
|  |  | 44738.0013 | 49.878
|  |  | 44738.0013 | 49.8772
|  |  | 44738.0013 | 49.8765
|  |  | 44738.0013 | 49.8757
|  |  | 44738.0013 | 49.875
|  |  | 44738.0013 | 49.8743
|  |  | 44738.0013 | 49.8735
|  |  | 44738.0013 | 49.8728
|  |  | 44738.0013 | 49.8722
|  |  | 44738.0013 | 49.8714
|  |  | 44738.0013 | 49.8708
|  |  | 44738.0013 | 49.8701
|  |  | 44738.0013 | 49.8694
|  |  | 44738.0013 | 49.8686
|  |  | 44738.0013 | 49.868
|  |  | 44738.0013 | 49.8672
|  |  | 44738.0013 | 49.8665
|  |  | 44738.0013 | 49.8658
|  |  | 44738.0013 | 49.8652
|  |  | 44738.0013 | 49.8646
|  |  | 44738.0013 | 49.864
|  |  | 44738.0013 | 49.8636
|  |  | 44738.0013 | 49.8632
|  |  | 44738.0013 | 49.8629
|  |  | 44738.0013 | 49.8625
|  |  | 44738.0013 | 49.8622
|  |  | 44738.0013 | 49.8619
|  |  | 44738.0013 | 49.8615
|  |  | 44738.0013 | 49.8611
|  |  | 44738.0013 | 49.8607
|  |  | 44738.0013 | 49.8602
|  |  | 44738.0013 | 49.8597
|  |  | 44738.0013 | 49.8592
|  |  | 44738.0013 | 49.8587
|  |  | 44738.0013 | 49.8582
|  |  | 44738.0013 | 49.8577
|  |  | 44738.0013 | 49.8572
|  |  | 44738.0013 | 49.8568
|  |  | 2022-06-26 00:02 | 49.8563
|  |  | 44738.0013 | 49.8558
|  |  | 44738.0013 | 49.8554
|  |  | 44738.0013 | 49.855
|  |  | 44738.0013 | 49.8546
|  |  | 44738.0013 | 49.8542
|  |  | 44738.0013 | 49.8538
|  |  | 44738.0013 | 49.8534
|  |  | 44738.0013 | 49.8531
|  |  | 44738.0013 | 49.8528
|  |  | 44738.0013 | 49.8524
|  |  | 44738.0013 | 49.8521
|  |  | 44738.0013 | 49.8518
|  |  | 44738.0013 | 49.8515
|  |  | 44738.0013 | 49.8512
|  |  | 44738.0013 | 49.8509
|  |  | 44738.0013 | 49.8505
|  |  | 44738.0013 | 49.8502
|  |  | 44738.0013 | 49.8498
|  |  | 44738.0013 | 49.8495
|  |  | 44738.0013 | 49.8491
|  |  | 44738.0013 | 49.8488
|  |  | 44738.0013 | 49.8485
|  |  | 44738.0013 | 49.8483
|  |  | 44738.0013 | 49.848
|  |  | 44738.0013 | 49.8477
|  |  | 44738.0013 | 49.8474
|  |  | 44738.0013 | 49.8472
|  |  | 44738.0013 | 49.8469
|  |  | 44738.0013 | 49.8467
|  |  | 44738.0013 | 49.8466
|  |  | 44738.0013 | 49.8464
|  |  | 44738.0013 | 49.8462
|  |  | 44738.0013 | 49.8461
|  |  | 44738.0013 | 49.8459
|  |  | 44738.0013 | 49.8456
|  |  | 44738.0013 | 49.8453
|  |  | 44738.0013 | 49.845
|  |  | 44738.0013 | 49.8447
|  |  | 44738.0013 | 49.8445
|  |  | 44738.0013 | 49.8443
|  |  | 44738.0013 | 49.8441
|  |  | 44738.0013 | 49.844
|  |  | 44738.0013 | 49.844
|  |  | 44738.0013 | 49.8439
|  |  | 44738.0013 | 49.8438
|  |  | 44738.0013 | 49.8436
|  |  | 44738.0013 | 49.8434
|  |  | 44738.0013 | 49.8432
|  |  | 44738.0013 | 49.8429
|  |  | 2022-06-26 00:02 | 49.8426
|  |  | 44738.0013 | 49.8424
|  |  | 44738.0013 | 49.8422
|  |  | 44738.0013 | 49.842
|  |  | 44738.0013 | 49.8419
|  |  | 44738.0013 | 49.8419
|  |  | 44738.0013 | 49.8418
|  |  | 44738.0013 | 49.8418
|  |  | 44738.0013 | 49.8418
|  |  | 44738.0013 | 49.8419
|  |  | 44738.0013 | 49.8419
|  |  | 44738.0013 | 49.842
|  |  | 44738.0013 | 49.842
|  |  | 44738.0013 | 49.842
|  |  | 44738.0013 | 49.842
|  |  | 44738.0013 | 49.842
|  |  | 44738.0013 | 49.8419
|  |  | 44738.0013 | 49.8418
|  |  | 44738.0013 | 49.8417
|  |  | 44738.0013 | 49.8416
|  |  | 44738.0013 | 49.8415
|  |  | 44738.0013 | 49.8413
|  |  | 44738.0013 | 49.8412
|  |  | 44738.0013 | 49.8412
|  |  | 44738.0013 | 49.8412
|  |  | 44738.0013 | 49.8412
|  |  | 44738.0013 | 49.8412
|  |  | 44738.0013 | 49.8412
|  |  | 44738.0013 | 49.8412
|  |  | 44738.0013 | 49.8412
|  |  | 44738.0013 | 49.8412
|  |  | 44738.0013 | 49.8412
|  |  | 44738.0013 | 49.8412
|  |  | 44738.0013 | 49.8412
|  |  | 44738.0013 | 49.8411
|  |  | 44738.0013 | 49.8411
|  |  | 44738.0013 | 49.841
|  |  | 44738.0013 | 49.8409
|  |  | 44738.0013 | 49.8409
|  |  | 44738.0013 | 49.8409
|  |  | 44738.0013 | 49.8409
|  |  | 44738.0013 | 49.841
|  |  | 44738.0013 | 49.8411
|  |  | 44738.0013 | 49.8412
|  |  | 44738.0013 | 49.8413
|  |  | 44738.0013 | 49.8414
|  |  | 44738.0013 | 49.8415
|  |  | 44738.0013 | 49.8416
|  |  | 44738.0013 | 49.8417
|  |  | 44738.0013 | 49.8418
|  |  | 2022-06-26 00:02 | 49.8419
|  |  | 44738.0013 | 49.8419
|  |  | 44738.0013 | 49.842
|  |  | 44738.0013 | 49.842
|  |  | 44738.0013 | 49.8421
|  |  | 44738.0013 | 49.8422
|  |  | 44738.0013 | 49.8424
|  |  | 44738.0013 | 49.8425
|  |  | 44738.0013 | 49.8426
|  |  | 44738.0013 | 49.8427
|  |  | 44738.0013 | 49.8428
|  |  | 44738.0013 | 49.8428
|  |  | 44738.0013 | 49.8429
|  |  | 44738.0013 | 49.843
|  |  | 44738.0013 | 49.8431
|  |  | 44738.0013 | 49.8432
|  |  | 44738.0013 | 49.8434
|  |  | 44738.0013 | 49.8435
|  |  | 44738.0013 | 49.8436
|  |  | 44738.0013 | 49.8436
|  |  | 44738.0013 | 49.8436
|  |  | 44738.0013 | 49.8436
|  |  | 44738.0013 | 49.8436
|  |  | 44738.0013 | 49.8436
|  |  | 44738.0013 | 49.8437
|  |  | 44738.0013 | 49.8438
|  |  | 44738.0013 | 49.8439
|  |  | 44738.0013 | 49.8439
|  |  | 44738.0013 | 49.8441
|  |  | 44738.0013 | 49.8442
|  |  | 44738.0013 | 49.8444
|  |  | 44738.0013 | 49.8445
|  |  | 44738.0013 | 49.8446
|  |  | 44738.0013 | 49.8448
|  |  | 44738.0013 | 49.8449
|  |  | 44738.0013 | 49.845
|  |  | 44738.0013 | 49.8452
|  |  | 44738.0013 | 49.8453
|  |  | 44738.0013 | 49.8455
|  |  | 44738.0013 | 49.8456
|  |  | 44738.0013 | 49.8458
|  |  | 44738.0013 | 49.846
|  |  | 44738.0013 | 49.8462
|  |  | 44738.0013 | 49.8464
|  |  | 44738.0013 | 49.8466
|  |  | 44738.0013 | 49.8468
|  |  | 44738.0013 | 49.847
|  |  | 44738.0013 | 49.8471
|  |  | 44738.0013 | 49.8472
|  |  | 44738.0013 | 49.8474
|  |  | 2022-06-26 00:02 | 49.8476
|  |  | 44738.0013 | 49.8478
|  |  | 44738.0013 | 49.8481
|  |  | 44738.0013 | 49.8483
|  |  | 44738.0013 | 49.8485
|  |  | 44738.0013 | 49.8488
|  |  | 44738.0013 | 49.849
|  |  | 44738.0013 | 49.8492
|  |  | 44738.0013 | 49.8494
|  |  | 44738.0013 | 49.8495
|  |  | 44738.0013 | 49.8496
|  |  | 44738.0013 | 49.8497
|  |  | 44738.0013 | 49.8498
|  |  | 44738.0013 | 49.8499
|  |  | 44738.0013 | 49.8501
|  |  | 44738.0013 | 49.8502
|  |  | 44738.0013 | 49.8504
|  |  | 44738.0013 | 49.8506
|  |  | 44738.0013 | 49.8507
|  |  | 44738.0013 | 49.8509
|  |  | 44738.0013 | 49.851
|  |  | 44738.0013 | 49.8512
|  |  | 44738.0013 | 49.8514
|  |  | 44738.0013 | 49.8515
|  |  | 44738.0013 | 49.8516
|  |  | 44738.0013 | 49.8517
|  |  | 44738.0013 | 49.8518
|  |  | 44738.0013 | 49.8519
|  |  | 44738.0013 | 49.852
|  |  | 44738.0013 | 49.8521
|  |  | 44738.0013 | 49.8523
|  |  | 44738.0013 | 49.8524
|  |  | 44738.0013 | 49.8527
|  |  | 44738.0014 | 49.8529
|  |  | 44738.0014 | 49.8532
|  |  | 44738.0014 | 49.8535
|  |  | 44738.0014 | 49.8538
|  |  | 44738.0014 | 49.854
|  |  | 44738.0014 | 49.8543
|  |  | 44738.0014 | 49.8545
|  |  | 44738.0014 | 49.8546
|  |  | 44738.0014 | 49.8548
|  |  | 44738.0014 | 49.855
|  |  | 44738.0014 | 49.8552
|  |  | 44738.0014 | 49.8554
|  |  | 44738.0014 | 49.8556
|  |  | 44738.0014 | 49.8558
|  |  | 44738.0014 | 49.856
|  |  | 44738.0014 | 49.8563
|  |  | 44738.0014 | 49.8565
|  |  | 2022-06-26 00:02 | 49.8567
|  |  | 44738.0014 | 49.8569
|  |  | 44738.0014 | 49.8571
|  |  | 44738.0014 | 49.8574
|  |  | 44738.0014 | 49.8576
|  |  | 44738.0014 | 49.8578
|  |  | 44738.0014 | 49.8579
|  |  | 44738.0014 | 49.8581
|  |  | 44738.0014 | 49.8583
|  |  | 44738.0014 | 49.8586
|  |  | 44738.0014 | 49.8587
|  |  | 44738.0014 | 49.8589
|  |  | 44738.0014 | 49.8591
|  |  | 44738.0014 | 49.8593
|  |  | 44738.0014 | 49.8595
|  |  | 44738.0014 | 49.8596
|  |  | 44738.0014 | 49.8598
|  |  | 44738.0014 | 49.86
|  |  | 44738.0014 | 49.8602
|  |  | 44738.0014 | 49.8604
|  |  | 44738.0014 | 49.8606
|  |  | 44738.0014 | 49.8609
|  |  | 44738.0014 | 49.8611
|  |  | 44738.0014 | 49.8613
|  |  | 44738.0014 | 49.8614
|  |  | 44738.0014 | 49.8616
|  |  | 44738.0014 | 49.8618
|  |  | 44738.0014 | 49.8619
|  |  | 44738.0014 | 49.8621
|  |  | 44738.0014 | 49.8622
|  |  | 44738.0014 | 49.8623
|  |  | 44738.0014 | 49.8625
|  |  | 44738.0014 | 49.8627
|  |  | 44738.0014 | 49.8628
|  |  | 44738.0014 | 49.863
|  |  | 44738.0014 | 49.8632
|  |  | 44738.0014 | 49.8634
|  |  | 44738.0014 | 49.8636
|  |  | 44738.0014 | 49.8637
|  |  | 44738.0014 | 49.8638
|  |  | 44738.0014 | 49.8639
|  |  | 44738.0014 | 49.8641
|  |  | 44738.0014 | 49.8642
|  |  | 44738.0014 | 49.8644
|  |  | 44738.0014 | 49.8646
|  |  | 44738.0014 | 49.8648
|  |  | 44738.0014 | 49.865
|  |  | 44738.0014 | 49.8652
|  |  | 44738.0014 | 49.8654
|  |  | 44738.0014 | 49.8656
|  |  | 2022-06-26 00:02 | 49.8657
|  |  | 44738.0014 | 49.8659
|  |  | 44738.0014 | 49.866
|  |  | 44738.0014 | 49.8661
|  |  | 44738.0014 | 49.8663
|  |  | 44738.0014 | 49.8665
|  |  | 44738.0014 | 49.8666
|  |  | 44738.0014 | 49.8668
|  |  | 44738.0014 | 49.867
|  |  | 44738.0014 | 49.8673
|  |  | 44738.0014 | 49.8675
|  |  | 44738.0014 | 49.8677
|  |  | 44738.0014 | 49.8679
|  |  | 44738.0014 | 49.868
|  |  | 44738.0014 | 49.8682
|  |  | 44738.0014 | 49.8684
|  |  | 44738.0014 | 49.8685
|  |  | 44738.0014 | 49.8687
|  |  | 44738.0014 | 49.8688
|  |  | 44738.0014 | 49.869
|  |  | 44738.0014 | 49.8691
|  |  | 44738.0014 | 49.8692
|  |  | 44738.0014 | 49.8694
|  |  | 44738.0014 | 49.8695
|  |  | 44738.0014 | 49.8696
|  |  | 44738.0014 | 49.8697
|  |  | 44738.0014 | 49.8698
|  |  | 44738.0014 | 49.8699
|  |  | 44738.0014 | 49.87
|  |  | 44738.0014 | 49.8701
|  |  | 44738.0014 | 49.8701
|  |  | 44738.0014 | 49.8702
|  |  | 44738.0014 | 49.8704
|  |  | 44738.0014 | 49.8704
|  |  | 44738.0014 | 49.8706
|  |  | 44738.0014 | 49.8707
|  |  | 44738.0014 | 49.8709
|  |  | 44738.0014 | 49.871
|  |  | 44738.0014 | 49.8711
|  |  | 44738.0014 | 49.8712
|  |  | 44738.0014 | 49.8712
|  |  | 44738.0014 | 49.8713
|  |  | 44738.0014 | 49.8714
|  |  | 44738.0014 | 49.8714
|  |  | 44738.0014 | 49.8715
|  |  | 44738.0014 | 49.8715
|  |  | 44738.0014 | 49.8715
|  |  | 44738.0014 | 49.8716
|  |  | 44738.0014 | 49.8717
|  |  | 44738.0014 | 49.8718
|  |  | 2022-06-26 00:02 | 49.8719
|  |  | 44738.0014 | 49.8721
|  |  | 44738.0014 | 49.8723
|  |  | 44738.0014 | 49.8725
|  |  | 44738.0014 | 49.8727
|  |  | 44738.0014 | 49.8729
|  |  | 44738.0014 | 49.873
|  |  | 44738.0014 | 49.873
|  |  | 44738.0014 | 49.8731
|  |  | 44738.0014 | 49.8732
|  |  | 44738.0014 | 49.8732
|  |  | 44738.0014 | 49.8733
|  |  | 44738.0014 | 49.8735
|  |  | 44738.0014 | 49.8737
|  |  | 44738.0014 | 49.8738
|  |  | 44738.0014 | 49.8741
|  |  | 44738.0014 | 49.8742
|  |  | 44738.0014 | 49.8744
|  |  | 44738.0014 | 49.8745
|  |  | 44738.0014 | 49.8746
|  |  | 44738.0014 | 49.8746
|  |  | 44738.0014 | 49.8746
|  |  | 44738.0014 | 49.8746
|  |  | 44738.0014 | 49.8746
|  |  | 44738.0014 | 49.8747
|  |  | 44738.0014 | 49.8748
|  |  | 44738.0014 | 49.8749
|  |  | 44738.0014 | 49.875
|  |  | 44738.0014 | 49.8751
|  |  | 44738.0014 | 49.8752
|  |  | 44738.0014 | 49.8753
|  |  | 44738.0014 | 49.8754
|  |  | 44738.0014 | 49.8755
|  |  | 44738.0014 | 49.8755
|  |  | 44738.0014 | 49.8756
|  |  | 44738.0014 | 49.8757
|  |  | 44738.0014 | 49.8757
|  |  | 44738.0014 | 49.8757
|  |  | 44738.0014 | 49.8758
|  |  | 44738.0014 | 49.8758
|  |  | 44738.0014 | 49.8758
|  |  | 44738.0014 | 49.8758
|  |  | 44738.0014 | 49.8758
|  |  | 44738.0014 | 49.8758
|  |  | 44738.0014 | 49.8758
|  |  | 44738.0014 | 49.8759
|  |  | 44738.0014 | 49.8759
|  |  | 44738.0014 | 49.8759
|  |  | 44738.0014 | 49.876
|  |  | 44738.0014 | 49.8761
|  |  | 2022-06-26 00:02 | 49.8761
|  |  | 44738.0014 | 49.8761
|  |  | 44738.0014 | 49.8762
|  |  | 44738.0014 | 49.8762
|  |  | 44738.0014 | 49.8763
|  |  | 44738.0014 | 49.8762
|  |  | 44738.0014 | 49.8762
|  |  | 44738.0014 | 49.8761
|  |  | 44738.0014 | 49.8759
|  |  | 44738.0014 | 49.8758
|  |  | 44738.0014 | 49.8756
|  |  | 44738.0014 | 49.8755
|  |  | 44738.0014 | 49.8754
|  |  | 44738.0014 | 49.8754
|  |  | 44738.0014 | 49.8755
|  |  | 44738.0014 | 49.8756
|  |  | 44738.0014 | 49.8757
|  |  | 44738.0014 | 49.8758
|  |  | 44738.0014 | 49.876
|  |  | 44738.0014 | 49.876
|  |  | 44738.0014 | 49.8759
|  |  | 44738.0014 | 49.8759
|  |  | 44738.0014 | 49.8758
|  |  | 44738.0014 | 49.8757
|  |  | 44738.0014 | 49.8756
|  |  | 44738.0014 | 49.8754
|  |  | 44738.0014 | 49.8754
|  |  | 44738.0014 | 49.8753
|  |  | 44738.0014 | 49.8752
|  |  | 44738.0014 | 49.8752
|  |  | 44738.0014 | 49.8753
|  |  | 44738.0014 | 49.8754
|  |  | 44738.0014 | 49.8754
|  |  | 44738.0014 | 49.8755
|  |  | 44738.0014 | 49.8755
|  |  | 44738.0014 | 49.8756
|  |  | 44738.0014 | 49.8756
|  |  | 44738.0014 | 49.8756
|  |  | 44738.0014 | 49.8756
|  |  | 44738.0014 | 49.8755
|  |  | 44738.0014 | 49.8755
|  |  | 44738.0014 | 49.8754
|  |  | 44738.0014 | 49.8753
|  |  | 44738.0014 | 49.8753
|  |  | 44738.0014 | 49.8752
|  |  | 44738.0014 | 49.8751
|  |  | 44738.0014 | 49.8751
|  |  | 44738.0014 | 49.8751
|  |  | 44738.0014 | 49.8751
|  |  | 44738.0014 | 49.8751
|  |  | 2022-06-26 00:02 | 49.8751
|  |  | 44738.0014 | 49.8751
|  |  | 44738.0014 | 49.8752
|  |  | 44738.0014 | 49.8752
|  |  | 44738.0014 | 49.8753
|  |  | 44738.0014 | 49.8753
|  |  | 44738.0014 | 49.8754
|  |  | 44738.0014 | 49.8754
|  |  | 44738.0014 | 49.8754
|  |  | 44738.0014 | 49.8755
|  |  | 44738.0014 | 49.8755
|  |  | 44738.0014 | 49.8756
|  |  | 44738.0014 | 49.8756
|  |  | 44738.0014 | 49.8756
|  |  | 44738.0014 | 49.8756
|  |  | 44738.0014 | 49.8755
|  |  | 44738.0014 | 49.8755
|  |  | 44738.0014 | 49.8755
|  |  | 44738.0014 | 49.8755
|  |  | 44738.0014 | 49.8755
|  |  | 44738.0014 | 49.8756
|  |  | 44738.0014 | 49.8756
|  |  | 44738.0014 | 49.8756
|  |  | 44738.0014 | 49.8757
|  |  | 44738.0014 | 49.8757
|  |  | 44738.0014 | 49.8757
|  |  | 44738.0014 | 49.8757
|  |  | 44738.0014 | 49.8756
|  |  | 44738.0014 | 49.8756
|  |  | 44738.0014 | 49.8756
|  |  | 44738.0014 | 49.8756
|  |  | 44738.0014 | 49.8755
|  |  | 44738.0014 | 49.8755
|  |  | 44738.0014 | 49.8755
|  |  | 44738.0014 | 49.8754
|  |  | 44738.0014 | 49.8754
|  |  | 44738.0014 | 49.8754
|  |  | 44738.0014 | 49.8754
|  |  | 44738.0014 | 49.8755
|  |  | 44738.0014 | 49.8755
|  |  | 44738.0014 | 49.8755
|  |  | 44738.0014 | 49.8755
|  |  | 44738.0014 | 49.8755
|  |  | 44738.0014 | 49.8754
|  |  | 44738.0014 | 49.8753
|  |  | 44738.0014 | 49.8753
|  |  | 44738.0014 | 49.8753
|  |  | 44738.0014 | 49.8753
|  |  | 44738.0014 | 49.8752
|  |  | 44738.0014 | 49.8753
|  |  | 2022-06-26 00:02 | 49.8753
|  |  | 44738.0014 | 49.8753
|  |  | 44738.0014 | 49.8753
|  |  | 44738.0014 | 49.8753
|  |  | 44738.0014 | 49.8753
|  |  | 44738.0014 | 49.8753
|  |  | 44738.0014 | 49.8753
|  |  | 44738.0014 | 49.8753
|  |  | 44738.0014 | 49.8754
|  |  | 44738.0014 | 49.8755
|  |  | 44738.0014 | 49.8755
|  |  | 44738.0014 | 49.8756
|  |  | 44738.0014 | 49.8756
|  |  | 44738.0014 | 49.8756
|  |  | 44738.0014 | 49.8756
|  |  | 44738.0014 | 49.8756
|  |  | 44738.0014 | 49.8755
|  |  | 44738.0014 | 49.8755
|  |  | 44738.0014 | 49.8755
|  |  | 44738.0014 | 49.8754
|  |  | 44738.0014 | 49.8754
|  |  | 44738.0014 | 49.8754
|  |  | 44738.0014 | 49.8754
|  |  | 44738.0014 | 49.8754
|  |  | 44738.0014 | 49.8754
|  |  | 44738.0014 | 49.8754
|  |  | 44738.0014 | 49.8754
|  |  | 44738.0014 | 49.8755
|  |  | 44738.0014 | 49.8755
|  |  | 44738.0014 | 49.8755
|  |  | 44738.0014 | 49.8755
|  |  | 44738.0014 | 49.8755
|  |  | 44738.0014 | 49.8754
|  |  | 44738.0014 | 49.8753
|  |  | 44738.0014 | 49.8752
|  |  | 44738.0014 | 49.875
|  |  | 44738.0014 | 49.8749
|  |  | 44738.0014 | 49.8748
|  |  | 44738.0014 | 49.8747
|  |  | 44738.0014 | 49.8747
|  |  | 44738.0014 | 49.8747
|  |  | 44738.0014 | 49.8748
|  |  | 44738.0014 | 49.8748
|  |  | 44738.0014 | 49.8749
|  |  | 44738.0014 | 49.875
|  |  | 44738.0014 | 49.875
|  |  | 44738.0014 | 49.875
|  |  | 44738.0014 | 49.875
|  |  | 44738.0014 | 49.875
|  |  | 44738.0014 | 49.8749
|  |  | 2022-06-26 00:02 | 49.8749
|  |  | 44738.0014 | 49.8748
|  |  | 44738.0014 | 49.8747
|  |  | 44738.0014 | 49.8747
|  |  | 44738.0014 | 49.8747
|  |  | 44738.0014 | 49.8746
|  |  | 44738.0014 | 49.8747
|  |  | 44738.0014 | 49.8747
|  |  | 44738.0014 | 49.8747
|  |  | 44738.0014 | 49.8746
|  |  | 44738.0014 | 49.8746
|  |  | 44738.0014 | 49.8745
|  |  | 44738.0014 | 49.8744
|  |  | 44738.0014 | 49.8744
|  |  | 44738.0014 | 49.8744
|  |  | 44738.0014 | 49.8743
|  |  | 44738.0014 | 49.8744
|  |  | 44738.0014 | 49.8745
|  |  | 44738.0014 | 49.8746
|  |  | 44738.0014 | 49.8747
|  |  | 44738.0014 | 49.8747
|  |  | 44738.0014 | 49.8747
|  |  | 44738.0014 | 49.8747
|  |  | 44738.0014 | 49.8747
|  |  | 44738.0014 | 49.8746
|  |  | 44738.0014 | 49.8745
|  |  | 44738.0014 | 49.8743
|  |  | 44738.0014 | 49.8742
|  |  | 44738.0014 | 49.8741
|  |  | 44738.0014 | 49.874
|  |  | 44738.0014 | 49.8739
|  |  | 44738.0014 | 49.8739
|  |  | 44738.0014 | 49.8739
|  |  | 44738.0014 | 49.8739
|  |  | 44738.0014 | 49.8739
|  |  | 44738.0014 | 49.8739
|  |  | 44738.0014 | 49.874
|  |  | 44738.0014 | 49.874
|  |  | 44738.0014 | 49.8741
|  |  | 44738.0014 | 49.8741
|  |  | 44738.0014 | 49.8741
|  |  | 44738.0014 | 49.874
|  |  | 44738.0014 | 49.8739
|  |  | 44738.0014 | 49.8738
|  |  | 44738.0014 | 49.8737
|  |  | 44738.0014 | 49.8735
|  |  | 44738.0014 | 49.8734
|  |  | 44738.0014 | 49.8733
|  |  | 44738.0014 | 49.8733
|  |  | 44738.0014 | 49.8732
|  |  | 2022-06-26 00:02 | 49.8732
|  |  | 44738.0014 | 49.8732
|  |  | 44738.0014 | 49.8732
|  |  | 44738.0014 | 49.8732
|  |  | 44738.0014 | 49.8732
|  |  | 44738.0014 | 49.8732
|  |  | 44738.0014 | 49.8731
|  |  | 44738.0014 | 49.8731
|  |  | 44738.0014 | 49.873
|  |  | 44738.0014 | 49.8729
|  |  | 44738.0014 | 49.8729
|  |  | 44738.0014 | 49.8729
|  |  | 44738.0014 | 49.8729
|  |  | 44738.0014 | 49.8729
|  |  | 44738.0014 | 49.873
|  |  | 44738.0014 | 49.8731
|  |  | 44738.0014 | 49.8731
|  |  | 44738.0014 | 49.8731
|  |  | 44738.0014 | 49.8731
|  |  | 44738.0014 | 49.8731
|  |  | 44738.0014 | 49.8731
|  |  | 44738.0014 | 49.8731
|  |  | 44738.0014 | 49.873
|  |  | 44738.0014 | 49.8729
|  |  | 44738.0014 | 49.8728
|  |  | 44738.0014 | 49.8727
|  |  | 44738.0014 | 49.8726
|  |  | 44738.0014 | 49.8726
|  |  | 44738.0014 | 49.8725
|  |  | 44738.0014 | 49.8725
|  |  | 44738.0014 | 49.8726
|  |  | 44738.0014 | 49.8726
|  |  | 44738.0014 | 49.8727
|  |  | 44738.0014 | 49.8726
|  |  | 44738.0014 | 49.8726
|  |  | 44738.0014 | 49.8727
|  |  | 44738.0014 | 49.8726
|  |  | 44738.0014 | 49.8726
|  |  | 44738.0014 | 49.8725
|  |  | 44738.0014 | 49.8724
|  |  | 44738.0014 | 49.8723
|  |  | 44738.0014 | 49.8721
|  |  | 44738.0014 | 49.872
|  |  | 44738.0014 | 49.8719
|  |  | 44738.0014 | 49.8718
|  |  | 44738.0014 | 49.8717
|  |  | 44738.0014 | 49.8716
|  |  | 44738.0014 | 49.8715
|  |  | 44738.0014 | 49.8715
|  |  | 44738.0014 | 49.8714
|  |  | 2022-06-26 00:02 | 49.8713
|  |  | 44738.0014 | 49.8713
|  |  | 44738.0014 | 49.8712
|  |  | 44738.0014 | 49.8711
|  |  | 44738.0014 | 49.871
|  |  | 44738.0014 | 49.8708
|  |  | 44738.0014 | 49.8707
|  |  | 44738.0014 | 49.8706
|  |  | 44738.0014 | 49.8705
|  |  | 44738.0014 | 49.8705
|  |  | 44738.0014 | 49.8705
|  |  | 44738.0014 | 49.8705
|  |  | 44738.0014 | 49.8704
|  |  | 44738.0014 | 49.8705
|  |  | 44738.0015 | 49.8705
|  |  | 44738.0015 | 49.8704
|  |  | 44738.0015 | 49.8704
|  |  | 44738.0015 | 49.8703
|  |  | 44738.0015 | 49.8703
|  |  | 44738.0015 | 49.8702
|  |  | 44738.0015 | 49.8702
|  |  | 44738.0015 | 49.8702
|  |  | 44738.0015 | 49.8701
|  |  | 44738.0015 | 49.8702
|  |  | 44738.0015 | 49.8702
|  |  | 44738.0015 | 49.8702
|  |  | 44738.0015 | 49.8702
|  |  | 44738.0015 | 49.8701
|  |  | 44738.0015 | 49.8701
|  |  | 44738.0015 | 49.87
|  |  | 44738.0015 | 49.8699
|  |  | 44738.0015 | 49.8698
|  |  | 44738.0015 | 49.8697
|  |  | 44738.0015 | 49.8697
|  |  | 44738.0015 | 49.8697
|  |  | 44738.0015 | 49.8697
|  |  | 44738.0015 | 49.8696
|  |  | 44738.0015 | 49.8696
|  |  | 44738.0015 | 49.8696
|  |  | 44738.0015 | 49.8697
|  |  | 44738.0015 | 49.8697
|  |  | 44738.0015 | 49.8697
|  |  | 44738.0015 | 49.8696
|  |  | 44738.0015 | 49.8696
|  |  | 44738.0015 | 49.8695
|  |  | 44738.0015 | 49.8695
|  |  | 44738.0015 | 49.8695
|  |  | 44738.0015 | 49.8694
|  |  | 44738.0015 | 49.8694
|  |  | 44738.0015 | 49.8694
|  |  | 2022-06-26 00:02 | 49.8695
|  |  | 44738.0015 | 49.8695
|  |  | 44738.0015 | 49.8694
|  |  | 44738.0015 | 49.8694
|  |  | 44738.0015 | 49.8693
|  |  | 44738.0015 | 49.8693
|  |  | 44738.0015 | 49.8691
|  |  | 44738.0015 | 49.869
|  |  | 44738.0015 | 49.869
|  |  | 44738.0015 | 49.8689
|  |  | 44738.0015 | 49.8689
|  |  | 44738.0015 | 49.8688
|  |  | 44738.0015 | 49.8688
|  |  | 44738.0015 | 49.8688
|  |  | 44738.0015 | 49.8688
|  |  | 44738.0015 | 49.8688
|  |  | 44738.0015 | 49.8688
|  |  | 44738.0015 | 49.8688
|  |  | 44738.0015 | 49.8688
|  |  | 44738.0015 | 49.8688
|  |  | 44738.0015 | 49.8687
|  |  | 44738.0015 | 49.8687
|  |  | 44738.0015 | 49.8687
|  |  | 44738.0015 | 49.8686
|  |  | 44738.0015 | 49.8686
|  |  | 44738.0015 | 49.8685
|  |  | 44738.0015 | 49.8685
|  |  | 44738.0015 | 49.8686
|  |  | 44738.0015 | 49.8686
|  |  | 44738.0015 | 49.8687
|  |  | 44738.0015 | 49.8687
|  |  | 44738.0015 | 49.8687
|  |  | 44738.0015 | 49.8687
|  |  | 44738.0015 | 49.8687
|  |  | 44738.0015 | 49.8686
|  |  | 44738.0015 | 49.8685
|  |  | 44738.0015 | 49.8685
|  |  | 44738.0015 | 49.8684
|  |  | 44738.0015 | 49.8684
|  |  | 44738.0015 | 49.8683
|  |  | 44738.0015 | 49.8684
|  |  | 44738.0015 | 49.8684
|  |  | 44738.0015 | 49.8685
|  |  | 44738.0015 | 49.8685
|  |  | 44738.0015 | 49.8685
|  |  | 44738.0015 | 49.8685
|  |  | 44738.0015 | 49.8685
|  |  | 44738.0015 | 49.8684
|  |  | 44738.0015 | 49.8684
|  |  | 44738.0015 | 49.8683
|  |  | 2022-06-26 00:02 | 49.8683
|  |  | 44738.0015 | 49.8682
|  |  | 44738.0015 | 49.8682
|  |  | 44738.0015 | 49.8682
|  |  | 44738.0015 | 49.8682
|  |  | 44738.0015 | 49.8682
|  |  | 44738.0015 | 49.8683
|  |  | 44738.0015 | 49.8683
|  |  | 44738.0015 | 49.8684
|  |  | 44738.0015 | 49.8684
|  |  | 44738.0015 | 49.8685
|  |  | 44738.0015 | 49.8685
|  |  | 44738.0015 | 49.8684
|  |  | 44738.0015 | 49.8683
|  |  | 44738.0015 | 49.8682
|  |  | 44738.0015 | 49.8682
|  |  | 44738.0015 | 49.8682
|  |  | 44738.0015 | 49.8682
|  |  | 44738.0015 | 49.8683
|  |  | 44738.0015 | 49.8683
|  |  | 44738.0015 | 49.8683
|  |  | 44738.0015 | 49.8683
|  |  | 44738.0015 | 49.8684
|  |  | 44738.0015 | 49.8684
|  |  | 44738.0015 | 49.8683
|  |  | 44738.0015 | 49.8684
|  |  | 44738.0015 | 49.8684
|  |  | 44738.0015 | 49.8684
|  |  | 44738.0015 | 49.8683
|  |  | 44738.0015 | 49.8683
|  |  | 44738.0015 | 49.8682
|  |  | 44738.0015 | 49.8682
|  |  | 44738.0015 | 49.8681
|  |  | 44738.0015 | 49.8681
|  |  | 44738.0015 | 49.8681
|  |  | 44738.0015 | 49.8681
|  |  | 44738.0015 | 49.8681
|  |  | 44738.0015 | 49.8682
|  |  | 44738.0015 | 49.8682
|  |  | 44738.0015 | 49.8682
|  |  | 44738.0015 | 49.8682
|  |  | 44738.0015 | 49.8681
|  |  | 44738.0015 | 49.8681
|  |  | 44738.0015 | 49.868
|  |  | 44738.0015 | 49.868
|  |  | 44738.0015 | 49.8679
|  |  | 44738.0015 | 49.8678
|  |  | 44738.0015 | 49.8677
|  |  | 44738.0015 | 49.8676
|  |  | 44738.0015 | 49.8676
|  |  | 2022-06-26 00:02 | 49.8675
|  |  | 44738.0015 | 49.8674
|  |  | 44738.0015 | 49.8674
|  |  | 44738.0015 | 49.8674
|  |  | 44738.0015 | 49.8674
|  |  | 44738.0015 | 49.8674
|  |  | 44738.0015 | 49.8675
|  |  | 44738.0015 | 49.8675
|  |  | 44738.0015 | 49.8676
|  |  | 44738.0015 | 49.8676
|  |  | 44738.0015 | 49.8677
|  |  | 44738.0015 | 49.8677
|  |  | 44738.0015 | 49.8676
|  |  | 44738.0015 | 49.8675
|  |  | 44738.0015 | 49.8674
|  |  | 44738.0015 | 49.8673
|  |  | 44738.0015 | 49.8672
|  |  | 44738.0015 | 49.8671
|  |  | 44738.0015 | 49.8671
|  |  | 44738.0015 | 49.867
|  |  | 44738.0015 | 49.867
|  |  | 44738.0015 | 49.867
|  |  | 44738.0015 | 49.867
|  |  | 44738.0015 | 49.867
|  |  | 44738.0015 | 49.8669
|  |  | 44738.0015 | 49.8668
|  |  | 44738.0015 | 49.8668
|  |  | 44738.0015 | 49.8668
|  |  | 44738.0015 | 49.8667
|  |  | 44738.0015 | 49.8667
|  |  | 44738.0015 | 49.8667
|  |  | 44738.0015 | 49.8666
|  |  | 44738.0015 | 49.8666
|  |  | 44738.0015 | 49.8666
|  |  | 44738.0015 | 49.8665
|  |  | 44738.0015 | 49.8665
|  |  | 44738.0015 | 49.8665
|  |  | 44738.0015 | 49.8665
|  |  | 44738.0015 | 49.8665
|  |  | 44738.0015 | 49.8664
|  |  | 44738.0015 | 49.8663
|  |  | 44738.0015 | 49.8663
|  |  | 44738.0015 | 49.8663
|  |  | 44738.0015 | 49.8663
|  |  | 44738.0015 | 49.8664
|  |  | 44738.0015 | 49.8664
|  |  | 44738.0015 | 49.8664
|  |  | 44738.0015 | 49.8664
|  |  | 44738.0015 | 49.8664
|  |  | 44738.0015 | 49.8664
|  |  | 2022-06-26 00:02 | 49.8663
|  |  | 44738.0015 | 49.8663
|  |  | 44738.0015 | 49.8662
|  |  | 44738.0015 | 49.8662
|  |  | 44738.0015 | 49.8661
|  |  | 44738.0015 | 49.866
|  |  | 44738.0015 | 49.866
|  |  | 44738.0015 | 49.866
|  |  | 44738.0015 | 49.866
|  |  | 44738.0015 | 49.866
|  |  | 44738.0015 | 49.8661
|  |  | 44738.0015 | 49.8661
|  |  | 44738.0015 | 49.8661
|  |  | 44738.0015 | 49.8661
|  |  | 44738.0015 | 49.8661
|  |  | 44738.0015 | 49.866
|  |  | 44738.0015 | 49.866
|  |  | 44738.0015 | 49.8659
|  |  | 44738.0015 | 49.8658
|  |  | 44738.0015 | 49.8658
|  |  | 44738.0015 | 49.8658
|  |  | 44738.0015 | 49.8658
|  |  | 44738.0015 | 49.8658
|  |  | 44738.0015 | 49.8658
|  |  | 44738.0015 | 49.8659
|  |  | 44738.0015 | 49.8659
|  |  | 44738.0015 | 49.8659
|  |  | 44738.0015 | 49.8659
|  |  | 44738.0015 | 49.8658
|  |  | 44738.0015 | 49.8658
|  |  | 44738.0015 | 49.8657
|  |  | 44738.0015 | 49.8657
|  |  | 44738.0015 | 49.8657
|  |  | 44738.0015 | 49.8657
|  |  | 44738.0015 | 49.8658
|  |  | 44738.0015 | 49.8658
|  |  | 44738.0015 | 49.8659
|  |  | 44738.0015 | 49.866
|  |  | 44738.0015 | 49.866
|  |  | 44738.0015 | 49.8659
|  |  | 44738.0015 | 49.8659
|  |  | 44738.0015 | 49.8658
|  |  | 44738.0015 | 49.8657
|  |  | 44738.0015 | 49.8656
|  |  | 44738.0015 | 49.8656
|  |  | 44738.0015 | 49.8656
|  |  | 44738.0015 | 49.8656
|  |  | 44738.0015 | 49.8656
|  |  | 44738.0015 | 49.8657
|  |  | 44738.0015 | 49.8658
|  |  | 2022-06-26 00:02 | 49.8659
|  |  | 44738.0015 | 49.866
|  |  | 44738.0015 | 49.8662
|  |  | 44738.0015 | 49.8663
|  |  | 44738.0015 | 49.8662
|  |  | 44738.0015 | 49.8662
|  |  | 44738.0015 | 49.8662
|  |  | 44738.0015 | 49.8661
|  |  | 44738.0015 | 49.8661
|  |  | 44738.0015 | 49.866
|  |  | 44738.0015 | 49.866
|  |  | 44738.0015 | 49.8659
|  |  | 44738.0015 | 49.8658
|  |  | 44738.0015 | 49.8657
|  |  | 44738.0015 | 49.8657
|  |  | 44738.0015 | 49.8657
|  |  | 44738.0015 | 49.8657
|  |  | 44738.0015 | 49.8658
|  |  | 44738.0015 | 49.8659
|  |  | 44738.0015 | 49.866
|  |  | 44738.0015 | 49.8661
|  |  | 44738.0015 | 49.8662
|  |  | 44738.0015 | 49.8662
|  |  | 44738.0015 | 49.8663
|  |  | 44738.0015 | 49.8663
|  |  | 44738.0015 | 49.8663
|  |  | 44738.0015 | 49.8662
|  |  | 44738.0015 | 49.8661
|  |  | 44738.0015 | 49.866
|  |  | 44738.0015 | 49.866
|  |  | 44738.0015 | 49.8661
|  |  | 44738.0015 | 49.8661
|  |  | 44738.0015 | 49.8662
|  |  | 44738.0015 | 49.8662
|  |  | 44738.0015 | 49.8662
|  |  | 44738.0015 | 49.8663
|  |  | 44738.0015 | 49.8663
|  |  | 44738.0015 | 49.8663
|  |  | 44738.0015 | 49.8663
|  |  | 44738.0015 | 49.8663
|  |  | 44738.0015 | 49.8663
|  |  | 44738.0015 | 49.8663
|  |  | 44738.0015 | 49.8663
|  |  | 44738.0015 | 49.8663
|  |  | 44738.0015 | 49.8663
|  |  | 44738.0015 | 49.8663
|  |  | 44738.0015 | 49.8664
|  |  | 44738.0015 | 49.8665
|  |  | 44738.0015 | 49.8666
|  |  | 44738.0015 | 49.8666
|  |  | 2022-06-26 00:02 | 49.8667
|  |  | 44738.0015 | 49.8667
|  |  | 44738.0015 | 49.8667
|  |  | 44738.0015 | 49.8668
|  |  | 44738.0015 | 49.8667
|  |  | 44738.0015 | 49.8667
|  |  | 44738.0015 | 49.8667
|  |  | 44738.0015 | 49.8667
|  |  | 44738.0015 | 49.8667
|  |  | 44738.0015 | 49.8668
|  |  | 44738.0015 | 49.8668
|  |  | 44738.0015 | 49.8669
|  |  | 44738.0015 | 49.8669
|  |  | 44738.0015 | 49.867
|  |  | 44738.0015 | 49.867
|  |  | 44738.0015 | 49.867
|  |  | 44738.0015 | 49.867
|  |  | 44738.0015 | 49.867
|  |  | 44738.0015 | 49.867
|  |  | 44738.0015 | 49.867
|  |  | 44738.0015 | 49.8671
|  |  | 44738.0015 | 49.8671
|  |  | 44738.0015 | 49.8671
|  |  | 44738.0015 | 49.8671
|  |  | 44738.0015 | 49.8672
|  |  | 44738.0015 | 49.8672
|  |  | 44738.0015 | 49.8672
|  |  | 44738.0015 | 49.8672
|  |  | 44738.0015 | 49.8672
|  |  | 44738.0015 | 49.8673
|  |  | 44738.0015 | 49.8673
|  |  | 44738.0015 | 49.8673
|  |  | 44738.0015 | 49.8674
|  |  | 44738.0015 | 49.8674
|  |  | 44738.0015 | 49.8674
|  |  | 44738.0015 | 49.8673
|  |  | 44738.0015 | 49.8673
|  |  | 44738.0015 | 49.8673
|  |  | 44738.0015 | 49.8673
|  |  | 44738.0015 | 49.8673
|  |  | 44738.0015 | 49.8673
|  |  | 44738.0015 | 49.8673
|  |  | 44738.0015 | 49.8672
|  |  | 44738.0015 | 49.8673
|  |  | 44738.0015 | 49.8673
|  |  | 44738.0015 | 49.8673
|  |  | 44738.0015 | 49.8674
|  |  | 44738.0015 | 49.8674
|  |  | 44738.0015 | 49.8675
|  |  | 44738.0015 | 49.8675
|  |  | 2022-06-26 00:02 | 49.8676
|  |  | 44738.0015 | 49.8677
|  |  | 44738.0015 | 49.8677
|  |  | 44738.0015 | 49.8678
|  |  | 44738.0015 | 49.8678
|  |  | 44738.0015 | 49.8679
|  |  | 44738.0015 | 49.8679
|  |  | 44738.0015 | 49.8678
|  |  | 44738.0015 | 49.8678
|  |  | 44738.0015 | 49.8679
|  |  | 44738.0015 | 49.8679
|  |  | 44738.0015 | 49.868
|  |  | 44738.0015 | 49.8681
|  |  | 44738.0015 | 49.8681
|  |  | 44738.0015 | 49.8682
|  |  | 44738.0015 | 49.8682
|  |  | 44738.0015 | 49.8683
|  |  | 44738.0015 | 49.8684
|  |  | 44738.0015 | 49.8685
|  |  | 44738.0015 | 49.8685
|  |  | 44738.0015 | 49.8686
|  |  | 44738.0015 | 49.8686
|  |  | 44738.0015 | 49.8687
|  |  | 44738.0015 | 49.8687
|  |  | 44738.0015 | 49.8687
|  |  | 44738.0015 | 49.8688
|  |  | 44738.0015 | 49.8688
|  |  | 44738.0015 | 49.8689
|  |  | 44738.0015 | 49.8689
|  |  | 44738.0015 | 49.8689
|  |  | 44738.0015 | 49.8689
|  |  | 44738.0015 | 49.8689
|  |  | 44738.0015 | 49.8688
|  |  | 44738.0015 | 49.8688
|  |  | 44738.0015 | 49.8688
|  |  | 44738.0015 | 49.8687
|  |  | 44738.0015 | 49.8687
|  |  | 44738.0015 | 49.8686
|  |  | 44738.0015 | 49.8686
|  |  | 44738.0015 | 49.8686
|  |  | 44738.0015 | 49.8686
|  |  | 44738.0015 | 49.8687
|  |  | 44738.0015 | 49.8688
|  |  | 44738.0015 | 49.8688
|  |  | 44738.0015 | 49.8687
|  |  | 44738.0015 | 49.8688
|  |  | 44738.0015 | 49.8688
|  |  | 44738.0015 | 49.8688
|  |  | 44738.0015 | 49.8687
|  |  | 44738.0015 | 49.8686
|  |  | 2022-06-26 00:02 | 49.8686
|  |  | 44738.0015 | 49.8685
|  |  | 44738.0015 | 49.8684
|  |  | 44738.0015 | 49.8684
|  |  | 44738.0015 | 49.8683
|  |  | 44738.0015 | 49.8683
|  |  | 44738.0015 | 49.8683
|  |  | 44738.0015 | 49.8683
|  |  | 44738.0015 | 49.8684
|  |  | 44738.0015 | 49.8684
|  |  | 44738.0015 | 49.8685
|  |  | 44738.0015 | 49.8685
|  |  | 44738.0015 | 49.8686
|  |  | 44738.0015 | 49.8686
|  |  | 44738.0015 | 49.8685
|  |  | 44738.0015 | 49.8686
|  |  | 44738.0015 | 49.8685
|  |  | 44738.0015 | 49.8685
|  |  | 44738.0015 | 49.8685
|  |  | 44738.0015 | 49.8685
|  |  | 44738.0015 | 49.8684
|  |  | 44738.0015 | 49.8684
|  |  | 44738.0015 | 49.8684
|  |  | 44738.0015 | 49.8684
|  |  | 44738.0015 | 49.8684
|  |  | 44738.0015 | 49.8685
|  |  | 44738.0015 | 49.8685
|  |  | 44738.0015 | 49.8686
|  |  | 44738.0015 | 49.8688
|  |  | 44738.0015 | 49.8689
|  |  | 44738.0015 | 49.869
|  |  | 44738.0015 | 49.8691
|  |  | 44738.0015 | 49.8692
|  |  | 44738.0015 | 49.8693
|  |  | 44738.0015 | 49.8692
|  |  | 44738.0015 | 49.8692
|  |  | 44738.0015 | 49.8692
|  |  | 44738.0015 | 49.8691
|  |  | 44738.0015 | 49.8691
|  |  | 44738.0015 | 49.8691
|  |  | 44738.0015 | 49.8691
|  |  | 44738.0015 | 49.8691
|  |  | 44738.0015 | 49.8692
|  |  | 44738.0015 | 49.8692
|  |  | 44738.0015 | 49.8694
|  |  | 44738.0015 | 49.8695
|  |  | 44738.0016 | 49.8696
|  |  | 44738.0016 | 49.8697
|  |  | 44738.0016 | 49.8697
|  |  | 44738.0016 | 49.8698
|  |  | 2022-06-26 00:02 | 49.8699
|  |  | 44738.0016 | 49.8699
|  |  | 44738.0016 | 49.8699
|  |  | 44738.0016 | 49.87
|  |  | 44738.0016 | 49.87
|  |  | 44738.0016 | 49.87
|  |  | 44738.0016 | 49.8699
|  |  | 44738.0016 | 49.8699
|  |  | 44738.0016 | 49.8698
|  |  | 44738.0016 | 49.8698
|  |  | 44738.0016 | 49.8698
|  |  | 44738.0016 | 49.8698
|  |  | 44738.0016 | 49.8699
|  |  | 44738.0016 | 49.87
|  |  | 44738.0016 | 49.8701
|  |  | 44738.0016 | 49.8703
|  |  | 44738.0016 | 49.8705
|  |  | 44738.0016 | 49.8707
|  |  | 44738.0016 | 49.8708
|  |  | 44738.0016 | 49.8709
|  |  | 44738.0016 | 49.871
|  |  | 44738.0016 | 49.8709
|  |  | 44738.0016 | 49.871
|  |  | 44738.0016 | 49.8709
|  |  | 44738.0016 | 49.8709
|  |  | 44738.0016 | 49.8709
|  |  | 44738.0016 | 49.8709
|  |  | 44738.0016 | 49.8709
|  |  | 44738.0016 | 49.8709
|  |  | 44738.0016 | 49.8709
|  |  | 44738.0016 | 49.871
|  |  | 44738.0016 | 49.871
|  |  | 44738.0016 | 49.8711
|  |  | 44738.0016 | 49.8712
|  |  | 44738.0016 | 49.8713
|  |  | 44738.0016 | 49.8714
|  |  | 44738.0016 | 49.8715
|  |  | 44738.0016 | 49.8716
|  |  | 44738.0016 | 49.8718
|  |  | 44738.0016 | 49.8719
|  |  | 44738.0016 | 49.8719
|  |  | 44738.0016 | 49.8719
|  |  | 44738.0016 | 49.8719
|  |  | 44738.0016 | 49.8719
|  |  | 44738.0016 | 49.872
|  |  | 44738.0016 | 49.872
|  |  | 44738.0016 | 49.872
|  |  | 44738.0016 | 49.872
|  |  | 44738.0016 | 49.8721
|  |  | 44738.0016 | 49.8723
|  |  | 2022-06-26 00:02 | 49.8725
|  |  | 44738.0016 | 49.8726
|  |  | 44738.0016 | 49.8728
|  |  | 44738.0016 | 49.8729
|  |  | 44738.0016 | 49.8729
|  |  | 44738.0016 | 49.873
|  |  | 44738.0016 | 49.873
|  |  | 44738.0016 | 49.873
|  |  | 44738.0016 | 49.8731
|  |  | 44738.0016 | 49.8731
|  |  | 44738.0016 | 49.8731
|  |  | 44738.0016 | 49.8731
|  |  | 44738.0016 | 49.8731
|  |  | 44738.0016 | 49.8732
|  |  | 44738.0016 | 49.8732
|  |  | 44738.0016 | 49.8733
|  |  | 44738.0016 | 49.8734
|  |  | 44738.0016 | 49.8735
|  |  | 44738.0016 | 49.8736
|  |  | 44738.0016 | 49.8737
|  |  | 44738.0016 | 49.8739
|  |  | 44738.0016 | 49.8739
|  |  | 44738.0016 | 49.874
|  |  | 44738.0016 | 49.874
|  |  | 44738.0016 | 49.8741
|  |  | 44738.0016 | 49.8741
|  |  | 44738.0016 | 49.8742
|  |  | 44738.0016 | 49.8742
|  |  | 44738.0016 | 49.8742
|  |  | 44738.0016 | 49.8742
|  |  | 44738.0016 | 49.8742
|  |  | 44738.0016 | 49.8743
|  |  | 44738.0016 | 49.8744
|  |  | 44738.0016 | 49.8744
|  |  | 44738.0016 | 49.8745
|  |  | 44738.0016 | 49.8745
|  |  | 44738.0016 | 49.8746
|  |  | 44738.0016 | 49.8746
|  |  | 44738.0016 | 49.8748
|  |  | 44738.0016 | 49.8749
|  |  | 44738.0016 | 49.875
|  |  | 44738.0016 | 49.875
|  |  | 44738.0016 | 49.8751
|  |  | 44738.0016 | 49.8751
|  |  | 44738.0016 | 49.8751
|  |  | 44738.0016 | 49.8751
|  |  | 44738.0016 | 49.8751
|  |  | 44738.0016 | 49.875
|  |  | 44738.0016 | 49.875
|  |  | 44738.0016 | 49.875
|  |  | 2022-06-26 00:02 | 49.875
|  |  | 44738.0016 | 49.875
|  |  | 44738.0016 | 49.8751
|  |  | 44738.0016 | 49.8752
|  |  | 44738.0016 | 49.8753
|  |  | 44738.0016 | 49.8754
|  |  | 44738.0016 | 49.8756
|  |  | 44738.0016 | 49.8757
|  |  | 44738.0016 | 49.8758
|  |  | 44738.0016 | 49.876
|  |  | 44738.0016 | 49.876
|  |  | 44738.0016 | 49.876
|  |  | 44738.0016 | 49.876
|  |  | 44738.0016 | 49.876
|  |  | 44738.0016 | 49.876
|  |  | 44738.0016 | 49.8759
|  |  | 44738.0016 | 49.8759
|  |  | 44738.0016 | 49.8759
|  |  | 44738.0016 | 49.8758
|  |  | 44738.0016 | 49.8759
|  |  | 44738.0016 | 49.876
|  |  | 44738.0016 | 49.8761
|  |  | 44738.0016 | 49.8761
|  |  | 44738.0016 | 49.8762
|  |  | 44738.0016 | 49.8762
|  |  | 44738.0016 | 49.8762
|  |  | 44738.0016 | 49.8762
|  |  | 44738.0016 | 49.8763
|  |  | 44738.0016 | 49.8764
|  |  | 44738.0016 | 49.8764
|  |  | 44738.0016 | 49.8765
|  |  | 44738.0016 | 49.8766
|  |  | 44738.0016 | 49.8766
|  |  | 44738.0016 | 49.8767
|  |  | 44738.0016 | 49.8767
|  |  | 44738.0016 | 49.8768
|  |  | 44738.0016 | 49.8769
|  |  | 44738.0016 | 49.877
|  |  | 44738.0016 | 49.8771
|  |  | 44738.0016 | 49.8773
|  |  | 44738.0016 | 49.8774
|  |  | 44738.0016 | 49.8775
|  |  | 44738.0016 | 49.8777
|  |  | 44738.0016 | 49.8778
|  |  | 44738.0016 | 49.8779
|  |  | 44738.0016 | 49.8779
|  |  | 44738.0016 | 49.878
|  |  | 44738.0016 | 49.878
|  |  | 44738.0016 | 49.878
|  |  | 44738.0016 | 49.8781
|  |  | 2022-06-26 00:02 | 49.8781
|  |  | 44738.0016 | 49.8782
|  |  | 44738.0016 | 49.8782
|  |  | 44738.0016 | 49.8783
|  |  | 44738.0016 | 49.8783
|  |  | 44738.0016 | 49.8784
|  |  | 44738.0016 | 49.8784
|  |  | 44738.0016 | 49.8784
|  |  | 44738.0016 | 49.8784
|  |  | 44738.0016 | 49.8785
|  |  | 44738.0016 | 49.8785
|  |  | 44738.0016 | 49.8786
|  |  | 44738.0016 | 49.8787
|  |  | 44738.0016 | 49.8789
|  |  | 44738.0016 | 49.879
|  |  | 44738.0016 | 49.8791
|  |  | 44738.0016 | 49.8791
|  |  | 44738.0016 | 49.8792
|  |  | 44738.0016 | 49.8793
|  |  | 44738.0016 | 49.8793
|  |  | 44738.0016 | 49.8793
|  |  | 44738.0016 | 49.8793
|  |  | 44738.0016 | 49.8794
|  |  | 44738.0016 | 49.8794
|  |  | 44738.0016 | 49.8794
|  |  | 44738.0016 | 49.8794
|  |  | 44738.0016 | 49.8794
|  |  | 44738.0016 | 49.8795
|  |  | 44738.0016 | 49.8796
|  |  | 44738.0016 | 49.8796
|  |  | 44738.0016 | 49.8797
|  |  | 44738.0016 | 49.8796
|  |  | 44738.0016 | 49.8796
|  |  | 44738.0016 | 49.8795
|  |  | 44738.0016 | 49.8795
|  |  | 44738.0016 | 49.8795
|  |  | 44738.0016 | 49.8795
|  |  | 44738.0016 | 49.8795
|  |  | 44738.0016 | 49.8795
|  |  | 44738.0016 | 49.8796
|  |  | 44738.0016 | 49.8797
|  |  | 44738.0016 | 49.8798
|  |  | 44738.0016 | 49.8799
|  |  | 44738.0016 | 49.88
|  |  | 44738.0016 | 49.8801
|  |  | 44738.0016 | 49.8801
|  |  | 44738.0016 | 49.8801
|  |  | 44738.0016 | 49.8801
|  |  | 44738.0016 | 49.8801
|  |  | 44738.0016 | 49.8801
|  |  | 2022-06-26 00:02 | 49.8801
|  |  | 44738.0016 | 49.88
|  |  | 44738.0016 | 49.88
|  |  | 44738.0016 | 49.88
|  |  | 44738.0016 | 49.88
|  |  | 44738.0016 | 49.88
|  |  | 44738.0016 | 49.8801
|  |  | 44738.0016 | 49.8802
|  |  | 44738.0016 | 49.8803
|  |  | 44738.0016 | 49.8804
|  |  | 44738.0016 | 49.8805
|  |  | 44738.0016 | 49.8806
|  |  | 44738.0016 | 49.8807
|  |  | 44738.0016 | 49.8808
|  |  | 44738.0016 | 49.8808
|  |  | 44738.0016 | 49.8807
|  |  | 44738.0016 | 49.8807
|  |  | 44738.0016 | 49.8806
|  |  | 44738.0016 | 49.8806
|  |  | 44738.0016 | 49.8806
|  |  | 44738.0016 | 49.8806
|  |  | 44738.0016 | 49.8807
|  |  | 44738.0016 | 49.8807
|  |  | 44738.0016 | 49.8807
|  |  | 44738.0016 | 49.8807
|  |  | 44738.0016 | 49.8807
|  |  | 44738.0016 | 49.8808
|  |  | 44738.0016 | 49.8808
|  |  | 44738.0016 | 49.8809
|  |  | 44738.0016 | 49.8809
|  |  | 44738.0016 | 49.881
|  |  | 44738.0016 | 49.8811
|  |  | 44738.0016 | 49.8811
|  |  | 44738.0016 | 49.8812
|  |  | 44738.0016 | 49.8813
|  |  | 44738.0016 | 49.8813
|  |  | 44738.0016 | 49.8813
|  |  | 44738.0016 | 49.8814
|  |  | 44738.0016 | 49.8814
|  |  | 44738.0016 | 49.8815
|  |  | 44738.0016 | 49.8815
|  |  | 44738.0016 | 49.8816
|  |  | 44738.0016 | 49.8817
|  |  | 44738.0016 | 49.8817
|  |  | 44738.0016 | 49.8817
|  |  | 44738.0016 | 49.8817
|  |  | 44738.0016 | 49.8818
|  |  | 44738.0016 | 49.8819
|  |  | 44738.0016 | 49.882
|  |  | 44738.0016 | 49.8821
|  |  | 2022-06-26 00:02 | 49.8822
|  |  | 44738.0016 | 49.8822
|  |  | 44738.0016 | 49.8823
|  |  | 44738.0016 | 49.8823
|  |  | 44738.0016 | 49.8823
|  |  | 44738.0016 | 49.8823
|  |  | 44738.0016 | 49.8823
|  |  | 44738.0016 | 49.8824
|  |  | 44738.0016 | 49.8823
|  |  | 44738.0016 | 49.8824
|  |  | 44738.0016 | 49.8824
|  |  | 44738.0016 | 49.8824
|  |  | 44738.0016 | 49.8825
|  |  | 44738.0016 | 49.8825
|  |  | 44738.0016 | 49.8825
|  |  | 44738.0016 | 49.8826
|  |  | 44738.0016 | 49.8826
|  |  | 44738.0016 | 49.8826
|  |  | 44738.0016 | 49.8825
|  |  | 44738.0016 | 49.8825
|  |  | 44738.0016 | 49.8825
|  |  | 44738.0016 | 49.8825
|  |  | 44738.0016 | 49.8825
|  |  | 44738.0016 | 49.8825
|  |  | 44738.0016 | 49.8826
|  |  | 44738.0016 | 49.8826
|  |  | 44738.0016 | 49.8828
|  |  | 44738.0016 | 49.8829
|  |  | 44738.0016 | 49.8831
|  |  | 44738.0016 | 49.8832
|  |  | 44738.0016 | 49.8833
|  |  | 44738.0016 | 49.8834
|  |  | 44738.0016 | 49.8834
|  |  | 44738.0016 | 49.8834
|  |  | 44738.0016 | 49.8834
|  |  | 44738.0016 | 49.8833
|  |  | 44738.0016 | 49.8833
|  |  | 44738.0016 | 49.8833
|  |  | 44738.0016 | 49.8834
|  |  | 44738.0016 | 49.8834
|  |  | 44738.0016 | 49.8834
|  |  | 44738.0016 | 49.8835
|  |  | 44738.0016 | 49.8836
|  |  | 44738.0016 | 49.8837
|  |  | 44738.0016 | 49.8839
|  |  | 44738.0016 | 49.884
|  |  | 44738.0016 | 49.8842
|  |  | 44738.0016 | 49.8843
|  |  | 44738.0016 | 49.8844
|  |  | 44738.0016 | 49.8844
|  |  | 2022-06-26 00:02 | 49.8845

## 20220630-1
In GMT |  |  | High resolution Incident data
Date | Time | Freq | time | freq
2022-06-30 | 22:47 | 50.137 | 2022-06-30 23:47 | 50.1415
2022-06-30 | 22:47 | 50.136 | 44742.9911 | 50.1415
2022-06-30 | 22:47 | 50.138 | 44742.9911 | 50.1415
2022-06-30 | 22:47 | 50.14 | 44742.9911 | 50.1414
2022-06-30 | 22:47 | 50.14 | 44742.9911 | 50.1414
2022-06-30 | 22:47 | 50.142 | 44742.9911 | 50.1413
2022-06-30 | 22:47 | 50.142 | 44742.9911 | 50.1412
2022-06-30 | 22:47 | 50.144 | 44742.9911 | 50.1412
2022-06-30 | 22:47 | 50.143 | 44742.9911 | 50.1411
2022-06-30 | 22:47 | 50.144 | 44742.9911 | 50.1411
2022-06-30 | 22:47 | 50.142 | 44742.9911 | 50.1411
2022-06-30 | 22:47 | 50.144 | 44742.9911 | 50.1411
2022-06-30 | 22:47 | 50.143 | 44742.9911 | 50.1411
2022-06-30 | 22:47 | 50.144 | 44742.9911 | 50.1411
2022-06-30 | 22:47 | 50.143 | 44742.9911 | 50.141
2022-06-30 | 22:47 | 50.14 | 44742.9911 | 50.141
2022-06-30 | 22:47 | 50.139 | 44742.9911 | 50.1409
2022-06-30 | 22:47 | 50.137 | 44742.9911 | 50.1409
2022-06-30 | 22:47 | 50.134 | 44742.9912 | 50.1408
2022-06-30 | 22:47 | 50.132 | 44742.9912 | 50.1407
2022-06-30 | 22:47 | 50.129 | 44742.9912 | 50.1407
2022-06-30 | 22:47 | 50.129 | 44742.9912 | 50.1406
2022-06-30 | 22:47 | 50.129 | 44742.9912 | 50.1406
2022-06-30 | 22:47 | 50.129 | 44742.9912 | 50.1406
2022-06-30 | 22:47 | 50.125 | 44742.9912 | 50.1405
2022-06-30 | 22:47 | 50.124 | 44742.9912 | 50.1405
2022-06-30 | 22:47 | 50.123 | 44742.9912 | 50.1405
2022-06-30 | 22:47 | 50.122 | 44742.9912 | 50.1405
2022-06-30 | 22:47 | 50.121 | 44742.9912 | 50.1405
2022-06-30 | 22:47 | 50.121 | 44742.9912 | 50.1404
2022-06-30 | 22:48 | 50.12 | 44742.9912 | 50.1404
2022-06-30 | 22:48 | 50.121 | 44742.9912 | 50.1403
2022-06-30 | 22:48 | 50.12 | 44742.9912 | 50.1403
2022-06-30 | 22:48 | 50.117 | 44742.9912 | 50.1403
2022-06-30 | 22:48 | 50.115 | 44742.9912 | 50.1402
2022-06-30 | 22:48 | 50.116 | 44742.9912 | 50.1401
2022-06-30 | 22:48 | 50.115 | 44742.9912 | 50.1401
2022-06-30 | 22:48 | 50.114 | 44742.9912 | 50.14
2022-06-30 | 22:48 | 50.114 | 44742.9912 | 50.14
2022-06-30 | 22:48 | 50.111 | 44742.9912 | 50.1399
2022-06-30 | 22:48 | 50.111 | 44742.9912 | 50.1399
2022-06-30 | 22:48 | 50.115 | 44742.9912 | 50.1398
2022-06-30 | 22:48 | 50.116 | 44742.9912 | 50.1398
2022-06-30 | 22:48 | 50.119 | 44742.9912 | 50.1397
2022-06-30 | 22:48 | 50.121 | 44742.9912 | 50.1396
2022-06-30 | 22:48 | 50.121 | 44742.9912 | 50.1396
2022-06-30 | 22:48 | 50.12 | 44742.9912 | 50.1396
2022-06-30 | 22:48 | 50.116 | 44742.9912 | 50.1395
2022-06-30 | 22:48 | 50.11 | 44742.9912 | 50.1395
2022-06-30 | 22:48 | 50.095 | 44742.9912 | 50.1394
2022-06-30 | 22:48 | 50.078 | 2022-06-30 23:47 | 50.1394
2022-06-30 | 22:48 | 50.058 | 44742.9912 | 50.1393
2022-06-30 | 22:48 | 50.039 | 44742.9912 | 50.1392
2022-06-30 | 22:48 | 50.018 | 44742.9912 | 50.1392
2022-06-30 | 22:48 | 49.966 | 44742.9912 | 50.1391
2022-06-30 | 22:48 | 49.918 | 44742.9912 | 50.1391
2022-06-30 | 22:48 | 49.885 | 44742.9912 | 50.139
2022-06-30 | 22:48 | 49.859 | 44742.9912 | 50.1389
2022-06-30 | 22:48 | 49.838 | 44742.9912 | 50.1388
2022-06-30 | 22:48 | 49.824 | 44742.9912 | 50.1387
2022-06-30 | 22:48 | 49.812 | 44742.9912 | 50.1386
2022-06-30 | 22:48 | 49.802 | 44742.9912 | 50.1386
2022-06-30 | 22:48 | 49.796 | 44742.9912 | 50.1385
2022-06-30 | 22:48 | 49.795 | 44742.9912 | 50.1384
2022-06-30 | 22:48 | 49.792 | 44742.9912 | 50.1383
2022-06-30 | 22:48 | 49.793 | 44742.9912 | 50.1383
2022-06-30 | 22:48 | 49.793 | 44742.9912 | 50.1383
2022-06-30 | 22:48 | 49.795 | 44742.9912 | 50.1383
2022-06-30 | 22:48 | 49.796 | 44742.9912 | 50.1382
2022-06-30 | 22:48 | 49.797 | 44742.9912 | 50.1382
2022-06-30 | 22:48 | 49.797 | 44742.9912 | 50.1381
2022-06-30 | 22:48 | 49.795 | 44742.9912 | 50.138
2022-06-30 | 22:48 | 49.796 | 44742.9912 | 50.138
2022-06-30 | 22:48 | 49.797 | 44742.9912 | 50.138
2022-06-30 | 22:48 | 49.8 | 44742.9912 | 50.1379
2022-06-30 | 22:48 | 49.803 | 44742.9912 | 50.1379
2022-06-30 | 22:48 | 49.805 | 44742.9912 | 50.1379
2022-06-30 | 22:48 | 49.804 | 44742.9912 | 50.1378
2022-06-30 | 22:48 | 49.803 | 44742.9912 | 50.1378
2022-06-30 | 22:48 | 49.803 | 44742.9912 | 50.1377
2022-06-30 | 22:48 | 49.805 | 44742.9912 | 50.1377
2022-06-30 | 22:48 | 49.806 | 44742.9912 | 50.1377
2022-06-30 | 22:48 | 49.807 | 44742.9912 | 50.1376
2022-06-30 | 22:48 | 49.808 | 44742.9912 | 50.1376
2022-06-30 | 22:48 | 49.811 | 44742.9912 | 50.1376
2022-06-30 | 22:48 | 49.811 | 44742.9912 | 50.1377
2022-06-30 | 22:48 | 49.808 | 44742.9912 | 50.1376
2022-06-30 | 22:48 | 49.807 | 44742.9912 | 50.1376
2022-06-30 | 22:48 | 49.806 | 44742.9912 | 50.1376
2022-06-30 | 22:48 | 49.807 | 44742.9912 | 50.1375
2022-06-30 | 22:48 | 49.805 | 44742.9912 | 50.1375
2022-06-30 | 22:49 | 49.805 | 44742.9912 | 50.1374
2022-06-30 | 22:49 | 49.805 | 44742.9912 | 50.1373
2022-06-30 | 22:49 | 49.805 | 44742.9912 | 50.1372
2022-06-30 | 22:49 | 49.802 | 44742.9912 | 50.1372
2022-06-30 | 22:49 | 49.803 | 44742.9912 | 50.1371
2022-06-30 | 22:49 | 49.798 | 44742.9912 | 50.137
2022-06-30 | 22:49 | 49.796 | 44742.9912 | 50.137
2022-06-30 | 22:49 | 49.795 | 44742.9912 | 50.137
2022-06-30 | 22:49 | 49.793 | 44742.9912 | 50.1369
2022-06-30 | 22:49 | 49.793 | 2022-06-30 23:47 | 50.1369
2022-06-30 | 22:49 | 49.789 | 44742.9912 | 50.1368
2022-06-30 | 22:49 | 49.789 | 44742.9912 | 50.1368
2022-06-30 | 22:49 | 49.789 | 44742.9912 | 50.1367
2022-06-30 | 22:49 | 49.79 | 44742.9912 | 50.1367
2022-06-30 | 22:49 | 49.791 | 44742.9912 | 50.1367
2022-06-30 | 22:49 | 49.788 | 44742.9912 | 50.1367
2022-06-30 | 22:49 | 49.79 | 44742.9912 | 50.1366
2022-06-30 | 22:49 | 49.79 | 44742.9912 | 50.1366
2022-06-30 | 22:49 | 49.791 | 44742.9912 | 50.1366
2022-06-30 | 22:49 | 49.792 | 44742.9912 | 50.1365
2022-06-30 | 22:49 | 49.792 | 44742.9912 | 50.1365
2022-06-30 | 22:49 | 49.79 | 44742.9912 | 50.1364
2022-06-30 | 22:49 | 49.791 | 44742.9912 | 50.1364
2022-06-30 | 22:49 | 49.79 | 44742.9912 | 50.1363
2022-06-30 | 22:49 | 49.792 | 44742.9912 | 50.1363
2022-06-30 | 22:49 | 49.79 | 44742.9912 | 50.1363
2022-06-30 | 22:49 | 49.789 | 44742.9912 | 50.1363
2022-06-30 | 22:49 | 49.79 | 44742.9912 | 50.1362
2022-06-30 | 22:49 | 49.789 | 44742.9912 | 50.1362
2022-06-30 | 22:49 | 49.788 | 44742.9912 | 50.1361
2022-06-30 | 22:49 | 49.785 | 44742.9912 | 50.136
2022-06-30 | 22:49 | 49.784 | 44742.9912 | 50.1359
2022-06-30 | 22:49 | 49.783 | 44742.9912 | 50.1358
2022-06-30 | 22:49 | 49.78 | 44742.9912 | 50.1358
2022-06-30 | 22:49 | 49.779 | 44742.9912 | 50.1357
2022-06-30 | 22:49 | 49.78 | 44742.9912 | 50.1357
2022-06-30 | 22:49 | 49.778 | 44742.9912 | 50.1356
2022-06-30 | 22:49 | 49.779 | 44742.9912 | 50.1356
2022-06-30 | 22:49 | 49.778 | 44742.9912 | 50.1356
2022-06-30 | 22:49 | 49.776 | 44742.9912 | 50.1355
2022-06-30 | 22:49 | 49.774 | 44742.9912 | 50.1355
2022-06-30 | 22:49 | 49.77 | 44742.9912 | 50.1355
2022-06-30 | 22:49 | 49.769 | 44742.9912 | 50.1354
2022-06-30 | 22:49 | 49.767 | 44742.9912 | 50.1353
2022-06-30 | 22:49 | 49.765 | 44742.9912 | 50.1352
2022-06-30 | 22:49 | 49.765 | 44742.9912 | 50.1352
2022-06-30 | 22:49 | 49.763 | 44742.9912 | 50.1351
2022-06-30 | 22:49 | 49.763 | 44742.9912 | 50.1351
2022-06-30 | 22:49 | 49.759 | 44742.9912 | 50.135
2022-06-30 | 22:49 | 49.758 | 44742.9912 | 50.135
2022-06-30 | 22:49 | 49.757 | 44742.9912 | 50.1349
2022-06-30 | 22:49 | 49.754 | 44742.9912 | 50.1349
2022-06-30 | 22:49 | 49.754 | 44742.9912 | 50.1348
2022-06-30 | 22:49 | 49.753 | 44742.9912 | 50.1348
2022-06-30 | 22:49 | 49.75 | 44742.9912 | 50.1347
2022-06-30 | 22:49 | 49.749 | 44742.9912 | 50.1347
2022-06-30 | 22:49 | 49.746 | 44742.9912 | 50.1346
2022-06-30 | 22:49 | 49.748 | 44742.9912 | 50.1345
2022-06-30 | 22:49 | 49.746 | 44742.9912 | 50.1344
2022-06-30 | 22:50 | 49.747 | 2022-06-30 23:47 | 50.1344
2022-06-30 | 22:50 | 49.748 | 44742.9912 | 50.1343
2022-06-30 | 22:50 | 49.749 | 44742.9912 | 50.1343
2022-06-30 | 22:50 | 49.753 | 44742.9912 | 50.1342
2022-06-30 | 22:50 | 49.756 | 44742.9912 | 50.1342
2022-06-30 | 22:50 | 49.756 | 44742.9912 | 50.1342
2022-06-30 | 22:50 | 49.759 | 44742.9912 | 50.1341
2022-06-30 | 22:50 | 49.758 | 44742.9912 | 50.134
2022-06-30 | 22:50 | 49.76 | 44742.9912 | 50.134
2022-06-30 | 22:50 | 49.76 | 44742.9912 | 50.134
2022-06-30 | 22:50 | 49.76 | 44742.9912 | 50.134
2022-06-30 | 22:50 | 49.76 | 44742.9912 | 50.1339
2022-06-30 | 22:50 | 49.76 | 44742.9912 | 50.1339
2022-06-30 | 22:50 | 49.761 | 44742.9912 | 50.1338
2022-06-30 | 22:50 | 49.762 | 44742.9912 | 50.1338
2022-06-30 | 22:50 | 49.763 | 44742.9912 | 50.1337
2022-06-30 | 22:50 | 49.765 | 44742.9912 | 50.1336
2022-06-30 | 22:50 | 49.766 | 44742.9912 | 50.1336
2022-06-30 | 22:50 | 49.768 | 44742.9912 | 50.1335
2022-06-30 | 22:50 | 49.772 | 44742.9912 | 50.1334
2022-06-30 | 22:50 | 49.775 | 44742.9912 | 50.1334
2022-06-30 | 22:50 | 49.782 | 44742.9912 | 50.1333
2022-06-30 | 22:50 | 49.792 | 44742.9912 | 50.1333
2022-06-30 | 22:50 | 49.798 | 44742.9912 | 50.1333
2022-06-30 | 22:50 | 49.803 | 44742.9912 | 50.1333
2022-06-30 | 22:50 | 49.804 | 44742.9912 | 50.1332
2022-06-30 | 22:50 | 49.807 | 44742.9912 | 50.1332
2022-06-30 | 22:50 | 49.811 | 44742.9912 | 50.1332
2022-06-30 | 22:50 | 49.813 | 44742.9912 | 50.1332
2022-06-30 | 22:50 | 49.816 | 44742.9912 | 50.1332
2022-06-30 | 22:50 | 49.819 | 44742.9912 | 50.1331
2022-06-30 | 22:50 | 49.821 | 44742.9912 | 50.1331
2022-06-30 | 22:50 | 49.824 | 44742.9912 | 50.133
2022-06-30 | 22:50 | 49.825 | 44742.9912 | 50.1329
2022-06-30 | 22:50 | 49.823 | 44742.9912 | 50.1328
2022-06-30 | 22:50 | 49.823 | 44742.9912 | 50.1327
2022-06-30 | 22:50 | 49.821 | 44742.9912 | 50.1326
2022-06-30 | 22:50 | 49.817 | 44742.9912 | 50.1325
2022-06-30 | 22:50 | 49.818 | 44742.9912 | 50.1324
2022-06-30 | 22:50 | 49.816 | 44742.9912 | 50.1323
2022-06-30 | 22:50 | 49.816 | 44742.9912 | 50.1323
2022-06-30 | 22:50 | 49.814 | 44742.9912 | 50.1323
2022-06-30 | 22:50 | 49.815 | 44742.9912 | 50.1323
2022-06-30 | 22:50 | 49.816 | 44742.9912 | 50.1323
2022-06-30 | 22:50 | 49.816 | 44742.9912 | 50.1322
2022-06-30 | 22:50 | 49.819 | 44742.9912 | 50.1322
2022-06-30 | 22:50 | 49.818 | 44742.9912 | 50.1322
2022-06-30 | 22:50 | 49.82 | 44742.9912 | 50.1322
2022-06-30 | 22:50 | 49.819 | 44742.9912 | 50.1321
2022-06-30 | 22:50 | 49.82 | 44742.9912 | 50.132
2022-06-30 | 22:50 | 49.82 | 2022-06-30 23:47 | 50.1319
2022-06-30 | 22:50 | 49.822 | 44742.9912 | 50.1318
2022-06-30 | 22:50 | 49.822 | 44742.9912 | 50.1318
2022-06-30 | 22:50 | 49.822 | 44742.9912 | 50.1316
2022-06-30 | 22:50 | 49.82 | 44742.9912 | 50.1316
2022-06-30 | 22:50 | 49.82 | 44742.9912 | 50.1315
2022-06-30 | 22:50 | 49.82 | 44742.9912 | 50.1314
2022-06-30 | 22:50 | 49.818 | 44742.9912 | 50.1313
2022-06-30 | 22:50 | 49.814 | 44742.9912 | 50.1312
2022-06-30 | 22:50 | 49.812 | 44742.9912 | 50.1312
2022-06-30 | 22:50 | 49.81 | 44742.9912 | 50.1311
2022-06-30 | 22:51 | 49.809 | 44742.9912 | 50.1311
2022-06-30 | 22:51 | 49.808 | 44742.9912 | 50.131
2022-06-30 | 22:51 | 49.812 | 44742.9912 | 50.1309
2022-06-30 | 22:51 | 49.814 | 44742.9912 | 50.131
2022-06-30 | 22:51 | 49.816 | 44742.9912 | 50.1309
2022-06-30 | 22:51 | 49.817 | 44742.9912 | 50.1309
2022-06-30 | 22:51 | 49.82 | 44742.9912 | 50.1309
2022-06-30 | 22:51 | 49.823 | 44742.9912 | 50.1308
2022-06-30 | 22:51 | 49.826 | 44742.9912 | 50.1307
2022-06-30 | 22:51 | 49.829 | 44742.9912 | 50.1307
2022-06-30 | 22:51 | 49.831 | 44742.9912 | 50.1307
2022-06-30 | 22:51 | 49.837 | 44742.9912 | 50.1307
2022-06-30 | 22:51 | 49.842 | 44742.9912 | 50.1306
2022-06-30 | 22:51 | 49.846 | 44742.9912 | 50.1306
2022-06-30 | 22:51 | 49.849 | 44742.9912 | 50.1306
2022-06-30 | 22:51 | 49.85 | 44742.9912 | 50.1306
2022-06-30 | 22:51 | 49.851 | 44742.9912 | 50.1306
2022-06-30 | 22:51 | 49.856 | 44742.9912 | 50.1306
2022-06-30 | 22:51 | 49.861 | 44742.9912 | 50.1306
2022-06-30 | 22:51 | 49.866 | 44742.9912 | 50.1306
2022-06-30 | 22:51 | 49.87 | 44742.9912 | 50.1306
2022-06-30 | 22:51 | 49.875 | 44742.9912 | 50.1306
2022-06-30 | 22:51 | 49.876 | 44742.9912 | 50.1306
2022-06-30 | 22:51 | 49.876 | 44742.9912 | 50.1306
2022-06-30 | 22:51 | 49.878 | 44742.9912 | 50.1305
2022-06-30 | 22:51 | 49.879 | 44742.9912 | 50.1305
2022-06-30 | 22:51 | 49.88 | 44742.9912 | 50.1305
2022-06-30 | 22:51 | 49.884 | 44742.9912 | 50.1304
2022-06-30 | 22:51 | 49.886 | 44742.9912 | 50.1304
2022-06-30 | 22:51 | 49.887 | 44742.9912 | 50.1303
2022-06-30 | 22:51 | 49.888 | 44742.9912 | 50.1303
2022-06-30 | 22:51 | 49.887 | 44742.9912 | 50.1302
2022-06-30 | 22:51 | 49.885 | 44742.9912 | 50.1302
2022-06-30 | 22:51 | 49.884 | 44742.9912 | 50.1302
2022-06-30 | 22:51 | 49.885 | 44742.9912 | 50.1302
2022-06-30 | 22:51 | 49.888 | 44742.9912 | 50.1302
2022-06-30 | 22:51 | 49.893 | 44742.9912 | 50.1301
2022-06-30 | 22:51 | 49.896 | 44742.9912 | 50.1301
2022-06-30 | 22:51 | 49.903 | 44742.9912 | 50.1301
2022-06-30 | 22:51 | 49.896 | 2022-06-30 23:47 | 50.1301
2022-06-30 | 22:51 | 49.897 | 44742.9912 | 50.1301
2022-06-30 | 22:51 | 49.898 | 44742.9912 | 50.13
2022-06-30 | 22:51 | 49.9 | 44742.9912 | 50.13
2022-06-30 | 22:51 | 49.9 | 44742.9912 | 50.1299
2022-06-30 | 22:51 | 49.902 | 44742.9912 | 50.1299
2022-06-30 | 22:51 | 49.901 | 44742.9912 | 50.1298
2022-06-30 | 22:51 | 49.899 | 44742.9912 | 50.1298
2022-06-30 | 22:51 | 49.898 | 44742.9912 | 50.1298
2022-06-30 | 22:51 | 49.897 | 44742.9912 | 50.1298
2022-06-30 | 22:51 | 49.898 | 44742.9912 | 50.1298
2022-06-30 | 22:51 | 49.895 | 44742.9912 | 50.1297
2022-06-30 | 22:51 | 49.895 | 44742.9912 | 50.1298
2022-06-30 | 22:51 | 49.892 | 44742.9912 | 50.1298
2022-06-30 | 22:51 | 49.89 | 44742.9912 | 50.1298
2022-06-30 | 22:51 | 49.889 | 44742.9912 | 50.1299
2022-06-30 | 22:51 | 49.886 | 44742.9912 | 50.1299
2022-06-30 | 22:51 | 49.886 | 44742.9912 | 50.13
2022-06-30 | 22:51 | 49.884 | 44742.9912 | 50.13
2022-06-30 | 22:51 | 49.884 | 44742.9912 | 50.1301
2022-06-30 | 22:52 | 49.883 | 44742.9912 | 50.1301
2022-06-30 | 22:52 | 49.885 | 44742.9912 | 50.1301
2022-06-30 | 22:52 | 49.886 | 44742.9912 | 50.13
2022-06-30 | 22:52 | 49.886 | 44742.9912 | 50.13
2022-06-30 | 22:52 | 49.889 | 44742.9912 | 50.13
2022-06-30 | 22:52 | 49.889 | 44742.9912 | 50.1299
2022-06-30 | 22:52 | 49.892 | 44742.9912 | 50.1299
2022-06-30 | 22:52 | 49.892 | 44742.9912 | 50.1298
2022-06-30 | 22:52 | 49.895 | 44742.9912 | 50.1298
2022-06-30 | 22:52 | 49.897 | 44742.9912 | 50.1298
2022-06-30 | 22:52 | 49.9 | 44742.9912 | 50.1298
2022-06-30 | 22:52 | 49.903 | 44742.9912 | 50.1297
2022-06-30 | 22:52 | 49.905 | 44742.9912 | 50.1298
2022-06-30 | 22:52 | 49.907 | 44742.9912 | 50.1298
2022-06-30 | 22:52 | 49.91 | 44742.9912 | 50.1298
2022-06-30 | 22:52 | 49.912 | 44742.9912 | 50.1298
2022-06-30 | 22:52 | 49.914 | 44742.9912 | 50.1298
2022-06-30 | 22:52 | 49.917 | 44742.9912 | 50.1299
2022-06-30 | 22:52 | 49.92 | 44742.9912 | 50.1299
2022-06-30 | 22:52 | 49.918 | 44742.9912 | 50.1299
2022-06-30 | 22:52 | 49.92 | 44742.9912 | 50.1299
2022-06-30 | 22:52 | 49.92 | 44742.9912 | 50.1299
2022-06-30 | 22:52 | 49.916 | 44742.9912 | 50.1299
2022-06-30 | 22:52 | 49.915 | 44742.9912 | 50.1299
2022-06-30 | 22:52 | 49.915 | 44742.9912 | 50.1299
2022-06-30 | 22:52 | 49.913 | 44742.9912 | 50.1299
2022-06-30 | 22:52 | 49.913 | 44742.9912 | 50.1299
2022-06-30 | 22:52 | 49.915 | 44742.9912 | 50.1299
2022-06-30 | 22:52 | 49.917 | 44742.9912 | 50.1299
2022-06-30 | 22:52 | 49.918 | 44742.9912 | 50.1299
2022-06-30 | 22:52 | 49.919 | 2022-06-30 23:47 | 50.1299
2022-06-30 | 22:52 | 49.918 | 44742.9912 | 50.1299
2022-06-30 | 22:52 | 49.919 | 44742.9912 | 50.1299
2022-06-30 | 22:52 | 49.922 | 44742.9912 | 50.1299
2022-06-30 | 22:52 | 49.921 | 44742.9912 | 50.1299
2022-06-30 | 22:52 | 49.92 | 44742.9912 | 50.1299
2022-06-30 | 22:52 | 49.92 | 44742.9912 | 50.1299
2022-06-30 | 22:52 | 49.919 | 44742.9912 | 50.1299
2022-06-30 | 22:52 | 49.917 | 44742.9912 | 50.1299
2022-06-30 | 22:52 | 49.915 | 44742.9912 | 50.1299
2022-06-30 | 22:52 | 49.914 | 44742.9912 | 50.1299
2022-06-30 | 22:52 | 49.911 | 44742.9912 | 50.1299
2022-06-30 | 22:52 | 49.909 | 44742.9912 | 50.1299
2022-06-30 | 22:52 | 49.908 | 44742.9912 | 50.1299
2022-06-30 | 22:52 | 49.905 | 44742.9912 | 50.1299
2022-06-30 | 22:52 | 49.906 | 44742.9912 | 50.1299
2022-06-30 | 22:52 | 49.907 | 44742.9912 | 50.1298
2022-06-30 | 22:52 | 49.909 | 44742.9912 | 50.1298
2022-06-30 | 22:52 | 49.91 | 44742.9912 | 50.1298
2022-06-30 | 22:52 | 49.913 | 44742.9912 | 50.1298
2022-06-30 | 22:52 | 49.916 | 44742.9912 | 50.1298
2022-06-30 | 22:52 | 49.917 | 44742.9912 | 50.1297
2022-06-30 | 22:52 | 49.92 | 44742.9912 | 50.1297
2022-06-30 | 22:52 | 49.922 | 44742.9912 | 50.1297
2022-06-30 | 22:52 | 49.924 | 44742.9912 | 50.1297
2022-06-30 | 22:52 | 49.926 | 44742.9912 | 50.1297
2022-06-30 | 22:52 | 49.927 | 44742.9912 | 50.1297
2022-06-30 | 22:52 | 49.929 | 44742.9912 | 50.1298
2022-06-30 | 22:52 | 49.929 | 44742.9912 | 50.1298
2022-06-30 | 22:52 | 49.929 | 44742.9912 | 50.1298
2022-06-30 | 22:52 | 49.929 | 44742.9912 | 50.1298
2022-06-30 | 22:53 | 49.929 | 44742.9912 | 50.1299
2022-06-30 | 22:53 | 49.926 | 44742.9912 | 50.1299
2022-06-30 | 22:53 | 49.926 | 44742.9912 | 50.13
2022-06-30 | 22:53 | 49.926 | 44742.9912 | 50.13
2022-06-30 | 22:53 | 49.925 | 44742.9912 | 50.13
2022-06-30 | 22:53 | 49.925 | 44742.9912 | 50.13
2022-06-30 | 22:53 | 49.925 | 44742.9912 | 50.13
2022-06-30 | 22:53 | 49.923 | 44742.9912 | 50.13
2022-06-30 | 22:53 | 49.926 | 44742.9912 | 50.13
2022-06-30 | 22:53 | 49.928 | 44742.9912 | 50.13
2022-06-30 | 22:53 | 49.931 | 44742.9912 | 50.13
2022-06-30 | 22:53 | 49.93 | 44742.9912 | 50.13
2022-06-30 | 22:53 | 49.93 | 44742.9912 | 50.1299
2022-06-30 | 22:53 | 49.929 | 44742.9912 | 50.13
2022-06-30 | 22:53 | 49.93 | 44742.9912 | 50.1299
2022-06-30 | 22:53 | 49.931 | 44742.9912 | 50.1299
2022-06-30 | 22:53 | 49.932 | 44742.9912 | 50.13
2022-06-30 | 22:53 | 49.933 | 44742.9912 | 50.1299
2022-06-30 | 22:53 | 49.936 | 44742.9912 | 50.1299
2022-06-30 | 22:53 | 49.937 | 2022-06-30 23:47 | 50.1299
2022-06-30 | 22:53 | 49.939 | 44742.9912 | 50.1298
2022-06-30 | 22:53 | 49.941 | 44742.9912 | 50.1298
2022-06-30 | 22:53 | 49.945 | 44742.9912 | 50.1297
2022-06-30 | 22:53 | 49.945 | 44742.9912 | 50.1297
2022-06-30 | 22:53 | 49.944 | 44742.9912 | 50.1297
2022-06-30 | 22:53 | 49.944 | 44742.9912 | 50.1297
2022-06-30 | 22:53 | 49.945 | 44742.9912 | 50.1297
2022-06-30 | 22:53 | 49.946 | 44742.9912 | 50.1297
2022-06-30 | 22:53 | 49.947 | 44742.9912 | 50.1297
2022-06-30 | 22:53 | 49.949 | 44742.9912 | 50.1297
2022-06-30 | 22:53 | 49.948 | 44742.9912 | 50.1296
2022-06-30 | 22:53 | 49.946 | 44742.9912 | 50.1296
2022-06-30 | 22:53 | 49.946 | 44742.9912 | 50.1296
2022-06-30 | 22:53 | 49.945 | 44742.9912 | 50.1296
2022-06-30 | 22:53 | 49.942 | 44742.9912 | 50.1296
2022-06-30 | 22:53 | 49.944 | 44742.9912 | 50.1296
2022-06-30 | 22:53 | 49.945 | 44742.9912 | 50.1295
2022-06-30 | 22:53 | 49.945 | 44742.9912 | 50.1295
2022-06-30 | 22:53 | 49.946 | 44742.9912 | 50.1295
2022-06-30 | 22:53 | 49.944 | 44742.9912 | 50.1294
2022-06-30 | 22:53 | 49.945 | 44742.9912 | 50.1294
2022-06-30 | 22:53 | 49.945 | 44742.9912 | 50.1294
2022-06-30 | 22:53 | 49.945 | 44742.9912 | 50.1295
2022-06-30 | 22:53 | 49.947 | 44742.9912 | 50.1294
2022-06-30 | 22:53 | 49.946 | 44742.9912 | 50.1294
2022-06-30 | 22:53 | 49.946 | 44742.9912 | 50.1294
2022-06-30 | 22:53 | 49.945 | 44742.9912 | 50.1293
2022-06-30 | 22:53 | 49.941 | 44742.9912 | 50.1293
2022-06-30 | 22:53 | 49.939 | 44742.9912 | 50.1293
2022-06-30 | 22:53 | 49.939 | 44742.9912 | 50.1293
2022-06-30 | 22:53 | 49.939 | 44742.9912 | 50.1293
2022-06-30 | 22:53 | 49.938 | 44742.9912 | 50.1293
2022-06-30 | 22:53 | 49.941 | 44742.9912 | 50.1293
2022-06-30 | 22:53 | 49.943 | 44742.9912 | 50.1293
2022-06-30 | 22:53 | 49.945 | 44742.9912 | 50.1293
2022-06-30 | 22:53 | 49.946 | 44742.9912 | 50.1293
2022-06-30 | 22:53 | 49.947 | 44742.9912 | 50.1293
2022-06-30 | 22:53 | 49.95 | 44742.9912 | 50.1292
2022-06-30 | 22:53 | 49.95 | 44742.9912 | 50.1292
2022-06-30 | 22:53 | 49.949 | 44742.9912 | 50.1291
2022-06-30 | 22:54 | 49.95 | 44742.9912 | 50.129
2022-06-30 | 22:54 | 49.949 | 44742.9912 | 50.1289
2022-06-30 | 22:54 | 49.948 | 44742.9912 | 50.1289
2022-06-30 | 22:54 | 49.947 | 44742.9912 | 50.1288
2022-06-30 | 22:54 | 49.946 | 44742.9912 | 50.1287
2022-06-30 | 22:54 | 49.944 | 44742.9912 | 50.1286
2022-06-30 | 22:54 | 49.944 | 44742.9912 | 50.1286
2022-06-30 | 22:54 | 49.942 | 44742.9912 | 50.1286
2022-06-30 | 22:54 | 49.941 | 44742.9912 | 50.1285
2022-06-30 | 22:54 | 49.939 | 2022-06-30 23:47 | 50.1285
2022-06-30 | 22:54 | 49.937 | 44742.9912 | 50.1285
2022-06-30 | 22:54 | 49.936 | 44742.9912 | 50.1285
2022-06-30 | 22:54 | 49.936 | 44742.9912 | 50.1285
2022-06-30 | 22:54 | 49.934 | 44742.9912 | 50.1284
2022-06-30 | 22:54 | 49.934 | 44742.9912 | 50.1284
2022-06-30 | 22:54 | 49.935 | 44742.9912 | 50.1284
2022-06-30 | 22:54 | 49.938 | 44742.9912 | 50.1284
2022-06-30 | 22:54 | 49.94 | 44742.9912 | 50.1283
2022-06-30 | 22:54 | 49.946 | 44742.9912 | 50.1282
2022-06-30 | 22:54 | 49.946 | 44742.9912 | 50.1281
2022-06-30 | 22:54 | 49.947 | 44742.9912 | 50.1281
2022-06-30 | 22:54 | 49.948 | 44742.9912 | 50.128
2022-06-30 | 22:54 | 49.948 | 44742.9912 | 50.1279
2022-06-30 | 22:54 | 49.951 | 44742.9912 | 50.1278
2022-06-30 | 22:54 | 49.953 | 44742.9912 | 50.1277
2022-06-30 | 22:54 | 49.954 | 44742.9912 | 50.1277
2022-06-30 | 22:54 | 49.958 | 44742.9912 | 50.1277
2022-06-30 | 22:54 | 49.959 | 44742.9912 | 50.1277
2022-06-30 | 22:54 | 49.958 | 44742.9912 | 50.1277
2022-06-30 | 22:54 | 49.957 | 44742.9912 | 50.1277
2022-06-30 | 22:54 | 49.956 | 44742.9912 | 50.1277
2022-06-30 | 22:54 | 49.953 | 44742.9912 | 50.1277
2022-06-30 | 22:54 | 49.952 | 44742.9912 | 50.1277
2022-06-30 | 22:54 | 49.951 | 44742.9912 | 50.1276
2022-06-30 | 22:54 | 49.95 | 44742.9912 | 50.1276
2022-06-30 | 22:54 | 49.95 | 44742.9912 | 50.1275
2022-06-30 | 22:54 | 49.949 | 44742.9912 | 50.1274
2022-06-30 | 22:54 | 49.949 | 44742.9912 | 50.1273
2022-06-30 | 22:54 | 49.948 | 44742.9912 | 50.1272
2022-06-30 | 22:54 | 49.948 | 44742.9912 | 50.1272
2022-06-30 | 22:54 | 49.948 | 44742.9912 | 50.1271
2022-06-30 | 22:54 | 49.948 | 44742.9912 | 50.1271
2022-06-30 | 22:54 | 49.947 | 44742.9912 | 50.1271
2022-06-30 | 22:54 | 49.948 | 44742.9912 | 50.1271
2022-06-30 | 22:54 | 49.949 | 44742.9912 | 50.127
2022-06-30 | 22:54 | 49.953 | 44742.9912 | 50.127
2022-06-30 | 22:54 | 49.954 | 44742.9912 | 50.1269
2022-06-30 | 22:54 | 49.955 | 44742.9912 | 50.1268
2022-06-30 | 22:54 | 49.955 | 44742.9912 | 50.1268
2022-06-30 | 22:54 | 49.956 | 44742.9912 | 50.1268
2022-06-30 | 22:54 | 49.957 | 44742.9912 | 50.1268
2022-06-30 | 22:54 | 49.957 | 44742.9912 | 50.1267
2022-06-30 | 22:54 | 49.956 | 44742.9912 | 50.1266
2022-06-30 | 22:54 | 49.958 | 44742.9912 | 50.1266
2022-06-30 | 22:54 | 49.96 | 44742.9912 | 50.1265
2022-06-30 | 22:54 | 49.958 | 44742.9912 | 50.1265
2022-06-30 | 22:54 | 49.959 | 44742.9912 | 50.1265
2022-06-30 | 22:54 | 49.955 | 44742.9912 | 50.1264
2022-06-30 | 22:54 | 49.952 | 44742.9912 | 50.1264
2022-06-30 | 22:55 | 49.951 | 2022-06-30 23:47 | 50.1264
2022-06-30 | 22:55 | 49.949 | 44742.9913 | 50.1263
2022-06-30 | 22:55 | 49.946 | 44742.9913 | 50.1263
2022-06-30 | 22:55 | 49.944 | 44742.9913 | 50.1262
2022-06-30 | 22:55 | 49.941 | 44742.9913 | 50.1262
2022-06-30 | 22:55 | 49.94 | 44742.9913 | 50.1261
2022-06-30 | 22:55 | 49.94 | 44742.9913 | 50.1261
2022-06-30 | 22:55 | 49.938 | 44742.9913 | 50.126
2022-06-30 | 22:55 | 49.939 | 44742.9913 | 50.126
2022-06-30 | 22:55 | 49.941 | 44742.9913 | 50.126
2022-06-30 | 22:55 | 49.939 | 44742.9913 | 50.1259
2022-06-30 | 22:55 | 49.937 | 44742.9913 | 50.1259
2022-06-30 | 22:55 | 49.936 | 44742.9913 | 50.1259
2022-06-30 | 22:55 | 49.934 | 44742.9913 | 50.1258
2022-06-30 | 22:55 | 49.934 | 44742.9913 | 50.1258
2022-06-30 | 22:55 | 49.932 | 44742.9913 | 50.1258
2022-06-30 | 22:55 | 49.928 | 44742.9913 | 50.1258
2022-06-30 | 22:55 | 49.927 | 44742.9913 | 50.1258
2022-06-30 | 22:55 | 49.926 | 44742.9913 | 50.1257
2022-06-30 | 22:55 | 49.927 | 44742.9913 | 50.1257
2022-06-30 | 22:55 | 49.93 | 44742.9913 | 50.1257
2022-06-30 | 22:55 | 49.933 | 44742.9913 | 50.1257
2022-06-30 | 22:55 | 49.936 | 44742.9913 | 50.1256
2022-06-30 | 22:55 | 49.941 | 44742.9913 | 50.1257
2022-06-30 | 22:55 | 49.946 | 44742.9913 | 50.1256
2022-06-30 | 22:55 | 49.948 | 44742.9913 | 50.1256
2022-06-30 | 22:55 | 49.952 | 44742.9913 | 50.1255
2022-06-30 | 22:55 | 49.955 | 44742.9913 | 50.1254
2022-06-30 | 22:55 | 49.959 | 44742.9913 | 50.1253
2022-06-30 | 22:55 | 49.96 | 44742.9913 | 50.1253
2022-06-30 | 22:55 | 49.963 | 44742.9913 | 50.1253
2022-06-30 | 22:55 | 49.961 | 44742.9913 | 50.1253
2022-06-30 | 22:55 | 49.961 | 44742.9913 | 50.1253
2022-06-30 | 22:55 | 49.958 | 44742.9913 | 50.1253
2022-06-30 | 22:55 | 49.955 | 44742.9913 | 50.1253
2022-06-30 | 22:55 | 49.954 | 44742.9913 | 50.1253
2022-06-30 | 22:55 | 49.951 | 44742.9913 | 50.1253
2022-06-30 | 22:55 | 49.947 | 44742.9913 | 50.1253
2022-06-30 | 22:55 | 49.947 | 44742.9913 | 50.1253
2022-06-30 | 22:55 | 49.943 | 44742.9913 | 50.1252
2022-06-30 | 22:55 | 49.942 | 44742.9913 | 50.1252
2022-06-30 | 22:55 | 49.943 | 44742.9913 | 50.1252
2022-06-30 | 22:55 | 49.946 | 44742.9913 | 50.1252
2022-06-30 | 22:55 | 49.951 | 44742.9913 | 50.1251
2022-06-30 | 22:55 | 49.957 | 44742.9913 | 50.1251
2022-06-30 | 22:55 | 49.961 | 44742.9913 | 50.1251
2022-06-30 | 22:55 | 49.963 | 44742.9913 | 50.1251
2022-06-30 | 22:55 | 49.966 | 44742.9913 | 50.1251
2022-06-30 | 22:55 | 49.969 | 44742.9913 | 50.125
2022-06-30 | 22:55 | 49.967 | 44742.9913 | 50.125
2022-06-30 | 22:55 | 49.968 | 2022-06-30 23:47 | 50.125
2022-06-30 | 22:55 | 49.965 | 44742.9913 | 50.1249
2022-06-30 | 22:55 | 49.963 | 44742.9913 | 50.1249
2022-06-30 | 22:55 | 49.961 | 44742.9913 | 50.1249
2022-06-30 | 22:55 | 49.959 | 44742.9913 | 50.1248
2022-06-30 | 22:55 | 49.959 | 44742.9913 | 50.1248
2022-06-30 | 22:55 | 49.957 | 44742.9913 | 50.1248
2022-06-30 | 22:55 | 49.957 | 44742.9913 | 50.1247
2022-06-30 | 22:55 | 49.955 | 44742.9913 | 50.1247
2022-06-30 | 22:55 | 49.954 | 44742.9913 | 50.1247
2022-06-30 | 22:55 | 49.955 | 44742.9913 | 50.1246
2022-06-30 | 22:56 | 49.955 | 44742.9913 | 50.1246
2022-06-30 | 22:56 | 49.956 | 44742.9913 | 50.1245
2022-06-30 | 22:56 | 49.958 | 44742.9913 | 50.1245
2022-06-30 | 22:56 | 49.959 | 44742.9913 | 50.1245
2022-06-30 | 22:56 | 49.958 | 44742.9913 | 50.1245
2022-06-30 | 22:56 | 49.961 | 44742.9913 | 50.1244
2022-06-30 | 22:56 | 49.961 | 44742.9913 | 50.1244
2022-06-30 | 22:56 | 49.962 | 44742.9913 | 50.1244
2022-06-30 | 22:56 | 49.962 | 44742.9913 | 50.1244
2022-06-30 | 22:56 | 49.962 | 44742.9913 | 50.1244
2022-06-30 | 22:56 | 49.963 | 44742.9913 | 50.1244
2022-06-30 | 22:56 | 49.96 | 44742.9913 | 50.1245
2022-06-30 | 22:56 | 49.963 | 44742.9913 | 50.1245
2022-06-30 | 22:56 | 49.96 | 44742.9913 | 50.1245
2022-06-30 | 22:56 | 49.96 | 44742.9913 | 50.1246
2022-06-30 | 22:56 | 49.959 | 44742.9913 | 50.1246
2022-06-30 | 22:56 | 49.959 | 44742.9913 | 50.1246
2022-06-30 | 22:56 | 49.957 | 44742.9913 | 50.1246
2022-06-30 | 22:56 | 49.959 | 44742.9913 | 50.1246
2022-06-30 | 22:56 | 49.955 | 44742.9913 | 50.1246
2022-06-30 | 22:56 | 49.957 | 44742.9913 | 50.1246
2022-06-30 | 22:56 | 49.956 | 44742.9913 | 50.1246
2022-06-30 | 22:56 | 49.957 | 44742.9913 | 50.1245
2022-06-30 | 22:56 | 49.957 | 44742.9913 | 50.1244
2022-06-30 | 22:56 | 49.957 | 44742.9913 | 50.1243
2022-06-30 | 22:56 | 49.958 | 44742.9913 | 50.1243
2022-06-30 | 22:56 | 49.958 | 44742.9913 | 50.1242
2022-06-30 | 22:56 | 49.959 | 44742.9913 | 50.1241
2022-06-30 | 22:56 | 49.96 | 44742.9913 | 50.1241
2022-06-30 | 22:56 | 49.961 | 44742.9913 | 50.124
2022-06-30 | 22:56 | 49.96 | 44742.9913 | 50.124
2022-06-30 | 22:56 | 49.961 | 44742.9913 | 50.1239
2022-06-30 | 22:56 | 49.958 | 44742.9913 | 50.1239
2022-06-30 | 22:56 | 49.956 | 44742.9913 | 50.1239
2022-06-30 | 22:56 | 49.954 | 44742.9913 | 50.1238
2022-06-30 | 22:56 | 49.952 | 44742.9913 | 50.1238
2022-06-30 | 22:56 | 49.952 | 44742.9913 | 50.1237
2022-06-30 | 22:56 | 49.951 | 44742.9913 | 50.1237
2022-06-30 | 22:56 | 49.952 | 44742.9913 | 50.1237
2022-06-30 | 22:56 | 49.956 | 2022-06-30 23:47 | 50.1236
2022-06-30 | 22:56 | 49.959 | 44742.9913 | 50.1236
2022-06-30 | 22:56 | 49.963 | 44742.9913 | 50.1236
2022-06-30 | 22:56 | 49.964 | 44742.9913 | 50.1236
2022-06-30 | 22:56 | 49.967 | 44742.9913 | 50.1236
2022-06-30 | 22:56 | 49.969 | 44742.9913 | 50.1236
2022-06-30 | 22:56 | 49.971 | 44742.9913 | 50.1235
2022-06-30 | 22:56 | 49.972 | 44742.9913 | 50.1235
2022-06-30 | 22:56 | 49.974 | 44742.9913 | 50.1235
2022-06-30 | 22:56 | 49.972 | 44742.9913 | 50.1234
2022-06-30 | 22:56 | 49.972 | 44742.9913 | 50.1234
2022-06-30 | 22:56 | 49.971 | 44742.9913 | 50.1233
2022-06-30 | 22:56 | 49.972 | 44742.9913 | 50.1233
2022-06-30 | 22:56 | 49.974 | 44742.9913 | 50.1233
2022-06-30 | 22:56 | 49.975 | 44742.9913 | 50.1232
2022-06-30 | 22:56 | 49.975 | 44742.9913 | 50.1232
2022-06-30 | 22:56 | 49.973 | 44742.9913 | 50.1232
2022-06-30 | 22:56 | 49.973 | 44742.9913 | 50.1232
2022-06-30 | 22:56 | 49.973 | 44742.9913 | 50.1233
2022-06-30 | 22:56 | 49.972 | 44742.9913 | 50.1233
2022-06-30 | 22:57 | 49.971 | 44742.9913 | 50.1233
2022-06-30 | 22:57 | 49.97 | 44742.9913 | 50.1233
2022-06-30 | 22:57 | 49.969 | 44742.9913 | 50.1233
2022-06-30 | 22:57 | 49.97 | 44742.9913 | 50.1233
2022-06-30 | 22:57 | 49.97 | 44742.9913 | 50.1232
2022-06-30 | 22:57 | 49.969 | 44742.9913 | 50.1231
2022-06-30 | 22:57 | 49.971 | 44742.9913 | 50.1231
2022-06-30 | 22:57 | 49.973 | 44742.9913 | 50.123
2022-06-30 | 22:57 | 49.975 | 44742.9913 | 50.123
2022-06-30 | 22:57 | 49.977 | 44742.9913 | 50.1229
2022-06-30 | 22:57 | 49.978 | 44742.9913 | 50.1229
2022-06-30 | 22:57 | 49.982 | 44742.9913 | 50.1229
2022-06-30 | 22:57 | 49.986 | 44742.9913 | 50.123
2022-06-30 | 22:57 | 49.987 | 44742.9913 | 50.123
2022-06-30 | 22:57 | 49.989 | 44742.9913 | 50.123
2022-06-30 | 22:57 | 49.989 | 44742.9913 | 50.123
2022-06-30 | 22:57 | 49.99 | 44742.9913 | 50.123
2022-06-30 | 22:57 | 49.992 | 44742.9913 | 50.123
2022-06-30 | 22:57 | 49.99 | 44742.9913 | 50.123
2022-06-30 | 22:57 | 49.991 | 44742.9913 | 50.123
2022-06-30 | 22:57 | 49.992 | 44742.9913 | 50.123
2022-06-30 | 22:57 | 49.993 | 44742.9913 | 50.1229
2022-06-30 | 22:57 | 49.994 | 44742.9913 | 50.1229
2022-06-30 | 22:57 | 49.993 | 44742.9913 | 50.123
2022-06-30 | 22:57 | 49.992 | 44742.9913 | 50.123
2022-06-30 | 22:57 | 49.995 | 44742.9913 | 50.123
2022-06-30 | 22:57 | 49.997 | 44742.9913 | 50.123
2022-06-30 | 22:57 | 49.996 | 44742.9913 | 50.123
2022-06-30 | 22:57 | 49.994 | 44742.9913 | 50.123
2022-06-30 | 22:57 | 49.994 | 44742.9913 | 50.123
2022-06-30 | 22:57 | 49.994 | 2022-06-30 23:47 | 50.1231
2022-06-30 | 22:57 | 49.988 | 44742.9913 | 50.123
2022-06-30 | 22:57 | 49.984 | 44742.9913 | 50.1231
2022-06-30 | 22:57 | 49.983 | 44742.9913 | 50.123
2022-06-30 | 22:57 | 49.983 | 44742.9913 | 50.123
2022-06-30 | 22:57 | 49.979 | 44742.9913 | 50.123
2022-06-30 | 22:57 | 49.973 | 44742.9913 | 50.1229
2022-06-30 | 22:57 | 49.97 | 44742.9913 | 50.1229
2022-06-30 | 22:57 | 49.969 | 44742.9913 | 50.1229
2022-06-30 | 22:57 | 49.966 | 44742.9913 | 50.1228
2022-06-30 | 22:57 | 49.962 | 44742.9913 | 50.1228
2022-06-30 | 22:57 | 49.962 | 44742.9913 | 50.1228
2022-06-30 | 22:57 | 49.962 | 44742.9913 | 50.1227
2022-06-30 | 22:57 | 49.963 | 44742.9913 | 50.1227
2022-06-30 | 22:57 | 49.963 | 44742.9913 | 50.1227
2022-06-30 | 22:57 | 49.963 | 44742.9913 | 50.1226
2022-06-30 | 22:57 | 49.963 | 44742.9913 | 50.1226
2022-06-30 | 22:57 | 49.965 | 44742.9913 | 50.1225
2022-06-30 | 22:57 | 49.969 | 44742.9913 | 50.1225
2022-06-30 | 22:57 | 49.973 | 44742.9913 | 50.1225
2022-06-30 | 22:57 | 49.974 | 44742.9913 | 50.1225
2022-06-30 | 22:57 | 49.977 | 44742.9913 | 50.1225
2022-06-30 | 22:57 | 49.975 | 44742.9913 | 50.1225
2022-06-30 | 22:57 | 49.975 | 44742.9913 | 50.1225
2022-06-30 | 22:57 | 49.973 | 44742.9913 | 50.1225
2022-06-30 | 22:57 | 49.975 | 44742.9913 | 50.1225
2022-06-30 | 22:57 | 49.973 | 44742.9913 | 50.1225
2022-06-30 | 22:57 | 49.971 | 44742.9913 | 50.1225
2022-06-30 | 22:57 | 49.97 | 44742.9913 | 50.1225
2022-06-30 | 22:57 | 49.97 | 44742.9913 | 50.1224
2022-06-30 | 22:57 | 49.97 | 44742.9913 | 50.1224
2022-06-30 | 22:58 | 49.971 | 44742.9913 | 50.1224
2022-06-30 | 22:58 | 49.973 | 44742.9913 | 50.1223
2022-06-30 | 22:58 | 49.972 | 44742.9913 | 50.1223
2022-06-30 | 22:58 | 49.972 | 44742.9913 | 50.1223
2022-06-30 | 22:58 | 49.971 | 44742.9913 | 50.1223
2022-06-30 | 22:58 | 49.969 | 44742.9913 | 50.1222
2022-06-30 | 22:58 | 49.966 | 44742.9913 | 50.1222
2022-06-30 | 22:58 | 49.966 | 44742.9913 | 50.1223
2022-06-30 | 22:58 | 49.968 | 44742.9913 | 50.1223
2022-06-30 | 22:58 | 49.968 | 44742.9913 | 50.1223
2022-06-30 | 22:58 | 49.967 | 44742.9913 | 50.1224
2022-06-30 | 22:58 | 49.968 | 44742.9913 | 50.1224
2022-06-30 | 22:58 | 49.968 | 44742.9913 | 50.1224
2022-06-30 | 22:58 | 49.968 | 44742.9913 | 50.1223
2022-06-30 | 22:58 | 49.968 | 44742.9913 | 50.1223
2022-06-30 | 22:58 | 49.965 | 44742.9913 | 50.1222
2022-06-30 | 22:58 | 49.963 | 44742.9913 | 50.1222
2022-06-30 | 22:58 | 49.963 | 44742.9913 | 50.1222
2022-06-30 | 22:58 | 49.965 | 44742.9913 | 50.1222
2022-06-30 | 22:58 | 49.968 | 2022-06-30 23:47 | 50.1222
2022-06-30 | 22:58 | 49.969 | 44742.9913 | 50.1221
2022-06-30 | 22:58 | 49.972 | 44742.9913 | 50.1221
2022-06-30 | 22:58 | 49.974 | 44742.9913 | 50.1221
2022-06-30 | 22:58 | 49.977 | 44742.9913 | 50.1221
2022-06-30 | 22:58 | 49.978 | 44742.9913 | 50.1221
2022-06-30 | 22:58 | 49.976 | 44742.9913 | 50.1221
2022-06-30 | 22:58 | 49.978 | 44742.9913 | 50.1222
2022-06-30 | 22:58 | 49.979 | 44742.9913 | 50.1222
2022-06-30 | 22:58 | 49.98 | 44742.9913 | 50.1222
2022-06-30 | 22:58 | 49.981 | 44742.9913 | 50.1222
2022-06-30 | 22:58 | 49.978 | 44742.9913 | 50.1222
2022-06-30 | 22:58 | 49.976 | 44742.9913 | 50.1221
2022-06-30 | 22:58 | 49.975 | 44742.9913 | 50.1221
2022-06-30 | 22:58 | 49.974 | 44742.9913 | 50.122
2022-06-30 | 22:58 | 49.975 | 44742.9913 | 50.122
2022-06-30 | 22:58 | 49.976 | 44742.9913 | 50.1219
2022-06-30 | 22:58 | 49.977 | 44742.9913 | 50.1218
2022-06-30 | 22:58 | 49.977 | 44742.9913 | 50.1218
2022-06-30 | 22:58 | 49.976 | 44742.9913 | 50.1217
2022-06-30 | 22:58 | 49.977 | 44742.9913 | 50.1217
2022-06-30 | 22:58 | 49.977 | 44742.9913 | 50.1217
2022-06-30 | 22:58 | 49.976 | 44742.9913 | 50.1217
2022-06-30 | 22:58 | 49.976 | 44742.9913 | 50.1217
2022-06-30 | 22:58 | 49.977 | 44742.9913 | 50.1218
2022-06-30 | 22:58 | 49.976 | 44742.9913 | 50.1218
2022-06-30 | 22:58 | 49.977 | 44742.9913 | 50.1219
2022-06-30 | 22:58 | 49.976 | 44742.9913 | 50.1219
2022-06-30 | 22:58 | 49.976 | 44742.9913 | 50.1219
2022-06-30 | 22:58 | 49.975 | 44742.9913 | 50.1219
2022-06-30 | 22:58 | 49.975 | 44742.9913 | 50.1218
2022-06-30 | 22:58 | 49.975 | 44742.9913 | 50.1217
2022-06-30 | 22:58 | 49.976 | 44742.9913 | 50.1217
2022-06-30 | 22:58 | 49.975 | 44742.9913 | 50.1216
2022-06-30 | 22:58 | 49.975 | 44742.9913 | 50.1215
2022-06-30 | 22:58 | 49.977 | 44742.9913 | 50.1215
2022-06-30 | 22:58 | 49.979 | 44742.9913 | 50.1215
2022-06-30 | 22:58 | 49.98 | 44742.9913 | 50.1214
2022-06-30 | 22:58 | 49.981 | 44742.9913 | 50.1214
2022-06-30 | 22:58 | 49.981 | 44742.9913 | 50.1214
2022-06-30 | 22:59 | 49.98 | 44742.9913 | 50.1214
2022-06-30 | 22:59 | 49.98 | 44742.9913 | 50.1215
2022-06-30 | 22:59 | 49.98 | 44742.9913 | 50.1215
2022-06-30 | 22:59 | 49.979 | 44742.9913 | 50.1215
2022-06-30 | 22:59 | 49.978 | 44742.9913 | 50.1215
2022-06-30 | 22:59 | 49.977 | 44742.9913 | 50.1215
2022-06-30 | 22:59 | 49.975 | 44742.9913 | 50.1215
2022-06-30 | 22:59 | 49.972 | 44742.9913 | 50.1215
2022-06-30 | 22:59 | 49.971 | 44742.9913 | 50.1215
2022-06-30 | 22:59 | 49.971 | 44742.9913 | 50.1215
2022-06-30 | 22:59 | 49.971 | 2022-06-30 23:47 | 50.1214
2022-06-30 | 22:59 | 49.972 | 44742.9913 | 50.1214
2022-06-30 | 22:59 | 49.973 | 44742.9913 | 50.1214
2022-06-30 | 22:59 | 49.972 | 44742.9913 | 50.1214
2022-06-30 | 22:59 | 49.973 | 44742.9913 | 50.1213
2022-06-30 | 22:59 | 49.971 | 44742.9913 | 50.1213
2022-06-30 | 22:59 | 49.97 | 44742.9913 | 50.1213
2022-06-30 | 22:59 | 49.968 | 44742.9913 | 50.1212
2022-06-30 | 22:59 | 49.968 | 44742.9913 | 50.1212
2022-06-30 | 22:59 | 49.965 | 44742.9913 | 50.1212
2022-06-30 | 22:59 | 49.966 | 44742.9913 | 50.1212
2022-06-30 | 22:59 | 49.969 | 44742.9913 | 50.1211
2022-06-30 | 22:59 | 49.973 | 44742.9913 | 50.1211
2022-06-30 | 22:59 | 49.978 | 44742.9913 | 50.1211
2022-06-30 | 22:59 | 49.982 | 44742.9913 | 50.121
2022-06-30 | 22:59 | 49.984 | 44742.9913 | 50.121
2022-06-30 | 22:59 | 49.988 | 44742.9913 | 50.121
2022-06-30 | 22:59 | 49.988 | 44742.9913 | 50.121
2022-06-30 | 22:59 | 49.989 | 44742.9913 | 50.121
2022-06-30 | 22:59 | 49.988 | 44742.9913 | 50.121
2022-06-30 | 22:59 | 49.985 | 44742.9913 | 50.121
2022-06-30 | 22:59 | 49.981 | 44742.9913 | 50.121
2022-06-30 | 22:59 | 49.976 | 44742.9913 | 50.121
2022-06-30 | 22:59 | 49.975 | 44742.9913 | 50.121
2022-06-30 | 22:59 | 49.974 | 44742.9913 | 50.121
2022-06-30 | 22:59 | 49.975 | 44742.9913 | 50.121
2022-06-30 | 22:59 | 49.978 | 44742.9913 | 50.121
2022-06-30 | 22:59 | 49.976 | 44742.9913 | 50.121
2022-06-30 | 22:59 | 49.978 | 44742.9913 | 50.121
2022-06-30 | 22:59 | 49.978 | 44742.9913 | 50.121
2022-06-30 | 22:59 | 49.978 | 44742.9913 | 50.1211
2022-06-30 | 22:59 | 49.98 | 44742.9913 | 50.1211
2022-06-30 | 22:59 | 49.982 | 44742.9913 | 50.1212
2022-06-30 | 22:59 | 49.984 | 44742.9913 | 50.1212
2022-06-30 | 22:59 | 49.986 | 44742.9913 | 50.1212
2022-06-30 | 22:59 | 49.987 | 44742.9913 | 50.1212
2022-06-30 | 22:59 | 49.989 | 44742.9913 | 50.1213
2022-06-30 | 22:59 | 49.988 | 44742.9913 | 50.1212
2022-06-30 | 22:59 | 49.986 | 44742.9913 | 50.1212
2022-06-30 | 22:59 | 49.985 | 44742.9913 | 50.1212
2022-06-30 | 22:59 | 49.983 | 44742.9913 | 50.1212
2022-06-30 | 22:59 | 49.982 | 44742.9913 | 50.1212
2022-06-30 | 22:59 | 49.979 | 44742.9913 | 50.1211
2022-06-30 | 22:59 | 49.979 | 44742.9913 | 50.1211
2022-06-30 | 22:59 | 49.982 | 44742.9913 | 50.1211
2022-06-30 | 22:59 | 49.984 | 44742.9913 | 50.1211
2022-06-30 | 22:59 | 49.988 | 44742.9913 | 50.1212
2022-06-30 | 22:59 | 49.991 | 44742.9913 | 50.1212
2022-06-30 | 22:59 | 49.993 | 44742.9913 | 50.1212
2022-06-30 | 22:59 | 49.995 | 44742.9913 | 50.1213
2022-06-30 | 22:59 | 49.998 | 2022-06-30 23:47 | 50.1213
2022-06-30 | 23:00 | 49.999 | 44742.9913 | 50.1213
2022-06-30 | 23:00 | 50.001 | 44742.9913 | 50.1213
2022-06-30 | 23:00 | 50.004 | 44742.9913 | 50.1214
2022-06-30 | 23:00 | 50.005 | 44742.9913 | 50.1214
2022-06-30 | 23:00 | 50.007 | 44742.9913 | 50.1214
2022-06-30 | 23:00 | 50.008 | 44742.9913 | 50.1214
2022-06-30 | 23:00 | 50.009 | 44742.9913 | 50.1214
2022-06-30 | 23:00 | 50.011 | 44742.9913 | 50.1214
2022-06-30 | 23:00 | 50.011 | 44742.9913 | 50.1214
2022-06-30 | 23:00 | 50.012 | 44742.9913 | 50.1214
2022-06-30 | 23:00 | 50.011 | 44742.9913 | 50.1214
2022-06-30 | 23:00 | 50.012 | 44742.9913 | 50.1215
2022-06-30 | 23:00 | 50.011 | 44742.9913 | 50.1215
2022-06-30 | 23:00 | 50.013 | 44742.9913 | 50.1215
2022-06-30 | 23:00 | 50.015 | 44742.9913 | 50.1215
2022-06-30 | 23:00 | 50.016 | 44742.9913 | 50.1215
2022-06-30 | 23:00 | 50.019 | 44742.9913 | 50.1215
2022-06-30 | 23:00 | 50.022 | 44742.9913 | 50.1215
2022-06-30 | 23:00 | 50.024 | 44742.9913 | 50.1215
2022-06-30 | 23:00 | 50.026 | 44742.9913 | 50.1214
2022-06-30 | 23:00 | 50.03 | 44742.9913 | 50.1215
2022-06-30 | 23:00 | 50.033 | 44742.9913 | 50.1215
2022-06-30 | 23:00 | 50.036 | 44742.9913 | 50.1216
2022-06-30 | 23:00 | 50.04 | 44742.9913 | 50.1215
2022-06-30 | 23:00 | 50.04 | 44742.9913 | 50.1215
2022-06-30 | 23:00 | 50.044 | 44742.9913 | 50.1215
2022-06-30 | 23:00 | 50.045 | 44742.9913 | 50.1215
2022-06-30 | 23:00 | 50.046 | 44742.9913 | 50.1215
2022-06-30 | 23:00 | 50.046 | 44742.9913 | 50.1214
2022-06-30 | 23:00 | 50.045 | 44742.9913 | 50.1214
2022-06-30 | 23:00 | 50.037 | 44742.9913 | 50.1214
2022-06-30 | 23:00 | 50.03 | 44742.9913 | 50.1214
2022-06-30 | 23:00 | 50.025 | 44742.9913 | 50.1214
2022-06-30 | 23:00 | 50.023 | 44742.9913 | 50.1214
2022-06-30 | 23:00 | 50.021 | 44742.9913 | 50.1214
2022-06-30 | 23:00 | 50.023 | 44742.9913 | 50.1214
2022-06-30 | 23:00 | 50.024 | 44742.9913 | 50.1214
2022-06-30 | 23:00 | 50.027 | 44742.9913 | 50.1213
2022-06-30 | 23:00 | 50.031 | 44742.9913 | 50.1214
2022-06-30 | 23:00 | 50.035 | 44742.9913 | 50.1214
2022-06-30 | 23:00 | 50.041 | 44742.9913 | 50.1214
2022-06-30 | 23:00 | 50.044 | 44742.9913 | 50.1213
2022-06-30 | 23:00 | 50.046 | 44742.9913 | 50.1213
2022-06-30 | 23:00 | 50.051 | 44742.9913 | 50.1212
2022-06-30 | 23:00 | 50.055 | 44742.9913 | 50.1212
2022-06-30 | 23:00 | 50.057 | 44742.9913 | 50.1212
2022-06-30 | 23:00 | 50.059 | 44742.9913 | 50.1212
2022-06-30 | 23:00 | 50.066 | 44742.9913 | 50.1212
2022-06-30 | 23:00 | 50.069 | 44742.9913 | 50.1212
2022-06-30 | 23:00 | 50.071 | 2022-06-30 23:48 | 50.1212
2022-06-30 | 23:00 | 50.073 | 44742.9913 | 50.1212
2022-06-30 | 23:00 | 50.071 | 44742.9913 | 50.1213
2022-06-30 | 23:00 | 50.071 | 44742.9913 | 50.1213
2022-06-30 | 23:00 | 50.069 | 44742.9913 | 50.1213
2022-06-30 | 23:00 | 50.065 | 44742.9913 | 50.1213
2022-06-30 | 23:00 | 50.064 | 44742.9913 | 50.1213
2022-06-30 | 23:00 | 50.06 | 44742.9913 | 50.1213
2022-06-30 | 23:00 | 50.057 | 44742.9913 | 50.1214
2022-06-30 | 23:00 | 50.057 | 44742.9913 | 50.1214
2022-06-30 | 23:01 | 50.057 | 44742.9913 | 50.1214
2022-06-30 | 23:01 | 50.057 | 44742.9913 | 50.1215
2022-06-30 | 23:01 | 50.059 | 44742.9913 | 50.1215
2022-06-30 | 23:01 | 50.058 | 44742.9913 | 50.1215
2022-06-30 | 23:01 | 50.06 | 44742.9913 | 50.1215
2022-06-30 | 23:01 | 50.062 | 44742.9913 | 50.1215
2022-06-30 | 23:01 | 50.064 | 44742.9913 | 50.1214
2022-06-30 | 23:01 | 50.062 | 44742.9913 | 50.1214
2022-06-30 | 23:01 | 50.064 | 44742.9913 | 50.1214
2022-06-30 | 23:01 | 50.064 | 44742.9913 | 50.1214
2022-06-30 | 23:01 | 50.062 | 44742.9913 | 50.1214
2022-06-30 | 23:01 | 50.062 | 44742.9913 | 50.1213
2022-06-30 | 23:01 | 50.064 | 44742.9913 | 50.1213
2022-06-30 | 23:01 | 50.066 | 44742.9913 | 50.1213
2022-06-30 | 23:01 | 50.069 | 44742.9913 | 50.1212
2022-06-30 | 23:01 | 50.072 | 44742.9913 | 50.1212
2022-06-30 | 23:01 | 50.074 | 44742.9913 | 50.1212
2022-06-30 | 23:01 | 50.075 | 44742.9913 | 50.1213
2022-06-30 | 23:01 | 50.077 | 44742.9913 | 50.1213
2022-06-30 | 23:01 | 50.075 | 44742.9913 | 50.1214
2022-06-30 | 23:01 | 50.074 | 44742.9913 | 50.1214
2022-06-30 | 23:01 | 50.075 | 44742.9913 | 50.1213
2022-06-30 | 23:01 | 50.074 | 44742.9913 | 50.1213
2022-06-30 | 23:01 | 50.073 | 44742.9913 | 50.1211
2022-06-30 | 23:01 | 50.071 | 44742.9913 | 50.1211
2022-06-30 | 23:01 | 50.069 | 44742.9913 | 50.121
2022-06-30 | 23:01 | 50.068 | 44742.9913 | 50.121
2022-06-30 | 23:01 | 50.065 | 44742.9913 | 50.1209
2022-06-30 | 23:01 | 50.063 | 44742.9913 | 50.1209
2022-06-30 | 23:01 | 50.061 | 44742.9913 | 50.1209
2022-06-30 | 23:01 | 50.058 | 44742.9913 | 50.1208
|  |  | 44742.9913 | 50.1208
|  |  | 44742.9913 | 50.1208
|  |  | 44742.9913 | 50.1207
|  |  | 44742.9913 | 50.1206
|  |  | 44742.9913 | 50.1205
|  |  | 44742.9913 | 50.1204
|  |  | 44742.9913 | 50.1204
|  |  | 44742.9913 | 50.1203
|  |  | 44742.9913 | 50.1203
|  |  | 2022-06-30 23:48 | 50.1202
|  |  | 44742.9913 | 50.1202
|  |  | 44742.9913 | 50.1202
|  |  | 44742.9913 | 50.1202
|  |  | 44742.9913 | 50.1201
|  |  | 44742.9913 | 50.1201
|  |  | 44742.9913 | 50.12
|  |  | 44742.9913 | 50.12
|  |  | 44742.9913 | 50.1199
|  |  | 44742.9913 | 50.1199
|  |  | 44742.9913 | 50.1198
|  |  | 44742.9913 | 50.1198
|  |  | 44742.9913 | 50.1198
|  |  | 44742.9913 | 50.1198
|  |  | 44742.9913 | 50.1198
|  |  | 44742.9913 | 50.1198
|  |  | 44742.9913 | 50.1198
|  |  | 44742.9913 | 50.1198
|  |  | 44742.9913 | 50.1197
|  |  | 44742.9913 | 50.1197
|  |  | 44742.9913 | 50.1197
|  |  | 44742.9913 | 50.1196
|  |  | 44742.9913 | 50.1195
|  |  | 44742.9913 | 50.1194
|  |  | 44742.9913 | 50.1193
|  |  | 44742.9913 | 50.1193
|  |  | 44742.9913 | 50.1192
|  |  | 44742.9913 | 50.1192
|  |  | 44742.9913 | 50.1191
|  |  | 44742.9913 | 50.1191
|  |  | 44742.9913 | 50.1191
|  |  | 44742.9913 | 50.119
|  |  | 44742.9913 | 50.119
|  |  | 44742.9914 | 50.1189
|  |  | 44742.9914 | 50.1188
|  |  | 44742.9914 | 50.1188
|  |  | 44742.9914 | 50.1187
|  |  | 44742.9914 | 50.1186
|  |  | 44742.9914 | 50.1186
|  |  | 44742.9914 | 50.1185
|  |  | 44742.9914 | 50.1185
|  |  | 44742.9914 | 50.1185
|  |  | 44742.9914 | 50.1185
|  |  | 44742.9914 | 50.1185
|  |  | 44742.9914 | 50.1186
|  |  | 44742.9914 | 50.1186
|  |  | 44742.9914 | 50.1186
|  |  | 44742.9914 | 50.1186
|  |  | 44742.9914 | 50.1186
|  |  | 44742.9914 | 50.1186
|  |  | 2022-06-30 23:48 | 50.1186
|  |  | 44742.9914 | 50.1185
|  |  | 44742.9914 | 50.1185
|  |  | 44742.9914 | 50.1184
|  |  | 44742.9914 | 50.1184
|  |  | 44742.9914 | 50.1184
|  |  | 44742.9914 | 50.1183
|  |  | 44742.9914 | 50.1183
|  |  | 44742.9914 | 50.1183
|  |  | 44742.9914 | 50.1182
|  |  | 44742.9914 | 50.1182
|  |  | 44742.9914 | 50.1182
|  |  | 44742.9914 | 50.1181
|  |  | 44742.9914 | 50.1181
|  |  | 44742.9914 | 50.118
|  |  | 44742.9914 | 50.118
|  |  | 44742.9914 | 50.1179
|  |  | 44742.9914 | 50.1178
|  |  | 44742.9914 | 50.1177
|  |  | 44742.9914 | 50.1177
|  |  | 44742.9914 | 50.1176
|  |  | 44742.9914 | 50.1176
|  |  | 44742.9914 | 50.1175
|  |  | 44742.9914 | 50.1175
|  |  | 44742.9914 | 50.1174
|  |  | 44742.9914 | 50.1173
|  |  | 44742.9914 | 50.1173
|  |  | 44742.9914 | 50.1173
|  |  | 44742.9914 | 50.1173
|  |  | 44742.9914 | 50.1173
|  |  | 44742.9914 | 50.1172
|  |  | 44742.9914 | 50.1172
|  |  | 44742.9914 | 50.1172
|  |  | 44742.9914 | 50.1172
|  |  | 44742.9914 | 50.1172
|  |  | 44742.9914 | 50.1172
|  |  | 44742.9914 | 50.1171
|  |  | 44742.9914 | 50.1171
|  |  | 44742.9914 | 50.1171
|  |  | 44742.9914 | 50.1171
|  |  | 44742.9914 | 50.1171
|  |  | 44742.9914 | 50.1171
|  |  | 44742.9914 | 50.117
|  |  | 44742.9914 | 50.117
|  |  | 44742.9914 | 50.1169
|  |  | 44742.9914 | 50.1169
|  |  | 44742.9914 | 50.1168
|  |  | 44742.9914 | 50.1167
|  |  | 44742.9914 | 50.1167
|  |  | 44742.9914 | 50.1167
|  |  | 2022-06-30 23:48 | 50.1167
|  |  | 44742.9914 | 50.1167
|  |  | 44742.9914 | 50.1167
|  |  | 44742.9914 | 50.1167
|  |  | 44742.9914 | 50.1166
|  |  | 44742.9914 | 50.1166
|  |  | 44742.9914 | 50.1166
|  |  | 44742.9914 | 50.1166
|  |  | 44742.9914 | 50.1166
|  |  | 44742.9914 | 50.1165
|  |  | 44742.9914 | 50.1166
|  |  | 44742.9914 | 50.1166
|  |  | 44742.9914 | 50.1166
|  |  | 44742.9914 | 50.1166
|  |  | 44742.9914 | 50.1166
|  |  | 44742.9914 | 50.1165
|  |  | 44742.9914 | 50.1166
|  |  | 44742.9914 | 50.1166
|  |  | 44742.9914 | 50.1166
|  |  | 44742.9914 | 50.1167
|  |  | 44742.9914 | 50.1166
|  |  | 44742.9914 | 50.1167
|  |  | 44742.9914 | 50.1167
|  |  | 44742.9914 | 50.1168
|  |  | 44742.9914 | 50.1168
|  |  | 44742.9914 | 50.1167
|  |  | 44742.9914 | 50.1167
|  |  | 44742.9914 | 50.1167
|  |  | 44742.9914 | 50.1166
|  |  | 44742.9914 | 50.1166
|  |  | 44742.9914 | 50.1166
|  |  | 44742.9914 | 50.1166
|  |  | 44742.9914 | 50.1166
|  |  | 44742.9914 | 50.1166
|  |  | 44742.9914 | 50.1165
|  |  | 44742.9914 | 50.1165
|  |  | 44742.9914 | 50.1164
|  |  | 44742.9914 | 50.1164
|  |  | 44742.9914 | 50.1164
|  |  | 44742.9914 | 50.1164
|  |  | 44742.9914 | 50.1164
|  |  | 44742.9914 | 50.1164
|  |  | 44742.9914 | 50.1164
|  |  | 44742.9914 | 50.1165
|  |  | 44742.9914 | 50.1165
|  |  | 44742.9914 | 50.1165
|  |  | 44742.9914 | 50.1165
|  |  | 44742.9914 | 50.1166
|  |  | 44742.9914 | 50.1166
|  |  | 44742.9914 | 50.1166
|  |  | 2022-06-30 23:48 | 50.1166
|  |  | 44742.9914 | 50.1166
|  |  | 44742.9914 | 50.1165
|  |  | 44742.9914 | 50.1165
|  |  | 44742.9914 | 50.1166
|  |  | 44742.9914 | 50.1165
|  |  | 44742.9914 | 50.1165
|  |  | 44742.9914 | 50.1165
|  |  | 44742.9914 | 50.1165
|  |  | 44742.9914 | 50.1164
|  |  | 44742.9914 | 50.1164
|  |  | 44742.9914 | 50.1163
|  |  | 44742.9914 | 50.1164
|  |  | 44742.9914 | 50.1163
|  |  | 44742.9914 | 50.1163
|  |  | 44742.9914 | 50.1162
|  |  | 44742.9914 | 50.1163
|  |  | 44742.9914 | 50.1162
|  |  | 44742.9914 | 50.1163
|  |  | 44742.9914 | 50.1163
|  |  | 44742.9914 | 50.1163
|  |  | 44742.9914 | 50.1164
|  |  | 44742.9914 | 50.1164
|  |  | 44742.9914 | 50.1163
|  |  | 44742.9914 | 50.1163
|  |  | 44742.9914 | 50.1163
|  |  | 44742.9914 | 50.1163
|  |  | 44742.9914 | 50.1162
|  |  | 44742.9914 | 50.1162
|  |  | 44742.9914 | 50.1162
|  |  | 44742.9914 | 50.1161
|  |  | 44742.9914 | 50.1161
|  |  | 44742.9914 | 50.1161
|  |  | 44742.9914 | 50.1161
|  |  | 44742.9914 | 50.116
|  |  | 44742.9914 | 50.1161
|  |  | 44742.9914 | 50.1161
|  |  | 44742.9914 | 50.116
|  |  | 44742.9914 | 50.116
|  |  | 44742.9914 | 50.1161
|  |  | 44742.9914 | 50.1161
|  |  | 44742.9914 | 50.1161
|  |  | 44742.9914 | 50.1161
|  |  | 44742.9914 | 50.1161
|  |  | 44742.9914 | 50.1162
|  |  | 44742.9914 | 50.1162
|  |  | 44742.9914 | 50.1162
|  |  | 44742.9914 | 50.1161
|  |  | 44742.9914 | 50.1161
|  |  | 44742.9914 | 50.1161
|  |  | 2022-06-30 23:48 | 50.1161
|  |  | 44742.9914 | 50.1161
|  |  | 44742.9914 | 50.1161
|  |  | 44742.9914 | 50.1161
|  |  | 44742.9914 | 50.1161
|  |  | 44742.9914 | 50.116
|  |  | 44742.9914 | 50.116
|  |  | 44742.9914 | 50.116
|  |  | 44742.9914 | 50.116
|  |  | 44742.9914 | 50.116
|  |  | 44742.9914 | 50.116
|  |  | 44742.9914 | 50.116
|  |  | 44742.9914 | 50.116
|  |  | 44742.9914 | 50.116
|  |  | 44742.9914 | 50.116
|  |  | 44742.9914 | 50.116
|  |  | 44742.9914 | 50.1159
|  |  | 44742.9914 | 50.1159
|  |  | 44742.9914 | 50.1158
|  |  | 44742.9914 | 50.1158
|  |  | 44742.9914 | 50.1157
|  |  | 44742.9914 | 50.1156
|  |  | 44742.9914 | 50.1156
|  |  | 44742.9914 | 50.1156
|  |  | 44742.9914 | 50.1156
|  |  | 44742.9914 | 50.1155
|  |  | 44742.9914 | 50.1155
|  |  | 44742.9914 | 50.1154
|  |  | 44742.9914 | 50.1154
|  |  | 44742.9914 | 50.1154
|  |  | 44742.9914 | 50.1154
|  |  | 44742.9914 | 50.1154
|  |  | 44742.9914 | 50.1155
|  |  | 44742.9914 | 50.1155
|  |  | 44742.9914 | 50.1154
|  |  | 44742.9914 | 50.1154
|  |  | 44742.9914 | 50.1153
|  |  | 44742.9914 | 50.1153
|  |  | 44742.9914 | 50.1153
|  |  | 44742.9914 | 50.1152
|  |  | 44742.9914 | 50.1151
|  |  | 44742.9914 | 50.1151
|  |  | 44742.9914 | 50.115
|  |  | 44742.9914 | 50.115
|  |  | 44742.9914 | 50.1149
|  |  | 44742.9914 | 50.1149
|  |  | 44742.9914 | 50.1148
|  |  | 44742.9914 | 50.1148
|  |  | 44742.9914 | 50.1148
|  |  | 44742.9914 | 50.1147
|  |  | 2022-06-30 23:48 | 50.1148
|  |  | 44742.9914 | 50.1148
|  |  | 44742.9914 | 50.1148
|  |  | 44742.9914 | 50.1147
|  |  | 44742.9914 | 50.1147
|  |  | 44742.9914 | 50.1147
|  |  | 44742.9914 | 50.1147
|  |  | 44742.9914 | 50.1146
|  |  | 44742.9914 | 50.1146
|  |  | 44742.9914 | 50.1146
|  |  | 44742.9914 | 50.1146
|  |  | 44742.9914 | 50.1147
|  |  | 44742.9914 | 50.1148
|  |  | 44742.9914 | 50.1147
|  |  | 44742.9914 | 50.1147
|  |  | 44742.9914 | 50.1147
|  |  | 44742.9914 | 50.1147
|  |  | 44742.9914 | 50.1146
|  |  | 44742.9914 | 50.1146
|  |  | 44742.9914 | 50.1146
|  |  | 44742.9914 | 50.1146
|  |  | 44742.9914 | 50.1146
|  |  | 44742.9914 | 50.1146
|  |  | 44742.9914 | 50.1145
|  |  | 44742.9914 | 50.1145
|  |  | 44742.9914 | 50.1145
|  |  | 44742.9914 | 50.1145
|  |  | 44742.9914 | 50.1145
|  |  | 44742.9914 | 50.1145
|  |  | 44742.9914 | 50.1145
|  |  | 44742.9914 | 50.1145
|  |  | 44742.9914 | 50.1145
|  |  | 44742.9914 | 50.1145
|  |  | 44742.9914 | 50.1145
|  |  | 44742.9914 | 50.1145
|  |  | 44742.9914 | 50.1145
|  |  | 44742.9914 | 50.1145
|  |  | 44742.9914 | 50.1145
|  |  | 44742.9914 | 50.1145
|  |  | 44742.9914 | 50.1145
|  |  | 44742.9914 | 50.1144
|  |  | 44742.9914 | 50.1144
|  |  | 44742.9914 | 50.1144
|  |  | 44742.9914 | 50.1144
|  |  | 44742.9914 | 50.1144
|  |  | 44742.9914 | 50.1143
|  |  | 44742.9914 | 50.1142
|  |  | 44742.9914 | 50.1142
|  |  | 44742.9914 | 50.1141
|  |  | 44742.9914 | 50.1141
|  |  | 2022-06-30 23:48 | 50.114
|  |  | 44742.9914 | 50.114
|  |  | 44742.9914 | 50.114
|  |  | 44742.9914 | 50.114
|  |  | 44742.9914 | 50.114
|  |  | 44742.9914 | 50.114
|  |  | 44742.9914 | 50.114
|  |  | 44742.9914 | 50.1139
|  |  | 44742.9914 | 50.1139
|  |  | 44742.9914 | 50.1139
|  |  | 44742.9914 | 50.1138
|  |  | 44742.9914 | 50.1138
|  |  | 44742.9914 | 50.1137
|  |  | 44742.9914 | 50.1137
|  |  | 44742.9914 | 50.1136
|  |  | 44742.9914 | 50.1136
|  |  | 44742.9914 | 50.1136
|  |  | 44742.9914 | 50.1135
|  |  | 44742.9914 | 50.1135
|  |  | 44742.9914 | 50.1135
|  |  | 44742.9914 | 50.1135
|  |  | 44742.9914 | 50.1134
|  |  | 44742.9914 | 50.1134
|  |  | 44742.9914 | 50.1134
|  |  | 44742.9914 | 50.1134
|  |  | 44742.9914 | 50.1133
|  |  | 44742.9914 | 50.1132
|  |  | 44742.9914 | 50.1131
|  |  | 44742.9914 | 50.1131
|  |  | 44742.9914 | 50.113
|  |  | 44742.9914 | 50.1129
|  |  | 44742.9914 | 50.1129
|  |  | 44742.9914 | 50.113
|  |  | 44742.9914 | 50.113
|  |  | 44742.9914 | 50.113
|  |  | 44742.9914 | 50.113
|  |  | 44742.9914 | 50.113
|  |  | 44742.9914 | 50.113
|  |  | 44742.9914 | 50.113
|  |  | 44742.9914 | 50.1129
|  |  | 44742.9914 | 50.1128
|  |  | 44742.9914 | 50.1127
|  |  | 44742.9914 | 50.1127
|  |  | 44742.9914 | 50.1127
|  |  | 44742.9914 | 50.1126
|  |  | 44742.9914 | 50.1126
|  |  | 44742.9914 | 50.1125
|  |  | 44742.9914 | 50.1125
|  |  | 44742.9914 | 50.1125
|  |  | 44742.9914 | 50.1125
|  |  | 2022-06-30 23:48 | 50.1125
|  |  | 44742.9914 | 50.1125
|  |  | 44742.9914 | 50.1126
|  |  | 44742.9914 | 50.1126
|  |  | 44742.9914 | 50.1127
|  |  | 44742.9914 | 50.1127
|  |  | 44742.9914 | 50.1127
|  |  | 44742.9914 | 50.1127
|  |  | 44742.9914 | 50.1127
|  |  | 44742.9914 | 50.1127
|  |  | 44742.9914 | 50.1126
|  |  | 44742.9914 | 50.1125
|  |  | 44742.9914 | 50.1125
|  |  | 44742.9914 | 50.1124
|  |  | 44742.9914 | 50.1124
|  |  | 44742.9914 | 50.1123
|  |  | 44742.9914 | 50.1123
|  |  | 44742.9914 | 50.1123
|  |  | 44742.9914 | 50.1123
|  |  | 44742.9914 | 50.1123
|  |  | 44742.9914 | 50.1123
|  |  | 44742.9914 | 50.1124
|  |  | 44742.9914 | 50.1124
|  |  | 44742.9914 | 50.1124
|  |  | 44742.9914 | 50.1123
|  |  | 44742.9914 | 50.1123
|  |  | 44742.9914 | 50.1123
|  |  | 44742.9914 | 50.1124
|  |  | 44742.9914 | 50.1124
|  |  | 44742.9914 | 50.1124
|  |  | 44742.9914 | 50.1123
|  |  | 44742.9914 | 50.1124
|  |  | 44742.9914 | 50.1124
|  |  | 44742.9914 | 50.1124
|  |  | 44742.9914 | 50.1124
|  |  | 44742.9914 | 50.1124
|  |  | 44742.9914 | 50.1124
|  |  | 44742.9914 | 50.1124
|  |  | 44742.9914 | 50.1123
|  |  | 44742.9914 | 50.1123
|  |  | 44742.9914 | 50.1123
|  |  | 44742.9914 | 50.1122
|  |  | 44742.9914 | 50.1122
|  |  | 44742.9914 | 50.1123
|  |  | 44742.9914 | 50.1123
|  |  | 44742.9914 | 50.1123
|  |  | 44742.9914 | 50.1124
|  |  | 44742.9914 | 50.1124
|  |  | 44742.9914 | 50.1124
|  |  | 44742.9914 | 50.1125
|  |  | 2022-06-30 23:48 | 50.1125
|  |  | 44742.9914 | 50.1125
|  |  | 44742.9914 | 50.1125
|  |  | 44742.9914 | 50.1125
|  |  | 44742.9914 | 50.1125
|  |  | 44742.9914 | 50.1125
|  |  | 44742.9914 | 50.1125
|  |  | 44742.9914 | 50.1125
|  |  | 44742.9914 | 50.1125
|  |  | 44742.9914 | 50.1125
|  |  | 44742.9914 | 50.1125
|  |  | 44742.9914 | 50.1125
|  |  | 44742.9914 | 50.1126
|  |  | 44742.9914 | 50.1126
|  |  | 44742.9914 | 50.1127
|  |  | 44742.9914 | 50.1128
|  |  | 44742.9914 | 50.1129
|  |  | 44742.9914 | 50.113
|  |  | 44742.9914 | 50.113
|  |  | 44742.9914 | 50.1131
|  |  | 44742.9914 | 50.1132
|  |  | 44742.9914 | 50.1134
|  |  | 44742.9914 | 50.1134
|  |  | 44742.9914 | 50.1135
|  |  | 44742.9914 | 50.1135
|  |  | 44742.9914 | 50.1136
|  |  | 44742.9914 | 50.1136
|  |  | 44742.9914 | 50.1137
|  |  | 44742.9914 | 50.1137
|  |  | 44742.9914 | 50.1138
|  |  | 44742.9914 | 50.1138
|  |  | 44742.9914 | 50.1139
|  |  | 44742.9914 | 50.1139
|  |  | 44742.9914 | 50.114
|  |  | 44742.9914 | 50.1141
|  |  | 44742.9914 | 50.1142
|  |  | 44742.9914 | 50.1143
|  |  | 44742.9914 | 50.1143
|  |  | 44742.9914 | 50.1145
|  |  | 44742.9914 | 50.1145
|  |  | 44742.9914 | 50.1146
|  |  | 44742.9914 | 50.1146
|  |  | 44742.9914 | 50.1146
|  |  | 44742.9914 | 50.1146
|  |  | 44742.9914 | 50.1146
|  |  | 44742.9914 | 50.1146
|  |  | 44742.9914 | 50.1147
|  |  | 44742.9914 | 50.1148
|  |  | 44742.9914 | 50.1148
|  |  | 44742.9914 | 50.1149
|  |  | 2022-06-30 23:48 | 50.115
|  |  | 44742.9914 | 50.1151
|  |  | 44742.9914 | 50.1152
|  |  | 44742.9914 | 50.1152
|  |  | 44742.9914 | 50.1153
|  |  | 44742.9914 | 50.1153
|  |  | 44742.9914 | 50.1154
|  |  | 44742.9914 | 50.1155
|  |  | 44742.9914 | 50.1155
|  |  | 44742.9914 | 50.1156
|  |  | 44742.9914 | 50.1157
|  |  | 44742.9914 | 50.1157
|  |  | 44742.9914 | 50.1158
|  |  | 44742.9914 | 50.1159
|  |  | 44742.9915 | 50.1159
|  |  | 44742.9915 | 50.116
|  |  | 44742.9915 | 50.116
|  |  | 44742.9915 | 50.116
|  |  | 44742.9915 | 50.116
|  |  | 44742.9915 | 50.116
|  |  | 44742.9915 | 50.1161
|  |  | 44742.9915 | 50.1161
|  |  | 44742.9915 | 50.1162
|  |  | 44742.9915 | 50.1163
|  |  | 44742.9915 | 50.1163
|  |  | 44742.9915 | 50.1164
|  |  | 44742.9915 | 50.1164
|  |  | 44742.9915 | 50.1165
|  |  | 44742.9915 | 50.1165
|  |  | 44742.9915 | 50.1166
|  |  | 44742.9915 | 50.1167
|  |  | 44742.9915 | 50.1167
|  |  | 44742.9915 | 50.1167
|  |  | 44742.9915 | 50.1168
|  |  | 44742.9915 | 50.1168
|  |  | 44742.9915 | 50.1168
|  |  | 44742.9915 | 50.1168
|  |  | 44742.9915 | 50.1169
|  |  | 44742.9915 | 50.1169
|  |  | 44742.9915 | 50.117
|  |  | 44742.9915 | 50.1171
|  |  | 44742.9915 | 50.1171
|  |  | 44742.9915 | 50.1173
|  |  | 44742.9915 | 50.1174
|  |  | 44742.9915 | 50.1175
|  |  | 44742.9915 | 50.1175
|  |  | 44742.9915 | 50.1177
|  |  | 44742.9915 | 50.1177
|  |  | 44742.9915 | 50.1178
|  |  | 44742.9915 | 50.1179
|  |  | 2022-06-30 23:48 | 50.1179
|  |  | 44742.9915 | 50.118
|  |  | 44742.9915 | 50.118
|  |  | 44742.9915 | 50.1181
|  |  | 44742.9915 | 50.1182
|  |  | 44742.9915 | 50.1183
|  |  | 44742.9915 | 50.1183
|  |  | 44742.9915 | 50.1184
|  |  | 44742.9915 | 50.1185
|  |  | 44742.9915 | 50.1186
|  |  | 44742.9915 | 50.1187
|  |  | 44742.9915 | 50.1187
|  |  | 44742.9915 | 50.1188
|  |  | 44742.9915 | 50.1188
|  |  | 44742.9915 | 50.1188
|  |  | 44742.9915 | 50.1189
|  |  | 44742.9915 | 50.1189
|  |  | 44742.9915 | 50.1189
|  |  | 44742.9915 | 50.1189
|  |  | 44742.9915 | 50.119
|  |  | 44742.9915 | 50.119
|  |  | 44742.9915 | 50.1191
|  |  | 44742.9915 | 50.1192
|  |  | 44742.9915 | 50.1193
|  |  | 44742.9915 | 50.1193
|  |  | 44742.9915 | 50.1194
|  |  | 44742.9915 | 50.1195
|  |  | 44742.9915 | 50.1195
|  |  | 44742.9915 | 50.1196
|  |  | 44742.9915 | 50.1196
|  |  | 44742.9915 | 50.1196
|  |  | 44742.9915 | 50.1196
|  |  | 44742.9915 | 50.1197
|  |  | 44742.9915 | 50.1197
|  |  | 44742.9915 | 50.1197
|  |  | 44742.9915 | 50.1197
|  |  | 44742.9915 | 50.1197
|  |  | 44742.9915 | 50.1198
|  |  | 44742.9915 | 50.1198
|  |  | 44742.9915 | 50.1198
|  |  | 44742.9915 | 50.1198
|  |  | 44742.9915 | 50.1199
|  |  | 44742.9915 | 50.1199
|  |  | 44742.9915 | 50.12
|  |  | 44742.9915 | 50.12
|  |  | 44742.9915 | 50.1201
|  |  | 44742.9915 | 50.1201
|  |  | 44742.9915 | 50.1202
|  |  | 44742.9915 | 50.1203
|  |  | 44742.9915 | 50.1203
|  |  | 2022-06-30 23:48 | 50.1203
|  |  | 44742.9915 | 50.1203
|  |  | 44742.9915 | 50.1203
|  |  | 44742.9915 | 50.1203
|  |  | 44742.9915 | 50.1204
|  |  | 44742.9915 | 50.1203
|  |  | 44742.9915 | 50.1204
|  |  | 44742.9915 | 50.1204
|  |  | 44742.9915 | 50.1204
|  |  | 44742.9915 | 50.1205
|  |  | 44742.9915 | 50.1206
|  |  | 44742.9915 | 50.1207
|  |  | 44742.9915 | 50.1208
|  |  | 44742.9915 | 50.1208
|  |  | 44742.9915 | 50.1209
|  |  | 44742.9915 | 50.1209
|  |  | 44742.9915 | 50.1209
|  |  | 44742.9915 | 50.1209
|  |  | 44742.9915 | 50.1208
|  |  | 44742.9915 | 50.1208
|  |  | 44742.9915 | 50.1208
|  |  | 44742.9915 | 50.1208
|  |  | 44742.9915 | 50.1209
|  |  | 44742.9915 | 50.1209
|  |  | 44742.9915 | 50.1209
|  |  | 44742.9915 | 50.121
|  |  | 44742.9915 | 50.121
|  |  | 44742.9915 | 50.1211
|  |  | 44742.9915 | 50.1211
|  |  | 44742.9915 | 50.1211
|  |  | 44742.9915 | 50.1212
|  |  | 44742.9915 | 50.1212
|  |  | 44742.9915 | 50.1212
|  |  | 44742.9915 | 50.1213
|  |  | 44742.9915 | 50.1213
|  |  | 44742.9915 | 50.1213
|  |  | 44742.9915 | 50.1214
|  |  | 44742.9915 | 50.1214
|  |  | 44742.9915 | 50.1215
|  |  | 44742.9915 | 50.1215
|  |  | 44742.9915 | 50.1215
|  |  | 44742.9915 | 50.1215
|  |  | 44742.9915 | 50.1215
|  |  | 44742.9915 | 50.1216
|  |  | 44742.9915 | 50.1216
|  |  | 44742.9915 | 50.1216
|  |  | 44742.9915 | 50.1217
|  |  | 44742.9915 | 50.1217
|  |  | 44742.9915 | 50.1217
|  |  | 44742.9915 | 50.1218
|  |  | 2022-06-30 23:48 | 50.1217
|  |  | 44742.9915 | 50.1217
|  |  | 44742.9915 | 50.1217
|  |  | 44742.9915 | 50.1216
|  |  | 44742.9915 | 50.1216
|  |  | 44742.9915 | 50.1216
|  |  | 44742.9915 | 50.1216
|  |  | 44742.9915 | 50.1216
|  |  | 44742.9915 | 50.1217
|  |  | 44742.9915 | 50.1217
|  |  | 44742.9915 | 50.1218
|  |  | 44742.9915 | 50.1218
|  |  | 44742.9915 | 50.1219
|  |  | 44742.9915 | 50.1219
|  |  | 44742.9915 | 50.1219
|  |  | 44742.9915 | 50.122
|  |  | 44742.9915 | 50.122
|  |  | 44742.9915 | 50.1219
|  |  | 44742.9915 | 50.1219
|  |  | 44742.9915 | 50.1219
|  |  | 44742.9915 | 50.1219
|  |  | 44742.9915 | 50.1219
|  |  | 44742.9915 | 50.1219
|  |  | 44742.9915 | 50.1219
|  |  | 44742.9915 | 50.1219
|  |  | 44742.9915 | 50.1219
|  |  | 44742.9915 | 50.1219
|  |  | 44742.9915 | 50.1219
|  |  | 44742.9915 | 50.1219
|  |  | 44742.9915 | 50.1218
|  |  | 44742.9915 | 50.1218
|  |  | 44742.9915 | 50.1218
|  |  | 44742.9915 | 50.1219
|  |  | 44742.9915 | 50.1219
|  |  | 44742.9915 | 50.1219
|  |  | 44742.9915 | 50.1219
|  |  | 44742.9915 | 50.1219
|  |  | 44742.9915 | 50.1218
|  |  | 44742.9915 | 50.1218
|  |  | 44742.9915 | 50.1218
|  |  | 44742.9915 | 50.1218
|  |  | 44742.9915 | 50.1218
|  |  | 44742.9915 | 50.1218
|  |  | 44742.9915 | 50.1218
|  |  | 44742.9915 | 50.1218
|  |  | 44742.9915 | 50.1218
|  |  | 44742.9915 | 50.1217
|  |  | 44742.9915 | 50.1217
|  |  | 44742.9915 | 50.1217
|  |  | 44742.9915 | 50.1216
|  |  | 2022-06-30 23:48 | 50.1216
|  |  | 44742.9915 | 50.1217
|  |  | 44742.9915 | 50.1217
|  |  | 44742.9915 | 50.1216
|  |  | 44742.9915 | 50.1216
|  |  | 44742.9915 | 50.1216
|  |  | 44742.9915 | 50.1215
|  |  | 44742.9915 | 50.1215
|  |  | 44742.9915 | 50.1215
|  |  | 44742.9915 | 50.1215
|  |  | 44742.9915 | 50.1215
|  |  | 44742.9915 | 50.1215
|  |  | 44742.9915 | 50.1214
|  |  | 44742.9915 | 50.1214
|  |  | 44742.9915 | 50.1214
|  |  | 44742.9915 | 50.1214
|  |  | 44742.9915 | 50.1214
|  |  | 44742.9915 | 50.1214
|  |  | 44742.9915 | 50.1214
|  |  | 44742.9915 | 50.1213
|  |  | 44742.9915 | 50.1213
|  |  | 44742.9915 | 50.1213
|  |  | 44742.9915 | 50.1212
|  |  | 44742.9915 | 50.1211
|  |  | 44742.9915 | 50.1211
|  |  | 44742.9915 | 50.121
|  |  | 44742.9915 | 50.121
|  |  | 44742.9915 | 50.121
|  |  | 44742.9915 | 50.1209
|  |  | 44742.9915 | 50.1209
|  |  | 44742.9915 | 50.121
|  |  | 44742.9915 | 50.121
|  |  | 44742.9915 | 50.1209
|  |  | 44742.9915 | 50.1208
|  |  | 44742.9915 | 50.1208
|  |  | 44742.9915 | 50.1207
|  |  | 44742.9915 | 50.1207
|  |  | 44742.9915 | 50.1206
|  |  | 44742.9915 | 50.1206
|  |  | 44742.9915 | 50.1205
|  |  | 44742.9915 | 50.1204
|  |  | 44742.9915 | 50.1204
|  |  | 44742.9915 | 50.1203
|  |  | 44742.9915 | 50.1202
|  |  | 44742.9915 | 50.1202
|  |  | 44742.9915 | 50.1202
|  |  | 44742.9915 | 50.1201
|  |  | 44742.9915 | 50.1201
|  |  | 44742.9915 | 50.1201
|  |  | 44742.9915 | 50.12
|  |  | 2022-06-30 23:48 | 50.12
|  |  | 44742.9915 | 50.1199
|  |  | 44742.9915 | 50.1199
|  |  | 44742.9915 | 50.1198
|  |  | 44742.9915 | 50.1198
|  |  | 44742.9915 | 50.1198
|  |  | 44742.9915 | 50.1198
|  |  | 44742.9915 | 50.1198
|  |  | 44742.9915 | 50.1198
|  |  | 44742.9915 | 50.1198
|  |  | 44742.9915 | 50.1197
|  |  | 44742.9915 | 50.1197
|  |  | 44742.9915 | 50.1195
|  |  | 44742.9915 | 50.1195
|  |  | 44742.9915 | 50.1194
|  |  | 44742.9915 | 50.1193
|  |  | 44742.9915 | 50.1192
|  |  | 44742.9915 | 50.1191
|  |  | 44742.9915 | 50.119
|  |  | 44742.9915 | 50.119
|  |  | 44742.9915 | 50.1189
|  |  | 44742.9915 | 50.1188
|  |  | 44742.9915 | 50.1188
|  |  | 44742.9915 | 50.1187
|  |  | 44742.9915 | 50.1186
|  |  | 44742.9915 | 50.1186
|  |  | 44742.9915 | 50.1185
|  |  | 44742.9915 | 50.1184
|  |  | 44742.9915 | 50.1184
|  |  | 44742.9915 | 50.1183
|  |  | 44742.9915 | 50.1183
|  |  | 44742.9915 | 50.1182
|  |  | 44742.9915 | 50.1182
|  |  | 44742.9915 | 50.1181
|  |  | 44742.9915 | 50.118
|  |  | 44742.9915 | 50.118
|  |  | 44742.9915 | 50.118
|  |  | 44742.9915 | 50.1179
|  |  | 44742.9915 | 50.1179
|  |  | 44742.9915 | 50.1178
|  |  | 44742.9915 | 50.1178
|  |  | 44742.9915 | 50.1177
|  |  | 44742.9915 | 50.1176
|  |  | 44742.9915 | 50.1176
|  |  | 44742.9915 | 50.1175
|  |  | 44742.9915 | 50.1174
|  |  | 44742.9915 | 50.1175
|  |  | 44742.9915 | 50.1174
|  |  | 44742.9915 | 50.1174
|  |  | 44742.9915 | 50.1173
|  |  | 2022-06-30 23:48 | 50.1172
|  |  | 44742.9915 | 50.1171
|  |  | 44742.9915 | 50.117
|  |  | 44742.9915 | 50.1169
|  |  | 44742.9915 | 50.1168
|  |  | 44742.9915 | 50.1167
|  |  | 44742.9915 | 50.1166
|  |  | 44742.9915 | 50.1165
|  |  | 44742.9915 | 50.1164
|  |  | 44742.9915 | 50.1163
|  |  | 44742.9915 | 50.1162
|  |  | 44742.9915 | 50.1161
|  |  | 44742.9915 | 50.116
|  |  | 44742.9915 | 50.1159
|  |  | 44742.9915 | 50.1158
|  |  | 44742.9915 | 50.1157
|  |  | 44742.9915 | 50.1156
|  |  | 44742.9915 | 50.1155
|  |  | 44742.9915 | 50.1153
|  |  | 44742.9915 | 50.1152
|  |  | 44742.9915 | 50.115
|  |  | 44742.9915 | 50.1149
|  |  | 44742.9915 | 50.1148
|  |  | 44742.9915 | 50.1146
|  |  | 44742.9915 | 50.1145
|  |  | 44742.9915 | 50.1144
|  |  | 44742.9915 | 50.1142
|  |  | 44742.9915 | 50.1141
|  |  | 44742.9915 | 50.114
|  |  | 44742.9915 | 50.1139
|  |  | 44742.9915 | 50.1137
|  |  | 44742.9915 | 50.1136
|  |  | 44742.9915 | 50.1134
|  |  | 44742.9915 | 50.1133
|  |  | 44742.9915 | 50.1132
|  |  | 44742.9915 | 50.113
|  |  | 44742.9915 | 50.1128
|  |  | 44742.9915 | 50.1126
|  |  | 44742.9915 | 50.1123
|  |  | 44742.9915 | 50.112
|  |  | 44742.9915 | 50.1118
|  |  | 44742.9915 | 50.1116
|  |  | 44742.9915 | 50.1115
|  |  | 44742.9915 | 50.1113
|  |  | 44742.9915 | 50.1112
|  |  | 44742.9915 | 50.111
|  |  | 44742.9915 | 50.1109
|  |  | 44742.9915 | 50.1107
|  |  | 44742.9915 | 50.1106
|  |  | 44742.9915 | 50.1104
|  |  | 2022-06-30 23:48 | 50.1102
|  |  | 44742.9915 | 50.11
|  |  | 44742.9915 | 50.1098
|  |  | 44742.9915 | 50.1096
|  |  | 44742.9915 | 50.1093
|  |  | 44742.9915 | 50.109
|  |  | 44742.9915 | 50.1087
|  |  | 44742.9915 | 50.1084
|  |  | 44742.9915 | 50.1081
|  |  | 44742.9915 | 50.1079
|  |  | 44742.9915 | 50.1076
|  |  | 44742.9915 | 50.1074
|  |  | 44742.9915 | 50.1072
|  |  | 44742.9915 | 50.1069
|  |  | 44742.9915 | 50.1067
|  |  | 44742.9915 | 50.1065
|  |  | 44742.9915 | 50.1062
|  |  | 44742.9915 | 50.1058
|  |  | 44742.9915 | 50.1055
|  |  | 44742.9915 | 50.1052
|  |  | 44742.9915 | 50.1049
|  |  | 44742.9915 | 50.1045
|  |  | 44742.9915 | 50.1042
|  |  | 44742.9915 | 50.1039
|  |  | 44742.9915 | 50.1036
|  |  | 44742.9915 | 50.1033
|  |  | 44742.9915 | 50.103
|  |  | 44742.9915 | 50.1027
|  |  | 44742.9915 | 50.1025
|  |  | 44742.9915 | 50.1022
|  |  | 44742.9915 | 50.1019
|  |  | 44742.9915 | 50.1016
|  |  | 44742.9915 | 50.1013
|  |  | 44742.9915 | 50.101
|  |  | 44742.9915 | 50.1007
|  |  | 44742.9915 | 50.1003
|  |  | 44742.9915 | 50.1
|  |  | 44742.9915 | 50.0997
|  |  | 44742.9915 | 50.0994
|  |  | 44742.9915 | 50.0991
|  |  | 44742.9915 | 50.0988
|  |  | 44742.9915 | 50.0985
|  |  | 44742.9915 | 50.0982
|  |  | 44742.9915 | 50.0979
|  |  | 44742.9915 | 50.0975
|  |  | 44742.9915 | 50.0972
|  |  | 44742.9915 | 50.0968
|  |  | 44742.9915 | 50.0964
|  |  | 44742.9915 | 50.0961
|  |  | 44742.9915 | 50.0957
|  |  | 2022-06-30 23:48 | 50.0953
|  |  | 44742.9915 | 50.0949
|  |  | 44742.9915 | 50.0946
|  |  | 44742.9915 | 50.0943
|  |  | 44742.9915 | 50.0939
|  |  | 44742.9915 | 50.0936
|  |  | 44742.9915 | 50.0932
|  |  | 44742.9915 | 50.0929
|  |  | 44742.9915 | 50.0925
|  |  | 44742.9915 | 50.0921
|  |  | 44742.9915 | 50.0917
|  |  | 44742.9915 | 50.0914
|  |  | 44742.9915 | 50.0911
|  |  | 44742.9915 | 50.0907
|  |  | 44742.9915 | 50.0903
|  |  | 44742.9915 | 50.09
|  |  | 44742.9915 | 50.0896
|  |  | 44742.9915 | 50.0892
|  |  | 44742.9915 | 50.0889
|  |  | 44742.9915 | 50.0886
|  |  | 44742.9915 | 50.0882
|  |  | 44742.9915 | 50.0879
|  |  | 44742.9915 | 50.0875
|  |  | 44742.9915 | 50.0871
|  |  | 44742.9915 | 50.0868
|  |  | 44742.9915 | 50.0864
|  |  | 44742.9915 | 50.086
|  |  | 44742.9915 | 50.0856
|  |  | 44742.9915 | 50.0853
|  |  | 44742.9915 | 50.0849
|  |  | 44742.9915 | 50.0845
|  |  | 44742.9915 | 50.0842
|  |  | 44742.9915 | 50.0839
|  |  | 44742.9915 | 50.0836
|  |  | 44742.9915 | 50.0832
|  |  | 44742.9915 | 50.0829
|  |  | 44742.9915 | 50.0826
|  |  | 44742.9915 | 50.0822
|  |  | 44742.9915 | 50.0819
|  |  | 44742.9915 | 50.0816
|  |  | 44742.9915 | 50.0812
|  |  | 44742.9915 | 50.0809
|  |  | 44742.9915 | 50.0806
|  |  | 44742.9915 | 50.0802
|  |  | 44742.9915 | 50.0797
|  |  | 44742.9915 | 50.0793
|  |  | 44742.9915 | 50.0789
|  |  | 44742.9916 | 50.0785
|  |  | 44742.9916 | 50.0781
|  |  | 44742.9916 | 50.0777
|  |  | 2022-06-30 23:48 | 50.0773
|  |  | 44742.9916 | 50.0769
|  |  | 44742.9916 | 50.0765
|  |  | 44742.9916 | 50.0761
|  |  | 44742.9916 | 50.0757
|  |  | 44742.9916 | 50.0754
|  |  | 44742.9916 | 50.075
|  |  | 44742.9916 | 50.0746
|  |  | 44742.9916 | 50.0742
|  |  | 44742.9916 | 50.0738
|  |  | 44742.9916 | 50.0735
|  |  | 44742.9916 | 50.073
|  |  | 44742.9916 | 50.0726
|  |  | 44742.9916 | 50.0722
|  |  | 44742.9916 | 50.0718
|  |  | 44742.9916 | 50.0714
|  |  | 44742.9916 | 50.071
|  |  | 44742.9916 | 50.0706
|  |  | 44742.9916 | 50.0702
|  |  | 44742.9916 | 50.0698
|  |  | 44742.9916 | 50.0695
|  |  | 44742.9916 | 50.0691
|  |  | 44742.9916 | 50.0688
|  |  | 44742.9916 | 50.0684
|  |  | 44742.9916 | 50.0681
|  |  | 44742.9916 | 50.0677
|  |  | 44742.9916 | 50.0674
|  |  | 44742.9916 | 50.067
|  |  | 44742.9916 | 50.0666
|  |  | 44742.9916 | 50.0663
|  |  | 44742.9916 | 50.0659
|  |  | 44742.9916 | 50.0654
|  |  | 44742.9916 | 50.065
|  |  | 44742.9916 | 50.0646
|  |  | 44742.9916 | 50.0643
|  |  | 44742.9916 | 50.0639
|  |  | 44742.9916 | 50.0636
|  |  | 44742.9916 | 50.0632
|  |  | 44742.9916 | 50.0629
|  |  | 44742.9916 | 50.0625
|  |  | 44742.9916 | 50.0622
|  |  | 44742.9916 | 50.0619
|  |  | 44742.9916 | 50.0616
|  |  | 44742.9916 | 50.0612
|  |  | 44742.9916 | 50.0608
|  |  | 44742.9916 | 50.0604
|  |  | 44742.9916 | 50.0601
|  |  | 44742.9916 | 50.0597
|  |  | 44742.9916 | 50.0593
|  |  | 44742.9916 | 50.059
|  |  | 2022-06-30 23:48 | 50.0586
|  |  | 44742.9916 | 50.0582
|  |  | 44742.9916 | 50.0578
|  |  | 44742.9916 | 50.0574
|  |  | 44742.9916 | 50.0571
|  |  | 44742.9916 | 50.0567
|  |  | 44742.9916 | 50.0563
|  |  | 44742.9916 | 50.0559
|  |  | 44742.9916 | 50.0555
|  |  | 44742.9916 | 50.0551
|  |  | 44742.9916 | 50.0547
|  |  | 44742.9916 | 50.0543
|  |  | 44742.9916 | 50.0539
|  |  | 44742.9916 | 50.0535
|  |  | 44742.9916 | 50.0531
|  |  | 44742.9916 | 50.0527
|  |  | 44742.9916 | 50.0523
|  |  | 44742.9916 | 50.0519
|  |  | 44742.9916 | 50.0515
|  |  | 44742.9916 | 50.0511
|  |  | 44742.9916 | 50.0507
|  |  | 44742.9916 | 50.0503
|  |  | 44742.9916 | 50.05
|  |  | 44742.9916 | 50.0496
|  |  | 44742.9916 | 50.0493
|  |  | 44742.9916 | 50.0489
|  |  | 44742.9916 | 50.0485
|  |  | 44742.9916 | 50.0481
|  |  | 44742.9916 | 50.0477
|  |  | 44742.9916 | 50.0473
|  |  | 44742.9916 | 50.0469
|  |  | 44742.9916 | 50.0465
|  |  | 44742.9916 | 50.046
|  |  | 44742.9916 | 50.0456
|  |  | 44742.9916 | 50.0451
|  |  | 44742.9916 | 50.0446
|  |  | 44742.9916 | 50.0442
|  |  | 44742.9916 | 50.0437
|  |  | 44742.9916 | 50.0433
|  |  | 44742.9916 | 50.0428
|  |  | 44742.9916 | 50.0423
|  |  | 44742.9916 | 50.0418
|  |  | 44742.9916 | 50.0413
|  |  | 44742.9916 | 50.0409
|  |  | 44742.9916 | 50.0404
|  |  | 44742.9916 | 50.04
|  |  | 44742.9916 | 50.0395
|  |  | 44742.9916 | 50.0391
|  |  | 44742.9916 | 50.0387
|  |  | 44742.9916 | 50.0383
|  |  | 2022-06-30 23:48 | 50.0378
|  |  | 44742.9916 | 50.0374
|  |  | 44742.9916 | 50.037
|  |  | 44742.9916 | 50.0366
|  |  | 44742.9916 | 50.0361
|  |  | 44742.9916 | 50.0357
|  |  | 44742.9916 | 50.0353
|  |  | 44742.9916 | 50.0349
|  |  | 44742.9916 | 50.0346
|  |  | 44742.9916 | 50.0343
|  |  | 44742.9916 | 50.034
|  |  | 44742.9916 | 50.0337
|  |  | 44742.9916 | 50.0333
|  |  | 44742.9916 | 50.033
|  |  | 44742.9916 | 50.0326
|  |  | 44742.9916 | 50.0323
|  |  | 44742.9916 | 50.032
|  |  | 44742.9916 | 50.0317
|  |  | 44742.9916 | 50.0315
|  |  | 44742.9916 | 50.0312
|  |  | 44742.9916 | 50.031
|  |  | 44742.9916 | 50.0308
|  |  | 44742.9916 | 50.0306
|  |  | 44742.9916 | 50.0304
|  |  | 44742.9916 | 50.0302
|  |  | 44742.9916 | 50.03
|  |  | 44742.9916 | 50.0297
|  |  | 44742.9916 | 50.0295
|  |  | 44742.9916 | 50.0293
|  |  | 44742.9916 | 50.0291
|  |  | 44742.9916 | 50.0289
|  |  | 44742.9916 | 50.0288
|  |  | 44742.9916 | 50.0285
|  |  | 44742.9916 | 50.0283
|  |  | 44742.9916 | 50.0281
|  |  | 44742.9916 | 50.0278
|  |  | 44742.9916 | 50.0276
|  |  | 44742.9916 | 50.0274
|  |  | 44742.9916 | 50.0271
|  |  | 44742.9916 | 50.0269
|  |  | 44742.9916 | 50.0264
|  |  | 44742.9916 | 50.0261
|  |  | 44742.9916 | 50.0256
|  |  | 44742.9916 | 50.0251
|  |  | 44742.9916 | 50.0246
|  |  | 44742.9916 | 50.024
|  |  | 44742.9916 | 50.0234
|  |  | 44742.9916 | 50.0227
|  |  | 44742.9916 | 50.0219
|  |  | 44742.9916 | 50.0211
|  |  | 2022-06-30 23:48 | 50.0203
|  |  | 44742.9916 | 50.0194
|  |  | 44742.9916 | 50.0186
|  |  | 44742.9916 | 50.0177
|  |  | 44742.9916 | 50.0166
|  |  | 44742.9916 | 50.0156
|  |  | 44742.9916 | 50.0145
|  |  | 44742.9916 | 50.0135
|  |  | 44742.9916 | 50.0123
|  |  | 44742.9916 | 50.0112
|  |  | 44742.9916 | 50.01
|  |  | 44742.9916 | 50.0087
|  |  | 44742.9916 | 50.0075
|  |  | 44742.9916 | 50.0061
|  |  | 44742.9916 | 50.0047
|  |  | 44742.9916 | 50.0033
|  |  | 44742.9916 | 50.0019
|  |  | 44742.9916 | 50.0005
|  |  | 44742.9916 | 49.9991
|  |  | 44742.9916 | 49.9976
|  |  | 44742.9916 | 49.9963
|  |  | 44742.9916 | 49.9949
|  |  | 44742.9916 | 49.9934
|  |  | 44742.9916 | 49.992
|  |  | 44742.9916 | 49.9905
|  |  | 44742.9916 | 49.9891
|  |  | 44742.9916 | 49.9877
|  |  | 44742.9916 | 49.9863
|  |  | 44742.9916 | 49.9849
|  |  | 44742.9916 | 49.9836
|  |  | 44742.9916 | 49.9823
|  |  | 44742.9916 | 49.981
|  |  | 44742.9916 | 49.9798
|  |  | 44742.9916 | 49.9785
|  |  | 44742.9916 | 49.9771
|  |  | 44742.9916 | 49.9757
|  |  | 44742.9916 | 49.9742
|  |  | 44742.9916 | 49.9729
|  |  | 44742.9916 | 49.9713
|  |  | 44742.9916 | 49.9697
|  |  | 44742.9916 | 49.9681
|  |  | 44742.9916 | 49.9666
|  |  | 44742.9916 | 49.965
|  |  | 44742.9916 | 49.9636
|  |  | 44742.9916 | 49.9623
|  |  | 44742.9916 | 49.961
|  |  | 44742.9916 | 49.9598
|  |  | 44742.9916 | 49.9587
|  |  | 44742.9916 | 49.9576
|  |  | 44742.9916 | 49.9567
|  |  | 2022-06-30 23:48 | 49.9557
|  |  | 44742.9916 | 49.9547
|  |  | 44742.9916 | 49.9536
|  |  | 44742.9916 | 49.9526
|  |  | 44742.9916 | 49.9517
|  |  | 44742.9916 | 49.9507
|  |  | 44742.9916 | 49.9497
|  |  | 44742.9916 | 49.9488
|  |  | 44742.9916 | 49.9479
|  |  | 44742.9916 | 49.947
|  |  | 44742.9916 | 49.9462
|  |  | 44742.9916 | 49.9454
|  |  | 44742.9916 | 49.9447
|  |  | 44742.9916 | 49.9441
|  |  | 44742.9916 | 49.9434
|  |  | 44742.9916 | 49.9428
|  |  | 44742.9916 | 49.9422
|  |  | 44742.9916 | 49.9417
|  |  | 44742.9916 | 49.9412
|  |  | 44742.9916 | 49.9406
|  |  | 44742.9916 | 49.94
|  |  | 44742.9916 | 49.9396
|  |  | 44742.9916 | 49.939
|  |  | 44742.9916 | 49.9384
|  |  | 44742.9916 | 49.9378
|  |  | 44742.9916 | 49.9372
|  |  | 44742.9916 | 49.9366
|  |  | 44742.9916 | 49.936
|  |  | 44742.9916 | 49.9354
|  |  | 44742.9916 | 49.9348
|  |  | 44742.9916 | 49.9342
|  |  | 44742.9916 | 49.9336
|  |  | 44742.9916 | 49.933
|  |  | 44742.9916 | 49.9324
|  |  | 44742.9916 | 49.9318
|  |  | 44742.9916 | 49.931
|  |  | 44742.9916 | 49.9303
|  |  | 44742.9916 | 49.9295
|  |  | 44742.9916 | 49.9288
|  |  | 44742.9916 | 49.928
|  |  | 44742.9916 | 49.9272
|  |  | 44742.9916 | 49.9264
|  |  | 44742.9916 | 49.9256
|  |  | 44742.9916 | 49.9248
|  |  | 44742.9916 | 49.924
|  |  | 44742.9916 | 49.923
|  |  | 44742.9916 | 49.9222
|  |  | 44742.9916 | 49.9213
|  |  | 44742.9916 | 49.9204
|  |  | 44742.9916 | 49.9194
|  |  | 2022-06-30 23:48 | 49.9185
|  |  | 44742.9916 | 49.9175
|  |  | 44742.9916 | 49.9166
|  |  | 44742.9916 | 49.9155
|  |  | 44742.9916 | 49.9145
|  |  | 44742.9916 | 49.9136
|  |  | 44742.9916 | 49.9127
|  |  | 44742.9916 | 49.9119
|  |  | 44742.9916 | 49.911
|  |  | 44742.9916 | 49.9101
|  |  | 44742.9916 | 49.9092
|  |  | 44742.9916 | 49.9083
|  |  | 44742.9916 | 49.9074
|  |  | 44742.9916 | 49.9065
|  |  | 44742.9916 | 49.9056
|  |  | 44742.9916 | 49.9046
|  |  | 44742.9916 | 49.9037
|  |  | 44742.9916 | 49.9028
|  |  | 44742.9916 | 49.902
|  |  | 44742.9916 | 49.9012
|  |  | 44742.9916 | 49.9004
|  |  | 44742.9916 | 49.8998
|  |  | 44742.9916 | 49.899
|  |  | 44742.9916 | 49.8982
|  |  | 44742.9916 | 49.8976
|  |  | 44742.9916 | 49.8969
|  |  | 44742.9916 | 49.8964
|  |  | 44742.9916 | 49.8957
|  |  | 44742.9916 | 49.8951
|  |  | 44742.9916 | 49.8944
|  |  | 44742.9916 | 49.8939
|  |  | 44742.9916 | 49.8933
|  |  | 44742.9916 | 49.8928
|  |  | 44742.9916 | 49.8923
|  |  | 44742.9916 | 49.8918
|  |  | 44742.9916 | 49.8913
|  |  | 44742.9916 | 49.8908
|  |  | 44742.9916 | 49.8903
|  |  | 44742.9916 | 49.8898
|  |  | 44742.9916 | 49.8893
|  |  | 44742.9916 | 49.8888
|  |  | 44742.9916 | 49.8884
|  |  | 44742.9916 | 49.8879
|  |  | 44742.9916 | 49.8875
|  |  | 44742.9916 | 49.887
|  |  | 44742.9916 | 49.8866
|  |  | 44742.9916 | 49.886
|  |  | 44742.9916 | 49.8855
|  |  | 44742.9916 | 49.885
|  |  | 44742.9916 | 49.8846
|  |  | 2022-06-30 23:48 | 49.8841
|  |  | 44742.9916 | 49.8837
|  |  | 44742.9916 | 49.8833
|  |  | 44742.9916 | 49.8828
|  |  | 44742.9916 | 49.8824
|  |  | 44742.9916 | 49.8819
|  |  | 44742.9916 | 49.8814
|  |  | 44742.9916 | 49.8809
|  |  | 44742.9916 | 49.8803
|  |  | 44742.9916 | 49.8797
|  |  | 44742.9916 | 49.8791
|  |  | 44742.9916 | 49.8785
|  |  | 44742.9916 | 49.8779
|  |  | 44742.9916 | 49.8773
|  |  | 44742.9916 | 49.8766
|  |  | 44742.9916 | 49.876
|  |  | 44742.9916 | 49.8754
|  |  | 44742.9916 | 49.8748
|  |  | 44742.9916 | 49.8742
|  |  | 44742.9916 | 49.8736
|  |  | 44742.9916 | 49.873
|  |  | 44742.9916 | 49.8725
|  |  | 44742.9916 | 49.8719
|  |  | 44742.9916 | 49.8712
|  |  | 44742.9916 | 49.8706
|  |  | 44742.9916 | 49.87
|  |  | 44742.9916 | 49.8694
|  |  | 44742.9916 | 49.8688
|  |  | 44742.9916 | 49.8683
|  |  | 44742.9916 | 49.8677
|  |  | 44742.9916 | 49.8671
|  |  | 44742.9916 | 49.8665
|  |  | 44742.9916 | 49.8659
|  |  | 44742.9916 | 49.8654
|  |  | 44742.9916 | 49.8648
|  |  | 44742.9916 | 49.8642
|  |  | 44742.9916 | 49.8637
|  |  | 44742.9916 | 49.8631
|  |  | 44742.9916 | 49.8626
|  |  | 44742.9916 | 49.862
|  |  | 44742.9916 | 49.8615
|  |  | 44742.9916 | 49.8609
|  |  | 44742.9916 | 49.8604
|  |  | 44742.9916 | 49.8599
|  |  | 44742.9916 | 49.8594
|  |  | 44742.9916 | 49.8589
|  |  | 44742.9916 | 49.8584
|  |  | 44742.9916 | 49.8579
|  |  | 44742.9916 | 49.8575
|  |  | 44742.9916 | 49.8571
|  |  | 2022-06-30 23:48 | 49.8567
|  |  | 44742.9916 | 49.8562
|  |  | 44742.9916 | 49.8558
|  |  | 44742.9916 | 49.8555
|  |  | 44742.9916 | 49.8551
|  |  | 44742.9916 | 49.8548
|  |  | 44742.9916 | 49.8544
|  |  | 44742.9916 | 49.854
|  |  | 44742.9916 | 49.8536
|  |  | 44742.9916 | 49.8532
|  |  | 44742.9916 | 49.8528
|  |  | 44742.9916 | 49.8524
|  |  | 44742.9916 | 49.852
|  |  | 44742.9916 | 49.8516
|  |  | 44742.9916 | 49.8513
|  |  | 44742.9916 | 49.8509
|  |  | 44742.9916 | 49.8506
|  |  | 44742.9916 | 49.8503
|  |  | 44742.9916 | 49.8499
|  |  | 44742.9916 | 49.8496
|  |  | 44742.9916 | 49.8493
|  |  | 44742.9916 | 49.8489
|  |  | 44742.9916 | 49.8486
|  |  | 44742.9916 | 49.8482
|  |  | 44742.9916 | 49.8479
|  |  | 44742.9916 | 49.8475
|  |  | 44742.9916 | 49.8471
|  |  | 44742.9916 | 49.8467
|  |  | 44742.9916 | 49.8463
|  |  | 44742.9916 | 49.8459
|  |  | 44742.9916 | 49.8455
|  |  | 44742.9916 | 49.8451
|  |  | 44742.9916 | 49.8447
|  |  | 44742.9916 | 49.8443
|  |  | 44742.9916 | 49.8439
|  |  | 44742.9916 | 49.8435
|  |  | 44742.9916 | 49.8431
|  |  | 44742.9916 | 49.8426
|  |  | 44742.9916 | 49.8422
|  |  | 44742.9916 | 49.8418
|  |  | 44742.9916 | 49.8414
|  |  | 44742.9916 | 49.841
|  |  | 44742.9916 | 49.8407
|  |  | 44742.9916 | 49.8403
|  |  | 44742.9916 | 49.8399
|  |  | 44742.9916 | 49.8396
|  |  | 44742.9916 | 49.8392
|  |  | 44742.9916 | 49.8388
|  |  | 44742.9916 | 49.8383
|  |  | 44742.9916 | 49.8379
|  |  | 2022-06-30 23:48 | 49.8374
|  |  | 44742.9916 | 49.837
|  |  | 44742.9916 | 49.8366
|  |  | 44742.9916 | 49.8361
|  |  | 44742.9916 | 49.8357
|  |  | 44742.9916 | 49.8354
|  |  | 44742.9916 | 49.835
|  |  | 44742.9916 | 49.8346
|  |  | 44742.9916 | 49.8342
|  |  | 44742.9916 | 49.8339
|  |  | 44742.9916 | 49.8337
|  |  | 44742.9916 | 49.8333
|  |  | 44742.9916 | 49.833
|  |  | 44742.9916 | 49.8326
|  |  | 44742.9916 | 49.8323
|  |  | 44742.9916 | 49.832
|  |  | 44742.9916 | 49.8317
|  |  | 44742.9916 | 49.8314
|  |  | 44742.9916 | 49.8311
|  |  | 44742.9916 | 49.8308
|  |  | 44742.9916 | 49.8306
|  |  | 44742.9916 | 49.8303
|  |  | 44742.9916 | 49.8299
|  |  | 44742.9916 | 49.8297
|  |  | 44742.9916 | 49.8295
|  |  | 44742.9916 | 49.8293
|  |  | 44742.9916 | 49.829
|  |  | 44742.9916 | 49.8288
|  |  | 44742.9917 | 49.8285
|  |  | 44742.9917 | 49.8283
|  |  | 44742.9917 | 49.828
|  |  | 44742.9917 | 49.8278
|  |  | 44742.9917 | 49.8275
|  |  | 44742.9917 | 49.8272
|  |  | 44742.9917 | 49.827
|  |  | 44742.9917 | 49.8267
|  |  | 44742.9917 | 49.8264
|  |  | 44742.9917 | 49.8261
|  |  | 44742.9917 | 49.8258
|  |  | 44742.9917 | 49.8256
|  |  | 44742.9917 | 49.8254
|  |  | 44742.9917 | 49.8253
|  |  | 44742.9917 | 49.8251
|  |  | 44742.9917 | 49.8249
|  |  | 44742.9917 | 49.8247
|  |  | 44742.9917 | 49.8245
|  |  | 44742.9917 | 49.8243
|  |  | 44742.9917 | 49.824
|  |  | 44742.9917 | 49.8238
|  |  | 44742.9917 | 49.8235
|  |  | 2022-06-30 23:48 | 49.8233
|  |  | 44742.9917 | 49.823
|  |  | 44742.9917 | 49.8226
|  |  | 44742.9917 | 49.8223
|  |  | 44742.9917 | 49.8221
|  |  | 44742.9917 | 49.8218
|  |  | 44742.9917 | 49.8215
|  |  | 44742.9917 | 49.8214
|  |  | 44742.9917 | 49.8212
|  |  | 44742.9917 | 49.821
|  |  | 44742.9917 | 49.8208
|  |  | 44742.9917 | 49.8206
|  |  | 44742.9917 | 49.8204
|  |  | 44742.9917 | 49.8202
|  |  | 44742.9917 | 49.8199
|  |  | 44742.9917 | 49.8197
|  |  | 44742.9917 | 49.8194
|  |  | 44742.9917 | 49.8191
|  |  | 44742.9917 | 49.8188
|  |  | 44742.9917 | 49.8185
|  |  | 44742.9917 | 49.8182
|  |  | 44742.9917 | 49.8179
|  |  | 44742.9917 | 49.8176
|  |  | 44742.9917 | 49.8174
|  |  | 44742.9917 | 49.8171
|  |  | 44742.9917 | 49.8169
|  |  | 44742.9917 | 49.8167
|  |  | 44742.9917 | 49.8165
|  |  | 44742.9917 | 49.8164
|  |  | 44742.9917 | 49.8162
|  |  | 44742.9917 | 49.816
|  |  | 44742.9917 | 49.8158
|  |  | 44742.9917 | 49.8156
|  |  | 44742.9917 | 49.8153
|  |  | 44742.9917 | 49.8151
|  |  | 44742.9917 | 49.8148
|  |  | 44742.9917 | 49.8146
|  |  | 44742.9917 | 49.8143
|  |  | 44742.9917 | 49.8141
|  |  | 44742.9917 | 49.8139
|  |  | 44742.9917 | 49.8137
|  |  | 44742.9917 | 49.8136
|  |  | 44742.9917 | 49.8134
|  |  | 44742.9917 | 49.8132
|  |  | 44742.9917 | 49.813
|  |  | 44742.9917 | 49.8128
|  |  | 44742.9917 | 49.8126
|  |  | 44742.9917 | 49.8123
|  |  | 44742.9917 | 49.8121
|  |  | 44742.9917 | 49.8118
|  |  | 2022-06-30 23:48 | 49.8116
|  |  | 44742.9917 | 49.8114
|  |  | 44742.9917 | 49.8111
|  |  | 44742.9917 | 49.8109
|  |  | 44742.9917 | 49.8108
|  |  | 44742.9917 | 49.8106
|  |  | 44742.9917 | 49.8104
|  |  | 44742.9917 | 49.8102
|  |  | 44742.9917 | 49.8099
|  |  | 44742.9917 | 49.8097
|  |  | 44742.9917 | 49.8095
|  |  | 44742.9917 | 49.8093
|  |  | 44742.9917 | 49.8091
|  |  | 44742.9917 | 49.8089
|  |  | 44742.9917 | 49.8087
|  |  | 44742.9917 | 49.8085
|  |  | 44742.9917 | 49.8084
|  |  | 44742.9917 | 49.8082
|  |  | 44742.9917 | 49.808
|  |  | 44742.9917 | 49.8078
|  |  | 44742.9917 | 49.8076
|  |  | 44742.9917 | 49.8074
|  |  | 44742.9917 | 49.8073
|  |  | 44742.9917 | 49.8071
|  |  | 44742.9917 | 49.8069
|  |  | 44742.9917 | 49.8067
|  |  | 44742.9917 | 49.8065
|  |  | 44742.9917 | 49.8063
|  |  | 44742.9917 | 49.8061
|  |  | 44742.9917 | 49.806
|  |  | 44742.9917 | 49.8059
|  |  | 44742.9917 | 49.8057
|  |  | 44742.9917 | 49.8055
|  |  | 44742.9917 | 49.8053
|  |  | 44742.9917 | 49.8051
|  |  | 44742.9917 | 49.805
|  |  | 44742.9917 | 49.8049
|  |  | 44742.9917 | 49.8047
|  |  | 44742.9917 | 49.8045
|  |  | 44742.9917 | 49.8044
|  |  | 44742.9917 | 49.8042
|  |  | 44742.9917 | 49.804
|  |  | 44742.9917 | 49.8039
|  |  | 44742.9917 | 49.8037
|  |  | 44742.9917 | 49.8036
|  |  | 44742.9917 | 49.8034
|  |  | 44742.9917 | 49.8033
|  |  | 44742.9917 | 49.8031
|  |  | 44742.9917 | 49.8029
|  |  | 44742.9917 | 49.8027
|  |  | 2022-06-30 23:48 | 49.8025
|  |  | 44742.9917 | 49.8023
|  |  | 44742.9917 | 49.8021
|  |  | 44742.9917 | 49.8019
|  |  | 44742.9917 | 49.8018
|  |  | 44742.9917 | 49.8016
|  |  | 44742.9917 | 49.8015
|  |  | 44742.9917 | 49.8014
|  |  | 44742.9917 | 49.8013
|  |  | 44742.9917 | 49.8012
|  |  | 44742.9917 | 49.8011
|  |  | 44742.9917 | 49.801
|  |  | 44742.9917 | 49.8009
|  |  | 44742.9917 | 49.8007
|  |  | 44742.9917 | 49.8005
|  |  | 44742.9917 | 49.8003
|  |  | 44742.9917 | 49.8001
|  |  | 44742.9917 | 49.8
|  |  | 44742.9917 | 49.7998
|  |  | 44742.9917 | 49.7998
|  |  | 44742.9917 | 49.7996
|  |  | 44742.9917 | 49.7996
|  |  | 44742.9917 | 49.7995
|  |  | 44742.9917 | 49.7994
|  |  | 44742.9917 | 49.7993
|  |  | 44742.9917 | 49.7993
|  |  | 44742.9917 | 49.7992
|  |  | 44742.9917 | 49.7991
|  |  | 44742.9917 | 49.799
|  |  | 44742.9917 | 49.7989
|  |  | 44742.9917 | 49.7987
|  |  | 44742.9917 | 49.7986
|  |  | 44742.9917 | 49.7985
|  |  | 44742.9917 | 49.7984
|  |  | 44742.9917 | 49.7983
|  |  | 44742.9917 | 49.7982
|  |  | 44742.9917 | 49.7981
|  |  | 44742.9917 | 49.798
|  |  | 44742.9917 | 49.798
|  |  | 44742.9917 | 49.7979
|  |  | 44742.9917 | 49.7979
|  |  | 44742.9917 | 49.7978
|  |  | 44742.9917 | 49.7978
|  |  | 44742.9917 | 49.7977
|  |  | 44742.9917 | 49.7976
|  |  | 44742.9917 | 49.7976
|  |  | 44742.9917 | 49.7975
|  |  | 44742.9917 | 49.7975
|  |  | 44742.9917 | 49.7975
|  |  | 44742.9917 | 49.7974
|  |  | 2022-06-30 23:48 | 49.7973
|  |  | 44742.9917 | 49.7971
|  |  | 44742.9917 | 49.797
|  |  | 44742.9917 | 49.7969
|  |  | 44742.9917 | 49.7968
|  |  | 44742.9917 | 49.7967
|  |  | 44742.9917 | 49.7966
|  |  | 44742.9917 | 49.7966
|  |  | 44742.9917 | 49.7966
|  |  | 44742.9917 | 49.7965
|  |  | 44742.9917 | 49.7965
|  |  | 44742.9917 | 49.7964
|  |  | 44742.9917 | 49.7964
|  |  | 44742.9917 | 49.7963
|  |  | 44742.9917 | 49.7963
|  |  | 44742.9917 | 49.7962
|  |  | 44742.9917 | 49.7961
|  |  | 44742.9917 | 49.796
|  |  | 44742.9917 | 49.7959
|  |  | 44742.9917 | 49.7959
|  |  | 44742.9917 | 49.7959
|  |  | 44742.9917 | 49.7958
|  |  | 44742.9917 | 49.7958
|  |  | 44742.9917 | 49.7958
|  |  | 44742.9917 | 49.7958
|  |  | 44742.9917 | 49.7957
|  |  | 44742.9917 | 49.7956
|  |  | 44742.9917 | 49.7956
|  |  | 44742.9917 | 49.7955
|  |  | 44742.9917 | 49.7954
|  |  | 44742.9917 | 49.7954
|  |  | 44742.9917 | 49.7953
|  |  | 44742.9917 | 49.7953
|  |  | 44742.9917 | 49.7952
|  |  | 44742.9917 | 49.7951
|  |  | 44742.9917 | 49.795
|  |  | 44742.9917 | 49.7949
|  |  | 44742.9917 | 49.7949
|  |  | 44742.9917 | 49.7949
|  |  | 44742.9917 | 49.7949
|  |  | 44742.9917 | 49.7948
|  |  | 44742.9917 | 49.7947
|  |  | 44742.9917 | 49.7947
|  |  | 44742.9917 | 49.7947
|  |  | 44742.9917 | 49.7946
|  |  | 44742.9917 | 49.7946
|  |  | 44742.9917 | 49.7945
|  |  | 44742.9917 | 49.7945
|  |  | 44742.9917 | 49.7945
|  |  | 44742.9917 | 49.7945
|  |  | 2022-06-30 23:48 | 49.7945
|  |  | 44742.9917 | 49.7945
|  |  | 44742.9917 | 49.7945
|  |  | 44742.9917 | 49.7944
|  |  | 44742.9917 | 49.7944
|  |  | 44742.9917 | 49.7944
|  |  | 44742.9917 | 49.7944
|  |  | 44742.9917 | 49.7944
|  |  | 44742.9917 | 49.7944
|  |  | 44742.9917 | 49.7944
|  |  | 44742.9917 | 49.7943
|  |  | 44742.9917 | 49.7943
|  |  | 44742.9917 | 49.7942
|  |  | 44742.9917 | 49.7942
|  |  | 44742.9917 | 49.7942
|  |  | 44742.9917 | 49.7941
|  |  | 44742.9917 | 49.7941
|  |  | 44742.9917 | 49.7941
|  |  | 44742.9917 | 49.7941
|  |  | 44742.9917 | 49.794
|  |  | 44742.9917 | 49.794
|  |  | 44742.9917 | 49.7939
|  |  | 44742.9917 | 49.7939
|  |  | 44742.9917 | 49.7939
|  |  | 44742.9917 | 49.7939
|  |  | 44742.9917 | 49.7939
|  |  | 44742.9917 | 49.7938
|  |  | 44742.9917 | 49.7939
|  |  | 44742.9917 | 49.7939
|  |  | 44742.9917 | 49.7939
|  |  | 44742.9917 | 49.7938
|  |  | 44742.9917 | 49.7938
|  |  | 44742.9917 | 49.7938
|  |  | 44742.9917 | 49.7938
|  |  | 44742.9917 | 49.7937
|  |  | 44742.9917 | 49.7936
|  |  | 44742.9917 | 49.7936
|  |  | 44742.9917 | 49.7935
|  |  | 44742.9917 | 49.7935
|  |  | 44742.9917 | 49.7934
|  |  | 44742.9917 | 49.7934
|  |  | 44742.9917 | 49.7933
|  |  | 44742.9917 | 49.7932
|  |  | 44742.9917 | 49.7932
|  |  | 44742.9917 | 49.7931
|  |  | 44742.9917 | 49.7931
|  |  | 44742.9917 | 49.793
|  |  | 44742.9917 | 49.793
|  |  | 44742.9917 | 49.793
|  |  | 44742.9917 | 49.793
|  |  | 2022-06-30 23:48 | 49.793
|  |  | 44742.9917 | 49.7931
|  |  | 44742.9917 | 49.7931
|  |  | 44742.9917 | 49.7931
|  |  | 44742.9917 | 49.793
|  |  | 44742.9917 | 49.793
|  |  | 44742.9917 | 49.7929
|  |  | 44742.9917 | 49.7928
|  |  | 44742.9917 | 49.7927
|  |  | 44742.9917 | 49.7926
|  |  | 44742.9917 | 49.7926
|  |  | 44742.9917 | 49.7925
|  |  | 44742.9917 | 49.7925
|  |  | 44742.9917 | 49.7925
|  |  | 44742.9917 | 49.7925
|  |  | 44742.9917 | 49.7925
|  |  | 44742.9917 | 49.7925
|  |  | 44742.9917 | 49.7925
|  |  | 44742.9917 | 49.7925
|  |  | 44742.9917 | 49.7924
|  |  | 44742.9917 | 49.7924
|  |  | 44742.9917 | 49.7924
|  |  | 44742.9917 | 49.7924
|  |  | 44742.9917 | 49.7924
|  |  | 44742.9917 | 49.7924
|  |  | 44742.9917 | 49.7924
|  |  | 44742.9917 | 49.7924
|  |  | 44742.9917 | 49.7924
|  |  | 44742.9917 | 49.7924
|  |  | 44742.9917 | 49.7923
|  |  | 44742.9917 | 49.7924
|  |  | 44742.9917 | 49.7924
|  |  | 44742.9917 | 49.7924
|  |  | 44742.9917 | 49.7924
|  |  | 44742.9917 | 49.7925
|  |  | 44742.9917 | 49.7925
|  |  | 44742.9917 | 49.7926
|  |  | 44742.9917 | 49.7927
|  |  | 44742.9917 | 49.7927
|  |  | 44742.9917 | 49.7927
|  |  | 44742.9917 | 49.7927
|  |  | 44742.9917 | 49.7928
|  |  | 44742.9917 | 49.7927
|  |  | 44742.9917 | 49.7927
|  |  | 44742.9917 | 49.7927
|  |  | 44742.9917 | 49.7927
|  |  | 44742.9917 | 49.7927
|  |  | 44742.9917 | 49.7927
|  |  | 44742.9917 | 49.7928
|  |  | 44742.9917 | 49.7928
|  |  | 2022-06-30 23:48 | 49.7928
|  |  | 44742.9917 | 49.7928
|  |  | 44742.9917 | 49.7928
|  |  | 44742.9917 | 49.7929
|  |  | 44742.9917 | 49.793
|  |  | 44742.9917 | 49.793
|  |  | 44742.9917 | 49.793
|  |  | 44742.9917 | 49.793
|  |  | 44742.9917 | 49.793
|  |  | 44742.9917 | 49.7931
|  |  | 44742.9917 | 49.7931
|  |  | 44742.9917 | 49.7931
|  |  | 44742.9917 | 49.7931
|  |  | 44742.9917 | 49.7931
|  |  | 44742.9917 | 49.7931
|  |  | 44742.9917 | 49.7931
|  |  | 44742.9917 | 49.7931
|  |  | 44742.9917 | 49.7931
|  |  | 44742.9917 | 49.7932
|  |  | 44742.9917 | 49.7933
|  |  | 44742.9917 | 49.7933
|  |  | 44742.9917 | 49.7933
|  |  | 44742.9917 | 49.7933
|  |  | 44742.9917 | 49.7934
|  |  | 44742.9917 | 49.7934
|  |  | 44742.9917 | 49.7934
|  |  | 44742.9917 | 49.7935
|  |  | 44742.9917 | 49.7935
|  |  | 44742.9917 | 49.7936
|  |  | 44742.9917 | 49.7937
|  |  | 44742.9917 | 49.7937
|  |  | 44742.9917 | 49.7938
|  |  | 44742.9917 | 49.7938
|  |  | 44742.9917 | 49.7938
|  |  | 44742.9917 | 49.7938
|  |  | 44742.9917 | 49.7939
|  |  | 44742.9917 | 49.7939
|  |  | 44742.9917 | 49.7938
|  |  | 44742.9917 | 49.7938
|  |  | 44742.9917 | 49.7938
|  |  | 44742.9917 | 49.7938
|  |  | 44742.9917 | 49.7938
|  |  | 44742.9917 | 49.7938
|  |  | 44742.9917 | 49.7938
|  |  | 44742.9917 | 49.7938
|  |  | 44742.9917 | 49.7938
|  |  | 44742.9917 | 49.7938
|  |  | 44742.9917 | 49.7938
|  |  | 44742.9917 | 49.7938
|  |  | 44742.9917 | 49.7939
|  |  | 2022-06-30 23:48 | 49.7938
|  |  | 44742.9917 | 49.7938
|  |  | 44742.9917 | 49.7939
|  |  | 44742.9917 | 49.7939
|  |  | 44742.9917 | 49.7939
|  |  | 44742.9917 | 49.7939
|  |  | 44742.9917 | 49.794
|  |  | 44742.9917 | 49.7941
|  |  | 44742.9917 | 49.7941
|  |  | 44742.9917 | 49.7942
|  |  | 44742.9917 | 49.7942
|  |  | 44742.9917 | 49.7942
|  |  | 44742.9917 | 49.7943
|  |  | 44742.9917 | 49.7944
|  |  | 44742.9917 | 49.7944
|  |  | 44742.9917 | 49.7944
|  |  | 44742.9917 | 49.7944
|  |  | 44742.9917 | 49.7944
|  |  | 44742.9917 | 49.7944
|  |  | 44742.9917 | 49.7945
|  |  | 44742.9917 | 49.7945
|  |  | 44742.9917 | 49.7946
|  |  | 44742.9917 | 49.7946
|  |  | 44742.9917 | 49.7946
|  |  | 44742.9917 | 49.7946
|  |  | 44742.9917 | 49.7947
|  |  | 44742.9917 | 49.7948
|  |  | 44742.9917 | 49.7948
|  |  | 44742.9917 | 49.7949
|  |  | 44742.9917 | 49.7949
|  |  | 44742.9917 | 49.795
|  |  | 44742.9917 | 49.795
|  |  | 44742.9917 | 49.7951
|  |  | 44742.9917 | 49.7951
|  |  | 44742.9917 | 49.7951
|  |  | 44742.9917 | 49.7952
|  |  | 44742.9917 | 49.7952
|  |  | 44742.9917 | 49.7952
|  |  | 44742.9917 | 49.7953
|  |  | 44742.9917 | 49.7953
|  |  | 44742.9917 | 49.7953
|  |  | 44742.9917 | 49.7954
|  |  | 44742.9917 | 49.7954
|  |  | 44742.9917 | 49.7955
|  |  | 44742.9917 | 49.7956
|  |  | 44742.9917 | 49.7957
|  |  | 44742.9917 | 49.7957
|  |  | 44742.9917 | 49.7957
|  |  | 44742.9917 | 49.7958
|  |  | 44742.9917 | 49.7958
|  |  | 2022-06-30 23:48 | 49.7958
|  |  | 44742.9917 | 49.7958
|  |  | 44742.9917 | 49.7959
|  |  | 44742.9917 | 49.7959
|  |  | 44742.9917 | 49.7959
|  |  | 44742.9917 | 49.7959
|  |  | 44742.9917 | 49.7959
|  |  | 44742.9917 | 49.796
|  |  | 44742.9917 | 49.7961
|  |  | 44742.9917 | 49.7961
|  |  | 44742.9918 | 49.7961
|  |  | 44742.9918 | 49.7961
|  |  | 44742.9918 | 49.7961
|  |  | 44742.9918 | 49.7961
|  |  | 44742.9918 | 49.7961
|  |  | 44742.9918 | 49.7962
|  |  | 44742.9918 | 49.7962
|  |  | 44742.9918 | 49.7963
|  |  | 44742.9918 | 49.7964
|  |  | 44742.9918 | 49.7964
|  |  | 44742.9918 | 49.7964
|  |  | 44742.9918 | 49.7965
|  |  | 44742.9918 | 49.7965
|  |  | 44742.9918 | 49.7965
|  |  | 44742.9918 | 49.7965
|  |  | 44742.9918 | 49.7965
|  |  | 44742.9918 | 49.7965
|  |  | 44742.9918 | 49.7965
|  |  | 44742.9918 | 49.7966
|  |  | 44742.9918 | 49.7966
|  |  | 44742.9918 | 49.7966
|  |  | 44742.9918 | 49.7966
|  |  | 44742.9918 | 49.7966
|  |  | 44742.9918 | 49.7966
|  |  | 44742.9918 | 49.7966
|  |  | 44742.9918 | 49.7966
|  |  | 44742.9918 | 49.7967
|  |  | 44742.9918 | 49.7968
|  |  | 44742.9918 | 49.7968
|  |  | 44742.9918 | 49.7969
|  |  | 44742.9918 | 49.797
|  |  | 44742.9918 | 49.797
|  |  | 44742.9918 | 49.7971
|  |  | 44742.9918 | 49.7971
|  |  | 44742.9918 | 49.7972
|  |  | 44742.9918 | 49.7972
|  |  | 44742.9918 | 49.7973
|  |  | 44742.9918 | 49.7973
|  |  | 44742.9918 | 49.7973
|  |  | 44742.9918 | 49.7974
|  |  | 2022-06-30 23:48 | 49.7974
|  |  | 44742.9918 | 49.7974
|  |  | 44742.9918 | 49.7975
|  |  | 44742.9918 | 49.7975
|  |  | 44742.9918 | 49.7975
|  |  | 44742.9918 | 49.7976
|  |  | 44742.9918 | 49.7976
|  |  | 44742.9918 | 49.7976
|  |  | 44742.9918 | 49.7977
|  |  | 44742.9918 | 49.7977
|  |  | 44742.9918 | 49.7978
|  |  | 44742.9918 | 49.7978
|  |  | 44742.9918 | 49.7978
|  |  | 44742.9918 | 49.7978
|  |  | 44742.9918 | 49.7978
|  |  | 44742.9918 | 49.7979
|  |  | 44742.9918 | 49.7979
|  |  | 44742.9918 | 49.7978
|  |  | 44742.9918 | 49.7978
|  |  | 44742.9918 | 49.7978
|  |  | 44742.9918 | 49.7979
|  |  | 44742.9918 | 49.7979
|  |  | 44742.9918 | 49.7979
|  |  | 44742.9918 | 49.798
|  |  | 44742.9918 | 49.798
|  |  | 44742.9918 | 49.798
|  |  | 44742.9918 | 49.798
|  |  | 44742.9918 | 49.7979
|  |  | 44742.9918 | 49.7979
|  |  | 44742.9918 | 49.7978
|  |  | 44742.9918 | 49.7978
|  |  | 44742.9918 | 49.7978
|  |  | 44742.9918 | 49.7978
|  |  | 44742.9918 | 49.7978
|  |  | 44742.9918 | 49.7978
|  |  | 44742.9918 | 49.7979
|  |  | 44742.9918 | 49.7979
|  |  | 44742.9918 | 49.7979
|  |  | 44742.9918 | 49.798
|  |  | 44742.9918 | 49.798
|  |  | 44742.9918 | 49.798
|  |  | 44742.9918 | 49.798
|  |  | 44742.9918 | 49.798
|  |  | 44742.9918 | 49.798
|  |  | 44742.9918 | 49.7981
|  |  | 44742.9918 | 49.7981
|  |  | 44742.9918 | 49.7981
|  |  | 44742.9918 | 49.7982
|  |  | 44742.9918 | 49.7981
|  |  | 44742.9918 | 49.7981
|  |  | 2022-06-30 23:48 | 49.7981
|  |  | 44742.9918 | 49.798
|  |  | 44742.9918 | 49.798
|  |  | 44742.9918 | 49.7979
|  |  | 44742.9918 | 49.7978
|  |  | 44742.9918 | 49.7978
|  |  | 44742.9918 | 49.7978
|  |  | 44742.9918 | 49.7977
|  |  | 44742.9918 | 49.7977
|  |  | 44742.9918 | 49.7977
|  |  | 44742.9918 | 49.7977
|  |  | 44742.9918 | 49.7977
|  |  | 44742.9918 | 49.7977
|  |  | 44742.9918 | 49.7976
|  |  | 44742.9918 | 49.7976
|  |  | 44742.9918 | 49.7976
|  |  | 44742.9918 | 49.7975
|  |  | 44742.9918 | 49.7975
|  |  | 44742.9918 | 49.7975
|  |  | 44742.9918 | 49.7975
|  |  | 44742.9918 | 49.7975
|  |  | 44742.9918 | 49.7975
|  |  | 44742.9918 | 49.7974
|  |  | 44742.9918 | 49.7974
|  |  | 44742.9918 | 49.7974
|  |  | 44742.9918 | 49.7974
|  |  | 44742.9918 | 49.7975
|  |  | 44742.9918 | 49.7975
|  |  | 44742.9918 | 49.7975
|  |  | 44742.9918 | 49.7975
|  |  | 44742.9918 | 49.7975
|  |  | 44742.9918 | 49.7974
|  |  | 44742.9918 | 49.7974
|  |  | 44742.9918 | 49.7973
|  |  | 44742.9918 | 49.7973
|  |  | 44742.9918 | 49.7973
|  |  | 44742.9918 | 49.7973
|  |  | 44742.9918 | 49.7972
|  |  | 44742.9918 | 49.7972
|  |  | 44742.9918 | 49.7971
|  |  | 44742.9918 | 49.7972
|  |  | 44742.9918 | 49.7971
|  |  | 44742.9918 | 49.7971
|  |  | 44742.9918 | 49.7971
|  |  | 44742.9918 | 49.7971
|  |  | 44742.9918 | 49.7971
|  |  | 44742.9918 | 49.797
|  |  | 44742.9918 | 49.797
|  |  | 44742.9918 | 49.797
|  |  | 44742.9918 | 49.797
|  |  | 2022-06-30 23:48 | 49.797
|  |  | 44742.9918 | 49.797
|  |  | 44742.9918 | 49.7969
|  |  | 44742.9918 | 49.797
|  |  | 44742.9918 | 49.7969
|  |  | 44742.9918 | 49.7969
|  |  | 44742.9918 | 49.7969
|  |  | 44742.9918 | 49.7969
|  |  | 44742.9918 | 49.7969
|  |  | 44742.9918 | 49.7969
|  |  | 44742.9918 | 49.7969
|  |  | 44742.9918 | 49.7969
|  |  | 44742.9918 | 49.7969
|  |  | 44742.9918 | 49.7969
|  |  | 44742.9918 | 49.7968
|  |  | 44742.9918 | 49.7969
|  |  | 44742.9918 | 49.7968
|  |  | 44742.9918 | 49.7968
|  |  | 44742.9918 | 49.7967
|  |  | 44742.9918 | 49.7967
|  |  | 44742.9918 | 49.7967
|  |  | 44742.9918 | 49.7967
|  |  | 44742.9918 | 49.7967
|  |  | 44742.9918 | 49.7967
|  |  | 44742.9918 | 49.7967
|  |  | 44742.9918 | 49.7967
|  |  | 44742.9918 | 49.7968
|  |  | 44742.9918 | 49.7967
|  |  | 44742.9918 | 49.7967
|  |  | 44742.9918 | 49.7966
|  |  | 44742.9918 | 49.7966
|  |  | 44742.9918 | 49.7966
|  |  | 44742.9918 | 49.7965
|  |  | 44742.9918 | 49.7965
|  |  | 44742.9918 | 49.7965
|  |  | 44742.9918 | 49.7965
|  |  | 44742.9918 | 49.7964
|  |  | 44742.9918 | 49.7965
|  |  | 44742.9918 | 49.7965
|  |  | 44742.9918 | 49.7965
|  |  | 44742.9918 | 49.7965
|  |  | 44742.9918 | 49.7965
|  |  | 44742.9918 | 49.7964
|  |  | 44742.9918 | 49.7964
|  |  | 44742.9918 | 49.7963
|  |  | 44742.9918 | 49.7963
|  |  | 44742.9918 | 49.7962
|  |  | 44742.9918 | 49.7963
|  |  | 44742.9918 | 49.7962
|  |  | 44742.9918 | 49.7962
|  |  | 2022-06-30 23:48 | 49.7963
|  |  | 44742.9918 | 49.7963
|  |  | 44742.9918 | 49.7963
|  |  | 44742.9918 | 49.7963
|  |  | 44742.9918 | 49.7962
|  |  | 44742.9918 | 49.7962
|  |  | 44742.9918 | 49.7962
|  |  | 44742.9918 | 49.7962
|  |  | 44742.9918 | 49.7961
|  |  | 44742.9918 | 49.7962
|  |  | 44742.9918 | 49.7961
|  |  | 44742.9918 | 49.7961
|  |  | 44742.9918 | 49.7962
|  |  | 44742.9918 | 49.7962
|  |  | 44742.9918 | 49.7962
|  |  | 44742.9918 | 49.7963
|  |  | 44742.9918 | 49.7964
|  |  | 44742.9918 | 49.7964
|  |  | 44742.9918 | 49.7965
|  |  | 44742.9918 | 49.7965
|  |  | 44742.9918 | 49.7965
|  |  | 44742.9918 | 49.7965
|  |  | 44742.9918 | 49.7965
|  |  | 44742.9918 | 49.7965
|  |  | 44742.9918 | 49.7965
|  |  | 44742.9918 | 49.7964
|  |  | 44742.9918 | 49.7964
|  |  | 44742.9918 | 49.7964
|  |  | 44742.9918 | 49.7964
|  |  | 44742.9918 | 49.7964
|  |  | 44742.9918 | 49.7964
|  |  | 44742.9918 | 49.7965
|  |  | 44742.9918 | 49.7965
|  |  | 44742.9918 | 49.7965
|  |  | 44742.9918 | 49.7966
|  |  | 44742.9918 | 49.7966
|  |  | 44742.9918 | 49.7966
|  |  | 44742.9918 | 49.7966
|  |  | 44742.9918 | 49.7966
|  |  | 44742.9918 | 49.7966
|  |  | 44742.9918 | 49.7966
|  |  | 44742.9918 | 49.7966
|  |  | 44742.9918 | 49.7966
|  |  | 44742.9918 | 49.7966
|  |  | 44742.9918 | 49.7966
|  |  | 44742.9918 | 49.7966
|  |  | 44742.9918 | 49.7966
|  |  | 44742.9918 | 49.7966
|  |  | 44742.9918 | 49.7966
|  |  | 44742.9918 | 49.7966
|  |  | 2022-06-30 23:48 | 49.7967
|  |  | 44742.9918 | 49.7968
|  |  | 44742.9918 | 49.7968
|  |  | 44742.9918 | 49.7968
|  |  | 44742.9918 | 49.7969
|  |  | 44742.9918 | 49.7969
|  |  | 44742.9918 | 49.7969
|  |  | 44742.9918 | 49.7969
|  |  | 44742.9918 | 49.7969
|  |  | 44742.9918 | 49.797
|  |  | 44742.9918 | 49.797
|  |  | 44742.9918 | 49.797
|  |  | 44742.9918 | 49.797
|  |  | 44742.9918 | 49.797
|  |  | 44742.9918 | 49.7969
|  |  | 44742.9918 | 49.797
|  |  | 44742.9918 | 49.7969
|  |  | 44742.9918 | 49.7969
|  |  | 44742.9918 | 49.7969
|  |  | 44742.9918 | 49.7969
|  |  | 44742.9918 | 49.7969
|  |  | 44742.9918 | 49.7969
|  |  | 44742.9918 | 49.7969
|  |  | 44742.9918 | 49.797
|  |  | 44742.9918 | 49.797
|  |  | 44742.9918 | 49.797
|  |  | 44742.9918 | 49.7971
|  |  | 44742.9918 | 49.7971
|  |  | 44742.9918 | 49.7972
|  |  | 44742.9918 | 49.7972
|  |  | 44742.9918 | 49.7972
|  |  | 44742.9918 | 49.7972
|  |  | 44742.9918 | 49.7973
|  |  | 44742.9918 | 49.7974
|  |  | 44742.9918 | 49.7974
|  |  | 44742.9918 | 49.7975
|  |  | 44742.9918 | 49.7975
|  |  | 44742.9918 | 49.7976
|  |  | 44742.9918 | 49.7977
|  |  | 44742.9918 | 49.7977
|  |  | 44742.9918 | 49.7978
|  |  | 44742.9918 | 49.7978
|  |  | 44742.9918 | 49.7978
|  |  | 44742.9918 | 49.7979
|  |  | 44742.9918 | 49.7979
|  |  | 44742.9918 | 49.798
|  |  | 44742.9918 | 49.798
|  |  | 44742.9918 | 49.7981
|  |  | 44742.9918 | 49.7981
|  |  | 44742.9918 | 49.7982
|  |  | 2022-06-30 23:48 | 49.7983
|  |  | 44742.9918 | 49.7983
|  |  | 44742.9918 | 49.7984
|  |  | 44742.9918 | 49.7985
|  |  | 44742.9918 | 49.7985
|  |  | 44742.9918 | 49.7986
|  |  | 44742.9918 | 49.7986
|  |  | 44742.9918 | 49.7986
|  |  | 44742.9918 | 49.7987
|  |  | 44742.9918 | 49.7987
|  |  | 44742.9918 | 49.7987
|  |  | 44742.9918 | 49.7987
|  |  | 44742.9918 | 49.7987
|  |  | 44742.9918 | 49.7987
|  |  | 44742.9918 | 49.7987
|  |  | 44742.9918 | 49.7988
|  |  | 44742.9918 | 49.7989
|  |  | 44742.9918 | 49.799
|  |  | 44742.9918 | 49.7991
|  |  | 44742.9918 | 49.7991
|  |  | 44742.9918 | 49.7992
|  |  | 44742.9918 | 49.7992
|  |  | 44742.9918 | 49.7992
|  |  | 44742.9918 | 49.7992
|  |  | 44742.9918 | 49.7993
|  |  | 44742.9918 | 49.7994
|  |  | 44742.9918 | 49.7994
|  |  | 44742.9918 | 49.7995
|  |  | 44742.9918 | 49.7995
|  |  | 44742.9918 | 49.7996
|  |  | 44742.9918 | 49.7997
|  |  | 44742.9918 | 49.7998
|  |  | 44742.9918 | 49.7999
|  |  | 44742.9918 | 49.7999
|  |  | 44742.9918 | 49.7998
|  |  | 44742.9918 | 49.7999
|  |  | 44742.9918 | 49.7999
|  |  | 44742.9918 | 49.7999
|  |  | 44742.9918 | 49.7999
|  |  | 44742.9918 | 49.8
|  |  | 44742.9918 | 49.8
|  |  | 44742.9918 | 49.8
|  |  | 44742.9918 | 49.8
|  |  | 44742.9918 | 49.8
|  |  | 44742.9918 | 49.8001
|  |  | 44742.9918 | 49.8001
|  |  | 44742.9918 | 49.8002
|  |  | 44742.9918 | 49.8003
|  |  | 44742.9918 | 49.8003
|  |  | 44742.9918 | 49.8004
|  |  | 2022-06-30 23:48 | 49.8005
|  |  | 44742.9918 | 49.8006
|  |  | 44742.9918 | 49.8007
|  |  | 44742.9918 | 49.8008
|  |  | 44742.9918 | 49.8008
|  |  | 44742.9918 | 49.8009
|  |  | 44742.9918 | 49.8009
|  |  | 44742.9918 | 49.8009
|  |  | 44742.9918 | 49.801
|  |  | 44742.9918 | 49.801
|  |  | 44742.9918 | 49.801
|  |  | 44742.9918 | 49.8011
|  |  | 44742.9918 | 49.8011
|  |  | 44742.9918 | 49.8012
|  |  | 44742.9918 | 49.8012
|  |  | 44742.9918 | 49.8013
|  |  | 44742.9918 | 49.8013
|  |  | 44742.9918 | 49.8014
|  |  | 44742.9918 | 49.8015
|  |  | 44742.9918 | 49.8016
|  |  | 44742.9918 | 49.8016
|  |  | 44742.9918 | 49.8017
|  |  | 44742.9918 | 49.8018
|  |  | 44742.9918 | 49.8018
|  |  | 44742.9918 | 49.8019
|  |  | 44742.9918 | 49.802
|  |  | 44742.9918 | 49.802
|  |  | 44742.9918 | 49.8021
|  |  | 44742.9918 | 49.8021
|  |  | 44742.9918 | 49.8022
|  |  | 44742.9918 | 49.8022
|  |  | 44742.9918 | 49.8023
|  |  | 44742.9918 | 49.8024
|  |  | 44742.9918 | 49.8024
|  |  | 44742.9918 | 49.8025
|  |  | 44742.9918 | 49.8026
|  |  | 44742.9918 | 49.8026
|  |  | 44742.9918 | 49.8027
|  |  | 44742.9918 | 49.8027
|  |  | 44742.9918 | 49.8028
|  |  | 44742.9918 | 49.8028
|  |  | 44742.9918 | 49.8029
|  |  | 44742.9918 | 49.8029
|  |  | 44742.9918 | 49.803
|  |  | 44742.9918 | 49.8031
|  |  | 44742.9918 | 49.8032
|  |  | 44742.9918 | 49.8032
|  |  | 44742.9918 | 49.8032
|  |  | 44742.9918 | 49.8033
|  |  | 44742.9918 | 49.8033
|  |  | 2022-06-30 23:48 | 49.8033