DISTRIBUTED RESTART – DRAFT LEGAL TEXT

EXTRACTS FROM GRID CODE

DATED 25 March 2022

Extracts from Glossary and Definitions

| Anchor Generator | A Generator who has a Restoration Service Contract in respect of any Anchor Plant and in this context is a Restoration Service Provider. |  |
| --- | --- | --- |
| Anchor DC Converter | An Embedded DC Converter with an Anchor Plant Capability. |  |
| Anchor DC Converter Owner | A DC Converter owner who owns and is responsible for an Anchor DC Converter. |  |
| Anchor DC Converter Test | A test carried out by an Anchor DC Converter Owner at an Anchor DC Converter while the Anchor DC Converter is disconnected from all external electrical power supplies from the Total System. |  |
| Anchor Power Station | An Embedded Power Station comprising Anchor Plant. |  |
| Anchor Power Station Test | A test carried out by an Anchor Generator at an Anchor Power Station while that Anchor Power Station is disconnected from all external electrical power supplies from the Network Operator’s System. |  |
| Anchor Generating Unit | An Embedded Generating Unit with Anchor Plant Capability. |  |
| Anchor Generating Unit Test | A test carried out on an Anchor Generating Unit or a Power Generating Module, as the case may be, at an Anchor Power Station while the Anchor Power Station remains energised from the Network Operator’s System. |  |
| Anchor HVDC System | An Embedded HVDC System with Anchor Plant Capability. |  |
| Anchor HVDC System Owner | An HVDC System Owner who owns and is responsible for an Anchor HVDC System. |  |
| Anchor HVDC System Test | A Test carried out by an Anchor HVDC System Owner with an Anchor HVDC System while the Anchor HVDC System is not energised from the Network Operator’s System. |  |
| Anchor Plant | Anchor Plant is Plant which has Anchor Plant Capabilities. |  |
| Anchor Plant Capability | Is the ability of a Plant to Start-Up from Shutdown and to energise part of the Network Operator’s System forming part of a Distribution Restoration Zone within 8 hours of being instructed to do so, without an external electrical power supply from the Network Operator’s System. |  |
| Anchor Plant Owner | The owner and/or operator who has a Restoration Service Contract in respect of any Anchor Plant the Generator owns and in this context is a Restoration Service Provider. |  |
| Anchor Plant Test | A test conducted on an Anchor Plant to confirm it is capable of meeting the requirements of the relevant Distribution Restoration Contract. |  |
| Apparatus | Other than in OC8, means all equipment in which electrical conductors are used, supported or of which they may form a part. It includes Users’ equipment which imposes Demand on the System. In OC8, it means High Voltage electrical circuits forming part of a System on which Safety Precautions may be applied to allow work and/or testing to be carried out on a System. |  |
| Auxiliary Energy Supplies | An electricity supply (which could be derived from an Auxiliary Diesel Engine or Auxiliary Gas Turbine or other source of energy) that is necessary to power the auxiliary and ancillary equipment on which a Power Generating Module or HVDC System or DC Converter or other item of Plant relies for it to be capable of generating Active or Reactive Power and which is generally supplied via a Unit Board or Station Board, or equivalent. Auxiliary Energy Supplies must be able to start without an electrical power supply from outside the Power Station or HVDC System or HVDC Converter or DC Converter Station, or other Restoration Service Providers site, within which it is situated. Auxiliary Energy Supplies do not include the mains-independent light current supplies necessary to operate Critical Tools and Facilities. |  |
| Black Start Capability | In the case of a Black Start Station, is the ability for at least one of its Gensets to Start-Up from Shutdown and to energise a part of the Total System and be Synchronised to the System upon instruction from The Company, within two hours, without an external electrical power supply. In the case of a Black Start HVDC System is the ability of an HVDC System to Start-Up from Shutdown and to energise a part of the Total System and be Synchronised to the System upon instruction from The Company, within two hours, without an external electrical power supply from the Total System. |  |
| Black Start Contract | An agreement between a Black Start Service Provider and The Company under which the Black Start Service Provider provides Black Start Capability and other associated services. |  |
| Black Start HVDC System | An HVDC System or DC Converter Station which are registered, pursuant to the Bilateral Agreement with a User, as having a Black Start Capability. |  |
| Black Start HVDC Test | A Black Start Test carried out by an HVDC System Owner or DC Converter Station Owner with a Black Start HVDC System while the Black Start HVDC System is disconnected from all external electrical power supplies from the Total System. |  |
| Black Start Service Provider | A Generator with a Black Start Station or an HVDC System Owner or DC Converter Station Owner with a Black Start HVDC System. |  |
| Black Start Stations | Power Stations which are registered, pursuant to the Bilateral Agreement with a User, as having a Black Start Capability. |  |
| Black Start Station Test | A Black Start Test carried out by a Generator with a Black Start Station while the Black Start Station is disconnected from all external electrical power supplies from the Total System. |  |
| Black Start Test | A Black Start Test carried out by a Black Start Service Provider on the instructions of The Company, in order to demonstrate that a Black Start Station or a Black Start HVDC System has a Black Start Capability. For the avoidance of doubt, a Black Start Test could comprise a Black Start Station Test, a Black Start Unit Test or Black Start HVDC Test. |  |
| Black Start Unit Test | A Black Start Test carried out on a Generating Unit or a CCGT Unit or a Power Generating Module, as the case may be, at a Black Start Station while the Black Start Station remains energised from an external alternating current electrical supply. |  |
| Block Loading Capability | The incremental Active Power steps, from no load to Rated MW, which a Generating Unit or Power Generating Module or Power Park Module or HVDC System (including Anchor Plant and Plant owned and operated by a Restoration Service Provider) can instantaneously supply without causing it to trip or go outside the Frequency range of 47.5 – 52Hz assuming the Plant is initially operating at a nominal System Frequency of 50Hz (or an otherwise agreed Frequency range). The time between each incremental step shall also be provided. |  |
| De-synchronised Island Procedure | Has the meaning set out in OC9.5.4. |  |
| De-synchronised Island(s) | Has the meaning set out in OC9.5.1(a). |  |
| Distribution Restoration Zone | Part of a Network Operator’s System which is capable of being energised by Anchor Plant following a Total System Shutdown or Partial System Shutdown. The Distribution Restoration Zone shall contain Anchor Plant and may also include one or more Restoration Service Providers’ Plant and Demand. The Distribution Restoration Zone is primarily comprised of part of the Network Operator’s System, but may include relevant parts of the National Electricity Transmission System as provided for in the Distribution Restoration Zone Plan. |  |
| Distribution Restoration Contract | An agreement between an Anchor Plant Owner or other Restoration Service Provider and The Company and a Network Operator under which the Restoration Service Provider, on instruction, can provide services to energise and/or contribute to the establishment of a Distribution Restoration Zone. |
| Distribution Restoration Zone Control System | A mains-independent automatic control and supervisory system which assesses the status and operational conditions of a Network Operator’s System for the purposes of operating Anchor Plant and Restoration Service Providers’ Plant and/or modulating Restoration Service Providers’ Demand in addition to operating items of the Network Operator’s Plant and Apparatus for the purposes of establishing and operating a Distribution Restoration Zone. |  |
| Distribution Restoration Zone Plan | A plan produced under OC9.4.7.5.2 detailing the agreed method and procedure by which a Network Operator or Distribution Restoration Zone Control System will instruct an Anchor Plant Owner to energise part of the Network Operator’s System together with other Restoration Service Providers to meet blocks of local Demand so as to form a Power Island. A Distribution Restoration Zone Plan is distinct from and falls outside the provisions of a Local Joint Restoration Plan. |  |
| Local Joint Restoration Plan | A plan produced under OC9.4.7.5.1 detailing the agreed method and procedure by which a Black Start Service Provider will energise part of the Total System and meet complementary blocks of local Demand so as to form a Power Island. In Scotland, the plan may also: cover more than one Black Start Service Provider; including Gensets other than those at a Black Start Station and cover the creation of one or more Power Islands. AA Local Joint Restoration Plan is distinct from and falls outside the provisions of a. Distribution Restoration Zone Plan. |  |
| Part 1 System Ancillary Services | Ancillary Services which are required for System reasons and which must be provided by Users in accordance with the Connection Conditions or European Connection Conditions. An exhaustive list of Part 1 System Ancillary Services is included in that part of CC.8.1 or ECC.8.1 headed Part 1. |  |
| Power Island | Generating Units at one or more Power Stations, and/or HVDC Systems and/or DC Converters, together with complementary local Demand, and is connected to a section of network that is disconnected from, and out of Synchronism with, the rest of the Total System. |  |
| Quick Resynchronisation Capability | The capability of a Type C or Type D Power Generating Module as defined in ECC.6.3.5.6. For the avoidance of doubt, this requirement is only mandatory for EU Code Generators who own or operate a Type C or Type D Power Generating Module, but does not preclude owners of other generation Plant electing to provide the capability. |  |
| Quick Resynchronisation Unit Test | A test undertaken on a Generating Unit forming part of a Type C or Type D Power Generating Module as detailed in OC5.7.1, OC5.7.3 and OC5.7.4 necessary to demonstrate its Quick Resynchronisation Capability. |  |
| Restoration Service Provider | A party with a legal or contractual obligation to provide a service contributing to one or several measures of Grid Code (as described in the System Restoration Plan) which contribute to restoring parts of the Total System following a Total Shutdown or Partial Shutdown. For the avoidance of doubt this shall include any party contributing to either a Local Joint Restoration Plan or a Distribution Restoration Zone Plan. In the case of a Distribution Restoration Zone Plan, a Restoration Service Provider includes Anchor Plant Owners and other parties who are contracted to provide services from their Plant and Apparatus used to establish a Distribution Restoration Zone. |  |
| Shutdown | In the case of a Generating Unit is the condition of a Generating Unit where the generator rotor is at rest or on barring , or equivalent. In the case of an HVDC System or DC Converter Station, is the condition of an HVDC System or DC Converter Station where the HVDC System or DC Converter Station is de-energized and therefore not importing or exporting Apparent Power to or from the Total System. In the case of Auxiliaries, the state where they are de-energized and not capable of fulfilling their function until restarted or resupplied. |  |
| Target Frequency | That Frequency determined by The Company, in its reasonable opinion, as the desired operating Frequency of the Total System or of a relevant Power Island. This will normally be 50.00Hz plus or minus 0.05Hz, except in exceptional circumstances as determined by The Company, in its reasonable opinion, when this may be 49.90 or 50.10Hz. An example of exceptional circumstances may be difficulties caused in operating the System during disputes affecting fuel supplies or following a Total Shutdown or Partial Shutdown where Power Islands are established, and each Power Island has its own unique Frequency. |  |

Extracts from Planning Code

PC.A.2.5.5.1	 For each Generating Unit (including Synchronous Generating Units forming part of a Synchronous Power Generating Module) with one or more associated Unit Transformers, the Generator, or the Network Operator in respect of Embedded Medium Power Stations not subject to a Bilateral Agreement and Embedded DC Converter Stations not subject to a Bilateral Agreement and Embedded HVDC Systems within such Network Operator’s System is required to provide values for the contribution of the Power Station Auxiliaries (including Auxiliary Energy Supplies) to the fault current flowing through the Unit Transformer(s).

………..

PC.A.5.7	Black Start Related Information (excluding Distribution Restoration Zone information formulated as part of a Distribution Restoration Zone Plan)

Data relating to Anchor Plant and Plant and Apparatus owned and/or operated by Restoration Service Providers, as well as data relating to Restoration Service Providers’ Demand, forming part of a Distribution Restoration Zone, should be supplied in accordance with the requirements of PC.A.5.8

Data identified under this section PC.A.5.7 must be submitted as required under PC.A.1.2.  This information may also be requested by The Company during a Black Start and should be provided by Generators. HVDC System Owners and DC Converter Station Owners - where reasonably possible.  For the avoidance of doubt, Generators in this section PC.A.5.7 means Generators only in respect of their Large Power Stations.

The following data items/text must be supplied, by each Generator and HVDC System Converter Station Owner – to The Company. In the case of Generators, the data supplied should be with respect to each BM Unit at a Large Power Station.  For the avoidance of doubt, the data required under PC.A.5.7 (a) and (b) below, does i) not need to be supplied in respect of Generators that are contracted to provide a Black Start Capability and ii), the data only needs to be supplied in respect of the BM Unit at a Large Power Station and does not need to include Generating Unit data;

(a)	The expected time for each BM Unit to be Synchronised following a Total Shutdown or Partial Shutdown.  The assessment should include the Power Station’s or HVDC System’s or DC Converter Station’s ability to re-synchronise all BM Units, if all were running immediately prior to the Total Shutdown or Partial Shutdown.  Additionally, this should highlight any specific issues (i.e. those that would impact on the BM Unit’s time to be Synchronised) that may arise, as time progresses without external supplies being restored.

(b)	Block Loading Capability.  This should be provided in either graphical or tabular format showing the estimated block loading capability from 0MW to Registered Capacity.  Any particular Active Power loading points at which the BM Unit should be operated until further changes in output can be accommodated should also be identified.  The data of each BM Unit should be provided for the condition of a Generating Unit (which is considered as both a ‘hot’ unit (run prior to the Shutdown) and cold unit (not run for 48 hours or more prior to the Shutdown)) that was Synchronised just prior to the Total Shutdown or Partial Shutdown. In the case of an HVDC System or DC Converter Station, data should be provided 	when the HVDC System or DC Converter Station has been considered to have run immediately before the Total Shutdown or Partial Shutdown and equally when the HVDC System or DC Converter Station has been considered to have been Shutdown for a period of 48 hours or more. The block loading assessment should be done against a frequency variation of 49.5Hz – 50.5Hz.

PC.A.5.8	Distributed Restoration Zone Related Information (excluding Black Start information formulated as part of a Local Joint Restoration Plan)

Data identified under this section PC.A.5.8 shall be submitted as required under PC.A.1.2.by Restoration Service Providers party to a Distribution Restoration Zone Plan to the relevant Network Operator annually so that the Network Operator can provide this to The Company as required under PC.A.1.2.  This information may also be requested by The Company during Black Start and should be provided by Network Operators where reasonably practicable.  Restoration Service Providers party to a Distribution Restoration Zone Plan shall, where reasonably practicable, submit the relevant information to the Network Operator who shall then supply the relevant information to The Company.

The following data items/text shall be supplied, by each Network Operator in respect of each Distribution Restoration Zone.

- The expected time for each Anchor Plant Owner and Restoration Service Provider’s Plant to be Synchronised following a Total Shutdown or Partial Shutdown.  The assessment should include the Anchor Plant Owner’s and Restoration Service Provider’s ability to re-synchronise all their Plant, if all were running immediately prior to the Total Shutdown or Partial Shutdown.  Additionally, the data and supporting text should highlight any specific issues (eg those that would affect the time before which the Anchor Plant and Restoration Service Provider’s Plant could be Synchronised) that may arise as time progresses from Shutdown without external supplies being restored.

- Block Loading Capability.  This should be provided in either graphical or tabular format showing the estimated Block Loading Capability from 0MW to Registered Capacity or Maximum Capacity as the case may be.  Any particular Active Power loading points at which the Anchor Plant or Restoration Service Provider’s Plant should be operated until further changes in output can be accommodated should also be identified.  The data of each Anchor Plant and Restoration Service Provider’s Plant forming part of a Distribution Restoration Zone should be provided for the conditions of the Anchor Plant or Restoration Service Provider’s Plant both as ‘hot’ units (operating immediately prior to, and at the point of, Shutdown) and cold units (not operated for 48 hours or more prior to Shutdown).  In the case of an Anchor HVDC System or Anchor DC Converter, data should be provided when the HVDC System or DC Converter has been operated immediately before the Total Shutdown or Partial Shutdown and also when the Embedded HVDC System or Embedded DC Converter has been considered to have been Shutdown for a period of 48 hours or more.  The block loading assessment should be done against a frequency variation of 49.5Hz – 50.5Hz assuming the Plant is initially operating at a nominal System Frequency of 50Hz.

Extracts from Connection Conditions

………………..

CC.3 SCOPE

CC.3.1 The CC applies to The Company and to GB Code Users, which in the CC means:

(a) 	GB Generators (other than those which only have Embedded Small Power Stations), including those undertaking OTSDUW;

(b) 	Network Operators;

(c) 	Non-Embedded Customers

(d) 	DC Converter Station owners; and

(e) 	BM Participants and Externally Interconnected System Operators in respect of CC.6.5 only.

(f)	Restoration Service Providers other than any already included in (a) to (e) above who provide services in respect of CC.8.1 in relation to Distribution Restoration Zones only.

………………..

CC.6.3.5	It is an essential requirement that the National Electricity Transmission System must be able to undertake Black Start.  This will be achieved by agreeing a Black Start Capability with a number of strategically located Restoration Service Providers.  In the case of Restoration Service Providers who are party to a Distribution Restoration Zone Plan, The Company shall agree the requirements with the relevant Network Operator and Restoration Service Providers in a Distribution Restoration Contract.

………………...

CC.8	ANCILLARY SERVICES

CC.8.1	System Ancillary Services

The CC contain requirements for the capability for certain Ancillary Services, which are needed for System reasons ("System Ancillary Services").  There follows a list of these System Ancillary Services, together with the paragraph number of the CC (or other part of the Grid Code) in which the minimum capability is required or referred to.  The list is divided into two categories:  Part 1 lists the System Ancillary Services which

(a)	GB Generators in respect of Large Power Stations are obliged to provide (except GB Generators in respect of Large Power Stations which have a Registered Capacity of less than 50MW and comprise Power Park Modules); and,

(b)	GB Generators in respect of Large Power Stations with a Registered Capacity of less than 50MW and comprise Power Park Modules are obliged to provide in respect of Reactive Power only; and,

(c)	DC Converter Station owners are obliged to have the capability to supply; and

(d)	GB Generators in respect of Medium Power Stations (except Embedded Medium Power Stations) are obliged to provide in respect of Reactive Power only.

Part 2 lists the System Ancillary Services which GB Generators or Restoration Service Providers will provide only if agreement to provide them is reached with The Company (and the Network Operator in the case where a Restoration Service Provider is party to a Distribution Restoration Zone Plan).

Part 1

(a)	Reactive Power supplied (in accordance with CC.6.3.2) otherwise than by means of synchronous or static compensators (except in the case of a Power Park Module where synchronous or static compensators within the Power Park Module may be used to provide Reactive Power)

(b)	Frequency Control by means of Frequency sensitive generation - CC.6.3.7 and BC3.5.1

Part 2

(c)	Frequency Control by means of Fast Start - CC.6.3.14

(d)	Black Start CC.6.3.5

(e)	System to Generator Operational Intertripping

(f)	Services provided by Restoration Service Providers.

CC.8.2	Commercial Ancillary Services

Other Ancillary Services are also utilised by The Company in operating the Total System if these have been agreed to be provided by a GB Code User (or other person) under an Ancillary Services Agreement or under a Bilateral Agreement, with payment being dealt with under an Ancillary Services Agreement or in the case of Externally Interconnected System Operators or Interconnector Users, under any other agreement (and in the case of Externally Interconnected System Operators and Interconnector Users includes ancillary services equivalent to or similar to System Ancillary Services) ("Commercial Ancillary Services").  The capability for these Commercial Ancillary Services is set out in the relevant Ancillary Services Agreement or Bilateral Agreement (as the case may be).

……………

Extracts from European Connection Conditions

……………

ECC.3 SCOPE

ECC.3.1 	The ECC applies to The Company and to Users, which in the ECC means:

(a) 	EU Generators (other than those which only have Embedded Small Power Stations), including those undertaking OTSDUW including Power Generating Modules, and DC Connected Power Park Modules. For the avoidance of doubt, Electricity Storage Modules are included within the definition of Power Generating Modules for which the requirements of the ECC would be equally applicable.

(b)	Network Operators but only in respect of:-

(i) 	Network Operators who are EU Code Users

(ii) 	Network Operators who only have EU Grid Supply Points

(iii) 	Embedded Medium Power Stations not subject to a Bilateral Agreement as provided for in ECC.3.2, ECC.3.3, EC3.4, EC3.5, ECC5.1, ECC.6.4.4 and ECA.3.4;

(iv) 	Notwithstanding the requirements of ECC3.1(b)(i)(ii) and (iii) , Network Operators who own and/or operate EU Grid Supply Points, are only required to satisfy the requirements of this ECC in relation to each EU Grid Supply Point. Network Operators in respect of all other Grid Supply Points should continue to satisfy the requirements as specified in the CCs.

(c) 	Non-Embedded Customers who are also EU Code Users;

(d) 	HVDC System Owners who are also EU Code Users; and

(e) 	BM Participants and Externally Interconnected System Operators who are also EU Code Users in respect of ECC.6.5 only.

(f)	Restoration Service Providers other than any already included in (a) to (e) above who provide services in respect of ECC.6.3.5 and ECC.8 in relation to Distribution Restoration Zones only

……………………

ECC.6.3.5	BLACK START

ECC.6.3.5.1		Black Start Capability is not a mandatory requirement, however EU Code Users, or Restoration Service Providers, may wish to notify The Company of their ability to provide a Black Start facility and the cost of the service. The Company will then consider whether it wishes to contract with the EU Code User for the provision of a Black Start service which would be specified via a Black Start Contract oror, in conjunction with the Network Operator, a Distribution Restoration Contract. Where an EU Code User does not offer to provide a cost for the provision of a Black Start Capability, The Company may make such a request if it considers System security to be at risk due to a lack of Black Start capability.

ECC.6.3.5.2	It is an essential requirement that The Company must be able to undertake Black Start.  This will be achieved by agreeing Black Start Capability at a number of strategically located Power Stations and HVDC Systems. For each Power Station or HVDC System, The Company will state in the Bilateral Agreement whether or not a Black Start Capability is required.  In the case of Restoration Service Providers who are party to a Distribution Restoration Zone Plan, The Company shall agree the requirements with the relevant Network Operator and Restoration Service Providers in a Distribution Restoration Contract.

ECC.6.3.5.3	Where an EU Code User has entered into a Black Start Contract to provide Black Start Capability or a Distribution Restoration Contract to provide Anchor Plant Capability in respect of a Type C Power Generating Module or Type D Power Generating Module (including DC Connected Power Park Modules) the following requirements shall apply.

- The Power-Generating Module or DC Connected Power Park Module shall be capable of starting from shutdown without any external electrical energy supply within a time frame agreed with The Company in the Black Start Contract or agreed with The Company and the Network Operator in a Distribution Restoration Contract.

- Each Power Generating Module or DC Connected Power Park Module shall be able to synchronise within the frequency limits defined in ECC.6.1. and, where applicable, voltage limits specified in ECC.6.1.4;

- The Power Generating Module or DC Connected Power Park Module shall be capable of energising an unenergised part of the System.

- The Power-Generating Module or DC Connected Power Park Module shall be capable of automatically regulating dips in voltage caused by connection of demand;

- The Power Generating Module or DC Connected Power Park Module shall:

        - be capable of Block Loading Capability,

        - be capable of operating in LFSM-O and LFSM-U, as specified in ECC.6.3.7.1 and ECC.6.3.7.2

        - control Frequency in case of overfrequency and underfrequency within the whole Active Power output range between the Minimum Regulating Level and Maximum Capacity as well as at houseload operation levels

        - be capable of parallel operation together with other Power Generating Modules including DC Connected Power Park Modules within an isolated part of the Total System that is still supplying Customers, and controlling voltage automatically during the system restoration phase.

ECC.6.3.5.4	Each HVDC System or Remote End HVDC Converter Station which has a Black Start Capability shall be capable of energising the busbar of an AC substation to which another HVDC Converter Station is connected.  The timeframe after shutdown of the HVDC System prior to energisation of the AC substation shall be pursuant to the terms of the Black Start Contract.  The HVDC System shall be able to synchronise within the Frequency limits defined in ECC.6.1.2.1.2 and voltage limits defined in ECC.6.1.4.1 unless otherwise specified in the Black Start Contract.  Wider Frequency and voltage ranges can be specified in the Black Start Contract in order to restore System security.

ECC.6.3.5.5	With regard to the capability to take part in operation of an isolated part of the Total System that is still supplying Customers:

- Power Generating Modules including DC Connected Power Park Modules shall be capable of taking part in island operation if specified by The Company;

- the Frequency limits for island operation shall be those specified in ECC.6.1.2;

- the voltage limits for island operation shall be those defined in ECC.6.1.4;

- Power Generating Modules including DC Connected Power Park Modules shall be able to operate in Frequency Sensitive Mode during island operation, as specified in ECC.6.3.7.3. In the event of a power surplus, Power Generating Modules including DC Connected Power Park Modules shall be capable of reducing the Active Power output from a previous operating point to any new operating point within the Power Generating Module Performance Chart. Power Generating Modules including DC Connected Power Park Modules shall be capable of reducing Active Power output as much as inherently technically feasible, but to at least 55 % of Maximum Capacity;

- The method for detecting a change from interconnected system operation to island operation shall be agreed between the EU Generator, The Company, the Relevant Transmission Licensee. The agreed method of detection must not rely solely on The Company, Relevant Transmission Licensee’s switchgear position signals; anc

- Power Generating Modules including DC Connected Power Park Modules shall be able to operate in LFSM-O and LFSM-U during island operation, as specified in ECC.6.3.7.1 and ECC.6.3.7.2.

ECC.6.3.5.6	 	With regard to quick re-synchronisation capability:

(i)		In case of disconnection of the Power Generating Module including DC Connected Power Park Modules from the System, the Power Generating Module shall be capable of quick re-synchronisation in line with the Protection strategy agreed between The Company and/or Network Operator  in co-ordination with the Relevant Transmission Licensee and the Generator;

- A Power Generating Module including a DC Connected Power Park Module with a minimum re-synchronisation time greater than 15 minutes after its disconnection from any external power supply must be capable of Houseload Operation from any operating point on its Power Generating Module Performance Chart. In this case, the identification of Houseload Operation must not be based solely on the Total System’s switchgear position signals;

- Power Generating Modules including DC Connected Power Park Modules shall be capable of Houseload Operation, irrespective of any auxiliary connection to the Total System. The minimum operation time shall be specified by The Company, taking into consideration the specific characteristics of prime mover technology.

…………………

ECC.8	ANCILLARY SERVICES

ECC.8.1	System Ancillary Services

The ECC contain requirements for the capability for certain Ancillary Services, which are needed for System reasons ("System Ancillary Services").  There follows a list of these System Ancillary Services, together with the paragraph number of the ECC (or other part of the Grid Code) in which the minimum capability is required or referred to.  The list is divided into two categories:  Part 1 lists the System Ancillary Services which

(a)	Generators in respect of Type C and Type D Power Generating Modules (including DC Connected Power Park Modules and Electricity Storage Modules) are obliged to provide; and,

(b)	HVDC System Owners are obliged to have the capability to supply;

(c)	EU Generators in respect of Medium Power Stations (except Embedded Medium Power Stations) are obliged to provide in respect of Reactive Power only:

and Part 2 lists the System Ancillary Services which EU Generators or Restoration Service Providers will provide only if agreement to provide them is reached with The Company:

Part 1

(a)	Reactive Power supplied (in accordance with ECC.6.3.2)

(b)	Frequency Control by means of Frequency sensitive generation - ECC.6.3.7 and BC3.5.1

Part 2

(c)	Frequency Control by means of Fast Start - ECC.6.3.14

(d)	Black Start - ECC.6.3.5

(e)	System to Generator Operational Intertripping

(f)	Services provided by Restoration Service Providers.

ECC.8.2	Commercial Ancillary Services

Other Ancillary Services are also utilised by The Company in operating the Total System if these have been agreed to be provided by a User (or other person) under an Ancillary Services Agreement or under a Bilateral Agreement, with payment being dealt with under an Ancillary Services Agreement or in the case of Externally Interconnected System Operators or Interconnector Users, under any other agreement (and in the case of Externally Interconnected System Operators and Interconnector Users includes ancillary services equivalent to or similar to System Ancillary Services) ("Commercial Ancillary Services").  The capability for these Commercial Ancillary Services is set out in the relevant Ancillary Services Agreement or Bilateral Agreement (as the case may be).

…………………

Extracts from Operating Code 5

OC5.1	INTRODUCTION

Operating Code No. 5 ("OC5") specifies the procedures to be followed by The Company in carrying out:

(a)	monitoring

(i)	of BM Units against their expected input or output;

(ii)	of compliance by Users with the CC or ECC as applicable and in the case of response to Frequency, BC3; and

(iii)	of the provision by Users of Ancillary Services which they are required or have agreed to provide; and

(b)	the following tests (which are subject to System conditions prevailing on the day):

(i)	tests on Gensets, CCGT Modules, Power Generating Modules, Power Park Modules, DC Converters, HVDC Equipment, OTSUA (prior to the OTSUA Transfer Time) and Generating Units (excluding Power Park Units) to test that they have the capability to comply with the CC and ECC,  and in the case of response to Frequency, BC3 and to provide the Ancillary Services that they are either required or have agreed to provide;

(ii)	tests on BM Units, to ensure that the BM Units are available in accordance with their submitted Export and Import Limits and Dynamic Parameters.

The tests specified in OC5.7 include the procedures relating to Black Start Tests and procedures relating to testing Restoration Service Providers’ Plant and Apparatus in respect of Distribution Restoration Zones.

OC5 also specifies in OC5.8 the procedures which apply to the monitoring and testing of Embedded Medium Power Stations not subject to a Bilateral Agreement and Embedded DC Converter Stations (or Embedded HVDC Equipment) not subject to a Bilateral Agreement.

In respect of a Cascade Hydro Scheme the provisions of OC5 shall be applied as follows:

(a)	in respect of the BM Unit for the Cascade Hydro Scheme the parameters referred to at OC5.4.1 (a) and (c) in respect of Commercial Ancillary Services will be monitored and tested;

(b)	in respect of each Genset forming part of the Cascade Hydro Scheme the parameters referred to at OC5.4.1 (a), (b) and (c) will be tested and monitored.  In respect of OC5.4.1 (a) the performance of the Gensets will be tested and monitored against their expected input or output derived from the data submitted under BC1.4.2(a)(2).  Where necessary to give effect to the requirements for Cascade Hydro Schemes in the following provisions of OC5 the term Genset will be read and construed in the place of BM Unit.

In respect of Embedded Exemptable Large Power Stations the provisions of OC5 shall be applied as follows:

(a)	where there is a BM Unit registered in the BSC in respect of Generating Units the provisions of OC5 shall apply as written;

(b)	in all other cases, in respect of each Power Generating Module, and/or Generating Unit and HVDC Equipment the parameters referred to at OC5.4.1(a), (b) and (c) will be tested and monitored.  In respect of OC5.4.1(a) the performance of the Power Generating Module and/or Generating Unit and HVDC Equipment will be tested and monitored against their expected input or output derived from the data submitted under BC1.4.2(a)(2).  Where necessary to give effect to the requirements for such Embedded Exemptable Large Power Stations in the provisions of OC5 the term Generating Unit will be read and construed in place of BM Unit.

OC5.2	OBJECTIVE

The objectives of OC5 are to establish:

(a)	that Users comply with the CC or ECC as applicable (including in the case of OTSUA prior to the OTSUA Transfer Time);

(b)	whether BM Units operate in accordance with their expected input or output derived from their Final Physical Notification Data and agreed Bid-Offer Acceptances issued under BC2;

(c)	whether each BM Unit is available as declared in accordance with its submitted Export and Import Limits and Dynamic Parameters; and

(d)	whether Generators, DC Converter Station owners, HVDC Equipment Owners and Suppliers can provide those Ancillary Services which they are either required or have agreed to provide.

In certain limited circumstances as specified in this OC5 the output of CCGT Units may be verified, namely the monitoring of the provision of Ancillary Services and the testing of Reactive Power and automatic Frequency Sensitive Operation.

OC5.3	SCOPE

OC5 applies to The Company and to Users, which in OC5 means:

(a)	Generators (including those undertaking OTSDUW);

(b)	Network Operators;

(c)	Non-Embedded Customers;

(d)	Suppliers; and

(e)	DC Converter Station owners or HVDC Equipment Owners.

OC5.4	MONITORING

OC5.4.1	Parameters to be monitored

The Company will monitor the performance of:

(a)	BM Units against their expected input or output derived from their Final Physical Notification Data and agreed Bid-Offer Acceptances issued under BC2;

(b)	compliance by Users with the CC or ECC as applicable; and

(c)	the provision by Users of Ancillary Services which they are required or have agreed to provide.

OC5.4.2	Procedure for Monitoring

OC5.4.2.1	In the event that a BM Unit fails persistently, in The Company's reasonable view, to follow, in any material respect, its expected input or output or a User fails persistently to comply with the CC or ECC as applicable and in the case of response to Frequency, BC3 or to provide the Ancillary Services it is required, or has agreed, to provide, The Company shall notify the relevant User giving details of the failure and of the monitoring that The Company has carried out.

OC5.4.2.2	The relevant User will, as soon as possible, provide The Company with an explanation of the reasons for the failure and details of the action that it proposes to take to:

(a)	enable the BM Unit to meet its expected input or output or to provide the Ancillary Services it is required or has agreed to provide, within a reasonable period, or

(b)	in the case of a Power Generating Module, Generating Unit (excluding a Power Park Unit), CCGT Module, Power Park Module, OTSUA (prior to the OTSUA Transfer Time), HVDC Equipment or DC Converter to comply with the CC or ECC as applicable and in the case of response to Frequency, BC3 or to provide the Ancillary Services it is required or has agreed to provide, within a reasonable period.

OC5.4.2.3	The Company and the User will then discuss the action the User proposes to take and will endeavour to reach agreement as to:

(a)	any short term operational measures necessary to protect other Users; and

(b)	the parameters which are to be submitted for the BM Unit and the effective date(s) for the application of the agreed parameters.

OC5.4.2.4	In the event that agreement cannot be reached within 10 days of notification of the failure by The Company to the User, The Company or the User shall be entitled to require a test, as set out in OC5.5 and OC5.6, to be carried out.

OC5.5	PROCEDURE FOR TESTING

OC5.5.1	The Company’s Instruction for Testing

OC5.5.1.1	The Company may at any time (although not normally more than twice in any calendar year in respect of any particular BM Unit) issue an instruction requiring a User to carry out a test, provided The Company has reasonable grounds of justification based upon:

(a)	a failure to agree arising from the process in CP.8.1 or ECP.8.1; or

(b)	monitoring carried out in accordance with OC5.4.2.

OC5.5.1.2	The test, referred to in OC5.5.1.1 and carried out at a time no sooner than 48 hours from the time that the instruction was issued, on any one or more of the User’s BM Units should only be to demonstrate that the relevant BM Unit:

(a)	if active in the Balancing Mechanism, meets the ability to operate in accordance with its submitted Export and Import Limits and Dynamic Parameters and achieve its expected input or output which has been monitored under OC5.4; and

(b)	meets the requirements of the paragraphs in the CC which are applicable to such BM Units; and

in the case of a BM Unit comprising a Generating Unit, a CCGT Module, a Power Park Module, a Power Generating Module, HVDC System or a DC Converter meets,

(c)	the requirements for operation in Frequency Sensitive Mode and compliance with the requirements for operation in Limited Frequency Sensitive Mode in accordance with CC.6.3.3, ECC.6.3.3, CC.6.3.7, ECC.6.3.7, BC3.5.2 and BC3.7.2; or

(d)	the terms of the applicable Bilateral Agreement agreed with the Generator to have a Fast Start Capability; or

(e)	the Reactive Power capability registered with The Company under OC2 which shall meet the requirements set out in CC.6.3.2 or ECC.6.3.2 as applicable.  In the case of a test on a Generating Unit within a CCGT Module the instruction need not identify the particular CCGT Unit within the CCGT Module which is to be tested, but instead may specify that a test is to be carried out on one of the CCGT Units within the CCGT Module.

OC5.5.1.3	(a)	The instruction referred to in OC5.5.1.1 may only be issued if the relevant User has submitted Export and Import Limits which notify that the relevant BM Unit is available in respect of the Operational Day current at the time at which the instruction is issued. The relevant User shall then be obliged to submit Export and Import Limits with a magnitude greater than zero for that BM Unit in respect of the time and the duration that the test is instructed to be carried out, unless that BM Unit would not then be available by reason of forced outage or Planned Outage expected prior to this instruction.

(b)	In the case of a CCGT Module the Export and Import Limits data must relate to the same CCGT Units which were included in respect of the Operational Day current at the time at which the instruction referred to in OC5.5.1.1 is issued and must include, in relation to each of the CCGT Units within the CCGT Module, details of the various data set out in BC1.A.1.3 and BC1.A.1.5, which parameters The Company will utilise in instructing in accordance with this OC5 in issuing Bid-Offer Acceptances.  The parameters shall reasonably reflect the true operating characteristics of each CCGT Unit.

(c)	The test referred to in OC5.5.1.1 will be initiated by the issue of instructions, which may be accompanied by a Bid-Offer Acceptance, under BC2 (in accordance with the Export and Import Limits and Dynamic Parameters which have been submitted for the day on which the test was called, or in the case of a CCGT Unit, in accordance with the parameters submitted under OC5.5.1.3(b)).  The instructions in respect of a CCGT Unit within a CCGT Module will be in respect of the CCGT Unit, as provided in BC2.

OC5.5.2	User Request for Testing

OC5.5.2.1	Where a GB Code User undertakes a test to demonstrate compliance with the Grid Code and Bilateral Agreement in accordance with CP.6 or CP.7 or CP.8 (other than a failure between The Company and a GB Code User to agree in CP.8.1 where OC5.5.1.1 applies) the GB Code User shall request permission to test using the process laid out in OC7.5.

OC5.5.2.2	Where an EU Code User undertakes a test to demonstrate compliance with the Grid Code and Bilateral Agreement in accordance with ECP.6.1, ECP.6.2, ECP.6.3 or ECP.7 or ECP.8 (other than a failure between The Company and a EU Code User to agree in ECP.8.1 where OC5.5.1.1 applies) the EU Code User shall request permission to test using the process laid out in OC7.5.

OC5.5.3	Conduct of Test

OC5.5.3.1	The performance of the BM Unit will be recorded at Transmission Control Centres notified by The Company with monitoring at site when necessary, from voltage and current signals provided by the User for each BM Unit under CC.6.6.1 or ECC.6.6.1 as applicable.

OC5.5.3.2	If monitoring at site is undertaken, the performance of the BM Unit will be recorded on a suitable recorder (with measurements, in the case of a Synchronous Generating Unit (which could be part of a Synchronous Power Generating Module), taken on the Generating Unit Stator Terminals / on the LV side of the generator transformer) or in the case of a Non-Synchronous Generating Unit (excluding Power Park Units), Power Generating Module, Power Park Module or HVDC Equipment or DC Converter at the point of connection (including where the OTSUA is operational prior to the OTSUA Transfer Time, the Transmission Interface Point) in the relevant User’s Control Room, in the presence of a reasonable number of representatives appointed and authorised by The Company. If The Company or the User requests, monitoring at site will include measurement of the parameters set out in OC5.A.1.2 or OC5.A.1.3 or ECP.A4.2 or ECP.A.4.3  as appropriate.

OC5.5.3.3	The User is responsible for carrying out the test and retains the responsibility for the safety of personnel and plant during the test.

OC5.5.4	Test and Monitoring Assessment

The criteria must be read in conjunction with the full text under the Grid Code reference.  The BM Unit, Power Generating Module, CCGT Module, Power Park Module or Generating Unit (excluding Power Park Units), HVDC Equipment and DC Converters and OTSUA will pass the test the criteria below are met:

| Parameter to be Tested |  | Criteria against which the test results will be assessed by The Company. |
| --- | --- | --- |
| Voltage Quality | Harmonic Content | CC.6.1.5(a) or ECC.6.1.5(a) Measured harmonic emissions do not exceed the limits specified in the Bilateral Agreement or where no such limits are specified, the relevant planning level specified in Engineering Recommendation G5. |
|  | Phase Unbalance | CC.6.1.5(b) or ECC.6.1.5(b), The measured maximum Phase (Voltage) Unbalance on the National Electricity Transmission System should remain, in England and Wales, below 1% and, in Scotland, below 2% and Offshore will be defined in relevant Bilateral Agreement. CC.6.1.6 or ECC.6.1.6 In England and Wales, measured infrequent short duration peaks in Phase (Voltage) Unbalance should not exceed the maximum value stated in the Bilateral Agreement. |
|  | Rapid Voltage Change | CC.6.1.7(a) or ECC.6.1.7(a) The measured Rapid Voltage Change at the Point of Common Coupling shall not exceed the Planning Levels specified in CC.6.1.7(a) or ECC 6.1.7.(i) |
|  | Flicker Severity | CC.6.1.7(j) or ECC.6.1.7(j) The measured Flicker Severity at the Point of Common Coupling shall not exceed the limits specified in the table of CC.6.1.7(j) or ECC 6.1.7(j). |
|  | Voltage Fluctuation | CC.6.1.8 or ECC.6.1.8 Offshore, measured voltage fluctuations at the Point of Common Coupling shall not exceed the limits set out in the Bilateral Agreement. |
| Fault Clearance | Fault Clearance Times | CC.6.2.2.2.2(a), CC.6.2.3.1.1(a), ECC.6.2.2.2.2(a), ECC.6.2.3.1.1(a), Bilateral Agreement |
|  | Back Up Protection | CC.6.2.2.2.2(b), CC.6.2.3.1.1(b), ECC.6.2.2.2.2(a), ECC.6.2.3.1.1(a), Bilateral Agreement |
|  | Circuit Breaker Fail Protection | CC.6.2.2.2.2(c), CC.6.2.3.1.1(c), ECC.6.2.2.2.2(c), ECC.6.2.3.1.1(c) |
|  | Reactive Capability | CC.6.3.2 or ECC.6.3.2 (and in the case of CC.6.3.2(e)(iii) and ECC.6.3.2.5 and ECC.6.3.2.6, the Bilateral Agreement), CC.6.3.4 or ECC.6.3.4, Ancillary Services Agreement. For a test initiated under OC.5.5.1.1 the Power Generating Module, Generating Unit, HVDC Equipment, DC Converter or Power Park Module or (prior to the OTSUA Transfer Time) OTSUA will pass the test if it is within ±5% of the reactive capability registered with The Company under OC2. The duration of the test will be for a period of up to 60 minutes during which period the system voltage at the Grid Entry Point for the relevant Power Generating Module, Generating Unit, HVDC Equipment, DC Converter or Power Park Module or Interface Point in the case of OTSUA will be maintained by the Generator or HVDC System Owner, DC Converter Station owner at the voltage specified pursuant to BC2.8 by adjustment of Reactive Power on the remaining Power Generating Module, Generating Unit, HVDC Equipment, DC Converter or Power Park Modules or OTSUA, if necessary. Any test performed in respect of an Embedded Medium Power Station not subject to a Bilateral Agreement or, an Embedded DC Converter Station or Embedded HVDC System not subject to a Bilateral Agreement shall be as confirmed pursuant to OC5.8.3. Measurements of the Reactive Power output under steady state conditions should be consistent with Grid Code requirements i.e. fully available within the voltage range ±5% at all voltages. |
| Governor / Frequency Control | Primary Secondary and High Frequency Response | Ancillary Services Agreement, CC.6.3.7 and where applicable CC.A.3 or ECC.6.3.7 and where applicable ECC.A.3. For a test initiated under OC.5.5.1.1 the measured response in MW/Hz is within ±5% of the level of response specified in the Ancillary Services Agreement for that Genset. |
|  | Stability with Voltage | CC.6.3.4 or ECC.6.3.4 |
|  | Governor / Load / Frequency Controller System Compliance | CC.6.3.6(a), CC.6.3.7, CC.6.3.9, CC.8.1, where applicable CC.A.3, BC3.5, BC3.6, BC3.7 or ECC.6.3.6, ECC.6.3.7, ECC.6.3.9, ECC8.1, where applicable ECC.A.3, BC3.5, BC3.6, BC3.7 |
|  | Output at Reduced System Frequency | CC.6.3.3 or ECC.6.3.3 - For variations in System Frequency exceeding 0.1Hz within a period of less than 10 seconds, the Active Power output is within ±0.2% of the requirements of CC.6.3.3 or ECC.6.3.3 when monitored at prevailing external air temperatures of up to 25ºC., BC3.5.1 |
|  | Fast Start | Ancillary Services Agreement requirements |
|  | Black Start | OC5.7 |
|  | Excitation/Voltage Control System | CC.6.3.6(b), CC.6.3.8, CC.A.6 or CC.A.7 as applicable, BC2.11.2, and the Bilateral Agreement or ECC.6.3.6, ECC.6.3.8, ECC.A.6 or ECC.A.7 or ECC.A.8 as applicable |
|  | Fault Ride Through and Fast Fault Current Injection | CC.6.3.15, CC.A.4.A or CC.A.4.B as applicable or ECC.6.3.15, ECC.6.3.16, ECC.A.4. or ECC.A.4EC as applicable |
| Dynamic Parameters | Export and Import Limits, and Dynamic Parameters | BC2 The Export and Import Limits Dynamic Parameters under test are within 2½% of the declared value being tested. |
|  | Synchronisation time | BC2.5.2.3 Synchronisation takes place within ±5 minutes of the time it should have achieved Synchronisation. |
|  | Run-up rates | BC2 Achieves the instructed output and, where applicable, the first and/or second intermediate breakpoints, each within ±3 minutes of the time it should have reached such output and breakpoints from Synchronisation (or break point, as the case may be), calculated from the run-up rates in its Dynamic Parameters. |
|  | Run-down rates | BC2 Achieves the instructed output and, where applicable, the first and/or second intermediate breakpoints, each within ±5 minutes of the time it should have reached such output and breakpoints from Synchronisation (or break point, as the case may be), calculated from the run-up rates in its Dynamic Parameters. |
|  | Demand Response | DRSC.11.7 Non-Embedded Customers and BM Participants who are also Demand Response Providers shall execute a demand modification test when requested as per DRSC.11.7 to ensure the requirements of the Ancillary Services agreement and Demand Response Services Code are satisfied. |

OC5.5.4.1	The duration of the Dynamic Parameter tests in the above table will be consistent with and sufficient to measure the relevant expected input or output derived from the Final Physical Notification Data and Bid-Offer Acceptances issued under BC2 which are still in dispute following the procedure in OC5.4.2.

OC5.5.4.2	Due account will be taken of any conditions on the System which may affect the results of the test.  The relevant User must, if requested, demonstrate, to The Company's reasonable satisfaction, the reliability of the suitable recorders, disclosing calibration records to the extent appropriate.

OC5.5.5	Test Failure / Re-test

OC5.5.5.1	If the BM Unit, Power Generating Module, CCGT Modules, Power Park Module, OTSUA, or Generating Unit (excluding Power Park Units), HVDC Equipment or DC Converter Station concerned fails to pass the test instructed by The Company under OC5.5.1.1 the User must provide The Company with a written report specifying in reasonable detail the reasons for any failure of the test so far as they are then known to the User after due and careful enquiry.  This must be provided within five Business Days of the test.

OC5.5.5.2	If in The Company’s reasonable opinion the failure to pass the test relates to compliance with the CC or ECC as applicable then The Company may invoke the process detailed in CP.8.2 to CP.9, or ECP.8.2 to ECP.9

OC5.5.5.3	If a dispute arises relating to the failure, The Company and the relevant User shall seek to resolve the dispute by discussion, and, if they fail to reach agreement, the User may by notice require The Company to carry out a re-test on 48 hours' notice which shall be carried out following the procedure set out in OC5.5.3 and OC5.5.4 and subject as provided in OC5.5.1.3, as if The Company had issued an instruction at the time of notice from the User.

OC5.5.6	Dispute Following Re-Test

If the BM Unit, Power Generating Module, CCGT Module, Power Park Module, OTSUA, or Generating Unit (excluding Power Park Units), HVDC Equipment or DC Converter in The Company's view fails to pass the re-test and a dispute arises on that re-test, either party may use the Disputes Resolution Procedure for a ruling in relation to the dispute, which ruling shall be binding.

OC5.6	DISPUTE RESOLUTION

OC5.6.1	If following the procedure set out in OC5.5 it is accepted that the BM Unit, Power Generating Module, CCGT Module, Power Park Module, OTSUA (prior to the OTSUA Transfer Time) or Generating Unit (excluding Power Park Units) ), HVDC Equipment or DC Converter has failed the test or re-test (as applicable), the User shall within 14 days, or such longer period as The Company may reasonably agree, following such failure, submit in writing to The Company for approval the date and time by which the User shall have brought the BM Unit concerned to a condition where it complies with the relevant requirement. The Company will not unreasonably withhold or delay its approval of the User’s proposed date and time submitted.  Should The Company not approve the User’s proposed date or time (or any revised proposal), the User should amend such proposal having regard to any comments The Company may have made and re-submit it for approval.

OC5.6.2	If a BM Unit fails the test, the User shall submit revised Export and Import Limits and/or Dynamic Parameters, or in the case of a BM Unit comprising a Generating Unit, Power Generating Module, CCGT Module, HVDC Equipment, DC Converter, OTSUA (prior to the OTSUA Transfer Time) or Power Park Module, the User may amend, with The Company's approval, the relevant registered parameters of that Generating Unit, Power Generating Module, CCGT Module, HVDC Equipment, DC Converter, OTSUA (prior to the OTSUA Transfer Time) or Power Park Module, as the case may be, relating to the criteria, for the period of time until the BM Unit can achieve the parameters previously registered, as demonstrated in a re-test.

OC5.6.3	Once the User has indicated to The Company the date and time that the BM Unit, Power Generating Module, CCGT Module, Power Park Module, Generating Unit (excluding Power Park Units) or OTSUA (prior to the OTSUA Transfer Time), HVDC Equipment or DC Converter Station can achieve the parameters previously registered or submitted, The Company shall either accept this information or require the User to demonstrate the restoration of the capability by means of a repetition of the test referred to in OC5.5.3 by an instruction requiring the User on 48 hours notice to carry out such a test.  The provisions of this OC5.6 will apply to such further test.

OC5.7	BLACK START TESTING

OC5.7.1 	General

As provided for in OC9.1.1 there are two ways in which the Total System (or disconnecteddisonnected part of the Total System in the case of a Partial Shutdown) can be re-established. These being a top-down approach using Local Joint Restoration Plans or a bottom-up approach using one or more Distribution Restoration Zone Plans.  In practice, and in order to re-establish the Total System to normal operational conditions and restore User’s Demand in the shortest possible time and in the most reliable way, The Company may initiate a top-down and bottom-up approach in parallel.

To achieve this objective, it is essential that Black Start Service Providers and Anchor Plant Owners, test their Plant and Apparatus at regular intervals to demonstrate that there is a high level of confidence that they will be able to satisfy the requirements of the Grid Code and their Black Start Contracts or their Distribution Restoration Contracts.

OC5.7.1.1	General Requirements applicable to Black Start Service Providers forming part of a Local Joint Restoration Plan

- The Company shall require a Black Start Service Provider to carry out a Black Start Test in order to demonstrate that a Black Start Station or Black Start HVDC System has a Black Start Capability.

- In the case of a Generator, The Company shall require a Generator with a Black Start Station to carry out a test (either a “Black Start Unit Test” or a Black Start Station Test”) in order to demonstrate that a Black Start Station has a Black Start Capability.

- In the case of an HVDC System Owner or DC Converter Station Owner, The Company shall require an HVDC System Owner or DC Converter Station Owner with a Black Start HVDC System to carry out a test (a “Black Start HVDC Test”) on a HVDC System or DC Converter, in order to demonstrate that a Black Start HVDC System has a Black Start Capability.

- In the case of an EU Generator, The Company may also require a Generator with a Black Start Station to carry out a test (a Quick Resynchronisation Unit Test) in order to demonstrate that a Black Start Station has a Quick Re-Synchronisation Capability.

(b) 	Where The Company requires a Black Start Service Provider to undertake testing, the following requirements shall apply:-

(i)	Where The Company requires a Generator with a Black Start Station to carry out a Black Start Unit Test, on each Genset, which has Black Start Capability, within such a Black Start Station, the Generator shall execute such a test at least once every three years. The Company shall not require the Black Start Unit Test to be carried out on more than one Genset at that Black Start Station at the same time, and would not, in the absence of exceptional circumstances, expect any of the other Gensets at the Black Start Station to be directly affected by the Black Start Unit Test.

(ii)	The Company may occasionally require the Generator to carry out a Black 	 Start Station Test at any time (but will not require a Black Start Station Test to 	 be carried out more than once in every three calendar years in respect of any 	 particular Genset unless it can justify on reasonable grounds the necessity for 	 further tests or unless the further test is a re-test).  If successful, this Black Start 	 Station Test shall count as a successful Black Start Unit Test for the Genset 	 used in the test.

(iii)	The Company may require the HVDC System 	Owner or DC Converter 	 Station Owner to carry out a Black Start HVDC Test at any time (but will not 	 require such a test to be carried out more than once in every three calendar 	 years unless it can justify on reasonable grounds the necessity for further tests or 	 unless the further test is a re-test).

- The Company may occasionally require the EU Generator to carry out a Quick Re-Synchronisation Test at any time, but will generally only be required where the EU Generator has made a change to its Plant and Apparatus which has an impact on its Houseload Operation or after two unsuccessful tripping Events in the operational environment.

The above tests will be deemed a success where starting from Shutdown is 	achieved within a time frame specified by The Company and which may 	be 	agreed in the Black Start Contract.

(c)	The Company may require a Generator to carry out a Black Start Unit Test at any time (but will not require a Black Start Unit Test to be carried out more than once in each calendar year in respect of any particular Genset unless it can justify on reasonable grounds the necessity for further tests or unless the further test is a re-test).

(d) When The Company wishes a  Black Start Service Provider to carry out a Black Start Test, it shall notify the relevant  Black Start Service Provider at least 7 days prior to the time of the Black Start Test with details of the proposed Black Start Test.

OC5.7.1.2	General Requirements applicable to Anchor Plant Owners forming part of a Distribution Restoration Zone Plan

- The Company shall require a Network Operator in coordination with an Anchor Plant Owner to carry out tests in order to demonstrate that an Anchor Plant has Anchor Plant Capability.  Prior to any test taking place, the Network Operator shall ensure its System is appropriately configured to undertake the test.

  - In the case of an Anchor Generator, The Company shall require a Network Operator to instruct an Anchor Generator to carry out a test (either an “Anchor Generating Unit Test” or an Anchor Power Station Test”) in order to demonstrate that an Anchor Power Station has Anchor Plant Capability.

  - In the case of an Anchor HVDC System Owner or an Anchor DC Converter Owner, The Company shall require a Network Operator to instruct an Anchor HVDC System Owner or Anchor DC Converter Owner to carry out an Anchor HVDC Test or Anchor DC Converter Test on a HVDC System or DC Converter respectively, in order to demonstrate Anchor Plant Capability.

- The Company shall instruct the relevant Network Operator to instruct an Anchor Generator with an Anchor Power Station to carry out an Anchor Generating Unit Test, on each Anchor Generating Unit, within such an Anchor Power Station.  The test is required to be conducted at least once every three calendar years.  The Company shall not require the Network Operator to instruct an Anchor Generating Unit Test to be carried out on more than one Anchor Generating Unit at that Anchor Power Station at the same time, and would not, in the absence of exceptional circumstances, expect any of the other Anchor Generating Units at the Anchor Power Station to be directly affected by the Anchor Generating Unit Test.

- The Company may occasionally require the relevant Network Operator to instruct an Anchor Generator to carry out an Anchor Power Station Test at any time (but will not require an Anchor Power Station Test to be carried out more than once in every three calendar years in respect of any particular Anchor Generating Unit unless it can reasonably justify the necessity for further tests or unless the further test is a re-test).  If successful, this Anchor Power Station Test shall count as a successful Anchor Generating Unit Test for the Anchor Generating Unit used in the test.

- The Company may require the Network Operator to instruct an Anchor HVDC System Owner or Anchor DC Converter Owner to carry out an Anchor HVDC Test or Anchor DC Converter Test at any time (but will not require such a test to be carried out more than once in every three calendar years unless it can reasonably justify the necessity for further tests, unless the further test is a re-test).

- The Company may occasionally require a Network Operator to instruct an EU Generator which is also an Anchor Generator to carry out a Quick Re-Synchronisation Test at any time, but will generally only be required where such an Anchor Generator has made a change to its Plant and Apparatus which has an impact on its Houseload Operation or after two unsuccessful tripping Events in the operational environment.

OC5.7.1.3	The above tests defined in OC5.7.1.2 (b)– (e) will be deemed a success where stable operation is achieved within a time frame which may be specified in the Distribution Restoration Contract.

OC5.7.1.4	The Company may require a Network Operator to instruct an Anchor Generator to carry out an Anchor Generating Unit Test at any time (but will not require an Anchor Generating Unit Test to be carried out more than once in each calendar year in respect of any particular Anchor Generating Unit unless it can reasonably justify the necessity for further tests, unless the further test is a re-test).

OC5.7.1.5	When The Company instructs a Network Operator to instruct an Anchor Plant Owner to carry out an Anchor Plant Test, the Network Operator shall instruct the relevant Anchor Plant Owner at least 7 days prior to the time of the Anchor Plant Test with details of the required Anchor Plant Test.

OC5.7.2	Procedure for a Black Start Tests in respect of Local Joint Restoration Plans and Restoration Service Provider Tests in respect of Distribution Restoration Zone Plans

For Black Start Service Providers, who own and/or operate Plant with Black Start Capability the procedure for Black Start Tests will, so far as practicable, be carried out in accordance with the applicable requirements and sequence defined in OC5.7.2.1 to OC5.7.2.9 and OC5.7.3.

For Anchor Plant Owners who own and/or operate Anchor Plant forming part of a Distribution Restoration Zone Plan, the procedure for Anchor Plant Tests is detailed in OC5.7.4,  Anchor Plant Owners are not required to satisfy the requirements of OC5.7.2.1 to OC5.7.2.9 and OC5.7.3.

OC5.7.2.1	Black Start Unit Tests

(a)	The relevant Generating Unit shall be Synchronised and Loaded;

(b)	All the Auxiliary Energy Supplies in the Black Start Station in which that Generating Unit is situated, shall be Shutdown.

(c)	The Generating Unit shall be De-Loaded and De-Synchronised and all alternating current electrical supplies to its Auxiliaries shall be disconnected.

(d)	The Auxiliary Energy Supplies to the relevant Generating Unit shall be started, and shall re-energise the Unit Board of the relevant Generating Unit.

(e)	The Auxiliaries of the relevant Generating Unit shall be fed by the Auxiliary Energy Supplies or Auxiliary Diesel Engine(s), via the Unit Board, to enable the relevant Generating Unit to return to Synchronous Speed.

(f)	The relevant Generating Unit shall be Synchronised to the System but not Loaded, unless the appropriate instruction has been given by The Company under BC2 which would also be in accordance with the requirements of the Black Start Contract.

(g)	In respect of EU Generators, the above tests defined in OC5.7.2.1(a) – (e) shall be in accordance with the requirements of ECC.6.3.5.3.

OC5.7.2.2	Black Start Station Test

(a)	All Generating Units at the Black Start Station, other than the Generating Unit on which the Black Start Test is to be carried out, and all the Auxiliary Energy Supplies at the Black Start Station, shall be Shutdown.

(b)	The relevant Generating Unit shall be Synchronised and Loaded.

(c)	The relevant Generating Unit shall be De-Loaded and De-Synchronised.

(d)	All external alternating current electrical supplies to the Unit Board of the relevant Generating Unit, and to the Station Board of the relevant Black Start Station, shall be disconnected.

(e)	An Auxiliary Energy Supplies at the Black Start Station shall be started, and shall re-energise either directly, or via the Station Board, the Unit Board of the relevant Generating Unit.

(f)	The provisions of OC5.7.2.1 (e) and (f) shall thereafter be followed.

(g)	In respect of EU Generators, the above tests defined in OC5.7.2.2(a) – (e) shall be in accordance with the requirements of ECC.6.3.5.3.

OC5.7.2.3	Procedure for a Black Start HVDC Test

- The HVDC System or DC Converter Station shall demonstrate its technical capability to energise the busbar of the disconnected AC substation to which it is connected, within the GB Synchronous Area within a timeframe specified by The Company.  In the case of HVDC Systems this shall be in accordance with the requirements of ECC.6.3.5.4.  As part of this test, all Auxiliaries are required to be derived from within the HVDC System or DC Converter Station.

- The test shall be carried out while the HVDC System or DC Converter Station starts from Shutdown;

- The test shall be deemed passed, provided that the following conditions are cumulatively fulfilled:

- The HVDC System Owner has demonstrated its HVDC System or DC Converter Station is able to energise the busbar of the isolated AC-substation to which it is connected within the GB Synchronous Area

- The HVDC System or DC Converter Station can achieve a stable operating point at an agreed capacity as agreed with The Company. theThe relevant HVDC System or DC Converter Station can be connected to the System but not Loaded, unless appropriate instructions are given by The Company under BC2 which would also be in accordance with the requirements of the Black Start Contract.

- In respect of HVDC Systems and Remote End HVDC Converter Stations, the above tests defined in OC5.7.2.3(a) – (c) shall be in accordance with the requirements of, ECC.6.1.2, ECC.6.1.4, ECC.6.2.2.9.4 and ECC.6.3.5.4.

- In respect of DC Converter Stations, the above tests defined in OC5.7.2.3(a) – (c) shall be in accordance with the requirements of, CC.6.1.2, CC.6.1.3 and CC.6.1.4.

OC5.7.2.4	All Black Start Tests shall be carried out at the time specified by The Company in the notice given under OC5.7.1 and shall be undertaken in the presence of a reasonable number of representatives appointed and authorised by The Company, who shall be given access to all information relevant to the Black Start Test.

OC5.7.2.5	Failure of a Black Start Test

A Black Start Station or Black Start HVDC System shall fail a Black Start Test if the Black Start Test shows that it does not have a Black Start Capability (ie. if the relevant Generating Unit or HVDC System or DC Converter fails to be Synchronised to the System within two hours of the Auxiliary Energy Supplies being required to start unless this is part of a Local Joint Restoration Plan where the times will be adjusted accordingly).

OC5.7.2.6	If a Black Start Station or Black Start HVDC System fails to pass a Black Start Test the Black Start Service Provider must provide The Company with a written report specifying in reasonable detail the reasons for any failure of the test so far as they are then known to the Black Start Service Provider after due and careful enquiry. This must be provided within five Business Days of the test.  If a dispute arises relating to the failure, The Company and the relevant Black Start Service Provider shall seek to resolve the dispute by discussion, and if they fail to reach agreement, the Black Start Service Provider may require The Company to carry out a further Black Start Test on 48 hours notice which shall be carried out following the procedure set out in OC5.7.2.1 or OC5.7.2.2 or OC5.7.2.3 as the case may be, as if The Company had issued an instruction at the time of notice from the Black Start Service Provider.

OC5.7.2.7	If the Black Start Station or Black Start HVDC System concerned fails to pass the re-test and a dispute arises on that re-test, either party may use the Disputes Resolution Procedure for a ruling in relation to the dispute, which ruling shall be binding.

OC5.7.2.8	If following the procedure in OC5.7.2.6 and OC5.7.2.7 it is accepted that the Black Start Station or Black Start HVDC System has failed the Black Start Test (or a re-test carried out under OC5.7.2.5), within 14 days, or such longer period as The Company may reasonably agree, following such failure, the relevant Black Start Service Provider shall submit to The Company in writing for approval, the date and time by which that Black Start Service Provider shall have brought that Black Start Station or Black Start HVDC System to a condition where it has a Black Start Capability and would pass the Black Start Test, and The Company will not unreasonably withhold or delay its approval of the Black Start Service Provider’s proposed date and time submitted.  Should The Company not approve the Black Start Service Provider’s proposed date and time (or any revised proposal) the Black Start Service Provider shall revise such proposal having regard to any comments The Company may have made and resubmit it for approval.

OC5.7.2.9	Once the Black Start Service Provider has indicated to The Company that the PowerStation or HVDC System or DC Converter Station has a Black Start Capability, The Company shall either accept this information or require the Black Start Service Provider to demonstrate that the relevant Black Start Station or Black Start HVDC System has its Black Start Capability restored, by means of a repetition of the Black Start Test referred to in OC5.7.1.1 following the same procedure as for the initial Black Start Test.  The provisions of this OC5.7.2, will apply to such test.

- OC5.7.3 	Quick Re-synchronisation Unit Test

- The relevant Generating Unit shall be Synchronised and 					Loaded;

- All the Auxiliary Energy Supplies in the 				Black Start Station in which that Generating Unit is situated, shall be

- Shutdown.

- The Generating Unit shall be tripped to house load.

- The relevant Generating Unit shall be Synchronised to the System but not 			Loaded, unless the appropriate instruction has been given by The Company 			under BC2 which would also be in accordance with the requirements of the 				Black Start Contract.

In respect of EU Generators, the above tests defined in OC5.7.3(a) – (d) shall be in 		accordance with the requirements of ECC.6.3.5.6.

OC5.7.4	Procedure for Testing of Plant and Apparatus required by a Distribution Restoration Zone Plan

Restoration Service Provider’s Plant and Apparatus will be subject to testing for the contracted services they have agreed to provide as specified in the Distribution Restoration Contract and as required under the Distribution Restoration Zone Plan.  Such Plant and Apparatus which forms part of a Distribution Restoration Zone Plan is required to satisfy the requirements of OC5.7.4 only, and not the requirements of OC5.7.2 and OC5.7.3.

All tests shall be instructed and coordinated by the Network Operator.  The Network Operator shall inform The Company of the progress and completion of the tests.

All the tests required by OC5.7.4 shall be carried out at the time agreed by The Company, the Network Operator and Restoration Service Provider in the notice periods given under OC5.7.1.5 and shall be undertaken by the Restoration Service Provider in the presence of a reasonable number of representatives appointed by The Company and/or Network Operator, who shall be given access to all information relevant to the each test.

OC5.7.4.1	Anchor Generating Unit Tests

(a)	Prior to the test, the Network Operator shall reconfigure its System as necessary to enable the Anchor Generating Unit Test to be completed whilst having due regard for the safety of plant and personnel on its System.

(b)	The relevant Anchor Generating Unit shall be Synchronised and Loaded;

(c)	All the Auxiliary Energy Supplies in the Anchor Power Station which relate to the relevant Anchor Generating Unit, shall be Shutdown.

(d)	The Anchor Generating Unit shall be De-Loaded, De-Synchronised and Shutdown and all alternating current electrical supplies to its Auxiliaries shall be disconnected.

(e)	The Auxiliary Energy Supplies to the relevant Anchor Generating Unit shall be made available and shall re-energise the Unit Board (or equivalent) of the relevant Anchor Generating Unit.

(f)	The Auxiliaries of the relevant Anchor Generating Unit shall be fed by the Auxiliary Energy Supplies, via the Unit Board (or equivalent), to enable the relevant Anchor Generating Unit to return to a condition when it is ready to synchronise to the Network Operator’s System.

(g)	The relevant Anchor Generating Unit shall be Synchronised to the System but not Loaded, unless the appropriate instruction has been given by The Company to the Network Operator under BC2 which would also be in accordance with the requirements of the Distribution Restoration Contract.

(h)	The Company and Network Operator shall agree with the Anchor Generator when the test has been completed in accordance with the test requirements of the Distribution Restoration Zone Plan.

(i)	In respect of Anchor Generators which are EU Generators, the above tests defined in OC5.7.4.1(b) – (h) shall be in accordance with the requirements of ECC.6.3.5.

OC5.7.4.2	Anchor Power Station Tests

(a)	Prior to the test, the Network Operator shall reconfigure its System as necessary to enable the Anchor Generating Unit Test to be completed whilst having due regard for the safety of plant and personnel on its System.

(b)	All Anchor Generating Units at the Anchor Power Station, other than the Anchor Generating Unit on which the Anchor Generating Unit Test is to be carried out, and all the Auxiliary Energy Supplies at the Anchor Power Station, shall be Shutdown.

(c)	The relevant Anchor Generating Unit shall be Synchronised and Loaded.

(d)	The relevant Anchor Generating Unit shall be De-Loaded and De-Synchronised.

(e)	All external alternating current electrical supplies to the Unit Board (or equivalent) of the relevant Anchor Generating Unit, and to the Station Board of the relevant Anchor Power Station, shall be disconnected.

(f)	An Auxiliary Energy Supply at the Anchor Power Station shall be made available and shall re-energise either directly, or via the Station Board or the Unit Board (or equivalent) of the relevant Anchor Generating Unit.

(g)	The provisions of OC5.7.4.1 (e) to (h) shall thereafter be followed.

(h)	The Company and Network Operator shall agree with the Anchor Generator when the test has been completed in accordance with the test requirements of the Distribution Restoration Zone Plan.

(i)	In respect of EU Generators, the above tests defined in OC5.7.4.2(a) – (h) shall be in accordance with the requirements of ECC.6.3.5.

OC5.7.4.3	Tests on Restoration Service Providers’ Plant and Apparatus other than Anchor Plant

(a)	Prior to the test, the Network Operator shall reconfigure its System as necessary to enable the test of the relevant Plant and Apparatus to be completed whilst having due regard for the safety of plant and personnel on its System.

(b)	The relevant Plant and/or Apparatus shall be operating normally, ie in the operational state it is anticipated to be in if a Shutdown were to occur;

(c)	All the Auxiliary Energy Supplies which relate to the relevant Plant and/or Apparatus shall be Shutdown.

(d)	The Plant and/or Equipment shall be De-Loaded, De-Synchronised and Shutdown as appropriate and all alternating current electrical supplies to its Auxiliaries shall be disconnected.

(e)	The Auxiliary Energy Supplies to the relevant Plant and/or Apparatus shall be made available and shall re-energise the Unit Board (or equivalent) of the relevant Plant and/or Apparatus.

(f)	The Auxiliaries of the relevant Plant and/or Apparatus shall be fed by the Auxiliary Energy Supplies, via the Unit Board (or equivalent), to enable the relevant Plant and/or Apparatus to return to a condition when it is ready to be reconnected and/or Synchronised to the Network Operator’s System.

(g)	Relevant Plant shall be Synchronised to the System but not Loaded, unless the appropriate instruction has been given by The Company to the Network Operator under BC2 which would also be in accordance with the requirements of the Distribution Restoration Contract.

(h)	The Company and Network Operator shall agree with the Restoration Service Provider when the test has been completed in accordance with the test requirements of the Distribution Restoration Zone Plan.

(i)	In respect of Restoration Providers who are EU Generators, the above tests defined in OC5.7.4.3(b) – (h) shall be in accordance with the requirements of ECC.6.3.5.

OC5.7.4.4	Procedure for an Anchor HVDC System Test or Anchor DC Converter Test

- The Anchor HVDC System‘s technical capability or Anchor DC Converter‘s technical capability to energise the busbar of the disconnected AC substation to which it is connected, within a timeframe specified by the Network Operator, shall be demonstrated.  In the case of Anchor HVDC Systems the timeframe shall be in accordance with the requirements of ECC.6.3.5.4.  As part of this test, all Auxiliaries are required to be derived from within the Anchor HVDC System or Anchor DC Converter.

- The test shall be carried out with the Anchor HVDC System or Anchor DC Converter starting from Shutdown ;

- The test shall be deemed to have been successfully completed, provided that the following conditions are cumulatively fulfilled:

- The Anchor HVDC System Owner or Anchor DC Converter Owner has demonstrated its Anchor HVDC System or Anchor DC Converter is able to energise the busbar of the disconnected AC-substation to which it is connected.

- The Anchor HVDC System or Anchor DC Converter can achieve a stable operating point at an agreed capacity as agreed with the Network Operator. The Anchor HVDC System or Anchor DC Converter can be connected to the Network Operator’s System but not Loaded, unless appropriate instructions have been given by The Company to the Network Operator under BC2 which would also be in accordance with the requirements of the Distribution Restoration Contract.

- In respect of Anchor HVDC Systems, the above tests defined in OC5.7.4.4(a) – (c) shall be in accordance with the requirements of, ECC.6.1.2, ECC.6.1.4, ECC.6.2.2.9.4 and ECC.6.3.5.4.

- In respect of Anchor DC Converter Stations, the above tests defined in OC5.7.4.4(a) – (c) shall be in accordance with the requirements of, CC.6.1.2, CC.6.1.3 and CC.6.1.4.

OC5.7.4.5	Quick Re-synchronisation Unit Test

- The relevant Anchor Generating Unit shall be Synchronised and Loaded;

- All the Auxiliary Energy Supplies in the Anchor Power Station in which that Anchor Generating Unit is situated, shall be Shutdown.

- The Anchor Generating Unit shall be tripped to house load.

- The relevant Anchor Generating Unit shall be Synchronised to the System but not Loaded, unless the appropriate instruction has been given by The Company to the Network Operator under BC2 which would also be in accordance with the requirements of the Distribution Restoration Zone Plan.

- The Company and Network Operator shall agree with the Restoration Service Provider when the test has been completed in accordance with the test requirements of the Distribution Restoration Zone Plan.

In respect of EU Generators, the above tests defined in OC5.7.4.5(a) – (d) shall be in accordance with the requirements of ECC.6.3.5.6.

OC5.7.4.6	Distribution Restoration Zone Control System Tests

Where a Network Operator uses a Distribution Restoration Zone Control System as part of the implementation of a Distribution Restoration Zone Plan, the Network Operator shall undertake tests to establish the correct functioning of the Distribution Restoration Zone Control System.  These shall include the following:-

- that communications systems maintain correct operation when operating in mains independent mode for at least [24] hours.

- that the Distribution Restoration Zone Control System is able to reconfigure the Network Operator’s System in response to the appropriate test or simulated signals etc.  This functionality shall be demonstrated as being available for at least [24] hours when operating in mains independent mode.

- that the Distribution Restoration Zone control Control System is able to instruct Restoration Service Providers Plant and Apparatus (including Anchor Plant) in response to the appropriate test or simulated signals etc.  This functionality shall be demonstrated as being available for at least [24] hours when operating in mains independent mode.

The relevant Network Operator should conduct the above tests at least once every three years.

OC5.7.4.7	Test Failures/Re-Tests and Disputes

The relevant Network Operator shall:

(a)	ensure that Restoration Service Providers’ Plant and Apparatus is capable of meeting the requirements of OC5.7.4 and the relevant Distribution Restoration Contracts.

(b)	notify The Company where any such failure has an impact on the Network Operators ability to activate a Distributed Restoration Zone Plan.

(c)	liaise with The Company to allow The Company to work with the Restoration Service Provider to undertake tests or investigations where there has been a repeated failure of the Restoration Service Provider’s Plant and Apparatus.

OC5.8	PROCEDURES APPLYING TO EMBEDDED MEDIUM POWER STATIONS NOT SUBJECT TO A BILATERAL AGREEMENT AND EMBEDDED DC CONVERTER STATIONS NOT SUBJECT TO A BILATERAL AGREEMENT

OC5.8.1	Compliance Statement

Each Network Operator shall ensure that each Embedded Person provides to the Network Operator upon The Company's request:

(a)	written confirmation that each such Power Generating Module, Generating Unit, Power Park Module, HVDC Equipment, or DC Converter complies with the requirements of the CC; and

(b)	evidence, where requested, reasonably satisfactory to The Company, of such compliance.  Such a request shall not normally be made by The Company more than twice in any calendar year in respect of any Generator’s Power Generating Module, Generating Unit or Power Park Module or HVDC System Owner’s HVDC System, or DC Converter owner's DC Converter.

The Network Operator shall provide the evidence or written confirmation required under OC5.8.1 (a) and (b) forthwith upon receipt to The Company.

OC5.8.2	Network Operator’s Obligations To Facilitate Tests

If:

(a)	the Network Operator fails to procure the confirmation referred to at OC5.8.1(a); or

(b)	the evidence of compliance is not to The Company’s reasonable satisfaction,

then, The Company shall be entitled to require the Network Operator to procure access upon terms reasonably satisfactory to The Company to enable The Company to witness the Embedded Person carrying out the tests referred to in OC5.8.3 in respect of the relevant Embedded Medium Power Station or Embedded DC Converter Station or Embedded HVDC System.

OC5.8.3	Testing Of Embedded Medium Power Stations Not Subject To A Bilateral Agreement Or Embedded DC Converter Stations Not Subject To A Bilateral Agreement or Embedded HVDC Equipment Not Subject To A Bilateral Agreement

The Company may, in accordance with the provisions of OC5.8.2, at any time (although not normally more than twice in any calendar year in respect of any particular Embedded Medium Power Station not subject to a Bilateral Agreement or Embedded DC Converter Station or Embedded HVDC Equipment not subject to a Bilateral Agreement) issue an instruction requiring the Network Operator within whose System the relevant Medium Power Station not subject to a Bilateral Agreement or DC Converter Station or HVDC Equipment not subject to a Bilateral Agreement is Embedded, to require the Embedded Person to carry out a test.

Such test shall be carried out at a time no sooner than 48 hours from the time that the instruction was issued, on any one or more of the Generating Units, Power Generating Module, Power Park Module or DC Converter or HVDC Equipment comprising part of the relevant Embedded Medium Power Station or Embedded DC Converter Station or HVDC System and should only be to demonstrate that:

(a)	the relevant Generating Unit, Power Generating Module, Power Park Module or DC Converter or HVDC Equipment meets the requirements of the paragraphs in the CC or ECC which are applicable to such Generating Units, Power Generating Modules, Power Park Module or DC Converter or HVDC Equipment;

(b)	the Reactive Power capability registered with The Company under OC2 meets the requirements set out in CC.6.3.2 or ECC.6.3.2 as applicable.

The instruction may only be issued where, following consultation with the relevant Network Operator, The Company has:

(a)	confirmed to the relevant Network Operator the manner in which the test will be conducted, which shall be consistent with the principles established in OC5.5.3; and

(b)	received confirmation from the relevant Network Operator that the relevant Generating Unit, Power Generating Module, Power Park Module or DC Converter or HVDC Equipment would not then be unavailable by reason of forced outage or Planned Outage expected prior to the instruction.

The relevant Network Operator is responsible for ensuring the performance of any test so required by The Company and the Network Operator shall ensure that the Embedded Person retains the responsibility for ensuring the safety of personnel and plant during the test.

OC5.8.4	Test Failures/Re-Tests and Disputes

The relevant Network Operator shall:

(a)	ensure that provisions equivalent to OC5.5.5, OC5.5.6 and OC5.6 apply to Embedded Medium Power Stations not the subject of a Bilateral Agreement, Embedded DC Converter Stations not the subject of a Bilateral Agreement or Embedded HVDC Equipment not the subject of a Bilateral Agreement within its System in respect of test failures, re-tests and disputes as to test failures and re-tests;

(b)	ensure that the provisions equivalent to OC5.5.5, OC5.5.6 and OC5.6 referred to in OC5.8.4(a) are effective so that The Company may require, if it so wishes, the provision to it of any reports or other information equivalent to those or that to which The Company would be entitled in relation to test failures, re-tests and disputes as to test failures and re-tests under the provisions of OC5.5.5, OC5.5.6 and OC5.6; and

(c)	the provisions equivalent to OC5.5.5, OC5.5.6 and OC5.6 referred to in OC5.8.4(a) are effective to permit The Company to conduct itself and take decisions in such a manner in relation to test failures, re-tests and disputes as to test failures and re-tests in respect of Embedded Medium Power Stations not the subject of a Bilateral Agreement,  Embedded DC Converter Stations not the subject of a Bilateral Agreement or Embedded HVDC Equipment not the subject of a Bilateral Agreement as it is able to conduct itself and take decisions in relation to test failures, re-tests and disputes as to test failures and re-tests under OC5.5.5, OC5.5.6 and OC5.6.

Extracts from Operating Code 9

To aid readability the order of some of OC9 sections has been changed.  To help make comparisons with the existing Grid Code OC9 text, the relationship of these sections is as follows:

| Old Reference | Topic | New Reference |
| --- | --- | --- |
| OC9.4.7.12 | Plan establishment (ie creation) | OC9.4.7.5 |
| OC9.4.7.12.(b)(xii) | Plan testing | OC9.4.7.5.3 |
| OC9.4.7.6 | Plan provisions | OC9.4.7.6 |
| - | DRZP operation | OC9.4.7.7 |
| OC9.4.7.8 | Expansion of power islands | OC9.4.7.8 |
| OC9.4.7.7 | Interconnexion of power islands | OC9.4.7.10 |
| OC9.4.7.9 | Return to normal | OC9.4.7.11 |
| OC9.4.7.10 | Conclusion of black start | OC9.4.7.12 |
| OC9.4.7.11 | Interconnectors | OC9.4.7.13 |

OC9.1	INTRODUCTION

Operating Code No.9 ("OC9") covers the processes and procedures by which The Company in coordination and liaison with Users, will restore the Total System or parts of the System following a Total Shutdown or Partial Shutdown.

OC9.1.1	Approach to System Restoration

Following a Total Shutdown or Partial Shutdown, there are two ways in which the Total System (or the disconnected part of the System in the case of a Partial Shutdown) can be re-established.  These being a top-down approach using Local Joint Restoration Plans or a bottom-up approach using one or more Distribution Restoration Zone Plans.

In the case of a Local Joint Restoration Plan, The Company (or Relevant Scottish Transmission Licensee as applicable) will issue instructions to Black Start Service Providers who will then energise parts of the Total System to form a Power Island.

Where Restoration Service Providers have agreed to enter into a Distribution Restoration Contract, The Company (or Relevant Scottish Transmission Licensee as applicable) will issue instructions to the Network Operator who in turn will instruct an Anchor Plant Owner to energise a part of the Network Operator’s System and subsequently for Restoration Service Providers Plant and Apparatus to be Synchronised to that part of the Network Operator’s System to form a Power Islands.

In practice in order to re-establish the Total System to normal operational conditions and restore supplies to Users in the shortest possible time and in the most reliable way, it is expected that The Company would initiate Local Joint Restoration Plans and Distribution Restoration Zone Plans in parallel.

OC9.1.2	Re-Synchronisation of Power Islands

Following the establishment of Power Islands (either through the implementation of Local Joint Restoration Plans or Distribution Restoration Zone Plans) The Company will then co-ordinate the Re-Synchronisation of parts of the Total System which have become Out of Synchronism with each other irrespective of whether or not a Total Shutdown or Partial Shutdown has occurred.

OC9.1.3	Joint System Incident Procedure

A Joint System Incident procedure requires the establishment of communication routes and arrangements between senior management representatives of The Company and Users involved in, or who may be involved in, an actual or potential serious or widespread disruption to the Total System or a part of the Total System, which requires, or may require, urgent managerial response, day or night, but which does not fall within the provisions of OC9.1.4.

OC9.1.4	It should be noted that under section 96 of the Act, the Secretary of State may give directions to The Company and/or any Generator and/or any Supplier, for the purpose of "mitigating the effects of any civil emergency which may occur" (ie. for the purposes of planning for a civil emergency); a civil emergency is defined in the Act as "any natural disaster or other emergency which, in the opinion of the Secretary of State, is or may be likely to disrupt electricity supplies".  Under the Energy Act 1976, the Secretary of State has powers to make orders and give directions controlling the production, supply, acquisition or use of electricity, where an Order in Council under section 3 is in force declaring that there is an actual or imminent emergency affecting electricity supplies.  In the event that any such directions are given, or orders made under the Energy Act 1976, the provisions of the Grid Code will be suspended in so far as they are inconsistent with them.

OC9.1.5	The Company shall procure that Relevant Transmission Licensees shall comply with OC9.4 and OC9.5 and any relevant Local Joint Restoration Plan or OC9 De-Synchronised Island Procedure where and to the extent that such matters apply to them.

OC9.2	OBJECTIVE

The overall objectives of OC9 are:

OC9.2.1	To achieve, as far as possible, restoration of the Total System and associated Demand in the shortest possible time, taking into account Power Station and Restoration Service Providers Plant and Apparatus capabilities, including Embedded Generating Units and External Interconnections and the operational constraints of the Total System.

OC9.2.2	To achieve the Re-Synchronisation of parts of the Total System which have become Out of Synchronism with each other.

OC9.2.3	To ensure that communication routes and arrangements are available to enable senior management representatives of The Company and Users, who are authorised to make binding decisions on behalf of The Company or the relevant User, as the case may be, to communicate with each other in the situation described in OC9.1.3.

OC9.2.4	To describe the role that in respect of Transmission Systems, Relevant Transmission Licensees and Network Operators may have in the restoration processes as detailed in the relevant OC9 De-Synchronised Island Procedures, Local Joint Restoration Plans and Distribution Restoration Zone Plans.

OC9.2.5	To identify and address as far as possible the events and processes necessary to enable the restoration of the Total System, after a Total Shutdown or Partial Shutdown.  This is likely to require the following key processes to be implemented, typically, but not necessarily, in the order given below:

(i) 	Selectively implement Local Joint Restoration Plans

(ii)	Selectively implement Distribution Restoration Zone Plans through Network Operators

(iii)	Expand and merge Power Islands leading to Total System energisation

(iv)	Selectively reconnect Demand

- Facilitate and co-ordinate returning the Total System back to normal operation

- Resumption of the Balancing Mechanism if suspended in accordance with the provisions of the BSC.

OC9.3	SCOPE

OC9.3.1	OC9 applies to The Company and to Users, which in OC9 means:-

- Generators;

- HVDC System Owners;

- DC Converter Station owners;

(d)	Network Operators;

(e)	Non-Embedded Customers; and

(f)	Relevant Restoration Service Providers.

OC9.3.2	The procedure for the establishment of emergency support/contingency planning between The Company and Externally Interconnected System Operators is set out in the Interconnection Agreement with each Externally Interconnected System Operator.

OC9.3.3	In respect of Transmission Systems, OC9.4 and OC9.5 also apply to Relevant Transmission Licensees.

OC9.4	SYSTEM RESTORATION

Total Shutdown and Partial Shutdown

OC9.4.1	A "Total Shutdown" is the situation existing when all generation has ceased and there is no electricity supply from External Interconnections. Therefore, the Total System has shutdown with the result that it is not possible for the Total System to begin to function again without The Company's directions relating to Black Start.

OC9.4.2	A "Partial Shutdown" is the same as a Total Shutdown except that all generation has ceased in a separate part of the Total System and there is no electricity supply from External Interconnections or other parts of the Total System to that part of the Total System. Therefore, that part of the Total System is shutdown with the result that it is not possible for that part of the Total System to begin to function again without The Company's directions relating to Black Start.

OC9.4.3	During a Total Shutdown or Partial Shutdown and during the subsequent recovery, the Licence Standards may not apply and the Total System may be operated outside normal voltage and Frequency standards.

OC9.4.4	In a Total Shutdown and in a Partial Shutdown and during the subsequent recovery, it is likely to be necessary for The Company to issue Emergency Instructions in accordance with BC2.9.

OC9.4.5	Contribution to System Restoration

The Company will restore the System following a Total Shutdown or Partial Shutdown by issuing instructions to Black Start Service Providers through one or more Local Joint Restoration Plans as provided for in OC9.4.5.1 and by instructing Network Operators to activate one or more Distribution Restoration ZonesZone Plans as provided for in OC9.4.5.2

OC9.4.5.1	Local Joint Restoration

OC9.4.5.1.1	Local Joint Restoration Plans are dependent upon Black Start Service Providers who, are registered pursuant to the Bilateral Agreement as having the ability to Start-Up from Shutdown and to energise a part of the Total System, or be Synchronised to the System, upon instruction from The Company within two hours, without an external electrical power supply ("Black Start Capability").

OC9.4.5.1.2 	For each Black Start Station and Black Start HVDC System, a Local Joint Restoration Plan will be produced jointly by The Company, the relevant Black Start Service Provider and Network Operator in accordance with the provisions of OC9.4.7.5.1. The Local Joint Restoration Plan will detail the agreed method and procedure by which a Genset at a Black Start Station (possibly with other Gensets at that Black Start Station) and Black Start HVDC Systems will energise part of the Total System and meet complementary local Demand so as to form a Power Island.

OC9.4.5.1.3	In respect of Scottish Transmission Systems, a Local Joint Restoration Plan may cover more than one Black Start Station or Black Start HVDC System and may be produced with and include obligations on Relevant Scottish Transmission Licensees, Generators responsible for Gensets not at a Black Start Station and other Users including HVDC System Owners and DC Converter Station Owners.  The instruction to initiate a Local Joint Restoration Plan in Scotland will be the responsibility of the Scottish Transmission Licensee as provided for in STCP 06-1.

OC9.4.5.2	Distribution Restoration Zones

OC9.4.5.2.1	In a Distribution Restoration Zone, Anchor Plant Owners are required to have Anchor Plant with the capability to Start-Up from Shutdown and to energise a part of a Network Operator’s System, upon instruction from theThe Network Operator within 8 hours, without an external electrical power supply. ("Anchor Plant Capability").

OC9.4.5.2.2	For each Distribution Restoration Zone, a Distribution Restoration Zone Plan will be produced jointly by the Network Operator, The Company, relevant Transmission Licensee, Anchor Plant Owner and Restoration Service Providers in accordance with the provisions of OC9.4.7.6.2.  The Distribution Restoration Zone Plan will detail the agreed method and procedure by which an Anchor Plant will energise the Distribution Restoration Zone, ie a part of the Network Operator’s System, and meet complementary local Demand so as to form a Power Island.

OC9.4.5.2.3	In respect of Scottish Transmission Systems, Scottish Transmission Licensees, may instruct relevant Network Operators to activate one or more Distribution Restoration ZonesZone Plans as provided for in STCP 06-1.  In this instance, the instruction to activate a Distribution Restoration Zone Plan to a Scottish Network Operator will be the responsibility of the Scottish Transmission Licensee.

OC9.4.6	Situations requiring Black Start

In the event of a Total Shutdown or Partial Shutdown, The Company will, as soon as reasonably practical, inform Users (or, in the case of a Partial Shutdown, Users which in The Company's opinion need to be informed) and the BSCCo that a Total Shutdown, or, as the case may be, a Partial Shutdown, exists and that The Company intends to implement a Black Start. The Company shall (as soon as is practicable) determine, in its reasonable opinion, the time and date with effect from which the Total Shutdown or Partial Shutdown commenced and notify the BSCCo of that time and date.

In the event of a Total Shutdown and following such notification, in accordance with the provisions of the BSC, the BSCCo will determine the Settlement Period with effect from which the Balancing Mechanism is suspended.

In the event of a Partial Shutdown and following such notification, the Balancing Mechanism will not be suspended until such time and date that the Market Suspension Threshold has been met, or deemed to have been met, in accordance with the provisions of the BSC.  The Company shall carry out the monitoring activities required by paragraph G3.1 of the BSC.

Following determination by The Company pursuant to its obligations under the BSC that the Market Suspension Threshold has been met, or deemed to have been met, The Company shall (as soon as practicable) inform the BSCCo of that time and date at which the Market Suspension Threshold was met, or deemed to have been met, and the BSCCo will determine the Settlement Period in accordance with the provisions of the BSC with effect from which the Balancing Mechanism will be suspended.

Should The Company determine that the Total System is capable of returning to normal operation without meeting the Market Suspension Threshold, The Company will follow the procedure given in OC9.4.7.11. .

The Black Start will conclude with effect from the time and date determined in accordance with OC9.4.7.12.

In respect of Scottish Transmission Systems, in exceptional circumstances, as specified in the Local Joint Restoration Plan, SPT or SHETL, may invoke such Local Joint Restoration Plan for its own Transmission System and Scottish Offshore Transmission Systems connected to it and operate within its provisions.  Under such circumstances a Scottish Transmission Licensee may also activate one or more Distribution Restoration Zone Plans in coordination with the relevant Network Operators.

OC9.4.7	Black Start

OC9.4.7.1	The procedure necessary for a recovery from a Total Shutdown or Partial Shutdown is known as a "Black Start".  The procedure for a Partial Shutdown is the same as that for a Total Shutdown except that it applies only to a part of the Total System.  It should be remembered that a Partial Shutdown may affect parts of the Total System which are not themselves shutdown.

OC9.4.7.2	The complexities and uncertainties of recovery from a Total Shutdown or Partial Shutdown require that OC9 is sufficiently flexible in order to accommodate the full range of User’s Plant and Apparatus and Total System characteristics and operational possibilities, and this precludes the setting out in the Grid Code itself of concise chronological sequences.  The overall strategy will, in general, include the overlapping phases of establishment of Gensets at an isolated Power Station or isolated HVDC System or isolated DC Converter Station, together with complementary local Demand, termed "Power Islands", step by step integration of these Power Islands into larger sub-systems which includes utilising the procedures in OC9.5 (Re-Synchronisation of De-Synchronised Island) and eventually re-establishment of the complete Total System.

The Company Instructions

OC9.4.7.3	The procedures for a Black Start will, therefore, be those specified by The Company at the time.  These will normally recognise any applicable Local Joint Restoration Plan and/or Distribution Restoration Zone Plan.  Users shall abide by The Company's instructions during a Black Start situation, even if these conflict with the general overall strategy outlined in OC9.4.7.2 or any applicable Local Joint Restoration Plan.  The Company's instructions may (although this list should not be regarded as exhaustive) be to:-

- a Black Start Station or Black Start HVDC System relating to the commencement of supplying Active Power, to a Network Operator or Non-Embedded Customer relating to the restoration of Demand, and to a Power Station or HVDC System or DC Converter Station relating to preparation for commencement of supplying Active Power when an external power supply is made available to it, and in each case may include the requirement to undertake switching and/or:-

- a Network Operator to activate a Distribution Restoration Zone Plan.

In respect of Scottish Transmission Systems SPT and SHETL will act on The Company’s behalf in accordance with its duties under the relevant Local Joint Restoration Plan or Distribution Restoration Zone Plan.  Scottish Users shall abide by SPT’s or SHETL’s instructions given in accordance with the Local Joint Restoration Plan or Distribution Restoration Zone Plan during a Black Start situation.

OC9.4.7.4	(a)	Black Start following a Total Shutdown or where the Balancing Mechanism has been suspended following a Partial Shutdown

During a Black Start situation where the Balancing Mechanism has been suspended, all instructions to Users in England and Wales will be deemed to be Emergency Instructions under BC2.9.2.2 (iii).  All such Emergency Instructions will recognise any differing Black Start operational capabilities (however termed) set out in the relevant Ancillary Services Agreement in preference to the declared operational capability as registered pursuant to BC1 (or as amended from time to time in accordance with the BC).  For the purposes of these instructions the Black Start will be an emergency circumstance under BC2.9.

In Scotland, Gensets or HVDC Systems or DC Converter Station that are not at Black Start Stations or Black Start HVDC Systems, but which are part of a Local Joint Restoration Plan, may be instructed in accordance with the provisions of that Local Joint Restoration Plan.

Instructions issued to Network Operators in England and Wales to activate a Distribution Restoration Zone Plan to energise a Distribution Restoration Zone will be issued by The Company to Network Operators as Emergency Instructions.  Network Operators will then proceed in accordance with the provisions of the Distribution Restoration Zone Plan.  Such instructions will (unless The Company specifies otherwise) be deemed to be Emergency Instructions under BC2.9.2.2 (iv).  The Network Operator will be responsible for the operation of the Distribution Restoration Zone which will take into account the capabilities of Anchor Plant, relevant Restoration Service Providers’ Plant and other Plant and Apparatus within the Network Operator’s System including the Distribution Restoration Zone Control System.  Such instructions would be pursuant to the terms of the Distribution Restoration Zone Plan.

In Scotland, Scottish Transmission Licensees will issue instructions (which unless specified otherwise, would be deemed to be Emergency Instructions) to relevant Scottish Network Operators to activate a Distribution Restoration Zone Plan.

(b)	Black Start following a Partial Shutdown where the Balancing Mechanism has not been suspended

During a Black Start situation where the Balancing Mechanism has not been suspended, instructions in relation to Black Start Stations and to Network Operators, Black Start HVDC Systems which are part of an invoked Local Joint Restoration Plan will (unless The Company  specifies otherwise) be deemed to be Emergency Instructions under BC2.9.2.2 (iv) and will recognise any differing Black Start operational capabilities (however termed) set out in the relevant Ancillary Services Agreement in preference to the declared operational capability as registered pursuant to BC1 (or as amended from time to time in accordance with the BC). For the purposes of these instructions the Black Start will be an emergency circumstance under BC2.9.

During a Black Start situation where the Balancing Mechanism has not been suspended, The Company may issue instructions to Users other than Black Start Stations and Network Operators which are part of an invoked Local Joint Restoration Plan. Such instructions would be Emergency Instructions pursuant to BC2.9.1.2(e)(i) subject to the requirements of BC2.9.2.2 being met.

In Scotland Gensets and HVDC Systems or DC Converter Station that are not at Black Start Stations or Black Start HVDC Systems, but which are part of an invoked Local Joint Restoration Plan, may be instructed in accordance with the provisions of that Local Joint Restoration Plan.

During Black Start where the Balancing Mechanism has not been suspended, The Company may issue instructions to Network Operators in England and Wales to activate a Distribution Restoration Zone Plan to energise one or more Distribution Restoration Zones in accordance with the provisions of the Distribution Restoration Zone Plans.  Such instructions will (unless The Company specifies otherwise) be deemed to be Emergency Instructions under BC2.9.2.2 (iv).  The Network Operator will be responsible for the operation of the Distribution Restoration Zone which will take into account the capabilities of Anchor Plant, relevant Restoration Service Providers’ Plant and other Plant and Apparatus within the Network Operator’s System including the Distribution Restoration Zone Control System. Such instructions would be pursuant to the terms of the Distribution Restoration Zone Plan.

In Scotland, Relevant Transmission Licensee’s may issue instructions (which unless specified otherwise, would be deemed to be Emergency Instructions) to Scottish Network Operators, to activate on one or more Distribution Restoration Zone Plans.

(c) Requirements to inform The Company where a Genset, HVDC System or DC Converter cannot operate within its safe operating limits during the Demand restoration process

If during the Demand restoration process, any Genset or HVDC System or DC Converter Station cannot, because of the Demand being experienced, keep within its safe operating parameters, the Black Start Service Provider shall, unless a Local Joint Restoration Plan is in operation, inform The Company. The Company will, where possible, either instruct Demand to be altered or will re-configure the National Electricity Transmission System or will instruct a User to re-configure its System in order to alleviate the problem being experienced by the Genset or HVDC System or DC Converter Station.  If a Local Joint Restoration Plan is in operation, then the arrangements set out therein shall apply.  However, The Company accepts that any decision to keep a Genset or HVDC System or DC Converter Station operating, if outside its safe operating parameters, is one for the Black Start Service Providers concerned alone and accepts that the Black Start Service Provide may change output on that Genset or HVDC System or DC Converter Station if it believes it is necessary for safety reasons (whether relating to personnel or Plant and/or Apparatus).  If such a change is made without prior notice, then the Black Start Service Provider shall inform The Company as soon as reasonably practical (unless a Local Joint Restoration Plan is in operation in which case the arrangements set out therein shall apply).

OC9.4.7.5

Local Joint Restoration Plan and Distribution Restoration Zone Plan Establishment

OC9.4.7.5.1		Local Joint Restoration Plan Establishment

(a)	In England and Wales, in relation to each Black Start Station and each Black Start HVDC System, The Company, NGET, Network Operator and the relevant Black Start Service Provider will discuss and agree a Local Joint Restoration Plan.  Where at the date of the first inclusion of this OC9.4.7.115.1 into the Grid Code a local plan covering the procedures to be covered in a Local Joint Restoration Plan is in existence and agreed, The Company will discuss this with NGET, the Network Operator and the relevant Generator or HVDC System Owner or DC Converter Station Owner to agree whether it is consistent with the principles set out in this OC9.4.  If it is agreed to be so consistent, then it shall become a Local Joint Restoration Plan under this OC9 and the relevant provisions of OC9.4.7.115.1(b) shall apply.  If it is not agreed to be so consistent, then the provisions of OC9.4.7.115.1(b) shall apply as if there is no Local Joint Restoration Plan in place.  For the avoidance of doubt, a Local Joint Restoration Plan would not cover the situation where a Distribution Restoration Zone has been established.  The requirements associated with Distribution Restoration Zones which are pursuant to a Distribution Restoration Zone Plan are covered under OC9.4.7.5.2.

In respect of Scottish Transmission Systems where a requirement for a Local Joint Restoration Plan is identified, The Company, the Relevant Scottish Transmission Licensee(s), the Network Operator and Black Start Service Providers will discuss and agree a Local Joint Restoration Plan. In addition, other Users, including other Generators or HVDC System Owners or DC Converter Station Owners, may be reasonably required by The Company to discuss and agree a Local Joint Restoration Plan.  For the avoidance of doubt, a Local Joint Restoration Plan would not cover the situation where a Distribution Restoration Zone has been established.  The requirements associated with Distribution Restoration Zones in Scotland which are pursuant to a Scottish Distribution Restoration Zone Plan are covered under OC9.4.7.5.2(b).

(b)	In England and Wales, where the need for a Local Joint Restoration Plan arises when there is none in place, the following provisions shall apply:

(i)	The Company, NGET, the Network Operator and the relevant Black Start Service Provider will discuss and agree the detail of the Local Joint Restoration Plan as soon as the requirement for a Local Joint Restoration Plan is identified by The Company. The Company will notify all affected Users and will initiate these discussions.

(ii)	Each Local Joint Restoration Plan will be in relation to a specific Black Start Station or Black Start HVDC System.

(iii)	The Local Joint Restoration Plan will record which Users and which User Sites are covered by the Local Joint Restoration Plan and set out what is required from The Company, NGET and each User should a Black Start situation arise.

(iv)	Each Local Joint Restoration Plan shall be prepared by The Company to reflect the above discussions and agreement.

(v)	Each page of the Local Joint Restoration Plan shall bear a date of issue and the issue number.

(vi)	When a Local Joint Restoration Plan has been prepared, it shall be sent by The Company to NGET and the Users involved for confirmation of its accuracy.

(vii)	The Local Joint Restoration Plan shall then (if its accuracy has been confirmed) be signed on behalf of The Company and on behalf of NGET and each relevant User by way of written confirmation of its accuracy.

(viii)	Once agreed under this OC9.4.7.115.1(b), the procedure will become a Local Joint Restoration Plan under the Grid Code and (subject to any change pursuant to this OC9) will apply between The Company and NGET and the relevant Users as if it were part of the Grid Code.

(ix)	Once signed, a copy of the Local Joint Restoration Plan will be distributed by The Company to NGET and each User which is a party to it accompanied by a note indicating the date of implementation.

(x)	The Company, NGET and Users must make the Local Joint Restoration Plan readily available to the relevant operational staff.

(xi)	If The Company, or NGET or any User which is a party to a Local Joint Restoration Plan, becomes aware that a change is needed to that Local Joint Restoration Plan, it shall (in the case of The Company) initiate a discussion between The Company and the relevant Users to seek to agree the relevant change.  If NGET or a User becomes so aware, it shall contact The Company who will then initiate such discussions. The principles applying to establishing a new Local Joint Restoration Plan under this OC9.4.7.115.1(b) shall apply to such discussions and to any consequent changes.

The objectives of such exercises include:

- To test the effectiveness of the Local Joint Restoration Plan;

- To provide for joint training of the parties in respect of the Local Joint Restoration Plan;

- To maintain the parties’ awareness and familiarity of the Local Joint Restoration Plan;

- To promote understanding of each parties’ roles under a Local Joint Restoration Plan;

- To identify any improvement areas which should be incorporated

- OC9.4.7.11

The Company will propose to the parties of a Local Joint Restoration Plan a date for the exercise to take place, to be agreed with the other parties.  All the Local Joint Restoration Plan parties will jointly share the task of planning, preparing, participating in and facilitating the exercises, which will normally be in desktop format or as otherwise agreed.  The precise timing of the exercise for each Local Joint Restoration Plan will be agreed by all parties, but will not be less than

(c)	In respect of Scottish Transmission Systems, where the need for a Local Joint Restoration Plan arises, the following provisions shall apply:

(i)	The Company, the Relevant Scottish Transmission Licensee(s), the Network Operator and the relevant Black Start Service Provider will discuss and agree the detail of the Local Joint Restoration Plan as soon as the requirement for a Local Joint Restoration Plan is identified by The Company. In addition, other Scottish Users, including other Generators, HVDC System Owners and DC Converter Station Owners, may be reasonably required by The Company to discuss and agree details of the Local Joint Restoration Plan as soon as the requirement for a Local Joint Restoration Plan is identified by The Company. The Company will notify the Relevant Scottish Transmission Licensee(s) and all affected Scottish Users, and will initiate these discussions.

(ii)	Each Local Joint Restoration Plan may be in relation to either a specific Black Start Station or a number of Black Start Stations, and may include Gensets at Power Stations other than a Black Start Station. Each Local Joint Restoration Plan could equally apply to a specific Black Start HVDC System or a number of Black Start HVDC Systems and may include HVDC Systems or DC Converter Stations other than a Black Start HVDC System.  For the avoidance of doubt, this would not preclude a Local Joint Restoration Plan from comprising a combination of Power Stations, HVDC Systems or DC Converter Stations irrespective of whether they have a Black Start Capability.

(iii)	The Local Joint Restoration Plan will record which Scottish Users and which Scottish User Sites are covered by the Local Joint Restoration Plan and set out what is required from The Company, the Relevant Scottish Transmission Licensee(s) and each Scottish User should a Black Start situation arise.

(iv)	Each Local Joint Restoration Plan shall be prepared by The Company to reflect the above discussions and agreement.

(v)	Each page of the Local Joint Restoration Plan shall bear a date of issue and the issue number.

(vi)	When a Local Joint Restoration Plan has been prepared, it shall be sent by The Company to the Relevant Scottish Transmission Licensee(s) and Scottish Users involved for confirmation of its accuracy.

(vii)	The Local Joint Restoration Plan shall then (if its accuracy has been confirmed) be signed on behalf of The Company and on behalf of each relevant Scottish User and Relevant Scottish Transmission Licensee(s) by way of written confirmation of its accuracy.

(viii)	Once agreed under this OC9.4.7.115.1(c), the procedure will become a Local Joint Restoration Plan under the Grid Code and (subject to any change pursuant to this OC9) will apply between The Company, Relevant Scottish Transmission Licensees and the relevant Scottish Users as if it were part of the Grid Code.

(ix)	Once signed, a copy of the Local Joint Restoration Plan will be distributed by The Company to the Relevant Scottish Transmission Licensee(s) and each Scottish User which is a party to it accompanied by a note indicating the date of implementation.

(x)	The Company, the Relevant Scottish Transmission Licensee(s) and Scottish Users must make the Local Joint Restoration Plan readily available to the relevant operational staff.

(xi)	If The Company, the Relevant Scottish Transmission Licensee(s) or any Scottish User which is a party to a Local Joint Restoration Plan, becomes aware that a change is needed to that Local Joint Restoration Plan, it shall (in the case of The Company) initiate a discussion between The Company, the Relevant Scottish Transmission Licensee(s) and the relevant Scottish Users to seek to agree the relevant change.  If a Scottish User or a Relevant Scottish Transmission Licensee becomes so aware, it shall contact The Company who will then initiate such discussions. The principles applying to establishing a new Local Joint Restoration Plan under this OC9.4.7.115.1(c) shall apply to such discussions and to any consequent changes.

OC9.4.7.5.2	Distribution Restoration Zone Plan Establishment

(a)	In England and Wales, where The Company believe that a Distribution Restoration Zone would be beneficial, The Company, NGET and Network Operator shallexplore the possibility of establishing a Distribution Restoration Zone Plan, the following provisions shall apply:

(i)	The Company, NGET and the Network Operator will discuss and agree the detail of a Distribution Restoration Zone Plan as soon as reasonably practicable after the potential requirement for a Distribution Restoration Zone Plan is identified by  The Company. mayThis may involve relevant potential Restoration Service Providers.  The Company in conjunction with the Network Operator and will initiate these discussions.  An initial feasibility assessment carried out jointly by The Company and the Network Operators may result in The Company running a procurement /tender process. .  .  If after discussions or analysis, The Company, NGET and Network Operator agree a Distribution Restoration Zone Plan is not viable, then no further work to develop the Distribution Restoration Zone Plan needs to be carried out.

(ii)	Each Distribution Restoration Zone Plan will be in relation to a specific part of the Network Operator’s System and in each case each Distribution Restoration Zone Plan will be specific to a single Anchor Plant.

(iii)	The Distribution Restoration Zone Plan will record the relevant Restoration Service Providers and the relevant Restoration Service Providers’ Plant and Apparatus and set out what is required from The Company, NGET, Network Operator and each relevant Restoration Service Provider.  It shall include the detailed requirements for the routine testing of Restoration Services Provider’s Plant and Apparatus for the contracted services provided, in accordance with the procedures in OC.5.7.4.

(iv)	Each Distribution Restoration Zone Plan shall be prepared by the relevant Network Operator and agreed with The Company, NGET and relevant Restoration Service Providers to reflect the above discussions and agreement.

(v)	Each Distribution Restoration Zone Plan will include the test criteria to be satisfied by each Restoration Service Provider’s Plant and Apparatus when subject to the testing requirements of OC5.7.4.

(vi)	Each page of the Distribution Restoration Zone Plan shall bear a date of issue and the issue number.

(vii)	When a Distribution Restoration Zone Plan has been prepared, it shall be sent by the relevant Network Operator to The Company, NGET and the relevant Restoration Service Providers involved for confirmation of its accuracy.

(viii)	The Distribution Restoration Zone Plan shall then (pending its accuracy being confirmed) be signed on behalf of the Network Operator, The Company, NGET and each relevant Restoration Service Provider as a written confirmation of its accuracy.

(ix)	Once agreed under this OC9.4.7.5.2(a), the procedure shall become a Distribution Restoration Zone Plan under the Grid Code and Distribution Code (subject to any change pursuant to this OC9 and DOC9 of the Distribution Code) and will apply between The Company, NGET, Network Operator and the relevant Restoration Service Provider(s) as if it were part of the Grid Code.

(x)	Once signed, a copy of the Distribution Restoration Zone Plan shall be distributed by the Network Operator to The Company, NGET and each relevant Restoration Service Provider which is a party to it, indicating the date of implementation.

(xi)	The Network Operator, The Company, NGET and relevant Restoration Service Providers must make the Distribution Restoration Zone Plan readily available to the relevant operational staff.

(xii)	If the Network Operator, The Company, NGET or any other relevant Restoration Service Provider which is a party to a Distribution Restoration Zone Plan, becomes aware that a change is needed to that Distribution Restoration Zone Plan, it shall initiate a discussion between the Network Operator, The Company, NGET, and the relevant Restoration Service Provider(s) to seek to agree the relevant change.  If a Network Operator, or relevant Restoration Service Provider becomes so aware, it shall contact The Company in coordination with the Network Operator who will then initiate such discussions. The principles applying to establishing a new Distribution Restoration Zone Plan under this OC9.4.7.5.2(a) shall apply to such discussions and to any consequent changes.

(b)	In respect of Scottish Transmission Systems, where the need for a Distribution Restoration Zone Plan arises, the following provisions shall apply:

(i)	The Company, the Relevant Scottish Transmission Licensee(s), the Network Operator and the relevant Restoration Service Providers (including Anchor Plant Owners) will discuss and agree the detail of the Distribution Restoration Zone Plan as soon as the requirement for a Distribution Restoration Zone Plan is identified by The Company. In addition, other potential Restoration Service Providers located within a Scottish Distribution Restoration Zone including other Generators, HVDC System Owners and DC Converter Owners, may be reasonably required by The Company and Network Operator to discuss and agree details of the Distribution Restoration Zone Plan as soon as reasonably practicable after the requirement for a Distribution Restoration Zone Plan is identified by The Company.  The Company will notify the Relevant Scottish Transmission Licensee(s) and Network Operator of the initiation of the Distribution Restoration Zone Plan development.  The Network Operator will be responsible for notifying all affected Scottish Restoration Service Providers party to one or more Distribution Restoration Zones.

(ii)	Each Distribution Restoration Zone Plan will be in relation to a specific Network Operator’s System and will include The Company, the Relevant Scottish Transmission Licensee, relevant Network Operator and relevant Restoration Service Providers.

(iii)	The Distribution Restoration Zone Plan will record which Restoration Service Providers and which of their sites are within the scope of the Distribution Restoration Zone Plan and set out what is required from the relevant Network Operator, The Company, the Relevant Scottish Transmission Licensee(s) and each relevant Restoration Service Provider should a Black Start situation arise.  It shall include the detailed requirements for the routine testing of any Restoration Services Provider’s Plant and Apparatus for the contracted services provided, in accordance with the procedures in OC.5.7.4.

(iv)	Each Distribution Restoration Zone Plan shall be prepared by the relevant Scottish Network Operator in coordination with The Company to reflect the above discussions and agreement.

(v)	Each Distribution Restoration Zone Plan will include the test criteria to be satisfied by each Restoration Service Provider’s Plant and Apparatus when subject to the testing requirements of OC5.7.4.

(vi)	Each page of the Distribution Restoration Zone Plan shall bear a date of issue and the issue number.

(vii)	When a Distribution Restoration Zone Plan has been prepared, it shall be sent by the relevant Network Operator to The Company, the Relevant Scottish Transmission Licensee(s) and the relevant Restoration Service Providers involved for confirmation of its accuracy.

(viii)	The Distribution Restoration Zone Plan shall then (if its accuracy has been confirmed) be signed by the relevant Network Operator, The Company, the Relevant Scottish Transmission Licensee(s) and Relevant Restoration Service Providers to confirm accuracy.

(ix)	Once agreed under this OC9.4.7.5.2(b), the procedure will become a Distribution Restoration Zone Plan under the Grid Code and Distribution Code (subject to any change pursuant to this OC9 and DOC9 of the Distribution Code) and will apply between The Company, Scottish Transmission Licensee, the Network Operator and the relevant Restoration Service Providers as if it were part of the Grid Code.

(x)	Once signed, a copy of the Distribution Restoration Zone Plan shall be distributed by the relevant Network Operator to The Company, the Relevant Scottish Transmission Licensee(s) and each relevant Restoration Service Provider which is a party to it accompanied by a note indicating the date of implementation.

(xi)	The Network Operator, The Company, the Relevant Scottish Transmission Licensee(s) and each relevant Restoration Service Provider must make the Distribution Restoration Zone Plan readily available to the relevant operational staff.

(xii)	If the relevant Network Operator, The Company, the Relevant Scottish Transmission Licensee(s) or any relevant Restoration Service Provider which is a party to a Distribution Restoration Zone Plan, becomes aware that a change is needed to that Distribution Restoration Zone Plan, it shall initiate a discussion between the relevant Network Operator, The Company, the Relevant Scottish Transmission Licensee(s) and the relevant Restoration Service Provider(s) to seek to agree the relevant change.  If a Network Operator, a Relevant Scottish Transmission Licensee or relevant Restoration Service Provider becomes so aware, it shall contact The Company in coordination with the Network Operator who will then initiate such discussions. The principles applying to establishing a new Distribution Restoration Zone Plan under this OC9.4.7.5.2(b) shall apply to such discussions and to any consequent changes.

OC9.4.7.5.3	Local Joint Restoration Plan and Distributed Restoration Plan Testing

- Local Joint Restoration Plan testing in England and Wales

The Company, NGET, the Network Operator and the relevant Generator or HVDC System Owner or DC Converter Station Owner shall conduct regular joint exercises of the Local Joint Restoration Plan to which they are parties.  The objectives of such exercises include:

- To test the effectiveness of the Local Joint Restoration Plan;

- To provide for joint training of the parties in respect of the Local Joint Restoration Plan;

- To maintain the parties’ awareness and familiarity of the Local Joint Restoration Plan;

- To promote understanding of each parties’ roles under a Local Joint Restoration Plan; and

- To identify any improvement areas which should be incorporated into the Local Joint Restoration Plan.

- The principles applying to the establishment of a new Local Joint Restoration Plan under this OC9.4.7.5.1(b) shall apply to any changes to the Local Joint Restoration Plan.

The Company will propose to the parties of a Local Joint Restoration Plan a date for the exercise to take place, to be agreed with the other parties.  All the Local Joint Restoration Plan parties will jointly share the task of planning, preparing, participating in and facilitating the exercises, which will normally be in desktop format or as otherwise agreed.  The precise timing of the exercise for each Local Joint Restoration Plan will be agreed by all parties, but will not be less than once every 5 years.

- Local Joint Restoration Plan testing in Scotland

The Company, the Relevant Scottish Transmission Licensee(s), the Network Operator and the relevant Black Start Service Provider will conduct regular joint exercises of the Local Joint Restoration Plan to which they are parties.  The objectives of such exercises include:

- To test the effectiveness of the Local Joint Restoration Plan;

- To provide for joint training of the parties in respect of the Local Joint Restoration Plan;

- To maintain the parties’ awareness and familiarity of the Local Joint Restoration Plan;

- To promote understanding of each parties’ roles under a Local Joint Restoration Plan; and

- To identify any improvement areas which should be incorporated in to the Local Joint Restoration Plan.

- The principles applying to the establishment of a new Local Joint Restoration Plan under this OC9.4.7.115.1(c) shall apply to any changes to the Local Joint Restoration Plan.

The Company will propose to the parties of a Local Joint Restoration Plan a date for the exercise to take place, to be agreed with the other parties.  All the Local Joint Restoration Plan parties will jointly share the task of planning, preparing, participating in and facilitating the exercises, which will normally be in desktop format or as otherwise agreed.  The precise timing of the exercise for each Local Joint Restoration Plan will be agreed by all parties, but will not be less than once every 5 years.

- Distribution Restoration Zone Plan testing in England and Wales

The Company, NGET, the Network Operator and the relevant Restoration Service Provider(s) will conduct regular joint exercises of the Distribution Restoration Zone Plan to which they are parties.  The objectives of such exercises include:

- To test the effectiveness of the Distribution Restoration Zone Plan;

- To provide for joint training of the parties in respect of the Distribution Restoration Zone Plan;

- To maintain the parties’ awareness and familiarity of the Distribution Restoration Zone Plan;

- To promote understanding of each parties’ roles under the Distribution Restoration Zone Plan;

- To identify any improvement areas which should be incorporated into the Distribution Restoration Zone Plan.

- The principles applying to the establishment of a new Distribution Restoration Zone Plan under this OC9.4.7.5.2(a) shall apply to any changes to the Distribution Restoration Zone Plan.

The Company in coordination with the Network Operator will propose to the other parties of a Distribution Restoration Zone Plan a date for the exercise to take place to be agreed with the other parties.  All the Distribution Restoration Zone parties will jointly share the task of planning, preparing, participating in and facilitating the exercises, which will normally be in desktop format or as otherwise agreed.  The precise timing of the exercise for each Distribution Restoration Zone Plan will be agreed by all parties, but will not be less than once every 5 years.

- Distribution Restoration Zone Plan testing in Scotland

The Company, the Relevant Scottish Transmission Licensee(s), the Network Operator and the Relevant Restoration Service Providers will conduct regular joint exercises of the Distribution Restoration Zone Plan to which they are parties.  The objectives of such exercises include:

- To test the effectiveness of the Distribution Restoration Zone Plan;

- To provide for joint training of the parties in respect of the Distribution Restoration Zone Plan;

- To maintain the parties’ awareness and familiarity of the Distribution Restoration Zone Plan;

- To promote understanding of each parties’ roles under the Distribution Restoration Zone Plan;

- To identify any improvement areas which should be incorporated into the Distribution Restoration Zone Plan.

- The principles applying to the establishment of a new Distribution Restoration Zone Plan under this OC9.4.9 shall apply to any changes to the Distribution Restoration Zone Plan.

The Company in coordination with the Relevant Network Operator and Relevant Scottish Transmission Licensee will propose to the parties of a Distribution Restoration Zone Plan a date for the exercise to take place, to be agreed with the other parties.  All the Distribution Restoration Zone Plan parties will jointly share the task of planning, preparing, participating in and facilitating the exercises, which will normally be in desktop format or as otherwise agreed.  The precise timing of the exercise for each Distribution Restoration Zone Plan will be agreed by all parties but will not be less than one every 5 years.

OC9.4.7.6	Local Joint Restoration Plan and Distribution Restoration Zone Plan provisions.

OC9.4.7.6.1.	Local Joint Restoration Plan

(a)	The following provisions apply in relation to a Local Joint Restoration Plan.  A Distribution Restoration Zone shall not form part of a Local Joint Restoration Plan but instead would be treated separately under a Distribution Restoration Zone Plan as detailed in OC9.4.7.5.2.  As set out in OC9.4.7.3, The Company may issue instructions which conflict with a Local Joint Restoration Plan.  In such cases, these instructions will take precedence over the requirements of the Local Joint Restoration Plan. When issuing such instructions, The Company shall state whether or not it wishes the remainder of the Local Joint Restoration Plan to apply.  If, notwithstanding the conflict, The Company has stated that it wishes the remainder of the Local Joint Restoration Plan to apply, the Black Start Service Provider or the relevant Network Operator consider that The Company’s instructions mean that it is not possible to operate the Local Joint Restoration Plan as modified by those instructions, any of them may give notice to The Company and the other parties to the Local Joint Restoration Plan to this effect and The Company shall immediately consult with all parties to the Local Joint Restoration Plan.  Unless all parties to the Local Joint Restoration Plan reach an agreement forthwith as to how the Local Joint Restoration Plan shall operate in those circumstances, operation in accordance with the Local Joint Restoration Plan will terminate.

(b)	Where The Company, as part of a Black Start, has given an instruction to a Black Start Service Provider to initiate Start-Up, the relevant Genset(s) at the Black Start Station or Black Start HVDC System will Start-Up in accordance with the Local Joint Restoration Plan.

(c)	The Company will advise the relevant Network Operator of the requirement to switch its User System to segregate its Demand and to carry out such other actions as set out in the Local Joint Restoration Plan.  The relevant Network Operator will then operate in accordance with the provisions of the Local Joint Restoration Plan.

(d)	The Company will ensure that switching carried out on the National Electricity Transmission System and other actions are as set out in the Local Joint Restoration Plan.

(e)	Following notification from the Black Start Service Provider that the Black Start Station or Black Start HVDC System is ready to accept load, The Company will instruct the Black Start Service Provider to energise part of the Total System.  The Black Start Service Provider and the relevant Network Operator will then, in accordance with the requirements of the Local Joint Restoration Plan, establish communication and agree the output of the relevant Genset(s) and/or HVDC System and/or DC Converter Station and the connection of Demand so as to establish a Power Island.  During this period, the Black Start Service Provider will be required to regulate the output of the relevant Black Start Station or Black Start HVDC System to the Demand prevailing in the Power Island in which it is situated, on the basis that it will (where practicable) seek to maintain the Target Frequency.  The Genset(s) at the Black Start Station or Black Start HVDC System will (where practical) also seek to follow the requirements relating to Reactive Power (which may include the requirement to maintain a target voltage) set out in the Local Joint Restoration Plan.

(f)	Operation in accordance with the Local Joint Restoration Plan will be terminated by The Company (by notifying the relevant Users) prior to connecting the Power Island to other Power Islands (other than, in Scotland, as allowed for in the Local Joint Restoration Plan), or to the User System of another Network Operator, or to the synchronising of Gensets at other Power Stations or HVDC Systems or DC Converter Station (other than, in Scotland, those forming part of the Local Joint Restoration Plan).  Operation in accordance with the Local Joint Restoration Plan will also terminate in the circumstances provided for in OC9.4.7.5.1 if an agreement is not reached or if The Company states that it does not wish the remainder of the Local Joint Restoration Plan to apply.  Users will then comply with the Bid-Offer Acceptances or Emergency Instructions of The Company.

(g)	In Scotland, Gensets or HVDC Systems or DC Converter Stations included in a Local Joint Restoration Plan, but not at a Black Start Station or Black Start HVDC System, will operate in accordance with the requirements of the Local Joint Restoration Plan.

OC9.4.7.6.2	Distribution Restoration Zone Plan

(a)	The following provisions apply in relation to a Distribution Restoration Zone Plan.  For the avoidance of doubt, a Local Joint Restoration Plan would not be considered to incorporate  a Distribution Restoration Zone but instead would be treated under a Local Joint Restoration Plan as detailed in OC9.4.7.5.1.  As set out in OC9.4.7.3, The Company may issue instructions which conflict with a Distribution Restoration Zone Plan.  In such cases, these instructions will take precedence over the requirements of the Distribution Restoration Zone Plan.  When issuing such instructions, The Company shall state whether or not it wishes the remainder of the Distribution Restoration Zone Plan to apply.  If, notwithstanding the conflict, The Company has stated that it wishes the remainder of the Distribution Restoration Zone Plan to apply, the Network Operator or the relevant  Restoration Service Provider(s) consider that The Company’s instructions mean that it is not possible to operate the Distribution Restoration Zone Plan as modified by those instructions, any of them may give notice to The Company and the other parties to the Distribution Restoration Zone Plan to this effect and The Company shall immediately consult with all parties to the Distribution Restoration Zone Plan.  Unless all parties to the Distribution Restoration Zone Plan reach an agreement forthwith as to how the Distribution Restoration Zone Plan shall operate in those circumstances, operation in accordance with the Distribution Restoration Zone Plan will terminate.

(b)	Where The Company, as part of a Black Start condition, has given an instruction to a Network Operator to activate a Distribution Restoration Zone Plan, the relevant Restoration Service Provider(s) will Start-Up their Plant in accordance with the Distribution Restoration Zone Plan.

(c)	The Company will ensure that switching is carried out on the National Electricity Transmission System and other actions are as set out in the Distribution Restoration Zone Plan.

(d)	Following confirmation from the Network Operator and Relevant Transmission Licensee that their Systems have been configured to form a Distribution Restoration Zone, the necessary protection, control and any automatic facilities (including the use of a Distribution Restoration Zone Control System if applicable) are ready and relevant Restoration Service Providers are ready, The Company will instruct the Network Operator to instruct the Anchor Plant Owner  to energise the appropriate part of the Network Operator’s System.  The Network Operator will then, in accordance with the requirements of the Distribution Restoration Zone Plan, establish communication and agree the output of the relevant Anchor Plant, the operation of relevant Restoration Service Providers Plant and Apparatus and the reconnection of Demand so as to establish a Power Island.  During this period, the Network Operator or Distribution Restoration Control System will manage the output of the relevant Anchor Plant and relevant Restoration Service Providers’ Plant to the Demand prevailing in the Power Island, on the basis that it will (where practicable) seek to maintain the Target Frequency.  Relevant Restoration Service Providers will (where reasonably practicable) shall seek to follow the requirements relating to Reactive Power (which may include the requirement to maintain a target voltage) set out in the Distribution Restoration Zone Plan.

(e)	Operation in accordance with the Distribution Restoration Zone Plan will be terminated by The Company (by notifying the relevant Users) when appropriate to do so which would be dependent upon System conditions.  Operation in accordance with the Distribution Restoration Zone Plan will also terminate in the circumstances provided for in OC9.4.7.6.2(a) if an agreement is not reached or if The Company states that it does not wish the remainder of the Distribution Restoration Zone Plan to apply.

OC9.4.7.7	Distribution Restoration Zone Operation

Following a Total or Partial Shutdown the following shall apply:

OC9.4.7.7.1	In England and Wales a Distribution Restoration Zone is activated where The Company issues Emergency Instructions to the relevant Network Operators to re-energise a section of their disconnected System using relevant Restoration Service Provider’s Plant and Apparatus to form one or more Power Islands.  In Scotland the Relevant Transmission Operator will instruct the relevant Network Operator, following an instruction to do so from The Company.

OC9.4.7.7.2	It is imperative that where a Network Operator has a Distribution Restoration Zone Plan available for use, the Anchor Plant forming part of that Distribution Restoration Zone is capable of satisfying the requirements of CC.8.1 or ECC.6.3.5, as appropriate, and that the Network Operator has confirmed to The Company that the Distribution Restoration Zone Plan is ready to activate.

OC9.4.7.7.3	Where The Company wishes a Network Operator to activate a Distribution Restoration ZonesZone Plan, The Company will issue an Emergency Instruction to that Network Operator for it to activate the relevant Distribution Restoration Zone Plan.  In Scotland the instruction to a Scottish Network Operator to activate a Scottish Distribution Restoration Zone Plan would be undertaken by the relevant Scottish Transmission Licensee.  For the avoidance of doubt, The Company will issue instructions to initiate Black Start in Scotland via STCP 06-1 which includes arrangements for the activation of Scottish Distribution Restoration ZonesZone Plans.

OC9.4.7.7.4	Upon receipt of an Emergency Instruction from The Company (or instruction from the relevant Scottish Transmission Licensee), the Network Operator will confirm and acknowledge receipt in accordance with the requirements of BC2.9.2 and start initiating the process to activate the Distribution Restoration Zone Plan in accordance with the Distribution Restoration Zone Plan.

OC9.4.7.7.5	Upon receipt of the Emergency Instruction from The Company (or instruction from the relevant Scottish Transmission Licensee) to the Network Operator to activate a Distribution Restoration Zone Plan as provided for in OC9.4.7.7.4, all instructions to relevant Restoration Service Providers party to the Distribution Restoration Zone Plan will be issued by the Network Operator.  All instructions to Restoration Service Providers forming part of the Distribution Restoration Zone will be issued by the relevant Network Operator.  The operation of the Distribution Restoration Zone will then continue in accordance with OC 9.4.7.7 and the Distribution Restoration Zone Plan until the Distribution Restoration Zone Plan can be terminated as provided for in that Distribution Restoration Zone Plan.  From that point instructions to Users and Restoration Service Providers will revert back to the provisions of the Grid Code Operating Codes and Balancing Codes, as appropriate, covering normal operating conditions.

OC9.4.7.7.6	Where The Company issues an Emergency Instruction (or in Scotland where a Scottish Transmission Licensee issues an instruction) to a Network Operator to activate a Distribution Restoration Zone Plan, the Network Operator will first issue instructions to the Anchor Plant Owner informing the Anchor Plant Owner of the requirement to prepare thetheir Anchor Plant to re-energise a Distribution Restoration Zone (or part thereof) in accordance with the Distribution Restoration Zone Plan.  The Network Operator in liaison with the Anchor Plant Owner will discuss when their Anchor Plant is expected to be available and ready to start re-energising the Distribution Restoration Zone.  For the avoidance of doubt, the Anchor Plant Owner shall not start to re-energise the Distribution Restoration Zone until given a formal instruction by the Network Operator in accordance with OC9.4.7.7.12 and this instruction shall only be given once the Network Operator has configured its System and taken the necessary additional actions to prepare the Distribution Restoration Zone to be re-energised.  This will include any automatic switching that takes place through the action of a Distribution Restoration Zone Control System.

OC9.4.7.7.7	Following activation of the Distribution Restoration Zone Plan in accordance with OC9.4.7.7.6, the Network Operator will then issue instructions to other relevant Restoration Service Providers party to the Distribution Restoration Zone Plan to inform them that a Distribution Restoration Zone Plan has been activated and to prepare their Plant and Apparatus so that it is in a state of readiness for contributing to the further planned operation of the Distribution Restoration Zone.  All relevant Restoration Service Providers will inform the Network Operator of the indicative time of when their Plant and Apparatus will be in a state of readiness to be re-energised and/or Synchronised to the Distribution Restoration Zone.  Relevant Restoration Service Providers shall not start to re-energize or Synchronise to the Distribution Restoration Zone until given a formal instruction by the Network Operator in accordance with OC9.4.7.7.12.  Such instructions would only be issued to relevant Restoration Service Providers other than the Anchor Plant Owner once the Network Operator has re-energised the Distribution Restoration Zone (or part thereof) by issuing instructions to the Anchor Plant Owner and the Distribution Restoration Zone is in a position to expand and supply more Demand in accordance with the Distribution Restoration Zone Plan.  These instructions can also be issued automatically by a Distribution Restoration Zone Control System.

OC9.4.7.7.8	The Network Operator shall inform The Company (and the relevant Scottish Transmission Licensee in the case of a Scottish Distribution Restoration Zone) advising that it has contacted the appropriate Anchor Plant Owner and Restoration Service Providers in accordance with the Distribution Restoration Zone Plan and provide an indicative time of when the Distribution Restoration Zone and associated Plant and Apparatus is ready to be re-energised and the expected time of when the Anchor Plant Owner in a position to re-energise the Distribution Restoration Zone (or part thereof).

OC9.4.7.7.9	In addition to the requirements of OC9.4.7.7.6 to OC9.4.7.7.8, the Network Operator shall start to reconfigure its System such that it is in an appropriate state of readiness to enable the Anchor Plant Owner to re-energise Distribution Restoration Zone (or part thereof) in accordance with the Distribution Restoration Zone Plan.  To enable this process to take place, the Network Operator may need to change the topology and status of its System which may include but shall not be limited to changing the status of circuit breakers in addition to adjusting control system and Protection settings.  Reconfiguration of the Network Operator’s System prior to re-energisation of the Distribution Restoration Zone, may be achieved by instructions carried out by manual means, switching carried out remotely from the Network Operators Control Centre or via fully automatic means which could include a Distribution Restoration Zone Control System.

OC9.4.7.7.10	Once the Network Operator has reconfigured its System and associated Plant and Apparatus (including but not limited to Protection and control system settings) it will contact the Anchor Plant Owner (which could also be achieved by the Distribution Restoration Zone Control System) to confirm the foregoing and agree a time for the Anchor Plant Owner to operate their Plant so as to re-energise the Distribution Restoration Zone (or part thereof). Where the Anchor Plant Owner or Network Operator needs to change the agreed re-energisation time as a result of an unforeseen event such as, but not limited to, a faulty item of Plant or Apparatus, safety issue or unavailability of personnel, the Anchor Plant Owner and/or Network Operator will agree a revised re-energisation time.

OC9.4.7.7.11	The Network Operator will inform The Company (or relevant Scottish Transmission Licensee in the case of a Scottish Distribution Restoration Zone) of the time when the Anchor Plant Owner is scheduled to re-energise a section of the Network Operator’s System.  Should this scheduled time vary, the Network Operator will inform The Company (or relevant Scottish Transmission Licensee in the case of a Scottish Distribution Restoration Zone) as necessary and provide an indication of any revised re-energisation time and the reason for the change.

OC9.4.7.7.12	At the agreed re-energisation time as detailed in OC.9.4.7.8.11, the Network Operator will contact the Anchor Plant Owner and issue an instruction to the Anchor Plant Owner to re-energise the Distribution Restoration Zone (or part thereof) unless this is achieved via fully automatic means which could include a Distribution Restoration Zone Control System.  Following the issue of instructions to the Anchor Plant Owner, and successful re-energization of the Distribution Restoration Zone (or part thereof) the Network Operator will instruct other Restoration Service Providers in the Distribution Restoration Zone as part of the wider restoration phase which again could be achieved through fully automatic means using a Distribution Restoration Zone Control System.

OC9.4.7.7.13	Once the Distribution Restoration Zone (or part thereof) has been re-energised and feeding some local Demand or controllable Demand provided by a relevant Restoration Service Provider, the Anchor Plant Owner will be required to follow instruction from the Network Operator (or via fully automatic means which could include a Distribution Restoration Zone Control System) as envisaged in the Distribution Restoration Zone Plan.  The Network Operator and/or Distribution Restoration Zone Control System shall issue instructions to the Anchor Plant Owner as necessary to ensure the Distribution Restoration Zone continues to run in a stable manner.  The Network Operator will restore additional Demand or instruct the relevant Restoration Service Providers to do so, when it is appropriate to do so.  As part of this process, the Network Operator in coordination with the Anchor Plant Owner shall ensure risks to the Network Operator’s System or the Anchor Plant, that could arise through disturbances in the Distribution Restoration Zone, are minimised.  as far as reasonably practicable.  This may be assisted through a planned series of re-energisation steps within the Distribution Restoration Zone, taking account of the Anchor Plant capability and performance at this time.

OC9.4.7.7.14	Demand within the Distribution Restoration Zone can be restored by manual or remote controlled switching, or automatically by a Distribution Restoration Zone Control System.  If during the Demand restoration process any relevant Restoration Service Providers Plant or Apparatus cannot, because of the nature of the Demand being supplied, keep within its safe operating parameters, the relevant Restoration Service Provider shall inform the Network Operator without undue delay who in turn shall inform The Company.  In the case of a Distribution Restoration Zone in Scotland the Scottish Network Operator shall inform the relevant Scottish Transmission Licensee.

The relevant Network Operator or Distribution Restoration Zone Control System will, where possible:

- Instruct relevant Restoration Service Providers to alter their Demand; or

- will re-configure the Distribution Restoration Zone; or

- will instruct the relevant Restoration Service Provider forming part of the Distribution Restoration Zone to re-configure its System in order to alleviate the problem.

The Company and Network Operator (and Relevant Transmission Licensee in Scotland) accepts that any decision to keep a relevant Restoration Service Provider’s Plant or Apparatus operating, if outside its safe operating parameters, is one for the Restoration Service Provider concerned alone.  The Company, the Network Operator, and the Relevant Scottish Transmission Licensee (for Distribution Restoration Zones in Scotland) accepts that the relevant Restoration Service Provider’s Plant and Apparatus may have its operating point changed by the relevant Restoration Service Provider if it believes it is necessary for safety reasons (whether relating to personnel or Plant and/or Apparatus).  If such a change is made without prior notice, then the relevant Restoration Service Provider shall inform the Network Operator as soon as reasonably practical.

OC9.4.7.7.15	To stabilise the voltage and Frequency of the Network Operator’s System and increase the Demand supplied within the Distribution Restoration Zone, the Network Operator may need to instruct additional relevant Restoration Service Providers to synchroniseSynchronise their Plant to the Distribution Restoration Zone, either via manual instruction or through the use of a Distribution Restoration Zone Control System.  For the avoidance of doubt, the overall control of System Frequency during Black Start is the responsibility of The Company, although The Company will require Transmission Licensees in Scotland to manage the Frequency and voltage of Power Islands in Scotland as provided for in STCP 06-1 or Network Operators to manage the Frequency and voltage of Distribution Restoration Zones.

OC9.4.7.7.16	With the Distribution Restoration Zone operating as described in OC9.4.7.7.14 and OC9.4.7.7.15 and in accordance with the Distribution Restoration Zone Plan, the Network Operator shall then undertake a step by step process of re-energising more elements of its System by restoring auxiliary supplies to substations, other Users and the restoration of supplies to Customers.   in accordance with the Distribution Restoration Zone Plan.  These steps may include energisation of parts of the Transmission System where provided for in the Distribution Restoration Zone Plan.  During this phase, each relevant Restoration Service Provider’s Plant and Apparatus is to be operated within its designed operational limits.  The Network Operator and/or the Distribution Restoration Zone Control System shall ensure Restoration Service Providers are able (where applicable) to contribute to voltage and Frequency control and ensure that adequate positive and negative headroom is maintained on relevant Plant and Apparatus to enable the management of Power Island contingences.  During this period, there may be a need to instruct relevant Restoration Service Providers to Synchronise additional Plant and Apparatus, or to change operating points of Plant and Apparatus already Synchronised, to balance the Distribution Restoration Zone.

OC9.4.7.7.17	As the Distribution Restoration Zone supports increasing Demand, and as implementation of the Distribution Restoration Plan progresses, the Network Operator may need to update the Protection and control settings as the need arises.

OC9.4.7.7.18	Once the Distribution Restoration Zone is in stable operation, the Network Operator and/or Distribution Restoration Zone Control System shall ensure that that relevant Restoration Service Provider’s Plant and Apparatus are operated with sufficient headroom to be able to contribute to voltage and Frequency control, and in accordance with the safe operating limits in accordance with OC.9.4.7.8.14.  This is an essential pre-requisite to enable the Power Island to withstand volatility in Demand and generation, Network Operator interaction or credible faults and disturbances.

OC9.4.7.7.19	Expansion of a Distribution Restoration Zone to a Transmission busbar and to wider parts of the Transmission System would fall under the Distribution Restoration Zone Plan and the requirements of OC9.5.

Expansion of Power Islands

OC9.4.7.8	The Company will instruct the relevant Users to expand Power Islands to achieve larger sub-systems.

OC9.4.7.9	As part of Black Start, each Network Operator which:-

- has an Embedded Black Start Station or an Embedded HVDC System or Embedded DC Converter Station, and which has established a Power Island, howsoever arising within its User System may in liaison with The Company sustain and expand these islands in accordance with the relevant provisions of OC9.5 which shall apply to this OC9.4 as if set out here. In this instance, the arrangements would fall under the provisions of a Local Joint Restoration Plan; and/or

- has activated one or more Distribution Restoration ZonesZone Plans upon instruction from The Company or Relevant Scottish Transmission Licensee, will notify The Company or the Relevant Scottish Transmission Licensee when the Distribution Restoration Zone is operational and supplying local Demand.  The Network Operator in liaison with The Company or the Relevant Scottish Transmission Licensee may sustain and expand these Power Islands in accordance the Distribution Restoration Zone Plan with the relevant provisions of OC9.5 which shall apply to this OC9.4 as if set out here.  In this instance, the arrangements would fall under the provisions of a Distribution Restoration Zone Plan.

In either case, the Network Operator will inform The Company or the Relevant Scottish Transmission Licensee of their actions and will not Re-Synchronise a Power Island formed under a Local Joint Restoration Plan or Distribution Restoration Zone formed under a Distribution Restoration Zone Plan to the National Electricity Transmission System or any User's System which is already Synchronised to the National Electricity Transmission System without The Company's agreement.

OC9.4.7.10	Interconnection of Power Islands

The Company will subsequently interconnect the expanded Power Islands detailed in OC9.4.7.8 and OC9.4.7.9 to form sub-systems which will then be connected to form an integrated system as detailed in OC9.5.  This should eventually achieve the re-establishment of the Total System, or that part of the Total System subject to the Partial Shutdown, as the case may be.  The interconnection of Power Islands and sub-systems will utilise the provisions of all or part of OC9.5 (Re-Synchronisation of De-synchronised Islands) and in such a situation, such provisions will be part of Black Start.  In the case of multiple Distribution Restoration Zones existing in any one Network Operator’s System, The Company may instruct the Network Operator to interconnect them in accordance with OC9.5.6 and OC9.5.7.

Return the Total System Back to Normal Operation

OC9.4.7.11	The Company shall, as soon as reasonably practical, inform Users and the BSCCo when the Total System could return to normal operation.  Any such determination by The Company does not mean that the provisions of Section G paragraph 3 (Black Start) of the BSC shall cease to apply.

In making the determination that the Total System could return to normal operation, The Company, would consider, amongst other things, the following areas:

(a)	the extent to which the National Electricity Transmission System is contiguous and energised;

(b)	the integrity and stability of the National Electricity Transmission System and its ability to operate in accordance with the Licence Standards;

(c)	the impact that returning to normal may have on transmission constraints and the corresponding ability to maximise the Demand connected; and

(d)	the volume of generation, Electricity Storage or Demand not connected to the National Electricity Transmission System; and

(e)	the functionality of normal communication systems (ie electronic data communication facilities, Control Telephony, etc).

In the event that the Balancing Mechanism has been suspended, it will not resume until the start of the Settlement Period determined by the BSC Panel in accordance with paragraph G3.1.2(d)(i) of the BSC.

For the avoidance of doubt, until resumption of the Balancing Mechanism, The Company   is likely to continue to issue Emergency Instructions in accordance with BC2.9.

Users shall use reasonable endeavours to submit Physical notifications ten hours prior to the start of the Settlement Period determined by the BSC Panel in accordance with paragraph G3.1.2(d)(i) of the BSC and as notified by The Company to Users, in preparation for a return to normal operations.

In the event that the Balancing Mechanism has not been suspended and The Company   has determined that the Total System has returned to normal operation, The Company   shall inform Users and the BSCCo as soon as possible of the time and date at which (in The Company’s determination) the Total System returned to normal operation.

Conclusion of Black Start

OC9.4.7.12	The provisions of this OC9 shall cease to apply with effect from either:

(a)   Where the Balancing Mechanism was suspended, the start of the Settlement Period that the Balancing Mechanism resumed normal operation, as determined by the BSC Panel and notified by the BSCCo in accordance with the provisions of the BSC; or

(b)   Where the Balancing Mechanism was not suspended, the end of the Settlement Period determined and notified by the BSCCo (in accordance with the provisions of the BSC) and corresponding to the time and date that The Company determined that the Total System had returned to normal operation.

Externally Interconnected System Operators

OC9.4.7.13		Unless an Interconnector has a Black Start Contract, The Company will, pursuant to the Interconnection Agreement with Externally Interconnected System Operators, agree with Externally Interconnected System Operators when their transmission systems can be Re-Synchronised to the Total System, if they have become separated.

OC9.5	RE-SYNCHRONISATION OF DE-SYNCHRONISED ISLANDS

The provisions in this OC9.5 do not apply to the parts of the Total System that normally operate Out of Synchronism with the rest of the National Electricity Transmission System.

Further requirements, including the provision of information, applying to Re-synchronisation of De-synchronised Islands following any Total Shutdown or Partial Shutdown are detailed in OC9.5.6.

OC9.5.1	(a)	Where parts of the Total System are Out of Synchronism with each other (each such part being termed a "De-Synchronised Island") but where there has been no Total Shutdown or Partial Shutdown, The Company will instruct Users to regulate generation or Demand, as the case may be, to enable the De-Synchronised Islands to be Re-Synchronised and The Company will inform those Users when Re-Synchronisation has taken place.

(b)	As part of that process, there may be a need to deal specifically with Embedded generation or storage in those De-Synchronised Islands.  This OC9.5 provides for how such Embedded generation or storage should be dealt with. In Scotland, this OC9.5 also provides for how Transmission connected generation in De-Synchronised Islands should be dealt with.

(c)	In accordance with the provisions of the BC, The Company may decide that, to enable Re-Synchronisation, it will issue Emergency Instructions in accordance with BC2.9 and it may be necessary to depart from normal Balancing Mechanism operation in accordance with BC2 in issuing Bid-Offer Acceptances.

(d)	The provisions of this OC9.5 shall also apply during a Black Start to the Re-Synchronising of parts of the System following a Total or Partial Shutdown, as indicated in OC9.4.  In such cases, the provisions of OC9.5 shall apply following completion and/or termination of the relevant Local Joint Restoration Plan(s) process as referred to in OC9.4.7.6.1.(f) or relevant Distribution Restoration Zone Plans processes as referred to in OC9.4.7.6.2(e).

OC9.5.2	Island loading and generation data management

Generation in those De-Synchronised Islands may be dealt with in three different ways, more than one of which may be utilised in relation to any particular incident:-

OC9.5.2.1	Indirect Data

- In this section OC9.5.2.1, relevant loading and other operational parameters are exchanged indirectly between Generators and Network Operators via The Company.

(b)	The Company, each Generator with Synchronised (or connected and available to generate although not Synchronised) Gensets in the De-Synchronised Island and the Network Operator whose User System forms all or part of the De-Synchronised Island shall exchange information as set out in this OC9.5.2.1.1 to enable The Company to issue a Bid-Offer Acceptance or an Emergency Instruction to that Generator in relation to its Gensets in the De-Synchronised Island until Re-Synchronisation takes place, on the basis that the Generator will (where practicable) seek to maintain the Target Frequency.

c)	The information to The Company from the Generator will cover its relevant operational parameters as outlined in the BC and from The Company to the Generator will cover data on Demand and changes in Demand in the De-Synchronised Island.

(d)	The information from the Network Operator to The Company will comprise data on Demand in the De-Synchronised Island, including data on any constraints within the De-Synchronised Island.

(e)	The Company will keep the Network Operator informed of the Bid-Offer Acceptances or Emergency Instructions it is issuing to Embedded Gensets within the Network Operator’s User System forming part of the De-Synchronised Island.

OC9.5.2.2	Direct Data

(a)	In this section OC9.5.2.2 relevant loading and other operational parameters are exchanged directly between Generators and Network Operators.

(b)	The Company will issue an Emergency Instruction and/or a Bid-Offer Acceptance, to the Generator to "float" local Demand and maintain Frequency at Target Frequency.  Under this instruction, the Generator will be required to regulate the output of its Genset(s) at the Power Station in question to the Demand prevailing in the De-Synchronised Island in which it is situated, until Re-Synchronisation takes place, on the basis that it will (where practicable) seek to maintain the Target Frequency.

(c)	The Network Operator is required to be in contact with the Generator at the Power Station so that the Network Operator can supply data to the Generator on Demand changes within the De-Synchronised Island.

(d)	If more than one Genset is Synchronised on the De-Synchronised Island, or is connected to the De-Synchronised Island and available to generate although not Synchronised, the Network Operator will need to liaise with The Company to agree which Genset(s) will be utilised to accommodate changes in Demand in the De-Synchronised Island. The Network Operator will then maintain contact with the relevant Generator (or Generators) in relation to that Genset(s).

(e)	The Generator at the Power Station must contact the Network Operator if the level of Demand which it has been asked to meet as a result of the Emergency Instruction and/or Bid-Offer Acceptance to "float" and the detail on Demand passed on by the Network Operator, is likely to cause problems for safety reasons (whether relating to personnel or Plant and/or Apparatus) in the operation of its Genset(s), in order that the Network Operator can alter the level of Demand which that Generator needs to arrange to meet. Any decision to operate outside any relevant parameters is one entirely for the Generator.

OC9.5.2.3	Distribution Restoration Zones

(a)	Where a Distribution Restoration Zone Plan has been activated a Network Operator will issue instructions to the Anchor Plant Owner, and other Restoration Services Providers as required by the Distribution Restoration Zone Plan, to "float" local Demand and maintain Frequency at the Target Frequency.  The relevant Restoration Service Providers shall set the operating points of their Plant and Apparatus to meet the Demand prevailing in the De-Synchronised Island in which it is situated, on the basis that it will (where practicable) seek to maintain the Target Frequency until Re-Synchronisation takes place.

(b)	The Network Operator will request any other relevant operational parameters required from Restoration Service Providers necessary for the operation of the Distribution Restoration Zone.

(c)	The Network Operator will keep The Company informed of the progress of activating the Distribution Restoration Zone Plan and running the Distribution Restoration Zone within the Network Operator’s System.  The Network Operator shall be in contact with the Anchor Plant Owner and other Restoration Service Providers to supply data on Demand changes within the Distribution Restoration Zone.

(d)	Restoration Service Providers must contact the Network Operator if the level of Demand which they have been asked to meet as a result of the instruction to "float", is likely to cause problems for safety reasons (whether relating to personnel or Plant and/or Apparatus) in the operation of its Plant and Apparatus, in order that the Network Operator can alter the level of Demand which the Restoration Service Providers need to meet.  Any decision to operate Restoration Service Providers Plant and Apparatus outside any relevant parameters is one entirely for the relevant Restoration Service Provider.

OC9.5.2.4	Control Features

(a)	A system may be established in relation to a part of the National Electricity Transmission System and a Network Operator’s User System, if agreed between The Company and the Network Operator and any relevant Generators, whereby upon a defined fault(s) occurring, manual or automatic control features will operate to protect the National Electricity Transmission System and relevant Network Operator’s User System and Gensets and simplify the restoration of Demand in the De-Synchronised Island.

(b)	In agreeing the establishment of such a system of control features The Company will need to consider its impact on the operation of the National Electricity Transmission System.

OC9.5.2.5	Absence of Control Features System

If a system of control features under OC9.5.2.4 has not been agreed as part of an OC9 De-Synchronised Island procedure under OC9.5.4 below, The Company may choose to utilise the procedures set out in OC9.5.2.1 or OC9.5.2.2, or may instruct the Gensets (or some of them) in the De-Synchronised Island to De-Synchronise.

OC9.5.3	Choice Of Option

In relation to each of the methods set out in OC9.5.2, where a De-Synchronised Island has come into existence and where an OC9 De-Synchronised Island procedure under OC9.5.4 has been agreed, The Company, the Network Operator and the relevant Generator(s) will operate in accordance with that OC9 De-Synchronised Islands Procedure unless The Company considers that the nature of the De-Synchronised Island situation is such that either:-

(i)	the OC9 De-Synchronised Island Procedure does not cover the situation; or

(ii)	the provisions of the OC9 De-Synchronised Island Procedure are not appropriate,

in which case The Company will instruct the relevant Users and the Users will comply with The Company's instructions (which in the case of Generators will relate to generation and in the case of Network Operators will relate to Demand).

OC9.5.4	Agreeing Procedures

In relation to each relevant part of the Total System, The Company, the Network Operator and the relevant Generator will discuss and may agree a local procedure (an "OC9 De-Synchronised Island Procedure").

Where the need for an OC9 De-Synchronised Island procedure arises for the first time, the following provisions shall apply:

(a)	The Company, the Network Operator(s) and the relevant Generator(s) will discuss the need for, and the detail of, the OC9 De-Synchronised Island Procedure.  As soon as the need for an OC9 De-Synchronised Island procedure is identified by The Company or a User, and the party which identifies such a need will notify all affected Users (and The Company, if that party is a User), and The Company will initiate these discussions.

(b)	Each OC9 De-Synchronised Island Procedure will be in relation to a specific Grid Supply Point, but if there is more than one Grid Supply Point between The Company and the Network Operator then the OC9 De-Synchronised Island Procedure may cover all relevant Grid Supply Points. In Scotland, the OC9 De-Synchronised Island Procedure may also cover parts of the National Electricity Transmission System connected to the User’s System(s) and Power Stations directly connected to the National Electricity Transmission System which are also likely to form part of the Power Island.

(c)	The OC9 De-Synchronised Island Procedure will:

(i)	record which Users and which User Sites are covered by the OC9 De-Synchronised Island Procedure;

(ii)	record which of the three methods set out in OC9.5 (or combination of the three) shall apply, with any conditions as to applicability being set out as well;

(iii)	set out what is required from The Company and each User should a De-Synchronised Island arise;

(iv)	set out what action should be taken if the OC9 De-Synchronised Island Procedure does not cover a particular set of circumstances and will reflect that in the absence of any specified action, the provisions of OC9.5.3 will apply;

(v)	in respect of Scottish Transmission Systems, the OC9 De-Synchronised Island Procedure may be produced with and include obligations on the Relevant Scottish Transmission Licensee(s) ; and

(vi)	in respect of Scottish Transmission Systems, where the OC9 De-Synchronised Island Procedure includes the establishment of a De-synchronised Island, describe the route for establishment of the De-Synchronised Island	.

(d)	Each OC9 De-Synchronised Island procedure shall be prepared by The Company to reflect the above discussions.

(e)	Each page of the OC9 De-Synchronised Island Procedure shall bear a date of issue and the issue number.

(f)	When an OC9 De-Synchronised Island procedure is prepared, it shall be sent by The Company to the Users involved for confirmation of its accuracy.

(g)	The OC9 De-Synchronised Island Procedure shall then be signed on behalf of The Company and on behalf of each relevant User by way of written confirmation of its accuracy.

(h)	Once agreed under this OC9.5.4, the procedure will become an OC9 De-Synchronised Island Procedure under the Grid Code and (subject to any change pursuant to this OC9) will apply between The Company, Relevant Transmission Licensee and the relevant Users as if it were part of the Grid Code.

(i)	Once signed, a copy will be distributed by The Company to each User which is a party accompanied by a note indicating the issue number and the date of implementation.

(j)	The Company and Users must make the OC9 De-Synchronised Island Procedure readily available to the relevant operational staff.

(k)	If a new User connects to the Total System and needs to be included with an existing OC9 De-Synchronised Island procedure, The Company will initiate a discussion with that User and the Users which are parties to the relevant OC9 De-Synchronised Island Procedure.  The principles applying to a new OC9 De-Synchronised Island procedure under this OC9.5.4 shall apply to such discussions and to any consequent changes.

(l)	If The Company, or any User which is a party to an OC9 De-Synchronised Island procedure, becomes aware that a change is needed to that OC9 De-Synchronised Island Procedure, it shall (in the case of The Company) initiate a discussion between The Company and the relevant Users to seek to agree the relevant change.  The principles applying to establishing a new OC9 De-Synchronised Island Procedure under this OC9.5.4 shall apply to such discussions and to any consequent changes.  If a User becomes so aware, it shall contact The Company who will then initiate such discussions.

(m)	If in relation to any discussions, agreement cannot be reached between The Company and the relevant Users, The Company will operate the System on the basis that it will discuss which of the three methods set out in OC9.5.2.1 to OC9.5.2.3 would be most appropriate at the time, if practicable.  The complexities and uncertainties of recovery from a De-Synchronised Island means that The Company will decide, having discussed the situation with the relevant Users and taking into account the fact that the three methods may not cover the situation or be appropriate, the approach which is to be followed.  The Company will instruct the relevant Users and the Users will comply with The Company's instructions as provided in OC9.5.3.

OC9.5.5	Where the National Electricity Transmission System is Out of Synchronism with the Transmission System of an Externally Interconnected System Operator, The Company will, pursuant to the Interconnection Agreement with that Externally Interconnected System Operator, agree with that Externally Interconnected System Operator when its Transmission System can be Re-Synchronised to the National Electricity Transmission System.

OC9.5.6	Further requirements regarding Re-synchronisation of De-synchronised Islands following any Total Shutdown or Partial Shutdown

Following any Total Shutdown or Partial Shutdown, The Company expects that it will be necessary to interconnect Power Islands utilising the provisions of OC9.5.  The complexities and uncertainties of recovery from a Total Shutdown or Partial Shutdown requires the provisions of OC9.5 to be flexible, however, the strategies which The Company will, where practicable, be seeking to follow when Re-synchronising De-synchronised Islands following any Total Shutdown or Partial Shutdown, include the following:

(a)	the provision of supplies to appropriate Power Stations to facilitate their synchronisation as soon as practicable;

(b)	energisation of a skeletal National Electricity Transmission System;

(c)	the strategic restoration of Demand in co-ordination with relevant Network Operators.

(d)	the activation by Network Operators of one or more Distribution Restoration Zones Plans upon instruction from The Company (or Relevant Scottish Transmission Licensee).

As highlighted in OC9.4.3, during a Total Shutdown or Partial Shutdown and during the subsequent recovery, which includes any period during which the procedures in this OC9.5 apply, the Licence Standards may not apply and the Total System may be operated outside normal voltage and Frequency standards.

OC9.5.7	To manage effectively and co-ordinate the restoration strategies of the Total System (any Re-Synchronisation of De-Synchronised Islands) following any Total Shutdown or Partial Shutdown, requires The Company and relevant Users to undertake certain planning activities as set out below:

(a)	The Company and Network Operators shall review on a regular basis the processes by which each Power Island will be interconnected.  This is likely to cover an exchange of information regarding the typical size, location and timing requirements for Demand to be reconnected and also include details (ability to change/disable) of the low frequency trip relay settings of the Demand identified.  There may also be a requirement for specific Protection settings to be used during Black Start.

(b)	Each Generator shall provide to The Company information to assist The Company in the formulation of the restoration strategies of Power Island expansion.  This information shall be provided in accordance with PC.A.5.7.

(c)	Where a Distribution Restoration Zone Plan is to be established, the Distribution Restoration Zone Plan will include the formulation of how the Distribution Restoration Zone will be re-energized from its de-energised state.

OC9.6	JOINT SYSTEM INCIDENT PROCEDURE

OC9.6.1	A "Joint System Incident" is

(a)	an Event, wherever occurring (other than on an Embedded Small Power Station or Embedded Medium Power Station), which, in the opinion of The Company or a User, has or may have a serious and/or widespread effect.

(b)	In the case of an Event on a User(s) System(s) (other than on an Embedded Small Power Station or Embedded Medium Power Station), the effect must be on the National Electricity Transmission System, and in the case of an Event on the National Electricity Transmission System, the effect must be on a User(s) System(s) (other than on an Embedded Small Power Station or Embedded Medium Power Station).

Where an Event on a User(s) System(s) has or may have no effect on the National Electricity Transmission System, then such an Event does not fall within OC9 and accordingly OC9 shall not apply to it.

OC9.6.2	(a)	(i)	Each User (other than Generators which only have Embedded Small Power Stations and/or Embedded Medium Power Stations) will provide in writing to The Company, and

(ii)	The Company will provide in writing to each User (other than Generators which only have Embedded Small Power Stations and/or Embedded Medium Power Stations), a telephone number or numbers at which, or through which, senior management representatives nominated for this purpose and who are fully authorised to make binding decisions on behalf of The Company or the relevant User, as the case may be, can be contacted day or night when there is a Joint System Incident.

(b)	The lists of telephone numbers will be provided in accordance with the timing requirements of the Bilateral Agreement and/or Construction Agreement with that User, prior to the time that a User connects to the National Electricity Transmission System and must be up-dated (in writing) as often as the information contained in them changes.

OC9.6.3	Following notification of an Event under OC7, The Company or a User, as the case may be, will, if it considers necessary, telephone the User or The Company, as the case may be, on the telephone number referred to in OC9.6.2, to obtain such additional information as it requires.

OC9.6.4	Following notification of an Event under OC7, and/or the receipt of any additional information requested pursuant to OC9.6.3, The Company or a User, as the case may be, will determine whether or not the Event is a Joint System Incident, and, if so, The Company and/or the User may set up an Incident Centre in order to avoid overloading the existing The Company or that User's, as the case may be, operational/control arrangements.

OC9.6.5	Where The Company has determined that an Event is a Joint System Incident, The Company shall, as soon as possible, notify all relevant Users that a Joint System Incident has occurred and, if appropriate, that it has established an Incident Centre and the telephone number(s) of its Incident Centre if different from those already supplied pursuant to OC9.6.2.

OC9.6.6	If a User establishes an Incident Centre it shall, as soon as possible, notify The Company that it has been established and the telephone number(s) of the Incident Centre if different from those already supplied pursuant to OC9.6.2.

OC9.6.7	The Company's Incident Centre and/or the User's Incident Centre will not assume any responsibility for the operation of the National Electricity Transmission System or User's System, as the case may be, but will be the focal point in The Company or the User, as the case may be, for:

(a)	the communication and dissemination of information between The Company and the senior management representatives of User(s); or

(b)	between the User and the senior management representatives of The Company, as the case may be,

relating to the Joint System Incident.  The term "Incident Centre" does not imply a specially built centre for dealing with Joint System Incidents, but is a communications focal point.  During a Joint System Incident, the normal communication channels, for operational/control communication between The Company and Users will continue to be used.

OC9.6.8	All communications between the senior management representatives of the relevant parties with regard to The Company's role in the Joint System Incident shall be made via The Company's Incident Centre if it has been established.

OC9.6.9	All communications between the senior management representatives of The Company and a User with regard to that User's role in the Joint System Incident shall be made via that User's Incident Centre if it has been established.

OC9.6.10	The Company will decide when conditions no longer justify the need to use its Incident Centre and will inform all relevant Users of this decision.

OC9.6.11	Each User which has established an Incident Centre will decide when conditions no longer justify the need to use that Incident Centre and will inform The Company of this decision.

< END OF OPERATING CODE NO. 9 >

Extracts from BC2

BC2.5.4	Operation In The Absence Of Instructions From The Company

In the absence of any Bid-Offer Acceptances, Ancillary Service instructions issued pursuant to BC2.8 or Emergency Instructions issued pursuant to BC2.9:

(a)	as provided for in BC3, each Synchronised Genset producing Active Power must operate at all times in Limited Frequency Sensitive Mode (unless instructed in accordance with BC3.5.4 to operate in Frequency Sensitive Mode);

(b)	(i)	in the absence of any MVAr Ancillary Service instructions, the MVAr output of each Synchronised Genset located Onshore should be 0 MVAr upon Synchronisation at the circuit-breaker where the Genset is Synchronised. For the avoidance of doubt, in the case of a Genset located Onshore comprising of Non-Synchronous Generating Units, Power Park Modules, HVDC Systems or DC Converters the steady state tolerance allowed in CC.6.3.2(b) or ECC.6.3.2.4.4 may be applied

(ii)	In the absence of any MVAr Ancillary Service instructions, the MVAr output of each Synchronised Genset comprising Synchronous Generating Units located Offshore (which could be part of a Synchronous Power Generating Module) should be 0MVAr at the Grid Entry Point upon Synchronisation. For the avoidance of doubt, in the case of a Genset located Offshore comprising of Non-Synchronous Generating Units, Power Park Modules, HVDC Systems or DC Converters the steady state tolerance allowed in CC.6.3.2(e) or ECC.6.3.2.5.1 or ECC.6.3.2.6.2 (as applicable) may be applied;

(c)	(i)	subject to the provisions of 2.5.4(c) (ii) and 2.5.4 (c) (iii) below, the excitation system or the voltage control system of a Genset located Offshore which has agreed an alternative Reactive Power capability range under CC.6.3.2 (e) (iii) or  ECC.6.3.2.5.2 or ECC.6.3.2.6.3 (as applicable) or a Genset located Onshore, unless otherwise agreed with The Company, must be operated only in its constant terminal voltage mode of operation with VAR limiters in service, with any constant Reactive Power output control mode or constant Power Factor output control mode always disabled, unless agreed otherwise with The Company. In the event of any change in System voltage, a Generator must not take any action to override automatic MVAr response which is produced as a result of constant terminal voltage mode of operation of the automatic excitation control system unless instructed otherwise by The Company or unless immediate action is necessary to comply with Stability Limits or unless constrained by plant operational limits or safety grounds (relating to personnel or plant);

(ii)	In the case of all Gensets comprising Non-Synchronous Generating Units, DC Converters, HVDC Systems and Power Park Modules that are located Offshore and which have agreed an alternative Reactive Power capability range under CC.6.3.2 (e) (iii), or  ECC.6.3.2.5.2 or ECC.6.3.2.6.3 (as applicable) or that are located Onshore only when operating below 20 % of the Rated MW output, the voltage control system shall maintain the Reactive Power transfer at the Grid Entry Point (or User System Entry Point if Embedded) to 0 MVAr.  For the avoidance of doubt, the relevant steady state tolerance allowed for GB Generators in CC.6.3.2(b) or CC.6.3.2 (e) and for EU Generators in ECC.6.3.2.4.4, ECC.6.3.2.5.1 and ECC.6.3.2.6.2 and ECC.6.3.2.8.2.may be applied.  In the case of any such Gensets owned or operated by GB Code Users comprising current source DC Converter technology or comprising Power Park Modules connected to the Total System by a current source DC Converter when operating at any power output, the voltage control system shall maintain the Reactive Power transfer at the Grid Entry Point (or User System Entry Point if Embedded)  to 0 MVAr.  For the avoidance of doubt the relevant steady state tolerance allowed in CC.6.3.2(b) or CC.6.3.2 (c) (i) may be applied.

(iii)	In the case of all Gensets located Offshore which are not subject to the requirements of BC2.5.4 (c) (i) or BC2.5.4 (c) (ii) the control system shall maintain the Reactive Power transfer at the Offshore Grid Entry Point at 0MVAr.  For the avoidance of doubt the steady state tolerance allowed by CC.6.3.2 (e) or ECC.6.3.2.4.4, ECC.6.3.2.5.1 and ECC.6.3.2.6.2 may be applied.

(d)	In the absence of any MVAr Ancillary Service instructions,

(i)	the MVAr output of each Genset located Onshore should be 0 MVAr immediately prior to De-Synchronisation at the circuit-breaker where the Genset is Synchronised, other than in the case of a rapid unplanned De-Synchronisation or in the case of a Genset comprising of Power Generating Modules and/or Non-Synchronous Generating Units and/or Power Park Modules and/or HVDC Converters or DC Converters which is operating at less than 20% of its Rated MW output where the requirements of BC2.5.4 (c) part (ii) apply, or;

(ii)	the MVAr output of each Genset located Offshore should be 0MVAr immediately prior to De-Synchronisation at the Offshore Grid Entry Point, other than in the case of a rapid unplanned De-Synchronisation or in the case of a Genset comprising of Non-Synchronous Generating Units, Power Park Modules, HVDC Converters or DC Converters which is operating at less than 20% of its Rated MW output and which has agreed an alternative Reactive Power capability range (for GB Code  Users ) under CC.6.3.2 (e) (iii) or ECC.6.3.2.4.4, ECC.6.3.2.5.1 and ECC.6.3.2.6.2 (for EU Code Users ) where the requirements of BC2.5.4 (c) (ii) apply.

(e)	a Generator should at all times operate its CCGT Units in accordance with the applicable CCGT Module Matrix;

(f)	in the case of a Range CCGT Module, a Generator must operate that CCGT Module so that power is provided at the single Grid Entry Point identified in the data given pursuant to PC.A.3.2.1 or at the single Grid Entry Point to which The Company has agreed pursuant to BC1.4.2(f);

(g)	in the event of the System Frequency being above 50.3Hz or below 49.7Hz, BM Participants must not commence any reasonably avoidable action to regulate the input or output of any BM Unit in a manner that could cause the System Frequency to deviate further from 50Hz without first using reasonable endeavours to discuss the proposed actions with The Company.  The Company shall either agree to these changes in input or output or issue a Bid-Offer Acceptance in accordance with BC2.7 to delay the change.

(h)	a Generator should at all times operate its Power Park Units in accordance with the applicable Power Park Module Availability Matrix.

BC2.5.5	Commencement or Termination of Participation in the Balancing Mechanism

BC2.5.5.1	In the event that a BM Participant in respect of a BM Unit with a Demand Capacity with a magnitude of less than 50MW in NGET’s Transmission Area or less than 10MW in SHETL’s Transmission Area or less than 30MW in SPT’s Transmission Area or comprising Generating Units (as defined in the Glossary and Definitions and not limited by BC2.2) and/or Power Generating Modules and/or CCGT Modules and/or Power Park Modules at a Small Power Station notifies The Company at least 30 days in advance that from a specified Operational Day it will:

(a)	no longer submit Bid-Offer Data under BC1.4.2(d), then with effect from that Operational Day that BM Participant no longer has to meet the requirements of BC2.5.1 nor the requirements of CC.6.5.8(b) or ECC.6.5.8(b) (as applicable)  in relation to that BM Unit. Also, with effect from that Operational Day, any defaulted Physical Notification and defaulted Bid-Offer Data in relation to that BM Unit arising from the Data Validation, Consistency and Defaulting Rules will be disregarded and the provisions of BC2.5.2 will not apply;

(b)	submit Bid-Offer Data under BC1.4.2(d), then with effect from that Operational Day that BM Participant will need to meet the requirements of BC2.5.1 and the requirements of CC.6.5.8(b) or ECC.6.5.8(b) (as applicable) in relation to that BM Unit.

BC2.5.5.2	In the event that a BM Participant in respect of a BM Unit with a Demand Capacity with a magnitude of 50MW or more in NGET’s Transmission Area or 10MW or more in SHETL’s Transmission Area or 30MW or more in SPT’s Transmission Area or comprising Generating Units (as defined in the Glossary and Definitions and not limited by BC2.2) and/or Power Generating Modules and/or CCGT Modules and/or Power Park Modules at a Medium Power Station or Large Power Station notifies The Company at least 30 days in advance that from a specified Operational Day it will:

(a)	no longer submit Bid-Offer Data under BC1.4.2(d), then with effect from that Operational Day that BM Participant no longer has to meet the requirements of CC.6.5.8(b) or ECC.6.5.8(b) (as applicable) in relation to that BM Unit; Also, with effect from that Operational Day, any defaulted Bid-Offer Data in relation to that BM Unit arising from the Data Validation, Consistency and Defaulting Rules will be disregarded;

(b)	submit Bid-Offer Data under BC1.4.2(d), then with effect from that Operational Day that BM Participant will need to meet the requirements of CC.6.5.8(b) or ECC.6.5.8(b) (as applicable) in relation to that BM Unit.

BC2.6	COMMUNICATIONS

Electronic communications are always conducted in GMT. However, the input of data and display of information to Users and The Company and all other communications are conducted in London time.

BC2.6.1	Normal Communication With Control Points

(a)	With the exception of BC2.6.1(c) below, Bid-Offer Acceptances and, unless otherwise agreed with The Company, Ancillary Service instructions shall be given by automatic logging device and will be given to the Control Point for the BM Unit.  For all Planned Maintenance Outages the provisions of BC2.6.5 will apply.  For Generating Units (including DC Connected Power Park Modules (if relevant)) communications under BC2 shall be by telephone unless otherwise agreed by The Company and the User.

(b)	Bid-Offer Acceptances and Ancillary Service instructions must be formally acknowledged immediately by the BM Participant (or the relevant person on its behalf) via the Control Point for the BM Unit or Generating Unit in respect of that BM Unit or that Generating Unit. The acknowledgement and subsequent confirmation or rejection, within two minutes of receipt, is normally given electronically by automatic logging device. If no confirmation or rejection is received by The Company within two minutes of the issue of the Bid-Offer Acceptance, then The Company will contact the Control Point for the BM Unit by telephone to determine the reason for the lack of confirmation or rejection. Any rejection must be given in accordance with BC2.7.3 or BC2.8.3.

(c)	In the event of a failure of the logging device or an outage of The Company’s computer system, Bid-Offer Acceptances and instructions will be given, acknowledged, and confirmed or rejected by telephone. The provisions of BC2.9.7 are also applicable.

(d)	In the event that in carrying out the Bid-Offer Acceptances or providing the Ancillary Services, or when operating at the level of the Final Physical Notification Data as provided in BC2.5.1, an unforeseen problem arises, caused on safety grounds (relating to personnel or plant), The Company must be notified without delay by telephone.

(e)	The provisions of BC2.5.3 are also relevant.

(f)	Submissions of revised MVAr capability may be made by facsimile transmission, using the format given in Appendix 3 to BC2.

(g)	Communication will normally be by telephone for any purpose other than Bid-Offer Acceptances, in relation to Ancillary Services or for revisions of MVAr Data.

(h)	Submissions of revised availability of Frequency Sensitive Mode may be made by facsimile transmission, using the format given in Appendix 4 to BC2. This process should only be used for technical restrictions to the availability of Frequency Sensitive Mode.

BC2.6.2	Communication With Control Points In Emergency Circumstances

The Company will issue Emergency Instructions direct to the Control Point for each BM Unit [or Generating Unit] in Great Britain. Emergency Instructions to a Control Point will normally be given by telephone (and will include an exchange of operator names).

BC2.6.3	Communication With Network Operators In Emergency Circumstances

The Company will issue Emergency Instructions direct to the Network Operator at each Control Centre in relation to actions including special actions as set out in BC1.7, actions in the categories set out under BC2.9.3.3, and Demand Control actions.  Emergency Instructions to a Network Operator will normally be given by telephone (and will include an exchange of operator names). OC6 contains further provisions relating to Demand Control instructions.

BC2.6.4	Communication With Externally Interconnected System Operators In Emergency Circumstances

The Company will issue Emergency Instructions directly to the Externally Interconnected System Operator at each Control Centre.  Emergency Instructions to an Externally Interconnected System Operator will normally be given by telephone (and will include an exchange of operator names).

BC2.6.5	Communications During Planned Outages Of Electronic Data Communication Facilities

Planned Maintenance Outages will normally be arranged to take place during periods of low data transfer activity. Upon any such Planned Maintenance Outage in relation to a post Gate Closure period:-

(a)	BM Participants should operate in relation to any period of time in accordance with the Physical Notification prevailing at Gate Closure current at the time of the start of the Planned Maintenance Outage in relation to each such period of time.  Such operation shall be subject to the provisions of BC2.5.1, which will apply as if set out in this BC2.6.5.  No further submissions of BM Unit Data (other than data specified in BC1.4.2(c) and BC1.4.2(e)) should be attempted or Generating Unit Data. Plant failure or similar problems causing significant deviation from Physical Notification should be notified to The Company by the submission of a revision to Export and Import Limits in relation to the BM Unit or Generating Unit so affected;

(b)	during the outage, revisions to the data specified in BC1.4.2(c) and BC1.4.2(e) may be submitted.  Communication between Users Control Points and The Company during the outage will be conducted by telephone;

(c)	The Company will issue Bid-Offer Acceptances by telephone; and

(d)	no data will be transferred from The Company to the BMRA until the communication facilities are re-established.

(e)	The provisions of BC2.9.7 may also be relevant.

BC2.7	BID-OFFER ACCEPTANCES

BC2.7.1	Acceptance of Bids and Offers by The Company

Bid-Offer Acceptances may be issued to the Control Point at any time following Gate Closure.  Any Bid-Offer Acceptance will be consistent with the Dynamic Parameters and Export and Import Limits of the BM Unit in so far as the Balancing Mechanism timescales will allow (see BC2.7.2).

(a)	The Company is entitled to assume that each BM Unit is available in accordance with the BM Unit Data submitted unless and until it is informed of any changes.

(b)	Bid-Offer Acceptances sent to the Control Point will specify the data necessary to define a MW profile to be provided (ramp rate break-points are not normally explicitly sent to the Control Point) and to be achieved consistent with the respective BM Unit's Export and Import Limits provided or modified under BC1 or BC2, and Dynamic Parameters given under BC2.5.3 or, if agreed with the relevant User, such rate within those Dynamic Parameters as is specified by The Company in the Bid-Offer Acceptances.

(c)	All Bid-Offer Acceptances will be deemed to be at the current "Target Frequency", namely where a Genset is in Frequency Sensitive Mode they refer to target output at Target Frequency.

(d)	The form of and terms to be used by The Company in issuing Bid-Offer Acceptances together with their meanings are set out in Appendix 1 in the form of a non-exhaustive list of examples.

BC2.7.2	Consistency With Export And Import Limits And Dynamic Parameters

(a)	Bid-Offer Acceptances will be consistent with the Export and Import Limits provided or modified under BC1 or BC2 and the Dynamic Parameters provided or modified under BC2.  Bid-Offer Acceptances may also recognise Other Relevant Data provided or modified under BC1 or BC2

(b)	In the case of consistency with Dynamic Parameters this will be limited to the time until the end of the Settlement Period for which Gate Closure has most recently occurred.  If  The Company intends to issue a Bid-Offer Acceptance covering a period after the end of the Settlement Period for which Gate Closure has most recently occurred, based upon the then submitted Dynamic Parameters, Export and Import Limits, and Bid-Offer Data applicable to that period,  The Company will indicate this to the BM Participant at the Control Point for the BM Unit.  The intention will then be reflected in the issue of a Bid-Offer Acceptance to return the BM Unit to its previously notified Physical Notification after the relevant Gate Closure provided the submitted data used to formulate this intention has not changed and subject to System conditions which may affect that intention.  Subject to that, assumptions regarding Bid-Offer Acceptances may be made by BM Participants for Settlement Periods for which Gate Closure has not yet occurred when assessing consistency with Dynamic Parameters in Settlement Periods for which Gate Closure has occurred.  If no such subsequent Bid–Offer Acceptance is issued, the original Bid-Offer Acceptance will include an instantaneous return to Physical Notification at the end of the Balancing Mechanism period.

BC2.7.3	Confirmation And Rejection Of Acceptances

Bid-Offer Acceptances may only be rejected by a BM Participant :

(a)	on safety grounds (relating to personnel or plant) as soon as reasonably possible and in any event within five minutes; or

(b)	because they are not consistent with the Export and Import Limits or Dynamic Parameters applicable at the time of issue of the Bid-Offer Acceptance.

A reason must always be given for rejection by telephone.

Where a Bid-Offer Acceptance is not confirmed within two minutes or is rejected,  The Company will seek to contact the Control Point for the BM Unit.  The Company must then, within 15 minutes of issuing the Bid-Offer Acceptance, withdraw the Bid-Offer Acceptance or log the Bid-Offer Acceptance as confirmed. The Company will only log a rejected Bid-Offer Acceptance as confirmed following discussion and if the reason given is, in The Company’s reasonable opinion, not acceptable and The Company will inform the BM Participant accordingly.

BC2.7.4	Action Required From BM Participants

(a)	Each BM Participant in respect of its BM Units will comply in accordance with BC2.7.1 with all Bid-Offer Acceptances given by The Company with no more than the delay allowed for by the Dynamic Parameters unless the BM Unit has given notice to The Company under the provisions of BC2.7.3 regarding non-acceptance of a Bid-Offer Acceptance.

(b)	Where a BM Unit’s input or output changes in accordance with a Bid-Offer Acceptance issued under BC2.7.1, such variation does not need to be notified to The Company in accordance with BC2.5.1.

(c)	In the event that while carrying out the Bid-Offer Acceptance an unforeseen problem arises caused by safety reasons (relating to personnel or plant), The Company must be notified immediately by telephone and this may lead to revision of BM Unit Data in accordance with BC2.5.3

BC2.7.5	Additional Action Required when responding to Bid-Offer Acceptances

(a)	When complying with Bid-Offer Acceptances for a CCGT Module a Generator will operate its CCGT Units in accordance with the applicable CCGT Module Matrix.

(b)	When complying with Bid-Offer Acceptances for a CCGT Module which is a Range CCGT Module, a Generator must operate that CCGT Module so that power is provided at the single Grid Entry Point identified in the data given pursuant to PC.A.3.2.1 or at the single Grid Entry Point to which The Company has agreed pursuant to BC1.4.2 (f).

(c)	On receiving a new MW Bid-Offer Acceptance, no tap changing shall be carried out to change the MVAr output unless there is a new MVAr Ancillary Service instruction issued pursuant to BC2.8.

(d)	When complying with Bid-Offer Acceptances for a Power Park Module a Generator will operate its Power Park Units in accordance with the applicable Power Park Module Availability Matrix.

(e)	When complying with Bid-Offer Acceptances for a Synchronous Power Generating Module a Generator will operate its Generating Units in accordance with the applicable Synchronous Power Generating Module Availability Matrix.

(f)    When complying with Bid-Offer Acceptances for an Additional BM unit or Secondary BM Unit they will operate in accordance with the applicable Aggregator Impact Matrix.

BC2.8	ANCILLARY SERVICES

This section primarily covers the call-off of System Ancillary Services. The provisions relating to Commercial Ancillary Services will normally be covered in the relevant Ancillary Services Agreement.

BC2.8.1	Call-Off Of Ancillary Services By The Company

(a)	Ancillary Service instructions may be issued at any time.

(b)	The Company is entitled to assume that each BM Unit (or Generating Unit) is available in accordance with the BM Unit Data (or the Generating Unit Data) and data contained in the Ancillary Services Agreement unless and until it is informed of any changes.

(c)	Frequency control instructions may be issued in conjunction with, or separate from, a Bid-Offer Acceptance.

(d)	The form of and terms to be used by The Company in issuing Ancillary Service instructions together with their meanings are set out in Appendix 2 in the form of a non-exhaustive list of examples including Reactive Power and associated instructions.

(e)	In the case of Generating Units that do not form part of a BM Unit any change in Active Power as a result of, or required to enable, the provision of an Ancillary Service will be dealt with as part of that Ancillary Service Agreement and/or provisions under the CUSC.

(f)	A System to Generator Operational Intertripping Scheme will be armed in accordance with BC2.10.2(a).

BC2.8.2	Consistency With Export And Import Limits And Dynamic Parameters

Ancillary Service instructions will be consistent with the Export and Import Limits provided or modified under BC1 or BC2 and the Dynamic Parameters provided or modified under BC2.  Ancillary Service instructions may also recognise Other Relevant Data provided or modified under BC1 or BC2.

BC2.8.3	Rejection Of Ancillary Service Instructions

(a)	Ancillary Service instructions may only be rejected, by automatic logging device or by telephone, on safety grounds (relating to personnel or plant) or because they are not consistent with the applicable Export and Import Limits, Dynamic Parameters, Other Relevant Data or data contained in the Ancillary Services Agreement and a reason must be given immediately for non-acceptance.

(b)	The issue of Ancillary Service instructions for Reactive Power will be made with due regard to any resulting change in Active Power output. The instruction may be rejected if it conflicts with any Bid-Offer Acceptance issued in accordance with BC2.7 or with the Physical Notification.

(c)	Where Ancillary Service instructions relating to Active Power and Reactive Power are given together, and to achieve the Reactive Power output would cause the BM Unit to operate outside Dynamic Parameters as a result of the Active Power instruction being met at the same time, then the timescale of implementation of the Reactive Power instruction may be extended to be no longer than the timescale for implementing the Active Power instruction but in any case to achieve the MVAr Ancillary Service instruction as soon as possible.

BC2.8.4	Action Required From BM Units

(a)	Each BM Unit (or Generating Unit) will comply in accordance with BC2.8.1 with all Ancillary Service instructions relating to Reactive Power properly given by The Company within 2 minutes or such longer period as The Company may instruct, and all other Ancillary Service instructions without delay, unless the BM Unit or Generating Unit has given notice to The Company under the provisions of BC2.8.3 regarding non-acceptance of Ancillary Service instructions.

(b)	Each BM Unit may deviate from the profile of its Final Physical Notification Data, as modified by any Bid-Offer Acceptances issued in accordance with BC2.7.1, only as a result of responding to Frequency deviations when operating in Frequency Sensitive Mode in accordance with the Ancillary Services Agreement.

(c)	Each Generating Unit that does not form part of a BM Unit may deviate from the profile of its Final Physical Notification Data where agreed by The Company and the User, including but not limited to, as a result of providing an Ancillary Service in accordance with the Ancillary Service Agreement.

(d)	In the event that while carrying out the Ancillary Service instructions an unforeseen problem arises caused by safety reasons (relating to personnel or plant), The Company must be notified immediately by telephone and this may lead to revision of BM Unit Data or Generating Unit Data in accordance with BC2.5.3.

BC2.8.5 	Reactive Despatch Network Restrictions

Where The Company has received notification pursuant to the Grid Code that a Reactive Despatch to Zero MVAr Network Restriction is in place with respect to any Embedded Power Generating Module and/or  Embedded Generating Unit and/or Embedded Power Park Module or HVDC Converter at an Embedded HVDC Converter Station or DC Converter at an Embedded DC Converter Station, then The Company will not issue any Reactive Despatch Instruction with respect to that Power Generating Module and/or Generating Unit and/or Power Park Module or DC Converter or HVDC Converter until such time as notification is given to The Company pursuant to the Grid Code that such Reactive Despatch to Zero MVAr Network Restriction is no longer affecting that Power Generating Module and/or Generating Unit and/or Power Park Module or DC Converter or HVDC Converter.

BC2.9	EMERGENCY CIRCUMSTANCES

BC2.9.1	Emergency Actions

BC2.9.1.1	In certain circumstances (as determined by The Company in its reasonable opinion) it will be necessary, in order to preserve the integrity of the  National Electricity Transmission System and any synchronously connected External System, for The Company to issue Emergency Instructions. In such circumstances, it may be necessary to depart from normal Balancing Mechanism operation in accordance with BC2.7 in issuing Bid-Offer Acceptances. BM Participants must also comply with the requirements of BC3.

BC2.9.1.2	Examples of circumstances that may require the issue of Emergency Instructions include:-

(a)	Events on the National Electricity Transmission System or the System of another User; or

(b)	the need to maintain adequate System and Localised NRAPM in accordance with BC2.9.4 below; or

(c)	the need to maintain adequate frequency sensitive Gensets in accordance with BC2.9.5 below; or

(d)	the need to implement Demand Control in accordance with OC6; or

(e)	(i)	the need to invoke the Black Start process or the Re-Synchronisation of De-Synchronised Island process or Distribution Restoration Zone Plans in accordance with OC9; or

(ii)	the need to request provision of a Maximum Generation Service; or

(iii)	the need to issue an Emergency Deenergisation Instruction in circumstances where the condition or manner of operation of any Transmission Plant and/or Apparatus is such that it may cause damage or injury to any person or to the National Electricity Transmission System.

BC2.9.1.3	In the case of BM Units and Generating Units in Great Britain, Emergency Instructions will be issued by The Company direct to the User at the Control Point for the BM Unit or Generating Unit and may require an action or response which is outside its Other Relevant Data or Export and Import Limits submitted under BC1, or revised under BC1 or BC2, or Dynamic Parameters submitted or revised under BC2.

BC2.9.1.4	In the case of a Network Operator or an Externally Interconnected System Operator, Emergency Instructions will be issued to its Control Centre.

BC2.9.2	Implementation of Emergency Instructions

BC2.9.2.1	Users will respond to Emergency Instructions issued by The Company without delay and using all reasonable endeavours to so respond. Emergency Instructions may only be rejected by an User on safety grounds (relating to personnel or plant) and this must be notified to The Company immediately by telephone.

BC2.9.2.2	Emergency Instructions will always be prefixed with the words “This is an Emergency Instruction” except in the case of:

(i)	Maximum Generation Service instructed by electronic data communication facilities where the instruction will be issued in accordance with the provisions of the Maximum Generation Service Agreement; and

(ii)	an Emergency Deenergisation Instruction, where the Emergency Deenergisation Instruction will be pre-fixed with the words ‘This is an Emergency Deenergisation Instruction’; and

- during a Black Start situation where the Balancing Mechanism has been suspended, any instruction given by The Company will (unless The Company specifies otherwise) be deemed to be an Emergency Instruction and need not be pre-fixed with the words ‘This is an Emergency Instruction’; and

- during a Black Start where the Balancing Mechanism has not been suspended, any instruction in relation to Black Start Stations, Black Start HVDC Systems and to Network Operators which are part of an invoked Local Joint Restoration Plan will (unless The Company specifies otherwise) be deemed to be an Emergency Instruction and need not be prefixed with the words ‘This is an Emergency Instruction’.  Equally during a Black Start where the Balancing Mechanism has not been suspended, any instruction to Network Operators which are part of an activated Distribution Restoration Zone Plan will (unless The Company specifies otherwise) be deemed to be an Emergency Instruction and need not be prefixed with the words ‘This is an Emergency Instruction’.

In Scotland, any instruction from the Relevant Transmission Licensee in relation to Gensets that are not at Black Start Stations or to HVDC Systems or DC Converter Stations that are not part of Black Start HVDC Systems, but which are part of an invoked Local Joint Restoration Plan and are instructed in accordance with the provisions of that Local Joint Restoration Plan, will be deemed to be an Emergency Instruction and need not be prefixed with the words ‘This is an Emergency Instruction’.  Equally any instruction from the Relevant Transmission Licensee to Network Operators who are part of an activated Distribution Restoration Zone Plan and are instructed in accordance with the provisions of that Distribution Restoration Zone Plan, will be deemed to be an Emergency Instruction and need not be prefixed with the words ‘This is an Emergency Instruction’.

BC2.9.2.3	In all cases under this BC2.9 except BC2.9.1.2 (e) where The Company issues an Emergency Instruction to a BM Participant which is not rejected under BC2.9.2.1, the Emergency Instruction shall be treated as a Bid-Offer Acceptance.  For the avoidance of doubt, any Emergency Instruction issued to a Network Operator or to an Externally Interconnected System Operator or in respect of a Generating Unit that does not form part of a BM Unit, will not be treated as a Bid-Offer Acceptance.

BC2.9.2.4	In the case of BC2.9.1.2 (e) (ii) where The Company issues an Emergency Instruction pursuant to a Maximum Generation Service Agreement payment will be dealt with in accordance with the CUSC and the Maximum Generation Service Agreement.

BC2.9.2.5	In the case of BC2.9.1.2 (e) (iii) where The Company issues an Emergency Deenergisation Instruction payment will be dealt with in accordance with the CUSC, Section 5.

BC2.9.2.6	In the of BC2.9.1.2 (e) (i) upon receipt of an Emergency Instruction by a Generator during a Black Start the provisions of Section G of the BSC relating to compensation shall apply.

BC2.9.3	Examples of Emergency Instructions

BC2.9.3.1	In the case of a BM Unit or a Generating Unit, Emergency Instructions may include an instruction for the BM Unit or the Generating Unit to operate in a way that is not consistent with the Dynamic Parameters and/or Export and Import Limits.

BC2.9.3.2	In the case of a Generator, Emergency Instructions may include:

(a)	an instruction to trip one or more Gensets (excluding Operational Intertripping); or

(b)	an instruction to trip Mills or to Part Load a Generating Unit (as defined in the Glossary and Definitions and not limited by BC2.2); or

(c)	an instruction to Part Load a Power Generating Module and/or CCGT Module or Power Park Module; or

(d)	an instruction for the operation of CCGT Units within a CCGT Module (on the basis of the information contained within the CCGT Module Matrix) when emergency circumstances prevail (as determined by The Company in The Company's reasonable opinion); or

(e)	an instruction to generate outside normal parameters, as allowed for in 4.2 of the CUSC; or

(f)	an instruction for the operation of Generating Units within a Cascade Hydro Scheme (on the basis of the additional information supplied in relation to individual Generating Units) when emergency circumstances prevail (as determined by The Company in The Company’s reasonable opinion); or

(g)	an instruction for the operation of a Power Park Module (on the basis of the information contained within the Power Park Module Availability Matrix) when emergency circumstances prevail (as determined by The Company in The Company's reasonable opinion).

BC2.9.3.3	Instructions to Network Operators relating to the Operational Day may include:

(a) 	a requirement for Demand reduction and disconnection or restoration pursuant to OC6;

(b)	an instruction to effect a load transfer between Grid Supply Points;

(c)	an instruction to switch in a System to Demand Intertrip Scheme;

(d)	an instruction to split a network;

(e)	an instruction to disconnect an item of Plant or Apparatus from the System.

(f)	until October 25 2020, an instruction requiring a Network Operator to disconnect Embedded Power Stations from their System.  For the avoidance of doubt, this includes the disconnection of Embedded Power Stations connected to the Network Operator’s System which are owned or operated by generators that are not BM Participants. Such an instruction may:

i)	be specific and require the Network Operator to disconnect specified Embedded Power Stations;

ii)	be for the Network Operator to disconnect Embedded Power Stations supplied via one or more specified Grid Supply Points with an aggregate Registered Capacity of a specified value; or

iii)	be for the Network Operator to disconnect Embedded Power Stations supplied via 	one or more specified Grid Supply Points such that a specified proportion of the aggregate Registered Capacity is disconnected.

(g)	an instruction to activate a Distribution Restoration Zone Plan as provided for in OC9.4.7.6.2.

In the case of BC2.9.3.3(f), the Network Operator will not be required to disconnect Embedded Power Stations with an aggregated Registered Capacity greater than that of the Embedded Power Stations supplied via the specified Grid Supply Point(s). An instruction from The Company to the Network Operator will be given to commence reconnection. Reconnection shall not take place until such an instruction has been received and be carried out in accordance with the instruction.

BC2.9.4	Maintaining adequate System and Localised NRAPM (Negative Reserve Active Power Margin)

BC2.9.4.1	Where The Company is unable to satisfy the required System NRAPM or Localised NRAPM by following the process described in BC1.5.5, The Company will issue an Emergency Instruction to exporting BM Units for De-Synchronising on the basis of Bid-Offer Data submitted to The Company in accordance with BC1.4.2(d). If The Company is still unable to satisfy the required System NRAPM or Localised NRAPM then The Company may issue Emergency Instructions to Network Operators as set out under BC2.9.3.3(f) to disconnect Embedded Power Stations from their System.

BC2.9.4.2	In the event that The Company is unable to differentiate between exporting BM Units according to Bid-Offer Data, The Company will instruct a BM Participant to Shutdown a specified exporting BM Unit for such period based upon the following factors:

(a)	effect on power flows (resulting in the minimisation of transmission losses);

(b)	reserve capability;

(c)	Reactive Power worth;

(d)	Dynamic Parameters;

(e)	in the case of Localised NRAPM, effectiveness of output reduction in the management of the System Constraint.

BC2.9.4.3	Where The Company is still unable to differentiate between exporting BM Units, having considered all the foregoing, The Company will decide which exporting BM Unit to Shutdown by the application of a quota for each BM Participant in the ratio of each BM Participant’s Physical Notifications.

BC2.9.4.4	Other than as provided in BC2.9.4.5 and BC2.9.4.6 below, in determining which exporting BM Units to De-Synchronise under this BC2.9.4, The Company shall not consider in such determination (and accordingly shall not instruct to De-Synchronise) any Generating Unit (as defined in the Glossary and Definitions and not limited by BC2.2) within an Existing Gas Cooled Reactor Plant.

BC2.9.4.5	The Company shall be permitted to instruct a Generating Unit (as defined in the Glossary and Definitions and not limited by BC2.2) within an Existing AGR Plant to De-Synchronise if the relevant Generating Unit within the Existing AGR Plant has failed to offer to be flexible for the relevant instance at the request of The Company within the Existing AGR Plant Flexibility Limit.

BC2.9.4.6	Notwithstanding the provisions of BC2.9.4.5 above, if the level of System NRAPM (taken together with System constraints) or Localised NRAPM is such that it is not possible to avoid instructing a Generating Unit (as defined in the Glossary and Definitions and not limited by BC2.2) within an Existing Magnox Reactor Plant and/or an Existing AGR Plant whether or not it has met requests within the Existing AGR Flexibility Limit to De-Synchronise The Company may, provided the power flow across each External Interconnection is either at zero or results in an export of power from the Total System, so instruct a Generating Unit (as defined in the Glossary and Definitions and not limited by BC2.2) within an Existing Magnox Reactor Plant and/or an Existing AGR Plant to De-Synchronise in the case of System NRAPM, in all cases and in the case of Localised NRAPM, when the power flow would have a relevant effect.

BC2.9.4.7	When instructing exporting BM Units which form part of an On-Site Generator Site to reduce generation or export under this BC2.9.4, The Company will not issue an instruction which would reduce generation or export below the reasonably anticipated Demand of the On-Site Generator Site. For the avoidance of doubt, it should be noted that the term “On-Site Generator Site” only relates to Trading Units which have fulfilled the Class 1 or Class 2 requirements.

BC2.9.5	Maintaining Adequate Frequency Sensitive Generation

BC2.9.5.1	If, post Gate Closure, The Company determines, in its reasonable opinion, from the information then available to it (including information relating to a Generating Unit (as defined in the Glossary and Definitions and not limited by BC2.2) breakdown) that the number of and level of Primary, Secondary and High Frequency Response available from Gensets (other than those units within Existing Gas Cooled Reactor Plant, which are permitted to operate in Limited Frequency Sensitive Mode at all times under BC3.5.3) available to operate in Frequency Sensitive Mode is such that it is not possible to avoid De-Synchronising Existing Gas Cooled Reactor Plant then provided that:

(a)	there are (or, as the case may be, that The Company anticipates, in its reasonable opinion, that at the time that the instruction is to take effect there will be) no other Gensets generating and exporting on to the Total System which are not operating in Frequency Sensitive Mode (or which are operating with only a nominal amount in terms of level and duration) (unless, in The Company's reasonable opinion, necessary to assist the relief of System constraints or necessary as a result of other System conditions); and

(b)	the power flow across each External Interconnection is (or, as the case may be, is anticipated to be at the time that the instruction is to take effect) either at zero or results in an export of power from the Total System,

then The Company may instruct such of the Existing Gas Cooled Reactor Plant to De-Synchronise as it is, in The Company's reasonable opinion, necessary to De-Synchronise and for the period for which the De-Synchronising is, in The Company's reasonable opinion, necessary.

BC2.9.5.2	If in The Company's reasonable opinion it is necessary for both the procedure in BC2.9.4 and that set out in BC2.9.5.1 to be followed in any given situation, the procedure in BC2.9.4 will be followed first, and then the procedure set out in BC2.9.5.1. For the avoidance of doubt, nothing in this sub-paragraph shall prevent either procedure from being followed separately and independently of the other.

BC2.9.6	Emergency Assistance To And From External Systems

(a)	An Externally Interconnected System Operator (in its role as operator of the External System) may request that The Company takes any available action to increase the Active Energy transferred into its External System, or reduce the Active Energy transferred into the National Electricity Transmission System by way of emergency assistance if the alternative is to instruct a demand reduction on all or part of its External System (or on the system of an Interconnector User using its External System). Such request must be met by The Company providing this does not require a reduction of Demand on the National Electricity Transmission System, or lead to a reduction in security on the National Electricity Transmission System.

(b)	The Company may request that an Externally Interconnected System Operator takes any available action to increase the Active Energy transferred into the National Electricity Transmission System, or reduce the Active Energy transferred into its External System by way of emergency assistance if the alternative is to instruct a Demand reduction on all or part of the National Electricity Transmission System. Such request must be met by the Externally Interconnected System Operator providing this does not require a reduction of Demand on its External System (or on the system of Interconnector Users using its External System), or lead to a reduction in security on such External System or system.

BC2.9.7	Unplanned Outages Of Electronic Communication And Computing Facilities

BC2.9.7.1	In the event of an unplanned outage of the electronic data communication facilities or of The Company’s associated computing facilities or in the event of a Planned Maintenance Outage lasting longer than the planned duration, in relation to a post-Gate Closure period The Company will, as soon as it is reasonably able to do so, issue a The Company Computing System Failure notification by telephone or such other means agreed between Users and The Company indicating the likely duration of the outage.

BC2.9.7.2	During the period of any such outage, the following provisions will apply:

(a)	The Company will issue further The Company Computing System Failure notifications by telephone or such other means agreed between Users and The Company to all BM Participants to provide updates on the likely duration of the outage;

(b)	BM Participants should operate in relation to any period of time in accordance with the Physical Notification prevailing at Gate Closure current at the time of the computer system failure in relation to each such period of time. Such operation shall be subject to the provisions of BC2.5.1, which will apply as if set out in this BC2.9.7.2. No further submissions of BM Unit Data or Generating Unit Data (other than data specified in BC1.4.2(c) (Export and Import Limits) and BC1.4.2(e) (Dynamic Parameters) should be attempted. Plant failure or similar problems causing significant deviation from Physical Notification should be notified to The Company by telephone by the submission of a revision to Export and Import Limits in relation to the BM Unit or Generating Unit Data so affected;

(c)	Revisions to Export and Import Limits and to Dynamic Parameters should be notified to The Company by telephone and will be recorded for subsequent use;

(d)	The Company will issue Bid-Offer Acceptances by telephone which will be recorded for subsequent use;

(e)	No data will be transferred from The Company to the BMRA until the communication facilities are re-established.

BC2.9.7.3	The Company will advise BM Participants of the withdrawal of The Company Computing System Failure notification following the re-establishment of the communication facilities.

BC2.10	OTHER OPERATIONAL INSTRUCTIONS AND NOTIFICATIONS

BC2.10.1	The Company may, from time to time, need to issue other instructions or notifications associated with the operation of the National Electricity Transmission System.

BC2.10.2	Such instructions or notifications may include:

Intertrips

(a)	an instruction to arm or disarm an Operational Intertripping scheme;

Tap Positions

(b)	a request for a Genset step-up transformer tap position (for security assessment);

Tests

(c)	an instruction to carry out tests as required under OC5, which may include the issue of an instruction regarding the operation of CCGT Units within a CCGT Module at a Large Power Station;

Future BM Unit Requirements

(d)	a reference to any implications for future BM Unit requirements and the security of the National Electricity Transmission System, including arrangements for change in output to meet post fault security requirements;

Changes to Target Frequency

(e)	a notification of a change in Target Frequency, which will normally only be 49.95, 50.00, or 50.05Hz but in exceptional circumstances as determined by The Company in its reasonable opinion, may be 49.90 or 50.10Hz.

BC2.10.3	Where an instruction or notification under BC2.10.2 (c) or (d) results in a change to the input or output level of the BM Unit then The Company shall issue a Bid-Offer Acceptance or Emergency Instruction as appropriate.

BC2.11	LIAISON WITH GENERATORS FOR RISK OF TRIP AND AVR TESTING

BC2.11.1	A Generator at the Control Point for any of its Large Power Stations may request The Company's agreement for one of the Gensets at that Power Station to be operated under a risk of trip. The Company's agreement will be dependent on the risk to the National Electricity Transmission System that a trip of the Genset would constitute.

BC2.11.2	(a)	Each Generator at the Control Point for any of its Large Power Stations will operate its Synchronised Gensets (excluding Power Park Modules) with:

(i)	AVRs in constant terminal voltage mode with VAR limiters in service at all times. AVR constant Reactive Power or Power Factor mode should, if installed, be disabled; and

(ii)	its generator step-up transformer tap changer selected to manual mode,

unless released from this obligation in respect of a particular Genset by The Company.

(b)	Each Generator at the Control Point for any of its Large Power Stations will operate its Power Park Modules with a Completion Date before 1st January 2006 at unity power factor at the Grid Entry Point (or User System Entry Point if Embedded).

(c)	Each Generator at the Control Point for any of its Large Power Stations will operate its Power Park Modules with a Completion Date on or after 1st January 2006 in voltage control mode at the Grid Entry Point (or User System Entry Point if Embedded). Constant Reactive Power or Power Factor mode should, if installed, be disabled.

(d)	Where a Power System Stabiliser is fitted as part of the excitation system or voltage control system of a Genset, it requires on-load commissioning which must be witnessed by The Company. Only when the performance of the Power System Stabiliser has been approved by The Company shall it be switched into service by a Generator and then it will be kept in service at all times unless otherwise agreed with The Company. Further reference is made to this in CC.6.3.8 and ECC.6.3.8.

BC2.11.3	A Generator at the Control Point for any of its Power Stations may request The Company's agreement for one of its Gensets at that Power Station to be operated with the AVR in manual mode, or Power System Stabiliser switched out, or VAR limiter switched out. The Company's agreement will be dependent on the risk that would be imposed on the National Electricity Transmission System and any User System. Provided that in any event a Generator may take such action as is reasonably necessary on safety grounds (relating to personnel or plant) .

BC2.11.4 	Each Generator shall operate its dynamically controlled OTSDUW Plant and Apparatus to ensure that the reactive capability and voltage control performance requirements as specified in CC.6.3.2, CC.6.3.8, CC.A.7 or ECC.6.3.2, ECC.6.3.8, ECC.A.7, ECC.A.8 and the Bilateral Agreement can be satisfied in response to the Setpoint Voltage and Slope as instructed by The Company at the Transmission Interface Point.

BC2.12	LIAISON WITH EXTERNALLY INTERCONNECTED SYSTEM OPERATORS

BC2.12.1	Co-Ordination Role Of Externally Interconnected System Operators

(a)	The Externally Interconnected System Operator will act as the Control Point for Bid-Offer Acceptances on behalf of Interconnector Users and will co-ordinate instructions relating to Ancillary Services and Emergency Instructions on behalf of Interconnector Users using its External System in respect of each Interconnector Users BM Units.

(b)	The Company will issue Bid-Offer Acceptances and instructions for Ancillary Services relating to Interconnector Users BM Units to each Externally Interconnected System Operator in respect of each Interconnector User using its External System.

(c)	If, as a result of a reduction in the capability (in MW) of the External Interconnection, the total of the Physical Notifications and Bid-Offer Acceptances issued for the relevant period using that External Interconnection, as stated in the BM Unit Data exceeds the reduced capability (in MW) of the respective External Interconnection in that period then The Company shall notify the Externally Interconnected System Operator accordingly. The Externally Interconnected System Operator should seek a revision of Export and Import Limits from one or more of its Interconnector Users for the remainder of the Balancing Mechanism period during which Physical Notifications cannot be revised.

BC2.13		LIAISON WITH INTERCONNECTOR OWNERS

- Calculate the Interconnector Scheduled Transfer

- Interconnector Owners shall use best endeavours to deliver an updated

Interconnector Scheduled Transfer to NGET by 10 minutes after each Intraday Cross-Zonal Gate Closure Time.

- The updated Interconnector Scheduled Transfer shall

fully reflect the results of the Single Intraday Coupling.

- Interconnector Owners must ensure that the updated

Interconnector Scheduled Transfer is received in its entirety and logged into NGET’s computer systems by the time of 10 minutes after each Intraday Cross-zonal Gate Closure Time.

APPENDIX 1 - FORM OF BID-OFFER ACCEPTANCES

BC2.A.1.1	This Appendix describes the forms of Bid-Offer Acceptances. As described in BC2.6.1 Bid-Offer Acceptances are normally given by an automatic logging device, but in the event of failure of the logging device, Bid-Offer Acceptances will be given by telephone.

BC2.A.1.2	For each BM Unit the Bid-Offer Acceptance will consist of a series of MW figures and associated times.

BC2.A.1.3	The Bid-Offer Acceptances relating to CCGT Modules will assume that the CCGT Units within the CCGT Module will operate in accordance with the CCGT Module Matrix, as required by BC1. The Bid-Offer Acceptances relating to Cascade Hydro Schemes will assume that the Generating Unit forming part of the Cascade Hydro Scheme will operate, where submitted, in accordance with the Cascade Hydro Scheme Matrix submitted under BC1. The Bid-Offer Acceptances relating to Synchronous Power Generating Modules will assume that the Synchronous Generating Units within the Synchronous Power Generating Module will operate in accordance with the Synchronous Power Generating Module Matrix, as required by BC1.

BC2.A.1.4	Bid-Offer Acceptances Given By Automatic Logging Device

(a)	The complete form of the Bid-Offer Acceptance is given in the EDL Message Interface Specification which can be made available to Users on request.

(b)	Bid-Offer Acceptances will normally follow the form:

(i)	BM Unit Name

(ii)	Instruction Reference Number

(iii)	Time of instruction

(iv)	Type of instruction

(v)	BM Unit Bid-Offer Acceptance number

(vi)	Number of MW/Time points making up instruction (minimum 2, maximum 5)

(vii)	MW value and Time value for each point identified in (vi)

The times required in the instruction are input and displayed in London time, but communicated electronically in GMT.

BC2.A.1.5	Bid-Offer Acceptances Given By Telephone

(a)	All run-up/run-down rates will be assumed to be constant and consistent with Dynamic Parameters. Each Bid-Offer Acceptance will, wherever possible, be kept simple, drawing as necessary from the following forms and BC2.7

(b)	Bid-Offer Acceptances given by telephone will normally follow the form:

(i)	an exchange of operator names;

(ii)	BM Unit Name;

(iii)	Time of instruction;

(iv)	Type of instruction;

(v)	Number of MW/Time points making up instruction (minimum 2, maximum 5)

(vi)	MW value and Time value for each point identified in (v)

The times required in the instruction are expressed in London time.

For example, for a BM Unit ABCD-1 acceptance logged with a start time at 1400 hours and with a FPN at 300MW:

“BM Unit ABCD-1 Bid-Offer Acceptance timed at 1400 hours.  Acceptance consists of 4 MW/Time points as follows:

300MW at 1400 hours

400MW at 1415 hours

400MW at 1450 hours

300MW at 1500 hours”

BC2.A.1.6	Submission Of Bid-Offer Acceptance Data To The Bmra

The relevant information contained in Bid-Offer Acceptances issued by The Company will be converted into “from” and “to” MW levels and times before they are submitted to the BMRA by The Company.

APPENDIX 2 - TYPE AND FORM OF ANCILLARY SERVICE INSTRUCTIONS

BC2.A.2.1	This part of the Appendix consists of a non-exhaustive list of the forms and types of instruction for a Genset to provide System Ancillary Services. There may be other types of Commercial Ancillary Services and these will be covered in the relevant Ancillary Services Agreement.  In respect of the provision of Ancillary Services by Generating Units the forms and types of instruction will be in the form of this Appendix 2 unless amended in the Ancillary Services Agreement.

As described in CC.8 and ECC.8, System Ancillary Services consist of Part 1 and Part 2 System Ancillary Services.

Part 1 System Ancillary Services Comprise:

(a)	Reactive Power supplied other than by means of synchronous or static compensators. This is required to ensure that a satisfactory System voltage profile is maintained and that sufficient Reactive Power reserves are maintained under normal and fault conditions. Ancillary Service instructions in relation to Reactive Power may include:

(i)	MVAr Output

(ii)	Target Voltage Levels

(iii)	Tap Changes

(iv)	Maximum MVAr Output (‘maximum excitation’)

(v)	Maximum MVAr Absorption (‘minimum excitation’)

(b)	Frequency Control by means of Frequency sensitive generation. Gensets may be required to move to or from Frequency Sensitive Mode in the combinations agreed in the relevant Ancillary Services Agreement. They will be specifically requested to operate so as to provide Primary Response and/or Secondary Response and/or High Frequency Response.

Part 2 System Ancillary Services Comprise:

(c)	Frequency Control by means of Fast Start.

(d)	Black Start Capability

(e)	A restoration service provided by Restoration Service Providers party to a Distribution Restoration Contract.

(f)	System to Generator Operational Intertripping

BC2.A.2.2	As Ancillary Service instructions are not part of Bid-Offer Acceptances they do not need to be closed instructions and can cover any period of time, not just limited to the period of the Balancing Mechanism.

BC2.A.2.3	As described in BC2.6.1, unless otherwise agreed with The Company, Ancillary Service instructions are normally given by automatic logging device, but in the absence of, or in the event of failure of the logging device, instructions will be given by telephone.

BC2.A.2.4	Instructions given by Automatic Logging Device

(a)	The complete form of the Ancillary Service instruction is given in the EDL Message Interface Specification which is available to Users on request from The Company.

(b)	Ancillary Service instructions for Frequency Control will normally follow the form:

(i)	BM Unit Name

(ii)	Instruction Reference Number

(iii)	Time of instruction

(iv)	Type of instruction (REAS)

(v)	Reason Code

(vi)	Start Time

(c)	Ancillary Service instructions for Reactive Power will normally follow the form:

(i)	BM Unit Name

(ii)	Instruction Reference Number

(iii)	Time of instruction

(iv)	Type of instruction (MVAr, VOLT or TAPP)

(v)	Target Value

(vi)	Target Time

The times required in the instruction are input and displayed in London time, but communicated electronically in GMT.

BC2.A.2.5	Instructions Given By Telephone

(a)	Ancillary Service instructions for Frequency Control will normally follow the form:

(i)	an exchange of operator names;

(ii)	BM Unit Name;

(iii)	Time of instruction;

(iv)	Type of instruction;

(v)	Start Time.

The times required in the instruction are expressed in London time.

For example, for BM Unit ABCD-1 instructed at 1400 hours to provide Primary and High Frequency response starting at 1415 hours:

“BM Unit ABCD-1 message timed at 1400 hours. Unit to Primary and High Frequency Response at 1415 hours”

(b)	Ancillary Service instructions for Reactive Power will normally follow the form:

(a)	an exchange of operator names;

(b)	BM Unit Name;

(c)	Time of instruction;

(d)	Type of instruction (MVAr, VOLT, SETPOINT, SLOPE or TAPP)

(e)	Target Value

(f)	Target Time.

The times required in the instruction are expressed as London time.

For example, for BM Unit ABCD-1 instructed at 1400 hours to provide 100MVAr by 1415 hours:

“BM Unit ABCD-1 message timed at 1400 hours.  MVAr instruction.  Unit to plus 100 MVAr target time 1415 hours.”

BC2.A.2.6	Reactive Power

As described in BC2.A.2.4 and BC2.A.2.5 instructions for Ancillary Services relating to Reactive Power may consist of any of several specific types of instruction. The following table describes these instructions in more detail:

| Instruction Name | Description | Type of Instruction |
| --- | --- | --- |
| MVAr Output | The individual MVAr output from the Genset onto the National Electricity Transmission System at the Grid Entry Point (or onto the User System at the User System Entry Point in the case of Embedded Power Stations), namely on the higher voltage side of the generator step-up transformer or Grid Entry Point or User System Entry Point in the case of a Power Generating Module. In relation to each Genset, where there is no HV indication, The Company and the Generator will discuss and agree equivalent MVAr levels for the corresponding LV indication. Where a Genset is instructed to a specific MVAr output, the Generator must achieve that output within a tolerance of +/-25 MVAr (for Gensets in England and Wales) or the lesser of +/-5% of rated output or 25MVAr (for Gensets in Scotland) (or such other figure as may be agreed with The Company) by tap changing on the generator step-up transformer, or adjusting the Genset terminal voltage, subject to compliance with CC.6.3.8 (a) (v), or ECC.6.3.8.3.3 (as applicable) to a value that is equal to or higher than 1.0p.u. of the rated terminal voltage, or a combination of both. Once this has been achieved, the Generator will not tap again and will not readjust the Genset terminal voltage without prior consultation with and the agreement of The Company, on the basis that MVAr output will be allowed to vary with System conditions. | MVAr |
| Target Voltage Levels | Target voltage levels to be achieved by the Genset on the National Electricity Transmission System at the Grid Entry Point (or on the User System at the User System Entry Point in the case of Embedded Power Stations, namely on the higher voltage side of the generator step-up transformer or Grid Entry Point or User System Entry Point in the case of a Power Generating Module. Where a Genset is instructed to a specific target voltage, the Generator must achieve that target within a tolerance of ±1 kV (or such other figure as may be agreed with The Company) by tap changing on the generator step-up transformer, or adjusting the Genset terminal voltage, subject to compliance with CC.6.3.8 (a) (v) or ECC.6.3.8.3.3 (as applicable), to a value that is equal to or higher than 1.0p.u. of the rated terminal voltage, or a combination of both. In relation to each Genset, where there is no HV indication, The Company and the Generator will discuss and agree equivalent voltage levels for the corresponding LV indication. Under normal operating conditions, once this target voltage level has been achieved the Generator will not tap again and will not readjust the Genset terminal voltage without prior consultation with, and with the agreement of, The Company. However, under certain circumstances the Generator may be instructed to maintain a target voltage until otherwise instructed and this will be achieved by tap changing on the generator step-up transformer, or adjusting the Genset terminal voltage, subject to compliance with CC.6.3.8 (a) (v) or ECC.6.3.8.3.3 (as applicable), to a value that is equal to or higher than 1.0p.u. of the rated terminal voltage, or a combination of both without reference to The Company. | VOLT |
| Setpoint Voltage | Where a Non-Synchronous Generating Unit, DC Converter or Power Park Module or HVDC Converter is instructed to a specific Setpoint Voltage, the Generator must achieve that Setpoint Voltage within a tolerance of ±0.25% (or such other figure as may be agreed with The Company). The Generator must maintain the specified Setpoint Voltage target until an alternative target is received from The Company. | SETPOINT |
| Slope | Where a Non-Synchronous Generating Unit, DC Converter or Power Park Module or HVDC Converter is instructed to a specific Slope, the Generator must achieve that Slope within a tolerance of ±0.5% (or such other figure as may be agreed with The Company). The Generator must maintain the specified Slope target until an alternative target is received from The Company. The Generator will not be required to implement a new Slope setting in a time of less than 1 week from the time of the instruction. | SLOPE |
| Tap Changes | Details of the required generator step-up transformer tap changes in relation to a Genset. The instruction for tap changes may be a Simultaneous Tap Change instruction, whereby the tap change must be effected by the Generator in response to an instruction from The Company issued simultaneously to relevant Power Stations. The instruction, which is normally preceded by advance notice, must be effected as soon as possible, and in any event within one minute of receipt from The Company of the instruction. For a Simultaneous Tap Change, change Genset generator step-up transformer tap position by one [two] taps to raise or lower (as relevant) System voltage, to be executed at time of instruction. | TAPP |
| Maximum MVAr Output (“maximum excitation”) | Under certain conditions, such as low System voltage, an instruction to maximum MVAr output at instructed MW output ("maximum excitation") may be given, and a Generator should take appropriate actions to maximise MVAr output unless constrained by plant operational limits or safety grounds (relating to personnel or plant). |  |
| Maximum MVAr Absorption ("minimum excitation") | Under certain conditions, such as high System voltage, an instruction to maximum MVAr absorption at instructed MW output ("minimum excitation") may be given, and a Generator should take appropriate actions to maximise MVAr absorption unless constrained by plant operational limits or safety grounds (relating to personnel or plant). |  |

BC2.A.2.7	In addition, the following provisions will apply to Reactive Power instructions:

(a)	In circumstances where The Company issues new instructions in relation to more than one BM Unit at the same Power Station at the same time, tapping will be carried out by the Generator one tap at a time either alternately between (or in sequential order, if more than two), or at the same time on, each BM Unit.

(b)	Where the instructions require more than two taps per BM Unit and that means that the instructions cannot be achieved within 2 minutes of the instruction time (or such longer period at The Company may have instructed), the instructions must each be achieved with the minimum of delay after the expiry of that period.

(c)	It should be noted that should System conditions require, The Company may need to instruct maximum MVAr output to be achieved as soon as possible, but (subject to the provisions of paragraph (BC2.A.2.7(b) above) in any event no later than 2 minutes after the instruction is issued.

(d)	An Ancillary Service instruction relating to Reactive Power may be given in respect of CCGT Units within a CCGT Module at a Power Station or Generating Units within a Synchronous Power Generating Module at a Power Station where running arrangements and/or System conditions require, in both cases where exceptional circumstances apply and connection arrangements permit.

(e)	In relation to MVAr matters, MVAr generation/output is an export onto the System and is referred to as "lagging MVAr", and MVAr absorption is an import from the System and is referred to as "leading MVAr".

(f)	It should be noted that the excitation control system constant Reactive Power output control mode or constant Power Factor output control mode will always be disabled, unless agreed otherwise with The Company.

APPENDIX 3 - SUBMISSION OF REVISED MVAr CAPABILITY

BC2.A.3.1	For the purpose of submitting revised MVAr data the following terms shall apply:

| Full Output | In the case of a Synchronous Generating Unit (as defined in the Glossary and Definitions ((which could be part of a Synchronous Power Generating Module) and not limited by BC2.2) is the MW output measured at the generator stator terminals representing the LV equivalent of the Registered Capacity at the Grid Entry Point, and in the case of a Non-Synchronous Generating Unit (excluding Power Park Units), HVDC Converter or DC Converter or Power Park Module is the Registered Capacity at the Grid Entry Point |
| --- | --- |
| Minimum Output | In the case of a Synchronous Generating Unit (as defined in the Glossary and Definitions ((which could be part of a Synchronous Power Generating Module) and not limited by BC2.2) is the MW output measured at the generator stator terminals representing the LV equivalent of the Minimum Generation or Minimum Stable Operating Level at the Grid Entry Point, and in the case of a Non-Synchronous Generating Unit (excluding Power Park Units), HVDC Converter or DC Converter or Power Park Module is the Minimum Generation or Minimum Stable Operating Level or Minimum Active Power Transmission Capacity at the Grid Entry Point |

BC2.A.3.2	The following provisions apply to faxed submission of revised MVAr data:

(a)	The fax must be transmitted to The Company (to the relevant location in accordance with GC6) and must contain all the sections from the relevant part of Annexure 1 and from either Annexure 2 or 3 (as applicable) but with only the data changes set out. The "notification time" must be completed to refer to the time of transmission, where the time is expressed as London time.

(b)	Upon receipt of the fax, The Company will acknowledge receipt by sending a fax back to the User. The acknowledgement will either state that the fax has been received and is legible or will state that it (or part of it) is not legible and will request re-transmission of the whole (or part) of the fax.

(c)	Upon receipt of the acknowledging fax the User will, if requested, re-transmit the whole or the relevant part of the fax.

(d)	The provisions of paragraphs (b) and (c) then apply to that re-transmitted fax.

APPENDIX 3 - ANNEXURE 1

Optional Logo

Company name REVISED REACTIVE POWER

CAPABILITY DATA

| TO: | National Electricity Transmission System Control Centre |  |  | Fax telephone No. |
| --- | --- | --- | --- | --- |

Number of pages inc. header:.............................

Sent By : ........................................................................................................

Return Acknowledgement Fax to ....................................................................

For Retransmission or Clarification ring..........................................................

Acknowledged by The Company: (Signature)

................................................................................

Acknowledgement time and date

....................................................................................

Legibility of FAX :

| Acceptable |  |  |
| --- | --- | --- |
| Unacceptable (List pages if appropriate) |  | ( Resend FAX ) |

APPENDIX 3 - ANNEXURE 2

To:	 National Electricity Transmission System Control Centre

From :	[Company Name & Location]

REVISED REACTIVE POWER CAPABILITY DATA – GENERATING UNITS EXCLUDING POWER PARK MODULES AND DC CONVERTERS

| Notification Time (HH:MM): | Notification Date (DD/MM/YY): |
| --- | --- |
| Start Time (HH:MM): | Start Date (DD/MM/YY): |
| Generating Unit* |  |

* For a Synchronous Power Generating Module and/or CCGT Module and/or a Cascade Hydro Scheme, the redeclaration is for a Generating Unit within a Synchronous Power Generating Module and/or CCGT Module and/or Cascade Hydro Scheme. For BM Units quote The Company BM Unit id, for other units quote the Generating Unit id used for OC2.4.1.2 Outage Planning submissions. Generating Unit has the meaning given in the Glossary and Definitions and is not limited by BC2.2.

REVISION TO THE REACTIVE POWER CAPABILITY AT THE GENERATING UNIT STATOR TERMINALS (at rated terminal volts) AS STATED IN THE RELEVANT ANCILLARY SERVICES AGREEMENT:

|  | MW | MINIMUM (MVAr +ve for lag, -ve for lead) | MAXIUM (MVAr +ve for lag, -ve for lead) |
| --- | --- | --- | --- |
| AT RATED MW |  |  |  |
| AT FULL OUTPUT (MW) |  |  |  |
| AT MINIMUM OUTPUT (MW) |  |  |  |

COMMENTS e.g. generator transformer tap restrictions, predicted end time if known

_________________________________________________________________________

_________________________________________________________________________

Redeclaration made by (Signature)

_________________________________________________

APPENDIX 3 - ANNEXURE 3

To:	 National Electricity Transmission System Control Centre

From :	[Company Name & Location]

REVISED REACTIVE POWER CAPABILITY DATA – POWER PARK MODULES, HVDC CONVERTERS AND DC  CONVERTERS

| Notification Time (HH:MM): | Notification Date (DD/MM/YY): |
| --- | --- |
| Start Time (HH:MM): | Start Date (DD/MM/YY): |
| Power Park Module / DC Converter* |  |

* For BM Units quote The Company BM Unit id, for other units quote the id used for OC2.4.1.2 Outage Planning submissions

Start Time/Date (if not effective immediately)

REVISION TO THE REACTIVE POWER CAPABILITY AT THE COMMERCIAL BOUNDARY AS STATED IN THE RELEVANT ANCILLARY SERVICES AGREEMENT:

|  | MINIMUM (MVAr +ve for lag, -ve for lead) | MAXIMUM (MVAr +ve for lag, -ve for lead) |
| --- | --- | --- |
| AT RATED MW |  |  |
| AT 50% OF RATED MW |  |  |
| AT 20% OF RATED MW |  |  |
| BELOW 20% OF RATED MW |  |  |
| AT 0% OF RATED MW |  |  |

COMMENTS e.g. generator transformer tap restrictions, predicted end time if known

_________________________________________________________________________

_________________________________________________________________________

Redeclaration made by (Signature)

_________________________________________________
APPENDIX 4 - SUBMISSION OF AVAILABILITY OF FREQUENCY SENSITIVE MODE

BC2.A.4.1	For the purpose of submitting availability of Frequency Sensitive Mode, this process only relates to the provision of response under the Frequency Sensitive Mode and does not cover the provision of response under the Limited Frequency Sensitive Mode.

BC2.A.4.2	The following provisions apply to the faxed submission of the Frequency Sensitive Mode availability;

(a)	The fax must be transmitted to The Company (to the relevant location in accordance with GC6) and must contain all the sections relevant to Appendix 4 - Annexure1 but with only the data changes set out. The “notification time” must be completed to refer to the time and date of transmission, where the time is expressed in London time.

(b)	Upon receipt of the fax, The Company will acknowledge receipt by sending a fax back to the User.  This acknowledging fax should be in the format of Appendix 4 – Annexure 1. The acknowledgement will either state that the fax has been received and is legible or will state that it (or part of it) is not legible and will request re-transmission of the whole (or part) of the fax.

(c)	Upon receipt of the acknowledging fax the User will, if requested re-transmit the whole or the relevant part of the fax.

(d)	The provisions of paragraph (b) and (c) then apply to the re-transmitted fax.

BC2.A.4.3	The User shall ensure the availability of operating in the Frequency Sensitive Mode is restored as soon as reasonably practicable and will notify The Company using the format of Appendix 4 – Annexure 1. In the event of a sustained unavailability of Frequency Sensitive Mode, The Company may seek to confirm compliance with the relevant requirements in the CC or ECC through the process in OC5 or ECP.

APPENDIX 4 - ANNEXURE 1

To:	 National Electricity Transmission System Control Centre

From :	[Company Name & Location]

Submission of availability of Frequency Sensitive Mode

| Notification Time (HH:MM): | Notification Date (DD/MM/YY): |
| --- | --- |
| Start Time (HH:MM): | Start Date (DD/MM/YY): |
| Genset or DC Converter |  |

The availability of the above unit to operate in Frequency Sensitive Mode is as follows:

All contract modes: Available / Unavailable [delete as applicable]; or

Change to the availability of individual contract modes:

| Contract Mode e.g. A | Availability for operation in Frequency Sensitive Mode [Y/N] |
| --- | --- |

COMMENTS e.g. reason for submission, predicted end time if known

_________________________________________________________________________

_________________________________________________________________________

Redeclaration made by (Signature)______________________________________________

Receipt Acknowledgement from The Company

| Legible (tick box) |  | Illegible (tick box) |  |
| --- | --- | --- | --- |
| Explanation: |  |  |  |
| Time: Date: Signature: |  |  |  |

< END OF BALANCING CODE 2 >

Extracts from Data Registration Code

SCHEDULE 5 Users System Data

Page 8 of 11

Table 5 (h)

| Distribution Restoration INFORMATION The following data/text items are required from Network Operators as detailed in PC.A.5.8 in relation to a Distribution Restoration Zone Plan. The data should be provided in accordance with PC.A.1.2 and also, where possible, upon request from The Company during a Black Start. |  |  |
| --- | --- | --- |
| Data Description (PC.A.5.8) (■ CUSC Contract) | Units | Data Category |
| Assuming all Restoration Service Provider’s Plant and Apparatus were running immediately prior to the Total Shutdown or Partial Shutdown and in the event of loss of all external power supplies, provide the following information: |  |  |
| a) Expected time for Restoration Service Provider’ s Plant to be Synchronised, following a Total Shutdown or Partial Shutdown. | Tabular or Graphical | DPD II |
| b) Describe any likely any specific issues (eg those that would affect the time before which the Anchor Plant and Restoration Service Provider’s Plant could be Synchronised) that may arise as time progresses from Shutdown without external supplies being restored. | Text |  |
| (c) The expected time for each Power Generating Module or HVDC System or DC Converter to re-synchronise to the Network Operator’s System if all were running immediately prior to the Total Shutdown or Partial Shutdown. Additionally, this should highlight any specific issues (ie those that would affect the time before which the Power Generating Module or HVDC System or DC Converter could be Synchronised) that may arise, as time progresses without external supplies being restored. | Text | DPD II |
| Block Loading Capability: |  |  |
| a) Provide estimated Block Loading Capability. This should be provided in either graphical or tabular format showing the estimated Block Loading Capability from 0MW to Registered Capacity. Any particular Active Power loading points at which the Anchor Plant or Restoration Service Provider’s Plant should be operated until further changes in output can be accommodated should also be identified. The data of each Anchor Plant and Restoration Service Provider’s Plant forming part of a Distribution Restoration Zone should be provided for the condition of an Anchor Plant or Restoration Service Provider’ s Plant (which is considered as both a ‘ hot’ unit (operating immediately prior to, and at the point of, Shutdown) and cold unit (not operated for 48 hours or more prior to the Shutdown). In the case of an Anchor HVDC System or Anchor DC Converter, data should be provided when the Anchor HVDC System or Anchor DC Converter has been considered to have run immediately prior to the Total Shutdown or Partial Shutdown and equally when the HVDC System or DC Converter has been considered to have been Shutdown for a period of 48 hours or more. The block loading assessment should be done against a frequency variation of 49.5Hz – 50.5Hz. | Tabular or Graphical | DPD II |

……………

SCHEDULE 14 - FAULT INFEED DATA (GENERATORS INCLUDING UNIT TRANSFORMERS AND STATION TRANSFORMERS)

PAGE 1 OF 5

The data in this Schedule 14 is all Standard Planning Data, and is to be provided by Generators, with respect to all directly connected Power Stations, all Embedded Large Power Stations and all Embedded Medium Power Stations connected to the Subtransmission System. A data submission is to be made each year in Week 24.

Fault infeeds via Unit Transformers

A submission should be made for each Generating Unit (including those which are part of a Synchronous Power Generating Module) with an associated Unit Transformer. Where there is more than one Unit Transformer associated with a Generating Unit, a value for the total infeed through all Unit Transformers should be provided. The infeed through the Unit Transformer(s) should include contributions from all motors normally connected to the Unit Board, together with any generation (e.g. Auxiliary Energy Supplies) which would normally be connected to the Unit Board, and should be expressed as a fault current at the Generating Unit terminals for a fault at that location.

………………………..

SCHEDULE 14 - FAULT INFEED DATA (GENERATORS INCLUDING UNIT TRANSFORMERS AND STATION TRANSFORMERS)

PAGE 2 OF 5

Fault infeeds via Station Transformers

A submission is required for each Station Transformer directly connected to the National Electricity Transmission System. The submission should represent normal operating conditions when the maximum number of Gensets are Synchronised to the System, and should include the fault current from all motors normally connected to the Station Board, together with any Generation (e.g. Auxiliary Energy Supplies) which would normally be connected to the Station Board. The fault infeed should be expressed as a fault current at the hv terminals of the Station Transformer for a fault at that location.

……………….

SCHEDULE 19 – USER DATA FILE STRUCTURE

PAGE 1 OF 2

The structure of the User Data File Structure is given below.

| i.d. | Folder name | Description of contents |
| --- | --- | --- |
| Part A: Commercial & Legal |  |  |
| A2 | Commissioning | Commissioning & Test Programmes |
| A3 | Statements | Statements of Readiness |
| A9 | AS Monitoring | Ancillary Services Monitoring |
| A10 | Self Certification | User Self Certification of Compliance |
| A11 | Compliance statements | Compliance Statement |
| Part 1: Safety & System Operation |  |  |
| 1.1 | Interface Agreements | Interface Agreements |
| 1.2 | Safety Rules | Safety Rules |
| 1.3 | Switching Procedures | Local Switching Procedures |
| 1.4 | Earthing | Earthing |
| 1.5 | SRS | Site Responsibility Schedules |
| 1.6 | Diagrams | Operational and Gas Zone Diagrams |
| 1.7 | Drawings | Site Common Drawings |
| 1.8 | Telephony | Control Telephony |
| 1.9 | Safety Procedures | Local Safety Procedures |
| 1.10 | Co-ordinators | Safety Co-ordinators |
| 1.11 | RISSP | Record of Inter System Safety Precautions |
| 1.12 | Tel Numbers | Telephone Numbers for Joint System Incidents |
| 1.13 | Contact Details | Contact Details (fax, tel, email) |
| 1.14 | Restoration Plan | Local Joint Restoration Plan and Distribution Restoration Zone Plan (incl. black start if applicable) |
| 1.15 | Maintenance | Maintenance Standards |
| Part 2: Connection Technical Data |  |  |
| 2.1 | DRC Schedule 5 | DRC Schedule 5 – Users System Data |
| 2.2 | Protection Report | Protection Settings Reports |
| 2.3 | Special Automatic Facilities | Special Automatic Facilities e.g. intertrip |
| 2.4 | Operational Metering | Operational Metering |
| 2.5 | Tariff Metering | Tariff Metering |
| 2.6 | Operational Comms | Operational Communications |
| 2.7 | Monitoring | Performance Monitoring |
| 2.8 | Power Quality | Power Quality Test Results (if required) |

SCHEDULE 19 – USER DATA FILE STRUCTURE

PAGE 2 OF 2

| Part 3: Generator Technical Data |  |  |
| --- | --- | --- |
| 3.1 | DRC Schedule 1 | DRC Schedule 1 - Generating Unit, Power Generating Module, HVDC System and DC Converter Technical Data |
| 3.2 | DRC Schedule 2 | DRC Schedule 2 - Generation Planning Data |
| 3.3 | DRC Schedule 4 | DRC Schedule 4 – Frequency Droop & Response |
| 3.4 | DRC Schedule 14 | DRC Schedule 14 – Fault Infeed Data – Generators |
| 3.5 | Special Generator Protection | Special Generator Protection eg Pole slipping; islanding |
| 3.6 | Compliance Tests | Compliance Tests & Evidence |
| 3.7 | Compliance Studies | Compliance Simulation Studies |
| 3.8 | Site Specific | Bilateral Connections Agreement Technical Data & Compliance |
| Part 4: General DRC Schedules |  |  |
| 4.1 | DRC Schedule 3 | DRC Schedule 3 – Large Power Station Outage Information |
| 4.2 | DRC Schedule 6 | DRC Schedule 6 – Users Outage Information |
| 4.3 | DRC Schedule 7 | DRC Schedule 7 – Load Characteristics |
| 4.4 | DRC Schedule 8 | DRC Schedule 8 – BM Unit Data (if applicable) |
| 4.5 | DRC Schedule 10 | DRC Schedule 10 –Demand Profiles |
| 4.6 | DRC Schedule 11 | DRC Schedule 11 – Connection Point Data |
| Part 5: OTSDUW Data And Information (if applicable and prior to OTSUA Transfer Time) |  |  |
|  |  | Diagrams |
|  |  | Circuits Plant and Apparatus |
|  |  | Circuit Parameters |
|  |  | Protection Operation and Autoswitching |
|  |  | Automatic Control Systems |
|  |  | Mathematical model of dynamic compensation plant |

< END OF DATA REGISTRATION CODE >

Extracts from General Conditions

……………….

GC.A.1.11	The following matters potentially require amendments to the GB Grid Code:

(a)	The specific detail of the obligations needed to manage implementation in the period up to and following (for a temporary period) Go-Live to achieve the change to operation under the GB Grid Code (to be included in GC.A.3).

(b)	Information (including data) and other requirements under the GB Grid Code applicable to Scottish Users during the Transition Period (to be included in GC.A.2).

(c)	The conclusions of Ofgem/DTI in relation to small and/or embedded generator issues under BETTA and allocation of access rights on a GB basis.

(d)	Any arrangements required to make provision for operational liaison, including Black Start and islanding arrangements in Scotland.

(e)	Any arrangements required to make provision for cascade hydro BM Units.

(f)	Any consequential changes to the safety co-ordination arrangements resulting from STC and STC procedure development.

(g)	Any arrangements required to reflect the Electrical Standards for the Transmission Systems of SPT and SHETL.

(h)	The conclusions of Ofgem/DTI in relation to planning and operating standards.

GC.A.1.12	The Company shall notify the Authority of any amendments that The Company identifies as needed pursuant to GC.A.1.10 and shall make such amendments as the Authority approves.

…………………