## Version
Date | Version | Details
2022-10-14 | 1 | This file only contains the indicative reporting associated with draft data for GC151 for October 2022. This file will be updated in November to reflect the full data set.
2022-11-11 | 2 | This file only contains the indicative reporting associated with data for GC151 for October 2022.
2023-01-06 | 3 | This file only contains the reporting associated with data for GC0105 & GC151 for October 2022.

## Notes
Subject | Notes
RoCoF | RoCoF=(frequency_500ms - frequency_0ms)/500ms RoCoF is calculated using 500ms sliding window. Note that smaller losses will have less accurate ROCOF calculations The RoCoF figure in this report is from external service
System Inertia | Monitoring which transmission-connected generators are running and adding an estimate of inertia from embedded generation and demand
Data 'N/A' | N/A: data not applicable or potentially unreliable. For example, there maybe events when the loss of infeed or exfeed is not instantaneous (over long time period), the calculated RoCoF may not be indicative. For some events, during a disturbance the data may potentially be unreliable. NGESO will apply engineering judgement to determine whether the derived/calculated data is suitable for sharing.
MW trip/loss of all generation/ interconnection related to the incident | Positive sign: indicates a loss of infeed, generator or importing interconnector. Negative sign: indicates a loss of outfeed, exporting interconnector.

## Transmission Faults (GC0151)
Location | Network Operator | Date Time | Voltage Trace (Refer to sheet) | Notes
AMEM -ECLA -IVER 1 Tripped and DAR'd, and IVER SGT5B and SGT6B Tripped | NGET | 2022-10-03 23:50
Blackhillock Converter Tripped | SHETL | 2022-10-08 11:43
Sundon MSC1 Tripped | NGET | 2022-10-17 15:38
Feckenham SGT4 Tripped | NGET | 2022-10-20 09:12
Abham - Langage - Exeter 1 and Abham SGT2 Tripped | NGET | 2022-10-23 03:23 | 20221023-1
Pelham - Rye House - Waltham Cross 2 and Rye House SGT2 Tripped and Partially DAR'd | NGET | 2022-10-23 17:43
Bradford West - Monk Fryston and Bradford West SGT4 and MC4 Tripped | NGET | 2022-10-31 19:05

## System Incidents (GC0105)
|  |  | Date and time of the incident | System frequency trace (1-second interval) for the incident | System frequency immediately before the incident | System frequency immediately after the incident | Maximum/Minimum rate of change of frequency (RoCoF) of the incident | System inertia at the time of the incident | Where known, MW trip/loss of all generation/ interconnection related to the incident |  | Where known, MW trip/loss of all Embedded Generation(EG) related to the incident | Where known, MW trip/loss of all DNO demand related to the incident; | Transmission fault associated with the incident; | Any transient voltage dip (loss % and duration) at the local substation associated with the incident | Any other data to gain a clearer understanding of the incident and its potential implications
Reference | Name | Notes | Date Time | System Frequency (Refer to sheet) | Pre-Event Frequency (Hz) | Post-Event Frequency (Hz) | RoCoF (Hz/s) | System Inertia (GVAs) | Generation/Interconnection (MW) |  | EG (MW) | Demand (MW) | Transmission fault | Voltage Dip | Additional data
20221006-1 | DINO-2 Trip |  | 2022-10-06 03:15 | 20221006-1 | 49.917 | 50.048 | 0.045812 | 141 | DINO-2 | -270
20221007-1 | DAMC-1 Trip |  | 2022-10-07 16:51 | 20221007-1 | 49.977 | 49.777 | -0.059823 | 180 | DAMC-1 | 540
20221015-1 | IFA1 BP2 deloaded |  | 2022-10-15 08:47 | 20221015-1 | 49.814 | 49.893 | 0.010902 | 205 | IFA1 BP2 | -458
20221017-1 | IFA1 BP2 Trip |  | 2022-10-17 22:43 | 20221017-1 | 49.98 | 50.271 | 0.097799 | 256 | IFA1 BP2 | -1028
20221017-2 | DAMC-1 Trip |  | 2022-10-17 23:32 | 20221017-2 | 49.956 | 49.813 | -0.051627 | 245 | DAMC-1 | 461
20221025-1 | PEMB-51 ramped down to zero |  | 2022-10-25 20:12 | 20221025-1 | 50.021 | 49.949 | -0.015355 | 280 | PEMB-51 | 411
20221028-1 | HUMR-1 Trip |  | 2022-10-28 08:39 | 20221028-1 | 50.099 | 49.981 | -0.04574 | 223 | HUMR-1 | 294
20221030-1 | DINO-3 Trip |  | 2022-10-30 20:30 | 20221030-1 | 50.035 | 49.778 | -0.011986 | 233 | DINO-3 | 300

## 20221023-1
<DATE(0/DATE) | TIME(1/TIME) | IA (A) | IB (A) | IC (A) | IG (A) | VA (pu) | VB (pu) | VC (pu) | VN (pu)
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.0414 | 1.0408 | 1.0382 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.0414 | 1.0407 | 1.0383 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0415 | 1.0406 | 1.0384 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0414 | 1.0405 | 1.0385 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0413 | 1.0404 | 1.0386 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0413 | 1.0404 | 1.0387 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0411 | 1.0405 | 1.0387 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.041 | 1.0406 | 1.0387 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0409 | 1.0407 | 1.0388 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0409 | 1.0408 | 1.0387 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0409 | 1.0409 | 1.0386 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0409 | 1.041 | 1.0385 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.041 | 1.0411 | 1.0384 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0411 | 1.0411 | 1.0383 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0412 | 1.041 | 1.0383 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0413 | 1.0409 | 1.0382 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0414 | 1.0408 | 1.0383 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0415 | 1.0406 | 1.0383 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0416 | 1.0405 | 1.0384 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0415 | 1.0405 | 1.0386 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0414 | 1.0404 | 1.0387 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0414 | 1.0404 | 1.0388 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0412 | 1.0405 | 1.0388 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0411 | 1.0406 | 1.0388 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.041 | 1.0407 | 1.0388 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.041 | 1.0408 | 1.0388 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.041 | 1.041 | 1.0387 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.041 | 1.041 | 1.0386 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0411 | 1.0411 | 1.0385 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0412 | 1.0411 | 1.0384 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0413 | 1.0409 | 1.0383 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0414 | 1.0408 | 1.0383 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0415 | 1.0407 | 1.0383 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0415 | 1.0405 | 1.0384 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0415 | 1.0404 | 1.0385 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0414 | 1.0404 | 1.0386 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0414 | 1.0403 | 1.0388 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0412 | 1.0403 | 1.0389 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0411 | 1.0404 | 1.0389 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0409 | 1.0405 | 1.0389 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0408 | 1.0406 | 1.0388 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0408 | 1.0407 | 1.0388 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0408 | 1.0409 | 1.0387 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0408 | 1.041 | 1.0386 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0409 | 1.041 | 1.0385 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.041 | 1.041 | 1.0383 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0411 | 1.0409 | 1.0383 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0412 | 1.0408 | 1.0382 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0412 | 1.0406 | 1.0383 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0412 | 1.0405 | 1.0383 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0412 | 1.0404 | 1.0384 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0411 | 1.0403 | 1.0385 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.041 | 1.0403 | 1.0386 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0408 | 1.0403 | 1.0386 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0406 | 1.0403 | 1.0387 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0405 | 1.0404 | 1.0387 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0404 | 1.0405 | 1.0386 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0403 | 1.0407 | 1.0385 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0403 | 1.0408 | 1.0383 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0404 | 1.0409 | 1.0382 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0405 | 1.0409 | 1.0381 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0406 | 1.0409 | 1.038 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0407 | 1.0409 | 1.0379 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0408 | 1.0408 | 1.0379 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0409 | 1.0406 | 1.0379 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0409 | 1.0405 | 1.038 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0409 | 1.0404 | 1.0381 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0409 | 1.0403 | 1.0382 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0407 | 1.0403 | 1.0383 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0406 | 1.0403 | 1.0384 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0405 | 1.0403 | 1.0385 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0403 | 1.0404 | 1.0386 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0403 | 1.0406 | 1.0386 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0402 | 1.0407 | 1.0385 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0402 | 1.0409 | 1.0383 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0403 | 1.0409 | 1.0382 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0403 | 1.041 | 1.038 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0404 | 1.041 | 1.0379 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0406 | 1.0409 | 1.0379 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0407 | 1.0408 | 1.0378 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0408 | 1.0407 | 1.0379 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0409 | 1.0406 | 1.0379 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0409 | 1.0404 | 1.038 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0409 | 1.0403 | 1.0382 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0408 | 1.0403 | 1.0383 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0406 | 1.0403 | 1.0385 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0405 | 1.0404 | 1.0385 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0404 | 1.0405 | 1.0386 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0403 | 1.0406 | 1.0386 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0403 | 1.0407 | 1.0385 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0403 | 1.0408 | 1.0385 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0403 | 1.0409 | 1.0383 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0404 | 1.041 | 1.0382 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0405 | 1.041 | 1.0381 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0406 | 1.0409 | 1.038 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0408 | 1.0408 | 1.038 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0408 | 1.0407 | 1.0381 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0408 | 1.0405 | 1.0381 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0409 | 1.0404 | 1.0383 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0409 | 1.0403 | 1.0384 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0408 | 1.0403 | 1.0385 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0407 | 1.0403 | 1.0386 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0406 | 1.0404 | 1.0387 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0405 | 1.0405 | 1.0388 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0405 | 1.0406 | 1.0387 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0404 | 1.0407 | 1.0387 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0404 | 1.0407 | 1.0386 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0404 | 1.0408 | 1.0385 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0405 | 1.0408 | 1.0384 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0406 | 1.0409 | 1.0383 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0407 | 1.0408 | 1.0382 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0408 | 1.0407 | 1.0382 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0409 | 1.0406 | 1.0383 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.041 | 1.0405 | 1.0383 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0411 | 1.0404 | 1.0384 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0411 | 1.0403 | 1.0386 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0411 | 1.0403 | 1.0387 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.041 | 1.0403 | 1.0389 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0409 | 1.0404 | 1.039 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0408 | 1.0405 | 1.039 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0407 | 1.0406 | 1.039 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0407 | 1.0407 | 1.039 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0407 | 1.0407 | 1.0389 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0407 | 1.0408 | 1.0387 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0408 | 1.0408 | 1.0386 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0409 | 1.0408 | 1.0385 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.041 | 1.0407 | 1.0385 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0411 | 1.0406 | 1.0385 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0412 | 1.0405 | 1.0385 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0413 | 1.0404 | 1.0386 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0413 | 1.0403 | 1.0386 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0413 | 1.0402 | 1.0388 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0412 | 1.0402 | 1.0389 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0411 | 1.0402 | 1.039 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.041 | 1.0402 | 1.0391 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0409 | 1.0403 | 1.0392 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0409 | 1.0404 | 1.0392 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0408 | 1.0405 | 1.0391 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0408 | 1.0406 | 1.039 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0409 | 1.0406 | 1.0388 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0409 | 1.0406 | 1.0387 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.041 | 1.0406 | 1.0386 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0411 | 1.0406 | 1.0386 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0412 | 1.0405 | 1.0385 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0414 | 1.0404 | 1.0386 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0414 | 1.0403 | 1.0386 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0414 | 1.0402 | 1.0388 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0414 | 1.0401 | 1.0389 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0414 | 1.0401 | 1.0391 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0413 | 1.0401 | 1.0392 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0412 | 1.0401 | 1.0393 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0411 | 1.0402 | 1.0393 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.041 | 1.0403 | 1.0393 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.041 | 1.0404 | 1.0392 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.041 | 1.0405 | 1.039 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.041 | 1.0406 | 1.0389 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0411 | 1.0407 | 1.0388 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0412 | 1.0407 | 1.0387 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0414 | 1.0407 | 1.0387 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0416 | 1.0407 | 1.0386 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0417 | 1.0406 | 1.0387 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0418 | 1.0404 | 1.0388 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0419 | 1.0403 | 1.0389 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0419 | 1.0402 | 1.0391 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0418 | 1.0402 | 1.0392 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0417 | 1.0402 | 1.0393 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0416 | 1.0403 | 1.0393 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0414 | 1.0404 | 1.0392 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0414 | 1.0405 | 1.0392 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0413 | 1.0406 | 1.0392 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0413 | 1.0407 | 1.0391 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0414 | 1.0408 | 1.039 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0414 | 1.0409 | 1.0389 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0416 | 1.0409 | 1.0388 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0418 | 1.0409 | 1.0387 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0419 | 1.0408 | 1.0387 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0421 | 1.0407 | 1.0387 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0422 | 1.0405 | 1.0388 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0422 | 1.0404 | 1.0389 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0421 | 1.0403 | 1.039 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0419 | 1.0403 | 1.0391 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0417 | 1.0403 | 1.0391 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0416 | 1.0404 | 1.0391 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0414 | 1.0405 | 1.0391 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0413 | 1.0407 | 1.0391 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0413 | 1.0409 | 1.039 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0413 | 1.041 | 1.039 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0413 | 1.0412 | 1.0389 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0415 | 1.0412 | 1.0387 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0416 | 1.0411 | 1.0386 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0417 | 1.0409 | 1.0385 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0418 | 1.0408 | 1.0385 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0418 | 1.0407 | 1.0385 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0418 | 1.0406 | 1.0386 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0418 | 1.0405 | 1.0386 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0417 | 1.0404 | 1.0387 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0416 | 1.0403 | 1.0389 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0414 | 1.0403 | 1.039 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0412 | 1.0404 | 1.039 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0411 | 1.0405 | 1.0391 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.041 | 1.0407 | 1.039 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0409 | 1.0408 | 1.0389 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0409 | 1.041 | 1.0388 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.041 | 1.0411 | 1.0387 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0411 | 1.0411 | 1.0386 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0412 | 1.0411 | 1.0384 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0413 | 1.041 | 1.0384 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0414 | 1.0408 | 1.0383 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0414 | 1.0406 | 1.0384 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0414 | 1.0405 | 1.0384 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0414 | 1.0404 | 1.0385 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0414 | 1.0403 | 1.0386 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0414 | 1.0403 | 1.0387 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0413 | 1.0403 | 1.0389 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0411 | 1.0404 | 1.0391 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.041 | 1.0405 | 1.0391 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0409 | 1.0406 | 1.0391 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0409 | 1.0407 | 1.039 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0409 | 1.0408 | 1.0389 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0409 | 1.0409 | 1.0387 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.041 | 1.0409 | 1.0386 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0411 | 1.0409 | 1.0385 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0412 | 1.0409 | 1.0384 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0413 | 1.0408 | 1.0384 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0414 | 1.0407 | 1.0385 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0415 | 1.0406 | 1.0385 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0415 | 1.0404 | 1.0386 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0415 | 1.0404 | 1.0388 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0414 | 1.0403 | 1.0389 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0414 | 1.0403 | 1.0391 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0413 | 1.0404 | 1.0392 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0411 | 1.0405 | 1.0392 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0411 | 1.0406 | 1.0392 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.041 | 1.0407 | 1.0391 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.041 | 1.0408 | 1.0389 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0411 | 1.0408 | 1.0388 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0412 | 1.0408 | 1.0387 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0413 | 1.0409 | 1.0386 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0414 | 1.0408 | 1.0385 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0415 | 1.0408 | 1.0385 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0416 | 1.0406 | 1.0386 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0417 | 1.0405 | 1.0386 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0417 | 1.0404 | 1.0388 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0417 | 1.0403 | 1.0389 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0416 | 1.0403 | 1.039 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0414 | 1.0403 | 1.0391 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0413 | 1.0403 | 1.0391 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0412 | 1.0404 | 1.0391 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0411 | 1.0406 | 1.039 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.041 | 1.0406 | 1.0389 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.041 | 1.0407 | 1.0388 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0411 | 1.0408 | 1.0387 | 0.00028346
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0412 | 1.0409 | 1.0386 | 0.00028346
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0413 | 1.0409 | 1.0385 | 0.00028346
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0414 | 1.0408 | 1.0384 | 0.00028346
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0416 | 1.0407 | 1.0384 | 0.00028346
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0417 | 1.0406 | 1.0384 | 0.00028346
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0417 | 1.0404 | 1.0385 | 0.00028346
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0417 | 1.0404 | 1.0386 | 0.00028346
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0416 | 1.0403 | 1.0386 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0415 | 1.0403 | 1.0386 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0413 | 1.0403 | 1.0387 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.0411 | 1.0403 | 1.0386 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.0409 | 1.0405 | 1.0386 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.0408 | 1.0406 | 1.0385 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.0408 | 1.0408 | 1.0385 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.0408 | 1.041 | 1.0385 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.0409 | 1.0411 | 1.0384 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.0409 | 1.0412 | 1.0382 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.0411 | 1.0411 | 1.0381 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.0412 | 1.041 | 1.038 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0413 | 1.0409 | 1.038 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0414 | 1.0407 | 1.038 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.049 | 0.006 | 1.0414 | 1.0406 | 1.0381 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.049 | 0.006 | 1.0413 | 1.0405 | 1.0382 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.049 | 0.006 | 1.0412 | 1.0405 | 1.0383 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.049 | 0.006 | 1.041 | 1.0404 | 1.0383 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.049 | 0.006 | 1.0409 | 1.0404 | 1.0383 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.049 | 0.006 | 1.0407 | 1.0405 | 1.0384 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.049 | 0.006 | 1.0406 | 1.0406 | 1.0384 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.049 | 0.006 | 1.0405 | 1.0407 | 1.0384 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.049 | 0.006 | 1.0405 | 1.0409 | 1.0383 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.049 | 0.006 | 1.0405 | 1.041 | 1.0382 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.049 | 0.006 | 1.0406 | 1.0411 | 1.0381 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.049 | 0.006 | 1.0406 | 1.0411 | 1.038 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0408 | 1.0411 | 1.0379 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0409 | 1.041 | 1.0378 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0409 | 1.0409 | 1.0378 | 0.00028346
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.041 | 1.0408 | 1.0378 | 0.00028346
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.041 | 1.0406 | 1.0379 | 0.00028346
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.041 | 1.0405 | 1.038 | 0.00028346
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.041 | 1.0404 | 1.0381 | 0.00028346
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0409 | 1.0404 | 1.0383 | 0.00028346
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0408 | 1.0404 | 1.0384 | 0.00028346
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0407 | 1.0405 | 1.0385 | 0.00028346
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0406 | 1.0406 | 1.0386 | 0.00028346
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0405 | 1.0407 | 1.0386 | 0.00028346
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0405 | 1.0408 | 1.0385 | 0.00028346
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0405 | 1.0408 | 1.0383 | 0.00028346
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0405 | 1.0409 | 1.0382 | 0.00028346
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0406 | 1.0409 | 1.038 | 0.00028346
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0407 | 1.0409 | 1.038 | 0.00028346
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0408 | 1.0408 | 1.0379 | 0.00028346
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0409 | 1.0408 | 1.0379 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.041 | 1.0407 | 1.0379 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0411 | 1.0406 | 1.038 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0411 | 1.0405 | 1.0381 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.041 | 1.0404 | 1.0382 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.041 | 1.0403 | 1.0383 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0409 | 1.0404 | 1.0385 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0407 | 1.0404 | 1.0386 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0406 | 1.0405 | 1.0386 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0406 | 1.0406 | 1.0386 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0405 | 1.0407 | 1.0385 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0405 | 1.0408 | 1.0383 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0406 | 1.0409 | 1.0382 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0406 | 1.0409 | 1.038 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0408 | 1.0409 | 1.0379 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0409 | 1.0408 | 1.0378 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.041 | 1.0408 | 1.0378 | 0.00031496
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0412 | 1.0407 | 1.0379 | 0.00031496
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0412 | 1.0406 | 1.0379 | 0.00031496
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0412 | 1.0405 | 1.0381 | 0.00031496
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0411 | 1.0404 | 1.0382 | 0.00031496
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.041 | 1.0403 | 1.0383 | 0.00031496
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0409 | 1.0403 | 1.0384 | 0.00031496
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0408 | 1.0404 | 1.0385 | 0.00031496
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0407 | 1.0405 | 1.0385 | 0.00031496
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0406 | 1.0406 | 1.0384 | 0.00031496
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0405 | 1.0408 | 1.0384 | 0.00031496
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0405 | 1.0409 | 1.0382 | 0.00031496
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0406 | 1.041 | 1.0381 | 0.00031496
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0407 | 1.0411 | 1.038 | 0.00031496
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.0408 | 1.0411 | 1.0379 | 0.00031496
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.0409 | 1.041 | 1.0378 | 0.00031496
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.0411 | 1.0409 | 1.0378 | 0.00031496
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.0412 | 1.0408 | 1.0378 | 0.00031496
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.0412 | 1.0406 | 1.0379 | 0.00031496
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.0413 | 1.0405 | 1.0381 | 0.00031496
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0412 | 1.0404 | 1.0382 | 0.00031496
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0411 | 1.0404 | 1.0383 | 0.00031496
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.041 | 1.0404 | 1.0384 | 0.00031496
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0409 | 1.0405 | 1.0385 | 0.00031496
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0408 | 1.0406 | 1.0385 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0407 | 1.0407 | 1.0385 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0407 | 1.0408 | 1.0384 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0407 | 1.0409 | 1.0383 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0407 | 1.041 | 1.0382 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0408 | 1.0411 | 1.0381 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0409 | 1.0411 | 1.038 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0411 | 1.0411 | 1.0379 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0413 | 1.041 | 1.0379 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0414 | 1.0409 | 1.038 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0415 | 1.0407 | 1.0381 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0416 | 1.0406 | 1.0382 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0415 | 1.0406 | 1.0383 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0414 | 1.0405 | 1.0384 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0413 | 1.0405 | 1.0385 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0411 | 1.0406 | 1.0385 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.041 | 1.0407 | 1.0385 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0409 | 1.0408 | 1.0385 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0409 | 1.0409 | 1.0384 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0409 | 1.041 | 1.0383 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.041 | 1.0411 | 1.0382 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0411 | 1.0412 | 1.0381 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0412 | 1.0412 | 1.038 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0413 | 1.0411 | 1.0379 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0414 | 1.041 | 1.0379 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0415 | 1.0409 | 1.0379 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0416 | 1.0407 | 1.038 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0415 | 1.0406 | 1.0381 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0415 | 1.0406 | 1.0382 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0414 | 1.0406 | 1.0383 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0413 | 1.0406 | 1.0383 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0412 | 1.0406 | 1.0384 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0411 | 1.0407 | 1.0384 | 0.00031496
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.041 | 1.0409 | 1.0384 | 0.00031496
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0409 | 1.0411 | 1.0383 | 0.00031496
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.0409 | 1.0413 | 1.0383 | 0.00031496
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.041 | 1.0414 | 1.0382 | 0.00031496
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.0411 | 1.0415 | 1.0381 | 0.00031496
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.049 | 0.006 | 1.0412 | 1.0414 | 1.038 | 0.00031496
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.0413 | 1.0413 | 1.0379 | 0.00031496
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.0413 | 1.0411 | 1.0379 | 0.00031496
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.0412 | 1.041 | 1.0379 | 0.00031496
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.0412 | 1.0409 | 1.038 | 0.00031496
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.0412 | 1.0408 | 1.0381 | 0.00031496
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.0412 | 1.0407 | 1.0382 | 0.00031496
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.0411 | 1.0407 | 1.0383 | 0.00031496
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.041 | 1.0407 | 1.0384 | 0.00031496
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.0409 | 1.0408 | 1.0385 | 0.00031496
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.0408 | 1.0409 | 1.0386 | 0.00031496
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.0406 | 1.041 | 1.0386 | 0.00031496
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.0406 | 1.0411 | 1.0385 | 0.00031496
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.0406 | 1.0412 | 1.0383 | 0.00031496
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.0407 | 1.0413 | 1.0382 | 0.00031496
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.0407 | 1.0413 | 1.0381 | 0.00031496
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.0408 | 1.0412 | 1.038 | 0.00031496
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.0409 | 1.0412 | 1.038 | 0.00031496
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.041 | 1.0411 | 1.038 | 0.00031496
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.0411 | 1.041 | 1.038 | 0.00031496
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.0411 | 1.0409 | 1.0381 | 0.00031496
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.0411 | 1.0408 | 1.0382 | 0.00031496
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.0411 | 1.0407 | 1.0383 | 0.00031496
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.0409 | 1.0407 | 1.0384 | 0.00031496
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.0408 | 1.0407 | 1.0386 | 0.00031496
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.0407 | 1.0408 | 1.0386 | 0.00031496
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.0406 | 1.0409 | 1.0386 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.0405 | 1.041 | 1.0386 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.0405 | 1.0411 | 1.0385 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.0405 | 1.0411 | 1.0383 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.0405 | 1.0412 | 1.0382 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.0406 | 1.0412 | 1.0381 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.0407 | 1.0412 | 1.038 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.0408 | 1.0411 | 1.038 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.0409 | 1.0411 | 1.038 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.0411 | 1.0409 | 1.038 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.0411 | 1.0408 | 1.0381 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.0411 | 1.0407 | 1.0382 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.0411 | 1.0406 | 1.0383 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.041 | 1.0406 | 1.0384 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.0408 | 1.0406 | 1.0384 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.0407 | 1.0407 | 1.0385 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.0406 | 1.0408 | 1.0385 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.0405 | 1.0409 | 1.0385 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.0405 | 1.0411 | 1.0384 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.0405 | 1.0413 | 1.0384 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.0406 | 1.0414 | 1.0383 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.0406 | 1.0414 | 1.0381 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.0408 | 1.0413 | 1.0381 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.0408 | 1.0412 | 1.038 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.0409 | 1.0411 | 1.038 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.041 | 1.0409 | 1.038 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.041 | 1.0408 | 1.0381 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.041 | 1.0407 | 1.0382 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.041 | 1.0406 | 1.0383 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.041 | 1.0406 | 1.0385 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.0409 | 1.0406 | 1.0386 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.0407 | 1.0408 | 1.0388 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.0406 | 1.0409 | 1.0389 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.0406 | 1.041 | 1.0389 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.0405 | 1.0411 | 1.0387 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.0405 | 1.0411 | 1.0386 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.0406 | 1.0411 | 1.0385 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.0406 | 1.0412 | 1.0383 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.0408 | 1.0411 | 1.0383 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.0409 | 1.0411 | 1.0382 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.041 | 1.041 | 1.0382 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.0411 | 1.0409 | 1.0382 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.0412 | 1.0407 | 1.0383 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.0413 | 1.0406 | 1.0385 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.0412 | 1.0405 | 1.0387 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0411 | 1.0404 | 1.0388 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.041 | 1.0405 | 1.0389 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0409 | 1.0405 | 1.039 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0408 | 1.0406 | 1.039 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0407 | 1.0407 | 1.0389 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0406 | 1.0407 | 1.0388 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0406 | 1.0408 | 1.0386 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0407 | 1.0408 | 1.0384 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0408 | 1.0409 | 1.0383 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0409 | 1.0409 | 1.0382 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.041 | 1.0409 | 1.0382 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0412 | 1.0408 | 1.0382 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0413 | 1.0406 | 1.0382 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0414 | 1.0404 | 1.0383 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0413 | 1.0403 | 1.0384 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0412 | 1.0403 | 1.0386 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0411 | 1.0402 | 1.0387 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.041 | 1.0403 | 1.0388 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.041 | 1.0403 | 1.0388 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0409 | 1.0404 | 1.0389 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0408 | 1.0406 | 1.0388 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0407 | 1.0406 | 1.0388 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0407 | 1.0407 | 1.0386 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0408 | 1.0408 | 1.0385 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0409 | 1.0408 | 1.0383 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.041 | 1.0408 | 1.0383 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0411 | 1.0408 | 1.0382 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0412 | 1.0407 | 1.0382 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0412 | 1.0406 | 1.0383 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0413 | 1.0405 | 1.0383 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0413 | 1.0404 | 1.0385 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0414 | 1.0403 | 1.0386 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0414 | 1.0403 | 1.0388 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0413 | 1.0403 | 1.0389 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0412 | 1.0404 | 1.0389 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0411 | 1.0405 | 1.039 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.041 | 1.0406 | 1.039 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.041 | 1.0408 | 1.039 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.041 | 1.0409 | 1.039 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.041 | 1.041 | 1.0389 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0411 | 1.041 | 1.0388 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.051 | 0.006 | 1.0412 | 1.041 | 1.0387 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.051 | 0.006 | 1.0413 | 1.041 | 1.0387 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.051 | 0.006 | 1.0414 | 1.0409 | 1.0387 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.051 | 0.006 | 1.0415 | 1.0408 | 1.0387 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.051 | 0.006 | 1.0416 | 1.0407 | 1.0388 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.051 | 0.006 | 1.0417 | 1.0406 | 1.0389 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.051 | 0.006 | 1.0418 | 1.0406 | 1.0391 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.051 | 0.006 | 1.0418 | 1.0406 | 1.0393 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.051 | 0.006 | 1.0417 | 1.0406 | 1.0395 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.051 | 0.006 | 1.0416 | 1.0407 | 1.0396 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.051 | 0.006 | 1.0414 | 1.0408 | 1.0395 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.051 | 0.006 | 1.0413 | 1.0409 | 1.0395 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.051 | 0.006 | 1.0413 | 1.041 | 1.0394 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.051 | 0.006 | 1.0413 | 1.0411 | 1.0394 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.051 | 0.006 | 1.0414 | 1.0411 | 1.0393 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.051 | 0.006 | 1.0414 | 1.0412 | 1.0392 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.051 | 0.006 | 1.0416 | 1.0413 | 1.0391 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0417 | 1.0412 | 1.039 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0419 | 1.0411 | 1.039 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.042 | 1.041 | 1.039 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.042 | 1.0408 | 1.0391 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.042 | 1.0407 | 1.0392 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.042 | 1.0406 | 1.0394 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0419 | 1.0406 | 1.0395 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0418 | 1.0406 | 1.0396 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0417 | 1.0407 | 1.0397 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0416 | 1.0408 | 1.0397 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0415 | 1.0409 | 1.0396 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0415 | 1.041 | 1.0394 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0415 | 1.041 | 1.0393 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0415 | 1.0411 | 1.0391 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0416 | 1.0411 | 1.039 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0418 | 1.0411 | 1.0389 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0419 | 1.041 | 1.0388 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.042 | 1.041 | 1.0388 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0422 | 1.0408 | 1.0389 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0422 | 1.0406 | 1.039 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.042 | 1.0406 | 1.0391 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.042 | 1.0405 | 1.0391 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0418 | 1.0405 | 1.0391 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0417 | 1.0405 | 1.0391 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0416 | 1.0405 | 1.0391 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0415 | 1.0406 | 1.0392 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0414 | 1.0408 | 1.0391 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0414 | 1.0409 | 1.0391 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0414 | 1.041 | 1.039 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0414 | 1.0411 | 1.0389 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0416 | 1.0411 | 1.0387 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0416 | 1.041 | 1.0386 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0418 | 1.0409 | 1.0386 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0418 | 1.0407 | 1.0386 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0418 | 1.0406 | 1.0386 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0419 | 1.0405 | 1.0386 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0418 | 1.0405 | 1.0387 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0418 | 1.0404 | 1.0388 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0417 | 1.0403 | 1.0389 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0415 | 1.0404 | 1.039 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0414 | 1.0405 | 1.0391 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0412 | 1.0406 | 1.0391 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0411 | 1.0407 | 1.0391 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0411 | 1.0408 | 1.039 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0411 | 1.0409 | 1.0389 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0412 | 1.0409 | 1.0388 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0412 | 1.041 | 1.0386 | 0.00028346
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0414 | 1.0409 | 1.0385 | 0.00028346
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0415 | 1.0408 | 1.0385 | 0.00028346
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0416 | 1.0407 | 1.0385 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0416 | 1.0406 | 1.0385 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0417 | 1.0405 | 1.0386 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0417 | 1.0403 | 1.0387 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0416 | 1.0403 | 1.0388 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0415 | 1.0402 | 1.039 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0414 | 1.0403 | 1.0391 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0412 | 1.0403 | 1.0392 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0411 | 1.0404 | 1.0393 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.041 | 1.0406 | 1.0392 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.041 | 1.0407 | 1.039 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.041 | 1.0408 | 1.0389 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0411 | 1.0408 | 1.0387 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0411 | 1.0409 | 1.0386 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0413 | 1.0409 | 1.0385 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0413 | 1.0409 | 1.0385 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0414 | 1.0408 | 1.0385 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0415 | 1.0406 | 1.0385 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0416 | 1.0405 | 1.0386 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0417 | 1.0404 | 1.0388 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0416 | 1.0403 | 1.0389 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0415 | 1.0403 | 1.0391 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0414 | 1.0403 | 1.0391 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0413 | 1.0404 | 1.0392 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0412 | 1.0405 | 1.0392 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0411 | 1.0406 | 1.0392 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0411 | 1.0407 | 1.039 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0411 | 1.0408 | 1.0389 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0411 | 1.0409 | 1.0387 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0412 | 1.0409 | 1.0386 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0413 | 1.0409 | 1.0386 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0414 | 1.0409 | 1.0385 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0415 | 1.0408 | 1.0385 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0417 | 1.0407 | 1.0386 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0417 | 1.0405 | 1.0386 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0417 | 1.0404 | 1.0388 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0417 | 1.0404 | 1.0389 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0416 | 1.0404 | 1.039 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0414 | 1.0404 | 1.0391 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0413 | 1.0405 | 1.0391 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0412 | 1.0406 | 1.0391 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0411 | 1.0407 | 1.0391 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0411 | 1.0408 | 1.039 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0411 | 1.0409 | 1.0389 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0412 | 1.0409 | 1.0388 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0413 | 1.041 | 1.0387 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0414 | 1.0409 | 1.0386 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0416 | 1.0409 | 1.0386 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0417 | 1.0408 | 1.0386 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0418 | 1.0407 | 1.0386 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0419 | 1.0406 | 1.0387 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0418 | 1.0405 | 1.0388 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0417 | 1.0405 | 1.0388 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0417 | 1.0404 | 1.0389 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0416 | 1.0405 | 1.039 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0414 | 1.0405 | 1.039 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0414 | 1.0406 | 1.039 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0413 | 1.0408 | 1.039 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0413 | 1.0409 | 1.039 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0413 | 1.041 | 1.0389 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0413 | 1.041 | 1.0388 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0414 | 1.0411 | 1.0386 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0416 | 1.0411 | 1.0385 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0417 | 1.041 | 1.0384 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0418 | 1.0409 | 1.0384 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0419 | 1.0408 | 1.0385 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0419 | 1.0406 | 1.0386 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0418 | 1.0406 | 1.0386 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0418 | 1.0405 | 1.0387 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0417 | 1.0405 | 1.0388 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0415 | 1.0405 | 1.0388 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0414 | 1.0406 | 1.0389 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0413 | 1.0407 | 1.0389 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0412 | 1.0408 | 1.0388 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0412 | 1.0409 | 1.0388 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0412 | 1.041 | 1.0387 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0413 | 1.0411 | 1.0386 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0414 | 1.0411 | 1.0384 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0415 | 1.0411 | 1.0384 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0416 | 1.041 | 1.0383 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0417 | 1.0409 | 1.0383 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0417 | 1.0408 | 1.0383 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0418 | 1.0407 | 1.0384 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0417 | 1.0406 | 1.0385 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0417 | 1.0406 | 1.0386 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0415 | 1.0406 | 1.0387 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0414 | 1.0406 | 1.0388 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0413 | 1.0406 | 1.0388 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0412 | 1.0407 | 1.0389 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0411 | 1.0409 | 1.0389 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0411 | 1.0411 | 1.0388 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0411 | 1.0412 | 1.0387 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0412 | 1.0413 | 1.0386 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0413 | 1.0413 | 1.0386 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0414 | 1.0413 | 1.0385 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0415 | 1.0412 | 1.0384 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0416 | 1.0411 | 1.0384 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0417 | 1.041 | 1.0385 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0418 | 1.0409 | 1.0385 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0418 | 1.0408 | 1.0387 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0418 | 1.0408 | 1.0388 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0417 | 1.0407 | 1.039 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0416 | 1.0408 | 1.0391 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0415 | 1.0408 | 1.0392 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0414 | 1.041 | 1.0392 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0413 | 1.0411 | 1.0392 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0413 | 1.0412 | 1.0391 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0413 | 1.0413 | 1.039 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0413 | 1.0414 | 1.0388 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0414 | 1.0414 | 1.0387 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0415 | 1.0414 | 1.0386 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0417 | 1.0414 | 1.0386 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0418 | 1.0412 | 1.0386 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0419 | 1.0411 | 1.0386 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0419 | 1.0409 | 1.0387 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.042 | 1.0408 | 1.0388 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0419 | 1.0407 | 1.039 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0418 | 1.0407 | 1.0392 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0417 | 1.0407 | 1.0394 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0416 | 1.0408 | 1.0394 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0414 | 1.0409 | 1.0394 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0413 | 1.041 | 1.0393 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0413 | 1.0411 | 1.0391 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0413 | 1.0411 | 1.0389 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0414 | 1.0411 | 1.0388 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0414 | 1.0411 | 1.0386 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0416 | 1.0411 | 1.0385 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0417 | 1.0411 | 1.0385 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0418 | 1.041 | 1.0385 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0419 | 1.0408 | 1.0385 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.042 | 1.0406 | 1.0386 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0419 | 1.0405 | 1.0388 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0418 | 1.0404 | 1.0389 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0416 | 1.0404 | 1.0389 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0414 | 1.0404 | 1.039 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0413 | 1.0405 | 1.039 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0412 | 1.0406 | 1.0391 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0411 | 1.0407 | 1.039 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0411 | 1.0408 | 1.0389 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0411 | 1.041 | 1.0388 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0412 | 1.0411 | 1.0387 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0413 | 1.0411 | 1.0386 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0414 | 1.041 | 1.0385 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0415 | 1.0409 | 1.0384 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0416 | 1.0408 | 1.0384 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0417 | 1.0406 | 1.0384 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0417 | 1.0405 | 1.0385 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0417 | 1.0404 | 1.0386 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0416 | 1.0404 | 1.0387 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0415 | 1.0404 | 1.0388 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0414 | 1.0404 | 1.0389 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0413 | 1.0405 | 1.039 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0412 | 1.0406 | 1.039 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0411 | 1.0407 | 1.0389 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0411 | 1.0408 | 1.0389 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0411 | 1.0409 | 1.0388 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0412 | 1.041 | 1.0387 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0412 | 1.0411 | 1.0386 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0414 | 1.0411 | 1.0386 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0414 | 1.041 | 1.0385 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0416 | 1.0408 | 1.0385 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0416 | 1.0407 | 1.0386 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0417 | 1.0406 | 1.0387 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0417 | 1.0405 | 1.0388 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0418 | 1.0405 | 1.039 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0418 | 1.0405 | 1.0391 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0417 | 1.0405 | 1.0393 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0416 | 1.0406 | 1.0393 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0414 | 1.0407 | 1.0393 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0414 | 1.0408 | 1.0393 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0413 | 1.0409 | 1.0391 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0413 | 1.0409 | 1.039 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0414 | 1.041 | 1.0389 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0415 | 1.041 | 1.0388 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0416 | 1.0411 | 1.0388 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0418 | 1.0411 | 1.0387 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0419 | 1.0409 | 1.0387 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.042 | 1.0408 | 1.0388 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.042 | 1.0407 | 1.0389 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.051 | 0.006 | 1.042 | 1.0406 | 1.039 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.051 | 0.006 | 1.042 | 1.0405 | 1.0391 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.051 | 0.006 | 1.0419 | 1.0405 | 1.0392 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.051 | 0.006 | 1.0418 | 1.0405 | 1.0392 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.051 | 0.006 | 1.0417 | 1.0406 | 1.0392 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.051 | 0.006 | 1.0415 | 1.0407 | 1.0393 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.051 | 0.006 | 1.0415 | 1.0409 | 1.0393 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.051 | 0.006 | 1.0414 | 1.0411 | 1.0393 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.051 | 0.006 | 1.0415 | 1.0412 | 1.0392 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.051 | 0.006 | 1.0415 | 1.0412 | 1.0391 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.051 | 0.006 | 1.0417 | 1.0412 | 1.0389 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0418 | 1.0412 | 1.0388 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0419 | 1.0411 | 1.0388 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.042 | 1.041 | 1.0388 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.042 | 1.0409 | 1.0388 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.042 | 1.0408 | 1.0388 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.042 | 1.0407 | 1.0389 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0419 | 1.0406 | 1.039 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0417 | 1.0406 | 1.0391 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0416 | 1.0406 | 1.0392 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0415 | 1.0407 | 1.0392 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0414 | 1.0408 | 1.0393 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0413 | 1.041 | 1.0392 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0413 | 1.0411 | 1.0391 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0413 | 1.0411 | 1.039 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0413 | 1.0412 | 1.0389 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0414 | 1.0412 | 1.0388 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0415 | 1.0412 | 1.0387 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0416 | 1.0411 | 1.0387 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0417 | 1.041 | 1.0387 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0418 | 1.0409 | 1.0387 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0419 | 1.0408 | 1.0388 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0418 | 1.0407 | 1.0389 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0417 | 1.0406 | 1.0391 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0416 | 1.0406 | 1.0392 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0415 | 1.0406 | 1.0393 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0414 | 1.0407 | 1.0394 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0413 | 1.0408 | 1.0394 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0412 | 1.0409 | 1.0393 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0412 | 1.0409 | 1.0391 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0412 | 1.041 | 1.0389 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0413 | 1.0411 | 1.0388 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0413 | 1.0411 | 1.0387 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0414 | 1.0411 | 1.0387 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0416 | 1.0411 | 1.0386 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0417 | 1.041 | 1.0386 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0418 | 1.0409 | 1.0387 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0419 | 1.0407 | 1.0388 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0419 | 1.0406 | 1.039 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0418 | 1.0406 | 1.0391 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0417 | 1.0406 | 1.0392 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0416 | 1.0406 | 1.0392 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0415 | 1.0407 | 1.0392 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0414 | 1.0408 | 1.0392 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0413 | 1.0409 | 1.0391 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0413 | 1.041 | 1.039 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0413 | 1.0411 | 1.0389 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0413 | 1.0412 | 1.0388 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0414 | 1.0412 | 1.0387 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0416 | 1.0412 | 1.0386 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0417 | 1.0411 | 1.0385 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0418 | 1.041 | 1.0385 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0418 | 1.0409 | 1.0386 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0419 | 1.0408 | 1.0386 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0418 | 1.0407 | 1.0387 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0417 | 1.0407 | 1.0388 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0416 | 1.0406 | 1.0388 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0414 | 1.0407 | 1.0388 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0412 | 1.0407 | 1.0389 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0411 | 1.0408 | 1.0389 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0411 | 1.041 | 1.0388 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.041 | 1.0411 | 1.0388 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.041 | 1.0412 | 1.0386 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0411 | 1.0413 | 1.0385 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0412 | 1.0412 | 1.0383 | 0.00028346
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.0413 | 1.0412 | 1.0382 | 0.00028346
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.0415 | 1.0411 | 1.0382 | 0.00028346
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.0416 | 1.041 | 1.0382 | 0.00028346
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.0417 | 1.0409 | 1.0382 | 0.00028346
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.0417 | 1.0408 | 1.0383 | 0.00028346
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.0416 | 1.0407 | 1.0383 | 0.00028346
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.0415 | 1.0406 | 1.0384 | 0.00028346
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.0413 | 1.0406 | 1.0384 | 0.00028346
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.0411 | 1.0406 | 1.0384 | 0.00028346
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.0409 | 1.0407 | 1.0384 | 0.00028346
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.0408 | 1.0408 | 1.0385 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0408 | 1.0409 | 1.0384 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0407 | 1.041 | 1.0384 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0408 | 1.0411 | 1.0382 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0408 | 1.0411 | 1.038 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.041 | 1.0411 | 1.0379 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0411 | 1.0411 | 1.0378 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0412 | 1.041 | 1.0377 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0414 | 1.0409 | 1.0377 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0415 | 1.0407 | 1.0378 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0415 | 1.0406 | 1.0379 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0415 | 1.0405 | 1.038 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0414 | 1.0404 | 1.0382 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0413 | 1.0404 | 1.0383 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0411 | 1.0404 | 1.0384 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.041 | 1.0405 | 1.0385 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0409 | 1.0406 | 1.0384 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0408 | 1.0408 | 1.0383 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0408 | 1.0409 | 1.0382 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0408 | 1.041 | 1.038 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0409 | 1.0411 | 1.0379 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.041 | 1.0411 | 1.0378 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0411 | 1.0411 | 1.0377 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0412 | 1.041 | 1.0377 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0413 | 1.0409 | 1.0377 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0414 | 1.0407 | 1.0377 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0414 | 1.0405 | 1.0378 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0414 | 1.0404 | 1.0379 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0414 | 1.0404 | 1.0381 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0413 | 1.0404 | 1.0382 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0412 | 1.0404 | 1.0383 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.041 | 1.0405 | 1.0383 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0409 | 1.0406 | 1.0382 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0408 | 1.0408 | 1.0382 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0408 | 1.0409 | 1.038 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0408 | 1.0411 | 1.038 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0409 | 1.0412 | 1.0378 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0409 | 1.0412 | 1.0377 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.0411 | 1.0412 | 1.0376 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.0412 | 1.0411 | 1.0376 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.0413 | 1.041 | 1.0376 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.0414 | 1.0409 | 1.0376 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.0414 | 1.0407 | 1.0377 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.0414 | 1.0406 | 1.0378 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.0413 | 1.0406 | 1.0379 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0412 | 1.0405 | 1.038 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.041 | 1.0406 | 1.0381 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0409 | 1.0407 | 1.0381 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0408 | 1.0408 | 1.0381 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0407 | 1.0409 | 1.038 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0407 | 1.041 | 1.0379 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0407 | 1.041 | 1.0378 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0408 | 1.0411 | 1.0377 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0409 | 1.0411 | 1.0376 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.041 | 1.0411 | 1.0375 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0411 | 1.0411 | 1.0374 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0412 | 1.0409 | 1.0374 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0413 | 1.0408 | 1.0375 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0413 | 1.0407 | 1.0376 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0413 | 1.0406 | 1.0377 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0412 | 1.0405 | 1.0378 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0411 | 1.0405 | 1.0379 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.041 | 1.0406 | 1.038 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0409 | 1.0406 | 1.038 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0408 | 1.0407 | 1.0381 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.057 | 0.05 | 0.006 | 1.0407 | 1.0409 | 1.038 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.0407 | 1.041 | 1.038 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.0407 | 1.0411 | 1.0379 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.0408 | 1.0411 | 1.0378 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.0409 | 1.0412 | 1.0377 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.041 | 1.0411 | 1.0376 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.0411 | 1.041 | 1.0375 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.0412 | 1.0408 | 1.0375 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.0412 | 1.0407 | 1.0376 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.0412 | 1.0406 | 1.0377 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.0412 | 1.0406 | 1.0378 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.0411 | 1.0405 | 1.0379 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.041 | 1.0405 | 1.038 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.0409 | 1.0405 | 1.038 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.0408 | 1.0406 | 1.0381 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.0407 | 1.0407 | 1.0382 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.0406 | 1.0408 | 1.0381 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.0406 | 1.0409 | 1.0381 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.0406 | 1.041 | 1.0379 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.0407 | 1.0411 | 1.0378 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.0408 | 1.0411 | 1.0377 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.0409 | 1.0411 | 1.0376 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.041 | 1.041 | 1.0376 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.041 | 1.0409 | 1.0376 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.0411 | 1.0408 | 1.0376 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.0411 | 1.0407 | 1.0377 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.0411 | 1.0406 | 1.0378 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.0411 | 1.0406 | 1.0379 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.041 | 1.0405 | 1.0381 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.0408 | 1.0406 | 1.0382 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.0407 | 1.0407 | 1.0383 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.0406 | 1.0408 | 1.0383 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.0405 | 1.0409 | 1.0383 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.0405 | 1.0411 | 1.0382 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.0405 | 1.0411 | 1.0381 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.0406 | 1.0412 | 1.038 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.0407 | 1.0412 | 1.0378 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.0408 | 1.0411 | 1.0377 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.0408 | 1.0411 | 1.0377 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.0409 | 1.041 | 1.0377 | 0.00028346
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.041 | 1.0408 | 1.0378 | 0.00028346
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.041 | 1.0407 | 1.0379 | 0.00028346
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.041 | 1.0406 | 1.038 | 0.00028346
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.041 | 1.0405 | 1.0381 | 0.00028346
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.0409 | 1.0405 | 1.0383 | 0.00028346
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.0408 | 1.0405 | 1.0384 | 0.00028346
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.0406 | 1.0406 | 1.0385 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.0406 | 1.0407 | 1.0385 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.0405 | 1.0408 | 1.0385 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.0404 | 1.041 | 1.0383 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.0405 | 1.041 | 1.0382 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.0405 | 1.0411 | 1.0381 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.0406 | 1.0411 | 1.0379 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.0408 | 1.0411 | 1.0379 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.0409 | 1.041 | 1.0378 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.041 | 1.0409 | 1.0378 | 0.00028346
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.0411 | 1.0407 | 1.0379 | 0.00028346
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.0412 | 1.0405 | 1.038 | 0.00028346
10/23/2022 | 3:23 | 0.054 | 0.057 | 0.05 | 0.006 | 1.0411 | 1.0404 | 1.0382 | 0.00028346
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0411 | 1.0403 | 1.0383 | 0.00028346
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.041 | 1.0403 | 1.0385 | 0.00028346
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0408 | 1.0403 | 1.0386 | 0.00028346
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0407 | 1.0404 | 1.0386 | 0.00028346
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0406 | 1.0405 | 1.0385 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0405 | 1.0406 | 1.0385 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0405 | 1.0407 | 1.0384 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0405 | 1.0408 | 1.0382 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0406 | 1.0408 | 1.0381 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0407 | 1.0409 | 1.038 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0408 | 1.0409 | 1.038 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.041 | 1.0408 | 1.0379 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0411 | 1.0406 | 1.0379 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0411 | 1.0405 | 1.038 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0412 | 1.0403 | 1.0381 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0412 | 1.0403 | 1.0382 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0411 | 1.0402 | 1.0384 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0411 | 1.0402 | 1.0385 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0409 | 1.0402 | 1.0386 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0408 | 1.0403 | 1.0386 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0407 | 1.0404 | 1.0386 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0406 | 1.0406 | 1.0386 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0406 | 1.0407 | 1.0385 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0406 | 1.0408 | 1.0384 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0407 | 1.0409 | 1.0383 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0408 | 1.0409 | 1.0382 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0409 | 1.0409 | 1.038 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.041 | 1.0409 | 1.038 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0412 | 1.0407 | 1.038 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0413 | 1.0406 | 1.0381 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0413 | 1.0405 | 1.0382 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0413 | 1.0404 | 1.0383 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0412 | 1.0403 | 1.0384 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0411 | 1.0403 | 1.0385 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.041 | 1.0404 | 1.0386 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0409 | 1.0405 | 1.0387 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0409 | 1.0406 | 1.0388 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0408 | 1.0407 | 1.0388 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0408 | 1.0408 | 1.0387 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0408 | 1.0409 | 1.0386 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.0409 | 1.0409 | 1.0384 | 0.00029921
10/23/2022 | 3:23 | 0.054 | 0.056 | 0.05 | 0.006 | 1.041 | 1.0409 | 1.0383 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0411 | 1.041 | 1.0382 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0412 | 1.041 | 1.0382 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0413 | 1.0409 | 1.0382 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0414 | 1.0408 | 1.0383 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0415 | 1.0407 | 1.0383 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0415 | 1.0406 | 1.0385 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0415 | 1.0405 | 1.0386 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0414 | 1.0405 | 1.0388 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0413 | 1.0405 | 1.0389 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0412 | 1.0406 | 1.039 | 0.00028346
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0411 | 1.0407 | 1.039 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0411 | 1.0408 | 1.039 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0411 | 1.041 | 1.0389 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0411 | 1.0411 | 1.0388 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0412 | 1.0411 | 1.0387 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0413 | 1.0412 | 1.0386 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0414 | 1.0412 | 1.0386 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0415 | 1.0411 | 1.0385 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0416 | 1.041 | 1.0385 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0417 | 1.0409 | 1.0386 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0417 | 1.0408 | 1.0387 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0418 | 1.0407 | 1.0388 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0418 | 1.0407 | 1.0389 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0418 | 1.0407 | 1.0391 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0417 | 1.0407 | 1.0392 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0416 | 1.0408 | 1.0393 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.056 | 0.05 | 0.006 | 1.0415 | 1.0409 | 1.0394 | 0.00029921
10/23/2022 | 3:23 | 0.055 | 0.302 | 0.05 | 0.304 | 1.0402 | 1.0321 | 1.0444 | 0.00040945
10/23/2022 | 3:23 | 0.055 | 0.673 | 0.05 | 0.682 | 1.0399 | 1.0125 | 1.0472 | 0.00050394
10/23/2022 | 3:23 | 0.054 | 1.074 | 0.05 | 1.079 | 1.0403 | 0.9885 | 1.0495 | 0.00051969
10/23/2022 | 3:23 | 0.054 | 1.529 | 0.049 | 1.533 | 1.0399 | 0.95937 | 1.0481 | 0.00051969
10/23/2022 | 3:23 | 0.054 | 2.05 | 0.048 | 2.052 | 1.0388 | 0.92646 | 1.0464 | 0.00075591
10/23/2022 | 3:23 | 0.053 | 2.656 | 0.047 | 2.654 | 1.0374 | 0.89282 | 1.0453 | 0.00077165
10/23/2022 | 3:23 | 0.053 | 3.312 | 0.046 | 3.307 | 1.0346 | 0.86082 | 1.0448 | 0.00080315
10/23/2022 | 3:23 | 0.053 | 3.964 | 0.044 | 3.958 | 1.031 | 0.83307 | 1.0449 | 0.00088189
10/23/2022 | 3:23 | 0.053 | 4.608 | 0.043 | 4.602 | 1.0267 | 0.81238 | 1.0456 | 0.00091339
10/23/2022 | 3:23 | 0.053 | 5.248 | 0.043 | 5.242 | 1.0235 | 0.79969 | 1.0458 | 0.00092913
10/23/2022 | 3:23 | 0.054 | 5.866 | 0.043 | 5.858 | 1.0209 | 0.79348 | 1.0452 | 0.00094488
10/23/2022 | 3:23 | 0.054 | 6.446 | 0.044 | 6.438 | 1.019 | 0.79194 | 1.0443 | 0.00094488
10/23/2022 | 3:23 | 0.055 | 6.969 | 0.046 | 6.96 | 1.0166 | 0.7923 | 1.044 | 0.00094488
10/23/2022 | 3:23 | 0.056 | 7.418 | 0.049 | 7.41 | 1.0145 | 0.79146 | 1.0444 | 0.00096063
10/23/2022 | 3:23 | 0.057 | 7.796 | 0.053 | 7.789 | 1.0131 | 0.78643 | 1.045 | 0.00097638
10/23/2022 | 3:23 | 0.058 | 8.104 | 0.057 | 8.098 | 1.0127 | 0.77479 | 1.0442 | 0.00099213
10/23/2022 | 3:23 | 0.058 | 8.338 | 0.061 | 8.333 | 1.0126 | 0.75477 | 1.042 | 0.0010236
10/23/2022 | 3:23 | 0.058 | 8.503 | 0.065 | 8.499 | 1.0126 | 0.72529 | 1.0393 | 0.0010709
10/23/2022 | 3:23 | 0.058 | 8.611 | 0.069 | 8.609 | 1.0125 | 0.68671 | 1.0373 | 0.0011339
10/23/2022 | 3:23 | 0.058 | 8.671 | 0.074 | 8.671 | 1.0122 | 0.63953 | 1.0363 | 0.0011969
10/23/2022 | 3:23 | 0.058 | 8.699 | 0.078 | 8.7 | 1.0113 | 0.58485 | 1.0359 | 0.0012756
10/23/2022 | 3:23 | 0.058 | 8.707 | 0.083 | 8.709 | 1.0098 | 0.52491 | 1.0356 | 0.0013386
10/23/2022 | 3:23 | 0.058 | 8.707 | 0.087 | 8.709 | 1.0076 | 0.46357 | 1.0354 | 0.0014173
10/23/2022 | 3:23 | 0.058 | 8.71 | 0.09 | 8.711 | 1.0045 | 0.40609 | 1.0355 | 0.0014646
10/23/2022 | 3:23 | 0.058 | 8.72 | 0.092 | 8.72 | 1.0009 | 0.35808 | 1.0361 | 0.0015118
10/23/2022 | 3:23 | 0.059 | 8.741 | 0.094 | 8.739 | 0.99688 | 0.32463 | 1.0371 | 0.0015433
10/23/2022 | 3:23 | 0.061 | 8.769 | 0.095 | 8.766 | 0.99326 | 0.30611 | 1.0379 | 0.0015591
10/23/2022 | 3:23 | 0.064 | 8.803 | 0.095 | 8.797 | 0.9903 | 0.30006 | 1.0378 | 0.0015748
10/23/2022 | 3:23 | 0.068 | 8.836 | 0.095 | 8.828 | 0.98831 | 0.29989 | 1.0368 | 0.0015748
10/23/2022 | 3:23 | 0.072 | 8.865 | 0.095 | 8.854 | 0.98728 | 0.29729 | 1.035 | 0.0015748
10/23/2022 | 3:23 | 0.076 | 8.886 | 0.095 | 8.873 | 0.98676 | 0.28369 | 1.0328 | 0.0015748
10/23/2022 | 3:23 | 0.08 | 8.897 | 0.095 | 8.884 | 0.98666 | 0.2502 | 1.03 | 0.0015748
10/23/2022 | 3:23 | 0.083 | 8.895 | 0.095 | 8.881 | 0.98806 | 0.22543 | 1.0219 | 0.0015591
10/23/2022 | 3:23 | 0.086 | 8.875 | 0.096 | 8.86 | 0.98849 | 0.21962 | 1.0161 | 0.0015276
10/23/2022 | 3:23 | 0.089 | 8.84 | 0.096 | 8.826 | 0.98794 | 0.20717 | 1.0114 | 0.0015433
10/23/2022 | 3:23 | 0.092 | 8.792 | 0.097 | 8.778 | 0.98737 | 0.19641 | 1.0113 | 0.0015591
10/23/2022 | 3:23 | 0.094 | 8.73 | 0.098 | 8.718 | 0.9865 | 0.18739 | 1.0122 | 0.0014803
10/23/2022 | 3:23 | 0.096 | 8.647 | 0.099 | 8.636 | 0.9852 | 0.17631 | 1.013 | 0.0014961
10/23/2022 | 3:23 | 0.097 | 8.543 | 0.099 | 8.533 | 0.98477 | 0.16617 | 1.0134 | 0.0014961
10/23/2022 | 3:23 | 0.098 | 8.434 | 0.1 | 8.424 | 0.98498 | 0.15957 | 1.0133 | 0.0014646
10/23/2022 | 3:23 | 0.098 | 8.32 | 0.101 | 8.31 | 0.98584 | 0.15356 | 1.0126 | 0.0014646
10/23/2022 | 3:23 | 0.097 | 8.195 | 0.101 | 8.185 | 0.98557 | 0.14762 | 1.0123 | 0.0014803
10/23/2022 | 3:23 | 0.097 | 8.062 | 0.101 | 8.052 | 0.98482 | 0.14304 | 1.0128 | 0.0014803
10/23/2022 | 3:23 | 0.096 | 7.92 | 0.1 | 7.91 | 0.98394 | 0.13964 | 1.0141 | 0.0014646
10/23/2022 | 3:23 | 0.096 | 7.777 | 0.1 | 7.767 | 0.98452 | 0.13759 | 1.0153 | 0.0014646
10/23/2022 | 3:23 | 0.096 | 7.644 | 0.099 | 7.635 | 0.98603 | 0.13674 | 1.0156 | 0.0014803
10/23/2022 | 3:23 | 0.096 | 7.519 | 0.099 | 7.51 | 0.98764 | 0.13641 | 1.0148 | 0.0014803
10/23/2022 | 3:23 | 0.096 | 7.405 | 0.1 | 7.397 | 0.98868 | 0.13655 | 1.0141 | 0.0014646
10/23/2022 | 3:23 | 0.097 | 7.312 | 0.1 | 7.304 | 0.98934 | 0.13698 | 1.0136 | 0.0014646
10/23/2022 | 3:23 | 0.097 | 7.239 | 0.101 | 7.232 | 0.98961 | 0.13762 | 1.0133 | 0.0014646
10/23/2022 | 3:23 | 0.097 | 7.184 | 0.102 | 7.176 | 0.98946 | 0.13846 | 1.0129 | 0.0014488
10/23/2022 | 3:23 | 0.098 | 7.145 | 0.104 | 7.138 | 0.98882 | 0.1394 | 1.0126 | 0.0014488
10/23/2022 | 3:23 | 0.098 | 7.122 | 0.105 | 7.114 | 0.98778 | 0.14052 | 1.0124 | 0.0014488
10/23/2022 | 3:23 | 0.098 | 7.113 | 0.106 | 7.104 | 0.98658 | 0.14167 | 1.0123 | 0.0014331
10/23/2022 | 3:23 | 0.098 | 7.116 | 0.107 | 7.106 | 0.98569 | 0.14293 | 1.0123 | 0.0014173
10/23/2022 | 3:23 | 0.098 | 7.13 | 0.108 | 7.118 | 0.98569 | 0.14438 | 1.0122 | 0.0014016
10/23/2022 | 3:23 | 0.099 | 7.153 | 0.11 | 7.139 | 0.98657 | 0.14554 | 1.012 | 0.0014016
10/23/2022 | 3:23 | 0.099 | 7.182 | 0.111 | 7.166 | 0.9883 | 0.14639 | 1.0114 | 0.0014016
10/23/2022 | 3:23 | 0.1 | 7.217 | 0.112 | 7.197 | 0.98981 | 0.14704 | 1.011 | 0.0014016
10/23/2022 | 3:23 | 0.101 | 7.254 | 0.112 | 7.232 | 0.99079 | 0.14737 | 1.011 | 0.0014016
10/23/2022 | 3:23 | 0.103 | 7.289 | 0.112 | 7.264 | 0.99117 | 0.1474 | 1.0117 | 0.0014016
10/23/2022 | 3:23 | 0.104 | 7.321 | 0.112 | 7.294 | 0.99128 | 0.1472 | 1.0128 | 0.0014016
10/23/2022 | 3:23 | 0.106 | 7.347 | 0.112 | 7.318 | 0.99154 | 0.1468 | 1.0139 | 0.0014016
10/23/2022 | 3:23 | 0.109 | 7.367 | 0.112 | 7.337 | 0.99184 | 0.14627 | 1.0151 | 0.0014016
10/23/2022 | 3:23 | 0.111 | 7.379 | 0.112 | 7.348 | 0.99219 | 0.14556 | 1.0159 | 0.0014016
10/23/2022 | 3:23 | 0.113 | 7.383 | 0.113 | 7.351 | 0.99235 | 0.14447 | 1.0166 | 0.0014016
10/23/2022 | 3:23 | 0.116 | 7.378 | 0.113 | 7.345 | 0.9923 | 0.1429 | 1.0172 | 0.0014016
10/23/2022 | 3:23 | 0.118 | 7.362 | 0.114 | 7.329 | 0.99208 | 0.14033 | 1.0177 | 0.0014016
10/23/2022 | 3:23 | 0.12 | 7.336 | 0.115 | 7.303 | 0.99175 | 0.13822 | 1.018 | 0.0014173
10/23/2022 | 3:23 | 0.122 | 7.3 | 0.116 | 7.268 | 0.9914 | 0.13682 | 1.0181 | 0.0014173
10/23/2022 | 3:23 | 0.123 | 7.255 | 0.118 | 7.223 | 0.99123 | 0.13556 | 1.018 | 0.0014173
10/23/2022 | 3:23 | 0.124 | 7.202 | 0.118 | 7.171 | 0.99145 | 0.13441 | 1.0181 | 0.0014173
10/23/2022 | 3:23 | 0.124 | 7.143 | 0.119 | 7.112 | 0.99216 | 0.13348 | 1.0182 | 0.0014173
10/23/2022 | 3:23 | 0.124 | 7.078 | 0.119 | 7.048 | 0.99353 | 0.13254 | 1.0185 | 0.0014173
10/23/2022 | 3:23 | 0.124 | 7.012 | 0.12 | 6.981 | 0.99537 | 0.13172 | 1.0187 | 0.0014173
10/23/2022 | 3:23 | 0.124 | 6.947 | 0.12 | 6.916 | 0.99713 | 0.13121 | 1.0186 | 0.0014173
10/23/2022 | 3:23 | 0.124 | 6.886 | 0.119 | 6.853 | 0.99839 | 0.13098 | 1.0179 | 0.0014173
10/23/2022 | 3:23 | 0.124 | 6.829 | 0.119 | 6.795 | 0.99887 | 0.13091 | 1.017 | 0.0014016
10/23/2022 | 3:23 | 0.124 | 6.777 | 0.118 | 6.741 | 0.9988 | 0.13102 | 1.0161 | 0.0014016
10/23/2022 | 3:23 | 0.125 | 6.728 | 0.117 | 6.691 | 0.99863 | 0.13137 | 1.0158 | 0.0014173
10/23/2022 | 3:23 | 0.125 | 6.684 | 0.116 | 6.646 | 0.9986 | 0.13189 | 1.0164 | 0.0014173
10/23/2022 | 3:23 | 0.126 | 6.646 | 0.115 | 6.607 | 0.99866 | 0.1328 | 1.0175 | 0.0014173
10/23/2022 | 3:23 | 0.126 | 6.617 | 0.115 | 6.578 | 0.99863 | 0.13375 | 1.0189 | 0.0014173
10/23/2022 | 3:23 | 0.127 | 6.597 | 0.115 | 6.558 | 0.99844 | 0.13471 | 1.0201 | 0.0014173
10/23/2022 | 3:23 | 0.127 | 6.589 | 0.116 | 6.548 | 0.99806 | 0.13572 | 1.0208 | 0.0014016
10/23/2022 | 3:23 | 0.128 | 6.59 | 0.116 | 6.548 | 0.9975 | 0.1368 | 1.0211 | 0.0014016
10/23/2022 | 3:23 | 0.128 | 6.599 | 0.116 | 6.557 | 0.99691 | 0.13767 | 1.0212 | 0.0014016
10/23/2022 | 3:23 | 0.128 | 6.615 | 0.117 | 6.572 | 0.99639 | 0.13828 | 1.0212 | 0.0014016
10/23/2022 | 3:23 | 0.127 | 6.636 | 0.117 | 6.592 | 0.99631 | 0.13896 | 1.0213 | 0.0014016
10/23/2022 | 3:23 | 0.127 | 6.662 | 0.117 | 6.617 | 0.99655 | 0.13961 | 1.0215 | 0.0014016
10/23/2022 | 3:23 | 0.126 | 6.691 | 0.117 | 6.645 | 0.99709 | 0.14006 | 1.0216 | 0.0014016
10/23/2022 | 3:23 | 0.126 | 6.722 | 0.118 | 6.675 | 0.99764 | 0.14039 | 1.0215 | 0.0014016
10/23/2022 | 3:23 | 0.125 | 6.754 | 0.118 | 6.705 | 0.99814 | 0.14054 | 1.021 | 0.0014016
10/23/2022 | 3:23 | 0.125 | 6.784 | 0.118 | 6.734 | 0.9985 | 0.14052 | 1.0204 | 0.0014016
10/23/2022 | 3:23 | 0.125 | 6.81 | 0.118 | 6.759 | 0.99876 | 0.14031 | 1.02 | 0.0014016
10/23/2022 | 3:23 | 0.125 | 6.832 | 0.118 | 6.78 | 0.99891 | 0.13998 | 1.0199 | 0.0014016
10/23/2022 | 3:23 | 0.125 | 6.848 | 0.117 | 6.794 | 0.99896 | 0.13953 | 1.0203 | 0.0014173
10/23/2022 | 3:23 | 0.124 | 6.856 | 0.117 | 6.801 | 0.99896 | 0.13888 | 1.0206 | 0.0014016
10/23/2022 | 3:23 | 0.123 | 6.857 | 0.116 | 6.802 | 0.99896 | 0.13813 | 1.0209 | 0.0014173
10/23/2022 | 3:23 | 0.12 | 6.852 | 0.114 | 6.796 | 0.99902 | 0.13795 | 1.0212 | 0.0014173
10/23/2022 | 3:23 | 0.117 | 6.843 | 0.112 | 6.787 | 0.99896 | 0.13762 | 1.0213 | 0.0014173
10/23/2022 | 3:23 | 0.114 | 6.833 | 0.11 | 6.775 | 0.99913 | 0.13706 | 1.0214 | 0.0014173
10/23/2022 | 3:23 | 0.112 | 6.823 | 0.109 | 6.761 | 0.99888 | 0.13639 | 1.0213 | 0.0014173
10/23/2022 | 3:23 | 0.112 | 6.815 | 0.108 | 6.747 | 0.99872 | 0.13575 | 1.0214 | 0.0014173
10/23/2022 | 3:23 | 0.116 | 6.809 | 0.107 | 6.732 | 0.99836 | 0.1352 | 1.0214 | 0.0014173
10/23/2022 | 3:23 | 0.121 | 6.805 | 0.107 | 6.719 | 0.99822 | 0.13477 | 1.0216 | 0.0014173
10/23/2022 | 3:23 | 0.127 | 6.804 | 0.108 | 6.707 | 0.99787 | 0.13444 | 1.0217 | 0.0014173
10/23/2022 | 3:23 | 0.131 | 6.802 | 0.109 | 6.695 | 0.99792 | 0.13416 | 1.0217 | 0.0014173
10/23/2022 | 3:23 | 0.135 | 6.798 | 0.109 | 6.68 | 0.99775 | 0.134 | 1.0218 | 0.0014173
10/23/2022 | 3:23 | 0.137 | 6.793 | 0.11 | 6.665 | 0.99789 | 0.13403 | 1.0218 | 0.0014173
10/23/2022 | 3:23 | 0.139 | 6.785 | 0.11 | 6.648 | 0.99789 | 0.13425 | 1.0219 | 0.0014173
10/23/2022 | 3:23 | 0.14 | 6.775 | 0.109 | 6.63 | 0.99798 | 0.13465 | 1.0218 | 0.0014173
10/23/2022 | 3:23 | 0.14 | 6.764 | 0.108 | 6.612 | 0.998 | 0.13526 | 1.0217 | 0.0014173
10/23/2022 | 3:23 | 0.139 | 6.752 | 0.105 | 6.595 | 0.998 | 0.13573 | 1.0213 | 0.0014173
10/23/2022 | 3:23 | 0.138 | 6.74 | 0.102 | 6.58 | 0.998 | 0.13644 | 1.021 | 0.0014331
10/23/2022 | 3:23 | 0.137 | 6.732 | 0.097 | 6.57 | 0.99808 | 0.13737 | 1.0206 | 0.0014488
10/23/2022 | 3:23 | 0.136 | 6.73 | 0.091 | 6.567 | 0.9983 | 0.13841 | 1.0205 | 0.0014488
10/23/2022 | 3:23 | 0.136 | 6.736 | 0.085 | 6.573 | 0.99863 | 0.13951 | 1.0205 | 0.0014488
10/23/2022 | 3:23 | 0.136 | 6.751 | 0.078 | 6.59 | 0.99902 | 0.14049 | 1.0205 | 0.0014646
10/23/2022 | 3:23 | 0.137 | 6.776 | 0.071 | 6.617 | 0.9995 | 0.14124 | 1.0205 | 0.0014646
10/23/2022 | 3:23 | 0.137 | 6.809 | 0.065 | 6.653 | 0.99981 | 0.14186 | 1.0206 | 0.0014646
10/23/2022 | 3:23 | 0.138 | 6.85 | 0.061 | 6.697 | 1 | 0.14228 | 1.0208 | 0.0014646
10/23/2022 | 3:23 | 0.138 | 6.895 | 0.057 | 6.746 | 1.0001 | 0.1425 | 1.0214 | 0.0014646
10/23/2022 | 3:23 | 0.138 | 6.941 | 0.055 | 6.796 | 1.0001 | 0.1426 | 1.0226 | 0.0014646
10/23/2022 | 3:23 | 0.136 | 6.984 | 0.054 | 6.844 | 0.99997 | 0.14261 | 1.025 | 0.0014646
10/23/2022 | 3:23 | 0.134 | 7.022 | 0.054 | 6.887 | 0.99981 | 0.14261 | 1.028 | 0.0014646
10/23/2022 | 3:23 | 0.13 | 7.054 | 0.054 | 6.922 | 0.99969 | 0.14263 | 1.0304 | 0.0014646
10/23/2022 | 3:23 | 0.125 | 7.079 | 0.053 | 6.95 | 0.9997 | 0.14265 | 1.031 | 0.0014646
10/23/2022 | 3:23 | 0.12 | 7.096 | 0.053 | 6.97 | 0.99973 | 0.14274 | 1.0298 | 0.0014646
10/23/2022 | 3:23 | 0.115 | 7.105 | 0.053 | 6.982 | 0.9997 | 0.14294 | 1.0282 | 0.0014646
10/23/2022 | 3:23 | 0.111 | 7.108 | 0.053 | 6.985 | 0.9997 | 0.14331 | 1.027 | 0.0014646
10/23/2022 | 3:23 | 0.11 | 7.105 | 0.053 | 6.982 | 0.99898 | 0.14137 | 1.025 | 0.0014646
10/23/2022 | 3:23 | 0.109 | 7.085 | 0.052 | 6.961 | 0.99627 | 0.1382 | 1.0233 | 0.0014331
10/23/2022 | 3:23 | 0.11 | 7.034 | 0.051 | 6.908 | 0.98972 | 0.13378 | 1.0216 | 0.0014016
10/23/2022 | 3:23 | 0.109 | 6.939 | 0.05 | 6.814 | 0.98162 | 0.12937 | 1.0212 | 0.0013858
10/23/2022 | 3:23 | 0.108 | 6.792 | 0.049 | 6.67 | 0.9751 | 0.12539 | 1.0211 | 0.0013543
10/23/2022 | 3:23 | 0.103 | 6.591 | 0.048 | 6.474 | 0.97476 | 0.12216 | 1.0205 | 0.0013386
10/23/2022 | 3:23 | 0.097 | 6.337 | 0.046 | 6.227 | 0.97939 | 0.11981 | 1.0191 | 0.0013228
10/23/2022 | 3:23 | 0.09 | 6.035 | 0.045 | 5.933 | 0.98565 | 0.11847 | 1.0185 | 0.0013071
10/23/2022 | 3:23 | 0.083 | 5.7 | 0.043 | 5.606 | 0.99072 | 0.11794 | 1.0207 | 0.0013071
10/23/2022 | 3:23 | 0.076 | 5.349 | 0.041 | 5.264 | 0.9954 | 0.11787 | 1.0269 | 0.0013071
10/23/2022 | 3:23 | 0.07 | 5.005 | 0.039 | 4.929 | 1.0004 | 0.11786 | 1.0375 | 0.0013071
10/23/2022 | 3:23 | 0.063 | 4.692 | 0.038 | 4.624 | 1.006 | 0.11751 | 1.0516 | 0.0013071
10/23/2022 | 3:23 | 0.059 | 4.428 | 0.036 | 4.367 | 1.0114 | 0.11649 | 1.068 | 0.0012913
10/23/2022 | 3:23 | 0.055 | 4.229 | 0.035 | 4.173 | 1.0159 | 0.1146 | 1.0846 | 0.0012598
10/23/2022 | 3:23 | 0.054 | 4.103 | 0.033 | 4.05 | 1.0193 | 0.11169 | 1.0996 | 0.0012283
10/23/2022 | 3:23 | 0.053 | 4.041 | 0.032 | 3.991 | 1.0209 | 0.10762 | 1.1119 | 0.0011654
10/23/2022 | 3:23 | 0.053 | 4.025 | 0.03 | 3.975 | 1.0195 | 0.1023 | 1.1213 | 0.0010866
10/23/2022 | 3:23 | 0.053 | 4.025 | 0.029 | 3.975 | 1.0143 | 0.095811 | 1.1273 | 0.0010236
10/23/2022 | 3:23 | 0.053 | 4.014 | 0.028 | 3.964 | 1.0051 | 0.08822 | 1.1294 | 0.00092913
10/23/2022 | 3:23 | 0.052 | 3.967 | 0.027 | 3.917 | 0.99224 | 0.080142 | 1.1292 | 0.00085039
10/23/2022 | 3:23 | 0.049 | 3.867 | 0.026 | 3.819 | 0.97616 | 0.072016 | 1.1306 | 0.00075591
10/23/2022 | 3:23 | 0.047 | 3.703 | 0.025 | 3.658 | 0.95754 | 0.064488 | 1.1377 | 0.00067717
10/23/2022 | 3:23 | 0.043 | 3.47 | 0.025 | 3.429 | 0.93748 | 0.058346 | 1.1494 | 0.00059843
10/23/2022 | 3:23 | 0.038 | 3.167 | 0.025 | 3.132 | 0.91849 | 0.054236 | 1.1611 | 0.00053543
10/23/2022 | 3:23 | 0.033 | 2.804 | 0.025 | 2.775 | 0.90334 | 0.052189 | 1.1684 | 0.00048819
10/23/2022 | 3:23 | 0.028 | 2.394 | 0.025 | 2.371 | 0.89408 | 0.051622 | 1.1698 | 0.00048819
10/23/2022 | 3:23 | 0.024 | 1.953 | 0.025 | 1.936 | 0.8914 | 0.051654 | 1.1664 | 0.00048819
10/23/2022 | 3:23 | 0.021 | 1.501 | 0.026 | 1.491 | 0.89443 | 0.051339 | 1.1611 | 0.00048819
10/23/2022 | 3:23 | 0.02 | 1.059 | 0.026 | 1.056 | 0.90169 | 0.049874 | 1.1565 | 0.00047244
10/23/2022 | 3:23 | 0.02 | 0.657 | 0.026 | 0.659 | 0.91161 | 0.04652 | 1.1537 | 0.00045669
10/23/2022 | 3:23 | 0.022 | 0.358 | 0.026 | 0.364 | 0.92217 | 0.040394 | 1.1523 | 0.00040945
10/23/2022 | 3:23 | 0.024 | 0.274 | 0.026 | 0.281 | 0.93107 | 0.02885 | 1.1516 | 0.00029921
10/23/2022 | 3:23 | 0.026 | 0.273 | 0.026 | 0.281 | 0.93669 | 0.021402 | 1.1523 | 0.00025197
10/23/2022 | 3:23 | 0.028 | 0.272 | 0.026 | 0.281 | 0.93857 | 0.014142 | 1.1537 | 0.00025197
10/23/2022 | 3:23 | 0.03 | 0.271 | 0.026 | 0.28 | 0.93666 | 0.012346 | 1.1555 | 0.00025197
10/23/2022 | 3:23 | 0.032 | 0.27 | 0.025 | 0.281 | 0.92874 | 0.011685 | 1.1565 | 0.00025197
10/23/2022 | 3:23 | 0.035 | 0.269 | 0.025 | 0.282 | 0.91129 | 0.011402 | 1.1565 | 0.00025197
10/23/2022 | 3:23 | 0.037 | 0.268 | 0.025 | 0.282 | 0.88118 | 0.011055 | 1.1559 | 0.00025197
10/23/2022 | 3:23 | 0.039 | 0.267 | 0.025 | 0.282 | 0.8409 | 0.010787 | 1.1541 | 0.00025197
10/23/2022 | 3:23 | 0.041 | 0.266 | 0.024 | 0.282 | 0.79757 | 0.010457 | 1.1498 | 0.00025197
10/23/2022 | 3:23 | 0.042 | 0.265 | 0.024 | 0.282 | 0.75778 | 0.010268 | 1.1413 | 0.00026772
10/23/2022 | 3:23 | 0.042 | 0.264 | 0.023 | 0.281 | 0.72569 | 0.010315 | 1.1269 | 0.00026772
10/23/2022 | 3:23 | 0.043 | 0.263 | 0.023 | 0.28 | 0.70246 | 0.010693 | 1.1066 | 0.00026772
10/23/2022 | 3:23 | 0.043 | 0.262 | 0.022 | 0.279 | 0.68877 | 0.011102 | 1.0812 | 0.00026772
10/23/2022 | 3:23 | 0.043 | 0.261 | 0.021 | 0.278 | 0.68409 | 0.01148 | 1.0525 | 0.00026772
10/23/2022 | 3:23 | 0.043 | 0.26 | 0.02 | 0.276 | 0.6865 | 0.01189 | 1.0233 | 0.00026772
10/23/2022 | 3:23 | 0.043 | 0.259 | 0.02 | 0.274 | 0.69269 | 0.012315 | 0.99654 | 0.00026772
10/23/2022 | 3:23 | 0.043 | 0.257 | 0.019 | 0.272 | 0.69984 | 0.012772 | 0.97444 | 0.00026772
10/23/2022 | 3:23 | 0.043 | 0.256 | 0.018 | 0.27 | 0.70602 | 0.013244 | 0.95798 | 0.00026772
10/23/2022 | 3:23 | 0.043 | 0.255 | 0.017 | 0.268 | 0.70995 | 0.013701 | 0.94794 | 0.00025197
10/23/2022 | 3:23 | 0.044 | 0.254 | 0.017 | 0.267 | 0.71027 | 0.014063 | 0.94455 | 0.00025197
10/23/2022 | 3:23 | 0.044 | 0.252 | 0.017 | 0.265 | 0.70565 | 0.014236 | 0.94517 | 0.00025197
10/23/2022 | 3:23 | 0.044 | 0.251 | 0.018 | 0.264 | 0.69554 | 0.01422 | 0.94337 | 0.00025197
10/23/2022 | 3:23 | 0.045 | 0.25 | 0.018 | 0.263 | 0.68069 | 0.014142 | 0.93301 | 0.00025197
10/23/2022 | 3:23 | 0.045 | 0.248 | 0.018 | 0.262 | 0.66255 | 0.014031 | 0.91381 | 0.00025197
10/23/2022 | 3:23 | 0.045 | 0.247 | 0.018 | 0.261 | 0.64222 | 0.013906 | 0.89044 | 0.00025197
10/23/2022 | 3:23 | 0.046 | 0.246 | 0.018 | 0.259 | 0.62054 | 0.01378 | 0.86831 | 0.00025197
10/23/2022 | 3:23 | 0.046 | 0.245 | 0.018 | 0.258 | 0.5986 | 0.013669 | 0.84942 | 0.00026772
10/23/2022 | 3:23 | 0.045 | 0.244 | 0.017 | 0.257 | 0.57732 | 0.013575 | 0.83345 | 0.00026772
10/23/2022 | 3:23 | 0.045 | 0.244 | 0.017 | 0.256 | 0.55767 | 0.013496 | 0.8188 | 0.00028346
10/23/2022 | 3:23 | 0.045 | 0.244 | 0.016 | 0.256 | 0.54063 | 0.013417 | 0.80425 | 0.00028346
10/23/2022 | 3:23 | 0.045 | 0.244 | 0.016 | 0.256 | 0.52698 | 0.013354 | 0.78918 | 0.00028346
10/23/2022 | 3:23 | 0.044 | 0.245 | 0.016 | 0.255 | 0.51795 | 0.013354 | 0.77402 | 0.00028346
10/23/2022 | 3:23 | 0.043 | 0.245 | 0.015 | 0.255 | 0.51477 | 0.013339 | 0.76005 | 0.00028346
10/23/2022 | 3:23 | 0.042 | 0.246 | 0.015 | 0.254 | 0.51797 | 0.013291 | 0.7491 | 0.00028346
10/23/2022 | 3:23 | 0.04 | 0.247 | 0.015 | 0.254 | 0.52631 | 0.013165 | 0.74247 | 0.00028346
10/23/2022 | 3:23 | 0.038 | 0.248 | 0.015 | 0.253 | 0.53707 | 0.013024 | 0.74022 | 0.00028346
10/23/2022 | 3:23 | 0.035 | 0.249 | 0.015 | 0.252 | 0.5472 | 0.012882 | 0.74161 | 0.00029921
10/23/2022 | 3:23 | 0.033 | 0.249 | 0.015 | 0.251 | 0.5546 | 0.012772 | 0.74504 | 0.00029921
10/23/2022 | 3:23 | 0.03 | 0.25 | 0.015 | 0.25 | 0.55841 | 0.012677 | 0.74843 | 0.00029921
10/23/2022 | 3:23 | 0.027 | 0.25 | 0.015 | 0.249 | 0.55843 | 0.01263 | 0.7491 | 0.00029921
10/23/2022 | 3:23 | 0.025 | 0.25 | 0.015 | 0.248 | 0.55449 | 0.01263 | 0.74438 | 0.00029921
10/23/2022 | 3:23 | 0.023 | 0.25 | 0.015 | 0.246 | 0.54639 | 0.012551 | 0.73239 | 0.00029921
10/23/2022 | 3:23 | 0.021 | 0.249 | 0.015 | 0.245 | 0.53394 | 0.012283 | 0.71332 | 0.00029921
10/23/2022 | 3:23 | 0.02 | 0.248 | 0.015 | 0.243 | 0.51743 | 0.011701 | 0.68891 | 0.00031496
10/23/2022 | 3:23 | 0.02 | 0.247 | 0.015 | 0.241 | 0.49803 | 0.011039 | 0.66211 | 0.00031496
10/23/2022 | 3:23 | 0.02 | 0.245 | 0.015 | 0.239 | 0.47836 | 0.010362 | 0.63602 | 0.00031496
10/23/2022 | 3:23 | 0.02 | 0.243 | 0.014 | 0.237 | 0.46233 | 0.0096535 | 0.61307 | 0.00031496
10/23/2022 | 3:23 | 0.02 | 0.24 | 0.014 | 0.236 | 0.45335 | 0.0089134 | 0.59496 | 0.00031496
10/23/2022 | 3:23 | 0.02 | 0.238 | 0.014 | 0.234 | 0.45236 | 0.008126 | 0.58285 | 0.00031496
10/23/2022 | 3:23 | 0.02 | 0.235 | 0.014 | 0.233 | 0.458 | 0.0072598 | 0.57732 | 0.00031496
10/23/2022 | 3:23 | 0.02 | 0.232 | 0.014 | 0.231 | 0.46787 | 0.0063465 | 0.57831 | 0.00031496
10/23/2022 | 3:23 | 0.019 | 0.229 | 0.014 | 0.23 | 0.48 | 0.0054646 | 0.58465 | 0.00031496
10/23/2022 | 3:23 | 0.018 | 0.227 | 0.014 | 0.229 | 0.49288 | 0.0046457 | 0.59428 | 0.00031496
10/23/2022 | 3:23 | 0.017 | 0.224 | 0.014 | 0.229 | 0.5055 | 0.0039055 | 0.60469 | 0.00031496
10/23/2022 | 3:23 | 0.016 | 0.222 | 0.014 | 0.228 | 0.51715 | 0.0032283 | 0.61346 | 0.00031496
10/23/2022 | 3:23 | 0.015 | 0.22 | 0.014 | 0.228 | 0.52704 | 0.0026772 | 0.61833 | 0.00031496
10/23/2022 | 3:23 | 0.014 | 0.219 | 0.014 | 0.228 | 0.53433 | 0.0023307 | 0.61778 | 0.00029921
10/23/2022 | 3:23 | 0.014 | 0.218 | 0.014 | 0.228 | 0.53838 | 0.0021102 | 0.61098 | 0.00029921
10/23/2022 | 3:23 | 0.014 | 0.217 | 0.013 | 0.229 | 0.53904 | 0.0019685 | 0.59797 | 0.00029921
10/23/2022 | 3:23 | 0.014 | 0.216 | 0.013 | 0.228 | 0.53683 | 0.001874 | 0.57953 | 0.00028346
10/23/2022 | 3:23 | 0.014 | 0.216 | 0.013 | 0.227 | 0.53287 | 0.001811 | 0.55693 | 0.00028346
10/23/2022 | 3:23 | 0.014 | 0.215 | 0.013 | 0.227 | 0.52753 | 0.0017953 | 0.53225 | 0.00028346
10/23/2022 | 3:23 | 0.014 | 0.214 | 0.013 | 0.226 | 0.52083 | 0.001811 | 0.50833 | 0.00028346
10/23/2022 | 3:23 | 0.013 | 0.213 | 0.013 | 0.225 | 0.51213 | 0.001811 | 0.48798 | 0.00028346
10/23/2022 | 3:23 | 0.013 | 0.213 | 0.013 | 0.225 | 0.50057 | 0.001811 | 0.47285 | 0.00028346
10/23/2022 | 3:23 | 0.013 | 0.212 | 0.013 | 0.224 | 0.48591 | 0.0017953 | 0.46254 | 0.00028346
10/23/2022 | 3:23 | 0.013 | 0.211 | 0.013 | 0.223 | 0.46923 | 0.001811 | 0.4555 | 0.00028346
10/23/2022 | 3:23 | 0.013 | 0.211 | 0.013 | 0.223 | 0.45294 | 0.0018268 | 0.45008 | 0.00028346
10/23/2022 | 3:23 | 0.013 | 0.21 | 0.013 | 0.222 | 0.43961 | 0.0018583 | 0.44494 | 0.00026772
10/23/2022 | 3:23 | 0.013 | 0.209 | 0.013 | 0.221 | 0.4306 | 0.001874 | 0.43931 | 0.00026772
10/23/2022 | 3:23 | 0.013 | 0.208 | 0.013 | 0.221 | 0.42559 | 0.0018898 | 0.43283 | 0.00026772
10/23/2022 | 3:23 | 0.013 | 0.208 | 0.013 | 0.22 | 0.42331 | 0.001937 | 0.42608 | 0.00026772
10/23/2022 | 3:23 | 0.013 | 0.207 | 0.013 | 0.219 | 0.42244 | 0.0019685 | 0.42035 | 0.00026772
10/23/2022 | 3:23 | 0.012 | 0.206 | 0.012 | 0.218 | 0.42211 | 0.0019843 | 0.41688 | 0.00026772
10/23/2022 | 3:23 | 0.012 | 0.206 | 0.012 | 0.218 | 0.42198 | 0.0019213 | 0.41583 | 0.00026772
10/23/2022 | 3:23 | 0.012 | 0.205 | 0.012 | 0.217 | 0.42198 | 0.001811 | 0.41589 | 0.00025197
10/23/2022 | 3:23 | 0.012 | 0.204 | 0.012 | 0.216 | 0.4218 | 0.0017165 | 0.41494 | 0.00025197
10/23/2022 | 3:23 | 0.012 | 0.204 | 0.012 | 0.216 | 0.4202 | 0.0016535 | 0.41094 | 0.00025197
10/23/2022 | 3:23 | 0.012 | 0.203 | 0.012 | 0.215 | 0.41499 | 0.0016693 | 0.40282 | 0.00025197
10/23/2022 | 3:23 | 0.012 | 0.202 | 0.012 | 0.215 | 0.40454 | 0.0017008 | 0.39049 | 0.00025197
10/23/2022 | 3:23 | 0.012 | 0.202 | 0.012 | 0.214 | 0.38902 | 0.0017795 | 0.37461 | 0.00025197
10/23/2022 | 3:23 | 0.012 | 0.201 | 0.012 | 0.213 | 0.37008 | 0.0018268 | 0.35594 | 0.00023622
10/23/2022 | 3:23 | 0.011 | 0.2 | 0.012 | 0.213 | 0.34951 | 0.0018583 | 0.33521 | 0.00023622
10/23/2022 | 3:23 | 0.011 | 0.2 | 0.012 | 0.212 | 0.32843 | 0.001874 | 0.31323 | 0.00023622
10/23/2022 | 3:23 | 0.011 | 0.199 | 0.011 | 0.211 | 0.30728 | 0.0018583 | 0.29074 | 0.00023622
10/23/2022 | 3:23 | 0.011 | 0.198 | 0.011 | 0.211 | 0.28597 | 0.0018425 | 0.26824 | 0.00023622
10/23/2022 | 3:23 | 0.011 | 0.198 | 0.011 | 0.21 | 0.26424 | 0.001811 | 0.24591 | 0.00023622
10/23/2022 | 3:23 | 0.011 | 0.197 | 0.011 | 0.209 | 0.24187 | 0.0017795 | 0.22424 | 0.00023622
10/23/2022 | 3:23 | 0.011 | 0.197 | 0.011 | 0.209 | 0.21876 | 0.001748 | 0.20354 | 0.00023622
10/23/2022 | 3:23 | 0.011 | 0.196 | 0.011 | 0.208 | 0.19528 | 0.0017323 | 0.18447 | 0.00023622
10/23/2022 | 3:23 | 0.011 | 0.195 | 0.011 | 0.208 | 0.17173 | 0.0017008 | 0.16699 | 0.00023622
10/23/2022 | 3:23 | 0.011 | 0.195 | 0.011 | 0.207 | 0.14887 | 0.0016535 | 0.1506 | 0.00023622
10/23/2022 | 3:23 | 0.011 | 0.194 | 0.011 | 0.206 | 0.12756 | 0.001622 | 0.13487 | 0.00023622
10/23/2022 | 3:23 | 0.011 | 0.194 | 0.011 | 0.206 | 0.10891 | 0.0015906 | 0.11948 | 0.00023622
10/23/2022 | 3:23 | 0.011 | 0.193 | 0.011 | 0.205 | 0.093559 | 0.0015748 | 0.10443 | 0.00023622
10/23/2022 | 3:23 | 0.01 | 0.192 | 0.011 | 0.205 | 0.081685 | 0.0015591 | 0.089795 | 0.00023622
10/23/2022 | 3:23 | 0.01 | 0.192 | 0.011 | 0.204 | 0.073087 | 0.0015591 | 0.076063 | 0.00023622
10/23/2022 | 3:23 | 0.01 | 0.191 | 0.011 | 0.203 | 0.067512 | 0.0015591 | 0.064094 | 0.00023622
10/23/2022 | 3:23 | 0.01 | 0.19 | 0.011 | 0.203 | 0.064488 | 0.0015591 | 0.055669 | 0.00023622
10/23/2022 | 3:23 | 0.01 | 0.19 | 0.01 | 0.202 | 0.063843 | 0.0015433 | 0.052236 | 0.00023622
10/23/2022 | 3:23 | 0.01 | 0.189 | 0.01 | 0.202 | 0.065575 | 0.0015906 | 0.054457 | 0.00025197
10/23/2022 | 3:23 | 0.01 | 0.189 | 0.01 | 0.201 | 0.069953 | 0.0016693 | 0.061118 | 0.00025197
10/23/2022 | 3:23 | 0.01 | 0.188 | 0.01 | 0.2 | 0.077213 | 0.0018268 | 0.070331 | 0.00025197
10/23/2022 | 3:23 | 0.01 | 0.188 | 0.01 | 0.2 | 0.08726 | 0.0019843 | 0.080598 | 0.00025197
10/23/2022 | 3:23 | 0.01 | 0.187 | 0.01 | 0.199 | 0.099354 | 0.0021102 | 0.091165 | 0.00025197
10/23/2022 | 3:23 | 0.01 | 0.186 | 0.01 | 0.199 | 0.11255 | 0.002189 | 0.10169 | 0.00025197
10/23/2022 | 3:23 | 0.009 | 0.186 | 0.01 | 0.198 | 0.12595 | 0.0022677 | 0.11208 | 0.00025197
10/23/2022 | 3:23 | 0.009 | 0.185 | 0.01 | 0.198 | 0.1389 | 0.0023307 | 0.12241 | 0.00025197
10/23/2022 | 3:23 | 0.009 | 0.185 | 0.01 | 0.197 | 0.15088 | 0.0024094 | 0.13272 | 0.00025197
10/23/2022 | 3:23 | 0.009 | 0.184 | 0.01 | 0.196 | 0.16156 | 0.0024882 | 0.14294 | 0.00025197
10/23/2022 | 3:23 | 0.009 | 0.184 | 0.01 | 0.196 | 0.17096 | 0.0025512 | 0.15283 | 0.00026772
10/23/2022 | 3:23 | 0.009 | 0.183 | 0.01 | 0.195 | 0.17924 | 0.0025984 | 0.16214 | 0.00026772
10/23/2022 | 3:23 | 0.009 | 0.183 | 0.01 | 0.195 | 0.18663 | 0.0026299 | 0.17066 | 0.00026772
10/23/2022 | 3:23 | 0.009 | 0.182 | 0.01 | 0.194 | 0.19329 | 0.0026614 | 0.1782 | 0.00026772
10/23/2022 | 3:23 | 0.009 | 0.182 | 0.01 | 0.194 | 0.19943 | 0.0026772 | 0.18469 | 0.00026772
10/23/2022 | 3:23 | 0.009 | 0.181 | 0.01 | 0.193 | 0.20509 | 0.0027087 | 0.19011 | 0.00026772
10/23/2022 | 3:23 | 0.009 | 0.181 | 0.01 | 0.193 | 0.21027 | 0.0027244 | 0.19458 | 0.00026772
10/23/2022 | 3:23 | 0.009 | 0.18 | 0.01 | 0.192 | 0.21488 | 0.0027402 | 0.19835 | 0.00025197
10/23/2022 | 3:23 | 0.009 | 0.18 | 0.01 | 0.192 | 0.21887 | 0.0027717 | 0.20156 | 0.00025197
10/23/2022 | 3:23 | 0.009 | 0.179 | 0.01 | 0.191 | 0.22216 | 0.0028189 | 0.20438 | 0.00025197
10/23/2022 | 3:23 | 0.008 | 0.178 | 0.01 | 0.19 | 0.22479 | 0.0028819 | 0.20693 | 0.00025197
10/23/2022 | 3:23 | 0.008 | 0.178 | 0.01 | 0.19 | 0.22679 | 0.0029291 | 0.20924 | 0.00025197
10/23/2022 | 3:23 | 0.008 | 0.177 | 0.01 | 0.189 | 0.22831 | 0.0029764 | 0.21137 | 0.00025197
10/23/2022 | 3:23 | 0.008 | 0.177 | 0.009 | 0.189 | 0.22945 | 0.0030079 | 0.2132 | 0.00025197
10/23/2022 | 3:23 | 0.008 | 0.176 | 0.009 | 0.188 | 0.23035 | 0.0030551 | 0.21471 | 0.00025197
10/23/2022 | 3:23 | 0.008 | 0.176 | 0.009 | 0.188 | 0.23104 | 0.0031181 | 0.21589 | 0.00025197
10/23/2022 | 3:23 | 0.008 | 0.175 | 0.009 | 0.187 | 0.23157 | 0.0031811 | 0.21674 | 0.00026772
10/23/2022 | 3:23 | 0.008 | 0.175 | 0.009 | 0.187 | 0.23192 | 0.0032441 | 0.21731 | 0.00025197
10/23/2022 | 3:23 | 0.008 | 0.174 | 0.009 | 0.186 | 0.23205 | 0.0033071 | 0.21765 | 0.00026772
10/23/2022 | 3:23 | 0.008 | 0.174 | 0.009 | 0.186 | 0.23189 | 0.0033701 | 0.21775 | 0.00026772
10/23/2022 | 3:23 | 0.008 | 0.173 | 0.009 | 0.185 | 0.23137 | 0.0034173 | 0.21753 | 0.00025197
10/23/2022 | 3:23 | 0.008 | 0.173 | 0.009 | 0.185 | 0.23044 | 0.0034331 | 0.21688 | 0.00025197
10/23/2022 | 3:23 | 0.008 | 0.172 | 0.009 | 0.184 | 0.22901 | 0.0034331 | 0.21561 | 0.00025197
10/23/2022 | 3:23 | 0.008 | 0.172 | 0.009 | 0.184 | 0.22693 | 0.0034173 | 0.21357 | 0.00025197
10/23/2022 | 3:23 | 0.007 | 0.171 | 0.009 | 0.183 | 0.224 | 0.0033701 | 0.21072 | 0.00025197
10/23/2022 | 3:23 | 0.007 | 0.171 | 0.009 | 0.183 | 0.21997 | 0.0033071 | 0.2071 | 0.00025197
10/23/2022 | 3:23 | 0.007 | 0.17 | 0.009 | 0.182 | 0.21468 | 0.0032283 | 0.20272 | 0.00025197
10/23/2022 | 3:23 | 0.007 | 0.17 | 0.009 | 0.182 | 0.20814 | 0.0031654 | 0.19767 | 0.00025197
10/23/2022 | 3:23 | 0.007 | 0.169 | 0.009 | 0.181 | 0.20049 | 0.0030866 | 0.19197 | 0.00025197
10/23/2022 | 3:23 | 0.007 | 0.169 | 0.009 | 0.181 | 0.192 | 0.0029921 | 0.18561 | 0.00025197
10/23/2022 | 3:23 | 0.007 | 0.168 | 0.008 | 0.18 | 0.18301 | 0.0029134 | 0.1785 | 0.00025197
10/23/2022 | 3:23 | 0.007 | 0.168 | 0.008 | 0.18 | 0.17387 | 0.0028346 | 0.17065 | 0.00025197
10/23/2022 | 3:23 | 0.007 | 0.167 | 0.008 | 0.179 | 0.16482 | 0.0027559 | 0.16213 | 0.00025197
10/23/2022 | 3:23 | 0.007 | 0.167 | 0.008 | 0.179 | 0.15589 | 0.0027087 | 0.15313 | 0.00025197
10/23/2022 | 3:23 | 0.007 | 0.167 | 0.008 | 0.179 | 0.14701 | 0.0026299 | 0.14392 | 0.00025197
10/23/2022 | 3:23 | 0.007 | 0.166 | 0.008 | 0.178 | 0.13813 | 0.0025669 | 0.13482 | 0.00025197
10/23/2022 | 3:23 | 0.007 | 0.166 | 0.008 | 0.178 | 0.12904 | 0.0025197 | 0.12608 | 0.00023622
10/23/2022 | 3:23 | 0.007 | 0.165 | 0.008 | 0.177 | 0.11967 | 0.0024724 | 0.11798 | 0.00025197
10/23/2022 | 3:23 | 0.007 | 0.165 | 0.008 | 0.177 | 0.11006 | 0.0024724 | 0.11054 | 0.00025197
10/23/2022 | 3:23 | 0.007 | 0.164 | 0.008 | 0.176 | 0.10043 | 0.0024882 | 0.10367 | 0.00025197
10/23/2022 | 3:23 | 0.007 | 0.164 | 0.008 | 0.176 | 0.091008 | 0.0025039 | 0.09726 | 0.00025197
10/23/2022 | 3:23 | 0.006 | 0.163 | 0.008 | 0.175 | 0.082299 | 0.0025197 | 0.091165 | 0.00025197
10/23/2022 | 3:23 | 0.006 | 0.163 | 0.008 | 0.175 | 0.074535 | 0.0024882 | 0.085197 | 0.00025197
10/23/2022 | 3:23 | 0.006 | 0.162 | 0.008 | 0.174 | 0.068094 | 0.0024567 | 0.07926 | 0.00025197
10/23/2022 | 3:23 | 0.006 | 0.162 | 0.008 | 0.174 | 0.063118 | 0.0024252 | 0.073339 | 0.00025197
10/23/2022 | 3:23 | 0.006 | 0.162 | 0.008 | 0.173 | 0.059543 | 0.0023937 | 0.067701 | 0.00025197
10/23/2022 | 3:23 | 0.006 | 0.161 | 0.008 | 0.173 | 0.057165 | 0.0023307 | 0.06263 | 0.00025197
10/23/2022 | 3:23 | 0.006 | 0.161 | 0.008 | 0.173 | 0.055543 | 0.0022677 | 0.058457 | 0.00026772
10/23/2022 | 3:23 | 0.006 | 0.16 | 0.008 | 0.172 | 0.054346 | 0.0021732 | 0.055386 | 0.00025197
10/23/2022 | 3:23 | 0.006 | 0.16 | 0.008 | 0.172 | 0.05337 | 0.002063 | 0.053559 | 0.00025197
10/23/2022 | 3:23 | 0.006 | 0.159 | 0.008 | 0.171 | 0.052677 | 0.0019685 | 0.052929 | 0.00025197
10/23/2022 | 3:23 | 0.006 | 0.159 | 0.008 | 0.171 | 0.052535 | 0.001874 | 0.053244 | 0.00023622
10/23/2022 | 3:23 | 0.006 | 0.158 | 0.007 | 0.17 | 0.053291 | 0.0017795 | 0.05411 | 0.00023622
10/23/2022 | 3:23 | 0.006 | 0.158 | 0.007 | 0.17 | 0.055197 | 0.0017165 | 0.055071 | 0.00023622
10/23/2022 | 3:23 | 0.006 | 0.158 | 0.007 | 0.169 | 0.058315 | 0.0016535 | 0.055874 | 0.00023622
10/23/2022 | 3:23 | 0.006 | 0.157 | 0.007 | 0.169 | 0.062535 | 0.0015906 | 0.05652 | 0.00023622
10/23/2022 | 3:23 | 0.006 | 0.157 | 0.007 | 0.169 | 0.067528 | 0.0015118 | 0.05726 | 0.00023622
10/23/2022 | 3:23 | 0.006 | 0.156 | 0.007 | 0.168 | 0.072882 | 0.0013858 | 0.058551 | 0.00023622
10/23/2022 | 3:23 | 0.005 | 0.156 | 0.007 | 0.168 | 0.078205 | 0.0012756 | 0.060803 | 0.00023622
10/23/2022 | 3:23 | 0.005 | 0.155 | 0.007 | 0.167 | 0.083244 | 0.0011654 | 0.064362 | 0.00023622
10/23/2022 | 3:23 | 0.005 | 0.155 | 0.007 | 0.167 | 0.087984 | 0.0011181 | 0.069213 | 0.00023622
10/23/2022 | 3:23 | 0.005 | 0.155 | 0.007 | 0.166 | 0.092614 | 0.0011181 | 0.075071 | 0.00023622
10/23/2022 | 3:23 | 0.005 | 0.154 | 0.007 | 0.166 | 0.097449 | 0.0011811 | 0.08148 | 0.00023622
10/23/2022 | 3:23 | 0.005 | 0.154 | 0.007 | 0.166 | 0.10276 | 0.0012913 | 0.087969 | 0.00023622
10/23/2022 | 3:23 | 0.005 | 0.153 | 0.007 | 0.165 | 0.10868 | 0.0014331 | 0.094236 | 0.00023622
10/23/2022 | 3:23 | 0.005 | 0.153 | 0.007 | 0.165 | 0.11518 | 0.0015748 | 0.10016 | 0.00023622
10/23/2022 | 3:23 | 0.005 | 0.152 | 0.007 | 0.164 | 0.12203 | 0.0017008 | 0.10576 | 0.00023622
10/23/2022 | 3:23 | 0.005 | 0.152 | 0.007 | 0.164 | 0.1289 | 0.001811 | 0.11131 | 0.00023622
10/23/2022 | 3:23 | 0.005 | 0.152 | 0.007 | 0.164 | 0.1355 | 0.0019055 | 0.11693 | 0.00023622
10/23/2022 | 3:23 | 0.005 | 0.151 | 0.006 | 0.163 | 0.14159 | 0.002 | 0.12277 | 0.00022047
10/23/2022 | 3:23 | 0.005 | 0.151 | 0.006 | 0.163 | 0.1471 | 0.0020945 | 0.1288 | 0.00022047
10/23/2022 | 3:23 | 0.005 | 0.151 | 0.006 | 0.162 | 0.15214 | 0.002189 | 0.1349 | 0.00023622
10/23/2022 | 3:23 | 0.005 | 0.15 | 0.006 | 0.162 | 0.15682 | 0.0022835 | 0.14085 | 0.00023622
10/23/2022 | 3:23 | 0.005 | 0.15 | 0.006 | 0.162 | 0.16128 | 0.002378 | 0.14639 | 0.00023622
10/23/2022 | 3:23 | 0.005 | 0.149 | 0.006 | 0.161 | 0.16561 | 0.0024724 | 0.15143 | 0.00023622
10/23/2022 | 3:23 | 0.004 | 0.149 | 0.006 | 0.161 | 0.16984 | 0.0025669 | 0.15591 | 0.00023622
10/23/2022 | 3:23 | 0.004 | 0.149 | 0.006 | 0.161 | 0.17392 | 0.0026614 | 0.15986 | 0.00025197
10/23/2022 | 3:23 | 0.004 | 0.148 | 0.006 | 0.16 | 0.17775 | 0.0027244 | 0.16337 | 0.00028346
10/23/2022 | 3:23 | 0.004 | 0.148 | 0.006 | 0.16 | 0.18118 | 0.0027717 | 0.16657 | 0.00028346
10/23/2022 | 3:23 | 0.004 | 0.148 | 0.006 | 0.159 | 0.18414 | 0.0028031 | 0.16954 | 0.00028346
10/23/2022 | 3:23 | 0.004 | 0.147 | 0.006 | 0.159 | 0.1866 | 0.0028189 | 0.17236 | 0.00028346
10/23/2022 | 3:23 | 0.004 | 0.147 | 0.006 | 0.159 | 0.1886 | 0.0028504 | 0.17496 | 0.00028346
10/23/2022 | 3:23 | 0.004 | 0.146 | 0.006 | 0.158 | 0.19024 | 0.0028661 | 0.17731 | 0.00028346
10/23/2022 | 3:23 | 0.004 | 0.146 | 0.006 | 0.158 | 0.1915 | 0.0028976 | 0.17929 | 0.00028346
10/23/2022 | 3:23 | 0.004 | 0.146 | 0.006 | 0.158 | 0.19244 | 0.0029134 | 0.18087 | 0.00028346
10/23/2022 | 3:23 | 0.004 | 0.145 | 0.006 | 0.157 | 0.19306 | 0.0029134 | 0.18202 | 0.00029921
10/23/2022 | 3:23 | 0.004 | 0.145 | 0.006 | 0.157 | 0.19328 | 0.0029291 | 0.18277 | 0.00029921
10/23/2022 | 3:23 | 0.004 | 0.145 | 0.006 | 0.156 | 0.19307 | 0.0029291 | 0.18315 | 0.00029921
10/23/2022 | 3:23 | 0.004 | 0.144 | 0.006 | 0.156 | 0.19239 | 0.0029291 | 0.18321 | 0.00029921
10/23/2022 | 3:23 | 0.004 | 0.144 | 0.006 | 0.156 | 0.19123 | 0.0029291 | 0.18294 | 0.00029921
10/23/2022 | 3:23 | 0.004 | 0.143 | 0.006 | 0.155 | 0.18964 | 0.0029291 | 0.18231 | 0.00029921
10/23/2022 | 3:23 | 0.004 | 0.143 | 0.006 | 0.155 | 0.18775 | 0.0029449 | 0.18121 | 0.00029921
10/23/2022 | 3:23 | 0.004 | 0.143 | 0.006 | 0.155 | 0.18559 | 0.0029449 | 0.17957 | 0.00029921
10/23/2022 | 3:23 | 0.004 | 0.142 | 0.006 | 0.154 | 0.18317 | 0.0029449 | 0.17737 | 0.00029921
10/23/2022 | 3:23 | 0.004 | 0.142 | 0.006 | 0.154 | 0.18043 | 0.0029134 | 0.17461 | 0.00029921
10/23/2022 | 3:23 | 0.004 | 0.142 | 0.005 | 0.154 | 0.17726 | 0.0028661 | 0.17143 | 0.00029921
10/23/2022 | 3:23 | 0.004 | 0.141 | 0.005 | 0.153 | 0.17354 | 0.0028031 | 0.16794 | 0.00029921
10/23/2022 | 3:23 | 0.004 | 0.141 | 0.005 | 0.153 | 0.1692 | 0.0027244 | 0.16424 | 0.00029921
10/23/2022 | 3:23 | 0.004 | 0.141 | 0.005 | 0.152 | 0.16428 | 0.0026457 | 0.16036 | 0.00029921
10/23/2022 | 3:23 | 0.004 | 0.14 | 0.005 | 0.152 | 0.15893 | 0.0025669 | 0.15624 | 0.00029921
10/23/2022 | 3:23 | 0.004 | 0.14 | 0.005 | 0.152 | 0.15334 | 0.0024882 | 0.15181 | 0.00029921
10/23/2022 | 3:23 | 0.004 | 0.14 | 0.005 | 0.151 | 0.14772 | 0.0023937 | 0.14694 | 0.00029921
10/23/2022 | 3:23 | 0.004 | 0.139 | 0.005 | 0.151 | 0.14222 | 0.0022835 | 0.14159 | 0.00029921
10/23/2022 | 3:23 | 0.004 | 0.139 | 0.005 | 0.151 | 0.13683 | 0.0021575 | 0.1358 | 0.00029921
10/23/2022 | 3:23 | 0.004 | 0.139 | 0.005 | 0.15 | 0.13148 | 0.0019843 | 0.12964 | 0.00028346
10/23/2022 | 3:23 | 0.004 | 0.138 | 0.005 | 0.15 | 0.12598 | 0.0017953 | 0.12337 | 0.00028346
10/23/2022 | 3:23 | 0.004 | 0.138 | 0.005 | 0.15 | 0.1202 | 0.0016063 | 0.11713 | 0.00028346
10/23/2022 | 3:23 | 0.004 | 0.138 | 0.005 | 0.149 | 0.11402 | 0.0014173 | 0.1111 | 0.00028346
10/23/2022 | 3:23 | 0.004 | 0.137 | 0.005 | 0.149 | 0.10737 | 0.0013071 | 0.10529 | 0.00028346
10/23/2022 | 3:23 | 0.004 | 0.137 | 0.005 | 0.149 | 0.10031 | 0.0013071 | 0.099717 | 0.00026772
10/23/2022 | 3:23 | 0.004 | 0.137 | 0.005 | 0.148 | 0.093087 | 0.0014961 | 0.094189 | 0.00025197
10/23/2022 | 3:23 | 0.003 | 0.136 | 0.005 | 0.148 | 0.085874 | 0.0018583 | 0.088583 | 0.00025197
10/23/2022 | 3:23 | 0.003 | 0.136 | 0.005 | 0.148 | 0.078976 | 0.002315 | 0.082661 | 0.00025197
10/23/2022 | 3:23 | 0.003 | 0.136 | 0.004 | 0.147 | 0.07252 | 0.0028031 | 0.076378 | 0.00025197
10/23/2022 | 3:23 | 0.003 | 0.135 | 0.004 | 0.147 | 0.066488 | 0.0033386 | 0.069732 | 0.00025197
10/23/2022 | 3:23 | 0.003 | 0.135 | 0.004 | 0.147 | 0.060898 | 0.003874 | 0.062866 | 0.00025197
10/23/2022 | 3:23 | 0.003 | 0.135 | 0.004 | 0.146 | 0.055543 | 0.0045039 | 0.055984 | 0.00025197
10/23/2022 | 3:23 | 0.003 | 0.134 | 0.004 | 0.146 | 0.050205 | 0.0054016 | 0.049528 | 0.00025197
10/23/2022 | 3:23 | 0.003 | 0.134 | 0.004 | 0.146 | 0.044756 | 0.0069291 | 0.043953 | 0.00025197
10/23/2022 | 3:23 | 0.003 | 0.134 | 0.004 | 0.145 | 0.039291 | 0.0095591 | 0.039748 | 0.00025197
10/23/2022 | 3:23 | 0.003 | 0.134 | 0.004 | 0.145 | 0.034189 | 0.013354 | 0.037181 | 0.00025197
10/23/2022 | 3:23 | 0.003 | 0.133 | 0.004 | 0.145 | 0.030315 | 0.017795 | 0.036425 | 0.00025197
10/23/2022 | 3:23 | 0.003 | 0.133 | 0.004 | 0.144 | 0.02874 | 0.022126 | 0.037622 | 0.00026772
10/23/2022 | 3:23 | 0.003 | 0.133 | 0.004 | 0.144 | 0.030063 | 0.025606 | 0.040819 | 0.00026772
10/23/2022 | 3:23 | 0.003 | 0.132 | 0.004 | 0.144 | 0.034063 | 0.027969 | 0.045858 | 0.00026772
10/23/2022 | 3:23 | 0.003 | 0.132 | 0.004 | 0.143 | 0.040126 | 0.029307 | 0.052315 | 0.00026772
10/23/2022 | 3:23 | 0.003 | 0.132 | 0.004 | 0.143 | 0.047811 | 0.029921 | 0.059543 | 0.00026772
10/23/2022 | 3:23 | 0.003 | 0.131 | 0.004 | 0.143 | 0.056913 | 0.030126 | 0.066945 | 0.00026772
10/23/2022 | 3:23 | 0.002 | 0.131 | 0.004 | 0.142 | 0.067118 | 0.030142 | 0.074142 | 0.00026772
10/23/2022 | 3:23 | 0.002 | 0.131 | 0.004 | 0.142 | 0.077969 | 0.030173 | 0.080976 | 0.00026772
10/23/2022 | 3:23 | 0.002 | 0.13 | 0.004 | 0.142 | 0.088835 | 0.030425 | 0.08748 | 0.00026772
10/23/2022 | 3:23 | 0.002 | 0.13 | 0.004 | 0.142 | 0.099118 | 0.031024 | 0.093669 | 0.00026772
10/23/2022 | 3:23 | 0.002 | 0.13 | 0.004 | 0.141 | 0.1086 | 0.031811 | 0.099638 | 0.00026772
10/23/2022 | 3:23 | 0.002 | 0.13 | 0.004 | 0.141 | 0.11706 | 0.032472 | 0.10537 | 0.00026772
10/23/2022 | 3:23 | 0.002 | 0.129 | 0.004 | 0.141 | 0.12444 | 0.032756 | 0.11087 | 0.00026772
10/23/2022 | 3:23 | 0.002 | 0.129 | 0.004 | 0.14 | 0.13071 | 0.032772 | 0.11613 | 0.00026772
10/23/2022 | 3:23 | 0.002 | 0.129 | 0.004 | 0.14 | 0.13591 | 0.032882 | 0.12118 | 0.00026772
10/23/2022 | 3:23 | 0.002 | 0.129 | 0.004 | 0.14 | 0.14008 | 0.033449 | 0.12605 | 0.00028346
10/23/2022 | 3:23 | 0.002 | 0.128 | 0.004 | 0.139 | 0.14337 | 0.034551 | 0.13071 | 0.00028346
10/23/2022 | 3:23 | 0.002 | 0.128 | 0.004 | 0.139 | 0.14591 | 0.035969 | 0.13513 | 0.00028346
10/23/2022 | 3:23 | 0.002 | 0.128 | 0.004 | 0.139 | 0.14789 | 0.037402 | 0.13912 | 0.00028346
10/23/2022 | 3:23 | 0.002 | 0.127 | 0.004 | 0.139 | 0.14951 | 0.038677 | 0.14258 | 0.00028346
10/23/2022 | 3:23 | 0.002 | 0.127 | 0.004 | 0.138 | 0.15093 | 0.03978 | 0.14551 | 0.00029921
10/23/2022 | 3:23 | 0.002 | 0.127 | 0.004 | 0.138 | 0.15224 | 0.040772 | 0.14786 | 0.00029921
10/23/2022 | 3:23 | 0.002 | 0.127 | 0.004 | 0.138 | 0.15346 | 0.041669 | 0.14975 | 0.00028346
10/23/2022 | 3:23 | 0.002 | 0.126 | 0.004 | 0.137 | 0.15455 | 0.042488 | 0.15131 | 0.00029921
10/23/2022 | 3:23 | 0.002 | 0.126 | 0.004 | 0.137 | 0.15543 | 0.043181 | 0.15271 | 0.00029921
10/23/2022 | 3:23 | 0.002 | 0.126 | 0.004 | 0.137 | 0.15611 | 0.04378 | 0.15406 | 0.00029921
10/23/2022 | 3:23 | 0.002 | 0.125 | 0.004 | 0.136 | 0.15657 | 0.044346 | 0.15543 | 0.00029921
10/23/2022 | 3:23 | 0.002 | 0.125 | 0.004 | 0.136 | 0.15687 | 0.044976 | 0.15685 | 0.00029921
10/23/2022 | 3:23 | 0.002 | 0.125 | 0.004 | 0.136 | 0.15707 | 0.045764 | 0.15824 | 0.00029921
10/23/2022 | 3:23 | 0.002 | 0.125 | 0.004 | 0.136 | 0.1572 | 0.046756 | 0.15957 | 0.00029921
10/23/2022 | 3:23 | 0.002 | 0.124 | 0.004 | 0.135 | 0.15718 | 0.047906 | 0.16082 | 0.00029921
10/23/2022 | 3:23 | 0.002 | 0.124 | 0.004 | 0.135 | 0.15699 | 0.04915 | 0.16194 | 0.00029921
10/23/2022 | 3:23 | 0.002 | 0.124 | 0.004 | 0.135 | 0.15654 | 0.05052 | 0.16294 | 0.00028346
10/23/2022 | 3:23 | 0.002 | 0.123 | 0.004 | 0.135 | 0.15578 | 0.052252 | 0.16375 | 0.00028346
10/23/2022 | 3:23 | 0.002 | 0.123 | 0.004 | 0.134 | 0.15466 | 0.054567 | 0.16428 | 0.00028346
10/23/2022 | 3:23 | 0.002 | 0.123 | 0.004 | 0.134 | 0.15304 | 0.05748 | 0.16444 | 0.00028346
10/23/2022 | 3:23 | 0.002 | 0.123 | 0.004 | 0.134 | 0.15074 | 0.06085 | 0.16419 | 0.00028346
10/23/2022 | 3:23 | 0.002 | 0.122 | 0.004 | 0.133 | 0.14751 | 0.064457 | 0.16361 | 0.00028346
10/23/2022 | 3:23 | 0.002 | 0.122 | 0.004 | 0.133 | 0.14315 | 0.067984 | 0.16274 | 0.00028346
10/23/2022 | 3:23 | 0.002 | 0.122 | 0.004 | 0.133 | 0.13753 | 0.071118 | 0.16165 | 0.00028346
10/23/2022 | 3:23 | 0.002 | 0.122 | 0.004 | 0.133 | 0.13076 | 0.073575 | 0.16033 | 0.00028346
10/23/2022 | 3:23 | 0.002 | 0.121 | 0.003 | 0.132 | 0.12313 | 0.075244 | 0.15872 | 0.00028346
10/23/2022 | 3:23 | 0.002 | 0.121 | 0.003 | 0.132 | 0.11485 | 0.076268 | 0.15674 | 0.00028346
10/23/2022 | 3:23 | 0.002 | 0.121 | 0.003 | 0.132 | 0.10624 | 0.076866 | 0.15431 | 0.00029921
10/23/2022 | 3:23 | 0.002 | 0.121 | 0.003 | 0.132 | 0.097449 | 0.07726 | 0.1514 | 0.00028346
10/23/2022 | 3:23 | 0.002 | 0.12 | 0.003 | 0.131 | 0.088866 | 0.077496 | 0.14805 | 0.00028346
10/23/2022 | 3:23 | 0.002 | 0.12 | 0.003 | 0.131 | 0.080646 | 0.077496 | 0.14428 | 0.00028346
10/23/2022 | 3:23 | 0.002 | 0.12 | 0.003 | 0.131 | 0.07315 | 0.07726 | 0.1402 | 0.00026772
10/23/2022 | 3:23 | 0.002 | 0.119 | 0.003 | 0.131 | 0.066488 | 0.076866 | 0.13591 | 0.00026772
10/23/2022 | 3:23 | 0.002 | 0.119 | 0.003 | 0.13 | 0.060756 | 0.076551 | 0.13151 | 0.00026772
10/23/2022 | 3:23 | 0.002 | 0.119 | 0.003 | 0.13 | 0.055732 | 0.076567 | 0.12729 | 0.00026772
10/23/2022 | 3:23 | 0.002 | 0.119 | 0.003 | 0.13 | 0.051213 | 0.077024 | 0.12343 | 0.00026772
10/23/2022 | 3:23 | 0.002 | 0.118 | 0.003 | 0.129 | 0.04685 | 0.077858 | 0.12013 | 0.00025197
10/23/2022 | 3:23 | 0.002 | 0.118 | 0.003 | 0.129 | 0.042378 | 0.078913 | 0.11748 | 0.00025197
10/23/2022 | 3:23 | 0.002 | 0.118 | 0.003 | 0.129 | 0.037717 | 0.080047 | 0.11546 | 0.00025197
10/23/2022 | 3:23 | 0.002 | 0.118 | 0.003 | 0.129 | 0.032976 | 0.081197 | 0.11387 | 0.00025197
10/23/2022 | 3:23 | 0.002 | 0.117 | 0.003 | 0.128 | 0.028394 | 0.082378 | 0.1125 | 0.00023622
10/23/2022 | 3:23 | 0.002 | 0.117 | 0.003 | 0.128 | 0.024268 | 0.083528 | 0.11112 | 0.00023622
10/23/2022 | 3:23 | 0.002 | 0.117 | 0.003 | 0.128 | 0.02085 | 0.084551 | 0.10956 | 0.00023622
10/23/2022 | 3:23 | 0.002 | 0.117 | 0.003 | 0.127 | 0.018189 | 0.085307 | 0.10778 | 0.00023622
10/23/2022 | 3:23 | 0.002 | 0.116 | 0.002 | 0.127 | 0.016142 | 0.085606 | 0.1058 | 0.00023622
10/23/2022 | 3:23 | 0.002 | 0.116 | 0.002 | 0.127 | 0.014488 | 0.085307 | 0.10361 | 0.00023622
10/23/2022 | 3:23 | 0.002 | 0.116 | 0.002 | 0.127 | 0.013197 | 0.084378 | 0.10118 | 0.00023622
10/23/2022 | 3:23 | 0.002 | 0.116 | 0.002 | 0.126 | 0.01252 | 0.082898 | 0.098457 | 0.00023622
10/23/2022 | 3:23 | 0.002 | 0.115 | 0.002 | 0.126 | 0.01274 | 0.081008 | 0.095323 | 0.00023622
10/23/2022 | 3:23 | 0.002 | 0.115 | 0.002 | 0.126 | 0.01389 | 0.078866 | 0.091701 | 0.00023622
10/23/2022 | 3:23 | 0.002 | 0.115 | 0.002 | 0.126 | 0.015591 | 0.076488 | 0.087591 | 0.00023622
10/23/2022 | 3:23 | 0.002 | 0.115 | 0.002 | 0.125 | 0.017433 | 0.073906 | 0.083071 | 0.00023622
10/23/2022 | 3:23 | 0.002 | 0.114 | 0.002 | 0.125 | 0.019118 | 0.071087 | 0.078268 | 0.00023622
10/23/2022 | 3:23 | 0.002 | 0.114 | 0.002 | 0.125 | 0.02052 | 0.068079 | 0.073354 | 0.00023622
10/23/2022 | 3:23 | 0.002 | 0.114 | 0.002 | 0.125 | 0.021654 | 0.064945 | 0.068378 | 0.00023622
10/23/2022 | 3:23 | 0.002 | 0.114 | 0.002 | 0.124 | 0.022614 | 0.061906 | 0.063402 | 0.00023622
10/23/2022 | 3:23 | 0.002 | 0.114 | 0.002 | 0.124 | 0.023496 | 0.059181 | 0.058394 | 0.00023622
10/23/2022 | 3:23 | 0.002 | 0.113 | 0.002 | 0.124 | 0.024299 | 0.056913 | 0.053433 | 0.00023622
10/23/2022 | 3:23 | 0.002 | 0.113 | 0.002 | 0.124 | 0.025008 | 0.055165 | 0.048693 | 0.00023622
10/23/2022 | 3:23 | 0.002 | 0.113 | 0.002 | 0.123 | 0.025559 | 0.053937 | 0.044425 | 0.00023622
10/23/2022 | 3:23 | 0.002 | 0.113 | 0.002 | 0.123 | 0.025906 | 0.053213 | 0.040961 | 0.00023622
10/23/2022 | 3:23 | 0.002 | 0.112 | 0.002 | 0.123 | 0.026094 | 0.052961 | 0.038535 | 0.00023622
10/23/2022 | 3:23 | 0.002 | 0.112 | 0.002 | 0.123 | 0.026142 | 0.053181 | 0.037228 | 0.00023622
10/23/2022 | 3:23 | 0.002 | 0.112 | 0.002 | 0.122 | 0.02611 | 0.053795 | 0.037008 | 0.00023622
10/23/2022 | 3:23 | 0.002 | 0.112 | 0.002 | 0.122 | 0.026063 | 0.054772 | 0.037669 | 0.00023622
10/23/2022 | 3:23 | 0.002 | 0.111 | 0.002 | 0.122 | 0.026047 | 0.056016 | 0.039024 | 0.00023622
10/23/2022 | 3:23 | 0.002 | 0.111 | 0.002 | 0.122 | 0.026047 | 0.057433 | 0.040898 | 0.00023622
10/23/2022 | 3:23 | 0.002 | 0.111 | 0.002 | 0.122 | 0.026047 | 0.058898 | 0.04315 | 0.00023622
10/23/2022 | 3:23 | 0.002 | 0.111 | 0.002 | 0.121 | 0.026047 | 0.060378 | 0.045654 | 0.00023622
10/23/2022 | 3:23 | 0.002 | 0.111 | 0.002 | 0.121 | 0.026016 | 0.061748 | 0.048315 | 0.00023622
10/23/2022 | 3:23 | 0.002 | 0.11 | 0.002 | 0.121 | 0.025969 | 0.062976 | 0.050976 | 0.00023622
10/23/2022 | 3:23 | 0.002 | 0.11 | 0.002 | 0.121 | 0.025953 | 0.064047 | 0.053543 | 0.00023622
10/23/2022 | 3:23 | 0.002 | 0.11 | 0.002 | 0.12 | 0.025953 | 0.064945 | 0.05589 | 0.00023622
10/23/2022 | 3:23 | 0.002 | 0.11 | 0.002 | 0.12 | 0.026 | 0.065685 | 0.057953 | 0.00023622
10/23/2022 | 3:23 | 0.002 | 0.109 | 0.002 | 0.12 | 0.026079 | 0.066268 | 0.059685 | 0.00023622
10/23/2022 | 3:23 | 0.001 | 0.109 | 0.002 | 0.12 | 0.026157 | 0.066724 | 0.061087 | 0.00023622
10/23/2022 | 3:23 | 0.001 | 0.109 | 0.002 | 0.119 | 0.026236 | 0.067039 | 0.062236 | 0.00023622
10/23/2022 | 3:23 | 0.001 | 0.109 | 0.002 | 0.119 | 0.026299 | 0.067244 | 0.063134 | 0.00023622
10/23/2022 | 3:23 | 0.001 | 0.109 | 0.002 | 0.119 | 0.026346 | 0.06737 | 0.063827 | 0.00022047
10/23/2022 | 3:23 | 0.001 | 0.108 | 0.002 | 0.119 | 0.026378 | 0.067417 | 0.064315 | 0.00022047
10/23/2022 | 3:23 | 0.001 | 0.108 | 0.002 | 0.118 | 0.026394 | 0.067433 | 0.064567 | 0.00022047
10/23/2022 | 3:23 | 0.001 | 0.108 | 0.002 | 0.118 | 0.026378 | 0.067433 | 0.064598 | 0.00022047
10/23/2022 | 3:23 | 0.001 | 0.108 | 0.002 | 0.118 | 0.026331 | 0.067433 | 0.064425 | 0.00022047
10/23/2022 | 3:23 | 0.001 | 0.108 | 0.002 | 0.118 | 0.026268 | 0.067433 | 0.064079 | 0.00022047
10/23/2022 | 3:23 | 0.001 | 0.107 | 0.002 | 0.118 | 0.02622 | 0.067433 | 0.063622 | 0.00022047
10/23/2022 | 3:23 | 0.001 | 0.107 | 0.002 | 0.117 | 0.026205 | 0.067433 | 0.063102 | 0.00022047
10/23/2022 | 3:23 | 0.001 | 0.107 | 0.002 | 0.117 | 0.026205 | 0.067449 | 0.062583 | 0.00022047
10/23/2022 | 3:23 | 0.001 | 0.107 | 0.002 | 0.117 | 0.026252 | 0.067449 | 0.062063 | 0.00022047
10/23/2022 | 3:23 | 0.001 | 0.106 | 0.002 | 0.117 | 0.026315 | 0.067449 | 0.061559 | 0.00022047
10/23/2022 | 3:23 | 0.001 | 0.106 | 0.002 | 0.117 | 0.026394 | 0.067449 | 0.061087 | 0.00022047
10/23/2022 | 3:23 | 0.001 | 0.106 | 0.002 | 0.116 | 0.026504 | 0.067449 | 0.060756 | 0.00022047
10/23/2022 | 3:23 | 0.001 | 0.106 | 0.002 | 0.116 | 0.026693 | 0.067433 | 0.060646 | 0.00022047
10/23/2022 | 3:23 | 0.001 | 0.106 | 0.002 | 0.116 | 0.026913 | 0.067465 | 0.060945 | 0.00022047
10/23/2022 | 3:23 | 0.001 | 0.106 | 0.002 | 0.116 | 0.027197 | 0.067559 | 0.06178 | 0.00022047
10/23/2022 | 3:23 | 0.001 | 0.105 | 0.002 | 0.116 | 0.027528 | 0.067795 | 0.063354 | 0.00022047
10/23/2022 | 3:23 | 0.001 | 0.105 | 0.002 | 0.115 | 0.027937 | 0.068252 | 0.06578 | 0.00022047
10/23/2022 | 3:23 | 0.001 | 0.105 | 0.002 | 0.115 | 0.028425 | 0.069039 | 0.069134 | 0.00022047
10/23/2022 | 3:23 | 0.001 | 0.105 | 0.002 | 0.115 | 0.029071 | 0.07022 | 0.073402 | 0.00022047
10/23/2022 | 3:23 | 0.001 | 0.105 | 0.002 | 0.115 | 0.02989 | 0.071858 | 0.078567 | 0.00022047
10/23/2022 | 3:23 | 0.001 | 0.104 | 0.002 | 0.114 | 0.030835 | 0.073921 | 0.08452 | 0.00022047
10/23/2022 | 3:23 | 0.001 | 0.104 | 0.002 | 0.114 | 0.031827 | 0.076283 | 0.09115 | 0.00022047
10/23/2022 | 3:23 | 0.001 | 0.104 | 0.002 | 0.114 | 0.032835 | 0.078803 | 0.098063 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.104 | 0.002 | 0.114 | 0.033811 | 0.081386 | 0.10507 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.104 | 0.002 | 0.114 | 0.03485 | 0.083937 | 0.11181 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.103 | 0.002 | 0.113 | 0.036 | 0.086346 | 0.11808 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.103 | 0.002 | 0.113 | 0.037276 | 0.088567 | 0.12378 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.103 | 0.002 | 0.113 | 0.038646 | 0.090504 | 0.12885 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.103 | 0.002 | 0.113 | 0.040047 | 0.092094 | 0.13329 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.103 | 0.002 | 0.113 | 0.041386 | 0.093354 | 0.13715 | 0.00020472
10/23/2022 | 3:23 | 0 | 0.102 | 0.002 | 0.112 | 0.042614 | 0.094268 | 0.14043 | 0.00020472
10/23/2022 | 3:23 | 0 | 0.102 | 0.002 | 0.112 | 0.043764 | 0.094898 | 0.14313 | 0.00020472
10/23/2022 | 3:23 | 0 | 0.102 | 0.002 | 0.112 | 0.04485 | 0.095291 | 0.14532 | 0.00020472
10/23/2022 | 3:23 | 0 | 0.102 | 0.002 | 0.112 | 0.045921 | 0.095512 | 0.14701 | 0.00020472
10/23/2022 | 3:23 | 0 | 0.102 | 0.002 | 0.112 | 0.046929 | 0.095575 | 0.14825 | 0.00020472
10/23/2022 | 3:23 | 0 | 0.101 | 0.002 | 0.112 | 0.047858 | 0.095559 | 0.14913 | 0.00020472
10/23/2022 | 3:23 | 0 | 0.101 | 0.002 | 0.111 | 0.048661 | 0.095496 | 0.14973 | 0.00020472
10/23/2022 | 3:23 | 0 | 0.101 | 0.002 | 0.111 | 0.049291 | 0.095402 | 0.15013 | 0.00020472
10/23/2022 | 3:23 | 0 | 0.101 | 0.002 | 0.111 | 0.04978 | 0.095323 | 0.15039 | 0.00020472
10/23/2022 | 3:23 | 0 | 0.101 | 0.002 | 0.111 | 0.050173 | 0.095276 | 0.15058 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.101 | 0.002 | 0.111 | 0.050457 | 0.095276 | 0.15072 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.1 | 0.002 | 0.11 | 0.050693 | 0.095307 | 0.15083 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.1 | 0.002 | 0.11 | 0.050819 | 0.09537 | 0.15094 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.1 | 0.002 | 0.11 | 0.05085 | 0.095449 | 0.15106 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.1 | 0.002 | 0.11 | 0.050772 | 0.095512 | 0.15118 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.1 | 0.002 | 0.11 | 0.050614 | 0.095528 | 0.15128 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.099 | 0.002 | 0.109 | 0.050425 | 0.095402 | 0.15128 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.099 | 0.002 | 0.109 | 0.05022 | 0.095087 | 0.15107 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.099 | 0.002 | 0.109 | 0.049969 | 0.094472 | 0.15055 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.099 | 0.002 | 0.109 | 0.049669 | 0.093465 | 0.14957 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.099 | 0.002 | 0.109 | 0.049291 | 0.091937 | 0.14808 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.099 | 0.002 | 0.109 | 0.048787 | 0.089764 | 0.14595 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.098 | 0.002 | 0.108 | 0.048205 | 0.086929 | 0.14315 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.098 | 0.002 | 0.108 | 0.047591 | 0.083449 | 0.13956 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.098 | 0.002 | 0.108 | 0.046992 | 0.079465 | 0.13523 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.098 | 0.002 | 0.108 | 0.046409 | 0.075118 | 0.1302 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.098 | 0.002 | 0.108 | 0.045748 | 0.070488 | 0.12465 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.098 | 0.002 | 0.107 | 0.044945 | 0.065622 | 0.11877 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.097 | 0.002 | 0.107 | 0.043921 | 0.060583 | 0.11276 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.097 | 0.002 | 0.107 | 0.042661 | 0.055543 | 0.10677 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.097 | 0.002 | 0.107 | 0.041197 | 0.050756 | 0.10096 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.097 | 0.002 | 0.107 | 0.039622 | 0.046598 | 0.095386 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.097 | 0.002 | 0.106 | 0.038016 | 0.043433 | 0.090173 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.096 | 0.002 | 0.106 | 0.036394 | 0.041512 | 0.085465 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.096 | 0.002 | 0.106 | 0.034677 | 0.040866 | 0.081386 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.096 | 0.002 | 0.106 | 0.032787 | 0.041323 | 0.078094 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.096 | 0.002 | 0.106 | 0.030661 | 0.042677 | 0.075654 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.096 | 0.002 | 0.106 | 0.028315 | 0.044709 | 0.074079 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.096 | 0.002 | 0.105 | 0.025858 | 0.047276 | 0.073244 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.096 | 0.002 | 0.105 | 0.023402 | 0.05022 | 0.073008 | 0.00028346
10/23/2022 | 3:23 | 0 | 0.095 | 0.002 | 0.105 | 0.021071 | 0.053339 | 0.073181 | 0.00028346
10/23/2022 | 3:23 | 0 | 0.095 | 0.002 | 0.105 | 0.018898 | 0.056425 | 0.073654 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.095 | 0.002 | 0.105 | 0.016835 | 0.059291 | 0.074331 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.095 | 0.002 | 0.104 | 0.014772 | 0.061811 | 0.075134 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.095 | 0.002 | 0.104 | 0.012756 | 0.063937 | 0.075937 | 0.00028346
10/23/2022 | 3:23 | 0 | 0.094 | 0.002 | 0.104 | 0.011024 | 0.065669 | 0.076583 | 0.00028346
10/23/2022 | 3:23 | 0 | 0.094 | 0.002 | 0.104 | 0.010016 | 0.067055 | 0.076961 | 0.00028346
10/23/2022 | 3:23 | 0 | 0.094 | 0.002 | 0.104 | 0.010063 | 0.068126 | 0.076913 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.094 | 0.002 | 0.104 | 0.011008 | 0.06885 | 0.076457 | 0.00028346
10/23/2022 | 3:23 | 0 | 0.094 | 0.002 | 0.103 | 0.012457 | 0.069244 | 0.075591 | 0.00028346
10/23/2022 | 3:23 | 0 | 0.094 | 0.002 | 0.103 | 0.014031 | 0.069291 | 0.074362 | 0.00028346
10/23/2022 | 3:23 | 0 | 0.094 | 0.002 | 0.103 | 0.015559 | 0.069039 | 0.072835 | 0.00028346
10/23/2022 | 3:23 | 0 | 0.093 | 0.002 | 0.103 | 0.016992 | 0.068535 | 0.070992 | 0.00028346
10/23/2022 | 3:23 | 0 | 0.093 | 0.002 | 0.103 | 0.018346 | 0.067843 | 0.068866 | 0.00028346
10/23/2022 | 3:23 | 0 | 0.093 | 0.002 | 0.103 | 0.019638 | 0.067039 | 0.066441 | 0.00028346
10/23/2022 | 3:23 | 0 | 0.093 | 0.002 | 0.102 | 0.020929 | 0.066205 | 0.063748 | 0.00028346
10/23/2022 | 3:23 | 0 | 0.093 | 0.002 | 0.102 | 0.02222 | 0.065402 | 0.060866 | 0.00028346
10/23/2022 | 3:23 | 0 | 0.093 | 0.002 | 0.102 | 0.023449 | 0.064661 | 0.057874 | 0.00028346
10/23/2022 | 3:23 | 0 | 0.092 | 0.002 | 0.102 | 0.024551 | 0.063969 | 0.054898 | 0.00028346
10/23/2022 | 3:23 | 0 | 0.092 | 0.002 | 0.102 | 0.025433 | 0.063386 | 0.052047 | 0.00028346
10/23/2022 | 3:23 | 0 | 0.092 | 0.002 | 0.102 | 0.026094 | 0.062929 | 0.049449 | 0.00028346
10/23/2022 | 3:23 | 0 | 0.092 | 0.002 | 0.101 | 0.026567 | 0.062598 | 0.047197 | 0.00028346
10/23/2022 | 3:23 | 0 | 0.092 | 0.002 | 0.101 | 0.026882 | 0.062409 | 0.045386 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.092 | 0.002 | 0.101 | 0.027134 | 0.062331 | 0.043984 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.092 | 0.002 | 0.101 | 0.027354 | 0.062346 | 0.043071 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.091 | 0.002 | 0.101 | 0.027559 | 0.062441 | 0.042614 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.091 | 0.002 | 0.101 | 0.027701 | 0.062551 | 0.04263 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.091 | 0.002 | 0.1 | 0.02778 | 0.062661 | 0.043102 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.091 | 0.002 | 0.1 | 0.027811 | 0.062709 | 0.043969 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.091 | 0.002 | 0.1 | 0.027795 | 0.062693 | 0.045197 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.091 | 0.002 | 0.1 | 0.02778 | 0.062567 | 0.046614 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.09 | 0.002 | 0.1 | 0.02778 | 0.062378 | 0.048126 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.09 | 0.002 | 0.1 | 0.02778 | 0.062126 | 0.049622 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.09 | 0.002 | 0.099 | 0.027811 | 0.061811 | 0.051039 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.09 | 0.002 | 0.099 | 0.027827 | 0.061449 | 0.052378 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.09 | 0.002 | 0.099 | 0.027843 | 0.061024 | 0.053622 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.09 | 0.002 | 0.099 | 0.027858 | 0.060567 | 0.054756 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.09 | 0.002 | 0.099 | 0.027858 | 0.060079 | 0.055732 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.089 | 0.002 | 0.099 | 0.027843 | 0.059591 | 0.056567 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.089 | 0.002 | 0.098 | 0.027795 | 0.05915 | 0.057197 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.089 | 0.002 | 0.098 | 0.027701 | 0.058772 | 0.057638 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.089 | 0.002 | 0.098 | 0.027591 | 0.058488 | 0.057906 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.089 | 0.002 | 0.098 | 0.027465 | 0.058346 | 0.058047 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.088 | 0.002 | 0.098 | 0.027307 | 0.058331 | 0.058079 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.088 | 0.001 | 0.098 | 0.027118 | 0.058457 | 0.058047 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.088 | 0.001 | 0.098 | 0.026882 | 0.058709 | 0.057937 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.088 | 0.001 | 0.097 | 0.026614 | 0.059087 | 0.057764 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.088 | 0.001 | 0.097 | 0.026283 | 0.059559 | 0.057559 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.088 | 0.001 | 0.097 | 0.025937 | 0.060047 | 0.057307 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.088 | 0.001 | 0.097 | 0.025559 | 0.060551 | 0.057087 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.088 | 0.001 | 0.097 | 0.025197 | 0.061039 | 0.056882 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.087 | 0.001 | 0.096 | 0.024866 | 0.061512 | 0.056709 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.087 | 0.001 | 0.096 | 0.024567 | 0.061937 | 0.056583 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.087 | 0.001 | 0.096 | 0.024299 | 0.062315 | 0.056488 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.087 | 0.001 | 0.096 | 0.024079 | 0.062614 | 0.056425 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.087 | 0.001 | 0.096 | 0.023874 | 0.062787 | 0.056394 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.087 | 0.001 | 0.096 | 0.023669 | 0.062803 | 0.056394 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.086 | 0.001 | 0.096 | 0.023496 | 0.062646 | 0.056409 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.086 | 0.001 | 0.096 | 0.023354 | 0.062331 | 0.056441 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.086 | 0.001 | 0.095 | 0.02326 | 0.061906 | 0.056472 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.086 | 0.001 | 0.095 | 0.023228 | 0.06137 | 0.056488 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.086 | 0.001 | 0.095 | 0.023244 | 0.060724 | 0.056504 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.086 | 0.001 | 0.095 | 0.023291 | 0.059969 | 0.05652 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.086 | 0.001 | 0.095 | 0.023323 | 0.059102 | 0.056535 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.086 | 0.001 | 0.094 | 0.023339 | 0.058126 | 0.056551 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.085 | 0.001 | 0.094 | 0.023307 | 0.057087 | 0.056551 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.085 | 0.001 | 0.094 | 0.023276 | 0.056063 | 0.05652 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.085 | 0.001 | 0.094 | 0.023228 | 0.055118 | 0.056457 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.085 | 0.001 | 0.094 | 0.023181 | 0.054268 | 0.056378 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.085 | 0.001 | 0.094 | 0.023118 | 0.053543 | 0.056299 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.085 | 0.001 | 0.094 | 0.023008 | 0.052913 | 0.05622 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.085 | 0.001 | 0.094 | 0.022819 | 0.052394 | 0.056157 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.084 | 0.001 | 0.093 | 0.022598 | 0.052031 | 0.05611 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.084 | 0.001 | 0.093 | 0.022331 | 0.051827 | 0.056079 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.084 | 0.001 | 0.093 | 0.022079 | 0.051811 | 0.056047 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.084 | 0.001 | 0.093 | 0.021843 | 0.051953 | 0.056031 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.084 | 0.001 | 0.093 | 0.021638 | 0.052283 | 0.056031 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.084 | 0.001 | 0.093 | 0.021449 | 0.05274 | 0.056047 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.084 | 0.001 | 0.093 | 0.021244 | 0.053323 | 0.056063 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.084 | 0.001 | 0.092 | 0.021055 | 0.053969 | 0.056094 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.083 | 0.001 | 0.092 | 0.02085 | 0.054646 | 0.056142 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.083 | 0.001 | 0.092 | 0.020661 | 0.055307 | 0.056173 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.083 | 0.001 | 0.092 | 0.02052 | 0.055921 | 0.056205 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.083 | 0.001 | 0.092 | 0.020441 | 0.056488 | 0.056252 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.083 | 0.001 | 0.092 | 0.020394 | 0.057008 | 0.056283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.083 | 0 | 0.092 | 0.020362 | 0.057465 | 0.056315 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.083 | 0 | 0.092 | 0.020362 | 0.057858 | 0.056315 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.082 | 0.001 | 0.091 | 0.020346 | 0.058126 | 0.056315 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.082 | 0.001 | 0.091 | 0.020346 | 0.058252 | 0.056315 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.082 | 0.001 | 0.091 | 0.020362 | 0.058252 | 0.056315 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.082 | 0.001 | 0.091 | 0.020378 | 0.058142 | 0.056331 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.082 | 0 | 0.091 | 0.020378 | 0.057953 | 0.056362 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.082 | 0 | 0.091 | 0.020378 | 0.057701 | 0.056409 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.082 | 0 | 0.091 | 0.020362 | 0.057417 | 0.056488 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.082 | 0 | 0.09 | 0.020331 | 0.057071 | 0.056598 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.081 | 0 | 0.09 | 0.020299 | 0.056693 | 0.05674 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.081 | 0 | 0.09 | 0.020283 | 0.056268 | 0.056929 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.081 | 0 | 0.09 | 0.020283 | 0.055858 | 0.05715 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.081 | 0 | 0.09 | 0.020283 | 0.055449 | 0.057386 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.081 | 0 | 0.09 | 0.020299 | 0.055087 | 0.057638 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.081 | 0.001 | 0.09 | 0.020331 | 0.054772 | 0.05789 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.081 | 0.001 | 0.09 | 0.020394 | 0.054535 | 0.05811 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.081 | 0.001 | 0.089 | 0.020504 | 0.054346 | 0.058331 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.081 | 0.001 | 0.089 | 0.020661 | 0.05422 | 0.058535 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.08 | 0.001 | 0.089 | 0.020882 | 0.054126 | 0.058693 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.08 | 0.001 | 0.089 | 0.021134 | 0.05411 | 0.058803 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.08 | 0.001 | 0.089 | 0.021417 | 0.054157 | 0.058882 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.08 | 0.001 | 0.089 | 0.021717 | 0.054236 | 0.058913 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.08 | 0.001 | 0.089 | 0.022031 | 0.054346 | 0.058929 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.08 | 0.001 | 0.088 | 0.022315 | 0.054472 | 0.058898 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.08 | 0.001 | 0.088 | 0.022598 | 0.054583 | 0.05885 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.08 | 0.001 | 0.088 | 0.022882 | 0.054693 | 0.058756 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.079 | 0.001 | 0.088 | 0.02315 | 0.054756 | 0.05863 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.079 | 0.001 | 0.088 | 0.023386 | 0.054787 | 0.058472 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.079 | 0.001 | 0.088 | 0.023606 | 0.054787 | 0.058283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.079 | 0.001 | 0.088 | 0.023764 | 0.05474 | 0.05811 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.079 | 0.001 | 0.088 | 0.023874 | 0.054661 | 0.057937 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.079 | 0.001 | 0.087 | 0.023969 | 0.054535 | 0.057827 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.079 | 0.001 | 0.087 | 0.024031 | 0.054378 | 0.057748 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.079 | 0.001 | 0.087 | 0.024079 | 0.054236 | 0.057732 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.079 | 0.001 | 0.087 | 0.02411 | 0.054142 | 0.057764 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.078 | 0.001 | 0.087 | 0.024126 | 0.054126 | 0.057858 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.078 | 0.001 | 0.087 | 0.024126 | 0.054205 | 0.058047 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.078 | 0.001 | 0.087 | 0.024126 | 0.054362 | 0.058346 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.078 | 0 | 0.087 | 0.024126 | 0.05463 | 0.058756 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.078 | 0 | 0.086 | 0.024126 | 0.055008 | 0.05926 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.078 | 0 | 0.086 | 0.024142 | 0.055496 | 0.059811 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.078 | 0 | 0.086 | 0.024157 | 0.056094 | 0.060409 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.078 | 0 | 0.086 | 0.024173 | 0.056787 | 0.061024 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.077 | 0 | 0.086 | 0.024189 | 0.057512 | 0.061622 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.077 | 0 | 0.086 | 0.024173 | 0.058205 | 0.06222 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.077 | 0 | 0.086 | 0.024173 | 0.058866 | 0.062772 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.077 | 0 | 0.086 | 0.024142 | 0.059433 | 0.06326 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.077 | 0 | 0.086 | 0.024094 | 0.059937 | 0.063654 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.077 | 0 | 0.085 | 0.023969 | 0.060362 | 0.063921 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.077 | 0 | 0.085 | 0.023764 | 0.060693 | 0.064094 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.077 | 0 | 0.085 | 0.023449 | 0.060913 | 0.06422 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.077 | 0 | 0.085 | 0.023008 | 0.061008 | 0.064283 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.076 | 0 | 0.085 | 0.022425 | 0.060961 | 0.064315 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.076 | 0 | 0.085 | 0.02178 | 0.060803 | 0.064331 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.076 | 0 | 0.085 | 0.021055 | 0.06052 | 0.064331 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.076 | 0 | 0.085 | 0.020283 | 0.060142 | 0.064331 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.076 | 0 | 0.084 | 0.01948 | 0.059669 | 0.064362 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.076 | 0 | 0.084 | 0.018583 | 0.059165 | 0.064425 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.076 | 0 | 0.084 | 0.017543 | 0.058646 | 0.064535 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.076 | 0 | 0.084 | 0.016362 | 0.058173 | 0.064677 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.076 | 0 | 0.084 | 0.015071 | 0.057748 | 0.064835 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.075 | 0 | 0.084 | 0.013858 | 0.05737 | 0.065008 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.075 | 0 | 0.084 | 0.01285 | 0.057039 | 0.065181 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.075 | 0 | 0.084 | 0.012157 | 0.056756 | 0.065339 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.075 | 0 | 0.083 | 0.011764 | 0.056551 | 0.065433 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.075 | 0 | 0.083 | 0.011575 | 0.056441 | 0.06548 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.075 | 0 | 0.083 | 0.011528 | 0.056394 | 0.065465 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.075 | 0 | 0.083 | 0.011591 | 0.056394 | 0.065354 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.075 | 0 | 0.083 | 0.011827 | 0.056441 | 0.065134 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.075 | 0 | 0.083 | 0.012346 | 0.056472 | 0.06474 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.074 | 0 | 0.083 | 0.013118 | 0.056488 | 0.064173 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.074 | 0 | 0.083 | 0.014079 | 0.056472 | 0.063433 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.074 | 0 | 0.083 | 0.015087 | 0.056394 | 0.062504 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.074 | 0 | 0.083 | 0.016031 | 0.056283 | 0.061386 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.074 | 0 | 0.082 | 0.01685 | 0.056094 | 0.060126 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.074 | 0 | 0.082 | 0.017543 | 0.055827 | 0.058756 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.074 | 0 | 0.082 | 0.018173 | 0.055528 | 0.057323 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.074 | 0 | 0.082 | 0.018772 | 0.055228 | 0.055827 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.073 | 0 | 0.082 | 0.019323 | 0.054913 | 0.054331 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.073 | 0 | 0.082 | 0.019764 | 0.054614 | 0.052882 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.073 | 0 | 0.082 | 0.020047 | 0.054362 | 0.051591 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.073 | 0 | 0.082 | 0.020126 | 0.054157 | 0.050488 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.073 | 0 | 0.081 | 0.020063 | 0.054 | 0.049669 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.073 | 0 | 0.081 | 0.019874 | 0.053921 | 0.049118 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.073 | 0 | 0.081 | 0.019622 | 0.053937 | 0.048819 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.073 | 0 | 0.081 | 0.019354 | 0.054047 | 0.048772 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.073 | 0 | 0.081 | 0.019102 | 0.054236 | 0.048961 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.073 | 0 | 0.081 | 0.018866 | 0.054535 | 0.04937 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.072 | 0 | 0.081 | 0.01863 | 0.054898 | 0.049953 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.072 | 0 | 0.081 | 0.018346 | 0.055307 | 0.050724 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.072 | 0 | 0.081 | 0.018047 | 0.055748 | 0.051638 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.072 | 0 | 0.081 | 0.017732 | 0.056189 | 0.05263 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.072 | 0 | 0.08 | 0.01748 | 0.056614 | 0.053669 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.072 | 0 | 0.08 | 0.017339 | 0.057024 | 0.05463 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.072 | 0 | 0.08 | 0.017339 | 0.057417 | 0.055512 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.072 | 0 | 0.08 | 0.01748 | 0.05778 | 0.056236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.071 | 0 | 0.08 | 0.017717 | 0.058079 | 0.056787 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.071 | 0 | 0.08 | 0.018031 | 0.058315 | 0.057197 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.071 | 0 | 0.08 | 0.018362 | 0.058425 | 0.057449 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.071 | 0 | 0.08 | 0.018677 | 0.058425 | 0.057559 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.071 | 0 | 0.079 | 0.019024 | 0.058315 | 0.05748 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.071 | 0 | 0.079 | 0.019386 | 0.058126 | 0.057197 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.071 | 0 | 0.079 | 0.01978 | 0.057874 | 0.056724 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.071 | 0 | 0.079 | 0.020205 | 0.057528 | 0.056047 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.071 | 0 | 0.079 | 0.02063 | 0.057134 | 0.055228 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.071 | 0 | 0.079 | 0.021008 | 0.056661 | 0.054331 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.071 | 0 | 0.079 | 0.021339 | 0.056157 | 0.05337 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.071 | 0 | 0.079 | 0.021606 | 0.055638 | 0.052394 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.071 | 0 | 0.079 | 0.021827 | 0.05515 | 0.05137 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.07 | 0 | 0.079 | 0.021984 | 0.054724 | 0.050378 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.07 | 0 | 0.078 | 0.022126 | 0.054362 | 0.049433 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.07 | 0 | 0.078 | 0.02222 | 0.054063 | 0.048598 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.07 | 0 | 0.078 | 0.022299 | 0.053811 | 0.047953 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.07 | 0 | 0.078 | 0.022346 | 0.053622 | 0.047496 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.07 | 0 | 0.078 | 0.022362 | 0.053528 | 0.047228 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.07 | 0 | 0.078 | 0.022362 | 0.053496 | 0.04715 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.07 | 0 | 0.078 | 0.022362 | 0.053543 | 0.047228 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.07 | 0 | 0.078 | 0.022362 | 0.053654 | 0.047449 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.07 | 0 | 0.078 | 0.022362 | 0.053795 | 0.047764 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.07 | 0 | 0.077 | 0.022362 | 0.053984 | 0.048173 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.07 | 0 | 0.077 | 0.022362 | 0.054189 | 0.048646 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.069 | 0 | 0.077 | 0.022378 | 0.054409 | 0.049165 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.069 | 0 | 0.077 | 0.022394 | 0.05463 | 0.049732 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.069 | 0 | 0.077 | 0.022409 | 0.054819 | 0.050283 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.069 | 0 | 0.077 | 0.022441 | 0.054992 | 0.050819 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.069 | 0 | 0.077 | 0.022441 | 0.055118 | 0.051323 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.069 | 0 | 0.077 | 0.022409 | 0.055228 | 0.05178 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.069 | 0 | 0.077 | 0.022346 | 0.055307 | 0.052142 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.069 | 0 | 0.077 | 0.022236 | 0.055386 | 0.052441 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.069 | 0 | 0.077 | 0.022094 | 0.055433 | 0.052646 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.069 | 0 | 0.077 | 0.021937 | 0.055465 | 0.052803 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.069 | 0 | 0.076 | 0.02178 | 0.055465 | 0.052898 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.068 | 0 | 0.076 | 0.021575 | 0.055465 | 0.052929 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.068 | 0 | 0.076 | 0.021339 | 0.055449 | 0.052929 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.068 | 0 | 0.076 | 0.021055 | 0.055449 | 0.052866 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.068 | 0 | 0.076 | 0.020709 | 0.055433 | 0.052772 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.068 | 0 | 0.076 | 0.020315 | 0.055417 | 0.052646 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.068 | 0 | 0.076 | 0.019921 | 0.055417 | 0.052488 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.068 | 0 | 0.076 | 0.019512 | 0.055433 | 0.052346 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.068 | 0 | 0.076 | 0.01915 | 0.055433 | 0.052189 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.068 | 0 | 0.075 | 0.018803 | 0.055433 | 0.052063 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.068 | 0 | 0.075 | 0.018472 | 0.055449 | 0.051937 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.068 | 0 | 0.075 | 0.018126 | 0.055449 | 0.051843 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.067 | 0 | 0.075 | 0.017827 | 0.055465 | 0.05178 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.067 | 0 | 0.075 | 0.017575 | 0.05548 | 0.051717 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.067 | 0 | 0.075 | 0.017417 | 0.055465 | 0.051685 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.068 | 0 | 0.075 | 0.017528 | 0.057449 | 0.051701 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.068 | 0 | 0.075 | 0.017528 | 0.05748 | 0.051701 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.068 | 0 | 0.075 | 0.018346 | 0.057622 | 0.052189 | 0.00029921
10/23/2022 | 3:23 | 0 | 0.068 | 0 | 0.075 | 0.019937 | 0.057575 | 0.05315 | 0.00033071
10/23/2022 | 3:23 | 0 | 0.067 | 0 | 0.075 | 0.020866 | 0.057291 | 0.053969 | 0.00033071
10/23/2022 | 3:23 | 0 | 0.067 | 0 | 0.075 | 0.021339 | 0.057102 | 0.054504 | 0.00033071
10/23/2022 | 3:23 | 0 | 0.067 | 0 | 0.075 | 0.021339 | 0.057276 | 0.054283 | 0.00033071
10/23/2022 | 3:23 | 0 | 0.067 | 0 | 0.075 | 0.021512 | 0.057874 | 0.053402 | 0.00034646
10/23/2022 | 3:23 | 0 | 0.067 | 0 | 0.075 | 0.021937 | 0.058614 | 0.052063 | 0.00034646
10/23/2022 | 3:23 | 0 | 0.067 | 0 | 0.075 | 0.022016 | 0.058866 | 0.050898 | 0.00034646
10/23/2022 | 3:23 | 0 | 0.067 | 0 | 0.075 | 0.022079 | 0.058457 | 0.050598 | 0.00034646
10/23/2022 | 3:23 | 0 | 0.067 | 0 | 0.075 | 0.02263 | 0.057465 | 0.051339 | 0.00034646
10/23/2022 | 3:23 | 0 | 0.067 | 0 | 0.075 | 0.023402 | 0.056315 | 0.052614 | 0.00034646
10/23/2022 | 3:23 | 0 | 0.067 | 0 | 0.075 | 0.023606 | 0.05537 | 0.053339 | 0.00034646
10/23/2022 | 3:23 | 0 | 0.067 | 0 | 0.075 | 0.023528 | 0.054961 | 0.05326 | 0.00034646
10/23/2022 | 3:23 | 0 | 0.067 | 0 | 0.074 | 0.023969 | 0.055134 | 0.052772 | 0.00034646
10/23/2022 | 3:23 | 0 | 0.067 | 0 | 0.074 | 0.024945 | 0.05548 | 0.052346 | 0.00034646
10/23/2022 | 3:23 | 0 | 0.067 | 0 | 0.074 | 0.025669 | 0.055575 | 0.052126 | 0.00034646
10/23/2022 | 3:23 | 0 | 0.067 | 0 | 0.074 | 0.025732 | 0.055622 | 0.052079 | 0.00034646
10/23/2022 | 3:23 | 0 | 0.066 | 0 | 0.074 | 0.02548 | 0.055575 | 0.052079 | 0.00034646
10/23/2022 | 3:23 | 0 | 0.066 | 0 | 0.074 | 0.025622 | 0.055606 | 0.052425 | 0.00034646
10/23/2022 | 3:23 | 0 | 0.066 | 0 | 0.074 | 0.025228 | 0.055181 | 0.052283 | 0.00033071
10/23/2022 | 3:23 | 0 | 0.066 | 0 | 0.074 | 0.024598 | 0.054614 | 0.05189 | 0.00033071
10/23/2022 | 3:23 | 0 | 0.066 | 0 | 0.074 | 0.023969 | 0.053496 | 0.051291 | 0.00033071
10/23/2022 | 3:23 | 0 | 0.066 | 0 | 0.074 | 0.023417 | 0.05222 | 0.050709 | 0.00034646
10/23/2022 | 3:23 | 0 | 0.066 | 0 | 0.074 | 0.022961 | 0.050709 | 0.050236 | 0.00034646
10/23/2022 | 3:23 | 0 | 0.066 | 0 | 0.074 | 0.022567 | 0.049181 | 0.049764 | 0.00034646
10/23/2022 | 3:23 | 0 | 0.066 | 0 | 0.074 | 0.022189 | 0.047843 | 0.049213 | 0.00034646
10/23/2022 | 3:23 | 0 | 0.066 | 0 | 0.074 | 0.021874 | 0.046866 | 0.04863 | 0.0003622
10/23/2022 | 3:23 | 0 | 0.066 | 0 | 0.074 | 0.021669 | 0.046189 | 0.048142 | 0.0003622
10/23/2022 | 3:23 | 0 | 0.066 | 0 | 0.074 | 0.021654 | 0.045732 | 0.04778 | 0.00034646
10/23/2022 | 3:23 | 0 | 0.066 | 0 | 0.074 | 0.02178 | 0.04548 | 0.047591 | 0.00034646
10/23/2022 | 3:23 | 0 | 0.065 | 0 | 0.073 | 0.021795 | 0.042913 | 0.047528 | 0.00034646
10/23/2022 | 3:23 | 0 | 0.065 | 0 | 0.073 | 0.021969 | 0.043055 | 0.047591 | 0.00034646
10/23/2022 | 3:23 | 0 | 0.065 | 0 | 0.073 | 0.02148 | 0.04326 | 0.047118 | 0.00031496
10/23/2022 | 3:23 | 0 | 0.065 | 0 | 0.073 | 0.020346 | 0.043795 | 0.046189 | 0.00029921
10/23/2022 | 3:23 | 0 | 0.065 | 0 | 0.073 | 0.019843 | 0.044646 | 0.045559 | 0.00028346
10/23/2022 | 3:23 | 0 | 0.065 | 0 | 0.073 | 0.019843 | 0.045276 | 0.045386 | 0.00028346
10/23/2022 | 3:23 | 0 | 0.065 | 0 | 0.073 | 0.020378 | 0.04526 | 0.046142 | 0.00029921
10/23/2022 | 3:23 | 0 | 0.064 | 0 | 0.072 | 0.020661 | 0.04463 | 0.047496 | 0.00028346
10/23/2022 | 3:23 | 0 | 0.064 | 0 | 0.072 | 0.020598 | 0.043953 | 0.049134 | 0.00029921
10/23/2022 | 3:23 | 0 | 0.064 | 0 | 0.072 | 0.020787 | 0.044031 | 0.050378 | 0.00029921
10/23/2022 | 3:23 | 0 | 0.064 | 0 | 0.072 | 0.020929 | 0.044961 | 0.050614 | 0.00029921
10/23/2022 | 3:23 | 0 | 0.064 | 0 | 0.072 | 0.020488 | 0.046315 | 0.049795 | 0.00029921
10/23/2022 | 3:23 | 0 | 0.064 | 0 | 0.072 | 0.019717 | 0.047528 | 0.048457 | 0.00029921
10/23/2022 | 3:23 | 0 | 0.064 | 0 | 0.072 | 0.019512 | 0.048346 | 0.047764 | 0.00029921
10/23/2022 | 3:23 | 0 | 0.064 | 0 | 0.072 | 0.019496 | 0.04852 | 0.047984 | 0.00029921
10/23/2022 | 3:23 | 0 | 0.064 | 0 | 0.072 | 0.018756 | 0.048079 | 0.048551 | 0.00029921
10/23/2022 | 3:23 | 0 | 0.064 | 0 | 0.072 | 0.017228 | 0.047559 | 0.048945 | 0.00029921
10/23/2022 | 3:23 | 0 | 0.064 | 0 | 0.071 | 0.015921 | 0.047417 | 0.049071 | 0.00029921
10/23/2022 | 3:23 | 0 | 0.064 | 0 | 0.071 | 0.015669 | 0.047433 | 0.049087 | 0.00028346
10/23/2022 | 3:23 | 0 | 0.063 | 0 | 0.071 | 0.016094 | 0.047732 | 0.049087 | 0.00028346
10/23/2022 | 3:23 | 0 | 0.063 | 0 | 0.071 | 0.015165 | 0.047827 | 0.048661 | 0.00028346
10/23/2022 | 3:23 | 0 | 0.063 | 0 | 0.071 | 0.014866 | 0.048646 | 0.048583 | 0.00029921
10/23/2022 | 3:23 | 0 | 0.063 | 0 | 0.071 | 0.014929 | 0.050189 | 0.04885 | 0.00029921
10/23/2022 | 3:23 | 0 | 0.063 | 0 | 0.071 | 0.015071 | 0.051827 | 0.049307 | 0.00029921
10/23/2022 | 3:23 | 0 | 0.063 | 0 | 0.071 | 0.015764 | 0.053669 | 0.050126 | 0.00028346
10/23/2022 | 3:23 | 0 | 0.063 | 0 | 0.071 | 0.016961 | 0.055354 | 0.051402 | 0.00029921
10/23/2022 | 3:23 | 0 | 0.063 | 0 | 0.071 | 0.018157 | 0.056898 | 0.052772 | 0.00029921
10/23/2022 | 3:23 | 0 | 0.063 | 0 | 0.071 | 0.019024 | 0.05822 | 0.05411 | 0.00029921
10/23/2022 | 3:23 | 0 | 0.063 | 0 | 0.071 | 0.019307 | 0.059622 | 0.054898 | 0.00029921
10/23/2022 | 3:23 | 0 | 0.063 | 0 | 0.071 | 0.019339 | 0.061118 | 0.055339 | 0.00029921
10/23/2022 | 3:23 | 0 | 0.063 | 0 | 0.071 | 0.019197 | 0.062535 | 0.055606 | 0.00029921
10/23/2022 | 3:23 | 0 | 0.063 | 0 | 0.07 | 0.019008 | 0.06348 | 0.055732 | 0.00031496
10/23/2022 | 3:23 | 0 | 0.063 | 0 | 0.07 | 0.018835 | 0.063811 | 0.055827 | 0.00031496
10/23/2022 | 3:23 | 0 | 0.063 | 0 | 0.07 | 0.01863 | 0.063748 | 0.055811 | 0.00029921
10/23/2022 | 3:23 | 0 | 0.062 | 0 | 0.07 | 0.018457 | 0.063433 | 0.055685 | 0.00029921
10/23/2022 | 3:23 | 0 | 0.062 | 0 | 0.07 | 0.018126 | 0.062945 | 0.055339 | 0.00031496
10/23/2022 | 3:23 | 0 | 0.062 | 0 | 0.07 | 0.017638 | 0.062236 | 0.054819 | 0.00031496
10/23/2022 | 3:23 | 0 | 0.062 | 0 | 0.07 | 0.017213 | 0.061323 | 0.054268 | 0.00031496
10/23/2022 | 3:23 | 0 | 0.062 | 0 | 0.07 | 0.016898 | 0.060236 | 0.053874 | 0.00031496
10/23/2022 | 3:23 | 0 | 0.062 | 0 | 0.07 | 0.016677 | 0.059008 | 0.053496 | 0.00031496
10/23/2022 | 3:23 | 0 | 0.062 | 0 | 0.07 | 0.016378 | 0.057732 | 0.052929 | 0.00029921
10/23/2022 | 3:23 | 0 | 0.062 | 0 | 0.07 | 0.016047 | 0.056598 | 0.05211 | 0.00029921
10/23/2022 | 3:23 | 0 | 0.062 | 0 | 0.07 | 0.015764 | 0.055717 | 0.051118 | 0.00029921
10/23/2022 | 3:23 | 0 | 0.062 | 0 | 0.07 | 0.015559 | 0.055039 | 0.050126 | 0.00029921
10/23/2022 | 3:23 | 0 | 0.062 | 0 | 0.069 | 0.015402 | 0.054394 | 0.049276 | 0.00031496
10/23/2022 | 3:23 | 0 | 0.062 | 0 | 0.069 | 0.015323 | 0.053748 | 0.048646 | 0.00031496
10/23/2022 | 3:23 | 0 | 0.062 | 0 | 0.069 | 0.015307 | 0.053213 | 0.048268 | 0.00031496
10/23/2022 | 3:23 | 0 | 0.062 | 0 | 0.069 | 0.015307 | 0.052913 | 0.048047 | 0.00031496
10/23/2022 | 3:23 | 0 | 0.062 | 0 | 0.069 | 0.015402 | 0.05285 | 0.047858 | 0.00031496
10/23/2022 | 3:23 | 0 | 0.061 | 0 | 0.069 | 0.015701 | 0.052992 | 0.047748 | 0.00031496
10/23/2022 | 3:23 | 0 | 0.061 | 0 | 0.069 | 0.016299 | 0.053197 | 0.047795 | 0.00031496
10/23/2022 | 3:23 | 0 | 0.061 | 0 | 0.069 | 0.016945 | 0.053402 | 0.048063 | 0.00033071
10/23/2022 | 3:23 | 0 | 0.061 | 0 | 0.069 | 0.018031 | 0.054031 | 0.048567 | 0.00033071
10/23/2022 | 3:23 | 0 | 0.061 | 0 | 0.068 | 0.018882 | 0.054992 | 0.049276 | 0.00031496
10/23/2022 | 3:23 | 0 | 0.061 | 0 | 0.068 | 0.019402 | 0.055984 | 0.04989 | 0.00033071
10/23/2022 | 3:23 | 0 | 0.061 | 0 | 0.068 | 0.019764 | 0.057606 | 0.050535 | 0.00033071
10/23/2022 | 3:23 | 0 | 0.061 | 0 | 0.068 | 0.019843 | 0.059008 | 0.050976 | 0.00033071
10/23/2022 | 3:23 | 0 | 0.061 | 0 | 0.068 | 0.019748 | 0.060378 | 0.051181 | 0.00031496
10/23/2022 | 3:23 | 0 | 0.061 | 0 | 0.068 | 0.019874 | 0.061512 | 0.051622 | 0.00031496
10/23/2022 | 3:23 | 0 | 0.06 | 0 | 0.068 | 0.020252 | 0.062488 | 0.052268 | 0.00031496
10/23/2022 | 3:23 | 0 | 0.06 | 0 | 0.068 | 0.020866 | 0.063039 | 0.053228 | 0.00031496
10/23/2022 | 3:23 | 0 | 0.06 | 0 | 0.068 | 0.021276 | 0.063307 | 0.054016 | 0.00031496
10/23/2022 | 3:23 | 0 | 0.06 | 0 | 0.067 | 0.021417 | 0.06348 | 0.054535 | 0.00031496
10/23/2022 | 3:23 | 0 | 0.06 | 0 | 0.067 | 0.021417 | 0.063827 | 0.05485 | 0.00031496
10/23/2022 | 3:23 | 0 | 0.06 | 0 | 0.067 | 0.021417 | 0.064252 | 0.055008 | 0.00031496
10/23/2022 | 3:23 | 0 | 0.06 | 0 | 0.067 | 0.021417 | 0.064472 | 0.055087 | 0.00033071
10/23/2022 | 3:23 | 0 | 0.06 | 0 | 0.067 | 0.021417 | 0.064504 | 0.055118 | 0.00033071
10/23/2022 | 3:23 | 0 | 0.06 | 0 | 0.067 | 0.021449 | 0.064457 | 0.055102 | 0.00031496
10/23/2022 | 3:23 | 0 | 0.06 | 0 | 0.067 | 0.021465 | 0.064394 | 0.054945 | 0.00031496
10/23/2022 | 3:23 | 0 | 0.06 | 0 | 0.067 | 0.021323 | 0.064346 | 0.054583 | 0.00031496
10/23/2022 | 3:23 | 0 | 0.06 | 0 | 0.067 | 0.021118 | 0.064315 | 0.054016 | 0.00031496
10/23/2022 | 3:23 | 0 | 0.059 | 0 | 0.067 | 0.020929 | 0.064283 | 0.053528 | 0.00031496
10/23/2022 | 3:23 | 0 | 0.059 | 0 | 0.067 | 0.020866 | 0.064126 | 0.053228 | 0.00031496
10/23/2022 | 3:23 | 0 | 0.059 | 0 | 0.067 | 0.020866 | 0.063827 | 0.053024 | 0.00031496
10/23/2022 | 3:23 | 0 | 0.059 | 0 | 0.066 | 0.020866 | 0.063465 | 0.052819 | 0.00031496
10/23/2022 | 3:23 | 0 | 0.059 | 0 | 0.066 | 0.020882 | 0.06326 | 0.052504 | 0.00031496
10/23/2022 | 3:23 | 0 | 0.059 | 0 | 0.066 | 0.020961 | 0.06326 | 0.052126 | 0.00029921
10/23/2022 | 3:23 | 0 | 0.059 | 0 | 0.066 | 0.021039 | 0.063307 | 0.051685 | 0.00029921
10/23/2022 | 3:23 | 0 | 0.059 | 0 | 0.066 | 0.021118 | 0.063323 | 0.051244 | 0.00029921
10/23/2022 | 3:23 | 0 | 0.059 | 0 | 0.066 | 0.021197 | 0.063323 | 0.050929 | 0.00029921
10/23/2022 | 3:23 | 0 | 0.059 | 0 | 0.066 | 0.021244 | 0.063339 | 0.050803 | 0.00029921
10/23/2022 | 3:23 | 0 | 0.059 | 0 | 0.066 | 0.021228 | 0.063386 | 0.050803 | 0.00029921
10/23/2022 | 3:23 | 0 | 0.059 | 0 | 0.066 | 0.021181 | 0.06348 | 0.050819 | 0.00028346
10/23/2022 | 3:23 | 0 | 0.058 | 0 | 0.066 | 0.021213 | 0.063559 | 0.050945 | 0.00028346
10/23/2022 | 3:23 | 0 | 0.058 | 0 | 0.066 | 0.021433 | 0.063528 | 0.051197 | 0.00028346
10/23/2022 | 3:23 | 0 | 0.058 | 0 | 0.066 | 0.021811 | 0.063291 | 0.051575 | 0.00028346
10/23/2022 | 3:23 | 0 | 0.058 | 0 | 0.066 | 0.022173 | 0.062882 | 0.051969 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.058 | 0 | 0.065 | 0.022409 | 0.062472 | 0.052331 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.058 | 0 | 0.065 | 0.022425 | 0.062236 | 0.052598 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.058 | 0 | 0.065 | 0.022283 | 0.062094 | 0.052709 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.058 | 0 | 0.065 | 0.022016 | 0.061937 | 0.052693 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.058 | 0 | 0.065 | 0.021843 | 0.061622 | 0.052661 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.058 | 0 | 0.065 | 0.021795 | 0.061197 | 0.052787 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.058 | 0 | 0.065 | 0.021843 | 0.06063 | 0.053039 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.058 | 0 | 0.065 | 0.021906 | 0.060016 | 0.05326 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.058 | 0 | 0.065 | 0.021906 | 0.059449 | 0.053354 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.058 | 0 | 0.065 | 0.021906 | 0.059039 | 0.053354 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.058 | 0 | 0.065 | 0.02189 | 0.05885 | 0.053323 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.058 | 0 | 0.065 | 0.021843 | 0.058803 | 0.053291 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.057 | 0 | 0.065 | 0.021795 | 0.058913 | 0.053291 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.057 | 0 | 0.065 | 0.021764 | 0.059181 | 0.053323 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.057 | 0 | 0.064 | 0.02178 | 0.059638 | 0.053354 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.057 | 0 | 0.064 | 0.021795 | 0.06022 | 0.053339 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.057 | 0 | 0.064 | 0.021858 | 0.06085 | 0.05337 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.057 | 0 | 0.064 | 0.022 | 0.061496 | 0.053512 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.057 | 0 | 0.064 | 0.022173 | 0.062126 | 0.053811 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.057 | 0 | 0.064 | 0.022299 | 0.062772 | 0.054205 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.057 | 0 | 0.064 | 0.022299 | 0.063417 | 0.054551 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.057 | 0 | 0.064 | 0.02222 | 0.06411 | 0.054803 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.057 | 0 | 0.064 | 0.022142 | 0.064772 | 0.054976 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.057 | 0 | 0.064 | 0.022079 | 0.065323 | 0.055102 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.057 | 0 | 0.064 | 0.022 | 0.065606 | 0.055228 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.057 | 0 | 0.064 | 0.021858 | 0.065638 | 0.055339 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.056 | 0 | 0.064 | 0.021591 | 0.065496 | 0.055386 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.056 | 0 | 0.064 | 0.021102 | 0.065197 | 0.055307 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.056 | 0 | 0.063 | 0.020394 | 0.06474 | 0.055055 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.056 | 0 | 0.063 | 0.019575 | 0.064079 | 0.054724 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.056 | 0 | 0.063 | 0.018835 | 0.06315 | 0.054378 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.056 | 0 | 0.063 | 0.018236 | 0.061921 | 0.054031 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.056 | 0 | 0.063 | 0.017732 | 0.060441 | 0.053638 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.056 | 0 | 0.063 | 0.01715 | 0.05885 | 0.053134 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.056 | 0 | 0.063 | 0.016425 | 0.057307 | 0.052472 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.056 | 0 | 0.063 | 0.015465 | 0.05589 | 0.051654 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.056 | 0 | 0.063 | 0.014362 | 0.054614 | 0.050787 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.056 | 0 | 0.063 | 0.013307 | 0.053433 | 0.05 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.056 | 0 | 0.063 | 0.012567 | 0.052346 | 0.049402 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.056 | 0 | 0.063 | 0.01222 | 0.051354 | 0.049008 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.056 | 0 | 0.063 | 0.012236 | 0.050567 | 0.048756 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.056 | 0 | 0.062 | 0.012504 | 0.050079 | 0.048598 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.056 | 0 | 0.062 | 0.012945 | 0.049953 | 0.048504 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.055 | 0 | 0.062 | 0.013417 | 0.050126 | 0.04852 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.055 | 0 | 0.062 | 0.013827 | 0.050583 | 0.048614 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.055 | 0 | 0.062 | 0.014189 | 0.05126 | 0.048787 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.055 | 0 | 0.062 | 0.014567 | 0.052157 | 0.049008 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.055 | 0 | 0.062 | 0.014992 | 0.053213 | 0.04926 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.055 | 0 | 0.062 | 0.015512 | 0.054315 | 0.049512 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.055 | 0 | 0.062 | 0.016126 | 0.055354 | 0.049827 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.055 | 0 | 0.062 | 0.016819 | 0.056252 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.055 | 0 | 0.062 | 0.01748 | 0.057039 | 0.05074 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.055 | 0 | 0.062 | 0.017953 | 0.057764 | 0.051228 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.055 | 0 | 0.062 | 0.018189 | 0.058457 | 0.051622 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.055 | 0 | 0.062 | 0.018283 | 0.059134 | 0.05189 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.055 | 0 | 0.061 | 0.018315 | 0.059748 | 0.052047 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.054 | 0 | 0.061 | 0.018346 | 0.060189 | 0.052157 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.054 | 0 | 0.061 | 0.018378 | 0.060441 | 0.052252 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.054 | 0 | 0.061 | 0.018378 | 0.06052 | 0.052315 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.054 | 0 | 0.061 | 0.018283 | 0.060488 | 0.052331 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.054 | 0 | 0.061 | 0.018031 | 0.060409 | 0.052236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.054 | 0 | 0.061 | 0.017638 | 0.060283 | 0.052079 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.054 | 0 | 0.061 | 0.017228 | 0.060063 | 0.051874 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.054 | 0 | 0.061 | 0.016913 | 0.059764 | 0.051685 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.054 | 0 | 0.061 | 0.016693 | 0.05937 | 0.051559 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.054 | 0 | 0.061 | 0.016551 | 0.058961 | 0.051417 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.054 | 0 | 0.061 | 0.016409 | 0.058614 | 0.051228 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.054 | 0 | 0.061 | 0.016268 | 0.058378 | 0.050976 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.054 | 0 | 0.061 | 0.016079 | 0.058236 | 0.050677 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.054 | 0 | 0.061 | 0.01589 | 0.058157 | 0.050378 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.054 | 0 | 0.061 | 0.015795 | 0.058079 | 0.050189 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.054 | 0 | 0.06 | 0.015795 | 0.058 | 0.050094 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.053 | 0 | 0.06 | 0.015858 | 0.057953 | 0.050063 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.053 | 0 | 0.06 | 0.015969 | 0.057937 | 0.050047 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.053 | 0 | 0.06 | 0.016142 | 0.057937 | 0.050031 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.053 | 0 | 0.06 | 0.016394 | 0.057937 | 0.050063 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.053 | 0 | 0.06 | 0.016677 | 0.057874 | 0.05011 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.053 | 0 | 0.06 | 0.016945 | 0.057764 | 0.050189 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.053 | 0 | 0.06 | 0.017118 | 0.057622 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.053 | 0 | 0.06 | 0.017228 | 0.057512 | 0.050299 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.053 | 0 | 0.06 | 0.017276 | 0.057417 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.053 | 0 | 0.06 | 0.017276 | 0.057291 | 0.05022 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.053 | 0 | 0.06 | 0.017307 | 0.057118 | 0.050205 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.053 | 0 | 0.06 | 0.017433 | 0.056835 | 0.050252 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.053 | 0 | 0.06 | 0.017575 | 0.056457 | 0.050346 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.053 | 0 | 0.06 | 0.017701 | 0.056047 | 0.050441 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.053 | 0 | 0.06 | 0.017732 | 0.055685 | 0.050488 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.053 | 0 | 0.059 | 0.017732 | 0.055386 | 0.050472 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.053 | 0 | 0.059 | 0.017717 | 0.055213 | 0.050409 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.053 | 0 | 0.059 | 0.017685 | 0.055102 | 0.050362 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.053 | 0 | 0.059 | 0.017669 | 0.055039 | 0.050346 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.052 | 0 | 0.059 | 0.017654 | 0.055055 | 0.050331 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.052 | 0 | 0.059 | 0.017654 | 0.05515 | 0.050331 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.052 | 0 | 0.059 | 0.017654 | 0.055307 | 0.050315 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.052 | 0 | 0.059 | 0.017654 | 0.055528 | 0.050315 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.052 | 0 | 0.059 | 0.017685 | 0.05578 | 0.050346 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.052 | 0 | 0.059 | 0.017764 | 0.056047 | 0.050425 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.052 | 0 | 0.059 | 0.017827 | 0.056331 | 0.050551 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.052 | 0 | 0.059 | 0.017874 | 0.056646 | 0.050661 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.052 | 0 | 0.059 | 0.01789 | 0.057008 | 0.05074 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.052 | 0 | 0.059 | 0.017906 | 0.057386 | 0.05074 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.052 | 0 | 0.059 | 0.017906 | 0.057748 | 0.050724 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.052 | 0 | 0.059 | 0.017906 | 0.058 | 0.050724 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.052 | 0 | 0.058 | 0.017906 | 0.058189 | 0.05074 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.052 | 0 | 0.058 | 0.017827 | 0.058283 | 0.050787 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.052 | 0 | 0.058 | 0.017685 | 0.058331 | 0.050835 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.052 | 0 | 0.058 | 0.017465 | 0.058315 | 0.050835 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.051 | 0 | 0.058 | 0.017276 | 0.05822 | 0.050819 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.051 | 0 | 0.058 | 0.017134 | 0.058016 | 0.050819 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.051 | 0 | 0.058 | 0.017024 | 0.057685 | 0.050819 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.051 | 0 | 0.058 | 0.016913 | 0.057276 | 0.050819 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.051 | 0 | 0.058 | 0.01674 | 0.05685 | 0.050787 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.051 | 0 | 0.058 | 0.016488 | 0.056457 | 0.050693 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.051 | 0 | 0.058 | 0.016142 | 0.056063 | 0.050535 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.051 | 0 | 0.058 | 0.015748 | 0.055701 | 0.050378 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.051 | 0 | 0.058 | 0.015433 | 0.055291 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.051 | 0 | 0.058 | 0.015213 | 0.05485 | 0.050173 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.051 | 0 | 0.058 | 0.015087 | 0.054378 | 0.050157 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.051 | 0 | 0.058 | 0.015008 | 0.053937 | 0.050126 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.051 | 0 | 0.057 | 0.014961 | 0.053606 | 0.050094 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.051 | 0 | 0.057 | 0.014945 | 0.05337 | 0.050047 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.051 | 0 | 0.057 | 0.014929 | 0.05326 | 0.049984 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.051 | 0 | 0.057 | 0.014913 | 0.053228 | 0.049953 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.051 | 0 | 0.057 | 0.014913 | 0.053276 | 0.049937 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.051 | 0 | 0.057 | 0.014961 | 0.053402 | 0.049953 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.051 | 0 | 0.057 | 0.015024 | 0.053591 | 0.049969 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.051 | 0 | 0.057 | 0.015134 | 0.053843 | 0.049984 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.05 | 0 | 0.057 | 0.01526 | 0.054126 | 0.050031 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.05 | 0 | 0.057 | 0.015433 | 0.054394 | 0.050126 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.05 | 0 | 0.057 | 0.015606 | 0.054646 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.05 | 0 | 0.057 | 0.015732 | 0.054898 | 0.050378 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.05 | 0 | 0.057 | 0.015827 | 0.05515 | 0.050504 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.05 | 0 | 0.057 | 0.01589 | 0.055417 | 0.050583 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.05 | 0 | 0.057 | 0.015921 | 0.055685 | 0.050614 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.05 | 0 | 0.057 | 0.015953 | 0.055921 | 0.050646 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.05 | 0 | 0.056 | 0.015953 | 0.056079 | 0.050661 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.05 | 0 | 0.056 | 0.015921 | 0.056173 | 0.050693 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.05 | 0 | 0.056 | 0.015827 | 0.05622 | 0.050724 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.05 | 0 | 0.056 | 0.015669 | 0.05622 | 0.05074 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.05 | 0 | 0.056 | 0.01548 | 0.056189 | 0.050724 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.05 | 0 | 0.056 | 0.015307 | 0.056126 | 0.050709 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.05 | 0 | 0.056 | 0.015181 | 0.056 | 0.050693 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.05 | 0 | 0.056 | 0.015071 | 0.055811 | 0.050677 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.049 | 0 | 0.056 | 0.014961 | 0.055606 | 0.050677 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.049 | 0 | 0.056 | 0.014803 | 0.055417 | 0.05063 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.049 | 0 | 0.056 | 0.014583 | 0.055276 | 0.050551 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.049 | 0 | 0.056 | 0.014315 | 0.05515 | 0.050457 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.049 | 0 | 0.056 | 0.014063 | 0.055039 | 0.050346 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.049 | 0 | 0.056 | 0.013874 | 0.054898 | 0.050268 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.049 | 0 | 0.056 | 0.013764 | 0.054756 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.049 | 0 | 0.056 | 0.013717 | 0.054598 | 0.050205 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.049 | 0 | 0.055 | 0.013717 | 0.054472 | 0.050189 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.049 | 0 | 0.055 | 0.013732 | 0.054394 | 0.050157 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.049 | 0 | 0.055 | 0.013764 | 0.054362 | 0.050142 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.049 | 0 | 0.055 | 0.013811 | 0.054362 | 0.05011 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.049 | 0 | 0.055 | 0.013858 | 0.054378 | 0.05011 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.049 | 0 | 0.055 | 0.013921 | 0.054409 | 0.050126 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.049 | 0 | 0.055 | 0.014 | 0.054488 | 0.050142 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.049 | 0 | 0.055 | 0.014079 | 0.054567 | 0.050173 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.049 | 0 | 0.055 | 0.014157 | 0.054677 | 0.050173 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.049 | 0 | 0.055 | 0.014268 | 0.054772 | 0.05022 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.049 | 0 | 0.055 | 0.014378 | 0.054835 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.049 | 0 | 0.055 | 0.014488 | 0.054866 | 0.050362 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.049 | 0 | 0.055 | 0.014598 | 0.054898 | 0.050457 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.049 | 0 | 0.055 | 0.014661 | 0.054945 | 0.05052 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.049 | 0 | 0.055 | 0.014709 | 0.054992 | 0.050551 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.049 | 0 | 0.055 | 0.014724 | 0.055055 | 0.050567 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.048 | 0 | 0.055 | 0.01474 | 0.055087 | 0.050567 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.048 | 0 | 0.055 | 0.01474 | 0.055118 | 0.050567 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.048 | 0 | 0.055 | 0.014709 | 0.055118 | 0.050583 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.048 | 0 | 0.055 | 0.014646 | 0.055118 | 0.050583 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.048 | 0 | 0.055 | 0.014551 | 0.055134 | 0.050583 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.048 | 0 | 0.055 | 0.014457 | 0.055134 | 0.050567 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.048 | 0 | 0.055 | 0.014378 | 0.055134 | 0.050551 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.048 | 0 | 0.054 | 0.014331 | 0.055102 | 0.050551 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.048 | 0 | 0.054 | 0.014299 | 0.055071 | 0.050567 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.048 | 0 | 0.054 | 0.014268 | 0.055039 | 0.050567 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.048 | 0 | 0.054 | 0.014205 | 0.055024 | 0.050551 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.048 | 0 | 0.054 | 0.01411 | 0.055039 | 0.050488 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.048 | 0 | 0.054 | 0.013984 | 0.055071 | 0.050409 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.048 | 0 | 0.054 | 0.01389 | 0.055102 | 0.050362 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.048 | 0 | 0.054 | 0.013827 | 0.055118 | 0.050315 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.048 | 0 | 0.054 | 0.013811 | 0.055102 | 0.050315 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.048 | 0 | 0.054 | 0.013811 | 0.055087 | 0.050315 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.047 | 0 | 0.054 | 0.013827 | 0.055071 | 0.050299 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.047 | 0 | 0.054 | 0.013843 | 0.055055 | 0.050299 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.047 | 0 | 0.054 | 0.013874 | 0.055071 | 0.050283 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.047 | 0 | 0.054 | 0.013906 | 0.055055 | 0.050299 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.047 | 0 | 0.054 | 0.013953 | 0.055039 | 0.050299 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.047 | 0 | 0.054 | 0.014 | 0.055024 | 0.050315 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.047 | 0 | 0.054 | 0.014031 | 0.055024 | 0.050331 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.047 | 0 | 0.053 | 0.014047 | 0.055024 | 0.050331 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.047 | 0 | 0.053 | 0.014047 | 0.055039 | 0.050315 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.047 | 0 | 0.053 | 0.014079 | 0.055039 | 0.050331 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.047 | 0 | 0.053 | 0.014126 | 0.054992 | 0.050362 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.047 | 0 | 0.053 | 0.014189 | 0.054929 | 0.050425 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.047 | 0 | 0.053 | 0.01422 | 0.054866 | 0.050472 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.047 | 0 | 0.053 | 0.014252 | 0.054819 | 0.050504 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.047 | 0 | 0.053 | 0.014268 | 0.054803 | 0.050504 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.047 | 0 | 0.053 | 0.014252 | 0.054803 | 0.050488 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.047 | 0 | 0.053 | 0.014252 | 0.054803 | 0.050472 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.047 | 0 | 0.053 | 0.014252 | 0.054787 | 0.050457 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.047 | 0 | 0.053 | 0.014236 | 0.054787 | 0.050472 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.047 | 0 | 0.053 | 0.014205 | 0.054803 | 0.050457 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.047 | 0 | 0.053 | 0.014173 | 0.054819 | 0.050457 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.047 | 0 | 0.053 | 0.014142 | 0.05485 | 0.050441 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.047 | 0 | 0.053 | 0.014126 | 0.054882 | 0.050441 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.046 | 0 | 0.053 | 0.014126 | 0.054898 | 0.050457 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.046 | 0 | 0.053 | 0.014142 | 0.054898 | 0.050472 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.046 | 0 | 0.053 | 0.014142 | 0.054913 | 0.050488 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.046 | 0 | 0.053 | 0.014126 | 0.054945 | 0.050488 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.046 | 0 | 0.053 | 0.014079 | 0.054992 | 0.050457 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.046 | 0 | 0.053 | 0.014047 | 0.055039 | 0.050409 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.046 | 0 | 0.052 | 0.014016 | 0.055102 | 0.050394 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.046 | 0 | 0.052 | 0.014016 | 0.055118 | 0.050394 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.046 | 0 | 0.052 | 0.014016 | 0.055118 | 0.050394 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.046 | 0 | 0.052 | 0.014016 | 0.055118 | 0.050394 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.046 | 0 | 0.052 | 0.014016 | 0.055118 | 0.050394 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.046 | 0 | 0.052 | 0.014016 | 0.055118 | 0.050394 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.046 | 0 | 0.052 | 0.014031 | 0.055102 | 0.050394 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.046 | 0 | 0.052 | 0.014047 | 0.055087 | 0.050409 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.046 | 0 | 0.052 | 0.014079 | 0.055071 | 0.050425 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.046 | 0 | 0.052 | 0.014079 | 0.055055 | 0.050425 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.046 | 0 | 0.052 | 0.014079 | 0.055055 | 0.050425 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.045 | 0 | 0.052 | 0.014047 | 0.055055 | 0.050409 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.045 | 0 | 0.052 | 0.014016 | 0.055055 | 0.050394 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.045 | 0 | 0.052 | 0.014016 | 0.055055 | 0.050409 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.045 | 0 | 0.052 | 0.014031 | 0.055008 | 0.050425 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.045 | 0 | 0.052 | 0.014047 | 0.054976 | 0.050441 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.045 | 0 | 0.052 | 0.014063 | 0.054929 | 0.050472 | 0.00028346
10/23/2022 | 3:23 | 0 | 0.045 | 0 | 0.051 | 0.014063 | 0.054898 | 0.050488 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.045 | 0 | 0.051 | 0.014063 | 0.054882 | 0.050488 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.045 | 0 | 0.051 | 0.014063 | 0.054882 | 0.050472 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.045 | 0 | 0.051 | 0.014063 | 0.054882 | 0.050457 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.045 | 0 | 0.051 | 0.014079 | 0.054882 | 0.050457 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.045 | 0 | 0.051 | 0.014079 | 0.054882 | 0.050457 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.045 | 0 | 0.051 | 0.014063 | 0.054898 | 0.050457 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.045 | 0 | 0.051 | 0.014047 | 0.054929 | 0.050457 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.045 | 0 | 0.051 | 0.014047 | 0.054961 | 0.050441 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.045 | 0 | 0.051 | 0.014063 | 0.054976 | 0.050457 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.045 | 0 | 0.051 | 0.014094 | 0.054976 | 0.050472 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.045 | 0 | 0.051 | 0.01411 | 0.054992 | 0.050504 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.045 | 0 | 0.051 | 0.014126 | 0.055008 | 0.05052 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.045 | 0 | 0.051 | 0.014126 | 0.055024 | 0.050504 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.045 | 0 | 0.051 | 0.01411 | 0.055055 | 0.050504 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.045 | 0 | 0.051 | 0.014094 | 0.055071 | 0.050472 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.045 | 0 | 0.051 | 0.014094 | 0.055087 | 0.050457 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.045 | 0 | 0.051 | 0.014094 | 0.055087 | 0.050457 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.045 | 0 | 0.051 | 0.014094 | 0.055087 | 0.050457 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.045 | 0 | 0.051 | 0.014079 | 0.055087 | 0.050457 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.045 | 0 | 0.051 | 0.014079 | 0.055087 | 0.050457 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.045 | 0 | 0.051 | 0.014079 | 0.055087 | 0.050457 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.045 | 0 | 0.051 | 0.014094 | 0.055087 | 0.050472 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.044 | 0 | 0.051 | 0.014094 | 0.055071 | 0.050488 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.044 | 0 | 0.05 | 0.01411 | 0.055071 | 0.050504 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.044 | 0 | 0.05 | 0.014094 | 0.055071 | 0.050504 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.044 | 0 | 0.05 | 0.014079 | 0.055087 | 0.050504 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.044 | 0 | 0.05 | 0.014063 | 0.055102 | 0.050504 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.044 | 0 | 0.05 | 0.014031 | 0.055118 | 0.050488 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.044 | 0 | 0.05 | 0.014031 | 0.055102 | 0.050504 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.044 | 0 | 0.05 | 0.014031 | 0.055087 | 0.05052 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.044 | 0 | 0.05 | 0.014031 | 0.055055 | 0.050535 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.044 | 0 | 0.05 | 0.014031 | 0.055055 | 0.050535 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.044 | 0 | 0.05 | 0.014031 | 0.055039 | 0.050535 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.044 | 0 | 0.05 | 0.014031 | 0.055039 | 0.05052 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.044 | 0 | 0.05 | 0.014047 | 0.055055 | 0.05052 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.044 | 0 | 0.05 | 0.014063 | 0.055055 | 0.05052 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.044 | 0 | 0.05 | 0.014063 | 0.055055 | 0.05052 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.044 | 0 | 0.05 | 0.014063 | 0.055055 | 0.05052 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.044 | 0 | 0.05 | 0.014063 | 0.055071 | 0.050504 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.043 | 0 | 0.05 | 0.014063 | 0.055087 | 0.050488 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.043 | 0 | 0.049 | 0.014063 | 0.055102 | 0.050488 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.043 | 0 | 0.049 | 0.014079 | 0.055102 | 0.050504 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.043 | 0 | 0.049 | 0.01411 | 0.055087 | 0.05052 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.043 | 0 | 0.049 | 0.014142 | 0.055071 | 0.050535 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.043 | 0 | 0.049 | 0.014157 | 0.055071 | 0.050551 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.043 | 0 | 0.049 | 0.014173 | 0.055071 | 0.050535 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.043 | 0 | 0.049 | 0.014157 | 0.055087 | 0.050504 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.043 | 0 | 0.049 | 0.014157 | 0.055102 | 0.050488 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.043 | 0 | 0.049 | 0.014157 | 0.055102 | 0.050472 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.043 | 0 | 0.049 | 0.014157 | 0.055102 | 0.050472 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.043 | 0 | 0.049 | 0.014142 | 0.055087 | 0.050472 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.043 | 0 | 0.049 | 0.014142 | 0.055087 | 0.050472 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.043 | 0 | 0.049 | 0.014126 | 0.055102 | 0.050472 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.043 | 0 | 0.049 | 0.01411 | 0.055102 | 0.050472 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.043 | 0 | 0.049 | 0.014126 | 0.055102 | 0.050472 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.043 | 0 | 0.049 | 0.014142 | 0.055102 | 0.050504 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.043 | 0 | 0.049 | 0.014142 | 0.055102 | 0.05052 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.043 | 0 | 0.049 | 0.014142 | 0.055102 | 0.050535 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.043 | 0 | 0.049 | 0.014126 | 0.055134 | 0.050535 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.043 | 0 | 0.049 | 0.01411 | 0.05515 | 0.050535 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.043 | 0 | 0.049 | 0.014094 | 0.055181 | 0.050535 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.043 | 0 | 0.049 | 0.014079 | 0.055197 | 0.050551 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.043 | 0 | 0.049 | 0.014079 | 0.055197 | 0.050567 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.043 | 0 | 0.049 | 0.014079 | 0.055197 | 0.050583 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.043 | 0 | 0.049 | 0.014079 | 0.055181 | 0.050583 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.043 | 0 | 0.049 | 0.014094 | 0.055181 | 0.050598 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.043 | 0 | 0.049 | 0.014094 | 0.055181 | 0.050598 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.043 | 0 | 0.048 | 0.01411 | 0.055181 | 0.050598 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.043 | 0 | 0.048 | 0.014126 | 0.055181 | 0.050598 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.043 | 0 | 0.048 | 0.014126 | 0.055181 | 0.050598 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.043 | 0 | 0.048 | 0.014142 | 0.055181 | 0.050598 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.043 | 0 | 0.048 | 0.014142 | 0.055197 | 0.050598 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.043 | 0 | 0.048 | 0.014142 | 0.055197 | 0.050583 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.043 | 0 | 0.048 | 0.014142 | 0.055213 | 0.050583 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.042 | 0 | 0.048 | 0.014157 | 0.055213 | 0.050567 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.042 | 0 | 0.048 | 0.014189 | 0.055197 | 0.050567 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.042 | 0 | 0.048 | 0.014205 | 0.055181 | 0.050567 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.042 | 0 | 0.048 | 0.014205 | 0.055165 | 0.050567 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.042 | 0 | 0.048 | 0.014205 | 0.05515 | 0.050551 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.042 | 0 | 0.048 | 0.014205 | 0.05515 | 0.050535 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.042 | 0 | 0.048 | 0.014205 | 0.05515 | 0.05052 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.042 | 0 | 0.048 | 0.014205 | 0.05515 | 0.050504 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.042 | 0 | 0.048 | 0.014205 | 0.055134 | 0.050488 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.042 | 0 | 0.048 | 0.014205 | 0.055134 | 0.050488 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.042 | 0 | 0.047 | 0.014205 | 0.05515 | 0.050488 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.042 | 0 | 0.047 | 0.014189 | 0.05515 | 0.050488 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.042 | 0 | 0.047 | 0.014189 | 0.055165 | 0.050504 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.042 | 0 | 0.047 | 0.014189 | 0.055181 | 0.05052 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.042 | 0 | 0.047 | 0.014205 | 0.055181 | 0.050535 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.042 | 0 | 0.047 | 0.01422 | 0.055181 | 0.050551 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.042 | 0 | 0.047 | 0.014236 | 0.055181 | 0.050567 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.041 | 0 | 0.047 | 0.01422 | 0.055181 | 0.050567 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.041 | 0 | 0.047 | 0.014205 | 0.055197 | 0.050567 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.041 | 0 | 0.047 | 0.014205 | 0.055213 | 0.050551 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.041 | 0 | 0.047 | 0.014189 | 0.055228 | 0.050551 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.041 | 0 | 0.047 | 0.014189 | 0.055228 | 0.050567 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.041 | 0 | 0.047 | 0.014189 | 0.055213 | 0.050567 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.041 | 0 | 0.047 | 0.014189 | 0.055213 | 0.050567 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.041 | 0 | 0.047 | 0.014189 | 0.055213 | 0.050583 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.041 | 0 | 0.047 | 0.014205 | 0.055213 | 0.050583 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.041 | 0 | 0.047 | 0.014205 | 0.055213 | 0.050583 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.041 | 0 | 0.047 | 0.01422 | 0.055197 | 0.050583 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.041 | 0 | 0.047 | 0.014236 | 0.055197 | 0.050583 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.041 | 0 | 0.047 | 0.014236 | 0.055197 | 0.050567 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.041 | 0 | 0.047 | 0.01422 | 0.055213 | 0.050551 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.041 | 0 | 0.047 | 0.014205 | 0.055213 | 0.050535 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.041 | 0 | 0.047 | 0.014189 | 0.055213 | 0.05052 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.041 | 0 | 0.047 | 0.014189 | 0.055213 | 0.050504 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.041 | 0 | 0.047 | 0.014205 | 0.055197 | 0.050504 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.041 | 0 | 0.047 | 0.01422 | 0.055165 | 0.050504 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.041 | 0 | 0.047 | 0.01422 | 0.05515 | 0.050488 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.041 | 0 | 0.047 | 0.01422 | 0.055134 | 0.050488 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.041 | 0 | 0.047 | 0.01422 | 0.055118 | 0.050457 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.041 | 0 | 0.047 | 0.01422 | 0.055118 | 0.050441 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.041 | 0 | 0.047 | 0.014236 | 0.055118 | 0.050441 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.041 | 0 | 0.046 | 0.014236 | 0.055118 | 0.050425 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.041 | 0 | 0.046 | 0.014236 | 0.055118 | 0.050425 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.041 | 0 | 0.046 | 0.014236 | 0.055134 | 0.050425 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.041 | 0 | 0.046 | 0.014236 | 0.05515 | 0.050441 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.041 | 0 | 0.046 | 0.014236 | 0.05515 | 0.050441 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.041 | 0 | 0.046 | 0.014252 | 0.055165 | 0.050457 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.041 | 0 | 0.046 | 0.014268 | 0.055181 | 0.050488 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.041 | 0 | 0.046 | 0.014283 | 0.055181 | 0.050504 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.041 | 0 | 0.046 | 0.014283 | 0.055197 | 0.05052 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.041 | 0 | 0.046 | 0.014299 | 0.055213 | 0.050535 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.041 | 0 | 0.046 | 0.014299 | 0.055228 | 0.050551 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.041 | 0 | 0.046 | 0.014283 | 0.055244 | 0.050535 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.041 | 0 | 0.046 | 0.014283 | 0.05526 | 0.050535 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.041 | 0 | 0.046 | 0.014283 | 0.05526 | 0.050551 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.041 | 0 | 0.046 | 0.014283 | 0.05526 | 0.050551 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.041 | 0 | 0.046 | 0.014283 | 0.05526 | 0.050551 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.04 | 0 | 0.045 | 0.014268 | 0.05526 | 0.050567 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.04 | 0 | 0.045 | 0.014268 | 0.05526 | 0.050567 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.04 | 0 | 0.045 | 0.014268 | 0.05526 | 0.050551 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.04 | 0 | 0.045 | 0.014268 | 0.055244 | 0.050551 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.04 | 0 | 0.045 | 0.014268 | 0.055228 | 0.050551 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.04 | 0 | 0.045 | 0.014268 | 0.055228 | 0.050551 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.04 | 0 | 0.045 | 0.014268 | 0.055213 | 0.050535 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.04 | 0 | 0.045 | 0.014252 | 0.055213 | 0.05052 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.04 | 0 | 0.045 | 0.01422 | 0.055197 | 0.050488 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.04 | 0 | 0.045 | 0.014205 | 0.055181 | 0.050472 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.04 | 0 | 0.045 | 0.014205 | 0.05515 | 0.050472 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.04 | 0 | 0.045 | 0.014205 | 0.055118 | 0.050457 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.04 | 0 | 0.045 | 0.014205 | 0.055102 | 0.050441 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.04 | 0 | 0.045 | 0.014205 | 0.055087 | 0.050425 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.04 | 0 | 0.045 | 0.014205 | 0.055087 | 0.050425 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.04 | 0 | 0.045 | 0.014205 | 0.055071 | 0.050409 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.039 | 0 | 0.045 | 0.01422 | 0.055071 | 0.050409 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.039 | 0 | 0.045 | 0.01422 | 0.055087 | 0.050409 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.039 | 0 | 0.045 | 0.01422 | 0.055102 | 0.050409 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.039 | 0 | 0.045 | 0.014236 | 0.055102 | 0.050425 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.039 | 0 | 0.045 | 0.014236 | 0.055134 | 0.050425 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.039 | 0 | 0.045 | 0.014268 | 0.05515 | 0.050441 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.039 | 0 | 0.045 | 0.014268 | 0.055165 | 0.050441 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.039 | 0 | 0.045 | 0.014283 | 0.055165 | 0.050457 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.039 | 0 | 0.045 | 0.014299 | 0.055181 | 0.050472 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.039 | 0 | 0.045 | 0.014315 | 0.055181 | 0.050472 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.039 | 0 | 0.045 | 0.014315 | 0.055197 | 0.050472 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.039 | 0 | 0.045 | 0.014331 | 0.055213 | 0.050488 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.039 | 0 | 0.045 | 0.014331 | 0.055213 | 0.050488 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.039 | 0 | 0.045 | 0.014331 | 0.055228 | 0.050488 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.039 | 0 | 0.045 | 0.014331 | 0.055228 | 0.050488 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.039 | 0 | 0.045 | 0.014315 | 0.055228 | 0.050504 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.039 | 0 | 0.045 | 0.014315 | 0.055228 | 0.050504 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.039 | 0 | 0.045 | 0.014299 | 0.055228 | 0.050504 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.039 | 0 | 0.045 | 0.014299 | 0.055228 | 0.050504 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.039 | 0 | 0.045 | 0.014283 | 0.055213 | 0.050488 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.039 | 0 | 0.045 | 0.014283 | 0.055197 | 0.050488 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.039 | 0 | 0.045 | 0.014268 | 0.055181 | 0.050488 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.039 | 0 | 0.045 | 0.014252 | 0.055165 | 0.050472 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.039 | 0 | 0.045 | 0.01422 | 0.05515 | 0.050457 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.039 | 0 | 0.045 | 0.014205 | 0.055134 | 0.050441 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.039 | 0 | 0.044 | 0.014189 | 0.055134 | 0.050425 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.039 | 0 | 0.044 | 0.014173 | 0.055118 | 0.050409 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.039 | 0 | 0.044 | 0.014173 | 0.055102 | 0.050394 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.039 | 0 | 0.044 | 0.014173 | 0.055071 | 0.050394 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.039 | 0 | 0.044 | 0.014173 | 0.055055 | 0.050378 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.039 | 0 | 0.044 | 0.014173 | 0.055055 | 0.050362 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.039 | 0 | 0.044 | 0.014173 | 0.055055 | 0.050362 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.039 | 0 | 0.044 | 0.014189 | 0.055055 | 0.050362 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.039 | 0 | 0.044 | 0.014205 | 0.055055 | 0.050362 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.039 | 0 | 0.044 | 0.014205 | 0.055055 | 0.050362 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.039 | 0 | 0.044 | 0.01422 | 0.055071 | 0.050362 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.039 | 0 | 0.044 | 0.01422 | 0.055087 | 0.050378 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.039 | 0 | 0.044 | 0.014236 | 0.055102 | 0.050378 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.039 | 0 | 0.044 | 0.014252 | 0.055118 | 0.050394 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.038 | 0 | 0.044 | 0.014268 | 0.055118 | 0.050409 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.038 | 0 | 0.044 | 0.014283 | 0.055134 | 0.050409 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.038 | 0 | 0.043 | 0.014299 | 0.055134 | 0.050425 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.038 | 0 | 0.043 | 0.014315 | 0.055134 | 0.050425 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.038 | 0 | 0.043 | 0.014315 | 0.055134 | 0.050425 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.038 | 0 | 0.043 | 0.014315 | 0.05515 | 0.050425 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.038 | 0 | 0.043 | 0.014331 | 0.05515 | 0.050409 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.038 | 0 | 0.043 | 0.014331 | 0.05515 | 0.050409 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.038 | 0 | 0.043 | 0.014315 | 0.05515 | 0.050409 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.038 | 0 | 0.043 | 0.014315 | 0.05515 | 0.050409 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.038 | 0 | 0.043 | 0.014299 | 0.05515 | 0.050409 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.038 | 0 | 0.043 | 0.014283 | 0.05515 | 0.050409 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.038 | 0 | 0.043 | 0.014268 | 0.05515 | 0.050409 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.038 | 0 | 0.043 | 0.014268 | 0.055134 | 0.050409 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.038 | 0 | 0.043 | 0.014252 | 0.055118 | 0.050425 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.038 | 0 | 0.043 | 0.014236 | 0.055102 | 0.050425 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.038 | 0 | 0.043 | 0.01422 | 0.055102 | 0.050409 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.038 | 0 | 0.043 | 0.014205 | 0.055087 | 0.050409 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.037 | 0 | 0.043 | 0.014189 | 0.055087 | 0.050409 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.037 | 0 | 0.043 | 0.014173 | 0.055071 | 0.050394 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.037 | 0 | 0.043 | 0.014173 | 0.055071 | 0.050394 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.037 | 0 | 0.043 | 0.014173 | 0.055055 | 0.050378 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.037 | 0 | 0.043 | 0.014173 | 0.055055 | 0.050378 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.037 | 0 | 0.043 | 0.014173 | 0.055039 | 0.050378 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.037 | 0 | 0.043 | 0.014189 | 0.055039 | 0.050378 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.037 | 0 | 0.043 | 0.014189 | 0.055039 | 0.050378 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.037 | 0 | 0.043 | 0.014189 | 0.055039 | 0.050378 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.037 | 0 | 0.043 | 0.014205 | 0.055039 | 0.050378 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.037 | 0 | 0.043 | 0.014205 | 0.055039 | 0.050378 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.037 | 0 | 0.043 | 0.01422 | 0.055039 | 0.050378 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.037 | 0 | 0.043 | 0.01422 | 0.055055 | 0.050362 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.037 | 0 | 0.043 | 0.01422 | 0.055055 | 0.050362 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.037 | 0 | 0.043 | 0.01422 | 0.055055 | 0.050362 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.037 | 0 | 0.043 | 0.014236 | 0.055055 | 0.050362 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.037 | 0 | 0.043 | 0.014252 | 0.055039 | 0.050362 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.037 | 0 | 0.043 | 0.014252 | 0.055024 | 0.050346 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.037 | 0 | 0.043 | 0.014252 | 0.055008 | 0.050346 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.037 | 0 | 0.043 | 0.014252 | 0.055008 | 0.050331 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.037 | 0 | 0.043 | 0.014252 | 0.055008 | 0.050331 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.037 | 0 | 0.043 | 0.014252 | 0.054992 | 0.050315 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.037 | 0 | 0.043 | 0.014252 | 0.054992 | 0.050315 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.037 | 0 | 0.042 | 0.014252 | 0.054992 | 0.050315 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.037 | 0 | 0.042 | 0.014236 | 0.054992 | 0.050315 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.037 | 0 | 0.042 | 0.014236 | 0.055008 | 0.050315 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.037 | 0 | 0.042 | 0.01422 | 0.055008 | 0.050315 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.037 | 0 | 0.042 | 0.01422 | 0.055024 | 0.050315 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.037 | 0 | 0.042 | 0.01422 | 0.055024 | 0.050331 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.037 | 0 | 0.042 | 0.01422 | 0.055024 | 0.050331 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.037 | 0 | 0.042 | 0.01422 | 0.055024 | 0.050346 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.037 | 0 | 0.042 | 0.014205 | 0.055024 | 0.050362 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.037 | 0 | 0.042 | 0.014205 | 0.055039 | 0.050362 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.037 | 0 | 0.042 | 0.014189 | 0.055039 | 0.050346 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.037 | 0 | 0.042 | 0.014173 | 0.055055 | 0.050346 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.037 | 0 | 0.042 | 0.014173 | 0.055055 | 0.050346 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.037 | 0 | 0.042 | 0.014173 | 0.055039 | 0.050362 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.037 | 0 | 0.042 | 0.014173 | 0.055039 | 0.050362 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.037 | 0 | 0.042 | 0.014173 | 0.055039 | 0.050362 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.037 | 0 | 0.041 | 0.014173 | 0.055039 | 0.050362 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.037 | 0 | 0.041 | 0.014189 | 0.055039 | 0.050362 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.037 | 0 | 0.041 | 0.014189 | 0.055039 | 0.050362 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.037 | 0 | 0.041 | 0.014189 | 0.055024 | 0.050378 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.037 | 0 | 0.041 | 0.014189 | 0.055024 | 0.050378 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.036 | 0 | 0.041 | 0.014189 | 0.055024 | 0.050378 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.036 | 0 | 0.041 | 0.014189 | 0.055024 | 0.050362 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.036 | 0 | 0.041 | 0.014189 | 0.055008 | 0.050346 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.036 | 0 | 0.041 | 0.014173 | 0.055008 | 0.050331 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.036 | 0 | 0.041 | 0.014173 | 0.054992 | 0.050299 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.036 | 0 | 0.041 | 0.014173 | 0.054961 | 0.050299 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.036 | 0 | 0.041 | 0.014173 | 0.054945 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.036 | 0 | 0.041 | 0.014173 | 0.054945 | 0.050252 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.036 | 0 | 0.041 | 0.014173 | 0.054929 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.036 | 0 | 0.041 | 0.014173 | 0.054929 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.036 | 0 | 0.041 | 0.014173 | 0.054913 | 0.05022 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.036 | 0 | 0.041 | 0.014173 | 0.054913 | 0.05022 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.036 | 0 | 0.041 | 0.014189 | 0.054913 | 0.05022 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.036 | 0 | 0.041 | 0.014189 | 0.054929 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.036 | 0 | 0.041 | 0.014189 | 0.054945 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.036 | 0 | 0.041 | 0.014189 | 0.054945 | 0.050252 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.035 | 0 | 0.041 | 0.014189 | 0.054961 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.035 | 0 | 0.041 | 0.014189 | 0.054976 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.035 | 0 | 0.041 | 0.014189 | 0.054976 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.035 | 0 | 0.041 | 0.014189 | 0.054992 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.035 | 0 | 0.041 | 0.014189 | 0.054992 | 0.050299 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.035 | 0 | 0.041 | 0.014189 | 0.054992 | 0.050315 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.035 | 0 | 0.041 | 0.014189 | 0.054992 | 0.050331 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.035 | 0 | 0.041 | 0.014189 | 0.054992 | 0.050346 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.035 | 0 | 0.041 | 0.014189 | 0.055008 | 0.050346 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.035 | 0 | 0.041 | 0.014189 | 0.055008 | 0.050346 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.035 | 0 | 0.041 | 0.014189 | 0.055008 | 0.050346 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.035 | 0 | 0.041 | 0.014189 | 0.055008 | 0.050346 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.035 | 0 | 0.041 | 0.014205 | 0.054992 | 0.050346 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.035 | 0 | 0.041 | 0.014189 | 0.054992 | 0.050346 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.035 | 0 | 0.041 | 0.014189 | 0.054992 | 0.050346 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.035 | 0 | 0.041 | 0.014173 | 0.054992 | 0.050331 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.035 | 0 | 0.041 | 0.014157 | 0.054992 | 0.050315 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.035 | 0 | 0.041 | 0.014126 | 0.054976 | 0.050315 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.035 | 0 | 0.041 | 0.014126 | 0.054976 | 0.050299 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.035 | 0 | 0.041 | 0.014126 | 0.054945 | 0.050299 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.035 | 0 | 0.041 | 0.01411 | 0.054929 | 0.050283 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.035 | 0 | 0.041 | 0.01411 | 0.054913 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.035 | 0 | 0.041 | 0.01411 | 0.054898 | 0.050252 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.035 | 0 | 0.041 | 0.01411 | 0.054882 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.035 | 0 | 0.041 | 0.01411 | 0.054882 | 0.050205 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.035 | 0 | 0.04 | 0.01411 | 0.054866 | 0.050205 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.035 | 0 | 0.04 | 0.01411 | 0.054866 | 0.050189 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.035 | 0 | 0.04 | 0.01411 | 0.054866 | 0.050189 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.035 | 0 | 0.04 | 0.01411 | 0.054866 | 0.050189 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.035 | 0 | 0.04 | 0.01411 | 0.054882 | 0.050189 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.035 | 0 | 0.04 | 0.01411 | 0.054882 | 0.050205 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.035 | 0 | 0.04 | 0.014126 | 0.054913 | 0.050205 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.035 | 0 | 0.04 | 0.014142 | 0.054913 | 0.05022 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.035 | 0 | 0.04 | 0.014157 | 0.054929 | 0.050252 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.035 | 0 | 0.04 | 0.014157 | 0.054929 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.035 | 0 | 0.04 | 0.014173 | 0.054945 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.035 | 0 | 0.04 | 0.014173 | 0.054945 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.035 | 0 | 0.04 | 0.014173 | 0.054961 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.035 | 0 | 0.04 | 0.014157 | 0.054976 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.035 | 0 | 0.04 | 0.014157 | 0.054976 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.035 | 0 | 0.04 | 0.014157 | 0.054976 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.035 | 0 | 0.04 | 0.014157 | 0.054961 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.035 | 0 | 0.04 | 0.014157 | 0.054961 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.035 | 0 | 0.04 | 0.014157 | 0.054961 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.035 | 0 | 0.039 | 0.014157 | 0.054961 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.035 | 0 | 0.039 | 0.014157 | 0.054961 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.035 | 0 | 0.039 | 0.014157 | 0.054961 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.035 | 0 | 0.039 | 0.014157 | 0.054961 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.035 | 0 | 0.039 | 0.014142 | 0.054945 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.035 | 0 | 0.039 | 0.014126 | 0.054945 | 0.050268 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.035 | 0 | 0.039 | 0.01411 | 0.054945 | 0.050252 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.035 | 0 | 0.039 | 0.014094 | 0.054929 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.035 | 0 | 0.039 | 0.014079 | 0.054913 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.035 | 0 | 0.039 | 0.014079 | 0.054898 | 0.05022 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.034 | 0 | 0.039 | 0.014063 | 0.054882 | 0.05022 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.034 | 0 | 0.039 | 0.014063 | 0.054866 | 0.050205 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.034 | 0 | 0.039 | 0.014063 | 0.05485 | 0.050205 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.034 | 0 | 0.039 | 0.014063 | 0.05485 | 0.050189 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.034 | 0 | 0.039 | 0.014079 | 0.05485 | 0.050173 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.034 | 0 | 0.039 | 0.014079 | 0.05485 | 0.050173 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.034 | 0 | 0.039 | 0.014079 | 0.05485 | 0.050173 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.034 | 0 | 0.039 | 0.014094 | 0.05485 | 0.050189 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.034 | 0 | 0.039 | 0.014094 | 0.054866 | 0.050189 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.034 | 0 | 0.039 | 0.014094 | 0.054882 | 0.050189 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.034 | 0 | 0.039 | 0.014094 | 0.054898 | 0.050205 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.034 | 0 | 0.039 | 0.01411 | 0.054898 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.034 | 0 | 0.039 | 0.01411 | 0.054898 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.034 | 0 | 0.039 | 0.014126 | 0.054898 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.034 | 0 | 0.039 | 0.014126 | 0.054913 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.034 | 0 | 0.039 | 0.014126 | 0.054913 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.034 | 0 | 0.039 | 0.014126 | 0.054913 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.033 | 0 | 0.039 | 0.014126 | 0.054913 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.033 | 0 | 0.039 | 0.014126 | 0.054913 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.033 | 0 | 0.039 | 0.014126 | 0.054913 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.033 | 0 | 0.039 | 0.01411 | 0.054913 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.033 | 0 | 0.039 | 0.01411 | 0.054913 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.033 | 0 | 0.039 | 0.01411 | 0.054929 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.033 | 0 | 0.039 | 0.01411 | 0.054929 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.033 | 0 | 0.039 | 0.014094 | 0.054929 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.033 | 0 | 0.039 | 0.014094 | 0.054913 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.033 | 0 | 0.039 | 0.014079 | 0.054913 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.033 | 0 | 0.039 | 0.014079 | 0.054913 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.033 | 0 | 0.039 | 0.014063 | 0.054913 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.033 | 0 | 0.039 | 0.014047 | 0.054913 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.033 | 0 | 0.039 | 0.014031 | 0.054898 | 0.05022 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.033 | 0 | 0.038 | 0.014031 | 0.054882 | 0.050205 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.033 | 0 | 0.038 | 0.014031 | 0.054882 | 0.050189 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.033 | 0 | 0.038 | 0.014016 | 0.054866 | 0.050173 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.033 | 0 | 0.038 | 0.014016 | 0.054866 | 0.050173 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.033 | 0 | 0.038 | 0.014016 | 0.054866 | 0.050157 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.033 | 0 | 0.038 | 0.014031 | 0.05485 | 0.050157 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.033 | 0 | 0.038 | 0.014031 | 0.05485 | 0.050157 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.033 | 0 | 0.038 | 0.014047 | 0.05485 | 0.050157 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.033 | 0 | 0.038 | 0.014047 | 0.054866 | 0.050157 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.033 | 0 | 0.038 | 0.014047 | 0.054866 | 0.050173 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.033 | 0 | 0.038 | 0.014063 | 0.054866 | 0.050173 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.033 | 0 | 0.038 | 0.014063 | 0.054866 | 0.050173 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.033 | 0 | 0.038 | 0.014063 | 0.054882 | 0.050173 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.033 | 0 | 0.038 | 0.014063 | 0.054898 | 0.050189 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.033 | 0 | 0.038 | 0.014063 | 0.054898 | 0.050189 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.033 | 0 | 0.038 | 0.014079 | 0.054898 | 0.050189 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.033 | 0 | 0.038 | 0.014079 | 0.054898 | 0.050205 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.033 | 0 | 0.037 | 0.014079 | 0.054898 | 0.050205 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.033 | 0 | 0.037 | 0.014094 | 0.054898 | 0.050205 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.033 | 0 | 0.037 | 0.014094 | 0.054898 | 0.050205 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.033 | 0 | 0.037 | 0.014094 | 0.054898 | 0.050205 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.033 | 0 | 0.037 | 0.014094 | 0.054898 | 0.050205 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.033 | 0 | 0.037 | 0.014094 | 0.054898 | 0.050205 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.033 | 0 | 0.037 | 0.014079 | 0.054898 | 0.050205 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.033 | 0 | 0.037 | 0.014079 | 0.054898 | 0.050205 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.033 | 0 | 0.037 | 0.014063 | 0.054913 | 0.050205 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.033 | 0 | 0.037 | 0.014063 | 0.054913 | 0.050205 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.033 | 0 | 0.037 | 0.014063 | 0.054913 | 0.050205 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.033 | 0 | 0.037 | 0.014063 | 0.054913 | 0.050205 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.033 | 0 | 0.037 | 0.014063 | 0.054913 | 0.05022 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.033 | 0 | 0.037 | 0.014063 | 0.054913 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.033 | 0 | 0.037 | 0.014063 | 0.054913 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.033 | 0 | 0.037 | 0.014063 | 0.054913 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.033 | 0 | 0.037 | 0.014047 | 0.054913 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.033 | 0 | 0.037 | 0.014047 | 0.054898 | 0.050205 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.033 | 0 | 0.037 | 0.014047 | 0.054898 | 0.050205 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.033 | 0 | 0.037 | 0.014047 | 0.054882 | 0.050189 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.033 | 0 | 0.037 | 0.014047 | 0.054882 | 0.050189 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.033 | 0 | 0.037 | 0.014047 | 0.054882 | 0.050189 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.033 | 0 | 0.037 | 0.014047 | 0.054898 | 0.050189 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.033 | 0 | 0.037 | 0.014047 | 0.054898 | 0.050189 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.033 | 0 | 0.037 | 0.014063 | 0.054898 | 0.050205 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.033 | 0 | 0.037 | 0.014063 | 0.054913 | 0.050205 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.033 | 0 | 0.037 | 0.014063 | 0.054929 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.033 | 0 | 0.037 | 0.014063 | 0.054929 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.033 | 0 | 0.037 | 0.014063 | 0.054945 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.033 | 0 | 0.037 | 0.014079 | 0.054961 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.033 | 0 | 0.037 | 0.014079 | 0.054961 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.032 | 0 | 0.037 | 0.014079 | 0.054961 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.032 | 0 | 0.037 | 0.014079 | 0.054961 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.032 | 0 | 0.037 | 0.014079 | 0.054945 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.032 | 0 | 0.037 | 0.014079 | 0.054945 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.032 | 0 | 0.037 | 0.014079 | 0.054945 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.032 | 0 | 0.037 | 0.014079 | 0.054945 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.032 | 0 | 0.037 | 0.014063 | 0.054945 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.032 | 0 | 0.037 | 0.014063 | 0.054945 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.032 | 0 | 0.037 | 0.014063 | 0.054945 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.032 | 0 | 0.037 | 0.014063 | 0.054961 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.032 | 0 | 0.037 | 0.014063 | 0.054961 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.032 | 0 | 0.037 | 0.014063 | 0.054961 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.032 | 0 | 0.037 | 0.014063 | 0.054976 | 0.050268 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.032 | 0 | 0.037 | 0.014063 | 0.054976 | 0.050268 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.032 | 0 | 0.037 | 0.014063 | 0.054976 | 0.050268 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.032 | 0 | 0.037 | 0.014047 | 0.054976 | 0.050268 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.032 | 0 | 0.037 | 0.014047 | 0.054976 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.031 | 0 | 0.037 | 0.014047 | 0.054961 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.031 | 0 | 0.037 | 0.014047 | 0.054961 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.031 | 0 | 0.037 | 0.014031 | 0.054961 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.031 | 0 | 0.037 | 0.014047 | 0.054961 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.031 | 0 | 0.037 | 0.014047 | 0.054945 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.031 | 0 | 0.037 | 0.014047 | 0.054945 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.031 | 0 | 0.037 | 0.014047 | 0.054945 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.031 | 0 | 0.037 | 0.014047 | 0.054961 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.031 | 0 | 0.037 | 0.014047 | 0.054961 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.031 | 0 | 0.037 | 0.014063 | 0.054976 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.031 | 0 | 0.037 | 0.014063 | 0.054976 | 0.050268 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.031 | 0 | 0.036 | 0.014063 | 0.054976 | 0.050268 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.031 | 0 | 0.036 | 0.014079 | 0.054976 | 0.050283 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.031 | 0 | 0.036 | 0.014079 | 0.054976 | 0.050283 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.031 | 0 | 0.036 | 0.014079 | 0.054976 | 0.050283 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.031 | 0 | 0.036 | 0.014063 | 0.054976 | 0.050268 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.031 | 0 | 0.036 | 0.014063 | 0.054976 | 0.050268 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.031 | 0 | 0.036 | 0.014063 | 0.054976 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.031 | 0 | 0.036 | 0.014063 | 0.054976 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.031 | 0 | 0.036 | 0.014063 | 0.054961 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.031 | 0 | 0.036 | 0.014063 | 0.054961 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.031 | 0 | 0.036 | 0.014063 | 0.054961 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.031 | 0 | 0.036 | 0.014063 | 0.054961 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.031 | 0 | 0.036 | 0.014063 | 0.054961 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.031 | 0 | 0.036 | 0.014079 | 0.054961 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.031 | 0 | 0.036 | 0.014079 | 0.054961 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.031 | 0 | 0.036 | 0.014079 | 0.054961 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.031 | 0 | 0.036 | 0.014063 | 0.054961 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.031 | 0 | 0.036 | 0.014063 | 0.054976 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.031 | 0 | 0.036 | 0.014047 | 0.054976 | 0.050252 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.031 | 0 | 0.036 | 0.014047 | 0.054961 | 0.050252 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.031 | 0 | 0.036 | 0.014047 | 0.054945 | 0.050252 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.031 | 0 | 0.036 | 0.014047 | 0.054945 | 0.050252 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.031 | 0 | 0.035 | 0.014047 | 0.054929 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.031 | 0 | 0.035 | 0.014047 | 0.054929 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.031 | 0 | 0.035 | 0.014047 | 0.054929 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.031 | 0 | 0.035 | 0.014047 | 0.054929 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.031 | 0 | 0.035 | 0.014047 | 0.054929 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.031 | 0 | 0.035 | 0.014063 | 0.054929 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.031 | 0 | 0.035 | 0.014063 | 0.054929 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.031 | 0 | 0.035 | 0.014063 | 0.054929 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.031 | 0 | 0.035 | 0.014063 | 0.054945 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.031 | 0 | 0.035 | 0.014063 | 0.054961 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.031 | 0 | 0.035 | 0.014063 | 0.054961 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.031 | 0 | 0.035 | 0.014063 | 0.054961 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.031 | 0 | 0.035 | 0.014063 | 0.054945 | 0.050252 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.031 | 0 | 0.035 | 0.014079 | 0.054945 | 0.050252 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.031 | 0 | 0.035 | 0.014079 | 0.054945 | 0.050252 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.031 | 0 | 0.035 | 0.014079 | 0.054945 | 0.050252 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.031 | 0 | 0.035 | 0.014079 | 0.054945 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.031 | 0 | 0.035 | 0.014079 | 0.054945 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.031 | 0 | 0.035 | 0.014079 | 0.054945 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.031 | 0 | 0.035 | 0.014079 | 0.054945 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.031 | 0 | 0.035 | 0.014063 | 0.054945 | 0.050236 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.031 | 0 | 0.035 | 0.014063 | 0.054945 | 0.050236 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.031 | 0 | 0.035 | 0.014063 | 0.054961 | 0.050236 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.031 | 0 | 0.035 | 0.014063 | 0.054961 | 0.050236 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.031 | 0 | 0.035 | 0.014063 | 0.054961 | 0.050252 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.031 | 0 | 0.035 | 0.014063 | 0.054961 | 0.050252 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.031 | 0 | 0.035 | 0.014063 | 0.054961 | 0.050252 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.031 | 0 | 0.035 | 0.014063 | 0.054961 | 0.050252 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.031 | 0 | 0.035 | 0.014047 | 0.054961 | 0.050252 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.031 | 0 | 0.035 | 0.014047 | 0.054961 | 0.050236 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.031 | 0 | 0.035 | 0.014031 | 0.054961 | 0.050236 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.031 | 0 | 0.035 | 0.014031 | 0.054961 | 0.050236 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.031 | 0 | 0.035 | 0.014031 | 0.054961 | 0.050236 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.031 | 0 | 0.035 | 0.014031 | 0.054945 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.03 | 0 | 0.035 | 0.014031 | 0.054945 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.03 | 0 | 0.035 | 0.014047 | 0.054945 | 0.050236 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.03 | 0 | 0.035 | 0.014047 | 0.054945 | 0.05022 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.03 | 0 | 0.035 | 0.014047 | 0.054945 | 0.05022 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.03 | 0 | 0.035 | 0.014047 | 0.054945 | 0.05022 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.03 | 0 | 0.035 | 0.014047 | 0.054961 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.03 | 0 | 0.035 | 0.014047 | 0.054961 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.03 | 0 | 0.035 | 0.014047 | 0.054976 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.03 | 0 | 0.035 | 0.014063 | 0.054976 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.03 | 0 | 0.035 | 0.014063 | 0.054976 | 0.050252 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.03 | 0 | 0.035 | 0.014063 | 0.054976 | 0.050252 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.03 | 0 | 0.035 | 0.014047 | 0.054976 | 0.050252 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.03 | 0 | 0.035 | 0.014047 | 0.054976 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.03 | 0 | 0.035 | 0.014047 | 0.054961 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.03 | 0 | 0.035 | 0.014047 | 0.054961 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.03 | 0 | 0.035 | 0.014047 | 0.054961 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.03 | 0 | 0.035 | 0.014047 | 0.054945 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.03 | 0 | 0.035 | 0.014047 | 0.054945 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.03 | 0 | 0.035 | 0.014047 | 0.054945 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.03 | 0 | 0.035 | 0.014047 | 0.054945 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.03 | 0 | 0.035 | 0.014047 | 0.054945 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.03 | 0 | 0.035 | 0.014047 | 0.054961 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.03 | 0 | 0.034 | 0.014047 | 0.054961 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.03 | 0 | 0.034 | 0.014047 | 0.054961 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.029 | 0 | 0.034 | 0.014047 | 0.054976 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.029 | 0 | 0.034 | 0.014047 | 0.054976 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.029 | 0 | 0.034 | 0.014047 | 0.054976 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.029 | 0 | 0.034 | 0.014047 | 0.054976 | 0.050252 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.029 | 0 | 0.034 | 0.014047 | 0.054976 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.029 | 0 | 0.034 | 0.014047 | 0.054976 | 0.050236 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.029 | 0 | 0.034 | 0.014047 | 0.054976 | 0.050236 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.029 | 0 | 0.034 | 0.014047 | 0.054961 | 0.05022 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.029 | 0 | 0.034 | 0.014047 | 0.054961 | 0.05022 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.029 | 0 | 0.034 | 0.014047 | 0.054961 | 0.05022 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.029 | 0 | 0.034 | 0.014047 | 0.054961 | 0.05022 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.029 | 0 | 0.034 | 0.014047 | 0.054961 | 0.05022 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.029 | 0 | 0.034 | 0.014047 | 0.054976 | 0.05022 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.029 | 0 | 0.034 | 0.014063 | 0.054976 | 0.050236 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.029 | 0 | 0.034 | 0.014063 | 0.054976 | 0.050236 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.029 | 0 | 0.034 | 0.014063 | 0.054992 | 0.050236 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.029 | 0 | 0.034 | 0.014047 | 0.054992 | 0.050252 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.029 | 0 | 0.034 | 0.014047 | 0.055008 | 0.050236 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.029 | 0 | 0.034 | 0.014047 | 0.055008 | 0.050236 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.029 | 0 | 0.033 | 0.014047 | 0.055008 | 0.05022 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.029 | 0 | 0.033 | 0.014047 | 0.055008 | 0.05022 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.029 | 0 | 0.033 | 0.014047 | 0.055008 | 0.05022 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.029 | 0 | 0.033 | 0.014047 | 0.055008 | 0.05022 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.029 | 0 | 0.033 | 0.014047 | 0.054992 | 0.05022 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.029 | 0 | 0.033 | 0.014047 | 0.054992 | 0.050205 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.029 | 0 | 0.033 | 0.014047 | 0.054992 | 0.050205 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.029 | 0 | 0.033 | 0.014047 | 0.054992 | 0.050205 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.029 | 0 | 0.033 | 0.014047 | 0.054992 | 0.050205 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.029 | 0 | 0.033 | 0.014047 | 0.055008 | 0.050205 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.029 | 0 | 0.033 | 0.014047 | 0.055008 | 0.05022 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.029 | 0 | 0.033 | 0.014047 | 0.055008 | 0.05022 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.029 | 0 | 0.033 | 0.014047 | 0.055008 | 0.05022 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.029 | 0 | 0.033 | 0.014031 | 0.055024 | 0.05022 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.029 | 0 | 0.033 | 0.014031 | 0.055024 | 0.050236 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.029 | 0 | 0.033 | 0.014031 | 0.055024 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.029 | 0 | 0.033 | 0.014031 | 0.055024 | 0.050252 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.029 | 0 | 0.033 | 0.014031 | 0.055008 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.029 | 0 | 0.033 | 0.014031 | 0.055008 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.029 | 0 | 0.033 | 0.014031 | 0.055008 | 0.050236 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.029 | 0 | 0.033 | 0.014031 | 0.055008 | 0.050236 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.029 | 0 | 0.033 | 0.014031 | 0.054992 | 0.05022 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.029 | 0 | 0.033 | 0.014031 | 0.054992 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.029 | 0 | 0.033 | 0.014031 | 0.054992 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.029 | 0 | 0.033 | 0.014031 | 0.054992 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.029 | 0 | 0.033 | 0.014016 | 0.055008 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.029 | 0 | 0.033 | 0.014016 | 0.055008 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.029 | 0 | 0.033 | 0.014016 | 0.055008 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.029 | 0 | 0.033 | 0.014016 | 0.055024 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.029 | 0 | 0.033 | 0.014016 | 0.055024 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.029 | 0 | 0.033 | 0.014016 | 0.055024 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.029 | 0 | 0.033 | 0.014031 | 0.055024 | 0.050268 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.029 | 0 | 0.033 | 0.014031 | 0.055024 | 0.050283 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.029 | 0 | 0.033 | 0.014031 | 0.055024 | 0.050268 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.029 | 0 | 0.033 | 0.014031 | 0.055024 | 0.050268 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.029 | 0 | 0.033 | 0.014031 | 0.055024 | 0.050252 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.029 | 0 | 0.033 | 0.014031 | 0.055024 | 0.050236 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.029 | 0 | 0.033 | 0.014031 | 0.055008 | 0.050236 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.029 | 0 | 0.033 | 0.014031 | 0.055008 | 0.050236 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.029 | 0 | 0.033 | 0.014016 | 0.055008 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.029 | 0 | 0.033 | 0.014016 | 0.055024 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.029 | 0 | 0.033 | 0.014016 | 0.055024 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.029 | 0 | 0.033 | 0.014016 | 0.055024 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.029 | 0 | 0.033 | 0.014016 | 0.055039 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.029 | 0 | 0.033 | 0.014031 | 0.055039 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.029 | 0 | 0.033 | 0.014031 | 0.055039 | 0.050268 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.029 | 0 | 0.033 | 0.014031 | 0.055024 | 0.050268 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.029 | 0 | 0.033 | 0.014031 | 0.055024 | 0.050252 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.029 | 0 | 0.033 | 0.014016 | 0.055024 | 0.050252 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.029 | 0 | 0.033 | 0.014016 | 0.055024 | 0.05022 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.029 | 0 | 0.033 | 0.014016 | 0.055008 | 0.05022 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.029 | 0 | 0.033 | 0.014016 | 0.055008 | 0.05022 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.029 | 0 | 0.033 | 0.014016 | 0.055008 | 0.05022 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.029 | 0 | 0.033 | 0.014016 | 0.054992 | 0.050205 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.029 | 0 | 0.033 | 0.014 | 0.054992 | 0.050205 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.029 | 0 | 0.033 | 0.014016 | 0.054992 | 0.050205 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.029 | 0 | 0.033 | 0.014016 | 0.054992 | 0.050205 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.028 | 0 | 0.033 | 0.014031 | 0.054992 | 0.05022 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.028 | 0 | 0.033 | 0.014031 | 0.055008 | 0.05022 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.028 | 0 | 0.033 | 0.014031 | 0.055008 | 0.05022 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.028 | 0 | 0.032 | 0.014031 | 0.055024 | 0.05022 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.028 | 0 | 0.032 | 0.014031 | 0.055039 | 0.050205 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.028 | 0 | 0.032 | 0.014031 | 0.055039 | 0.050205 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.028 | 0 | 0.032 | 0.014031 | 0.055039 | 0.050189 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.028 | 0 | 0.032 | 0.014031 | 0.055024 | 0.050189 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.028 | 0 | 0.032 | 0.014031 | 0.055008 | 0.050189 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.028 | 0 | 0.032 | 0.014031 | 0.055008 | 0.050189 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.028 | 0 | 0.032 | 0.014031 | 0.054992 | 0.050189 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.028 | 0 | 0.032 | 0.014031 | 0.054992 | 0.050173 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.028 | 0 | 0.032 | 0.014031 | 0.054992 | 0.050173 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.028 | 0 | 0.032 | 0.014031 | 0.054992 | 0.050173 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.028 | 0 | 0.032 | 0.014031 | 0.054992 | 0.050173 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.028 | 0 | 0.032 | 0.014031 | 0.054992 | 0.050173 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.028 | 0 | 0.032 | 0.014031 | 0.054992 | 0.050173 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.028 | 0 | 0.032 | 0.014031 | 0.055008 | 0.050173 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.028 | 0 | 0.032 | 0.014031 | 0.055008 | 0.050173 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.028 | 0 | 0.032 | 0.014031 | 0.055008 | 0.050173 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.028 | 0 | 0.032 | 0.014031 | 0.055008 | 0.050173 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.028 | 0 | 0.032 | 0.014031 | 0.055008 | 0.050173 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.028 | 0 | 0.032 | 0.014031 | 0.055008 | 0.050189 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.028 | 0 | 0.032 | 0.014031 | 0.055008 | 0.050189 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.028 | 0 | 0.032 | 0.014016 | 0.055008 | 0.050173 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.028 | 0 | 0.032 | 0.014016 | 0.055008 | 0.050173 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.028 | 0 | 0.032 | 0.014016 | 0.054992 | 0.050157 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.028 | 0 | 0.032 | 0.014016 | 0.054992 | 0.050157 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.028 | 0 | 0.032 | 0.014016 | 0.054992 | 0.050157 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.028 | 0 | 0.032 | 0.014016 | 0.054992 | 0.050142 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.028 | 0 | 0.032 | 0.014016 | 0.054992 | 0.050142 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.028 | 0 | 0.032 | 0.014016 | 0.054992 | 0.050142 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.028 | 0 | 0.032 | 0.014016 | 0.054992 | 0.050157 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.028 | 0 | 0.032 | 0.014016 | 0.054992 | 0.050157 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.028 | 0 | 0.032 | 0.014016 | 0.055008 | 0.050173 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.028 | 0 | 0.032 | 0.014031 | 0.055008 | 0.050189 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.028 | 0 | 0.032 | 0.014031 | 0.055008 | 0.050189 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.028 | 0 | 0.032 | 0.014016 | 0.055024 | 0.050189 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.028 | 0 | 0.032 | 0.014016 | 0.055024 | 0.050189 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.028 | 0 | 0.032 | 0.014 | 0.055024 | 0.050173 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.028 | 0 | 0.032 | 0.014 | 0.055024 | 0.050173 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.028 | 0 | 0.032 | 0.014 | 0.055024 | 0.050173 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.028 | 0 | 0.032 | 0.014 | 0.055008 | 0.050173 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.028 | 0 | 0.032 | 0.014 | 0.055008 | 0.050173 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.028 | 0 | 0.032 | 0.014 | 0.055008 | 0.050173 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.028 | 0 | 0.032 | 0.014 | 0.055008 | 0.050173 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.028 | 0 | 0.032 | 0.014 | 0.055008 | 0.050173 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.028 | 0 | 0.032 | 0.014 | 0.055008 | 0.050173 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.028 | 0 | 0.032 | 0.014016 | 0.055008 | 0.050173 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.028 | 0 | 0.032 | 0.014016 | 0.055008 | 0.050173 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.028 | 0 | 0.032 | 0.014016 | 0.055008 | 0.050173 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.028 | 0 | 0.032 | 0.014 | 0.055024 | 0.050189 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.028 | 0 | 0.032 | 0.014 | 0.055039 | 0.050189 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.028 | 0 | 0.032 | 0.014 | 0.055039 | 0.050205 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.028 | 0 | 0.032 | 0.014 | 0.055024 | 0.050205 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.028 | 0 | 0.032 | 0.014 | 0.055024 | 0.050205 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.028 | 0 | 0.032 | 0.014 | 0.055008 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.028 | 0 | 0.032 | 0.014 | 0.054992 | 0.050205 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.028 | 0 | 0.032 | 0.013984 | 0.054992 | 0.050205 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.028 | 0 | 0.032 | 0.013984 | 0.054992 | 0.050189 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.028 | 0 | 0.032 | 0.013984 | 0.054992 | 0.050173 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.028 | 0 | 0.032 | 0.014 | 0.054976 | 0.050173 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.028 | 0 | 0.032 | 0.013984 | 0.054976 | 0.050173 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.028 | 0 | 0.032 | 0.013984 | 0.054992 | 0.050173 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.028 | 0 | 0.032 | 0.013984 | 0.054992 | 0.050173 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.028 | 0 | 0.032 | 0.013984 | 0.054992 | 0.050189 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.028 | 0 | 0.032 | 0.013984 | 0.054992 | 0.050189 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.028 | 0 | 0.032 | 0.014 | 0.054992 | 0.050205 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.028 | 0 | 0.032 | 0.014 | 0.054992 | 0.050205 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.028 | 0 | 0.032 | 0.014 | 0.054992 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.028 | 0 | 0.032 | 0.014 | 0.055008 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.027 | 0 | 0.031 | 0.014 | 0.055008 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.027 | 0 | 0.031 | 0.014 | 0.055008 | 0.050205 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.027 | 0 | 0.031 | 0.014 | 0.055008 | 0.050205 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.027 | 0 | 0.031 | 0.014 | 0.055008 | 0.050189 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.027 | 0 | 0.031 | 0.014 | 0.054992 | 0.050189 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.027 | 0 | 0.031 | 0.014 | 0.054992 | 0.050189 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.027 | 0 | 0.031 | 0.014 | 0.054992 | 0.050189 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.027 | 0 | 0.031 | 0.014 | 0.054992 | 0.050189 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.027 | 0 | 0.031 | 0.014 | 0.054992 | 0.050189 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.027 | 0 | 0.031 | 0.014 | 0.054992 | 0.050189 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.027 | 0 | 0.031 | 0.014016 | 0.055008 | 0.050205 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.027 | 0 | 0.031 | 0.014 | 0.055008 | 0.05022 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.027 | 0 | 0.031 | 0.014 | 0.055024 | 0.05022 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.027 | 0 | 0.031 | 0.014 | 0.055024 | 0.05022 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.027 | 0 | 0.031 | 0.014 | 0.055039 | 0.05022 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.027 | 0 | 0.031 | 0.014 | 0.055039 | 0.05022 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.027 | 0 | 0.031 | 0.014 | 0.055024 | 0.05022 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.027 | 0 | 0.031 | 0.014 | 0.055024 | 0.050205 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.027 | 0 | 0.031 | 0.014 | 0.055024 | 0.050205 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.027 | 0 | 0.031 | 0.014 | 0.055024 | 0.050205 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.027 | 0 | 0.031 | 0.014 | 0.055024 | 0.050189 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.027 | 0 | 0.031 | 0.014 | 0.055024 | 0.050189 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.027 | 0 | 0.031 | 0.014 | 0.055024 | 0.050189 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.027 | 0 | 0.031 | 0.014 | 0.055024 | 0.050189 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.027 | 0 | 0.031 | 0.014 | 0.055024 | 0.050189 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.027 | 0 | 0.031 | 0.014 | 0.055024 | 0.050189 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.027 | 0 | 0.03 | 0.014 | 0.055024 | 0.050189 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.027 | 0 | 0.03 | 0.014 | 0.055039 | 0.050205 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.027 | 0 | 0.03 | 0.014 | 0.055039 | 0.050205 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.027 | 0 | 0.03 | 0.014 | 0.055039 | 0.050205 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.027 | 0 | 0.03 | 0.014 | 0.055039 | 0.050205 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.027 | 0 | 0.03 | 0.014 | 0.055039 | 0.050205 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.027 | 0 | 0.03 | 0.013984 | 0.055039 | 0.050205 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.027 | 0 | 0.03 | 0.013984 | 0.055039 | 0.050205 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.027 | 0 | 0.03 | 0.013984 | 0.055024 | 0.050205 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.027 | 0 | 0.03 | 0.013984 | 0.055024 | 0.050205 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.026 | 0 | 0.03 | 0.013984 | 0.055008 | 0.050189 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.026 | 0 | 0.03 | 0.013984 | 0.055008 | 0.050189 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.026 | 0 | 0.03 | 0.013984 | 0.055008 | 0.050173 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.026 | 0 | 0.03 | 0.013984 | 0.055008 | 0.050173 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.026 | 0 | 0.03 | 0.013984 | 0.055008 | 0.050173 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.026 | 0 | 0.03 | 0.013984 | 0.055008 | 0.050173 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.026 | 0 | 0.03 | 0.013984 | 0.055024 | 0.050173 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.026 | 0 | 0.03 | 0.013984 | 0.055024 | 0.050173 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.026 | 0 | 0.03 | 0.013984 | 0.055024 | 0.050173 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.026 | 0 | 0.03 | 0.013984 | 0.055024 | 0.050189 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.026 | 0 | 0.03 | 0.014 | 0.055024 | 0.050189 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.026 | 0 | 0.03 | 0.014 | 0.055008 | 0.050189 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.026 | 0 | 0.03 | 0.014 | 0.055008 | 0.050189 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.026 | 0 | 0.03 | 0.014 | 0.055008 | 0.050189 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.026 | 0 | 0.03 | 0.014 | 0.055008 | 0.050173 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.026 | 0 | 0.03 | 0.013984 | 0.054992 | 0.050157 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.026 | 0 | 0.03 | 0.013984 | 0.054992 | 0.050157 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.026 | 0 | 0.03 | 0.013984 | 0.054976 | 0.050142 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.026 | 0 | 0.03 | 0.013984 | 0.054976 | 0.050142 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.026 | 0 | 0.03 | 0.013984 | 0.054976 | 0.050142 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.026 | 0 | 0.03 | 0.013984 | 0.054976 | 0.050142 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.026 | 0 | 0.03 | 0.013984 | 0.054992 | 0.050142 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.026 | 0 | 0.03 | 0.013984 | 0.054992 | 0.050142 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.026 | 0 | 0.03 | 0.013984 | 0.054992 | 0.050157 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.026 | 0 | 0.03 | 0.013969 | 0.054992 | 0.050157 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.026 | 0 | 0.03 | 0.013969 | 0.054992 | 0.050173 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.026 | 0 | 0.03 | 0.013969 | 0.054992 | 0.050173 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.026 | 0 | 0.03 | 0.013969 | 0.054992 | 0.050173 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.026 | 0 | 0.03 | 0.013969 | 0.054992 | 0.050173 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.026 | 0 | 0.03 | 0.013969 | 0.054976 | 0.050173 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.026 | 0 | 0.03 | 0.013969 | 0.054976 | 0.050173 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.026 | 0 | 0.03 | 0.013969 | 0.054976 | 0.050173 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.026 | 0 | 0.03 | 0.013969 | 0.054961 | 0.050157 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.026 | 0 | 0.03 | 0.013969 | 0.054961 | 0.050157 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.026 | 0 | 0.03 | 0.013969 | 0.054961 | 0.050157 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.026 | 0 | 0.03 | 0.013969 | 0.054961 | 0.050157 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.026 | 0 | 0.03 | 0.013969 | 0.054961 | 0.050157 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.026 | 0 | 0.03 | 0.013969 | 0.054976 | 0.050157 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.026 | 0 | 0.03 | 0.013969 | 0.054976 | 0.050157 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.026 | 0 | 0.03 | 0.013969 | 0.054992 | 0.050173 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.026 | 0 | 0.03 | 0.013969 | 0.054992 | 0.050189 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.026 | 0 | 0.03 | 0.013969 | 0.055008 | 0.050189 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.026 | 0 | 0.03 | 0.013969 | 0.055008 | 0.050189 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.026 | 0 | 0.03 | 0.013969 | 0.055024 | 0.050205 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.026 | 0 | 0.03 | 0.013969 | 0.055024 | 0.050205 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.026 | 0 | 0.03 | 0.013969 | 0.055024 | 0.050205 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.026 | 0 | 0.03 | 0.013969 | 0.055008 | 0.050189 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.026 | 0 | 0.03 | 0.013969 | 0.055024 | 0.050189 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.026 | 0 | 0.03 | 0.013969 | 0.055024 | 0.050173 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.026 | 0 | 0.03 | 0.013969 | 0.055024 | 0.050173 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.026 | 0 | 0.03 | 0.013969 | 0.055008 | 0.050173 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.026 | 0 | 0.03 | 0.013969 | 0.055008 | 0.050173 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.026 | 0 | 0.03 | 0.013969 | 0.055024 | 0.050173 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.026 | 0 | 0.03 | 0.013969 | 0.055024 | 0.050173 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.026 | 0 | 0.03 | 0.013969 | 0.055024 | 0.050189 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.026 | 0 | 0.03 | 0.013969 | 0.055039 | 0.050189 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.026 | 0 | 0.03 | 0.013969 | 0.055039 | 0.050189 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.026 | 0 | 0.03 | 0.013969 | 0.055039 | 0.050205 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.026 | 0 | 0.03 | 0.013969 | 0.055055 | 0.050205 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.026 | 0 | 0.03 | 0.013953 | 0.055055 | 0.050205 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.026 | 0 | 0.03 | 0.013953 | 0.055055 | 0.050205 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.026 | 0 | 0.03 | 0.013937 | 0.055055 | 0.050205 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.026 | 0 | 0.03 | 0.013937 | 0.055055 | 0.050189 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.026 | 0 | 0.03 | 0.013937 | 0.055055 | 0.050189 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.026 | 0 | 0.03 | 0.013937 | 0.055039 | 0.050189 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.026 | 0 | 0.03 | 0.013937 | 0.055039 | 0.050189 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.026 | 0 | 0.03 | 0.013937 | 0.055039 | 0.050189 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.026 | 0 | 0.03 | 0.013937 | 0.055039 | 0.050189 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.026 | 0 | 0.03 | 0.013953 | 0.055039 | 0.050189 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.026 | 0 | 0.03 | 0.013953 | 0.055039 | 0.050189 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.026 | 0 | 0.03 | 0.013969 | 0.055039 | 0.050189 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.026 | 0 | 0.03 | 0.013969 | 0.055055 | 0.050205 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.026 | 0 | 0.03 | 0.013969 | 0.055055 | 0.050205 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.026 | 0 | 0.03 | 0.013969 | 0.055071 | 0.050205 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.026 | 0 | 0.03 | 0.013969 | 0.055071 | 0.050205 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.026 | 0 | 0.03 | 0.013969 | 0.055071 | 0.050189 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.026 | 0 | 0.03 | 0.013969 | 0.055071 | 0.050189 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.026 | 0 | 0.03 | 0.013969 | 0.055071 | 0.050189 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.026 | 0 | 0.03 | 0.013969 | 0.055055 | 0.050189 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.026 | 0 | 0.03 | 0.013969 | 0.055055 | 0.050189 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.026 | 0 | 0.03 | 0.013969 | 0.055039 | 0.050189 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.026 | 0 | 0.03 | 0.013969 | 0.055039 | 0.050173 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.026 | 0 | 0.03 | 0.013969 | 0.055039 | 0.050173 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.026 | 0 | 0.03 | 0.013969 | 0.055039 | 0.050173 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.026 | 0 | 0.03 | 0.013969 | 0.055039 | 0.050173 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.026 | 0 | 0.03 | 0.013969 | 0.055055 | 0.050173 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.026 | 0 | 0.03 | 0.013969 | 0.055055 | 0.050173 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.026 | 0 | 0.029 | 0.013969 | 0.055055 | 0.050189 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.026 | 0 | 0.029 | 0.013969 | 0.055055 | 0.050189 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.026 | 0 | 0.029 | 0.013969 | 0.055055 | 0.050189 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.026 | 0 | 0.029 | 0.013984 | 0.055055 | 0.050205 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.026 | 0 | 0.029 | 0.013984 | 0.055055 | 0.050205 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.026 | 0 | 0.029 | 0.013984 | 0.055039 | 0.050205 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.026 | 0 | 0.029 | 0.013984 | 0.055039 | 0.050205 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.026 | 0 | 0.029 | 0.013984 | 0.055039 | 0.050205 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.026 | 0 | 0.029 | 0.013984 | 0.055024 | 0.050205 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.026 | 0 | 0.029 | 0.013984 | 0.055024 | 0.050205 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.026 | 0 | 0.029 | 0.013984 | 0.055024 | 0.050189 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.026 | 0 | 0.029 | 0.013984 | 0.055024 | 0.050189 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.026 | 0 | 0.029 | 0.013984 | 0.055024 | 0.050189 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.026 | 0 | 0.029 | 0.013984 | 0.055024 | 0.050189 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.026 | 0 | 0.029 | 0.013984 | 0.055024 | 0.050205 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.026 | 0 | 0.029 | 0.013984 | 0.055024 | 0.050205 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.026 | 0 | 0.029 | 0.013984 | 0.055024 | 0.050205 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.026 | 0 | 0.029 | 0.014 | 0.055024 | 0.050205 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.026 | 0 | 0.028 | 0.014 | 0.055039 | 0.05022 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.026 | 0 | 0.028 | 0.014 | 0.055039 | 0.050205 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.026 | 0 | 0.028 | 0.014 | 0.055039 | 0.050205 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.026 | 0 | 0.028 | 0.014 | 0.055055 | 0.050205 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.026 | 0 | 0.028 | 0.014 | 0.055055 | 0.050189 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.026 | 0 | 0.028 | 0.014 | 0.055055 | 0.050189 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.026 | 0 | 0.028 | 0.014 | 0.055055 | 0.050189 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.025 | 0 | 0.028 | 0.014 | 0.055055 | 0.050189 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.025 | 0 | 0.028 | 0.014 | 0.055039 | 0.050189 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.025 | 0 | 0.028 | 0.014 | 0.055039 | 0.050189 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.025 | 0 | 0.028 | 0.014016 | 0.055039 | 0.050189 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.025 | 0 | 0.028 | 0.014016 | 0.055039 | 0.050189 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.025 | 0 | 0.028 | 0.014016 | 0.055055 | 0.050205 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.025 | 0 | 0.028 | 0.014016 | 0.055055 | 0.050205 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.025 | 0 | 0.028 | 0.014016 | 0.055055 | 0.050205 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.025 | 0 | 0.028 | 0.014016 | 0.055055 | 0.050205 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.025 | 0 | 0.028 | 0.014016 | 0.055055 | 0.050205 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.025 | 0 | 0.028 | 0.014 | 0.055071 | 0.050205 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.025 | 0 | 0.028 | 0.014 | 0.055055 | 0.050189 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.025 | 0 | 0.028 | 0.014 | 0.055055 | 0.050189 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.025 | 0 | 0.028 | 0.014 | 0.055055 | 0.050189 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.025 | 0 | 0.028 | 0.014 | 0.055055 | 0.050189 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.025 | 0 | 0.028 | 0.014 | 0.055055 | 0.050189 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.025 | 0 | 0.028 | 0.014 | 0.055039 | 0.050189 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.025 | 0 | 0.028 | 0.014 | 0.055039 | 0.050189 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.025 | 0 | 0.028 | 0.014 | 0.055039 | 0.050173 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.024 | 0 | 0.028 | 0.014 | 0.055039 | 0.050173 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.024 | 0 | 0.028 | 0.014 | 0.055039 | 0.050173 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.024 | 0 | 0.028 | 0.014016 | 0.055039 | 0.050189 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.024 | 0 | 0.028 | 0.014016 | 0.055055 | 0.050189 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.024 | 0 | 0.028 | 0.014 | 0.055071 | 0.050173 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.024 | 0 | 0.028 | 0.014 | 0.055071 | 0.050189 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.024 | 0 | 0.028 | 0.014 | 0.055087 | 0.050189 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.024 | 0 | 0.028 | 0.014 | 0.055087 | 0.050189 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.024 | 0 | 0.028 | 0.014 | 0.055087 | 0.050205 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.024 | 0 | 0.028 | 0.014016 | 0.055087 | 0.050205 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.024 | 0 | 0.028 | 0.014016 | 0.055071 | 0.05022 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.024 | 0 | 0.028 | 0.014 | 0.055071 | 0.05022 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.024 | 0 | 0.028 | 0.014 | 0.055055 | 0.050205 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.024 | 0 | 0.028 | 0.014 | 0.055055 | 0.050189 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.024 | 0 | 0.028 | 0.014 | 0.055055 | 0.050189 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.024 | 0 | 0.028 | 0.014 | 0.055055 | 0.050189 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.024 | 0 | 0.028 | 0.014 | 0.055055 | 0.050189 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.024 | 0 | 0.028 | 0.014 | 0.055071 | 0.050189 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.024 | 0 | 0.028 | 0.013984 | 0.055071 | 0.050189 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.024 | 0 | 0.028 | 0.013984 | 0.055087 | 0.050189 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.024 | 0 | 0.028 | 0.013984 | 0.055087 | 0.050205 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.024 | 0 | 0.028 | 0.014 | 0.055071 | 0.050205 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.024 | 0 | 0.028 | 0.014 | 0.055071 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.024 | 0 | 0.028 | 0.014 | 0.055071 | 0.05022 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.024 | 0 | 0.028 | 0.014 | 0.055087 | 0.05022 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.024 | 0 | 0.028 | 0.014 | 0.055087 | 0.050205 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.024 | 0 | 0.028 | 0.013984 | 0.055087 | 0.050205 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.024 | 0 | 0.028 | 0.013984 | 0.055087 | 0.050189 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.024 | 0 | 0.028 | 0.013984 | 0.055071 | 0.050189 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.024 | 0 | 0.028 | 0.013984 | 0.055071 | 0.050189 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.024 | 0 | 0.028 | 0.013984 | 0.055071 | 0.050189 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.024 | 0 | 0.028 | 0.013984 | 0.055055 | 0.050189 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.024 | 0 | 0.028 | 0.013984 | 0.055071 | 0.050189 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.024 | 0 | 0.028 | 0.013984 | 0.055071 | 0.050189 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.024 | 0 | 0.028 | 0.014 | 0.055071 | 0.050189 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.024 | 0 | 0.028 | 0.014 | 0.055071 | 0.050189 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.024 | 0 | 0.028 | 0.014 | 0.055087 | 0.050205 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.024 | 0 | 0.028 | 0.014 | 0.055102 | 0.050205 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.024 | 0 | 0.028 | 0.013984 | 0.055102 | 0.050205 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.024 | 0 | 0.028 | 0.013984 | 0.055102 | 0.050205 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.024 | 0 | 0.028 | 0.013984 | 0.055102 | 0.050205 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.024 | 0 | 0.028 | 0.013984 | 0.055102 | 0.050205 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.024 | 0 | 0.028 | 0.013984 | 0.055102 | 0.050205 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.024 | 0 | 0.028 | 0.013984 | 0.055102 | 0.050189 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.024 | 0 | 0.028 | 0.013969 | 0.055102 | 0.050189 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.024 | 0 | 0.028 | 0.013969 | 0.055087 | 0.050189 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.024 | 0 | 0.028 | 0.013969 | 0.055087 | 0.050189 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.024 | 0 | 0.028 | 0.013969 | 0.055087 | 0.050189 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.024 | 0 | 0.028 | 0.013969 | 0.055087 | 0.050173 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.024 | 0 | 0.028 | 0.013984 | 0.055087 | 0.050189 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.024 | 0 | 0.028 | 0.013984 | 0.055087 | 0.050189 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.024 | 0 | 0.028 | 0.014 | 0.055087 | 0.050189 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.024 | 0 | 0.028 | 0.014 | 0.055102 | 0.050189 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.024 | 0 | 0.028 | 0.014 | 0.055102 | 0.050189 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.024 | 0 | 0.028 | 0.013984 | 0.055118 | 0.050189 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.024 | 0 | 0.028 | 0.013984 | 0.055118 | 0.050189 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.024 | 0 | 0.028 | 0.013984 | 0.055102 | 0.050173 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.024 | 0 | 0.028 | 0.013969 | 0.055102 | 0.050173 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.024 | 0 | 0.028 | 0.013969 | 0.055102 | 0.050157 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.024 | 0 | 0.028 | 0.013969 | 0.055087 | 0.050157 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.024 | 0 | 0.028 | 0.013969 | 0.055087 | 0.050157 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.024 | 0 | 0.028 | 0.013969 | 0.055071 | 0.050157 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.024 | 0 | 0.028 | 0.013969 | 0.055071 | 0.050157 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.024 | 0 | 0.028 | 0.013969 | 0.055071 | 0.050157 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.024 | 0 | 0.027 | 0.013969 | 0.055071 | 0.050157 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.024 | 0 | 0.027 | 0.013969 | 0.055071 | 0.050157 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.024 | 0 | 0.027 | 0.013984 | 0.055071 | 0.050173 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.024 | 0 | 0.027 | 0.013984 | 0.055071 | 0.050173 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.024 | 0 | 0.027 | 0.013984 | 0.055071 | 0.050173 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.024 | 0 | 0.027 | 0.013969 | 0.055087 | 0.050173 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.024 | 0 | 0.027 | 0.013969 | 0.055087 | 0.050157 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.024 | 0 | 0.027 | 0.013953 | 0.055102 | 0.050173 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.024 | 0 | 0.027 | 0.013953 | 0.055102 | 0.050173 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.024 | 0 | 0.027 | 0.013953 | 0.055087 | 0.050173 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.024 | 0 | 0.027 | 0.013969 | 0.055071 | 0.050173 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.024 | 0 | 0.027 | 0.013969 | 0.055071 | 0.050189 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.024 | 0 | 0.027 | 0.013969 | 0.055071 | 0.050173 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.024 | 0 | 0.027 | 0.013969 | 0.055071 | 0.050173 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.024 | 0 | 0.027 | 0.013969 | 0.055071 | 0.050157 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.024 | 0 | 0.027 | 0.013969 | 0.055071 | 0.050157 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.024 | 0 | 0.027 | 0.013969 | 0.055071 | 0.050157 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.024 | 0 | 0.027 | 0.013953 | 0.055071 | 0.050157 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.024 | 0 | 0.027 | 0.013953 | 0.055071 | 0.050157 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.024 | 0 | 0.027 | 0.013937 | 0.055071 | 0.050157 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.024 | 0 | 0.027 | 0.013937 | 0.055071 | 0.050157 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.024 | 0 | 0.026 | 0.013937 | 0.055071 | 0.050157 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.024 | 0 | 0.026 | 0.013953 | 0.055071 | 0.050173 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.024 | 0 | 0.026 | 0.013969 | 0.055055 | 0.050189 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.024 | 0 | 0.026 | 0.013969 | 0.055055 | 0.050189 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.024 | 0 | 0.026 | 0.013969 | 0.055055 | 0.050189 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.024 | 0 | 0.026 | 0.013969 | 0.055055 | 0.050189 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.024 | 0 | 0.026 | 0.013969 | 0.055039 | 0.050173 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.024 | 0 | 0.026 | 0.013969 | 0.055039 | 0.050157 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.024 | 0 | 0.026 | 0.013969 | 0.055039 | 0.050142 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.024 | 0 | 0.026 | 0.013969 | 0.055039 | 0.050142 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.024 | 0 | 0.026 | 0.013969 | 0.055039 | 0.050142 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.024 | 0 | 0.026 | 0.013969 | 0.055039 | 0.050142 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.024 | 0 | 0.026 | 0.013969 | 0.055039 | 0.050142 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.024 | 0 | 0.026 | 0.013969 | 0.055039 | 0.050142 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.024 | 0 | 0.026 | 0.013969 | 0.055039 | 0.050157 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.024 | 0 | 0.026 | 0.013984 | 0.055039 | 0.050157 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.024 | 0 | 0.026 | 0.013984 | 0.055039 | 0.050173 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.024 | 0 | 0.026 | 0.014 | 0.055039 | 0.050173 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.024 | 0 | 0.026 | 0.014 | 0.055039 | 0.050173 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.024 | 0 | 0.026 | 0.014 | 0.055039 | 0.050173 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.024 | 0 | 0.026 | 0.014 | 0.055055 | 0.050157 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.024 | 0 | 0.026 | 0.014 | 0.055055 | 0.050157 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.024 | 0 | 0.026 | 0.014 | 0.055055 | 0.050157 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.024 | 0 | 0.026 | 0.014 | 0.055039 | 0.050157 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.024 | 0 | 0.026 | 0.014 | 0.055039 | 0.050157 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.024 | 0 | 0.026 | 0.014 | 0.055039 | 0.050157 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.024 | 0 | 0.026 | 0.014 | 0.055039 | 0.050157 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.024 | 0 | 0.026 | 0.014 | 0.055039 | 0.050157 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.024 | 0 | 0.026 | 0.014016 | 0.055039 | 0.050157 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.024 | 0 | 0.026 | 0.014016 | 0.055039 | 0.050157 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.024 | 0 | 0.026 | 0.014016 | 0.055039 | 0.050157 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.023 | 0 | 0.026 | 0.014016 | 0.055055 | 0.050157 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.023 | 0 | 0.026 | 0.014016 | 0.055055 | 0.050157 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.023 | 0 | 0.026 | 0.014 | 0.055055 | 0.050157 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.023 | 0 | 0.026 | 0.013984 | 0.055055 | 0.050157 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.023 | 0 | 0.026 | 0.014 | 0.055039 | 0.050157 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.023 | 0 | 0.026 | 0.014 | 0.055039 | 0.050173 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.023 | 0 | 0.026 | 0.014 | 0.055039 | 0.050173 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.023 | 0 | 0.026 | 0.014 | 0.055039 | 0.050173 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.023 | 0 | 0.026 | 0.014 | 0.055039 | 0.050157 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.023 | 0 | 0.026 | 0.014 | 0.055039 | 0.050142 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.023 | 0 | 0.026 | 0.014 | 0.055039 | 0.050142 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.023 | 0 | 0.026 | 0.014 | 0.055039 | 0.050126 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.023 | 0 | 0.026 | 0.014 | 0.055039 | 0.050126 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.023 | 0 | 0.026 | 0.014 | 0.055039 | 0.050126 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.023 | 0 | 0.026 | 0.013984 | 0.055039 | 0.050142 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.023 | 0 | 0.026 | 0.013984 | 0.055055 | 0.050142 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.023 | 0 | 0.026 | 0.014 | 0.055055 | 0.050142 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.023 | 0 | 0.026 | 0.014 | 0.055055 | 0.050142 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.023 | 0 | 0.026 | 0.014 | 0.055055 | 0.050157 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.023 | 0 | 0.026 | 0.014 | 0.055071 | 0.050157 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.023 | 0 | 0.026 | 0.014 | 0.055071 | 0.050157 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.023 | 0 | 0.026 | 0.014 | 0.055071 | 0.050157 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.022 | 0 | 0.026 | 0.014 | 0.055071 | 0.050157 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.022 | 0 | 0.026 | 0.014 | 0.055071 | 0.050157 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.022 | 0 | 0.026 | 0.014 | 0.055071 | 0.050157 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.022 | 0 | 0.026 | 0.014 | 0.055071 | 0.050157 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.022 | 0 | 0.026 | 0.014 | 0.055055 | 0.050173 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.022 | 0 | 0.026 | 0.014 | 0.055055 | 0.050173 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.022 | 0 | 0.026 | 0.014 | 0.055055 | 0.050173 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.022 | 0 | 0.026 | 0.014 | 0.055071 | 0.050173 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.022 | 0 | 0.026 | 0.014 | 0.055071 | 0.050173 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.022 | 0 | 0.026 | 0.014016 | 0.055071 | 0.050173 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.022 | 0 | 0.026 | 0.014016 | 0.055087 | 0.050189 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.022 | 0 | 0.026 | 0.014016 | 0.055087 | 0.050189 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.022 | 0 | 0.026 | 0.014016 | 0.055102 | 0.050173 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.022 | 0 | 0.026 | 0.014016 | 0.055102 | 0.050173 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.022 | 0 | 0.026 | 0.014016 | 0.055102 | 0.050173 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.022 | 0 | 0.026 | 0.014016 | 0.055102 | 0.050173 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.022 | 0 | 0.026 | 0.014016 | 0.055087 | 0.050173 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.022 | 0 | 0.026 | 0.014016 | 0.055071 | 0.050173 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.022 | 0 | 0.026 | 0.014016 | 0.055055 | 0.050173 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.022 | 0 | 0.026 | 0.014016 | 0.055055 | 0.050157 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.022 | 0 | 0.026 | 0.014016 | 0.055055 | 0.050157 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.022 | 0 | 0.026 | 0.014016 | 0.055055 | 0.050157 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.022 | 0 | 0.026 | 0.014016 | 0.055055 | 0.050157 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.022 | 0 | 0.026 | 0.014016 | 0.055055 | 0.050157 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.022 | 0 | 0.026 | 0.014016 | 0.055055 | 0.050157 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.022 | 0 | 0.026 | 0.014016 | 0.055071 | 0.050173 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.022 | 0 | 0.026 | 0.014016 | 0.055087 | 0.050173 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.022 | 0 | 0.026 | 0.014016 | 0.055087 | 0.050189 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.022 | 0 | 0.026 | 0.014016 | 0.055087 | 0.050189 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.022 | 0 | 0.026 | 0.014016 | 0.055087 | 0.050205 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.022 | 0 | 0.026 | 0.014016 | 0.055087 | 0.050205 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.022 | 0 | 0.026 | 0.014016 | 0.055087 | 0.050205 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.022 | 0 | 0.026 | 0.014016 | 0.055071 | 0.050205 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.022 | 0 | 0.026 | 0.014016 | 0.055071 | 0.050189 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.022 | 0 | 0.026 | 0.014016 | 0.055071 | 0.050189 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.022 | 0 | 0.026 | 0.014016 | 0.055071 | 0.050173 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.022 | 0 | 0.026 | 0.014016 | 0.055071 | 0.050173 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.022 | 0 | 0.026 | 0.014016 | 0.055055 | 0.050173 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.022 | 0 | 0.026 | 0.014016 | 0.055071 | 0.050173 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.022 | 0 | 0.026 | 0.014016 | 0.055071 | 0.050173 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.022 | 0 | 0.026 | 0.014016 | 0.055071 | 0.050173 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.022 | 0 | 0.026 | 0.014016 | 0.055071 | 0.050173 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.022 | 0 | 0.026 | 0.014016 | 0.055071 | 0.050189 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.022 | 0 | 0.026 | 0.014031 | 0.055071 | 0.050189 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.022 | 0 | 0.026 | 0.014031 | 0.055071 | 0.050189 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.022 | 0 | 0.026 | 0.014031 | 0.055087 | 0.050189 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.022 | 0 | 0.026 | 0.014031 | 0.055087 | 0.050189 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.022 | 0 | 0.026 | 0.014031 | 0.055087 | 0.050189 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.022 | 0 | 0.026 | 0.014031 | 0.055087 | 0.050189 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.022 | 0 | 0.026 | 0.014031 | 0.055087 | 0.050189 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.022 | 0 | 0.026 | 0.014031 | 0.055071 | 0.050189 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.022 | 0 | 0.026 | 0.014031 | 0.055071 | 0.050189 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.022 | 0 | 0.026 | 0.014031 | 0.055071 | 0.050173 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.022 | 0 | 0.026 | 0.014031 | 0.055071 | 0.050173 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.022 | 0 | 0.026 | 0.014031 | 0.055071 | 0.050173 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.022 | 0 | 0.025 | 0.014031 | 0.055071 | 0.050173 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.022 | 0 | 0.025 | 0.014031 | 0.055087 | 0.050173 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.022 | 0 | 0.025 | 0.014031 | 0.055087 | 0.050189 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.022 | 0 | 0.025 | 0.014031 | 0.055087 | 0.050189 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.022 | 0 | 0.025 | 0.014031 | 0.055087 | 0.050189 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.022 | 0 | 0.025 | 0.014031 | 0.055102 | 0.050205 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.022 | 0 | 0.025 | 0.014031 | 0.055102 | 0.05022 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.022 | 0 | 0.025 | 0.014031 | 0.055102 | 0.05022 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.022 | 0 | 0.025 | 0.014031 | 0.055102 | 0.05022 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.022 | 0 | 0.025 | 0.014031 | 0.055118 | 0.05022 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.022 | 0 | 0.025 | 0.014031 | 0.055118 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.022 | 0 | 0.025 | 0.014031 | 0.055118 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.022 | 0 | 0.025 | 0.014031 | 0.055102 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.022 | 0 | 0.025 | 0.014047 | 0.055102 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.022 | 0 | 0.025 | 0.014047 | 0.055102 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.022 | 0 | 0.025 | 0.014047 | 0.055102 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.022 | 0 | 0.025 | 0.014047 | 0.055102 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.022 | 0 | 0.025 | 0.014047 | 0.055118 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.022 | 0 | 0.025 | 0.014047 | 0.055118 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.022 | 0 | 0.025 | 0.014063 | 0.055118 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.022 | 0 | 0.025 | 0.014063 | 0.055118 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.022 | 0 | 0.025 | 0.014063 | 0.055118 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.022 | 0 | 0.025 | 0.014063 | 0.055102 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.022 | 0 | 0.025 | 0.014063 | 0.055102 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.022 | 0 | 0.025 | 0.014063 | 0.055102 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.022 | 0 | 0.025 | 0.014063 | 0.055102 | 0.05022 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.022 | 0 | 0.025 | 0.014063 | 0.055102 | 0.05022 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.022 | 0 | 0.025 | 0.014063 | 0.055102 | 0.05022 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.022 | 0 | 0.025 | 0.014063 | 0.055087 | 0.05022 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.022 | 0 | 0.025 | 0.014063 | 0.055087 | 0.050205 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.022 | 0 | 0.025 | 0.014063 | 0.055087 | 0.050205 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.022 | 0 | 0.024 | 0.014063 | 0.055087 | 0.050205 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.022 | 0 | 0.024 | 0.014063 | 0.055087 | 0.050205 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.022 | 0 | 0.024 | 0.014063 | 0.055087 | 0.050205 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.022 | 0 | 0.024 | 0.014063 | 0.055102 | 0.050205 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.022 | 0 | 0.024 | 0.014047 | 0.055102 | 0.050205 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.022 | 0 | 0.024 | 0.014047 | 0.055118 | 0.050205 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.022 | 0 | 0.024 | 0.014031 | 0.055118 | 0.050189 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.022 | 0 | 0.024 | 0.014047 | 0.055118 | 0.050205 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.022 | 0 | 0.024 | 0.014047 | 0.055102 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.022 | 0 | 0.024 | 0.014047 | 0.055087 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.022 | 0 | 0.024 | 0.014047 | 0.055087 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.022 | 0 | 0.024 | 0.014031 | 0.055071 | 0.05022 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.022 | 0 | 0.024 | 0.014031 | 0.055071 | 0.050205 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.022 | 0 | 0.024 | 0.014031 | 0.055071 | 0.050205 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.022 | 0 | 0.024 | 0.014031 | 0.055071 | 0.050189 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.022 | 0 | 0.024 | 0.014031 | 0.055071 | 0.050189 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.022 | 0 | 0.024 | 0.014031 | 0.055071 | 0.050189 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.022 | 0 | 0.024 | 0.014031 | 0.055071 | 0.050189 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.022 | 0 | 0.024 | 0.014031 | 0.055071 | 0.050189 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.022 | 0 | 0.024 | 0.014031 | 0.055071 | 0.050189 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.022 | 0 | 0.024 | 0.014031 | 0.055071 | 0.050189 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.022 | 0 | 0.024 | 0.014031 | 0.055071 | 0.050205 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.022 | 0 | 0.024 | 0.014031 | 0.055087 | 0.050205 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.022 | 0 | 0.024 | 0.014031 | 0.055087 | 0.050205 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.022 | 0 | 0.024 | 0.014016 | 0.055087 | 0.050205 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.022 | 0 | 0.024 | 0.014016 | 0.055087 | 0.050189 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.022 | 0 | 0.024 | 0.014016 | 0.055071 | 0.050189 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.022 | 0 | 0.024 | 0.014016 | 0.055071 | 0.050189 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.022 | 0 | 0.024 | 0.014016 | 0.055071 | 0.050189 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.022 | 0 | 0.024 | 0.014016 | 0.055055 | 0.050173 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.022 | 0 | 0.024 | 0.014016 | 0.055055 | 0.050173 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.022 | 0 | 0.024 | 0.014016 | 0.055055 | 0.050173 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.022 | 0 | 0.024 | 0.014016 | 0.055055 | 0.050173 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.022 | 0 | 0.024 | 0.014016 | 0.055055 | 0.050173 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.022 | 0 | 0.024 | 0.014031 | 0.055055 | 0.050173 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.022 | 0 | 0.024 | 0.014031 | 0.055055 | 0.050173 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.022 | 0 | 0.024 | 0.014031 | 0.055055 | 0.050189 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.022 | 0 | 0.024 | 0.014031 | 0.055055 | 0.050189 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.022 | 0 | 0.024 | 0.014031 | 0.055055 | 0.050205 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.022 | 0 | 0.024 | 0.014016 | 0.055055 | 0.050205 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.022 | 0 | 0.024 | 0.014016 | 0.055055 | 0.050205 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.022 | 0 | 0.024 | 0.014016 | 0.055055 | 0.050205 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.022 | 0 | 0.024 | 0.014016 | 0.055039 | 0.050205 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.022 | 0 | 0.024 | 0.014016 | 0.055039 | 0.050205 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.022 | 0 | 0.024 | 0.014016 | 0.055039 | 0.050205 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.022 | 0 | 0.024 | 0.014016 | 0.055024 | 0.050205 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.022 | 0 | 0.024 | 0.014016 | 0.055024 | 0.050189 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.021 | 0 | 0.024 | 0.014031 | 0.055024 | 0.050189 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.021 | 0 | 0.024 | 0.014031 | 0.055024 | 0.050189 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.021 | 0 | 0.024 | 0.014031 | 0.055024 | 0.050189 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.021 | 0 | 0.024 | 0.014016 | 0.055039 | 0.050189 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.021 | 0 | 0.024 | 0.014016 | 0.055039 | 0.050205 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.021 | 0 | 0.024 | 0.014031 | 0.055039 | 0.050205 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.021 | 0 | 0.024 | 0.014031 | 0.055024 | 0.050205 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.021 | 0 | 0.024 | 0.014047 | 0.055024 | 0.05022 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.021 | 0 | 0.024 | 0.014047 | 0.055024 | 0.05022 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.021 | 0 | 0.024 | 0.014047 | 0.055024 | 0.05022 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.021 | 0 | 0.024 | 0.014031 | 0.055039 | 0.05022 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.021 | 0 | 0.024 | 0.014031 | 0.055039 | 0.05022 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.021 | 0 | 0.024 | 0.014031 | 0.055039 | 0.050205 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.021 | 0 | 0.024 | 0.014031 | 0.055039 | 0.050205 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.021 | 0 | 0.024 | 0.014031 | 0.055024 | 0.050205 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.021 | 0 | 0.024 | 0.014031 | 0.055024 | 0.050205 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.021 | 0 | 0.024 | 0.014031 | 0.055024 | 0.050189 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.021 | 0 | 0.024 | 0.014031 | 0.055024 | 0.050189 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.021 | 0 | 0.024 | 0.014031 | 0.055024 | 0.050205 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.021 | 0 | 0.024 | 0.014031 | 0.055024 | 0.050205 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.021 | 0 | 0.024 | 0.014031 | 0.055039 | 0.050205 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.021 | 0 | 0.024 | 0.014031 | 0.055039 | 0.050205 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.021 | 0 | 0.024 | 0.014031 | 0.055039 | 0.05022 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.021 | 0 | 0.024 | 0.014031 | 0.055055 | 0.05022 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.021 | 0 | 0.024 | 0.014031 | 0.055055 | 0.05022 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.021 | 0 | 0.024 | 0.014031 | 0.055055 | 0.05022 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.021 | 0 | 0.024 | 0.014031 | 0.055039 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.024 | 0.014031 | 0.055039 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.024 | 0.014031 | 0.055039 | 0.050236 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.024 | 0.014031 | 0.055039 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.024 | 0.014031 | 0.055024 | 0.05022 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.024 | 0.014031 | 0.055024 | 0.05022 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.024 | 0.014031 | 0.055024 | 0.05022 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.024 | 0.014031 | 0.055024 | 0.05022 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.024 | 0.014031 | 0.055039 | 0.05022 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.024 | 0.014031 | 0.055039 | 0.05022 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.024 | 0.014031 | 0.055039 | 0.05022 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.024 | 0.014031 | 0.055055 | 0.05022 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.024 | 0.014047 | 0.055055 | 0.050236 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.024 | 0.014047 | 0.055055 | 0.050236 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.024 | 0.014047 | 0.055055 | 0.050236 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.024 | 0.014047 | 0.055055 | 0.050236 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.024 | 0.014047 | 0.055055 | 0.050236 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.024 | 0.014047 | 0.055055 | 0.05022 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.024 | 0.014031 | 0.055055 | 0.05022 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.024 | 0.014031 | 0.055039 | 0.05022 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.024 | 0.014031 | 0.055039 | 0.05022 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.024 | 0.014031 | 0.055039 | 0.05022 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.024 | 0.014031 | 0.055039 | 0.05022 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.024 | 0.014031 | 0.055039 | 0.05022 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.024 | 0.014031 | 0.055039 | 0.05022 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.024 | 0.014047 | 0.055039 | 0.05022 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.024 | 0.014047 | 0.055055 | 0.05022 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.024 | 0.014047 | 0.055055 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.024 | 0.014031 | 0.055071 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.024 | 0.014031 | 0.055071 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.024 | 0.014031 | 0.055071 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.024 | 0.014031 | 0.055071 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.024 | 0.014031 | 0.055055 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.024 | 0.014031 | 0.055055 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.024 | 0.014031 | 0.055039 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.024 | 0.014031 | 0.055039 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.024 | 0.014031 | 0.055039 | 0.05022 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.024 | 0.014031 | 0.055039 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.024 | 0.014031 | 0.055039 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.024 | 0.014031 | 0.055039 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.024 | 0.014031 | 0.055039 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.024 | 0.014031 | 0.055039 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.024 | 0.014031 | 0.055039 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.024 | 0.014047 | 0.055055 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.024 | 0.014047 | 0.055055 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.024 | 0.014047 | 0.055055 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.024 | 0.014047 | 0.055055 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.024 | 0.014047 | 0.055055 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.024 | 0.014047 | 0.055039 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.024 | 0.014047 | 0.055039 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.024 | 0.014047 | 0.055039 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.024 | 0.014047 | 0.055039 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.023 | 0.014047 | 0.055039 | 0.05022 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.023 | 0.014047 | 0.055039 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.023 | 0.014047 | 0.055024 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.023 | 0.014047 | 0.055024 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.023 | 0.014047 | 0.055024 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.023 | 0.014047 | 0.055024 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.023 | 0.014047 | 0.055039 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.023 | 0.014047 | 0.055039 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.023 | 0.014047 | 0.055039 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.023 | 0.014047 | 0.055039 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.023 | 0.014047 | 0.055039 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.023 | 0.014047 | 0.055024 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.023 | 0.014047 | 0.055024 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.023 | 0.014047 | 0.055024 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.023 | 0.014047 | 0.055024 | 0.050205 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.023 | 0.014047 | 0.055008 | 0.050205 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.023 | 0.014047 | 0.055008 | 0.050205 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.023 | 0.014047 | 0.055008 | 0.050205 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.023 | 0.014047 | 0.055008 | 0.050189 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.023 | 0.014047 | 0.055008 | 0.050189 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.023 | 0.014047 | 0.055008 | 0.050189 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.023 | 0.014047 | 0.055008 | 0.050205 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.023 | 0.014047 | 0.055008 | 0.050205 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.023 | 0.014047 | 0.055024 | 0.050205 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.023 | 0.014047 | 0.055024 | 0.050205 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.023 | 0.014047 | 0.055039 | 0.050205 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.023 | 0.014047 | 0.055039 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.023 | 0.014047 | 0.055039 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.023 | 0.014047 | 0.055039 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.022 | 0.014047 | 0.055024 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.022 | 0.014047 | 0.055024 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.022 | 0.014047 | 0.055024 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.022 | 0.014047 | 0.055024 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.022 | 0.014047 | 0.055024 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.022 | 0.014047 | 0.055024 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.022 | 0.014047 | 0.055024 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.022 | 0.014047 | 0.055039 | 0.05022 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.022 | 0.014047 | 0.055039 | 0.05022 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.022 | 0.014047 | 0.055039 | 0.05022 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.022 | 0.014063 | 0.055039 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.022 | 0.014079 | 0.055039 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.022 | 0.014079 | 0.055039 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.022 | 0.014079 | 0.055039 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.022 | 0.014079 | 0.055055 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.022 | 0.014063 | 0.055055 | 0.05022 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.022 | 0.014063 | 0.055055 | 0.05022 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.022 | 0.014063 | 0.055055 | 0.05022 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.022 | 0.014063 | 0.055039 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.022 | 0.014063 | 0.055039 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.022 | 0.014063 | 0.055039 | 0.050205 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.022 | 0.014063 | 0.055039 | 0.050205 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.022 | 0.014063 | 0.055039 | 0.050205 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.022 | 0.014079 | 0.055039 | 0.050205 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.022 | 0.014079 | 0.055039 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.022 | 0.014094 | 0.055039 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.022 | 0.014079 | 0.055039 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.022 | 0.014079 | 0.055055 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.022 | 0.014063 | 0.055055 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.022 | 0.014063 | 0.055055 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.022 | 0.014063 | 0.055055 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.022 | 0.014063 | 0.055055 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.022 | 0.014063 | 0.055055 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.022 | 0.014063 | 0.055055 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.022 | 0.014063 | 0.055039 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.022 | 0.014063 | 0.055039 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.022 | 0.014063 | 0.055039 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.022 | 0.014063 | 0.055039 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.022 | 0.014063 | 0.055039 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.022 | 0.014063 | 0.055039 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.022 | 0.014063 | 0.055039 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.022 | 0.014063 | 0.055055 | 0.05022 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.022 | 0.014063 | 0.055055 | 0.050236 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.022 | 0.014063 | 0.055055 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.022 | 0.014063 | 0.055055 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.022 | 0.014063 | 0.055055 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.022 | 0.014063 | 0.055055 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.022 | 0.014063 | 0.055055 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.022 | 0.014063 | 0.055039 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.022 | 0.014063 | 0.055039 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.022 | 0.014063 | 0.055039 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.022 | 0.014063 | 0.055039 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.022 | 0.014063 | 0.055039 | 0.05022 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.022 | 0.014063 | 0.055039 | 0.05022 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.022 | 0.014063 | 0.055039 | 0.05022 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.022 | 0.014063 | 0.055039 | 0.05022 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.022 | 0.014063 | 0.055039 | 0.05022 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.022 | 0.014063 | 0.055039 | 0.05022 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.022 | 0.014063 | 0.055039 | 0.05022 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.022 | 0.014079 | 0.055055 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.022 | 0.014079 | 0.055055 | 0.050252 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.022 | 0.014094 | 0.055055 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.022 | 0.014094 | 0.055039 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.022 | 0.014094 | 0.055055 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.022 | 0.014079 | 0.055055 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.022 | 0.014079 | 0.055055 | 0.050252 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.022 | 0.014079 | 0.055055 | 0.050252 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.022 | 0.014079 | 0.055055 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.022 | 0.014079 | 0.055055 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.022 | 0.014079 | 0.055039 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.022 | 0.014079 | 0.055039 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.022 | 0.014079 | 0.055055 | 0.050252 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.022 | 0.014094 | 0.055055 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.022 | 0.014094 | 0.055055 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.022 | 0.01411 | 0.055055 | 0.050283 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.022 | 0.01411 | 0.055071 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.022 | 0.014094 | 0.055071 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.022 | 0.014094 | 0.055087 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.022 | 0.014079 | 0.055087 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.022 | 0.014079 | 0.055087 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.022 | 0.014079 | 0.055071 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.02 | 0 | 0.022 | 0.014079 | 0.055055 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.019 | 0 | 0.022 | 0.014079 | 0.055039 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.019 | 0 | 0.022 | 0.014079 | 0.055039 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.019 | 0 | 0.022 | 0.014094 | 0.055039 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.019 | 0 | 0.022 | 0.014094 | 0.055039 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.019 | 0 | 0.022 | 0.014094 | 0.055039 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.019 | 0 | 0.022 | 0.014094 | 0.055055 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.019 | 0 | 0.022 | 0.014079 | 0.055055 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.019 | 0 | 0.022 | 0.014079 | 0.055071 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.019 | 0 | 0.022 | 0.014079 | 0.055071 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.019 | 0 | 0.022 | 0.014079 | 0.055071 | 0.050299 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.019 | 0 | 0.022 | 0.014079 | 0.055071 | 0.050299 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.019 | 0 | 0.022 | 0.014079 | 0.055071 | 0.050315 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.019 | 0 | 0.022 | 0.014094 | 0.055071 | 0.050315 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.019 | 0 | 0.022 | 0.014079 | 0.055071 | 0.050299 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.019 | 0 | 0.022 | 0.014079 | 0.055071 | 0.050299 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.019 | 0 | 0.022 | 0.014079 | 0.055071 | 0.050299 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.019 | 0 | 0.022 | 0.014079 | 0.055071 | 0.050299 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.019 | 0 | 0.022 | 0.014079 | 0.055071 | 0.050299 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.019 | 0 | 0.022 | 0.014079 | 0.055055 | 0.050299 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.019 | 0 | 0.022 | 0.014079 | 0.055055 | 0.050299 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.019 | 0 | 0.022 | 0.014079 | 0.055055 | 0.050299 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.019 | 0 | 0.022 | 0.014079 | 0.055055 | 0.050299 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.019 | 0 | 0.022 | 0.014079 | 0.055055 | 0.050299 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.022 | 0.014079 | 0.055055 | 0.050299 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.022 | 0.014079 | 0.055055 | 0.050299 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.022 | 0.014079 | 0.055055 | 0.050299 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.022 | 0.014079 | 0.055055 | 0.050299 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.022 | 0.014079 | 0.055055 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.022 | 0.014079 | 0.055055 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.022 | 0.014079 | 0.055055 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.022 | 0.014079 | 0.055055 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.022 | 0.014079 | 0.055055 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.022 | 0.014079 | 0.055055 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.022 | 0.014079 | 0.055055 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.022 | 0.014079 | 0.055039 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.022 | 0.014079 | 0.055039 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.022 | 0.014094 | 0.055039 | 0.050268 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.022 | 0.014094 | 0.055039 | 0.050268 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.022 | 0.014094 | 0.055039 | 0.050268 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.022 | 0.014094 | 0.055039 | 0.050268 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.022 | 0.014094 | 0.055055 | 0.050268 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.022 | 0.014094 | 0.055055 | 0.050268 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.022 | 0.014079 | 0.055071 | 0.050268 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.022 | 0.014094 | 0.055055 | 0.050268 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.022 | 0.014094 | 0.055055 | 0.050283 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.022 | 0.014094 | 0.055055 | 0.050299 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.022 | 0.014094 | 0.055055 | 0.050315 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.022 | 0.014094 | 0.055055 | 0.050315 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.022 | 0.014094 | 0.055055 | 0.050299 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.022 | 0.014094 | 0.055039 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.022 | 0.01411 | 0.055039 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.022 | 0.01411 | 0.055039 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.022 | 0.01411 | 0.055039 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.022 | 0.01411 | 0.055055 | 0.050283 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.022 | 0.014094 | 0.055055 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.022 | 0.014094 | 0.055055 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.022 | 0.01411 | 0.055055 | 0.050299 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.022 | 0.01411 | 0.055055 | 0.050299 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.022 | 0.01411 | 0.055071 | 0.050299 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.022 | 0.01411 | 0.055071 | 0.050299 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.022 | 0.01411 | 0.055071 | 0.050299 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.022 | 0.01411 | 0.055071 | 0.050299 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.022 | 0.01411 | 0.055071 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.022 | 0.014094 | 0.055055 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.022 | 0.014094 | 0.055055 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.022 | 0.014094 | 0.055055 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.022 | 0.014094 | 0.055039 | 0.050252 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.021 | 0.014094 | 0.055039 | 0.050252 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.021 | 0.014094 | 0.055039 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.021 | 0.014094 | 0.055039 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.021 | 0.01411 | 0.055055 | 0.050268 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.021 | 0.01411 | 0.055055 | 0.050268 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.021 | 0.01411 | 0.055055 | 0.050283 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.021 | 0.01411 | 0.055055 | 0.050283 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.021 | 0.01411 | 0.055055 | 0.050299 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.021 | 0.014094 | 0.055071 | 0.050299 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.021 | 0.014094 | 0.055055 | 0.050299 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.021 | 0.014094 | 0.055055 | 0.050299 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.021 | 0.014094 | 0.055039 | 0.050299 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.021 | 0.014094 | 0.055039 | 0.050283 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.021 | 0.014094 | 0.055024 | 0.050283 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.021 | 0.014094 | 0.055024 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.021 | 0.014094 | 0.055024 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.021 | 0.014094 | 0.055024 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.021 | 0.014094 | 0.055024 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.021 | 0.014094 | 0.055024 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.021 | 0.014094 | 0.055039 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.021 | 0.014094 | 0.055039 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.02 | 0.014094 | 0.055055 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.02 | 0.014094 | 0.055055 | 0.050299 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.02 | 0.01411 | 0.055055 | 0.050299 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.02 | 0.01411 | 0.055039 | 0.050299 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.02 | 0.01411 | 0.055039 | 0.050299 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.02 | 0.01411 | 0.055039 | 0.050299 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.02 | 0.014094 | 0.055024 | 0.050299 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.02 | 0.014094 | 0.055024 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.02 | 0.014094 | 0.055024 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.02 | 0.014094 | 0.055024 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.02 | 0.014094 | 0.055024 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.02 | 0.014094 | 0.055024 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.02 | 0.014094 | 0.055024 | 0.050268 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.02 | 0.014094 | 0.055024 | 0.050268 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.02 | 0.01411 | 0.055024 | 0.050268 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.02 | 0.01411 | 0.055024 | 0.050283 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.02 | 0.014126 | 0.055024 | 0.050283 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.02 | 0.014126 | 0.055024 | 0.050283 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.02 | 0.014126 | 0.055024 | 0.050283 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.02 | 0.01411 | 0.055024 | 0.050283 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.02 | 0.01411 | 0.055024 | 0.050283 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.02 | 0.014094 | 0.055024 | 0.050283 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.02 | 0.014094 | 0.055008 | 0.050283 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.02 | 0.014094 | 0.055008 | 0.050283 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.02 | 0.014094 | 0.055008 | 0.050283 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.02 | 0.014094 | 0.054992 | 0.050283 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.02 | 0.014094 | 0.054992 | 0.050283 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.02 | 0.014094 | 0.054992 | 0.050283 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.02 | 0.01411 | 0.054992 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.02 | 0.01411 | 0.054992 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.02 | 0.01411 | 0.054992 | 0.050283 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.02 | 0.01411 | 0.054992 | 0.050283 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.02 | 0.01411 | 0.055008 | 0.050283 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.02 | 0.01411 | 0.055008 | 0.050283 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.02 | 0.01411 | 0.055008 | 0.050283 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.02 | 0.01411 | 0.055008 | 0.050283 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.02 | 0.01411 | 0.054992 | 0.050299 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.02 | 0.01411 | 0.054992 | 0.050299 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.02 | 0.01411 | 0.054992 | 0.050299 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.02 | 0.01411 | 0.054992 | 0.050299 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.02 | 0.01411 | 0.054992 | 0.050283 | 0.00028346
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.02 | 0.01411 | 0.054992 | 0.050283 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.02 | 0.01411 | 0.054992 | 0.050283 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.02 | 0.01411 | 0.054992 | 0.050283 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.02 | 0.01411 | 0.054992 | 0.050283 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.02 | 0.01411 | 0.054992 | 0.050283 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.02 | 0.01411 | 0.054992 | 0.050283 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.02 | 0.01411 | 0.054992 | 0.050283 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.02 | 0.014094 | 0.054992 | 0.050283 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.02 | 0.014094 | 0.055008 | 0.050283 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.02 | 0.01411 | 0.055008 | 0.050283 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.02 | 0.01411 | 0.055008 | 0.050299 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.02 | 0.01411 | 0.055008 | 0.050299 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.02 | 0.01411 | 0.055008 | 0.050315 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.02 | 0.01411 | 0.055008 | 0.050315 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.02 | 0.01411 | 0.055008 | 0.050299 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.02 | 0.01411 | 0.054992 | 0.050299 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.02 | 0.01411 | 0.054992 | 0.050283 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.02 | 0.01411 | 0.054992 | 0.050283 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.02 | 0.01411 | 0.054992 | 0.050283 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.02 | 0.01411 | 0.054992 | 0.050283 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.02 | 0.01411 | 0.054992 | 0.050283 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.02 | 0.01411 | 0.055008 | 0.050283 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.02 | 0.01411 | 0.055008 | 0.050283 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.02 | 0.01411 | 0.055008 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.02 | 0.01411 | 0.055008 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.02 | 0.014126 | 0.055008 | 0.050299 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.02 | 0.014142 | 0.055008 | 0.050315 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.02 | 0.014142 | 0.054992 | 0.050315 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.02 | 0.014142 | 0.054992 | 0.050315 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.02 | 0.014126 | 0.054992 | 0.050299 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.02 | 0.014126 | 0.054992 | 0.050299 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.02 | 0.014126 | 0.054992 | 0.050299 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.02 | 0.014126 | 0.054992 | 0.050299 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.02 | 0.014126 | 0.054976 | 0.050299 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.02 | 0.014126 | 0.054976 | 0.050299 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.02 | 0.014126 | 0.054976 | 0.050299 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.02 | 0.014126 | 0.054976 | 0.050299 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.02 | 0.014126 | 0.054976 | 0.050299 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.02 | 0.014126 | 0.054976 | 0.050299 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.02 | 0.014142 | 0.054976 | 0.050315 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.02 | 0.014142 | 0.054976 | 0.050331 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.02 | 0.014142 | 0.054976 | 0.050331 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.02 | 0.014142 | 0.054976 | 0.050315 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.02 | 0.014126 | 0.054992 | 0.050315 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.02 | 0.014126 | 0.054992 | 0.050299 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.02 | 0.014126 | 0.054992 | 0.050299 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.02 | 0.014126 | 0.054976 | 0.050299 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.02 | 0.014126 | 0.054976 | 0.050315 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.02 | 0.014126 | 0.054961 | 0.050315 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.02 | 0.014126 | 0.054961 | 0.050315 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.02 | 0.014126 | 0.054961 | 0.050315 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.02 | 0.014126 | 0.054961 | 0.050315 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.02 | 0.014142 | 0.054961 | 0.050315 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.02 | 0.014142 | 0.054961 | 0.050315 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.02 | 0.014142 | 0.054976 | 0.050331 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.02 | 0.014142 | 0.054976 | 0.050331 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.02 | 0.014126 | 0.054992 | 0.050331 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.02 | 0.01411 | 0.054992 | 0.050331 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.02 | 0.01411 | 0.054992 | 0.050331 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.02 | 0.01411 | 0.054992 | 0.050331 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.02 | 0.01411 | 0.054992 | 0.050346 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.02 | 0.01411 | 0.054976 | 0.050346 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.02 | 0.01411 | 0.054976 | 0.050346 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.02 | 0.01411 | 0.054961 | 0.050331 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.02 | 0.01411 | 0.054961 | 0.050331 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.02 | 0.01411 | 0.054961 | 0.050315 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.02 | 0.01411 | 0.054961 | 0.050315 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.02 | 0.01411 | 0.054961 | 0.050315 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.02 | 0.01411 | 0.054961 | 0.050315 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.02 | 0.01411 | 0.054976 | 0.050315 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.02 | 0.01411 | 0.054976 | 0.050315 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.02 | 0.01411 | 0.054976 | 0.050331 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.02 | 0.01411 | 0.054976 | 0.050331 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.02 | 0.014126 | 0.054976 | 0.050346 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.02 | 0.01411 | 0.054976 | 0.050346 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.02 | 0.01411 | 0.054976 | 0.050346 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.02 | 0.01411 | 0.054976 | 0.050346 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.02 | 0.014094 | 0.054976 | 0.050331 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.02 | 0.014094 | 0.054976 | 0.050315 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.02 | 0.014094 | 0.054961 | 0.050299 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.02 | 0.014094 | 0.054961 | 0.050299 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.02 | 0.014094 | 0.054961 | 0.050299 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.02 | 0.014094 | 0.054961 | 0.050299 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.02 | 0.014094 | 0.054961 | 0.050299 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.02 | 0.014094 | 0.054961 | 0.050299 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.02 | 0.01411 | 0.054961 | 0.050299 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.02 | 0.01411 | 0.054961 | 0.050299 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.018 | 0 | 0.02 | 0.01411 | 0.054961 | 0.050315 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.017 | 0 | 0.02 | 0.014094 | 0.054976 | 0.050315 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.017 | 0 | 0.02 | 0.014094 | 0.054976 | 0.050315 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.017 | 0 | 0.02 | 0.014079 | 0.054992 | 0.050299 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.017 | 0 | 0.02 | 0.014079 | 0.054992 | 0.050299 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.017 | 0 | 0.02 | 0.014079 | 0.054992 | 0.050299 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.017 | 0 | 0.02 | 0.014079 | 0.054976 | 0.050299 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.017 | 0 | 0.02 | 0.014079 | 0.054961 | 0.050299 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.017 | 0 | 0.02 | 0.014079 | 0.054961 | 0.050299 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.017 | 0 | 0.02 | 0.014079 | 0.054961 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.017 | 0 | 0.02 | 0.014079 | 0.054961 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.017 | 0 | 0.02 | 0.014094 | 0.054961 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.017 | 0 | 0.02 | 0.014094 | 0.054961 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.017 | 0 | 0.02 | 0.014094 | 0.054961 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.017 | 0 | 0.02 | 0.014079 | 0.054961 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.017 | 0 | 0.02 | 0.014079 | 0.054976 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.017 | 0 | 0.02 | 0.014079 | 0.054992 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.017 | 0 | 0.02 | 0.014079 | 0.054992 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.017 | 0 | 0.02 | 0.014079 | 0.054992 | 0.050299 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.017 | 0 | 0.02 | 0.014094 | 0.054976 | 0.050299 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.017 | 0 | 0.02 | 0.01411 | 0.054976 | 0.050315 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.017 | 0 | 0.02 | 0.01411 | 0.054976 | 0.050315 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.017 | 0 | 0.02 | 0.014094 | 0.054961 | 0.050315 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.017 | 0 | 0.02 | 0.014094 | 0.054961 | 0.050299 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.017 | 0 | 0.02 | 0.014094 | 0.054961 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.017 | 0 | 0.02 | 0.014094 | 0.054961 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.017 | 0 | 0.02 | 0.014094 | 0.054961 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.017 | 0 | 0.02 | 0.014094 | 0.054961 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.017 | 0 | 0.02 | 0.014079 | 0.054961 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.017 | 0 | 0.02 | 0.014079 | 0.054961 | 0.050283 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.02 | 0.014079 | 0.054961 | 0.050283 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.02 | 0.014094 | 0.054976 | 0.050299 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.02 | 0.014094 | 0.054976 | 0.050315 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.02 | 0.01411 | 0.054976 | 0.050315 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.02 | 0.01411 | 0.054976 | 0.050315 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.02 | 0.01411 | 0.054976 | 0.050331 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.02 | 0.01411 | 0.054976 | 0.050331 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.02 | 0.01411 | 0.054976 | 0.050331 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.02 | 0.01411 | 0.054976 | 0.050331 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.02 | 0.01411 | 0.054976 | 0.050331 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.02 | 0.01411 | 0.054961 | 0.050331 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.02 | 0.01411 | 0.054961 | 0.050331 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.02 | 0.01411 | 0.054961 | 0.050331 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.02 | 0.01411 | 0.054961 | 0.050331 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.02 | 0.01411 | 0.054961 | 0.050331 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.02 | 0.01411 | 0.054961 | 0.050331 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.02 | 0.01411 | 0.054961 | 0.050331 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.02 | 0.01411 | 0.054976 | 0.050331 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.02 | 0.01411 | 0.054976 | 0.050331 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.02 | 0.01411 | 0.054976 | 0.050331 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.02 | 0.01411 | 0.054976 | 0.050331 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.02 | 0.01411 | 0.054976 | 0.050331 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.02 | 0.01411 | 0.054976 | 0.050331 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.019 | 0.01411 | 0.054961 | 0.050331 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.019 | 0.01411 | 0.054976 | 0.050331 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.019 | 0.01411 | 0.054976 | 0.050331 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.019 | 0.01411 | 0.054976 | 0.050331 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.019 | 0.01411 | 0.054976 | 0.050331 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.019 | 0.01411 | 0.054961 | 0.050315 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.019 | 0.01411 | 0.054961 | 0.050315 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.019 | 0.01411 | 0.054961 | 0.050315 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.019 | 0.01411 | 0.054976 | 0.050315 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.019 | 0.01411 | 0.054976 | 0.050331 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.019 | 0.014126 | 0.054976 | 0.050331 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.019 | 0.014126 | 0.054976 | 0.050331 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.019 | 0.014126 | 0.054976 | 0.050346 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.019 | 0.014126 | 0.054992 | 0.050346 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.019 | 0.01411 | 0.054992 | 0.050331 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.019 | 0.01411 | 0.055008 | 0.050331 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.019 | 0.01411 | 0.055008 | 0.050331 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.019 | 0.01411 | 0.055008 | 0.050331 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.019 | 0.01411 | 0.054992 | 0.050346 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.019 | 0.014126 | 0.054992 | 0.050346 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.019 | 0.014126 | 0.054992 | 0.050346 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.019 | 0.014126 | 0.054992 | 0.050346 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.019 | 0.014126 | 0.054992 | 0.050346 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.019 | 0.014126 | 0.054992 | 0.050346 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.019 | 0.014142 | 0.054992 | 0.050346 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.019 | 0.014142 | 0.054992 | 0.050346 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.019 | 0.014142 | 0.054992 | 0.050346 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.019 | 0.014142 | 0.054992 | 0.050346 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.019 | 0.014126 | 0.054992 | 0.050346 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.019 | 0.014126 | 0.054992 | 0.050331 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.019 | 0.014126 | 0.054992 | 0.050331 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.019 | 0.014142 | 0.054992 | 0.050346 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.019 | 0.014142 | 0.054992 | 0.050346 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.019 | 0.014142 | 0.054992 | 0.050346 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.014142 | 0.054976 | 0.050346 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.014142 | 0.054976 | 0.050346 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.014142 | 0.054976 | 0.050331 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.014142 | 0.054976 | 0.050331 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.014142 | 0.054976 | 0.050331 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.014142 | 0.054976 | 0.050331 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.014142 | 0.054976 | 0.050331 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.014142 | 0.054976 | 0.050331 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.014126 | 0.054976 | 0.050331 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.014126 | 0.054976 | 0.050331 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.014126 | 0.054976 | 0.050331 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.014142 | 0.054976 | 0.050331 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.014142 | 0.054961 | 0.050346 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.014142 | 0.054961 | 0.050362 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.014142 | 0.054961 | 0.050362 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.014142 | 0.054945 | 0.050346 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.014142 | 0.054945 | 0.050346 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.014142 | 0.054945 | 0.050331 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.014142 | 0.054945 | 0.050331 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.014142 | 0.054945 | 0.050315 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.014142 | 0.054945 | 0.050315 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.014142 | 0.054945 | 0.050315 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.014126 | 0.054945 | 0.050315 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.014126 | 0.054945 | 0.050315 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.014126 | 0.054945 | 0.050331 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.014126 | 0.054945 | 0.050331 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.014142 | 0.054945 | 0.050331 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.014142 | 0.054945 | 0.050346 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.014142 | 0.054945 | 0.050346 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.014126 | 0.054945 | 0.050346 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.014126 | 0.054929 | 0.050331 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.01411 | 0.054929 | 0.050315 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.01411 | 0.054929 | 0.050315 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.01411 | 0.054929 | 0.050315 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.01411 | 0.054929 | 0.050299 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.01411 | 0.054913 | 0.050299 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.01411 | 0.054913 | 0.050299 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.01411 | 0.054913 | 0.050299 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.014126 | 0.054929 | 0.050299 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.014126 | 0.054929 | 0.050315 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.014142 | 0.054929 | 0.050315 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.014142 | 0.054929 | 0.050315 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.014142 | 0.054929 | 0.050331 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.014142 | 0.054945 | 0.050331 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.014126 | 0.054945 | 0.050315 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.014126 | 0.054945 | 0.050315 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.014126 | 0.054945 | 0.050315 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.014126 | 0.054929 | 0.050315 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.014126 | 0.054929 | 0.050315 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.014126 | 0.054929 | 0.050315 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.014126 | 0.054929 | 0.050299 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.014126 | 0.054929 | 0.050299 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.014126 | 0.054929 | 0.050299 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.014126 | 0.054929 | 0.050299 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.014126 | 0.054929 | 0.050299 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.014126 | 0.054929 | 0.050299 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.014126 | 0.054929 | 0.050299 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.014126 | 0.054929 | 0.050299 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.014126 | 0.054929 | 0.050299 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.014126 | 0.054929 | 0.050299 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.014126 | 0.054929 | 0.050299 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.014126 | 0.054929 | 0.050299 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.014126 | 0.054929 | 0.050299 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.014126 | 0.054929 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.014126 | 0.054913 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.014126 | 0.054898 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.014126 | 0.054898 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.014126 | 0.054898 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.014126 | 0.054898 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.014126 | 0.054898 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.014126 | 0.054898 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.014126 | 0.054898 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.014126 | 0.054913 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.014126 | 0.054913 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.014126 | 0.054913 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.014126 | 0.054913 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.014126 | 0.054913 | 0.050299 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.014126 | 0.054913 | 0.050299 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.014126 | 0.054898 | 0.050299 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.014126 | 0.054898 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.014126 | 0.054882 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.014126 | 0.054882 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.014126 | 0.054866 | 0.050283 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.014126 | 0.054866 | 0.050283 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.014126 | 0.054866 | 0.050283 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.014126 | 0.054866 | 0.050283 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.014126 | 0.054866 | 0.050283 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.01411 | 0.054882 | 0.050283 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.01411 | 0.054882 | 0.050283 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.01411 | 0.054882 | 0.050283 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.01411 | 0.054882 | 0.050299 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.01411 | 0.054882 | 0.050299 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.01411 | 0.054882 | 0.050315 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.01411 | 0.054882 | 0.050315 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.01411 | 0.054882 | 0.050315 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.01411 | 0.054882 | 0.050315 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.01411 | 0.054882 | 0.050315 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.01411 | 0.054882 | 0.050315 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.01411 | 0.054882 | 0.050299 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.014126 | 0.054882 | 0.050299 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.014126 | 0.054882 | 0.050299 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.014126 | 0.054882 | 0.050299 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.014126 | 0.054882 | 0.050299 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.014126 | 0.054882 | 0.050299 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.01411 | 0.054898 | 0.050299 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.01411 | 0.054898 | 0.050299 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.014126 | 0.054913 | 0.050299 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.014126 | 0.054913 | 0.050315 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.014126 | 0.054898 | 0.050315 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.014142 | 0.054882 | 0.050315 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.014126 | 0.054882 | 0.050299 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.014126 | 0.054882 | 0.050299 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.014126 | 0.054898 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.014126 | 0.054913 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.014126 | 0.054898 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.01411 | 0.054898 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.01411 | 0.054898 | 0.050283 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.01411 | 0.054898 | 0.050283 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.014126 | 0.054898 | 0.050283 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.014126 | 0.054898 | 0.050299 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.014142 | 0.054898 | 0.050299 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.014142 | 0.054898 | 0.050315 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.014142 | 0.054913 | 0.050315 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.014142 | 0.054913 | 0.050315 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.014142 | 0.054929 | 0.050315 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.014142 | 0.054913 | 0.050299 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.014126 | 0.054913 | 0.050299 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.014126 | 0.054913 | 0.050299 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.014126 | 0.054913 | 0.050299 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.014126 | 0.054898 | 0.050299 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.014126 | 0.054898 | 0.050299 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.014126 | 0.054898 | 0.050299 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.014126 | 0.054898 | 0.050299 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.014142 | 0.054898 | 0.050299 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.014142 | 0.054898 | 0.050299 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.014142 | 0.054898 | 0.050315 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.014157 | 0.054898 | 0.050315 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.014157 | 0.054913 | 0.050315 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.014142 | 0.054913 | 0.050315 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.014142 | 0.054929 | 0.050299 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.014142 | 0.054929 | 0.050299 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.014142 | 0.054929 | 0.050299 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.014142 | 0.054929 | 0.050315 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.014142 | 0.054929 | 0.050331 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.014142 | 0.054913 | 0.050331 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.014142 | 0.054913 | 0.050315 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.014142 | 0.054913 | 0.050315 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.014142 | 0.054913 | 0.050315 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.014142 | 0.054913 | 0.050299 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.014142 | 0.054913 | 0.050299 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.014142 | 0.054913 | 0.050315 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.014142 | 0.054913 | 0.050315 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.014126 | 0.054913 | 0.050315 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.014126 | 0.054913 | 0.050315 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.014126 | 0.054913 | 0.050315 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.014126 | 0.054913 | 0.050315 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.014126 | 0.054913 | 0.050315 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.01411 | 0.054929 | 0.050315 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.014126 | 0.054913 | 0.050315 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.014126 | 0.054913 | 0.050315 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.014126 | 0.054913 | 0.050315 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.014126 | 0.054913 | 0.050299 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.014126 | 0.054898 | 0.050299 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.014126 | 0.054898 | 0.050299 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.014126 | 0.054898 | 0.050283 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.014126 | 0.054898 | 0.050283 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.014126 | 0.054913 | 0.050283 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.01411 | 0.054913 | 0.050283 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.01411 | 0.054913 | 0.050283 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.01411 | 0.054913 | 0.050299 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.01411 | 0.054913 | 0.050299 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.01411 | 0.054898 | 0.050315 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.01411 | 0.054898 | 0.050315 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.01411 | 0.054898 | 0.050315 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.01411 | 0.054898 | 0.050299 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.01411 | 0.054898 | 0.050299 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.01411 | 0.054898 | 0.050283 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.01411 | 0.054882 | 0.050283 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.01411 | 0.054882 | 0.050283 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.01411 | 0.054882 | 0.050283 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.01411 | 0.054882 | 0.050283 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.016 | 0 | 0.018 | 0.01411 | 0.054882 | 0.050283 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.015 | 0 | 0.018 | 0.01411 | 0.054882 | 0.050283 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.015 | 0 | 0.018 | 0.01411 | 0.054882 | 0.050283 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.015 | 0 | 0.018 | 0.01411 | 0.054898 | 0.050283 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.015 | 0 | 0.018 | 0.014094 | 0.054898 | 0.050299 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.015 | 0 | 0.018 | 0.014094 | 0.054913 | 0.050299 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.015 | 0 | 0.018 | 0.01411 | 0.054913 | 0.050315 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.015 | 0 | 0.018 | 0.01411 | 0.054913 | 0.050315 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.015 | 0 | 0.018 | 0.01411 | 0.054898 | 0.050315 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.015 | 0 | 0.018 | 0.014094 | 0.054898 | 0.050315 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.015 | 0 | 0.018 | 0.014094 | 0.054898 | 0.050315 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.015 | 0 | 0.018 | 0.014094 | 0.054898 | 0.050299 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.015 | 0 | 0.018 | 0.014094 | 0.054898 | 0.050299 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.015 | 0 | 0.018 | 0.014094 | 0.054898 | 0.050299 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.015 | 0 | 0.018 | 0.014094 | 0.054882 | 0.050299 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.015 | 0 | 0.018 | 0.014094 | 0.054882 | 0.050299 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.015 | 0 | 0.018 | 0.014094 | 0.054882 | 0.050299 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.015 | 0 | 0.018 | 0.01411 | 0.054882 | 0.050299 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.015 | 0 | 0.018 | 0.01411 | 0.054882 | 0.050299 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.015 | 0 | 0.018 | 0.01411 | 0.054882 | 0.050299 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.015 | 0 | 0.018 | 0.01411 | 0.054898 | 0.050299 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.015 | 0 | 0.017 | 0.01411 | 0.054898 | 0.050299 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.015 | 0 | 0.017 | 0.01411 | 0.054898 | 0.050299 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.015 | 0 | 0.017 | 0.01411 | 0.054898 | 0.050299 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.015 | 0 | 0.017 | 0.01411 | 0.054898 | 0.050299 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.017 | 0.014094 | 0.054898 | 0.050299 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.017 | 0.014094 | 0.054898 | 0.050299 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.017 | 0.014094 | 0.054882 | 0.050299 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.017 | 0.014094 | 0.054882 | 0.050283 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.017 | 0.014094 | 0.054882 | 0.050283 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.017 | 0.014094 | 0.054866 | 0.050283 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.017 | 0.014094 | 0.054866 | 0.050283 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.017 | 0.014094 | 0.054866 | 0.050283 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.017 | 0.014094 | 0.054866 | 0.050283 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.017 | 0.01411 | 0.054866 | 0.050283 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.017 | 0.01411 | 0.054882 | 0.050283 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.017 | 0.01411 | 0.054882 | 0.050283 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.017 | 0.01411 | 0.054882 | 0.050283 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.017 | 0.014094 | 0.054882 | 0.050283 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.017 | 0.014094 | 0.054882 | 0.050299 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.017 | 0.01411 | 0.054882 | 0.050299 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.017 | 0.01411 | 0.054882 | 0.050299 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.017 | 0.01411 | 0.054882 | 0.050299 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.017 | 0.01411 | 0.054866 | 0.050299 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.017 | 0.01411 | 0.054866 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.017 | 0.01411 | 0.054866 | 0.050283 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.01411 | 0.054866 | 0.050268 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.01411 | 0.054866 | 0.050268 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.01411 | 0.054866 | 0.050268 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014094 | 0.054866 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014094 | 0.054882 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014094 | 0.054882 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.01411 | 0.054882 | 0.050299 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.01411 | 0.054882 | 0.050299 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.01411 | 0.054882 | 0.050315 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.01411 | 0.054898 | 0.050315 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.01411 | 0.054898 | 0.050299 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.01411 | 0.054898 | 0.050283 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014094 | 0.054898 | 0.050283 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014094 | 0.054898 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014094 | 0.054898 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014094 | 0.054882 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014094 | 0.054882 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014094 | 0.054882 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.01411 | 0.054882 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.01411 | 0.054882 | 0.050299 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014126 | 0.054898 | 0.050299 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014126 | 0.054898 | 0.050299 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014126 | 0.054898 | 0.050315 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.01411 | 0.054913 | 0.050315 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.01411 | 0.054913 | 0.050299 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.01411 | 0.054929 | 0.050299 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.01411 | 0.054929 | 0.050299 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014126 | 0.054929 | 0.050299 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014126 | 0.054913 | 0.050299 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014126 | 0.054913 | 0.050299 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014126 | 0.054913 | 0.050299 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014126 | 0.054913 | 0.050299 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014126 | 0.054913 | 0.050299 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014142 | 0.054913 | 0.050299 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014142 | 0.054913 | 0.050299 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014142 | 0.054913 | 0.050299 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014126 | 0.054913 | 0.050299 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014126 | 0.054913 | 0.050299 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014126 | 0.054929 | 0.050283 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014126 | 0.054929 | 0.050299 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014126 | 0.054929 | 0.050299 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014126 | 0.054929 | 0.050315 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014126 | 0.054929 | 0.050331 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014142 | 0.054913 | 0.050331 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014142 | 0.054913 | 0.050315 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014126 | 0.054913 | 0.050315 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014126 | 0.054913 | 0.050299 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014126 | 0.054913 | 0.050299 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014126 | 0.054913 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014126 | 0.054913 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014126 | 0.054913 | 0.050283 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014126 | 0.054913 | 0.050283 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014126 | 0.054913 | 0.050283 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014126 | 0.054913 | 0.050299 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014142 | 0.054913 | 0.050299 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014142 | 0.054913 | 0.050299 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014126 | 0.054913 | 0.050315 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014126 | 0.054913 | 0.050315 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.01411 | 0.054913 | 0.050315 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.01411 | 0.054913 | 0.050299 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014094 | 0.054913 | 0.050299 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014094 | 0.054913 | 0.050283 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014094 | 0.054898 | 0.050283 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014094 | 0.054898 | 0.050283 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014094 | 0.054882 | 0.050283 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014094 | 0.054882 | 0.050283 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.01411 | 0.054882 | 0.050283 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.01411 | 0.054898 | 0.050283 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.01411 | 0.054898 | 0.050283 | 0.00028346
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.01411 | 0.054898 | 0.050299 | 0.00028346
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.01411 | 0.054913 | 0.050299 | 0.00028346
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014094 | 0.054913 | 0.050299 | 0.00028346
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014094 | 0.054913 | 0.050299 | 0.00028346
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014094 | 0.054913 | 0.050299 | 0.00028346
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014094 | 0.054913 | 0.050299 | 0.00028346
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014094 | 0.054898 | 0.050299 | 0.00028346
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014094 | 0.054882 | 0.050299 | 0.00028346
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014094 | 0.054882 | 0.050283 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014094 | 0.054866 | 0.050268 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014094 | 0.054866 | 0.050268 | 0.00028346
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014094 | 0.054866 | 0.050268 | 0.00028346
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014094 | 0.054866 | 0.050268 | 0.00028346
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014094 | 0.054866 | 0.050268 | 0.00028346
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014094 | 0.054866 | 0.050268 | 0.00028346
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014094 | 0.054882 | 0.050268 | 0.00028346
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014079 | 0.054882 | 0.050268 | 0.00028346
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014079 | 0.054882 | 0.050268 | 0.00028346
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014094 | 0.054882 | 0.050283 | 0.00028346
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014094 | 0.054882 | 0.050283 | 0.00028346
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014094 | 0.054882 | 0.050299 | 0.00028346
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014094 | 0.054882 | 0.050299 | 0.00028346
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014079 | 0.054882 | 0.050299 | 0.00028346
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014079 | 0.054882 | 0.050283 | 0.00028346
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014079 | 0.054882 | 0.050283 | 0.00028346
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014079 | 0.054882 | 0.050268 | 0.00028346
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014079 | 0.054866 | 0.050268 | 0.00028346
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014079 | 0.054866 | 0.050268 | 0.00028346
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014079 | 0.054866 | 0.050268 | 0.00028346
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014079 | 0.054866 | 0.050268 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014079 | 0.054866 | 0.050268 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014079 | 0.054866 | 0.050268 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014079 | 0.054866 | 0.050283 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014079 | 0.054866 | 0.050283 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014079 | 0.054866 | 0.050283 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014079 | 0.054882 | 0.050283 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014079 | 0.054882 | 0.050268 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014079 | 0.054882 | 0.050268 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014079 | 0.054882 | 0.050268 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014079 | 0.054866 | 0.050283 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014079 | 0.054866 | 0.050283 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014079 | 0.05485 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014079 | 0.05485 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014079 | 0.05485 | 0.050252 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014079 | 0.05485 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014079 | 0.05485 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014079 | 0.05485 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014079 | 0.054866 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014079 | 0.054866 | 0.050268 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014079 | 0.054882 | 0.050268 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014079 | 0.054882 | 0.050268 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014079 | 0.054882 | 0.050268 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014079 | 0.054882 | 0.050268 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014079 | 0.054882 | 0.050268 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014063 | 0.054882 | 0.050268 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014063 | 0.054882 | 0.050268 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014063 | 0.054866 | 0.050268 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014063 | 0.054866 | 0.050268 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014063 | 0.054866 | 0.050252 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014063 | 0.054866 | 0.050252 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014063 | 0.054866 | 0.050252 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014063 | 0.054866 | 0.050252 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014063 | 0.054866 | 0.050252 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014063 | 0.054866 | 0.050268 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014063 | 0.054866 | 0.050268 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014063 | 0.054882 | 0.050268 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014063 | 0.054882 | 0.050268 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014063 | 0.054882 | 0.050283 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014063 | 0.054898 | 0.050283 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014063 | 0.054898 | 0.050283 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014063 | 0.054898 | 0.050283 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014063 | 0.054898 | 0.050283 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014063 | 0.054882 | 0.050283 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014047 | 0.054882 | 0.050283 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014047 | 0.054882 | 0.050268 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014063 | 0.054882 | 0.050268 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014063 | 0.054882 | 0.050268 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014063 | 0.054882 | 0.050268 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014063 | 0.054882 | 0.050268 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014063 | 0.054898 | 0.050268 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014063 | 0.054898 | 0.050283 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014063 | 0.054898 | 0.050283 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014063 | 0.054898 | 0.050283 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014079 | 0.054898 | 0.050299 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014079 | 0.054898 | 0.050299 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014079 | 0.054882 | 0.050299 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014079 | 0.054882 | 0.050299 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014079 | 0.054882 | 0.050283 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014063 | 0.054882 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014063 | 0.054882 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014063 | 0.054882 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014063 | 0.054866 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014063 | 0.054866 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014079 | 0.054866 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014079 | 0.054866 | 0.050268 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014094 | 0.054866 | 0.050268 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014094 | 0.054866 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014094 | 0.054882 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014094 | 0.054882 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014079 | 0.054898 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014079 | 0.054898 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014079 | 0.054882 | 0.050252 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014079 | 0.054882 | 0.050252 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014079 | 0.054866 | 0.050252 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014079 | 0.05485 | 0.050252 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014079 | 0.05485 | 0.050252 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014079 | 0.054835 | 0.050236 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014079 | 0.054835 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014079 | 0.054835 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014079 | 0.054835 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014079 | 0.05485 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014079 | 0.05485 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014079 | 0.05485 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014079 | 0.05485 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014079 | 0.054866 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014079 | 0.054866 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014079 | 0.054866 | 0.050252 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014079 | 0.054866 | 0.050252 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014079 | 0.05485 | 0.050252 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014079 | 0.05485 | 0.050252 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014063 | 0.054835 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014063 | 0.054835 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014079 | 0.054835 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014079 | 0.054835 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014079 | 0.054835 | 0.05022 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014063 | 0.054835 | 0.05022 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014063 | 0.054835 | 0.05022 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014047 | 0.05485 | 0.05022 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014047 | 0.05485 | 0.05022 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014047 | 0.05485 | 0.05022 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014063 | 0.05485 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014063 | 0.05485 | 0.050252 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014063 | 0.05485 | 0.050252 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014063 | 0.05485 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014063 | 0.05485 | 0.050252 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014063 | 0.05485 | 0.050252 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014047 | 0.05485 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014047 | 0.05485 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014047 | 0.05485 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014047 | 0.054835 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014047 | 0.054835 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014047 | 0.054835 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014047 | 0.05485 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014047 | 0.05485 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014047 | 0.05485 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014047 | 0.05485 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014047 | 0.05485 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014047 | 0.054866 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014031 | 0.054866 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014031 | 0.054866 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014031 | 0.054866 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014031 | 0.054866 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014031 | 0.054866 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014031 | 0.054866 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014031 | 0.05485 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014047 | 0.05485 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014047 | 0.05485 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014047 | 0.05485 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014047 | 0.054866 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014047 | 0.054866 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014047 | 0.054882 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014047 | 0.054882 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014047 | 0.054882 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014063 | 0.054882 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014063 | 0.054882 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014063 | 0.054882 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014063 | 0.054866 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014047 | 0.054866 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014047 | 0.054866 | 0.050252 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014047 | 0.05485 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014047 | 0.05485 | 0.050236 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014047 | 0.05485 | 0.050236 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014047 | 0.05485 | 0.050236 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014047 | 0.05485 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014047 | 0.05485 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014047 | 0.05485 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014063 | 0.054866 | 0.050252 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014063 | 0.054866 | 0.050252 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014063 | 0.054882 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014063 | 0.054882 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014063 | 0.054882 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014047 | 0.054882 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014047 | 0.054866 | 0.050252 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014047 | 0.054866 | 0.050252 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014047 | 0.05485 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014047 | 0.05485 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014047 | 0.05485 | 0.05022 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014047 | 0.05485 | 0.05022 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014047 | 0.054835 | 0.05022 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014047 | 0.05485 | 0.05022 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014047 | 0.05485 | 0.05022 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014063 | 0.05485 | 0.05022 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.014 | 0 | 0.016 | 0.014063 | 0.05485 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.013 | 0 | 0.015 | 0.014063 | 0.054866 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.013 | 0 | 0.015 | 0.014063 | 0.054866 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.013 | 0 | 0.015 | 0.014063 | 0.054866 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.013 | 0 | 0.015 | 0.014063 | 0.054866 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.013 | 0 | 0.015 | 0.014047 | 0.054882 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.013 | 0 | 0.015 | 0.014047 | 0.054882 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.013 | 0 | 0.015 | 0.014047 | 0.054866 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.013 | 0 | 0.015 | 0.014047 | 0.05485 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.013 | 0 | 0.015 | 0.014047 | 0.05485 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.013 | 0 | 0.015 | 0.014047 | 0.05485 | 0.05022 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.013 | 0 | 0.015 | 0.014063 | 0.05485 | 0.05022 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.013 | 0 | 0.015 | 0.014063 | 0.05485 | 0.05022 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.013 | 0 | 0.015 | 0.014063 | 0.05485 | 0.05022 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.013 | 0 | 0.015 | 0.014063 | 0.05485 | 0.05022 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.013 | 0 | 0.015 | 0.014063 | 0.05485 | 0.05022 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.013 | 0 | 0.015 | 0.014063 | 0.054866 | 0.05022 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.013 | 0 | 0.015 | 0.014063 | 0.054882 | 0.05022 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.013 | 0 | 0.015 | 0.014063 | 0.054882 | 0.05022 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.013 | 0 | 0.015 | 0.014063 | 0.054882 | 0.05022 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.013 | 0 | 0.015 | 0.014063 | 0.054866 | 0.05022 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.013 | 0 | 0.015 | 0.014063 | 0.054866 | 0.050236 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.013 | 0 | 0.015 | 0.014047 | 0.054866 | 0.05022 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.013 | 0 | 0.015 | 0.014047 | 0.05485 | 0.05022 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.013 | 0 | 0.015 | 0.014047 | 0.05485 | 0.050205 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.013 | 0 | 0.015 | 0.014047 | 0.05485 | 0.050205 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.013 | 0 | 0.015 | 0.014047 | 0.054835 | 0.050205 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.013 | 0 | 0.015 | 0.014047 | 0.054835 | 0.050205 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.013 | 0 | 0.015 | 0.014047 | 0.054835 | 0.050205 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.013 | 0 | 0.015 | 0.014047 | 0.054835 | 0.050205 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.013 | 0 | 0.015 | 0.014047 | 0.054835 | 0.050205 | 0.00020472
10/23/2022 | 3:23 | 0 | 0.013 | 0 | 0.015 | 0.014047 | 0.05485 | 0.050205 | 0.00020472
10/23/2022 | 3:23 | 0 | 0.013 | 0 | 0.015 | 0.014047 | 0.05485 | 0.050205 | 0.00020472
10/23/2022 | 3:23 | 0 | 0.013 | 0 | 0.015 | 0.014047 | 0.05485 | 0.05022 | 0.00020472
10/23/2022 | 3:23 | 0 | 0.013 | 0 | 0.015 | 0.014031 | 0.054866 | 0.05022 | 0.00020472
10/23/2022 | 3:23 | 0 | 0.013 | 0 | 0.015 | 0.014031 | 0.054866 | 0.05022 | 0.00020472
10/23/2022 | 3:23 | 0 | 0.013 | 0 | 0.015 | 0.014031 | 0.054866 | 0.05022 | 0.00020472
10/23/2022 | 3:23 | 0 | 0.013 | 0 | 0.015 | 0.014031 | 0.054866 | 0.05022 | 0.00020472
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.015 | 0.014031 | 0.05485 | 0.05022 | 0.00020472
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.015 | 0.014031 | 0.05485 | 0.05022 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.015 | 0.014031 | 0.05485 | 0.05022 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.015 | 0.014031 | 0.05485 | 0.050205 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.015 | 0.014031 | 0.054835 | 0.050205 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.015 | 0.014031 | 0.054835 | 0.050205 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.015 | 0.014031 | 0.054835 | 0.050205 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.015 | 0.014031 | 0.054835 | 0.050205 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.015 | 0.014031 | 0.054835 | 0.050205 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.015 | 0.014031 | 0.054835 | 0.050205 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.015 | 0.014016 | 0.05485 | 0.050205 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.015 | 0.014016 | 0.05485 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.015 | 0.014016 | 0.054866 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.015 | 0.014016 | 0.054866 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.015 | 0.014031 | 0.054866 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.015 | 0.014031 | 0.054882 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.015 | 0.014031 | 0.054882 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.015 | 0.014031 | 0.054882 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.015 | 0.014031 | 0.054866 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014031 | 0.054866 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014031 | 0.054866 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014031 | 0.054866 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.015 | 0.014031 | 0.054866 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014031 | 0.054866 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014031 | 0.054866 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014031 | 0.054882 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014031 | 0.054882 | 0.050252 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014047 | 0.054882 | 0.050252 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014063 | 0.054882 | 0.050268 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014047 | 0.054882 | 0.050268 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014047 | 0.054898 | 0.050268 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014031 | 0.054898 | 0.050252 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014031 | 0.054913 | 0.050252 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014031 | 0.054913 | 0.050252 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014031 | 0.054898 | 0.050252 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014031 | 0.054898 | 0.050252 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014031 | 0.054882 | 0.050252 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014031 | 0.054882 | 0.050252 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014047 | 0.054882 | 0.050252 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014047 | 0.054882 | 0.050252 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014047 | 0.054898 | 0.050252 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014047 | 0.054898 | 0.050252 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014047 | 0.054913 | 0.050252 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014047 | 0.054913 | 0.050268 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014047 | 0.054913 | 0.050268 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014063 | 0.054913 | 0.050268 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014063 | 0.054913 | 0.050283 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014063 | 0.054913 | 0.050283 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014063 | 0.054898 | 0.050283 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014063 | 0.054898 | 0.050268 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014063 | 0.054898 | 0.050252 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014063 | 0.054898 | 0.050252 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014063 | 0.054898 | 0.050252 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014063 | 0.054898 | 0.050252 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014063 | 0.054898 | 0.050252 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014063 | 0.054898 | 0.050252 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014063 | 0.054913 | 0.050252 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014063 | 0.054913 | 0.050252 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014063 | 0.054913 | 0.050252 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014063 | 0.054913 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014063 | 0.054929 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014063 | 0.054929 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014063 | 0.054929 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014063 | 0.054929 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014063 | 0.054929 | 0.050252 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014047 | 0.054929 | 0.050252 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014047 | 0.054929 | 0.050252 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014047 | 0.054929 | 0.050252 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014047 | 0.054913 | 0.050252 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014047 | 0.054913 | 0.050252 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014047 | 0.054913 | 0.050252 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014047 | 0.054913 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014063 | 0.054913 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014063 | 0.054913 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014079 | 0.054913 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014063 | 0.054913 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014063 | 0.054929 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014047 | 0.054945 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014031 | 0.054945 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014031 | 0.054945 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014047 | 0.054929 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014047 | 0.054898 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014047 | 0.054898 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014047 | 0.054882 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014063 | 0.054882 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014063 | 0.054882 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014063 | 0.054882 | 0.05022 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014063 | 0.054882 | 0.05022 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014063 | 0.054882 | 0.05022 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014063 | 0.054898 | 0.05022 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014047 | 0.054898 | 0.05022 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014047 | 0.054913 | 0.05022 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014047 | 0.054898 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014063 | 0.054898 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014063 | 0.054882 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014063 | 0.054882 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014063 | 0.054866 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014063 | 0.054866 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014047 | 0.054866 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014047 | 0.054866 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014047 | 0.054866 | 0.050205 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014047 | 0.054866 | 0.050205 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014047 | 0.054866 | 0.050205 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014031 | 0.054866 | 0.050205 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014031 | 0.054866 | 0.050205 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014031 | 0.054866 | 0.050205 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014031 | 0.054882 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014031 | 0.054882 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014031 | 0.054882 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014031 | 0.054866 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014031 | 0.054866 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014016 | 0.054882 | 0.050205 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014 | 0.054882 | 0.050205 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014 | 0.054882 | 0.050205 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014 | 0.054882 | 0.050205 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014 | 0.054866 | 0.050205 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014 | 0.054866 | 0.050189 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014 | 0.054866 | 0.050189 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014 | 0.054866 | 0.050189 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014 | 0.054866 | 0.050189 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014016 | 0.054866 | 0.050189 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014016 | 0.054866 | 0.050189 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014016 | 0.054866 | 0.050205 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014016 | 0.054866 | 0.050205 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014 | 0.054882 | 0.050205 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014 | 0.054898 | 0.050205 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014016 | 0.054898 | 0.050205 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014016 | 0.054898 | 0.050205 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014016 | 0.054882 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014016 | 0.054882 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014016 | 0.054882 | 0.050205 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014016 | 0.054882 | 0.050205 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014016 | 0.054882 | 0.050189 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014016 | 0.054882 | 0.050189 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014016 | 0.054882 | 0.050189 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014016 | 0.054882 | 0.050189 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014016 | 0.054882 | 0.050189 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014 | 0.054898 | 0.050189 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014 | 0.054898 | 0.050205 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014016 | 0.054898 | 0.050205 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014016 | 0.054898 | 0.05022 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014016 | 0.054898 | 0.05022 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014016 | 0.054898 | 0.050236 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014016 | 0.054898 | 0.050236 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014016 | 0.054898 | 0.050236 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014 | 0.054898 | 0.05022 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014 | 0.054898 | 0.05022 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014 | 0.054898 | 0.05022 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014 | 0.054882 | 0.05022 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014 | 0.054882 | 0.050205 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014 | 0.054882 | 0.050205 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014016 | 0.054882 | 0.050205 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014016 | 0.054882 | 0.05022 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014016 | 0.054898 | 0.05022 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014016 | 0.054898 | 0.05022 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014016 | 0.054913 | 0.050236 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014016 | 0.054913 | 0.050236 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014016 | 0.054929 | 0.050236 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014 | 0.054929 | 0.050236 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014 | 0.054929 | 0.050236 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014 | 0.054913 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014 | 0.054913 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014 | 0.054913 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014 | 0.054898 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014 | 0.054898 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014 | 0.054882 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014016 | 0.054882 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014016 | 0.054898 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014016 | 0.054898 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014016 | 0.054898 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014016 | 0.054913 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014016 | 0.054929 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014016 | 0.054929 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014016 | 0.054929 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014031 | 0.054929 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014031 | 0.054929 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014031 | 0.054929 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014031 | 0.054929 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014016 | 0.054929 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014016 | 0.054929 | 0.050205 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014016 | 0.054913 | 0.050205 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014016 | 0.054913 | 0.050205 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014016 | 0.054913 | 0.050205 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014016 | 0.054913 | 0.050205 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014016 | 0.054929 | 0.050205 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014016 | 0.054929 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014031 | 0.054913 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014031 | 0.054929 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014016 | 0.054929 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014016 | 0.054945 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014 | 0.054945 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014 | 0.054961 | 0.05022 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014 | 0.054961 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014 | 0.054945 | 0.05022 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014 | 0.054945 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014 | 0.054945 | 0.05022 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014 | 0.054945 | 0.05022 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014016 | 0.054945 | 0.05022 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014016 | 0.054945 | 0.05022 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014016 | 0.054945 | 0.05022 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014016 | 0.054945 | 0.05022 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014016 | 0.054945 | 0.05022 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014016 | 0.054961 | 0.05022 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014016 | 0.054961 | 0.05022 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014016 | 0.054961 | 0.05022 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014016 | 0.054961 | 0.05022 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014016 | 0.054961 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014016 | 0.054961 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014016 | 0.054961 | 0.050252 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014016 | 0.054961 | 0.050252 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014016 | 0.054961 | 0.050252 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014016 | 0.054945 | 0.050252 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014016 | 0.054945 | 0.050236 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014016 | 0.054945 | 0.050236 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014016 | 0.054945 | 0.050236 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014016 | 0.054945 | 0.050236 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014016 | 0.054945 | 0.050236 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014016 | 0.054961 | 0.050236 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014016 | 0.054961 | 0.050236 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014016 | 0.054961 | 0.050236 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014016 | 0.054976 | 0.050236 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014016 | 0.054976 | 0.050252 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014016 | 0.054976 | 0.050252 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014016 | 0.054976 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014016 | 0.054976 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014016 | 0.054976 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014016 | 0.054976 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014016 | 0.054961 | 0.050252 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014016 | 0.054961 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014016 | 0.054961 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014016 | 0.054961 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014016 | 0.054961 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014016 | 0.054961 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014016 | 0.054976 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014016 | 0.054976 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014016 | 0.054976 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014031 | 0.054992 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014031 | 0.054992 | 0.050268 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014031 | 0.054992 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014031 | 0.054992 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014016 | 0.054976 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014016 | 0.054976 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014016 | 0.054961 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014016 | 0.054961 | 0.05022 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014016 | 0.054961 | 0.05022 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014016 | 0.054961 | 0.05022 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014016 | 0.054961 | 0.05022 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014016 | 0.054961 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014031 | 0.054961 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014031 | 0.054961 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014031 | 0.054976 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014031 | 0.054976 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014031 | 0.054976 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014031 | 0.054992 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014031 | 0.054992 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014031 | 0.054976 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014031 | 0.054976 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014031 | 0.054961 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014031 | 0.054961 | 0.05022 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014031 | 0.054961 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014031 | 0.054961 | 0.05022 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014031 | 0.054961 | 0.05022 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014031 | 0.054961 | 0.05022 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014031 | 0.054961 | 0.05022 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014031 | 0.054961 | 0.05022 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014031 | 0.054961 | 0.05022 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014031 | 0.054976 | 0.05022 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014031 | 0.054976 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014031 | 0.054976 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014031 | 0.054992 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014031 | 0.054992 | 0.050252 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014031 | 0.054992 | 0.050252 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014031 | 0.054992 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014031 | 0.054992 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014031 | 0.054976 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014031 | 0.054976 | 0.050236 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014031 | 0.054976 | 0.05022 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014031 | 0.054976 | 0.05022 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014031 | 0.054976 | 0.05022 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014031 | 0.054976 | 0.05022 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014031 | 0.054976 | 0.05022 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014031 | 0.054976 | 0.050236 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014031 | 0.054976 | 0.050236 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014031 | 0.054992 | 0.050252 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014031 | 0.054992 | 0.050252 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014031 | 0.054992 | 0.050268 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014016 | 0.055008 | 0.050268 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014016 | 0.055008 | 0.050252 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014016 | 0.055008 | 0.050252 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014016 | 0.054992 | 0.050252 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014016 | 0.054976 | 0.050252 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014016 | 0.054976 | 0.050252 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014016 | 0.054976 | 0.050236 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014016 | 0.054976 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014016 | 0.054976 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014016 | 0.054976 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014016 | 0.054976 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014016 | 0.054976 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014016 | 0.054992 | 0.050252 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014016 | 0.054992 | 0.050252 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014016 | 0.054992 | 0.050252 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014031 | 0.054976 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014031 | 0.054976 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014016 | 0.054976 | 0.050252 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014016 | 0.054976 | 0.050252 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014016 | 0.054976 | 0.050252 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014016 | 0.054976 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014016 | 0.054961 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014016 | 0.054961 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014016 | 0.054961 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014016 | 0.054961 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014016 | 0.054961 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014016 | 0.054961 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014016 | 0.054961 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014016 | 0.054976 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.013 | 0.014016 | 0.054976 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.013 | 0.014016 | 0.054976 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.013 | 0.014016 | 0.054976 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.013 | 0.014016 | 0.054961 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.013 | 0.014016 | 0.054961 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.013 | 0.014 | 0.054961 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.014 | 0.014 | 0.054961 | 0.05022 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.013 | 0.014 | 0.054961 | 0.05022 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.013 | 0.014 | 0.054961 | 0.05022 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.013 | 0.014 | 0.054945 | 0.050205 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.013 | 0.014 | 0.054945 | 0.050205 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.013 | 0.014 | 0.054945 | 0.050205 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.013 | 0.014 | 0.054945 | 0.050205 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.013 | 0.014 | 0.054945 | 0.050205 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.013 | 0.014 | 0.054961 | 0.05022 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.013 | 0.014 | 0.054961 | 0.05022 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.013 | 0.014 | 0.054976 | 0.05022 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.013 | 0.014 | 0.054976 | 0.05022 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.013 | 0.013984 | 0.054992 | 0.05022 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.013 | 0.013984 | 0.054992 | 0.05022 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.013 | 0.013984 | 0.054992 | 0.05022 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.013 | 0.013984 | 0.054976 | 0.05022 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.013 | 0.013984 | 0.054976 | 0.05022 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.013 | 0.013984 | 0.054976 | 0.05022 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.013 | 0.013984 | 0.054976 | 0.05022 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.013 | 0.013984 | 0.054976 | 0.050205 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.013 | 0.013984 | 0.054976 | 0.050205 | 0.00028346
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.013 | 0.013984 | 0.054976 | 0.050205 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.013 | 0.013984 | 0.054976 | 0.050205 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.013 | 0.013984 | 0.054976 | 0.050205 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.013 | 0.013984 | 0.054992 | 0.050205 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.013 | 0.013984 | 0.054992 | 0.050205 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.013 | 0.013984 | 0.055008 | 0.05022 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.013 | 0.013984 | 0.055008 | 0.05022 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.013 | 0.013984 | 0.055024 | 0.05022 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.013 | 0.013984 | 0.055024 | 0.05022 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.013 | 0.013984 | 0.055024 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.013 | 0.013984 | 0.055008 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.013 | 0.013984 | 0.055008 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.013 | 0.013984 | 0.054992 | 0.05022 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.013 | 0.013984 | 0.054992 | 0.05022 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.013 | 0.013984 | 0.054992 | 0.05022 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.013 | 0.013984 | 0.054976 | 0.050205 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.013 | 0.013984 | 0.054976 | 0.050205 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.013 | 0.013984 | 0.054992 | 0.050205 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.013 | 0.013984 | 0.054992 | 0.050205 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.013 | 0.013984 | 0.054992 | 0.05022 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.013 | 0.013984 | 0.055008 | 0.05022 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.013 | 0.013984 | 0.055008 | 0.05022 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.013 | 0.013984 | 0.055008 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.013 | 0.014 | 0.055008 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.013 | 0.014 | 0.055008 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.012 | 0 | 0.013 | 0.014 | 0.054992 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.011 | 0 | 0.013 | 0.014 | 0.054992 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.011 | 0 | 0.013 | 0.014 | 0.054992 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.011 | 0 | 0.013 | 0.013984 | 0.054992 | 0.050205 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.011 | 0 | 0.013 | 0.013984 | 0.054992 | 0.050205 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.011 | 0 | 0.013 | 0.013984 | 0.054976 | 0.050205 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.011 | 0 | 0.013 | 0.013984 | 0.054976 | 0.050205 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.011 | 0 | 0.013 | 0.013984 | 0.054976 | 0.050205 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.011 | 0 | 0.013 | 0.013984 | 0.054976 | 0.050205 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.011 | 0 | 0.013 | 0.013984 | 0.054976 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.011 | 0 | 0.013 | 0.014 | 0.054976 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.011 | 0 | 0.013 | 0.014 | 0.054976 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.011 | 0 | 0.013 | 0.014 | 0.054976 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.011 | 0 | 0.013 | 0.014 | 0.054992 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.011 | 0 | 0.013 | 0.013984 | 0.054992 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.011 | 0 | 0.013 | 0.013984 | 0.054992 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.011 | 0 | 0.013 | 0.013984 | 0.054992 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.011 | 0 | 0.013 | 0.013984 | 0.054992 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.011 | 0 | 0.013 | 0.013984 | 0.054976 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.011 | 0 | 0.013 | 0.013984 | 0.054976 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.011 | 0 | 0.013 | 0.013984 | 0.054976 | 0.05022 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.011 | 0 | 0.013 | 0.013984 | 0.054976 | 0.05022 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.011 | 0 | 0.013 | 0.013984 | 0.054976 | 0.050205 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.011 | 0 | 0.012 | 0.013984 | 0.054976 | 0.050205 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.011 | 0 | 0.012 | 0.014 | 0.054976 | 0.050205 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.011 | 0 | 0.012 | 0.014 | 0.054976 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.011 | 0 | 0.012 | 0.014 | 0.054976 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.011 | 0 | 0.012 | 0.014 | 0.054976 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.011 | 0 | 0.012 | 0.014 | 0.054992 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.011 | 0 | 0.012 | 0.014 | 0.054992 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.011 | 0 | 0.012 | 0.014 | 0.054992 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.011 | 0 | 0.012 | 0.014 | 0.054992 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.011 | 0 | 0.012 | 0.014 | 0.054992 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.011 | 0 | 0.012 | 0.014016 | 0.054992 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.011 | 0 | 0.012 | 0.014016 | 0.054976 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.011 | 0 | 0.012 | 0.014016 | 0.054976 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.011 | 0 | 0.012 | 0.014016 | 0.054976 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.011 | 0 | 0.012 | 0.014016 | 0.054976 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.011 | 0 | 0.012 | 0.014016 | 0.054976 | 0.05022 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.011 | 0 | 0.012 | 0.014016 | 0.054976 | 0.05022 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.011 | 0 | 0.012 | 0.014016 | 0.054976 | 0.05022 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.011 | 0 | 0.012 | 0.014016 | 0.054992 | 0.05022 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.011 | 0 | 0.012 | 0.014016 | 0.054992 | 0.05022 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014016 | 0.054992 | 0.05022 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014016 | 0.054992 | 0.05022 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.054992 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.055008 | 0.050252 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.055008 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.055008 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.055008 | 0.050252 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.055008 | 0.050252 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.055008 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.055008 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.055008 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.054992 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.054992 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.054992 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.055008 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.055008 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.055024 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.055024 | 0.050252 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.055024 | 0.050252 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.055024 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.055024 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.055024 | 0.050252 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.055024 | 0.050252 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.055024 | 0.050252 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.055024 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.055008 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.055008 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.054992 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.054992 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.054992 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.055008 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.055008 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.055024 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.055024 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.055024 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.055024 | 0.050252 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.055024 | 0.050236 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.055024 | 0.050236 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014016 | 0.055024 | 0.050236 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014016 | 0.055024 | 0.05022 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014016 | 0.055008 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014016 | 0.055008 | 0.05022 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014016 | 0.054992 | 0.050205 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014016 | 0.054992 | 0.050205 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014016 | 0.054992 | 0.050205 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.054992 | 0.050205 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.054992 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.055008 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.055008 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.055024 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.055024 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.055024 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.055008 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.055008 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014016 | 0.054992 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014016 | 0.054992 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014016 | 0.054992 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014016 | 0.054992 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014016 | 0.054992 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014016 | 0.054992 | 0.050252 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014016 | 0.054992 | 0.050236 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.054992 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.054992 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.054992 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.055008 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.055008 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014016 | 0.055008 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014016 | 0.055008 | 0.050268 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014016 | 0.055008 | 0.050268 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.054992 | 0.050268 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.054976 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.054976 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.054976 | 0.050268 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.054976 | 0.050252 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.054976 | 0.050252 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.054976 | 0.050252 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.054976 | 0.050252 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.054976 | 0.050252 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.054976 | 0.050252 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.054992 | 0.050252 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.054992 | 0.050252 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.054992 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.054992 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014047 | 0.054992 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014047 | 0.054992 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014047 | 0.055008 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014047 | 0.055008 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014047 | 0.054992 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014047 | 0.054976 | 0.050268 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014047 | 0.054976 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014047 | 0.054976 | 0.050252 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014047 | 0.054976 | 0.050252 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014063 | 0.054976 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014063 | 0.054976 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014047 | 0.054976 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014047 | 0.054992 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.054992 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014047 | 0.055008 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014063 | 0.055008 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014079 | 0.054992 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014079 | 0.054992 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014063 | 0.054992 | 0.050252 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014047 | 0.055008 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014047 | 0.055008 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014047 | 0.055008 | 0.05022 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014047 | 0.055008 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014047 | 0.055008 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014047 | 0.054992 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014047 | 0.054992 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014047 | 0.054992 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014047 | 0.054992 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014047 | 0.054992 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014047 | 0.055008 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014047 | 0.055008 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014047 | 0.055024 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.055024 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.055024 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.055024 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.055024 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.055008 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014016 | 0.055008 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014016 | 0.055008 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014016 | 0.055008 | 0.050205 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014016 | 0.054992 | 0.050205 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014016 | 0.054992 | 0.050205 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014016 | 0.055008 | 0.050205 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014016 | 0.055008 | 0.050205 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014016 | 0.055008 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014016 | 0.055008 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014016 | 0.055008 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014016 | 0.055008 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014016 | 0.055024 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014016 | 0.055024 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014016 | 0.055024 | 0.050252 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014016 | 0.055008 | 0.050236 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014016 | 0.055008 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014016 | 0.055008 | 0.050236 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014 | 0.054992 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014 | 0.054992 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014 | 0.054992 | 0.05022 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014 | 0.054992 | 0.05022 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014 | 0.054992 | 0.05022 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014016 | 0.054992 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014016 | 0.055008 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.055008 | 0.050252 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.055008 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.055008 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.055008 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014016 | 0.055024 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014 | 0.055024 | 0.050252 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014 | 0.055024 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014 | 0.055024 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014 | 0.055008 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014 | 0.055008 | 0.050252 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014 | 0.054992 | 0.050252 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014 | 0.054992 | 0.050252 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014 | 0.054992 | 0.050252 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014016 | 0.054992 | 0.050252 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014016 | 0.054992 | 0.050252 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.054992 | 0.050252 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.055008 | 0.050268 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.055024 | 0.050268 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014016 | 0.055039 | 0.050252 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014 | 0.055039 | 0.050252 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014 | 0.055039 | 0.050252 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014 | 0.055039 | 0.050252 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014016 | 0.055024 | 0.050252 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014016 | 0.055008 | 0.050252 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014016 | 0.055008 | 0.050252 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014016 | 0.055008 | 0.050252 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.055008 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.055008 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.055008 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.055008 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014016 | 0.055008 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014016 | 0.055024 | 0.05022 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014 | 0.055024 | 0.05022 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014 | 0.055024 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014016 | 0.055024 | 0.050252 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.055024 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014047 | 0.055024 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014047 | 0.055024 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.055024 | 0.050252 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.055024 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014016 | 0.055024 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014016 | 0.055024 | 0.05022 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014016 | 0.055024 | 0.05022 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014016 | 0.055024 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014016 | 0.055024 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014016 | 0.055024 | 0.05022 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014016 | 0.055024 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.055024 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.055024 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014047 | 0.055024 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.055024 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.055039 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014016 | 0.055039 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014016 | 0.055039 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014016 | 0.055024 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014016 | 0.055024 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014016 | 0.055008 | 0.050252 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014016 | 0.055008 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014016 | 0.055008 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.055008 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.055008 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.055008 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.055008 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.055024 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.055024 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014016 | 0.055039 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014016 | 0.055055 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.055039 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.055039 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014047 | 0.055024 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014047 | 0.055024 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.055024 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.055024 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.055024 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.055024 | 0.05022 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.055024 | 0.05022 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.055024 | 0.05022 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.055024 | 0.05022 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.055039 | 0.05022 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014016 | 0.055039 | 0.05022 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.055039 | 0.05022 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.055039 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014047 | 0.055024 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014047 | 0.055024 | 0.050252 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014047 | 0.055024 | 0.050252 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014047 | 0.055039 | 0.050252 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.055039 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.055039 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.055024 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.055024 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.055024 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.055008 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.055008 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.055024 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.055024 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.055024 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.055024 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.055024 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014016 | 0.055024 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014016 | 0.055039 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014016 | 0.055024 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014016 | 0.055024 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014016 | 0.055008 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014016 | 0.055008 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014016 | 0.054992 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014016 | 0.054992 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014016 | 0.054992 | 0.050236 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014016 | 0.054992 | 0.050236 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014016 | 0.054992 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014016 | 0.054992 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014016 | 0.054992 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014016 | 0.054992 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014016 | 0.055008 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.055008 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014047 | 0.055008 | 0.050268 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014047 | 0.055008 | 0.050268 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014047 | 0.055008 | 0.050268 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014047 | 0.055008 | 0.050268 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.055008 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.055008 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.055008 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.055008 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.054992 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.054992 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.054992 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.054992 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014047 | 0.054992 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014063 | 0.054992 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014063 | 0.054992 | 0.050268 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014063 | 0.054992 | 0.050268 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014047 | 0.055024 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014047 | 0.055024 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.055024 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.055024 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014047 | 0.055008 | 0.050268 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014047 | 0.054992 | 0.050268 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014047 | 0.054976 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014047 | 0.054976 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014047 | 0.054976 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014047 | 0.054976 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014063 | 0.054976 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014047 | 0.054976 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014047 | 0.054976 | 0.050236 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.054992 | 0.050236 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.055008 | 0.050236 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014016 | 0.055008 | 0.050236 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.055008 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.054992 | 0.050268 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014047 | 0.054992 | 0.050283 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014047 | 0.054976 | 0.050299 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.054976 | 0.050299 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.054976 | 0.050283 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.054976 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.054961 | 0.050252 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.054961 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.054961 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.054961 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014016 | 0.054961 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014016 | 0.054976 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014016 | 0.054976 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014016 | 0.054976 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.054976 | 0.050268 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014047 | 0.054976 | 0.050283 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014047 | 0.054961 | 0.050299 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014047 | 0.054976 | 0.050299 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.054976 | 0.050283 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.054992 | 0.050268 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.054992 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.054992 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.054976 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014016 | 0.054961 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014016 | 0.054961 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.054961 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.054961 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014047 | 0.054961 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014063 | 0.054961 | 0.050268 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014063 | 0.054976 | 0.050268 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014047 | 0.054992 | 0.050268 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.055008 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.055024 | 0.050252 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014016 | 0.055024 | 0.050236 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014016 | 0.055008 | 0.050252 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.054992 | 0.050252 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.054992 | 0.050268 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.054976 | 0.050268 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.054976 | 0.050268 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.054976 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.054976 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.054976 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.054976 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.054992 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.054992 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014031 | 0.054992 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014047 | 0.054992 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014047 | 0.054992 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014047 | 0.054992 | 0.050268 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.011 | 0.014047 | 0.054992 | 0.050268 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.011 | 0.014047 | 0.055008 | 0.050268 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014047 | 0.055008 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014047 | 0.055008 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.012 | 0.014047 | 0.055008 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.011 | 0.014047 | 0.054992 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.011 | 0.014047 | 0.054992 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.011 | 0.014047 | 0.054992 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.011 | 0.014047 | 0.054992 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.011 | 0.014047 | 0.054992 | 0.050268 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.011 | 0.014047 | 0.054992 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.011 | 0.014047 | 0.055008 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.011 | 0.014063 | 0.055008 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.011 | 0.014063 | 0.055008 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.011 | 0.014063 | 0.055024 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.011 | 0.014047 | 0.055024 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.011 | 0.014047 | 0.055024 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.011 | 0.014047 | 0.055024 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.011 | 0.014047 | 0.055024 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.011 | 0.014063 | 0.055008 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.011 | 0.014063 | 0.055008 | 0.050283 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.011 | 0.014063 | 0.055008 | 0.050268 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.011 | 0.014063 | 0.055008 | 0.050268 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.011 | 0.014063 | 0.055008 | 0.050268 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.011 | 0.014063 | 0.055008 | 0.050268 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.011 | 0.014063 | 0.055008 | 0.050268 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.011 | 0.014063 | 0.055008 | 0.050268 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.011 | 0.014063 | 0.055024 | 0.050268 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.011 | 0.014063 | 0.055024 | 0.050268 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.011 | 0.014047 | 0.055039 | 0.050283 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.011 | 0.014047 | 0.055039 | 0.050283 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.011 | 0.014063 | 0.055039 | 0.050283 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.011 | 0.014063 | 0.055039 | 0.050283 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.011 | 0.014063 | 0.055024 | 0.050283 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.011 | 0.014063 | 0.055024 | 0.050268 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.011 | 0.014047 | 0.055024 | 0.050268 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.011 | 0.014047 | 0.055024 | 0.050268 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.011 | 0.014047 | 0.055024 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.011 | 0.014047 | 0.055024 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.011 | 0.014047 | 0.055008 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.011 | 0.014047 | 0.055008 | 0.050252 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.011 | 0.014047 | 0.055008 | 0.050252 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.011 | 0.014047 | 0.055008 | 0.050252 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.011 | 0.014063 | 0.055008 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.011 | 0.014063 | 0.055024 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.011 | 0.014063 | 0.055024 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.011 | 0.014063 | 0.055024 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.011 | 0.014063 | 0.055024 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.011 | 0.014063 | 0.055008 | 0.050299 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.011 | 0.014063 | 0.055008 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.011 | 0.014063 | 0.055008 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.011 | 0.014063 | 0.055008 | 0.050283 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.011 | 0.014063 | 0.055008 | 0.050283 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.011 | 0.014063 | 0.054992 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.011 | 0.014063 | 0.054992 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.011 | 0.014063 | 0.054992 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.011 | 0.014063 | 0.054992 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.011 | 0.014063 | 0.054992 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.011 | 0.014063 | 0.054992 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.011 | 0.014063 | 0.055008 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.011 | 0.014063 | 0.055008 | 0.050299 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.011 | 0.014063 | 0.055008 | 0.050299 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.011 | 0.014063 | 0.055008 | 0.050299 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.011 | 0.014047 | 0.055008 | 0.050315 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.011 | 0.014047 | 0.055008 | 0.050315 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.011 | 0.014047 | 0.055008 | 0.050299 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.011 | 0.014047 | 0.054992 | 0.050299 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.011 | 0.014047 | 0.054992 | 0.050299 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.011 | 0.014047 | 0.054976 | 0.050299 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.011 | 0.014047 | 0.054976 | 0.050283 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.011 | 0.014047 | 0.054976 | 0.050283 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.011 | 0.014063 | 0.054976 | 0.050283 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.011 | 0.014063 | 0.054976 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.011 | 0.014063 | 0.054976 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.011 | 0.014063 | 0.054976 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.011 | 0.014047 | 0.054992 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.011 | 0.014047 | 0.054992 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.011 | 0.014047 | 0.054992 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.011 | 0.014047 | 0.054992 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.011 | 0.014047 | 0.055008 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.011 | 0.014047 | 0.055008 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.011 | 0.014047 | 0.054992 | 0.050299 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.011 | 0.014047 | 0.054992 | 0.050299 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.011 | 0.014047 | 0.054992 | 0.050283 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.011 | 0.014047 | 0.054976 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.011 | 0.014047 | 0.054976 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.011 | 0.014047 | 0.054976 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.011 | 0.014047 | 0.054976 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.011 | 0.014047 | 0.054976 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.011 | 0.014031 | 0.054976 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.011 | 0.014031 | 0.054976 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.01 | 0 | 0.011 | 0.014031 | 0.054976 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.009 | 0 | 0.011 | 0.014031 | 0.054976 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.009 | 0 | 0.011 | 0.014031 | 0.054976 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.009 | 0 | 0.011 | 0.014031 | 0.054976 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.009 | 0 | 0.011 | 0.014047 | 0.054976 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.009 | 0 | 0.011 | 0.014047 | 0.054976 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.009 | 0 | 0.011 | 0.014047 | 0.054976 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.009 | 0 | 0.011 | 0.014047 | 0.054976 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.009 | 0 | 0.011 | 0.014047 | 0.054961 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.009 | 0 | 0.011 | 0.014047 | 0.054961 | 0.050268 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.009 | 0 | 0.011 | 0.014047 | 0.054961 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.009 | 0 | 0.011 | 0.014047 | 0.054961 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.009 | 0 | 0.011 | 0.014047 | 0.054961 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.009 | 0 | 0.011 | 0.014047 | 0.054961 | 0.050252 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.009 | 0 | 0.011 | 0.014047 | 0.054961 | 0.050252 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.009 | 0 | 0.011 | 0.014047 | 0.054961 | 0.050252 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.009 | 0 | 0.011 | 0.014047 | 0.054976 | 0.050252 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.009 | 0 | 0.011 | 0.014047 | 0.054976 | 0.050252 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.009 | 0 | 0.011 | 0.014047 | 0.054976 | 0.050252 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.009 | 0 | 0.011 | 0.014047 | 0.054976 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.009 | 0 | 0.011 | 0.014063 | 0.054976 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.009 | 0 | 0.011 | 0.014063 | 0.054976 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.009 | 0 | 0.011 | 0.014063 | 0.054976 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.009 | 0 | 0.011 | 0.014063 | 0.054976 | 0.050252 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.009 | 0 | 0.011 | 0.014047 | 0.054976 | 0.050252 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.009 | 0 | 0.011 | 0.014047 | 0.054976 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.009 | 0 | 0.011 | 0.014047 | 0.054976 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.009 | 0 | 0.011 | 0.014047 | 0.054961 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.009 | 0 | 0.011 | 0.014047 | 0.054961 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.009 | 0 | 0.011 | 0.014063 | 0.054961 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.009 | 0 | 0.011 | 0.014063 | 0.054961 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.009 | 0 | 0.011 | 0.014063 | 0.054961 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.009 | 0 | 0.011 | 0.014063 | 0.054961 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.009 | 0 | 0.011 | 0.014063 | 0.054976 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.009 | 0 | 0.011 | 0.014063 | 0.054976 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.009 | 0 | 0.011 | 0.014063 | 0.054992 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.009 | 0 | 0.011 | 0.014047 | 0.054992 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.009 | 0 | 0.011 | 0.014063 | 0.054976 | 0.050268 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.009 | 0 | 0.011 | 0.014063 | 0.054976 | 0.050268 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.009 | 0 | 0.011 | 0.014063 | 0.054961 | 0.050268 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.009 | 0 | 0.011 | 0.014063 | 0.054961 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.009 | 0 | 0.011 | 0.014063 | 0.054945 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.009 | 0 | 0.011 | 0.014063 | 0.054945 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.009 | 0 | 0.011 | 0.014063 | 0.054945 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.009 | 0 | 0.011 | 0.014063 | 0.054945 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.009 | 0 | 0.011 | 0.014063 | 0.054945 | 0.05022 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.009 | 0 | 0.011 | 0.014063 | 0.054945 | 0.050236 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.009 | 0 | 0.011 | 0.014063 | 0.054961 | 0.050236 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.009 | 0 | 0.011 | 0.014063 | 0.054961 | 0.050236 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014079 | 0.054961 | 0.050252 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.009 | 0 | 0.011 | 0.014079 | 0.054961 | 0.050252 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.009 | 0 | 0.011 | 0.014094 | 0.054961 | 0.050268 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.009 | 0 | 0.011 | 0.014094 | 0.054961 | 0.050268 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.009 | 0 | 0.011 | 0.014094 | 0.054961 | 0.050252 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.009 | 0 | 0.011 | 0.014079 | 0.054961 | 0.050252 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.009 | 0 | 0.011 | 0.014079 | 0.054961 | 0.050236 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.009 | 0 | 0.011 | 0.014079 | 0.054945 | 0.050236 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.009 | 0 | 0.011 | 0.014079 | 0.054929 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.009 | 0 | 0.011 | 0.014079 | 0.054929 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.009 | 0 | 0.011 | 0.014079 | 0.054929 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.009 | 0 | 0.011 | 0.014079 | 0.054929 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.009 | 0 | 0.011 | 0.014079 | 0.054929 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.009 | 0 | 0.011 | 0.014079 | 0.054929 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.009 | 0 | 0.011 | 0.014094 | 0.054929 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.009 | 0 | 0.011 | 0.014094 | 0.054929 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.009 | 0 | 0.011 | 0.01411 | 0.054929 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.009 | 0 | 0.011 | 0.01411 | 0.054945 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.009 | 0 | 0.011 | 0.014094 | 0.054945 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.009 | 0 | 0.011 | 0.014094 | 0.054961 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.009 | 0 | 0.011 | 0.014094 | 0.054961 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.009 | 0 | 0.011 | 0.014094 | 0.054961 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.009 | 0 | 0.011 | 0.014094 | 0.054945 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.009 | 0 | 0.011 | 0.014094 | 0.054945 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.009 | 0 | 0.011 | 0.014094 | 0.054945 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.009 | 0 | 0.011 | 0.014094 | 0.054929 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.009 | 0 | 0.011 | 0.014094 | 0.054929 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.009 | 0 | 0.011 | 0.014094 | 0.054929 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.009 | 0 | 0.011 | 0.014094 | 0.054929 | 0.05022 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.009 | 0 | 0.011 | 0.014094 | 0.054929 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.009 | 0 | 0.011 | 0.014094 | 0.054929 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.009 | 0 | 0.011 | 0.014094 | 0.054945 | 0.050236 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.009 | 0 | 0.011 | 0.014094 | 0.054945 | 0.050236 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.009 | 0 | 0.011 | 0.014094 | 0.054961 | 0.050252 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.009 | 0 | 0.011 | 0.014094 | 0.054961 | 0.050252 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014094 | 0.054961 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014094 | 0.054961 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014094 | 0.054961 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014094 | 0.054961 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014094 | 0.054961 | 0.050268 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014094 | 0.054961 | 0.050252 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014094 | 0.054945 | 0.050252 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014094 | 0.054945 | 0.050252 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014094 | 0.054945 | 0.050252 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014094 | 0.054945 | 0.050252 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014094 | 0.054945 | 0.050252 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014094 | 0.054945 | 0.050252 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014094 | 0.054961 | 0.050252 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014094 | 0.054961 | 0.050252 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014094 | 0.054961 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014094 | 0.054976 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014079 | 0.054976 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014079 | 0.054976 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014094 | 0.054976 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014094 | 0.054961 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014094 | 0.054961 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014094 | 0.054961 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014094 | 0.054961 | 0.050268 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014094 | 0.054961 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014094 | 0.054961 | 0.050268 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014094 | 0.054961 | 0.050252 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014094 | 0.054961 | 0.050252 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014094 | 0.054961 | 0.050252 | 0.00028346
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014094 | 0.054976 | 0.050268 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014079 | 0.054976 | 0.050268 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014079 | 0.054976 | 0.050268 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014079 | 0.054976 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014094 | 0.054992 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014094 | 0.054992 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014094 | 0.054992 | 0.050299 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014094 | 0.054976 | 0.050299 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014094 | 0.054976 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014094 | 0.054976 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014094 | 0.054976 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014094 | 0.054961 | 0.050252 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014094 | 0.054961 | 0.050252 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014079 | 0.054961 | 0.050252 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014079 | 0.054976 | 0.050252 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014079 | 0.054976 | 0.050252 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014079 | 0.054976 | 0.050252 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014079 | 0.054976 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014094 | 0.054976 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014094 | 0.054976 | 0.050299 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.01411 | 0.054976 | 0.050299 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.01411 | 0.054976 | 0.050299 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014094 | 0.054976 | 0.050299 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014094 | 0.054976 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014079 | 0.054976 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014079 | 0.054976 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014079 | 0.054961 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014079 | 0.054961 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014079 | 0.054961 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014079 | 0.054961 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014079 | 0.054961 | 0.050283 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014094 | 0.054961 | 0.050283 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014094 | 0.054961 | 0.050299 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.01411 | 0.054961 | 0.050299 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.01411 | 0.054976 | 0.050299 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.01411 | 0.054992 | 0.050299 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014094 | 0.054992 | 0.050299 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014094 | 0.054992 | 0.050299 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014094 | 0.054976 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014094 | 0.054976 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014094 | 0.054976 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014094 | 0.054976 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014094 | 0.054976 | 0.050283 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014094 | 0.054976 | 0.050283 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014094 | 0.054976 | 0.050283 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014094 | 0.054976 | 0.050283 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014094 | 0.054976 | 0.050283 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014094 | 0.054976 | 0.050283 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014094 | 0.054976 | 0.050299 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014094 | 0.054992 | 0.050299 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014094 | 0.054992 | 0.050299 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014079 | 0.054992 | 0.050299 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014079 | 0.054992 | 0.050299 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014079 | 0.054992 | 0.050299 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014079 | 0.054992 | 0.050299 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014079 | 0.054992 | 0.050283 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014079 | 0.054992 | 0.050283 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014079 | 0.054976 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014079 | 0.054976 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014079 | 0.054976 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014079 | 0.054976 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014079 | 0.054976 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014079 | 0.054976 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014079 | 0.054976 | 0.050268 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014079 | 0.054976 | 0.050268 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014079 | 0.054992 | 0.050268 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014063 | 0.054992 | 0.050268 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014063 | 0.054992 | 0.050268 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014063 | 0.054992 | 0.050268 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014063 | 0.054976 | 0.050283 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014063 | 0.054976 | 0.050283 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014063 | 0.054976 | 0.050283 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014063 | 0.054961 | 0.050283 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014063 | 0.054961 | 0.050283 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014063 | 0.054961 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014063 | 0.054945 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014079 | 0.054945 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014079 | 0.054945 | 0.050252 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014079 | 0.054945 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014079 | 0.054961 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014079 | 0.054961 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014079 | 0.054961 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014063 | 0.054976 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014079 | 0.054976 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014079 | 0.054976 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014079 | 0.054976 | 0.050299 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014079 | 0.054961 | 0.050299 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014079 | 0.054961 | 0.050299 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014079 | 0.054945 | 0.050299 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014079 | 0.054945 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014079 | 0.054945 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014079 | 0.054945 | 0.050268 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014079 | 0.054945 | 0.050268 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014079 | 0.054945 | 0.050268 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014079 | 0.054945 | 0.050268 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014079 | 0.054961 | 0.050268 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014079 | 0.054961 | 0.050283 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014094 | 0.054961 | 0.050283 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.01411 | 0.054961 | 0.050299 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014126 | 0.054961 | 0.050299 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.01411 | 0.054976 | 0.050299 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.01411 | 0.054976 | 0.050299 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.01411 | 0.054992 | 0.050283 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.01411 | 0.054976 | 0.050283 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.01411 | 0.054976 | 0.050283 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.01411 | 0.054961 | 0.050283 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.01411 | 0.054961 | 0.050283 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.01411 | 0.054961 | 0.050283 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.01411 | 0.054961 | 0.050268 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.01411 | 0.054961 | 0.050268 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.01411 | 0.054961 | 0.050283 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.01411 | 0.054961 | 0.050283 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.01411 | 0.054976 | 0.050283 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.01411 | 0.054976 | 0.050283 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.01411 | 0.054976 | 0.050283 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.01411 | 0.054992 | 0.050299 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.01411 | 0.054992 | 0.050299 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.01411 | 0.054992 | 0.050315 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.01411 | 0.054976 | 0.050299 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.01411 | 0.054976 | 0.050299 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.01411 | 0.054976 | 0.050299 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.01411 | 0.054961 | 0.050283 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.01411 | 0.054961 | 0.050283 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.01411 | 0.054961 | 0.050268 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.01411 | 0.054961 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.01411 | 0.054961 | 0.050268 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.01411 | 0.054961 | 0.050268 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.01411 | 0.054961 | 0.050268 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.01411 | 0.054976 | 0.050268 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.01411 | 0.054976 | 0.050283 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.01411 | 0.054976 | 0.050283 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.01411 | 0.054976 | 0.050299 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.01411 | 0.054976 | 0.050299 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.01411 | 0.054976 | 0.050299 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014094 | 0.054976 | 0.050299 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014094 | 0.054976 | 0.050283 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014094 | 0.054976 | 0.050283 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014094 | 0.054976 | 0.050283 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014094 | 0.054961 | 0.050283 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014079 | 0.054961 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014079 | 0.054945 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014079 | 0.054945 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014094 | 0.054961 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014094 | 0.054961 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014094 | 0.054961 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.01411 | 0.054961 | 0.050299 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.01411 | 0.054961 | 0.050299 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.01411 | 0.054961 | 0.050299 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014094 | 0.054961 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014094 | 0.054961 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014094 | 0.054961 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014094 | 0.054961 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014094 | 0.054961 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014094 | 0.054945 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014094 | 0.054945 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014094 | 0.054945 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014094 | 0.054945 | 0.050283 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.01411 | 0.054945 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.01411 | 0.054945 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.01411 | 0.054945 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.01411 | 0.054945 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.01411 | 0.054945 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014094 | 0.054961 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014094 | 0.054961 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014094 | 0.054961 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014094 | 0.054945 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.01411 | 0.054929 | 0.050315 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.01411 | 0.054929 | 0.050315 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.01411 | 0.054929 | 0.050315 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.01411 | 0.054929 | 0.050315 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.01411 | 0.054929 | 0.050299 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.01411 | 0.054929 | 0.050299 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.01411 | 0.054929 | 0.050299 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.01411 | 0.054929 | 0.050299 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014094 | 0.054929 | 0.050299 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014094 | 0.054929 | 0.050299 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014079 | 0.054945 | 0.050299 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014079 | 0.054945 | 0.050299 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014094 | 0.054945 | 0.050299 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014094 | 0.054945 | 0.050315 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014094 | 0.054945 | 0.050315 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014094 | 0.054945 | 0.050331 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014079 | 0.054945 | 0.050331 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014079 | 0.054945 | 0.050331 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014079 | 0.054945 | 0.050315 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014079 | 0.054929 | 0.050315 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014079 | 0.054929 | 0.050315 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014079 | 0.054929 | 0.050315 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014079 | 0.054929 | 0.050315 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014079 | 0.054929 | 0.050315 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014079 | 0.054929 | 0.050315 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014079 | 0.054929 | 0.050315 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014079 | 0.054945 | 0.050315 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014079 | 0.054945 | 0.050331 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014094 | 0.054945 | 0.050331 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014094 | 0.054945 | 0.050346 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014094 | 0.054961 | 0.050346 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014079 | 0.054961 | 0.050346 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014079 | 0.054961 | 0.050331 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014063 | 0.054961 | 0.050331 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014063 | 0.054945 | 0.050331 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014063 | 0.054945 | 0.050315 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014063 | 0.054945 | 0.050315 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014063 | 0.054929 | 0.050315 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014079 | 0.054929 | 0.050315 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014079 | 0.054929 | 0.050315 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014079 | 0.054929 | 0.050315 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014079 | 0.054945 | 0.050315 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014079 | 0.054945 | 0.050331 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014079 | 0.054961 | 0.050331 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014079 | 0.054961 | 0.050331 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014079 | 0.054961 | 0.050331 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014079 | 0.054961 | 0.050331 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014079 | 0.054961 | 0.050331 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014079 | 0.054961 | 0.050331 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014079 | 0.054961 | 0.050331 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014079 | 0.054945 | 0.050331 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014079 | 0.054945 | 0.050331 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014079 | 0.054945 | 0.050331 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014079 | 0.054929 | 0.050315 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014079 | 0.054929 | 0.050315 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014079 | 0.054929 | 0.050315 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014079 | 0.054929 | 0.050315 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014094 | 0.054929 | 0.050315 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014094 | 0.054929 | 0.050331 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014094 | 0.054945 | 0.050331 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014094 | 0.054945 | 0.050331 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014079 | 0.054945 | 0.050315 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014079 | 0.054945 | 0.050315 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014079 | 0.054945 | 0.050315 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014079 | 0.054945 | 0.050315 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014079 | 0.054929 | 0.050315 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014094 | 0.054913 | 0.050315 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014094 | 0.054913 | 0.050315 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014094 | 0.054913 | 0.050299 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014094 | 0.054913 | 0.050299 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014094 | 0.054913 | 0.050299 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014094 | 0.054913 | 0.050299 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014094 | 0.054913 | 0.050299 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014094 | 0.054913 | 0.050299 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014094 | 0.054929 | 0.050299 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014094 | 0.054929 | 0.050299 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014094 | 0.054929 | 0.050299 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014094 | 0.054929 | 0.050299 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.01411 | 0.054913 | 0.050315 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.01411 | 0.054913 | 0.050315 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.01411 | 0.054913 | 0.050299 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.01411 | 0.054913 | 0.050299 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.01411 | 0.054913 | 0.050299 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.01411 | 0.054913 | 0.050283 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.01411 | 0.054913 | 0.050283 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.01411 | 0.054898 | 0.050268 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.01411 | 0.054898 | 0.050268 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.01411 | 0.054898 | 0.050268 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.01411 | 0.054913 | 0.050268 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.01411 | 0.054913 | 0.050268 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.01411 | 0.054913 | 0.050268 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.01411 | 0.054929 | 0.050283 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014126 | 0.054929 | 0.050283 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014126 | 0.054929 | 0.050299 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014142 | 0.054929 | 0.050299 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014142 | 0.054929 | 0.050299 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014126 | 0.054929 | 0.050299 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014126 | 0.054929 | 0.050299 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014126 | 0.054945 | 0.050299 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014126 | 0.054929 | 0.050283 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014126 | 0.054929 | 0.050283 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014126 | 0.054913 | 0.050283 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014126 | 0.054913 | 0.050283 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014126 | 0.054913 | 0.050283 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014126 | 0.054929 | 0.050283 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014126 | 0.054929 | 0.050299 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014126 | 0.054929 | 0.050299 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014126 | 0.054929 | 0.050315 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014126 | 0.054945 | 0.050315 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014126 | 0.054945 | 0.050315 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.01411 | 0.054961 | 0.050315 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.01411 | 0.054961 | 0.050315 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014094 | 0.054945 | 0.050315 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014094 | 0.054945 | 0.050315 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014094 | 0.054945 | 0.050315 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014094 | 0.054945 | 0.050315 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014094 | 0.054929 | 0.050315 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014094 | 0.054929 | 0.050315 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014094 | 0.054929 | 0.050315 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014094 | 0.054929 | 0.050315 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014094 | 0.054929 | 0.050315 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014094 | 0.054929 | 0.050315 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014094 | 0.054929 | 0.050315 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014094 | 0.054945 | 0.050315 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014079 | 0.054945 | 0.050315 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014079 | 0.054961 | 0.050315 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.01 | 0.014063 | 0.054961 | 0.050331 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014063 | 0.054961 | 0.050331 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.01 | 0.014079 | 0.054961 | 0.050346 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.01 | 0.014079 | 0.054945 | 0.050346 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.01 | 0.014079 | 0.054929 | 0.050346 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014079 | 0.054929 | 0.050346 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.011 | 0.014079 | 0.054929 | 0.050331 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.01 | 0.014079 | 0.054929 | 0.050331 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.01 | 0.014079 | 0.054929 | 0.050331 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.01 | 0.014079 | 0.054929 | 0.050331 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.01 | 0.014079 | 0.054929 | 0.050331 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.01 | 0.014079 | 0.054945 | 0.050331 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.01 | 0.014079 | 0.054945 | 0.050331 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.01 | 0.014079 | 0.054945 | 0.050331 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.01 | 0.014079 | 0.054945 | 0.050346 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.01 | 0.014094 | 0.054945 | 0.050362 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.01 | 0.01411 | 0.054929 | 0.050378 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.01 | 0.01411 | 0.054929 | 0.050378 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.01 | 0.014094 | 0.054945 | 0.050362 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.01 | 0.014079 | 0.054945 | 0.050346 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.01 | 0.014079 | 0.054945 | 0.050331 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.01 | 0.014079 | 0.054945 | 0.050331 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.01 | 0.014079 | 0.054929 | 0.050315 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.01 | 0.014079 | 0.054929 | 0.050315 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.01 | 0.014079 | 0.054929 | 0.050315 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.01 | 0.014079 | 0.054929 | 0.050315 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.01 | 0.014079 | 0.054929 | 0.050315 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.01 | 0.014094 | 0.054929 | 0.050331 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.01 | 0.014094 | 0.054929 | 0.050331 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.01 | 0.014094 | 0.054929 | 0.050346 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.01 | 0.014094 | 0.054929 | 0.050346 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.01 | 0.014094 | 0.054945 | 0.050346 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.01 | 0.014079 | 0.054945 | 0.050331 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.01 | 0.014079 | 0.054945 | 0.050331 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.01 | 0.014079 | 0.054945 | 0.050331 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.01 | 0.014079 | 0.054929 | 0.050331 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.01 | 0.014079 | 0.054929 | 0.050331 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.01 | 0.014079 | 0.054929 | 0.050315 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.01 | 0.014079 | 0.054913 | 0.050315 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.01 | 0.014079 | 0.054913 | 0.050315 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.01 | 0.014079 | 0.054913 | 0.050299 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.01 | 0.014079 | 0.054913 | 0.050299 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.01 | 0.014079 | 0.054913 | 0.050299 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.01 | 0.014079 | 0.054929 | 0.050299 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.01 | 0.014079 | 0.054945 | 0.050299 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.01 | 0.014063 | 0.054945 | 0.050299 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.01 | 0.014063 | 0.054945 | 0.050299 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.01 | 0.014063 | 0.054945 | 0.050315 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.01 | 0.014063 | 0.054945 | 0.050315 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.01 | 0.014063 | 0.054929 | 0.050315 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.01 | 0.014063 | 0.054929 | 0.050315 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.01 | 0.014063 | 0.054929 | 0.050315 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.01 | 0.014063 | 0.054929 | 0.050315 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.01 | 0.014063 | 0.054929 | 0.050299 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.01 | 0.014063 | 0.054913 | 0.050299 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.01 | 0.014063 | 0.054913 | 0.050299 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.01 | 0.014063 | 0.054913 | 0.050299 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.01 | 0.014063 | 0.054913 | 0.050299 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.01 | 0.014063 | 0.054913 | 0.050299 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.01 | 0.014063 | 0.054913 | 0.050299 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.01 | 0.014079 | 0.054929 | 0.050299 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.01 | 0.014079 | 0.054929 | 0.050315 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.01 | 0.014079 | 0.054929 | 0.050315 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.01 | 0.014079 | 0.054929 | 0.050315 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.01 | 0.014063 | 0.054929 | 0.050315 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.01 | 0.014063 | 0.054929 | 0.050315 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.01 | 0.014063 | 0.054929 | 0.050315 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.01 | 0.014063 | 0.054929 | 0.050299 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.01 | 0.014063 | 0.054913 | 0.050299 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.01 | 0.014063 | 0.054898 | 0.050299 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.01 | 0.014063 | 0.054898 | 0.050283 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.01 | 0.014063 | 0.054898 | 0.050283 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.01 | 0.014063 | 0.054898 | 0.050283 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.01 | 0.014063 | 0.054898 | 0.050283 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.01 | 0.014063 | 0.054898 | 0.050283 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.01 | 0.014063 | 0.054898 | 0.050283 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.01 | 0.014079 | 0.054898 | 0.050283 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.01 | 0.014079 | 0.054913 | 0.050299 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.01 | 0.014063 | 0.054929 | 0.050299 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.01 | 0.014063 | 0.054929 | 0.050299 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.009 | 0.014079 | 0.054913 | 0.050299 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.009 | 0.014079 | 0.054913 | 0.050299 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.009 | 0.014094 | 0.054882 | 0.050299 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.009 | 0.014094 | 0.054882 | 0.050299 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.009 | 0.014079 | 0.054882 | 0.050283 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.009 | 0.014079 | 0.054882 | 0.050268 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.009 | 0.014079 | 0.054882 | 0.050268 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.009 | 0.014079 | 0.054882 | 0.050268 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.009 | 0.014079 | 0.054882 | 0.050268 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.009 | 0.014079 | 0.054882 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.009 | 0.014079 | 0.054882 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.009 | 0.014079 | 0.054898 | 0.050268 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.009 | 0.014079 | 0.054898 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.009 | 0.014094 | 0.054898 | 0.050283 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.009 | 0.014094 | 0.054898 | 0.050299 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.009 | 0.014094 | 0.054913 | 0.050299 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.009 | 0.014094 | 0.054913 | 0.050299 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.009 | 0.014079 | 0.054929 | 0.050299 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.009 | 0.014079 | 0.054929 | 0.050299 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.009 | 0.014079 | 0.054929 | 0.050299 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.009 | 0.014094 | 0.054913 | 0.050299 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.009 | 0.014094 | 0.054913 | 0.050315 | 0.00026772
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.009 | 0.014094 | 0.054898 | 0.050315 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.009 | 0.014094 | 0.054898 | 0.050315 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.009 | 0.014094 | 0.054898 | 0.050299 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.009 | 0.014094 | 0.054898 | 0.050299 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.009 | 0.01411 | 0.054898 | 0.050299 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.009 | 0.01411 | 0.054898 | 0.050315 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.009 | 0.014094 | 0.054913 | 0.050315 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.009 | 0.014094 | 0.054913 | 0.050315 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.009 | 0.014094 | 0.054913 | 0.050315 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.009 | 0.014094 | 0.054929 | 0.050315 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.009 | 0.014094 | 0.054945 | 0.050331 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.009 | 0.014094 | 0.054945 | 0.050331 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.009 | 0.01411 | 0.054945 | 0.050346 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.009 | 0.01411 | 0.054929 | 0.050346 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.009 | 0.01411 | 0.054929 | 0.050346 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.009 | 0.01411 | 0.054913 | 0.050331 | 0.00025197
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.009 | 0.01411 | 0.054913 | 0.050331 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.009 | 0.01411 | 0.054913 | 0.050315 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.009 | 0.01411 | 0.054913 | 0.050315 | 0.00023622
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.009 | 0.01411 | 0.054913 | 0.050315 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.009 | 0.01411 | 0.054929 | 0.050315 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.009 | 0.01411 | 0.054945 | 0.050315 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.009 | 0.014094 | 0.054945 | 0.050315 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.009 | 0.01411 | 0.054945 | 0.050315 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.009 | 0.014126 | 0.054945 | 0.050331 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.009 | 0.014142 | 0.054929 | 0.050346 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.009 | 0.014142 | 0.054929 | 0.050346 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.009 | 0.014126 | 0.054929 | 0.050346 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.009 | 0.014126 | 0.054945 | 0.050346 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.009 | 0.01411 | 0.054945 | 0.050331 | 0.00022047
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.009 | 0.014094 | 0.054945 | 0.050315 | 0.00020472
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.009 | 0.014094 | 0.054929 | 0.050299 | 0.00020472
10/23/2022 | 3:23 | 0 | 0.008 | 0 | 0.009 | 0.014094 | 0.054929 | 0.050299 | 0.00022047

## 20221006-1
In GMT
Date | Time | Freq
2022-10-06 | 2:13 | 49.929
2022-10-06 | 2:13 | 49.928
2022-10-06 | 2:13 | 49.928
2022-10-06 | 2:13 | 49.931
2022-10-06 | 2:13 | 49.934
2022-10-06 | 2:13 | 49.934
2022-10-06 | 2:13 | 49.937
2022-10-06 | 2:13 | 49.94
2022-10-06 | 2:13 | 49.943
2022-10-06 | 2:13 | 49.945
2022-10-06 | 2:13 | 49.945
2022-10-06 | 2:13 | 49.947
2022-10-06 | 2:13 | 49.947
2022-10-06 | 2:13 | 49.944
2022-10-06 | 2:13 | 49.944
2022-10-06 | 2:13 | 49.943
2022-10-06 | 2:13 | 49.94
2022-10-06 | 2:13 | 49.937
2022-10-06 | 2:13 | 49.935
2022-10-06 | 2:13 | 49.932
2022-10-06 | 2:13 | 49.927
2022-10-06 | 2:13 | 49.923
2022-10-06 | 2:13 | 49.92
2022-10-06 | 2:13 | 49.925
2022-10-06 | 2:13 | 49.925
2022-10-06 | 2:13 | 49.925
2022-10-06 | 2:13 | 49.93
2022-10-06 | 2:13 | 49.933
2022-10-06 | 2:13 | 49.937
2022-10-06 | 2:13 | 49.937
2022-10-06 | 2:13 | 49.936
2022-10-06 | 2:14 | 49.937
2022-10-06 | 2:14 | 49.937
2022-10-06 | 2:14 | 49.936
2022-10-06 | 2:14 | 49.934
2022-10-06 | 2:14 | 49.933
2022-10-06 | 2:14 | 49.93
2022-10-06 | 2:14 | 49.928
2022-10-06 | 2:14 | 49.927
2022-10-06 | 2:14 | 49.926
2022-10-06 | 2:14 | 49.926
2022-10-06 | 2:14 | 49.929
2022-10-06 | 2:14 | 49.935
2022-10-06 | 2:14 | 49.937
2022-10-06 | 2:14 | 49.94
2022-10-06 | 2:14 | 49.941
2022-10-06 | 2:14 | 49.943
2022-10-06 | 2:14 | 49.943
2022-10-06 | 2:14 | 49.942
2022-10-06 | 2:14 | 49.94
2022-10-06 | 2:14 | 49.937
2022-10-06 | 2:14 | 49.932
2022-10-06 | 2:14 | 49.927
2022-10-06 | 2:14 | 49.925
2022-10-06 | 2:14 | 49.928
2022-10-06 | 2:14 | 49.931
2022-10-06 | 2:14 | 49.933
2022-10-06 | 2:14 | 49.934
2022-10-06 | 2:14 | 49.932
2022-10-06 | 2:14 | 49.931
2022-10-06 | 2:14 | 49.928
2022-10-06 | 2:14 | 49.923
2022-10-06 | 2:14 | 49.921
2022-10-06 | 2:14 | 49.923
2022-10-06 | 2:14 | 49.923
2022-10-06 | 2:14 | 49.923
2022-10-06 | 2:14 | 49.922
2022-10-06 | 2:14 | 49.92
2022-10-06 | 2:14 | 49.918
2022-10-06 | 2:14 | 49.919
2022-10-06 | 2:14 | 49.92
2022-10-06 | 2:14 | 49.919
2022-10-06 | 2:14 | 49.924
2022-10-06 | 2:14 | 49.931
2022-10-06 | 2:14 | 49.935
2022-10-06 | 2:14 | 49.938
2022-10-06 | 2:14 | 49.939
2022-10-06 | 2:14 | 49.938
2022-10-06 | 2:14 | 49.94
2022-10-06 | 2:14 | 49.938
2022-10-06 | 2:14 | 49.937
2022-10-06 | 2:14 | 49.934
2022-10-06 | 2:14 | 49.93
2022-10-06 | 2:14 | 49.926
2022-10-06 | 2:14 | 49.924
2022-10-06 | 2:14 | 49.921
2022-10-06 | 2:14 | 49.919
2022-10-06 | 2:14 | 49.917
2022-10-06 | 2:14 | 49.918
2022-10-06 | 2:14 | 49.923
2022-10-06 | 2:15 | 49.925
2022-10-06 | 2:15 | 49.926
2022-10-06 | 2:15 | 49.929
2022-10-06 | 2:15 | 49.93
2022-10-06 | 2:15 | 49.93
2022-10-06 | 2:15 | 49.93
2022-10-06 | 2:15 | 49.93
2022-10-06 | 2:15 | 49.93
2022-10-06 | 2:15 | 49.929
2022-10-06 | 2:15 | 49.927
2022-10-06 | 2:15 | 49.928
2022-10-06 | 2:15 | 49.929
2022-10-06 | 2:15 | 49.928
2022-10-06 | 2:15 | 49.927
2022-10-06 | 2:15 | 49.928
2022-10-06 | 2:15 | 49.929
2022-10-06 | 2:15 | 49.929
2022-10-06 | 2:15 | 49.929
2022-10-06 | 2:15 | 49.931
2022-10-06 | 2:15 | 49.93
2022-10-06 | 2:15 | 49.929
2022-10-06 | 2:15 | 49.926
2022-10-06 | 2:15 | 49.927
2022-10-06 | 2:15 | 49.924
2022-10-06 | 2:15 | 49.919
2022-10-06 | 2:15 | 49.918
2022-10-06 | 2:15 | 49.917
2022-10-06 | 2:15 | 49.926
2022-10-06 | 2:15 | 49.965
2022-10-06 | 2:15 | 49.993
2022-10-06 | 2:15 | 50.014
2022-10-06 | 2:15 | 50.03
2022-10-06 | 2:15 | 50.036
2022-10-06 | 2:15 | 50.043
2022-10-06 | 2:15 | 50.048
2022-10-06 | 2:15 | 50.045
2022-10-06 | 2:15 | 50.042
2022-10-06 | 2:15 | 50.043
2022-10-06 | 2:15 | 50.041
2022-10-06 | 2:15 | 50.041
2022-10-06 | 2:15 | 50.039
2022-10-06 | 2:15 | 50.036
2022-10-06 | 2:15 | 50.035
2022-10-06 | 2:15 | 50.034
2022-10-06 | 2:15 | 50.029
2022-10-06 | 2:15 | 50.029
2022-10-06 | 2:15 | 50.031
2022-10-06 | 2:15 | 50.031
2022-10-06 | 2:15 | 50.027
2022-10-06 | 2:15 | 50.022
2022-10-06 | 2:15 | 50.02
2022-10-06 | 2:15 | 50.019
2022-10-06 | 2:15 | 50.015
2022-10-06 | 2:15 | 50.015
2022-10-06 | 2:15 | 50.016
2022-10-06 | 2:15 | 50.016
2022-10-06 | 2:15 | 50.018
2022-10-06 | 2:15 | 50.02
2022-10-06 | 2:15 | 50.017
2022-10-06 | 2:15 | 50.015
2022-10-06 | 2:15 | 50.011
2022-10-06 | 2:16 | 50.011
2022-10-06 | 2:16 | 50.009
2022-10-06 | 2:16 | 50.007
2022-10-06 | 2:16 | 50.006
2022-10-06 | 2:16 | 50.007
2022-10-06 | 2:16 | 50.005
2022-10-06 | 2:16 | 50.005
2022-10-06 | 2:16 | 50.002
2022-10-06 | 2:16 | 50.006
2022-10-06 | 2:16 | 50.006
2022-10-06 | 2:16 | 50.006
2022-10-06 | 2:16 | 50.008
2022-10-06 | 2:16 | 50.009
2022-10-06 | 2:16 | 50.011
2022-10-06 | 2:16 | 50.014
2022-10-06 | 2:16 | 50.015
2022-10-06 | 2:16 | 50.015
2022-10-06 | 2:16 | 50.014
2022-10-06 | 2:16 | 50.013
2022-10-06 | 2:16 | 50.012
2022-10-06 | 2:16 | 50.011
2022-10-06 | 2:16 | 50.011
2022-10-06 | 2:16 | 50.008
2022-10-06 | 2:16 | 50.008
2022-10-06 | 2:16 | 50.009
2022-10-06 | 2:16 | 50.01
2022-10-06 | 2:16 | 50.011
2022-10-06 | 2:16 | 50.013
2022-10-06 | 2:16 | 50.015
2022-10-06 | 2:16 | 50.014
2022-10-06 | 2:16 | 50.012
2022-10-06 | 2:16 | 50.014
2022-10-06 | 2:16 | 50.013
2022-10-06 | 2:16 | 50.012
2022-10-06 | 2:16 | 50.012
2022-10-06 | 2:16 | 50.014
2022-10-06 | 2:16 | 50.016
2022-10-06 | 2:16 | 50.017
2022-10-06 | 2:16 | 50.016
2022-10-06 | 2:16 | 50.015
2022-10-06 | 2:16 | 50.012
2022-10-06 | 2:16 | 50.011
2022-10-06 | 2:16 | 50.013
2022-10-06 | 2:16 | 50.012
2022-10-06 | 2:16 | 50.012
2022-10-06 | 2:16 | 50.009
2022-10-06 | 2:16 | 50.009
2022-10-06 | 2:16 | 50.008
2022-10-06 | 2:16 | 50.007
2022-10-06 | 2:16 | 50.007
2022-10-06 | 2:16 | 50.009
2022-10-06 | 2:16 | 50.012
2022-10-06 | 2:16 | 50.012
2022-10-06 | 2:16 | 50.012
2022-10-06 | 2:16 | 50.016
2022-10-06 | 2:16 | 50.018
2022-10-06 | 2:16 | 50.016
2022-10-06 | 2:16 | 50.015
2022-10-06 | 2:16 | 50.019
2022-10-06 | 2:17 | 50.02
2022-10-06 | 2:17 | 50.019
2022-10-06 | 2:17 | 50.02
2022-10-06 | 2:17 | 50.02
2022-10-06 | 2:17 | 50.02
2022-10-06 | 2:17 | 50.017
2022-10-06 | 2:17 | 50.016
2022-10-06 | 2:17 | 50.015
2022-10-06 | 2:17 | 50.014
2022-10-06 | 2:17 | 50.012
2022-10-06 | 2:17 | 50.013
2022-10-06 | 2:17 | 50.014
2022-10-06 | 2:17 | 50.016
2022-10-06 | 2:17 | 50.015
2022-10-06 | 2:17 | 50.019
2022-10-06 | 2:17 | 50.02
2022-10-06 | 2:17 | 50.019
2022-10-06 | 2:17 | 50.018
2022-10-06 | 2:17 | 50.017
2022-10-06 | 2:17 | 50.016
2022-10-06 | 2:17 | 50.015
2022-10-06 | 2:17 | 50.012
2022-10-06 | 2:17 | 50.011
2022-10-06 | 2:17 | 50.011
2022-10-06 | 2:17 | 50.012
2022-10-06 | 2:17 | 50.012
2022-10-06 | 2:17 | 50.017
2022-10-06 | 2:17 | 50.018
2022-10-06 | 2:17 | 50.019
2022-10-06 | 2:17 | 50.018
2022-10-06 | 2:17 | 50.017
2022-10-06 | 2:17 | 50.014
2022-10-06 | 2:17 | 50.008
2022-10-06 | 2:17 | 50.005
2022-10-06 | 2:17 | 50.007
2022-10-06 | 2:17 | 50.006
2022-10-06 | 2:17 | 50.002
2022-10-06 | 2:17 | 50.003
2022-10-06 | 2:17 | 50.005
2022-10-06 | 2:17 | 50.006
2022-10-06 | 2:17 | 50.007
2022-10-06 | 2:17 | 50.012
2022-10-06 | 2:17 | 50.022
2022-10-06 | 2:17 | 50.025
2022-10-06 | 2:17 | 50.026
2022-10-06 | 2:17 | 50.026
2022-10-06 | 2:17 | 50.027
2022-10-06 | 2:17 | 50.025
2022-10-06 | 2:17 | 50.022
2022-10-06 | 2:17 | 50.019
2022-10-06 | 2:17 | 50.015
2022-10-06 | 2:17 | 50.013
2022-10-06 | 2:17 | 50.012
2022-10-06 | 2:17 | 50.014
2022-10-06 | 2:17 | 50.02
2022-10-06 | 2:17 | 50.023
2022-10-06 | 2:17 | 50.025
2022-10-06 | 2:17 | 50.025
2022-10-06 | 2:17 | 50.026
2022-10-06 | 2:17 | 50.025
2022-10-06 | 2:18 | 50.024
2022-10-06 | 2:18 | 50.024
2022-10-06 | 2:18 | 50.02
2022-10-06 | 2:18 | 50.014
2022-10-06 | 2:18 | 50.012
2022-10-06 | 2:18 | 50.008
2022-10-06 | 2:18 | 50.005
2022-10-06 | 2:18 | 50.003
2022-10-06 | 2:18 | 50
2022-10-06 | 2:18 | 49.998
2022-10-06 | 2:18 | 50.002
2022-10-06 | 2:18 | 50.005
2022-10-06 | 2:18 | 50.011
2022-10-06 | 2:18 | 50.012
2022-10-06 | 2:18 | 50.015
2022-10-06 | 2:18 | 50.016
2022-10-06 | 2:18 | 50.017
2022-10-06 | 2:18 | 50.016
2022-10-06 | 2:18 | 50.01
2022-10-06 | 2:18 | 50.007
2022-10-06 | 2:18 | 50.008
2022-10-06 | 2:18 | 50.007
2022-10-06 | 2:18 | 50.007
2022-10-06 | 2:18 | 50.006
2022-10-06 | 2:18 | 50.007
2022-10-06 | 2:18 | 50.009
2022-10-06 | 2:18 | 50.009
2022-10-06 | 2:18 | 50.011
2022-10-06 | 2:18 | 50.012
2022-10-06 | 2:18 | 50.016
2022-10-06 | 2:18 | 50.019

## 20221007-1
In GMT
Date | Time | Freq
2022-10-07 | 15:50 | 49.984
2022-10-07 | 15:50 | 49.981
2022-10-07 | 15:50 | 49.977
2022-10-07 | 15:50 | 49.976
2022-10-07 | 15:50 | 49.977
2022-10-07 | 15:50 | 49.979
2022-10-07 | 15:50 | 49.982
2022-10-07 | 15:50 | 49.979
2022-10-07 | 15:50 | 49.978
2022-10-07 | 15:50 | 49.973
2022-10-07 | 15:50 | 49.97
2022-10-07 | 15:50 | 49.966
2022-10-07 | 15:50 | 49.964
2022-10-07 | 15:50 | 49.961
2022-10-07 | 15:50 | 49.958
2022-10-07 | 15:50 | 49.957
2022-10-07 | 15:50 | 49.955
2022-10-07 | 15:50 | 49.952
2022-10-07 | 15:50 | 49.95
2022-10-07 | 15:50 | 49.954
2022-10-07 | 15:50 | 49.954
2022-10-07 | 15:50 | 49.955
2022-10-07 | 15:50 | 49.961
2022-10-07 | 15:50 | 49.962
2022-10-07 | 15:50 | 49.964
2022-10-07 | 15:50 | 49.962
2022-10-07 | 15:50 | 49.967
2022-10-07 | 15:50 | 49.969
2022-10-07 | 15:50 | 49.972
2022-10-07 | 15:50 | 49.975
2022-10-07 | 15:51 | 49.975
2022-10-07 | 15:51 | 49.976
2022-10-07 | 15:51 | 49.97
2022-10-07 | 15:51 | 49.96
2022-10-07 | 15:51 | 49.947
2022-10-07 | 15:51 | 49.935
2022-10-07 | 15:51 | 49.93
2022-10-07 | 15:51 | 49.926
2022-10-07 | 15:51 | 49.925
2022-10-07 | 15:51 | 49.924
2022-10-07 | 15:51 | 49.923
2022-10-07 | 15:51 | 49.923
2022-10-07 | 15:51 | 49.922
2022-10-07 | 15:51 | 49.921
2022-10-07 | 15:51 | 49.921
2022-10-07 | 15:51 | 49.922
2022-10-07 | 15:51 | 49.925
2022-10-07 | 15:51 | 49.923
2022-10-07 | 15:51 | 49.924
2022-10-07 | 15:51 | 49.926
2022-10-07 | 15:51 | 49.927
2022-10-07 | 15:51 | 49.927
2022-10-07 | 15:51 | 49.93
2022-10-07 | 15:51 | 49.935
2022-10-07 | 15:51 | 49.938
2022-10-07 | 15:51 | 49.937
2022-10-07 | 15:51 | 49.935
2022-10-07 | 15:51 | 49.935
2022-10-07 | 15:51 | 49.935
2022-10-07 | 15:51 | 49.931
2022-10-07 | 15:51 | 49.929
2022-10-07 | 15:51 | 49.924
2022-10-07 | 15:51 | 49.917
2022-10-07 | 15:51 | 49.909
2022-10-07 | 15:51 | 49.909
2022-10-07 | 15:51 | 49.908
2022-10-07 | 15:51 | 49.909
2022-10-07 | 15:51 | 49.913
2022-10-07 | 15:51 | 49.921
2022-10-07 | 15:51 | 49.928
2022-10-07 | 15:51 | 49.938
2022-10-07 | 15:51 | 49.945
2022-10-07 | 15:51 | 49.952
2022-10-07 | 15:51 | 49.966
2022-10-07 | 15:51 | 49.972
2022-10-07 | 15:51 | 49.973
2022-10-07 | 15:51 | 49.975
2022-10-07 | 15:51 | 49.977
2022-10-07 | 15:51 | 49.975
2022-10-07 | 15:51 | 49.975
2022-10-07 | 15:51 | 49.978
2022-10-07 | 15:51 | 49.977
2022-10-07 | 15:51 | 49.949
2022-10-07 | 15:51 | 49.897
2022-10-07 | 15:51 | 49.858
2022-10-07 | 15:51 | 49.826
2022-10-07 | 15:51 | 49.802
2022-10-07 | 15:51 | 49.786
2022-10-07 | 15:51 | 49.78
2022-10-07 | 15:51 | 49.779
2022-10-07 | 15:52 | 49.777
2022-10-07 | 15:52 | 49.777
2022-10-07 | 15:52 | 49.779
2022-10-07 | 15:52 | 49.782
2022-10-07 | 15:52 | 49.783
2022-10-07 | 15:52 | 49.786
2022-10-07 | 15:52 | 49.79
2022-10-07 | 15:52 | 49.791
2022-10-07 | 15:52 | 49.794
2022-10-07 | 15:52 | 49.798
2022-10-07 | 15:52 | 49.804
2022-10-07 | 15:52 | 49.805
2022-10-07 | 15:52 | 49.807
2022-10-07 | 15:52 | 49.807
2022-10-07 | 15:52 | 49.811
2022-10-07 | 15:52 | 49.808
2022-10-07 | 15:52 | 49.807
2022-10-07 | 15:52 | 49.806
2022-10-07 | 15:52 | 49.804
2022-10-07 | 15:52 | 49.798
2022-10-07 | 15:52 | 49.792
2022-10-07 | 15:52 | 49.787
2022-10-07 | 15:52 | 49.786
2022-10-07 | 15:52 | 49.785
2022-10-07 | 15:52 | 49.785
2022-10-07 | 15:52 | 49.786
2022-10-07 | 15:52 | 49.782
2022-10-07 | 15:52 | 49.781
2022-10-07 | 15:52 | 49.782
2022-10-07 | 15:52 | 49.785
2022-10-07 | 15:52 | 49.785
2022-10-07 | 15:52 | 49.786
2022-10-07 | 15:52 | 49.785
2022-10-07 | 15:52 | 49.788
2022-10-07 | 15:52 | 49.787
2022-10-07 | 15:52 | 49.785
2022-10-07 | 15:52 | 49.785
2022-10-07 | 15:52 | 49.785
2022-10-07 | 15:52 | 49.787
2022-10-07 | 15:52 | 49.79
2022-10-07 | 15:52 | 49.788
2022-10-07 | 15:52 | 49.789
2022-10-07 | 15:52 | 49.79
2022-10-07 | 15:52 | 49.793
2022-10-07 | 15:52 | 49.796
2022-10-07 | 15:52 | 49.798
2022-10-07 | 15:52 | 49.795
2022-10-07 | 15:52 | 49.794
2022-10-07 | 15:52 | 49.797
2022-10-07 | 15:52 | 49.802
2022-10-07 | 15:52 | 49.803
2022-10-07 | 15:52 | 49.806
2022-10-07 | 15:52 | 49.81
2022-10-07 | 15:52 | 49.815
2022-10-07 | 15:52 | 49.817
2022-10-07 | 15:52 | 49.819
2022-10-07 | 15:52 | 49.825
2022-10-07 | 15:52 | 49.828
2022-10-07 | 15:52 | 49.83
2022-10-07 | 15:52 | 49.836
2022-10-07 | 15:52 | 49.841
2022-10-07 | 15:53 | 49.845
2022-10-07 | 15:53 | 49.846
2022-10-07 | 15:53 | 49.849
2022-10-07 | 15:53 | 49.852
2022-10-07 | 15:53 | 49.856
2022-10-07 | 15:53 | 49.859
2022-10-07 | 15:53 | 49.861
2022-10-07 | 15:53 | 49.862
2022-10-07 | 15:53 | 49.862
2022-10-07 | 15:53 | 49.863
2022-10-07 | 15:53 | 49.864
2022-10-07 | 15:53 | 49.867
2022-10-07 | 15:53 | 49.865
2022-10-07 | 15:53 | 49.863
2022-10-07 | 15:53 | 49.862
2022-10-07 | 15:53 | 49.863
2022-10-07 | 15:53 | 49.863
2022-10-07 | 15:53 | 49.864
2022-10-07 | 15:53 | 49.866
2022-10-07 | 15:53 | 49.867
2022-10-07 | 15:53 | 49.872
2022-10-07 | 15:53 | 49.876
2022-10-07 | 15:53 | 49.88
2022-10-07 | 15:53 | 49.882
2022-10-07 | 15:53 | 49.88
2022-10-07 | 15:53 | 49.88
2022-10-07 | 15:53 | 49.883
2022-10-07 | 15:53 | 49.883
2022-10-07 | 15:53 | 49.881
2022-10-07 | 15:53 | 49.88
2022-10-07 | 15:53 | 49.877
2022-10-07 | 15:53 | 49.876
2022-10-07 | 15:53 | 49.874
2022-10-07 | 15:53 | 49.874
2022-10-07 | 15:53 | 49.875
2022-10-07 | 15:53 | 49.879
2022-10-07 | 15:53 | 49.88
2022-10-07 | 15:53 | 49.884
2022-10-07 | 15:53 | 49.89
2022-10-07 | 15:53 | 49.894
2022-10-07 | 15:53 | 49.901
2022-10-07 | 15:53 | 49.91
2022-10-07 | 15:53 | 49.915
2022-10-07 | 15:53 | 49.918
2022-10-07 | 15:53 | 49.918
2022-10-07 | 15:53 | 49.918
2022-10-07 | 15:53 | 49.922
2022-10-07 | 15:53 | 49.921
2022-10-07 | 15:53 | 49.918
2022-10-07 | 15:53 | 49.916
2022-10-07 | 15:53 | 49.917
2022-10-07 | 15:53 | 49.915
2022-10-07 | 15:53 | 49.913
2022-10-07 | 15:53 | 49.913
2022-10-07 | 15:53 | 49.912
2022-10-07 | 15:53 | 49.911
2022-10-07 | 15:53 | 49.917
2022-10-07 | 15:53 | 49.921
2022-10-07 | 15:53 | 49.925
2022-10-07 | 15:54 | 49.926
2022-10-07 | 15:54 | 49.923
2022-10-07 | 15:54 | 49.922
2022-10-07 | 15:54 | 49.921
2022-10-07 | 15:54 | 49.926
2022-10-07 | 15:54 | 49.93
2022-10-07 | 15:54 | 49.934
2022-10-07 | 15:54 | 49.941
2022-10-07 | 15:54 | 49.942
2022-10-07 | 15:54 | 49.945
2022-10-07 | 15:54 | 49.948
2022-10-07 | 15:54 | 49.947
2022-10-07 | 15:54 | 49.946
2022-10-07 | 15:54 | 49.946
2022-10-07 | 15:54 | 49.945
2022-10-07 | 15:54 | 49.939
2022-10-07 | 15:54 | 49.932
2022-10-07 | 15:54 | 49.925
2022-10-07 | 15:54 | 49.923
2022-10-07 | 15:54 | 49.922
2022-10-07 | 15:54 | 49.919
2022-10-07 | 15:54 | 49.917
2022-10-07 | 15:54 | 49.919
2022-10-07 | 15:54 | 49.918
2022-10-07 | 15:54 | 49.919
2022-10-07 | 15:54 | 49.918
2022-10-07 | 15:54 | 49.915
2022-10-07 | 15:54 | 49.91
2022-10-07 | 15:54 | 49.908
2022-10-07 | 15:54 | 49.906
2022-10-07 | 15:54 | 49.911
2022-10-07 | 15:54 | 49.91
2022-10-07 | 15:54 | 49.907
2022-10-07 | 15:54 | 49.906
2022-10-07 | 15:54 | 49.904
2022-10-07 | 15:54 | 49.901
2022-10-07 | 15:54 | 49.896
2022-10-07 | 15:54 | 49.896
2022-10-07 | 15:54 | 49.894
2022-10-07 | 15:54 | 49.893
2022-10-07 | 15:54 | 49.894
2022-10-07 | 15:54 | 49.896
2022-10-07 | 15:54 | 49.897
2022-10-07 | 15:54 | 49.903
2022-10-07 | 15:54 | 49.911
2022-10-07 | 15:54 | 49.918
2022-10-07 | 15:54 | 49.92
2022-10-07 | 15:54 | 49.921
2022-10-07 | 15:54 | 49.924
2022-10-07 | 15:54 | 49.927
2022-10-07 | 15:54 | 49.922
2022-10-07 | 15:54 | 49.918
2022-10-07 | 15:54 | 49.912
2022-10-07 | 15:54 | 49.911
2022-10-07 | 15:54 | 49.907
2022-10-07 | 15:54 | 49.91
2022-10-07 | 15:54 | 49.914
2022-10-07 | 15:54 | 49.919
2022-10-07 | 15:54 | 49.921
2022-10-07 | 15:54 | 49.922
2022-10-07 | 15:54 | 49.923
2022-10-07 | 15:55 | 49.921
2022-10-07 | 15:55 | 49.92
2022-10-07 | 15:55 | 49.923
2022-10-07 | 15:55 | 49.927
2022-10-07 | 15:55 | 49.928
2022-10-07 | 15:55 | 49.936
2022-10-07 | 15:55 | 49.94
2022-10-07 | 15:55 | 49.95
2022-10-07 | 15:55 | 49.958
2022-10-07 | 15:55 | 49.963
2022-10-07 | 15:55 | 49.965
2022-10-07 | 15:55 | 49.97
2022-10-07 | 15:55 | 49.978
2022-10-07 | 15:55 | 49.982
2022-10-07 | 15:55 | 49.985
2022-10-07 | 15:55 | 49.988
2022-10-07 | 15:55 | 49.99
2022-10-07 | 15:55 | 49.986
2022-10-07 | 15:55 | 49.981
2022-10-07 | 15:55 | 49.976
2022-10-07 | 15:55 | 49.971
2022-10-07 | 15:55 | 49.965
2022-10-07 | 15:55 | 49.962
2022-10-07 | 15:55 | 49.962
2022-10-07 | 15:55 | 49.964
2022-10-07 | 15:55 | 49.965
2022-10-07 | 15:55 | 49.973
2022-10-07 | 15:55 | 49.978
2022-10-07 | 15:55 | 49.981
2022-10-07 | 15:55 | 49.987
2022-10-07 | 15:55 | 49.99
2022-10-07 | 15:55 | 49.992
2022-10-07 | 15:55 | 49.993
2022-10-07 | 15:55 | 49.995
2022-10-07 | 15:55 | 50.001
2022-10-07 | 15:55 | 50.001
2022-10-07 | 15:55 | 50.001
2022-10-07 | 15:55 | 49.999
2022-10-07 | 15:55 | 49.997
2022-10-07 | 15:55 | 49.992
2022-10-07 | 15:55 | 49.987
2022-10-07 | 15:55 | 49.981
2022-10-07 | 15:55 | 49.979
2022-10-07 | 15:55 | 49.979
2022-10-07 | 15:55 | 49.981
2022-10-07 | 15:55 | 49.982
2022-10-07 | 15:55 | 49.983
2022-10-07 | 15:55 | 49.986
2022-10-07 | 15:55 | 49.988
2022-10-07 | 15:55 | 49.991
2022-10-07 | 15:55 | 49.994
2022-10-07 | 15:55 | 49.993
2022-10-07 | 15:55 | 49.993
2022-10-07 | 15:55 | 49.989
2022-10-07 | 15:55 | 49.985
2022-10-07 | 15:55 | 49.98
2022-10-07 | 15:55 | 49.979
2022-10-07 | 15:55 | 49.977
2022-10-07 | 15:55 | 49.977
2022-10-07 | 15:56 | 49.976
2022-10-07 | 15:56 | 49.977
2022-10-07 | 15:56 | 49.976
2022-10-07 | 15:56 | 49.977
2022-10-07 | 15:56 | 49.977
2022-10-07 | 15:56 | 49.978
2022-10-07 | 15:56 | 49.981
2022-10-07 | 15:56 | 49.983
2022-10-07 | 15:56 | 49.984
2022-10-07 | 15:56 | 49.981
2022-10-07 | 15:56 | 49.979
2022-10-07 | 15:56 | 49.976
2022-10-07 | 15:56 | 49.971
2022-10-07 | 15:56 | 49.969
2022-10-07 | 15:56 | 49.968
2022-10-07 | 15:56 | 49.963
2022-10-07 | 15:56 | 49.961
2022-10-07 | 15:56 | 49.958
2022-10-07 | 15:56 | 49.957
2022-10-07 | 15:56 | 49.958
2022-10-07 | 15:56 | 49.959
2022-10-07 | 15:56 | 49.962
2022-10-07 | 15:56 | 49.962
2022-10-07 | 15:56 | 49.962
2022-10-07 | 15:56 | 49.963
2022-10-07 | 15:56 | 49.969
2022-10-07 | 15:56 | 49.971
2022-10-07 | 15:56 | 49.974
2022-10-07 | 15:56 | 49.976
2022-10-07 | 15:56 | 49.976
2022-10-07 | 15:56 | 49.975

## 20221015-1
In GMT
Date | Time | Freq
2022-10-15 | 7:45 | 49.889
2022-10-15 | 7:45 | 49.888
2022-10-15 | 7:45 | 49.886
2022-10-15 | 7:45 | 49.888
2022-10-15 | 7:45 | 49.886
2022-10-15 | 7:45 | 49.887
2022-10-15 | 7:45 | 49.889
2022-10-15 | 7:45 | 49.893
2022-10-15 | 7:45 | 49.895
2022-10-15 | 7:45 | 49.895
2022-10-15 | 7:45 | 49.896
2022-10-15 | 7:45 | 49.896
2022-10-15 | 7:45 | 49.896
2022-10-15 | 7:45 | 49.896
2022-10-15 | 7:45 | 49.898
2022-10-15 | 7:45 | 49.901
2022-10-15 | 7:45 | 49.902
2022-10-15 | 7:45 | 49.902
2022-10-15 | 7:45 | 49.903
2022-10-15 | 7:45 | 49.902
2022-10-15 | 7:45 | 49.9
2022-10-15 | 7:45 | 49.896
2022-10-15 | 7:45 | 49.893
2022-10-15 | 7:45 | 49.893
2022-10-15 | 7:45 | 49.892
2022-10-15 | 7:45 | 49.888
2022-10-15 | 7:45 | 49.888
2022-10-15 | 7:45 | 49.889
2022-10-15 | 7:45 | 49.893
2022-10-15 | 7:45 | 49.895
2022-10-15 | 7:46 | 49.898
2022-10-15 | 7:46 | 49.898
2022-10-15 | 7:46 | 49.898
2022-10-15 | 7:46 | 49.899
2022-10-15 | 7:46 | 49.899
2022-10-15 | 7:46 | 49.9
2022-10-15 | 7:46 | 49.9
2022-10-15 | 7:46 | 49.902
2022-10-15 | 7:46 | 49.904
2022-10-15 | 7:46 | 49.905
2022-10-15 | 7:46 | 49.903
2022-10-15 | 7:46 | 49.901
2022-10-15 | 7:46 | 49.902
2022-10-15 | 7:46 | 49.901
2022-10-15 | 7:46 | 49.899
2022-10-15 | 7:46 | 49.899
2022-10-15 | 7:46 | 49.897
2022-10-15 | 7:46 | 49.896
2022-10-15 | 7:46 | 49.895
2022-10-15 | 7:46 | 49.893
2022-10-15 | 7:46 | 49.889
2022-10-15 | 7:46 | 49.885
2022-10-15 | 7:46 | 49.88
2022-10-15 | 7:46 | 49.881
2022-10-15 | 7:46 | 49.876
2022-10-15 | 7:46 | 49.877
2022-10-15 | 7:46 | 49.876
2022-10-15 | 7:46 | 49.874
2022-10-15 | 7:46 | 49.874
2022-10-15 | 7:46 | 49.871
2022-10-15 | 7:46 | 49.871
2022-10-15 | 7:46 | 49.868
2022-10-15 | 7:46 | 49.867
2022-10-15 | 7:46 | 49.862
2022-10-15 | 7:46 | 49.861
2022-10-15 | 7:46 | 49.854
2022-10-15 | 7:46 | 49.852
2022-10-15 | 7:46 | 49.851
2022-10-15 | 7:46 | 49.852
2022-10-15 | 7:46 | 49.855
2022-10-15 | 7:46 | 49.856
2022-10-15 | 7:46 | 49.855
2022-10-15 | 7:46 | 49.855
2022-10-15 | 7:46 | 49.853
2022-10-15 | 7:46 | 49.852
2022-10-15 | 7:46 | 49.848
2022-10-15 | 7:46 | 49.847
2022-10-15 | 7:46 | 49.843
2022-10-15 | 7:46 | 49.839
2022-10-15 | 7:46 | 49.835
2022-10-15 | 7:46 | 49.832
2022-10-15 | 7:46 | 49.83
2022-10-15 | 7:46 | 49.825
2022-10-15 | 7:46 | 49.824
2022-10-15 | 7:46 | 49.825
2022-10-15 | 7:46 | 49.825
2022-10-15 | 7:46 | 49.827
2022-10-15 | 7:46 | 49.826
2022-10-15 | 7:46 | 49.829
2022-10-15 | 7:46 | 49.83
2022-10-15 | 7:46 | 49.831
2022-10-15 | 7:47 | 49.834
2022-10-15 | 7:47 | 49.836
2022-10-15 | 7:47 | 49.836
2022-10-15 | 7:47 | 49.837
2022-10-15 | 7:47 | 49.836
2022-10-15 | 7:47 | 49.838
2022-10-15 | 7:47 | 49.837
2022-10-15 | 7:47 | 49.838
2022-10-15 | 7:47 | 49.834
2022-10-15 | 7:47 | 49.831
2022-10-15 | 7:47 | 49.827
2022-10-15 | 7:47 | 49.827
2022-10-15 | 7:47 | 49.826
2022-10-15 | 7:47 | 49.829
2022-10-15 | 7:47 | 49.829
2022-10-15 | 7:47 | 49.832
2022-10-15 | 7:47 | 49.835
2022-10-15 | 7:47 | 49.839
2022-10-15 | 7:47 | 49.841
2022-10-15 | 7:47 | 49.841
2022-10-15 | 7:47 | 49.845
2022-10-15 | 7:47 | 49.847
2022-10-15 | 7:47 | 49.847
2022-10-15 | 7:47 | 49.848
2022-10-15 | 7:47 | 49.848
2022-10-15 | 7:47 | 49.848
2022-10-15 | 7:47 | 49.845
2022-10-15 | 7:47 | 49.845
2022-10-15 | 7:47 | 49.841
2022-10-15 | 7:47 | 49.84
2022-10-15 | 7:47 | 49.836
2022-10-15 | 7:47 | 49.831
2022-10-15 | 7:47 | 49.827
2022-10-15 | 7:47 | 49.823
2022-10-15 | 7:47 | 49.817
2022-10-15 | 7:47 | 49.817
2022-10-15 | 7:47 | 49.816
2022-10-15 | 7:47 | 49.816
2022-10-15 | 7:47 | 49.814
2022-10-15 | 7:47 | 49.819
2022-10-15 | 7:47 | 49.826
2022-10-15 | 7:47 | 49.835
2022-10-15 | 7:47 | 49.839
2022-10-15 | 7:47 | 49.847
2022-10-15 | 7:47 | 49.855
2022-10-15 | 7:47 | 49.866
2022-10-15 | 7:47 | 49.871
2022-10-15 | 7:47 | 49.878
2022-10-15 | 7:47 | 49.884
2022-10-15 | 7:47 | 49.888
2022-10-15 | 7:47 | 49.889
2022-10-15 | 7:47 | 49.892
2022-10-15 | 7:47 | 49.893
2022-10-15 | 7:47 | 49.892
2022-10-15 | 7:47 | 49.888
2022-10-15 | 7:47 | 49.884
2022-10-15 | 7:47 | 49.881
2022-10-15 | 7:47 | 49.876
2022-10-15 | 7:47 | 49.875
2022-10-15 | 7:48 | 49.875
2022-10-15 | 7:48 | 49.877
2022-10-15 | 7:48 | 49.876
2022-10-15 | 7:48 | 49.876
2022-10-15 | 7:48 | 49.88
2022-10-15 | 7:48 | 49.885
2022-10-15 | 7:48 | 49.888
2022-10-15 | 7:48 | 49.887
2022-10-15 | 7:48 | 49.89
2022-10-15 | 7:48 | 49.893
2022-10-15 | 7:48 | 49.891
2022-10-15 | 7:48 | 49.89
2022-10-15 | 7:48 | 49.889
2022-10-15 | 7:48 | 49.885
2022-10-15 | 7:48 | 49.881
2022-10-15 | 7:48 | 49.883
2022-10-15 | 7:48 | 49.883
2022-10-15 | 7:48 | 49.886
2022-10-15 | 7:48 | 49.889
2022-10-15 | 7:48 | 49.889
2022-10-15 | 7:48 | 49.894
2022-10-15 | 7:48 | 49.896
2022-10-15 | 7:48 | 49.896
2022-10-15 | 7:48 | 49.894
2022-10-15 | 7:48 | 49.891
2022-10-15 | 7:48 | 49.889
2022-10-15 | 7:48 | 49.888
2022-10-15 | 7:48 | 49.887
2022-10-15 | 7:48 | 49.889
2022-10-15 | 7:48 | 49.892
2022-10-15 | 7:48 | 49.895
2022-10-15 | 7:48 | 49.901
2022-10-15 | 7:48 | 49.903
2022-10-15 | 7:48 | 49.905
2022-10-15 | 7:48 | 49.905
2022-10-15 | 7:48 | 49.908
2022-10-15 | 7:48 | 49.905
2022-10-15 | 7:48 | 49.903
2022-10-15 | 7:48 | 49.898
2022-10-15 | 7:48 | 49.894
2022-10-15 | 7:48 | 49.889
2022-10-15 | 7:48 | 49.884
2022-10-15 | 7:48 | 49.879
2022-10-15 | 7:48 | 49.879
2022-10-15 | 7:48 | 49.878
2022-10-15 | 7:48 | 49.878
2022-10-15 | 7:48 | 49.877
2022-10-15 | 7:48 | 49.877
2022-10-15 | 7:48 | 49.878
2022-10-15 | 7:48 | 49.878
2022-10-15 | 7:48 | 49.879
2022-10-15 | 7:48 | 49.88
2022-10-15 | 7:48 | 49.877
2022-10-15 | 7:48 | 49.88
2022-10-15 | 7:48 | 49.882
2022-10-15 | 7:48 | 49.885
2022-10-15 | 7:48 | 49.887
2022-10-15 | 7:48 | 49.888
2022-10-15 | 7:48 | 49.89
2022-10-15 | 7:48 | 49.892
2022-10-15 | 7:48 | 49.891
2022-10-15 | 7:49 | 49.895
2022-10-15 | 7:49 | 49.899
2022-10-15 | 7:49 | 49.903
2022-10-15 | 7:49 | 49.904
2022-10-15 | 7:49 | 49.907
2022-10-15 | 7:49 | 49.908
2022-10-15 | 7:49 | 49.912
2022-10-15 | 7:49 | 49.912
2022-10-15 | 7:49 | 49.912
2022-10-15 | 7:49 | 49.916
2022-10-15 | 7:49 | 49.918
2022-10-15 | 7:49 | 49.917
2022-10-15 | 7:49 | 49.919
2022-10-15 | 7:49 | 49.924
2022-10-15 | 7:49 | 49.925
2022-10-15 | 7:49 | 49.928
2022-10-15 | 7:49 | 49.928
2022-10-15 | 7:49 | 49.93
2022-10-15 | 7:49 | 49.931
2022-10-15 | 7:49 | 49.928
2022-10-15 | 7:49 | 49.924
2022-10-15 | 7:49 | 49.926
2022-10-15 | 7:49 | 49.921
2022-10-15 | 7:49 | 49.919
2022-10-15 | 7:49 | 49.921
2022-10-15 | 7:49 | 49.92
2022-10-15 | 7:49 | 49.922
2022-10-15 | 7:49 | 49.925
2022-10-15 | 7:49 | 49.928
2022-10-15 | 7:49 | 49.93
2022-10-15 | 7:49 | 49.932
2022-10-15 | 7:49 | 49.935
2022-10-15 | 7:49 | 49.935
2022-10-15 | 7:49 | 49.937
2022-10-15 | 7:49 | 49.937
2022-10-15 | 7:49 | 49.937
2022-10-15 | 7:49 | 49.939
2022-10-15 | 7:49 | 49.942
2022-10-15 | 7:49 | 49.947
2022-10-15 | 7:49 | 49.952
2022-10-15 | 7:49 | 49.958
2022-10-15 | 7:49 | 49.965
2022-10-15 | 7:49 | 49.968
2022-10-15 | 7:49 | 49.973
2022-10-15 | 7:49 | 49.975
2022-10-15 | 7:49 | 49.975
2022-10-15 | 7:49 | 49.977
2022-10-15 | 7:49 | 49.979
2022-10-15 | 7:49 | 49.98
2022-10-15 | 7:49 | 49.98
2022-10-15 | 7:49 | 49.978
2022-10-15 | 7:49 | 49.977
2022-10-15 | 7:49 | 49.977
2022-10-15 | 7:49 | 49.978
2022-10-15 | 7:49 | 49.978
2022-10-15 | 7:49 | 49.979
2022-10-15 | 7:49 | 49.981
2022-10-15 | 7:49 | 49.979
2022-10-15 | 7:49 | 49.979
2022-10-15 | 7:50 | 49.979
2022-10-15 | 7:50 | 49.978
2022-10-15 | 7:50 | 49.976
2022-10-15 | 7:50 | 49.976
2022-10-15 | 7:50 | 49.977
2022-10-15 | 7:50 | 49.981
2022-10-15 | 7:50 | 49.981
2022-10-15 | 7:50 | 49.981
2022-10-15 | 7:50 | 49.979
2022-10-15 | 7:50 | 49.979
2022-10-15 | 7:50 | 49.978
2022-10-15 | 7:50 | 49.98
2022-10-15 | 7:50 | 49.984
2022-10-15 | 7:50 | 49.984
2022-10-15 | 7:50 | 49.983
2022-10-15 | 7:50 | 49.984
2022-10-15 | 7:50 | 49.985
2022-10-15 | 7:50 | 49.984
2022-10-15 | 7:50 | 49.984
2022-10-15 | 7:50 | 49.986
2022-10-15 | 7:50 | 49.985
2022-10-15 | 7:50 | 49.983
2022-10-15 | 7:50 | 49.983
2022-10-15 | 7:50 | 49.986
2022-10-15 | 7:50 | 49.987
2022-10-15 | 7:50 | 49.99
2022-10-15 | 7:50 | 49.992
2022-10-15 | 7:50 | 49.992
2022-10-15 | 7:50 | 49.996
2022-10-15 | 7:50 | 49.997
2022-10-15 | 7:50 | 49.996
2022-10-15 | 7:50 | 49.995
2022-10-15 | 7:50 | 49.998
2022-10-15 | 7:50 | 49.997
2022-10-15 | 7:50 | 49.996
2022-10-15 | 7:50 | 49.996
2022-10-15 | 7:50 | 49.999
2022-10-15 | 7:50 | 50
2022-10-15 | 7:50 | 49.999
2022-10-15 | 7:50 | 50.004
2022-10-15 | 7:50 | 50.006
2022-10-15 | 7:50 | 50.005
2022-10-15 | 7:50 | 50.004
2022-10-15 | 7:50 | 50.004
2022-10-15 | 7:50 | 50.003
2022-10-15 | 7:50 | 50.001
2022-10-15 | 7:50 | 50.001
2022-10-15 | 7:50 | 50.001
2022-10-15 | 7:50 | 49.999
2022-10-15 | 7:50 | 49.997
2022-10-15 | 7:50 | 49.997
2022-10-15 | 7:50 | 49.999
2022-10-15 | 7:50 | 50.001
2022-10-15 | 7:50 | 50.001
2022-10-15 | 7:50 | 50.003
2022-10-15 | 7:50 | 50.005
2022-10-15 | 7:50 | 50.006
2022-10-15 | 7:50 | 50.012
2022-10-15 | 7:50 | 50.015
2022-10-15 | 7:50 | 50.017
2022-10-15 | 7:50 | 50.019
2022-10-15 | 7:51 | 50.018
2022-10-15 | 7:51 | 50.02
2022-10-15 | 7:51 | 50.021
2022-10-15 | 7:51 | 50.023
2022-10-15 | 7:51 | 50.023
2022-10-15 | 7:51 | 50.02
2022-10-15 | 7:51 | 50.02
2022-10-15 | 7:51 | 50.019
2022-10-15 | 7:51 | 50.021
2022-10-15 | 7:51 | 50.022
2022-10-15 | 7:51 | 50.026
2022-10-15 | 7:51 | 50.025
2022-10-15 | 7:51 | 50.023
2022-10-15 | 7:51 | 50.023
2022-10-15 | 7:51 | 50.022
2022-10-15 | 7:51 | 50.023
2022-10-15 | 7:51 | 50.021
2022-10-15 | 7:51 | 50.022
2022-10-15 | 7:51 | 50.02
2022-10-15 | 7:51 | 50.021
2022-10-15 | 7:51 | 50.023
2022-10-15 | 7:51 | 50.027
2022-10-15 | 7:51 | 50.03
2022-10-15 | 7:51 | 50.031
2022-10-15 | 7:51 | 50.032
2022-10-15 | 7:51 | 50.035
2022-10-15 | 7:51 | 50.039
2022-10-15 | 7:51 | 50.035
2022-10-15 | 7:51 | 50.037
2022-10-15 | 7:51 | 50.034
2022-10-15 | 7:51 | 50.028
2022-10-15 | 7:51 | 50.02
2022-10-15 | 7:51 | 50.016
2022-10-15 | 7:51 | 50.012
2022-10-15 | 7:51 | 50.007
2022-10-15 | 7:51 | 50.002
2022-10-15 | 7:51 | 50.004
2022-10-15 | 7:51 | 50.001
2022-10-15 | 7:51 | 50.001
2022-10-15 | 7:51 | 50
2022-10-15 | 7:51 | 50.001
2022-10-15 | 7:51 | 50
2022-10-15 | 7:51 | 50.001
2022-10-15 | 7:51 | 50.002
2022-10-15 | 7:51 | 50.006
2022-10-15 | 7:51 | 50.005
2022-10-15 | 7:51 | 50.004
2022-10-15 | 7:51 | 50.002
2022-10-15 | 7:51 | 49.999
2022-10-15 | 7:51 | 49.996
2022-10-15 | 7:51 | 49.991
2022-10-15 | 7:51 | 49.988
2022-10-15 | 7:51 | 49.988
2022-10-15 | 7:51 | 49.985
2022-10-15 | 7:51 | 49.982
2022-10-15 | 7:51 | 49.978
2022-10-15 | 7:51 | 49.977
2022-10-15 | 7:51 | 49.976
2022-10-15 | 7:51 | 49.974
2022-10-15 | 7:52 | 49.975
2022-10-15 | 7:52 | 49.978
2022-10-15 | 7:52 | 49.975
2022-10-15 | 7:52 | 49.973
2022-10-15 | 7:52 | 49.972
2022-10-15 | 7:52 | 49.973
2022-10-15 | 7:52 | 49.97
2022-10-15 | 7:52 | 49.968
2022-10-15 | 7:52 | 49.965
2022-10-15 | 7:52 | 49.964
2022-10-15 | 7:52 | 49.961
2022-10-15 | 7:52 | 49.961
2022-10-15 | 7:52 | 49.965
2022-10-15 | 7:52 | 49.967
2022-10-15 | 7:52 | 49.97
2022-10-15 | 7:52 | 49.971
2022-10-15 | 7:52 | 49.972
2022-10-15 | 7:52 | 49.974
2022-10-15 | 7:52 | 49.972
2022-10-15 | 7:52 | 49.972
2022-10-15 | 7:52 | 49.976
2022-10-15 | 7:52 | 49.978
2022-10-15 | 7:52 | 49.975
2022-10-15 | 7:52 | 49.976
2022-10-15 | 7:52 | 49.979
2022-10-15 | 7:52 | 49.98
2022-10-15 | 7:52 | 49.977
2022-10-15 | 7:52 | 49.975
2022-10-15 | 7:52 | 49.976
2022-10-15 | 7:52 | 49.974
2022-10-15 | 7:52 | 49.971

## 20221017-1
GMT
Date | Time | Freq
2022-10-17 | 21:42 | 49.991
2022-10-17 | 21:42 | 49.984
2022-10-17 | 21:42 | 49.979
2022-10-17 | 21:42 | 49.978
2022-10-17 | 21:42 | 49.976
2022-10-17 | 21:42 | 49.975
2022-10-17 | 21:42 | 49.977
2022-10-17 | 21:42 | 49.979
2022-10-17 | 21:42 | 49.979
2022-10-17 | 21:42 | 49.979
2022-10-17 | 21:42 | 49.982
2022-10-17 | 21:42 | 49.984
2022-10-17 | 21:42 | 49.988
2022-10-17 | 21:42 | 49.988
2022-10-17 | 21:42 | 49.99
2022-10-17 | 21:42 | 49.99
2022-10-17 | 21:42 | 49.99
2022-10-17 | 21:42 | 49.989
2022-10-17 | 21:42 | 49.989
2022-10-17 | 21:42 | 49.986
2022-10-17 | 21:42 | 49.987
2022-10-17 | 21:42 | 49.986
2022-10-17 | 21:42 | 49.986
2022-10-17 | 21:42 | 49.985
2022-10-17 | 21:42 | 49.984
2022-10-17 | 21:42 | 49.987
2022-10-17 | 21:42 | 49.989
2022-10-17 | 21:42 | 49.989
2022-10-17 | 21:42 | 49.991
2022-10-17 | 21:42 | 49.989
2022-10-17 | 21:42 | 49.989
2022-10-17 | 21:43 | 49.984
2022-10-17 | 21:43 | 49.981
2022-10-17 | 21:43 | 49.98
2022-10-17 | 21:43 | 49.978
2022-10-17 | 21:43 | 49.973
2022-10-17 | 21:43 | 49.971
2022-10-17 | 21:43 | 49.972
2022-10-17 | 21:43 | 49.974
2022-10-17 | 21:43 | 49.978
2022-10-17 | 21:43 | 49.984
2022-10-17 | 21:43 | 49.986
2022-10-17 | 21:43 | 49.988
2022-10-17 | 21:43 | 49.989
2022-10-17 | 21:43 | 49.988
2022-10-17 | 21:43 | 49.988
2022-10-17 | 21:43 | 49.985
2022-10-17 | 21:43 | 49.982
2022-10-17 | 21:43 | 49.98
2022-10-17 | 21:43 | 49.978
2022-10-17 | 21:43 | 49.978
2022-10-17 | 21:43 | 49.98
2022-10-17 | 21:43 | 49.98
2022-10-17 | 21:43 | 49.98
2022-10-17 | 21:43 | 49.98
2022-10-17 | 21:43 | 49.978
2022-10-17 | 21:43 | 49.978
2022-10-17 | 21:43 | 49.976
2022-10-17 | 21:43 | 49.974
2022-10-17 | 21:43 | 49.973
2022-10-17 | 21:43 | 49.972
2022-10-17 | 21:43 | 49.97
2022-10-17 | 21:43 | 49.967
2022-10-17 | 21:43 | 49.967
2022-10-17 | 21:43 | 49.968
2022-10-17 | 21:43 | 49.97
2022-10-17 | 21:43 | 49.97
2022-10-17 | 21:43 | 49.972
2022-10-17 | 21:43 | 49.973
2022-10-17 | 21:43 | 49.976
2022-10-17 | 21:43 | 49.975
2022-10-17 | 21:43 | 49.977
2022-10-17 | 21:43 | 49.978
2022-10-17 | 21:43 | 49.98
2022-10-17 | 21:43 | 49.978
2022-10-17 | 21:43 | 49.979
2022-10-17 | 21:43 | 49.981
2022-10-17 | 21:43 | 49.984
2022-10-17 | 21:43 | 49.985
2022-10-17 | 21:43 | 49.989
2022-10-17 | 21:43 | 49.991
2022-10-17 | 21:43 | 49.991
2022-10-17 | 21:43 | 49.99
2022-10-17 | 21:43 | 49.987
2022-10-17 | 21:43 | 49.987
2022-10-17 | 21:43 | 49.984
2022-10-17 | 21:43 | 49.982
2022-10-17 | 21:43 | 49.98
2022-10-17 | 21:43 | 49.995
2022-10-17 | 21:43 | 50.056
2022-10-17 | 21:43 | 50.146
2022-10-17 | 21:44 | 50.208
2022-10-17 | 21:44 | 50.248
2022-10-17 | 21:44 | 50.267
2022-10-17 | 21:44 | 50.271
2022-10-17 | 21:44 | 50.267
2022-10-17 | 21:44 | 50.255
2022-10-17 | 21:44 | 50.24
2022-10-17 | 21:44 | 50.227
2022-10-17 | 21:44 | 50.219
2022-10-17 | 21:44 | 50.213
2022-10-17 | 21:44 | 50.21
2022-10-17 | 21:44 | 50.207
2022-10-17 | 21:44 | 50.21
2022-10-17 | 21:44 | 50.213
2022-10-17 | 21:44 | 50.218
2022-10-17 | 21:44 | 50.222
2022-10-17 | 21:44 | 50.224
2022-10-17 | 21:44 | 50.23
2022-10-17 | 21:44 | 50.231
2022-10-17 | 21:44 | 50.234
2022-10-17 | 21:44 | 50.236
2022-10-17 | 21:44 | 50.239
2022-10-17 | 21:44 | 50.237
2022-10-17 | 21:44 | 50.238
2022-10-17 | 21:44 | 50.241
2022-10-17 | 21:44 | 50.242
2022-10-17 | 21:44 | 50.246
2022-10-17 | 21:44 | 50.249
2022-10-17 | 21:44 | 50.25
2022-10-17 | 21:44 | 50.252
2022-10-17 | 21:44 | 50.251
2022-10-17 | 21:44 | 50.251
2022-10-17 | 21:44 | 50.252
2022-10-17 | 21:44 | 50.251
2022-10-17 | 21:44 | 50.253
2022-10-17 | 21:44 | 50.256
2022-10-17 | 21:44 | 50.256
2022-10-17 | 21:44 | 50.259
2022-10-17 | 21:44 | 50.261
2022-10-17 | 21:44 | 50.264
2022-10-17 | 21:44 | 50.265
2022-10-17 | 21:44 | 50.267
2022-10-17 | 21:44 | 50.267
2022-10-17 | 21:44 | 50.27
2022-10-17 | 21:44 | 50.271
2022-10-17 | 21:44 | 50.269
2022-10-17 | 21:44 | 50.265
2022-10-17 | 21:44 | 50.262
2022-10-17 | 21:44 | 50.26
2022-10-17 | 21:44 | 50.257
2022-10-17 | 21:44 | 50.256
2022-10-17 | 21:44 | 50.256
2022-10-17 | 21:44 | 50.254
2022-10-17 | 21:44 | 50.252
2022-10-17 | 21:44 | 50.254
2022-10-17 | 21:44 | 50.252
2022-10-17 | 21:44 | 50.252
2022-10-17 | 21:44 | 50.251
2022-10-17 | 21:44 | 50.252
2022-10-17 | 21:45 | 50.255
2022-10-17 | 21:45 | 50.254
2022-10-17 | 21:45 | 50.256
2022-10-17 | 21:45 | 50.257
2022-10-17 | 21:45 | 50.258
2022-10-17 | 21:45 | 50.257
2022-10-17 | 21:45 | 50.256
2022-10-17 | 21:45 | 50.256
2022-10-17 | 21:45 | 50.256
2022-10-17 | 21:45 | 50.257
2022-10-17 | 21:45 | 50.256
2022-10-17 | 21:45 | 50.256
2022-10-17 | 21:45 | 50.259
2022-10-17 | 21:45 | 50.261
2022-10-17 | 21:45 | 50.264
2022-10-17 | 21:45 | 50.269
2022-10-17 | 21:45 | 50.272
2022-10-17 | 21:45 | 50.273
2022-10-17 | 21:45 | 50.273
2022-10-17 | 21:45 | 50.273
2022-10-17 | 21:45 | 50.272
2022-10-17 | 21:45 | 50.272
2022-10-17 | 21:45 | 50.274
2022-10-17 | 21:45 | 50.277
2022-10-17 | 21:45 | 50.275
2022-10-17 | 21:45 | 50.272
2022-10-17 | 21:45 | 50.27
2022-10-17 | 21:45 | 50.268
2022-10-17 | 21:45 | 50.265
2022-10-17 | 21:45 | 50.267
2022-10-17 | 21:45 | 50.267
2022-10-17 | 21:45 | 50.269
2022-10-17 | 21:45 | 50.272
2022-10-17 | 21:45 | 50.276
2022-10-17 | 21:45 | 50.276
2022-10-17 | 21:45 | 50.28
2022-10-17 | 21:45 | 50.278
2022-10-17 | 21:45 | 50.281
2022-10-17 | 21:45 | 50.282
2022-10-17 | 21:45 | 50.282
2022-10-17 | 21:45 | 50.28
2022-10-17 | 21:45 | 50.278
2022-10-17 | 21:45 | 50.276
2022-10-17 | 21:45 | 50.273
2022-10-17 | 21:45 | 50.271
2022-10-17 | 21:45 | 50.275
2022-10-17 | 21:45 | 50.274
2022-10-17 | 21:45 | 50.276
2022-10-17 | 21:45 | 50.279
2022-10-17 | 21:45 | 50.278
2022-10-17 | 21:45 | 50.28
2022-10-17 | 21:45 | 50.281
2022-10-17 | 21:45 | 50.282
2022-10-17 | 21:45 | 50.282
2022-10-17 | 21:45 | 50.282
2022-10-17 | 21:45 | 50.284
2022-10-17 | 21:45 | 50.287
2022-10-17 | 21:45 | 50.289
2022-10-17 | 21:45 | 50.289
2022-10-17 | 21:45 | 50.288
2022-10-17 | 21:45 | 50.29
2022-10-17 | 21:46 | 50.291
2022-10-17 | 21:46 | 50.291
2022-10-17 | 21:46 | 50.291
2022-10-17 | 21:46 | 50.293
2022-10-17 | 21:46 | 50.29
2022-10-17 | 21:46 | 50.293
2022-10-17 | 21:46 | 50.292
2022-10-17 | 21:46 | 50.293
2022-10-17 | 21:46 | 50.296
2022-10-17 | 21:46 | 50.297
2022-10-17 | 21:46 | 50.298
2022-10-17 | 21:46 | 50.298
2022-10-17 | 21:46 | 50.297
2022-10-17 | 21:46 | 50.295
2022-10-17 | 21:46 | 50.296
2022-10-17 | 21:46 | 50.296
2022-10-17 | 21:46 | 50.293
2022-10-17 | 21:46 | 50.293
2022-10-17 | 21:46 | 50.291
2022-10-17 | 21:46 | 50.291
2022-10-17 | 21:46 | 50.291
2022-10-17 | 21:46 | 50.287
2022-10-17 | 21:46 | 50.287
2022-10-17 | 21:46 | 50.288
2022-10-17 | 21:46 | 50.289
2022-10-17 | 21:46 | 50.292
2022-10-17 | 21:46 | 50.293
2022-10-17 | 21:46 | 50.296
2022-10-17 | 21:46 | 50.295
2022-10-17 | 21:46 | 50.298
2022-10-17 | 21:46 | 50.299
2022-10-17 | 21:46 | 50.303
2022-10-17 | 21:46 | 50.302
2022-10-17 | 21:46 | 50.303
2022-10-17 | 21:46 | 50.3
2022-10-17 | 21:46 | 50.3
2022-10-17 | 21:46 | 50.3
2022-10-17 | 21:46 | 50.3
2022-10-17 | 21:46 | 50.3
2022-10-17 | 21:46 | 50.297
2022-10-17 | 21:46 | 50.291
2022-10-17 | 21:46 | 50.287
2022-10-17 | 21:46 | 50.283
2022-10-17 | 21:46 | 50.282
2022-10-17 | 21:46 | 50.277
2022-10-17 | 21:46 | 50.273
2022-10-17 | 21:46 | 50.272
2022-10-17 | 21:46 | 50.273
2022-10-17 | 21:46 | 50.272
2022-10-17 | 21:46 | 50.269
2022-10-17 | 21:46 | 50.267
2022-10-17 | 21:46 | 50.268
2022-10-17 | 21:46 | 50.266
2022-10-17 | 21:46 | 50.264
2022-10-17 | 21:46 | 50.264
2022-10-17 | 21:46 | 50.266
2022-10-17 | 21:46 | 50.267
2022-10-17 | 21:46 | 50.266
2022-10-17 | 21:46 | 50.268
2022-10-17 | 21:47 | 50.271
2022-10-17 | 21:47 | 50.274
2022-10-17 | 21:47 | 50.272
2022-10-17 | 21:47 | 50.272
2022-10-17 | 21:47 | 50.271
2022-10-17 | 21:47 | 50.27
2022-10-17 | 21:47 | 50.267
2022-10-17 | 21:47 | 50.265
2022-10-17 | 21:47 | 50.263
2022-10-17 | 21:47 | 50.26
2022-10-17 | 21:47 | 50.256
2022-10-17 | 21:47 | 50.252
2022-10-17 | 21:47 | 50.249
2022-10-17 | 21:47 | 50.248
2022-10-17 | 21:47 | 50.246
2022-10-17 | 21:47 | 50.246
2022-10-17 | 21:47 | 50.243
2022-10-17 | 21:47 | 50.243
2022-10-17 | 21:47 | 50.241
2022-10-17 | 21:47 | 50.244
2022-10-17 | 21:47 | 50.244
2022-10-17 | 21:47 | 50.245
2022-10-17 | 21:47 | 50.247
2022-10-17 | 21:47 | 50.248
2022-10-17 | 21:47 | 50.248
2022-10-17 | 21:47 | 50.25
2022-10-17 | 21:47 | 50.25
2022-10-17 | 21:47 | 50.25
2022-10-17 | 21:47 | 50.25
2022-10-17 | 21:47 | 50.249
2022-10-17 | 21:47 | 50.248
2022-10-17 | 21:47 | 50.246
2022-10-17 | 21:47 | 50.243
2022-10-17 | 21:47 | 50.243
2022-10-17 | 21:47 | 50.242
2022-10-17 | 21:47 | 50.24
2022-10-17 | 21:47 | 50.234
2022-10-17 | 21:47 | 50.231
2022-10-17 | 21:47 | 50.227
2022-10-17 | 21:47 | 50.226
2022-10-17 | 21:47 | 50.227
2022-10-17 | 21:47 | 50.228
2022-10-17 | 21:47 | 50.229
2022-10-17 | 21:47 | 50.228
2022-10-17 | 21:47 | 50.229
2022-10-17 | 21:47 | 50.229
2022-10-17 | 21:47 | 50.229
2022-10-17 | 21:47 | 50.229
2022-10-17 | 21:47 | 50.227
2022-10-17 | 21:47 | 50.225
2022-10-17 | 21:47 | 50.225
2022-10-17 | 21:47 | 50.223
2022-10-17 | 21:47 | 50.223
2022-10-17 | 21:47 | 50.228
2022-10-17 | 21:47 | 50.231
2022-10-17 | 21:47 | 50.236
2022-10-17 | 21:47 | 50.236
2022-10-17 | 21:47 | 50.235
2022-10-17 | 21:47 | 50.236
2022-10-17 | 21:47 | 50.236
2022-10-17 | 21:48 | 50.236
2022-10-17 | 21:48 | 50.238
2022-10-17 | 21:48 | 50.237
2022-10-17 | 21:48 | 50.237
2022-10-17 | 21:48 | 50.235
2022-10-17 | 21:48 | 50.234
2022-10-17 | 21:48 | 50.236
2022-10-17 | 21:48 | 50.235
2022-10-17 | 21:48 | 50.235
2022-10-17 | 21:48 | 50.236
2022-10-17 | 21:48 | 50.236
2022-10-17 | 21:48 | 50.237
2022-10-17 | 21:48 | 50.234
2022-10-17 | 21:48 | 50.235
2022-10-17 | 21:48 | 50.231
2022-10-17 | 21:48 | 50.23
2022-10-17 | 21:48 | 50.226
2022-10-17 | 21:48 | 50.224
2022-10-17 | 21:48 | 50.223
2022-10-17 | 21:48 | 50.218
2022-10-17 | 21:48 | 50.217
2022-10-17 | 21:48 | 50.215
2022-10-17 | 21:48 | 50.214
2022-10-17 | 21:48 | 50.215
2022-10-17 | 21:48 | 50.215
2022-10-17 | 21:48 | 50.215
2022-10-17 | 21:48 | 50.215
2022-10-17 | 21:48 | 50.211
2022-10-17 | 21:48 | 50.21
2022-10-17 | 21:48 | 50.209
2022-10-17 | 21:48 | 50.211
2022-10-17 | 21:48 | 50.213
2022-10-17 | 21:48 | 50.217
2022-10-17 | 21:48 | 50.218
2022-10-17 | 21:48 | 50.221
2022-10-17 | 21:48 | 50.226
2022-10-17 | 21:48 | 50.231
2022-10-17 | 21:48 | 50.234
2022-10-17 | 21:48 | 50.235
2022-10-17 | 21:48 | 50.238
2022-10-17 | 21:48 | 50.238
2022-10-17 | 21:48 | 50.236
2022-10-17 | 21:48 | 50.232
2022-10-17 | 21:48 | 50.23
2022-10-17 | 21:48 | 50.223
2022-10-17 | 21:48 | 50.218
2022-10-17 | 21:48 | 50.214
2022-10-17 | 21:48 | 50.209
2022-10-17 | 21:48 | 50.205
2022-10-17 | 21:48 | 50.205
2022-10-17 | 21:48 | 50.207
2022-10-17 | 21:48 | 50.206
2022-10-17 | 21:48 | 50.206
2022-10-17 | 21:48 | 50.204
2022-10-17 | 21:48 | 50.206
2022-10-17 | 21:48 | 50.208
2022-10-17 | 21:48 | 50.208
2022-10-17 | 21:48 | 50.209
2022-10-17 | 21:48 | 50.211
2022-10-17 | 21:48 | 50.213
2022-10-17 | 21:49 | 50.213
2022-10-17 | 21:49 | 50.214
2022-10-17 | 21:49 | 50.212
2022-10-17 | 21:49 | 50.21
2022-10-17 | 21:49 | 50.211
2022-10-17 | 21:49 | 50.213
2022-10-17 | 21:49 | 50.213
2022-10-17 | 21:49 | 50.211
2022-10-17 | 21:49 | 50.212
2022-10-17 | 21:49 | 50.211
2022-10-17 | 21:49 | 50.211
2022-10-17 | 21:49 | 50.212
2022-10-17 | 21:49 | 50.213
2022-10-17 | 21:49 | 50.209
2022-10-17 | 21:49 | 50.21
2022-10-17 | 21:49 | 50.21
2022-10-17 | 21:49 | 50.208
2022-10-17 | 21:49 | 50.207
2022-10-17 | 21:49 | 50.206
2022-10-17 | 21:49 | 50.205
2022-10-17 | 21:49 | 50.205
2022-10-17 | 21:49 | 50.204
2022-10-17 | 21:49 | 50.202
2022-10-17 | 21:49 | 50.202
2022-10-17 | 21:49 | 50.2
2022-10-17 | 21:49 | 50.193
2022-10-17 | 21:49 | 50.192
2022-10-17 | 21:49 | 50.189
2022-10-17 | 21:49 | 50.184
2022-10-17 | 21:49 | 50.182
2022-10-17 | 21:49 | 50.179
2022-10-17 | 21:49 | 50.175
2022-10-17 | 21:49 | 50.173
2022-10-17 | 21:49 | 50.17
2022-10-17 | 21:49 | 50.168
2022-10-17 | 21:49 | 50.167
2022-10-17 | 21:49 | 50.165
2022-10-17 | 21:49 | 50.165
2022-10-17 | 21:49 | 50.163
2022-10-17 | 21:49 | 50.161
2022-10-17 | 21:49 | 50.159
2022-10-17 | 21:49 | 50.158
2022-10-17 | 21:49 | 50.16
2022-10-17 | 21:49 | 50.16
2022-10-17 | 21:49 | 50.161
2022-10-17 | 21:49 | 50.16
2022-10-17 | 21:49 | 50.161
2022-10-17 | 21:49 | 50.16
2022-10-17 | 21:49 | 50.158
2022-10-17 | 21:49 | 50.154
2022-10-17 | 21:49 | 50.152
2022-10-17 | 21:49 | 50.145
2022-10-17 | 21:49 | 50.138
2022-10-17 | 21:49 | 50.135
2022-10-17 | 21:49 | 50.134
2022-10-17 | 21:49 | 50.132
2022-10-17 | 21:49 | 50.128
2022-10-17 | 21:49 | 50.123
2022-10-17 | 21:49 | 50.121
2022-10-17 | 21:49 | 50.122
2022-10-17 | 21:50 | 50.124
2022-10-17 | 21:50 | 50.125
2022-10-17 | 21:50 | 50.127
2022-10-17 | 21:50 | 50.128
2022-10-17 | 21:50 | 50.129
2022-10-17 | 21:50 | 50.131
2022-10-17 | 21:50 | 50.136
2022-10-17 | 21:50 | 50.141
2022-10-17 | 21:50 | 50.145
2022-10-17 | 21:50 | 50.147
2022-10-17 | 21:50 | 50.149
2022-10-17 | 21:50 | 50.148
2022-10-17 | 21:50 | 50.145
2022-10-17 | 21:50 | 50.146
2022-10-17 | 21:50 | 50.143
2022-10-17 | 21:50 | 50.142
2022-10-17 | 21:50 | 50.142
2022-10-17 | 21:50 | 50.142
2022-10-17 | 21:50 | 50.142
2022-10-17 | 21:50 | 50.142
2022-10-17 | 21:50 | 50.141
2022-10-17 | 21:50 | 50.139
2022-10-17 | 21:50 | 50.139
2022-10-17 | 21:50 | 50.135
2022-10-17 | 21:50 | 50.139
2022-10-17 | 21:50 | 50.145
2022-10-17 | 21:50 | 50.153
2022-10-17 | 21:50 | 50.154
2022-10-17 | 21:50 | 50.155
2022-10-17 | 21:50 | 50.159
2022-10-17 | 21:50 | 50.166
2022-10-17 | 21:50 | 50.167
2022-10-17 | 21:50 | 50.164
2022-10-17 | 21:50 | 50.169
2022-10-17 | 21:50 | 50.17
2022-10-17 | 21:50 | 50.17
2022-10-17 | 21:50 | 50.169
2022-10-17 | 21:50 | 50.167
2022-10-17 | 21:50 | 50.165
2022-10-17 | 21:50 | 50.163
2022-10-17 | 21:50 | 50.161
2022-10-17 | 21:50 | 50.159
2022-10-17 | 21:50 | 50.155
2022-10-17 | 21:50 | 50.152
2022-10-17 | 21:50 | 50.149
2022-10-17 | 21:50 | 50.144
2022-10-17 | 21:50 | 50.138
2022-10-17 | 21:50 | 50.134
2022-10-17 | 21:50 | 50.135
2022-10-17 | 21:50 | 50.138
2022-10-17 | 21:50 | 50.139
2022-10-17 | 21:50 | 50.139
2022-10-17 | 21:50 | 50.14
2022-10-17 | 21:50 | 50.141
2022-10-17 | 21:50 | 50.141
2022-10-17 | 21:50 | 50.138
2022-10-17 | 21:50 | 50.135
2022-10-17 | 21:50 | 50.133
2022-10-17 | 21:50 | 50.132
2022-10-17 | 21:50 | 50.134
2022-10-17 | 21:50 | 50.135
2022-10-17 | 21:51 | 50.135
2022-10-17 | 21:51 | 50.135
2022-10-17 | 21:51 | 50.137
2022-10-17 | 21:51 | 50.141
2022-10-17 | 21:51 | 50.147
2022-10-17 | 21:51 | 50.151
2022-10-17 | 21:51 | 50.156
2022-10-17 | 21:51 | 50.16
2022-10-17 | 21:51 | 50.164
2022-10-17 | 21:51 | 50.164
2022-10-17 | 21:51 | 50.167
2022-10-17 | 21:51 | 50.167
2022-10-17 | 21:51 | 50.17
2022-10-17 | 21:51 | 50.171
2022-10-17 | 21:51 | 50.172
2022-10-17 | 21:51 | 50.172
2022-10-17 | 21:51 | 50.17
2022-10-17 | 21:51 | 50.17
2022-10-17 | 21:51 | 50.171
2022-10-17 | 21:51 | 50.169
2022-10-17 | 21:51 | 50.167
2022-10-17 | 21:51 | 50.165
2022-10-17 | 21:51 | 50.164
2022-10-17 | 21:51 | 50.163
2022-10-17 | 21:51 | 50.161
2022-10-17 | 21:51 | 50.161
2022-10-17 | 21:51 | 50.164
2022-10-17 | 21:51 | 50.166
2022-10-17 | 21:51 | 50.166
2022-10-17 | 21:51 | 50.164
2022-10-17 | 21:51 | 50.164
2022-10-17 | 21:51 | 50.165
2022-10-17 | 21:51 | 50.166
2022-10-17 | 21:51 | 50.168
2022-10-17 | 21:51 | 50.168
2022-10-17 | 21:51 | 50.167
2022-10-17 | 21:51 | 50.168
2022-10-17 | 21:51 | 50.168
2022-10-17 | 21:51 | 50.169
2022-10-17 | 21:51 | 50.17
2022-10-17 | 21:51 | 50.169
2022-10-17 | 21:51 | 50.168
2022-10-17 | 21:51 | 50.165
2022-10-17 | 21:51 | 50.16
2022-10-17 | 21:51 | 50.157
2022-10-17 | 21:51 | 50.156
2022-10-17 | 21:51 | 50.155
2022-10-17 | 21:51 | 50.152
2022-10-17 | 21:51 | 50.15
2022-10-17 | 21:51 | 50.152
2022-10-17 | 21:51 | 50.154
2022-10-17 | 21:51 | 50.154
2022-10-17 | 21:51 | 50.154
2022-10-17 | 21:51 | 50.157
2022-10-17 | 21:51 | 50.16
2022-10-17 | 21:51 | 50.164
2022-10-17 | 21:51 | 50.167
2022-10-17 | 21:51 | 50.17
2022-10-17 | 21:51 | 50.173
2022-10-17 | 21:52 | 50.175
2022-10-17 | 21:52 | 50.176
2022-10-17 | 21:52 | 50.174
2022-10-17 | 21:52 | 50.175
2022-10-17 | 21:52 | 50.173
2022-10-17 | 21:52 | 50.173
2022-10-17 | 21:52 | 50.172
2022-10-17 | 21:52 | 50.168
2022-10-17 | 21:52 | 50.164
2022-10-17 | 21:52 | 50.162
2022-10-17 | 21:52 | 50.162
2022-10-17 | 21:52 | 50.157
2022-10-17 | 21:52 | 50.153
2022-10-17 | 21:52 | 50.149
2022-10-17 | 21:52 | 50.147
2022-10-17 | 21:52 | 50.144
2022-10-17 | 21:52 | 50.14
2022-10-17 | 21:52 | 50.14
2022-10-17 | 21:52 | 50.139
2022-10-17 | 21:52 | 50.137
2022-10-17 | 21:52 | 50.135
2022-10-17 | 21:52 | 50.133
2022-10-17 | 21:52 | 50.132
2022-10-17 | 21:52 | 50.128
2022-10-17 | 21:52 | 50.125
2022-10-17 | 21:52 | 50.126
2022-10-17 | 21:52 | 50.127
2022-10-17 | 21:52 | 50.127
2022-10-17 | 21:52 | 50.126
2022-10-17 | 21:52 | 50.127
2022-10-17 | 21:52 | 50.129
2022-10-17 | 21:52 | 50.13
2022-10-17 | 21:52 | 50.13
2022-10-17 | 21:52 | 50.134
2022-10-17 | 21:52 | 50.138
2022-10-17 | 21:52 | 50.141
2022-10-17 | 21:52 | 50.142
2022-10-17 | 21:52 | 50.143
2022-10-17 | 21:52 | 50.145
2022-10-17 | 21:52 | 50.146
2022-10-17 | 21:52 | 50.145
2022-10-17 | 21:52 | 50.144
2022-10-17 | 21:52 | 50.147
2022-10-17 | 21:52 | 50.15
2022-10-17 | 21:52 | 50.152
2022-10-17 | 21:52 | 50.156
2022-10-17 | 21:52 | 50.156
2022-10-17 | 21:52 | 50.155
2022-10-17 | 21:52 | 50.155
2022-10-17 | 21:52 | 50.156
2022-10-17 | 21:52 | 50.157
2022-10-17 | 21:52 | 50.154
2022-10-17 | 21:52 | 50.154
2022-10-17 | 21:52 | 50.153
2022-10-17 | 21:52 | 50.151
2022-10-17 | 21:52 | 50.147
2022-10-17 | 21:52 | 50.148
2022-10-17 | 21:52 | 50.149
2022-10-17 | 21:52 | 50.148
2022-10-17 | 21:52 | 50.15
2022-10-17 | 21:52 | 50.154
2022-10-17 | 21:53 | 50.156
2022-10-17 | 21:53 | 50.163
2022-10-17 | 21:53 | 50.171
2022-10-17 | 21:53 | 50.181
2022-10-17 | 21:53 | 50.186
2022-10-17 | 21:53 | 50.188
2022-10-17 | 21:53 | 50.186
2022-10-17 | 21:53 | 50.188
2022-10-17 | 21:53 | 50.189
2022-10-17 | 21:53 | 50.186
2022-10-17 | 21:53 | 50.185
2022-10-17 | 21:53 | 50.184
2022-10-17 | 21:53 | 50.183
2022-10-17 | 21:53 | 50.178
2022-10-17 | 21:53 | 50.176
2022-10-17 | 21:53 | 50.174
2022-10-17 | 21:53 | 50.169
2022-10-17 | 21:53 | 50.166
2022-10-17 | 21:53 | 50.164
2022-10-17 | 21:53 | 50.16
2022-10-17 | 21:53 | 50.156
2022-10-17 | 21:53 | 50.152
2022-10-17 | 21:53 | 50.149
2022-10-17 | 21:53 | 50.148
2022-10-17 | 21:53 | 50.147
2022-10-17 | 21:53 | 50.144
2022-10-17 | 21:53 | 50.146
2022-10-17 | 21:53 | 50.149
2022-10-17 | 21:53 | 50.151
2022-10-17 | 21:53 | 50.15
2022-10-17 | 21:53 | 50.151
2022-10-17 | 21:53 | 50.152
2022-10-17 | 21:53 | 50.15
2022-10-17 | 21:53 | 50.149
2022-10-17 | 21:53 | 50.15
2022-10-17 | 21:53 | 50.144
2022-10-17 | 21:53 | 50.141
2022-10-17 | 21:53 | 50.139
2022-10-17 | 21:53 | 50.139
2022-10-17 | 21:53 | 50.139
2022-10-17 | 21:53 | 50.141
2022-10-17 | 21:53 | 50.144
2022-10-17 | 21:53 | 50.147
2022-10-17 | 21:53 | 50.148
2022-10-17 | 21:53 | 50.149
2022-10-17 | 21:53 | 50.152
2022-10-17 | 21:53 | 50.155
2022-10-17 | 21:53 | 50.154
2022-10-17 | 21:53 | 50.15
2022-10-17 | 21:53 | 50.147
2022-10-17 | 21:53 | 50.144
2022-10-17 | 21:53 | 50.144
2022-10-17 | 21:53 | 50.142
2022-10-17 | 21:53 | 50.141
2022-10-17 | 21:53 | 50.139
2022-10-17 | 21:53 | 50.135
2022-10-17 | 21:53 | 50.132
2022-10-17 | 21:53 | 50.131
2022-10-17 | 21:53 | 50.128
2022-10-17 | 21:54 | 50.125
2022-10-17 | 21:54 | 50.125
2022-10-17 | 21:54 | 50.127
2022-10-17 | 21:54 | 50.131
2022-10-17 | 21:54 | 50.134
2022-10-17 | 21:54 | 50.136
2022-10-17 | 21:54 | 50.138
2022-10-17 | 21:54 | 50.14
2022-10-17 | 21:54 | 50.143
2022-10-17 | 21:54 | 50.146
2022-10-17 | 21:54 | 50.15
2022-10-17 | 21:54 | 50.149
2022-10-17 | 21:54 | 50.148
2022-10-17 | 21:54 | 50.148
2022-10-17 | 21:54 | 50.146
2022-10-17 | 21:54 | 50.143
2022-10-17 | 21:54 | 50.141
2022-10-17 | 21:54 | 50.138
2022-10-17 | 21:54 | 50.136
2022-10-17 | 21:54 | 50.134
2022-10-17 | 21:54 | 50.131
2022-10-17 | 21:54 | 50.129
2022-10-17 | 21:54 | 50.127
2022-10-17 | 21:54 | 50.125
2022-10-17 | 21:54 | 50.123
2022-10-17 | 21:54 | 50.123
2022-10-17 | 21:54 | 50.125
2022-10-17 | 21:54 | 50.128
2022-10-17 | 21:54 | 50.129
2022-10-17 | 21:54 | 50.131
2022-10-17 | 21:54 | 50.13
2022-10-17 | 21:54 | 50.128
2022-10-17 | 21:54 | 50.127
2022-10-17 | 21:54 | 50.125
2022-10-17 | 21:54 | 50.122
2022-10-17 | 21:54 | 50.119
2022-10-17 | 21:54 | 50.116
2022-10-17 | 21:54 | 50.116
2022-10-17 | 21:54 | 50.114
2022-10-17 | 21:54 | 50.111
2022-10-17 | 21:54 | 50.107
2022-10-17 | 21:54 | 50.105
2022-10-17 | 21:54 | 50.099
2022-10-17 | 21:54 | 50.094
2022-10-17 | 21:54 | 50.093
2022-10-17 | 21:54 | 50.092
2022-10-17 | 21:54 | 50.089
2022-10-17 | 21:54 | 50.083
2022-10-17 | 21:54 | 50.075
2022-10-17 | 21:54 | 50.071
2022-10-17 | 21:54 | 50.063
2022-10-17 | 21:54 | 50.059
2022-10-17 | 21:54 | 50.057
2022-10-17 | 21:54 | 50.056
2022-10-17 | 21:54 | 50.056
2022-10-17 | 21:54 | 50.053
2022-10-17 | 21:54 | 50.052
2022-10-17 | 21:54 | 50.052
2022-10-17 | 21:54 | 50.052
2022-10-17 | 21:54 | 50.051
2022-10-17 | 21:54 | 50.053
2022-10-17 | 21:55 | 50.055
2022-10-17 | 21:55 | 50.053
2022-10-17 | 21:55 | 50.053
2022-10-17 | 21:55 | 50.053
2022-10-17 | 21:55 | 50.05
2022-10-17 | 21:55 | 50.049
2022-10-17 | 21:55 | 50.047
2022-10-17 | 21:55 | 50.046
2022-10-17 | 21:55 | 50.049
2022-10-17 | 21:55 | 50.049
2022-10-17 | 21:55 | 50.053
2022-10-17 | 21:55 | 50.053
2022-10-17 | 21:55 | 50.055
2022-10-17 | 21:55 | 50.056
2022-10-17 | 21:55 | 50.057
2022-10-17 | 21:55 | 50.058
2022-10-17 | 21:55 | 50.057
2022-10-17 | 21:55 | 50.055
2022-10-17 | 21:55 | 50.054
2022-10-17 | 21:55 | 50.054
2022-10-17 | 21:55 | 50.055
2022-10-17 | 21:55 | 50.056
2022-10-17 | 21:55 | 50.058
2022-10-17 | 21:55 | 50.059
2022-10-17 | 21:55 | 50.058
2022-10-17 | 21:55 | 50.059
2022-10-17 | 21:55 | 50.061
2022-10-17 | 21:55 | 50.062
2022-10-17 | 21:55 | 50.062
2022-10-17 | 21:55 | 50.062
2022-10-17 | 21:55 | 50.059
2022-10-17 | 21:55 | 50.055
2022-10-17 | 21:55 | 50.05
2022-10-17 | 21:55 | 50.05
2022-10-17 | 21:55 | 50.05
2022-10-17 | 21:55 | 50.049
2022-10-17 | 21:55 | 50.049
2022-10-17 | 21:55 | 50.047
2022-10-17 | 21:55 | 50.047
2022-10-17 | 21:55 | 50.048
2022-10-17 | 21:55 | 50.049
2022-10-17 | 21:55 | 50.049
2022-10-17 | 21:55 | 50.051
2022-10-17 | 21:55 | 50.048
2022-10-17 | 21:55 | 50.046
2022-10-17 | 21:55 | 50.048
2022-10-17 | 21:55 | 50.054
2022-10-17 | 21:55 | 50.058
2022-10-17 | 21:55 | 50.061
2022-10-17 | 21:55 | 50.063
2022-10-17 | 21:55 | 50.063
2022-10-17 | 21:55 | 50.064
2022-10-17 | 21:55 | 50.064
2022-10-17 | 21:55 | 50.063
2022-10-17 | 21:55 | 50.061
2022-10-17 | 21:55 | 50.058
2022-10-17 | 21:55 | 50.054
2022-10-17 | 21:55 | 50.051
2022-10-17 | 21:55 | 50.049
2022-10-17 | 21:56 | 50.047
2022-10-17 | 21:56 | 50.044
2022-10-17 | 21:56 | 50.046
2022-10-17 | 21:56 | 50.049
2022-10-17 | 21:56 | 50.05
2022-10-17 | 21:56 | 50.054
2022-10-17 | 21:56 | 50.058
2022-10-17 | 21:56 | 50.06
2022-10-17 | 21:56 | 50.063
2022-10-17 | 21:56 | 50.065
2022-10-17 | 21:56 | 50.066
2022-10-17 | 21:56 | 50.064
2022-10-17 | 21:56 | 50.064
2022-10-17 | 21:56 | 50.066
2022-10-17 | 21:56 | 50.069
2022-10-17 | 21:56 | 50.071
2022-10-17 | 21:56 | 50.071
2022-10-17 | 21:56 | 50.069
2022-10-17 | 21:56 | 50.067
2022-10-17 | 21:56 | 50.067
2022-10-17 | 21:56 | 50.065
2022-10-17 | 21:56 | 50.064
2022-10-17 | 21:56 | 50.062
2022-10-17 | 21:56 | 50.061
2022-10-17 | 21:56 | 50.058
2022-10-17 | 21:56 | 50.054
2022-10-17 | 21:56 | 50.052
2022-10-17 | 21:56 | 50.048
2022-10-17 | 21:56 | 50.048
2022-10-17 | 21:56 | 50.049
2022-10-17 | 21:56 | 50.05
2022-10-17 | 21:56 | 50.05
2022-10-17 | 21:56 | 50.049
2022-10-17 | 21:56 | 50.051
2022-10-17 | 21:56 | 50.051
2022-10-17 | 21:56 | 50.051
2022-10-17 | 21:56 | 50.05
2022-10-17 | 21:56 | 50.051
2022-10-17 | 21:56 | 50.052
2022-10-17 | 21:56 | 50.051
2022-10-17 | 21:56 | 50.053
2022-10-17 | 21:56 | 50.053
2022-10-17 | 21:56 | 50.052
2022-10-17 | 21:56 | 50.051
2022-10-17 | 21:56 | 50.052
2022-10-17 | 21:56 | 50.054
2022-10-17 | 21:56 | 50.055
2022-10-17 | 21:56 | 50.056
2022-10-17 | 21:56 | 50.057
2022-10-17 | 21:56 | 50.06
2022-10-17 | 21:56 | 50.065
2022-10-17 | 21:56 | 50.064
2022-10-17 | 21:56 | 50.064
2022-10-17 | 21:56 | 50.062
2022-10-17 | 21:56 | 50.061
2022-10-17 | 21:56 | 50.059
2022-10-17 | 21:56 | 50.058
2022-10-17 | 21:56 | 50.059
2022-10-17 | 21:56 | 50.056
2022-10-17 | 21:56 | 50.058
2022-10-17 | 21:56 | 50.059
2022-10-17 | 21:57 | 50.059
2022-10-17 | 21:57 | 50.061
2022-10-17 | 21:57 | 50.062
2022-10-17 | 21:57 | 50.065
2022-10-17 | 21:57 | 50.069
2022-10-17 | 21:57 | 50.07
2022-10-17 | 21:57 | 50.069
2022-10-17 | 21:57 | 50.069
2022-10-17 | 21:57 | 50.07
2022-10-17 | 21:57 | 50.065
2022-10-17 | 21:57 | 50.065
2022-10-17 | 21:57 | 50.062
2022-10-17 | 21:57 | 50.061
2022-10-17 | 21:57 | 50.061
2022-10-17 | 21:57 | 50.063
2022-10-17 | 21:57 | 50.066
2022-10-17 | 21:57 | 50.069
2022-10-17 | 21:57 | 50.071
2022-10-17 | 21:57 | 50.072
2022-10-17 | 21:57 | 50.072
2022-10-17 | 21:57 | 50.069
2022-10-17 | 21:57 | 50.067
2022-10-17 | 21:57 | 50.066
2022-10-17 | 21:57 | 50.068
2022-10-17 | 21:57 | 50.065
2022-10-17 | 21:57 | 50.062
2022-10-17 | 21:57 | 50.061
2022-10-17 | 21:57 | 50.061
2022-10-17 | 21:57 | 50.06
2022-10-17 | 21:57 | 50.061
2022-10-17 | 21:57 | 50.062
2022-10-17 | 21:57 | 50.063
2022-10-17 | 21:57 | 50.062
2022-10-17 | 21:57 | 50.062
2022-10-17 | 21:57 | 50.059
2022-10-17 | 21:57 | 50.057
2022-10-17 | 21:57 | 50.053
2022-10-17 | 21:57 | 50.051
2022-10-17 | 21:57 | 50.049
2022-10-17 | 21:57 | 50.051
2022-10-17 | 21:57 | 50.052
2022-10-17 | 21:57 | 50.051
2022-10-17 | 21:57 | 50.052
2022-10-17 | 21:57 | 50.053
2022-10-17 | 21:57 | 50.054
2022-10-17 | 21:57 | 50.056
2022-10-17 | 21:57 | 50.058
2022-10-17 | 21:57 | 50.062
2022-10-17 | 21:57 | 50.062
2022-10-17 | 21:57 | 50.064
2022-10-17 | 21:57 | 50.065
2022-10-17 | 21:57 | 50.064
2022-10-17 | 21:57 | 50.062
2022-10-17 | 21:57 | 50.063
2022-10-17 | 21:57 | 50.061
2022-10-17 | 21:57 | 50.058
2022-10-17 | 21:57 | 50.054
2022-10-17 | 21:57 | 50.052
2022-10-17 | 21:57 | 50.05
2022-10-17 | 21:58 | 50.045
2022-10-17 | 21:58 | 50.046
2022-10-17 | 21:58 | 50.047
2022-10-17 | 21:58 | 50.047
2022-10-17 | 21:58 | 50.044
2022-10-17 | 21:58 | 50.041
2022-10-17 | 21:58 | 50.04
2022-10-17 | 21:58 | 50.039
2022-10-17 | 21:58 | 50.042
2022-10-17 | 21:58 | 50.044
2022-10-17 | 21:58 | 50.05
2022-10-17 | 21:58 | 50.052
2022-10-17 | 21:58 | 50.053
2022-10-17 | 21:58 | 50.056
2022-10-17 | 21:58 | 50.057
2022-10-17 | 21:58 | 50.055
2022-10-17 | 21:58 | 50.054
2022-10-17 | 21:58 | 50.052
2022-10-17 | 21:58 | 50.052
2022-10-17 | 21:58 | 50.049
2022-10-17 | 21:58 | 50.046
2022-10-17 | 21:58 | 50.044
2022-10-17 | 21:58 | 50.048
2022-10-17 | 21:58 | 50.045
2022-10-17 | 21:58 | 50.043
2022-10-17 | 21:58 | 50.042
2022-10-17 | 21:58 | 50.038
2022-10-17 | 21:58 | 50.037
2022-10-17 | 21:58 | 50.035
2022-10-17 | 21:58 | 50.035
2022-10-17 | 21:58 | 50.033
2022-10-17 | 21:58 | 50.032
2022-10-17 | 21:58 | 50.033
2022-10-17 | 21:58 | 50.035
2022-10-17 | 21:58 | 50.037
2022-10-17 | 21:58 | 50.041
2022-10-17 | 21:58 | 50.043
2022-10-17 | 21:58 | 50.045
2022-10-17 | 21:58 | 50.046
2022-10-17 | 21:58 | 50.044
2022-10-17 | 21:58 | 50.04
2022-10-17 | 21:58 | 50.035
2022-10-17 | 21:58 | 50.032
2022-10-17 | 21:58 | 50.027
2022-10-17 | 21:58 | 50.024
2022-10-17 | 21:58 | 50.021
2022-10-17 | 21:58 | 50.019
2022-10-17 | 21:58 | 50.015
2022-10-17 | 21:58 | 50.014
2022-10-17 | 21:58 | 50.013
2022-10-17 | 21:58 | 50.012
2022-10-17 | 21:58 | 50.012
2022-10-17 | 21:58 | 50.012
2022-10-17 | 21:58 | 50.014
2022-10-17 | 21:58 | 50.015
2022-10-17 | 21:58 | 50.014
2022-10-17 | 21:58 | 50.014
2022-10-17 | 21:58 | 50.012
2022-10-17 | 21:58 | 50.011
2022-10-17 | 21:58 | 50.005
2022-10-17 | 21:58 | 50.002
2022-10-17 | 21:59 | 49.999
2022-10-17 | 21:59 | 49.996
2022-10-17 | 21:59 | 49.994
2022-10-17 | 21:59 | 49.995
2022-10-17 | 21:59 | 49.991
2022-10-17 | 21:59 | 49.989
2022-10-17 | 21:59 | 49.985
2022-10-17 | 21:59 | 49.984
2022-10-17 | 21:59 | 49.983
2022-10-17 | 21:59 | 49.985
2022-10-17 | 21:59 | 49.985
2022-10-17 | 21:59 | 49.987
2022-10-17 | 21:59 | 49.993
2022-10-17 | 21:59 | 50
2022-10-17 | 21:59 | 50.004
2022-10-17 | 21:59 | 50.012
2022-10-17 | 21:59 | 50.015
2022-10-17 | 21:59 | 50.015
2022-10-17 | 21:59 | 50.012
2022-10-17 | 21:59 | 50.01
2022-10-17 | 21:59 | 50.008
2022-10-17 | 21:59 | 50.006
2022-10-17 | 21:59 | 50.004
2022-10-17 | 21:59 | 50.003
2022-10-17 | 21:59 | 50
2022-10-17 | 21:59 | 49.999
2022-10-17 | 21:59 | 49.996
2022-10-17 | 21:59 | 49.996
2022-10-17 | 21:59 | 49.994
2022-10-17 | 21:59 | 49.994

## 20221017-2
In GMT
Date | Time | Freq
2022-10-17 | 22:31 | 50.019
2022-10-17 | 22:31 | 50.016
2022-10-17 | 22:31 | 50.015
2022-10-17 | 22:31 | 50.009
2022-10-17 | 22:31 | 50.007
2022-10-17 | 22:31 | 50.005
2022-10-17 | 22:31 | 50
2022-10-17 | 22:31 | 49.996
2022-10-17 | 22:31 | 49.994
2022-10-17 | 22:31 | 49.994
2022-10-17 | 22:31 | 49.992
2022-10-17 | 22:31 | 49.989
2022-10-17 | 22:31 | 49.987
2022-10-17 | 22:31 | 49.983
2022-10-17 | 22:31 | 49.979
2022-10-17 | 22:31 | 49.979
2022-10-17 | 22:31 | 49.98
2022-10-17 | 22:31 | 49.98
2022-10-17 | 22:31 | 49.979
2022-10-17 | 22:31 | 49.98
2022-10-17 | 22:31 | 49.981
2022-10-17 | 22:31 | 49.978
2022-10-17 | 22:31 | 49.977
2022-10-17 | 22:31 | 49.979
2022-10-17 | 22:31 | 49.978
2022-10-17 | 22:31 | 49.978
2022-10-17 | 22:31 | 49.977
2022-10-17 | 22:31 | 49.977
2022-10-17 | 22:31 | 49.978
2022-10-17 | 22:31 | 49.975
2022-10-17 | 22:32 | 49.975
2022-10-17 | 22:32 | 49.975
2022-10-17 | 22:32 | 49.974
2022-10-17 | 22:32 | 49.976
2022-10-17 | 22:32 | 49.978
2022-10-17 | 22:32 | 49.98
2022-10-17 | 22:32 | 49.98
2022-10-17 | 22:32 | 49.98
2022-10-17 | 22:32 | 49.98
2022-10-17 | 22:32 | 49.979
2022-10-17 | 22:32 | 49.979
2022-10-17 | 22:32 | 49.979
2022-10-17 | 22:32 | 49.975
2022-10-17 | 22:32 | 49.976
2022-10-17 | 22:32 | 49.974
2022-10-17 | 22:32 | 49.971
2022-10-17 | 22:32 | 49.968
2022-10-17 | 22:32 | 49.968
2022-10-17 | 22:32 | 49.967
2022-10-17 | 22:32 | 49.966
2022-10-17 | 22:32 | 49.967
2022-10-17 | 22:32 | 49.966
2022-10-17 | 22:32 | 49.964
2022-10-17 | 22:32 | 49.962
2022-10-17 | 22:32 | 49.961
2022-10-17 | 22:32 | 49.962
2022-10-17 | 22:32 | 49.959
2022-10-17 | 22:32 | 49.959
2022-10-17 | 22:32 | 49.958
2022-10-17 | 22:32 | 49.959
2022-10-17 | 22:32 | 49.96
2022-10-17 | 22:32 | 49.96
2022-10-17 | 22:32 | 49.961
2022-10-17 | 22:32 | 49.963
2022-10-17 | 22:32 | 49.963
2022-10-17 | 22:32 | 49.962
2022-10-17 | 22:32 | 49.962
2022-10-17 | 22:32 | 49.961
2022-10-17 | 22:32 | 49.959
2022-10-17 | 22:32 | 49.957
2022-10-17 | 22:32 | 49.958
2022-10-17 | 22:32 | 49.959
2022-10-17 | 22:32 | 49.958
2022-10-17 | 22:32 | 49.958
2022-10-17 | 22:32 | 49.958
2022-10-17 | 22:32 | 49.957
2022-10-17 | 22:32 | 49.956
2022-10-17 | 22:32 | 49.956
2022-10-17 | 22:32 | 49.956
2022-10-17 | 22:32 | 49.944
2022-10-17 | 22:32 | 49.91
2022-10-17 | 22:32 | 49.869
2022-10-17 | 22:32 | 49.843
2022-10-17 | 22:32 | 49.825
2022-10-17 | 22:32 | 49.814
2022-10-17 | 22:32 | 49.812
2022-10-17 | 22:32 | 49.813
2022-10-17 | 22:32 | 49.815
2022-10-17 | 22:32 | 49.818
2022-10-17 | 22:32 | 49.822
2022-10-17 | 22:32 | 49.824
2022-10-17 | 22:33 | 49.825
2022-10-17 | 22:33 | 49.824
2022-10-17 | 22:33 | 49.828
2022-10-17 | 22:33 | 49.832
2022-10-17 | 22:33 | 49.837
2022-10-17 | 22:33 | 49.837
2022-10-17 | 22:33 | 49.837
2022-10-17 | 22:33 | 49.836
2022-10-17 | 22:33 | 49.835
2022-10-17 | 22:33 | 49.835
2022-10-17 | 22:33 | 49.836
2022-10-17 | 22:33 | 49.837
2022-10-17 | 22:33 | 49.837
2022-10-17 | 22:33 | 49.839
2022-10-17 | 22:33 | 49.84
2022-10-17 | 22:33 | 49.84
2022-10-17 | 22:33 | 49.836
2022-10-17 | 22:33 | 49.833
2022-10-17 | 22:33 | 49.832
2022-10-17 | 22:33 | 49.829
2022-10-17 | 22:33 | 49.825
2022-10-17 | 22:33 | 49.823
2022-10-17 | 22:33 | 49.823
2022-10-17 | 22:33 | 49.823
2022-10-17 | 22:33 | 49.825
2022-10-17 | 22:33 | 49.825
2022-10-17 | 22:33 | 49.826
2022-10-17 | 22:33 | 49.824
2022-10-17 | 22:33 | 49.824
2022-10-17 | 22:33 | 49.824
2022-10-17 | 22:33 | 49.824
2022-10-17 | 22:33 | 49.823
2022-10-17 | 22:33 | 49.822
2022-10-17 | 22:33 | 49.822
2022-10-17 | 22:33 | 49.823
2022-10-17 | 22:33 | 49.824
2022-10-17 | 22:33 | 49.825
2022-10-17 | 22:33 | 49.827
2022-10-17 | 22:33 | 49.828
2022-10-17 | 22:33 | 49.828
2022-10-17 | 22:33 | 49.829
2022-10-17 | 22:33 | 49.829
2022-10-17 | 22:33 | 49.831
2022-10-17 | 22:33 | 49.832
2022-10-17 | 22:33 | 49.834
2022-10-17 | 22:33 | 49.833
2022-10-17 | 22:33 | 49.832
2022-10-17 | 22:33 | 49.834
2022-10-17 | 22:33 | 49.835
2022-10-17 | 22:33 | 49.836
2022-10-17 | 22:33 | 49.837
2022-10-17 | 22:33 | 49.836
2022-10-17 | 22:33 | 49.838
2022-10-17 | 22:33 | 49.841
2022-10-17 | 22:33 | 49.845
2022-10-17 | 22:33 | 49.849
2022-10-17 | 22:33 | 49.857
2022-10-17 | 22:33 | 49.864
2022-10-17 | 22:33 | 49.869
2022-10-17 | 22:34 | 49.873
2022-10-17 | 22:34 | 49.877
2022-10-17 | 22:34 | 49.878
2022-10-17 | 22:34 | 49.878
2022-10-17 | 22:34 | 49.878
2022-10-17 | 22:34 | 49.879
2022-10-17 | 22:34 | 49.877
2022-10-17 | 22:34 | 49.877
2022-10-17 | 22:34 | 49.877
2022-10-17 | 22:34 | 49.878
2022-10-17 | 22:34 | 49.881
2022-10-17 | 22:34 | 49.883
2022-10-17 | 22:34 | 49.884
2022-10-17 | 22:34 | 49.884
2022-10-17 | 22:34 | 49.885
2022-10-17 | 22:34 | 49.883
2022-10-17 | 22:34 | 49.882
2022-10-17 | 22:34 | 49.885
2022-10-17 | 22:34 | 49.887
2022-10-17 | 22:34 | 49.885
2022-10-17 | 22:34 | 49.886
2022-10-17 | 22:34 | 49.888
2022-10-17 | 22:34 | 49.889
2022-10-17 | 22:34 | 49.888
2022-10-17 | 22:34 | 49.888
2022-10-17 | 22:34 | 49.888
2022-10-17 | 22:34 | 49.887
2022-10-17 | 22:34 | 49.884
2022-10-17 | 22:34 | 49.885
2022-10-17 | 22:34 | 49.884
2022-10-17 | 22:34 | 49.882
2022-10-17 | 22:34 | 49.881
2022-10-17 | 22:34 | 49.881
2022-10-17 | 22:34 | 49.881
2022-10-17 | 22:34 | 49.879
2022-10-17 | 22:34 | 49.877
2022-10-17 | 22:34 | 49.877
2022-10-17 | 22:34 | 49.876
2022-10-17 | 22:34 | 49.874
2022-10-17 | 22:34 | 49.872
2022-10-17 | 22:34 | 49.869
2022-10-17 | 22:34 | 49.867
2022-10-17 | 22:34 | 49.864
2022-10-17 | 22:34 | 49.865
2022-10-17 | 22:34 | 49.865
2022-10-17 | 22:34 | 49.87
2022-10-17 | 22:34 | 49.87
2022-10-17 | 22:34 | 49.872
2022-10-17 | 22:34 | 49.875
2022-10-17 | 22:34 | 49.876
2022-10-17 | 22:34 | 49.874
2022-10-17 | 22:34 | 49.875
2022-10-17 | 22:34 | 49.875
2022-10-17 | 22:34 | 49.875
2022-10-17 | 22:34 | 49.871
2022-10-17 | 22:34 | 49.868
2022-10-17 | 22:34 | 49.868
2022-10-17 | 22:34 | 49.866
2022-10-17 | 22:34 | 49.866
2022-10-17 | 22:34 | 49.866
2022-10-17 | 22:34 | 49.87
2022-10-17 | 22:35 | 49.872
2022-10-17 | 22:35 | 49.874
2022-10-17 | 22:35 | 49.875
2022-10-17 | 22:35 | 49.877
2022-10-17 | 22:35 | 49.875
2022-10-17 | 22:35 | 49.876
2022-10-17 | 22:35 | 49.876
2022-10-17 | 22:35 | 49.875
2022-10-17 | 22:35 | 49.875
2022-10-17 | 22:35 | 49.877
2022-10-17 | 22:35 | 49.877
2022-10-17 | 22:35 | 49.877
2022-10-17 | 22:35 | 49.877
2022-10-17 | 22:35 | 49.88
2022-10-17 | 22:35 | 49.881
2022-10-17 | 22:35 | 49.879
2022-10-17 | 22:35 | 49.878
2022-10-17 | 22:35 | 49.878
2022-10-17 | 22:35 | 49.878
2022-10-17 | 22:35 | 49.879
2022-10-17 | 22:35 | 49.877
2022-10-17 | 22:35 | 49.88
2022-10-17 | 22:35 | 49.882
2022-10-17 | 22:35 | 49.885
2022-10-17 | 22:35 | 49.885
2022-10-17 | 22:35 | 49.888
2022-10-17 | 22:35 | 49.889
2022-10-17 | 22:35 | 49.893
2022-10-17 | 22:35 | 49.892
2022-10-17 | 22:35 | 49.894
2022-10-17 | 22:35 | 49.895
2022-10-17 | 22:35 | 49.892
2022-10-17 | 22:35 | 49.889
2022-10-17 | 22:35 | 49.891
2022-10-17 | 22:35 | 49.892
2022-10-17 | 22:35 | 49.891
2022-10-17 | 22:35 | 49.89
2022-10-17 | 22:35 | 49.891
2022-10-17 | 22:35 | 49.89
2022-10-17 | 22:35 | 49.888
2022-10-17 | 22:35 | 49.887
2022-10-17 | 22:35 | 49.884
2022-10-17 | 22:35 | 49.879
2022-10-17 | 22:35 | 49.875
2022-10-17 | 22:35 | 49.873
2022-10-17 | 22:35 | 49.872
2022-10-17 | 22:35 | 49.871
2022-10-17 | 22:35 | 49.871
2022-10-17 | 22:35 | 49.87
2022-10-17 | 22:35 | 49.874
2022-10-17 | 22:35 | 49.875
2022-10-17 | 22:35 | 49.877
2022-10-17 | 22:35 | 49.881
2022-10-17 | 22:35 | 49.882
2022-10-17 | 22:35 | 49.881
2022-10-17 | 22:35 | 49.882
2022-10-17 | 22:35 | 49.881
2022-10-17 | 22:35 | 49.88
2022-10-17 | 22:35 | 49.879
2022-10-17 | 22:35 | 49.88
2022-10-17 | 22:36 | 49.88
2022-10-17 | 22:36 | 49.885
2022-10-17 | 22:36 | 49.885
2022-10-17 | 22:36 | 49.887
2022-10-17 | 22:36 | 49.888
2022-10-17 | 22:36 | 49.888
2022-10-17 | 22:36 | 49.886
2022-10-17 | 22:36 | 49.882
2022-10-17 | 22:36 | 49.882
2022-10-17 | 22:36 | 49.88
2022-10-17 | 22:36 | 49.876
2022-10-17 | 22:36 | 49.873
2022-10-17 | 22:36 | 49.873
2022-10-17 | 22:36 | 49.871
2022-10-17 | 22:36 | 49.867
2022-10-17 | 22:36 | 49.867
2022-10-17 | 22:36 | 49.871
2022-10-17 | 22:36 | 49.874
2022-10-17 | 22:36 | 49.877
2022-10-17 | 22:36 | 49.88
2022-10-17 | 22:36 | 49.882
2022-10-17 | 22:36 | 49.884
2022-10-17 | 22:36 | 49.887
2022-10-17 | 22:36 | 49.889
2022-10-17 | 22:36 | 49.89
2022-10-17 | 22:36 | 49.892
2022-10-17 | 22:36 | 49.89
2022-10-17 | 22:36 | 49.89
2022-10-17 | 22:36 | 49.892
2022-10-17 | 22:36 | 49.891
2022-10-17 | 22:36 | 49.889
2022-10-17 | 22:36 | 49.887
2022-10-17 | 22:36 | 49.887
2022-10-17 | 22:36 | 49.885
2022-10-17 | 22:36 | 49.885
2022-10-17 | 22:36 | 49.884
2022-10-17 | 22:36 | 49.881
2022-10-17 | 22:36 | 49.877
2022-10-17 | 22:36 | 49.875
2022-10-17 | 22:36 | 49.872
2022-10-17 | 22:36 | 49.872
2022-10-17 | 22:36 | 49.87
2022-10-17 | 22:36 | 49.869
2022-10-17 | 22:36 | 49.87
2022-10-17 | 22:36 | 49.873
2022-10-17 | 22:36 | 49.875
2022-10-17 | 22:36 | 49.878
2022-10-17 | 22:36 | 49.883
2022-10-17 | 22:36 | 49.885
2022-10-17 | 22:36 | 49.889
2022-10-17 | 22:36 | 49.891
2022-10-17 | 22:36 | 49.891
2022-10-17 | 22:36 | 49.89
2022-10-17 | 22:36 | 49.886
2022-10-17 | 22:36 | 49.883
2022-10-17 | 22:36 | 49.883
2022-10-17 | 22:36 | 49.882
2022-10-17 | 22:36 | 49.877
2022-10-17 | 22:36 | 49.878
2022-10-17 | 22:37 | 49.876
2022-10-17 | 22:37 | 49.874
2022-10-17 | 22:37 | 49.871
2022-10-17 | 22:37 | 49.871
2022-10-17 | 22:37 | 49.869
2022-10-17 | 22:37 | 49.871
2022-10-17 | 22:37 | 49.869
2022-10-17 | 22:37 | 49.866
2022-10-17 | 22:37 | 49.865
2022-10-17 | 22:37 | 49.863
2022-10-17 | 22:37 | 49.863
2022-10-17 | 22:37 | 49.866
2022-10-17 | 22:37 | 49.865
2022-10-17 | 22:37 | 49.866
2022-10-17 | 22:37 | 49.868
2022-10-17 | 22:37 | 49.872
2022-10-17 | 22:37 | 49.872
2022-10-17 | 22:37 | 49.871
2022-10-17 | 22:37 | 49.868
2022-10-17 | 22:37 | 49.868
2022-10-17 | 22:37 | 49.867
2022-10-17 | 22:37 | 49.866
2022-10-17 | 22:37 | 49.863
2022-10-17 | 22:37 | 49.862
2022-10-17 | 22:37 | 49.863
2022-10-17 | 22:37 | 49.864
2022-10-17 | 22:37 | 49.864
2022-10-17 | 22:37 | 49.868
2022-10-17 | 22:37 | 49.87
2022-10-17 | 22:37 | 49.872
2022-10-17 | 22:37 | 49.872
2022-10-17 | 22:37 | 49.873
2022-10-17 | 22:37 | 49.873
2022-10-17 | 22:37 | 49.873
2022-10-17 | 22:37 | 49.875
2022-10-17 | 22:37 | 49.879
2022-10-17 | 22:37 | 49.88
2022-10-17 | 22:37 | 49.881
2022-10-17 | 22:37 | 49.883
2022-10-17 | 22:37 | 49.883
2022-10-17 | 22:37 | 49.882
2022-10-17 | 22:37 | 49.879
2022-10-17 | 22:37 | 49.878
2022-10-17 | 22:37 | 49.877
2022-10-17 | 22:37 | 49.874
2022-10-17 | 22:37 | 49.874
2022-10-17 | 22:37 | 49.875
2022-10-17 | 22:37 | 49.874
2022-10-17 | 22:37 | 49.875
2022-10-17 | 22:37 | 49.875
2022-10-17 | 22:37 | 49.875
2022-10-17 | 22:37 | 49.875
2022-10-17 | 22:37 | 49.872
2022-10-17 | 22:37 | 49.871
2022-10-17 | 22:37 | 49.871
2022-10-17 | 22:37 | 49.869
2022-10-17 | 22:37 | 49.868
2022-10-17 | 22:37 | 49.869
2022-10-17 | 22:37 | 49.87
2022-10-17 | 22:37 | 49.872
2022-10-17 | 22:37 | 49.873
2022-10-17 | 22:38 | 49.875
2022-10-17 | 22:38 | 49.877
2022-10-17 | 22:38 | 49.877
2022-10-17 | 22:38 | 49.88
2022-10-17 | 22:38 | 49.881
2022-10-17 | 22:38 | 49.883
2022-10-17 | 22:38 | 49.885
2022-10-17 | 22:38 | 49.884
2022-10-17 | 22:38 | 49.884
2022-10-17 | 22:38 | 49.881
2022-10-17 | 22:38 | 49.879
2022-10-17 | 22:38 | 49.88
2022-10-17 | 22:38 | 49.879
2022-10-17 | 22:38 | 49.878
2022-10-17 | 22:38 | 49.875
2022-10-17 | 22:38 | 49.874
2022-10-17 | 22:38 | 49.876
2022-10-17 | 22:38 | 49.875
2022-10-17 | 22:38 | 49.876
2022-10-17 | 22:38 | 49.878
2022-10-17 | 22:38 | 49.88
2022-10-17 | 22:38 | 49.883
2022-10-17 | 22:38 | 49.884
2022-10-17 | 22:38 | 49.882
2022-10-17 | 22:38 | 49.884
2022-10-17 | 22:38 | 49.882
2022-10-17 | 22:38 | 49.881
2022-10-17 | 22:38 | 49.88
2022-10-17 | 22:38 | 49.876
2022-10-17 | 22:38 | 49.873
2022-10-17 | 22:38 | 49.867
2022-10-17 | 22:38 | 49.864
2022-10-17 | 22:38 | 49.865
2022-10-17 | 22:38 | 49.863
2022-10-17 | 22:38 | 49.865
2022-10-17 | 22:38 | 49.867
2022-10-17 | 22:38 | 49.87
2022-10-17 | 22:38 | 49.869
2022-10-17 | 22:38 | 49.87
2022-10-17 | 22:38 | 49.868
2022-10-17 | 22:38 | 49.867
2022-10-17 | 22:38 | 49.865
2022-10-17 | 22:38 | 49.86
2022-10-17 | 22:38 | 49.86
2022-10-17 | 22:38 | 49.861
2022-10-17 | 22:38 | 49.86
2022-10-17 | 22:38 | 49.86
2022-10-17 | 22:38 | 49.859
2022-10-17 | 22:38 | 49.859
2022-10-17 | 22:38 | 49.858
2022-10-17 | 22:38 | 49.86
2022-10-17 | 22:38 | 49.864
2022-10-17 | 22:38 | 49.866
2022-10-17 | 22:38 | 49.865
2022-10-17 | 22:38 | 49.865
2022-10-17 | 22:38 | 49.867
2022-10-17 | 22:38 | 49.869
2022-10-17 | 22:38 | 49.873
2022-10-17 | 22:38 | 49.88
2022-10-17 | 22:39 | 49.883
2022-10-17 | 22:39 | 49.887
2022-10-17 | 22:39 | 49.888
2022-10-17 | 22:39 | 49.891
2022-10-17 | 22:39 | 49.892
2022-10-17 | 22:39 | 49.891
2022-10-17 | 22:39 | 49.891
2022-10-17 | 22:39 | 49.89
2022-10-17 | 22:39 | 49.887
2022-10-17 | 22:39 | 49.887
2022-10-17 | 22:39 | 49.882
2022-10-17 | 22:39 | 49.883
2022-10-17 | 22:39 | 49.883
2022-10-17 | 22:39 | 49.882
2022-10-17 | 22:39 | 49.88
2022-10-17 | 22:39 | 49.882
2022-10-17 | 22:39 | 49.884
2022-10-17 | 22:39 | 49.885
2022-10-17 | 22:39 | 49.885
2022-10-17 | 22:39 | 49.887
2022-10-17 | 22:39 | 49.888
2022-10-17 | 22:39 | 49.889
2022-10-17 | 22:39 | 49.89
2022-10-17 | 22:39 | 49.894
2022-10-17 | 22:39 | 49.896
2022-10-17 | 22:39 | 49.896
2022-10-17 | 22:39 | 49.899
2022-10-17 | 22:39 | 49.899
2022-10-17 | 22:39 | 49.902
2022-10-17 | 22:39 | 49.901
2022-10-17 | 22:39 | 49.903
2022-10-17 | 22:39 | 49.9
2022-10-17 | 22:39 | 49.9
2022-10-17 | 22:39 | 49.895
2022-10-17 | 22:39 | 49.891
2022-10-17 | 22:39 | 49.89
2022-10-17 | 22:39 | 49.888
2022-10-17 | 22:39 | 49.883
2022-10-17 | 22:39 | 49.883
2022-10-17 | 22:39 | 49.882
2022-10-17 | 22:39 | 49.884
2022-10-17 | 22:39 | 49.883
2022-10-17 | 22:39 | 49.885
2022-10-17 | 22:39 | 49.888
2022-10-17 | 22:39 | 49.889
2022-10-17 | 22:39 | 49.889
2022-10-17 | 22:39 | 49.891
2022-10-17 | 22:39 | 49.892
2022-10-17 | 22:39 | 49.892
2022-10-17 | 22:39 | 49.893
2022-10-17 | 22:39 | 49.894
2022-10-17 | 22:39 | 49.896
2022-10-17 | 22:39 | 49.894
2022-10-17 | 22:39 | 49.893
2022-10-17 | 22:39 | 49.893
2022-10-17 | 22:39 | 49.892
2022-10-17 | 22:39 | 49.891
2022-10-17 | 22:39 | 49.889
2022-10-17 | 22:39 | 49.887
2022-10-17 | 22:39 | 49.885
2022-10-17 | 22:39 | 49.884
2022-10-17 | 22:40 | 49.883
2022-10-17 | 22:40 | 49.884
2022-10-17 | 22:40 | 49.885
2022-10-17 | 22:40 | 49.886
2022-10-17 | 22:40 | 49.885
2022-10-17 | 22:40 | 49.884
2022-10-17 | 22:40 | 49.886
2022-10-17 | 22:40 | 49.885
2022-10-17 | 22:40 | 49.888
2022-10-17 | 22:40 | 49.891
2022-10-17 | 22:40 | 49.895
2022-10-17 | 22:40 | 49.899
2022-10-17 | 22:40 | 49.9
2022-10-17 | 22:40 | 49.903
2022-10-17 | 22:40 | 49.906
2022-10-17 | 22:40 | 49.907
2022-10-17 | 22:40 | 49.912
2022-10-17 | 22:40 | 49.914
2022-10-17 | 22:40 | 49.913
2022-10-17 | 22:40 | 49.912
2022-10-17 | 22:40 | 49.909
2022-10-17 | 22:40 | 49.906
2022-10-17 | 22:40 | 49.903
2022-10-17 | 22:40 | 49.899
2022-10-17 | 22:40 | 49.896
2022-10-17 | 22:40 | 49.891
2022-10-17 | 22:40 | 49.888
2022-10-17 | 22:40 | 49.884
2022-10-17 | 22:40 | 49.883
2022-10-17 | 22:40 | 49.882
2022-10-17 | 22:40 | 49.881
2022-10-17 | 22:40 | 49.881
2022-10-17 | 22:40 | 49.883
2022-10-17 | 22:40 | 49.885
2022-10-17 | 22:40 | 49.888
2022-10-17 | 22:40 | 49.888
2022-10-17 | 22:40 | 49.888
2022-10-17 | 22:40 | 49.888
2022-10-17 | 22:40 | 49.888
2022-10-17 | 22:40 | 49.887
2022-10-17 | 22:40 | 49.886
2022-10-17 | 22:40 | 49.886
2022-10-17 | 22:40 | 49.888
2022-10-17 | 22:40 | 49.89
2022-10-17 | 22:40 | 49.889
2022-10-17 | 22:40 | 49.887
2022-10-17 | 22:40 | 49.886
2022-10-17 | 22:40 | 49.884
2022-10-17 | 22:40 | 49.881
2022-10-17 | 22:40 | 49.879
2022-10-17 | 22:40 | 49.876
2022-10-17 | 22:40 | 49.875
2022-10-17 | 22:40 | 49.875
2022-10-17 | 22:40 | 49.872
2022-10-17 | 22:40 | 49.871
2022-10-17 | 22:40 | 49.874
2022-10-17 | 22:40 | 49.871
2022-10-17 | 22:40 | 49.871
2022-10-17 | 22:40 | 49.867
2022-10-17 | 22:41 | 49.868
2022-10-17 | 22:41 | 49.866
2022-10-17 | 22:41 | 49.869
2022-10-17 | 22:41 | 49.87
2022-10-17 | 22:41 | 49.873
2022-10-17 | 22:41 | 49.876
2022-10-17 | 22:41 | 49.879
2022-10-17 | 22:41 | 49.88
2022-10-17 | 22:41 | 49.885
2022-10-17 | 22:41 | 49.887
2022-10-17 | 22:41 | 49.892
2022-10-17 | 22:41 | 49.894
2022-10-17 | 22:41 | 49.896
2022-10-17 | 22:41 | 49.896
2022-10-17 | 22:41 | 49.895
2022-10-17 | 22:41 | 49.895
2022-10-17 | 22:41 | 49.895
2022-10-17 | 22:41 | 49.893
2022-10-17 | 22:41 | 49.891
2022-10-17 | 22:41 | 49.893
2022-10-17 | 22:41 | 49.893
2022-10-17 | 22:41 | 49.892
2022-10-17 | 22:41 | 49.891
2022-10-17 | 22:41 | 49.888
2022-10-17 | 22:41 | 49.887
2022-10-17 | 22:41 | 49.884
2022-10-17 | 22:41 | 49.883
2022-10-17 | 22:41 | 49.884
2022-10-17 | 22:41 | 49.884
2022-10-17 | 22:41 | 49.881
2022-10-17 | 22:41 | 49.882
2022-10-17 | 22:41 | 49.881
2022-10-17 | 22:41 | 49.884
2022-10-17 | 22:41 | 49.885
2022-10-17 | 22:41 | 49.888
2022-10-17 | 22:41 | 49.893
2022-10-17 | 22:41 | 49.896
2022-10-17 | 22:41 | 49.897
2022-10-17 | 22:41 | 49.899
2022-10-17 | 22:41 | 49.904
2022-10-17 | 22:41 | 49.905
2022-10-17 | 22:41 | 49.906
2022-10-17 | 22:41 | 49.904
2022-10-17 | 22:41 | 49.904
2022-10-17 | 22:41 | 49.903
2022-10-17 | 22:41 | 49.899
2022-10-17 | 22:41 | 49.896
2022-10-17 | 22:41 | 49.894
2022-10-17 | 22:41 | 49.892
2022-10-17 | 22:41 | 49.891
2022-10-17 | 22:41 | 49.891
2022-10-17 | 22:41 | 49.89
2022-10-17 | 22:41 | 49.89
2022-10-17 | 22:41 | 49.889
2022-10-17 | 22:41 | 49.889
2022-10-17 | 22:41 | 49.89
2022-10-17 | 22:41 | 49.889
2022-10-17 | 22:41 | 49.893
2022-10-17 | 22:41 | 49.894
2022-10-17 | 22:41 | 49.899
2022-10-17 | 22:41 | 49.901
2022-10-17 | 22:42 | 49.904
2022-10-17 | 22:42 | 49.905
2022-10-17 | 22:42 | 49.902
2022-10-17 | 22:42 | 49.901
2022-10-17 | 22:42 | 49.901
2022-10-17 | 22:42 | 49.903
2022-10-17 | 22:42 | 49.903
2022-10-17 | 22:42 | 49.902
2022-10-17 | 22:42 | 49.901
2022-10-17 | 22:42 | 49.9
2022-10-17 | 22:42 | 49.898
2022-10-17 | 22:42 | 49.897
2022-10-17 | 22:42 | 49.896
2022-10-17 | 22:42 | 49.897
2022-10-17 | 22:42 | 49.897
2022-10-17 | 22:42 | 49.897
2022-10-17 | 22:42 | 49.898
2022-10-17 | 22:42 | 49.899
2022-10-17 | 22:42 | 49.896
2022-10-17 | 22:42 | 49.897
2022-10-17 | 22:42 | 49.898
2022-10-17 | 22:42 | 49.897
2022-10-17 | 22:42 | 49.898
2022-10-17 | 22:42 | 49.898
2022-10-17 | 22:42 | 49.9
2022-10-17 | 22:42 | 49.899
2022-10-17 | 22:42 | 49.899
2022-10-17 | 22:42 | 49.902
2022-10-17 | 22:42 | 49.9
2022-10-17 | 22:42 | 49.901
2022-10-17 | 22:42 | 49.901
2022-10-17 | 22:42 | 49.901
2022-10-17 | 22:42 | 49.902
2022-10-17 | 22:42 | 49.903
2022-10-17 | 22:42 | 49.903
2022-10-17 | 22:42 | 49.903
2022-10-17 | 22:42 | 49.905
2022-10-17 | 22:42 | 49.905
2022-10-17 | 22:42 | 49.907
2022-10-17 | 22:42 | 49.907
2022-10-17 | 22:42 | 49.91
2022-10-17 | 22:42 | 49.912
2022-10-17 | 22:42 | 49.911
2022-10-17 | 22:42 | 49.911
2022-10-17 | 22:42 | 49.908
2022-10-17 | 22:42 | 49.908
2022-10-17 | 22:42 | 49.905
2022-10-17 | 22:42 | 49.901
2022-10-17 | 22:42 | 49.9
2022-10-17 | 22:42 | 49.896
2022-10-17 | 22:42 | 49.898
2022-10-17 | 22:42 | 49.895
2022-10-17 | 22:42 | 49.895
2022-10-17 | 22:42 | 49.893
2022-10-17 | 22:42 | 49.895
2022-10-17 | 22:42 | 49.897
2022-10-17 | 22:42 | 49.899
2022-10-17 | 22:42 | 49.901
2022-10-17 | 22:42 | 49.905
2022-10-17 | 22:43 | 49.909
2022-10-17 | 22:43 | 49.911
2022-10-17 | 22:43 | 49.91
2022-10-17 | 22:43 | 49.911
2022-10-17 | 22:43 | 49.911
2022-10-17 | 22:43 | 49.908
2022-10-17 | 22:43 | 49.908
2022-10-17 | 22:43 | 49.905
2022-10-17 | 22:43 | 49.905
2022-10-17 | 22:43 | 49.903
2022-10-17 | 22:43 | 49.901
2022-10-17 | 22:43 | 49.899
2022-10-17 | 22:43 | 49.895
2022-10-17 | 22:43 | 49.898
2022-10-17 | 22:43 | 49.896
2022-10-17 | 22:43 | 49.899
2022-10-17 | 22:43 | 49.9
2022-10-17 | 22:43 | 49.903
2022-10-17 | 22:43 | 49.903
2022-10-17 | 22:43 | 49.906
2022-10-17 | 22:43 | 49.91
2022-10-17 | 22:43 | 49.915
2022-10-17 | 22:43 | 49.915
2022-10-17 | 22:43 | 49.918
2022-10-17 | 22:43 | 49.92
2022-10-17 | 22:43 | 49.923
2022-10-17 | 22:43 | 49.923
2022-10-17 | 22:43 | 49.924
2022-10-17 | 22:43 | 49.927
2022-10-17 | 22:43 | 49.923
2022-10-17 | 22:43 | 49.922
2022-10-17 | 22:43 | 49.919
2022-10-17 | 22:43 | 49.917
2022-10-17 | 22:43 | 49.914
2022-10-17 | 22:43 | 49.91
2022-10-17 | 22:43 | 49.909
2022-10-17 | 22:43 | 49.91
2022-10-17 | 22:43 | 49.91
2022-10-17 | 22:43 | 49.91
2022-10-17 | 22:43 | 49.913
2022-10-17 | 22:43 | 49.916
2022-10-17 | 22:43 | 49.918
2022-10-17 | 22:43 | 49.921
2022-10-17 | 22:43 | 49.924
2022-10-17 | 22:43 | 49.921
2022-10-17 | 22:43 | 49.923
2022-10-17 | 22:43 | 49.924
2022-10-17 | 22:43 | 49.929
2022-10-17 | 22:43 | 49.93
2022-10-17 | 22:43 | 49.929
2022-10-17 | 22:43 | 49.93
2022-10-17 | 22:43 | 49.931
2022-10-17 | 22:43 | 49.933
2022-10-17 | 22:43 | 49.934
2022-10-17 | 22:43 | 49.937
2022-10-17 | 22:43 | 49.936
2022-10-17 | 22:43 | 49.937
2022-10-17 | 22:43 | 49.936
2022-10-17 | 22:43 | 49.933
2022-10-17 | 22:43 | 49.934
2022-10-17 | 22:44 | 49.931
2022-10-17 | 22:44 | 49.932
2022-10-17 | 22:44 | 49.93
2022-10-17 | 22:44 | 49.93
2022-10-17 | 22:44 | 49.928
2022-10-17 | 22:44 | 49.93
2022-10-17 | 22:44 | 49.932
2022-10-17 | 22:44 | 49.931
2022-10-17 | 22:44 | 49.931
2022-10-17 | 22:44 | 49.932
2022-10-17 | 22:44 | 49.942
2022-10-17 | 22:44 | 49.949
2022-10-17 | 22:44 | 49.953
2022-10-17 | 22:44 | 49.957
2022-10-17 | 22:44 | 49.958
2022-10-17 | 22:44 | 49.958
2022-10-17 | 22:44 | 49.956
2022-10-17 | 22:44 | 49.96
2022-10-17 | 22:44 | 49.963
2022-10-17 | 22:44 | 49.965
2022-10-17 | 22:44 | 49.969
2022-10-17 | 22:44 | 49.973
2022-10-17 | 22:44 | 49.978
2022-10-17 | 22:44 | 49.984
2022-10-17 | 22:44 | 49.984
2022-10-17 | 22:44 | 49.984
2022-10-17 | 22:44 | 49.985
2022-10-17 | 22:44 | 49.984
2022-10-17 | 22:44 | 49.983
2022-10-17 | 22:44 | 49.981
2022-10-17 | 22:44 | 49.978
2022-10-17 | 22:44 | 49.973
2022-10-17 | 22:44 | 49.973
2022-10-17 | 22:44 | 49.973
2022-10-17 | 22:44 | 49.971
2022-10-17 | 22:44 | 49.973
2022-10-17 | 22:44 | 49.974
2022-10-17 | 22:44 | 49.978
2022-10-17 | 22:44 | 49.984
2022-10-17 | 22:44 | 49.984
2022-10-17 | 22:44 | 49.987
2022-10-17 | 22:44 | 49.989
2022-10-17 | 22:44 | 49.993
2022-10-17 | 22:44 | 49.992
2022-10-17 | 22:44 | 49.993
2022-10-17 | 22:44 | 49.996
2022-10-17 | 22:44 | 49.993
2022-10-17 | 22:44 | 49.992
2022-10-17 | 22:44 | 49.991
2022-10-17 | 22:44 | 49.987
2022-10-17 | 22:44 | 49.983
2022-10-17 | 22:44 | 49.978
2022-10-17 | 22:44 | 49.975
2022-10-17 | 22:44 | 49.973
2022-10-17 | 22:44 | 49.97
2022-10-17 | 22:44 | 49.968
2022-10-17 | 22:44 | 49.969
2022-10-17 | 22:44 | 49.972
2022-10-17 | 22:44 | 49.975
2022-10-17 | 22:44 | 49.978
2022-10-17 | 22:45 | 49.981
2022-10-17 | 22:45 | 49.984
2022-10-17 | 22:45 | 49.986
2022-10-17 | 22:45 | 49.987
2022-10-17 | 22:45 | 49.993
2022-10-17 | 22:45 | 49.996
2022-10-17 | 22:45 | 49.994
2022-10-17 | 22:45 | 49.994
2022-10-17 | 22:45 | 49.998
2022-10-17 | 22:45 | 50
2022-10-17 | 22:45 | 50.003
2022-10-17 | 22:45 | 50.004
2022-10-17 | 22:45 | 50.006
2022-10-17 | 22:45 | 50.008
2022-10-17 | 22:45 | 50.011
2022-10-17 | 22:45 | 50.012
2022-10-17 | 22:45 | 50.013
2022-10-17 | 22:45 | 50.012
2022-10-17 | 22:45 | 50.012
2022-10-17 | 22:45 | 50.013
2022-10-17 | 22:45 | 50.014
2022-10-17 | 22:45 | 50.011
2022-10-17 | 22:45 | 50.008
2022-10-17 | 22:45 | 50.006
2022-10-17 | 22:45 | 50.004
2022-10-17 | 22:45 | 50
2022-10-17 | 22:45 | 49.997
2022-10-17 | 22:45 | 49.993
2022-10-17 | 22:45 | 49.99
2022-10-17 | 22:45 | 49.992
2022-10-17 | 22:45 | 49.989
2022-10-17 | 22:45 | 49.989
2022-10-17 | 22:45 | 49.985
2022-10-17 | 22:45 | 49.984
2022-10-17 | 22:45 | 49.981
2022-10-17 | 22:45 | 49.979
2022-10-17 | 22:45 | 49.98
2022-10-17 | 22:45 | 49.981
2022-10-17 | 22:45 | 49.983
2022-10-17 | 22:45 | 49.986
2022-10-17 | 22:45 | 49.99
2022-10-17 | 22:45 | 49.993
2022-10-17 | 22:45 | 49.996
2022-10-17 | 22:45 | 49.996
2022-10-17 | 22:45 | 49.996
2022-10-17 | 22:45 | 49.997
2022-10-17 | 22:45 | 49.998
2022-10-17 | 22:45 | 50.004
2022-10-17 | 22:45 | 50.011
2022-10-17 | 22:45 | 50.016
2022-10-17 | 22:45 | 50.018
2022-10-17 | 22:45 | 50.017
2022-10-17 | 22:45 | 50.016
2022-10-17 | 22:45 | 50.015
2022-10-17 | 22:45 | 50.012
2022-10-17 | 22:45 | 50.007
2022-10-17 | 22:45 | 50.001
2022-10-17 | 22:45 | 49.994
2022-10-17 | 22:45 | 49.988
2022-10-17 | 22:45 | 49.986
2022-10-17 | 22:46 | 49.983
2022-10-17 | 22:46 | 49.984
2022-10-17 | 22:46 | 49.986
2022-10-17 | 22:46 | 49.987
2022-10-17 | 22:46 | 49.984
2022-10-17 | 22:46 | 49.982
2022-10-17 | 22:46 | 49.981
2022-10-17 | 22:46 | 49.982
2022-10-17 | 22:46 | 49.983
2022-10-17 | 22:46 | 49.981
2022-10-17 | 22:46 | 49.978
2022-10-17 | 22:46 | 49.971
2022-10-17 | 22:46 | 49.966
2022-10-17 | 22:46 | 49.963
2022-10-17 | 22:46 | 49.959
2022-10-17 | 22:46 | 49.958
2022-10-17 | 22:46 | 49.96
2022-10-17 | 22:46 | 49.959
2022-10-17 | 22:46 | 49.96
2022-10-17 | 22:46 | 49.961
2022-10-17 | 22:46 | 49.962
2022-10-17 | 22:46 | 49.962
2022-10-17 | 22:46 | 49.965
2022-10-17 | 22:46 | 49.964
2022-10-17 | 22:46 | 49.964
2022-10-17 | 22:46 | 49.965
2022-10-17 | 22:46 | 49.968
2022-10-17 | 22:46 | 49.964
2022-10-17 | 22:46 | 49.962
2022-10-17 | 22:46 | 49.96
2022-10-17 | 22:46 | 49.961

## 20221025-1
In GMT
Date | Time | Freq
2022-10-25 | 19:09 | 49.984
2022-10-25 | 19:09 | 49.982
2022-10-25 | 19:09 | 49.979
2022-10-25 | 19:09 | 49.98
2022-10-25 | 19:09 | 49.978
2022-10-25 | 19:09 | 49.976
2022-10-25 | 19:09 | 49.974
2022-10-25 | 19:09 | 49.972
2022-10-25 | 19:09 | 49.97
2022-10-25 | 19:09 | 49.969
2022-10-25 | 19:09 | 49.968
2022-10-25 | 19:09 | 49.968
2022-10-25 | 19:09 | 49.966
2022-10-25 | 19:09 | 49.966
2022-10-25 | 19:09 | 49.964
2022-10-25 | 19:09 | 49.964
2022-10-25 | 19:09 | 49.962
2022-10-25 | 19:09 | 49.962
2022-10-25 | 19:09 | 49.961
2022-10-25 | 19:09 | 49.961
2022-10-25 | 19:09 | 49.961
2022-10-25 | 19:09 | 49.963
2022-10-25 | 19:09 | 49.965
2022-10-25 | 19:09 | 49.966
2022-10-25 | 19:09 | 49.968
2022-10-25 | 19:09 | 49.969
2022-10-25 | 19:09 | 49.969
2022-10-25 | 19:09 | 49.97
2022-10-25 | 19:09 | 49.966
2022-10-25 | 19:09 | 49.966
2022-10-25 | 19:10 | 49.966
2022-10-25 | 19:10 | 49.964
2022-10-25 | 19:10 | 49.959
2022-10-25 | 19:10 | 49.955
2022-10-25 | 19:10 | 49.953
2022-10-25 | 19:10 | 49.948
2022-10-25 | 19:10 | 49.947
2022-10-25 | 19:10 | 49.945
2022-10-25 | 19:10 | 49.942
2022-10-25 | 19:10 | 49.941
2022-10-25 | 19:10 | 49.94
2022-10-25 | 19:10 | 49.937
2022-10-25 | 19:10 | 49.934
2022-10-25 | 19:10 | 49.933
2022-10-25 | 19:10 | 49.929
2022-10-25 | 19:10 | 49.926
2022-10-25 | 19:10 | 49.926
2022-10-25 | 19:10 | 49.923
2022-10-25 | 19:10 | 49.922
2022-10-25 | 19:10 | 49.921
2022-10-25 | 19:10 | 49.922
2022-10-25 | 19:10 | 49.925
2022-10-25 | 19:10 | 49.926
2022-10-25 | 19:10 | 49.929
2022-10-25 | 19:10 | 49.933
2022-10-25 | 19:10 | 49.936
2022-10-25 | 19:10 | 49.937
2022-10-25 | 19:10 | 49.939
2022-10-25 | 19:10 | 49.941
2022-10-25 | 19:10 | 49.942
2022-10-25 | 19:10 | 49.942
2022-10-25 | 19:10 | 49.941
2022-10-25 | 19:10 | 49.941
2022-10-25 | 19:10 | 49.941
2022-10-25 | 19:10 | 49.942
2022-10-25 | 19:10 | 49.946
2022-10-25 | 19:10 | 49.951
2022-10-25 | 19:10 | 49.954
2022-10-25 | 19:10 | 49.96
2022-10-25 | 19:10 | 49.963
2022-10-25 | 19:10 | 49.965
2022-10-25 | 19:10 | 49.967
2022-10-25 | 19:10 | 49.967
2022-10-25 | 19:10 | 49.97
2022-10-25 | 19:10 | 49.973
2022-10-25 | 19:10 | 49.974
2022-10-25 | 19:10 | 49.975
2022-10-25 | 19:10 | 49.975
2022-10-25 | 19:10 | 49.976
2022-10-25 | 19:10 | 49.976
2022-10-25 | 19:10 | 49.976
2022-10-25 | 19:10 | 49.977
2022-10-25 | 19:10 | 49.975
2022-10-25 | 19:10 | 49.973
2022-10-25 | 19:10 | 49.973
2022-10-25 | 19:10 | 49.969
2022-10-25 | 19:10 | 49.965
2022-10-25 | 19:10 | 49.964
2022-10-25 | 19:10 | 49.962
2022-10-25 | 19:10 | 49.96
2022-10-25 | 19:10 | 49.958
2022-10-25 | 19:11 | 49.956
2022-10-25 | 19:11 | 49.956
2022-10-25 | 19:11 | 49.954
2022-10-25 | 19:11 | 49.95
2022-10-25 | 19:11 | 49.947
2022-10-25 | 19:11 | 49.944
2022-10-25 | 19:11 | 49.943
2022-10-25 | 19:11 | 49.941
2022-10-25 | 19:11 | 49.943
2022-10-25 | 19:11 | 49.945
2022-10-25 | 19:11 | 49.945
2022-10-25 | 19:11 | 49.947
2022-10-25 | 19:11 | 49.948
2022-10-25 | 19:11 | 49.953
2022-10-25 | 19:11 | 49.949
2022-10-25 | 19:11 | 49.948
2022-10-25 | 19:11 | 49.948
2022-10-25 | 19:11 | 49.949
2022-10-25 | 19:11 | 49.947
2022-10-25 | 19:11 | 49.946
2022-10-25 | 19:11 | 49.945
2022-10-25 | 19:11 | 49.943
2022-10-25 | 19:11 | 49.942
2022-10-25 | 19:11 | 49.942
2022-10-25 | 19:11 | 49.941
2022-10-25 | 19:11 | 49.941
2022-10-25 | 19:11 | 49.94
2022-10-25 | 19:11 | 49.939
2022-10-25 | 19:11 | 49.939
2022-10-25 | 19:11 | 49.936
2022-10-25 | 19:11 | 49.935
2022-10-25 | 19:11 | 49.933
2022-10-25 | 19:11 | 49.933
2022-10-25 | 19:11 | 49.933
2022-10-25 | 19:11 | 49.934
2022-10-25 | 19:11 | 49.936
2022-10-25 | 19:11 | 49.939
2022-10-25 | 19:11 | 49.941
2022-10-25 | 19:11 | 49.942
2022-10-25 | 19:11 | 49.941
2022-10-25 | 19:11 | 49.942
2022-10-25 | 19:11 | 49.939
2022-10-25 | 19:11 | 49.934
2022-10-25 | 19:11 | 49.932
2022-10-25 | 19:11 | 49.932
2022-10-25 | 19:11 | 49.934
2022-10-25 | 19:11 | 49.934
2022-10-25 | 19:11 | 49.937
2022-10-25 | 19:11 | 49.938
2022-10-25 | 19:11 | 49.94
2022-10-25 | 19:11 | 49.941
2022-10-25 | 19:11 | 49.94
2022-10-25 | 19:11 | 49.94
2022-10-25 | 19:11 | 49.939
2022-10-25 | 19:11 | 49.939
2022-10-25 | 19:11 | 49.942
2022-10-25 | 19:11 | 49.943
2022-10-25 | 19:11 | 49.942
2022-10-25 | 19:11 | 49.944
2022-10-25 | 19:12 | 49.946
2022-10-25 | 19:12 | 49.945
2022-10-25 | 19:12 | 49.946
2022-10-25 | 19:12 | 49.945
2022-10-25 | 19:12 | 49.945
2022-10-25 | 19:12 | 49.946
2022-10-25 | 19:12 | 49.948
2022-10-25 | 19:12 | 49.952
2022-10-25 | 19:12 | 49.954
2022-10-25 | 19:12 | 49.956
2022-10-25 | 19:12 | 49.959
2022-10-25 | 19:12 | 49.96
2022-10-25 | 19:12 | 49.963
2022-10-25 | 19:12 | 49.966
2022-10-25 | 19:12 | 49.97
2022-10-25 | 19:12 | 49.973
2022-10-25 | 19:12 | 49.975
2022-10-25 | 19:12 | 49.978
2022-10-25 | 19:12 | 49.981
2022-10-25 | 19:12 | 49.983
2022-10-25 | 19:12 | 49.984
2022-10-25 | 19:12 | 49.986
2022-10-25 | 19:12 | 49.986
2022-10-25 | 19:12 | 49.987
2022-10-25 | 19:12 | 49.988
2022-10-25 | 19:12 | 49.989
2022-10-25 | 19:12 | 49.99
2022-10-25 | 19:12 | 49.991
2022-10-25 | 19:12 | 49.994
2022-10-25 | 19:12 | 49.994
2022-10-25 | 19:12 | 49.997
2022-10-25 | 19:12 | 49.995
2022-10-25 | 19:12 | 49.995
2022-10-25 | 19:12 | 49.995
2022-10-25 | 19:12 | 49.995
2022-10-25 | 19:12 | 49.993
2022-10-25 | 19:12 | 49.991
2022-10-25 | 19:12 | 49.992
2022-10-25 | 19:12 | 49.993
2022-10-25 | 19:12 | 49.995
2022-10-25 | 19:12 | 49.996
2022-10-25 | 19:12 | 49.996
2022-10-25 | 19:12 | 49.998
2022-10-25 | 19:12 | 49.999
2022-10-25 | 19:12 | 50.001
2022-10-25 | 19:12 | 50.002
2022-10-25 | 19:12 | 50.003
2022-10-25 | 19:12 | 50.004
2022-10-25 | 19:12 | 50.005
2022-10-25 | 19:12 | 50.006
2022-10-25 | 19:12 | 50.006
2022-10-25 | 19:12 | 50.007
2022-10-25 | 19:12 | 50.009
2022-10-25 | 19:12 | 50.011
2022-10-25 | 19:12 | 50.014
2022-10-25 | 19:12 | 50.015
2022-10-25 | 19:12 | 50.016
2022-10-25 | 19:12 | 50.017
2022-10-25 | 19:12 | 50.019
2022-10-25 | 19:12 | 50.02
2022-10-25 | 19:12 | 50.021
2022-10-25 | 19:13 | 50.02
2022-10-25 | 19:13 | 50.019
2022-10-25 | 19:13 | 50.016
2022-10-25 | 19:13 | 50.013
2022-10-25 | 19:13 | 50.009
2022-10-25 | 19:13 | 50.005
2022-10-25 | 19:13 | 50.003
2022-10-25 | 19:13 | 50
2022-10-25 | 19:13 | 49.999
2022-10-25 | 19:13 | 49.998
2022-10-25 | 19:13 | 49.996
2022-10-25 | 19:13 | 49.995
2022-10-25 | 19:13 | 49.991
2022-10-25 | 19:13 | 49.991
2022-10-25 | 19:13 | 49.987
2022-10-25 | 19:13 | 49.985
2022-10-25 | 19:13 | 49.981
2022-10-25 | 19:13 | 49.982
2022-10-25 | 19:13 | 49.982
2022-10-25 | 19:13 | 49.985
2022-10-25 | 19:13 | 49.989
2022-10-25 | 19:13 | 49.991
2022-10-25 | 19:13 | 49.995
2022-10-25 | 19:13 | 50
2022-10-25 | 19:13 | 50.004
2022-10-25 | 19:13 | 50.007
2022-10-25 | 19:13 | 50.01
2022-10-25 | 19:13 | 50.011
2022-10-25 | 19:13 | 50.013
2022-10-25 | 19:13 | 50.013
2022-10-25 | 19:13 | 50.011
2022-10-25 | 19:13 | 50.012
2022-10-25 | 19:13 | 50.012
2022-10-25 | 19:13 | 50.013
2022-10-25 | 19:13 | 50.014
2022-10-25 | 19:13 | 50.015
2022-10-25 | 19:13 | 50.015
2022-10-25 | 19:13 | 50.015
2022-10-25 | 19:13 | 50.006
2022-10-25 | 19:13 | 49.995
2022-10-25 | 19:13 | 49.985
2022-10-25 | 19:13 | 49.973
2022-10-25 | 19:13 | 49.965
2022-10-25 | 19:13 | 49.956
2022-10-25 | 19:13 | 49.952
2022-10-25 | 19:13 | 49.95
2022-10-25 | 19:13 | 49.949
2022-10-25 | 19:13 | 49.95
2022-10-25 | 19:13 | 49.952
2022-10-25 | 19:13 | 49.953
2022-10-25 | 19:13 | 49.954
2022-10-25 | 19:13 | 49.955
2022-10-25 | 19:13 | 49.956
2022-10-25 | 19:13 | 49.956
2022-10-25 | 19:13 | 49.957
2022-10-25 | 19:13 | 49.957
2022-10-25 | 19:13 | 49.956
2022-10-25 | 19:13 | 49.958
2022-10-25 | 19:13 | 49.955
2022-10-25 | 19:14 | 49.956
2022-10-25 | 19:14 | 49.955
2022-10-25 | 19:14 | 49.952
2022-10-25 | 19:14 | 49.949
2022-10-25 | 19:14 | 49.946
2022-10-25 | 19:14 | 49.943
2022-10-25 | 19:14 | 49.94
2022-10-25 | 19:14 | 49.939
2022-10-25 | 19:14 | 49.938
2022-10-25 | 19:14 | 49.937
2022-10-25 | 19:14 | 49.939
2022-10-25 | 19:14 | 49.942
2022-10-25 | 19:14 | 49.945
2022-10-25 | 19:14 | 49.948
2022-10-25 | 19:14 | 49.953
2022-10-25 | 19:14 | 49.955
2022-10-25 | 19:14 | 49.958
2022-10-25 | 19:14 | 49.96
2022-10-25 | 19:14 | 49.959
2022-10-25 | 19:14 | 49.957
2022-10-25 | 19:14 | 49.957
2022-10-25 | 19:14 | 49.956
2022-10-25 | 19:14 | 49.955
2022-10-25 | 19:14 | 49.955
2022-10-25 | 19:14 | 49.955
2022-10-25 | 19:14 | 49.955
2022-10-25 | 19:14 | 49.955
2022-10-25 | 19:14 | 49.955
2022-10-25 | 19:14 | 49.956
2022-10-25 | 19:14 | 49.956
2022-10-25 | 19:14 | 49.958
2022-10-25 | 19:14 | 49.957
2022-10-25 | 19:14 | 49.957
2022-10-25 | 19:14 | 49.956
2022-10-25 | 19:14 | 49.956
2022-10-25 | 19:14 | 49.957
2022-10-25 | 19:14 | 49.957
2022-10-25 | 19:14 | 49.958
2022-10-25 | 19:14 | 49.956
2022-10-25 | 19:14 | 49.955
2022-10-25 | 19:14 | 49.955
2022-10-25 | 19:14 | 49.953
2022-10-25 | 19:14 | 49.952
2022-10-25 | 19:14 | 49.95
2022-10-25 | 19:14 | 49.947
2022-10-25 | 19:14 | 49.944
2022-10-25 | 19:14 | 49.943
2022-10-25 | 19:14 | 49.942
2022-10-25 | 19:14 | 49.94
2022-10-25 | 19:14 | 49.938
2022-10-25 | 19:14 | 49.937
2022-10-25 | 19:14 | 49.937
2022-10-25 | 19:14 | 49.939
2022-10-25 | 19:14 | 49.94
2022-10-25 | 19:14 | 49.94
2022-10-25 | 19:14 | 49.942
2022-10-25 | 19:14 | 49.945
2022-10-25 | 19:14 | 49.947
2022-10-25 | 19:14 | 49.95
2022-10-25 | 19:14 | 49.952
2022-10-25 | 19:14 | 49.951
2022-10-25 | 19:15 | 49.952
2022-10-25 | 19:15 | 49.951
2022-10-25 | 19:15 | 49.949
2022-10-25 | 19:15 | 49.946
2022-10-25 | 19:15 | 49.944
2022-10-25 | 19:15 | 49.944
2022-10-25 | 19:15 | 49.946
2022-10-25 | 19:15 | 49.947
2022-10-25 | 19:15 | 49.95
2022-10-25 | 19:15 | 49.953
2022-10-25 | 19:15 | 49.957
2022-10-25 | 19:15 | 49.962
2022-10-25 | 19:15 | 49.965
2022-10-25 | 19:15 | 49.969
2022-10-25 | 19:15 | 49.973
2022-10-25 | 19:15 | 49.975
2022-10-25 | 19:15 | 49.976
2022-10-25 | 19:15 | 49.977
2022-10-25 | 19:15 | 49.98
2022-10-25 | 19:15 | 49.983
2022-10-25 | 19:15 | 49.987
2022-10-25 | 19:15 | 49.988
2022-10-25 | 19:15 | 49.991
2022-10-25 | 19:15 | 49.993
2022-10-25 | 19:15 | 49.994
2022-10-25 | 19:15 | 49.994
2022-10-25 | 19:15 | 49.991
2022-10-25 | 19:15 | 49.989
2022-10-25 | 19:15 | 49.986
2022-10-25 | 19:15 | 49.984
2022-10-25 | 19:15 | 49.979
2022-10-25 | 19:15 | 49.978
2022-10-25 | 19:15 | 49.978
2022-10-25 | 19:15 | 49.98
2022-10-25 | 19:15 | 49.981
2022-10-25 | 19:15 | 49.98
2022-10-25 | 19:15 | 49.98
2022-10-25 | 19:15 | 49.98
2022-10-25 | 19:15 | 49.98
2022-10-25 | 19:15 | 49.979
2022-10-25 | 19:15 | 49.976
2022-10-25 | 19:15 | 49.976
2022-10-25 | 19:15 | 49.972
2022-10-25 | 19:15 | 49.971
2022-10-25 | 19:15 | 49.969
2022-10-25 | 19:15 | 49.967
2022-10-25 | 19:15 | 49.965
2022-10-25 | 19:15 | 49.962
2022-10-25 | 19:15 | 49.959
2022-10-25 | 19:15 | 49.957
2022-10-25 | 19:15 | 49.955
2022-10-25 | 19:15 | 49.956
2022-10-25 | 19:15 | 49.957
2022-10-25 | 19:15 | 49.958
2022-10-25 | 19:15 | 49.959
2022-10-25 | 19:15 | 49.961
2022-10-25 | 19:15 | 49.963
2022-10-25 | 19:15 | 49.965
2022-10-25 | 19:15 | 49.967
2022-10-25 | 19:16 | 49.968
2022-10-25 | 19:16 | 49.969
2022-10-25 | 19:16 | 49.969
2022-10-25 | 19:16 | 49.967
2022-10-25 | 19:16 | 49.965
2022-10-25 | 19:16 | 49.963
2022-10-25 | 19:16 | 49.964
2022-10-25 | 19:16 | 49.967
2022-10-25 | 19:16 | 49.968
2022-10-25 | 19:16 | 49.971
2022-10-25 | 19:16 | 49.971
2022-10-25 | 19:16 | 49.97
2022-10-25 | 19:16 | 49.97
2022-10-25 | 19:16 | 49.968
2022-10-25 | 19:16 | 49.969
2022-10-25 | 19:16 | 49.97
2022-10-25 | 19:16 | 49.971
2022-10-25 | 19:16 | 49.971
2022-10-25 | 19:16 | 49.972
2022-10-25 | 19:16 | 49.971
2022-10-25 | 19:16 | 49.972
2022-10-25 | 19:16 | 49.973
2022-10-25 | 19:16 | 49.976
2022-10-25 | 19:16 | 49.978
2022-10-25 | 19:16 | 49.979
2022-10-25 | 19:16 | 49.979
2022-10-25 | 19:16 | 49.978
2022-10-25 | 19:16 | 49.975
2022-10-25 | 19:16 | 49.973
2022-10-25 | 19:16 | 49.97
2022-10-25 | 19:16 | 49.967
2022-10-25 | 19:16 | 49.964
2022-10-25 | 19:16 | 49.964
2022-10-25 | 19:16 | 49.966
2022-10-25 | 19:16 | 49.969
2022-10-25 | 19:16 | 49.971
2022-10-25 | 19:16 | 49.972
2022-10-25 | 19:16 | 49.973
2022-10-25 | 19:16 | 49.976
2022-10-25 | 19:16 | 49.978
2022-10-25 | 19:16 | 49.981
2022-10-25 | 19:16 | 49.983
2022-10-25 | 19:16 | 49.984
2022-10-25 | 19:16 | 49.985
2022-10-25 | 19:16 | 49.986
2022-10-25 | 19:16 | 49.988
2022-10-25 | 19:16 | 49.988
2022-10-25 | 19:16 | 49.987
2022-10-25 | 19:16 | 49.988
2022-10-25 | 19:16 | 49.99
2022-10-25 | 19:16 | 49.989
2022-10-25 | 19:16 | 49.989
2022-10-25 | 19:16 | 49.991
2022-10-25 | 19:16 | 49.992
2022-10-25 | 19:16 | 49.992
2022-10-25 | 19:16 | 49.996
2022-10-25 | 19:16 | 50
2022-10-25 | 19:16 | 50.004
2022-10-25 | 19:16 | 50.011
2022-10-25 | 19:16 | 50.016
2022-10-25 | 19:16 | 50.021
2022-10-25 | 19:17 | 50.024
2022-10-25 | 19:17 | 50.028
2022-10-25 | 19:17 | 50.029
2022-10-25 | 19:17 | 50.033
2022-10-25 | 19:17 | 50.036
2022-10-25 | 19:17 | 50.036
2022-10-25 | 19:17 | 50.038
2022-10-25 | 19:17 | 50.038
2022-10-25 | 19:17 | 50.037
2022-10-25 | 19:17 | 50.035
2022-10-25 | 19:17 | 50.035
2022-10-25 | 19:17 | 50.036
2022-10-25 | 19:17 | 50.036
2022-10-25 | 19:17 | 50.037
2022-10-25 | 19:17 | 50.037
2022-10-25 | 19:17 | 50.036
2022-10-25 | 19:17 | 50.035
2022-10-25 | 19:17 | 50.036
2022-10-25 | 19:17 | 50.037
2022-10-25 | 19:17 | 50.039
2022-10-25 | 19:17 | 50.04
2022-10-25 | 19:17 | 50.042
2022-10-25 | 19:17 | 50.043
2022-10-25 | 19:17 | 50.044
2022-10-25 | 19:17 | 50.046
2022-10-25 | 19:17 | 50.046
2022-10-25 | 19:17 | 50.047
2022-10-25 | 19:17 | 50.046
2022-10-25 | 19:17 | 50.047
2022-10-25 | 19:17 | 50.047
2022-10-25 | 19:17 | 50.046
2022-10-25 | 19:17 | 50.043
2022-10-25 | 19:17 | 50.043
2022-10-25 | 19:17 | 50.044
2022-10-25 | 19:17 | 50.044
2022-10-25 | 19:17 | 50.045
2022-10-25 | 19:17 | 50.045
2022-10-25 | 19:17 | 50.044
2022-10-25 | 19:17 | 50.045
2022-10-25 | 19:17 | 50.043
2022-10-25 | 19:17 | 50.042
2022-10-25 | 19:17 | 50.042
2022-10-25 | 19:17 | 50.043
2022-10-25 | 19:17 | 50.045
2022-10-25 | 19:17 | 50.048
2022-10-25 | 19:17 | 50.049
2022-10-25 | 19:17 | 50.052
2022-10-25 | 19:17 | 50.054
2022-10-25 | 19:17 | 50.057
2022-10-25 | 19:17 | 50.06
2022-10-25 | 19:17 | 50.061
2022-10-25 | 19:17 | 50.063
2022-10-25 | 19:17 | 50.064
2022-10-25 | 19:17 | 50.064
2022-10-25 | 19:17 | 50.066
2022-10-25 | 19:17 | 50.069
2022-10-25 | 19:17 | 50.071
2022-10-25 | 19:17 | 50.073
2022-10-25 | 19:17 | 50.076
2022-10-25 | 19:18 | 50.077
2022-10-25 | 19:18 | 50.077
2022-10-25 | 19:18 | 50.077
2022-10-25 | 19:18 | 50.078
2022-10-25 | 19:18 | 50.078
2022-10-25 | 19:18 | 50.078
2022-10-25 | 19:18 | 50.077
2022-10-25 | 19:18 | 50.075
2022-10-25 | 19:18 | 50.072
2022-10-25 | 19:18 | 50.071
2022-10-25 | 19:18 | 50.068
2022-10-25 | 19:18 | 50.067
2022-10-25 | 19:18 | 50.064
2022-10-25 | 19:18 | 50.062
2022-10-25 | 19:18 | 50.06
2022-10-25 | 19:18 | 50.06
2022-10-25 | 19:18 | 50.06
2022-10-25 | 19:18 | 50.057
2022-10-25 | 19:18 | 50.058
2022-10-25 | 19:18 | 50.06
2022-10-25 | 19:18 | 50.062
2022-10-25 | 19:18 | 50.067
2022-10-25 | 19:18 | 50.068
2022-10-25 | 19:18 | 50.071
2022-10-25 | 19:18 | 50.072
2022-10-25 | 19:18 | 50.074
2022-10-25 | 19:18 | 50.075
2022-10-25 | 19:18 | 50.075
2022-10-25 | 19:18 | 50.078
2022-10-25 | 19:18 | 50.079
2022-10-25 | 19:18 | 50.082

## 20221028-1
In GMT
Date | Time | Freq
2022-10-28 | 7:38 | 50.085
2022-10-28 | 7:38 | 50.084
2022-10-28 | 7:38 | 50.084
2022-10-28 | 7:38 | 50.083
2022-10-28 | 7:38 | 50.079
2022-10-28 | 7:38 | 50.078
2022-10-28 | 7:38 | 50.08
2022-10-28 | 7:38 | 50.082
2022-10-28 | 7:38 | 50.083
2022-10-28 | 7:38 | 50.087
2022-10-28 | 7:38 | 50.087
2022-10-28 | 7:38 | 50.089
2022-10-28 | 7:38 | 50.092
2022-10-28 | 7:38 | 50.095
2022-10-28 | 7:38 | 50.098
2022-10-28 | 7:38 | 50.098
2022-10-28 | 7:38 | 50.098
2022-10-28 | 7:38 | 50.1
2022-10-28 | 7:38 | 50.102
2022-10-28 | 7:38 | 50.099
2022-10-28 | 7:38 | 50.098
2022-10-28 | 7:38 | 50.092
2022-10-28 | 7:38 | 50.088
2022-10-28 | 7:38 | 50.081
2022-10-28 | 7:38 | 50.078
2022-10-28 | 7:38 | 50.074
2022-10-28 | 7:38 | 50.073
2022-10-28 | 7:38 | 50.074
2022-10-28 | 7:38 | 50.077
2022-10-28 | 7:38 | 50.08
2022-10-28 | 7:39 | 50.08
2022-10-28 | 7:39 | 50.081
2022-10-28 | 7:39 | 50.08
2022-10-28 | 7:39 | 50.081
2022-10-28 | 7:39 | 50.079
2022-10-28 | 7:39 | 50.078
2022-10-28 | 7:39 | 50.079
2022-10-28 | 7:39 | 50.08
2022-10-28 | 7:39 | 50.081
2022-10-28 | 7:39 | 50.083
2022-10-28 | 7:39 | 50.083
2022-10-28 | 7:39 | 50.082
2022-10-28 | 7:39 | 50.08
2022-10-28 | 7:39 | 50.079
2022-10-28 | 7:39 | 50.081
2022-10-28 | 7:39 | 50.087
2022-10-28 | 7:39 | 50.092
2022-10-28 | 7:39 | 50.096
2022-10-28 | 7:39 | 50.099
2022-10-28 | 7:39 | 50.099
2022-10-28 | 7:39 | 50.096
2022-10-28 | 7:39 | 50.094
2022-10-28 | 7:39 | 50.089
2022-10-28 | 7:39 | 50.09
2022-10-28 | 7:39 | 50.089
2022-10-28 | 7:39 | 50.087
2022-10-28 | 7:39 | 50.084
2022-10-28 | 7:39 | 50.083
2022-10-28 | 7:39 | 50.081
2022-10-28 | 7:39 | 50.078
2022-10-28 | 7:39 | 50.074
2022-10-28 | 7:39 | 50.068
2022-10-28 | 7:39 | 50.031
2022-10-28 | 7:39 | 50.012
2022-10-28 | 7:39 | 50.001
2022-10-28 | 7:39 | 49.992
2022-10-28 | 7:39 | 49.987
2022-10-28 | 7:39 | 49.982
2022-10-28 | 7:39 | 49.981
2022-10-28 | 7:39 | 49.981
2022-10-28 | 7:39 | 49.982
2022-10-28 | 7:39 | 49.987
2022-10-28 | 7:39 | 49.99
2022-10-28 | 7:39 | 49.993
2022-10-28 | 7:39 | 49.993
2022-10-28 | 7:39 | 49.993
2022-10-28 | 7:39 | 49.991
2022-10-28 | 7:39 | 49.99
2022-10-28 | 7:39 | 49.988
2022-10-28 | 7:39 | 49.987
2022-10-28 | 7:39 | 49.984
2022-10-28 | 7:39 | 49.984
2022-10-28 | 7:39 | 49.981
2022-10-28 | 7:39 | 49.982
2022-10-28 | 7:39 | 49.981
2022-10-28 | 7:39 | 49.977
2022-10-28 | 7:39 | 49.976
2022-10-28 | 7:39 | 49.979
2022-10-28 | 7:39 | 49.979
2022-10-28 | 7:39 | 49.981
2022-10-28 | 7:39 | 49.983
2022-10-28 | 7:40 | 49.988
2022-10-28 | 7:40 | 49.991
2022-10-28 | 7:40 | 49.993
2022-10-28 | 7:40 | 49.993
2022-10-28 | 7:40 | 49.997
2022-10-28 | 7:40 | 50.001
2022-10-28 | 7:40 | 50
2022-10-28 | 7:40 | 50.003
2022-10-28 | 7:40 | 50.005
2022-10-28 | 7:40 | 50.006
2022-10-28 | 7:40 | 50.002
2022-10-28 | 7:40 | 50
2022-10-28 | 7:40 | 50.002
2022-10-28 | 7:40 | 49.998
2022-10-28 | 7:40 | 49.998
2022-10-28 | 7:40 | 49.994
2022-10-28 | 7:40 | 49.993
2022-10-28 | 7:40 | 49.991
2022-10-28 | 7:40 | 49.986
2022-10-28 | 7:40 | 49.98
2022-10-28 | 7:40 | 49.98
2022-10-28 | 7:40 | 49.977
2022-10-28 | 7:40 | 49.976
2022-10-28 | 7:40 | 49.978
2022-10-28 | 7:40 | 49.979
2022-10-28 | 7:40 | 49.978
2022-10-28 | 7:40 | 49.98
2022-10-28 | 7:40 | 49.98
2022-10-28 | 7:40 | 49.98
2022-10-28 | 7:40 | 49.982
2022-10-28 | 7:40 | 49.981
2022-10-28 | 7:40 | 49.984
2022-10-28 | 7:40 | 49.987
2022-10-28 | 7:40 | 49.989
2022-10-28 | 7:40 | 49.991
2022-10-28 | 7:40 | 49.994
2022-10-28 | 7:40 | 49.997
2022-10-28 | 7:40 | 49.999
2022-10-28 | 7:40 | 49.998
2022-10-28 | 7:40 | 49.997
2022-10-28 | 7:40 | 49.995
2022-10-28 | 7:40 | 49.991
2022-10-28 | 7:40 | 49.987
2022-10-28 | 7:40 | 49.984
2022-10-28 | 7:40 | 49.978
2022-10-28 | 7:40 | 49.972
2022-10-28 | 7:40 | 49.969
2022-10-28 | 7:40 | 49.969
2022-10-28 | 7:40 | 49.964
2022-10-28 | 7:40 | 49.96
2022-10-28 | 7:40 | 49.958
2022-10-28 | 7:40 | 49.958
2022-10-28 | 7:40 | 49.959
2022-10-28 | 7:40 | 49.961
2022-10-28 | 7:40 | 49.965
2022-10-28 | 7:40 | 49.969
2022-10-28 | 7:40 | 49.972
2022-10-28 | 7:40 | 49.973
2022-10-28 | 7:40 | 49.973
2022-10-28 | 7:41 | 49.973
2022-10-28 | 7:41 | 49.97
2022-10-28 | 7:41 | 49.969
2022-10-28 | 7:41 | 49.969
2022-10-28 | 7:41 | 49.966
2022-10-28 | 7:41 | 49.965
2022-10-28 | 7:41 | 49.965
2022-10-28 | 7:41 | 49.967
2022-10-28 | 7:41 | 49.967
2022-10-28 | 7:41 | 49.968
2022-10-28 | 7:41 | 49.967
2022-10-28 | 7:41 | 49.97
2022-10-28 | 7:41 | 49.973
2022-10-28 | 7:41 | 49.976
2022-10-28 | 7:41 | 49.979
2022-10-28 | 7:41 | 49.979
2022-10-28 | 7:41 | 49.98
2022-10-28 | 7:41 | 49.983
2022-10-28 | 7:41 | 49.982
2022-10-28 | 7:41 | 49.984
2022-10-28 | 7:41 | 49.984
2022-10-28 | 7:41 | 49.984
2022-10-28 | 7:41 | 49.983
2022-10-28 | 7:41 | 49.98
2022-10-28 | 7:41 | 49.976
2022-10-28 | 7:41 | 49.972
2022-10-28 | 7:41 | 49.971
2022-10-28 | 7:41 | 49.968
2022-10-28 | 7:41 | 49.963
2022-10-28 | 7:41 | 49.959
2022-10-28 | 7:41 | 49.957
2022-10-28 | 7:41 | 49.954
2022-10-28 | 7:41 | 49.953
2022-10-28 | 7:41 | 49.954
2022-10-28 | 7:41 | 49.954
2022-10-28 | 7:41 | 49.955
2022-10-28 | 7:41 | 49.951
2022-10-28 | 7:41 | 49.949
2022-10-28 | 7:41 | 49.946
2022-10-28 | 7:41 | 49.945
2022-10-28 | 7:41 | 49.947
2022-10-28 | 7:41 | 49.946
2022-10-28 | 7:41 | 49.949
2022-10-28 | 7:41 | 49.947
2022-10-28 | 7:41 | 49.947
2022-10-28 | 7:41 | 49.951
2022-10-28 | 7:41 | 49.957
2022-10-28 | 7:41 | 49.965
2022-10-28 | 7:41 | 49.967
2022-10-28 | 7:41 | 49.971
2022-10-28 | 7:41 | 49.972
2022-10-28 | 7:41 | 49.973
2022-10-28 | 7:41 | 49.975
2022-10-28 | 7:41 | 49.979
2022-10-28 | 7:41 | 49.982
2022-10-28 | 7:41 | 49.983
2022-10-28 | 7:41 | 49.983
2022-10-28 | 7:41 | 49.981
2022-10-28 | 7:41 | 49.979
2022-10-28 | 7:41 | 49.978
2022-10-28 | 7:41 | 49.973
2022-10-28 | 7:42 | 49.972
2022-10-28 | 7:42 | 49.97
2022-10-28 | 7:42 | 49.971
2022-10-28 | 7:42 | 49.972
2022-10-28 | 7:42 | 49.972
2022-10-28 | 7:42 | 49.972
2022-10-28 | 7:42 | 49.971
2022-10-28 | 7:42 | 49.975
2022-10-28 | 7:42 | 49.975
2022-10-28 | 7:42 | 49.974
2022-10-28 | 7:42 | 49.973
2022-10-28 | 7:42 | 49.972
2022-10-28 | 7:42 | 49.977
2022-10-28 | 7:42 | 49.977
2022-10-28 | 7:42 | 49.977
2022-10-28 | 7:42 | 49.976
2022-10-28 | 7:42 | 49.975
2022-10-28 | 7:42 | 49.971
2022-10-28 | 7:42 | 49.965
2022-10-28 | 7:42 | 49.961
2022-10-28 | 7:42 | 49.956
2022-10-28 | 7:42 | 49.952
2022-10-28 | 7:42 | 49.948
2022-10-28 | 7:42 | 49.945
2022-10-28 | 7:42 | 49.945
2022-10-28 | 7:42 | 49.947
2022-10-28 | 7:42 | 49.949
2022-10-28 | 7:42 | 49.95
2022-10-28 | 7:42 | 49.954
2022-10-28 | 7:42 | 49.955
2022-10-28 | 7:42 | 49.957
2022-10-28 | 7:42 | 49.958
2022-10-28 | 7:42 | 49.957
2022-10-28 | 7:42 | 49.956
2022-10-28 | 7:42 | 49.951
2022-10-28 | 7:42 | 49.95
2022-10-28 | 7:42 | 49.952
2022-10-28 | 7:42 | 49.953
2022-10-28 | 7:42 | 49.954
2022-10-28 | 7:42 | 49.955
2022-10-28 | 7:42 | 49.954
2022-10-28 | 7:42 | 49.954
2022-10-28 | 7:42 | 49.954
2022-10-28 | 7:42 | 49.954
2022-10-28 | 7:42 | 49.949
2022-10-28 | 7:42 | 49.945
2022-10-28 | 7:42 | 49.936
2022-10-28 | 7:42 | 49.932
2022-10-28 | 7:42 | 49.926
2022-10-28 | 7:42 | 49.921
2022-10-28 | 7:42 | 49.921
2022-10-28 | 7:42 | 49.923
2022-10-28 | 7:42 | 49.924
2022-10-28 | 7:42 | 49.925
2022-10-28 | 7:42 | 49.928
2022-10-28 | 7:42 | 49.929
2022-10-28 | 7:42 | 49.93
2022-10-28 | 7:42 | 49.932
2022-10-28 | 7:42 | 49.931
2022-10-28 | 7:43 | 49.933
2022-10-28 | 7:43 | 49.934
2022-10-28 | 7:43 | 49.933
2022-10-28 | 7:43 | 49.933
2022-10-28 | 7:43 | 49.93
2022-10-28 | 7:43 | 49.925
2022-10-28 | 7:43 | 49.924
2022-10-28 | 7:43 | 49.919
2022-10-28 | 7:43 | 49.915
2022-10-28 | 7:43 | 49.914
2022-10-28 | 7:43 | 49.911
2022-10-28 | 7:43 | 49.911
2022-10-28 | 7:43 | 49.912
2022-10-28 | 7:43 | 49.91
2022-10-28 | 7:43 | 49.91
2022-10-28 | 7:43 | 49.909
2022-10-28 | 7:43 | 49.91
2022-10-28 | 7:43 | 49.908
2022-10-28 | 7:43 | 49.91
2022-10-28 | 7:43 | 49.91
2022-10-28 | 7:43 | 49.913
2022-10-28 | 7:43 | 49.915
2022-10-28 | 7:43 | 49.919
2022-10-28 | 7:43 | 49.921
2022-10-28 | 7:43 | 49.924
2022-10-28 | 7:43 | 49.926
2022-10-28 | 7:43 | 49.925
2022-10-28 | 7:43 | 49.926
2022-10-28 | 7:43 | 49.928
2022-10-28 | 7:43 | 49.927
2022-10-28 | 7:43 | 49.927
2022-10-28 | 7:43 | 49.924
2022-10-28 | 7:43 | 49.92
2022-10-28 | 7:43 | 49.915
2022-10-28 | 7:43 | 49.911
2022-10-28 | 7:43 | 49.911
2022-10-28 | 7:43 | 49.911
2022-10-28 | 7:43 | 49.912
2022-10-28 | 7:43 | 49.915
2022-10-28 | 7:43 | 49.918
2022-10-28 | 7:43 | 49.92
2022-10-28 | 7:43 | 49.924
2022-10-28 | 7:43 | 49.927
2022-10-28 | 7:43 | 49.928
2022-10-28 | 7:43 | 49.928
2022-10-28 | 7:43 | 49.926
2022-10-28 | 7:43 | 49.927
2022-10-28 | 7:43 | 49.93
2022-10-28 | 7:43 | 49.933
2022-10-28 | 7:43 | 49.935
2022-10-28 | 7:43 | 49.938
2022-10-28 | 7:43 | 49.942
2022-10-28 | 7:43 | 49.945
2022-10-28 | 7:43 | 49.945
2022-10-28 | 7:43 | 49.947
2022-10-28 | 7:43 | 49.948
2022-10-28 | 7:43 | 49.946
2022-10-28 | 7:43 | 49.943
2022-10-28 | 7:43 | 49.943
2022-10-28 | 7:43 | 49.945
2022-10-28 | 7:44 | 49.943
2022-10-28 | 7:44 | 49.943
2022-10-28 | 7:44 | 49.944
2022-10-28 | 7:44 | 49.945
2022-10-28 | 7:44 | 49.946
2022-10-28 | 7:44 | 49.945
2022-10-28 | 7:44 | 49.942
2022-10-28 | 7:44 | 49.941
2022-10-28 | 7:44 | 49.939
2022-10-28 | 7:44 | 49.938
2022-10-28 | 7:44 | 49.941
2022-10-28 | 7:44 | 49.939
2022-10-28 | 7:44 | 49.94
2022-10-28 | 7:44 | 49.941
2022-10-28 | 7:44 | 49.942
2022-10-28 | 7:44 | 49.94
2022-10-28 | 7:44 | 49.942
2022-10-28 | 7:44 | 49.944
2022-10-28 | 7:44 | 49.945
2022-10-28 | 7:44 | 49.945
2022-10-28 | 7:44 | 49.945
2022-10-28 | 7:44 | 49.947
2022-10-28 | 7:44 | 49.944
2022-10-28 | 7:44 | 49.94
2022-10-28 | 7:44 | 49.936
2022-10-28 | 7:44 | 49.933
2022-10-28 | 7:44 | 49.932
2022-10-28 | 7:44 | 49.93
2022-10-28 | 7:44 | 49.929
2022-10-28 | 7:44 | 49.927
2022-10-28 | 7:44 | 49.925
2022-10-28 | 7:44 | 49.921
2022-10-28 | 7:44 | 49.917
2022-10-28 | 7:44 | 49.912
2022-10-28 | 7:44 | 49.911
2022-10-28 | 7:44 | 49.91
2022-10-28 | 7:44 | 49.911
2022-10-28 | 7:44 | 49.914
2022-10-28 | 7:44 | 49.916
2022-10-28 | 7:44 | 49.919
2022-10-28 | 7:44 | 49.924
2022-10-28 | 7:44 | 49.932
2022-10-28 | 7:44 | 49.939
2022-10-28 | 7:44 | 49.946
2022-10-28 | 7:44 | 49.954
2022-10-28 | 7:44 | 49.959
2022-10-28 | 7:44 | 49.963
2022-10-28 | 7:44 | 49.963
2022-10-28 | 7:44 | 49.962
2022-10-28 | 7:44 | 49.963
2022-10-28 | 7:44 | 49.966
2022-10-28 | 7:44 | 49.969
2022-10-28 | 7:44 | 49.975
2022-10-28 | 7:44 | 49.976
2022-10-28 | 7:44 | 49.977
2022-10-28 | 7:44 | 49.981
2022-10-28 | 7:44 | 49.987
2022-10-28 | 7:44 | 49.987
2022-10-28 | 7:44 | 49.984
2022-10-28 | 7:44 | 49.983
2022-10-28 | 7:44 | 49.981
2022-10-28 | 7:45 | 49.979
2022-10-28 | 7:45 | 49.98
2022-10-28 | 7:45 | 49.979
2022-10-28 | 7:45 | 49.977
2022-10-28 | 7:45 | 49.978
2022-10-28 | 7:45 | 49.979
2022-10-28 | 7:45 | 49.979
2022-10-28 | 7:45 | 49.979
2022-10-28 | 7:45 | 49.978
2022-10-28 | 7:45 | 49.978
2022-10-28 | 7:45 | 49.979
2022-10-28 | 7:45 | 49.979
2022-10-28 | 7:45 | 49.977
2022-10-28 | 7:45 | 49.975
2022-10-28 | 7:45 | 49.972
2022-10-28 | 7:45 | 49.969
2022-10-28 | 7:45 | 49.965
2022-10-28 | 7:45 | 49.961
2022-10-28 | 7:45 | 49.958
2022-10-28 | 7:45 | 49.956
2022-10-28 | 7:45 | 49.955
2022-10-28 | 7:45 | 49.954
2022-10-28 | 7:45 | 49.955
2022-10-28 | 7:45 | 49.954
2022-10-28 | 7:45 | 49.957
2022-10-28 | 7:45 | 49.959
2022-10-28 | 7:45 | 49.962
2022-10-28 | 7:45 | 49.961
2022-10-28 | 7:45 | 49.96
2022-10-28 | 7:45 | 49.963
2022-10-28 | 7:45 | 49.963
2022-10-28 | 7:45 | 49.962
2022-10-28 | 7:45 | 49.961
2022-10-28 | 7:45 | 49.959
2022-10-28 | 7:45 | 49.96
2022-10-28 | 7:45 | 49.959
2022-10-28 | 7:45 | 49.96
2022-10-28 | 7:45 | 49.959
2022-10-28 | 7:45 | 49.957
2022-10-28 | 7:45 | 49.957
2022-10-28 | 7:45 | 49.956
2022-10-28 | 7:45 | 49.955
2022-10-28 | 7:45 | 49.955
2022-10-28 | 7:45 | 49.953
2022-10-28 | 7:45 | 49.954
2022-10-28 | 7:45 | 49.952
2022-10-28 | 7:45 | 49.953
2022-10-28 | 7:45 | 49.955
2022-10-28 | 7:45 | 49.956
2022-10-28 | 7:45 | 49.956
2022-10-28 | 7:45 | 49.957
2022-10-28 | 7:45 | 49.954
2022-10-28 | 7:45 | 49.957
2022-10-28 | 7:45 | 49.958
2022-10-28 | 7:45 | 49.96
2022-10-28 | 7:45 | 49.963
2022-10-28 | 7:45 | 49.964
2022-10-28 | 7:45 | 49.969
2022-10-28 | 7:45 | 49.968
2022-10-28 | 7:46 | 49.969
2022-10-28 | 7:46 | 49.968
2022-10-28 | 7:46 | 49.967
2022-10-28 | 7:46 | 49.968
2022-10-28 | 7:46 | 49.964
2022-10-28 | 7:46 | 49.966
2022-10-28 | 7:46 | 49.967
2022-10-28 | 7:46 | 49.966
2022-10-28 | 7:46 | 49.968
2022-10-28 | 7:46 | 49.969
2022-10-28 | 7:46 | 49.973
2022-10-28 | 7:46 | 49.977
2022-10-28 | 7:46 | 49.979
2022-10-28 | 7:46 | 49.982
2022-10-28 | 7:46 | 49.987
2022-10-28 | 7:46 | 49.989
2022-10-28 | 7:46 | 49.991
2022-10-28 | 7:46 | 49.993
2022-10-28 | 7:46 | 49.993
2022-10-28 | 7:46 | 49.993
2022-10-28 | 7:46 | 49.993
2022-10-28 | 7:46 | 49.988
2022-10-28 | 7:46 | 49.984
2022-10-28 | 7:46 | 49.976
2022-10-28 | 7:46 | 49.968
2022-10-28 | 7:46 | 49.966
2022-10-28 | 7:46 | 49.96
2022-10-28 | 7:46 | 49.954
2022-10-28 | 7:46 | 49.951
2022-10-28 | 7:46 | 49.945
2022-10-28 | 7:46 | 49.942
2022-10-28 | 7:46 | 49.944
2022-10-28 | 7:46 | 49.944
2022-10-28 | 7:46 | 49.946
2022-10-28 | 7:46 | 49.947
2022-10-28 | 7:46 | 49.945
2022-10-28 | 7:46 | 49.946
2022-10-28 | 7:46 | 49.945
2022-10-28 | 7:46 | 49.942
2022-10-28 | 7:46 | 49.938
2022-10-28 | 7:46 | 49.937
2022-10-28 | 7:46 | 49.937
2022-10-28 | 7:46 | 49.936
2022-10-28 | 7:46 | 49.936
2022-10-28 | 7:46 | 49.931
2022-10-28 | 7:46 | 49.93
2022-10-28 | 7:46 | 49.927
2022-10-28 | 7:46 | 49.924
2022-10-28 | 7:46 | 49.923
2022-10-28 | 7:46 | 49.921
2022-10-28 | 7:46 | 49.92
2022-10-28 | 7:46 | 49.919
2022-10-28 | 7:46 | 49.919
2022-10-28 | 7:46 | 49.92
2022-10-28 | 7:46 | 49.919
2022-10-28 | 7:46 | 49.92
2022-10-28 | 7:46 | 49.922
2022-10-28 | 7:46 | 49.923
2022-10-28 | 7:46 | 49.923
2022-10-28 | 7:46 | 49.92
2022-10-28 | 7:46 | 49.922
2022-10-28 | 7:47 | 49.922
2022-10-28 | 7:47 | 49.921
2022-10-28 | 7:47 | 49.922
2022-10-28 | 7:47 | 49.924
2022-10-28 | 7:47 | 49.921
2022-10-28 | 7:47 | 49.919
2022-10-28 | 7:47 | 49.914
2022-10-28 | 7:47 | 49.911
2022-10-28 | 7:47 | 49.905
2022-10-28 | 7:47 | 49.899
2022-10-28 | 7:47 | 49.897
2022-10-28 | 7:47 | 49.895
2022-10-28 | 7:47 | 49.893
2022-10-28 | 7:47 | 49.896
2022-10-28 | 7:47 | 49.898
2022-10-28 | 7:47 | 49.904
2022-10-28 | 7:47 | 49.906
2022-10-28 | 7:47 | 49.911
2022-10-28 | 7:47 | 49.912
2022-10-28 | 7:47 | 49.912
2022-10-28 | 7:47 | 49.915
2022-10-28 | 7:47 | 49.915
2022-10-28 | 7:47 | 49.92
2022-10-28 | 7:47 | 49.923
2022-10-28 | 7:47 | 49.926
2022-10-28 | 7:47 | 49.93
2022-10-28 | 7:47 | 49.933
2022-10-28 | 7:47 | 49.933
2022-10-28 | 7:47 | 49.937
2022-10-28 | 7:47 | 49.937
2022-10-28 | 7:47 | 49.939
2022-10-28 | 7:47 | 49.937
2022-10-28 | 7:47 | 49.937
2022-10-28 | 7:47 | 49.934
2022-10-28 | 7:47 | 49.933
2022-10-28 | 7:47 | 49.929
2022-10-28 | 7:47 | 49.926
2022-10-28 | 7:47 | 49.925
2022-10-28 | 7:47 | 49.925
2022-10-28 | 7:47 | 49.926
2022-10-28 | 7:47 | 49.928
2022-10-28 | 7:47 | 49.931
2022-10-28 | 7:47 | 49.932
2022-10-28 | 7:47 | 49.927
2022-10-28 | 7:47 | 49.927
2022-10-28 | 7:47 | 49.924
2022-10-28 | 7:47 | 49.924
2022-10-28 | 7:47 | 49.92
2022-10-28 | 7:47 | 49.917
2022-10-28 | 7:47 | 49.914
2022-10-28 | 7:47 | 49.914
2022-10-28 | 7:47 | 49.914
2022-10-28 | 7:47 | 49.913
2022-10-28 | 7:47 | 49.916
2022-10-28 | 7:47 | 49.915
2022-10-28 | 7:47 | 49.914
2022-10-28 | 7:47 | 49.915
2022-10-28 | 7:47 | 49.915
2022-10-28 | 7:47 | 49.916
2022-10-28 | 7:48 | 49.919
2022-10-28 | 7:48 | 49.92
2022-10-28 | 7:48 | 49.923
2022-10-28 | 7:48 | 49.926
2022-10-28 | 7:48 | 49.926
2022-10-28 | 7:48 | 49.927
2022-10-28 | 7:48 | 49.931
2022-10-28 | 7:48 | 49.934
2022-10-28 | 7:48 | 49.934
2022-10-28 | 7:48 | 49.932
2022-10-28 | 7:48 | 49.931
2022-10-28 | 7:48 | 49.928
2022-10-28 | 7:48 | 49.927
2022-10-28 | 7:48 | 49.924
2022-10-28 | 7:48 | 49.919
2022-10-28 | 7:48 | 49.914
2022-10-28 | 7:48 | 49.912
2022-10-28 | 7:48 | 49.91
2022-10-28 | 7:48 | 49.91
2022-10-28 | 7:48 | 49.914
2022-10-28 | 7:48 | 49.921
2022-10-28 | 7:48 | 49.925
2022-10-28 | 7:48 | 49.931
2022-10-28 | 7:48 | 49.933
2022-10-28 | 7:48 | 49.935
2022-10-28 | 7:48 | 49.937
2022-10-28 | 7:48 | 49.939
2022-10-28 | 7:48 | 49.939
2022-10-28 | 7:48 | 49.938
2022-10-28 | 7:48 | 49.938
2022-10-28 | 7:48 | 49.933

## 20221030-1
In GMT
Date | Time | Freq
2022-10-30 | 20:29 | 50.043
2022-10-30 | 20:29 | 50.044
2022-10-30 | 20:29 | 50.044
2022-10-30 | 20:29 | 50.044
2022-10-30 | 20:29 | 50.048
2022-10-30 | 20:29 | 50.051
2022-10-30 | 20:29 | 50.057
2022-10-30 | 20:29 | 50.063
2022-10-30 | 20:29 | 50.067
2022-10-30 | 20:29 | 50.071
2022-10-30 | 20:29 | 50.072
2022-10-30 | 20:29 | 50.074
2022-10-30 | 20:29 | 50.073
2022-10-30 | 20:29 | 50.074
2022-10-30 | 20:29 | 50.075
2022-10-30 | 20:29 | 50.076
2022-10-30 | 20:29 | 50.078
2022-10-30 | 20:29 | 50.081
2022-10-30 | 20:29 | 50.081
2022-10-30 | 20:29 | 50.079
2022-10-30 | 20:29 | 50.076
2022-10-30 | 20:29 | 50.072
2022-10-30 | 20:29 | 50.068
2022-10-30 | 20:29 | 50.066
2022-10-30 | 20:29 | 50.067
2022-10-30 | 20:29 | 50.069
2022-10-30 | 20:29 | 50.071
2022-10-30 | 20:29 | 50.075
2022-10-30 | 20:29 | 50.078
2022-10-30 | 20:29 | 50.077
2022-10-30 | 20:30 | 50.074
2022-10-30 | 20:30 | 50.069
2022-10-30 | 20:30 | 50.064
2022-10-30 | 20:30 | 50.061
2022-10-30 | 20:30 | 50.058
2022-10-30 | 20:30 | 50.055
2022-10-30 | 20:30 | 50.052
2022-10-30 | 20:30 | 50.05
2022-10-30 | 20:30 | 50.047
2022-10-30 | 20:30 | 50.042
2022-10-30 | 20:30 | 50.04
2022-10-30 | 20:30 | 50.04
2022-10-30 | 20:30 | 50.039
2022-10-30 | 20:30 | 50.037
2022-10-30 | 20:30 | 50.038
2022-10-30 | 20:30 | 50.038
2022-10-30 | 20:30 | 50.038
2022-10-30 | 20:30 | 50.035
2022-10-30 | 20:30 | 50.028
2022-10-30 | 20:30 | 50.02
2022-10-30 | 20:30 | 50.014
2022-10-30 | 20:30 | 50.004
2022-10-30 | 20:30 | 49.994
2022-10-30 | 20:30 | 49.985
2022-10-30 | 20:30 | 49.976
2022-10-30 | 20:30 | 49.967
2022-10-30 | 20:30 | 49.956
2022-10-30 | 20:30 | 49.946
2022-10-30 | 20:30 | 49.934
2022-10-30 | 20:30 | 49.92
2022-10-30 | 20:30 | 49.904
2022-10-30 | 20:30 | 49.894
2022-10-30 | 20:30 | 49.888
2022-10-30 | 20:30 | 49.883
2022-10-30 | 20:30 | 49.877
2022-10-30 | 20:30 | 49.877
2022-10-30 | 20:30 | 49.876
2022-10-30 | 20:30 | 49.876
2022-10-30 | 20:30 | 49.876
2022-10-30 | 20:30 | 49.876
2022-10-30 | 20:30 | 49.875
2022-10-30 | 20:30 | 49.871
2022-10-30 | 20:30 | 49.871
2022-10-30 | 20:30 | 49.869
2022-10-30 | 20:30 | 49.869
2022-10-30 | 20:30 | 49.87
2022-10-30 | 20:30 | 49.87
2022-10-30 | 20:30 | 49.866
2022-10-30 | 20:30 | 49.86
2022-10-30 | 20:30 | 49.856
2022-10-30 | 20:30 | 49.852
2022-10-30 | 20:30 | 49.849
2022-10-30 | 20:30 | 49.848
2022-10-30 | 20:30 | 49.847
2022-10-30 | 20:30 | 49.844
2022-10-30 | 20:30 | 49.844
2022-10-30 | 20:30 | 49.842
2022-10-30 | 20:30 | 49.838
2022-10-30 | 20:30 | 49.836
2022-10-30 | 20:30 | 49.837
2022-10-30 | 20:31 | 49.838
2022-10-30 | 20:31 | 49.838
2022-10-30 | 20:31 | 49.836
2022-10-30 | 20:31 | 49.834
2022-10-30 | 20:31 | 49.831
2022-10-30 | 20:31 | 49.83
2022-10-30 | 20:31 | 49.83
2022-10-30 | 20:31 | 49.829
2022-10-30 | 20:31 | 49.825
2022-10-30 | 20:31 | 49.823
2022-10-30 | 20:31 | 49.823
2022-10-30 | 20:31 | 49.821
2022-10-30 | 20:31 | 49.822
2022-10-30 | 20:31 | 49.821
2022-10-30 | 20:31 | 49.82
2022-10-30 | 20:31 | 49.816
2022-10-30 | 20:31 | 49.814
2022-10-30 | 20:31 | 49.813
2022-10-30 | 20:31 | 49.81
2022-10-30 | 20:31 | 49.81
2022-10-30 | 20:31 | 49.809
2022-10-30 | 20:31 | 49.807
2022-10-30 | 20:31 | 49.804
2022-10-30 | 20:31 | 49.8
2022-10-30 | 20:31 | 49.797
2022-10-30 | 20:31 | 49.791
2022-10-30 | 20:31 | 49.789
2022-10-30 | 20:31 | 49.787
2022-10-30 | 20:31 | 49.787
2022-10-30 | 20:31 | 49.787
2022-10-30 | 20:31 | 49.785
2022-10-30 | 20:31 | 49.781
2022-10-30 | 20:31 | 49.78
2022-10-30 | 20:31 | 49.779
2022-10-30 | 20:31 | 49.779
2022-10-30 | 20:31 | 49.778
2022-10-30 | 20:31 | 49.779
2022-10-30 | 20:31 | 49.78
2022-10-30 | 20:31 | 49.782
2022-10-30 | 20:31 | 49.787
2022-10-30 | 20:31 | 49.794
2022-10-30 | 20:31 | 49.799
2022-10-30 | 20:31 | 49.803
2022-10-30 | 20:31 | 49.806
2022-10-30 | 20:31 | 49.809
2022-10-30 | 20:31 | 49.813
2022-10-30 | 20:31 | 49.816
2022-10-30 | 20:31 | 49.819
2022-10-30 | 20:31 | 49.821
2022-10-30 | 20:31 | 49.821
2022-10-30 | 20:31 | 49.824
2022-10-30 | 20:31 | 49.827
2022-10-30 | 20:31 | 49.828
2022-10-30 | 20:31 | 49.827
2022-10-30 | 20:31 | 49.827
2022-10-30 | 20:31 | 49.826
2022-10-30 | 20:31 | 49.824
2022-10-30 | 20:31 | 49.82
2022-10-30 | 20:31 | 49.813
2022-10-30 | 20:31 | 49.81
2022-10-30 | 20:31 | 49.809
2022-10-30 | 20:32 | 49.81
2022-10-30 | 20:32 | 49.811
2022-10-30 | 20:32 | 49.81
2022-10-30 | 20:32 | 49.812
2022-10-30 | 20:32 | 49.812
2022-10-30 | 20:32 | 49.809
2022-10-30 | 20:32 | 49.807
2022-10-30 | 20:32 | 49.806
2022-10-30 | 20:32 | 49.804
2022-10-30 | 20:32 | 49.802
2022-10-30 | 20:32 | 49.801
2022-10-30 | 20:32 | 49.8
2022-10-30 | 20:32 | 49.801
2022-10-30 | 20:32 | 49.803
2022-10-30 | 20:32 | 49.804
2022-10-30 | 20:32 | 49.805
2022-10-30 | 20:32 | 49.807
2022-10-30 | 20:32 | 49.807
2022-10-30 | 20:32 | 49.808
2022-10-30 | 20:32 | 49.809
2022-10-30 | 20:32 | 49.812
2022-10-30 | 20:32 | 49.815
2022-10-30 | 20:32 | 49.815
2022-10-30 | 20:32 | 49.815
2022-10-30 | 20:32 | 49.817
2022-10-30 | 20:32 | 49.814
2022-10-30 | 20:32 | 49.812
2022-10-30 | 20:32 | 49.808
2022-10-30 | 20:32 | 49.801
2022-10-30 | 20:32 | 49.795
2022-10-30 | 20:32 | 49.792
2022-10-30 | 20:32 | 49.789
2022-10-30 | 20:32 | 49.79
2022-10-30 | 20:32 | 49.79
2022-10-30 | 20:32 | 49.79
2022-10-30 | 20:32 | 49.792
2022-10-30 | 20:32 | 49.793
2022-10-30 | 20:32 | 49.797
2022-10-30 | 20:32 | 49.801
2022-10-30 | 20:32 | 49.805
2022-10-30 | 20:32 | 49.813
2022-10-30 | 20:32 | 49.818
2022-10-30 | 20:32 | 49.826
2022-10-30 | 20:32 | 49.832
2022-10-30 | 20:32 | 49.837
2022-10-30 | 20:32 | 49.844
2022-10-30 | 20:32 | 49.849
2022-10-30 | 20:32 | 49.858
2022-10-30 | 20:32 | 49.864
2022-10-30 | 20:32 | 49.872
2022-10-30 | 20:32 | 49.877
2022-10-30 | 20:32 | 49.879
2022-10-30 | 20:32 | 49.879
2022-10-30 | 20:32 | 49.876
2022-10-30 | 20:32 | 49.877
2022-10-30 | 20:32 | 49.876
2022-10-30 | 20:32 | 49.872
2022-10-30 | 20:32 | 49.866
2022-10-30 | 20:32 | 49.861
2022-10-30 | 20:33 | 49.859
2022-10-30 | 20:33 | 49.857
2022-10-30 | 20:33 | 49.859
2022-10-30 | 20:33 | 49.862
2022-10-30 | 20:33 | 49.865
2022-10-30 | 20:33 | 49.87
2022-10-30 | 20:33 | 49.876
2022-10-30 | 20:33 | 49.881
2022-10-30 | 20:33 | 49.887
2022-10-30 | 20:33 | 49.894
2022-10-30 | 20:33 | 49.901
2022-10-30 | 20:33 | 49.906
2022-10-30 | 20:33 | 49.91
2022-10-30 | 20:33 | 49.911
2022-10-30 | 20:33 | 49.912
2022-10-30 | 20:33 | 49.915
2022-10-30 | 20:33 | 49.917
2022-10-30 | 20:33 | 49.921
2022-10-30 | 20:33 | 49.927
2022-10-30 | 20:33 | 49.931
2022-10-30 | 20:33 | 49.933
2022-10-30 | 20:33 | 49.934
2022-10-30 | 20:33 | 49.935
2022-10-30 | 20:33 | 49.933
2022-10-30 | 20:33 | 49.934
2022-10-30 | 20:33 | 49.934
2022-10-30 | 20:33 | 49.935
2022-10-30 | 20:33 | 49.934
2022-10-30 | 20:33 | 49.932
2022-10-30 | 20:33 | 49.931
2022-10-30 | 20:33 | 49.929
2022-10-30 | 20:33 | 49.926
2022-10-30 | 20:33 | 49.926
2022-10-30 | 20:33 | 49.923
2022-10-30 | 20:33 | 49.923
2022-10-30 | 20:33 | 49.922
2022-10-30 | 20:33 | 49.923
2022-10-30 | 20:33 | 49.923
2022-10-30 | 20:33 | 49.925
2022-10-30 | 20:33 | 49.929
2022-10-30 | 20:33 | 49.932
2022-10-30 | 20:33 | 49.931
2022-10-30 | 20:33 | 49.928
2022-10-30 | 20:33 | 49.927
2022-10-30 | 20:33 | 49.925
2022-10-30 | 20:33 | 49.923
2022-10-30 | 20:33 | 49.919
2022-10-30 | 20:33 | 49.915
2022-10-30 | 20:33 | 49.913
2022-10-30 | 20:33 | 49.907
2022-10-30 | 20:33 | 49.904
2022-10-30 | 20:33 | 49.902
2022-10-30 | 20:33 | 49.898
2022-10-30 | 20:33 | 49.897
2022-10-30 | 20:33 | 49.896
2022-10-30 | 20:33 | 49.896
2022-10-30 | 20:33 | 49.896
2022-10-30 | 20:33 | 49.896
2022-10-30 | 20:33 | 49.896
2022-10-30 | 20:33 | 49.894
2022-10-30 | 20:33 | 49.895
2022-10-30 | 20:34 | 49.894
2022-10-30 | 20:34 | 49.891
2022-10-30 | 20:34 | 49.889
2022-10-30 | 20:34 | 49.887
2022-10-30 | 20:34 | 49.887
2022-10-30 | 20:34 | 49.884
2022-10-30 | 20:34 | 49.882
2022-10-30 | 20:34 | 49.879
2022-10-30 | 20:34 | 49.877
2022-10-30 | 20:34 | 49.877
2022-10-30 | 20:34 | 49.879
2022-10-30 | 20:34 | 49.88
2022-10-30 | 20:34 | 49.883
2022-10-30 | 20:34 | 49.884
2022-10-30 | 20:34 | 49.885
2022-10-30 | 20:34 | 49.887
2022-10-30 | 20:34 | 49.889
2022-10-30 | 20:34 | 49.889
2022-10-30 | 20:34 | 49.888
2022-10-30 | 20:34 | 49.886
2022-10-30 | 20:34 | 49.884
2022-10-30 | 20:34 | 49.881
2022-10-30 | 20:34 | 49.881
2022-10-30 | 20:34 | 49.882
2022-10-30 | 20:34 | 49.881
2022-10-30 | 20:34 | 49.881
2022-10-30 | 20:34 | 49.882
2022-10-30 | 20:34 | 49.88
2022-10-30 | 20:34 | 49.879
2022-10-30 | 20:34 | 49.874
2022-10-30 | 20:34 | 49.871
2022-10-30 | 20:34 | 49.866
2022-10-30 | 20:34 | 49.865
2022-10-30 | 20:34 | 49.859
2022-10-30 | 20:34 | 49.859
2022-10-30 | 20:34 | 49.858
2022-10-30 | 20:34 | 49.86
2022-10-30 | 20:34 | 49.863
2022-10-30 | 20:34 | 49.863
2022-10-30 | 20:34 | 49.864
2022-10-30 | 20:34 | 49.861
2022-10-30 | 20:34 | 49.859
2022-10-30 | 20:34 | 49.856
2022-10-30 | 20:34 | 49.853
2022-10-30 | 20:34 | 49.85
2022-10-30 | 20:34 | 49.847
2022-10-30 | 20:34 | 49.843
2022-10-30 | 20:34 | 49.84
2022-10-30 | 20:34 | 49.84
2022-10-30 | 20:34 | 49.838
2022-10-30 | 20:34 | 49.84
2022-10-30 | 20:34 | 49.843
2022-10-30 | 20:34 | 49.845
2022-10-30 | 20:34 | 49.851
2022-10-30 | 20:34 | 49.854
2022-10-30 | 20:34 | 49.856
2022-10-30 | 20:34 | 49.86
2022-10-30 | 20:34 | 49.863
2022-10-30 | 20:34 | 49.865
2022-10-30 | 20:35 | 49.867
2022-10-30 | 20:35 | 49.868
2022-10-30 | 20:35 | 49.868
2022-10-30 | 20:35 | 49.869
2022-10-30 | 20:35 | 49.868
2022-10-30 | 20:35 | 49.865
2022-10-30 | 20:35 | 49.861
2022-10-30 | 20:35 | 49.86
2022-10-30 | 20:35 | 49.859
2022-10-30 | 20:35 | 49.859
2022-10-30 | 20:35 | 49.859
2022-10-30 | 20:35 | 49.858
2022-10-30 | 20:35 | 49.857
2022-10-30 | 20:35 | 49.856
2022-10-30 | 20:35 | 49.858
2022-10-30 | 20:35 | 49.856
2022-10-30 | 20:35 | 49.856
2022-10-30 | 20:35 | 49.855
2022-10-30 | 20:35 | 49.853
2022-10-30 | 20:35 | 49.852
2022-10-30 | 20:35 | 49.851
2022-10-30 | 20:35 | 49.851
2022-10-30 | 20:35 | 49.85
2022-10-30 | 20:35 | 49.851
2022-10-30 | 20:35 | 49.852
2022-10-30 | 20:35 | 49.856
2022-10-30 | 20:35 | 49.859
2022-10-30 | 20:35 | 49.861
2022-10-30 | 20:35 | 49.865
2022-10-30 | 20:35 | 49.87
2022-10-30 | 20:35 | 49.873
2022-10-30 | 20:35 | 49.874
2022-10-30 | 20:35 | 49.875
2022-10-30 | 20:35 | 49.877
2022-10-30 | 20:35 | 49.876
2022-10-30 | 20:35 | 49.876
2022-10-30 | 20:35 | 49.872
2022-10-30 | 20:35 | 49.867
2022-10-30 | 20:35 | 49.864
2022-10-30 | 20:35 | 49.863
2022-10-30 | 20:35 | 49.862
2022-10-30 | 20:35 | 49.864
2022-10-30 | 20:35 | 49.864
2022-10-30 | 20:35 | 49.864
2022-10-30 | 20:35 | 49.862
2022-10-30 | 20:35 | 49.862
2022-10-30 | 20:35 | 49.859
2022-10-30 | 20:35 | 49.857
2022-10-30 | 20:35 | 49.855
2022-10-30 | 20:35 | 49.854
2022-10-30 | 20:35 | 49.854
2022-10-30 | 20:35 | 49.851
2022-10-30 | 20:35 | 49.852
2022-10-30 | 20:35 | 49.851
2022-10-30 | 20:35 | 49.85
2022-10-30 | 20:35 | 49.85
2022-10-30 | 20:35 | 49.855
2022-10-30 | 20:35 | 49.86
2022-10-30 | 20:35 | 49.867
2022-10-30 | 20:35 | 49.872
2022-10-30 | 20:35 | 49.872
2022-10-30 | 20:36 | 49.875
2022-10-30 | 20:36 | 49.874
2022-10-30 | 20:36 | 49.873
2022-10-30 | 20:36 | 49.873
2022-10-30 | 20:36 | 49.871
2022-10-30 | 20:36 | 49.867
2022-10-30 | 20:36 | 49.868
2022-10-30 | 20:36 | 49.871
2022-10-30 | 20:36 | 49.874
2022-10-30 | 20:36 | 49.877
2022-10-30 | 20:36 | 49.877
2022-10-30 | 20:36 | 49.877
2022-10-30 | 20:36 | 49.873
2022-10-30 | 20:36 | 49.869
2022-10-30 | 20:36 | 49.867
2022-10-30 | 20:36 | 49.862
2022-10-30 | 20:36 | 49.859
2022-10-30 | 20:36 | 49.856
2022-10-30 | 20:36 | 49.852
2022-10-30 | 20:36 | 49.847
2022-10-30 | 20:36 | 49.844
2022-10-30 | 20:36 | 49.843
2022-10-30 | 20:36 | 49.843
2022-10-30 | 20:36 | 49.848
2022-10-30 | 20:36 | 49.856
2022-10-30 | 20:36 | 49.865
2022-10-30 | 20:36 | 49.871
2022-10-30 | 20:36 | 49.876
2022-10-30 | 20:36 | 49.88
2022-10-30 | 20:36 | 49.883
2022-10-30 | 20:36 | 49.885
2022-10-30 | 20:36 | 49.885
2022-10-30 | 20:36 | 49.885
2022-10-30 | 20:36 | 49.884
2022-10-30 | 20:36 | 49.882
2022-10-30 | 20:36 | 49.879
2022-10-30 | 20:36 | 49.879
2022-10-30 | 20:36 | 49.879
2022-10-30 | 20:36 | 49.878
2022-10-30 | 20:36 | 49.88
2022-10-30 | 20:36 | 49.884
2022-10-30 | 20:36 | 49.888
2022-10-30 | 20:36 | 49.894
2022-10-30 | 20:36 | 49.898
2022-10-30 | 20:36 | 49.904
2022-10-30 | 20:36 | 49.911
2022-10-30 | 20:36 | 49.918
2022-10-30 | 20:36 | 49.923
2022-10-30 | 20:36 | 49.927
2022-10-30 | 20:36 | 49.934
2022-10-30 | 20:36 | 49.938
2022-10-30 | 20:36 | 49.944
2022-10-30 | 20:36 | 49.948
2022-10-30 | 20:36 | 49.953
2022-10-30 | 20:36 | 49.955
2022-10-30 | 20:36 | 49.96
2022-10-30 | 20:36 | 49.966
2022-10-30 | 20:36 | 49.971
2022-10-30 | 20:36 | 49.974
2022-10-30 | 20:37 | 49.976
2022-10-30 | 20:37 | 49.976
2022-10-30 | 20:37 | 49.979
2022-10-30 | 20:37 | 49.982
2022-10-30 | 20:37 | 49.981
2022-10-30 | 20:37 | 49.984
2022-10-30 | 20:37 | 49.985
2022-10-30 | 20:37 | 49.985
2022-10-30 | 20:37 | 49.983
2022-10-30 | 20:37 | 49.982
2022-10-30 | 20:37 | 49.98
2022-10-30 | 20:37 | 49.981
2022-10-30 | 20:37 | 49.98
2022-10-30 | 20:37 | 49.982
2022-10-30 | 20:37 | 49.987
2022-10-30 | 20:37 | 49.99
2022-10-30 | 20:37 | 49.996
2022-10-30 | 20:37 | 50.002
2022-10-30 | 20:37 | 50.006
2022-10-30 | 20:37 | 50.009
2022-10-30 | 20:37 | 50.011
2022-10-30 | 20:37 | 50.013
2022-10-30 | 20:37 | 50.017
2022-10-30 | 20:37 | 50.021
2022-10-30 | 20:37 | 50.024
2022-10-30 | 20:37 | 50.026
2022-10-30 | 20:37 | 50.023
2022-10-30 | 20:37 | 50.022
2022-10-30 | 20:37 | 50.018
2022-10-30 | 20:37 | 50.018
2022-10-30 | 20:37 | 50.016
2022-10-30 | 20:37 | 50.011
2022-10-30 | 20:37 | 50.009
2022-10-30 | 20:37 | 50.008
2022-10-30 | 20:37 | 50.01
2022-10-30 | 20:37 | 50.011
2022-10-30 | 20:37 | 50.012
2022-10-30 | 20:37 | 50.01
2022-10-30 | 20:37 | 50.007
2022-10-30 | 20:37 | 50.003
2022-10-30 | 20:37 | 49.995
2022-10-30 | 20:37 | 49.989
2022-10-30 | 20:37 | 49.981
2022-10-30 | 20:37 | 49.977
2022-10-30 | 20:37 | 49.974
2022-10-30 | 20:37 | 49.974
2022-10-30 | 20:37 | 49.978
2022-10-30 | 20:37 | 49.982
2022-10-30 | 20:37 | 49.985
2022-10-30 | 20:37 | 49.99
2022-10-30 | 20:37 | 49.995
2022-10-30 | 20:37 | 50
2022-10-30 | 20:37 | 50.006
2022-10-30 | 20:37 | 50.011
2022-10-30 | 20:37 | 50.015
2022-10-30 | 20:37 | 50.02
2022-10-30 | 20:37 | 50.02
2022-10-30 | 20:37 | 50.022
2022-10-30 | 20:37 | 50.024
2022-10-30 | 20:37 | 50.022
2022-10-30 | 20:38 | 50.024
2022-10-30 | 20:38 | 50.025
2022-10-30 | 20:38 | 50.025
2022-10-30 | 20:38 | 50.024
2022-10-30 | 20:38 | 50.026
2022-10-30 | 20:38 | 50.026
2022-10-30 | 20:38 | 50.026
2022-10-30 | 20:38 | 50.028
2022-10-30 | 20:38 | 50.032
2022-10-30 | 20:38 | 50.035
2022-10-30 | 20:38 | 50.035
2022-10-30 | 20:38 | 50.033
2022-10-30 | 20:38 | 50.031
2022-10-30 | 20:38 | 50.029
2022-10-30 | 20:38 | 50.028
2022-10-30 | 20:38 | 50.027
2022-10-30 | 20:38 | 50.028
2022-10-30 | 20:38 | 50.029
2022-10-30 | 20:38 | 50.028
2022-10-30 | 20:38 | 50.03
2022-10-30 | 20:38 | 50.032
2022-10-30 | 20:38 | 50.032
2022-10-30 | 20:38 | 50.032
2022-10-30 | 20:38 | 50.03
2022-10-30 | 20:38 | 50.029
2022-10-30 | 20:38 | 50.03
2022-10-30 | 20:38 | 50.033
2022-10-30 | 20:38 | 50.035
2022-10-30 | 20:38 | 50.038
2022-10-30 | 20:38 | 50.041
2022-10-30 | 20:38 | 50.041