## Options (hidden)
Options |  | For compatibility with the legacy approach, wind farms could be specified separately from other DG technology types in order to apply wind profile resolution correction factors from the following table. The correction factors are applied if only wind generation technology types are specified with minimum 30 minute profile resulotion.
List of seasons | List of generator profile types
All data | DG (excluding Wind)
Winter | Wind
Summer | ES | Wind profile resolution | Correction factors in % for Tm (h) of:
|  |  | 0.5 | 2 | 3 | 18 | 24 | 120
|  | 5 min | 97 | 93 | 92 | 85 | 84 | 42

## Read Me
Contribution to System Security from Non-Contracted DG and ES
The contribution to system security from non-contracted distributed generation (DG) and Electricity Storage (ES) can be calculated using this spreadsheet. Section 9 of the ENA Engineering Report 130, Issue 3, 2019 provides guidance and refers reader to Annex D where three potential assessment approaches are defined. Approach 3 refers to this spreadsheet.
Approach 3 relies on a set of input data as described in EREP 131 user's guide: - Demand profile for period of interest - DG and/or ES profiles for period of interest - Period of interest (all available data, winter or summer season) - Persistence (see EREP 130 Table D.2.3 for indicative values and Section E.3) - Number of states (typically between 11 and 1001; recommended 101)
For compatibility with the legacy approach, wind farms may need to be specified separately from other DG technology types in order to apply wind profile resolution correction factors. The correction factors are applied if only wind generation technology types are specified with 30 minute profile resolution.

## F Factor Profiles
Demand profile index or name | D1
Persistence, hours | 3 | hours | Please click the Recalculate before reading the results
Season (all data, winter or summer) | Winter
Demand and generation number of states | 101
DG or ES | Profile index or name
DG (excluding Wind) | DG 1 (kW) |  | Contribution
|  |  | Aggregate DNC of installed DG and ES | 15 | MW
|  |  | Maximum value of demand | 15 | MW
|  |  | Contribution (%) | 89.31%
|  |  | Contribution (MW) | 13.3967 | MW
|  |  | Probability of delivering contribution | 99.36%
|  |  | Probability of not delivering contribution | 0.6424%
|  |  | Expected energy not supplied per total DNC | 3.1426 | MWh/MW

## Contribution (hidden)
Installed DG capacity | 135 | MW
Maximum value of demand | 135 | MW
Contribution (%) | 71.78%
Contribution (MW) | 96.9078 | MW
Probability of delivering contribution | 63.61%
Probability of not delivering contribution | 36.39%
Expected energy not supplied per installed DG capacity | 104.1293 | MWh/MW
|  |  | Total | 36401.7239

## Generators (hidden)
Non-intermittent Generation
Number of Groups of Units | 1
Index of Group of Units | 1 |  | 2 |  | 3
Status On / Off | On |  | Off |  | Off
Number of Units | 3 |  | 1 |  | 1
Number of States | 2 |  | 3 |  | 8
State No | Capacity (MW) | Probability | Capacity (MW) | Probability | Capacity (MW) | Probability
1 | 40 | 0.86 | 60 | 0.8 | 100 | 0.8
2 | 0 | 0.14 | 30 | 0.15 | 90 | 0.04
3 |  |  | 0 | 0.05 | 80 | 0.02
4 |  |  |  |  | 70 | 0.02
5 |  |  |  |  | 60 | 0.02
6 |  |  |  |  | 30 | 0.02
7 |  |  |  |  | 15 | 0.02
8 |  |  |  |  | 0 | 0.06
9
10
Intermittent Generation
Persistence Tm (days, hours, minutes) | 0 | days | 2 | hours | 0 | minutes
Status On / Off | On |  |  |  | Persistence Tm
Generation Profile Index or Name | DG 1 |  |  |  | 0.083333 | days
Season | Winter |  |  |  | 2 | hours
Number of States | 20 |  |  |  | 120 | minutes
Note on A5: Author: Index starts from 1 for the first unit group given in the columns B and C, and successively increases by 1 for the following groups to the right.
Note on B4: Author: Unit Groups that have Index less than or equal to this value are taken into consideration.
Note on B29: Author: Number of derated states of capacity outage probability table calculated for intermittent generation. Greater the number the higher precision of calculation. Recommended value for sole intermittent generation is 101. For generation systems which also consists of several non-intermittent units the value can be less. Recommendation is to calculate contribution for several consecutive values of Number of States. If there is a significant change of contribution, increase the Number of States; otherwise the contribution has been calculated.
Note on F26: Author: Please do not overwrite these cells. They show persistence entered into row 25 in different units.

## Load (hidden)
Peak Value (MW) | 135
Duration (h) | 4368
Number of Lines | 2
Normalised Load Profile
Duration (%) | Load (%) | Duration | Load | Energy
0% | 100% | 0 | 135 | 389095.0409
2.2% | 83.9% | 96.096 | 113.265 | 1044.3233
100% | 46.9% | 4368 | 63.315 | 111490.7976
|  | 4368 | 0 | 276559.92
Energy is 389095 MWh
Note on B20: Author: Note: Rounded to a whole number
Note on C6: Author: A value of this cell can be used in formulas as a variable 'Duration' (without apostrophes)

## Demand Profiles
Profile index | 1 | 2
Profile name | D1 | D2
User reference 1 | Example Imp & Exp profile | Example Imp profile
User reference 2
Sampling rate (minutes) | 30 | 30
Unit conversion factor to MW | 0.001 | 1
Total export energy, MWh | 1930.3749 | 0
Total import energy, MWh | 181838.6106 | 37117.9674
Minimum profile value, MW | -17.7392 | 1.2911
Maximum profile value, MW | 39.404 | 8.6839
Sign | 1 | 1
Number of Periods | 17520 | 17520
Start period | 2016-04-01 | 2016-01-01
1 | 17318.9785 | 3.0833
2 | 16811.9531 | 3.0833
3 | 16542.4375 | 3.0833
4 | 16333.543 | 3.0833
5 | 16304.5322 | 3.0833
6 | 16714.6914 | 3.0833
7 | 16698.1855 | 3.0833
8 | 16775.082 | 2.7776
9 | 16740.0469 | 2.7128
10 | 17431.2383 | 2.7128
11 | 18331.2617 | 2.7128
12 | 20433.1367 | 2.7128
13 | 22115.4766 | 2.7128
14 | 23904.6895 | 2.7128
15 | 26041.1855 | 2.7128
16 | 27605.6602 | 2.7128
17 | 28617.4512 | 2.7128
18 | 29773.9062 | 2.7128
19 | 31223.3496 | 2.7128
20 | 30808.707 | 3.0839
21 | 31738.1289 | 3.1969
22 | 31281.2344 | 3.4729
23 | 31398.1074 | 3.5691
24 | 31048.7285 | 3.5691
25 | 30053.9277 | 4.1977
26 | 30353.9277 | 4.3318
27 | 30058.5488 | 4.3318
28 | 28364.3262 | 4.3318
29 | 28369.957 | 4.3318
30 | 28481.2207 | 4.2618
31 | 28048.5781 | 3.9664
32 | 27923.3145 | 3.9664
33 | 28037.3145 | 4.2262
34 | 27448.7871 | 4.403
35 | 26307.3438 | 4.7074
36 | 26642.7441 | 4.7074
37 | 26766.125 | 4.6366
38 | 27103.5234 | 4.3209
39 | 26536.4707 | 4.2554
40 | 26003.8281 | 3.9465
41 | 24564.8906 | 3.6025
42 | 22977.2891 | 3.5571
43 | 20658.2852 | 3.5571
44 | 19471.2305 | 3.5571
45 | 18658.4297 | 3.5571
46 | 17874.1348 | 3.5571
47 | 17218.6621 | 2.9345
48 | 16399.5352 | 2.7944
49 | 15802.8711 | 2.7944
50 | 15156.9443 | 2.7944
51 | 15091.3105 | 2.7944
52 | 15463.5137 | 2.7944
53 | 15052.3008 | 2.7944
54 | 14340.8359 | 2.7944
55 | 14297.9414 | 2.7944
56 | 14338.1943 | 2.7944
57 | 14487.0889 | 2.7944
58 | 14796.2363 | 2.7944
59 | 15120.2363 | 2.7944
60 | 16443.6797 | 2.7944
61 | 17934.2715 | 2.7944
62 | 18948.3145 | 2.7944
63 | 20175.5059 | 2.7944
64 | 21844.4863 | 2.8602
65 | 23158.0234 | 3.5023
66 | 24388.2461 | 3.6068
67 | 24995.5117 | 4.2734
68 | 25568.3125 | 4.3906
69 | 25046.6367 | 4.3906
70 | 24974.7734 | 4.3906
71 | 24807.0059 | 4.3906
72 | 25050.0371 | 4.3906
73 | 24750.8906 | 4.3906
74 | 24397.9727 | 4.3906
75 | 23865.2148 | 4.3906
76 | 22970.4141 | 4.659
77 | 23055.0352 | 4.7834
78 | 23131.4258 | 4.7834
79 | 22772.1621 | 4.7834
80 | 22334.3926 | 4.7834
81 | 21619.9609 | 4.7834
82 | 21471.707 | 4.7834
83 | 21347.707 | 4.7834
84 | 21143.4316 | 4.7834
85 | 21184.8125 | 4.7501
86 | 20916.3066 | 4.3704
87 | 21466.582 | 4.3683
88 | 20465.5273 | 4.3683
89 | 19163.5781 | 4.3683
90 | 18059.6504 | 4.1381
91 | 17440.3672 | 3.9847
92 | 16809.8398 | 3.9847
93 | 16151.7959 | 3.9847
94 | 15475.8682 | 3.6584
95 | 14504.3311 | 3.3846
96 | 14129.9629 | 2.9085
97 | 13561.4492 | 2.8504
98 | 13095.4141 | 2.8504
99 | 13001.0029 | 2.8504
100 | 12858.9805 | 2.8504
101 | 12804.4961 | 2.8504
102 | 12486.9805 | 2.8504
103 | 12417.9492 | 2.8504
104 | 12439.3516 | 2.8504
105 | 12480.959 | 2.8504
106 | 12540.8438 | 2.8504
107 | 12651.7383 | 2.8504
108 | 13178.4961 | 2.8504
109 | 13494.5186 | 2.8504
110 | 14123.1836 | 2.8504
111 | 14652.2158 | 2.8504
112 | 15775.7734 | 2.8504
113 | 16681.6797 | 2.8504
114 | 18223.2832 | 2.8504
115 | 19131.5996 | 2.8504
116 | 20051.6426 | 3.2197
117 | 20917.1797 | 3.2706
118 | 21341.5703 | 3.7478
119 | 21556.9492 | 3.7361
120 | 21977.75 | 3.6285
121 | 21822.6016 | 3.672
122 | 21659.3594 | 4.0018
123 | 21117.6855 | 4.0018
124 | 20883.3164 | 4.0018
125 | 20907.4531 | 4.3706
126 | 20863.0664 | 4.1219
127 | 20836.3066 | 4.0172
128 | 20780.6973 | 4.0172
129 | 20699.916 | 4.0172
130 | 19574.7266 | 4.3793
131 | 18507.9258 | 4.3855
132 | 17872.7773 | 4.3855
133 | 17808.1348 | 4.3855
134 | 17712.3867 | 4.3855
135 | 18390.4102 | 4.3855
136 | 18753.6953 | 4.3325
137 | 18461.168 | 3.9747
138 | 18399.7891 | 3.6427
139 | 17469.7227 | 3.6427
140 | 16725.4492 | 3.6427
141 | 15930.0273 | 3.6427
142 | 15264.7422 | 3.3057
143 | 14945.457 | 2.9427
144 | 15065.1533 | 2.9057
145 | 14778.8281 | 2.9057
146 | 14604.0479 | 2.9057
147 | 14495.4062 | 2.9057
148 | 14489.7529 | 2.9057
149 | 14472.8496 | 2.9057
150 | 14110.2158 | 2.9057
151 | 13621.5293 | 2.9057
152 | 13665.5293 | 2.9057
153 | 13784.9082 | 2.9057
154 | 14492.2139 | 2.9057
155 | 16330.9209 | 2.9057
156 | 20240.2637 | 2.9057
157 | 22402.875 | 3.2993
158 | 24517.2383 | 3.3094
159 | 27767.0391 | 3.6618
160 | 30076.6641 | 4.3094
161 | 30927.582 | 5.1096
162 | 30665.832 | 5.8315
163 | 30715.1895 | 6.5324
164 | 31630.75 | 7.0452
165 | 32798.0781 | 7.0611
166 | 32730.5605 | 7.0611
167 | 32558.9297 | 7.0611
168 | 32202.5195 | 7.0611
169 | 32537.4355 | 7.0611
170 | 31708.2441 | 6.7946
171 | 31282.1074 | 7.3748
172 | 31886.7715 | 7.0594
173 | 32225.1621 | 6.8323
174 | 31948.5195 | 6.6809
175 | 32167.1602 | 6.7251
176 | 29998.4102 | 7.0594
177 | 29896.4102 | 7.0594
178 | 29059.3574 | 7.0594
179 | 28785.2207 | 7.0594
180 | 28449.2207 | 6.5971
181 | 28217.9355 | 5.9531
182 | 28174.5566 | 6.157
183 | 27724.3984 | 6.0075
184 | 28268.9453 | 5.4505
185 | 27668.5352 | 5.3811
186 | 25216.7734 | 5.3165
187 | 23196.668 | 4.7461
188 | 21609.2031 | 4.6452
189 | 20624.4023 | 4.4133
190 | 19509.0938 | 4.2499
191 | 18371.2812 | 3.959
192 | 17109.6289 | 3.818
193 | 16587.2305 | 3.4853
194 | 16426.0488 | 3.1114
195 | 16170.2793 | 3.4367
196 | 16230.1641 | 3.4367
197 | 16173.1748 | 3.4367
198 | 15991.1543 | 3.4367
199 | 15663.248 | 3.4367
200 | 16174.6914 | 3.4367
201 | 16701.332 | 3.4367
202 | 17206.207 | 3.4367
203 | 18580.6836 | 3.4367
204 | 21770.4648 | 3.4367
205 | 23664.6875 | 3.7753
206 | 26844.9961 | 3.8237
207 | 28408.9453 | 4.5344
208 | 32776.4453 | 5.03
209 | 34856.3008 | 5.5146
210 | 34151.6133 | 5.9053
211 | 34876.9219 | 6.7755
212 | 35519.082 | 6.9321
213 | 36366.1328 | 7.0306
214 | 35743.5859 | 7.0593
215 | 35279.1953 | 6.9424
216 | 33591.6172 | 6.9424
217 | 34584.5312 | 6.9424
218 | 33893.3828 | 7.5277
219 | 32668.0566 | 7.4651
220 | 32168.6777 | 7.318
221 | 32781.9414 | 7.318
222 | 32514.3086 | 7.318
223 | 30314.6855 | 7.318
224 | 28806.4844 | 7.0868
225 | 28587.3574 | 7.0874
226 | 28214.8105 | 7.0865
227 | 27533.7988 | 6.9635
228 | 27657.0391 | 6.4805
229 | 27680.168 | 6.2478
230 | 27514.7871 | 6.1837
231 | 28119.3145 | 6.1837
232 | 28347.084 | 5.9018
233 | 28010.6719 | 5.8161
234 | 26340.7227 | 5.5236
235 | 23819.9531 | 5.0471
236 | 22266.3711 | 4.7673
237 | 20873.5469 | 4.411
238 | 19523.3477 | 3.9619
239 | 18718.6836 | 3.9619
240 | 17736.4102 | 3.6621
241 | 17232.4727 | 3.5948
242 | 16984.3164 | 3.3701
243 | 16340.46 | 3.2203
244 | 16343.543 | 3.2203
245 | 16168.7861 | 3.2203
246 | 16045.543 | 3.2203
247 | 16139.0381 | 3.2203
248 | 16522.5742 | 3.2203
249 | 16703.0078 | 3.2203
250 | 17391.9258 | 3.2203
251 | 18574.4961 | 3.2203
252 | 21873.0566 | 3.5507
253 | 23971.7344 | 3.8712
254 | 26838.2617 | 3.9927
255 | 28618.5996 | 4.6716
256 | 30318.6641 | 5.3859
257 | 31381.2344 | 6.1141
258 | 33215.8477 | 6.3264
259 | 32900.4453 | 6.8638
260 | 32894.8125 | 7.0469
261 | 32744.6973 | 7.0469
262 | 33135.2031 | 7.0469
263 | 32675.5508 | 7.0469
264 | 33856.9922 | 7.0469
265 | 33837.7734 | 7.0469
266 | 32170.9102 | 7.1026
267 | 30937.9707 | 7.4185
268 | 31677.0254 | 7.3697
269 | 29555.4004 | 7.0526
270 | 28578.0938 | 7.0526
271 | 29045.748 | 7.0526
272 | 29369.8633 | 7.0526
273 | 28497.7266 | 6.9193
274 | 28597.082 | 7.0256
275 | 28719.3574 | 7.1079
276 | 28170.3047 | 6.5394
277 | 28174.5781 | 6.3099
278 | 28483.8418 | 6.0249
279 | 29111.6113 | 5.6914
280 | 28935.9785 | 5.5752
281 | 28645.8418 | 5.5752
282 | 27845.3145 | 4.8958
283 | 25273.6484 | 4.8182
284 | 23756.7109 | 4.5423
285 | 22286.9922 | 4.1502
286 | 20937.043 | 4.0486
287 | 19955.2539 | 3.4901
288 | 18981.5977 | 3.2899
289 | 18352.7695 | 3.2899
290 | 17871.1172 | 3.2899
291 | 17525.9766 | 3.2899
292 | 17428.25 | 3.2899
293 | 17600.1133 | 3.2899
294 | 17627.7461 | 3.2899
295 | 17329.6094 | 3.5181
296 | 17285.3535 | 3.6701
297 | 17325.4922 | 3.6701
298 | 18357.9023 | 3.6701
299 | 19477.9688 | 3.6701
300 | 22645.6328 | 3.3237
301 | 24014.3398 | 3.278
302 | 27051.7539 | 3.9326
303 | 28895.6094 | 4.4552
304 | 29432.1152 | 5.4157
305 | 30416.5703 | 6.0984
306 | 31261.8555 | 6.7651
307 | 32618.9297 | 7.0549
308 | 32914.8359 | 7.0549
309 | 32684.9297 | 7.0549
310 | 32702.0566 | 7.806
311 | 31575.625 | 7.7717
312 | 31151.2344 | 7.4431
313 | 31281.2324 | 7.4431
314 | 30498.8223 | 7.4431
315 | 30050.1797 | 7.3258
316 | 29933.1699 | 7.4013
317 | 29579.0117 | 7.0968
318 | 29253.4004 | 7.0349
319 | 27816.9453 | 7.3561
320 | 27151.5234 | 7.4128
321 | 27091.4082 | 7.1612
322 | 25900.4492 | 7.4574
323 | 25126.1543 | 7.4053
324 | 25329.5547 | 6.9684
325 | 25384.4258 | 6.433
326 | 25409.7852 | 6.6868
327 | 26226.332 | 6.7167
328 | 26239.7129 | 6.2856
329 | 25719.0703 | 5.9097
330 | 23782.8242 | 5.5748
331 | 21629.0859 | 5.5352
332 | 19854.3789 | 5.2242
333 | 18532.1758 | 4.8102
334 | 17247.9766 | 4.1468
335 | 16383.9551 | 4.0195
336 | 15223.6797 | 3.7752
337 | 14514.9443 | 3.4276
338 | 14079.0156 | 3.2774
339 | 13657.9844 | 3.296
340 | 13554.7422 | 3.6556
341 | 13683.7959 | 3.681
342 | 13587.4355 | 3.681
343 | 13670.4023 | 3.681
344 | 13618.541 | 3.6336
345 | 13779.8037 | 3.3019
346 | 14444.4463 | 3.3019
347 | 15860.2793 | 3.589
348 | 19237.0938 | 3.6684
349 | 21648.9492 | 3.6684
350 | 23539.9512 | 3.9686
351 | 26279.8281 | 4.7854
352 | 27730.2812 | 5.8453
353 | 28467.2207 | 6.2542
354 | 28893.9785 | 6.888
355 | 28393.0625 | 7.4075
356 | 28801.1055 | 7.4693
357 | 28679.8418 | 7.4693
358 | 28652.4629 | 7.8277
359 | 28587.5898 | 7.8432
360 | 27302.6504 | 8.0313
361 | 27288.9043 | 7.8512
362 | 27680.9043 | 7.7665
363 | 27133.7773 | 7.5966
364 | 26988.9961 | 7.408
365 | 25744.9336 | 7.2992
366 | 25891.3242 | 7.2992
367 | 25357.9219 | 6.9315
368 | 25238.2891 | 6.6404
369 | 24558.6367 | 6.5428
370 | 23769.8359 | 6.5428
371 | 23370.9414 | 6.5428
372 | 23306.3203 | 6.491
373 | 23594.2051 | 5.8527
374 | 23170.9199 | 5.8064
375 | 22993.793 | 5.8064
376 | 23082.9199 | 5.8064
377 | 22657.8867 | 5.8064
378 | 21026.9277 | 5.5321
379 | 19103.5781 | 5.1831
380 | 17167.9766 | 4.3706
381 | 16476.3242 | 4.2833
382 | 15310.7422 | 4.0501
383 | 14809.9844 | 3.9151
384 | 14041.8467 | 3.6
385 | 13656.9434 | 3.548
386 | 13146.4258 | 3.548
387 | 12988.3809 | 3.548
388 | 12737.2344 | 3.548
389 | 12460.0859 | 3.548
390 | 12474.9805 | 3.548
391 | 12216.707 | 3.548
392 | 12090.959 | 3.548
393 | 11899.6758 | 3.548
394 | 12641.7383 | 3.548
395 | 13842.3086 | 3.5047
396 | 14544.9531 | 3.1769
397 | 15571.3848 | 3.5346
398 | 15861.4062 | 3.5937
399 | 16751.082 | 3.4627
400 | 19192.082 | 3.5634
401 | 20199.5059 | 3.6331
402 | 21078.9258 | 4.171
403 | 21084.4453 | 4.5607
404 | 21562.2109 | 5.0482
405 | 20804.2852 | 5.1215
406 | 20304.5391 | 5.0335
407 | 20094.127 | 5.0265
408 | 20198.7695 | 5.0265
409 | 20491.7812 | 5.0265
410 | 20292.5156 | 5.2574
411 | 19594.6094 | 5.359
412 | 18974.5898 | 5.0265
413 | 18905.4414 | 5.0265
414 | 19344.7266 | 5.0265
415 | 19383.8516 | 5.0265
416 | 19109.0938 | 5.0265
417 | 19184.084 | 5.0265
418 | 19272.1055 | 5.2651
419 | 19471.4609 | 5.3936
420 | 19478.7266 | 5.3198
421 | 19567.7148 | 4.9911
422 | 19635.4844 | 4.9911
423 | 20331.252 | 4.9911
424 | 19082.5684 | 4.9911
425 | 17729.2383 | 4.3312
426 | 16352.5537 | 4.2439
427 | 15640.7432 | 4.2439
428 | 14867.0889 | 4.1756
429 | 14241.9414 | 3.5907
430 | 13599.1387 | 3.5012
431 | 12483.4883 | 3.5012
432 | 12010.1504 | 3.5012
433 | 11511.5078 | 3.5012
434 | 11186.1094 | 3.5012
435 | 10828.0625 | 3.5012
436 | 10670.8438 | 3.5012
437 | 10206.791 | 3.1953
438 | 10051.084 | 3.1341
439 | 10081.5898 | 3.1341
440 | 10061.707 | 2.8522
441 | 10217.2207 | 2.7665
442 | 10329.8398 | 2.7665
443 | 10436.3672 | 2.7665
444 | 10609.3574 | 2.7665
445 | 11202.6445 | 2.7665
446 | 12000.8203 | 2.7665
447 | 12698.0859 | 2.7665
448 | 13535.5293 | 2.7665
449 | 14297.3193 | 2.7665
450 | 15819.6592 | 2.7794
451 | 16573.9531 | 3.0895
452 | 17614.8906 | 3.4297
453 | 18473.5547 | 3.5
454 | 18962.6836 | 3.8468
455 | 18853.5547 | 3.8682
456 | 18779.1895 | 3.8682
457 | 18733.5566 | 4.2848
458 | 18473.0508 | 4.2918
459 | 18390.5469 | 4.2918
460 | 18288.6621 | 4.2918
461 | 18671.3242 | 4.2918
462 | 18660.3164 | 4.2918
463 | 18549.5547 | 4.2918
464 | 18916.1992 | 4.2918
465 | 18778.6836 | 4.2918
466 | 17349.6504 | 4.5676
467 | 16348.0703 | 5.042
468 | 15480.373 | 5.0768
469 | 15298.626 | 4.8338
470 | 15248.9951 | 4.6932
471 | 15597.7754 | 4.6932
472 | 16201.6807 | 4.3561
473 | 16307.4268 | 4.3255
474 | 15949.1533 | 4.3255
475 | 15367.6162 | 4.2092
476 | 14654.4678 | 4.0582
477 | 13834.6562 | 4.02
478 | 13337.623 | 3.5722
479 | 12623.6016 | 3.56
480 | 11961.4219 | 2.8654
481 | 11670.916 | 2.7499
482 | 11327.0332 | 2.7499
483 | 11389.0547 | 2.7898
484 | 11368.7715 | 2.7465
485 | 11121.9922 | 2.7465
486 | 11186.5273 | 2.7465
487 | 11132.3906 | 2.7465
488 | 11162.7383 | 2.7465
489 | 11293.168 | 2.7465
490 | 12149.9492 | 2.7834
491 | 14139.3818 | 3.1153
492 | 17300.9863 | 3.0479
493 | 19655.084 | 3.2671
494 | 22258.8555 | 3.5879
495 | 24569.7617 | 4.6747
496 | 26690.2383 | 5.3497
497 | 27403.4082 | 6.0736
498 | 27745.6602 | 6.218
499 | 29709.9062 | 7.4004
500 | 31047.6016 | 7.7943
501 | 31105.9922 | 7.8689
502 | 28774.9883 | 7.8799
503 | 29009.6328 | 8.1751
504 | 28181.2207 | 8.2349
505 | 28767.6328 | 8.2349
506 | 28271.5898 | 7.6583
507 | 27760.832 | 7.5877
508 | 27761.084 | 7.4762
509 | 27372.3984 | 7.4762
510 | 26127.7109 | 7.4762
511 | 25547.6914 | 7.1729
512 | 25828.4473 | 7.1085
513 | 26196.9766 | 7.1725
514 | 25653.9434 | 7.6086
515 | 25097.5312 | 7.2545
516 | 25513.3008 | 6.7922
517 | 25514.9336 | 6.2712
518 | 25006.1523 | 6.1625
519 | 25227.0273 | 5.8435
520 | 26057.5977 | 5.8435
521 | 24897.5117 | 5.8435
522 | 23058.5508 | 5.5513
523 | 21249.9395 | 5.3565
524 | 19557.9688 | 4.9775
525 | 18381.2832 | 4.6574
526 | 17545.9961 | 4.2452
527 | 17012.9648 | 3.8638
528 | 16319.29 | 3.5159
529 | 15975.8389 | 3.4464
530 | 15254.4824 | 3.4464
531 | 14920.1855 | 3.4464
532 | 15086.1855 | 3.4464
533 | 15177.4277 | 3.4464
534 | 15001.123 | 3.4464
535 | 15061.5215 | 3.4464
536 | 14908.3516 | 3.4464
537 | 14939.7324 | 3.4464
538 | 15188.2363 | 3.4464
539 | 16264.9229 | 3.4464
540 | 19789.2539 | 3.7724
541 | 22938.3926 | 4.1388
542 | 25226.6582 | 4.2005
543 | 27209.0195 | 4.8157
544 | 28500.2109 | 5.6165
545 | 28458.9453 | 6.1641
546 | 28602.8535 | 6.7149
547 | 29680.5273 | 7.2073
548 | 30100.043 | 7.5158
549 | 31510.4961 | 7.9319
550 | 31762.1289 | 7.9471
551 | 31145.0957 | 7.9471
552 | 31072.3594 | 7.9471
553 | 30499.9277 | 7.9471
554 | 29793.1699 | 7.9471
555 | 29630.8945 | 7.611
556 | 29940.2969 | 7.1308
557 | 29743.5371 | 7.1308
558 | 28358.9473 | 7.1308
559 | 27775.9141 | 7.1308
560 | 27869.5469 | 7.1308
561 | 27671.293 | 7.1308
562 | 27375.9141 | 7.1308
563 | 25619.8066 | 7.1308
564 | 25419.9219 | 7.1308
565 | 24544.6367 | 6.8356
566 | 24802.752 | 6.3869
567 | 25013.3945 | 6.3807
568 | 25150.2695 | 6.0863
569 | 24968.0156 | 5.6771
570 | 23895.8359 | 5.5677
571 | 21865.6133 | 5.2435
572 | 20121.9902 | 4.9364
573 | 18649.0742 | 4.6125
574 | 17272.207 | 4.172
575 | 16443.9766 | 4.092
576 | 15732.5254 | 3.7678
577 | 14968.0703 | 3.7631
578 | 14446.9521 | 3.3002
579 | 13979.2988 | 3.63
580 | 14324.0781 | 3.739
581 | 13976.6562 | 4.0663
582 | 13990.9297 | 4.0663
583 | 13904.1729 | 4.0663
584 | 14157.1836 | 3.745
585 | 14200.3105 | 3.3185
586 | 15095.8691 | 3.3185
587 | 16240.6699 | 3.5605
588 | 19432.5879 | 3.726
589 | 22253.4961 | 4.0543
590 | 24668.752 | 4.0543
591 | 28642.4629 | 4.8736
592 | 30259.9277 | 5.6838
593 | 29938.5273 | 6.3948
594 | 30141.5586 | 6.7797
595 | 32155.7598 | 7.7243
596 | 31164.1074 | 7.6177
597 | 30715.834 | 7.9306
598 | 30598.5703 | 8.0048
599 | 32495.0664 | 8.0048
600 | 31354.6348 | 7.7808
601 | 29868.4102 | 7.6314
602 | 31817.5293 | 7.6851
603 | 30750.3398 | 7.761
604 | 29843.0547 | 7.3011
605 | 29250.5273 | 7.2609
606 | 27956.6934 | 7.2609
607 | 26580.7461 | 7.2609
608 | 26558.375 | 7.2609
609 | 26606.7441 | 7.1629
610 | 25991.8281 | 7.2899
611 | 24929.6484 | 7.2855
612 | 24815.0039 | 6.726
613 | 24669.6484 | 6.5251
614 | 24818.5 | 6.2161
615 | 24947.0273 | 6.158
616 | 25441.1641 | 6.158
617 | 25387.9219 | 5.8256
618 | 24158.3398 | 5.4478
619 | 21875.2461 | 5.349
620 | 20031.6211 | 4.8795
621 | 18691.7891 | 4.4944
622 | 17800.6387 | 4.0728
623 | 16771.1953 | 3.9213
624 | 16167.4707 | 3.6809
625 | 15542.3867 | 3.5514
626 | 14718.416 | 3.5514
627 | 14136.5107 | 3.5514
628 | 14343.1318 | 3.5514
629 | 14082.4609 | 3.5514
630 | 13814.1934 | 3.5514
631 | 13756.0352 | 3.5514
632 | 14094.0557 | 3.5514
633 | 14081.8027 | 3.5514
634 | 14687.8457 | 3.5514
635 | 15866.9004 | 3.5514
636 | 18710.9355 | 3.6223
637 | 21070.0547 | 4.0427
638 | 23204.5312 | 3.9213
639 | 25388.2891 | 4.6932
640 | 28231.0625 | 5.4109
641 | 29599.2637 | 6.2077
642 | 29064.8535 | 6.5771
643 | 30704.4531 | 7.7029
644 | 31581.7383 | 7.8284
645 | 32172.0352 | 7.8284
646 | 30408.1797 | 7.8284
647 | 30235.5391 | 7.8284
648 | 30616.5703 | 7.8284
649 | 29527.6523 | 7.5764
650 | 28932.4844 | 7.455
651 | 28451.957 | 7.455
652 | 28660.9688 | 7.455
653 | 28308.0723 | 7.455
654 | 28254.2109 | 7.455
655 | 27926.6504 | 7.455
656 | 27504.2812 | 7.455
657 | 27277.1562 | 7.455
658 | 26107.3223 | 7.455
659 | 25169.9004 | 7.3968
660 | 25765.3008 | 6.8114
661 | 25631.1855 | 6.3864
662 | 25317.6699 | 6.5832
663 | 25831.0703 | 6.7258
664 | 26191.8281 | 6.7258
665 | 25289.1641 | 6.015
666 | 23457.6758 | 5.9743
667 | 20862.9277 | 5.5839
668 | 19172.957 | 5.0856
669 | 18014.5254 | 5.0317
670 | 17198.8496 | 4.3511
671 | 16459.8164 | 4.3118
672 | 15271.4268 | 4.0461
673 | 14691.2598 | 3.9082
674 | 14088.4258 | 3.9082
675 | 13591.4141 | 3.9082
676 | 13496.2656 | 4.2747
677 | 13737.666 | 4.2939
678 | 13824.541 | 3.9953
679 | 13544.793 | 3.9282
680 | 13560.0137 | 3.6976
681 | 13609.1621 | 3.5592
682 | 14266.8145 | 3.5592
683 | 15028.4902 | 3.5592
684 | 18635.0508 | 3.8669
685 | 20865.043 | 3.9612
686 | 23405.9297 | 4.1945
687 | 25549.3008 | 5.0237
688 | 28099.7988 | 5.8399
689 | 27938.4414 | 6.1664
690 | 28462.9453 | 6.6085
691 | 28888.2305 | 7.2614
692 | 28771.7266 | 7.9253
693 | 30266.4336 | 8.0761
694 | 30405.3066 | 8.0761
695 | 30471.8125 | 8.0761
696 | 29857.0312 | 8.0761
697 | 29022.7363 | 8.0761
698 | 28451.7051 | 8.0761
699 | 28019.6836 | 8.024
700 | 27237.0195 | 7.7081
701 | 26849.1133 | 7.7081
702 | 26427.4805 | 7.3384
703 | 26141.8281 | 7.2688
704 | 25576.543 | 7.1601
705 | 25403.2793 | 6.5006
706 | 24915.3945 | 6.7287
707 | 24389.8574 | 6.8808
708 | 24371.9961 | 6.5506
709 | 24672.6152 | 6.2549
710 | 24818.543 | 6.1482
711 | 25339.1426 | 6.1482
712 | 25077.416 | 6.1322
713 | 24389.3516 | 5.8021
714 | 22530.7617 | 5.5191
715 | 20336.6543 | 5.1161
716 | 18714.9355 | 4.9819
717 | 17749.0078 | 4.6921
718 | 16811.8184 | 4.3069
719 | 15700.7637 | 3.8765
720 | 14678.2373 | 3.742
721 | 14229.9111 | 3.6717
722 | 13863.4062 | 3.3752
723 | 13432.9727 | 3.7083
724 | 13302.9736 | 3.4914
725 | 12851.3408 | 3.4488
726 | 12614.1211 | 3.4488
727 | 12668.3594 | 3.4488
728 | 12543.7383 | 3.4488
729 | 12202.3398 | 3.4488
730 | 12170.4551 | 3.4488
731 | 12673.3496 | 3.4488
732 | 14191.2979 | 3.4488
733 | 15230.7637 | 3.7454
734 | 16253.543 | 3.4668
735 | 17146.4805 | 3.4577
736 | 19161.9453 | 3.4602
737 | 20308.2637 | 3.4652
738 | 21572.2109 | 3.7393
739 | 21866.2344 | 4.5355
740 | 22043.3398 | 4.8679
741 | 21887.6133 | 4.954
742 | 21700.3496 | 5.1768
743 | 21409.5703 | 5.3253
744 | 21353.9609 | 5.3253
745 | 21122.4453 | 5.3253
746 | 21171.1797 | 5.3253
747 | 20234.7695 | 5.3253
748 | 18841.9258 | 5.3253
749 | 18778.8203 | 5.3253
750 | 18630.4316 | 5.0632
751 | 19137.0938 | 4.9418
752 | 19257.2109 | 4.9418
753 | 19307.5781 | 5.2335
754 | 19125.9688 | 5.3265
755 | 19142.082 | 5.3265
756 | 19549.7148 | 5.3265
757 | 19693.8516 | 5.3265
758 | 19899.7383 | 4.9861
759 | 19508.957 | 4.9552
760 | 18305.2812 | 4.9552
761 | 17566.2285 | 4.6334
762 | 16792.8281 | 4.2291
763 | 16123.9111 | 4.2137
764 | 15331.248 | 4.2137
765 | 14692.9727 | 3.8995
766 | 14059.9189 | 3.829
767 | 13395.7832 | 3.829
768 | 12852.1094 | 3.5652
769 | 12508.0352 | 3.1434
770 | 12086.8369 | 3.0808
771 | 11936.959 | 3.0808
772 | 11754.4102 | 3.0808
773 | 10769.6328 | 3.0808
774 | 10512.4824 | 3.0808
775 | 10565.1055 | 3.0808
776 | 10841.4941 | 3.0808
777 | 10742.7598 | 3.0808
778 | 10955.5156 | 3.0808
779 | 10912.873 | 3.0808
780 | 11882.4336 | 2.765
781 | 12680.4746 | 2.7128
782 | 13457.6445 | 2.7128
783 | 13769.667 | 2.7128
784 | 14487.5732 | 2.7128
785 | 15565.0156 | 2.7128
786 | 17190.2285 | 2.7128
787 | 18179.1445 | 2.787
788 | 18527.1895 | 3.4264
789 | 19579.0938 | 3.5166
790 | 19828.6094 | 3.8758
791 | 19791.9883 | 3.8758
792 | 19707.4824 | 3.8758
793 | 19651.5996 | 4.1318
794 | 20030.748 | 4.5539
795 | 19715.875 | 4.3972
796 | 19001.3262 | 4.2772
797 | 18366.7969 | 4.2772
798 | 18539.9258 | 4.2772
799 | 18196.5234 | 4.2772
800 | 18282.1758 | 4.2772
801 | 18382.4297 | 4.2772
802 | 17367.125 | 4.6238
803 | 16118.6699 | 4.6519
804 | 15425.3848 | 4.6519
805 | 15039.8691 | 4.6151
806 | 15072.8574 | 4.5691
807 | 15177.4785 | 4.6519
808 | 15771.5215 | 4.6519
809 | 16226.5322 | 4.6519
810 | 16014.5967 | 4.3344
811 | 15275.4707 | 4.2412
812 | 14824.3008 | 3.907
813 | 13974.9951 | 3.8469
814 | 13228.3311 | 3.4822
815 | 12496.8584 | 3.229
816 | 11938.3398 | 2.7655
817 | 11369.5391 | 2.7251
818 | 11195.0117 | 2.7251
819 | 11068.7598 | 2.7251
820 | 10877.127 | 2.7251
821 | 10728.7344 | 2.7251
822 | 10877.8867 | 2.7251
823 | 10802.6211 | 2.7251
824 | 10893.4941 | 2.7251
825 | 10951.6328 | 2.7251
826 | 11945.9258 | 2.7251
827 | 13906.6768 | 2.7251
828 | 18237.0293 | 2.7251
829 | 20540.2852 | 3.1066
830 | 23873.6055 | 3.5118
831 | 28440.0723 | 4.3561
832 | 32128.0137 | 4.9819
833 | 33250.6055 | 5.7094
834 | 31572.2441 | 6.2728
835 | 32890.1914 | 7.0329
836 | 32753.3203 | 7.2822
837 | 34098.5078 | 7.2822
838 | 32940.8359 | 7.2822
839 | 30640.5918 | 7.2822
840 | 30354.1816 | 7.2822
841 | 29360.3906 | 7.2822
842 | 29497.4004 | 7.2822
843 | 28896.873 | 7.5837
844 | 28190.9453 | 7.2655
845 | 28121.8203 | 7.2554
846 | 28679.1055 | 7.2554
847 | 29061.2637 | 7.2554
848 | 26880.2402 | 7.1802
849 | 26371.3438 | 6.863
850 | 25602.4277 | 6.863
851 | 24713.9004 | 6.863
852 | 24789.2578 | 6.5295
853 | 24712.0156 | 6.0548
854 | 24527.7637 | 5.7145
855 | 24544.9844 | 5.7145
856 | 24804.6152 | 5.7145
857 | 24602.5 | 5.3588
858 | 23043.0566 | 5.1264
859 | 21246.9492 | 4.9797
860 | 19979.5039 | 4.9797
861 | 19216.957 | 4.6322
862 | 18015.7656 | 4.3104
863 | 16697.4492 | 3.6544
864 | 15518.1855 | 3.5045
865 | 15094.7334 | 3.5045
866 | 14546.5537 | 3.7506
867 | 14464.7002 | 3.8736
868 | 14209.8047 | 3.8736
869 | 14222.9316 | 3.8736
870 | 14262.5625 | 3.8736
871 | 14174.6777 | 3.8736
872 | 14471.9629 | 3.8736
873 | 14382.5605 | 3.8736
874 | 15369.5 | 3.8736
875 | 16573.5645 | 3.8736
876 | 19512.7246 | 3.8736
877 | 21882.582 | 3.8986
878 | 24315.2363 | 4.2431
879 | 26925.25 | 4.8483
880 | 27983.5469 | 5.531
881 | 28729.5898 | 6.2209
882 | 28757.9785 | 6.5447
883 | 30088.6641 | 7.354
884 | 30636.5684 | 7.4339
885 | 31712.1289 | 7.4339
886 | 32293.918 | 7.4339
887 | 31304.2441 | 7.4339
888 | 29406.1367 | 7.4339
889 | 29723.4004 | 7.4339
890 | 29783.0312 | 7.4339
891 | 29458.1387 | 7.4339
892 | 29188.1152 | 7.3905
893 | 27936.9473 | 7.0625
894 | 27346.0293 | 7.0013
895 | 26933.6406 | 6.7215
896 | 25467.0488 | 6.6634
897 | 25335.0469 | 6.7132
898 | 24789.7637 | 6.9416
899 | 23888.4766 | 7.0258
900 | 24128.5938 | 6.7069
901 | 24130.2266 | 6.4607
902 | 24067.9727 | 5.9425
903 | 23872.5938 | 5.8962
904 | 24087.7188 | 5.8962
905 | 24564.5 | 5.331
906 | 23238.4141 | 5.1592
907 | 21450.4453 | 5.1592
908 | 20125.7578 | 4.8899
909 | 19037.0742 | 4.3594
910 | 17702.3652 | 3.9459
911 | 16775.2188 | 3.8491
912 | 16067.123 | 3.5201
913 | 15578.6191 | 3.5201
914 | 15154.3232 | 3.5201
915 | 14720.417 | 3.5201
916 | 14313.7754 | 3.5201
917 | 14400.9922 | 3.5201
918 | 14131.0938 | 3.5201
919 | 14247.5645 | 3.5201
920 | 14782.8369 | 3.5201
921 | 15021.2256 | 3.5201
922 | 15860.7432 | 3.5201
923 | 16560.1855 | 3.5201
924 | 19506.084 | 3.5201
925 | 22474.1172 | 3.9745
926 | 25196.8906 | 4.2995
927 | 27187.25 | 4.8946
928 | 28009.9141 | 5.654
929 | 28432.2109 | 5.8003
930 | 28467.2207 | 6.4139
931 | 29482.3906 | 7.0623
932 | 29423.5176 | 7.2822
933 | 29496.8965 | 7.6319
934 | 28918.1152 | 7.6535
935 | 28949.748 | 7.2914
936 | 28949.9785 | 7.3402
937 | 28295.5898 | 7.6468
938 | 28123.8203 | 7.6468
939 | 27445.041 | 7.2255
940 | 27451.2715 | 6.8451
941 | 27378.1895 | 6.8451
942 | 26577.3652 | 6.8451
943 | 26148.7227 | 6.8451
944 | 25799.7109 | 6.8451
945 | 25447.8281 | 6.8451
946 | 24432.1328 | 6.8451
947 | 24048.5 | 6.8451
948 | 24227.375 | 6.625
949 | 24014.7305 | 6.2972
950 | 23948.8672 | 6.0668
951 | 23958.7305 | 6.0668
952 | 24083.3516 | 6.0668
953 | 24329.3945 | 5.6971
954 | 23081.0566 | 5.3128
955 | 22907.0566 | 5.0615
956 | 20050.5156 | 4.8891
957 | 18589.9258 | 4.5515
958 | 17561.125 | 4.1906
959 | 16614.2285 | 3.841
960 | 15741.124 | 3.5494
961 | 15233.7451 | 3.4421
962 | 15017.248 | 3.4421
963 | 14697.1094 | 3.8008
964 | 14293.5732 | 3.81
965 | 14306.1943 | 3.81
966 | 14359.709 | 3.81
967 | 13979.9414 | 3.81
968 | 14436.1943 | 3.4856
969 | 14816.1211 | 3.432
970 | 15621.8896 | 3.432
971 | 16242.0801 | 3.619
972 | 19928.5273 | 3.5067
973 | 22491.7285 | 3.5067
974 | 25906.9551 | 3.846
975 | 27344.8828 | 4.5676
976 | 28115.6836 | 5.1536
977 | 28313.5664 | 5.7587
978 | 28629.1055 | 6.202
979 | 29258.873 | 6.8931
980 | 29186.2305 | 7.2202
981 | 30436.3164 | 7.5497
982 | 30577.0547 | 7.3555
983 | 29979.4219 | 7.3208
984 | 29685.6523 | 7.6346
985 | 29566.5273 | 7.6346
986 | 28421.2207 | 7.6346
987 | 29113.2422 | 7.2475
988 | 26977.4082 | 7.2443
989 | 26787.7559 | 6.8931
990 | 25547.3223 | 6.854
991 | 25626.8398 | 6.854
992 | 25404.6797 | 6.854
993 | 26885.2715 | 6.854
994 | 25559.3242 | 6.854
995 | 23919.1211 | 6.854
996 | 24525.8789 | 6.4928
997 | 24312.2461 | 6.0878
998 | 24043.2363 | 5.7452
999 | 24153.8574 | 5.6866
1000 | 24498.6152 | 5.6866
1001 | 24495.9941 | 5.6866
1002 | 22850.2773 | 5.3627
1003 | 20782.9258 | 4.9822
1004 | 19346.2188 | 4.9032
1005 | 18325.418 | 4.229
1006 | 17386.7344 | 4.2025
1007 | 16604.4375 | 4.1167
1008 | 15845.1016 | 3.4666
1009 | 15258.6182 | 3.4666
1010 | 15661.333 | 3.4666
1011 | 15363.1973 | 3.4666
1012 | 13967.6152 | 3.4666
1013 | 13580.7842 | 3.4666
1014 | 13866.3086 | 3.4666
1015 | 13824.5391 | 3.4666
1016 | 13760.793 | 3.4666
1017 | 13768.6797 | 3.4666
1018 | 14585.0664 | 3.4666
1019 | 15258.1221 | 3.4666
1020 | 18287.9023 | 3.527
1021 | 20746.5391 | 3.6979
1022 | 22614.5078 | 3.6582
1023 | 24097.7207 | 4.3876
1024 | 25987.4375 | 5.1463
1025 | 27745.041 | 5.871
1026 | 27980.8086 | 6.4784
1027 | 27908.7891 | 6.8366
1028 | 27699.6836 | 6.6723
1029 | 28552.8301 | 6.6723
1030 | 28526.4629 | 6.6723
1031 | 27784.8086 | 6.9993
1032 | 27255.7559 | 7.0425
1033 | 26290.4707 | 6.6846
1034 | 25345.416 | 6.9192
1035 | 24773.625 | 6.6486
1036 | 24688.5 | 6.6422
1037 | 24402.2461 | 6.4187
1038 | 24127.3516 | 6.2698
1039 | 24396.5 | 5.8982
1040 | 24775.9004 | 5.8327
1041 | 24778.3848 | 6.0964
1042 | 24275.7422 | 6.2006
1043 | 23601.9531 | 6.1797
1044 | 23736.0684 | 5.8456
1045 | 23530.0664 | 5.8338
1046 | 23362.9414 | 5.8338
1047 | 22987.1504 | 5.8338
1048 | 22738.1621 | 5.7725
1049 | 22358.875 | 5.1257
1050 | 20872.2852 | 5.0733
1051 | 18614.5684 | 4.5458
1052 | 17351.3555 | 4.3285
1053 | 16459.1738 | 4.3285
1054 | 15818.9004 | 4.0835
1055 | 15079.1104 | 3.6228
1056 | 14312.2578 | 3.5759
1057 | 13483.8174 | 3.5759
1058 | 12922.1709 | 3.5759
1059 | 12539.7383 | 3.5759
1060 | 12877.9707 | 3.5759
1061 | 12557.0977 | 3.2844
1062 | 12257.7188 | 3.1957
1063 | 12166.4336 | 3.1957
1064 | 11998.3398 | 3.1957
1065 | 11920.6855 | 3.1554
1066 | 11910.4336 | 2.8244
1067 | 11661.0547 | 2.8244
1068 | 12738.8652 | 3.1381
1069 | 13670.5195 | 3.1316
1070 | 14617.9629 | 2.849
1071 | 15732.0273 | 3.4194
1072 | 18014.8926 | 3.9437
1073 | 19357.4629 | 3.9594
1074 | 20400.6523 | 4.1816
1075 | 21034.5586 | 4.6158
1076 | 20879.8008 | 4.7154
1077 | 20126.8828 | 5.0766
1078 | 20296.5156 | 5.0956
1079 | 20123.3906 | 5.0956
1080 | 19973.1367 | 5.4513
1081 | 20038.7461 | 5.4002
1082 | 19498.9785 | 5.0834
1083 | 19234.957 | 5.0834
1084 | 18713.5566 | 5.0834
1085 | 18942.1992 | 5.0834
1086 | 18911.4414 | 5.0834
1087 | 18980.8203 | 5.0834
1088 | 19281.3262 | 5.0834
1089 | 19296.5898 | 5.0834
1090 | 19593.8516 | 5.0834
1091 | 19515.9688 | 5.3759
1092 | 19213.0938 | 5.2232
1093 | 19233.9473 | 5.0444
1094 | 21319.4531 | 5.0444
1095 | 20797.2754 | 5.0444
1096 | 17883.8809 | 4.8122
1097 | 16424.0469 | 4.33
1098 | 15511.6377 | 4.2304
1099 | 14924.373 | 4.2304
1100 | 14212.9297 | 3.9757
1101 | 13944.0566 | 3.8435
1102 | 13065.3711 | 3.8435
1103 | 12293.2344 | 3.4657
1104 | 11606.9805 | 3.38
1105 | 10934.2441 | 3.0529
1106 | 10683.9277 | 3.0529
1107 | 10564.4336 | 3.0529
1108 | 10428.4336 | 3.0529
1109 | 10016.3164 | 2.8125
1110 | 9872.5781 | 2.6783
1111 | 9743.4531 | 2.6783
1112 | 9807.0625 | 2.6783
1113 | 9824.3281 | 2.6783
1114 | 10020.7148 | 2.6783
1115 | 9735.1992 | 2.6783
1116 | 10798.5039 | 2.6783
1117 | 11421.9062 | 2.6783
1118 | 12080.0645 | 2.6783
1119 | 12731.2344 | 2.6783
1120 | 14060.0566 | 2.6783
1121 | 15055.9844 | 3.049
1122 | 16264.5537 | 3.0585
1123 | 16960.9648 | 3.0585
1124 | 17629.8594 | 3.0585
1125 | 18959.4414 | 3.6489
1126 | 19063.0742 | 3.8156
1127 | 19292.2188 | 3.8156
1128 | 19950.3789 | 3.8156
1129 | 20161.2754 | 3.8156
1130 | 19280.5684 | 3.8156
1131 | 18857.0742 | 4.0472
1132 | 19017.9453 | 4.1813
1133 | 18815.6953 | 4.1813
1134 | 18844.5664 | 4.1813
1135 | 18724.4297 | 4.1813
1136 | 18399.5352 | 4.1813
1137 | 18191.2832 | 4.1813
1138 | 17214.2285 | 4.2275
1139 | 16044.6914 | 4.5504
1140 | 15221.3643 | 4.5504
1141 | 14807.9619 | 4.5504
1142 | 14827.6172 | 4.5504
1143 | 14810.4473 | 4.5504
1144 | 15284.1211 | 4.2972
1145 | 15600.2578 | 4.1657
1146 | 15524.0059 | 3.8735
1147 | 14937.458 | 3.7403
1148 | 14178.0566 | 3.4209
1149 | 13393.666 | 3.4209
1150 | 12831.834 | 3.4209
1151 | 12312.707 | 3.1422
1152 | 11847.0547 | 2.741
1153 | 11687.9922 | 2.6727
1154 | 11347.4355 | 2.6727
1155 | 11278.707 | 2.6727
1156 | 11127.6328 | 2.6727
1157 | 10740.3672 | 2.6727
1158 | 11054.4844 | 2.6727
1159 | 10973.5176 | 2.911
1160 | 11013.832 | 3.054
1161 | 11128.6094 | 3.0064
1162 | 12036.5488 | 2.6727
1163 | 13723.3828 | 2.6727
1164 | 17336.6504 | 2.9296
1165 | 19781.6426 | 3.073
1166 | 22332.3496 | 3.073
1167 | 24717.375 | 3.8113
1168 | 27225.1348 | 4.6073
1169 | 29569.1484 | 5.2894
1170 | 30081.0547 | 5.6346
1171 | 30479.8125 | 6.3581
1172 | 32826.9297 | 6.5151
1173 | 32532.6777 | 6.8984
1174 | 30835.0762 | 6.9332
1175 | 31339.4863 | 6.9332
1176 | 29985.5371 | 6.9332
1177 | 28218.6934 | 6.9332
1178 | 28986.3477 | 6.9332
1179 | 28405.7031 | 6.6875
1180 | 29226.5059 | 6.6567
1181 | 27636.7871 | 6.5686
1182 | 27870.168 | 6.5686
1183 | 28242.9453 | 6.5686
1184 | 27120.6289 | 6.5686
1185 | 27296.168 | 6.2439
1186 | 26481.7109 | 6.1939
1187 | 25672.9316 | 6.4859
1188 | 25299.7617 | 6.26
1189 | 25535.0488 | 5.9656
1190 | 24956.0156 | 5.7891
1191 | 24819.7422 | 5.458
1192 | 24565.7422 | 5.458
1193 | 24449.7188 | 5.1443
1194 | 23291.3105 | 5.0778
1195 | 21497.9609 | 4.7763
1196 | 19898.8633 | 4.379
1197 | 18834.9355 | 4.333
1198 | 17714.1328 | 3.8069
1199 | 16834.0703 | 3.5948
1200 | 15857.4922 | 3.5948
1201 | 15114.7344 | 3.5346
1202 | 14500.0488 | 3.2146
1203 | 14106.5107 | 3.2146
1204 | 14214.5107 | 3.2146
1205 | 14272.3438 | 3.2146
1206 | 14405.3418 | 3.2146
1207 | 13997.7832 | 3.2146
1208 | 14322.9297 | 3.2146
1209 | 14383.5195 | 3.2146
1210 | 15285.1318 | 3.2146
1211 | 16344.0801 | 3.4699
1212 | 19365.5977 | 3.5881
1213 | 22014.6562 | 3.7018
1214 | 23858.2031 | 3.92
1215 | 27336.7656 | 4.2909
1216 | 28180.6934 | 5.0615
1217 | 28316.9453 | 5.8118
1218 | 31112.2227 | 6.4145
1219 | 31611.3711 | 6.9655
1220 | 32878.8164 | 6.9655
1221 | 32508.9297 | 6.9655
1222 | 31111.8555 | 6.9655
1223 | 30932.3594 | 6.9655
1224 | 31753.5078 | 6.9655
1225 | 29106.3691 | 6.9655
1226 | 28600.3477 | 6.9655
1227 | 28862.9688 | 6.9029
1228 | 33238.9727 | 6.9156
1229 | 32905.918 | 6.5641
1230 | 30541.4434 | 6.5485
1231 | 30283.9277 | 6.5485
1232 | 29381.5176 | 6.773
1233 | 29538.6211 | 6.5597
1234 | 28103.3359 | 6.4627
1235 | 27048.6289 | 6.8061
1236 | 26228.5859 | 6.4062
1237 | 25715.1855 | 5.9855
1238 | 25496.291 | 5.7633
1239 | 25510.7969 | 5.6587
1240 | 24486.4785 | 5.6587
1241 | 24828.3828 | 5.303
1242 | 23780.2031 | 4.9947
1243 | 21593.3398 | 4.5853
1244 | 20036.0117 | 4.5236
1245 | 18137.1445 | 4.2027
1246 | 17273.3555 | 3.8505
1247 | 16134.8066 | 3.7855
1248 | 15099.8389 | 3.7389
1249 | 14551.8389 | 3.4131
1250 | 14334.4473 | 3.4131
1251 | 13800.4248 | 3.4131
1252 | 13905.5293 | 3.4131
1253 | 13642.2656 | 3.4131
1254 | 13729.8027 | 3.4131
1255 | 13657.0352 | 3.4131
1256 | 13966.6035 | 3.4131
1257 | 14036.4775 | 3.4131
1258 | 14787.3311 | 3.4131
1259 | 15942.1211 | 3.4131
1260 | 18945.4629 | 3.4131
1261 | 22062.0137 | 3.7495
1262 | 24803.1523 | 3.8307
1263 | 26991.0293 | 4.4263
1264 | 28898.2305 | 5.0901
1265 | 30216.8008 | 5.5724
1266 | 30309.9277 | 6.2383
1267 | 32074.4023 | 6.7224
1268 | 31403.875 | 6.805
1269 | 32795.8086 | 7.1822
1270 | 34107.1523 | 7.1919
1271 | 33689.543 | 6.9382
1272 | 33775.8281 | 6.8206
1273 | 32306.3066 | 6.8206
1274 | 32737.3477 | 7.0888
1275 | 32174.0352 | 7.1837
1276 | 30083.6543 | 6.9733
1277 | 29862.252 | 7.086
1278 | 28895.7266 | 7.086
1279 | 28092.6934 | 7.086
1280 | 27863.4297 | 7.086
1281 | 27993.8418 | 7.086
1282 | 27278.3984 | 6.7394
1283 | 26088.9531 | 6.8409
1284 | 26164.332 | 6.6144
1285 | 25926.3105 | 6.5987
1286 | 25081.0059 | 6.2604
1287 | 24924.1328 | 6.2263
1288 | 25109.2793 | 5.8357
1289 | 25144.5215 | 5.4803
1290 | 24111.6055 | 5.0673
1291 | 21952.3496 | 5.0009
1292 | 20367.7578 | 4.6565
1293 | 19205.3457 | 4.2742
1294 | 18170.4102 | 4.0422
1295 | 16440.668 | 3.574
1296 | 15517.0156 | 3.5212
1297 | 14895.3408 | 3.5212
1298 | 14601.3408 | 3.5212
1299 | 14402.6992 | 3.5212
1300 | 14172.9297 | 3.5212
1301 | 14183.6885 | 3.5212
1302 | 14494.0781 | 3.5212
1303 | 14145.1826 | 3.5212
1304 | 14188.4463 | 3.5212
1305 | 14297.8887 | 3.5212
1306 | 14827.3193 | 3.5212
1307 | 15669.0156 | 3.5212
1308 | 19275.5566 | 3.5212
1309 | 23939.4473 | 3.529
1310 | 25975.4375 | 3.8556
1311 | 27763.1562 | 4.4889
1312 | 29118.959 | 5.0963
1313 | 29138.5918 | 5.822
1314 | 29137.4648 | 6.6262
1315 | 30752.7715 | 7.1217
1316 | 30659.1602 | 7.0815
1317 | 31804.6484 | 7.5205
1318 | 29828.6641 | 7.8364
1319 | 29841.5371 | 7.578
1320 | 29354.1152 | 7.4673
1321 | 29334.7578 | 7.4673
1322 | 29505.6328 | 7.528
1323 | 29170.3672 | 7.551
1324 | 29015.4941 | 7.464
1325 | 28446.2109 | 7.464
1326 | 28260.4414 | 7.464
1327 | 27770.9238 | 7.1861
1328 | 28729.2207 | 6.7439
1329 | 28858.4844 | 6.982
1330 | 28890.4844 | 6.8192
1331 | 28926.7148 | 6.6935
1332 | 28136.1875 | 6.6935
1333 | 27919.7988 | 6.1069
1334 | 27398.6504 | 5.9319
1335 | 26421.3438 | 5.9319
1336 | 25533.5547 | 5.9319
1337 | 25716.3125 | 5.9319
1338 | 24522.8691 | 5.5329
1339 | 22649.4043 | 5.1715
1340 | 20633.2969 | 4.6075
1341 | 18904.6836 | 4.4066
1342 | 17955.7891 | 4.3381
1343 | 16739.334 | 3.7184
1344 | 15986.3662 | 3.567
1345 | 15334.4297 | 3.567
1346 | 15294.6475 | 3.2554
1347 | 14896.8584 | 3.1968
1348 | 14926.7207 | 3.1968
1349 | 15221.6367 | 3.1968
1350 | 15142.2363 | 3.1968
1351 | 15188.9951 | 3.1968
1352 | 15153.3633 | 3.1968
1353 | 15112.7422 | 3.1968
1354 | 14748.4678 | 3.1968
1355 | 15391.752 | 3.1968
1356 | 19118.4531 | 3.1968
1357 | 21872.6016 | 3.4849
1358 | 23475.1934 | 3.918
1359 | 28145.4297 | 4.2316
1360 | 28831.2207 | 5.0299
1361 | 29991.0312 | 5.4897
1362 | 32372.6777 | 5.8485
1363 | 32686.9297 | 6.8001
1364 | 32529.2988 | 6.9388
1365 | 30663.832 | 6.9388
1366 | 29733.7695 | 6.9388
1367 | 29026.9883 | 6.7066
1368 | 29078.7363 | 6.8471
1369 | 28558.5996 | 6.9287
1370 | 28146.5781 | 6.8724
1371 | 28124.5781 | 6.8445
1372 | 27564.7871 | 6.9332
1373 | 27338.3984 | 6.619
1374 | 26838.5137 | 6.164
1375 | 25729.207 | 6.1326
1376 | 25849.4375 | 6.1326
1377 | 25539.8066 | 5.7522
1378 | 25032.9102 | 6.0174
1379 | 23955.7188 | 6.1783
1380 | 24220.1094 | 6.1783
1381 | 23912.0898 | 5.8182
1382 | 23771.9512 | 5.7959
1383 | 23294.6875 | 5.7959
1384 | 22789.1504 | 5.5085
1385 | 22412.875 | 5.429
1386 | 21585.9609 | 5.1072
1387 | 20009 | 4.7187
1388 | 18180.4102 | 4.4337
1389 | 16794.9453 | 4.0741
1390 | 15858.5332 | 3.9461
1391 | 15139.1973 | 3.6129
1392 | 14187.4277 | 3.5759
1393 | 13819.2676 | 3.5759
1394 | 13130.3516 | 3.3005
1395 | 12936.6768 | 3.2046
1396 | 12701.501 | 3.2046
1397 | 12288.0352 | 3.2046
1398 | 12260.3379 | 3.2046
1399 | 12251.4648 | 3.2046
1400 | 12094.4551 | 3.2046
1401 | 11877.3066 | 3.2046
1402 | 11826.1797 | 3.2046
1403 | 11700.0762 | 3.2046
1404 | 12583.3281 | 2.9669
1405 | 13426.9512 | 2.8244
1406 | 14412.1729 | 3.0873
1407 | 15475.3525 | 3.1912
1408 | 17096.207 | 3.1912
1409 | 18705.1895 | 3.4759
1410 | 20007 | 4.2876
1411 | 19913.2539 | 4.6853
1412 | 20730.6523 | 4.9757
1413 | 21912.625 | 5.0522
1414 | 22226.4883 | 5.0522
1415 | 21812.9922 | 5.4
1416 | 22761.4043 | 5.2497
1417 | 22633.8867 | 5.1146
1418 | 22035.75 | 5.1146
1419 | 21863.4746 | 5.3861
1420 | 22162.0039 | 5.5071
1421 | 21514.2109 | 5.5071
1422 | 20755.043 | 5.1787
1423 | 21802.3477 | 5.0265
1424 | 21693.2227 | 5.0265
1425 | 21045.0645 | 5.0766
1426 | 20567.2969 | 5.3655
1427 | 20590.7891 | 5.3881
1428 | 20483.5273 | 5.4792
1429 | 20280.6523 | 5.4792
1430 | 20113.2539 | 5.4668
1431 | 19700.6113 | 5.1394
1432 | 18855.0508 | 4.8553
1433 | 18405.6719 | 4.7076
1434 | 17916.7559 | 4.3787
1435 | 17193.1016 | 4.2204
1436 | 16563.4492 | 4.2204
1437 | 15732.0273 | 3.88
1438 | 15152.6055 | 3.6127
1439 | 14285.71 | 3.4688
1440 | 13638.7637 | 3.2281
1441 | 13150.6699 | 3.1031
1442 | 12708.4961 | 3.1031
1443 | 12715.6016 | 3.1031
1444 | 12415.2129 | 3.1031
1445 | 12309.9473 | 3.1031
1446 | 12089.0547 | 3.1031
1447 | 12040.0625 | 3.1031
1448 | 11977.9492 | 3.1031
1449 | 12020.1797 | 3.1031
1450 | 11773.1895 | 2.8083
1451 | 11565.6758 | 2.7307
1452 | 11976.0645 | 2.7307
1453 | 12676.9805 | 3.0438
1454 | 13340.6348 | 3.1065
1455 | 14048.6768 | 3.1065
1456 | 14747.3418 | 3.1065
1457 | 15732.0273 | 3.1065
1458 | 16796.0918 | 3.1065
1459 | 17702.3867 | 3.1065
1460 | 18876.7031 | 3.5992
1461 | 20426.9062 | 3.8502
1462 | 20939.1797 | 3.8502
1463 | 21221.5703 | 3.8502
1464 | 21511.5898 | 3.887
1465 | 21013.5703 | 3.9328
1466 | 21151.707 | 4.0847
1467 | 21088.0742 | 4.2126
1468 | 20978.1914 | 4.5124
1469 | 21134.9492 | 4.5995
1470 | 21136.9492 | 4.5995
1471 | 21059.5703 | 4.5995
1472 | 20906.3066 | 4.5995
1473 | 20959.6836 | 4.5995
1474 | 19592.4961 | 4.5995
1475 | 18290.5469 | 4.5995
1476 | 17077.8398 | 4.5995
1477 | 16437.8184 | 4.5995
1478 | 16351.4268 | 4.5995
1479 | 16051.6592 | 4.3082
1480 | 16325.3125 | 4.2315
1481 | 16534.4395 | 4.2315
1482 | 16701.4707 | 3.9662
1483 | 16170.165 | 3.8479
1484 | 15725.543 | 3.8479
1485 | 14890.9727 | 3.5107
1486 | 14237.5732 | 3.4766
1487 | 13695.667 | 3.1186
1488 | 12970.6777 | 3.0964
1489 | 12609.8467 | 3.0964
1490 | 12301.0674 | 2.6975
1491 | 12176.5195 | 2.6448
1492 | 12122.541 | 2.6448
1493 | 11963.8467 | 2.6448
1494 | 11705.4648 | 2.6448
1495 | 11634.6855 | 2.6448
1496 | 11706.4531 | 2.6448
1497 | 11790.1797 | 2.6448
1498 | 11795.6953 | 2.6448
1499 | 11782.5703 | 2.6448
1500 | 12752.1289 | 2.6915
1501 | 13293.2773 | 3.0184
1502 | 13904.8145 | 3.3953
1503 | 14796.7422 | 4.0854
1504 | 15823.9121 | 4.8041
1505 | 16932.8711 | 5.4393
1506 | 18359.8086 | 5.9834
1507 | 19305.8516 | 7.0025
1508 | 20180.5371 | 6.9786
1509 | 20663.8008 | 7.1488
1510 | 21236.7168 | 7.1763
1511 | 22417.4023 | 7.1763
1512 | 22584.5508 | 7.2918
1513 | 22472.7812 | 6.96
1514 | 22579.0352 | 6.96
1515 | 22753.0352 | 6.96
1516 | 23164.4141 | 6.7755
1517 | 22444.2773 | 6.841
1518 | 21001.707 | 6.7899
1519 | 20456.168 | 6.6755
1520 | 20316.9258 | 6.6344
1521 | 20284.4004 | 6.5667
1522 | 20823.9375 | 6.4579
1523 | 19996.9062 | 6.6073
1524 | 19865 | 6.3763
1525 | 19551.9902 | 5.9901
1526 | 19049.7148 | 5.7261
1527 | 18795.5781 | 5.742
1528 | 17722.5039 | 5.5787
1529 | 17037.8398 | 5.2584
1530 | 17037.9531 | 4.8907
1531 | 16660.6914 | 4.6426
1532 | 15642.3965 | 4.4461
1533 | 14700.8359 | 4.1065
1534 | 13838.3086 | 3.7662
1535 | 13032.8652 | 3.6574
1536 | 12506.4766 | 3.2915
1537 | 12178.8223 | 3.1898
1538 | 11807.9199 | 3.229
1539 | 11444.7715 | 3.6766
1540 | 11494.1797 | 3.5711
1541 | 11886.6855 | 3.5358
1542 | 11616.916 | 3.5473
1543 | 11471.9062 | 3.5638
1544 | 11649.5586 | 3.5265
1545 | 11743.0547 | 3.5235
1546 | 12213.0977 | 3.4371
1547 | 13490.6338 | 3.4748
1548 | 18157.1465 | 3.6275
1549 | 20859.1602 | 3.7796
1550 | 22935.0352 | 4.1031
1551 | 24119.2148 | 4.6795
1552 | 25943.5742 | 5.138
1553 | 26773.4805 | 5.7024
1554 | 27117.3867 | 6.2898
1555 | 28531.8418 | 7.0829
1556 | 28768.7363 | 7.2541
1557 | 28611.2207 | 7.4477
1558 | 28670.7363 | 7.4083
1559 | 28458.5781 | 7.4305
1560 | 30205.7891 | 7.31
1561 | 30321.3281 | 7.321
1562 | 29202.7578 | 7.2721
1563 | 28009.3359 | 7.0247
1564 | 29607.2852 | 6.8512
1565 | 28164.2109 | 6.7834
1566 | 28090.3027 | 6.7973
1567 | 26411.9863 | 6.7319
1568 | 24565.2793 | 6.5678
1569 | 24773.418 | 6.4788
1570 | 24809.9219 | 6.4718
1571 | 23959.0977 | 6.5323
1572 | 23840.7305 | 6.4804
1573 | 24303.9961 | 6.1997
1574 | 23913.6055 | 6.0627
1575 | 23926.9609 | 5.9339
1576 | 23828.709 | 5.7951
1577 | 23875.9727 | 5.3863
1578 | 23099.0352 | 5.2323
1579 | 21367.2012 | 4.8474
1580 | 19781.9902 | 4.5698
1581 | 18749.9473 | 4.0622
1582 | 17307.8594 | 3.8043
1583 | 16352.5537 | 3.6928
1584 | 15432.9219 | 3.4193
1585 | 14901.3535 | 3.4097
1586 | 14365.0371 | 3.2977
1587 | 15011.7871 | 3.5519
1588 | 17772.3262 | 3.4344
1589 | 18116.0938 | 3.5504
1590 | 18442.7363 | 3.3479
1591 | 17613.5664 | 3.3564
1592 | 16734.7441 | 3.5243
1593 | 16786.1992 | 3.612
1594 | 17469.4082 | 3.4493
1595 | 18689.8711 | 3.4185
1596 | 22247.0137 | 3.3895
1597 | 24580.1641 | 3.6976
1598 | 27086.7969 | 3.8754
1599 | 29426.5488 | 4.5826
1600 | 30159.7148 | 5.0007
1601 | 29333.8535 | 5.6495
1602 | 29453.0156 | 6.4343
1603 | 29098.1367 | 6.9192
1604 | 29453.0098 | 7.0821
1605 | 29012.4844 | 7.3341
1606 | 29507.4004 | 7.3845
1607 | 29671.1465 | 7.1908
1608 | 27874.5781 | 7.239
1609 | 28230.4629 | 7.2337
1610 | 28129.084 | 7.1292
1611 | 28441.3359 | 6.9204
1612 | 28226.1875 | 6.8989
1613 | 28604.1152 | 6.8309
1614 | 27741.3574 | 6.6164
1615 | 27970.2109 | 6.6159
1616 | 25109.5547 | 6.4823
1617 | 24968.3125 | 6.4959
1618 | 24478.6172 | 6.5222
1619 | 23784.7539 | 6.6356
1620 | 24156.2676 | 6.6335
1621 | 23880.6152 | 6.3236
1622 | 23921.0039 | 6.0898
1623 | 23709.0039 | 6.1482
1624 | 23568.3398 | 5.903
1625 | 23281.4688 | 5.5557
1626 | 22735.793 | 5.1625
1627 | 21257.4531 | 4.9903
1628 | 19641.3906 | 4.6151
1629 | 18609.5781 | 4.2709
1630 | 17527.2383 | 4.0053
1631 | 16602.2285 | 3.7801
1632 | 15578.251 | 3.439
1633 | 14849.334 | 3.2966
1634 | 14426.6699 | 3.2256
1635 | 13900.8789 | 3.388
1636 | 13987.29 | 3.2331
1637 | 13953.5645 | 3.2186
1638 | 14076.2666 | 3.2351
1639 | 14214.0352 | 3.3557
1640 | 14037.1826 | 3.296
1641 | 14056.3301 | 3.3507
1642 | 14601.0156 | 3.3144
1643 | 15408.583 | 3.4218
1644 | 18668.1152 | 3.48
1645 | 21044.3574 | 3.64
1646 | 22849.7832 | 3.9386
1647 | 24213.9727 | 4.4313
1648 | 27562.5352 | 5.1396
1649 | 28577.3574 | 5.8209
1650 | 28625.2207 | 6.3692
1651 | 29497.1484 | 7.0054
1652 | 29005.6328 | 7.1172
1653 | 29677.7891 | 7.3791
1654 | 29504.4102 | 7.3764
1655 | 29118.0215 | 7.2174
1656 | 28809.2422 | 7.2274
1657 | 29247.4219 | 7.1672
1658 | 28472.1152 | 7.2154
1659 | 27790.4629 | 7.2109
1660 | 27238.1875 | 6.9744
1661 | 27285.5684 | 6.7673
1662 | 26944.8086 | 6.546
1663 | 27023.293 | 6.4572
1664 | 25841.25 | 6.3093
1665 | 25214.9531 | 6.2903
1666 | 24850.9336 | 6.349
1667 | 24147.6484 | 6.4608
1668 | 24266.3848 | 6.279
1669 | 24483.7852 | 5.9961
1670 | 24161.3945 | 5.8142
1671 | 23892.7539 | 5.6795
1672 | 23808.9844 | 5.4205
1673 | 23635.9727 | 5.3919
1674 | 22964.1836 | 5.036
1675 | 21111.2227 | 4.6567
1676 | 19603.6211 | 4.433
1677 | 18774.4531 | 4.1708
1678 | 17990.1562 | 3.8463
1679 | 16681.9551 | 3.5934
1680 | 15397.1973 | 3.4059
1681 | 14948.3662 | 3.1889
1682 | 14620.5107 | 3.0975
1683 | 13874.793 | 3.278
1684 | 13700.0352 | 3.1612
1685 | 13720.5391 | 3.148
1686 | 13931.0459 | 3.1545
1687 | 13814.793 | 3.2262
1688 | 13790.1709 | 3.0913
1689 | 13857.2979 | 3.0599
1690 | 14356.1943 | 3.0809
1691 | 15046.4668 | 3.2524
1692 | 18250.6621 | 3.2512
1693 | 20226.2637 | 3.4788
1694 | 21943.2441 | 3.7034
1695 | 23704.3203 | 4.1333
1696 | 25007.1426 | 4.9049
1697 | 25831.6914 | 5.4389
1698 | 27203.6387 | 6.1341
1699 | 27235.5254 | 6.7037
1700 | 28124.4414 | 6.837
1701 | 28329.4512 | 6.2222
1702 | 28320.209 | 5.3672
1703 | 27972.1895 | 5.3443
1704 | 26460.998 | 5.372
1705 | 25929.3438 | 6.8086
1706 | 25315.9434 | 6.9115
1707 | 25521.3438 | 6.7874
1708 | 25009.5547 | 6.4976
1709 | 24150.5215 | 6.4065
1710 | 24143.3945 | 6.2647
1711 | 23825.1211 | 7.2626
1712 | 23817.1211 | 6.0194
1713 | 24152.5215 | 6.0308
1714 | 23705.7422 | 5.9759
1715 | 22900.0898 | 5.7827
1716 | 23042.457 | 5.859
1717 | 23011.8164 | 5.4637
1718 | 22411.793 | 5.5176
1719 | 22179.0137 | 5.4776
1720 | 21778.7402 | 5.3153
1721 | 21209.5918 | 5.0806
1722 | 20245.6641 | 4.7458
1723 | 18550.0625 | 4.4715
1724 | 16977.9766 | 4.308
1725 | 16571.1953 | 3.8815
1726 | 15686.6465 | 3.5831
1727 | 14940.4902 | 3.4335
1728 | 14269.5938 | 3.3105
1729 | 13636.3535 | 3.0612
1730 | 13095.3633 | 3.2065
1731 | 12839.8242 | 3.4161
1732 | 12367.2988 | 3.3441
1733 | 12145.2773 | 3.2727
1734 | 12152.1211 | 3.3614
1735 | 12008.8438 | 3.2069
1736 | 12651.6016 | 3.02
1737 | 12976.3809 | 2.8369
1738 | 12564.2227 | 2.9102
1739 | 13234.1289 | 3.0471
1740 | 14562.2168 | 3.0433
1741 | 15157.1094 | 3.2008
1742 | 16371.5645 | 3.0526
1743 | 17358.8496 | 2.9778
1744 | 19031.3242 | 3.2919
1745 | 20031.873 | 3.8021
1746 | 21333.0859 | 4.123
1747 | 22081.4961 | 4.7094
1748 | 22185.498 | 5.0111
1749 | 22259.3809 | 5.1542
1750 | 22092.2539 | 5.165
1751 | 21612.7383 | 5.0656
1752 | 21944.5078 | 5.151
1753 | 21225.4746 | 5.1575
1754 | 19418.8848 | 5.1447
1755 | 18968.2422 | 5.0042
1756 | 18473.9668 | 4.9826
1757 | 18511.5996 | 4.6646
1758 | 18521.4844 | 4.7286
1759 | 18500.9785 | 4.8473
1760 | 18842.3789 | 4.8521
1761 | 19239.2539 | 4.7716
1762 | 19010.3789 | 4.9434
1763 | 18910.9785 | 5.006
1764 | 18745.3457 | 5.2261
1765 | 18516.8203 | 4.987
1766 | 18147.3047 | 4.7422
1767 | 17860.5234 | 4.8197
1768 | 16673.4707 | 4.7125
1769 | 15397.0176 | 4.2175
1770 | 15026.374 | 4.0641
1771 | 14436.0781 | 4.1083
1772 | 13892.8145 | 3.9592
1773 | 13357.6465 | 3.7784
1774 | 12699.7383 | 3.5331
1775 | 12141.0762 | 3.3217
1776 | 11515.4219 | 2.9823
1777 | 11043.2344 | 3.0349
1778 | 10652.9082 | 2.8367
1779 | 10470.1367 | 3.1381
1780 | 10312.7363 | 2.9806
1781 | 10210.7148 | 2.8977
1782 | 9873.1992 | 2.8308
1783 | 9763.7031 | 2.8275
1784 | 9824.9453 | 2.7407
1785 | 9790.4629 | 2.8939
1786 | 9429.1367 | 2.9138
1787 | 9391.959 | 2.8517
1788 | 10352.9766 | 2.8022
1789 | 11092.3574 | 2.83
1790 | 11686.5586 | 2.9292
1791 | 12309.9277 | 2.8253
1792 | 13143.5918 | 2.7852
1793 | 14203.6348 | 2.7369
1794 | 15458.2578 | 2.8603
1795 | 15912.6699 | 3.0963
1796 | 17072.2285 | 3.3211
1797 | 18112.4297 | 3.6882
1798 | 18804.7051 | 3.6621
1799 | 19059.6211 | 3.826
1800 | 19499.6426 | 4.0494
1801 | 19529.5273 | 4.0775
1802 | 19188.5156 | 4.2147
1803 | 18912.8848 | 4.4779
1804 | 18865.3906 | 4.3824
1805 | 18704.1699 | 4.6119
1806 | 18432.8848 | 4.3368
1807 | 18433 | 4.0932
1808 | 18604.7891 | 4.2274
1809 | 17831.6211 | 4.3359
1810 | 16296.1348 | 4.4068
1811 | 15473.4707 | 4.7437
1812 | 14853.6797 | 4.8845
1813 | 14519.543 | 4.4183
1814 | 14813.0391 | 4.3308
1815 | 14496.0254 | 4.3919
1816 | 14683.6387 | 4.0837
1817 | 14545.7734 | 3.9752
1818 | 15086.1426 | 3.9994
1819 | 14783.3848 | 3.6896
1820 | 14363.2266 | 3.5579
1821 | 13617.4355 | 3.3644
1822 | 13051.666 | 3.0651
1823 | 12334.3398 | 2.8232
1824 | 11968.2012 | 2.7798
1825 | 11417.876 | 2.7313
1826 | 11061.002 | 2.755
1827 | 10780.1094 | 3.053
1828 | 10779.1914 | 3.0244
1829 | 10559.832 | 2.9513
1830 | 10637.666 | 2.9752
1831 | 10541.2441 | 2.8412
1832 | 10614.2539 | 2.7937
1833 | 10581.0625 | 2.8397
1834 | 10993.3281 | 2.8541
1835 | 12705.4648 | 2.9034
1836 | 16334.291 | 3.0599
1837 | 18894.1777 | 2.9692
1838 | 21070.6133 | 3.1305
1839 | 22796.7832 | 3.8581
1840 | 23654.5391 | 4.5972
1841 | 24585.8789 | 5.5145
1842 | 25772.9746 | 6.0931
1843 | 27127.1562 | 7.0146
1844 | 27329.293 | 7.054
1845 | 27891.7031 | 7.1532
1846 | 27481.8203 | 7.2385
1847 | 27253.0625 | 7.0554
1848 | 27663.1035 | 7.133
1849 | 27248.8516 | 7.1509
1850 | 27328.6211 | 7.2537
1851 | 26882.0938 | 6.9986
1852 | 26418.832 | 6.7349
1853 | 26114.4395 | 6.7566
1854 | 25980.3047 | 6.6948
1855 | 25847.6602 | 6.88
1856 | 24853.3438 | 6.9086
1857 | 24718.7227 | 6.6064
1858 | 24429.6914 | 6.5233
1859 | 23811.2793 | 6.3986
1860 | 23707.2812 | 6.2511
1861 | 23653.3945 | 5.8125
1862 | 22972.4785 | 5.5989
1863 | 22972.2051 | 5.5827
1864 | 22734.1836 | 5.4748
1865 | 22079.8867 | 5.3129
1866 | 21315.9805 | 5.0176
1867 | 20217.0195 | 4.6805
1868 | 18920.3574 | 4.4567
1869 | 17596.1348 | 4.2416
1870 | 16711.082 | 3.7616
1871 | 16032.4375 | 3.4676
1872 | 14891.4707 | 3.2032
1873 | 14392.6914 | 3.1385
1874 | 13830.0781 | 3.1702
1875 | 13664.9082 | 3.4234
1876 | 13524.9082 | 3.3542
1877 | 13032.4043 | 3.3094
1878 | 13138.8027 | 3.2472
1879 | 13104.8027 | 3.4527
1880 | 13107.1074 | 3.4411
1881 | 13281.1504 | 3.3583
1882 | 13657.1387 | 3.1868
1883 | 14578.3418 | 3.4189
1884 | 17757.4492 | 3.4564
1885 | 20032.3789 | 3.6072
1886 | 22020.1074 | 4.1312
1887 | 24390.6777 | 4.6643
1888 | 26493.4805 | 5.0712
1889 | 27475.6621 | 5.7549
1890 | 28363.7051 | 6.3649
1891 | 29549.2852 | 7.0071
1892 | 29669.6543 | 7.3935
1893 | 30174.8223 | 7.3738
1894 | 30959.2344 | 7.7138
1895 | 30898.8438 | 7.7494
1896 | 31339.5078 | 7.6913
1897 | 30929.7402 | 7.6784
1898 | 29986.2969 | 7.6529
1899 | 29956.3164 | 7.4405
1900 | 30199.6953 | 7.1501
1901 | 29221.0098 | 7.0369
1902 | 29003.5156 | 6.9372
1903 | 29167.4004 | 6.8577
1904 | 26651.3887 | 6.7338
1905 | 26800.9023 | 6.7078
1906 | 26243.7324 | 6.5835
1907 | 25856.332 | 6.3657
1908 | 25620.1953 | 6.343
1909 | 25789.207 | 6.1833
1910 | 25444.4492 | 5.9614
1911 | 24544.3848 | 5.967
1912 | 24258.6152 | 5.8639
1913 | 23842.9609 | 5.3433
1914 | 22903.1719 | 4.9932
1915 | 21289.5898 | 4.8187
1916 | 19801.9902 | 4.5958
1917 | 18752.3145 | 4.1859
1918 | 18009.0078 | 3.9708
1919 | 16866.5977 | 3.6579
1920 | 15625.1016 | 3.5246
1921 | 15214.208 | 3.2989
1922 | 15122.3242 | 3.3392
1923 | 14877.1738 | 3.6671
1924 | 14970.1855 | 3.4975
1925 | 14503.2383 | 3.4438
1926 | 14478.8789 | 3.4362
1927 | 14919.8477 | 3.5253
1928 | 14978.4883 | 3.4864
1929 | 14691.3418 | 3.5932
1930 | 15382.7637 | 3.4
1931 | 16134.8066 | 3.5211
1932 | 18923.8105 | 3.6632
1933 | 20827.2969 | 3.8463
1934 | 23082.9199 | 4.2039
1935 | 25263.5547 | 4.7637
1936 | 27743.293 | 5.2363
1937 | 28762.4844 | 5.7923
1938 | 28611.3359 | 6.5026
1939 | 29184.5059 | 7.2224
1940 | 29364 | 7.3827
1941 | 29758.918 | 7.494
1942 | 29082.3887 | 7.4949
1943 | 30871.2129 | 7.3847
1944 | 29625.2852 | 7.4502
1945 | 29307.1484 | 7.522
1946 | 29122.3887 | 7.2994
1947 | 29405.4219 | 7.1751
1948 | 29146.6426 | 6.9775
1949 | 29323.2852 | 6.9589
1950 | 28540.252 | 6.6993
1951 | 28061.7266 | 6.599
1952 | 26138.8613 | 6.6171
1953 | 26320.8828 | 6.4681
1954 | 25833.8496 | 6.5078
1955 | 25805.5957 | 6.29
1956 | 25168.9336 | 6.359
1957 | 25574.0586 | 6.2573
1958 | 25497.1855 | 6.2792
1959 | 25431.5742 | 6.1862
1960 | 24795.9219 | 6.0666
1961 | 23960.3633 | 5.7067
1962 | 23279.0566 | 5.3692
1963 | 21755.6133 | 5.2029
1964 | 20109.5488 | 4.8076
1965 | 19240.7051 | 4.5672
1966 | 18215.166 | 4.2958
1967 | 17330.9863 | 4.0149
1968 | 16258.6172 | 3.6024
1969 | 15357.8105 | 3.4062
1970 | 14946.2793 | 3.4441
1971 | 14790.2363 | 3.5367
1972 | 14656.2363 | 3.526
1973 | 14330.9521 | 3.4135
1974 | 14151.6875 | 3.3753
1975 | 14089.4355 | 3.3977
1976 | 13979.4355 | 3.4897
1977 | 13870.4238 | 3.4226
1978 | 14654.9746 | 3.3624
1979 | 15666.1426 | 3.5491
1980 | 18149.168 | 3.695
1981 | 20681.2969 | 3.8817
1982 | 22951.1719 | 4.1339
1983 | 26822.8828 | 4.778
1984 | 28978.4824 | 5.31
1985 | 28800.6211 | 5.9382
1986 | 28763.7266 | 6.6121
1987 | 29911.1914 | 7.1456
1988 | 28891.3574 | 7.2549
1989 | 29401.5371 | 7.7671
1990 | 30784.2441 | 7.7479
1991 | 29619.4219 | 7.6638
1992 | 29326.5703 | 7.7912
1993 | 28732.1387 | 7.5904
1994 | 28497.9062 | 7.458
1995 | 28640.1582 | 7.416
1996 | 29000.4531 | 7.0979
1997 | 28681.7695 | 7.0254
1998 | 27407.7266 | 6.915
1999 | 26173.0195 | 6.6744
2000 | 26010.6504 | 6.6722
2001 | 25435.7559 | 6.5668
2002 | 25417.2285 | 6.6881
2003 | 24668.332 | 6.5582
2004 | 24139.0273 | 6.5301
2005 | 24277.6699 | 6.4361
2006 | 23314.2266 | 6.4131
2007 | 23473.8359 | 6.2122
2008 | 23226.457 | 6.1626
2009 | 23259.3086 | 5.8326
2010 | 22332.0039 | 5.4278
2011 | 20889.6855 | 5.0129
2012 | 19292.2422 | 4.7962
2013 | 18211.5352 | 4.4268
2014 | 17196.5957 | 3.9328
2015 | 16439.4492 | 3.7416
2016 | 15504.4375 | 3.362
2017 | 14548.0703 | 3.1725
2018 | 14034.1641 | 3.2837
2019 | 13755.1094 | 3.3973
2020 | 13586.9951 | 3.3491
2021 | 13610.3223 | 3.2613
2022 | 13448.6777 | 3.1687
2023 | 13376.2656 | 3.2602
2024 | 13358.6562 | 3.4511
2025 | 13280.2129 | 3.3866
2026 | 13797.0566 | 3.3211
2027 | 14796.5117 | 3.2766
2028 | 17677.0625 | 3.3477
2029 | 20011.832 | 3.6436
2030 | 21728.2969 | 4.0837
2031 | 23170.9199 | 4.4131
2032 | 24500.248 | 4.8967
2033 | 25762.3125 | 5.5877
2034 | 26130.082 | 6.6168
2035 | 26090.332 | 7.2689
2036 | 26187.3438 | 7.3591
2037 | 26717.8711 | 7.6315
2038 | 26091.5957 | 7.5273
2039 | 25483.6914 | 7.4585
2040 | 26052.334 | 7.3658
2041 | 26083.1133 | 7.3711
2042 | 26071.8281 | 7.3918
2043 | 25840.332 | 7.1267
2044 | 24718.1328 | 6.7732
2045 | 23962.5938 | 6.6172
2046 | 23960.4785 | 6.4365
2047 | 23951.9727 | 6.3158
2048 | 23909.4688 | 6.1113
2049 | 23934.457 | 6.0686
2050 | 23340.4355 | 5.8942
2051 | 22827.1719 | 5.9073
2052 | 23027.541 | 5.9077
2053 | 23059.5605 | 5.6782
2054 | 22716.7617 | 5.6022
2055 | 22096.7383 | 5.7148
2056 | 21233.707 | 5.4823
2057 | 20763.918 | 5.1678
2058 | 20290.7695 | 4.9147
2059 | 18905.3262 | 4.5028
2060 | 17306.9863 | 4.205
2061 | 15974.7842 | 3.9661
2062 | 15105.6367 | 3.7059
2063 | 14153.9395 | 3.5596
2064 | 13754.2363 | 3.252
2065 | 13362.9434 | 3.0448
2066 | 12691.2559 | 3.0495
2067 | 12263.4883 | 3.2607
2068 | 12221.5586 | 3.1766
2069 | 12074.3184 | 3.0994
2070 | 11832.1797 | 3.1645
2071 | 11607.6758 | 3.1961
2072 | 11452.5488 | 3.139
2073 | 11103.3789 | 3.2091
2074 | 10899.0098 | 3.2078
2075 | 11383.4219 | 3.0182
2076 | 12930.3613 | 3.0179
2077 | 14025.5508 | 3.0583
2078 | 14969.3633 | 3.0667
2079 | 15727.4062 | 3.1084
2080 | 17286.2285 | 3.1266
2081 | 18449.4199 | 3.6721
2082 | 20217.7578 | 4.0455
2083 | 20245.8965 | 4.7263
2084 | 20260.4004 | 4.9609
2085 | 19951.1152 | 5.0562
2086 | 20054.0098 | 5.06
2087 | 20425.5273 | 5.1764
2088 | 20064.3789 | 5.0611
2089 | 19804.0098 | 4.9915
2090 | 19368.5898 | 4.8996
2091 | 18668.0625 | 4.9251
2092 | 18352.7988 | 4.8316
2093 | 18258.041 | 4.9065
2094 | 17817.9023 | 4.8282
2095 | 18009.9023 | 4.8413
2096 | 18442.3145 | 4.7778
2097 | 18406.4082 | 4.8486
2098 | 18328.4297 | 4.8617
2099 | 18048.4082 | 4.8719
2100 | 17845.6504 | 5.1024
2101 | 17801.377 | 5.1033
2102 | 17764.502 | 4.8017
2103 | 17351.9961 | 4.6742
2104 | 16170.668 | 4.7491
2105 | 14890.8574 | 4.4333
2106 | 14737.458 | 4.2222
2107 | 14670.584 | 4.0447
2108 | 14219.9629 | 3.8466
2109 | 13586.2656 | 3.5386
2110 | 12715.8555 | 3.4516
2111 | 12009.3281 | 3.1115
2112 | 11463.6973 | 2.8762
2113 | 10972.4961 | 2.92
2114 | 10645.4414 | 3.011
2115 | 10534.0645 | 3.2308
2116 | 10413.6758 | 3.3342
2117 | 10104.7305 | 3.0893
2118 | 9819.1055 | 2.7372
2119 | 9773.4316 | 2.8132
2120 | 9797.5664 | 2.9252
2121 | 9591.0625 | 2.8906
2122 | 9282.5371 | 2.8679
2123 | 9591.209 | 3.0052
2124 | 10871.4004 | 2.8111
2125 | 11363.2422 | 2.8504
2126 | 11906.3047 | 2.6998
2127 | 12781.0029 | 2.7725
2128 | 13676.2871 | 2.6829
2129 | 14454.1719 | 3.0674
2130 | 15816.2793 | 2.9246
2131 | 16768.3438 | 3.1949
2132 | 17770.1348 | 3.3924
2133 | 18631.3047 | 3.6894
2134 | 19316.9785 | 3.7231
2135 | 19557.8516 | 4.1294
2136 | 19914.3789 | 4.027
2137 | 19388.8633 | 4.0594
2138 | 19556.4727 | 4.0022
2139 | 18694.8203 | 4.2029
2140 | 18922.3359 | 4.0553
2141 | 18632.4512 | 4.029
2142 | 18445.3047 | 3.8936
2143 | 18637.6934 | 3.8764
2144 | 18620.3145 | 3.8915
2145 | 18354.5684 | 3.9408
2146 | 17359.4922 | 4.0198
2147 | 15987.7949 | 4.3215
2148 | 15108.0059 | 4.2801
2149 | 14665.6152 | 4.262
2150 | 14491.2051 | 4.3384
2151 | 14410.584 | 4.4326
2152 | 14419.7109 | 4.1811
2153 | 14738.3516 | 4.0039
2154 | 15063.7324 | 3.8335
2155 | 14755.7324 | 3.7955
2156 | 14394.4473 | 3.6607
2157 | 13595.5293 | 3.5643
2158 | 12825.4883 | 3.2987
2159 | 12145.832 | 3.2107
2160 | 11691.7598 | 3.0224
2161 | 11217.6875 | 3.0005
2162 | 10892.918 | 3.0322
2163 | 10621.4941 | 3.2741
2164 | 10531.3574 | 3.2066
2165 | 10488.2305 | 3.2914
2166 | 10683.5684 | 2.7318
2167 | 10542.0957 | 2.7714
2168 | 10585.5977 | 2.764
2169 | 10535.0215 | 2.7792
2170 | 11299.5156 | 2.7972
2171 | 12894.8125 | 3.217
2172 | 16540.3105 | 3.0134
2173 | 19145.125 | 3.2668
2174 | 20828.7793 | 3.4004
2175 | 22779.1191 | 4.1913
2176 | 26183.3125 | 4.7901
2177 | 27027.7539 | 5.5038
2178 | 27689.9141 | 6.0151
2179 | 28551.7246 | 6.6616
2180 | 29160.2305 | 7.0026
2181 | 29107.6328 | 7.0933
2182 | 27546.9258 | 7.1129
2183 | 27586.9258 | 6.9882
2184 | 28060.9453 | 6.9019
2185 | 27749.0625 | 6.9141
2186 | 26976.6504 | 6.8068
2187 | 26292.5859 | 6.8434
2188 | 27049.7988 | 6.7525
2189 | 27295.0391 | 6.7024
2190 | 26705.6406 | 6.6604
2191 | 27124.2812 | 6.5066
2192 | 24974.1543 | 6.4464
2193 | 24868.9121 | 6.3073
2194 | 24165.6055 | 6.4006
2195 | 23414.7305 | 6.1365
2196 | 23580.2051 | 6.0251
2197 | 23366.7109 | 5.7906
2198 | 23077.8164 | 5.8316
2199 | 23163.5605 | 5.6859
2200 | 22589.9102 | 5.6277
2201 | 22055.3613 | 5.3791
2202 | 21293.5684 | 5.1429
2203 | 20117.5039 | 4.8851
2204 | 19029.5781 | 4.7296
2205 | 17565.8809 | 4.3409
2206 | 16326.9434 | 4.0882
2207 | 15646.3945 | 3.7913
2208 | 14934.7119 | 3.533
2209 | 14444.6699 | 3.4399
2210 | 14046.2793 | 3.4318
2211 | 13762.2363 | 3.6085
2212 | 13680.0059 | 3.6133
2213 | 13456.2246 | 3.5735
2214 | 13502.5508 | 3.7484
2215 | 13392.0137 | 3.5496
2216 | 13942.457 | 3.5822
2217 | 13615.0781 | 3.3857
2218 | 13755.834 | 3.4218
2219 | 14725.3633 | 3.5622
2220 | 18078.1992 | 3.823
2221 | 19985.6523 | 3.9985
2222 | 22535.707 | 4.2673
2223 | 24648.0781 | 4.3661
2224 | 26989.5234 | 4.7773
2225 | 27743.4082 | 5.1472
2226 | 27794.3047 | 5.8239
2227 | 28445.3359 | 6.5477
2228 | 28046.8301 | 6.737
2229 | 29141.0098 | 7.006
2230 | 28930 | 7.1731
2231 | 29162.1367 | 7.1571
2232 | 28758.7578 | 7.098
2233 | 28957.6543 | 7.0632
2234 | 28764.5059 | 7.1649
2235 | 28666.1387 | 7.1282
2236 | 27885.4727 | 6.946
2237 | 27401.957 | 6.9168
2238 | 26235.8926 | 6.8283
2239 | 26008.375 | 6.726
2240 | 25975.3652 | 6.5253
2241 | 25739.1133 | 6.4695
2242 | 25049.9648 | 6.6492
2243 | 23715.6484 | 6.4406
2244 | 23770.2461 | 6.2726
2245 | 23825.5117 | 6.1852
2246 | 23156.9844 | 6.0563
2247 | 23230.7109 | 5.8276
2248 | 23160.457 | 5.7879
2249 | 22480.5508 | 5.3618
2250 | 21740.625 | 5.1556
2251 | 20335.4336 | 4.8992
2252 | 19064.4961 | 4.7076
2253 | 17952.9141 | 4.3018
2254 | 16575.2188 | 4.0338
2255 | 16160.0918 | 4.006
2256 | 15512.1348 | 3.4893
2257 | 15011.6504 | 3.334
2258 | 14876.7637 | 3.3258
2259 | 14118.9512 | 3.6668
2260 | 14097.457 | 3.563
2261 | 14177.0898 | 3.5222
2262 | 14264.4473 | 3.7018
2263 | 14006.2695 | 3.7319
2264 | 14275.71 | 3.6464
2265 | 14225.2695 | 3.5616
2266 | 14252.7949 | 3.5923
2267 | 14779.9219 | 3.5892
2268 | 18208.9453 | 3.7386
2269 | 20461.2637 | 3.9329
2270 | 23764.7812 | 4.2743
2271 | 26412.3555 | 4.5361
2272 | 27696.8086 | 4.8534
2273 | 27728.6719 | 5.1484
2274 | 29108.2539 | 5.6448
2275 | 30661.834 | 6.4397
2276 | 30149.5586 | 6.6857
2277 | 31607.7617 | 6.7855
2278 | 31909.4141 | 6.8491
2279 | 29766.2969 | 6.8254
2280 | 29368.6426 | 6.8112
2281 | 29250.6426 | 6.7677
2282 | 27977.4512 | 6.794
2283 | 27557.7988 | 6.6895
2284 | 27289.4082 | 6.6423
2285 | 27643.6836 | 6.5031
2286 | 27022.2812 | 6.4031
2287 | 26405.3652 | 6.3389
2288 | 26503.6172 | 6.2133
2289 | 26099.0918 | 5.9858
2290 | 25562.1953 | 6.2178
2291 | 24354.8906 | 5.9847
2292 | 24413.8789 | 5.9033
2293 | 25131.9004 | 5.9814
2294 | 25202.9121 | 5.9315
2295 | 24653.9004 | 5.8699
2296 | 24254.9844 | 5.982
2297 | 23634.7109 | 5.5117
2298 | 22634.5312 | 5.1414
2299 | 21153.5703 | 4.843
2300 | 19591.7363 | 4.7967
2301 | 18299.2812 | 4.3459
2302 | 17194.25 | 4.205
2303 | 16423.4492 | 3.8771
2304 | 15637.123 | 3.7412
2305 | 15069.4707 | 3.5389
2306 | 14887.0586 | 3.4988
2307 | 14178.9004 | 3.6446
2308 | 14318.7129 | 3.6407
2309 | 13980.5 | 3.5245
2310 | 14112.666 | 3.5187
2311 | 14057.7207 | 3.5098
2312 | 14482.71 | 3.5002
2313 | 14130.2363 | 3.5282
2314 | 13943.0352 | 3.4083
2315 | 15208.0156 | 3.4848
2316 | 18551.7988 | 3.5139
2317 | 20760.3281 | 3.7671
2318 | 23225.8145 | 4.2241
2319 | 24726.3301 | 4.5703
2320 | 27365.5469 | 4.7948
2321 | 29474.4102 | 5.4048
2322 | 29550.5273 | 6.3062
2323 | 29563.0312 | 6.9674
2324 | 30216.2012 | 7.0735
2325 | 30057.6953 | 7.0447
2326 | 32118.4238 | 7.1559
2327 | 33737.1523 | 7.1818
2328 | 33322.1211 | 7.0371
2329 | 32357.8457 | 6.9373
2330 | 30246.5918 | 6.9421
2331 | 27198.1875 | 6.7978
2332 | 27163.3145 | 6.4747
2333 | 27012.8086 | 6.4369
2334 | 26291.5254 | 6.342
2335 | 25975.8711 | 6.2579
2336 | 26222.1465 | 6.3432
2337 | 25756.4707 | 6.4355
2338 | 25663.4609 | 6.4049
2339 | 24540.8906 | 6.0745
2340 | 24544.9121 | 5.8079
2341 | 24414.7539 | 5.8057
2342 | 24636.0156 | 5.6691
2343 | 24664.7734 | 5.8267
2344 | 24381.5117 | 5.8629
2345 | 23685.0977 | 5.5317
2346 | 22955.3086 | 5.1964
2347 | 21557.3594 | 4.8528
2348 | 20002.6523 | 4.6476
2349 | 18323.9473 | 4.1881
2350 | 17118.25 | 3.8059
2351 | 16297.333 | 3.5139
2352 | 15731.4707 | 3.3739
2353 | 15187.2617 | 3.3843
2354 | 14659.7021 | 3.4688
2355 | 13992.0781 | 3.6987
2356 | 13807.8242 | 3.6832
2357 | 13712.9521 | 3.6591
2358 | 13647.0449 | 3.5219
2359 | 13664.8672 | 3.5488
2360 | 13410.0117 | 3.4971
2361 | 13417.5078 | 3.4378
2362 | 13255.9609 | 3.4423
2363 | 14097.0156 | 3.6355
2364 | 17302.8711 | 3.5199
2365 | 19864.0215 | 3.6376
2366 | 22373.7168 | 3.8596
2367 | 24530.373 | 4.1185
2368 | 25356.6582 | 4.7222
2369 | 26162.4922 | 5.5873
2370 | 26649.1562 | 6.0419
2371 | 27149.0625 | 6.7145
2372 | 27311.4297 | 6.7439
2373 | 28458.873 | 6.8112
2374 | 27694.4629 | 6.9325
2375 | 27517.8203 | 6.9543
2376 | 25718.7227 | 6.963
2377 | 25470.5859 | 6.8895
2378 | 25213.4609 | 6.8709
2379 | 24957.0703 | 6.7035
2380 | 24048.4062 | 6.3849
2381 | 24199.5312 | 6.2805
2382 | 23763.8789 | 6.1996
2383 | 23332.2461 | 6.1811
2384 | 23209.1211 | 5.9392
2385 | 22772.709 | 5.6419
2386 | 22802.3398 | 5.5369
2387 | 22526.3203 | 5.4849
2388 | 22465.0566 | 5.4406
2389 | 22200.2988 | 5.3205
2390 | 22234.7812 | 5.2317
2391 | 22002.8984 | 5.3402
2392 | 21035.7285 | 5.2144
2393 | 20533.9375 | 4.9194
2394 | 19657.6426 | 4.679
2395 | 17991.168 | 4.3592
2396 | 16887.1035 | 4.1568
2397 | 15685.4277 | 3.9364
2398 | 14765.1113 | 3.7292
2399 | 14298.6914 | 3.4918
2400 | 13682.0273 | 3.1152
2401 | 13185.6152 | 3.024
2402 | 13171.1113 | 2.9812
2403 | 13147.2471 | 3.2089
2404 | 12828.0059 | 3.1248
2405 | 12878.4248 | 3.2385
2406 | 13682.2041 | 3.2033
2407 | 13791.3242 | 2.9896
2408 | 13749 | 2.9855
2409 | 13268.8789 | 2.9417
2410 | 12225.0029 | 2.9095
2411 | 14547.5771 | 2.9591
2412 | 16683.8945 | 2.9494
2413 | 17889.957 | 3.1388
2414 | 18442.7363 | 2.8866
2415 | 19096.0215 | 2.9366
2416 | 20754.3594 | 3.1152
2417 | 22086.0547 | 3.7134
2418 | 22965.4785 | 4.1847
2419 | 23040.8555 | 4.6749
2420 | 23870.0254 | 4.867
2421 | 23794.6484 | 5.0178
2422 | 23669.0156 | 5.1042
2423 | 23995.6582 | 5.1193
2424 | 23694.1406 | 5.0858
2425 | 23844.8984 | 4.9663
2426 | 23819.7734 | 5.0425
2427 | 23091.1133 | 5.0573
2428 | 22890.1016 | 4.9542
2429 | 24480.1016 | 4.9601
2430 | 19577.3574 | 4.8532
2431 | 19813.3301 | 4.7648
2432 | 20003.5195 | 4.7501
2433 | 20055.4531 | 4.7183
2434 | 20923.0859 | 4.7351
2435 | 20680.5586 | 4.7896
2436 | 20086.9062 | 4.6782
2437 | 19540.125 | 4.9986
2438 | 18916.082 | 4.7902
2439 | 18247.4199 | 4.6753
2440 | 16808.4824 | 4.729
2441 | 15384.5117 | 4.3622
2442 | 14961.2266 | 3.9287
2443 | 14544.6973 | 3.8037
2444 | 13999.9199 | 3.8591
2445 | 13306.6348 | 3.6098
2446 | 12555.3262 | 3.3765
2447 | 11784.5469 | 2.9637
2448 | 11472.4766 | 2.7922
2449 | 10919.5801 | 2.728
2450 | 10677.9785 | 2.7977
2451 | 10369.7246 | 3.2132
2452 | 10388.0723 | 3.1522
2453 | 10236.5781 | 2.9321
2454 | 10079.0625 | 2.7308
2455 | 10039.5449 | 2.6973
2456 | 10072.4414 | 2.6502
2457 | 9932.9258 | 2.5688
2458 | 9895.9375 | 2.5762
2459 | 10261.7031 | 2.5721
2460 | 11497.5156 | 2.4937
2461 | 12228.8223 | 2.549
2462 | 13032.8652 | 2.4753
2463 | 13539.3203 | 2.5503
2464 | 14446.7207 | 2.5847
2465 | 15307.4062 | 2.7635
2466 | 16585.2188 | 2.7705
2467 | 17207.0078 | 3.059
2468 | 18320.4512 | 3.4815
2469 | 19662.8828 | 3.6607
2470 | 20106.3066 | 3.9066
2471 | 20267.8242 | 3.9183
2472 | 20153.8242 | 4.0512
2473 | 20311.5488 | 4.0155
2474 | 20167.8242 | 4.1436
2475 | 19930.9062 | 4.2884
2476 | 19957.9375 | 4.0943
2477 | 19677.2969 | 3.9311
2478 | 19406.1484 | 3.8726
2479 | 19262.2852 | 3.9205
2480 | 19053.5059 | 3.9236
2481 | 18188.5684 | 3.9241
2482 | 17287.1445 | 3.9383
2483 | 16131.8184 | 4.0946
2484 | 15025.7734 | 4.1434
2485 | 14338.7422 | 4.3775
2486 | 14434.9941 | 4.2532
2487 | 14334.8574 | 4.4251
2488 | 14485.8477 | 4.2133
2489 | 14259.9629 | 4.0315
2490 | 14650.8574 | 4.0051
2491 | 14828.4902 | 3.8724
2492 | 14512.9727 | 3.5374
2493 | 13677.666 | 3.315
2494 | 12993.7617 | 3.0505
2495 | 12389.0977 | 3.0808
2496 | 11588.0137 | 2.5938
2497 | 11049.624 | 2.5259
2498 | 10801.4648 | 2.578
2499 | 10699.5801 | 2.8322
2500 | 10734.9805 | 2.8085
2501 | 10642.4961 | 2.7721
2502 | 10913.125 | 2.691
2503 | 10783.1484 | 2.6776
2504 | 10712.1367 | 2.6499
2505 | 11506.6855 | 2.6308
2506 | 12624.1094 | 2.6251
2507 | 13868.5625 | 2.7237
2508 | 17010.3457 | 2.9992
2509 | 19383.7363 | 3.0416
2510 | 21539.8438 | 3.4845
2511 | 22853.4258 | 4.2792
2512 | 23715.2148 | 4.7287
2513 | 24745.1641 | 5.4837
2514 | 26649.6406 | 6.1505
2515 | 27605.9355 | 6.6975
2516 | 28208.8516 | 6.9497
2517 | 27359.5469 | 6.9639
2518 | 26845.7773 | 6.8989
2519 | 27319.6836 | 6.7471
2520 | 28653.6328 | 6.6784
2521 | 28045.082 | 6.5693
2522 | 27221.4316 | 6.582
2523 | 27286.9453 | 6.6484
2524 | 27286.168 | 6.3266
2525 | 27436.5781 | 6.2234
2526 | 25848.1016 | 6.1654
2527 | 25460.4707 | 6.1165
2528 | 25040.3125 | 6.2602
2529 | 25304.2188 | 6.1816
2530 | 24396.5215 | 6.1085
2531 | 23398.7305 | 5.8515
2532 | 23700.1094 | 5.4169
2533 | 23663.4883 | 5.5541
2534 | 23851.6055 | 5.4618
2535 | 23928.1094 | 5.4708
2536 | 23634.457 | 5.4154
2537 | 23166.4336 | 4.8499
2538 | 22186.2559 | 4.5269
2539 | 20724.4434 | 4.4788
2540 | 19115.5781 | 4.2342
2541 | 18017.168 | 4.044
2542 | 17375.0078 | 3.455
2543 | 16630.0703 | 3.278
2544 | 15259.0801 | 2.8216
2545 | 14648.7773 | 2.7601
2546 | 14207.0898 | 2.8133
2547 | 13575.4355 | 3.1632
2548 | 14208.0566 | 3.0103
2549 | 15545.7529 | 2.9905
2550 | 15315.7529 | 2.9969
2551 | 15494.9004 | 3.0475
2552 | 15639.2695 | 3.1229
2553 | 15117.7529 | 2.9915
2554 | 15779.0156 | 2.9225
2555 | 16832.9648 | 2.9957
2556 | 20825.043 | 3.3671
2557 | 22044.2344 | 3.4442
2558 | 24573.0059 | 3.8845
2559 | 26428.3555 | 4.5148
2560 | 27640.4199 | 4.949
2561 | 28772.4844 | 5.4866
2562 | 27708.9453 | 6.193
2563 | 27698.8086 | 7.1554
2564 | 29669.625 | 7.3009
2565 | 31332.5508 | 7.5555
2566 | 33016.0156 | 7.4804
2567 | 33870.3125 | 7.4148
2568 | 34825.1133 | 7.2775
2569 | 33342.6602 | 7.2286
2570 | 33468.2891 | 7.2102
2571 | 33970.8164 | 7.2629
2572 | 32248.0664 | 6.9904
2573 | 28757.8828 | 6.7874
2574 | 27104.6914 | 6.5679
2575 | 25613.7461 | 6.5863
2576 | 25471.5977 | 6.5822
2577 | 25335.207 | 6.4791
2578 | 24916.6797 | 6.4181
2579 | 23832.1328 | 6.0603
2580 | 23369.0996 | 5.9891
2581 | 23357.4688 | 5.919
2582 | 23333.4688 | 5.8807
2583 | 23034.8262 | 5.9519
2584 | 22695.9102 | 5.857
2585 | 22348.2773 | 5.4659
2586 | 21416.7188 | 5.1314
2587 | 20696.3066 | 4.9296
2588 | 19405.2305 | 4.5421
2589 | 17843.2832 | 4.2252
2590 | 17031.7441 | 3.8597
2591 | 16028.249 | 3.4728
2592 | 15217.2617 | 3.3658
2593 | 14822.502 | 3.3083
2594 | 14338.0488 | 3.2353
2595 | 13603.4062 | 3.5346
2596 | 13311.3105 | 3.5398
2597 | 13250.0996 | 3.2897
2598 | 13060.0352 | 3.2168
2599 | 13423.4648 | 3.3099
2600 | 13437.0244 | 3.1905
2601 | 13209.1504 | 3.2032
2602 | 13937.1387 | 3.211
2603 | 15055.2266 | 3.235
2604 | 18176.7891 | 3.3952
2605 | 20131.3672 | 3.7523
2606 | 22557.4238 | 4.078
2607 | 25161.3555 | 4.4965
2608 | 27457.7988 | 5.164
2609 | 29336.1152 | 5.7907
2610 | 29995.3066 | 6.483
2611 | 30349.0547 | 7.3889
2612 | 31257.7383 | 7.454
2613 | 31037.9922 | 7.4664
2614 | 32076.4023 | 7.3916
2615 | 31035.0977 | 7.3397
2616 | 30951.4863 | 7.2405
2617 | 31222.3828 | 7.1195
2618 | 30047.8125 | 6.9746
2619 | 30186.8008 | 6.8127
2620 | 30107.6758 | 6.5412
2621 | 28760.1152 | 6.7431
2622 | 27872.8086 | 6.6679
2623 | 27814.1875 | 6.5653
2624 | 27183.2715 | 6.4899
2625 | 26696.0078 | 6.3649
2626 | 25980.9551 | 6.2408
2627 | 25501.8066 | 6.1262
2628 | 25586.3125 | 5.949
2629 | 26194.4707 | 5.9656
2630 | 25787.8281 | 6.0169
2631 | 25385.668 | 6.2468
2632 | 25097.1641 | 6.1923
2633 | 24485.1211 | 5.8264
2634 | 23471.1934 | 5.3892
2635 | 21933.3594 | 4.999
2636 | 20557.2969 | 4.7767
2637 | 19609.7363 | 4.4514
2638 | 18767.1895 | 3.9802
2639 | 17358.502 | 3.5133
2640 | 16359.6738 | 3.234
2641 | 15735.7148 | 3.1029
2642 | 15209.9336 | 3.3161
2643 | 14278.9727 | 3.3818
2644 | 13861.5938 | 3.3061
2645 | 13648.584 | 3.2086
2646 | 13447.1836 | 3.0948
2647 | 13384.6992 | 3.335
2648 | 13763.5723 | 3.332
2649 | 13539.8242 | 3.3357
2650 | 14005.0684 | 3.3424
2651 | 14921.8682 | 3.4403
2652 | 18894.3145 | 3.3233
2653 | 20873.3164 | 3.5683
2654 | 22633.9102 | 4.0067
2655 | 24554.7539 | 4.4035
2656 | 27012.7656 | 5.1175
2657 | 27398.418 | 5.9445
2658 | 28097.5664 | 6.603
2659 | 29624.916 | 7.5387
2660 | 30496.959 | 7.5815
2661 | 29234.1387 | 7.834
2662 | 29368.1367 | 7.8445
2663 | 28934.2539 | 7.687
2664 | 29440.0215 | 7.6802
2665 | 28952.3906 | 7.6325
2666 | 28907.6328 | 7.5855
2667 | 27682.3047 | 7.2477
2668 | 27555.6836 | 7.1693
2669 | 27123.293 | 7.0491
2670 | 26775.6406 | 6.943
2671 | 26501.5039 | 6.7876
2672 | 26892.0293 | 6.7106
2673 | 26523.5039 | 6.8492
2674 | 25179.5547 | 6.758
2675 | 24382.7754 | 6.5166
2676 | 24017.0059 | 6.1706
2677 | 23911.7637 | 6.0577
2678 | 23811.7207 | 6.1276
2679 | 23519.7207 | 6.2381
2680 | 23345.332 | 6.0698
2681 | 22883.9297 | 5.8329
2682 | 21868.623 | 5.4394
2683 | 20235.2969 | 4.9405
2684 | 18505.8105 | 4.636
2685 | 17596.8926 | 4.3642
2686 | 16481.1973 | 3.7068
2687 | 15819.9336 | 3.2922
2688 | 15353.4492 | 3.2044
2689 | 14195.6797 | 3.1384
2690 | 13801.6797 | 3.1806
2691 | 13380.1426 | 3.2918
2692 | 13091.1543 | 3.1631
2693 | 13325.1758 | 3.1074
2694 | 12856.8145 | 3.0899
2695 | 12804.1289 | 3.2766
2696 | 12972.7715 | 3.1526
2697 | 12675.9805 | 3.0186
2698 | 13218.2461 | 3.0129
2699 | 14450.2266 | 3.1437
2700 | 17870.041 | 3.3245
2701 | 20558.4727 | 3.2953
2702 | 22425.8867 | 3.7578
2703 | 23706.2031 | 4.526
2704 | 25171.0273 | 5.0831
2705 | 25876.1973 | 5.7692
2706 | 26657.8711 | 6.4484
2707 | 26896.5137 | 7.3047
2708 | 27275.6621 | 7.5141
2709 | 28206.2109 | 7.5447
2710 | 27858.3242 | 7.5091
2711 | 27632.0508 | 7.4044
2712 | 28337.2207 | 7.3503
2713 | 27671.4512 | 7.2394
2714 | 27884.3242 | 7.2152
2715 | 27090.5352 | 7.0828
2716 | 26500.5137 | 6.783
2717 | 26299.7344 | 6.6296
2718 | 26192.375 | 6.4683
2719 | 26071.1133 | 6.5297
2720 | 24687.9219 | 6.354
2721 | 23534.6152 | 6.0102
2722 | 23154.9629 | 5.9285
2723 | 22499.4258 | 6.0193
2724 | 22447.0352 | 5.602
2725 | 22254.0234 | 5.6376
2726 | 22034.6445 | 5.6588
2727 | 21643.8652 | 5.7615
2728 | 20676.0547 | 5.4781
2729 | 19967.7793 | 5.1318
2730 | 18782.084 | 4.9259
2731 | 17787.9023 | 4.5817
2732 | 16505.7012 | 4.4304
2733 | 15739.1738 | 3.9546
2734 | 14463.3418 | 3.4991
2735 | 14049.0684 | 3.2944
2736 | 13539.1094 | 2.9057
2737 | 13052.165 | 2.7223
2738 | 12570.2676 | 2.7266
2739 | 12303.2129 | 2.9884
2740 | 11958.0859 | 2.978
2741 | 11867.3066 | 3.0216
2742 | 11676.9375 | 2.9902
2743 | 11503.6738 | 2.9926
2744 | 10945.6523 | 2.9554
2745 | 10630.9883 | 2.8649
2746 | 10890.0234 | 2.8485
2747 | 11403.0547 | 2.9628
2748 | 12923.4883 | 2.8445
2749 | 13951.9395 | 2.7914
2750 | 15076.8799 | 3.0416
2751 | 15801.3848 | 3.0337
2752 | 17499.8809 | 3.1377
2753 | 18578.5684 | 3.7754
2754 | 19627.1152 | 4.1301
2755 | 19989.918 | 4.6273
2756 | 20131.5039 | 4.8421
2757 | 20208.1699 | 5.021
2758 | 20389.4102 | 5.1568
2759 | 20261.8027 | 4.9116
2760 | 19790.6523 | 4.8403
2761 | 19621 | 4.8446
2762 | 19528.1484 | 4.8401
2763 | 19011.2305 | 4.8065
2764 | 18461.4629 | 4.7817
2765 | 18398.8418 | 4.8621
2766 | 18073.9238 | 4.7644
2767 | 18145.5781 | 4.6902
2768 | 18067.5566 | 4.7147
2769 | 18258.7246 | 4.6311
2770 | 17874.2949 | 4.5269
2771 | 17729.5352 | 4.6732
2772 | 17482.9141 | 4.6481
2773 | 17350.0195 | 4.72
2774 | 17338.2715 | 4.6905
2775 | 17062.1348 | 4.7689
2776 | 15903.4492 | 4.728
2777 | 14629.2471 | 4.4192
2778 | 13735.4355 | 4.1833
2779 | 13730.3086 | 3.9383
2780 | 13597.4355 | 3.9
2781 | 13136.0352 | 3.7532
2782 | 12376.0859 | 3.3715
2783 | 11883.834 | 3.2173
2784 | 11390.1094 | 3.1917
2785 | 10876.0137 | 3.0985
2786 | 10575.4453 | 3.1928
2787 | 10312.1797 | 3.389
2788 | 10169.9492 | 3.3528
2789 | 9777.2129 | 3.1122
2790 | 9560.4629 | 2.9997
2791 | 9569.4316 | 3.042
2792 | 9519.1992 | 3.1459
2793 | 9076.5586 | 2.9892
2794 | 8933.6621 | 2.9669
2795 | 9381.4316 | 2.946
2796 | 10402.1172 | 2.9194
2797 | 10855.7695 | 2.7353
2798 | 11422.6641 | 3.0794
2799 | 12039.2129 | 2.9829
2800 | 13016.8867 | 2.994
2801 | 14179.666 | 2.8995
2802 | 15130.0059 | 3.0113
2803 | 15885.0586 | 3.1952
2804 | 17316.25 | 3.4753
2805 | 18159.7871 | 3.4937
2806 | 18603.0723 | 3.7765
2807 | 18701.7148 | 4.0188
2808 | 19242.9785 | 3.9282
2809 | 19348.2637 | 3.8765
2810 | 19673.0215 | 4.3883
2811 | 18858.3379 | 4.4878
2812 | 18628.2207 | 4.1538
2813 | 18218.4297 | 3.9732
2814 | 18125.5781 | 3.9677
2815 | 17928.4316 | 3.9609
2816 | 17940.1992 | 3.9275
2817 | 17311.0293 | 3.9439
2818 | 16011.333 | 4.0315
2819 | 14737.6582 | 4.1939
2820 | 13774.0781 | 4.2141
2821 | 13584.0781 | 4.2505
2822 | 13558.4688 | 4.3763
2823 | 13087.2979 | 4.3061
2824 | 13115.9199 | 4.3481
2825 | 13022.793 | 4.1645
2826 | 12915.2773 | 4.034
2827 | 13189.8047 | 3.9619
2828 | 13234.2871 | 3.812
2829 | 12771.1406 | 3.4227
2830 | 12302.2227 | 3.1072
2831 | 13527.1963 | 3.0957
2832 | 12965.1934 | 2.6851
2833 | 12487.793 | 2.5699
2834 | 12286.7812 | 2.8239
2835 | 12010.3926 | 3.1312
2836 | 11784.2559 | 3.1324
2837 | 11734.002 | 2.8946
2838 | 11407.3613 | 2.6647
2839 | 11256.6016 | 2.7119
2840 | 11382.2324 | 2.6897
2841 | 11432.4863 | 2.7251
2842 | 11532.9922 | 2.7156
2843 | 11658.624 | 2.7705
2844 | 12538.0449 | 2.9223
2845 | 13015.4473 | 3.1757
2846 | 13467.7207 | 3.4781
2847 | 14271.7637 | 4.204
2848 | 15502.9551 | 4.9199
2849 | 16583.3867 | 5.7173
2850 | 18317.1055 | 6.3673
2851 | 19347.2852 | 7.1055
2852 | 20000.5703 | 7.6006
2853 | 20352.3379 | 7.7077
2854 | 20452.8418 | 7.8049
2855 | 20553.3477 | 7.8938
2856 | 21005.625 | 7.7746
2857 | 20176.4531 | 7.6818
2858 | 20452.8438 | 7.6412
2859 | 20452.8438 | 7.6403
2860 | 21081.0039 | 7.4663
2861 | 20930.2441 | 7.3282
2862 | 20678.9805 | 7.0836
2863 | 20729.2344 | 7.1221
2864 | 20829.7383 | 6.9624
2865 | 20729.2344 | 6.7694
2866 | 20302.0859 | 6.6236
2867 | 20276.959 | 6.3721
2868 | 20126.2031 | 6.0854
2869 | 19774.4336 | 6.0134
2870 | 19422.6641 | 5.9548
2871 | 19171.3984 | 5.9509
2872 | 18367.3574 | 5.6258
2873 | 17010.5352 | 5.2906
2874 | 16306.9961 | 5.0016
2875 | 16357.25 | 4.8582
2876 | 16357.25 | 4.5221
2877 | 16181.3652 | 4.1045
2878 | 15578.333 | 3.5498
2879 | 15075.8066 | 3.1711
2880 | 14221.5117 | 3.107
2881 | 13769.2363 | 2.8636
2882 | 13593.3516 | 2.8924
2883 | 13417.4668 | 3.2248
2884 | 13442.5938 | 3.3564
2885 | 13643.6035 | 3.296
2886 | 13392.3418 | 3.2871
2887 | 13367.2148 | 3.2939
2888 | 13517.9727 | 3.2723
2889 | 13593.3516 | 3.2165
2890 | 14422.5215 | 3.2275
2891 | 16457.7559 | 3.2983
2892 | 20528.2227 | 3.1682
2893 | 22663.9629 | 3.4712
2894 | 24548.4375 | 3.8901
2895 | 26834.9336 | 4.3939
2896 | 29221.9395 | 4.8921
2897 | 31458.1836 | 5.7636
2898 | 32387.8574 | 6.28
2899 | 32429.9297 | 6.8247
2900 | 31619.9961 | 6.997
2901 | 32300.123 | 7.1549
2902 | 31768.4785 | 7.2162
2903 | 29814.6328 | 7.1697
2904 | 29559.9531 | 7.0859
2905 | 29708.5391 | 7.0543
2906 | 29728.1797 | 7.1628
2907 | 29432 | 7.1324
2908 | 28422.9688 | 6.7899
2909 | 28044.4629 | 6.7969
2910 | 27404.0293 | 6.6252
2911 | 28552.9883 | 6.4805
2912 | 26961.1348 | 6.4953
2913 | 26596.9961 | 6.532
2914 | 26161.0918 | 6.581
2915 | 25263.9219 | 6.2789
2916 | 25281.9434 | 5.9696
2917 | 24760.543 | 5.957
2918 | 24566.0176 | 6.0135
2919 | 24389.6484 | 5.9524
2920 | 24066.7305 | 5.7039
2921 | 23431.0781 | 5.2018
2922 | 22619.1523 | 4.9245
2923 | 21037.0645 | 4.6893
2924 | 19752.1484 | 4.6034
2925 | 18974.8418 | 4.2634
2926 | 17731.6719 | 3.73
2927 | 16905.9766 | 3.2625
2928 | 16312.5254 | 3.009
2929 | 15942.7773 | 2.933
2930 | 15250.9863 | 2.9488
2931 | 14915.3125 | 3.264
2932 | 14633.0371 | 3.2239
2933 | 14328.46 | 3.2174
2934 | 14434.7852 | 3.1335
2935 | 14216.8359 | 3.1294
2936 | 14565.71 | 3.0989
2937 | 14534.3516 | 3.0569
2938 | 14691.9844 | 3.0431
2939 | 15608.6484 | 3.1836
2940 | 18481.0742 | 3.325
2941 | 20570.4004 | 3.5883
2942 | 22280.625 | 3.9036
2943 | 24795.418 | 4.6106
2944 | 26650.0293 | 5.2796
2945 | 27607.6836 | 5.9919
2946 | 28303.7246 | 6.5989
2947 | 28649.4941 | 7.3747
2948 | 30543.3496 | 7.3457
2949 | 31481.3926 | 7.3378
2950 | 30239.5801 | 7.6753
2951 | 30458.4531 | 7.7193
2952 | 30254.4531 | 7.5996
2953 | 31071.3711 | 7.3703
2954 | 29645.6758 | 7.2059
2955 | 29817.2852 | 7.1134
2956 | 30150.9395 | 6.9366
2957 | 29158.8965 | 6.8811
2958 | 27493.9355 | 6.8001
2959 | 27680.1895 | 6.6366
2960 | 27256.6719 | 6.5069
2961 | 26735.5039 | 6.4695
2962 | 26036.9746 | 6.3074
2963 | 25305.5762 | 6.2802
2964 | 25192.1758 | 6.1391
2965 | 24915.5547 | 5.9843
2966 | 24412.5 | 5.981
2967 | 23944.6172 | 5.8735
2968 | 23732.8477 | 5.7901
2969 | 23483.6992 | 5.5054
2970 | 22725.6758 | 5.2224
2971 | 21270.3496 | 4.9127
2972 | 19850.2637 | 4.6854
2973 | 18902.2207 | 4.3223
2974 | 17783.1465 | 3.7077
2975 | 16990.3652 | 3.3606
2976 | 16136.7129 | 3.2921
2977 | 15689.2617 | 2.939
2978 | 15300.1348 | 3.075
2979 | 14734.9941 | 3.4652
2980 | 14473.71 | 3.3314
2981 | 14213.0889 | 3.1786
2982 | 14351.2041 | 3.1523
2983 | 14510.7207 | 3.0627
2984 | 14852.1211 | 3.0653
2985 | 14366.7207 | 3.0749
2986 | 14315.2041 | 3.1615
2987 | 15485.1543 | 3.1247
2988 | 18556.9355 | 3.1967
2989 | 20617.1797 | 3.4818
2990 | 22769.2891 | 3.8858
2991 | 24140.3398 | 4.4774
2992 | 25729.8281 | 5.018
2993 | 26455.4805 | 6.0597
2994 | 27602.3047 | 6.5976
2995 | 27888.4414 | 7.2048
2996 | 28375.957 | 7.2731
2997 | 29855.7891 | 7.3873
2998 | 29832.8008 | 7.41
2999 | 28235.3359 | 7.3254
3000 | 28170.6934 | 7.4066
3001 | 28140.1875 | 7.3929
3002 | 27993.957 | 7.4759
3003 | 27659.5469 | 7.2505
3004 | 27332.6504 | 7.0464
3005 | 26925.0195 | 6.9711
3006 | 26680.123 | 6.8443
3007 | 26521.7344 | 6.8782
3008 | 26372.8594 | 6.7995
3009 | 26131.3438 | 6.7525
3010 | 25206.7949 | 6.7559
3011 | 23698.3398 | 6.6705
3012 | 23638.5938 | 6.2986
3013 | 23745.6035 | 6.2403
3014 | 23343.332 | 6.3838
3015 | 23387.0781 | 6.2764
3016 | 23267.0781 | 6.0107
3017 | 22855.1719 | 5.7399
3018 | 21840.4863 | 5.5313
3019 | 20668.4219 | 4.9205
3020 | 19913.5039 | 4.4422
3021 | 18928.4512 | 4.1613
3022 | 17864.1348 | 3.635
3023 | 16830.7129 | 3.3454
3024 | 16238.46 | 3.132
3025 | 15685.2383 | 3.0194
3026 | 15047.0811 | 3.0196
3027 | 14644.5332 | 3.2804
3028 | 14640.417 | 3.2235
3029 | 14362.208 | 3.142
3030 | 14439.4277 | 3.0876
3031 | 14180.5391 | 3.1219
3032 | 14130.9521 | 3.1161
3033 | 13814.4258 | 3.212
3034 | 13729.0449 | 3.25
3035 | 15012.2363 | 3.2539
3036 | 17838.3867 | 3.4736
3037 | 20079.1367 | 3.4882
3038 | 22301.1289 | 3.8614
3039 | 25318.543 | 4.5203
3040 | 26718.125 | 5.161
3041 | 27797.7988 | 6.0327
3042 | 26880.9961 | 6.626
3043 | 26663.25 | 7.6764
3044 | 28137.4512 | 7.7617
3045 | 27654.5566 | 7.7635
3046 | 28055.9141 | 7.7683
3047 | 28748 | 7.7705
3048 | 27697.8203 | 7.5681
3049 | 26585.7559 | 7.4742
3050 | 26689.3867 | 7.4504
3051 | 26038.1016 | 7.2628
3052 | 24465.2578 | 7.0487
3053 | 24576.7949 | 6.9332
3054 | 24523.6484 | 6.7063
3055 | 23994.7539 | 6.512
3056 | 24102.3848 | 6.3181
3057 | 23683.625 | 6.0537
3058 | 23203.3301 | 6.002
3059 | 22502.668 | 5.7506
3060 | 22723.0781 | 5.5231
3061 | 22651.1934 | 5.7684
3062 | 22261.6777 | 5.6203
3063 | 22185.2891 | 5.5921
3064 | 21932.6445 | 5.5367
3065 | 20947.3594 | 5.2885
3066 | 19691.2754 | 5.0087
3067 | 18320.0625 | 4.7005
3068 | 17370.5234 | 4.3545
3069 | 16670.6172 | 4.0383
3070 | 15822.418 | 3.5405
3071 | 15165.8184 | 3.0815
3072 | 14585.4707 | 2.9819
3073 | 13696.8281 | 2.9665
3074 | 13278.5625 | 2.9944
3075 | 13032.6562 | 3.0285
3076 | 12747.1406 | 3.0395
3077 | 12442.6348 | 3.1158
3078 | 12395.0029 | 2.9042
3079 | 12457.9922 | 2.7793
3080 | 12258.6133 | 2.7931
3081 | 12070.9805 | 2.8412
3082 | 11619.0742 | 2.9385
3083 | 11790.0859 | 2.7667
3084 | 13053.666 | 2.7156
3085 | 14103.71 | 2.9876
3086 | 15004.2363 | 3.1026
3087 | 15879.3105 | 3.1277
3088 | 17602.041 | 3.1966
3089 | 18792.4512 | 3.7921
3090 | 19894.5391 | 4.3078
3091 | 20456.9277 | 4.5753
3092 | 21049.0859 | 4.6446
3093 | 20960.3496 | 4.9033
3094 | 20929.959 | 4.9777
3095 | 21031.3594 | 5.0176
3096 | 21007.8652 | 5.0245
3097 | 20772.2109 | 4.8765
3098 | 20995.4961 | 4.8354
3099 | 20277.8242 | 4.738
3100 | 19805.4336 | 4.8995
3101 | 19490.9277 | 4.7723
3102 | 19498.6758 | 4.6681
3103 | 19423.918 | 4.4874
3104 | 19588.8125 | 4.5483
3105 | 19485.5488 | 4.6037
3106 | 19413.9375 | 4.5445
3107 | 19229.1602 | 4.5143
3108 | 18844.5156 | 4.5166
3109 | 18679.6211 | 4.5711
3110 | 18625.6211 | 4.6084
3111 | 18286.9785 | 4.7349
3112 | 16320.7559 | 4.6648
3113 | 14476.8789 | 4.2459
3114 | 13779.7305 | 4.0902
3115 | 14191.248 | 3.9572
3116 | 13946.3535 | 3.9744
3117 | 13497.5723 | 3.636
3118 | 12936.4043 | 3.5569
3119 | 12384.2441 | 3.3147
3120 | 12099.2344 | 3.0481
3121 | 11773.2344 | 3.0241
3122 | 11195.0234 | 3.1006
3123 | 10854.9082 | 3.3499
3124 | 10338.6133 | 3.2685
3125 | 10153.9707 | 3.2247
3126 | 10015.832 | 2.9252
3127 | 9980.0352 | 2.8677
3128 | 9761.2656 | 2.8451
3129 | 9566.832 | 2.8266
3130 | 9510.0723 | 2.6911
3131 | 9952.7812 | 2.7483
3132 | 11097.4336 | 2.7099
3133 | 12189.7402 | 2.6563
3134 | 14547.6465 | 2.9408
3135 | 15106.1338 | 2.8872
3136 | 16208.6904 | 2.8464
3137 | 17061.9883 | 2.8098
3138 | 18191.4727 | 3.0522
3139 | 18670.0742 | 3.216
3140 | 19598.5469 | 3.3868
3141 | 21005.625 | 3.607
3142 | 21256.8887 | 3.5877
3143 | 21382.5195 | 3.7807
3144 | 21332.2656 | 4.0904
3145 | 20980.4961 | 4.0586
3146 | 20704.1074 | 4.2277
3147 | 19824.6855 | 4.4363
3148 | 19874.9375 | 4.0876
3149 | 19849.8105 | 3.9874
3150 | 20302.0859 | 3.8242
3151 | 20201.5801 | 3.7062
3152 | 20503.0977 | 3.6967
3153 | 19975.4434 | 3.7464
3154 | 18794.5039 | 3.8493
3155 | 17513.0625 | 4.0563
3156 | 16583.3887 | 4.0846
3157 | 16181.3662 | 3.9277
3158 | 16080.8604 | 4.1067
3159 | 16080.8604 | 4.0932
3160 | 15980.3535 | 4.1204
3161 | 16030.6074 | 3.9926
3162 | 16055.7334 | 3.9374
3163 | 16105.9873 | 3.7704
3164 | 16306.9971 | 3.5915
3165 | 16030.6074 | 3.4714
3166 | 15553.207 | 3.3093
3167 | 15100.9336 | 2.9593
3168 | 14497.9004 | 2.9904
3169 | 14196.3848 | 2.9258
3170 | 13718.9844 | 2.9431
3171 | 13543.0996 | 3.2151
3172 | 13543.0996 | 2.9659
3173 | 13543.0996 | 2.8527
3174 | 13794.3633 | 2.774
3175 | 13794.3633 | 2.8286
3176 | 13718.9844 | 3.0002
3177 | 11252.7881 | 2.9514
3178 | 11437.5781 | 2.9855
3179 | 13588.8301 | 2.8842
3180 | 16922.9941 | 2.935
3181 | 19099.5273 | 3.2562
3182 | 20686.8086 | 3.5953
3183 | 22980.9863 | 4.1861
3184 | 23609.0469 | 5.0008
3185 | 24517.2578 | 5.8024
3186 | 26388.8613 | 6.1971
3187 | 27528.6934 | 7.0136
3188 | 27933.8418 | 7.2824
3189 | 28225.2422 | 7.4179
3190 | 27510.2109 | 7.3753
3191 | 27487.5664 | 7.1883
3192 | 27734.5996 | 7.1233
3193 | 27618.4629 | 7.2929
3194 | 27293.082 | 6.927
3195 | 27395.3359 | 7.2034
3196 | 27210.7168 | 7.2052
3197 | 27259.2207 | 7.1145
3198 | 26776.7168 | 6.9499
3199 | 26868.7168 | 6.8817
3200 | 26032.0293 | 6.8744
3201 | 26081.6816 | 6.7797
3202 | 25277.7559 | 6.6592
3203 | 23814.7949 | 6.3332
3204 | 24761.2285 | 6.0553
3205 | 24182.0586 | 5.71
3206 | 24258.8379 | 5.7396
3207 | 23923.0488 | 5.8406
3208 | 23312.1328 | 5.8398
3209 | 22887.1211 | 5.4186
3210 | 21909.6758 | 5.1231
3211 | 20732.7383 | 4.9688
3212 | 19975.2012 | 4.6034
3213 | 18844.127 | 4.1942
3214 | 17622.6836 | 3.5474
3215 | 16394.2285 | 3.3765
3216 | 15524.1133 | 3.1409
3217 | 15242.1348 | 2.8142
3218 | 15131.9971 | 2.8124
3219 | 14568.5742 | 3.118
3220 | 14345.7959 | 3.327
3221 | 14282.9668 | 3.2494
3222 | 14028.9219 | 3.1938
3223 | 13934.0566 | 3.2205
3224 | 13819.8887 | 3.1608
3225 | 13157.2568 | 3.1288
3226 | 13700.2773 | 3.1826
3227 | 14702.1113 | 3.2473
3228 | 18534.957 | 3.3721
3229 | 20538.5586 | 3.4014
3230 | 22953.1719 | 3.6496
3231 | 26382.168 | 4.2845
3232 | 27750.8301 | 4.88
3233 | 28385.8848 | 5.7445
3234 | 28611.7695 | 6.058
3235 | 29960.1074 | 6.696
3236 | 30884.2871 | 6.8129
3237 | 30770.2891 | 6.827
3238 | 30939.9414 | 6.9189
3239 | 31574.0977 | 6.9856
3240 | 30333.668 | 6.889
3241 | 29773.8965 | 7.0324
3242 | 28707.5801 | 7.0808
3243 | 28519.832 | 6.8741
3244 | 29440.2656 | 6.8517
3245 | 29645.5078 | 6.8195
3246 | 28754.4766 | 6.7052
3247 | 27213.4941 | 6.8122
3248 | 26305.5898 | 6.8904
3249 | 26238.7168 | 6.7403
3250 | 25685.6816 | 6.6951
3251 | 25163.7773 | 6.4911
3252 | 25621.1992 | 6.3298
3253 | 25489.9355 | 6.2442
3254 | 25263.6602 | 6.0533
3255 | 24578.4922 | 6.0358
3256 | 23849.1855 | 5.9267
3257 | 23616.7949 | 5.3019
3258 | 22357.582 | 5.0532
3259 | 21206.5312 | 4.853
3260 | 20043.3379 | 4.6742
3261 | 19364.9258 | 4.1611
3262 | 18477 | 3.6125
3263 | 17292.9355 | 3.1497
3264 | 16685.7168 | 2.8679
3265 | 15578.4746 | 3.0797
3266 | 15224.9648 | 3.1161
3267 | 14925.543 | 3.3854
3268 | 14867.29 | 3.3452
3269 | 14665.9111 | 3.2586
3270 | 14620.0059 | 2.9911
3271 | 14439.1328 | 3.0224
3272 | 14552.626 | 3.0522
3273 | 14097.5938 | 2.9707
3274 | 14239.7529 | 2.9796
3275 | 14924.7637 | 3.0793
3276 | 18718.3672 | 3.2069
3277 | 20781.2441 | 3.5227
3278 | 22959.9727 | 3.6717
3279 | 25327.9648 | 4.4485
3280 | 28267.8848 | 4.8456
3281 | 29120.8008 | 5.6063
3282 | 28384.2734 | 6.3071
3283 | 29604.4746 | 6.9967
3284 | 29570.5918 | 6.8988
3285 | 30230.1289 | 7.027
3286 | 30176.2441 | 7.0626
3287 | 31648.9512 | 7.0437
3288 | 32115.2246 | 6.9577
3289 | 32624.1426 | 7.0065
3290 | 29520.0859 | 6.9403
3291 | 29593.1172 | 6.5435
3292 | 30678.4023 | 6.3577
3293 | 30254.2656 | 6.4743
3294 | 28821.3066 | 6.321
3295 | 28812.1797 | 6.2492
3296 | 27005.8418 | 6.1498
3297 | 26408.1875 | 6.2248
3298 | 26123.5469 | 6.3512
3299 | 25297.502 | 6.36
3300 | 25810.3984 | 6.1398
3301 | 25726.1445 | 5.9837
3302 | 25355.4805 | 6.2429
3303 | 24759.7109 | 6.4779
3304 | 24281.1641 | 6.2152
3305 | 23368.5 | 5.7655
3306 | 22347.0566 | 5.3546
3307 | 21290.8555 | 5.1918
3308 | 20369.9375 | 4.8333
3309 | 19433.0215 | 4.355
3310 | 18391.5566 | 3.6039
3311 | 17470.3867 | 3.367
3312 | 16600.5957 | 2.9931
3313 | 16276.5977 | 2.9419
3314 | 15449.4922 | 3.0088
3315 | 14712.8496 | 3.2634
3316 | 14725.0801 | 3.2064
3317 | 14825.1953 | 3.182
3318 | 14626.9434 | 3.1107
3319 | 14511.1016 | 3.0896
3320 | 14462.8574 | 3.2335
3321 | 14068.4688 | 2.9844
3322 | 14383.2373 | 2.9959
3323 | 15324.3418 | 3.2422
3324 | 18760.6504 | 3.1979
3325 | 20397.2422 | 3.473
3326 | 22798.0352 | 3.7287
3327 | 24850.6055 | 4.2824
3328 | 26625.8496 | 5.0796
3329 | 27411.7988 | 5.8762
3330 | 27531.0625 | 6.5202
3331 | 27915.4512 | 7.0057
3332 | 28865.127 | 7.0904
3333 | 29153.9062 | 7.1801
3334 | 28963.4004 | 7.1965
3335 | 28874.3906 | 7.4003
3336 | 28452.3906 | 7.3761
3337 | 28702.4102 | 7.199
3338 | 29012.6855 | 7.1191
3339 | 28213.2637 | 6.8401
3340 | 27850.7578 | 6.5705
3341 | 27475.6094 | 6.3871
3342 | 26809.2207 | 6.2347
3343 | 26484.3477 | 6.0872
3344 | 26794.0957 | 6.0972
3345 | 26489.3359 | 6.1764
3346 | 26218.5566 | 6.1602
3347 | 25394.0078 | 6.0521
3348 | 25717.293 | 5.911
3349 | 25710.5352 | 5.9178
3350 | 25304.2617 | 6.031
3351 | 25133.25 | 6.2232
3352 | 24440.334 | 5.9829
3353 | 23134.1328 | 5.7153
3354 | 22505.9727 | 5.5757
3355 | 21053.8867 | 5.0533
3356 | 19771.4336 | 4.784
3357 | 18933.2734 | 4.4386
3358 | 17856.957 | 3.5713
3359 | 17387.9453 | 3.2453
3360 | 16711.7793 | 2.9271
3361 | 15588.2852 | 3.0363
3362 | 15134.1348 | 2.9183
3363 | 14574.3223 | 3.0397
3364 | 14569.3848 | 3.0978
3365 | 14740.7637 | 3.0533
3366 | 15191.7959 | 3.0276
3367 | 14788.1426 | 3.1798
3368 | 15037.7734 | 3.0651
3369 | 15043.0391 | 2.8577
3370 | 15673.1973 | 2.8549
3371 | 16149.1035 | 3.0176
3372 | 18719.5996 | 3.1985
3373 | 20540.4648 | 3.2014
3374 | 22947.3301 | 3.4373
3375 | 24864.8164 | 4.2243
3376 | 27862.8516 | 4.8965
3377 | 27964.7363 | 5.8754
3378 | 27449.9785 | 6.5483
3379 | 28157.5156 | 6.9993
3380 | 28575.4004 | 7.1465
3381 | 28692.5273 | 7.2452
3382 | 29524.7285 | 7.126
3383 | 30354.0137 | 7.2559
3384 | 29667.875 | 7.2888
3385 | 29029.582 | 7.2459
3386 | 26724.5781 | 7.3522
3387 | 26906.7148 | 7.2434
3388 | 25973.5469 | 7.0967
3389 | 25942.418 | 6.7833
3390 | 26348.0723 | 6.5657
3391 | 25675.1562 | 6.423
3392 | 25852.1445 | 6.1792
3393 | 25332.3555 | 6.0112
3394 | 25824.2617 | 5.9618
3395 | 25191.5762 | 5.7558
3396 | 25170.5859 | 5.3152
3397 | 23962.5215 | 5.3338
3398 | 24365.0488 | 5.6285
3399 | 23446.3848 | 5.6723
3400 | 23052.0898 | 5.6002
3401 | 22659.0996 | 5.4156
3402 | 21147.0566 | 5.2029
3403 | 19676.0977 | 4.5892
3404 | 18283.7793 | 4.2918
3405 | 17077.0938 | 3.9116
3406 | 16173.9023 | 3.4906
3407 | 15547.9336 | 3.0822
3408 | 14745.1016 | 2.7765
3409 | 14310.6621 | 2.5624
3410 | 13668.1348 | 2.7244
3411 | 13334.8496 | 2.907
3412 | 13356.8496 | 2.8376
3413 | 13273.9541 | 2.7432
3414 | 13032.4883 | 2.7247
3415 | 12971.9414 | 2.8353
3416 | 12697.9629 | 2.8089
3417 | 12223.9199 | 2.6702
3418 | 12375.5723 | 2.5681
3419 | 12551.9922 | 2.5529
3420 | 13974.1934 | 2.5161
3421 | 15286.5117 | 2.4526
3422 | 16067.6816 | 2.5315
3423 | 16981.2402 | 2.6524
3424 | 18746.5664 | 2.9147
3425 | 19789.252 | 3.3915
3426 | 21191.0859 | 3.9906
3427 | 21679.6133 | 4.3898
3428 | 21947.4961 | 4.449
3429 | 21970.877 | 4.5739
3430 | 21229.707 | 4.6628
3431 | 21139.5918 | 4.7599
3432 | 21224.9492 | 4.7379
3433 | 21071.9609 | 4.4559
3434 | 20971.3379 | 4.4546
3435 | 20159.043 | 4.494
3436 | 21819.3809 | 4.3549
3437 | 21315.4961 | 4.313
3438 | 19944.9062 | 4.1717
3439 | 19777.8965 | 4.0963
3440 | 19757.2969 | 4.0965
3441 | 19996.1699 | 4.2289
3442 | 19982.4219 | 4.2775
3443 | 19788.4023 | 4.3104
3444 | 19376.8828 | 4.2102
3445 | 19137.8516 | 4.215
3446 | 18904.9785 | 4.5057
3447 | 18501.3242 | 4.6193
3448 | 17063.125 | 4.4739
3449 | 15491.0391 | 4.148
3450 | 14828.8789 | 3.8905
3451 | 14563.7305 | 3.6568
3452 | 14376.7207 | 3.6497
3453 | 13880.3311 | 3.2741
3454 | 13328.1719 | 3.1452
3455 | 12747.2773 | 3.188
3456 | 12259.0449 | 2.7807
3457 | 11866.3516 | 2.6731
3458 | 11385.6465 | 2.8446
3459 | 11328.4336 | 2.9926
3460 | 11086.5273 | 2.8953
3461 | 10793.7695 | 2.817
3462 | 10358.6211 | 2.5576
3463 | 10169.6094 | 2.5931
3464 | 10119.9785 | 2.5149
3465 | 9745.4727 | 2.5087
3466 | 9730.0742 | 2.5229
3467 | 9892.4844 | 2.5254
3468 | 10616.6406 | 2.4387
3469 | 10953.5391 | 2.5594
3470 | 11784.4551 | 2.6248
3471 | 12533.2344 | 2.6211
3472 | 13464.793 | 2.4357
3473 | 14569.8682 | 2.6288
3474 | 15885.4277 | 2.9677
3475 | 16852.9863 | 3.0363
3476 | 18323.5781 | 3.1267
3477 | 19403.7578 | 3.421
3478 | 20063.6641 | 3.4297
3479 | 20298.5586 | 3.4485
3480 | 20455.0645 | 3.5123
3481 | 20298.4219 | 3.7636
3482 | 20632.9492 | 4.0237
3483 | 20618.8125 | 4.101
3484 | 19799.1367 | 3.8757
3485 | 20738.9473 | 3.7165
3486 | 21130.3477 | 3.6152
3487 | 19644.0117 | 3.7491
3488 | 19396.1484 | 3.7038
3489 | 18898.2637 | 3.7421
3490 | 17834.293 | 3.7319
3491 | 16894.25 | 3.7639
3492 | 15768.9434 | 3.6383
3493 | 15173.9111 | 3.6696
3494 | 14739.0596 | 3.7126
3495 | 14750.9844 | 4.1031
3496 | 15699.9316 | 3.9283
3497 | 15966.5547 | 3.8286
3498 | 16263.8398 | 3.7314
3499 | 16018.5547 | 3.6172
3500 | 15849.1758 | 3.5296
3501 | 14995.2676 | 3.2215
3502 | 14303.7734 | 2.8437
3503 | 13403.2266 | 2.6696
3504 | 12706.3516 | 2.4673
3505 | 12237.7305 | 2.6465
3506 | 12344.9521 | 2.6859
3507 | 12156.5605 | 2.7507
3508 | 12026.5391 | 2.5754
3509 | 11762.5107 | 2.6863
3510 | 11894.4766 | 2.7158
3511 | 11681.5586 | 2.8728
3512 | 11965.6953 | 2.8719
3513 | 11541.9277 | 2.8574
3514 | 12400.6133 | 2.8586
3515 | 13819.2979 | 2.9456
3516 | 17708.0195 | 2.9672
3517 | 20172.1465 | 3.0784
3518 | 22385.5195 | 3.3464
3519 | 23572.5742 | 3.8421
3520 | 25469.5547 | 4.5099
3521 | 25993.207 | 5.4038
3522 | 26913.3867 | 5.8266
3523 | 28069.9355 | 6.5386
3524 | 28729.4941 | 6.8479
3525 | 29782.1797 | 6.8993
3526 | 29432.7598 | 6.8656
3527 | 29263.0117 | 6.7824
3528 | 28495.1055 | 6.6465
3529 | 28652.9883 | 6.54
3530 | 29059.2422 | 6.5875
3531 | 28425.3574 | 6.382
3532 | 28839.7461 | 6.2314
3533 | 27980.832 | 6.0569
3534 | 28172.7148 | 5.9679
3535 | 27265.5469 | 6.1035
3536 | 26267.6172 | 5.9877
3537 | 26303.0195 | 5.9608
3538 | 26507.8711 | 5.8674
3539 | 25777.3438 | 5.8583
3540 | 25717.0918 | 5.5926
3541 | 25227.1641 | 5.4265
3542 | 25303.1855 | 5.4587
3543 | 24645.9004 | 5.6767
3544 | 24000.4785 | 5.6087
3545 | 23403.9531 | 5.1587
3546 | 22460.2773 | 4.8632
3547 | 21299.5898 | 4.6542
3548 | 20207.6641 | 4.2626
3549 | 19173.3477 | 4.0236
3550 | 18278.4316 | 3.6488
3551 | 17425.123 | 3.0202
3552 | 16449.5137 | 2.884
3553 | 15884.7031 | 2.7431
3554 | 15548.3008 | 2.6569
3555 | 14955.5 | 2.8051
3556 | 15130.8789 | 2.7418
3557 | 15065.1309 | 2.7468
3558 | 15137.6387 | 2.7448
3559 | 15207.7305 | 2.958
3560 | 15067.6367 | 2.9885
3561 | 14797.6162 | 2.9823
3562 | 15233.1318 | 3.0211
3563 | 16124.1855 | 3.1206
3564 | 19170.4531 | 3.0893
3565 | 21533.7285 | 3.1916
3566 | 23423.4473 | 3.3379
3567 | 25566.0605 | 4.2497
3568 | 27348.5352 | 4.6337
3569 | 28223.3359 | 5.3054
3570 | 29684.2734 | 6.0411
3571 | 30174.5703 | 6.6684
3572 | 31579.1406 | 6.8633
3573 | 31912.7715 | 6.7504
3574 | 30284.0645 | 6.7803
3575 | 30307.6953 | 6.7973
3576 | 32146.1719 | 6.7861
3577 | 31820.2656 | 6.7298
3578 | 29993.4219 | 6.4724
3579 | 30146.9375 | 6.489
3580 | 29358.3906 | 6.1972
3581 | 29606.2969 | 6.2115
3582 | 29369.9062 | 6.06
3583 | 29621.9062 | 6.0138
3584 | 26984.0293 | 6.0276
3585 | 26933.8926 | 5.9697
3586 | 26427.25 | 5.924
3587 | 25596.4492 | 5.8632
3588 | 25675.0918 | 5.352
3589 | 24969.1641 | 5.2587
3590 | 25216.5645 | 5.4454
3591 | 25419.3223 | 5.7486
3592 | 24687.6484 | 5.5557
3593 | 23987.2363 | 5.1074
3594 | 22437.793 | 4.8562
3595 | 21463.8438 | 4.6507
3596 | 20394.6758 | 4.5501
3597 | 19489.6211 | 4.1322
3598 | 17999.7891 | 3.6255
3599 | 17371.3984 | 3.1743
3600 | 16952.1992 | 2.9507
3601 | 16417.4414 | 2.7316
3602 | 15357.4707 | 2.7097
3603 | 14815.5645 | 2.9703
3604 | 14688.8066 | 2.7782
3605 | 14696.7344 | 2.7547
3606 | 14404.9727 | 2.7352
3607 | 14591.5938 | 2.8406
3608 | 15236.7637 | 2.8406
3609 | 14913.7305 | 2.8077
3610 | 15197.1318 | 2.8288
3611 | 16370.0703 | 3.1131
3612 | 19654.1035 | 3.2931
3613 | 21281.959 | 3.3243
3614 | 23564.709 | 3.4628
3615 | 26178.8398 | 4.2775
3616 | 28442.0938 | 4.7668
3617 | 29298.7578 | 5.8132
3618 | 29775.5371 | 6.3668
3619 | 30297.1895 | 6.9389
3620 | 32523.9414 | 7.0308
3621 | 33530.6055 | 7.0457
3622 | 32172.1719 | 7.2463
3623 | 31531.9922 | 7.0924
3624 | 31539.2773 | 7.1255
3625 | 29797.7891 | 6.8852
3626 | 30912.3594 | 6.922
3627 | 29683.4219 | 6.7355
3628 | 28314.4629 | 6.4176
3629 | 28396.7363 | 6.2636
3630 | 28293.8418 | 6.3225
3631 | 29046.3906 | 6.1006
3632 | 26901.4082 | 6.0236
3633 | 27189.293 | 5.9277
3634 | 27104.2812 | 5.9481
3635 | 25988.375 | 5.6615
3636 | 25907.5977 | 5.2979
3637 | 26249.4805 | 5.3822
3638 | 27036.3984 | 5.3069
3639 | 26176.1016 | 5.6266
3640 | 25085.0488 | 5.4594
3641 | 24722.3848 | 4.8428
3642 | 24231.2207 | 4.7429
3643 | 24568.4395 | 4.4748
3644 | 23266.9961 | 4.0726
3645 | 22086.0566 | 4.0124
3646 | 20930.2441 | 3.5062
3647 | 20302.0859 | 3.2558
3648 | 20176.4551 | 2.9726
3649 | 17066.8691 | 2.7365
3650 | 15600.5352 | 2.6762
3651 | 15095.0527 | 2.8713
3652 | 15173.8682 | 2.8612
3653 | 15026.2363 | 2.8665
3654 | 14733.3633 | 2.9179
3655 | 14465.0889 | 2.9329
3656 | 14976.3516 | 2.939
3657 | 14670.3516 | 2.9411
3658 | 15228.8799 | 2.9511
3659 | 16607.7031 | 3.0364
3660 | 19415.5996 | 3.0909
3661 | 22085.1289 | 3.0692
3662 | 23868.9629 | 3.1506
3663 | 26119.6172 | 3.5855
3664 | 27773.7988 | 3.6791
3665 | 28071.5879 | 4.1885
3666 | 28165.2207 | 4.4242
3667 | 29057.3789 | 4.72
3668 | 29689.9062 | 4.885
3669 | 30070.3164 | 4.8732
3670 | 29140.8945 | 4.8092
3671 | 29211.1484 | 4.8195
3672 | 28846.1387 | 4.7047
3673 | 27899.5898 | 4.6113
3674 | 27883.9355 | 4.5679
3675 | 26950.8105 | 4.5061
3676 | 26826.8828 | 4.3308
3677 | 26820.3984 | 4.2901
3678 | 26867.2715 | 4.2773
3679 | 26172.8828 | 4.3816
3680 | 26454.8594 | 4.2485
3681 | 26390.0078 | 4.2335
3682 | 26269.7559 | 4.2383
3683 | 25308.1973 | 4.3336
3684 | 25614.8184 | 4.3019
3685 | 26719.6406 | 4.2888
3686 | 26650.8828 | 4.5306
3687 | 25002.4062 | 4.9594
3688 | 24206.3848 | 4.7615
3689 | 23603.584 | 4.4439
3690 | 22475.6562 | 4.4151
3691 | 21316.2129 | 4.0355
3692 | 20127.8945 | 3.8099
3693 | 19212.1035 | 3.6532
3694 | 18118.6836 | 3.2117
3695 | 17485.0527 | 2.9752
3696 | 16829.8105 | 2.7194
3697 | 15767.7656 | 2.6567
3698 | 15317.3555 | 2.653
3699 | 14842.8066 | 2.8512
3700 | 14766.502 | 2.785
3701 | 14975.8398 | 2.7277
3702 | 14751.4785 | 2.666
3703 | 14692.4902 | 2.7112
3704 | 14731.8477 | 2.7244
3705 | 14476.3516 | 2.755
3706 | 14928.1211 | 2.9771
3707 | 16067.9111 | 3.093
3708 | 19304.6094 | 3.0326
3709 | 21026.6953 | 3.1392
3710 | 23286.4336 | 3.1883
3711 | 25209.9219 | 4.1336
3712 | 27830.5566 | 4.4239
3713 | 28142.2109 | 5.2211
3714 | 28877.1055 | 5.9631
3715 | 29053.6328 | 6.5732
3716 | 29241.2637 | 6.9022
3717 | 29323.5156 | 7.0137
3718 | 30025.0547 | 7.1356
3719 | 29367.9062 | 7.0681
3720 | 27647.9355 | 6.9713
3721 | 26757.5039 | 6.8732
3722 | 26521.1113 | 6.8483
3723 | 26206.8828 | 6.8238
3724 | 25801.9648 | 6.6844
3725 | 25426.8398 | 6.4351
3726 | 25522.5859 | 6.1793
3727 | 25023.0488 | 5.8434
3728 | 25080.7969 | 5.6201
3729 | 24555.9004 | 5.3436
3730 | 24478.0176 | 5.3551
3731 | 23852.7305 | 5.2295
3732 | 23554.1094 | 4.9931
3733 | 23549.582 | 4.8178
3734 | 23601.7207 | 4.975
3735 | 23819.4688 | 5.1966
3736 | 22802.668 | 5.0701
3737 | 21845.498 | 4.9263
3738 | 20786.1914 | 4.685
3739 | 19426.3574 | 4.3235
3740 | 18184.9141 | 3.941
3741 | 17553.7676 | 3.5761
3742 | 16839.1016 | 3.275
3743 | 15925.1758 | 2.9714
3744 | 15133.5 | 2.6717
3745 | 14481.4277 | 2.7506
3746 | 14049.0605 | 2.7165
3747 | 13706.8369 | 2.5989
3748 | 13399.1602 | 2.4994
3749 | 13454.4043 | 2.4384
3750 | 13162.8867 | 2.438
3751 | 13101.8984 | 2.5621
3752 | 12531.2344 | 2.5259
3753 | 12312.5918 | 2.4815
3754 | 12506.4766 | 2.487
3755 | 13106.4023 | 2.4482
3756 | 14332.584 | 2.5008
3757 | 15326.9004 | 2.5216
3758 | 16352.3008 | 2.6301
3759 | 17269.2402 | 2.8166
3760 | 19105.3457 | 2.9466
3761 | 19982.125 | 3.7902
3762 | 21121.8223 | 4.031
3763 | 21568.9688 | 4.4426
3764 | 21975.4961 | 4.7972
3765 | 21751.2441 | 4.9225
3766 | 21495.2246 | 5.0352
3767 | 21013.8242 | 4.9465
3768 | 20936.5605 | 4.926
3769 | 21040.6016 | 4.9239
3770 | 20702.6758 | 4.9681
3771 | 20208.4219 | 4.864
3772 | 20030.8848 | 4.745
3773 | 20173.0215 | 4.6378
3774 | 19896.1484 | 4.4834
3775 | 19833.8965 | 4.3915
3776 | 19970.8848 | 4.3254
3777 | 19683.7578 | 4.3762
3778 | 19485.3672 | 4.2612
3779 | 19297.4844 | 4.2217
3780 | 19480.1484 | 4.2398
3781 | 19292.1055 | 4.2445
3782 | 19276.4727 | 4.1608
3783 | 18969.8516 | 4.5929
3784 | 17875.168 | 4.4235
3785 | 16355.333 | 4.1662
3786 | 15606.417 | 4.0791
3787 | 15233.6367 | 3.8121
3788 | 14909.7529 | 3.4902
3789 | 14448.9727 | 3.2465
3790 | 13608.4238 | 3.1854
3791 | 12616.2656 | 3.1074
3792 | 12155.4121 | 2.7793
3793 | 11573.8984 | 2.58
3794 | 11315.9922 | 2.5892
3795 | 11099.3711 | 2.8179
3796 | 10923.2129 | 2.8422
3797 | 10636.9824 | 2.9232
3798 | 10581.2852 | 2.8599
3799 | 10569.6094 | 2.8771
3800 | 10422 | 2.8134
3801 | 9962.3262 | 2.7311
3802 | 9944.0938 | 2.7158
3803 | 10005.9785 | 2.6914
3804 | 10892.8945 | 2.655
3805 | 11340.6641 | 2.5543
3806 | 11916.959 | 2.5332
3807 | 12812.75 | 2.5446
3808 | 13586.583 | 2.4837
3809 | 14508.2148 | 2.9598
3810 | 15656.3008 | 2.8199
3811 | 16520.8496 | 2.9994
3812 | 18205.6934 | 3.4499
3813 | 19230.3574 | 3.7088
3814 | 19648.4004 | 3.6089
3815 | 19856.9062 | 3.6578
3816 | 20008.6758 | 3.7845
3817 | 20220.9062 | 4.0436
3818 | 20355.4336 | 4.2953
3819 | 20190.7891 | 4.1444
3820 | 20220.9277 | 4.0418
3821 | 20290.791 | 3.9126
3822 | 20127.8008 | 3.5672
3823 | 19994.9277 | 3.3743
3824 | 20199.6855 | 3.3365
3825 | 19779.3164 | 3.3943
3826 | 18420.1777 | 3.5335
3827 | 17279.1445 | 3.575
3828 | 16159.2383 | 3.548
3829 | 15718.4375 | 3.7436
3830 | 16029.2188 | 3.7607
3831 | 15898.4805 | 3.9386
3832 | 16052.3223 | 3.9457
3833 | 16054.8281 | 3.7829
3834 | 15921.5664 | 3.8218
3835 | 15957.9531 | 3.5142
3836 | 15915.3125 | 3.3978
3837 | 15167.5215 | 3.1511
3838 | 14584.0059 | 3.074
3839 | 13850.8359 | 2.8151
3840 | 13478.8066 | 2.8211
3841 | 12722.1641 | 2.7789
3842 | 12484.8867 | 2.7937
3843 | 12399.5078 | 3.0042
3844 | 12027.4883 | 2.9239
3845 | 11758.5918 | 2.9039
3846 | 11714.4531 | 2.8208
3847 | 11583.4648 | 2.8175
3848 | 11515.9473 | 2.7862
3849 | 11180.4316 | 2.8011
3850 | 11156.8203 | 2.6952
3851 | 12530.1289 | 2.6038
3852 | 16491.9766 | 2.8422
3853 | 19613.1387 | 2.9731
3854 | 22059.4023 | 3.1789
3855 | 23332.2266 | 3.9118
3856 | 26995.1562 | 4.5688
3857 | 27572.4414 | 5.3954
3858 | 29173.9062 | 5.9762
3859 | 29829.1914 | 6.5004
3860 | 30174.9375 | 6.6465
3861 | 30351.2344 | 6.6893
3862 | 29174.6426 | 6.7381
3863 | 30030.3594 | 6.7131
3864 | 29872.6855 | 6.8562
3865 | 29343.5371 | 6.8218
3866 | 30011.6953 | 6.9508
3867 | 29457.9277 | 6.6142
3868 | 29847.3066 | 6.4348
3869 | 29138.918 | 6.4842
3870 | 27551.957 | 6.2999
3871 | 27491.957 | 6.3897
3872 | 26352.7871 | 6.3605
3873 | 25929.8711 | 6.2795
3874 | 25554.1016 | 6.4473
3875 | 24623.5547 | 6.1256
3876 | 24935.207 | 5.8265
3877 | 24071.1426 | 5.5125
3878 | 23590.7539 | 5.5162
3879 | 23488.5938 | 5.8193
3880 | 22786.5508 | 5.6876
3881 | 22489.793 | 5.1767
3882 | 21510.7383 | 5.0605
3883 | 20001.1602 | 4.7718
3884 | 19596.6328 | 4.5194
3885 | 18671.4414 | 4.3182
3886 | 18222.1992 | 3.4593
3887 | 17294.25 | 2.9963
3888 | 16089.7227 | 2.7592
3889 | 15282.9863 | 2.6785
3890 | 15036.8496 | 2.7129
3891 | 14733.3125 | 2.8263
3892 | 14661.6797 | 2.7445
3893 | 14428.4805 | 2.9654
3894 | 14193.6582 | 2.969
3895 | 14391.8691 | 3.0616
3896 | 14366.7207 | 3.0366
3897 | 13888.8145 | 3.0163
3898 | 14256.1943 | 3.0194
3899 | 14987.1094 | 3.0529
3900 | 17728.6387 | 3.0749
3901 | 20208.1484 | 3.1668
3902 | 22299.2656 | 3.5839
3903 | 23950.1094 | 4.0532
3904 | 25380.1953 | 4.5998
3905 | 25526.1953 | 5.2345
3906 | 26934.9258 | 5.8096
3907 | 27870.4629 | 6.405
3908 | 28031.9785 | 6.6304
3909 | 29188.4336 | 6.4579
3910 | 28951.4004 | 6.4983
3911 | 29114.4336 | 6.6341
3912 | 29030.7793 | 6.649
3913 | 30185.5293 | 6.6796
3914 | 31023.5059 | 6.653
3915 | 30010.418 | 6.4825
3916 | 29270.2949 | 6.4529
3917 | 29537.457 | 6.3757
3918 | 28260.2656 | 6.3289
3919 | 26921.9355 | 6.1982
3920 | 26765.7988 | 6.1441
3921 | 26421.5234 | 5.9832
3922 | 25773.6172 | 5.9671
3923 | 25527.8711 | 5.5697
3924 | 25415.9863 | 5.2029
3925 | 24939.5547 | 5.1086
3926 | 24796.332 | 5.2655
3927 | 24372.543 | 5.5129
3928 | 23629.4883 | 5.4191
3929 | 23167.2148 | 5.1767
3930 | 21992.2773 | 4.7999
3931 | 20685.4531 | 4.6187
3932 | 19871.918 | 4.3932
3933 | 19061.3672 | 4.1509
3934 | 18274.1992 | 3.6969
3935 | 17391.0293 | 3.1919
3936 | 16328.1133 | 2.8057
3937 | 15731.3047 | 2.7107
3938 | 15337.4912 | 2.9282
3939 | 15024.3945 | 3.0385
3940 | 14673.3633 | 2.982
3941 | 13733.4355 | 2.9703
3942 | 14221.5957 | 2.9197
3943 | 14285.709 | 2.8254
3944 | 14106.8359 | 2.9523
3945 | 13918.0566 | 3.0815
3946 | 14231.9395 | 3.1189
3947 | 15576.0273 | 3.0909
3948 | 19306.7266 | 3.0187
3949 | 21991.75 | 3.4166
3950 | 23959.6055 | 3.4785
3951 | 25939.0898 | 3.9927
3952 | 27402.1875 | 4.562
3953 | 27965.4512 | 5.5092
3954 | 27943.8203 | 6.0028
3955 | 28782.6426 | 6.2633
3956 | 29267.9277 | 6.488
3957 | 29746.5703 | 6.3274
3958 | 30041.4434 | 6.3326
3959 | 31272.6562 | 6.4076
3960 | 32055.5742 | 6.4377
3961 | 31820.6777 | 6.4471
3962 | 30895.1406 | 6.4796
3963 | 30173.6016 | 6.3585
3964 | 31210.0352 | 6.1509
3965 | 30871.8984 | 6.0191
3966 | 29556.9609 | 6.0435
3967 | 29362.1582 | 6.0792
3968 | 27073.6836 | 5.9217
3969 | 26876.3047 | 5.8045
3970 | 26493.5254 | 5.7757
3971 | 25640.125 | 5.6477
3972 | 26070.9961 | 5.2484
3973 | 25708.0078 | 5.1005
3974 | 25546.7461 | 5.1689
3975 | 25370.1016 | 5.3646
3976 | 25161.8496 | 5.4084
3977 | 24155.2812 | 4.9769
3978 | 22914.0898 | 4.8571
3979 | 21341.3594 | 4.5468
3980 | 20550.4434 | 4.4356
3981 | 19848.7676 | 4.0008
3982 | 18850.3574 | 3.4651
3983 | 17887.2305 | 3.2945
3984 | 16967.9668 | 3.0721
3985 | 16229.3984 | 2.7273
3986 | 15584.4805 | 2.7074
3987 | 15241.4707 | 2.8749
3988 | 14762.6406 | 2.7502
3989 | 14305.4277 | 2.7003
3990 | 14250.4902 | 2.6072
3991 | 14328.8359 | 2.7616
3992 | 14325.0889 | 2.7145
3993 | 14107.2051 | 2.7079
3994 | 14547.9844 | 2.6784
3995 | 15654.0273 | 2.7319
3996 | 19293.7363 | 2.8523
3997 | 21451.3594 | 3.231
3998 | 23567.4688 | 3.4442
3999 | 26179.5957 | 4.1115
4000 | 27264.5352 | 4.5911
4001 | 29027.6328 | 5.2628
4002 | 29017.5176 | 5.8583
4003 | 30022.3164 | 6.263
4004 | 31277.0254 | 6.4721
4005 | 33091.8672 | 6.6173
4006 | 32746.3516 | 6.5732
4007 | 30910.3828 | 6.5381
4008 | 31776.0566 | 6.5207
4009 | 32051.4355 | 6.3912
4010 | 31453.8984 | 6.4076
4011 | 31089.1406 | 6.4495
4012 | 29385.0547 | 6.2852
4013 | 27693.5898 | 6.2102
4014 | 27198.5566 | 6.055
4015 | 26903.4297 | 6.0498
4016 | 26859.1777 | 5.8983
4017 | 27044.0723 | 5.8824
4018 | 26199.5234 | 5.7854
4019 | 25457.9863 | 5.43
4020 | 25534.8594 | 5.2805
4021 | 25665.5039 | 5.073
4022 | 25268.4707 | 5.1725
4023 | 25208.8594 | 5.5026
4024 | 25035.5762 | 5.5376
4025 | 23865.5117 | 5.2755
4026 | 22465.4453 | 5.1459
4027 | 21055.1074 | 4.6795
4028 | 19851.4121 | 4.3219
4029 | 19263.6406 | 3.9247
4030 | 18323.3242 | 3.3992
4031 | 17580.5469 | 3.3252
4032 | 16500.0391 | 3.1408
4033 | 15697.376 | 2.9594
4034 | 15316.9863 | 2.7881
4035 | 14760.5527 | 2.8951
4036 | 14943.334 | 2.8379
4037 | 14188.0918 | 2.764
4038 | 14414.6055 | 2.7119
4039 | 14266.6992 | 2.8031
4040 | 13864.3086 | 2.8029
4041 | 13773.0889 | 2.7941
4042 | 14165.9619 | 2.8814
4043 | 15339.0176 | 2.9763
4044 | 19064.7539 | 2.9752
4045 | 20861.25 | 3.0773
4046 | 23242.0352 | 3.0743
4047 | 25738.8574 | 3.4869
4048 | 27180.3438 | 3.9097
4049 | 28948.2188 | 4.4624
4050 | 31052.5586 | 5.0103
4051 | 29506.168 | 5.3293
4052 | 30923.2363 | 5.5714
4053 | 30792.9121 | 5.8796
4054 | 30785.4375 | 5.9488
4055 | 29976.7305 | 5.8243
4056 | 29933.625 | 5.7313
4057 | 29650.5938 | 5.7145
4058 | 27962.4883 | 5.7555
4059 | 27920.957 | 5.5337
4060 | 25921.3496 | 5.1943
4061 | 25232.3242 | 5.1744
4062 | 25926.6934 | 5.0959
4063 | 25068.3262 | 4.958
4064 | 25622.0859 | 4.7775
4065 | 24924.4531 | 4.7936
4066 | 25503.3828 | 4.8753
4067 | 23622.8301 | 4.8664
4068 | 23840.6719 | 4.732
4069 | 23628.2109 | 4.6239
4070 | 23086.0938 | 4.8399
4071 | 23839.3496 | 5.1641
4072 | 25367.6445 | 4.9383
4073 | 25553.4922 | 4.8305
4074 | 24372.5547 | 4.7658
4075 | 22588.584 | 4.4791
4076 | 21508.1523 | 4.0684
4077 | 20201.582 | 3.7108
4078 | 18618.6211 | 3.248
4079 | 17739.1992 | 2.68
4080 | 16508.0078 | 2.8095
4081 | 15879.8496 | 2.662
4082 | 15603.459 | 2.6158
4083 | 15276.8174 | 2.7135
4084 | 15176.3125 | 2.4393
4085 | 14271.7637 | 2.4054
4086 | 13894.8682 | 2.4052
4087 | 13643.6055 | 2.5211
4088 | 13643.6035 | 2.4591
4089 | 13342.0879 | 2.5689
4090 | 13241.584 | 2.6718
4091 | 13216.457 | 2.4501
4092 | 14673.7852 | 2.3992
4093 | 15377.3232 | 2.5764
4094 | 16231.6172 | 2.745
4095 | 17312.0508 | 2.8307
4096 | 18945.2617 | 2.6658
4097 | 20151.3281 | 3.4523
4098 | 21432.7734 | 3.8667
4099 | 22211.6875 | 4.076
4100 | 22287.0664 | 4.2999
4101 | 22010.6797 | 4.5776
4102 | 22186.5625 | 4.6207
4103 | 22337.3203 | 4.5788
4104 | 22211.6875 | 4.5523
4105 | 22387.5723 | 4.549
4106 | 22261.9414 | 4.4224
4107 | 22287.0684 | 4.4623
4108 | 21457.8984 | 4.5502
4109 | 21131.2539 | 4.3437
4110 | 21784.5391 | 4.217
4111 | 22136.3086 | 4.1283
4112 | 23744.3965 | 4.1277
4113 | 23945.4043 | 4.1602
4114 | 23945.4062 | 4.289
4115 | 22965.4766 | 4.2252
4116 | 22588.582 | 4.1862
4117 | 21633.7832 | 4.0969
4118 | 20628.7305 | 4.1309
4119 | 20075.9492 | 4.1616
4120 | 18417.6094 | 4.0676
4121 | 16558.2617 | 3.8478
4122 | 15930.1025 | 3.623
4123 | 15779.3457 | 3.4767
4124 | 15502.9531 | 3.5697
4125 | 15075.8066 | 3.2051
4126 | 14673.7852 | 2.9777
4127 | 14045.626 | 2.9343
4128 | 13643.6035 | 2.8123
4129 | 13166.2051 | 2.8235
4130 | 12914.9414 | 2.5
4131 | 12814.4355 | 2.7209
4132 | 12764.1836 | 2.6467
4133 | 12437.5391 | 2.5412
4134 | 12337.0352 | 2.5982
4135 | 12261.6562 | 2.6381
4136 | 12337.0352 | 2.3225
4137 | 12161.1504 | 2.3772
4138 | 11985.2656 | 2.313
4139 | 12035.5195 | 2.3052
4140 | 13040.5723 | 2.5381
4141 | 13568.2266 | 2.5989
4142 | 14271.7637 | 2.5867
4143 | 14975.3008 | 2.6225
4144 | 15854.7227 | 2.5479
4145 | 16834.6504 | 2.8935
4146 | 17111.041 | 2.773
4147 | 18266.8516 | 2.8954
4148 | 19824.6855 | 3.2363
4149 | 20678.9805 | 3.3889
4150 | 21382.5195 | 3.4803
4151 | 21809.668 | 3.5513
4152 | 21834.793 | 3.4562
4153 | 21533.2773 | 3.4794
4154 | 21382.5195 | 3.302
4155 | 20879.9922 | 3.0989
4156 | 20854.8672 | 3.0682
4157 | 20503.0977 | 3.0096
4158 | 20930.2441 | 2.9095
4159 | 21106.1289 | 2.7532
4160 | 21231.7617 | 2.7117
4161 | 20930.2441 | 2.795
4162 | 19849.8125 | 2.8859
4163 | 18216.5977 | 2.7925
4164 | 17286.9258 | 2.8346
4165 | 16709.0195 | 2.9282
4166 | 16759.2715 | 3.0556
4167 | 17035.6602 | 3.2789
4168 | 17060.7891 | 3.4219
4169 | 16935.1562 | 3.4559
4170 | 16784.3984 | 3.2918
4171 | 16558.2617 | 2.9825
4172 | 16558.2617 | 2.8654
4173 | 15829.5977 | 2.7742
4174 | 15352.1953 | 2.565
4175 | 14824.542 | 2.4221
4176 | 14196.3848 | 2.3113
4177 | 13794.3633 | 2.3054
4178 | 13266.709 | 2.2926
4179 | 13141.0781 | 2.4703
4180 | 12688.8027 | 2.4102
4181 | 12412.4141 | 2.5978
4182 | 12487.792 | 2.6285
4183 | 12462.666 | 2.7155
4184 | 12487.793 | 2.6892
4185 | 12236.5293 | 2.7379
4186 | 12764.1836 | 2.8154
4187 | 14523.0254 | 2.7223
4188 | 18116.0938 | 2.7835
4189 | 20151.3281 | 2.8952
4190 | 22161.4336 | 2.965
4191 | 25050.9648 | 3.3364
4192 | 27865.1133 | 3.2186
4193 | 28794.791 | 3.5225
4194 | 29598.834 | 3.9507
4195 | 29900.3496 | 3.8581
4196 | 29950.6016 | 3.7286
4197 | 30101.3594 | 3.8039
4198 | 30000.8555 | 3.7944
4199 | 30855.1484 | 3.8078
4200 | 31433.0547 | 3.8139
4201 | 31809.9512 | 3.7263
4202 | 31583.8145 | 3.5025
4203 | 30629.0117 | 3.751
4204 | 30176.7402 | 3.6821
4205 | 30528.5078 | 3.7407
4206 | 28417.8945 | 3.5358
4207 | 28417.8965 | 3.2945
4208 | 26633.9238 | 3.2988
4209 | 26633.9258 | 3.4419
4210 | 26257.0293 | 3.2501
4211 | 25603.7461 | 3.2181
4212 | 25452.9883 | 3.2055
4213 | 25076.0898 | 3.1466
4214 | 24849.9531 | 3.1365
4215 | 24849.9531 | 3.476
4216 | 23895.1523 | 3.4322
4217 | 23216.7422 | 3.2656
4218 | 22261.9414 | 3.1781
4219 | 20879.9922 | 3.0869
4220 | 20377.4648 | 2.7988
4221 | 19271.9062 | 2.7208
4222 | 18291.9766 | 2.7904
4223 | 17638.6953 | 2.6536
4224 | 16910.0312 | 2.4925
4225 | 16156.2402 | 2.5459
4226 | 15729.0918 | 2.5518
4227 | 15352.1953 | 2.7685
4228 | 15301.9434 | 2.7622
4229 | 15151.1855 | 2.7586
4230 | 15301.9434 | 2.6952
4231 | 15377.3223 | 2.7029
4232 | 15151.1855 | 2.6164
4233 | 14648.6582 | 2.7761
4234 | 15201.4375 | 2.7686
4235 | 16281.8711 | 2.9021
4236 | 19900.0625 | 2.9377
4237 | 21709.1621 | 3.1943
4238 | 24598.6895 | 3.3119
4239 | 26206.7754 | 3.5902
4240 | 27412.8418 | 3.7308
4241 | 29020.9258 | 4.2143
4242 | 30277.2441 | 4.251
4243 | 29347.5684 | 4.4984
4244 | 30101.3594 | 4.3836
4245 | 31106.4141 | 4.4525
4246 | 30277.2441 | 4.5583
4247 | 30453.1289 | 4.5231
4248 | 31081.2852 | 4.466
4249 | 30880.2773 | 4.3585
4250 | 30704.3926 | 4.1633
4251 | 30830.0234 | 4.1509
4252 | 30553.6328 | 4.2152
4253 | 30553.6328 | 4.4491
4254 | 28870.168 | 4.3198
4255 | 28518.4004 | 4.2641
4256 | 28141.5059 | 4.306
4257 | 28644.0312 | 4.1388
4258 | 28342.5156 | 4.0118
4259 | 27739.4844 | 4.0707
4260 | 27538.4727 | 3.8482
4261 | 27613.8516 | 3.9693
4262 | 27010.8203 | 4.07
4263 | 26483.168 | 4.0761
4264 | 26483.168 | 3.9445
4265 | 25553.4902 | 3.7427
4266 | 24422.8066 | 3.5923
4267 | 22613.7109 | 3.3419
4268 | 21081.0039 | 3.0666
4269 | 20377.4648 | 2.6367
4270 | 19573.4219 | 2.4512
4271 | 18543.2422 | 2.3506
4272 | 17714.0723 | 2.2831
4273 | 17085.9141 | 2.3216
4274 | 16734.1465 | 2.2998
4275 | 16306.9971 | 2.5454
4276 | 16407.502 | 2.5168
4277 | 16482.8809 | 2.5088
4278 | 16533.1348 | 2.5311
4279 | 16407.502 | 2.6482
4280 | 15553.207 | 2.6907
4281 | 14950.1758 | 2.9049
4282 | 15050.6797 | 2.7299
4283 | 16533.1328 | 2.8932
4284 | 19623.6738 | 3.0342
4285 | 21658.9102 | 3.6293
4286 | 23920.2812 | 4.1369
4287 | 26432.9141 | 4.9401
4288 | 28669.1602 | 5.2425
4289 | 29020.9258 | 5.8166
4290 | 30126.4863 | 6.026
4291 | 30051.1094 | 6.0142
4292 | 32036.0859 | 6.072
4293 | 31809.9512 | 6.0927
4294 | 31985.8359 | 6.0712
4295 | 32438.1074 | 6.1617
4296 | 34046.1953 | 6.1419
4297 | 35051.25 | 6.0077
4298 | 35578.9023 | 5.9248
4299 | 32764.7539 | 5.9461
4300 | 33141.6484 | 5.8874
4301 | 32840.1328 | 5.6301
4302 | 30779.7715 | 5.6322
4303 | 30830.0234 | 5.6086
4304 | 28292.2656 | 5.6285
4305 | 27940.4922 | 5.3911
4306 | 27463.0938 | 5.2004
4307 | 26608.8008 | 4.799
4308 | 26633.9258 | 4.868
4309 | 26332.4062 | 4.9239
4310 | 25829.8828 | 4.8719
4311 | 25880.1328 | 4.9048
4312 | 25327.3555 | 4.8478
4313 | 24322.3008 | 4.6723
4314 | 23040.8574 | 4.2694
4315 | 21332.2656 | 4.1922
4316 | 20477.9688 | 3.9048
4317 | 19874.9375 | 3.7522
4318 | 18895.0098 | 3.4176
4319 | 17915.082 | 3.3747
4320 | 17161.293 | 3.2523
4321 | 16709.0195 | 3.249
4322 | 16709.0195 | 3.2841
4323 | 16156.2402 | 3.5706
4324 | 16256.7451 | 3.5001
4325 | 16332.123 | 3.4479
4326 | 16131.1133 | 3.4039
4327 | 16156.2393 | 3.3355
4328 | 16181.3662 | 3.1474
4329 | 15829.5957 | 3.304
4330 | 16206.4932 | 3.3451
4331 | 17487.9355 | 3.6293
4332 | 20854.8672 | 3.6646
4333 | 23091.1094 | 3.9587
4334 | 26106.2695 | 4.4719
4335 | 28091.25 | 4.9529
4336 | 29247.0625 | 5.5263
4337 | 29046.0527 | 5.835
4338 | 29071.1797 | 5.9476
4339 | 28443.0215 | 6.0673
4340 | 29448.0742 | 6.1256
4341 | 30804.8965 | 6.0934
4342 | 30654.1387 | 5.935
4343 | 30252.1172 | 5.9687
4344 | 30151.6133 | 5.8891
4345 | 30352.623 | 5.7666
4346 | 30226.9922 | 5.6652
4347 | 30428.002 | 5.639
4348 | 29975.7285 | 5.4475
4349 | 29221.9375 | 5.4794
4350 | 29322.4434 | 5.2319
4351 | 28769.6641 | 5.2337
4352 | 28443.0215 | 5.1292
4353 | 27764.6094 | 4.974
4354 | 26659.0508 | 4.6769
4355 | 25754.502 | 4.5457
4356 | 25930.3867 | 4.6675
4357 | 26156.5234 | 4.5633
4358 | 26056.0195 | 4.4978
4359 | 26206.7773 | 4.7896
4360 | 26056.0195 | 4.7773
4361 | 25377.6094 | 4.306
4362 | 23895.1523 | 3.9875
4363 | 22312.1953 | 3.85
4364 | 20653.8555 | 3.6558
4365 | 19799.5586 | 3.3431
4366 | 19096.0195 | 3.1598
4367 | 18392.4844 | 2.9518
4368 | 17889.957 | 2.8582
4369 | 17337.1758 | 2.9121
4370 | 16809.5234 | 3.0229
4371 | 16382.375 | 3.1149
4372 | 16432.6289 | 3.134
4373 | 16583.3867 | 3.1614
4374 | 16357.249 | 3.0697
4375 | 16281.8711 | 2.917
4376 | 15804.4707 | 3.0282
4377 | 15201.4375 | 3.1508
4378 | 15151.1855 | 3.255
4379 | 16357.249 | 3.6308
4380 | 19096.0195 | 3.7756
4381 | 20678.9824 | 4.0226
4382 | 22462.9531 | 4.3875
4383 | 26231.9023 | 4.9175
4384 | 27664.1055 | 5.4495
4385 | 27412.8398 | 5.9645
4386 | 27890.2422 | 6.0877
4387 | 27839.9883 | 6.2239
4388 | 28895.2969 | 6.497
4389 | 29297.3164 | 6.5516
4390 | 29020.9277 | 6.5118
4391 | 28644.0312 | 6.3494
4392 | 28417.8965 | 6.3116
4393 | 29046.0527 | 6.3121
4394 | 28518.4004 | 6.3125
4395 | 29598.832 | 6.313
4396 | 27739.4805 | 6.3135
4397 | 27538.4727 | 6.314
4398 | 28041 | 6.3144
4399 | 27915.3672 | 6.3149
4400 | 26508.293 | 6.3154
4401 | 25880.1348 | 6.3159
4402 | 25025.8398 | 6.3163
4403 | 24372.5508 | 6.3168
4404 | 23920.2773 | 6.3173
4405 | 24045.9102 | 6.3178
4406 | 24096.1641 | 6.3182
4407 | 23794.6484 | 6.3187
4408 | 23141.3633 | 6.3192
4409 | 22663.9629 | 6.3197
4410 | 21030.75 | 6.3201
4411 | 18869.8828 | 6.3206
4412 | 18568.3672 | 6.3211
4413 | 17889.957 | 6.3216
4414 | 16558.2617 | 6.322
4415 | 15904.9766 | 6.3225
4416 | 15176.3125 | 6.323
4417 | 14749.1641 | 6.3235
4418 | 14422.5215 | 6.3239
4419 | 14397.3945 | 6.3244
4420 | 14271.7637 | 6.3249
4421 | 13693.8574 | 6.3254
4422 | 13367.2148 | 6.3258
4423 | 13090.8242 | 6.3263
4424 | 12814.4355 | 6.3268
4425 | 12387.2871 | 6.3273
4426 | 12161.1504 | 6.3277
4427 | 12286.7812 | 6.3282
4428 | 13643.6055 | 6.3287
4429 | 14497.9004 | 6.3292
4430 | 15804.4707 | 6.3296
4431 | 16382.376 | 6.3301
4432 | 18166.3477 | 6.3306
4433 | 19045.7695 | 6.3311
4434 | 20101.0742 | 6.3315
4435 | 20704.1074 | 6.332
4436 | 21256.8867 | 6.3325
4437 | 21055.875 | 6.333
4438 | 21935.2988 | 6.3334
4439 | 21432.7715 | 6.3339
4440 | 20955.3711 | 6.3344
4441 | 20477.9727 | 6.3349
4442 | 20729.2344 | 6.3353
4443 | 20477.9727 | 6.3358
4444 | 20352.3398 | 6.3363
4445 | 19824.6836 | 6.3368
4446 | 19900.0625 | 6.3372
4447 | 20176.4551 | 6.3377
4448 | 20151.3281 | 6.3382
4449 | 21407.6445 | 6.3387
4450 | 21935.2969 | 6.3391
4451 | 21382.5195 | 6.3396
4452 | 21432.7715 | 6.3401
4453 | 21885.0449 | 6.3406
4454 | 21734.2871 | 6.341
4455 | 20955.3711 | 6.3415
4456 | 19322.1582 | 6.342
4457 | 17814.5781 | 6.3425
4458 | 17186.418 | 6.3429
4459 | 16884.9023 | 6.3434
4460 | 17010.5352 | 6.3439
4461 | 16583.3887 | 6.3444
4462 | 16030.6074 | 6.3448
4463 | 15276.8164 | 6.3453
4464 | 14648.6582 | 6.3458
4465 | 14221.5117 | 6.3463
4466 | 14070.7529 | 6.3467
4467 | 13919.9941 | 6.3472
4468 | 13718.9824 | 6.3477
4469 | 13316.9629 | 6.3482
4470 | 13216.457 | 6.3486
4471 | 12839.5625 | 6.3491
4472 | 12839.5625 | 6.3496
4473 | 12387.2891 | 6.3501
4474 | 12362.1621 | 6.3505
4475 | 12638.5508 | 6.351
4476 | 13291.8359 | 6.3515
4477 | 13894.8672 | 6.352
4478 | 14749.1641 | 6.3524
4479 | 15276.8164 | 6.3529
4480 | 16080.8604 | 6.3534
4481 | 16859.7773 | 6.3539
4482 | 18166.3477 | 6.3543
4483 | 18995.5156 | 6.3548
4484 | 19849.8105 | 6.3553
4485 | 21030.75 | 6.3558
4486 | 21759.4141 | 6.3562
4487 | 22513.2031 | 6.3567
4488 | 22362.4453 | 6.3572
4489 | 22111.1836 | 6.3577
4490 | 22362.4473 | 6.3581
4491 | 22236.8164 | 6.3586
4492 | 21709.1602 | 6.3591
4493 | 21533.2773 | 6.3596
4494 | 21558.4023 | 6.36
4495 | 21382.5195 | 6.3605
4496 | 21558.4023 | 6.361
4497 | 21131.2559 | 6.3615
4498 | 19799.5586 | 6.3619
4499 | 18694 | 6.3624
4500 | 17789.4531 | 6.3629
4501 | 17337.1777 | 6.3634
4502 | 17312.0508 | 6.3638
4503 | 17337.1758 | 6.3643
4504 | 17136.168 | 6.3648
4505 | 16960.2812 | 6.3653
4506 | 16759.2715 | 6.3657
4507 | 16633.6406 | 6.3662
4508 | 16935.1562 | 6.3667
4509 | 16558.2617 | 6.3672
4510 | 16005.4814 | 6.3676
4511 | 15377.3203 | 6.3681
4512 | 14749.1641 | 6.3686
4513 | 14372.2695 | 6.3691
4514 | 14221.5117 | 6.3696
4515 | 13794.3633 | 6.37
4516 | 13819.4883 | 6.3705
4517 | 13517.9746 | 6.371
4518 | 13342.0879 | 6.3715
4519 | 13241.584 | 6.3719
4520 | 13316.9629 | 6.3724
4521 | 12965.1934 | 6.3729
4522 | 13869.7422 | 6.3734
4523 | 15377.3223 | 6.3738
4524 | 18844.7578 | 6.3743
4525 | 21206.6348 | 6.3748
4526 | 23317.2461 | 6.3753
4527 | 25327.3555 | 6.3757
4528 | 28317.3906 | 6.3762
4529 | 29498.3281 | 6.3767
4530 | 30528.5078 | 6.3772
4531 | 31558.6875 | 6.3776
4532 | 31056.1582 | 6.3781
4533 | 31407.9297 | 6.3786
4534 | 32186.8477 | 6.3791
4535 | 32613.9961 | 6.3795
4536 | 32689.375 | 6.3593
4537 | 31885.3301 | 6.7898
4538 | 31860.2031 | 6.7437
4539 | 31759.6992 | 6.6264
4540 | 32764.75 | 6.5091
4541 | 32262.2266 | 6.3918
4542 | 30302.3711 | 6.2744
4543 | 30252.1172 | 6.1571
4544 | 29347.5703 | 6.115
4545 | 29071.1797 | 5.6065
4546 | 28518.4023 | 5.4139
4547 | 27689.2305 | 5.2247
4548 | 27915.3672 | 5.0354
4549 | 28141.5039 | 4.8328
4550 | 27463.0938 | 4.7961
4551 | 27463.0938 | 4.8306
4552 | 27789.7344 | 4.8652
4553 | 26608.7969 | 4.8997
4554 | 25050.9648 | 4.9343
4555 | 23216.7422 | 4.9688
4556 | 21809.668 | 5.0033
4557 | 20503.0977 | 5.0379
4558 | 19598.5488 | 5.0724
4559 | 18643.7461 | 5.1069
4560 | 18141.2207 | 5.1415
4561 | 17513.0625 | 5.176
4562 | 17136.168 | 5.2105
4563 | 16784.3984 | 5.2451
4564 | 16407.502 | 5.2796
4565 | 16533.1348 | 5.3141
4566 | 16432.6289 | 5.3487
4567 | 16231.6191 | 5.3832
4568 | 16080.8604 | 5.4177
4569 | 15904.9756 | 5.4523
4570 | 16156.2402 | 5.4868
4571 | 17186.4199 | 5.5214
4572 | 20653.8555 | 5.5559
4573 | 23216.7422 | 5.5904
4574 | 25025.8398 | 5.625
4575 | 26709.3047 | 5.6595
4576 | 28819.916 | 5.694
4577 | 29146.5586 | 5.7286
4578 | 29925.4746 | 5.7631
4579 | 31081.2852 | 5.7976
4580 | 31885.332 | 5.8322
4581 | 33091.3984 | 5.8667
4582 | 33041.1445 | 5.9012
4583 | 34071.3242 | 5.9358
4584 | 33593.9219 | 5.9703
4585 | 32840.1328 | 6.0048
4586 | 33342.6602 | 6.0394
4587 | 33166.7734 | 6.0739
4588 | 33292.4062 | 5.9887
4589 | 32639.1211 | 5.8636
4590 | 30176.7383 | 5.8329
4591 | 30327.4961 | 5.7986
4592 | 28468.1484 | 5.6604
4593 | 28694.2852 | 5.3051
4594 | 28091.25 | 5.0302
4595 | 26583.6719 | 4.8052
4596 | 26784.6816 | 4.7302
4597 | 27111.3242 | 4.6094
4598 | 26583.6719 | 4.5866
4599 | 26709.3027 | 4.6195
4600 | 26206.7773 | 4.7134
4601 | 25603.7461 | 4.3899
4602 | 24221.7969 | 4.3202
4603 | 22689.0898 | 3.8881
4604 | 21809.668 | 3.7997
4605 | 20678.9805 | 3.4683
4606 | 19799.5586 | 3.282
4607 | 18945.2617 | 3.2091
4608 | 18065.8418 | 2.86
4609 | 17513.0625 | 3.0196
4610 | 16859.7773 | 3.1561
4611 | 16508.0098 | 3.4054
4612 | 16332.124 | 3.4046
4613 | 16256.7451 | 3.4476
4614 | 16332.125 | 3.3767
4615 | 16181.3652 | 3.3486
4616 | 16231.6182 | 3.3355
4617 | 15955.2285 | 3.4523
4618 | 16206.4922 | 3.5812
4619 | 17211.5469 | 3.5735
4620 | 21332.2676 | 3.7657
4621 | 23970.5312 | 4.3886
4622 | 25452.9863 | 4.6297
4623 | 26809.8086 | 5.4284
4624 | 28468.1465 | 5.9256
4625 | 28895.2969 | 6.416
4626 | 29422.9492 | 6.5127
4627 | 29950.6016 | 6.5794
4628 | 30629.0137 | 6.7625
4629 | 31684.3164 | 6.9226
4630 | 32291.3516 | 6.9187
4631 | 31244.2461 | 6.8163
4632 | 32169.1191 | 7.0914
4633 | 32789.8789 | 6.8434
4634 | 32012.3613 | 6.339
4635 | 31211.1172 | 6.3593
4636 | 31207.3203 | 6.1766
4637 | 30606.8867 | 6.1792
4638 | 30077.0352 | 6.1588
4639 | 29378.6953 | 6.0681
4640 | 29372.8945 | 6.1182
4641 | 29222.1367 | 6.0435
4642 | 28769.6621 | 5.6233
4643 | 27789.7363 | 5.3862
4644 | 27614.8516 | 5.4794
4645 | 27111.7246 | 5.3819
4646 | 26960.5664 | 5.1866
4647 | 27086.1992 | 4.8483
4648 | 26357.5352 | 4.8749
4649 | 25729.377 | 4.819
4650 | 24422.8066 | 4.6362
4651 | 23292.1211 | 4.3072
4652 | 22060.9297 | 3.8742
4653 | 21181.5078 | 3.6188
4654 | 20176.4531 | 3.4746
4655 | 19020.6406 | 3.1694
4656 | 18442.7383 | 3.0268
4657 | 17688.9453 | 3.0373
4658 | 17286.9258 | 3.0264
4659 | 16683.8926 | 3.1713
4660 | 16709.0195 | 3.1849
4661 | 16809.5234 | 3.2635
4662 | 16558.2617 | 3.2223
4663 | 16508.0078 | 3.4498
4664 | 16382.377 | 3.4144
4665 | 15980.3555 | 3.4434
4666 | 16784.3984 | 3.4117
4667 | 17412.5566 | 3.6655
4668 | 20628.7266 | 3.8072
4669 | 23243.0664 | 4.3256
4670 | 25378.209 | 4.8109
4671 | 28417.8945 | 5.6808
4672 | 30756.4453 | 6.2278
4673 | 31207.918 | 6.6878
4674 | 32036.2852 | 6.7732
4675 | 31961.1094 | 6.7116
4676 | 33596.7227 | 6.9264
4677 | 34377.0352 | 7.0273
4678 | 35029.125 | 6.9034
4679 | 34976.8672 | 6.8753
4680 | 35202.4062 | 6.8802
4681 | 34802.3828 | 6.804
4682 | 33522.7422 | 6.5962
4683 | 33952.2969 | 6.3969
4684 | 33404.1133 | 6.3505
4685 | 31913.8555 | 6.374
4686 | 31086.2891 | 6.3076
4687 | 30431.6016 | 6.1925
4688 | 30253.918 | 6.0596
4689 | 29775.7188 | 5.8011
4690 | 29073.5801 | 5.4003
4691 | 28046.4004 | 5.0813
4692 | 27719.5547 | 5.0849
4693 | 27490.6191 | 4.9087
4694 | 25680.5254 | 4.8379
4695 | 25930.9863 | 4.8822
4696 | 25729.377 | 5.0302
4697 | 24925.332 | 4.6699
4698 | 23518.2578 | 4.4595
4699 | 21885.0449 | 4.1924
4700 | 20729.2324 | 3.8769
4701 | 20000.5703 | 3.498
4702 | 19171.3984 | 3.4179
4703 | 18241.7266 | 3.1545
4704 | 17387.4297 | 3.0422
4705 | 16759.2734 | 3.0301
4706 | 16332.125 | 3.0452
4707 | 15854.7227 | 3.2895
4708 | 15879.8496 | 3.3674
4709 | 16910.0312 | 3.3868
4710 | 15258.6895 | 3.2866
4711 | 15075.8066 | 3.3095
4712 | 16105.9863 | 3.4767
4713 | 17060.7891 | 3.3428
4714 | 18040.7148 | 3.4454
4715 | 19824.6855 | 3.6542
4716 | 21734.2891 | 3.8777
4717 | 23568.5098 | 4.3335
4718 | 25603.7441 | 4.935
4719 | 27814.8613 | 5.7827
4720 | 28899.6973 | 6.444
4721 | 29727.6641 | 6.8271
4722 | 30880.2773 | 7.0323
4723 | 31433.0547 | 7.1018
4724 | 30630.2109 | 7.1713
4725 | 31132.3398 | 7.1627
4726 | 30885.0781 | 7.0471
4727 | 30516.7812 | 6.8561
4728 | 30614.2871 | 6.9174
4729 | 30145.4883 | 6.8021
4730 | 30361.623 | 6.597
4731 | 31003.9824 | 6.4782
4732 | 27690.5039 | 6.3665
4733 | 27119.9238 | 6.34
4734 | 28852.2422 | 6.004
4735 | 27020.6211 | 5.9442
4736 | 26199.248 | 5.8697
4737 | 25665.7969 | 5.6878
4738 | 25665.998 | 5.3025
4739 | 25239.4473 | 5.1295
4740 | 25688.5234 | 5.1546
4741 | 25632.0703 | 4.908
4742 | 25780.2285 | 4.6354
4743 | 25103.0176 | 4.7294
4744 | 24473.2578 | 4.7441
4745 | 23392.627 | 4.4508
4746 | 21985.5508 | 4.2427
4747 | 20578.4727 | 4.1606
4748 | 19523.1719 | 3.6594
4749 | 18895.0098 | 3.359
4750 | 18216.5996 | 3.3367
4751 | 17462.8086 | 3.0068
4752 | 16633.6406 | 2.825
4753 | 15904.9746 | 2.9444
4754 | 15703.9648 | 3.1089
4755 | 15226.5625 | 3.3512
4756 | 15000.4277 | 3.337
4757 | 15025.5547 | 3.3097
4758 | 15000.4277 | 3.2554
4759 | 14799.417 | 2.9052
4760 | 14724.0371 | 2.9026
4761 | 14497.9004 | 2.9684
4762 | 14573.2793 | 3.1
4763 | 14221.5117 | 2.9391
4764 | 15327.0684 | 2.9116
4765 | 16231.6182 | 2.9913
4766 | 17186.4199 | 3.2416
4767 | 17990.4629 | 3.9255
4768 | 19799.5586 | 4.2872
4769 | 21182.3086 | 4.5012
4770 | 22488.4785 | 4.8444
4771 | 23091.1094 | 4.9122
4772 | 23468.0039 | 5.0223
4773 | 24322.3008 | 5.0063
4774 | 24799.7031 | 4.9692
4775 | 24749.4492 | 4.8941
4776 | 24448.1328 | 4.7696
4777 | 23945.4062 | 4.6284
4778 | 24146.416 | 4.4654
4779 | 24121.2891 | 4.468
4780 | 23723.8691 | 4.4075
4781 | 23675.0156 | 4.4403
4782 | 23548.3828 | 4.4873
4783 | 23620.9609 | 4.5621
4784 | 23524.457 | 4.2923
4785 | 23299.1211 | 4.0343
4786 | 22870.9727 | 3.8357
4787 | 22020.0762 | 3.7265
4788 | 21789.541 | 3.614
4789 | 21491.625 | 3.5489
4790 | 21012.4258 | 3.7347
4791 | 20505.4961 | 3.4518
4792 | 19398.3359 | 3.7862
4793 | 18266.8516 | 3.7778
4794 | 17412.5566 | 3.6889
4795 | 17161.293 | 3.3791
4796 | 16985.4102 | 3.2542
4797 | 16382.377 | 3.1605
4798 | 15804.4707 | 3.0029
4799 | 15352.1953 | 2.89
4800 | 15000.4277 | 2.7235
4801 | 14573.2793 | 2.7481
4802 | 14121.0059 | 2.7014
4803 | 13794.3633 | 2.7014
4804 | 13668.7324 | 2.6485
4805 | 13316.9619 | 2.6214
4806 | 13090.8252 | 2.5399
4807 | 13090.8252 | 2.4826
4808 | 12940.0664 | 2.4974
4809 | 12362.1602 | 2.5786
4810 | 12412.4141 | 2.4822
4811 | 12563.1719 | 2.4951
4812 | 13645.4053 | 2.5817
4813 | 14401.3965 | 2.764
4814 | 14857.2695 | 2.6834
4815 | 15686.8389 | 2.7475
4816 | 16601.1875 | 2.8277
4817 | 17945.4102 | 3.1481
4818 | 19178.998 | 3.3121
4819 | 20036.4961 | 3.5582
4820 | 20886.5918 | 3.937
4821 | 22302.0664 | 3.8654
4822 | 22876.9727 | 3.9686
4823 | 22991.4766 | 4.0838
4824 | 23500.0059 | 4.3228
4825 | 23605.9121 | 4.2671
4826 | 23172.1641 | 4.2558
4827 | 23110.5098 | 4.0457
4828 | 22326.793 | 3.666
4829 | 22252.6133 | 3.6789
4830 | 22175.2344 | 3.58
4831 | 22545.3301 | 3.7182
4832 | 22418.2988 | 3.8417
4833 | 21716.1602 | 3.8792
4834 | 20381.0645 | 3.6867
4835 | 19278.9062 | 3.6738
4836 | 18498.9902 | 3.676
4837 | 19351.6855 | 3.5006
4838 | 19449.5898 | 3.2711
4839 | 18670.2734 | 3.3749
4840 | 17513.4629 | 3.6537
4841 | 16884.9043 | 3.753
4842 | 16859.7773 | 3.7946
4843 | 17010.5352 | 3.5029
4844 | 16960.2832 | 3.276
4845 | 16382.377 | 2.8662
4846 | 15779.3438 | 2.5183
4847 | 15075.8066 | 2.4142
4848 | 14548.1543 | 2.5401
4849 | 14171.2578 | 2.3699
4850 | 13970.2471 | 2.2587
4851 | 13492.8457 | 2.6207
4852 | 13291.8359 | 2.734
4853 | 13015.4473 | 2.7482
4854 | 12764.9814 | 2.7302
4855 | 12739.2568 | 2.7317
4856 | 12864.6875 | 2.7568
4857 | 12916.3418 | 2.8375
4858 | 13292.6357 | 2.9425
4859 | 14687.7852 | 2.8753
4860 | 18014.2617 | 3.1803
4861 | 20161.5273 | 4.0697
4862 | 22438.4238 | 4.705
4863 | 24448.9336 | 5.5177
4864 | 26759.5547 | 6.0906
4865 | 29799.8438 | 6.8147
4866 | 29975.7266 | 7.1843
4867 | 30679.2656 | 7.3981
4868 | 30252.5176 | 7.4908
4869 | 30308.3711 | 7.3609
4870 | 30584.5625 | 7.3687
4871 | 30353.8223 | 7.414
4872 | 32139.5918 | 7.416
4873 | 32264.8223 | 7.4192
4874 | 30038.7812 | 7.2521
4875 | 30392.3496 | 7.1716
4876 | 30175.0137 | 7.1313
4877 | 30140.2871 | 7.1058
4878 | 28806.1895 | 7.0155
4879 | 29539.6543 | 6.724
4880 | 27805.7363 | 6.5187
4881 | 27212.832 | 6.1166
4882 | 26081.7441 | 5.6965
4883 | 24499.7871 | 5.4526
4884 | 26464.8418 | 5.2568
4885 | 26534.8184 | 5.2058
4886 | 26407.9863 | 5.0524
4887 | 26407.7891 | 4.9432
4888 | 26407.7891 | 4.8909
4889 | 25528.3633 | 4.8138
4890 | 23819.7734 | 4.6623
4891 | 22186.5625 | 4.2686
4892 | 21030.75 | 4.0483
4893 | 19699.0547 | 3.6132
4894 | 18342.2305 | 3.2925
4895 | 17739.1992 | 3.2679
4896 | 16910.0312 | 3.1458
4897 | 16306.998 | 2.9855
4898 | 15829.5957 | 2.9917
4899 | 15402.4492 | 3.1858
4900 | 15226.5645 | 3.1805
4901 | 15000.4277 | 3.2322
4902 | 15000.4277 | 3.2068
4903 | 15026.1543 | 3.254
4904 | 15076.0068 | 3.3284
4905 | 15127.6582 | 3.3605
4906 | 15556.0068 | 3.4679
4907 | 16887.3047 | 3.7067
4908 | 20489.5684 | 3.9656
4909 | 22499.8789 | 4.3823
4910 | 24806.9023 | 4.9679
4911 | 28468.9473 | 5.6708
4912 | 29097.707 | 6.3384
4913 | 30629.0117 | 7.0811
4914 | 30202.0645 | 7.3901
4915 | 30629.6113 | 7.4624
4916 | 31508.834 | 7.5156
4917 | 30278.2441 | 7.4216
4918 | 30235.3926 | 7.3868
4919 | 31288.6973 | 7.3914
4920 | 31009.1074 | 7.3906
4921 | 32164.7188 | 7.093
4922 | 32417.3828 | 6.9291
4923 | 31811.3535 | 6.8065
4924 | 30779.7695 | 6.5282
4925 | 31407.9297 | 6.5445
4926 | 30503.3828 | 6.5017
4927 | 29322.4453 | 6.4605
4928 | 27664.1055 | 6.2213
4929 | 27463.4941 | 5.9406
4930 | 25779.6289 | 5.5777
4931 | 26534.0176 | 5.2692
4932 | 26558.5469 | 5.1732
4933 | 26231.9023 | 4.9094
4934 | 26181.6523 | 4.7072
4935 | 26282.1562 | 4.5472
4936 | 25980.6406 | 4.869
4937 | 25478.1133 | 4.8132
4938 | 23920.2793 | 4.5581
4939 | 22337.3184 | 4.3428
4940 | 20628.7285 | 3.9815
4941 | 19648.8027 | 3.6431
4942 | 18518.1152 | 3.359
4943 | 17839.7051 | 3.3625
4944 | 17437.6836 | 3.2331
4945 | 17387.4297 | 3.0227
4946 | 17337.1777 | 3.0177
4947 | 16910.0312 | 3.2664
4948 | 16935.1562 | 3.2896
4949 | 16859.7773 | 3.305
4950 | 18844.7578 | 3.2778
4951 | 18719.125 | 3.2926
4952 | 19020.6406 | 3.4955
4953 | 17085.3867 | 3.5438
4954 | 16266.7959 | 3.4503
4955 | 17443.6699 | 3.6225
4956 | 19303.7422 | 3.9118
4957 | 21059.0918 | 4.2411
4958 | 23396.752 | 4.806
4959 | 27042.4922 | 5.6282
4960 | 28606.5742 | 6.2583
4961 | 27572.5488 | 6.9349
4962 | 28389.8418 | 7.074
4963 | 29010.916 | 7.0979
4964 | 28942.6738 | 7.2902
4965 | 27571.4844 | 7.1747
4966 | 27556.1992 | 7.0802
4967 | 27739.2832 | 6.9989
4968 | 27960.4297 | 6.9682
4969 | 27864.3574 | 6.6328
4970 | 27819.7656 | 6.4813
4971 | 28377.043 | 6.544
4972 | 27406.0078 | 6.3732
4973 | 27935.7793 | 6.3329
4974 | 28321.5156 | 6.2515
4975 | 27669.4844 | 6.2564
4976 | 27649.7773 | 6.2276
4977 | 26025.1348 | 6.1157
4978 | 24688.2148 | 5.677
4979 | 23551.9297 | 5.4472
4980 | 23890.2051 | 5.2517
4981 | 23864.8477 | 5.2768
4982 | 25137.5312 | 5.2548
4983 | 25730.4805 | 5.1512
4984 | 24981.0273 | 5.0778
4985 | 24183.373 | 4.862
4986 | 23129.6758 | 4.7197
4987 | 20121.3906 | 4.4381
4988 | 19260.8418 | 3.9058
4989 | 19334.4727 | 3.6435
4990 | 17934.2715 | 3.5055
4991 | 17410.7559 | 3.3297
4992 | 16845.332 | 3.0594
4993 | 16587.7871 | 3.1953
4994 | 16141.5127 | 3.1736
4995 | 15685.1543 | 3.3262
4996 | 15540.0059 | 3.4046
4997 | 15559.0156 | 3.423
4998 | 15308.6055 | 3.3126
4999 | 15366.9004 | 3.2049
5000 | 15285.9854 | 3.2586
5001 | 14985.5938 | 3.3826
5002 | 15274.374 | 3.4727
5003 | 16717.1953 | 3.5374
5004 | 19436.3672 | 3.711
5005 | 21912.3828 | 4.2114
5006 | 24043.7188 | 4.7529
5007 | 27030.7012 | 5.5914
5008 | 27891.1152 | 6.2029
5009 | 27886.4512 | 6.8435
5010 | 27377.0938 | 7.0454
5011 | 28206.8633 | 7.1084
5012 | 27880.9668 | 7.2131
5013 | 27653.5664 | 7.1755
5014 | 27925.8184 | 7.0435
5015 | 27581.4297 | 7.0097
5016 | 27742.7363 | 6.9862
5017 | 27785.7148 | 6.832
5018 | 27771.4414 | 6.7207
5019 | 27962.2422 | 6.5945
5020 | 27274.7773 | 6.4848
5021 | 27048.3477 | 6.4813
5022 | 26782.3242 | 6.42
5023 | 25297.543 | 6.242
5024 | 22747.793 | 6.0475
5025 | 22321.4355 | 5.9403
5026 | 22187.4258 | 5.6987
5027 | 21455.5078 | 5.2585
5028 | 21536.9414 | 5.1981
5029 | 21809.2461 | 5.2442
5030 | 21794.2559 | 5.0968
5031 | 22070.6465 | 4.9902
5032 | 22199.6348 | 5.1021
5033 | 22615.2891 | 4.9026
5034 | 21483.959 | 4.7195
5035 | 19990.0117 | 4.4449
5036 | 18286.5469 | 3.9098
5037 | 17717.1465 | 3.6967
5038 | 16424.8281 | 3.4835
5039 | 15349.248 | 3.177
5040 | 14745.2695 | 3.0156
5041 | 13980.7627 | 3.0464
5042 | 13388.2373 | 3.0315
5043 | 12893.5508 | 3.326
5044 | 12664.541 | 3.3568
5045 | 12782.8906 | 3.3467
5046 | 12755.1406 | 3.4358
5047 | 12668.1719 | 3.3839
5048 | 12817.2109 | 3.3774
5049 | 12777.7598 | 3.5102
5050 | 13505.8359 | 3.5955
5051 | 14504.8584 | 3.5468
5052 | 17462.998 | 3.7919
5053 | 19810.4414 | 4.3529
5054 | 21610.9492 | 4.9105
5055 | 22844.3926 | 5.5576
5056 | 23751.9199 | 6.2542
5057 | 22181.1289 | 6.8139
5058 | 23053.6758 | 6.657
5059 | 22974.9199 | 6.8701
5060 | 23192.5508 | 6.9033
5061 | 23879.6992 | 6.908
5062 | 23497.7305 | 6.8703
5063 | 23174.3418 | 6.7863
5064 | 23005.5625 | 6.7601
5065 | 22997.4453 | 6.9283
5066 | 23051.457 | 6.4568
5067 | 22964.7402 | 6.2347
5068 | 22412.7715 | 6.0329
5069 | 22093.4238 | 5.8924
5070 | 23240.2266 | 5.8388
5071 | 24148.9844 | 5.5945
5072 | 24241.2812 | 5.3361
5073 | 23875.8789 | 5.1724
5074 | 23814.625 | 5.0914
5075 | 22952.7422 | 4.8418
5076 | 23092.457 | 4.7256
5077 | 22640.9297 | 4.7667
5078 | 22541.5625 | 4.5062
5079 | 22141.9941 | 4.4672
5080 | 21899.5195 | 4.7979
5081 | 20916.2344 | 4.6936
5082 | 19392.0117 | 4.201
5083 | 17834.4297 | 4.0733
5084 | 16865.125 | 3.4849
5085 | 16027.2178 | 3.1576
5086 | 15350.417 | 3.0498
5087 | 14645.1309 | 2.8413
5088 | 13922.584 | 2.5557
5089 | 13211.0674 | 2.5572
5090 | 12780.7725 | 2.5298
5091 | 12368.7725 | 2.7329
5092 | 12085.9922 | 2.7207
5093 | 12007.5078 | 2.7429
5094 | 11872.959 | 2.7388
5095 | 12064.2236 | 2.8008
5096 | 12195.8037 | 2.7569
5097 | 12018.75 | 2.8184
5098 | 11825.6836 | 2.6884
5099 | 11418.918 | 2.6904
5100 | 12879.3936 | 2.6467
5101 | 13579.5732 | 2.8856
5102 | 14090.8906 | 3.0155
5103 | 14654.1748 | 3.5169
5104 | 16659.8164 | 4.0521
5105 | 17714.5234 | 4.3639
5106 | 18938.7578 | 4.2103
5107 | 19840.4746 | 4.2994
5108 | 20448.0312 | 4.4134
5109 | 20273.8438 | 4.5084
5110 | 20101.0742 | 4.4256
5111 | 19710.1484 | 4.4799
5112 | 19600.4609 | 4.2949
5113 | 19402.9277 | 4.4139
5114 | 19927.2227 | 4.4906
5115 | 20402.2734 | 4.6737
5116 | 18905.6855 | 4.6152
5117 | 18954.2109 | 4.317
5118 | 19808.7383 | 4.1774
5119 | 19646.4102 | 4.167
5120 | 19623.9062 | 4.2512
5121 | 19378.1582 | 4.3858
5122 | 19304.2207 | 3.98
5123 | 18876.7461 | 3.671
5124 | 18836.2207 | 3.6812
5125 | 18716.5781 | 3.648
5126 | 18670.2324 | 3.7652
5127 | 18644.418 | 3.6022
5128 | 18289.9688 | 3.6133
5129 | 15345.7754 | 3.6188
5130 | 14033.8477 | 3.5018
5131 | 14016.0781 | 3.4936
5132 | 13944.8369 | 3.3421
5133 | 13459.5508 | 3.0202
5134 | 12812.75 | 3.09
5135 | 12319.1406 | 2.8405
5136 | 11844.7715 | 2.5189
5137 | 11208.3398 | 2.519
5138 | 10814.8438 | 2.538
5139 | 10434.1055 | 2.7151
5140 | 10333.6523 | 2.6777
5141 | 10155.1055 | 2.64
5142 | 9946.7695 | 2.5734
5143 | 9995.3906 | 2.5133
5144 | 9889.1484 | 2.5064
5145 | 9751.9902 | 2.5745
5146 | 9346.3145 | 2.428
5147 | 9482.3047 | 2.3108
5148 | 10554.8848 | 2.3142
5149 | 11548.0957 | 2.5864
5150 | 12191.4453 | 2.4321
5151 | 12517.7314 | 2.6437
5152 | 13053.7422 | 2.9066
5153 | 13953.6797 | 3.0749
5154 | 15240.9434 | 3.2627
5155 | 15965.8164 | 3.2835
5156 | 17306.8398 | 3.214
5157 | 18634.6406 | 3.4948
5158 | 18894.8438 | 3.5074
5159 | 18937.1055 | 3.9536
5160 | 19005.7695 | 4.0636
5161 | 19803.3496 | 4.0914
5162 | 19844.0117 | 3.9905
5163 | 19711.9258 | 3.9221
5164 | 19730.625 | 3.6258
5165 | 19267.6328 | 3.619
5166 | 19389.0547 | 3.5965
5167 | 19496.8125 | 3.6277
5168 | 19238.0117 | 3.6303
5169 | 19148.5586 | 3.7431
5170 | 17260.3867 | 3.5792
5171 | 15801.5654 | 3.3097
5172 | 14989.4922 | 3.3124
5173 | 14932.3223 | 3.2903
5174 | 15023.7637 | 3.2307
5175 | 14695.9434 | 3.3695
5176 | 14727.8906 | 3.4305
5177 | 14775.6367 | 3.3586
5178 | 14600.0049 | 3.4067
5179 | 14941.0156 | 3.0923
5180 | 14906.3945 | 2.8291
5181 | 14113.71 | 2.6356
5182 | 13787.6875 | 2.5295
5183 | 13194.6348 | 2.6163
5184 | 12726.6768 | 2.5366
5185 | 12282.626 | 2.4431
5186 | 11894.6113 | 2.1651
5187 | 11590.9375 | 2.3557
5188 | 11469.875 | 2.3597
5189 | 11065.8008 | 2.4027
5190 | 11159.1055 | 2.4314
5191 | 11036.6094 | 2.4526
5192 | 11251.707 | 2.4646
5193 | 11152.957 | 2.5323
5194 | 11602.4961 | 2.6004
5195 | 12755.2969 | 2.8973
5196 | 16594.5859 | 3.0949
5197 | 19124.5664 | 3.7665
5198 | 20745.877 | 4.4557
5199 | 22159.3828 | 5.254
5200 | 25071.543 | 5.6737
5201 | 26844.4297 | 6.3811
5202 | 27373.3457 | 6.4973
5203 | 28487.5059 | 6.7561
5204 | 30019.5586 | 7.0321
5205 | 29177.7402 | 7.0655
5206 | 29452.002 | 6.8015
5207 | 29684.1914 | 6.8119
5208 | 30353.623 | 6.9079
5209 | 29840.9199 | 6.9572
5210 | 30682.2148 | 6.7419
5211 | 31180.5293 | 6.7109
5212 | 30857.7715 | 6.6794
5213 | 29265.1504 | 6.6709
5214 | 28710.4219 | 6.4765
5215 | 29218.1387 | 6.3034
5216 | 25487.7871 | 6.2057
5217 | 25618.8398 | 5.9398
5218 | 26472.2832 | 5.3872
5219 | 26412.1387 | 4.9083
5220 | 26272.6328 | 4.7197
5221 | 26540.293 | 4.5724
5222 | 26174.3574 | 4.4221
5223 | 26010.1152 | 4.3993
5224 | 25413.9531 | 4.4882
5225 | 24310.4492 | 4.3917
5226 | 22105.6992 | 4.2565
5227 | 20870.877 | 3.8996
5228 | 19407.9375 | 3.6664
5229 | 18582.4727 | 3.6259
5230 | 17768.9355 | 3.3212
5231 | 16992.1562 | 3.1179
5232 | 16098.5459 | 3.0035
5233 | 15648.5459 | 3.0831
5234 | 15144.1123 | 3.0413
5235 | 14667.4492 | 3.1702
5236 | 14203.0811 | 3.2062
5237 | 13795.2178 | 3.286
5238 | 13992.1094 | 3.2528
5239 | 14219.5615 | 3.2696
5240 | 14339.0361 | 3.4299
5241 | 14401.1738 | 3.5418
5242 | 14788.9316 | 3.5442
5243 | 15456.1543 | 3.6697
5244 | 18566.2305 | 3.8915
5245 | 20746.4355 | 4.4166
5246 | 22084.0039 | 4.8696
5247 | 23993.6367 | 5.7121
5248 | 26923.3984 | 6.2417
5249 | 26796.6836 | 6.7436
5250 | 28359.0312 | 6.8214
5251 | 29006.0859 | 6.7698
5252 | 29622.3906 | 6.6407
5253 | 30428.0137 | 6.7103
5254 | 30017.5078 | 6.7008
5255 | 30069.1289 | 6.6243
5256 | 30140.75 | 6.5903
5257 | 29949.2656 | 6.3023
5258 | 29278.4336 | 6.1804
5259 | 28666.002 | 6.268
5260 | 29107.9922 | 6.1204
5261 | 28875.2227 | 6.1159
5262 | 28346.9805 | 5.9516
5263 | 27511.8105 | 5.7625
5264 | 27364.1172 | 5.8251
5265 | 27367.6523 | 5.5704
5266 | 28430.4766 | 5.282
5267 | 27248.2734 | 4.8373
5268 | 26033.3359 | 4.6419
5269 | 25925.084 | 4.6288
5270 | 26191.3574 | 4.5089
5271 | 26139.5879 | 4.285
5272 | 25732.3047 | 4.3559
5273 | 25899.5664 | 4.4891
5274 | 25650.7891 | 4.3543
5275 | 23086.8887 | 4.0534
5276 | 20758.0254 | 3.8743
5277 | 19758.4434 | 3.5983
5278 | 18783.7812 | 3.4137
5279 | 17995.7148 | 3.0225
5280 | 17120.1055 | 2.8508
5281 | 16310.8848 | 3.0019
5282 | 15409.8818 | 2.8942
5283 | 14880.0479 | 3.097
5284 | 14794.3945 | 3.1145
5285 | 14446.1211 | 3.1296
5286 | 14580.5107 | 3.1037
5287 | 14447.6152 | 3.09
5288 | 14653.2695 | 3.1146
5289 | 14413.8262 | 3.2414
5290 | 14733.1221 | 3.4382
5291 | 15914.7656 | 3.599
5292 | 20966.2012 | 3.7228
5293 | 23693.0781 | 4.3187
5294 | 25098.4922 | 4.8304
5295 | 26978.1348 | 5.4139
5296 | 27634.7363 | 5.9632
5297 | 28767.4844 | 6.4988
5298 | 29838.2227 | 6.6324
5299 | 30192.75 | 6.4314
5300 | 30341.625 | 6.5691
5301 | 33187.0469 | 6.5994
5302 | 33120.0273 | 6.4403
5303 | 31912.5527 | 6.353
5304 | 31607.6777 | 6.2298
5305 | 32412.1426 | 5.9994
5306 | 33846.207 | 5.8555
5307 | 32424.4902 | 5.6806
5308 | 31392.7109 | 5.8907
5309 | 31422.5117 | 5.8021
5310 | 30076.4023 | 5.7395
5311 | 30337.9609 | 5.6187
5312 | 27555.3789 | 5.4045
5313 | 27246.4512 | 5.339
5314 | 26849.127 | 5.1194
5315 | 26277.6719 | 4.7932
5316 | 26079.2715 | 4.7635
5317 | 25816.5137 | 4.7769
5318 | 25818.168 | 4.6203
5319 | 25027.0918 | 4.389
5320 | 24952.082 | 4.4692
5321 | 23871.9004 | 4.589
5322 | 21979.9297 | 4.5038
5323 | 20912.7188 | 4.1209
5324 | 19498.2852 | 3.765
5325 | 18196.2207 | 3.5734
5326 | 17503.9023 | 3.2671
5327 | 16751.7461 | 3.2039
5328 | 15688.4375 | 2.9119
5329 | 15072.0703 | 2.7999
5330 | 14546.3438 | 2.7811
5331 | 14292.0703 | 2.8643
5332 | 14319.9316 | 2.8961
5333 | 13558.7021 | 2.8834
5334 | 13540.3125 | 2.8456
5335 | 13702.8789 | 2.8586
5336 | 14004.5195 | 2.9692
5337 | 13818.1514 | 3.0886
5338 | 14231.0889 | 2.9827
5339 | 14599.8145 | 3.1605
5340 | 18516.7988 | 3.3815
5341 | 20195.1602 | 3.9757
5342 | 23034.709 | 4.7042
5343 | 25181.8691 | 5.5134
5344 | 28094.6621 | 6.0823
5345 | 28344.5254 | 6.569
5346 | 28748.1367 | 6.6759
5347 | 28412.8008 | 6.586
5348 | 30544.959 | 6.6923
5349 | 31685.5938 | 6.6577
5350 | 31591.4785 | 6.52
5351 | 30370.8047 | 6.5047
5352 | 31417.8789 | 6.4827
5353 | 29440.0547 | 6.1935
5354 | 29760.4121 | 5.9948
5355 | 30990.9512 | 6.1262
5356 | 29929.0762 | 5.8949
5357 | 30010.6133 | 5.923
5358 | 28130.2539 | 5.8842
5359 | 28300.2949 | 5.8638
5360 | 27176.2109 | 5.746
5361 | 26866.9473 | 5.4703
5362 | 26593.1777 | 5.1668
5363 | 25287.8496 | 5.0596
5364 | 24390.4492 | 5.0393
5365 | 24701.1855 | 4.9541
5366 | 24504.4277 | 4.78
5367 | 24470.5645 | 4.8337
5368 | 23766.5215 | 4.7764
5369 | 22910.2051 | 4.7282
5370 | 21565.6348 | 4.4714
5371 | 20223.043 | 4.0824
5372 | 18714.2422 | 3.6894
5373 | 17268.8906 | 3.4764
5374 | 16525.9766 | 3.2262
5375 | 16028.9658 | 3.0665
5376 | 15528.1133 | 2.9114
5377 | 15040.4512 | 3.0315
5378 | 14411.0586 | 3.0605
5379 | 14207.4785 | 3.1977
5380 | 13904.7207 | 3.2512
5381 | 13691.4355 | 3.2599
5382 | 13657.1094 | 3.2968
5383 | 13715.0352 | 3.2789
5384 | 13566.8145 | 3.218
5385 | 13465.6875 | 3.3872
5386 | 13771.9414 | 3.3749
5387 | 14845.0889 | 3.2472
5388 | 17583.5254 | 3.3665
5389 | 19592.3047 | 4.0636
5390 | 21690.1699 | 4.6207
5391 | 23522.6992 | 5.4482
5392 | 25805.5234 | 5.9705
5393 | 27015.6504 | 6.4298
5394 | 27058.6719 | 6.5371
5395 | 28439.8633 | 6.4825
5396 | 27648.5781 | 6.5377
5397 | 28002.7051 | 6.5162
5398 | 27404.7578 | 6.3528
5399 | 27474.6719 | 6.3312
5400 | 27369.6309 | 6.2545
5401 | 28338.3789 | 6.2093
5402 | 27687.5371 | 5.9295
5403 | 27480.0117 | 5.7454
5404 | 26030.9453 | 5.602
5405 | 26393.3262 | 5.381
5406 | 26686.5566 | 5.1118
5407 | 25906.6074 | 5.1996
5408 | 25711.7988 | 5.1753
5409 | 25824.8281 | 5.0147
5410 | 24823.7109 | 4.726
5411 | 23332.8906 | 4.7436
5412 | 23400.3125 | 4.5503
5413 | 22686.0996 | 4.5379
5414 | 22593.7422 | 4.3058
5415 | 21886.498 | 4.3516
5416 | 21258.0039 | 4.3758
5417 | 20765.2441 | 4.3536
5418 | 19583.5273 | 4.136
5419 | 18197.209 | 3.9641
5420 | 17035.9023 | 3.3848
5421 | 16432.1133 | 3.2939
5422 | 15159.29 | 3.2003
5423 | 14474.3945 | 3.0272
5424 | 14136.3516 | 2.657
5425 | 13694.2158 | 2.6303
5426 | 13233.4355 | 2.6594
5427 | 12996.3086 | 2.8013
5428 | 12813.2051 | 2.8091
5429 | 11803.2051 | 2.8795
5430 | 12494.3535 | 3.0232
5431 | 12477.3584 | 2.9069
5432 | 12125.7441 | 2.8604
5433 | 12063.2041 | 2.9212
5434 | 11730.6445 | 2.9278
5435 | 11975.9297 | 2.944
5436 | 13033.3086 | 2.6784
5437 | 14030.1406 | 2.5909
5438 | 14853.3203 | 2.8435
5439 | 15533.0586 | 3.2418
5440 | 17162.2598 | 3.4426
5441 | 18346.4414 | 3.8777
5442 | 19628.834 | 4.0562
5443 | 20148.3789 | 3.9394
5444 | 21011.4121 | 4.0934
5445 | 21159.541 | 4.2124
5446 | 21146.6445 | 4.2309
5447 | 20485.9062 | 4.1171
5448 | 20522.3711 | 4.0879
5449 | 20251.9922 | 4.0814
5450 | 20698.5391 | 3.9915
5451 | 20234.8438 | 4.0753
5452 | 19583.2461 | 4.0784
5453 | 19319.125 | 3.8558
5454 | 19463.6211 | 3.8308
5455 | 19341.4766 | 3.7003
5456 | 19419.5273 | 3.7074
5457 | 19237.4336 | 3.7657
5458 | 19042.6328 | 3.6505
5459 | 18817.6953 | 3.5252
5460 | 18725.8535 | 3.425
5461 | 18718.0527 | 3.6371
5462 | 18485.3574 | 3.5378
5463 | 17998.0117 | 3.4373
5464 | 16745.4805 | 3.2136
5465 | 15089.3125 | 3.518
5466 | 14450.2578 | 3.4007
5467 | 14637.5215 | 3.0618
5468 | 14068.4893 | 3.0869
5469 | 13518.9521 | 2.9612
5470 | 13016.1729 | 2.8689
5471 | 12232.4023 | 2.6936
5472 | 11974.4678 | 2.2828
5473 | 11448.8145 | 2.265
5474 | 11077.4219 | 2.4347
5475 | 10785.9062 | 2.3499
5476 | 10611.4746 | 2.3227
5477 | 10462.5898 | 2.3074
5478 | 10125 | 2.2389
5479 | 9931.9883 | 2.2373
5480 | 10001.9375 | 2.2248
5481 | 9861.0098 | 2.2652
5482 | 9580 | 2.1392
5483 | 9734.9473 | 2.1183
5484 | 10560.9902 | 2.0396
5485 | 11343.5273 | 2.1599
5486 | 11811.3496 | 2.4855
5487 | 12451.916 | 2.3411
5488 | 13826.2871 | 2.3565
5489 | 14577.8477 | 2.5512
5490 | 15911.1094 | 2.9532
5491 | 16533.9863 | 3.269
5492 | 17882.6074 | 3.4405
5493 | 19333.6211 | 3.5367
5494 | 19958.3066 | 3.5571
5495 | 19776.8848 | 3.5646
5496 | 20207.6758 | 3.8977
5497 | 20173.2129 | 3.9067
5498 | 20426.3828 | 3.6105
5499 | 20236.3281 | 3.4834
5500 | 19862.7285 | 3.6045
5501 | 19530.2227 | 3.5255
5502 | 19564.2422 | 3.5181
5503 | 19224.2539 | 3.4747
5504 | 19237.834 | 3.512
5505 | 18762.6406 | 3.646
5506 | 17490.6719 | 3.5183
5507 | 16228.6289 | 3.3315
5508 | 15314.2178 | 3.3273
5509 | 14875.2686 | 3.1249
5510 | 14934.4707 | 3.0555
5511 | 14888.7734 | 3.0968
5512 | 14972.4795 | 3.1204
5513 | 14648.2578 | 3.1723
5514 | 14420.627 | 3.1284
5515 | 14559.8896 | 3.0377
5516 | 14830.6484 | 2.9459
5517 | 14020.0986 | 2.5584
5518 | 13764.8359 | 2.6738
5519 | 13448.8154 | 2.5541
5520 | 12831.7812 | 2.331
5521 | 12282.4023 | 2.1538
5522 | 12082.0566 | 2.1032
5523 | 11788.6768 | 2.3032
5524 | 11546.9395 | 2.3068
5525 | 11157.3711 | 2.304
5526 | 11311.8867 | 2.2824
5527 | 11257.4453 | 2.2614
5528 | 11499.3809 | 2.2727
5529 | 11544.8203 | 2.3256
5530 | 11765.834 | 2.3408
5531 | 12649.71 | 2.6168
5532 | 16233.2109 | 2.7994
5533 | 18345.7383 | 3.6649
5534 | 20428.7812 | 4.38
5535 | 22402.541 | 4.9818
5536 | 27566.084 | 5.5897
5537 | 27623.9492 | 6.1534
5538 | 27559.3418 | 6.1907
5539 | 27809.3477 | 6.3374
5540 | 29481.0117 | 6.3476
5541 | 28651.3477 | 6.3761
5542 | 27561.5059 | 6.4034
5543 | 27345.9238 | 6.3307
5544 | 28424.832 | 6.3409
5545 | 28980.8418 | 6.2415
5546 | 28149.1875 | 6.1552
5547 | 27032.3867 | 6.2449
5548 | 27238.4414 | 5.99
5549 | 28360.3691 | 6.0411
5550 | 27711.0723 | 5.9282
5551 | 26014.9023 | 5.932
5552 | 25695.3223 | 5.8805
5553 | 25149.4375 | 5.6988
5554 | 24084.7109 | 5.3495
5555 | 23619.1094 | 5.0254
5556 | 23327.0977 | 4.9179
5557 | 23209.4258 | 4.9194
5558 | 23445.7207 | 4.6636
5559 | 23143.584 | 4.5347
5560 | 22787.3086 | 4.5275
5561 | 21849.498 | 4.5016
5562 | 20839.8223 | 4.3855
5563 | 19565.2539 | 4.076
5564 | 18395.3047 | 3.769
5565 | 16935.6074 | 3.6121
5566 | 16171.0586 | 3.3257
5567 | 15328.5547 | 3.1004
5568 | 14685.2402 | 3.1331
5569 | 14087.2676 | 3.1518
5570 | 13752.4473 | 3.1141
5571 | 13640.6777 | 3.3486
5572 | 13384.4023 | 3.3922
5573 | 13417.2988 | 3.3673
5574 | 13506.0332 | 3.3107
5575 | 13368.0566 | 3.2721
5576 | 13634.4238 | 3.2554
5577 | 13512.4238 | 3.3464
5578 | 13945.3203 | 3.3565
5579 | 14515.1621 | 3.4304
5580 | 16965.207 | 3.778
5581 | 19005.0742 | 4.2469
5582 | 20857.6836 | 5.0225
5583 | 22423.7285 | 5.549
5584 | 23517.4668 | 6.0517
5585 | 24864.4277 | 6.6602
5586 | 26391.5137 | 6.8461
5587 | 27864.9902 | 6.8498
5588 | 28560.832 | 6.7471
5589 | 29587.4121 | 6.7214
5590 | 29117.4434 | 6.6556
5591 | 29399.2012 | 6.7559
5592 | 29539.8867 | 6.7448
5593 | 29683.0527 | 6.798
5594 | 28789.4531 | 6.5487
5595 | 28586.6426 | 6.5431
5596 | 27810.3574 | 6.3219
5597 | 27622.3145 | 6.3272
5598 | 27181.5449 | 6.1114
5599 | 28350.252 | 6.0762
5600 | 26388.168 | 5.8826
5601 | 25965.7344 | 5.6571
5602 | 25579.2285 | 5.4122
5603 | 24496.9102 | 5.1416
5604 | 24739.9219 | 5.0005
5605 | 25021.1855 | 4.9847
5606 | 24374.6582 | 4.7616
5607 | 23960.6602 | 4.6827
5608 | 23535.3516 | 4.7008
5609 | 23024.4785 | 4.6204
5610 | 22164.4141 | 4.4406
5611 | 20558.6953 | 4.2531
5612 | 18920.6094 | 4.0139
5613 | 17923.4199 | 3.4054
5614 | 17165.3984 | 3.1078
5615 | 16193.334 | 3.0117
5616 | 15387.9766 | 3.0537
5617 | 14917.376 | 3.2114
5618 | 14714.3652 | 3.2642
5619 | 15100.6289 | 3.4494
5620 | 13954.7734 | 3.5048
5621 | 13257.7363 | 3.465
5622 | 13590.9746 | 3.431
5623 | 13584.9512 | 3.4386
5624 | 13634.3311 | 3.3839
5625 | 13633.9395 | 3.261
5626 | 14275.1094 | 3.2954
5627 | 15105.7734 | 3.7101
5628 | 17962.7988 | 3.7964
5629 | 20217.6855 | 4.2865
5630 | 21694.3496 | 4.882
5631 | 23103.8262 | 5.2837
5632 | 24618.4062 | 5.9714
5633 | 25664.4492 | 6.5245
5634 | 27361.1035 | 6.7328
5635 | 28831.9062 | 6.7367
5636 | 29063.2324 | 6.8146
5637 | 29311.7383 | 7.0396
5638 | 29628.1484 | 6.9309
5639 | 29604.4336 | 6.7826
5640 | 28904.7695 | 6.7441
5641 | 28580.7363 | 6.5645
5642 | 27438.3789 | 6.5816
5643 | 27580.5469 | 6.6547
5644 | 26952.9238 | 6.4147
5645 | 27587.5254 | 6.3413
5646 | 26982.9355 | 6.3305
5647 | 26591.4746 | 6.2417
5648 | 26362.9355 | 5.9385
5649 | 25510.082 | 5.7984
5650 | 24913.1016 | 5.5294
5651 | 23998.1836 | 5.1037
5652 | 24036.6055 | 4.9794
5653 | 24673.3594 | 4.9513
5654 | 24955.209 | 4.968
5655 | 23890.6777 | 4.6762
5656 | 22942.2051 | 4.4765
5657 | 22734.2988 | 4.6709
5658 | 21986.2539 | 4.6486
5659 | 20365.918 | 4.3079
5660 | 18661.6934 | 4.0737
5661 | 17758.0195 | 3.5904
5662 | 16877.3555 | 3.3063
5663 | 16114.46 | 3.2721
5664 | 15306.6406 | 3.1706
5665 | 14834.207 | 3.1851
5666 | 14287.9629 | 3.1971
5667 | 13518.9082 | 3.4513
5668 | 13694.4248 | 3.4578
5669 | 13958.1934 | 3.4649
5670 | 13501.666 | 3.3483
5671 | 13363.6445 | 3.3111
5672 | 13753.0664 | 3.3715
5673 | 13587.7812 | 3.4401
5674 | 14125.3203 | 3.4133
5675 | 14569.8906 | 3.4663
5676 | 17030.8281 | 3.7622
5677 | 19248.7148 | 4.3383
5678 | 20892.8867 | 5.087
5679 | 22897.9199 | 5.6368
5680 | 26435.2285 | 6.0923
5681 | 26748.207 | 6.8006
5682 | 27769.7773 | 7.047
5683 | 27421.0195 | 7.1547
5684 | 27087.6934 | 7.0448
5685 | 28532.1055 | 7.1557
5686 | 28949.7695 | 7.1664
5687 | 29122.6426 | 6.9083
5688 | 29184.4102 | 6.8412
5689 | 28708.8203 | 6.7598
5690 | 29084.3691 | 6.5483
5691 | 28827.3789 | 6.4801
5692 | 28883.6328 | 6.2572
5693 | 28167.4512 | 6.2024
5694 | 27965.5664 | 6.2844
5695 | 28407.4727 | 6.3376
5696 | 26757.3652 | 6.1409
5697 | 27893.9355 | 5.8567
5698 | 27572.7891 | 5.5345
5699 | 26744.8809 | 5.1172
5700 | 26806.5137 | 5.0276
5701 | 26549.7871 | 4.9459
5702 | 25654.8398 | 4.7912
5703 | 23522.8477 | 4.6018
5704 | 23121.0781 | 4.8063
5705 | 22985.6992 | 4.6404
5706 | 21868.0234 | 4.4602
5707 | 19902.2852 | 4.0521
5708 | 18262.5684 | 3.8115
5709 | 17485.3984 | 3.7342
5710 | 16535.1035 | 3.5297
5711 | 16141.8398 | 3.31
5712 | 15404.8496 | 3.0437
5713 | 14869.0049 | 3.0049
5714 | 14426.0723 | 2.9814
5715 | 13409.2227 | 3.2051
5716 | 13304.3086 | 3.2826
5717 | 13351.4141 | 3.273
5718 | 13505.5508 | 3.2481
5719 | 13249.6445 | 3.2707
5720 | 13273.0459 | 3.3695
5721 | 13444.9297 | 3.4495
5722 | 14007.2041 | 3.3362
5723 | 14314.8379 | 3.645
5724 | 16899.8809 | 3.8472
5725 | 18818.7051 | 4.2231
5726 | 21415.75 | 4.7418
5727 | 24552.3516 | 5.1618
5728 | 26292.377 | 5.7783
5729 | 27371.4316 | 6.3504
5730 | 28677.8848 | 6.7163
5731 | 28432.2539 | 6.6111
5732 | 27799.5898 | 6.6454
5733 | 28524.7578 | 6.5696
5734 | 28681.1055 | 6.6378
5735 | 27570.041 | 6.6175
5736 | 26969.9141 | 6.5181
5737 | 27620.8301 | 6.4748
5738 | 27579.8203 | 6.1279
5739 | 26290.9961 | 5.903
5740 | 25233.0703 | 5.6684
5741 | 24656.7969 | 5.4963
5742 | 25175.5215 | 5.3548
5743 | 24708.0391 | 5.1024
5744 | 24703.7852 | 5.043
5745 | 24604.7734 | 5.1295
5746 | 24312.2695 | 4.7623
5747 | 23825.4883 | 4.5794
5748 | 23806.8672 | 4.5465
5749 | 23180.9727 | 4.4629
5750 | 22844.8145 | 4.4142
5751 | 22386.3086 | 4.2239
5752 | 21892.7598 | 4.0859
5753 | 21177.7285 | 3.9698
5754 | 19680.5176 | 3.8497
5755 | 18051.5566 | 3.6538
5756 | 16169.9531 | 3.5302
5757 | 15502.5312 | 3.1988
5758 | 14470.4688 | 2.967
5759 | 13813.6152 | 2.7419
5760 | 13171.9111 | 2.5657
5761 | 12636.6973 | 2.6229
5762 | 12087.0449 | 2.6664
5763 | 11521.0254 | 3.1183
5764 | 11234.8145 | 3.0568
5765 | 11368.9375 | 3.0319
5766 | 11251.2852 | 2.9841
5767 | 11068.3906 | 2.9206
5768 | 10942.2969 | 2.8981
5769 | 10787.7695 | 2.952
5770 | 10670 | 2.8931
5771 | 10750.0215 | 2.8644
5772 | 11893.1367 | 2.8162
5773 | 12542.7715 | 2.6859
5774 | 13402.3828 | 2.8668
5775 | 14220.5625 | 3.589
5776 | 15980.8398 | 4.0669
5777 | 17163.8281 | 4.1766
5778 | 18338.7988 | 4.3887
5779 | 18946.3789 | 4.4832
5780 | 19424.9902 | 4.6967
5781 | 19142.0742 | 4.8366
5782 | 19225.4434 | 4.7896
5783 | 19003.5898 | 4.6286
5784 | 19256.2852 | 4.6156
5785 | 19168.2207 | 4.6543
5786 | 19818.4531 | 4.6044
5787 | 19369.8945 | 4.4758
5788 | 19057.8203 | 4.2583
5789 | 18880.2422 | 4.3296
5790 | 18555.4199 | 4.4786
5791 | 18195.3145 | 4.4338
5792 | 18279.9785 | 4.0416
5793 | 18186 | 4.0428
5794 | 18101.4414 | 3.7458
5795 | 17833.377 | 3.6469
5796 | 17907.8418 | 3.4394
5797 | 17539.0293 | 3.4258
5798 | 17419.6816 | 3.3092
5799 | 17114.0449 | 3.3975
5800 | 15534.915 | 3.4457
5801 | 14263.3418 | 3.5349
5802 | 13562.5625 | 3.5838
5803 | 13951.2031 | 3.3403
5804 | 13592.8164 | 3.1573
5805 | 12967.6445 | 2.892
5806 | 12328.1074 | 2.8302
5807 | 11548.8223 | 2.7541
5808 | 11079.168 | 2.5626
5809 | 10613.832 | 2.6127
5810 | 10245.2754 | 2.6166
5811 | 10002.7578 | 2.758
5812 | 9843.8398 | 2.6663
5813 | 9644.4609 | 2.5549
5814 | 9495.7051 | 2.2588
5815 | 9389.1992 | 2.2575
5816 | 9359.082 | 2.2524
5817 | 9521.082 | 2.3291
5818 | 9453.082 | 2.1466
5819 | 8865.0293 | 2.2141
5820 | 9177.1875 | 2.1887
5821 | 9711.4102 | 2.3244
5822 | 10287.4414 | 2.4011
5823 | 10608.3066 | 2.684
5824 | 10157.3066 | 2.9095
5825 | 10555.707 | 3.0064
5826 | 13665.8457 | 3.4198
5827 | 14172.1426 | 3.7183
5828 | 15239.4893 | 3.5638
5829 | 16334.9766 | 3.6795
5830 | 16864.3984 | 3.9087
5831 | 17062.4922 | 3.9002
5832 | 17464.3984 | 4.0491
5833 | 17858.2422 | 4.0918
5834 | 17817.6406 | 4.1601
5835 | 17525.7031 | 3.8699
5836 | 17358.5898 | 3.849
5837 | 17516.9258 | 3.8972
5838 | 17363.7344 | 3.8088
5839 | 17344.8945 | 3.7987
5840 | 17200.5762 | 3.8126
5841 | 16837.0293 | 3.9384
5842 | 15462.0488 | 3.6405
5843 | 14614.2578 | 3.2135
5844 | 13744.7422 | 3.2075
5845 | 13187.0244 | 2.8978
5846 | 13263.9219 | 2.7274
5847 | 13301.3516 | 2.7805
5848 | 13102.8848 | 2.9009
5849 | 12882.9668 | 2.8914
5850 | 13218.8145 | 3.1215
5851 | 13204.0352 | 3.1531
5852 | 13001.5293 | 2.8238
5853 | 12485.9922 | 2.5505
5854 | 11867.2109 | 2.3641
5855 | 11262.1797 | 2.4093
5856 | 10691.6973 | 2.4905
5857 | 10264.6133 | 2.4684
5858 | 10053.1699 | 2.4461
5859 | 9758.918 | 2.556
5860 | 9716.918 | 2.5261
5861 | 9445.3262 | 2.2168
5862 | 9412.4629 | 2.2218
5863 | 9352.4414 | 2.2541
5864 | 9506.6934 | 2.2897
5865 | 9555.7363 | 2.3992
5866 | 9983.8633 | 2.2854
5867 | 11133.0645 | 2.4456
5868 | 14090.373 | 2.5094
5869 | 15948.9766 | 2.9396
5870 | 17892.4512 | 3.0682
5871 | 19440.8633 | 3.1524
5872 | 21932.0664 | 3.601
5873 | 22451.0781 | 3.781
5874 | 23952.418 | 3.817
5875 | 24760.3223 | 3.9476
5876 | 24925.5332 | 4.1426
5877 | 25394.3984 | 4.2243
5878 | 25992.375 | 3.9363
5879 | 25441.8926 | 3.9921
5880 | 25894.9141 | 3.7649
5881 | 26284.4414 | 3.9354
5882 | 25607.7969 | 4.0392
5883 | 25739.5859 | 4.0846
5884 | 25203.2383 | 3.8967
5885 | 25669.5977 | 4.0407
5886 | 25928.2383 | 3.9531
5887 | 24351.2793 | 3.8942
5888 | 24463.5586 | 3.737
5889 | 24553.9961 | 3.764
5890 | 23837.8066 | 3.667
5891 | 22254.0664 | 3.6068
5892 | 22592.2031 | 3.6371
5893 | 22166.2363 | 3.7242
5894 | 21886.2891 | 3.5862
5895 | 21401.3066 | 3.4737
5896 | 21810.5488 | 3.2719
5897 | 20892.5059 | 3.3242
5898 | 20172.6719 | 3.2943
5899 | 18833.6191 | 3.1102
5900 | 16155.2148 | 3.0334
5901 | 14901.6348 | 2.8388
5902 | 14229.1074 | 2.689
5903 | 13234.4219 | 2.5518
5904 | 12490.7695 | 2.4617
5905 | 12108.7266 | 2.489
5906 | 12089.4844 | 2.4414
5907 | 11878.3789 | 2.5903
5908 | 11744.4941 | 2.5589
5909 | 11646.2207 | 2.5742
5910 | 11310.1992 | 2.3241
5911 | 11397.7588 | 2.2458
5912 | 11768.083 | 2.3446
5913 | 11915.8301 | 2.4718
5914 | 12622.2227 | 2.6233
5915 | 14841.0039 | 2.6465
5916 | 17464.5215 | 2.7452
5917 | 18840.1016 | 3.5018
5918 | 21457.8848 | 4.1957
5919 | 22803.4434 | 4.9994
5920 | 23975.9277 | 5.5444
5921 | 25123.1191 | 5.9553
5922 | 26138.5605 | 6.174
5923 | 27129.8477 | 6.2975
5924 | 27937.5215 | 6.5843
5925 | 27967.6367 | 6.462
5926 | 28916.9648 | 6.3568
5927 | 28048.3008 | 6.2512
5928 | 25833.2969 | 6.1793
5929 | 25917.3301 | 6.2582
5930 | 26237.668 | 6.0203
5931 | 25723.793 | 5.9208
5932 | 25323.7402 | 5.8411
5933 | 25511.0137 | 5.8898
5934 | 25055.3613 | 5.8215
5935 | 24731.0645 | 5.7659
5936 | 24258.2012 | 5.7227
5937 | 24631.875 | 5.3078
5938 | 23721.4551 | 4.9545
5939 | 23319.9902 | 4.8314
5940 | 22756.1582 | 4.5716
5941 | 22937.2637 | 4.4742
5942 | 22412.3477 | 4.2966
5943 | 21789.2207 | 4.182
5944 | 22170.2539 | 4.1009
5945 | 21416.5566 | 4.2766
5946 | 20536.9023 | 4.2499
5947 | 18326.6582 | 4.029
5948 | 16948.5723 | 3.5645
5949 | 15617.0137 | 3.4304
5950 | 14660.6953 | 3.2678
5951 | 13863.2529 | 3.0571
5952 | 12979.8311 | 2.9272
5953 | 12486.3789 | 2.9482
5954 | 12027.209 | 2.9116
5955 | 11689.0508 | 3.2533
5956 | 11673.9258 | 3.2322
5957 | 11366.3574 | 3.1697
5958 | 11399.2383 | 3.1418
5959 | 11490.2168 | 3.1399
5960 | 11841.6914 | 3.1194
5961 | 11758.7129 | 3.1946
5962 | 12449.377 | 3.2383
5963 | 13235.5352 | 3.35
5964 | 16000.0117 | 3.636
5965 | 17764.834 | 3.9409
5966 | 19902.207 | 4.5559
5967 | 22037.0605 | 5.1478
5968 | 24410.4961 | 5.6582
5969 | 25878.5625 | 6.1432
5970 | 26568.498 | 6.204
5971 | 27975.666 | 6.2171
5972 | 27564.3809 | 6.1419
5973 | 26726.8301 | 6.2331
5974 | 26484.1152 | 6.4045
5975 | 27444.7676 | 6.4938
5976 | 26707.6191 | 6.3898
5977 | 26839.8516 | 6.0567
5978 | 27495.9883 | 6.0788
5979 | 27121.0293 | 5.9975
5980 | 27256.5059 | 5.9273
5981 | 26590.6523 | 5.9019
5982 | 27122.3262 | 5.7719
5983 | 26777.5898 | 5.7189
5984 | 24859.7109 | 5.5228
5985 | 25634.377 | 5.3992
5986 | 23761.8359 | 5.2638
5987 | 22433.709 | 5.0991
5988 | 22773.0469 | 4.8602
5989 | 23092.457 | 4.6135
5990 | 23631.8477 | 4.4365
5991 | 22032.2969 | 4.2737
5992 | 21838.7832 | 4.1116
5993 | 21393.1289 | 4.2768
5994 | 20419.4551 | 4.2839
5995 | 18724.8633 | 4.0173
5996 | 16576.3652 | 3.6614
5997 | 15471.1973 | 3.4705
5998 | 14532.1211 | 3.4733
5999 | 13568.0781 | 3.0622
6000 | 12733.9902 | 2.9208
6001 | 12257.6426 | 3.0409
6002 | 11993.6934 | 2.8795
6003 | 11793.7383 | 3.0805
6004 | 12436.2363 | 2.877
6005 | 12713.8184 | 2.7949
6006 | 11135.043 | 2.7797
6007 | 11478.0859 | 2.9763
6008 | 12023.7402 | 3.1567
6009 | 13286.0566 | 3.2102
6010 | 13860.8359 | 3.0784
6011 | 14996.6484 | 3.0519
6012 | 17982.1777 | 3.4175
6013 | 19330.2949 | 3.7902
6014 | 21130.1602 | 4.3799
6015 | 23273.6172 | 4.7785
6016 | 26736.375 | 5.4521
6017 | 25392.5352 | 5.8773
6018 | 24928.9961 | 6.0094
6019 | 25464.4805 | 5.7914
6020 | 26062.25 | 5.9277
6021 | 26109.0078 | 5.89
6022 | 26717.4414 | 5.8771
6023 | 26601.377 | 5.9511
6024 | 27116.7988 | 5.8503
6025 | 26096.5996 | 5.9494
6026 | 27041.4297 | 5.9503
6027 | 26329.5781 | 5.8958
6028 | 26031.0918 | 5.8994
6029 | 26448.7656 | 5.8118
6030 | 26243.8809 | 5.8089
6031 | 25789.9238 | 5.6891
6032 | 23937.543 | 5.521
6033 | 23519.3105 | 5.2107
6034 | 22789.5 | 4.8261
6035 | 22153.2988 | 4.5146
6036 | 22447.1621 | 4.4473
6037 | 22330.5625 | 4.4037
6038 | 22268.2969 | 4.2488
6039 | 21982.0234 | 4.182
6040 | 21586.2344 | 4.1761
6041 | 21025.6562 | 4.0875
6042 | 19792.0117 | 4.1071
6043 | 17952.0625 | 3.9242
6044 | 16304.3438 | 3.6978
6045 | 15292.6689 | 3.4603
6046 | 14354.1211 | 3.2615
6047 | 13513.7812 | 3.1694
6048 | 12853.1406 | 3.0278
6049 | 12489.4355 | 2.9858
6050 | 11949.5938 | 2.8185
6051 | 11630.793 | 2.9032
6052 | 11648.0352 | 2.8631
6053 | 11595.8984 | 2.8397
6054 | 11461.2041 | 2.8772
6055 | 11301.9707 | 2.8653
6056 | 11390.0645 | 2.8412
6057 | 11440.5703 | 2.9793
6058 | 11930.0859 | 3.0015
6059 | 12756.6348 | 3.2262
6060 | 15099.0801 | 3.5498
6061 | 16641.0488 | 4.0549
6062 | 18576.4199 | 4.634
6063 | 19985.2422 | 5.1055
6064 | 21276.7285 | 5.4959
6065 | 21942.2109 | 6.1141
6066 | 22680.7812 | 6.1323
6067 | 23636.1934 | 6.1282
6068 | 24432.2383 | 6.1753
6069 | 24329.9648 | 6.0056
6070 | 24649.5117 | 6.0596
6071 | 25205.8281 | 6.0092
6072 | 25008.8066 | 5.8947
6073 | 24015.3008 | 5.8713
6074 | 23876.2578 | 5.7852
6075 | 25542.3984 | 5.7338
6076 | 25340.7559 | 5.5144
6077 | 25043.6387 | 5.5167
6078 | 24994.1855 | 5.4371
6079 | 25571.6914 | 4.9731
6080 | 25813.5547 | 4.7121
6081 | 22272.2344 | 4.5495
6082 | 21533.0781 | 4.3378
6083 | 21079.0332 | 4.3081
6084 | 21287.5391 | 4.2378
6085 | 21044.1289 | 4.0052
6086 | 20689.832 | 3.8195
6087 | 19754.0547 | 3.7496
6088 | 19624.6523 | 3.711
6089 | 19057.6211 | 3.6373
6090 | 17893.4414 | 3.456
6091 | 16131.0801 | 3.2373
6092 | 14868.5332 | 3.2505
6093 | 14044.3516 | 2.8607
6094 | 13299.9414 | 2.6348
6095 | 12628.6562 | 2.454
6096 | 12065.9629 | 2.5308
6097 | 11459.2051 | 2.3054
6098 | 11151.9473 | 2.2509
6099 | 11073.791 | 2.3691
6100 | 10613.6543 | 2.3337
6101 | 10433.3984 | 2.2676
6102 | 10392.0215 | 2.1881
6103 | 10220.7363 | 2.2107
6104 | 10273.2637 | 2.2126
6105 | 10235.6328 | 2.221
6106 | 10016.4844 | 2.2255
6107 | 10063.8633 | 2.3274
6108 | 11458.1797 | 2.394
6109 | 12136.2871 | 2.4955
6110 | 12941.0137 | 2.6208
6111 | 13658.8564 | 3.1064
6112 | 15414.6465 | 3.3947
6113 | 16609.2656 | 3.9737
6114 | 17756.7988 | 4.033
6115 | 18341.9043 | 4.1307
6116 | 18785.3359 | 4.3837
6117 | 18576.7051 | 4.4745
6118 | 18645.209 | 4.599
6119 | 18627.4727 | 4.6601
6120 | 18985.4023 | 4.5352
6121 | 18714.3047 | 4.5274
6122 | 18735 | 4.3268
6123 | 18376.1484 | 4.3152
6124 | 18408.8516 | 4.1598
6125 | 18103.873 | 4.1693
6126 | 18243.3789 | 4.1042
6127 | 18158.1895 | 4.0321
6128 | 18095.2207 | 4.0428
6129 | 18159.2637 | 4.0051
6130 | 18013.2637 | 3.7941
6131 | 18058.3457 | 3.7232
6132 | 17701.3047 | 3.6092
6133 | 17531.3164 | 3.5782
6134 | 17751.873 | 3.6711
6135 | 17035.6211 | 3.2889
6136 | 15879.2383 | 3.2544
6137 | 14384.165 | 3.4425
6138 | 14158.3945 | 3.4826
6139 | 13908.7637 | 3.2923
6140 | 13467.5938 | 3.1457
6141 | 12993.3184 | 2.7094
6142 | 12446.4248 | 2.4814
6143 | 11980.2656 | 2.5444
6144 | 11327.9199 | 2.2272
6145 | 10975.9619 | 2.2671
6146 | 10820.8203 | 2.2348
6147 | 10428.6562 | 2.2797
6148 | 10299.3711 | 2.1913
6149 | 10081.4121 | 2.117
6150 | 9791.8125 | 2.0256
6151 | 9794.1582 | 1.9771
6152 | 9877.9062 | 2.0086
6153 | 9797.9062 | 2.0064
6154 | 9490.8965 | 1.9456
6155 | 9320.873 | 2.1449
6156 | 9659.4961 | 2.101
6157 | 10180.2754 | 2.2026
6158 | 10746.5254 | 2.403
6159 | 11462.3281 | 2.2514
6160 | 12003.0449 | 2.5251
6161 | 12917.7832 | 2.7669
6162 | 13636.4785 | 3.0386
6163 | 14087.9004 | 2.9267
6164 | 15916.9219 | 3.0279
6165 | 16796.9355 | 3.1764
6166 | 17197.2109 | 3.3713
6167 | 17288.9238 | 3.6323
6168 | 17744.6621 | 3.6431
6169 | 17783.2109 | 3.5024
6170 | 17662.127 | 3.3834
6171 | 17483.1445 | 3.2543
6172 | 17879.8945 | 3.0205
6173 | 17626.0312 | 3.1378
6174 | 17755.873 | 3.1862
6175 | 17598.0508 | 2.9935
6176 | 17376.5684 | 4.2397
6177 | 16863.6719 | 4.2439
6178 | 15801.166 | 4.0977
6179 | 14838.9443 | 4.1024
6180 | 14057.9629 | 4.0454
6181 | 13648.9727 | 3.9828
6182 | 13664.1426 | 3.9991
6183 | 13440.3516 | 4.0374
6184 | 13665.7305 | 4.1198
6185 | 14048.1211 | 4.3924
6186 | 14373.6367 | 4.451
6187 | 13975.8672 | 4.2671
6188 | 13468.3311 | 4.0979
6189 | 12752.5391 | 3.6865
6190 | 12156.4961 | 3.3601
6191 | 11346.707 | 3.2173
6192 | 10959.2559 | 2.9991
6193 | 10617.3203 | 2.9175
6194 | 10457.9473 | 2.6128
6195 | 10337.791 | 2.6879
6196 | 10075.748 | 2.6506
6197 | 9720.2305 | 2.5862
6198 | 9446.5781 | 2.5643
6199 | 9434.3242 | 2.6128
6200 | 9540.4609 | 2.6232
6201 | 10550.1602 | 2.6061
6202 | 11915.3477 | 2.6831
6203 | 12610.749 | 2.8931
6204 | 14200.0781 | 3.241
6205 | 16320.3652 | 4.4307
6206 | 19372.6934 | 5.0731
6207 | 20967.3496 | 5.7472
6208 | 22815.4141 | 6.0404
6209 | 25283.4492 | 6.5272
6210 | 26008.0078 | 6.8231
6211 | 27270.9883 | 6.7051
6212 | 27987.9141 | 6.5665
6213 | 29075.0645 | 6.6439
6214 | 28914.4648 | 6.7215
6215 | 28551.209 | 6.5095
6216 | 27646.2109 | 6.5152
6217 | 27412.6211 | 6.4189
6218 | 27496.4297 | 6.2874
6219 | 25241.9648 | 6.3328
6220 | 24713.6367 | 6.1692
6221 | 24796.7344 | 6.3299
6222 | 23702.3008 | 6.3218
6223 | 24816.207 | 6.1711
6224 | 23505.1094 | 6.0865
6225 | 23204.5938 | 6.0036
6226 | 23549.2656 | 5.8071
6227 | 22182.6797 | 5.5112
6228 | 22420.584 | 5.4159
6229 | 21901.0117 | 5.2876
6230 | 22010.7812 | 5.1497
6231 | 21589.8867 | 5.0061
6232 | 21368.7188 | 5.1003
6233 | 21063.7285 | 5.1545
6234 | 20229.7793 | 5.3568
6235 | 18500.3359 | 5.13
6236 | 16362.207 | 4.5783
6237 | 15424.6689 | 3.9738
6238 | 14417.5957 | 4.0067
6239 | 13748.0547 | 3.3936
6240 | 13220.793 | 3.2398
6241 | 12664.9727 | 3.3629
6242 | 12379.6875 | 3.2329
6243 | 12115.5508 | 3.3317
6244 | 11760.1309 | 3.3015
6245 | 12173.5732 | 3.2781
6246 | 12199.2266 | 2.9455
6247 | 11929.4648 | 2.9117
6248 | 12237.3477 | 2.9518
6249 | 12144.8438 | 2.8798
6250 | 12528.2441 | 3.1807
6251 | 13648.9092 | 3.3396
6252 | 16903.2188 | 3.7116
6253 | 18435.6816 | 4.2212
6254 | 20432.2422 | 5.136
6255 | 23653.6777 | 5.495
6256 | 25312.625 | 6.0072
6257 | 26084.7773 | 6.5912
6258 | 26650.2617 | 6.8649
6259 | 28578.168 | 6.9549
6260 | 29050.9902 | 7.3102
6261 | 28273.9238 | 7.4239
6262 | 28855.5566 | 7.5169
6263 | 28099.7695 | 7.4237
6264 | 28043.1152 | 7.2005
6265 | 27624.8418 | 7.0653
6266 | 26780.0078 | 6.8634
6267 | 25917.6797 | 6.5925
6268 | 24384.0391 | 6.4494
6269 | 24335.7129 | 6.3237
6270 | 24439.8164 | 6.2841
6271 | 24796.082 | 6.2784
6272 | 23364.4785 | 6.4484
6273 | 23450.2578 | 6.5056
6274 | 23165.6562 | 6.2255
6275 | 22598.582 | 5.8074
6276 | 22494.1602 | 5.8303
6277 | 22229.6348 | 5.6108
6278 | 21901.3828 | 5.5138
6279 | 21610.3711 | 5.73
6280 | 21638.4863 | 5.5624
6281 | 21417.4766 | 5.5048
6282 | 20678.8125 | 5.3572
6283 | 18849.2109 | 5.1311
6284 | 17385.9961 | 4.0593
6285 | 16213.0586 | 3.1136
6286 | 15097.0176 | 3.0207
6287 | 14497.3418 | 2.7306
6288 | 13844.1211 | 2.7923
6289 | 13261.3125 | 2.8726
6290 | 12902.793 | 2.581
6291 | 12459.7383 | 2.5943
6292 | 12113.7188 | 2.5049
6293 | 12048.3398 | 2.4702
6294 | 11987.0977 | 2.4192
6295 | 12054.8438 | 2.4226
6296 | 11994.707 | 2.4364
6297 | 11852.0645 | 2.5476
6298 | 12124.8438 | 2.5713
6299 | 12810.8652 | 2.8331
6300 | 15757.4062 | 2.9501
6301 | 17448.1133 | 3.5515
6302 | 19872.0312 | 4.0469
6303 | 21793.2129 | 4.5604
6304 | 23107.457 | 5.266
6305 | 23984.6484 | 5.6988
6306 | 24680.8359 | 5.9318
6307 | 25133.8477 | 5.9824
6308 | 24523.4062 | 6.1719
6309 | 25683.4277 | 6.0269
6310 | 26521.6074 | 5.979
6311 | 26336.6719 | 5.9696
6312 | 27134.9863 | 5.9858
6313 | 27011.9668 | 5.77
6314 | 26950.8086 | 5.6463
6315 | 26961.7344 | 5.7343
6316 | 26718.4512 | 5.6795
6317 | 26185.1758 | 5.5983
6318 | 25382.0391 | 5.5058
6319 | 24130.6699 | 5.4732
6320 | 23585.2383 | 5.3844
6321 | 23797.8789 | 5.0932
6322 | 23569.4883 | 4.7378
6323 | 23020.8574 | 4.6893
6324 | 22885.5625 | 4.5734
6325 | 22319.0352 | 4.319
6326 | 21959.3828 | 4.2209
6327 | 21959.498 | 3.9729
6328 | 22113.0137 | 3.9701
6329 | 21826.875 | 3.9135
6330 | 20700.1914 | 3.9544
6331 | 18492.1992 | 3.7732
6332 | 17102.3652 | 3.5644
6333 | 15920.1855 | 3.3597
6334 | 14930.2578 | 3.1531
6335 | 14311.2266 | 3.1155
6336 | 13975.5215 | 3.1124
6337 | 13568.6914 | 3.0664
6338 | 13342.7422 | 2.8872
6339 | 13154.0996 | 2.7252
6340 | 12889.3203 | 2.7037
6341 | 12712.6484 | 2.7309
6342 | 12548.0352 | 2.7146
6343 | 12739.625 | 2.7027
6344 | 12432.2441 | 2.6786
6345 | 12497.0039 | 2.7376
6346 | 12935.6445 | 2.8513
6347 | 14458.7422 | 3.1206
6348 | 17782.4082 | 3.231
6349 | 20515.043 | 3.77
6350 | 21673.1074 | 4.2825
6351 | 23581.8672 | 5.0512
6352 | 24325.7617 | 5.597
6353 | 26279.6172 | 6.0579
6354 | 25377.4375 | 6.0943
6355 | 26086.8379 | 6.0685
6356 | 28576.1152 | 6.1202
6357 | 27654.0723 | 6.237
6358 | 28857.3066 | 6.0638
6359 | 28694.3789 | 5.9114
6360 | 27796.8633 | 5.8348
6361 | 27412.4199 | 5.6637
6362 | 26338.1016 | 5.5779
6363 | 27585.5273 | 5.6122
6364 | 27007.1875 | 5.6404
6365 | 26528.6289 | 5.6375
6366 | 26174.5469 | 5.3456
6367 | 25807.8711 | 5.2226
6368 | 24041.1641 | 5.1884
6369 | 23980.6582 | 4.9299
6370 | 23003.4453 | 4.8445
6371 | 22637.5625 | 4.5082
6372 | 22702.457 | 4.3916
6373 | 22536.2969 | 4.3191
6374 | 21869.1719 | 4.2216
6375 | 22217.2891 | 4.1819
6376 | 22282.6875 | 4.1802
6377 | 21722.6445 | 3.7868
6378 | 20889.9824 | 3.8756
6379 | 18643.1152 | 3.7795
6380 | 17055.6523 | 3.7034
6381 | 16142.9648 | 3.3391
6382 | 14932.1641 | 3.0904
6383 | 14146.9941 | 2.9662
6384 | 13566.3008 | 2.743
6385 | 12954.4375 | 2.7099
6386 | 12643.3203 | 2.6644
6387 | 13373.3203 | 2.6865
6388 | 12103.623 | 2.6207
6389 | 12082.4961 | 2.6083
6390 | 12148.3828 | 2.5321
6391 | 12044.3828 | 2.5378
6392 | 11736.6133 | 2.5472
6393 | 11877.623 | 2.5744
6394 | 12134.8652 | 2.6647
6395 | 13281.1836 | 2.8861
6396 | 15957.7871 | 3.1557
6397 | 17160.7773 | 3.8781
6398 | 18817.748 | 4.2226
6399 | 20426.3164 | 4.8131
6400 | 21826.9805 | 5.2934
6401 | 23754.6055 | 5.8117
6402 | 23989.7305 | 5.9253
6403 | 24332.0801 | 5.8876
6404 | 25957.6602 | 6.0103
6405 | 25700.8711 | 6.025
6406 | 26680.5566 | 5.9826
6407 | 25184.6504 | 5.8527
6408 | 24151.2285 | 5.8699
6409 | 23778.9102 | 5.7134
6410 | 24020.291 | 5.5043
6411 | 23162.7109 | 5.3103
6412 | 22837.2793 | 4.9958
6413 | 23204.9961 | 4.8226
6414 | 22933.7305 | 4.7798
6415 | 23764.2695 | 4.7526
6416 | 22502.752 | 4.6366
6417 | 21959.1934 | 4.5556
6418 | 21679.4883 | 4.435
6419 | 21230.5391 | 4.2213
6420 | 21319.9707 | 4.1321
6421 | 21273.75 | 4.0013
6422 | 20742.3496 | 4.0323
6423 | 20175.9609 | 3.9389
6424 | 19436.6523 | 3.8711
6425 | 19279.5059 | 3.6998
6426 | 18124.5664 | 3.7969
6427 | 16306.9863 | 3.6051
6428 | 16932.9863 | 3.2351
6429 | 14355.9844 | 2.8787
6430 | 13544.9512 | 2.6588
6431 | 12812.793 | 2.5729
6432 | 12417.6445 | 2.6577
6433 | 11751.623 | 2.4657
6434 | 11406.707 | 2.2514
6435 | 10950.707 | 2.3104
6436 | 10827.1914 | 2.3053
6437 | 10615.0547 | 2.2844
6438 | 10546.8652 | 2.2728
6439 | 10473.0254 | 2.3683
6440 | 10543.6016 | 2.3134
6441 | 10413.8555 | 2.446
6442 | 10277.5801 | 2.4851
6443 | 10407.7832 | 2.3526
6444 | 11513.8984 | 2.1374
6445 | 12700.7715 | 2.306
6446 | 13543.3184 | 2.4009
6447 | 14053.1113 | 3.0242
6448 | 15857.123 | 3.3718
6449 | 16668.5977 | 3.5118
6450 | 17881.8418 | 3.7803
6451 | 18451.5449 | 3.811
6452 | 18952.6836 | 3.8012
6453 | 18871.8516 | 3.8026
6454 | 18757.2188 | 3.7737
6455 | 18604.873 | 3.7784
6456 | 18409.1055 | 3.6579
6457 | 18287.4414 | 3.6748
6458 | 18481.6738 | 3.6368
6459 | 17975.8418 | 3.5609
6460 | 18176.1777 | 3.5824
6461 | 18097.9902 | 3.5504
6462 | 18250.7168 | 3.5465
6463 | 18086.4082 | 3.6062
6464 | 18324.4844 | 3.4271
6465 | 18359.5469 | 3.3864
6466 | 18193.5469 | 3.2574
6467 | 17785.8203 | 3.1781
6468 | 17935.5898 | 3.0964
6469 | 17616.7988 | 3.1163
6470 | 17446.4082 | 2.9946
6471 | 17180.6406 | 2.8806
6472 | 15712.4375 | 2.9746
6473 | 14696.8789 | 2.9647
6474 | 14260.4883 | 3.0013
6475 | 13682.0781 | 2.9659
6476 | 13280.1729 | 2.8192
6477 | 12708.7715 | 2.806
6478 | 12178.7285 | 2.4952
6479 | 11724.1094 | 2.2241
6480 | 11221.0449 | 2.0752
6481 | 10777.1602 | 2.0261
6482 | 10466.1582 | 2.1738
6483 | 10347.2637 | 2.3314
6484 | 10127.8848 | 2.2828
6485 | 10461.8848 | 2.2852
6486 | 9798.5977 | 2.2257
6487 | 9707.6094 | 2.2376
6488 | 9728.2305 | 2.2094
6489 | 9352.2109 | 1.9223
6490 | 9549.7266 | 1.6454
6491 | 9561.957 | 1.7872
6492 | 10013.4961 | 1.9891
6493 | 10696.0215 | 1.9497
6494 | 11223.1914 | 1.9249
6495 | 11683.3281 | 2.252
6496 | 12823.7285 | 2.2559
6497 | 13551.0254 | 2.5546
6498 | 15079.6797 | 2.7051
6499 | 15887.9023 | 3.083
6500 | 16883.8809 | 3.1546
6501 | 18075.0723 | 3.088
6502 | 18411.1152 | 3.0744
6503 | 18405.8418 | 3.1669
6504 | 18852.9453 | 3.3727
6505 | 19131.9062 | 3.4533
6506 | 19027.0312 | 3.226
6507 | 19014.0547 | 3.1566
6508 | 18791.3359 | 3.2863
6509 | 18031.1777 | 3.1574
6510 | 18507.5371 | 3.1166
6511 | 18169.6113 | 3.1979
6512 | 18095.1035 | 3.1815
6513 | 17902.6621 | 3.2542
6514 | 16537.9023 | 3.2085
6515 | 15422.459 | 2.9881
6516 | 14725.2695 | 2.7413
6517 | 14216.4668 | 2.7403
6518 | 14200.2363 | 2.7232
6519 | 13952.7207 | 2.8054
6520 | 14107.0898 | 3.0009
6521 | 14622.4883 | 2.9613
6522 | 14751.2471 | 2.8885
6523 | 14523.9844 | 2.9351
6524 | 14182.0781 | 2.6602
6525 | 13435.0459 | 2.5652
6526 | 13035.5078 | 2.2621
6527 | 12405.8555 | 2.2777
6528 | 12084.0352 | 1.9718
6529 | 11901.6875 | 1.9013
6530 | 11552.1289 | 1.8814
6531 | 11171.6016 | 1.9871
6532 | 11051.8555 | 1.951
6533 | 10862.9297 | 1.9189
6534 | 10658.6426 | 1.8859
6535 | 10761.7695 | 1.9309
6536 | 10922.4102 | 1.9295
6537 | 11039.1484 | 1.8843
6538 | 11493.5391 | 1.9207
6539 | 12509.1797 | 2.2549
6540 | 15813.8906 | 2.5923
6541 | 18375.9258 | 3.2256
6542 | 20177.043 | 3.9822
6543 | 21891.6855 | 4.7957
6544 | 25291.4277 | 5.1606
6545 | 25905.4277 | 5.4691
6546 | 27266.168 | 5.6723
6547 | 27669.1152 | 5.7603
6548 | 27757.6406 | 5.8624
6549 | 27433.4727 | 5.8264
6550 | 27396.7461 | 5.802
6551 | 27808.6113 | 5.7129
6552 | 29255.8008 | 5.6816
6553 | 29090.0215 | 5.528
6554 | 27947.4941 | 5.5029
6555 | 28274.1367 | 5.3
6556 | 27494.873 | 5.2242
6557 | 27821.8945 | 5.423
6558 | 27917.4512 | 5.4111
6559 | 26705.1055 | 5.1549
6560 | 25825.4922 | 5.062
6561 | 25493.7656 | 4.8774
6562 | 24844.1445 | 4.5805
6563 | 24042.7734 | 4.2922
6564 | 24201.668 | 4.2045
6565 | 23717.291 | 4.2417
6566 | 23516.1328 | 4.2238
6567 | 23203.625 | 4.1448
6568 | 23017.8359 | 3.8703
6569 | 22791.1934 | 3.9183
6570 | 22224.668 | 4.0264
6571 | 20521.4336 | 3.7928
6572 | 18484.1992 | 3.4504
6573 | 17074.4805 | 3.3545
6574 | 16760.9863 | 2.9917
6575 | 15640.5547 | 2.8402
6576 | 15089.4277 | 2.9938
6577 | 14624.1348 | 2.9333
6578 | 14123.7305 | 2.6006
6579 | 13841.8242 | 2.6648
6580 | 13521.1602 | 2.6638
6581 | 13062.5195 | 2.6155
6582 | 12997.8027 | 2.6006
6583 | 13332.9082 | 2.6571
6584 | 13530.9082 | 2.6188
6585 | 13391.3496 | 2.5667
6586 | 14072.8145 | 2.7149
6587 | 14673.3301 | 3.1046
6588 | 17573.7891 | 3.3007
6589 | 19647.3672 | 3.7064
6590 | 21607.3164 | 4.259
6591 | 23904.2266 | 4.8895
6592 | 26786.0801 | 5.4932
6593 | 27831.5234 | 5.7817
6594 | 27700.5137 | 5.8867
6595 | 27196.9453 | 5.9965
6596 | 28655.8535 | 6.0735
6597 | 29328.6035 | 6.1546
6598 | 29687.7285 | 6.3633
6599 | 30094.7188 | 6.3042
6600 | 28502.8945 | 6.3169
6601 | 28606.9688 | 5.9868
6602 | 28216.2852 | 5.7247
6603 | 29412.2949 | 5.9542
6604 | 28821.7578 | 5.8309
6605 | 28115.0547 | 5.8414
6606 | 28367.5996 | 5.8078
6607 | 27301.9355 | 5.6205
6608 | 26474.293 | 5.89
6609 | 25986.8203 | 5.7005
6610 | 25565.375 | 5.1222
6611 | 24229.9336 | 4.939
6612 | 24776.5957 | 4.8187
6613 | 24784.082 | 4.6154
6614 | 24270.543 | 4.4543
6615 | 23699.2578 | 4.2136
6616 | 23726.2461 | 4.1455
6617 | 23573.6055 | 4.1309
6618 | 22564.4355 | 4.1419
6619 | 20681.8223 | 3.8001
6620 | 19061.2305 | 3.556
6621 | 17927.168 | 3.3611
6622 | 17324.7559 | 3.1
6623 | 16171.0811 | 2.9191
6624 | 15394.3223 | 2.8
6625 | 14648.7344 | 2.7735
6626 | -12889.8145 | 2.7698
6627 | -13819.4883 | 3.0315
6628 | -14171.2578 | 3.067
6629 | -12487.793 | 3.0464
6630 | -14874.7959 | 3.041
6631 | -15000.4277 | 3.0545
6632 | -14849.6689 | 2.9761
6633 | -14874.7949 | 2.9905
6634 | -14322.0156 | 2.9969
6635 | -14171.2578 | 3.0291
6636 | -11456.4131 | 3.3965
6637 | -8819.3477 | 3.6523
6638 | -6633.355 | 4.3391
6639 | -5829.1118 | 4.8859
6640 | -4346.8569 | 5.4203
6641 | -3616.3938 | 6.0462
6642 | -2462.3811 | 6.1913
6643 | -2185.792 | 6.1375
6644 | -1381.949 | 6.2387
6645 | -376.895 | 6.4084
6646 | 4 | 6.4339
6647 | 125.832 | 6.4217
6648 | -21.526 | 6.3823
6649 | -239.064 | 5.9674
6650 | -339.369 | 5.9182
6651 | -459.601 | 5.8328
6652 | -1691.9911 | 5.7523
6653 | -111.432 | 5.5834
6654 | -1018.78 | 5.5126
6655 | -1572.36 | 5.4723
6656 | -1750.244 | 5.4163
6657 | -1752.844 | 5.1753
6658 | -2809.75 | 4.9676
6659 | -3867.457 | 4.8017
6660 | -3138.1929 | 4.6285
6661 | 21985.5508 | 4.52
6662 | 26508.293 | 4.472
6663 | 26005.7656 | 4.195
6664 | 26081.1465 | 4.0285
6665 | 26558.5449 | 4.0973
6666 | 25176.5957 | 4.1061
6667 | 23166.4883 | 3.8535
6668 | 21030.75 | 3.541
6669 | 19673.9277 | 3.2873
6670 | 19171.3984 | 3.0449
6671 | 18618.6211 | 2.8839
6672 | 17663.8184 | 2.987
6673 | 16608.5156 | 2.9543
6674 | 16005.4805 | 2.8384
6675 | 16005.4805 | 2.9294
6676 | 15879.8496 | 2.863
6677 | 15980.3555 | 2.8955
6678 | 16056.8076 | 2.8422
6679 | 16515.6074 | 2.8615
6680 | 16595.9863 | 2.6924
6681 | 16764.6191 | 2.6713
6682 | 17375.5039 | 2.7522
6683 | 18362.1055 | 2.8977
6684 | 19760.6523 | 3.168
6685 | 15570.4814 | 3.7835
6686 | 9921.1797 | 4.2924
6687 | -1042.7061 | 4.9869
6688 | -1779.5699 | 5.7367
6689 | -1958.855 | 6.2749
6690 | -2035.0331 | 6.5669
6691 | -2412.1289 | 6.6408
6692 | -525.453 | 6.5547
6693 | 431.948 | 6.4972
6694 | 29.327 | 6.4171
6695 | 160.358 | 6.5064
6696 | 183.884 | 6.4436
6697 | 70.253 | 6.137
6698 | 279.19 | 5.9292
6699 | -115.432 | 5.9022
6700 | 232.337 | 5.6837
6701 | 33.926 | 5.7221
6702 | 31850.4785 | 5.6903
6703 | 29755.3906 | 5.5456
6704 | 28624.5059 | 5.5077
6705 | 28045.8008 | 5.145
6706 | 27617.6523 | 4.9654
6707 | 26685.3789 | 4.8561
6708 | 26785.084 | 4.7192
6709 | 27035.9453 | 4.6557
6710 | 26960.5664 | 4.6013
6711 | 27262.082 | 4.5023
6712 | 24799.7012 | 4.4145
6713 | 3768.9519 | 4.1836
6714 | -5653.4268 | 4.1212
6715 | -8392.1992 | 3.9175
6716 | -10578.1895 | 3.5315
6717 | -11708.877 | 3.3281
6718 | -12412.4141 | 3.0795
6719 | -12864.6895 | 3.0729
6720 | -12487.793 | 2.7961
6721 | -11583.2441 | 2.7857
6722 | -13166.2031 | 2.6909
6723 | -13568.2266 | 2.824
6724 | -13919.9941 | 2.8377
6725 | -12613.4258 | 2.7864
6726 | -14548.1523 | 2.681
6727 | -15377.3223 | 2.6526
6728 | -15402.4492 | 2.6308
6729 | -15804.0703 | 2.7125
6730 | -14648.6582 | 2.7826
6731 | -14444.6484 | 3.0336
6732 | -11268.3281 | 3.4853
6733 | -8663.1875 | 3.741
6734 | -7231.5869 | 4.387
6735 | -6005.1963 | 5.005
6736 | -4849.3838 | 5.4208
6737 | -3316.6782 | 5.9003
6738 | -1783.97 | 6.0802
6739 | -1658.339 | 6.0682
6740 | -1331.696 | 6.0524
6741 | -452.274 | 5.9921
6742 | 276.39 | 5.9009
6743 | 251.264 | 5.8361
6744 | 201.011 | 5.9022
6745 | 376.895 | 5.9028
6746 | 427.147 | 5.7292
6747 | -100.506 | 5.5464
6748 | -1708.5911 | 5.5642
6749 | -1658.3391 | 5.6539
6750 | -1859.349 | 5.5834
6751 | -2261.3711 | 5.2762
6752 | -2261.3711 | 5.3146
6753 | -2412.1292 | 5.2373
6754 | -3567.3408 | 4.9139
6755 | -4496.415 | 4.7836
6756 | -4795.7319 | 4.7143
6757 | -4999.7432 | 4.5527
6758 | -5552.9219 | 4.5322
6759 | -5804.1851 | 4.316
6760 | -4397.1099 | 4.2783
6761 | -4371.9829 | 4.0831
6762 | -5075.522 | 4.0819
6763 | -7613.2822 | 4.0178
6764 | -8970.1045 | 3.4052
6765 | -9623.3896 | 3.2311
6766 | -10377.1797 | 3.0413
6767 | -12789.3086 | 2.8638
6768 | -12286.7822 | 2.9158
6769 | -11708.876 | 2.8626
6770 | -14372.2695 | 2.8145
6771 | -15100.9316 | 2.9075
6772 | -15553.207 | 2.9078
6773 | -16985.4082 | 2.8177
6774 | -16887.0293 | 2.5375
6775 | -17079.166 | 2.5424
6776 | -16179.3662 | 2.538
6777 | -15980.3555 | 2.5434
6778 | -16231.6191 | 2.7079
6779 | -15729.0918 | 2.7228
6780 | -13291.8359 | 2.4561
6781 | -12913.9414 | 2.521
6782 | -12387.0869 | 2.9113
6783 | -11029.2646 | 3.0368
6784 | -8490.7041 | 3.4891
6785 | -7284.0396 | 3.7054
6786 | -7050.9019 | 3.8936
6787 | -6496.7231 | 4.0407
6788 | -5415.6899 | 3.9876
6789 | -4559.395 | 4.1451
6790 | -4660.2998 | 4.116
6791 | -5405.8901 | 4.2125
6792 | -5592.9746 | 4.2903
6793 | -5230.6064 | 4.2139
6794 | -5022.9951 | 4.1665
6795 | -4830.3838 | 4.1598
6796 | -5528.7217 | 3.9919
6797 | -6506.2495 | 4.2332
6798 | -4942.4902 | 4.1093
6799 | -4746.2798 | 4.0921
6800 | -4835.1836 | 3.9246
6801 | -4732.6787 | 3.8337
6802 | -5445.0171 | 3.6026
6803 | -5871.1641 | 3.3856
6804 | -6025.7231 | 3.2782
6805 | -5802.186 | 3.221
6806 | -6080.5752 | 3.356
6807 | -6532.8486 | 3.2199
6808 | -7638.4092 | 3.2239
6809 | -8743.9678 | 3.2525
6810 | -9799.2754 | 3.2382
6811 | -10377.1787 | 3.1356
6812 | -11206.3486 | 2.8723
6813 | -11884.7607 | 2.6521
6814 | -12186.2773 | 2.5055
6815 | -11960.1396 | 2.2826
6816 | -12362.1611 | 2.1498
6817 | -13090.8242 | 2.1508
6818 | -14121.0049 | 2.0387
6819 | -14548.1533 | 2.1021
6820 | -13241.584 | 2.1519
6821 | -15000.4268 | 2.287
6822 | -15980.3535 | 2.2509
6823 | -15955.2285 | 2.2645
6824 | -16055.7334 | 1.9333
6825 | -15930.1016 | 1.7997
6826 | -15628.5859 | 1.7794
6827 | -15402.4492 | 1.8428
6828 | -14874.7949 | 1.8814
6829 | -13417.4668 | 2.0017
6830 | -12637.75 | 2.2201
6831 | -11979.666 | 2.102
6832 | -10518.1377 | 2.4577
6833 | -10363.3799 | 2.4865
6834 | -9455.832 | 2.7418
6835 | -8849.999 | 3.0349
6836 | -7622.8091 | 2.891
6837 | -6496.3232 | 3.0532
6838 | -6002.9224 | 3.0215
6839 | -5783.186 | 3.1352
6840 | -5161.4268 | 3.6227
6841 | -5106.7749 | 3.6217
6842 | -5569.248 | 3.4767
6843 | -5512.5947 | 3.2671
6844 | -5439.417 | 3.2748
6845 | -5987.9961 | 3.4267
6846 | -6058.9761 | 3.0959
6847 | -5768.6592 | 3.2572
6848 | -5445.417 | 3.3427
6849 | -5393.1641 | 3.4355
6850 | -5622.3008 | 3.255
6851 | -9141.3896 | 3.0667
6852 | -9999.2852 | 2.9496
6853 | -9975.1592 | 2.9299
6854 | -9924.9062 | 2.8381
6855 | -10879.7061 | 3.0318
6856 | -10100.791 | 2.9706
6857 | -10678.6963 | 3.0414
6858 | -10653.5703 | 3.0747
6859 | -10477.6855 | 3.038
6860 | -10678.6963 | 2.6462
6861 | -11382.2344 | 2.5613
6862 | -11683.749 | 2.4236
6863 | -12010.3926 | 2.1297
6864 | -11759.1289 | 2.0072
6865 | -10653.5684 | 1.954
6866 | -13266.709 | 1.8948
6867 | -14095.8779 | 1.9745
6868 | -14648.6582 | 1.9539
6869 | -14899.9219 | 1.944
6870 | -14899.9219 | 1.9103
6871 | -14673.7842 | 1.9229
6872 | -14146.1309 | 1.8498
6873 | -12990.3203 | 1.8375
6874 | -12136.0234 | 1.9817
6875 | -10904.833 | 2.4412
6876 | -7713.7871 | 2.5941
6877 | -6130.8281 | 3.511
6878 | -4321.731 | 3.9026
6879 | -1482.455 | 4.6072
6880 | 1734.1171 | 5.0752
6881 | 2412.1289 | 5.5632
6882 | 4899.6372 | 5.659
6883 | 5628.3013 | 5.7043
6884 | 7236.3877 | 5.9076
6885 | 6683.6074 | 6.0955
6886 | 4020.2148 | 6.0702
6887 | 5306.2583 | 5.9981
6888 | 7814.6929 | 5.9773
6889 | 6510.5229 | 5.7513
6890 | 6260.0601 | 5.6688
6891 | 7060.7031 | 5.5857
6892 | 6130.8281 | 5.5856
6893 | 4975.416 | 5.4913
6894 | 6134.8281 | 5.3614
6895 | 6005.3965 | 5.1946
6896 | 2971.1079 | 5.2669
6897 | 2487.7078 | 5.3535
6898 | 1736.5181 | 5.0435
6899 | 2768.698 | 4.6251
6900 | 2437.8562 | 4.4995
6901 | 552.78 | 4.5791
6902 | -854.295 | 4.2459
6903 | -1256.317 | 4.0529
6904 | -1080.433 | 4.092
6905 | -1005.054 | 3.7547
6906 | -2487.5081 | 3.7544
6907 | -5653.4268 | 3.696
6908 | -7613.2822 | 3.4238
6909 | -8693.7139 | 3.0526
6910 | -9497.7578 | 2.9985
6911 | -9723.8965 | 2.9044
6912 | -9547.8105 | 2.8216
6913 | -10526.5371 | 2.7257
6914 | -10474.2852 | 2.4234
6915 | -11902.2871 | 2.515
6916 | -10870.3066 | 2.5387
6917 | -11357.1074 | 2.5501
6918 | -12136.0234 | 2.4476
6919 | -12763.9814 | 2.4521
6920 | -12587.6982 | 2.4473
6921 | -12430.9404 | 2.4704
6922 | -12233.5293 | 2.5091
6923 | -11055.1904 | 2.7657
6924 | -7613.2832 | 3.0194
6925 | -5201.1543 | 3.5043
6926 | -1004.854 | 3.9953
6927 | -399.821 | 4.6026
6928 | 753.79 | 5.0625
6929 | 1959.854 | 5.7032
6930 | 3468.4351 | 5.8674
6931 | 3322.0767 | 5.7038
6932 | 6285.5859 | 5.7828
6933 | 6913.7441 | 5.9539
6934 | 7694.8613 | 5.9252
6935 | 7998.7769 | 6.0063
6936 | 7797.7671 | 5.8232
6937 | 7748.5142 | 5.2389
6938 | 8651.8623 | 5.3489
6939 | 8300.0938 | 5.4017
6940 | 7720.9883 | 5.101
6941 | 5131.374 | 4.9691
6942 | 5282.9321 | 5.053
6943 | 3848.73 | 4.9774
6944 | 3367.3298 | 4.9628
6945 | 2513.4341 | 4.8401
6946 | 2362.2759 | 4.6467
6947 | 653.285 | 4.4537
6948 | -251.264 | 4.3384
6949 | -577.9059 | 4.3237
6950 | 50.253 | 4.1063
6951 | -25.126 | 3.8784
6952 | -50.253 | 3.8258
6953 | -628.1591 | 3.8048
6954 | -1557.833 | 3.8949
6955 | -5000.1431 | 3.7089
6956 | -6155.9541 | 3.4079
6957 | -7889.6719 | 3.2627
6958 | -8266.5674 | 3.086
6959 | -9321.874 | 2.7077
6960 | -8794.2197 | 2.6786
6961 | -9774.1465 | 2.7786
6962 | -10402.3066 | 2.6579
6963 | -9548.0107 | 2.5298
6964 | -9924.9062 | 2.5737
6965 | -11960.1387 | 2.7455
6966 | -12136.0234 | 2.6725
6967 | -11884.7607 | 2.6627
6968 | -12010.3926 | 2.5982
6969 | -12236.5293 | 2.5911
6970 | -11834.5078 | 2.812
6971 | -10703.8223 | 2.8764
6972 | -8743.9678 | 3.1642
6973 | -5653.4268 | 3.5477
6974 | -3015.1611 | 4.1895
6975 | -1455.528 | 4.7146
6976 | 679.011 | 5.1073
6977 | 3140.9929 | 5.7296
6978 | 3170.3201 | 5.8213
6979 | 3323.4771 | 5.903
6980 | 5132.1738 | 5.9609
6981 | 6237.5332 | 6.0043
6982 | 6616.229 | 5.9388
6983 | 7472.5244 | 6.0206
6984 | 6542.0488 | 6.0102
6985 | 6495.1963 | 5.8303
6986 | 4890.1113 | 5.7039
6987 | 4082.2678 | 5.6824
6988 | 4957.0903 | 5.5424
6989 | 5784.6592 | 5.4745
6990 | 6158.354 | 5.4536
6991 | 5100.8481 | 5.359
6992 | 2638.2661 | 5.0868
6993 | 2889.53 | 5.0208
6994 | 1959.855 | 4.8841
6995 | 904.548 | 4.7425
6996 | -804.043 | 4.4052
6997 | 25.126 | 4.3778
6998 | -25.126 | 4.2699
6999 | -402.021 | 4.1707
7000 | -527.653 | 3.9536
7001 | -954.801 | 3.8106
7002 | -2437.2549 | 3.7708
7003 | -5301.6582 | 3.7712
7004 | -7286.6396 | 3.6107
7005 | -7814.293 | 3.2865
7006 | -8718.8408 | 2.8751
7007 | -9246.4941 | 2.84
7008 | -8568.083 | 2.622
7009 | -9422.3789 | 2.48
7010 | -10226.4219 | 2.3966
7011 | -10904.834 | 2.4684
7012 | -9573.1367 | 2.4338
7013 | -7035.376 | 2.446
7014 | 18744.252 | 2.3568
7015 | 19699.0527 | 2.3405
7016 | 19648.8008 | 2.299
7017 | 19221.6523 | 2.5645
7018 | 20050.8242 | 2.5941
7019 | 21231.7617 | 2.9362
7020 | 23719.2695 | 3.2537
7021 | 26030.8906 | 3.7207
7022 | 28845.043 | 4.3445
7023 | 31558.6895 | 4.9121
7024 | 32789.8789 | 5.6412
7025 | 0 | 6.2028
7026 | 33694.4297 | 6.2943
7027 | 34598.9766 | 6.2424
7028 | 36056.3047 | 6.1352
7029 | 38870.4531 | 6.0638
7030 | 36131.6797 | 6.2345
7031 | 36759.8438 | 6.1971
7032 | 36709.5898 | 6.224
7033 | 35830.168 | 6.0101
7034 | 35001 | 5.785
7035 | 33895.4375 | 5.7646
7036 | 34649.2305 | 5.8934
7037 | 36006.0469 | 5.8157
7038 | 35403.0195 | 5.8328
7039 | 35076.375 | 5.7309
7040 | 33116.5195 | 5.6579
7041 | 32865.2578 | 5.595
7042 | 32287.3516 | 5.447
7043 | 31583.8145 | 5.1985
7044 | 32287.3516 | 5.1091
7045 | 32186.8457 | 5.136
7046 | 32036.0898 | 4.9344
7047 | 32965.7617 | 4.6824
7048 | 33367.7852 | 4.7081
7049 | 31257.1719 | 4.2702
7050 | 28794.7891 | 4.0383
7051 | 26056.0156 | 3.8198
7052 | 24322.3008 | 3.7118
7053 | 23870.0273 | 3.2454
7054 | 22814.7207 | 3.1281
7055 | 22136.3086 | 2.8337
7056 | 22161.4355 | 2.6527
7057 | 21759.4141 | 2.6677
7058 | 20201.582 | 2.6282
7059 | 14975.3027 | 2.6824
7060 | 5779.0601 | 2.8837
7061 | -2562.887 | 2.8623
7062 | -7286.6396 | 2.8135
7063 | -10980.2129 | 2.8531
7064 | -11809.3818 | 2.8537
7065 | -10754.0752 | 3.0531
7066 | -8442.4512 | 3.0408
7067 | -6130.8271 | 3.1667
7068 | 2010.108 | 3.2675
7069 | -4673.5 | 3.715
7070 | -3742.825 | 4.2491
7071 | -1280.844 | 5.0897
7072 | 101.106 | 5.5794
7073 | 4048.1409 | 6.1282
7074 | 3320.8782 | 6.1693
7075 | 1792.1699 | 6.2161
7076 | 3051.488 | 6.1736
7077 | 3402.0562 | 6.0372
7078 | 2822.3508 | 6.0428
7079 | 2649.467 | 5.9733
7080 | 2446.656 | 5.9342
7081 | 2322.0239 | 5.825
7082 | 2323.2241 | 5.6916
7083 | 790.517 | 5.7451
7084 | 38.926 | 5.7392
7085 | 165.358 | 5.5447
7086 | 35.327 | 5.326
7087 | -295.116 | 5.2544
7088 | -320.843 | 5.3422
7089 | -1554.434 | 5.0814
7090 | -2785.4241 | 4.6423
7091 | -3215.772 | 4.4295
7092 | -3090.1411 | 4.4083
7093 | -1633.2119 | 4.3498
7094 | -2562.887 | 4.2074
7095 | -4095.5938 | 4.1014
7096 | -4120.7202 | 4.1097
7097 | -4271.478 | 3.82
7098 | -5552.9219 | 3.9146
7099 | -7663.5352 | 3.7781
7100 | -9246.4941 | 3.5644
7101 | -9874.6543 | 3.1524
7102 | -10402.3057 | 3.0864
7103 | -11256.6016 | 2.9516
7104 | -10854.5801 | 2.7817
7105 | -11382.2344 | 2.5884
7106 | -12538.0449 | 2.4845
7107 | -12814.4355 | 2.5543
7108 | -12512.9189 | 2.3406
7109 | -12940.0664 | 2.2166
7110 | -14221.5107 | 2.1805
7111 | -14372.2695 | 2.1791
7112 | -14799.417 | 2.1485
7113 | -14950.1738 | 2.1742
7114 | -15226.5645 | 2.1993
7115 | -14925.0479 | 2.3668
7116 | -14121.0059 | 2.4407
7117 | -12713.9297 | 2.4082
7118 | -12161.1504 | 2.5505
7119 | -11278.3281 | 3.0672
7120 | -9767.3486 | 3.3683
7121 | -8111.4092 | 3.7641
7122 | -6778.1133 | 3.9781
7123 | -6570.502 | 4.0688
7124 | -6336.7646 | 4.1799
7125 | -5193.7534 | 4.1508
7126 | -5402.1641 | 4.2187
7127 | -4899.6367 | 4.172
7128 | -5351.9111 | 4.0799
7129 | -5226.2793 | 3.9566
7130 | -5100.6479 | 4.018
7131 | -5804.1846 | 4.1274
7132 | -6055.248 | 4.0069
7133 | -5804.1846 | 4.0048
7134 | -5904.4912 | 3.7531
7135 | -7385.9448 | 3.5838
7136 | -8190.7886 | 3.5148
7137 | -7914.7988 | 3.5881
7138 | -7965.0508 | 3.4481
7139 | -8115.8091 | 3.4688
7140 | -7638.4092 | 3.4637
7141 | -7814.293 | 3.1924
7142 | -7713.7881 | 3.0687
7143 | -8166.0625 | 2.9641
7144 | -9548.0107 | 2.8264
7145 | -10980.2119 | 2.9768
7146 | -11809.3818 | 3.0063
7147 | -12914.9395 | 3.0534
7148 | -13065.6992 | 2.991
7149 | -13718.9834 | 2.6857
7150 | -14095.8779 | 2.5479
7151 | -14598.4062 | 2.4252
7152 | -14070.752 | 2.1004
7153 | -15025.5527 | 2.0749
7154 | -16281.8711 | 1.9888
7155 | -16432.6289 | 2.0702
7156 | -16030.6074 | 1.954
7157 | -16508.0078 | 1.9922
7158 | -16960.2832 | 2.1826
7159 | -17060.7871 | 2.1658
7160 | -17563.3145 | 2.0937
7161 | -11708.876 | 2.0869
7162 | -14849.6689 | 2.0958
7163 | -17035.6602 | 1.9528
7164 | -16859.7773 | 1.8684
7165 | -16105.9863 | 2.1923
7166 | -15327.0703 | 2.2009
7167 | -14799.416 | 2.0815
7168 | -14497.9004 | 2.2496
7169 | -13040.5723 | 2.5527
7170 | -12211.0029 | 2.6707
7171 | -11027.0635 | 2.7279
7172 | -10346.6533 | 2.7717
7173 | -8762.4932 | 2.9551
7174 | -7880.0718 | 2.9488
7175 | -7851.5449 | 3.0655
7176 | -1490.78 | 3.1489
7177 | 5131.1748 | 3.1947
7178 | 5708.2803 | 3.0618
7179 | -548.58 | 3.1428
7180 | -7458.5244 | 3.1064
7181 | -7407.6724 | 3.0935
7182 | -7410.8711 | 2.9746
7183 | -7663.335 | 3.0821
7184 | -3008.1611 | 3.0755
7185 | 3024.3621 | 2.9599
7186 | 1034.5801 | 2.885
7187 | 28.326 | 2.5977
7188 | 0.4 | 2.6317
7189 | 0.2 | 2.6226
7190 | 0 | 2.572
7191 | 0 | 2.5701
7192 | 0 | 2.5599
7193 | 0 | 2.7048
7194 | 0 | 2.5105
7195 | 0 | 2.8815
7196 | -1005.054 | 2.8527
7197 | -9372.126 | 2.5246
7198 | -12563.1719 | 2.3634
7199 | -14146.1318 | 2.2271
7200 | -16231.6191 | 2.0154
7201 | -16759.2695 | 2.0155
7202 | -16533.1328 | 1.9507
7203 | -15126.0586 | 1.9717
7204 | -12638.5498 | 1.9686
7205 | -5980.0713 | 2.1978
7206 | -6608.2285 | 2.1838
7207 | -12186.2773 | 2.1949
7208 | -17362.3047 | 1.9944
7209 | -17739.1992 | 2.1506
7210 | -17638.6953 | 2.0611
7211 | -17462.8105 | 2.1966
7212 | -16734.1445 | 2.5653
7213 | -16357.25 | 2.9642
7214 | -15477.4268 | 3.1755
7215 | -14596.6064 | 3.4365
7216 | -13311.7617 | 3.687
7217 | -12201.8037 | 4.0363
7218 | -10698.0225 | 4.1475
7219 | -10215.0215 | 4.2827
7220 | -9456.4307 | 4.3307
7221 | -8406.7256 | 4.4438
7222 | -8679.915 | 4.6913
7223 | -8430.252 | 4.742
7224 | -8006.1025 | 4.6681
7225 | -8541.2832 | 4.6636
7226 | -7735.6411 | 4.6592
7227 | -8494.4307 | 4.645
7228 | -8768.4199 | 4.5453
7229 | -8592.9346 | 4.5148
7230 | -8192.5156 | 4.4283
7231 | -8171.9893 | 4.3165
7232 | -8499.4307 | 4.1549
7233 | -8351.0732 | 4.3066
7234 | -8457.7783 | 4.0844
7235 | -8791.0195 | 3.9512
7236 | -8693.7148 | 3.9698
7237 | -8995.2314 | 3.9486
7238 | -8769.0938 | 3.9175
7239 | -9347 | 3.9126
7240 | -8266.5674 | 3.7336
7241 | -527.653 | 3.6405
7242 | -4321.73 | 3.712
7243 | -9799.2754 | 3.5526
7244 | -13015.4463 | 3.5355
7245 | -13970.2471 | 3.3968
7246 | -14171.2578 | 3.0222
7247 | -15176.3105 | 2.8629
7248 | 13005.2979 | 2.9654
7249 | 12690.6338 | 2.8758
7250 | 12540.4023 | 2.8902
7251 | 12397.8984 | 2.9561
7252 | 12043.9453 | 2.7582
7253 | 11764.1475 | 2.7722
7254 | 11597.793 | 2.6856
7255 | 11432.7041 | 2.5907
7256 | 11743.624 | 2.524
7257 | 11853.4434 | 2.5581
7258 | 12624.498 | 2.6937
7259 | 13693.0674 | 2.9952
7260 | 16690.1133 | 3.2285
7261 | 19297.9883 | 3.5476
7262 | 21754.5078 | 4.1076
7263 | 24331.3008 | 4.5988
7264 | 26677.4609 | 5.311
7265 | 28897.1797 | 5.6809
7266 | 29682.4277 | 5.7482
7267 | 27768.1367 | 5.7019
7268 | 28257.5469 | 5.8537
7269 | 28693.6855 | 5.8498
7270 | 28271.0859 | 5.8696
7271 | 29177.6953 | 5.8253
7272 | 29147.3613 | 5.858
7273 | 29455.623 | 5.6499
7274 | 29928.9492 | 5.5521
7275 | 29017.4004 | 5.5142
7276 | 27994.6211 | 5.3863
7277 | 28020.9688 | 5.3426
7278 | 28593.916 | 5.2416
7279 | 28807.3164 | 5.1583
7280 | 25873.8398 | 5.1364
7281 | 25955.7461 | 4.8925
7282 | 26648.9473 | 4.5697
7283 | 25922.168 | 4.3962
7284 | 24718.8398 | 4.2687
7285 | 26108.168 | 4.0693
7286 | 25976.6504 | 3.9653
7287 | 24507.5742 | 3.9173
7288 | 24673.8281 | 3.8887
7289 | 24463.6914 | 3.8453
7290 | 22185.3086 | 3.7205
7291 | 20147.6855 | 3.6047
7292 | 18301.7148 | 3.4751
7293 | 17541.6719 | 3.3531
7294 | 16718.1348 | 2.9719
7295 | 16091.0811 | 2.7634
7296 | 15339.9551 | 2.6405
7297 | 15494.3887 | 2.6672
7298 | 16048.9131 | 2.555
7299 | 14575.6797 | 2.6204
7300 | 15003.4707 | 2.8451
7301 | 14398.9648 | 2.6303
7302 | 14350.6484 | 2.7167
7303 | 14659.1543 | 2.7931
7304 | 14697.7529 | 2.6021
7305 | 15200.5332 | 2.5794
7306 | 16464.4727 | 2.6249
7307 | 16527.7031 | 3.034
7308 | 19150.5156 | 3.3159
7309 | 21672.3711 | 3.5968
7310 | 24059.627 | 4.0742
7311 | 25826.6387 | 4.6078
7312 | 27050.3145 | 5.2538
7313 | 27762.5996 | 5.7464
7314 | 28123.0938 | 5.8258
7315 | 28594.3887 | 5.724
7316 | 29116.7695 | 5.9302
7317 | 30760.9609 | 5.9533
7318 | 30396.0859 | 5.8319
7319 | 30056.8652 | 5.7551
7320 | 29131.3281 | 5.7997
7321 | 30123.875 | 5.6741
7322 | 31465.7012 | 5.5383
7323 | 30157.4609 | 5.5211
7324 | 28535.9199 | 5.4964
7325 | 28459.959 | 5.4222
7326 | 28159.3164 | 5.4607
7327 | 26459.209 | 5.2017
7328 | 25621.0723 | 5.1136
7329 | 25478.5977 | 4.9227
7330 | 24983.2402 | 4.7122
7331 | 24949.5312 | 4.5714
7332 | 24386.2598 | 4.4822
7333 | 24475.4395 | 4.4161
7334 | 24271.1641 | 4.3283
7335 | 24327.1641 | 4.1893
7336 | 25366.2168 | 4.0854
7337 | 24833.3008 | 4.1083
7338 | 22534.9414 | 3.7909
7339 | 20571.4551 | 3.83
7340 | 18868.125 | 3.6727
7341 | 17791.8105 | 3.439
7342 | 16947.6289 | 3.1642
7343 | 16081.7227 | 2.8743
7344 | 15535.2402 | 2.7933
7345 | 15295.8594 | 2.9917
7346 | 14926.8281 | 2.9046
7347 | 14590.6914 | 2.9562
7348 | 14624.8496 | 2.7525
7349 | 14321.6797 | 2.6719
7350 | 14149.5957 | 2.5903
7351 | 14200.4883 | 2.5694
7352 | 14255.7305 | 2.5553
7353 | 14287.7305 | 2.6729
7354 | 15126.6465 | 2.7561
7355 | 16063.3125 | 3.0306
7356 | 18994.1055 | 3.2593
7357 | 20700.8125 | 3.677
7358 | 22196.0234 | 4.043
7359 | 23856.4453 | 4.7364
7360 | 25057.8379 | 5.2544
7361 | 27972.5879 | 5.7196
7362 | 28852.6211 | 5.8061
7363 | 28982.9492 | 5.9033
7364 | 28827.7695 | 5.9792
7365 | 28438.8535 | 6.0277
7366 | 28614.9375 | 5.9273
7367 | 28586.9492 | 5.99
7368 | 28523.4727 | 5.9301
7369 | 29658.5078 | 5.6419
7370 | 28247.4121 | 5.5272
7371 | 26255.7656 | 5.4436
7372 | 27447.4844 | 5.326
7373 | 26818.8516 | 5.3012
7374 | 26700.1992 | 5.2457
7375 | 26002.123 | 5.1953
7376 | 25846.2617 | 5.0825
7377 | 25630.7656 | 4.7977
7378 | 24911.7109 | 4.6538
7379 | 23919.9434 | 4.5261
7380 | 23868.752 | 4.3685
7381 | 23443.9961 | 4.2108
7382 | 23932.1523 | 4.1918
7383 | 23981.0273 | 4.1466
7384 | 24117.1641 | 4.0783
7385 | 23416.2461 | 3.9186
7386 | 21747.6562 | 3.6895
7387 | 20196.6953 | 3.6801
7388 | 18487.7148 | 3.5471
7389 | 17428.6602 | 3.2787
7390 | 16844.7559 | 3.2086
7391 | 16242.7559 | 2.848
7392 | 15641.0293 | 2.8718
7393 | 15005.9336 | 2.7788
7394 | 14863.2676 | 2.5749
7395 | 14279.3633 | 2.5899
7396 | 14048.3516 | 2.5733
7397 | 13975.8477 | 2.5787
7398 | 13776.3311 | 2.5501
7399 | 13791.0889 | 2.6225
7400 | 13917.71 | 2.474
7401 | 14004.3516 | 2.574
7402 | 14690.5117 | 2.6139
7403 | 15798.6387 | 2.9025
7404 | 18856.4004 | 3.1517
7405 | 20724.2539 | 3.6038
7406 | 22679.8145 | 4.1149
7407 | 24172.6367 | 4.7075
7408 | 25906.1016 | 5.2543
7409 | 26989.041 | 5.6574
7410 | 26897.041 | 5.761
7411 | 28225.6074 | 5.6168
7412 | 28524.1641 | 5.676
7413 | 28653.5078 | 5.8244
7414 | 28049.1797 | 5.5933
7415 | 28184.2852 | 5.5073
7416 | 27946.9277 | 5.4864
7417 | 28215.6309 | 5.35
7418 | 27612.041 | 5.1585
7419 | 26261.4414 | 5.0888
7420 | 25884.2617 | 4.9845
7421 | 25990.6719 | 4.9653
7422 | 25907.9258 | 4.8467
7423 | 25221.459 | 4.4678
7424 | 25202.6074 | 4.4011
7425 | 24448.334 | 4.3528
7426 | 23530.0879 | 4.0699
7427 | 22572.9102 | 3.7754
7428 | 22778.373 | 3.7364
7429 | 22457.8359 | 3.7507
7430 | 22320.0664 | 3.4965
7431 | 22277.5625 | 3.4624
7432 | 22761.332 | 3.3767
7433 | 22200.4141 | 3.2141
7434 | 20343.3164 | 2.9928
7435 | 18342.7031 | 2.9998
7436 | 17235.2812 | 3.1071
7437 | 16396.4824 | 2.8984
7438 | 15415.6797 | 2.6301
7439 | 14688.9004 | 2.5592
7440 | 14322.4609 | 2.3275
7441 | 13539.71 | 2.2981
7442 | 12936.9082 | 2.4698
7443 | 12617.1387 | 2.4637
7444 | 12375.1387 | 2.4066
7445 | 12092.1094 | 2.3763
7446 | 12059.4883 | 2.3384
7447 | 12349.2559 | 2.3865
7448 | 12297.624 | 2.2663
7449 | 12167.623 | 1.9593
7450 | 12143.6016 | 1.9657
7451 | 12623.6465 | 2.1539
7452 | 13660.1934 | 2.3487
7453 | 14634.373 | 2.1767
7454 | 15523.6699 | 2.2778
7455 | 16502.8398 | 2.7442
7456 | 18277.6406 | 3.108
7457 | 20239.8027 | 3.4358
7458 | 21050.2109 | 3.4909
7459 | 21255.8867 | 3.6551
7460 | 20672.6445 | 3.6756
7461 | 21392.5391 | 3.7339
7462 | 21279.4336 | 3.7631
7463 | 21148.0742 | 3.829
7464 | 21342.8555 | 3.995
7465 | 21617.0039 | 4.0139
7466 | 21855.6348 | 3.7923
7467 | 21519.8672 | 3.6938
7468 | 21172.7188 | 3.5595
7469 | 21552.875 | 3.5452
7470 | 21619.498 | 3.5316
7471 | 21504.2559 | 3.5669
7472 | 21596.7402 | 3.6273
7473 | 21292.9922 | 3.558
7474 | 21143.4961 | 3.3973
7475 | 20742.4883 | 3.2941
7476 | 20518.7168 | 3.2437
7477 | 20520.8535 | 3.1922
7478 | 20117.4531 | 3.1268
7479 | 19847.5703 | 2.8251
7480 | 19187.8965 | 2.7561
7481 | 17575.5566 | 2.6719
7482 | 16551.375 | 2.6318
7483 | 15828.0918 | 2.634
7484 | 15310.3223 | 2.6332
7485 | 14570.7852 | 2.4878
7486 | 13854.3516 | 2.4281
7487 | 13392.8369 | 2.5132
7488 | 13151.71 | 2.1115
7489 | 12625.4355 | 2.0411
7490 | 12477.457 | 1.9606
7491 | 12189.2266 | 1.9535
7492 | 12006.9512 | 2.2069
7493 | 11816.4473 | 2.1633
7494 | 11695.1836 | 2.1088
7495 | 11583.6875 | 2.0957
7496 | 11748.6133 | 2.0363
7497 | 11686.7285 | 2.0545
7498 | 10533.4648 | 2.0193
7499 | 10764.2012 | 2.1352
7500 | 12104.3613 | 2.138
7501 | 12394.8867 | 1.824
7502 | 13295.5508 | 1.9464
7503 | 14064.6777 | 2.195
7504 | 15165.4482 | 2.2528
7505 | 16162.2402 | 2.4706
7506 | 17036.7988 | 2.7299
7507 | 17845.5781 | 2.7335
7508 | 19118.0117 | 2.7189
7509 | 20176.6016 | 2.9303
7510 | 21214.2129 | 3.2047
7511 | 21061.5078 | 3.1695
7512 | 21093.2871 | 3.1941
7513 | 21392.6992 | 3.2562
7514 | 21469.3398 | 3.1974
7515 | 21291.5195 | 3.0898
7516 | 20807.5195 | 2.9774
7517 | 20631.4023 | 2.8824
7518 | 20697.3398 | 2.8966
7519 | 20496.7383 | 2.9318
7520 | 20897.4238 | 2.9031
7521 | 21670.2344 | 2.9599
7522 | 20237.4863 | 2.968
7523 | 18229.6523 | 2.8259
7524 | 16116.2832 | 2.7695
7525 | 15481.9121 | 2.6687
7526 | 15653.1953 | 2.6297
7527 | 16243.1016 | 2.6558
7528 | 17012.3867 | 2.6162
7529 | 16885.2383 | 2.593
7530 | 17085.6719 | 2.7947
7531 | 18002.6797 | 2.8518
7532 | 16930.5215 | 2.7389
7533 | 16095.5859 | 2.5819
7534 | 14392.2363 | 2.2694
7535 | 13225.1602 | 2.0861
7536 | 13082.3311 | 2.0122
7537 | 12816.626 | 2.2813
7538 | 12387.1602 | 2.1688
7539 | 12993.1836 | 1.8965
7540 | 13363.4355 | 1.8411
7541 | 13132.793 | 1.8349
7542 | 12964.5195 | 1.7847
7543 | 11434.9707 | 1.7997
7544 | 11382.4121 | 1.7092
7545 | 11828.4531 | 1.7577
7546 | 13179.666 | 1.9201
7547 | 15012.5117 | 2.3612
7548 | 18344.8203 | 2.3819
7549 | 20618.4434 | 3.2156
7550 | 22436.2988 | 3.6242
7551 | 23556.4258 | 4.5616
7552 | 27626.6504 | 4.7485
7553 | 27826.5996 | 5.3917
7554 | 28580 | 5.6193
7555 | 28729.7695 | 5.6671
7556 | 29094.1582 | 5.9585
7557 | 30478.8652 | 5.9181
7558 | 29665.3281 | 5.8987
7559 | 30145.0977 | 5.8342
7560 | 31025.8652 | 5.5567
7561 | 30360.8438 | 5.8217
7562 | 30347.3281 | 5.7304
7563 | 29161.9062 | 5.5836
7564 | 30710.75 | 5.563
7565 | 30318.1289 | 5.4903
7566 | 28356.5898 | 5.5564
7567 | 28032.873 | 5.4189
7568 | 27165.7988 | 5.4516
7569 | 26739.5664 | 5.1181
7570 | 26217.8301 | 4.8874
7571 | 25868.6289 | 4.6338
7572 | 26115.6621 | 4.477
7573 | 25955.5234 | 4.4755
7574 | 25494.3555 | 4.3291
7575 | 25662.377 | 4.2036
7576 | 26242.6504 | 4.0408
7577 | 25938.1445 | 4.0381
7578 | 23178.6172 | 3.8759
7579 | 20844.6016 | 3.9297
7580 | 19285.7793 | 3.8671
7581 | 18214.8418 | 3.4845
7582 | 17168.293 | 3.1469
7583 | 16402.9141 | 3.0804
7584 | 15722.0625 | 2.8581
7585 | 15183.375 | 2.7849
7586 | 14688.0918 | 2.6729
7587 | 14232.4375 | 2.6982
7588 | 13979.1016 | 2.7154
7589 | 14055.7305 | 2.7184
7590 | 14228.8789 | 2.6738
7591 | 14190.7637 | 2.6923
7592 | 14310.3008 | 2.6887
7593 | 14541.0371 | 2.6361
7594 | 15492.7129 | 2.7909
7595 | 16550.1348 | 3.0896
7596 | 19412.3066 | 3.4443
7597 | 21125.1289 | 3.6943
7598 | 24712.9531 | 4.1961
7599 | 27535.957 | 4.8553
7600 | 30515.2559 | 5.412
7601 | 30784.1719 | 5.7881
7602 | 30566.2871 | 6.0056
7603 | 30417.6016 | 6.0759
7604 | 32156.7422 | 6.1926
7605 | 32665.6484 | 6.2678
7606 | 32531.1113 | 6.2642
7607 | 32376.543 | 6.2606
7608 | 33679.3125 | 6.111
7609 | 33001.7422 | 6.0731
7610 | 32892.7227 | 5.8259
7611 | 32273.0059 | 5.8809
7612 | 31428.1953 | 5.855
7613 | 32132.4062 | 5.8558
7614 | 30926.6055 | 5.7161
7615 | 29583.8555 | 5.5533
7616 | 28257.3281 | 5.493
7617 | 28049.0547 | 5.2755
7618 | 27614.3906 | 5.008
7619 | 26751.2207 | 4.8466
7620 | 27105.4004 | 4.7155
7621 | 26905.7266 | 4.602
7622 | 26887.8418 | 4.4693
7623 | 26630.9453 | 4.3254
7624 | 26532.9453 | 4.1487
7625 | 25897.7773 | 3.935
7626 | 23827.418 | 3.8911
7627 | 21599.5391 | 3.7994
7628 | 20032.0742 | 3.5628
7629 | 18928.5176 | 3.3253
7630 | 17840.7246 | 3.0712
7631 | 16899.4414 | 2.9304
7632 | 16318.9375 | 2.6742
7633 | 15858.4316 | 2.5991
7634 | 15386.3887 | 2.5073
7635 | 15577.1855 | 2.526
7636 | 14810.5059 | 2.4673
7637 | 14558.791 | 2.4922
7638 | 14543.0391 | 2.4403
7639 | 14489.2695 | 2.4317
7640 | 14766.7852 | 2.375
7641 | 14624.5332 | 2.7014
7642 | 15178.4395 | 2.7923
7643 | 16027.6074 | 2.8813
7644 | 19300.5391 | 3.133
7645 | 21700.7812 | 3.3871
7646 | 24273.6699 | 3.8675
7647 | 25881.5039 | 4.6178
7648 | 27040.2109 | 4.9275
7649 | 27980.2539 | 5.4679
7650 | 28856.918 | 5.8698
7651 | 29087.4434 | 5.8495
7652 | 28640.6309 | 5.9983
7653 | 28679.3281 | 6.0275
7654 | 29758.9297 | 6.058
7655 | 30352.541 | 5.8915
7656 | 30861.625 | 5.926
7657 | 30314.6992 | 5.7181
7658 | 30797.002 | 5.6138
7659 | 30241.584 | 5.5676
7660 | 30394.9102 | 5.4126
7661 | 29730.2656 | 5.4792
7662 | 28477.8125 | 5.3897
7663 | 27966.7793 | 5.2795
7664 | 27831.5898 | 5.1716
7665 | 27572.1152 | 5.1156
7666 | 27118.2305 | 4.7217
7667 | 26023.7988 | 4.2483
7668 | 26066.9258 | 4.1918
7669 | 26205.6836 | 4.1345
7670 | 25967.041 | 3.8243
7671 | 26291.4297 | 3.8297
7672 | 26711.3359 | 3.778
7673 | 26474.7871 | 3.519
7674 | 23877.2812 | 3.6061
7675 | 21286.4141 | 3.8714
7676 | 19510.6953 | 3.8779
7677 | 18356.3574 | 3.4693
7678 | 17282.0625 | 3.3197
7679 | 16544.25 | 2.9485
7680 | 16147.3984 | 2.8476
7681 | 15537.5137 | 2.7665
7682 | 15107.4922 | 2.6875
7683 | 14857.7227 | 2.676
7684 | 14835.9766 | 2.6778
7685 | 14253.7441 | 2.6918
7686 | 14190.0059 | 2.7409
7687 | 14274.1533 | 2.636
7688 | 14387.0156 | 2.6025
7689 | 14488.8789 | 2.6654
7690 | 15247.0586 | 2.7306
7691 | 16365.8398 | 2.9613
7692 | 19579.791 | 3.1849
7693 | 23049.8359 | 3.7187
7694 | 24343.207 | 4.1546
7695 | 26495.9453 | 4.8741
7696 | 27872.2305 | 5.1721
7697 | 27896.6211 | 5.6055
7698 | 28292.252 | 5.6192
7699 | 28197.2109 | 5.7459
7700 | 31445.6055 | 6.0269
7701 | 31827.6055 | 6.0226
7702 | 32764.0156 | 5.9749
7703 | 30932.9941 | 5.7707
7704 | 29941.4141 | 5.9559
7705 | 31150.3301 | 5.7294
7706 | 30152.6875 | 5.6365
7707 | 28500.9707 | 5.79
7708 | 29864.834 | 5.7317
7709 | 29792.0469 | 5.6084
7710 | 31106.9102 | 5.5198
7711 | 30283.2129 | 5.3897
7712 | 29790.3164 | 5.2839
7713 | 29917.3926 | 5.0334
7714 | 28914.1699 | 4.6658
7715 | 26909.0508 | 4.6239
7716 | 25610.2617 | 4.5807
7717 | 24381.3008 | 4.645
7718 | 23940.9121 | 4.4279
7719 | 24885.1855 | 4.4173
7720 | 25588.8594 | 4.3158
7721 | 24870.9336 | 4.1396
7722 | 22669.3086 | 4.0544
7723 | 20694.834 | 4.0843
7724 | 19023.9883 | 3.6189
7725 | 17362.7773 | 3.2738
7726 | 16601.1035 | 3.0373
7727 | 16015.9551 | 2.7933
7728 | 15531.0586 | 2.6492
7729 | 14814.5762 | 2.6031
7730 | 14561.0811 | 2.4474
7731 | 14142.9238 | 2.487
7732 | 14000.5527 | 2.4347
7733 | 13656.373 | 2.5003
7734 | 13919.0996 | 2.3904
7735 | 13850.2793 | 2.4369
7736 | 13771.8691 | 2.5597
7737 | 13897.3203 | 2.7024
7738 | 14591.0479 | 2.7421
7739 | 15403.8496 | 2.855
7740 | 18492.873 | 3.1083
7741 | 20485.4219 | 3.5973
7742 | 22579.0039 | 4.101
7743 | 24654.2676 | 4.6264
7744 | 26102.0918 | 5.0159
7745 | 26775.6836 | 5.5299
7746 | 26805.5234 | 5.7717
7747 | 27669.8848 | 5.8372
7748 | 27867.9375 | 5.893
7749 | 27592.9277 | 5.9249
7750 | 28156.8965 | 5.9663
7751 | 27552.7051 | 5.9825
7752 | 27634.0332 | 6.0266
7753 | 27766.4629 | 5.9801
7754 | 27515.5469 | 5.7214
7755 | 27468.5664 | 5.4101
7756 | 25938.3672 | 5.2188
7757 | 26069.3047 | 5.2504
7758 | 26098.9258 | 5.0644
7759 | 25821.377 | 4.9812
7760 | 25439.7559 | 4.6613
7761 | 25498.4824 | 4.6098
7762 | 25349.3867 | 4.4772
7763 | 24547.7129 | 4.3928
7764 | 24562.3555 | 4.223
7765 | 24343.0898 | 4.1877
7766 | 23990.0586 | 3.9947
7767 | 24549.0898 | 3.9468
7768 | 24089.4375 | 3.8401
7769 | 22907.9961 | 3.8747
7770 | 21227.0352 | 3.5569
7771 | 19195.5488 | 3.4729
7772 | 18267.5059 | 3.1362
7773 | 17187.0527 | 2.9641
7774 | 16362.502 | 2.6276
7775 | 15708.7344 | 2.6243
7776 | 15254.2285 | 2.5688
7777 | 14642.8711 | 2.5155
7778 | 14031.1973 | 2.4427
7779 | 13706.1641 | 2.4364
7780 | 13589.4062 | 2.3807
7781 | 13108.668 | 2.3439
7782 | 12904.9297 | 2.2822
7783 | 13296.3096 | 1.9451
7784 | 14504.4902 | 1.9068
7785 | 13965.8457 | 1.9732
7786 | 13746.0781 | 1.9462
7787 | 13319.4355 | 2.0808
7788 | 14354.3535 | 2.0567
7789 | 14601.3848 | 2.2666
7790 | 15617.1738 | 2.4086
7791 | 16502.9648 | 2.8281
7792 | 18088.209 | 3.1106
7793 | 19395.5273 | 3.4388
7794 | 21201.9395 | 3.7604
7795 | 23026.7598 | 3.8895
7796 | 23123.7305 | 3.9667
7797 | 22724.9414 | 3.9788
7798 | 22641.5625 | 3.8057
7799 | 22519.9316 | 3.83
7800 | 22453.6777 | 3.8483
7801 | 22306.2969 | 3.805
7802 | 22100.3926 | 3.8633
7803 | 22347.3086 | 3.8979
7804 | 22235.4902 | 3.852
7805 | 21914.0469 | 3.8746
7806 | 20971.0977 | 3.8777
7807 | 19489.8223 | 3.6514
7808 | 19403.4746 | 3.6839
7809 | 19675.3066 | 3.7887
7810 | 19779.5371 | 3.4876
7811 | 19404.0312 | 3.3908
7812 | 19363.8418 | 3.5124
7813 | 19483.3906 | 3.3917
7814 | 19352.7695 | 3.1458
7815 | 19666.2852 | 3.0349
7816 | 18620.8418 | 3.1243
7817 | 17076.3867 | 2.9469
7818 | 16213.7012 | 2.6986
7819 | 15613.9336 | 2.83
7820 | 15105.5215 | 2.9715
7821 | 14663.2461 | 2.7353
7822 | 13962.9727 | 2.434
7823 | 13498.4238 | 2.3838
7824 | 12796.5195 | 2.4384
7825 | 12282.1289 | 2.0821
7826 | 12004.3379 | 2.0186
7827 | 11723.832 | 2.0006
7828 | 11553.1172 | 1.9333
7829 | 11254.0137 | 1.9038
7830 | 11106.8672 | 1.7962
7831 | 11087.002 | 1.779
7832 | 10983.3926 | 1.8342
7833 | 10971.9258 | 2.053
7834 | 11136.5273 | 2.0208
7835 | 11185.9258 | 2.0889
7836 | 11738.2969 | 2.017
7837 | 12387.6016 | 1.8514
7838 | 12982.2656 | 2.0252
7839 | 13313.3184 | 2.2095
7840 | 14575.4375 | 2.5946
7841 | 15235.0596 | 2.5337
7842 | 16577.3008 | 2.7776
7843 | 17075.5977 | 2.8184
7844 | 17964.3262 | 3.0812
7845 | 18929.8008 | 3.2815
7846 | 19684.3496 | 3.1794
7847 | 20297.3926 | 3.2546
7848 | 20350.6562 | 3.4145
7849 | 20405.0977 | 3.4477
7850 | 20334.3691 | 3.3978
7851 | 19607.9824 | 3.3578
7852 | 19766.9902 | 3.2357
7853 | 19962.5918 | 3.1486
7854 | 19832.6758 | 3.3022
7855 | 19525.7383 | 3.2341
7856 | 19384.6855 | 3.2234
7857 | 19408.8438 | 3.2182
7858 | 18376.6934 | 3.2648
7859 | 17177.7656 | 3.2955
7860 | 16597.082 | 3.0721
7861 | 16350.9336 | 2.8578
7862 | 16518.25 | 2.7863
7863 | 17182.0195 | 2.758
7864 | 17676.4102 | 2.6848
7865 | 17148.0195 | 2.7083
7866 | 16571.4922 | 2.6785
7867 | 15942.6914 | 2.7057
7868 | 15273.8906 | 2.7362
7869 | 14402.6055 | 2.5622
7870 | 13849.2041 | 2.6609
7871 | 13358.1719 | 2.5185
7872 | 12910.54 | 2.3892
7873 | 12605.0664 | 2.192
7874 | 12343.5732 | 1.9356
7875 | 12146.6777 | 1.9383
7876 | 11885.0234 | 1.9162
7877 | 11662.2881 | 1.8816
7878 | 11691.2979 | 1.8765
7879 | 11756.0859 | 1.8558
7880 | 11896.4766 | 1.797
7881 | 11738.2852 | 1.7854
7882 | 12725.8438 | 1.8406
7883 | 14346.4893 | 2.1981
7884 | 17564.0078 | 2.4066
7885 | 19235.9902 | 3.2361
7886 | 21479.3594 | 3.7827
7887 | 23215.2266 | 4.439
7888 | 25344.6914 | 4.8883
7889 | 27479.5664 | 5.5459
7890 | 27495.5664 | 5.8066
7891 | 27593.2207 | 5.8106
7892 | 29386.6426 | 5.9772
7893 | 30280.9492 | 6.1162
7894 | 30820.6777 | 6.0556
7895 | 29058.1484 | 6.0635
7896 | 29818.9902 | 6.0324
7897 | 29074.2852 | 5.8563
7898 | 29701.1387 | 5.8052
7899 | 29593.3711 | 5.6007
7900 | 26749.4727 | 5.512
7901 | 27352.5059 | 5.5143
7902 | 26128.6621 | 5.6827
7903 | 26411.7988 | 5.7161
7904 | 26712.1035 | 5.7609
7905 | 26691.7891 | 5.4617
7906 | 26571.8203 | 5.1534
7907 | 26182.1875 | 4.8984
7908 | 26383.3145 | 4.7252
7909 | 26350.8086 | 4.672
7910 | 26511.1777 | 4.3456
7911 | 26759.4512 | 4.1554
7912 | 26521.6816 | 4.1824
7913 | 25663.3867 | 4.2317
7914 | 22612.457 | 3.9661
7915 | 20667.6133 | 3.8212
7916 | 19199.918 | 3.5982
7917 | 17952.957 | 3.418
7918 | 17175.418 | 3.1427
7919 | 16680.5254 | 2.9896
7920 | 15912.25 | 2.8941
7921 | 15391.7227 | 2.843
7922 | 14944.9863 | 2.7255
7923 | 14518.9648 | 2.7536
7924 | 14403.7012 | 2.7223
7925 | 14234.7129 | 2.7162
7926 | 14168.1426 | 2.6819
7927 | 13969.4785 | 2.7256
7928 | 13980.3301 | 2.7855
7929 | 13950.7822 | 2.9539
7930 | 14694.9629 | 2.9878
7931 | 15914.1338 | 2.884
7932 | 19762.9688 | 3.1171
7933 | 21235.6641 | 3.4865
7934 | 23180.0781 | 3.8987
7935 | 26468.6504 | 4.6195
7936 | 27268.1875 | 5.168
7937 | 29001.1484 | 5.4994
7938 | 30093.2344 | 5.7699
7939 | 30957.2773 | 5.6372
7940 | 31460.1719 | 5.8174
7941 | 31624.4453 | 6.014
7942 | 32399.3516 | 6.0807
7943 | 32737.9727 | 6.1448
7944 | 34220.7227 | 5.9147
7945 | 31885.3945 | 5.8529
7946 | 33330.8281 | 5.7655
7947 | 33828.1836 | 5.5973
7948 | 32334.4492 | 5.4266
7949 | 32147.0371 | 5.4792
7950 | 30803.3398 | 5.4197
7951 | 29783.8047 | 5.2889
7952 | 28192.5684 | 5.2007
7953 | 26668.2305 | 5.1381
7954 | 26318.4629 | 4.7187
7955 | 26638.5781 | 4.4611
7956 | 26469.084 | 4.4421
7957 | 26782.5781 | 4.265
7958 | 26159.084 | 4.3565
7959 | 26613.7031 | 4.2659
7960 | 27213.8418 | 3.9745
7961 | 27364.8301 | 3.8391
7962 | 24948.7246 | 3.6345
7963 | 22049.5625 | 3.5333
7964 | 20822.2539 | 3.4807
7965 | 19943.4336 | 3.2565
7966 | 18251.0723 | 3.1892
7967 | 16860.1562 | 2.9188
7968 | 16190.8926 | 2.8003
7969 | 15597.9023 | 2.8632
7970 | 15107.6074 | 2.9249
7971 | 14820.0918 | 2.9857
7972 | 14474.0703 | 2.9217
7973 | 14151.0811 | 2.9129
7974 | 14301.5 | 2.8623
7975 | 14299.1318 | 2.7114
7976 | 14540.1426 | 2.4687
7977 | 14475.5 | 2.4474
7978 | 15029.291 | 2.6234
7979 | 16624.6191 | 2.9012
7980 | 20271.9395 | 3.155
7981 | 21518.0039 | 3.6198
7982 | 24076.8359 | 4.0177
7983 | 26972.6719 | 4.7477
7984 | 28129.3789 | 5.2559
7985 | 28449.3789 | 5.5379
7986 | 29148.5273 | 5.6494
7987 | 29300.5703 | 5.6336
7988 | 30940.8867 | 5.9549
7989 | 34674.8516 | 5.9679
7990 | 30565.3711 | 5.9078
7991 | 30342.9707 | 5.9508
7992 | 29426.8652 | 5.9218
7993 | 29866.2227 | 5.6114
7994 | 29310.9805 | 5.5551
7995 | 28195.1152 | 5.318
7996 | 28977.4004 | 5.295
7997 | 29302.7285 | 5.2006
7998 | 28698.6309 | 5.1884
7999 | 29227.4551 | 5.1097
8000 | 27567.7793 | 5.0379
8001 | 27097.1992 | 4.9387
8002 | 26560.0723 | 4.7102
8003 | 25446.4609 | 4.2954
8004 | 25845.502 | 4.1614
8005 | 25760.2617 | 4.3785
8006 | 26733.1094 | 4.2267
8007 | 26673.4863 | 4.2438
8008 | 26136.2832 | 4.2396
8009 | 25117.0703 | 3.8863
8010 | 23307.8574 | 3.7216
8011 | 21085.7285 | 3.8819
8012 | 19466.4004 | 3.6337
8013 | 18355.4629 | 3.4032
8014 | 17927.6934 | 3.2973
8015 | 16916.1348 | 3.021
8016 | 16115.5859 | 2.9254
8017 | 15727.4492 | 3.0454
8018 | 15175.4707 | 2.9135
8019 | 14879.4492 | 2.9405
8020 | 14644.1855 | 2.9185
8021 | 14454.5742 | 2.8987
8022 | 14288.6914 | 2.8958
8023 | 14349.6152 | 2.8895
8024 | 14647.0176 | 2.6126
8025 | 14744.2578 | 2.5986
8026 | 15128.5312 | 2.6623
8027 | 15940.5762 | 2.8915
8028 | 19722.0117 | 3.2092
8029 | 21438.9922 | 3.4129
8030 | 24473.2793 | 3.9112
8031 | 27497.5664 | 4.6578
8032 | 29943.9492 | 5.1777
8033 | 30411.6016 | 5.7769
8034 | 29950.4531 | 5.9698
8035 | 30245.4648 | 5.9498
8036 | 31864.9297 | 6.0088
8037 | 32951.8672 | 6.1448
8038 | 32466.2578 | 6.1049
8039 | 31639.5723 | 6.1112
8040 | 31547.3301 | 6.1065
8041 | 31905.9531 | 6.0469
8042 | 30829.3301 | 5.8603
8043 | 33039.8398 | 5.7523
8044 | 31089.6152 | 5.7846
8045 | 29510.3828 | 5.6638
8046 | 30650.877 | 5.7649
8047 | 31308.7109 | 5.5907
8048 | 30300.1719 | 5.3327
8049 | 28015.0312 | 5.0506
8050 | 26613.9785 | 5.0045
8051 | 27115.9785 | 4.8059
8052 | 25481.6621 | 4.6697
8053 | 25643.6406 | 4.647
8054 | 25781.5254 | 4.393
8055 | 26137.5449 | 4.452
8056 | 26370.7871 | 4.1563
8057 | 25480.998 | 3.9251
8058 | 23281.375 | 4.0207
8059 | 20810.7402 | 3.8378
8060 | 18957.2734 | 3.7558
8061 | 17998.7266 | 3.5007
8062 | 17085.168 | 3.2016
8063 | 16579.1445 | 2.9135
8064 | 16005.8828 | 2.8222
8065 | 15421.3984 | 2.8381
8066 | 14737.1035 | 2.8732
8067 | 14335.0605 | 2.8913
8068 | 14131.0371 | 2.8661
8069 | 13998.7129 | 2.858
8070 | 14086.373 | 2.842
8071 | 13835.8691 | 2.7092
8072 | 13805.7305 | 2.535
8073 | 13861.9844 | 2.5524
8074 | 13975.4668 | 2.632
8075 | 15078.5312 | 2.9088
8076 | 19210.3789 | 3.0941
8077 | 20598.832 | 3.5667
8078 | 22464.8027 | 4.1189
8079 | 24219.0059 | 4.7038
8080 | 26008.2383 | 5.2518
8081 | 26639.5234 | 5.6338
8082 | 26830.5352 | 5.8685
8083 | 27961.1035 | 5.8857
8084 | 29150.2734 | 6.1157
8085 | 29238.5273 | 6.0259
8086 | 30579.3711 | 6.116
8087 | 29662.9375 | 5.9123
8088 | 29879.3594 | 5.8526
8089 | 29545.4863 | 5.7625
8090 | 29422.8223 | 6.0399
8091 | 28926.8945 | 5.8955
8092 | 27021.8828 | 5.8244
8093 | 25999.3652 | 5.7043
8094 | 25635.166 | 5.5916
8095 | 25358.0488 | 5.3909
8096 | 25233.8184 | 5.2518
8097 | 25086.0078 | 4.9011
8098 | 23948.3633 | 4.6469
8099 | 23390.2266 | 4.5788
8100 | 23610.1094 | 4.5497
8101 | 23465.6055 | 4.4352
8102 | 23571.9727 | 4.1406
8103 | 24009.5312 | 3.9807
8104 | 23519.2383 | 3.8387
8105 | 22513.6777 | 3.8271
8106 | 20854.9492 | 3.8344
8107 | 18687.8516 | 3.8104
8108 | 17178.2715 | 3.6855
8109 | 16365.8398 | 3.4301
8110 | 15793.5645 | 3.1043
8111 | 15148.1445 | 2.8861
8112 | 14431.8906 | 2.8633
8113 | 13900.2578 | 2.4948
8114 | 13114.9727 | 2.3938
8115 | 13049.2266 | 2.4044
8116 | 12884.3945 | 2.1244
8117 | 12650.793 | 2.0019
8118 | 12579.8984 | 1.9812
8119 | 12707.5078 | 1.9988
8120 | 12849.2773 | 1.8798
8121 | 12760.9082 | 1.8453
8122 | 12763.0234 | 1.8893
8123 | 12351.3711 | 2.0644
8124 | 13768.6445 | 2.347
8125 | 14380.8574 | 2.349
8126 | 15176.2793 | 2.3111
8127 | 16896.7559 | 2.7689
8128 | 19079.1836 | 3.1108
8129 | 19744.0762 | 3.5163
8130 | 20806.8984 | 3.7643
8131 | 21266.1406 | 3.8155
8132 | 21601.4766 | 3.9081
8133 | 21603.7715 | 3.9762
8134 | 22078.1172 | 3.9885
8135 | 22227.0898 | 4.0428
8136 | 21871.1074 | 3.9875
8137 | 21816.1836 | 3.7865
8138 | 22180.2656 | 3.7795
8139 | 20280.0762 | 3.6471
8140 | 19964.6641 | 3.6572
8141 | 20012.6641 | 3.6241
8142 | 20107.2461 | 3.544
8143 | 20082.8945 | 3.5417
8144 | 20018.7695 | 3.4973
8145 | 20181.2266 | 3.387
8146 | 20177.4727 | 3.2445
8147 | 19740.7266 | 3.236
8148 | 19394.543 | 3.1643
8149 | 19298.7188 | 3.1491
8150 | 19509.8945 | 3.065
8151 | 19938.5605 | 2.9373
8152 | 18803.0938 | 3.1341
8153 | 17423.5352 | 3.0465
8154 | 16377.4707 | 2.9747
8155 | 15573.0605 | 2.7667
8156 | 14986.6484 | 2.7183
8157 | 14306.2168 | 2.5911
8158 | 13790.4453 | 2.495
8159 | 13222.54 | 2.3793
8160 | 12609.1406 | 2.1285
8161 | 12057.3477 | 2.0584
8162 | 11809.9707 | 1.9776
8163 | 11448.0137 | 1.9622
8164 | 11094.3809 | 1.904
8165 | 10968.8672 | 1.8947
8166 | 10774.2227 | 2.1481
8167 | 10661.6016 | 1.9845
8168 | 10734.9824 | 1.6566
8169 | 10602.8145 | 1.6512
8170 | 10697.7383 | 1.6407
8171 | 11020.2969 | 2.0155
8172 | 12166.2441 | 1.8838
8173 | 12560.2461 | 1.9968
8174 | 12964.4043 | 2.2766
8175 | 13604.6045 | 2.3753
8176 | 14718.9941 | 2.2933
8177 | 15733.3008 | 2.5614
8178 | 16938.8477 | 2.7652
8179 | 17573.3672 | 3.0691
8180 | 18676.252 | 3.1844
8181 | 19624.8438 | 3.314
8182 | 20357.8555 | 3.2836
8183 | 20574.5078 | 3.4831
8184 | 21523.8047 | 3.3686
8185 | 20862.0664 | 3.4197
8186 | 20606.002 | 3.3899
8187 | 20391.8223 | 3.368
8188 | 20156.4863 | 3.2317
8189 | 19936.498 | 3.3199
8190 | 19967.8242 | 3.4303
8191 | 19959.7617 | 3.2492
8192 | 19652.5488 | 3.2024
8193 | 19676.8965 | 3.2203
8194 | 18491.5586 | 3.1376
8195 | 17319.293 | 3.2316
8196 | 16817.0293 | 2.9646
8197 | 17036.5234 | 2.9276
8198 | 16810.8711 | 2.8939
8199 | 17470.041 | 3.0548
8200 | 17179.5352 | 3.047
8201 | 16838.5039 | 3.0007
8202 | 16489.8613 | 2.9796
8203 | 15493.1953 | 2.9209
8204 | 14869.0176 | 2.6693
8205 | 14473.8672 | 2.4765
8206 | 14052.4688 | 2.4184
8207 | 13405.5723 | 2.1681
8208 | 13015.1826 | 2.0378
8209 | 12607.2773 | 1.9867
8210 | 12460.1504 | 1.9174
8211 | 11976.75 | 1.96
8212 | 11891.6016 | 1.9227
8213 | 11802.9824 | 1.9185
8214 | 11650.5586 | 1.9723
8215 | 11768.6133 | 2.2051
8216 | 11887.0664 | 2.1587
8217 | 11919.2129 | 2.0996
8218 | 12660.3828 | 1.9572
8219 | 14118.2051 | 2.4361
8220 | 17450.7988 | 2.4839
8221 | 19347.8125 | 3.1796
8222 | 21484.8652 | 3.6765
8223 | 22765.0879 | 4.4398
8224 | 24757.0488 | 4.9638
8225 | 27349.9355 | 5.3911
8226 | 28790.1367 | 5.3821
8227 | 28797.4004 | 5.3969
8228 | 29886.2012 | 5.5782
8229 | 31086.0137 | 5.5489
8230 | 29519.1914 | 5.554
8231 | 29089.9062 | 5.4702
8232 | 29990.0859 | 5.4903
8233 | 29538.4336 | 5.5502
8234 | 29543.3281 | 5.441
8235 | 28040.5996 | 5.2924
8236 | 28060.8516 | 5.2383
8237 | 28306.7363 | 4.8865
8238 | 28035.1055 | 4.9075
8239 | 28942.043 | 4.9688
8240 | 26773.8203 | 4.8561
8241 | 26177.8926 | 4.6219
8242 | 25807.3652 | 4.2483
8243 | 25242.4492 | 4.1055
8244 | 25505.3438 | 3.9605
8245 | 25381.2285 | 4.0427
8246 | 25464.9766 | 3.7313
8247 | 26143.3652 | 3.6864
8248 | 25839.9863 | 3.6892
8249 | 25023.1855 | 3.285
8250 | 23058.0879 | 3.2197
8251 | 20743.4531 | 3.3874
8252 | 19175.6211 | 3.2335
8253 | 18411.5781 | 3.0259
8254 | 17511.5352 | 2.9846
8255 | 16556.2285 | 2.5979
8256 | 16075.2188 | 2.4537
8257 | 15727.376 | 2.6308
8258 | 15339.8594 | 2.4247
8259 | 14713.9336 | 2.3664
8260 | 14755.7012 | 2.336
8261 | 14912.0918 | 2.3091
8262 | 14696.9238 | 2.3116
8263 | 14657.3848 | 2.3751
8264 | 14960.7637 | 2.2008
8265 | 15010.6484 | 2.3046
8266 | 15225.9121 | 2.3517
8267 | 17337.5137 | 2.6198
8268 | 21074.7188 | 2.7937
8269 | 23021.3301 | 3.2192
8270 | 25440.5859 | 3.8108
8271 | 27169.293 | 4.4618
8272 | 27808.5781 | 5.0391
8273 | 28992.0215 | 5.2886
8274 | 30746.6133 | 5.4661
8275 | 29829.8125 | 5.4099
8276 | 30719.0039 | 5.5463
8277 | 31755.9512 | 5.7705
8278 | 30915.3926 | 5.6619
8279 | 30232.2344 | 5.7402
8280 | 30031.9707 | 5.7462
8281 | 31209.9199 | 5.5169
8282 | 30394.9824 | 5.4243
8283 | 28268.3242 | 5.4182
8284 | 28146.9668 | 5.1869
8285 | 27793.8418 | 5.3395
8286 | 27862.2305 | 5.1574
8287 | 26638.5352 | 5.2061
8288 | 26405.7773 | 5.0371
8289 | 26222.293 | 5.0244
8290 | 25703.8496 | 4.7099
8291 | 24979.3223 | 4.5347
8292 | 25129.3223 | 4.1712
8293 | 25247.0918 | 4.0866
8294 | 26056.998 | 3.9271
8295 | 26273.6172 | 3.8556
8296 | 25654.8594 | 3.9632
8297 | 24726.4277 | 3.7187
8298 | 22992.457 | 3.4324
8299 | 21249.4961 | 3.3853
8300 | 19597.3906 | 3.3617
8301 | 18494.3145 | 3.0404
8302 | 17767.7871 | 2.8102
8303 | 17156.502 | 2.875
8304 | 16228.7129 | 2.5746
8305 | 16108.9863 | 2.657
8306 | 15430.1133 | 2.6657
8307 | 15067.7012 | 2.6956
8308 | 14881.0811 | 2.5622
8309 | 14888.4805 | 2.3012
8310 | 14914.1445 | 2.2561
8311 | 14693.8672 | 2.3187
8312 | 14776.2578 | 2.2995
8313 | 14749.3848 | 2.4125
8314 | 15192.6484 | 2.4302
8315 | 16029.6582 | 2.7252
8316 | 19618.6641 | 2.9626
8317 | 21990.6445 | 3.4106
8318 | 24305.3945 | 3.6853
8319 | 25946.6074 | 4.2767
8320 | 27397.5469 | 5.0009
8321 | 30200.707 | 5.2985
8322 | 31626.5391 | 5.3972
8323 | 31833.2988 | 5.4748
8324 | 33316.1445 | 5.4161
8325 | 34653.9531 | 5.4736
8326 | 33992.4609 | 5.2259
8327 | 32983.2148 | 5.1663
8328 | 32757.9512 | 5.1666
8329 | 30699.1719 | 5.1745
8330 | 30807.4453 | 5.0429
8331 | 29719.2773 | 5.1376
8332 | 29635.8672 | 5.0624
8333 | 29698.8438 | 5.1591
8334 | 30800.3496 | 5.0088
8335 | 29035.4434 | 5.0492
8336 | 28623.5371 | 5.2042
8337 | 28572.2969 | 5.037
8338 | 27073.6836 | 4.73
8339 | 26126.6504 | 4.6809
8340 | 26074.8828 | 4.397
8341 | 26135.3867 | 4.2706
8342 | 26310.0293 | 4.0294
8343 | 26236.7676 | 4.0065
8344 | 26486.2812 | 4.0866
8345 | 26252.7656 | 3.7386
8346 | 24553.1855 | 3.6353
8347 | 22450.6875 | 3.515
8348 | 21151.8652 | 3.4445
8349 | 19872.3066 | 3.2557
8350 | 19194.7695 | 3.1633
8351 | 18644.8848 | 2.96
8352 | 17813.7793 | 2.9158
8353 | 16678.5664 | 2.7797
8354 | 16052.7773 | 2.6433
8355 | 15755.7676 | 2.5999
8356 | 15842.9141 | 2.6052
8357 | 15400.8281 | 2.5945
8358 | 14893.5215 | 2.5401
8359 | 14630.8789 | 2.4716
8360 | 14430.7422 | 2.624
8361 | 14472.0059 | 2.6591
8362 | 15027.4062 | 2.6663
8363 | 15733.5664 | 2.9182
8364 | 19387.1367 | 3.0531
8365 | 21491.6133 | 3.5182
8366 | 23311.8594 | 4.0668
8367 | 26678.5352 | 4.7611
8368 | 28057.6094 | 5.005
8369 | 28267.3789 | 5.3103
8370 | 29143.5371 | 5.5698
8371 | 28413.0215 | 5.6931
8372 | 29332.7285 | 5.6114
8373 | 30338.2656 | 5.6394
8374 | 28407.0645 | 5.5526
8375 | 28169.7676 | 5.6174
8376 | 28246.7461 | 5.632
8377 | 28248.3789 | 5.6088
8378 | 28236.8535 | 5.5069
8379 | 27678.9258 | 5.5241
8380 | 27590.3359 | 5.5014
8381 | 27600.8516 | 5.3424
8382 | 27250.7246 | 5.4161
8383 | 26325.2812 | 5.3764
8384 | 25952.7344 | 5.4154
8385 | 25918.8809 | 5.2207
8386 | 25540.8594 | 5.0467
8387 | 24584.4277 | 4.8495
8388 | 25027.207 | 4.7568
8389 | 25046.7031 | 4.5644
8390 | 25787.7324 | 4.2699
8391 | 26101.7539 | 4.3143
8392 | 25916.377 | 4.1807
8393 | 24363.0273 | 4.0735
8394 | 23043.6992 | 3.8086
8395 | 21315.8652 | 3.4574
8396 | 19541.8945 | 3.4801
8397 | 18229.4414 | 3.3857
8398 | 17319.2812 | 3.1569
8399 | 16851.9961 | 3.063
8400 | 16246.8281 | 2.7592
8401 | 15736.4395 | 2.9277
8402 | 15239.0371 | 2.8412
8403 | 14871.5664 | 2.5777
8404 | 14686.6914 | 2.5796
8405 | 14480.416 | 2.5309
8406 | 14509.9551 | 2.5097
8407 | 14171.1758 | 2.4903
8408 | 14050.4688 | 2.4135
8409 | 14159.9619 | 2.5778
8410 | 14736.8789 | 2.6031
8411 | 15507.9111 | 2.829
8412 | 18915.2422 | 3.0947
8413 | 21490.1172 | 3.5435
8414 | 23156.0664 | 4.017
8415 | 25616.5859 | 4.7361
8416 | 26671.2715 | 5.3211
8417 | 26796.2617 | 5.5628
8418 | 26993.084 | 5.5225
8419 | 28840.875 | 5.7145
8420 | 28851.252 | 5.8634
8421 | 29418.5703 | 5.9665
8422 | 29444.6016 | 5.9422
8423 | 28797.6094 | 6.0148
8424 | 28716.959 | 5.7464
8425 | 27471.0625 | 5.8667
8426 | 27282.5684 | 5.9183
8427 | 27100.9785 | 5.5278
8428 | 25754.5449 | 5.1778
8429 | 24727.4492 | 4.9617
8430 | 25058.8711 | 5.0647
8431 | 24577.8281 | 5.1072
8432 | 24688.1953 | 5.1369
8433 | 24238.7969 | 4.9947
8434 | 23578.6484 | 4.5479
8435 | 22766.709 | 4.31
8436 | 23154.3633 | 4.26
8437 | 23166.8672 | 4.2938
8438 | 24070.0176 | 4.0584
8439 | 23853.7637 | 4.0442
8440 | 23467.2363 | 3.7974
8441 | 22509.0566 | 3.6406
8442 | 20878.7188 | 3.6392
8443 | 19146.8633 | 3.6743
8444 | 17753.0508 | 3.4116
8445 | 16407.3555 | 3.0577
8446 | 15711.5664 | 2.7945
8447 | 15112.9004 | 2.6159
8448 | 14555.8906 | 2.5882
8449 | 13962.165 | 2.4691
8450 | 13474.7422 | 2.309
8451 | 12985.5938 | 2.3118
8452 | 12846.8379 | 2.2953
8453 | 12427.0898 | 2.2535
8454 | 12230.1504 | 2.146
8455 | 12063.0957 | 2.1973
8456 | 12142.9805 | 2.3429
8457 | 12090.8652 | 2.1426
8458 | 12144.5586 | 2.126
8459 | 12193.9395 | 2.2972
8460 | 13479.6348 | 2.3491
8461 | 13962.9844 | 2.382
8462 | 14986.7207 | 2.4979
8463 | 15878.9121 | 2.7313
8464 | 17672.3262 | 3.2646
8465 | 18872.6426 | 3.4008
8466 | 19542.7383 | 3.7887
8467 | 20373.0312 | 3.8497
8468 | 20657.8438 | 3.7774
8469 | 20586.6465 | 3.8105
8470 | 20627.2559 | 3.8135
8471 | 20752.7617 | 3.8132
8472 | 20746.4863 | 3.8223
8473 | 20912.3496 | 3.9549
8474 | 20758.1289 | 3.7907
8475 | 20283.6758 | 3.7879
8476 | 19534.2227 | 3.728
8477 | 19703.6758 | 3.8158
8478 | 19854.875 | 3.7846
8479 | 19847.2852 | 3.7936
8480 | 19481.7695 | 3.7901
8481 | 19473.3906 | 3.6952
8482 | 19484.8125 | 3.5478
8483 | 19576.1914 | 3.3537
8484 | 19729.5703 | 3.0658
8485 | 19823.6855 | 3.1526
8486 | 20264.3496 | 3.1436
8487 | 20017.3164 | 3.1792
8488 | 18696.6523 | 3.013
8489 | 17048.1777 | 2.7611
8490 | 15926.7344 | 2.646
8491 | 15217.8184 | 2.6742
8492 | 14628.416 | 2.6844
8493 | 14014.373 | 2.5862
8494 | 13461.8457 | 2.6239
8495 | 12879.8037 | 2.1988
8496 | 12356.2871 | 2.0849
8497 | 12005.0459 | 2.1235
8498 | 11660.1934 | 2.2635
8499 | 11391.7832 | 2.2715
8500 | 11163.7617 | 2.2006
8501 | 10966.3828 | 2.1002
8502 | 10777.2773 | 2.0873
8503 | 10950.4336 | 2.0918
8504 | 11239.9492 | 1.7439
8505 | 11758.4766 | 1.5638
8506 | 12686.5195 | 1.5945
8507 | 12994.541 | 1.8919
8508 | 14085.9844 | 2.1416
8509 | 14983.1523 | 1.8638
8510 | 15493.4277 | 2.0072
8511 | 15979.8398 | 2.2505
8512 | 16762.9863 | 2.1978
8513 | 17381.7051 | 2.5565
8514 | 18424.6836 | 2.8131
8515 | 18983.0938 | 3.0936
8516 | 19697.9883 | 3.2908
8517 | 20814.5078 | 3.3023
8518 | 20871.666 | 3.2056
8519 | 21236.5625 | 3.2735
8520 | 21546.832 | 3.5264
8521 | 21194.4434 | 3.7431
8522 | 20553.6348 | 3.6439
8523 | 19506.834 | 3.1577
8524 | 19451.3691 | 3.1795
8525 | 19279.2109 | 3.1711
8526 | 19178.6328 | 3.0461
8527 | 19198.3906 | 3.1822
8528 | 18889.4629 | 3.2022
8529 | 18721.6641 | 3.1153
8530 | 18029.5781 | 3.0318
8531 | 16722.2285 | 2.8501
8532 | 15984.9648 | 2.8248
8533 | 16222.9648 | 2.8371
8534 | 17089.1445 | 2.9433
8535 | 17233.3984 | 2.9956
8536 | 17053.8828 | 2.9574
8537 | 16811.2383 | 2.944
8538 | 16679.7227 | 2.9145
8539 | 16017.5645 | 2.941
8540 | 15553.291 | 2.645
8541 | 14477.6152 | 2.3968
8542 | 13922.0781 | 2.4213
8543 | 13487.8037 | 2.105
8544 | 12987.8984 | 1.9886
8545 | 12349.666 | 1.9621
8546 | 12386.4453 | 1.8978
8547 | 11994.5391 | 1.9369
8548 | 11559.2559 | 1.8762
8549 | 11212.6133 | 1.8487
8550 | 11294.3828 | 1.8424
8551 | 11457.2109 | 1.8772
8552 | 11672.8984 | 1.9943
8553 | 11804.1582 | 2.1798
8554 | 11968.8008 | 2.1442
8555 | 12908.6133 | 2.1491
8556 | 16947.2402 | 2.3866
8557 | 19382.6934 | 3.0007
8558 | 21351.3926 | 3.4713
8559 | 23125.0137 | 3.9747
8560 | 24953.5762 | 4.6458
8561 | 26915.8711 | 4.9957
8562 | 28408.8301 | 5.2657
8563 | 27959.1992 | 5.327
8564 | 28002.4629 | 5.3381
8565 | 28835.6328 | 5.3732
8566 | 28251.3574 | 5.5318
8567 | 28328.8516 | 5.6182
8568 | 28719.8848 | 5.523
8569 | 29148.2734 | 5.3841
8570 | 29813.3711 | 5.0913
8571 | 29384.4219 | 5.1086
8572 | 29378.3906 | 5.0842
8573 | 29306.5488 | 5.0944
8574 | 27488.1875 | 4.9808
8575 | 27150.0508 | 4.9354
8576 | 27076.4199 | 4.8369
8577 | 26594.6504 | 4.8594
8578 | 26613.0195 | 4.5483
8579 | 26184.8828 | 4.3189
8580 | 26557.1562 | 4.199
8581 | 27132.6934 | 4.1546
8582 | 26898.9023 | 4.0674
8583 | 26823.7773 | 3.7268
8584 | 26761.1562 | 3.6343
8585 | 26280.377 | 3.6813
8586 | 24175.1426 | 3.6766
8587 | 22015.1504 | 3.5997
8588 | 20531.4531 | 3.4684
8589 | 18946.8633 | 3.154
8590 | 18247.9688 | 3.0028
8591 | 17431.3984 | 2.83
8592 | 16927.375 | 2.6306
8593 | 16192.04 | 2.4928
8594 | 15470.8926 | 2.4333
8595 | 14190.0391 | 2.4806
8596 | 14295.8281 | 2.4483
8597 | 14088.5312 | 2.4062
8598 | 13861.7949 | 2.3809
8599 | 14347.8672 | 2.402
8600 | 14380.2578 | 2.3309
8601 | 14291.0059 | 2.4335
8602 | 14430.709 | 2.4527
8603 | 16262.7949 | 2.7922
8604 | 20204.5059 | 3.0882
8605 | 22204.1094 | 3.2976
8606 | 24538.2168 | 3.5636
8607 | 26465.1445 | 4.1369
8608 | 28412.957 | 4.9053
8609 | 28630.3887 | 5.2835
8610 | 28393.5156 | 5.4871
8611 | 29728.4531 | 5.6178
8612 | 31968.4453 | 5.6429
8613 | 33129.3828 | 5.617
8614 | 30984.7715 | 5.6204
8615 | 31041.7285 | 5.5945
8616 | 31156.4473 | 5.6408
8617 | 31885.8359 | 5.6447
8618 | 31172.5195 | 5.3252
8619 | 29864.3594 | 5.3176
8620 | 28707.7793 | 5.4151
8621 | 28339.1699 | 5.442
8622 | 29434.9609 | 5.4753
8623 | 28857.5918 | 5.3424
8624 | 26909.7871 | 5.2059
8625 | 26151.8301 | 5.0206
8626 | 26520.3984 | 4.3972
8627 | 25286.8809 | 4.5407
8628 | 25576.125 | 4.4388
8629 | 26099.5234 | 4.2037
8630 | 26384.7871 | 4.0297
8631 | 26380.3984 | 3.9342
8632 | 26199.502 | 3.7676
8633 | 25542.1016 | 3.9786
8634 | 23590.2461 | 3.7436
8635 | 21561.8867 | 3.43
8636 | 20093.3164 | 3.3628
8637 | 18507.0938 | 3.149
8638 | 17490.9375 | 2.936
8639 | 16158.9648 | 2.856
8640 | 15561.7227 | 2.843
8641 | 15396.3652 | 2.6703
8642 | 15099.3555 | 2.4556
8643 | 14723.334 | 2.4895
8644 | 14433.1016 | 2.4584
8645 | 14028.7637 | 2.4197
8646 | 14013.7305 | 2.3852
8647 | 14138.6152 | 2.4375
8648 | 14273.1113 | 2.4865
8649 | 14373.457 | 2.4664
8650 | 14861.0801 | 2.5493
8651 | 15868.7734 | 2.7998
8652 | 19683.6738 | 3.0245
8653 | 21393.0352 | 3.2932
8654 | 23393.6484 | 3.6901
8655 | 26085.9551 | 4.3156
8656 | 26903.4746 | 4.9192
8657 | 26675.4082 | 5.4312
8658 | 28184 | 5.5089
8659 | 28155.7461 | 5.4725
8660 | 29881.7812 | 5.5848
8661 | 31482.6777 | 5.4956
8662 | 31841.3203 | 5.5668
8663 | 31526.668 | 5.5711
8664 | 31697.625 | 5.4934
8665 | 30012.8555 | 5.554
8666 | 30504.9297 | 5.3667
8667 | 29082.0859 | 5.4302
8668 | 29168.1074 | 5.2178
8669 | 30466.5625 | 5.2486
8670 | 30407.8984 | 5.1149
8671 | 29300.5508 | 5.2218
8672 | 27671.0645 | 5.1289
8673 | 27568.5586 | 4.9465
8674 | 27327.3809 | 4.562
8675 | 26423.1992 | 4.3978
8676 | 26138.0508 | 4.1327
8677 | 26630.7148 | 4.1656
8678 | 27940.4102 | 3.8696
8679 | 27080.9688 | 3.6994
8680 | 26215.1777 | 3.7044
8681 | 25205.1133 | 3.5794
8682 | 23277.0273 | 3.4193
8683 | 21223.9102 | 3.4697
8684 | 19400.8125 | 3.4673
8685 | 18137.4844 | 3.2857
8686 | 17828.8418 | 3.2819
8687 | 16839.0527 | 2.9034
8688 | 15895.1465 | 2.8003
8689 | 15448.1562 | 2.9255
8690 | 15058.1348 | 2.8351
8691 | 14549.4707 | 2.8955
8692 | 13870.3008 | 2.6511
8693 | 13900.8496 | 2.6033
8694 | 13939.2148 | 2.6166
8695 | 13925.0674 | 2.4304
8696 | 14333.1738 | 2.4088
8697 | 14403.3125 | 2.3797
8698 | 14954.1523 | 2.4057
8699 | 15605.3125 | 2.6672
8700 | 19108.918 | 2.841
8701 | 21401.0762 | 3.1049
8702 | 23041.8477 | 3.4959
8703 | 24262.1543 | 3.95
8704 | 26215.2715 | 4.6037
8705 | 26983.4297 | 5.0313
8706 | 27309.3145 | 5.1891
8707 | 27858.2422 | 5.4093
8708 | 28490.748 | 5.4467
8709 | 28485.6523 | 5.3862
8710 | 28380.7578 | 5.3319
8711 | 28352.0527 | 5.4249
8712 | 28277.3066 | 5.3407
8713 | 28702.5488 | 5.4444
8714 | 28034.4629 | 5.2781
8715 | 27615.957 | 5.0608
8716 | 26881.5059 | 5.0487
8717 | 26023.9766 | 4.9851
8718 | 26975.1035 | 5.1482
8719 | 26058.4727 | 5.2294
8720 | 27173.3359 | 5.1584
8721 | 26551.7988 | 5.1323
8722 | 25918.2617 | 5.0222
8723 | 25198.4707 | 4.7605
8724 | 25663.7324 | 4.6321
8725 | 25908.6074 | 4.4366
8726 | 26361.2715 | 4.3162
8727 | 26324.7676 | 4.4013
8728 | 26287.6406 | 4.313
8729 | 25445.8496 | 3.8338
8730 | 24163.8789 | 3.75
8731 | 22436.5508 | 3.5868
8732 | 20444.6973 | 3.5253
8733 | 18490.4727 | 3.4476
8734 | 17170.2715 | 3.015
8735 | 16217.8398 | 2.8397
8736 | 15458.5742 | 2.7978
8737 | 14776.6914 | 2.6967
8738 | 14339.543 | 2.5163
8739 | 14167.9121 | 2.5266
8740 | 13670.0488 | 2.4822
8741 | 13360.0781 | 2.4584
8742 | 13523.541 | 2.4512
8743 | 13543.8359 | 2.5468
8744 | 13844.752 | 2.3904
8745 | 13679.416 | 2.4964
8746 | 14411.4062 | 2.546
8747 | 15326.8066 | 2.851
8748 | 18473.166 | 3.1878
8749 | 21052.832 | 3.5278
8750 | 22728.8242 | 3.6446
8751 | 24428.0059 | 4.1186
8752 | 26155.5859 | 4.7101
8753 | 26671.3027 | 5.143
8754 | 27320.9902 | 5.1305
8755 | 28019.0723 | 5.3794
8756 | 28366.6641 | 5.4517
8757 | 29054.8633 | 5.2513
8758 | 29638.6855 | 5.1342
8759 | 28762.5488 | 5.2319
8760 | 28472.4941 | 5.362
8761 | 28736.3477 | 5.2094
8762 | 28136 | 5.0281
8763 | 27239.9141 | 4.8151
8764 | 25678.9453 | 4.9573
8765 | 25215.2188 | 4.9116
8766 | 25519.334 | 5.0006
8767 | 24999.3867 | 4.774
8768 | 25050.1445 | 4.4156
8769 | 25079.4062 | 4.2774
8770 | 24881.8281 | 4.0929
8771 | 23164.7305 | 4.0878
8772 | 23402.1113 | 3.8831
8773 | 23780.8906 | 3.6098
8774 | 24241.6484 | 3.6636
8775 | 23819.9961 | 3.457
8776 | 23308.1094 | 3.3531
8777 | 22198.8984 | 3.0628
8778 | 20177.918 | 3.1873
8779 | 18109.8086 | 3.1427
8780 | 16815.7441 | 2.993
8781 | 15912.9434 | 2.9184
8782 | 15222.0254 | 2.6454
8783 | 14623.8672 | 2.7102
8784 | 14327.3633 | 2.4187
8785 | 13903.8242 | 2.2601
8786 | 13323.7324 | 2.3447
8787 | 13125.7324 | 2.504
8788 | 12991.0898 | 2.4419
8789 | 12689.0684 | 2.3831
8790 | 12452.584 | 2.3368
8791 | 12122.9307 | 2.365
8792 | 12189.624 | 1.9962
8793 | 12217.8555 | 1.9771
8794 | 12173.3477 | 2.0182
8795 | 12303.6875 | 2.3434
8796 | 13683.584 | 2.0392
8797 | 14760.4902 | 2.3938
8798 | 15300.1445 | 2.4367
8799 | 16187.8184 | 2.7454
8800 | 17664.3457 | 3.1505
8801 | 18751.5469 | 3.3098
8802 | 19951.4941 | 3.6193
8803 | 20283.2754 | 3.717
8804 | 20417.127 | 3.848
8805 | 21110.7188 | 3.9225
8806 | 21075.5918 | 4.0077
8807 | 20855.9609 | 3.8974
8808 | 21116.7188 | 3.9013
8809 | 21203.4766 | 3.9681
8810 | 21033.5918 | 3.7099
8811 | 20782.9492 | 3.6025
8812 | 20353.4961 | 3.6581
8813 | 20034.0117 | 3.5893
8814 | 19979.707 | 3.4854
8815 | 19805.9062 | 3.3537
8816 | 19771.2227 | 3.4213
8817 | 19924.3477 | 3.489
8818 | 22028.5312 | 3.5086
8819 | 22367.0977 | 3.2216
8820 | 22546.918 | 3.1317
8821 | 22897.9297 | 3.2352
8822 | 22228.3926 | 2.9669
8823 | 21472.8555 | 3.0238
8824 | 19420.4961 | 2.9419
8825 | 17483.2617 | 2.7734
8826 | 16467.5859 | 2.61
8827 | 15464.165 | 2.6236
8828 | 14964.8789 | 2.6949
8829 | 14323.3418 | 2.6289
8830 | 13604.793 | 2.661
8831 | 12789.7598 | 2.3516
8832 | 12360.1289 | 2.2479
8833 | 11891.3926 | 2.3531
8834 | 11446.4961 | 2.0229
8835 | 11157.6016 | 2.0322
8836 | 11082.0137 | 1.9364
8837 | 10648.0859 | 1.8598
8838 | 10473.7695 | 1.7948
8839 | 10402 | 1.7535
8840 | 10590.1582 | 1.6339
8841 | 10357.2637 | 1.6192
8842 | 10662.7812 | 1.6072
8843 | 10755.4219 | 1.7183
8844 | 11772.2012 | 1.7844
8845 | 12445.2344 | 2.2413
8846 | 12903.0664 | 1.9957
8847 | 13395.2656 | 2.3572
8848 | 14429.1855 | 2.4057
8849 | 15411.8896 | 2.6912
8850 | 16386.2695 | 2.4869
8851 | 17221.2832 | 2.6096
8852 | 17961.998 | 2.9315
8853 | 18980.4941 | 2.9747
8854 | 19316.5898 | 3.0252
8855 | 19509.127 | 3.2764
8856 | 19993.8438 | 3.2743
8857 | 19894.4121 | 3.3592
8858 | 19834.5586 | 3.3749
8859 | 19941.1367 | 3.4048
8860 | 19849.0645 | 3.2632
8861 | 19480.4629 | 3.0507
8862 | 19673.8633 | 2.9209
8863 | 20099.623 | 2.9755
8864 | 19471.6211 | 2.9291
8865 | 19347.2734 | 2.9559
8866 | 18019.3867 | 2.9198
8867 | 16934.6172 | 2.8348
8868 | 16484.8496 | 2.7069
8869 | 16546.5977 | 2.6991
8870 | 19049.5996 | 2.5822
8871 | 18674.957 | 2.5957
8872 | 16946.3652 | 2.7298
8873 | 16374.5742 | 2.8275
8874 | 15842.3008 | 2.6641
8875 | 15070.1211 | 2.7904
8876 | 14597.7305 | 2.7261
8877 | 14307.7109 | 2.6489
8878 | 13953.0664 | 2.2913
8879 | 13442.0566 | 2.1475
8880 | 12917.7812 | 2.0013
8881 | 12623.6445 | 1.9953
8882 | 12256.3311 | 1.9273
8883 | 12032.2227 | 1.9507
8884 | 11904.4531 | 1.8878
8885 | 11948.3184 | 1.858
8886 | 11537.3047 | 2.1727
8887 | 11295.0527 | 2.2286
8888 | 11734.0645 | 2.1766
8889 | 11827.3281 | 2.1883
8890 | 12236.2227 | 2.2637
8891 | 13486.0352 | 2.1571
8892 | 17588.7012 | 2.5503
8893 | 20192.2617 | 3.0588
8894 | 22119.5195 | 3.6439
8895 | 24000.8789 | 4.0579
8896 | 27100.9453 | 4.7391
8897 | 27321.9141 | 5.3612
8898 | 27757.3145 | 5.3411
8899 | 28980.873 | 5.3708
8900 | 29336.5059 | 5.5366
8901 | 29386.7695 | 5.5474
8902 | 28765.1582 | 5.5646
8903 | 28120.8945 | 5.7833
8904 | 27400.9883 | 5.3818
8905 | 28015.7695 | 5.6829
8906 | 28469.5059 | 5.4122
8907 | 28215.5996 | 5.3559
8908 | 27071.1348 | 5.3192
8909 | 27163.377 | 5.3121
8910 | 27453.6504 | 5.2736
8911 | 27049.3359 | 5.2391
8912 | 25750.1348 | 5.212
8913 | 25689.2285 | 5.1042
8914 | 25231.5742 | 4.9752
8915 | 24634.7949 | 4.5277
8916 | 25156.4492 | 4.4823
8917 | 26328.2617 | 4.301
8918 | 26540.6504 | 4.0711
8919 | 26849.1562 | 4.0697
8920 | 26583.3887 | 4.0293
8921 | 24448.6387 | 3.7573
8922 | 22404.0469 | 3.6091
8923 | 20254.2852 | 3.7072
8924 | 18349.5781 | 3.5881
8925 | 17583.377 | 3.2555
8926 | 16437.5859 | 2.8776
8927 | 15923.7021 | 2.9508
8928 | 15503.1973 | 2.5689
8929 | 14920.5977 | 2.5748
8930 | 14830.8066 | 2.5269
8931 | 14320.9004 | 2.5031
8932 | 14341.29 | 2.451
8933 | 14130.8066 | 2.4468
8934 | 14024.2363 | 2.703
8935 | 13964.3311 | 2.555
8936 | 14485.1113 | 2.3613
8937 | 14294.0996 | 2.4799
8938 | 14872.9951 | 2.5987
8939 | 15996.5742 | 2.7952
8940 | 19509.4531 | 2.9054
8941 | 21567.2461 | 3.3848
8942 | 22999.8145 | 3.5581
8943 | 25375.6914 | 4.0955
8944 | 26534.6289 | 4.5207
8945 | 27179.9141 | 5.0473
8946 | 28461.6094 | 5.1686
8947 | 28963.7695 | 5.2635
8948 | 30368.3496 | 5.3464
8949 | 29269.959 | 5.5191
8950 | 29344.0547 | 5.5893
8951 | 29651.0527 | 5.3116
8952 | 30950.4141 | 5.4515
8953 | 29367.0957 | 5.3052
8954 | 28451.6641 | 5.3441
8955 | 29924.8555 | 5.2323
8956 | 30337.6953 | 5.2081
8957 | 29462.4746 | 5.2875
8958 | 28241.1387 | 5.2136
8959 | 27032.3789 | 5.0747
8960 | 26074.5977 | 5.0211
8961 | 26083.3867 | 5.0089
8962 | 25685.3652 | 4.7597
8963 | 25524.4922 | 4.5597
8964 | 25927.7539 | 4.3476
8965 | 26620.5352 | 4.3686
8966 | 26521.7773 | 4.2224
8967 | 26380.2617 | 3.9937
8968 | 26236.2617 | 3.9805
8969 | 24856.1758 | 3.8512
8970 | 23015.582 | 3.9859
8971 | 20446.6953 | 3.9646
8972 | 19134.3789 | 3.7652
8973 | 18432.7266 | 3.2734
8974 | 17503.2812 | 3.0454
8975 | 16789.8828 | 2.8388
8976 | 16326.7344 | 2.7273
8977 | 15764.25 | 2.8502
8978 | 15223.2383 | 2.8186
8979 | 14764.5312 | 2.6777
8980 | 14472.1445 | 2.6625
8981 | 14449.7529 | 2.6391
8982 | 14156.6035 | 2.5972
8983 | 13875.0889 | 2.6356
8984 | 14050.6055 | 2.5143
8985 | 13982.4688 | 2.6265
8986 | 14820.2578 | 2.7416
8987 | 15931.0811 | 2.9142
8988 | 19410.125 | 3.1707
8989 | 21952.0234 | 3.6278
8990 | 24078.6367 | 4.0131
8991 | 25046.9316 | 4.544
8992 | 25878.6074 | 4.9826
8993 | 26058.375 | 5.3471
8994 | 27317.0625 | 5.3808
8995 | 27882.0938 | 5.5677
8996 | 28588.7051 | 5.5034
8997 | 28849.7168 | 5.5992
8998 | 29138.4531 | 5.5674
8999 | 29189.5801 | 5.7082
9000 | 29038.5273 | 5.8362
9001 | 29041.7188 | 5.6731
9002 | 28963.4219 | 5.5738
9003 | 28900.0742 | 5.3971
9004 | 27280.1895 | 5.3364
9005 | 26966.8418 | 5.2868
9006 | 26714.9043 | 5.2465
9007 | 26871.377 | 5.2536
9008 | 26273.3984 | 5.2092
9009 | 26241.25 | 5.1876
9010 | 25857.7324 | 4.9408
9011 | 24960.0586 | 4.6122
9012 | 25412.0801 | 4.5648
9013 | 26492.1445 | 4.6673
9014 | 26918.6504 | 4.3725
9015 | 26687.0195 | 4.2368
9016 | 26100.8594 | 4.0848
9017 | 24559.2793 | 3.994
9018 | 22786.9199 | 3.7976
9019 | 20485.9375 | 3.8429
9020 | 19290.7461 | 3.57
9021 | 17870.041 | 3.2704
9022 | 17016.25 | 3.1614
9023 | 16513.9766 | 2.9034
9024 | 16058.207 | 2.8045
9025 | 15627.7441 | 2.9271
9026 | 14985.4492 | 2.7116
9027 | 14771.3125 | 2.6887
9028 | 14264.2793 | 2.6606
9029 | 14097.1953 | 2.6166
9030 | 13759.1113 | 2.5438
9031 | 13759.8242 | 2.5932
9032 | 13808.8145 | 2.4385
9033 | 13699.9414 | 2.706
9034 | 14515.7324 | 2.7117
9035 | 16226.4707 | 2.9013
9036 | 20549.1387 | 3.1341
9037 | 24104.9531 | 3.4731
9038 | 26608.8828 | 3.8293
9039 | 27096.375 | 4.4153
9040 | 27593.3359 | 4.7553
9041 | 27487.1777 | 5.2531
9042 | 29331.0312 | 5.5224
9043 | 29643.2852 | 5.4831
9044 | 30060.7402 | 5.591
9045 | 31287.9297 | 5.5808
9046 | 31303.4238 | 5.5785
9047 | 30467.0234 | 5.6363
9048 | 28609.916 | 5.6279
9049 | 28617.748 | 5.5069
9050 | 28743.8223 | 5.3472
9051 | 27489.1367 | 5.3051
9052 | 29083.3906 | 5.2142
9053 | 28344.2852 | 5.1077
9054 | 28291.7051 | 5.1066
9055 | 27244.1152 | 5.1584
9056 | 27281.1465 | 5.142
9057 | 27015.9355 | 5.1028
9058 | 26785.4922 | 4.9754
9059 | 25765.1113 | 4.7098
9060 | 26286.375 | 4.5857
9061 | 26858.7871 | 4.7055
9062 | 26777.9141 | 4.3622
9063 | 26624.6504 | 4.1692
9064 | 25759.9648 | 4.0995
9065 | 25071.4375 | 4.0527
9066 | 22852.3203 | 3.969
9067 | 20652.4434 | 3.9065
9068 | 18760.4727 | 3.719
9069 | 17523.9023 | 3.3768
9070 | 16479.9766 | 3.3396
9071 | 16180.207 | 2.9831
9072 | 15582.0918 | 2.7754
9073 | 14789.6074 | 2.8279
9074 | 14503.5 | 2.5226
9075 | 14330.2148 | 2.4723
9076 | 14130.9727 | 2.4402
9077 | 13794.0781 | 2.4338
9078 | 13830.0781 | 2.3364
9079 | 13631.8242 | 2.4161
9080 | 13902.584 | 2.3624
9081 | 14011.668 | 2.5094
9082 | 14462.5938 | 2.5739
9083 | 15581.7734 | 2.8436
9084 | 19170.8516 | 2.9588
9085 | 21644.9199 | 3.4198
9086 | 23775.4883 | 3.6942
9087 | 24520.1309 | 4.1385
9088 | 26063.7344 | 4.6676
9089 | 26715.0195 | 5.0034
9090 | 26931.6602 | 5.1371
9091 | 27581.0625 | 5.2412
9092 | 28601.127 | 5.3938
9093 | 28859.2109 | 5.4206
9094 | 29038.2734 | 5.411
9095 | 28319.4941 | 5.3472
9096 | 28518.9883 | 5.2562
9097 | 28148.4844 | 5.4822
9098 | 27831.7031 | 5.3656
9099 | 26591.1562 | 5.3757
9100 | 26282.4922 | 5.2838
9101 | 25919.25 | 5.1166
9102 | 25928.375 | 5.0145
9103 | 25405.7109 | 4.996
9104 | 25745.7324 | 4.8861
9105 | 25279.3223 | 4.6128
9106 | 25029.6914 | 4.3658
9107 | 24171.2578 | 4.0085
9108 | 24463.418 | 3.8652
9109 | 25143.6914 | 3.8429
9110 | 25115.3223 | 3.9425
9111 | 24542.7969 | 3.7261
9112 | 23269.4902 | 3.766
9113 | 22428.9414 | 3.6179
9114 | 20522.0547 | 3.5068
9115 | 18531.2109 | 3.5617
9116 | 17112.1348 | 3.3371
9117 | 16063.7012 | 2.9421
9118 | 15629.6797 | 2.8101
9119 | 15105.9121 | 2.6435
9120 | 14485.0605 | 2.6004
9121 | 13888.9219 | 2.3558
9122 | 13244.2588 | 2.2466
9123 | 12949.5957 | 2.2474
9124 | 12566.7207 | 2.3716
9125 | 12228.6992 | 2.4934
9126 | 12278.9805 | 2.4086
9127 | 12237.876 | 2.1147
9128 | 12109.3496 | 2.0455
9129 | 12054.1094 | 2.1264
9130 | 11892.3281 | 2.1461
9131 | 12180.3477 | 2.2315
9132 | 13652.6562 | 2.2212
9133 | 14368.8574 | 2.2864
9134 | 14855.3203 | 2.5509
9135 | 15648.3633 | 3.1014
9136 | 17463.8594 | 3.2946
9137 | 18565.125 | 3.6686
9138 | 19833.3281 | 3.8401
9139 | 20284.4434 | 3.8024
9140 | 20535.2969 | 3.8487
9141 | 20316.1172 | 3.9084
9142 | 20344.1914 | 3.9287
9143 | 20740.9492 | 4.1816
9144 | 20834.4648 | 4.1979
9145 | 20661.3164 | 4.0649
9146 | 20810.4648 | 3.8999
9147 | 20352.4219 | 3.8705
9148 | 19766.3672 | 3.7488
9149 | 20044.7695 | 3.7342
9150 | 20173.6641 | 3.7091
9151 | 19802.4023 | 3.6722
9152 | 19766.8008 | 3.6777
9153 | 20003.4121 | 3.6457
9154 | 19935.7812 | 3.5017
9155 | 19840.0098 | 3.4837
9156 | 20310.6738 | 3.2166
9157 | 20437.4336 | 3.0365
9158 | 20250.6758 | 2.9075
9159 | 19875.5273 | 2.8188
9160 | 18187.9258 | 2.9516
9161 | 16584.5977 | 2.9109
9162 | 15426.165 | 2.8333
9163 | 14785.6162 | 2.7384
9164 | 14201.8467 | 2.7548
9165 | 13453.4355 | 2.5377
9166 | 12722.0127 | 2.4091
9167 | 12224.1094 | 2.5112
9168 | 11763.832 | 2.207
9169 | 11317.4434 | 2.053
9170 | 10983.9492 | 2.1036
9171 | 10815.6035 | 2.3323
9172 | 10626.6338 | 2.2847
9173 | 10383.5391 | 2.2164
9174 | 10160.8965 | 1.8768
9175 | 10114.5273 | 1.8077
9176 | 10151.125 | 1.7139
9177 | 10146.5078 | 1.6766
9178 | 10166.1484 | 1.6341
9179 | 10605.4336 | 1.9539
9180 | 11606.3809 | 1.943
9181 | 12525.0557 | 1.8163
9182 | 13142.3926 | 2.1126
9183 | 13569.457 | 2.3077
9184 | 14410.1611 | 2.2837
9185 | 15113.5107 | 2.3975
9186 | 15952.3008 | 2.6778
9187 | 16730.0898 | 2.675
9188 | 17807.5039 | 2.658
9189 | 18931.418 | 2.8847
9190 | 19370.0547 | 3.2172
9191 | 19672.9492 | 3.3466
9192 | 20151.4531 | 3.3833
9193 | 20418.4531 | 3.2783
9194 | 20544.4648 | 3.2476
9195 | 19517.9375 | 3.2896
9196 | 19604.2422 | 3.2217
9197 | 19612.6309 | 3.197
9198 | 19679.2207 | 3.2248
9199 | 19799.2734 | 3.2357
9200 | 19853.084 | 3.2374
9201 | 19677.8945 | 3.2625
9202 | 18651.2109 | 2.9646
9203 | 17366.6406 | 3.0674
9204 | 16954.1133 | 3.0442
9205 | 17648.8926 | 2.9258
9206 | 18016.4102 | 2.7174
9207 | 17588.1348 | 2.6202
9208 | 17371.5137 | 2.5577
9209 | 16611.9551 | 2.5155
9210 | 16130.6904 | 2.518
9211 | 15269.8896 | 2.8507
9212 | 14675.7314 | 2.938
9213 | 13836.5635 | 2.7909
9214 | 13678.793 | 2.454
9215 | 13306.3105 | 2.1649
9216 | 12796.4678 | 2.2638
9217 | 12544.6777 | 2.349
9218 | 12164.6562 | 2.3035
9219 | 12013.6436 | 2.1556
9220 | 11868.3311 | 1.9144
9221 | 11626.3398 | 1.8875
9222 | 11440.3789 | 1.8871
9223 | 11510.1797 | 1.8778
9224 | 11638.5703 | 1.8398
9225 | 11432.4844 | 1.7884
9226 | 12306.5918 | 1.8518
9227 | 14031.2168 | 2.224
9228 | 17389.9551 | 2.2942
9229 | 20013.8516 | 2.6479
9230 | 22159.3086 | 2.8246
9231 | 23643.752 | 3.4557
9232 | 25233.5332 | 3.7899
9233 | 26627.8711 | 4.0239
9234 | 27941.0625 | 4.0755
9235 | 28252.832 | 4.1777
9236 | 30197.582 | 4.2316
9237 | 28965.6641 | 4.4467
9238 | 28786.0312 | 4.5025
9239 | 28260.9258 | 4.4089
9240 | 28974.4219 | 4.2772
9241 | 28317.3359 | 4.0883
9242 | 28185.9141 | 4.1413
9243 | 27670.0938 | 4.0652
9244 | 28006.3984 | 3.9825
9245 | 27927.4199 | 3.9289
9246 | 26842.1992 | 3.9211
9247 | 26358.2598 | 3.983
9248 | 26048.3965 | 3.9732
9249 | 26553.3867 | 3.8005
9250 | 25584.5645 | 3.7274
9251 | 25207.3008 | 3.45
9252 | 26086.9746 | 3.4007
9253 | 27106.0293 | 3.3218
9254 | 27093.5234 | 3.1671
9255 | 26496.377 | 2.8285
9256 | 25430.9551 | 2.8023
9257 | 24599.1426 | 2.7135
9258 | 23020.9414 | 2.6126
9259 | 20967.0859 | 2.6393
9260 | 19334.8398 | 2.6211
9261 | 18042.9141 | 2.5913
9262 | 16844.8711 | 2.2456
9263 | 16279.6514 | 2.3527
9264 | 15634.1123 | 2.1426
9265 | 15145.7754 | 1.9446
9266 | 14840.2578 | 1.8786
9267 | 14705.6152 | 1.8862
9268 | 14210.0996 | 2.0096
9269 | 13963.2051 | 2.1636
9270 | 14048.3311 | 2.1662
9271 | 14065.6562 | 2.1778
9272 | 14045.9316 | 1.976
9273 | 14133.3525 | 1.832
9274 | 14690.9951 | 2.0838
9275 | 15900.207 | 2.2407
9276 | 18962.1055 | 2.4065
9277 | 21483.0859 | 2.3438
9278 | 24130.752 | 2.7145
9279 | 26388.7441 | 2.7315
9280 | 27208.1367 | 2.8751
9281 | 28933.0957 | 2.9384
9282 | 30523.6875 | 2.9822
9283 | 30637.1816 | 3.0618
9284 | 33763.2422 | 3.1093
9285 | 32605.6797 | 3.2245
9286 | 32570.8066 | 3.2357
9287 | 32084.6484 | 3.2316
9288 | 30361.7383 | 3.3504
9289 | 29853.1367 | 3.1877
9290 | 29327.0332 | 3.1869
9291 | 29750.2969 | 3.1955
9292 | 28960.3906 | 3.1851
9293 | 29562.9062 | 3.1586
9294 | 29039.5273 | 3.26
9295 | 28643.2109 | 3.2147
9296 | 27574.9453 | 3.0583
9297 | 27491.8203 | 3.0962
9298 | 26940.0293 | 3.094
9299 | 26807.1562 | 3.3063
9300 | 27483.1992 | 3.209
9301 | 28031.4727 | 3.0017
9302 | 27895.957 | 2.8647
9303 | 27105.293 | 2.6738
9304 | 26104.6074 | 2.6283
9305 | 25293.1855 | 2.5788
9306 | 23615.2363 | 2.5158
9307 | 21443.9805 | 2.6071
9308 | 19852.0312 | 2.6913
9309 | 18414.5898 | 2.3357
9310 | 17482.7559 | 2.2021
9311 | 16532.7539 | 2.0736
9312 | 15890.8711 | 1.8623
9313 | 15465.7881 | 1.8653
9314 | 15069.6299 | 2.1199
9315 | 14816.2285 | 2.1756
9316 | 14671.333 | 2.1409
9317 | 14959.7246 | 1.9342
9318 | 15541.0381 | 1.7464
9319 | 15497.0381 | 1.7581
9320 | 15609.4268 | 1.6784
9321 | 15535.1533 | 1.7845
9322 | 16161.334 | 1.7658
9323 | 15964.4395 | 2.1916
9324 | 19465.9902 | 2.109
9325 | 21557.3594 | 2.4495
9326 | 24094.6172 | 2.5721
9327 | 25799.4609 | 2.923
9328 | 27178.0293 | 3.216
9329 | 28411.1055 | 3.5465
9330 | 30543.4648 | 3.6794
9331 | 29814.4219 | 3.947
9332 | 29464.4434 | 3.8154
9333 | 29618.6953 | 3.7496
9334 | 29896.8223 | 3.8766
9335 | 29672.8008 | 3.8653
9336 | 31157.918 | 3.828
9337 | 30492.4766 | 3.7157
9338 | 31838.6777 | 3.5638
9339 | 29095.6523 | 3.7971
9340 | 29777.6758 | 3.7002
9341 | 29455.2852 | 3.7488
9342 | 28842.1367 | 3.7197
9343 | 28942.5059 | 3.5348
9344 | 27916.5781 | 3.4969
9345 | 27338.6719 | 3.5648
9346 | 26969.9141 | 3.4238
9347 | 26605.5234 | 3.2834
9348 | 27249.7754 | 3.1597
9349 | 27974.2305 | 3.1431
9350 | 27665.4512 | 3.073
9351 | 26679.1348 | 2.9868
9352 | 25328.8164 | 3.0576
9353 | 24874.9102 | 2.8233
9354 | 23036.9395 | 2.6567
9355 | 21037.2227 | 2.9042
9356 | 19625.2539 | 2.8336
9357 | 18606.7031 | 2.5811
9358 | 17643.0312 | 2.4719
9359 | 16591.6074 | 2.456
9360 | 15801.4697 | 2.0251
9361 | 15167.2393 | 1.9714
9362 | 14952.9004 | 1.9354
9363 | 15329.543 | 1.9654
9364 | 15729.0586 | 1.9038
9365 | 15595.6797 | 2.0954
9366 | 15753.7021 | 2.1874
9367 | 15528.46 | 2.2073
9368 | 15887.3125 | 2.1209
9369 | 15931.5645 | 2.0237
9370 | 16605.4707 | 1.9912
9371 | 16968.9863 | 2.0981
9372 | 19967.2754 | 2.3144
9373 | 21820.7383 | 2.7408
9374 | 24285.375 | 3.0197
9375 | 27420.0508 | 3.3108
9376 | 28346.9688 | 3.7965
9377 | 28716.3477 | 4.3671
9378 | 29563.5176 | 4.5001
9379 | 31047.1172 | 4.4897
9380 | 33254.9727 | 4.5186
9381 | 32115.5508 | 4.4554
9382 | 32083.5508 | 4.3793
9383 | 30246.2012 | 4.3667
9384 | 29873.0547 | 4.4829
9385 | 29707.9277 | 4.5429
9386 | 30732.4766 | 4.5418
9387 | 32392.3926 | 4.5179
9388 | 33217.1836 | 4.4601
9389 | 31978.373 | 4.315
9390 | 32005.5508 | 4.0915
9391 | 30034.6855 | 4.1279
9392 | 29577.791 | 4.0356
9393 | 29533.2852 | 4.0129
9394 | 28820.6211 | 3.8295
9395 | 29302.1367 | 3.4502
9396 | 29691.1699 | 3.5272
9397 | 28499.1055 | 3.2799
9398 | 27531.7988 | 3.1513
9399 | 27626.4414 | 3.1495
9400 | 27284.7891 | 3.2894
9401 | 26254.6074 | 3.1245
9402 | 24123.2383 | 3.0309
9403 | 21968.1406 | 2.9482
9404 | 19914.5156 | 2.6884
9405 | 18480.5684 | 2.456
9406 | 19131.7148 | 2.2321
9407 | 17288.8711 | 2.0899
9408 | 15800.3008 | 1.9818
9409 | 15141.2695 | 2.1093
9410 | 14643.8691 | 2.2216
9411 | 14229.1318 | 2.2627
9412 | 15359.4492 | 2.23
9413 | 15809.333 | 2.148
9414 | 15429.6592 | 1.8547
9415 | 14018.584 | 1.8548
9416 | 13696.8145 | 1.8241
9417 | 13522.3809 | 1.8343
9418 | 14161.7422 | 1.8936
9419 | 15651.9004 | 2.2806
9420 | 21055.0859 | 2.417
9421 | 23710.1094 | 2.8186
9422 | 26308.1016 | 3.2058
9423 | 27051.8203 | 3.7657
9424 | 27574.4805 | 4.3162
9425 | 26829.7539 | 4.769
9426 | 27550.6719 | 4.745
9427 | 27062.0293 | 4.7133
9428 | 27815.6094 | 4.8167
9429 | 27392.4102 | 4.8805
9430 | 27629.1465 | 4.7986
9431 | 27473.4805 | 4.7237
9432 | 28242.4629 | 4.8409
9433 | 27345.5449 | 4.8883
9434 | 27430.7148 | 4.8554
9435 | 26557.2285 | 4.7095
9436 | 24988.7031 | 4.3768
9437 | 24340.3125 | 4.3821
9438 | 24823.2188 | 4.1431
9439 | 25137.4375 | 4.059
9440 | 24945.5547 | 3.9824
9441 | 24805.1641 | 3.9141
9442 | 25150.4258 | 3.7482
9443 | 24357.3945 | 3.6078
9444 | 24938.4277 | 3.5428
9445 | 24955.5547 | 3.5291
9446 | 24516.543 | 3.3851
9447 | 23796.7305 | 3.4826
9448 | 23037.6992 | 3.2463
9449 | 22420.4141 | 2.994
9450 | 20497.6855 | 2.7992
9451 | 18501.9473 | 2.8473
9452 | 17274.502 | 2.8205
9453 | 16404.207 | 2.7557
9454 | 15385.9121 | 2.4425
9455 | 14742.627 | 2.247
9456 | 13930.4678 | 2.215
9457 | 13374.1943 | 2.1727
9458 | 12928.1719 | 1.9823
9459 | 12594.8867 | 2.1484
9460 | 12379.623 | 2.2706
9461 | 12158.4766 | 2.2407
9462 | 12078.9082 | 2.2312
9463 | 11923.1387 | 2.111
9464 | 11953.2559 | 2.1287
9465 | 11848.4531 | 2.0558
9466 | 11803.4316 | 1.834
9467 | 12140.9297 | 1.9643
9468 | 13625.8145 | 1.9861
9469 | 14730.7744 | 2.344
9470 | 15610.7842 | 2.4698
9471 | 16438.5312 | 2.5851
9472 | 18109.0098 | 2.844
9473 | 19185.6289 | 3.2001
9474 | 20320.6836 | 3.3195
9475 | 21052.9805 | 3.3948
9476 | 21119.791 | 3.3855
9477 | 21037.2852 | 3.6193
9478 | 21099.3379 | 3.7616
9479 | 21531.4531 | 3.7883
9480 | 21493.3164 | 3.7986
9481 | 21139.2441 | 3.5267
9482 | 20976.5371 | 3.4211
9483 | 20563.2949 | 3.3674
9484 | 19785.707 | 3.302
9485 | 19780.2324 | 3.3668
9486 | 19875.7578 | 3.3727
9487 | 19721.6855 | 3.3014
9488 | 19712.4219 | 3.3621
9489 | 19791.2012 | 3.5555
9490 | 19951.043 | 3.4415
9491 | 19993.7812 | 3.3789
9492 | 20594.9277 | 3.234
9493 | 20865.5703 | 2.9035
9494 | 20439.5488 | 2.9668
9495 | 19900.0117 | 2.9848
9496 | 18384.1992 | 2.5512
9497 | 16944.1328 | 2.7055
9498 | 15726.4375 | 2.8266
9499 | 15316.4951 | 2.9124
9500 | 14449.3896 | 2.8915
9501 | 13735.0518 | 2.5642
9502 | 13161.5352 | 2.2788
9503 | 12517.2598 | 2.1755
9504 | 12049.2393 | 2.0428
9505 | 11484.207 | 2.2407
9506 | 11093.8174 | 2.2685
9507 | 10947.6797 | 2.2805
9508 | 10705.4062 | 2.0492
9509 | 10598.1641 | 1.8387
9510 | 10292.3115 | 1.7605
9511 | 10230.3633 | 1.7627
9512 | 10224.7422 | 1.7481
9513 | 10096.0059 | 1.9907
9514 | 10270.4277 | 1.964
9515 | 10669.2363 | 1.9997
9516 | 11941.9551 | 1.8754
9517 | 12588.5664 | 1.8163
9518 | 13247.6621 | 2.1035
9519 | 13872.9688 | 2.1686
9520 | 14749.6523 | 2.4092
9521 | 15767.6318 | 2.2378
9522 | 17220.7715 | 2.3543
9523 | 18461.4355 | 2.736
9524 | 19663.4492 | 2.5529
9525 | 21853.1348 | 2.788
9526 | 23600.7148 | 2.8136
9527 | 23688.1992 | 3.0596
9528 | 23135.6934 | 3.2113
9529 | 22394.8008 | 3.2871
9530 | 21402.6641 | 3.0884
9531 | 21415.2852 | 2.884
9532 | 21922.4297 | 2.7746
9533 | 21557.5352 | 2.726
9534 | 20934.9434 | 2.9465
9535 | 20949.9531 | 2.9961
9536 | 20390.8242 | 3.0452
9537 | 19689.4746 | 3.0252
9538 | 18668.1895 | 2.7782
9539 | 17595.7891 | 2.6417
9540 | 17790.6621 | 2.5266
9541 | 18263.0742 | 2.5437
9542 | 17629.2812 | 2.4559
9543 | 17402.0195 | 2.4618
9544 | 17223.8828 | 2.4793
9545 | 16628.2285 | 2.4754
9546 | 16359.334 | 2.5559
9547 | 15678.165 | 2.804
9548 | 15085.2676 | 2.6873
9549 | 14353.5938 | 2.481
9550 | 13829.9414 | 2.2253
9551 | 13257.5498 | 2.2286
9552 | 12656.75 | 2.3361
9553 | 12077.8555 | 2.2932
9554 | 11751.4648 | 2.0326
9555 | 11483.5586 | 1.9156
9556 | 11271.8105 | 1.8778
9557 | 11039.168 | 1.8746
9558 | 11017.3164 | 1.8798
9559 | 10909.3281 | 1.8943
9560 | 11032.875 | 1.8642
9561 | 11096.3809 | 1.9165
9562 | 11664.8203 | 1.9285
9563 | 13453.1494 | 2.1988
9564 | 16881.7891 | 2.361
9565 | 19210.0215 | 3.1218
9566 | 22267.8965 | 3.4479
9567 | 24122.543 | 4.0533
9568 | 27220.6836 | 4.4357
9569 | 27766.3242 | 4.8695
9570 | 28447.3574 | 5.1206
9571 | 28222.7578 | 5.2596
9572 | 30174.2773 | 5.4436
9573 | 28895.9375 | 5.3534
9574 | 28498.8418 | 5.3776
9575 | 27852.5156 | 5.459
9576 | 27649.2637 | 5.317
9577 | 27634.6113 | 5.4476
9578 | 28727.3496 | 5.2911
9579 | 29127.1406 | 5.4291
9580 | 27390.8008 | 5.4068
9581 | 26581.2324 | 5.318
9582 | 26376.748 | 5.0243
9583 | 26991.6719 | 4.975
9584 | 25782.6914 | 5.0806
9585 | 25701.9648 | 5.1859
9586 | 26022.6074 | 4.8075
9587 | 25603.2285 | 4.5653
9588 | 26401.1348 | 4.3753
9589 | 27752.0723 | 4.1748
9590 | 26682.1465 | 4.0412
9591 | 26004.8594 | 3.9101
9592 | 25193.5547 | 3.7612
9593 | 24293.6484 | 3.753
9594 | 22766.4355 | 3.6041
9595 | 20315.918 | 3.7767
9596 | 18536.3164 | 3.5473
9597 | 17355.5137 | 3.2569
9598 | 16367.334 | 2.9466
9599 | 15456.7852 | 2.7523
9600 | 14964.1631 | 2.7433
9601 | 14501.0811 | 2.6086
9602 | 14163.7744 | 2.4866
9603 | 14041.7734 | 2.537
9604 | 13782.1211 | 2.5222
9605 | 13612.1855 | 2.4841
9606 | 13426.9834 | 2.5013
9607 | 13458.1289 | 2.5778
9608 | 13672.5605 | 2.6109
9609 | 14113.6367 | 2.7504
9610 | 15026.1973 | 2.7964
9611 | 16528.9766 | 2.753
9612 | 19791.3086 | 2.9163
9613 | 22106.3086 | 3.1106
9614 | 24624.2695 | 3.5023
9615 | 28113.1055 | 4.0442
9616 | 29953.4434 | 4.3982
9617 | 30021.8125 | 4.7213
9618 | 32790.582 | 4.9329
9619 | 30240.4551 | 5.1969
9620 | 30156.6133 | 5.2168
9621 | 29527.0859 | 5.1567
9622 | 31417.8652 | 5.1896
9623 | 29742.3613 | 5.1746
9624 | 29573.6953 | 5.1287
9625 | 29573.2344 | 5.2195
9626 | 28667.125 | 5.1581
9627 | 28779.5781 | 5.2099
9628 | 29167.9062 | 5.2625
9629 | 28649.8301 | 5.1909
9630 | 29300.0215 | 5.3643
9631 | 28726.3906 | 5.2733
9632 | 27177.4316 | 5.1865
9633 | 26305.6191 | 5.0552
9634 | 26683.8926 | 4.7385
9635 | 26243.1348 | 4.6475
9636 | 27703.3145 | 4.566
9637 | 27880.9668 | 4.4099
9638 | 27558.0527 | 4.3118
9639 | 26747.7773 | 4.144
9640 | 25869.7109 | 4.1447
9641 | 24730.4062 | 4.1832
9642 | 23002.0664 | 4.0703
9643 | 21129.9609 | 4.1255
9644 | 19346.8828 | 3.8397
9645 | 18298.5664 | 3.3329
9646 | 17134.7773 | 3.165
9647 | 16130.4375 | 2.9953
9648 | 15445.334 | 2.8495
9649 | 14783.2393 | 3.0236
9650 | 14337.8682 | 2.8496
9651 | 14077.71 | 2.7381
9652 | 14052.0996 | 2.7108
9653 | 13957.4785 | 2.6993
9654 | 13859.5938 | 2.6509
9655 | 13924.3086 | 2.6565
9656 | 14005.2051 | 2.6684
9657 | 13921.2051 | 2.8426
9658 | 14249.4062 | 2.7843
9659 | 15597.1631 | 3.0622
9660 | 19424.1992 | 3.4344
9661 | 21668.5918 | 3.5923
9662 | 24386.5 | 3.7296
9663 | 26538.3652 | 4.1667
9664 | 28795 | 4.6705
9665 | 28384.9883 | 5.0117
9666 | 29503.1699 | 5.1492
9667 | 29090.8945 | 5.2235
9668 | 30390.707 | 5.2703
9669 | 30040.1289 | 5.4067
9670 | 29616.9492 | 5.4154
9671 | 28636.8535 | 5.4002
9672 | 29239.5586 | 5.4378
9673 | 28495.5273 | 5.3726
9674 | 28934.4316 | 5.3874
9675 | 28510.2305 | 5.258
9676 | 28818.6426 | 5.169
9677 | 28047.4199 | 5.1114
9678 | 27627.0605 | 5.1836
9679 | 27354.5566 | 5.2407
9680 | 27034.7891 | 5.2228
9681 | 26768.5137 | 5.0584
9682 | 26348.125 | 4.8057
9683 | 26256.2402 | 4.6039
9684 | 27793.3359 | 4.3872
9685 | 27774.6934 | 4.3353
9686 | 26960.7871 | 4.1467
9687 | 26184.2383 | 3.9838
9688 | 25479.8281 | 3.8695
9689 | 24664.2891 | 3.795
9690 | 22927.4473 | 3.8169
9691 | 20654.1914 | 3.9117
9692 | 18895.2109 | 3.6426
9693 | 18074.3164 | 3.3627
9694 | 16830.4805 | 3.1818
9695 | 15972.6914 | 2.9905
9696 | 15570.8066 | 2.8057
9697 | 14972.8057 | 2.758
9698 | 14337.9336 | 2.6498
9699 | 14232.3018 | 2.6617
9700 | 14153.0371 | 2.6238
9701 | 13977.0381 | 2.6082
9702 | 13934.5107 | 2.5774
9703 | 13882.3311 | 2.5793
9704 | 14238.0996 | 2.5457
9705 | 14167.3418 | 2.6212
9706 | 14807.3623 | 2.6689
9707 | 16245.4502 | 3.0069
9708 | 19254.2422 | 3.0911
9709 | 21892.875 | 3.3865
9710 | 24437.3945 | 3.795
9711 | 26236.2383 | 4.2387
9712 | 27166.9023 | 4.6645
9713 | 27595.5664 | 5.0753
9714 | 28698.873 | 5.0386
9715 | 29599.0547 | 5.2739
9716 | 29519.9883 | 5.509
9717 | 30304.4531 | 5.4574
9718 | 28912.7363 | 5.5322
9719 | 29883.1074 | 5.5707
9720 | 29407.707 | 5.5204
9721 | 28136.127 | 5.407
9722 | 27542.1348 | 5.3931
9723 | 27202.4941 | 5.3054
9724 | 27209.1465 | 5.0504
9725 | 27373.5566 | 5.2197
9726 | 27077.1445 | 5.2251
9727 | 26691.5254 | 5.2956
9728 | 26142.6289 | 5.2487
9729 | 26299.9863 | 5.3189
9730 | 24755.5527 | 5.0529
9731 | 24906.1426 | 4.6293
9732 | 26879.5234 | 4.5797
9733 | 27766.0723 | 4.4745
9734 | 27776.4414 | 4.2476
9735 | 27053.6602 | 4.1982
9736 | 26111.3438 | 4.2775
9737 | 24861.1641 | 4.1291
9738 | 23305.9531 | 3.8719
9739 | 21150.8555 | 3.8323
9740 | 19303.5977 | 3.6045
9741 | 18266.9355 | 3.3622
9742 | 17102.8711 | 3.2793
9743 | 16461.1035 | 3.1812
9744 | 15770.502 | 2.9029
9745 | 15196.5762 | 2.7503
9746 | 14745.8691 | 2.6196
9747 | 14425.9629 | 2.6595
9748 | 14179.9619 | 2.658
9749 | 14120.0781 | 2.6279
9750 | 13971.8262 | 2.8049
9751 | 13769.5732 | 2.8706
9752 | 13699.9414 | 2.901
9753 | 13677.6875 | 3.0352
9754 | 14659.6162 | 3.0511
9755 | 15862.6914 | 3.0527
9756 | 19069.8516 | 3.1057
9757 | 21299.4766 | 3.6024
9758 | 24211.375 | 3.9932
9759 | 26566.375 | 4.3108
9760 | 27920.8301 | 4.8295
9761 | 28037.1992 | 5.0063
9762 | 28362.5996 | 5.2623
9763 | 28412.3477 | 5.1021
9764 | 28581.4941 | 5.3467
9765 | 28310.0938 | 5.2253
9766 | 27646.6719 | 5.3582
9767 | 27598.4414 | 5.4495
9768 | 27246.9258 | 5.3293
9769 | 27094.6738 | 5.5375
9770 | 26961.2715 | 5.4302
9771 | 26272.9961 | 5.3288
9772 | 25873.7129 | 5.0897
9773 | 25944.9766 | 5.1143
9774 | 25644.8398 | 5.0645
9775 | 25204.5645 | 4.8908
9776 | 24791.6367 | 4.7897
9777 | 25370.1953 | 4.5797
9778 | 25343.4375 | 4.473
9779 | 25034.7949 | 4.3459
9780 | 25700.1074 | 4.2611
9781 | 25838.9531 | 4.2412
9782 | 25436.4414 | 4.1643
9783 | 24766.0391 | 3.9117
9784 | 23537.4668 | 3.8536
9785 | 22639.1719 | 3.708
9786 | 21084.5801 | 3.6783
9787 | 18976.7031 | 3.6293
9788 | 17441.7676 | 3.4118
9789 | 16655.4707 | 3.1081
9790 | 15693.543 | 2.664
9791 | 14769.8691 | 2.5491
9792 | 14061.8906 | 2.4833
9793 | 13330.7422 | 2.6945
9794 | 12940.584 | 2.5187
9795 | 12602.9297 | 2.3467
9796 | 12448.9746 | 2.2945
9797 | 12286.3105 | 2.2053
9798 | 12029.6016 | 2.1795
9799 | 11946.2012 | 2.1625
9800 | 12108.9805 | 2.1055
9801 | 12154.2227 | 2.2001
9802 | 12370.6133 | 2.1983
9803 | 12709.876 | 2.252
9804 | 13972.6777 | 2.0144
9805 | 15060.1855 | 2.0779
9806 | 16215.6797 | 2.413
9807 | 16855.6074 | 2.7757
9808 | 18334.0625 | 3.1041
9809 | 19582.2637 | 3.3486
9810 | 21238.4648 | 3.3911
9811 | 21614.1602 | 3.7839
9812 | 21882.2344 | 3.9388
9813 | 21249.4863 | 3.9023
9814 | 21073.5586 | 3.8346
9815 | 21442.1836 | 3.9359
9816 | 21696.4453 | 3.9541
9817 | 21001.3164 | 3.9433
9818 | 21103.3281 | 3.9012
9819 | 20949.7285 | 3.7733
9820 | 20352.3906 | 3.8781
9821 | 20268.748 | 3.8148
9822 | 20643.9707 | 3.6143
9823 | 20587.4336 | 3.5286
9824 | 20373.8027 | 3.5389
9825 | 20352.9277 | 3.5913
9826 | 20412.0547 | 3.571
9827 | 20610.1914 | 3.5498
9828 | 21434.0977 | 3.3909
9829 | 21563.8652 | 3.4066
9830 | 21271.7285 | 3.1639
9831 | 20911.3164 | 2.8862
9832 | 18999.8516 | 2.7985
9833 | 17486.8926 | 2.7035
9834 | 16377.1016 | 2.6912
9835 | 15916.8066 | 2.7622
9836 | 15242.0273 | 2.8225
9837 | 14462.3516 | 2.5302
9838 | 13894.1719 | 2.3351
9839 | 13220.4883 | 2.1973
9840 | 13610.0059 | 2.1141
9841 | 12184.9082 | 2.3571
9842 | 11670.749 | 2.2506
9843 | 11493.6445 | 1.988
9844 | 11262.8652 | 1.901
9845 | 10997.6523 | 1.84
9846 | 10690.6211 | 1.7677
9847 | 10513.7266 | 1.7525
9848 | 10667.7695 | 1.7454
9849 | 10642.6445 | 1.8965
9850 | 10718.5605 | 2.0294
9851 | 11018.9062 | 2.1403
9852 | 12015.4551 | 2.1214
9853 | 12872.2051 | 1.8837
9854 | 13726.5312 | 1.9672
9855 | 13801.7402 | 2.2033
9856 | 14879.3086 | 2.4941
9857 | 15819.7012 | 2.4697
9858 | 17181.3457 | 2.6153
9859 | 17799.8086 | 2.5317
9860 | 18463.0078 | 2.7062
9861 | 19528.6641 | 3.0985
9862 | 19751.252 | 3.0373
9863 | 20338.6641 | 3.1696
9864 | 20977.9375 | 3.5421
9865 | 21276.75 | 3.6366
9866 | 21205.8008 | 3.5038
9867 | 20925.3184 | 3.3074
9868 | 20298.623 | 3.144
9869 | 19892.1172 | 3.2758
9870 | 20037.8848 | 3.1436
9871 | 19774.4219 | 3.0725
9872 | 19927.5273 | 3.3543
9873 | 19914.9688 | 3.1945
9874 | 19058.8418 | 3.0102
9875 | 18429.4414 | 2.7989
9876 | 18598.7031 | 2.7277
9877 | 18241.3047 | 2.8725
9878 | 17829.3965 | 2.9332
9879 | 17514.6406 | 2.858
9880 | 17180.7559 | 2.5608
9881 | 16690.7129 | 2.5976
9882 | 15981.291 | 2.7175
9883 | 15289.8906 | 2.8318
9884 | 14876.4883 | 2.7285
9885 | 14206.0781 | 2.6212
9886 | 13613.5508 | 2.2731
9887 | 12896.0352 | 2.0987
9888 | 12473.6875 | 1.9529
9889 | 12067.4141 | 1.9356
9890 | 13569.3203 | 1.8923
9891 | 13112.0332 | 1.9028
9892 | 11735.7793 | 1.8487
9893 | 11110.6211 | 1.8499
9894 | 11059.2324 | 1.8189
9895 | 10953.959 | 1.8142
9896 | 11160.9805 | 1.8235
9897 | 11313.2324 | 1.7889
9898 | 12278.0547 | 1.8992
9899 | 13865.3398 | 2.3251
9900 | 17094.0703 | 2.3686
9901 | 19859.6836 | 3.1394
9902 | 22005.7715 | 3.6042
9903 | 23596.0352 | 4.1015
9904 | 25656.9102 | 4.5073
9905 | 26905.5664 | 4.8999
9906 | 28425.5684 | 5.0736
9907 | 29054.5586 | 5.2368
9908 | 29309.1797 | 5.4024
9909 | 29139.6309 | 5.4483
9910 | 29318.916 | 5.5058
9911 | 29488.7793 | 5.3941
9912 | 29453.7891 | 5.4606
9913 | 29715.0645 | 5.5234
9914 | 30924.5078 | 5.4528
9915 | 29540.6641 | 5.3171
9916 | 30150.4531 | 5.1687
9917 | 29461.2852 | 5.1999
9918 | 28597.3574 | 5.3208
9919 | 27846.7148 | 5.2469
9920 | 26430.3438 | 5.1932
9921 | 26515.1758 | 5.0372
9922 | 26016.8926 | 4.7381
9923 | 26321.4707 | 4.6345
9924 | 27264.4082 | 4.3563
9925 | 27209.6289 | 4.1994
9926 | 26822.5352 | 4.0601
9927 | 26100.082 | 4.1205
9928 | 26122.7012 | 3.9241
9929 | 25169.5742 | 3.8351
9930 | 23394.2051 | 3.9522
9931 | 21652.6016 | 4.003
9932 | 20031.5254 | 3.8088
9933 | 18309.4414 | 3.386
9934 | 17096.25 | 3.0229
9935 | 15903.1973 | 2.9428
9936 | 15373.9766 | 2.8446
9937 | 14637.5645 | 2.7938
9938 | 14344.2793 | 2.4593
9939 | 13878.5117 | 2.5342
9940 | 13884.7861 | 2.5526
9941 | 13648.3945 | 2.525
9942 | 13451.2441 | 2.5018
9943 | 13511.6875 | 2.499
9944 | 13910.9521 | 2.5411
9945 | 13956.7422 | 2.5684
9946 | 14238.6367 | 2.6589
9947 | 15217.1641 | 2.9166
9948 | 18671.8203 | 3.0585
9949 | 20708.9492 | 3.4162
9950 | 23658.668 | 3.8152
9951 | 26435.4922 | 4.4023
9952 | 28726.3672 | 4.8015
9953 | 30674.0859 | 5.2245
9954 | 29899.2539 | 5.3031
9955 | 29137.9277 | 5.2603
9956 | 29827.4219 | 5.3367
9957 | 29730.918 | 5.1917
9958 | 29761.4219 | 5.2454
9959 | 29564.2969 | 5.2078
9960 | 31043.002 | 5.404
9961 | 29712.707 | 5.4477
9962 | 28957.2637 | 5.4878
9963 | 29864.3613 | 5.3568
9964 | 29561.8105 | 5.373
9965 | 28719.8418 | 5.0552
9966 | 28842.5898 | 5.1483
9967 | 27445.1562 | 4.9978
9968 | 26065.7656 | 5.0346
9969 | 26006.9746 | 5.0212
9970 | 27029.9863 | 4.563
9971 | 27598.9453 | 4.409
9972 | 28096.5996 | 4.4872
9973 | 28124.5781 | 4.1982
9974 | 27013.1777 | 4.1653
9975 | 26798.6504 | 3.9385
9976 | 25263.3008 | 3.7661
9977 | 24597.0273 | 3.9311
9978 | 22921.5625 | 3.9789
9979 | 20821.2031 | 3.8155
9980 | 18958.7266 | 3.2986
9981 | 18216.1777 | 3.195
9982 | 17328.5254 | 2.9995
9983 | 16261.334 | 2.612
9984 | 15301.4707 | 2.5
9985 | 14691.3125 | 2.6972
9986 | 14324.3516 | 2.6466
9987 | 14197.2266 | 2.6647
9988 | 13822.584 | 2.6716
9989 | 13782.584 | 2.6497
9990 | 13589.6348 | 2.6463
9991 | 13566.0879 | 2.6313
9992 | 13928.6572 | 2.6685
9993 | 14157.458 | 2.4121
9994 | 14588.7959 | 2.4617
9995 | 15586.4697 | 2.8327
9996 | 18887.6211 | 2.8771
9997 | 20859.7168 | 3.3028
9998 | 23534.8789 | 3.5162
9999 | 26004.6074 | 4.3243
10000 | 28550.8105 | 4.7345
10001 | 28328.5781 | 5.1127
10002 | 29815.3184 | 5.2091
10003 | 29576.6641 | 5.3947
10004 | 30107.2441 | 5.4346
10005 | 30744.1289 | 5.4368
10006 | 31444.2441 | 5.3949
10007 | 31365.9297 | 5.4152
10008 | 31530.1719 | 5.4596
10009 | 31933.1758 | 5.5645
10010 | 31182.584 | 5.4704
10011 | 29966.6973 | 5.2365
10012 | 28805.2363 | 5.1771
10013 | 28375.875 | 5.233
10014 | 28732.0332 | 5.1029
10015 | 28387.8301 | 5.239
10016 | 26882.9258 | 5.1864
10017 | 26694.3242 | 5.0753
10018 | 26321.293 | 4.7073
10019 | 26341.9863 | 4.6211
10020 | 28265.1582 | 4.4761
10021 | 29764.5703 | 4.3703
10022 | 29498.8008 | 4.0533
10023 | 27295.5664 | 3.9751
10024 | 26244.377 | 4.0096
10025 | 24697.2793 | 4.0862
10026 | 22929.9512 | 3.8974
10027 | 20888.832 | 3.8591
10028 | 19507.6426 | 3.653
10029 | 18224.9375 | 3.3041
10030 | 17032.7773 | 3.1519
10031 | 16243.3555 | 2.8859
10032 | 15191.4922 | 2.7933
10033 | 14665.1738 | 2.9242
10034 | 14158.1641 | 2.835
10035 | 13790.374 | 2.8218
10036 | 13728.9004 | 2.8096
10037 | 13411.4258 | 2.7981
10038 | 13300.1406 | 2.771
10039 | 13377.0664 | 2.7384
10040 | 13599.5625 | 2.7534
10041 | 13445.4463 | 2.7794
10042 | 13852.1006 | 2.7275
10043 | 15322.7627 | 2.8374
10044 | 18408.2734 | 3.1576
10045 | 20273.3047 | 3.3969
10046 | 23107.7715 | 3.7387
10047 | 25303.8379 | 4.4156
10048 | 26966.3027 | 4.8771
10049 | 28348.3262 | 5.1756
10050 | 29401.4102 | 5.2676
10051 | 29204.1582 | 5.4415
10052 | 29096.8223 | 5.6069
10053 | 29699.582 | 5.5742
10054 | 30036.2012 | 5.5813
10055 | 29611.8125 | 5.636
10056 | 29495.2539 | 5.6001
10057 | 29457.0039 | 5.6904
10058 | 28945.6543 | 5.6022
10059 | 28704.8945 | 5.5516
10060 | 28663.2637 | 5.6384
10061 | 27671.3359 | 5.4955
10062 | 27717.3359 | 5.5271
10063 | 26324.5137 | 5.3972
10064 | 26369.7031 | 5.2756
10065 | 26287.8828 | 5.2663
10066 | 25986.8184 | 4.9886
10067 | 25892.0391 | 4.767
10068 | 27141.9785 | 4.6857
10069 | 27511.9355 | 4.6495
10070 | 27536.9453 | 4.4002
10071 | 27713.8203 | 4.3363
10072 | 25676.1016 | 4.3196
10073 | 24615.2793 | 4.3495
10074 | 22710.6875 | 4.2946
10075 | 20424.0547 | 4.1499
10076 | 18431.0938 | 3.4553
10077 | 17151.9961 | 3.2405
10078 | 16166.7129 | 3.1584
10079 | 15686.9434 | 2.8608
10080 | 14897.4492 | 2.7672
10081 | 14163.7959 | 2.8509
10082 | 13857.3418 | 2.8678
10083 | 13476.7002 | 2.6181
10084 | 13397.8037 | 2.5907
10085 | 13338.5625 | 2.5981
10086 | 13204.0029 | 2.5782
10087 | 13074.9512 | 2.5971
10088 | 13205.4453 | 2.5482
10089 | 13106.9297 | 2.675
10090 | 13615.625 | 2.7105
10091 | 15103.2695 | 2.9888
10092 | 18803.7695 | 3.2359
10093 | 20873.9922 | 3.5691
10094 | 23356.0781 | 3.8865
10095 | 25787.5762 | 4.2693
10096 | 28667.748 | 4.5213
10097 | 28883.4844 | 4.9574
10098 | 29116.2734 | 5.0121
10099 | 29976.5703 | 5.1927
10100 | 30098.8223 | 5.179
10101 | 30781.623 | 5.1712
10102 | 33159.75 | 5.3159
10103 | 32622.0781 | 5.272
10104 | 31836.9863 | 5.1798
10105 | 30503.1191 | 5.0499
10106 | 28566.3672 | 4.8976
10107 | 27701.7266 | 4.823
10108 | 25882.9258 | 4.9063
10109 | 25811.25 | 4.8574
10110 | 26049.8711 | 4.9
10111 | 25885.8281 | 5.006
10112 | 25534.5645 | 4.907
10113 | 25742.5859 | 4.6695
10114 | 25492.7012 | 4.3961
10115 | 25132.4277 | 4.2672
10116 | 26519.5039 | 4.1413
10117 | 26238.2383 | 4.1518
10118 | 25974.9961 | 3.8629
10119 | 24731.7852 | 3.7398
10120 | 23421.0996 | 3.783
10121 | 22583.0566 | 3.6696
10122 | 20899.9395 | 3.5838
10123 | 18778.2207 | 3.5081
10124 | 17299.8809 | 3.4795
10125 | 16500.5977 | 3.1516
10126 | 15373.7734 | 2.9668
10127 | 14751.3848 | 2.8902
10128 | 13963.8672 | 2.6623
10129 | 13373.2471 | 2.7957
10130 | 12825.9629 | 2.8454
10131 | 12706.3311 | 2.8314
10132 | 12487.458 | 2.7633
10133 | 12259.0684 | 2.7524
10134 | 12129.3301 | 2.6897
10135 | 11927.7285 | 2.6983
10136 | 11998.9824 | 2.6774
10137 | 11842.3398 | 2.7237
10138 | 11917.8223 | 2.6552
10139 | 12273.3086 | 2.6397
10140 | 13337.7725 | 2.2511
10141 | 14415.1094 | 2.5495
10142 | 15446.1523 | 2.6615
10143 | 16571.7344 | 2.8808
10144 | 18060.5566 | 3.0988
10145 | 18909.293 | 3.6921
10146 | 20010.5801 | 3.612
10147 | 20625.5586 | 3.7835
10148 | 21102.9707 | 3.8061
10149 | 22712.4023 | 3.904
10150 | 22810.8145 | 4.0442
10151 | 22979.6055 | 4.1346
10152 | 22819.2031 | 4.1478
10153 | 22873.0156 | 3.9828
10154 | 22505.1406 | 3.7567
10155 | 22188.7812 | 3.6176
10156 | 22065.2988 | 3.5839
10157 | 22090.666 | 3.6702
10158 | 22033.3496 | 3.749
10159 | 21568.4863 | 3.7369
10160 | 22575.6777 | 3.586
10161 | 22789.8145 | 3.6295
10162 | 23130.5723 | 3.447
10163 | 22749.4238 | 3.2323
10164 | 23350.457 | 3.3185
10165 | 22971.6992 | 3.0855
10166 | 22503.793 | 2.964
10167 | 22062.3926 | 3.0556
10168 | 21027.0859 | 2.7642
10169 | 19562.2637 | 2.8236
10170 | 18191.8105 | 2.8282
10171 | 17410.3887 | 2.762
10172 | 16928.6172 | 2.824
10173 | 16198.46 | 2.655
10174 | 15462.1641 | 2.3738
10175 | 13788.3311 | 2.3404
10176 | 13972.3311 | 2.0716
10177 | 13966.3311 | 2.2055
10178 | 13808.3311 | 2.2909
10179 | 13734.3311 | 2.2878
10180 | 13200.9727 | 2.183
10181 | 12906.0996 | 1.8289
10182 | 12688.3086 | 1.7635
10183 | 12609.8037 | 1.7613
10184 | 12769.5 | 1.7498
10185 | 12540.2871 | 1.6714
10186 | 12567.2559 | 1.6251
10187 | 12521.4883 | 1.6985
10188 | 12765.6445 | 1.7026
10189 | 13052.5195 | 2.1022
10190 | 13760.3105 | 1.9358
10191 | 14462.8574 | 2.2686
10192 | 15267.2695 | 2.1488
10193 | 15958.5527 | 2.3332
10194 | 16736.7344 | 2.5375
10195 | 17798.7773 | 2.8331
10196 | 19051.2305 | 3.0402
10197 | 19822.4629 | 2.8593
10198 | 20283.8438 | 2.9339
10199 | 21045.2227 | 3.2594
10200 | 21734.9707 | 3.4731
10201 | 22128.7715 | 3.4839
10202 | 22500.4766 | 3.1814
10203 | 22696.4668 | 2.9908
10204 | 23221.5938 | 3.1844
10205 | 22940.0391 | 3.1619
10206 | 22618.4355 | 3.0789
10207 | 22451.1504 | 3.2977
10208 | 22706.2969 | 3.1663
10209 | 23267.6992 | 3.0691
10210 | 23343.2148 | 2.9599
10211 | 23738.5938 | 2.8121
10212 | 22824.8047 | 2.6844
10213 | 21600.4863 | 2.8079
10214 | 20696.3066 | 2.8244
10215 | 20326.1699 | 2.5645
10216 | 19869.1387 | 2.5951
10217 | 19495 | 2.5822
10218 | 19114.9785 | 2.7272
10219 | 18775.832 | 2.7774
10220 | 18172.0391 | 2.733
10221 | 17382.502 | 2.521
10222 | 16792.9648 | 2.2482
10223 | 15963.3105 | 2.1504
10224 | 15495.4062 | 2.3188
10225 | 15186.626 | 2.2918
10226 | 14752.0273 | 2.2299
10227 | 14447.334 | 2.2576
10228 | 14392.2363 | 1.8529
10229 | 13924.1934 | 1.8326
10230 | 13615.1816 | 1.8072
10231 | 13289.5293 | 1.8586
10232 | 13246.793 | 1.8904
10233 | 13214.1504 | 1.9478
10234 | 13366.4238 | 2.0062
10235 | 13727.0684 | 2.4141
10236 | 14622.0996 | 2.4559
10237 | 16178.9443 | 3.1014
10238 | 19706.7461 | 3.4082
10239 | 22437.4023 | 3.9074
10240 | 24263.2578 | 4.3016
10241 | 26628.7461 | 4.7664
10242 | 29582.7793 | 4.9482
10243 | 30089.5586 | 5.0066
10244 | 31055.1191 | 5.222
10245 | 31392.5195 | 5.0585
10246 | 30823.2324 | 5.2118
10247 | 29884.5703 | 5.3988
10248 | 30863.9922 | 5.0617
10249 | 30438.4551 | 5.3744
10250 | 33258.375 | 5.2547
10251 | 32922.5117 | 5.1276
10252 | 31241.5 | 5.2182
10253 | 29998.4766 | 5.1023
10254 | 29054.7793 | 5.0378
10255 | 29067.4219 | 4.9813
10256 | 29165.4004 | 5.1418
10257 | 30106.1074 | 4.8849
10258 | 28416.6211 | 4.7505
10259 | 29187.6523 | 4.5151
10260 | 29483.7891 | 4.3261
10261 | 28854.5059 | 4.2236
10262 | 29188.8965 | 4.0991
10263 | 29634.6641 | 4.1819
10264 | 28720.7578 | 4.1573
10265 | 28508.4844 | 4.2173
10266 | 28127.1992 | 4.2441
10267 | 27886.4844 | 3.9931
10268 | 26466.6289 | 3.5779
10269 | 25103.4375 | 3.1591
10270 | 22289.2461 | 2.917
10271 | 20088.4004 | 2.732
10272 | 18878.082 | 2.8196
10273 | 18129.0527 | 2.6157
10274 | 17565.1875 | 2.4594
10275 | 17235.209 | 2.5329
10276 | 16946.7988 | 2.5143
10277 | 16697.9023 | 2.4967
10278 | 16465.6719 | 2.4465
10279 | 16146.249 | 2.4996
10280 | 15956.5547 | 2.4632
10281 | 16169.0811 | 2.6226
10282 | 16177.0586 | 2.5599
10283 | 16097.4277 | 2.8854
10284 | 16661.1016 | 2.973
10285 | 18182.4316 | 3.3997
10286 | 21740.4863 | 3.7178
10287 | 24618.6367 | 4.2286
10288 | 27000.3984 | 4.7306
10289 | 28473.2207 | 5.2443
10290 | 29296.0215 | 5.1966
10291 | 30297.6973 | 5.1805
10292 | 31542.1504 | 5.4785
10293 | 32125.4355 | 5.6097
10294 | 32998.332 | 5.5509
10295 | 33253.9844 | 5.5017
10296 | 33042.9727 | 5.5048
10297 | 32119.2773 | 5.5523
10298 | 32610.0781 | 5.5275
10299 | 32423.0684 | 5.4835
10300 | 31563.2461 | 5.3637
10301 | 30735.4648 | 5.3712
10302 | 29992.4336 | 5.2704
10303 | 31168.0566 | 5.2607
10304 | 30824.5625 | 5.2942
10305 | 30056.5488 | 4.9974
10306 | 29637.9062 | 4.8131
10307 | 30450.707 | 4.6426
10308 | 30403.4434 | 4.3549
10309 | 30068.5703 | 4.2979
10310 | 30557.0762 | 4.0572
10311 | 30717.6016 | 3.9238
10312 | 30453.3281 | 3.9253
10313 | 30212.5703 | 3.9748
10314 | 29184.6426 | 3.8947
10315 | 28039.3145 | 3.8633
10316 | 27394.5352 | 3.7162
10317 | 25764.4492 | 3.4222
10318 | 22960.4355 | 3.0846
10319 | 21083.8223 | 3.0863
10320 | 19704.2402 | 2.8035
10321 | 19108.4961 | 2.6909
10322 | 18148.9785 | 2.6357
10323 | 17720.957 | 2.6449
10324 | 17356.1348 | 2.6427
10325 | 17280.6191 | 2.624
10326 | 16727.4922 | 2.6723
10327 | 16432.1855 | 2.8075
10328 | 16482.207 | 2.8243
10329 | 16418.7109 | 2.9925
10330 | 16751.334 | 2.9143
10331 | 17061.1016 | 2.9844
10332 | 18315.3047 | 3.0644
10333 | 19657.875 | 3.3683
10334 | 22143.6348 | 3.7246
10335 | 24244.5 | 4.1451
10336 | 27052.6934 | 4.6783
10337 | 29819.5684 | 4.9816
10338 | 31494.7695 | 5.0215
10339 | 31107.8242 | 4.976
10340 | 32756.4473 | 5.0735
10341 | 33279.4766 | 5.1705
10342 | 34900.1328 | 5.1417
10343 | 36412.7656 | 5.0007
10344 | 36263.9141 | 5.172
10345 | 33884.625 | 5.1907
10346 | 33412.1523 | 5.0827
10347 | 32870.332 | 5.1517
10348 | 31648.8027 | 5.1586
10349 | 30399.5391 | 5.1418
10350 | 30021.3066 | 5.1086
10351 | 30974.6133 | 5.026
10352 | 32177.8047 | 5.0232
10353 | 31523.8984 | 4.8392
10354 | 30152.2012 | 4.8229
10355 | 31486.75 | 4.5999
10356 | 31855.6445 | 4.4303
10357 | 30894.2227 | 4.3062
10358 | 30783.0977 | 4.1576
10359 | 30389.9492 | 4.184
10360 | 30280.9375 | 4.0578
10361 | 30152.043 | 3.9824
10362 | 29080.8945 | 3.9587
10363 | 28090.3242 | 3.951
10364 | 27206.3984 | 3.5151
10365 | 25448.7031 | 3.3474
10366 | 23052.3203 | 3.1951
10367 | 21133.0645 | 2.8508
10368 | 19611.5059 | 2.8076
10369 | 19083.3672 | 2.9587
10370 | 18410.4727 | 2.8758
10371 | 18059.8516 | 2.8757
10372 | 17503.0723 | 2.8928
10373 | 17111.8105 | 2.7735
10374 | 16989.3047 | 2.5669
10375 | 17005.6738 | 2.5925
10376 | 16821.1016 | 2.5311
10377 | 17060.2285 | 2.6894
10378 | 17366.3887 | 2.7272
10379 | 17637.8809 | 2.9778
10380 | 18262.4316 | 3.174
10381 | 19652.6328 | 3.6031
10382 | 23107.8164 | 3.979
10383 | 25806.082 | 4.3373
10384 | 27972.1875 | 4.9045
10385 | 29273.2637 | 5.314
10386 | 30945.2344 | 5.4484
10387 | 32038.2871 | 5.4623
10388 | 33772.8984 | 5.4862
10389 | 34968.8281 | 5.4278
10390 | 36674.293 | 5.5332
10391 | 37524.082 | 5.6055
10392 | 37652.2188 | 5.5086
10393 | 37340.3359 | 5.468
10394 | 36794.3125 | 5.3962
10395 | 35755.4688 | 5.2883
10396 | 34491.0586 | 5.2946
10397 | 32844.4688 | 5.3738
10398 | 31815.5293 | 5.4971
10399 | 31764.4023 | 5.4269
10400 | 32178.4453 | 5.2386
10401 | 32176.793 | 5.1162
10402 | 32343.2969 | 4.7992
10403 | 32854.9727 | 4.655
10404 | 32468.0781 | 4.335
10405 | 31156.8652 | 4.1991
10406 | 30354.2227 | 4.1445
10407 | 30675.2129 | 4.0572
10408 | 30033.8125 | 4.1076
10409 | 29480.6641 | 4.1376
10410 | 28693.127 | 4.2558
10411 | 28274.0938 | 3.9905
10412 | 27237.7773 | 3.6658
10413 | 25181.0488 | 3.4234
10414 | 22731.9297 | 3.0342
10415 | 20697.8223 | 2.8268
10416 | 19351.9883 | 2.6367
10417 | 19041.3477 | 2.6273
10418 | 18309.6211 | 2.5597
10419 | 20176.0801 | 2.6111
10420 | 19498.043 | 2.5287
10421 | 18769.3789 | 2.5004
10422 | 18593.4941 | 2.7202
10423 | 18694 | 2.783
10424 | 18618.6211 | 2.8073
10425 | 18543.2422 | 2.874
10426 | 18719.125 | 2.8008
10427 | 18417.6094 | 2.7725
10428 | 19221.6543 | 2.9803
10429 | 20528.2227 | 3.5609
10430 | 23844.8984 | 3.815
10431 | 26407.7891 | 4.265
10432 | 28995.8008 | 4.684
10433 | 30754.6465 | 5.0156
10434 | 31583.8125 | 5.1289
10435 | 31985.8359 | 5.2439
10436 | 32714.5 | 5.3425
10437 | 32589.2695 | 5.3939
10438 | 33217.2266 | 5.3684
10439 | 33317.5312 | 5.2573
10440 | 33343.2578 | 5.2225
10441 | 32513.4883 | 5.3557
10442 | 32865.2578 | 5.07
10443 | 31910.457 | 4.9844
10444 | 31534.1621 | 4.7831
10445 | 30955.6562 | 4.8729
10446 | 30176.7383 | 4.9199
10447 | 30000.8555 | 4.9007
10448 | 30176.7383 | 4.848
10449 | 30151.6113 | 4.4828
10450 | 30629.0156 | 4.0184
10451 | 31307.4258 | 4.0542
10452 | 31357.6777 | 4.1462
10453 | 30830.0234 | 4.0661
10454 | 30804.8984 | 3.9224
10455 | 30729.5195 | 3.8447
10456 | 30352.623 | 3.7788
10457 | 29523.4531 | 3.6492
10458 | 28242.0117 | 3.6887
10459 | 27463.0957 | 3.4799
10460 | 26231.9023 | 3.1536
10461 | 25251.9746 | 2.9719
10462 | 23141.3633 | 2.6599
10463 | 21960.4238 | 2.5342
10464 | 20980.4961 | 2.5313
10465 | 20176.4531 | 2.6828
10466 | 19447.791 | 2.5034
10467 | 19020.6426 | 2.3634
10468 | 18794.5039 | 2.2615
10469 | 18141.2227 | 2.1817
10470 | 17940.2109 | 2.1604
10471 | 17940.2109 | 2.1445
10472 | 18065.8418 | 2.1381
10473 | 17714.0723 | 2.208
10474 | 17764.3242 | 2.3227
10475 | 17764.3242 | 2.2655
10476 | 17915.084 | 1.9699
10477 | 18266.8516 | 2.2924
10478 | 19548.2969 | 2.3259
10479 | 18051.8066 | 2.7012
10480 | 18924.3457 | 3.101
10481 | 19581.6328 | 3.4482
10482 | 21104.5371 | 3.5028
10483 | 22522.0215 | 3.6391
10484 | 23521.3711 | 3.6525
10485 | 23492.0938 | 3.6574
10486 | 23656.3867 | 3.8358
10487 | 23673.7305 | 3.9042
10488 | 23573.9141 | 3.8999
10489 | 23183.5938 | 3.6493
10490 | 23330.6328 | 3.5744
10491 | 23744.7441 | 3.5791
10492 | 23091.793 | 3.5702
10493 | 23160.1406 | 3.5386
10494 | 22865.3281 | 3.6874
10495 | 21772.1504 | 3.7437
10496 | 21529.0645 | 3.7143
10497 | 21350.7188 | 3.6204
10498 | 21506.6016 | 3.5009
10499 | 22290.1406 | 3.4232
10500 | 23113.1934 | 3.1828
10501 | 22629.793 | 3.3176
10502 | 22083.0117 | 3.049
10503 | 21405.707 | 2.9509
10504 | 20783.3164 | 2.8537
10505 | 20384.5391 | 2.9164
10506 | 18990.8418 | 2.9061
10507 | 17784.4082 | 2.7992
10508 | 16642.207 | 2.7992
10509 | 16286.0703 | 2.599
10510 | 15554.7861 | 2.3006
10511 | 14914.4902 | 2.1527
10512 | 14184.7002 | 2.3138
10513 | 13597.5527 | 2.3082
10514 | 13196.1504 | 2.2752
10515 | 12830.0137 | 2.285
10516 | 12635.5508 | 1.9765
10517 | 12325.8037 | 1.826
10518 | 13292.7207 | 1.7675
10519 | 13211.5723 | 1.7601
10520 | 13049.709 | 1.7541
10521 | 12957.0664 | 1.9426
10522 | 13166.7715 | 2.0155
10523 | 11851.0742 | 2.0381
10524 | 11372.2637 | 1.8553
10525 | 11499.6543 | 1.7329
10526 | 12407.0039 | 1.8071
10527 | 13356.7188 | 2.1473
10528 | 14335.9619 | 2.0859
10529 | 16232.9219 | 2.4569
10530 | 17491.9961 | 2.6819
10531 | 18204.1035 | 2.8913
10532 | 19617.2637 | 2.8104
10533 | 20125.7695 | 2.9929
10534 | 21375.9609 | 2.9834
10535 | 21629.791 | 3.2739
10536 | 22117.5293 | 3.4589
10537 | 22672.2227 | 3.5126
10538 | 23400.709 | 3.2593
10539 | 23686.1094 | 3.1941
10540 | 24122.9316 | 3.3596
10541 | 23813.332 | 3.3489
10542 | 22687.1719 | 3.2867
10543 | 22332.2344 | 3.243
10544 | 22598.2344 | 3.3197
10545 | 22909.9102 | 3.167
10546 | 23326.4141 | 2.9948
10547 | 23577.8145 | 2.9766
10548 | 23017.2891 | 3.0254
10549 | 21686.4648 | 2.8911
10550 | 21375.9609 | 2.6355
10551 | 20704.3066 | 2.5692
10552 | 19876.125 | 2.6713
10553 | 19297.8516 | 2.7444
10554 | 19187.5996 | 3.1399
10555 | 18576.4316 | 2.9955
10556 | 17999.6504 | 2.81
10557 | 17214.1133 | 2.497
10558 | 16360.46 | 2.2397
10559 | 15462.374 | 2.1245
10560 | 14986.9951 | 1.9646
10561 | 14282.3516 | 2.0934
10562 | 13766.0996 | 2.1838
10563 | 13163.1328 | 2.2483
10564 | 12919.2773 | 2.2047
10565 | 12562.1074 | 2.1149
10566 | 12220.0859 | 1.8048
10567 | 11859.2949 | 1.8006
10568 | 11951.832 | 1.8521
10569 | 11894.3906 | 2.3262
10570 | 12053.4102 | 2.3166
10571 | 12215.3516 | 2.1423
10572 | 13063.0342 | 2.2838
10573 | 14962.5732 | 2.9081
10574 | 19095.7363 | 3.4229
10575 | 21739.3066 | 4.1711
10576 | 24705.4258 | 4.457
10577 | 27481.2715 | 4.7387
10578 | 30377.1387 | 5.1349
10579 | 30508.8125 | 5.0171
10580 | 31073.3066 | 5.2601
10581 | 30989.6758 | 5.3341
10582 | 31234.4961 | 5.3114
10583 | 33506.2344 | 5.3377
10584 | 30335.4648 | 5.31
10585 | 30396.707 | 5.1568
10586 | 31638.75 | 5.2188
10587 | 32403.4355 | 5.2336
10588 | 33621.5 | 4.9986
10589 | 32891.2031 | 5.1351
10590 | 31998.5527 | 5.1543
10591 | 33909.5469 | 5.0996
10592 | 34457.9688 | 4.9685
10593 | 34272.3359 | 4.7229
10594 | 32086.3398 | 4.3544
10595 | 32551.6758 | 4.1075
10596 | 32660.2676 | 3.998
10597 | 31926.9512 | 3.9795
10598 | 32092.7656 | 4.0655
10599 | 31891.6992 | 4.0505
10600 | 29906.4297 | 4.0396
10601 | 29504.7051 | 3.973
10602 | 28210.7539 | 4.0835
10603 | 27040.8379 | 3.9741
10604 | 26052.252 | 3.6631
10605 | 24288.9844 | 3.2908
10606 | 21959.8672 | 2.7846
10607 | 19754.2422 | 2.7868
10608 | 18747.9453 | 2.7709
10609 | 17600.1348 | 2.5572
10610 | 17086.3867 | 2.5303
10611 | 16619.3047 | 2.5385
10612 | 15935.9766 | 2.4639
10613 | 15754.7344 | 2.4399
10614 | 15392.208 | 2.4324
10615 | 15217.2803 | 2.4283
10616 | 15645.3838 | 2.4176
10617 | 15539.7734 | 2.7283
10618 | 15708.9746 | 2.6653
10619 | 15789.0693 | 2.8194
10620 | 16797.8496 | 2.9402
10621 | 17853.6836 | 3.3895
10622 | 21193.0742 | 3.7572
10623 | 23375.0352 | 4.3533
10624 | 26786.3555 | 4.0654
10625 | 29796.6094 | 4.3182
10626 | 31869.5293 | 4.1318
10627 | 32439.4141 | 4.3811
10628 | 33007.7109 | 4.6528
10629 | 33332.6055 | 4.619
10630 | 34003.6562 | 4.595
10631 | 33910.2383 | 4.6395
10632 | 34103.0156 | 4.636
10633 | 33862.375 | 4.4793
10634 | 34879.0586 | 4.8202
10635 | 34936.5547 | 5.2098
10636 | 32988.0781 | 5.2291
10637 | 32651.0449 | 5.1942
10638 | 31895.5508 | 5.2813
10639 | 31362.3613 | 5.1232
10640 | 30585.582 | 5.0245
10641 | 31442.3809 | 4.9507
10642 | 30217.5586 | 4.7444
10643 | 30460.6426 | 4.3009
10644 | 29454.9453 | 4.2842
10645 | 27948.5664 | 4.0804
10646 | 29236.4316 | 3.867
10647 | 30633.2109 | 3.7956
10648 | 30370.8223 | 3.7406
10649 | 28927.8633 | 3.935
10650 | 28388.5781 | 3.9011
10651 | 27622.0508 | 3.5754
10652 | 26396.7461 | 3.3832
10653 | 24539.9961 | 3.09
10654 | 22308.5078 | 2.9175
10655 | 21067.0645 | 2.6026
10656 | 20249.5273 | 2.3156
10657 | 19183.5996 | 2.2906
10658 | 18162.4102 | 2.2403
10659 | 17778.9355 | 2.246
10660 | 17418.3574 | 2.1866
10661 | 17352.5039 | 2.2089
10662 | 16834.4609 | 2.1971
10663 | 16833.1035 | 2.2247
10664 | 17041.1016 | 2.2325
10665 | 16495.1973 | 2.5017
10666 | 16758.7129 | 2.4544
10667 | 16916.2285 | 2.7072
10668 | 17980.293 | 2.8326
10669 | 19163.5781 | 3.357
10670 | 22248.625 | 3.7242
10671 | 25155.3008 | 4.1874
10672 | 28054.5781 | 4.5418
10673 | 30473.3066 | 5.1389
10674 | 31917.4141 | 5.2306
10675 | 32982.9531 | 5.3578
10676 | 35535.6055 | 5.4023
10677 | 35618.8477 | 5.5107
10678 | 35903.7461 | 5.1004
10679 | 36137.6289 | 5.0201
10680 | 34972.4375 | 5.1141
10681 | 35143.7031 | 5.11
10682 | 35944.3672 | 5.1504
10683 | 35459.7227 | 5.1203
10684 | 34375.6602 | 5.1587
10685 | 35270.5977 | 5.2433
10686 | 35377.5859 | 5.1712
10687 | 34295.4297 | 5.0726
10688 | 33222.0977 | 5.1899
10689 | 32198.5391 | 5.2622
10690 | 31990.6602 | 4.8851
10691 | 30714.9727 | 4.4745
10692 | 29872.5 | 4.3774
10693 | 28945.1504 | 4.0945
10694 | 29587.5605 | 4.2017
10695 | 30317.7422 | 4.1676
10696 | 29870.8457 | 4.0988
10697 | 29175.9297 | 4.0395
10698 | 28573.0352 | 3.8402
10699 | 27677.4746 | 3.672
10700 | 26529.6426 | 3.3912
10701 | 25238.3008 | 3.0395
10702 | 22398.6641 | 2.6867
10703 | 20457.1992 | 2.6396
10704 | 18685.5977 | 2.7299
10705 | 18015.6895 | 2.7184
10706 | 17028.1328 | 2.6291
10707 | 16699.375 | 2.6618
10708 | 16054.5938 | 2.5769
10709 | 15866.9619 | 2.6183
10710 | 15389.793 | 2.5771
10711 | 15211.6777 | 2.5908
10712 | 15383.3516 | 2.5767
10713 | 15434.7314 | 2.859
10714 | 15270.373 | 2.7849
10715 | 15780.4688 | 2.6618
10716 | 16461.2852 | 2.925
10717 | 18287.1562 | 3.1669
10718 | 21451.4902 | 3.4585
10719 | 23570.2031 | 3.922
10720 | 26727.25 | 4.5198
10721 | 29720.7793 | 4.7883
10722 | 33037.3438 | 5.044
10723 | 33962.8789 | 5.1997
10724 | 33869.8906 | 5.2227
10725 | 33414.9961 | 5.2369
10726 | 33334.9727 | 5.2164
10727 | 33172.7188 | 5.2942
10728 | 32307.8027 | 5.2144
10729 | 32181.8047 | 5.2005
10730 | 32969.3398 | 5.1388
10731 | 33177.1094 | 5.2157
10732 | 33392.8594 | 5.2142
10733 | 31613.7812 | 5.1473
10734 | 30838.4531 | 5.1799
10735 | 31433.3926 | 5.2043
10736 | 31023.4863 | 5.1832
10737 | 33213.8672 | 5.0551
10738 | 32415.9414 | 4.6034
10739 | 33098.8359 | 4.5088
10740 | 33082.2969 | 4.4959
10741 | 29272.2207 | 4.4088
10742 | 29532.4219 | 4.2168
10743 | 29955.0742 | 4.2384
10744 | 29810.916 | 4.2852
10745 | 29355.5371 | 4.2926
10746 | 28113.8203 | 4.2398
10747 | 27069.7773 | 4.0323
10748 | 25843.9648 | 3.5662
10749 | 24181.8789 | 3.246
10750 | 21487.8438 | 3.1788
10751 | 19635.875 | 2.8669
10752 | 18369.0742 | 2.5207
10753 | 17867.4199 | 2.7081
10754 | 16934.7559 | 2.6155
10755 | 16545.1895 | 2.6729
10756 | 15760.0479 | 2.7699
10757 | 15286.7637 | 2.7599
10758 | 15151.3848 | 2.5701
10759 | 14878.6055 | 2.4819
10760 | 15033.6367 | 2.4386
10761 | 15336.1221 | 2.6524
10762 | 15352.5322 | 2.7516
10763 | 15448.9326 | 2.9106
10764 | 16311.5332 | 3.1027
10765 | 17156.8398 | 3.5325
10766 | 20508.2734 | 3.9936
10767 | 23085.7305 | 4.5477
10768 | 26170.8398 | 4.9503
10769 | 27974.7148 | 5.2218
10770 | 29740.1797 | 5.2683
10771 | 30231.5586 | 5.4675
10772 | 31590.2461 | 5.5757
10773 | 30596.5918 | 5.4532
10774 | 31585.5293 | 5.2541
10775 | 30380.8848 | 5.362
10776 | 29966.5371 | 5.4488
10777 | 28454.6211 | 5.4213
10778 | 30048.8438 | 5.2831
10779 | 30756.2344 | 5.1623
10780 | 28254.041 | 5.1682
10781 | 28015.7266 | 5.3589
10782 | 26704.1445 | 5.3598
10783 | 27074.2812 | 5.0851
10784 | 27479.1992 | 4.9167
10785 | 27472.9258 | 4.8183
10786 | 28396.3477 | 4.5271
10787 | 29479.4219 | 4.4466
10788 | 28839.4941 | 4.4203
10789 | 27956.4414 | 4.2743
10790 | 27656.3262 | 4.2311
10791 | 27194.6504 | 4.1605
10792 | 26930.3984 | 4.0804
10793 | 26105.9648 | 4.1003
10794 | 24975.1641 | 3.997
10795 | 24011.7422 | 3.7538
10796 | 23007.6992 | 3.4127
10797 | 21726.3496 | 3.1462
10798 | 20020.5391 | 3.0161
10799 | 18186.9375 | 2.8494
10800 | 16829.3555 | 2.7503
10801 | 16053.6797 | 2.5541
10802 | 15439.1738 | 2.4486
10803 | 14926.5957 | 2.4719
10804 | 14320.9004 | 2.6216
10805 | 13977.752 | 2.6273
10806 | 13656.9941 | 2.5755
10807 | 13240.7637 | 2.5015
10808 | 13149.0459 | 2.5346
10809 | 13006.1523 | 2.6537
10810 | 13207.2773 | 2.6175
10811 | 13216.9082 | 2.5312
10812 | 13500.6797 | 2.2577
10813 | 14376.7207 | 2.2552
10814 | 16608.8496 | 2.6275
10815 | 17744.4102 | 2.9551
10816 | 18856.3359 | 3.2137
10817 | 19751.7578 | 3.5492
10818 | 21051.0859 | 3.8232
10819 | 22344.8984 | 3.9476
10820 | 23937.4902 | 4.0219
10821 | 24059.375 | 4.1052
10822 | 24449.0039 | 4.0867
10823 | 24491.7852 | 4.0162
10824 | 24141.2363 | 4.0997
10825 | 24249.2793 | 4.0618
10826 | 23388.0664 | 3.9102
10827 | 22727.9629 | 3.6743
10828 | 22642.9727 | 3.4922
10829 | 22196.7285 | 3.4293
10830 | 21665.0762 | 3.4734
10831 | 21330.4453 | 3.5127
10832 | 21227.7285 | 3.4324
10833 | 21140.7188 | 3.5103
10834 | 21868.0039 | 3.3572
10835 | 23120.0684 | 3.3029
10836 | 23154.4355 | 3.2059
10837 | 23148.8242 | 3.2987
10838 | 23265.2148 | 3.0777
10839 | 22546.7812 | 2.7482
10840 | 22004.5078 | 2.8852
10841 | 21429.2227 | 2.8441
10842 | 19944.5391 | 2.8815
10843 | 18087.168 | 2.7817
10844 | 16609.3555 | 2.888
10845 | 15946.3008 | 2.6491
10846 | 15268.2793 | 2.3301
10847 | 14733.4785 | 2.3262
10848 | 14086.7207 | 2.3776
10849 | 13310.2871 | 2.2066
10850 | 12798.0566 | 2.3041
10851 | 12307.3203 | 2.3181
10852 | 12080.9082 | 2.242
10853 | 11711.2549 | 2.1878
10854 | 11506.0137 | 2.022
10855 | 11443.5293 | 1.7483
10856 | 11245.8125 | 1.703
10857 | 11258.6855 | 1.7307
10858 | 11236.1797 | 1.6572
10859 | 11031.7891 | 1.6746
10860 | 11110.8008 | 2.0787
10861 | 11506.2129 | 1.9834
10862 | 12892.5195 | 1.8801
10863 | 13699.6875 | 2.3038
10864 | 14696.6689 | 2.4821
10865 | 14949.1943 | 2.4865
10866 | 16044.8379 | 2.4869
10867 | 17234.6816 | 2.8117
10868 | 18160.418 | 2.9848
10869 | 18876.873 | 3.1586
10870 | 19810.7695 | 3.0153
10871 | 20699.959 | 3.3624
10872 | 20969.582 | 3.309
10873 | 21286.2559 | 3.5598
10874 | 21962.6777 | 3.3089
10875 | 21627.9922 | 3.155
10876 | 21628.8047 | 3.2478
10877 | 21498.7383 | 3.2683
10878 | 21452.541 | 3.1894
10879 | 21312.918 | 2.9111
10880 | 21656.3711 | 2.9709
10881 | 21959.6328 | 3.1611
10882 | 22588.7812 | 3.1657
10883 | 23063.5625 | 3.0559
10884 | 22243.7715 | 2.9806
10885 | 20632.1914 | 3.0283
10886 | 19924.7695 | 2.9711
10887 | 19692.7695 | 2.9609
10888 | 19249.6211 | 3.0416
10889 | 18971.7168 | 3.1506
10890 | 18594.9375 | 3.0764
10891 | 18080.293 | 2.898
10892 | 17537.1465 | 2.6457
10893 | 16790.8496 | 2.6399
10894 | 16575.4492 | 2.1709
10895 | 15902.0703 | 2.0176
10896 | 14980.2588 | 1.9676
10897 | 14524.7207 | 1.9339
10898 | 13950.0996 | 1.8534
10899 | 13615.1523 | 2.1345
10900 | 13159.9414 | 2.1782
10901 | 12990.6562 | 2.1378
10902 | 12681.8984 | 1.7728
10903 | 12297.8555 | 1.7861
10904 | 12311.9922 | 2.0295
10905 | 12318.6133 | 2.1552
10906 | 12524.5391 | 1.9377
10907 | 12343.5508 | 2.0497
10908 | 13043.666 | 2.3455
10909 | 14786.46 | 2.9585
10910 | 18745.1348 | 3.4632
10911 | 21012.2441 | 4.0762
10912 | 23299.8359 | 4.3902
10913 | 25289.0703 | 4.8116
10914 | 26694.2617 | 4.9772
10915 | 27678.3242 | 5.1913
10916 | 29684.043 | 5.1521
10917 | 30046.707 | 5.2194
10918 | 30254.8438 | 5.3019
10919 | 30330.9805 | 5.2516
10920 | 30093.4648 | 5.1726
10921 | 30621.3711 | 5.2232
10922 | 32603.8477 | 5.1359
10923 | 32785.8672 | 4.9984
10924 | 31250.3809 | 4.8939
10925 | 31762.3086 | 4.9515
10926 | 29245.7891 | 4.9259
10927 | 29010.0215 | 4.9827
10928 | 30252.8438 | 4.9468
10929 | 30956.2461 | 4.9786
10930 | 29110.748 | 4.4793
10931 | 29626.3164 | 4.3212
10932 | 29045.7695 | 4.3205
10933 | 27985.957 | 4.2617
10934 | 28415.6328 | 3.8811
10935 | 28016.5996 | 3.8449
10936 | 27283.293 | 3.7348
10937 | 27328.1875 | 3.9773
10938 | 26728.2812 | 3.8468
10939 | 26044.3535 | 3.7098
10940 | 24732.1758 | 3.3577
10941 | 23270.3418 | 2.9186
10942 | 20521.5684 | 2.7399
10943 | 18813.5996 | 2.534
10944 | 17194.0195 | 2.5543
10945 | 16508.4824 | 2.4849
10946 | 16002.3438 | 2.2976
10947 | 15787.6289 | 2.3409
10948 | 15314.1133 | 2.2802
10949 | 15203.9766 | 2.2635
10950 | 15017.333 | 2.2488
10951 | 14811.7227 | 2.244
10952 | 14684.7637 | 2.2706
10953 | 14530.2588 | 2.4673
10954 | 14674.0059 | 2.4285
10955 | 15009.7969 | 2.6621
10956 | 15722.6914 | 2.7343
10957 | 17282.5254 | 3.1281
10958 | 19947.5488 | 3.6295
10959 | 22118.2773 | 4.1248
10960 | 25345.7109 | 4.593
10961 | 27035.7988 | 4.7727
10962 | 28121.7266 | 4.7806
10963 | 30178.3594 | 4.8401
10964 | 30929.7617 | 4.8478
10965 | 31515.9199 | 4.8683
10966 | 33409.7539 | 5.117
10967 | 34136.9219 | 5.0827
10968 | 33912.8047 | 5.0426
10969 | 32979.5 | 5.0981
10970 | 33356.0039 | 5.1686
10971 | 34090.9453 | 5.1488
10972 | 32403.0879 | 5.1288
10973 | 32723.0898 | 5.107
10974 | 32187.6895 | 5.0933
10975 | 32223.8262 | 5.1414
10976 | 30237.4648 | 5.056
10977 | 29546.2734 | 4.7722
10978 | 29023.5176 | 4.326
10979 | 30448.9512 | 4.2713
10980 | 29342.793 | 4.2318
10981 | 28345.1875 | 4.1827
10982 | 28432.8516 | 4.0532
10983 | 28592.873 | 4.0185
10984 | 27663.5469 | 3.9851
10985 | 27563.8203 | 4.0799
10986 | 27356.6738 | 4.0303
10987 | 26720.4922 | 3.8997
10988 | 25415.5762 | 3.5016
10989 | 23323.582 | 3.2153
10990 | 20760.3066 | 2.9256
10991 | 18582.4512 | 2.7967
10992 | 17665.3984 | 2.911
10993 | 17639.7871 | 2.6943
10994 | 16813.2383 | 2.5163
10995 | 16107.9258 | 2.5434
10996 | 15545.6797 | 2.5468
10997 | 15453.7754 | 2.5188
10998 | 15102.6484 | 2.4475
10999 | 14736.374 | 2.4514
11000 | 14964.5322 | 2.4309
11001 | 16155.4707 | 2.6873
11002 | 17190.3652 | 2.7212
11003 | 17377.9043 | 2.8918
11004 | 17427.6504 | 3.1165
11005 | 17153.4824 | 3.4834
11006 | 20435.0137 | 3.7799
11007 | 22610.7617 | 4.4605
11008 | 26335.6602 | 4.9924
11009 | 27911.3379 | 5.3222
11010 | 29746.0137 | 5.2814
11011 | 30890.1094 | 5.3792
11012 | 32087.25 | 5.5929
11013 | 32140.8672 | 5.5435
11014 | 31730.4883 | 5.6029
11015 | 32640.2148 | 5.596
11016 | 32250.2148 | 5.5766
11017 | 32217.5742 | 5.6015
11018 | 32103.5742 | 5.509
11019 | 32061.5742 | 5.385
11020 | 32169.5742 | 5.363
11021 | 32073.5742 | 5.4454
11022 | 32389.5742 | 5.2958
11023 | 32401.5742 | 5.2551
11024 | 32319.5742 | 5.3102
11025 | 32225.5742 | 5.1861
11026 | 32175.5742 | 5.0074
11027 | 32271.5742 | 4.794
11028 | 32659.5742 | 4.6812
11029 | 29613.0547 | 4.5923
11030 | 29717.9062 | 4.3801
11031 | 29046.8945 | 4.255
11032 | 29680.2969 | 4.2776
11033 | 28674.9883 | 4.2586
11034 | 27716.6934 | 4.0626
11035 | 26924.1465 | 4.0826
11036 | 25752.1016 | 3.4588
11037 | 23522.3418 | 3.1873
11038 | 21275.3398 | 3.0787
11039 | 19352.4961 | 2.7995
11040 | 18131.8105 | 2.6663
11041 | 17390.3867 | 2.7765
11042 | 16690.5039 | 2.7937
11043 | 16450.0391 | 2.8359
11044 | 15966.5254 | 2.8091
11045 | 15537.4707 | 2.8183
11046 | 15390.46 | 2.4858
11047 | 15212.1133 | 2.4617
11048 | 15333.6592 | 2.3736
11049 | 15096.1426 | 2.5766
11050 | 15150.9004 | 2.8192
11051 | 15042.2363 | 2.9919
11052 | 15977.626 | 3.2142
11053 | 17250.5664 | 3.4787
11054 | 20902.8125 | 3.9206
11055 | 22949.1953 | 4.5257
11056 | 26381.2285 | 4.8797
11057 | 28734.3672 | 5.287
11058 | 31092.3828 | 5.3862
11059 | 31814.5391 | 5.5173
11060 | 32535.457 | 5.5167
11061 | 32539.9102 | 5.8022
11062 | 34293.4258 | 5.8814
11063 | 35603.6289 | 5.8998
11064 | 33955.0156 | 5.7411
11065 | 34429.5664 | 5.6037
11066 | 35780.3672 | 5.5995
11067 | 36272.0391 | 5.5092
11068 | 35457.1016 | 5.419
11069 | 35173.1016 | 5.5436
11070 | 34913.7031 | 5.5575
11071 | 34289.9336 | 5.4389
11072 | 33753.7734 | 5.5078
11073 | 30822.8652 | 5.3798
11074 | 31358.2676 | 5.038
11075 | 32391.2031 | 4.7847
11076 | 32176.8145 | 4.7213
11077 | 31666.6562 | 4.4196
11078 | 31520.5195 | 4.374
11079 | 30946.2461 | 4.3092
11080 | 30428.4551 | 4.4965
11081 | 29601.5371 | 4.3647
11082 | 28637.6328 | 4.3028
11083 | 28313.3359 | 4.0007
11084 | 27087.9141 | 3.7412
11085 | 25095.668 | 3.1902
11086 | 22781.1719 | 2.9781
11087 | 21091.7285 | 2.7999
11088 | 19803.875 | 2.8063
11089 | 18882.9785 | 2.7531
11090 | 18140.3359 | 2.802
11091 | 17715.7363 | 2.7891
11092 | 16378.8711 | 2.8005
11093 | 15781.9336 | 2.7722
11094 | 15656.5312 | 2.7105
11095 | 15895.543 | 2.7408
11096 | 15815.6797 | 2.7016
11097 | 15589.4277 | 2.8516
11098 | 15656.5312 | 2.809
11099 | 15885.7959 | 2.9814
11100 | 16816.8711 | 3.1229
11101 | 18024.1562 | 3.4455
11102 | 21374.6016 | 3.91
11103 | 23682.7305 | 4.4585
11104 | 27765.8203 | 5.0012
11105 | 30859.1172 | 5.4463
11106 | 33990.1445 | 5.5364
11107 | 35362.2266 | 5.5333
11108 | 37579.5977 | 5.6273
11109 | 36339.9023 | 5.6775
11110 | 36401.1641 | 5.7423
11111 | 37180.7031 | 5.698
11112 | 38332.2656 | 5.6538
11113 | 35653.9961 | 5.5876
11114 | 32744.3477 | 5.3801
11115 | 31437.916 | 5.2369
11116 | 30780.834 | 5.1709
11117 | 29721.7695 | 5.1705
11118 | 28680.5059 | 5.0753
11119 | 28506.6211 | 4.9135
11120 | 28801.5156 | 4.9469
11121 | 28509.3574 | 4.9886
11122 | 29163.0117 | 4.6971
11123 | 30775.8555 | 4.5471
11124 | 29433.2852 | 4.6972
11125 | 29032.0215 | 4.4837
11126 | 29237.8848 | 4.3264
11127 | 28630.3672 | 4.253
11128 | 28156.7148 | 4.2739
11129 | 27655.7031 | 4.2142
11130 | 26850.9023 | 4.0098
11131 | 25343.1855 | 3.5374
11132 | 24232.1328 | 3.2505
11133 | 22875.1719 | 3.1011
11134 | 20905.9609 | 2.8993
11135 | 19351.5039 | 2.7168
11136 | 18196.9375 | 2.4725
11137 | 17439.8828 | 2.3915
11138 | 16609.8809 | 2.2591
11139 | 15947.9971 | 2.5037
11140 | 15499.3555 | 2.5862
11141 | 15470.4805 | 2.5906
11142 | 15109.0605 | 2.2516
11143 | 15016.1133 | 2.2656
11144 | 14747.1543 | 2.4668
11145 | 14429.71 | 2.5872
11146 | 14421.6152 | 2.6357
11147 | 14164.0781 | 2.647
11148 | 14525.1104 | 2.2844
11149 | 14729.6152 | 2.1333
11150 | 16271.9326 | 2.2555
11151 | 17239.6289 | 2.7283
11152 | 18222.1777 | 3.139
11153 | 18962.2188 | 3.491
11154 | 20906.582 | 3.6921
11155 | 21710.877 | 3.7858
11156 | 22989.6875 | 3.7784
11157 | 23295.6445 | 3.7306
11158 | 23435.3828 | 3.9069
11159 | 23003.0059 | 4.1465
11160 | 22696.9414 | 4.1782
11161 | 22916.7109 | 4.1445
11162 | 24149.248 | 3.9982
11163 | 23866.8359 | 3.7569
11164 | 22426.4238 | 3.6037
11165 | 22438.1094 | 3.6424
11166 | 22263.2344 | 3.5886
11167 | 22045.3809 | 3.5837
11168 | 21806.7402 | 3.5818
11169 | 22095.5195 | 3.7032
11170 | 23210.8242 | 3.571
11171 | 24214.8691 | 3.3428
11172 | 24473.7637 | 3.4618
11173 | 24070.9844 | 3.2264
11174 | 23895.3945 | 3.1691
11175 | 23135.6992 | 3.358
11176 | 22706.3203 | 3.3171
11177 | 21962.9199 | 3.0803
11178 | 20596.625 | 2.9482
11179 | 18947.1152 | 3.0964
11180 | 17724.5469 | 2.8369
11181 | 17127.6074 | 2.788
11182 | 16505.8398 | 2.4209
11183 | 15495.4062 | 2.259
11184 | 14717.8682 | 2.1968
11185 | 14047.8477 | 2.3706
11186 | 13465.5723 | 2.1556
11187 | 13151.5293 | 2.3061
11188 | 12875.8242 | 2.2609
11189 | 12599.5732 | 2.2099
11190 | 12760.6562 | 2.1867
11191 | 13122.4043 | 1.9825
11192 | 13083.6465 | 1.8017
11193 | 13167.5293 | 1.812
11194 | 13216.6777 | 1.8084
11195 | 13196.2871 | 1.7622
11196 | 13443.5527 | 1.7875
11197 | 13979.5732 | 1.9082
11198 | 14899.5 | 1.9552
11199 | 15258.5312 | 2.072
11200 | 16194.0703 | 2.3204
11201 | 16409.7227 | 2.318
11202 | 17567.5137 | 2.6773
11203 | 18553.5781 | 3.0223
11204 | 20102.4844 | 2.8732
11205 | 20858.1699 | 2.8822
11206 | 22401.6875 | 2.9762
11207 | 23338.582 | 3.1446
11208 | 23569.3086 | 3.1676
11209 | 23722.9297 | 3.42
11210 | 23742.3848 | 3.3914
11211 | 24299.2051 | 3.3361
11212 | 25681.0703 | 3.1622
11213 | 23764.9844 | 3.026
11214 | 23331.9727 | 3.0721
11215 | 23006.6875 | 3.1369
11216 | 23204.9414 | 3.1446
11217 | 23745.4883 | 3.0733
11218 | 24951.1641 | 3.1047
11219 | 25342.4277 | 2.9454
11220 | 23734.1094 | 2.8882
11221 | 22158.5078 | 2.7344
11222 | 21409.0859 | 2.7151
11223 | 20913.4551 | 2.7813
11224 | 20548.3066 | 3.0156
11225 | 20085 | 3.1952
11226 | 19982.6543 | 3.0316
11227 | 19309.9883 | 2.6919
11228 | 18594.8203 | 2.7719
11229 | 18047.418 | 2.6128
11230 | 17395.9961 | 2.1675
11231 | 16651.332 | 2.0711
11232 | 16036.4375 | 2.0144
11233 | 15872.6875 | 2.1402
11234 | 14847.3037 | 2.2383
11235 | 14683.3105 | 2.2847
11236 | 14557.9316 | 2.2172
11237 | 14461.1748 | 2.2121
11238 | 13494.9951 | 2.2171
11239 | 13131.8467 | 2.2467
11240 | 13155.248 | 2.2456
11241 | 13086.8584 | 2.1536
11242 | 13279.1113 | 2.1815
11243 | 13532.1943 | 2.4004
11244 | 14603.8896 | 2.5377
11245 | 16371.0811 | 3.2392
11246 | 20840.3281 | 3.5958
11247 | 23250.8477 | 4.254
11248 | 26665.3867 | 4.6201
11249 | 30342.5918 | 5.2331
11250 | 32960.4688 | 5.4796
11251 | 34806.7109 | 5.3957
11252 | 37055.6953 | 5.5378
11253 | 37099.5781 | 5.4739
11254 | 36956.6797 | 5.7921
11255 | 37566.4727 | 5.6917
11256 | 37053.0703 | 5.6522
11257 | 36188.0391 | 5.6138
11258 | 36095.1445 | 5.5665
11259 | 36395.5352 | 5.4607
11260 | 36506.0391 | 5.3816
11261 | 36686.9336 | 5.5853
11262 | 35655.0078 | 5.4393
11263 | 36067.3984 | 5.2909
11264 | 35514.1328 | 5.2442
11265 | 36191.5547 | 5.0951
11266 | 34915.2188 | 4.7754
11267 | 33779.0391 | 4.5277
11268 | 32068.7715 | 4.5586
11269 | 31767.2988 | 4.3845
11270 | 31399.7617 | 4.1931
11271 | 31279.1387 | 4.0918
11272 | 30564.3398 | 4.1881
11273 | 29650.0645 | 4.2817
11274 | 28305.5898 | 4.0635
11275 | 27853.7031 | 3.8434
11276 | 26646.7656 | 3.328
11277 | 25397.0918 | 3.0466
11278 | 22881.5625 | 2.9917
11279 | 20559.5684 | 2.6845
11280 | 19502.3789 | 2.7925
11281 | 18346.4727 | 2.5371
11282 | 17621.5059 | 2.4699
11283 | 17061.0078 | 2.6237
11284 | 16805.4922 | 2.7678
11285 | 16468.4609 | 2.7399
11286 | 16001.5645 | 2.6931
11287 | 15884.4375 | 2.6916
11288 | 16262.208 | 2.7252
11289 | 16464.9648 | 2.8814
11290 | 16934.8711 | 2.7247
11291 | 16914.6172 | 3.0583
11292 | 17398.2715 | 3.0536
11293 | 18566.4941 | 3.4472
11294 | 23204.2012 | 3.8841
11295 | 25840.8789 | 4.3643
11296 | 28348.0898 | 5.7917
11297 | 30202.0898 | 6.2642
11298 | 31584.0996 | 6.4144
11299 | 32909.5938 | 6.4353
11300 | 35290.0938 | 6.6288
11301 | 34703.332 | 6.6526
11302 | 34762.7109 | 6.5682
11303 | 35025.8672 | 6.5536
11304 | 34746.5078 | 6.5601
11305 | 34807.7656 | 6.7135
11306 | 35523.8828 | 6.7006
11307 | 35459.2383 | 6.59
11308 | 33909.1523 | 6.3379
11309 | 35224.8516 | 6.4601
11310 | 33472.1211 | 6.5431
11311 | 34386.3008 | 6.3221
11312 | 32858.7227 | 5.3469
11313 | 32542.6992 | 5.2314
11314 | 31817.0469 | 5.0435
11315 | 32265.5723 | 4.6569
11316 | 30955.8555 | 4.5065
11317 | 30569.3496 | 4.5859
11318 | 30264.4531 | 4.3389
11319 | 30416.8438 | 4.145
11320 | 29946.9395 | 4.1678
11321 | 29031.7695 | 4.2094
11322 | 28397.8633 | 4.0436
11323 | 27262.7871 | 3.9457
11324 | 26715.3867 | 3.3833
11325 | 26467.7773 | 3.3512
11326 | 23493.0547 | 2.9996
11327 | 22767.1562 | 2.8781
11328 | 21467.25 | 2.6695
11329 | 20256.3125 | 2.5882
11330 | 19119.4258 | 2.4977
11331 | 18797.1895 | 2.5229
11332 | 18631.873 | 2.4891
11333 | 18201.2734 | 2.7421
11334 | 17864.9785 | 2.7167
11335 | 17647.2109 | 2.7042
11336 | 17817.7578 | 2.6755
11337 | 17867.4609 | 2.911
11338 | 18510.5684 | 2.839
11339 | 18802.7266 | 2.7384
11340 | 19325.6211 | 3.0456
11341 | 20854.0742 | 3.3881
11342 | 24531.418 | 3.8806
11343 | 27537.5684 | 4.4691
11344 | 30292.3398 | 4.8443
11345 | 32874.7188 | 5.0201
11346 | 34048.5312 | 5.185
11347 | 35730.8711 | 5.191
11348 | 36830.6836 | 5.2631
11349 | 36609.9258 | 5.4886
11350 | 36857.1875 | 5.5383
11351 | 37242.0312 | 5.395
11352 | 37118.8594 | 5.3341
11353 | 36070.4375 | 5.1464
11354 | 36907.6953 | 5.0879
11355 | 36759.1875 | 5.0167
11356 | 35299.8594 | 4.9491
11357 | 33600.3945 | 4.9818
11358 | 33215.5195 | 4.9298
11359 | 32506.2148 | 4.904
11360 | 32575.9609 | 4.9082
11361 | 33169.8672 | 4.7025
11362 | 31110.6348 | 4.5092
11363 | 31739.6875 | 4.3536
11364 | 30196.3164 | 4.1554
11365 | 29636.4316 | 3.8683
11366 | 30100.2012 | 3.7353
11367 | 31510.6562 | 3.8385
11368 | 30313.3496 | 4.0012
11369 | 29576.4316 | 4.0515
11370 | 29026.873 | 3.9109
11371 | 28944.0215 | 3.6141
11372 | 27528.6719 | 3.2306
11373 | 26382.8828 | 3.1565
11374 | 23554.6152 | 2.7439
11375 | 21561.498 | 2.7806
11376 | 20096.4219 | 2.6416
11377 | 19290.127 | 2.3469
11378 | 18375.3477 | 2.3169
11379 | 18213.043 | 2.6034
11380 | 17854.1777 | 2.4946
11381 | 17728.1777 | 2.4973
11382 | 16926.3652 | 2.4669
11383 | 16567.7246 | 2.4926
11384 | 16634.6172 | 2.4741
11385 | 16616.7344 | 2.5969
11386 | 16948.7539 | 2.7626
11387 | 16552.9863 | 2.6103
11388 | 17306.3867 | 2.8215
11389 | 19036.4727 | 2.9932
11390 | 22782.0664 | 3.6615
11391 | 25348.332 | 4.1911
11392 | 28843.4434 | 4.7963
11393 | 31983.8672 | 5.1238
11394 | 32510.7207 | 5.2502
11395 | 33015.1094 | 5.2762
11396 | 36344.7969 | 5.2022
11397 | 37092.6797 | 5.1737
11398 | 37104.5859 | 5.2167
11399 | 36316.7773 | 5.3478
11400 | 35210.4805 | 5.382
11401 | 34999.0781 | 5.2236
11402 | 34580.9453 | 5.2696
11403 | 35317.7227 | 5.0384
11404 | 36558.9141 | 5.0657
11405 | 35947.5156 | 5.0247
11406 | 34275.3125 | 4.9773
11407 | 35065.2188 | 5.01
11408 | 33730.9414 | 4.8692
11409 | 33981.9531 | 4.5218
11410 | 32335.5723 | 4.3999
11411 | 32117.1836 | 4.4149
11412 | 31701.9199 | 4.3182
11413 | 29767.9277 | 4.1409
11414 | 29593.6758 | 4.0893
11415 | 30376.5918 | 4.2591
11416 | 30829.9922 | 4.2503
11417 | 29477.1699 | 4.1516
11418 | 28733.4941 | 4.0301
11419 | 28206.0957 | 3.5917
11420 | 27116.6504 | 3.1728
11421 | 25600.9551 | 2.9757
11422 | 23143.9531 | 2.7809
11423 | 21052.9492 | 2.6347
11424 | 19651.3906 | 2.7445
11425 | 18961.8516 | 2.446
11426 | 18054.1992 | 2.3483
11427 | 17306.0625 | 2.3819
11428 | 16831.4414 | 2.4937
11429 | 16299.0078 | 2.4488
11430 | 16108.6182 | 2.3128
11431 | 15892.2715 | 2.3219
11432 | 15943.4922 | 2.2959
11433 | 15618.9219 | 2.4522
11434 | 15385.1533 | 2.6511
11435 | 15684.5537 | 2.745
11436 | 16505.7031 | 3.0424
11437 | 18253.8105 | 3.2429
11438 | 21502.4863 | 3.7897
11439 | 23996.3848 | 4.3246
11440 | 27684.6934 | 4.7517
11441 | 29418.1582 | 5.0254
11442 | 30724.6348 | 5.1217
11443 | 30806.7285 | 5.2205
11444 | 31974.2891 | 5.288
11445 | 31566.1504 | 5.2894
11446 | 32343.457 | 5.1931
11447 | 32238.5625 | 5.2138
11448 | 32123.1836 | 5.2245
11449 | 30781.4863 | 5.0476
11450 | 31165.5078 | 4.9731
11451 | 30176.5703 | 4.9574
11452 | 29323.7891 | 4.7858
11453 | 28459.2422 | 4.8523
11454 | 27396.8105 | 4.7931
11455 | 27369.6836 | 4.5818
11456 | 28006.9688 | 4.5589
11457 | 28005.8203 | 4.4114
11458 | 29368.6641 | 4.1692
11459 | 29880.9375 | 4.1168
11460 | 28636.2539 | 4.1144
11461 | 28942 | 3.833
11462 | 28000.0723 | 3.8438
11463 | 28304.3477 | 3.8959
11464 | 27950.4629 | 3.9543
11465 | 27072.5352 | 3.8598
11466 | 26446.375 | 3.4705
11467 | 25114.9336 | 3.2697
11468 | 24085.625 | 3.0108
11469 | 22998.6875 | 2.7262
11470 | 20912.0742 | 2.6541
11471 | 19575.6426 | 2.4337
11472 | 17649.9043 | 2.2201
11473 | 16768.4805 | 2.3758
11474 | 16003.9541 | 2.2657
11475 | 15459.2617 | 2.0519
11476 | 14889.0176 | 2.0193
11477 | 14689.3633 | 1.9643
11478 | 14511.1094 | 1.9365
11479 | 14050.8359 | 1.9103
11480 | 13602.1934 | 1.9106
11481 | 13738.3086 | 2.0206
11482 | 14001.457 | 2.0948
11483 | 13654.5625 | 2.0993
11484 | 13792.4473 | 1.9726
11485 | 14098.8369 | 2.1148
11486 | 15470.6484 | 2.3784
11487 | 16411.1016 | 2.8002
11488 | 17823.2812 | 3.1165
11489 | 19172.125 | 3.3043
11490 | 20672.4219 | 3.3743
11491 | 21844.7617 | 3.4341
11492 | 23179.8359 | 3.5147
11493 | 23565.4141 | 3.8033
11494 | 24197.416 | 3.6382
11495 | 23760.3105 | 3.7569
11496 | 23718.5723 | 3.7666
11497 | 23501.0352 | 3.6001
11498 | 23225.3086 | 3.5101
11499 | 22951.2988 | 3.4878
11500 | 22283.0742 | 3.4551
11501 | 22273.5293 | 3.4832
11502 | 22295.5391 | 3.5772
11503 | 22336.2344 | 3.6034
11504 | 22220.0254 | 3.5476
11505 | 22351.0117 | 3.4148
11506 | 23450.457 | 3.1672
11507 | 24558.5215 | 3.1008
11508 | 24428.5 | 3.0999
11509 | 24014.248 | 3.1503
11510 | 23576.4785 | 2.8876
11511 | 23250.8242 | 2.7382
11512 | 22932.1836 | 2.8264
11513 | 22158.3926 | 2.9408
11514 | 20979.707 | 3.0207
11515 | 19408.2422 | 2.9632
11516 | 17729.2812 | 2.8174
11517 | 16936.3652 | 2.5326
11518 | 16235.9551 | 2.2457
11519 | 15439.4062 | 2.0449
11520 | 14744.8789 | 1.9537
11521 | 14197.457 | 1.9052
11522 | 13672.5625 | 1.8648
11523 | 13288.4678 | 1.8612
11524 | 12797.0889 | 1.7918
11525 | 12183.4355 | 1.8864
11526 | 11794.2656 | 2.0494
11527 | 11686.5195 | 1.7077
11528 | 11498.7715 | 1.6605
11529 | 11291.8125 | 1.6786
11530 | 11325.0742 | 1.7356
11531 | 11219.3047 | 2.1009
11532 | 11440.2012 | 2.1263
11533 | 11885.8555 | 2.1572
11534 | 13166.0137 | 1.9701
11535 | 14009.8262 | 2.3446
11536 | 15237.0156 | 2.3432
11537 | 15938.9443 | 2.5203
11538 | 16938.3652 | 2.4669
11539 | 18107.3047 | 2.6526
11540 | 19201 | 2.8269
11541 | 20244.2031 | 3.0592
11542 | 21433.8984 | 3.0368
11543 | 21552.3379 | 2.9105
11544 | 22120.5723 | 3.1349
11545 | 21626.4258 | 3.2046
11546 | 22293.1191 | 3.029
11547 | 23382.0234 | 3.1677
11548 | 23484.2891 | 2.9981
11549 | 23403.7734 | 2.8535
11550 | 23388.1719 | 2.7206
11551 | 22959.1934 | 2.7884
11552 | 23204.0664 | 2.8249
11553 | 23688.4785 | 2.8271
11554 | 24647.418 | 2.7447
11555 | 24370.3613 | 2.5914
11556 | 23284.9609 | 2.4651
11557 | 21631.6133 | 2.4646
11558 | 20759.8242 | 2.4174
11559 | 20239.4102 | 2.4721
11560 | 19800.4004 | 2.6674
11561 | 19090.2207 | 2.7281
11562 | 19246.9785 | 2.7226
11563 | 18453.1895 | 2.8737
11564 | 17941.9043 | 2.5474
11565 | 17299.5137 | 2.2508
11566 | 16339.0586 | 2.2831
11567 | 15515.29 | 1.9533
11568 | 14760.2578 | 1.8473
11569 | 14198.8359 | 1.8428
11570 | 13945.8682 | 1.8072
11571 | 13488.2578 | 1.7891
11572 | 13157.666 | 1.7617
11573 | 12888.6797 | 1.7352
11574 | 12694.2666 | 1.6924
11575 | 12424.498 | 1.7247
11576 | 12416.498 | 1.7053
11577 | 12522.6348 | 1.8208
11578 | 12760.2656 | 1.9062
11579 | 12837.667 | 2.316
11580 | 13595.4355 | 2.2809
11581 | 15485.6582 | 2.5368
11582 | 19852.0742 | 2.6128
11583 | 22161.332 | 3.2773
11584 | 26023.1348 | 3.437
11585 | 28741.6094 | 3.6765
11586 | 30289.834 | 3.6299
11587 | 31185.1191 | 3.7317
11588 | 33816.7617 | 3.7901
11589 | 33248.9922 | 3.9431
11590 | 32665.8477 | 4.0662
11591 | 34433.6797 | 4.0435
11592 | 33708.3945 | 4.0483
11593 | 32468.5625 | 3.9823
11594 | 33253.7539 | 3.7339
11595 | 31750.0352 | 3.6782
11596 | 31403.2559 | 3.7219
11597 | 31705.1621 | 3.7249
11598 | 30889.1191 | 3.7751
11599 | 31072.6348 | 3.9853
11600 | 32700.1934 | 4.0194
11601 | 31107.5078 | 4.1106
11602 | 31187.625 | 3.8161
11603 | 31328.2871 | 3.8203
11604 | 30555.3379 | 3.823
11605 | 30476.3496 | 3.5307
11606 | 30952.9492 | 3.5593
11607 | 32087.1816 | 3.5182
11608 | 31254.1289 | 3.519
11609 | 30805.1191 | 3.4126
11610 | 30193.8125 | 3.4215
11611 | 29246.6211 | 3.2192
11612 | 28207.8418 | 2.8209
11613 | 27429.8203 | 2.7503
11614 | 25510.7969 | 2.5209
11615 | 22999.5605 | 2.3063
11616 | 21486.6016 | 2.4917
11617 | 20383.043 | 2.4584
11618 | 19241.5059 | 2.2838
11619 | 17212.3359 | 2.0501
11620 | 16883.1895 | 2.054
11621 | 16057.4922 | 2.0264
11622 | 16188.3867 | 1.99
11623 | 16107.6719 | 1.9885
11624 | 16397.7246 | 2.0152
11625 | 17179.2383 | 2.1864
11626 | 18082.5664 | 2.2659
11627 | 18511.8105 | 2.5101
11628 | 18797.5996 | 2.5661
11629 | 20560.9277 | 3.2147
11630 | 24309.5117 | 3.8359
11631 | 26476.9551 | 4.1727
11632 | 29169.8848 | 4.7241
11633 | 31566.4023 | 5.1089
11634 | 32311.8047 | 5.2284
11635 | 35040.0898 | 5.3701
11636 | 35994.25 | 5.4439
11637 | 36146.3867 | 5.5805
11638 | 36887.9258 | 5.3837
11639 | 36853.5547 | 5.3462
11640 | 36002.25 | 5.451
11641 | 37402.4727 | 5.4089
11642 | 38510.6328 | 5.4259
11643 | 37095.0742 | 5.3391
11644 | 34670.4375 | 5.314
11645 | 34448.3008 | 5.386
11646 | 34181.6602 | 5.394
11647 | 34536.3008 | 5.3195
11648 | 34719.6797 | 5.3522
11649 | 34745.3125 | 5.2129
11650 | 33062.9922 | 4.9405
11651 | 32471.4883 | 4.7639
11652 | 31540.9707 | 4.4804
11653 | 30557.9473 | 4.356
11654 | 31684.2754 | 4.2767
11655 | 32182.4785 | 4.2466
11656 | 31410.6348 | 4.4165
11657 | 31474.2656 | 4.4689
11658 | 30421.582 | 4.2355
11659 | 30264.8223 | 3.9267
11660 | 28873.8848 | 3.4077
11661 | 28230.0938 | 3.1849
11662 | 24575.0273 | 2.965
11663 | 21883.498 | 2.7621
11664 | 20326.5391 | 2.6559
11665 | 19713.5273 | 2.715
11666 | 18536.0332 | 2.807
11667 | 17936.5684 | 2.7845
11668 | 17782.041 | 2.5703
11669 | 17392.8926 | 2.5586
11670 | 16647.5859 | 2.5188
11671 | 16533.8398 | 2.519
11672 | 16654.5977 | 2.4742
11673 | 16277.9551 | 2.6603
11674 | 16472.0918 | 2.7896
11675 | 16732.6406 | 3.0117
11676 | 17304.293 | 3.2168
11677 | 19047.6602 | 3.524
11678 | 22599.2656 | 4.0174
11679 | 25542.9863 | 4.5448
11680 | 28917.4414 | 5.103
11681 | 31949.6328 | 5.4403
11682 | 33887.6172 | 5.5618
11683 | 35006.207 | 5.7626
11684 | 36946.7969 | 5.7822
11685 | 35798.7773 | 5.5997
11686 | 34904.4609 | 5.7034
11687 | 34883.332 | 5.7967
11688 | 34292.0703 | 5.8161
11689 | 34224.3008 | 5.4744
11690 | 35234.6602 | 5.4482
11691 | 36373.6719 | 5.467
11692 | 36885.6719 | 5.5081
11693 | 32501.8242 | 5.4777
11694 | 32991.1094 | 5.3094
11695 | 32634.582 | 5.3452
11696 | 32706.582 | 5.4428
11697 | 32923.0273 | 5.1302
11698 | 30908.2656 | 4.8341
11699 | 30546.2109 | 4.5744
11700 | 29422.4531 | 4.4269
11701 | 29141.7461 | 4.5472
11702 | 29133.7266 | 4.413
11703 | 29441.2324 | 4.2926
11704 | 29951.4434 | 4.4742
11705 | 30129.4434 | 4.2914
11706 | 28406.5996 | 3.8091
11707 | 28586.2305 | 3.789
11708 | 28126.8516 | 3.6565
11709 | 26473.1348 | 3.3228
11710 | 23019.0566 | 2.9834
11711 | 21294.9688 | 2.8321
11712 | 19686.1484 | 2.6187
11713 | 18500.084 | 2.7584
11714 | 17666.1992 | 2.7666
11715 | 17173.832 | 2.8149
11716 | 16836.4297 | 2.7938
11717 | 15992.0195 | 2.7589
11718 | 15902.25 | 2.8208
11719 | 15965.0293 | 2.6713
11720 | 15985.7061 | 2.6971
11721 | 15942.2773 | 2.8132
11722 | 16178.1992 | 2.8682
11723 | 16136.6387 | 2.9795
11724 | 16870.7344 | 3.0767
11725 | 18371.041 | 3.3352
11726 | 21398.1172 | 3.6716
11727 | 24329.373 | 4.1127
11728 | 27610.1562 | 4.5736
11729 | 30314.4531 | 5.1397
11730 | 32426.0781 | 5.5065
11731 | 32576.1934 | 5.6158
11732 | 35097.4688 | 5.6472
11733 | 34012.2812 | 5.6392
11734 | 34275.7969 | 5.711
11735 | 34724.7109 | 5.6756
11736 | 35936.7578 | 5.8016
11737 | 34523.9297 | 5.6347
11738 | 33583.0156 | 5.5125
11739 | 31974.6777 | 5.4469
11740 | 32300.0781 | 5.4417
11741 | 31957.0469 | 5.4863
11742 | 31981.2031 | 5.4505
11743 | 32065.5527 | 5.5063
11744 | 32033.4355 | 5.3504
11745 | 32160.0566 | 5.3489
11746 | 31208.3164 | 4.9427
11747 | 29201.832 | 4.6805
11748 | 28837.5156 | 4.5353
11749 | 29333.0938 | 4.4715
11750 | 30761.8555 | 4.4565
11751 | 29971.3281 | 4.5362
11752 | 28880.4844 | 4.6989
11753 | 28617.8633 | 4.4207
11754 | 28699.3574 | 4.0502
11755 | 28630.1152 | 3.8043
11756 | 27347.7988 | 3.5126
11757 | 25032.7969 | 3.2324
11758 | 22202.6445 | 2.8825
11759 | 20317.2969 | 2.9
11760 | 18822.8398 | 2.6351
11761 | 18171.5566 | 2.567
11762 | 17455.6523 | 2.4851
11763 | 16973.0742 | 2.5371
11764 | 16124.6182 | 2.5585
11765 | 15754.5537 | 2.5141
11766 | 15527.0371 | 2.7022
11767 | 15751.7959 | 2.7331
11768 | 15416.6484 | 2.6942
11769 | 15316.9014 | 2.7094
11770 | 15265.5215 | 2.7521
11771 | 15222.5107 | 2.9431
11772 | 16382.207 | 3.1329
11773 | 18120.6836 | 3.5798
11774 | 21132.5801 | 3.9266
11775 | 23319.9727 | 4.7041
11776 | 26104.9766 | 5.2567
11777 | 27821.0625 | 5.5691
11778 | 29162.1582 | 5.7857
11779 | 31340.1289 | 5.732
11780 | 31832.9082 | 5.7122
11781 | 32448.2871 | 5.675
11782 | 33104.4922 | 5.7988
11783 | 34532.9453 | 5.6912
11784 | 34525.5664 | 5.5644
11785 | 33527.1328 | 5.6546
11786 | 32493.0684 | 5.7306
11787 | 31086.3594 | 5.4584
11788 | 29059.127 | 5.2839
11789 | 27676.5781 | 5.0482
11790 | 28489.4727 | 4.9833
11791 | 28313.8418 | 4.7777
11792 | 28370.7148 | 4.5718
11793 | 28682.6211 | 4.4598
11794 | 29338.8945 | 4.1743
11795 | 29911.8125 | 4.0678
11796 | 28835.3789 | 4.0796
11797 | 28753.2422 | 3.9562
11798 | 28576.3691 | 3.8903
11799 | 28642.8516 | 4.2432
11800 | 28046.9688 | 4.1355
11801 | 27594.9258 | 3.9566
11802 | 26085.4805 | 3.8037
11803 | 25866.2188 | 3.6192
11804 | 24806.9102 | 3.2839
11805 | 23725.7207 | 2.9506
11806 | 21222.7168 | 2.9139
11807 | 19363.7363 | 2.6348
11808 | 18206.6836 | 2.6277
11809 | 16861.1035 | 2.6802
11810 | 15962.1133 | 2.5986
11811 | 15025.9531 | 2.602
11812 | 14656.3008 | 2.5846
11813 | 14239.5215 | 2.5503
11814 | 14277.9102 | 2.242
11815 | 14268.4375 | 2.1383
11816 | 14006.4473 | 2.1395
11817 | 13698.4238 | 2.2281
11818 | 13606.4248 | 2.3486
11819 | 13084.9297 | 2.4717
11820 | 13519.1182 | 2.6115
11821 | 13403.9727 | 2.7514
11822 | 15091.9521 | 2.8913
11823 | 15907.1641 | 3.0312
11824 | 17281.8496 | 3.1711
11825 | 18825.9355 | 3.311
11826 | 20141.3906 | 3.4509
11827 | 20923.6328 | 3.5908
11828 | 22263.9512 | 3.7307
11829 | 22595.3926 | 3.8656
11830 | 22899.9297 | 3.8724
11831 | 23097.8164 | 3.9488
11832 | 23119.9414 | 3.8149
11833 | 23383.7812 | 3.9346
11834 | 22971.4961 | 3.7531
11835 | 22922.2148 | 3.7375
11836 | 22617.5625 | 3.7647
11837 | 22471.75 | 3.7007
11838 | 22164.6133 | 3.6876
11839 | 22181.4961 | 3.7331
11840 | 22330.5312 | 3.7585
11841 | 22861.3086 | 3.6238
11842 | 23527.2148 | 3.4736
11843 | 23711.4668 | 3.3409
11844 | 23664.2266 | 3.2454
11845 | 23560.3418 | 3.3951
11846 | 22933.0566 | 3.4555
11847 | 22560.0234 | 3.5396
11848 | 22188.6445 | 3.3963
11849 | 21924.623 | 3.3607
11850 | 20527.2969 | 3.1156
11851 | 19013.7363 | 3.054
11852 | 17528.1328 | 2.6434
11853 | 16979.4922 | 2.4825
11854 | 16472.5762 | 2.5561
11855 | 15803.543 | 2.5051
11856 | 14966.9951 | 2.3395
11857 | 14094.7207 | 2.0277
11858 | 13490.1709 | 1.9823
11859 | 13001.2754 | 1.9766
11860 | 12669.5078 | 1.9227
11861 | 12268.0137 | 1.8914
11862 | 12071.0459 | 2.0727
11863 | 11814.1504 | 2.143
11864 | 11553.3711 | 2.1444
11865 | 11467.1396 | 2.1876
11866 | 11401.6445 | 2.1641
11867 | 11389.5801 | 2.2223
11868 | 11539.3281 | 2.0688
11869 | 12066.4746 | 1.9273
11870 | 13033.1396 | 2.0694
11871 | 14186.1113 | 2.1744
11872 | 15173.7734 | 2.6144
11873 | 15706.0488 | 2.6747
11874 | 16838.8711 | 2.7984
11875 | 17886.9121 | 2.9533
11876 | 18825.5469 | 2.9317
11877 | 19605.9375 | 2.94
11878 | 21119.9922 | 3.3203
11879 | 21773.6445 | 3.4246
11880 | 22191.6465 | 3.5781
11881 | 22116.8262 | 3.6404
11882 | 22719.5391 | 3.411
11883 | 23101.7617 | 3.089
11884 | 22792.8047 | 3.1108
11885 | 23218.9414 | 3.0943
11886 | 23383.7812 | 3.0164
11887 | 22971.0781 | 3.2765
11888 | 22910.8047 | 3.3754
11889 | 23464.7324 | 3.4477
11890 | 24209.1211 | 3.3802
11891 | 24428.3828 | 3.2291
11892 | 23277.6992 | 3.1983
11893 | 21660.9922 | 3.229
11894 | 20615.8008 | 3.264
11895 | 19818.3789 | 3.3976
11896 | 19990.5156 | 3.5609
11897 | 19960.7695 | 3.2421
11898 | 19746.748 | 3.2246
11899 | 18793.8301 | 3.0656
11900 | 18166.7988 | 2.829
11901 | 17574.2715 | 2.4373
11902 | 16755.2188 | 2.5225
11903 | 15994.1855 | 2.2954
11904 | 15058.374 | 2.0349
11905 | 14360.7207 | 2.0476
11906 | 13938.9727 | 1.9816
11907 | 13748.2578 | 1.9984
11908 | 13328.0996 | 1.971
11909 | 12943.8984 | 1.9398
11910 | 12937.8975 | 1.931
11911 | 12681.7607 | 1.9463
11912 | 12460.6113 | 1.9277
11913 | 12649.1396 | 2.0422
11914 | 12818.6338 | 2.1458
11915 | 12906.7715 | 2.6501
11916 | 13816.4453 | 2.6367
11917 | 15410.5859 | 3.3686
11918 | 19925.2031 | 3.8512
11919 | 22879.0137 | 4.542
11920 | 26562.3555 | 4.949
11921 | 28974.7051 | 5.5047
11922 | 31853.918 | 5.5805
11923 | 33482.2344 | 5.6168
11924 | 35611.4922 | 5.7518
11925 | 35593.4922 | 5.7994
11926 | 36268.7773 | 5.8173
11927 | 37640.9766 | 5.684
11928 | 36631.5547 | 5.4546
11929 | 36436.0391 | 5.7159
11930 | 36205.7656 | 5.3494
11931 | 37336.4531 | 5.4329
11932 | 36097.7656 | 5.256
11933 | 34638.9453 | 5.344
11934 | 33836.1445 | 5.3625
11935 | 33925.543 | 5.3065
11936 | 33608.625 | 5.2378
11937 | 34327.0391 | 5.0562
11938 | 31862.2656 | 4.7685
11939 | 31018.7715 | 4.5298
11940 | 29979.2207 | 4.3792
11941 | 29997.2227 | 4.2889
11942 | 30139.5918 | 4.3717
11943 | 30981.8555 | 4.3782
11944 | 29940.8008 | 4.3791
11945 | 29792.1797 | 4.1653
11946 | 29168.0215 | 3.969
11947 | 29159.9062 | 3.6927
11948 | 28656.5996 | 3.4764
11949 | 27033.4082 | 3.2672
11950 | 23765.9727 | 3.0113
11951 | 22391.4023 | 2.8537
11952 | 20311.043 | 2.7538
11953 | 18822.5898 | 2.9111
11954 | 17670.3145 | 2.9143
11955 | 17150.082 | 2.877
11956 | 16719.2812 | 2.6243
11957 | 16236.0195 | 2.5395
11958 | 16096.9873 | 2.4594
11959 | 15797.167 | 2.4412
11960 | 15988.4375 | 2.4361
11961 | 15794.0273 | 2.6142
11962 | 16135.0586 | 2.7707
11963 | 16212.1113 | 3.1328
11964 | 17208.125 | 3.1947
11965 | 18435.2422 | 3.6714
11966 | 22050.7285 | 4.2941
11967 | 24467.5215 | 4.7832
11968 | 28012.1895 | 5.2942
11969 | 31534.5918 | 5.6645
11970 | 34260.5234 | 5.9024
11971 | 35408.4844 | 5.8734
11972 | 35647.8438 | 5.9003
11973 | 35357.4922 | 5.9736
11974 | 35269.1016 | 6.0025
11975 | 35719.4844 | 5.9964
11976 | 35783.6016 | 6.0124
11977 | 34940.7344 | 5.9971
11978 | 35983.1445 | 5.8997
11979 | 35554.6172 | 5.7386
11980 | 35596.5977 | 5.6414
11981 | 36533.418 | 5.6017
11982 | 36034.8906 | 5.7241
11983 | 35066.4375 | 5.6353
11984 | 35137.8594 | 5.5088
11985 | 34963.7031 | 5.2627
11986 | 33650.1406 | 4.8863
11987 | 32410.2246 | 4.792
11988 | 31669.9512 | 4.5383
11989 | 31047.9414 | 4.6268
11990 | 30526.8848 | 4.5384
11991 | 29064.4922 | 4.3928
11992 | 28345.0645 | 4.2954
11993 | 29211.8848 | 4.2444
11994 | 28624.873 | 4.0505
11995 | 27595.0625 | 3.748
11996 | 26819.6406 | 3.3773
11997 | 25320.6797 | 3.1186
11998 | 23483.8359 | 2.7802
11999 | 21756.3379 | 2.6828
12000 | 20429.8008 | 2.5529
12001 | 18845.8516 | 2.6256
12002 | 17614.4531 | 2.7117
12003 | 16669.6719 | 2.7111
12004 | 15838.9434 | 2.6975
12005 | 15770.3223 | 2.7174
12006 | 15422.1426 | 2.6235
12007 | 15224.6484 | 2.3758
12008 | 15107.4062 | 2.3302
12009 | 15070.627 | 2.5304
12010 | 15420.3945 | 2.851
12011 | 15523.3848 | 3.1046
12012 | 16463.2812 | 3.2389
12013 | 17935.4531 | 3.5683
12014 | 21101.1797 | 4.2031
12015 | 23865.1523 | 4.6897
12016 | 27871.1777 | 5.197
12017 | 29833.834 | 5.7148
12018 | 31165.0039 | 5.6821
12019 | 32868.6055 | 5.734
12020 | 32753.0879 | 5.7987
12021 | 32828.4688 | 5.8189
12022 | 33113.6133 | 5.8279
12023 | 33067.5 | 5.7606
12024 | 32553.7305 | 5.7483
12025 | 32174.5625 | 5.7495
12026 | 32956.9961 | 5.5467
12027 | 32839.3633 | 5.5718
12028 | 31554.4023 | 5.5103
12029 | 31432.6777 | 5.4405
12030 | 30212.0859 | 5.4919
12031 | 30667.3711 | 5.3818
12032 | 30545.1172 | 5.1162
12033 | 31176.6348 | 5.0425
12034 | 32316.7539 | 4.5734
12035 | 30734.9375 | 4.3602
12036 | 30404.6973 | 4.2104
12037 | 30036.834 | 4.1051
12038 | 29105.5156 | 4.083
12039 | 29664.6855 | 4.3209
12040 | 29405.6738 | 4.3542
12041 | 28941.6328 | 4.2316
12042 | 28483.2637 | 4.0135
12043 | 27356.8086 | 3.6602
12044 | 27176.168 | 3.3268
12045 | 25529.8496 | 3.3406
12046 | 23103.8359 | 3.1274
12047 | 21688.3711 | 2.7976
12048 | 19614.4004 | 2.6973
12049 | 17917.5566 | 2.6585
12050 | 16769.2617 | 2.5784
12051 | 16572.5254 | 2.5867
12052 | 16188.7773 | 2.5684
12053 | 15883.6289 | 2.5467
12054 | 15454.46 | 2.7031
12055 | 15110.249 | 2.7316
12056 | 15329.3105 | 2.7354
12057 | 15337.29 | 2.8697
12058 | 15183.7324 | 2.8871
12059 | 15289.1328 | 3.0693
12060 | 16429.4922 | 3.2895
12061 | 17470.7344 | 3.663
12062 | 21207.7285 | 4.1469
12063 | 24721.7852 | 4.7259
12064 | 28493.6094 | 5.1667
12065 | 31861.666 | 5.4021
12066 | 33958.2812 | 5.5401
12067 | 35960.6406 | 5.748
12068 | 36415.7891 | 5.7082
12069 | 35802.6406 | 5.6641
12070 | 35880.8945 | 5.5828
12071 | 37219.0938 | 5.5523
12072 | 36019.5352 | 5.6111
12073 | 34817.7227 | 5.5729
12074 | 34583.5859 | 5.4796
12075 | 34527.5625 | 5.2589
12076 | 33629.0156 | 5.1136
12077 | 33149.7539 | 5.136
12078 | 33717.0391 | 5.2635
12079 | 32511.7324 | 5.0574
12080 | 33996.0273 | 5.0031
12081 | 34460.8281 | 5.0015
12082 | 33221.3633 | 4.6493
12083 | 32853.7305 | 4.4256
12084 | 31980.4238 | 4.2864
12085 | 30962.8867 | 4.1598
12086 | 30374.2012 | 4.1391
12087 | 29827.1914 | 4.5494
12088 | 29415.0312 | 4.4303
12089 | 28297.3574 | 4.269
12090 | 27525.6836 | 4.0861
12091 | 26999.1777 | 3.8945
12092 | 26011.8496 | 3.3858
12093 | 24323.3945 | 3.2115
12094 | 22548.0469 | 3.0345
12095 | 21206.3281 | 3.0499
12096 | 19159.8516 | 2.9238
12097 | 18143.0527 | 2.9149
12098 | 17084.25 | 2.5735
12099 | 16315.7656 | 2.5522
12100 | 16003.7441 | 2.5627
12101 | 15639.8398 | 2.5484
12102 | 15444.7344 | 2.4661
12103 | 15342.7852 | 2.4648
12104 | 15753.6797 | 2.4651
12105 | 15220.9648 | 2.8995
12106 | 15005.9541 | 3.0454
12107 | 15089.7754 | 3.14
12108 | 16275.9766 | 3.2663
12109 | 17720.0195 | 3.6925
12110 | 20566.834 | 4.2097
12111 | 22952.8262 | 5.0326
12112 | 26264.8828 | 5.4545
12113 | 28483.8633 | 5.9006
12114 | 31475.4141 | 5.9952
12115 | 31684.9297 | 5.9675
12116 | 32109.8242 | 6.1586
12117 | 32997.2461 | 6.1902
12118 | 32221.8242 | 6.1389
12119 | 33810.3008 | 6.1436
12120 | 32465.8477 | 6.124
12121 | 32019.6875 | 6.2514
12122 | 32370.0996 | 6.0027
12123 | 31850.9297 | 5.9249
12124 | 31241.8984 | 5.8128
12125 | 30361.6016 | 5.5308
12126 | 29751.9492 | 5.3471
12127 | 29677.3066 | 5.2893
12128 | 30022.707 | 5.2026
12129 | 30245.0977 | 5.0807
12130 | 29865.582 | 4.6257
12131 | 30023.5586 | 4.4698
12132 | 29501.1914 | 4.5739
12133 | 29160.8965 | 4.302
12134 | 28231.3789 | 4.3015
12135 | 27233.8203 | 4.44
12136 | 27167.5469 | 4.3191
12137 | 26792.1445 | 4.172
12138 | 25963.8711 | 3.9407
12139 | 24857.7852 | 3.6699
12140 | 23507.0781 | 3.5337
12141 | 22573.6777 | 3.2199
12142 | 21608.9922 | 3.0773
12143 | 20401.9375 | 2.7243
12144 | 17941.4414 | 2.8411
12145 | 16433.2168 | 2.7863
12146 | 15600.0703 | 2.4392
12147 | 14944.7129 | 2.3978
12148 | 14538.0703 | 2.3746
12149 | 14125.9121 | 2.5211
12150 | 14018.0059 | 2.5333
12151 | 13647.0605 | 2.5392
12152 | 13706.2148 | 2.5027
12153 | 13566.0566 | 2.5925
12154 | 13988.2363 | 2.5779
12155 | 15031.2695 | 2.5323
12156 | 15046.3945 | 2.2875
12157 | 14162.3301 | 2.2727
12158 | 15135.7422 | 2.4257
12159 | 16538.5762 | 2.9599
12160 | 18371.9453 | 3.3198
12161 | 19407.2539 | 3.4105
12162 | 21321.9805 | 3.6292
12163 | 23061.6992 | 3.731
12164 | 24404.8906 | 3.7882
12165 | 24105.0039 | 3.8605
12166 | 23042.3203 | 3.8637
12167 | 23315.8145 | 3.7731
12168 | 23824.0469 | 3.8412
12169 | 23380.7422 | 3.9453
12170 | 24059.0176 | 3.7847
12171 | 24844.9746 | 3.6607
12172 | 24820.2383 | 3.6142
12173 | 24228.5 | 3.5654
12174 | 23723.7422 | 3.6171
12175 | 23731.7422 | 3.4877
12176 | 22373.1719 | 3.5751
12177 | 22631.793 | 3.6385
12178 | 23178.5742 | 3.6225
12179 | 23597.6035 | 3.5725
12180 | 23806.0898 | 3.4017
12181 | 23445.6055 | 3.3364
12182 | 23087.6777 | 3.3868
12183 | 22715.9297 | 3.5007
12184 | 22621.1719 | 3.4785
12185 | 22787.5625 | 3.1441
12186 | 22277.6562 | 3.1663
12187 | 21350.7188 | 2.8165
12188 | 19756.6328 | 2.9005
12189 | 17659.5352 | 2.6489
12190 | 16231.5645 | 2.3426
12191 | 15607.291 | 2.1725
12192 | 14960.1426 | 2.2708
12193 | 14255.8477 | 2.3231
12194 | 13640.3105 | 2.2672
12195 | 13100.1504 | 2.0939
12196 | 12703.6445 | 1.8327
12197 | 12324.3398 | 1.8348
12198 | 12195.2773 | 1.7464
12199 | 12032.9512 | 1.7107
12200 | 11625.7188 | 1.7159
12201 | 11669.2109 | 1.734
12202 | 11765.834 | 1.7365
12203 | 11614.4766 | 2.1312
12204 | 11688.4551 | 2.1884
12205 | 12060.3594 | 2.1129
12206 | 13175.0459 | 2.2232
12207 | 13861.8252 | 2.3911
12208 | 15099.7754 | 2.2669
12209 | 15601.9336 | 2.7852
12210 | 16758.8711 | 2.9059
12211 | 17460.25 | 2.808
12212 | 18724.3691 | 2.9302
12213 | 19364.8633 | 2.9121
12214 | 21028.4648 | 2.9882
12215 | 22139.9082 | 3.082
12216 | 22591.3086 | 3.5291
12217 | 22656.4355 | 3.5716
12218 | 22901.1934 | 3.3462
12219 | 22857.8145 | 3.1978
12220 | 22986.9609 | 3.2282
12221 | 22706.918 | 3.0078
12222 | 22553.1719 | 2.9699
12223 | 22674.4355 | 2.9929
12224 | 23027.582 | 2.9752
12225 | 23345.0781 | 3.0709
12226 | 23975.0039 | 3.0766
12227 | 24027.625 | 3.0039
12228 | 22748.0449 | 3.0015
12229 | 21387.7285 | 2.8848
12230 | 20423.0645 | 3.0677
12231 | 19826.6543 | 3.3501
12232 | 19346.8613 | 3.1715
12233 | 19152.4727 | 3.1977
12234 | 18912.2207 | 3.0111
12235 | 18393.5566 | 2.8592
12236 | 17731.5352 | 2.6878
12237 | 17212.502 | 2.4675
12238 | 16534.9648 | 2.2637
12239 | 15545.9111 | 2.32
12240 | 14817.3848 | 2.2893
12241 | 14320.4688 | 2.2507
12242 | 13727.8037 | 2.1873
12243 | 13326.0791 | 2.2244
12244 | 13218.6797 | 2.211
12245 | 13508.4893 | 2.2067
12246 | 14333.4062 | 2.1876
12247 | 13992.2793 | 2.224
12248 | 12534.8555 | 2.239
12249 | 12465.71 | 2.0687
12250 | 12790.0566 | 2.1721
12251 | 13147.8047 | 2.4197
12252 | 14801.3848 | 2.5576
12253 | 17466.502 | 3.2167
12254 | 21628.2344 | 3.9749
12255 | 23689.8477 | 4.6107
12256 | 26070.7441 | 5.1089
12257 | 28866.3672 | 5.4934
12258 | 32668.582 | 5.6426
12259 | 35122.3438 | 5.7706
12260 | 36837.5547 | 5.9244
12261 | 36148.5234 | 5.9249
12262 | 34011.4062 | 5.9876
12263 | 34434.3008 | 6.0469
12264 | 34562.1875 | 6.0296
12265 | 33748.9023 | 5.8632
12266 | 36030.3633 | 5.8055
12267 | 36325.9023 | 5.6779
12268 | 36059.7656 | 5.5639
12269 | 35019.8359 | 5.5433
12270 | 34919.5859 | 5.6086
12271 | 34878.8086 | 5.6106
12272 | 35649.2617 | 5.5851
12273 | 35455.4922 | 5.4296
12274 | 33199.75 | 5.1212
12275 | 32950.0977 | 5.1657
12276 | 31695.5293 | 4.9808
12277 | 30712.3594 | 4.9968
12278 | 30362.9609 | 5.0416
12279 | 30376.8438 | 4.8674
12280 | 29927.8125 | 4.7728
12281 | 29617.9277 | 4.4938
12282 | 28179.957 | 4.2414
12283 | 27559.8203 | 3.8952
12284 | 27250.7871 | 3.5032
12285 | 25464.8184 | 3.3529
12286 | 23394.457 | 3.2524
12287 | 22436.9199 | 2.9628
12288 | 20095.6641 | 2.6587
12289 | 18393.8105 | 2.7624
12290 | 17295.166 | 2.8099
12291 | 16860.1777 | 2.8594
12292 | 16404.6406 | 2.8505
12293 | 15841.1973 | 2.8664
12294 | 15525.0371 | 2.8786
12295 | 15486.9219 | 2.8406
12296 | 15562.2812 | 2.8426
12297 | 15751.9336 | 2.9098
12298 | 15875.3125 | 2.7569
12299 | 15941.1973 | 3.0584
12300 | 16893.1035 | 3.3101
12301 | 18136.7988 | 3.8061
12302 | 21676.9922 | 4.3164
12303 | 24627.5312 | 4.7079
12304 | 28032.7148 | 5.2578
12305 | 28973.3789 | 5.7007
12306 | 31010.2441 | 5.6839
12307 | 31588.6562 | 5.752
12308 | 33730.0273 | 6.0213
12309 | 34151.543 | 6.0061
12310 | 34573.3125 | 5.8863
12311 | 35422.4844 | 5.8516
12312 | 34657.4492 | 5.9335
12313 | 35858.7539 | 5.8086
12314 | 36536.0625 | 5.5843
12315 | 36596.1562 | 5.583
12316 | 36389.9062 | 5.6385
12317 | 34720.8281 | 5.5422
12318 | 33931.1562 | 5.6193
12319 | 34855.332 | 5.6104
12320 | 34732.5547 | 5.3301
12321 | 34619.1719 | 5.2708
12322 | 33303.3633 | 4.8328
12323 | 32708.6973 | 4.7918
12324 | 32957.2266 | 4.5141
12325 | 32262.1934 | 4.4366
12326 | 32138.793 | 4.5127
12327 | 31991.9199 | 4.5685
12328 | 31144.0137 | 4.582
12329 | 30702.7285 | 4.4312
12330 | 30241.5801 | 4.2685
12331 | 28963.127 | 4.0228
12332 | 27375.0625 | 3.6431
12333 | 25860.5859 | 3.1619
12334 | 24026.752 | 2.9529
12335 | 22358.5312 | 2.8102
12336 | 19979.6641 | 2.6596
12337 | 18557.0723 | 2.5832
12338 | 17768.1777 | 2.5292
12339 | 17345.2109 | 2.5648
12340 | 16785.4414 | 2.5865
12341 | 16167.7656 | 2.6588
12342 | 15704.4805 | 2.7444
12343 | 15798.2715 | 2.8185
12344 | 16084.5029 | 2.8055
12345 | 16221.334 | 2.8626
12346 | 16399.4707 | 2.7681
12347 | 16094.9434 | 3.1546
12348 | 16605.6074 | 3.3652
12349 | 17677.9043 | 3.8154
12350 | 21165.9805 | 4.3232
12351 | 23343.2148 | 4.7104
12352 | 26283.1133 | 5.2056
12353 | 28736.3906 | 5.7434
12354 | 29909.4219 | 6.0259
12355 | 29989.5605 | 6.0487
12356 | 31360.5195 | 6.1145
12357 | 31811.8984 | 6.2318
12358 | 32384.4688 | 6.1841
12359 | 31805.0234 | 6.1143
12360 | 31610.4023 | 6.0289
12361 | 31166.2656 | 5.865
12362 | 33456.375 | 5.6433
12363 | 32713.3398 | 5.5472
12364 | 31895.7832 | 5.6295
12365 | 31621.1621 | 5.6666
12366 | 30282.8438 | 5.7537
12367 | 29817.4219 | 5.6931
12368 | 29197.2852 | 5.4354
12369 | 29874.9375 | 5.314
12370 | 30840.9805 | 5.0793
12371 | 30539.6016 | 4.7522
12372 | 30245.1914 | 4.733
12373 | 29872.6855 | 4.7396
12374 | 29624.1582 | 4.7023
12375 | 29504.918 | 4.783
12376 | 28733.4727 | 4.7513
12377 | 28499.1055 | 4.6253
12378 | 28110.0957 | 4.3817
12379 | 27401.7988 | 3.9427
12380 | 26508.2617 | 3.5474
12381 | 24754.4062 | 3.1733
12382 | 23250.457 | 2.97
12383 | 21942.875 | 2.8066
12384 | 19290.8613 | 2.7878
12385 | 17484.5254 | 2.8771
12386 | 16536.6172 | 2.8291
12387 | 15815.0078 | 2.871
12388 | 15577.2383 | 2.8498
12389 | 15289.8398 | 2.8037
12390 | 14974.6699 | 2.7599
12391 | 14918.3457 | 2.7379
12392 | 14882.2588 | 2.8172
12393 | 14804.6055 | 2.9333
12394 | 14978.7637 | 3.0212
12395 | 14973.7539 | 3.0661
12396 | 16028.0703 | 3.2938
12397 | 17580.6406 | 3.751
12398 | 20672.6953 | 4.4311
12399 | 23396.7109 | 5.0639
12400 | 26903.8926 | 5.5591
12401 | 30159.0742 | 6.0051
12402 | 32519.3203 | 6.1191
12403 | 34005.1875 | 6.0494
12404 | 34337.3164 | 6.2458
12405 | 34289.3672 | 6.3452
12406 | 34885.5078 | 6.2715
12407 | 33680.0703 | 6.2137
12408 | 33810.1406 | 6.0906
12409 | 33824.8789 | 6.1649
12410 | 35289.7461 | 6.0473
12411 | 33646.7617 | 5.8942
12412 | 32116.1719 | 5.7988
12413 | 31598.3828 | 5.7792
12414 | 30786.2441 | 5.7352
12415 | 30739.8535 | 5.5765
12416 | 30355.582 | 5.4883
12417 | 30715.7383 | 5.1464
12418 | 30434.2012 | 4.8635
12419 | 30238.5703 | 4.5621
12420 | 29596.8633 | 4.6189
12421 | 28937.6641 | 4.6705
12422 | 28629.1465 | 4.7476
12423 | 28252.5664 | 4.8543
12424 | 28268.3457 | 4.8296
12425 | 27557.1777 | 4.6526
12426 | 27199.5469 | 4.4458
12427 | 27373.6602 | 4.0311
12428 | 26511.6406 | 3.7434
12429 | 25224.1758 | 3.3108
12430 | 23721.3516 | 2.9771
12431 | 21933.4961 | 2.826
12432 | 19364.0117 | 2.6584
12433 | 17293.2617 | 2.5791
12434 | 15964.0918 | 2.5051
12435 | 15475.3555 | 2.5276
12436 | 15093.3105 | 2.5351
12437 | 14806.46 | 2.7321
12438 | 14779.7959 | 2.6732
12439 | 14668.6914 | 2.6982
12440 | 14740.7422 | 2.7856
12441 | 14245.1094 | 2.8564
12442 | 14228.7002 | 2.7847
12443 | 14428.4902 | 3.1115
12444 | 15801.7734 | 3.2768
12445 | 17324.7773 | 3.7107
12446 | 20186.5156 | 4.3826
12447 | 22409.5391 | 4.8812
12448 | 26047.8496 | 5.3638
12449 | 28349.9785 | 5.7694
12450 | 30777.9707 | 5.8315
12451 | 32306.3301 | 5.7652
12452 | 31572.9648 | 5.866
12453 | 31563.2383 | 5.9032
12454 | 30878.2773 | 5.9769
12455 | 30935.3516 | 5.8909
12456 | 30964.7617 | 5.8681
12457 | 29688.5918 | 5.8738
12458 | 29088.7578 | 5.7196
12459 | 28334.2305 | 5.6016
12460 | 28150.9688 | 5.3652
12461 | 27521.8203 | 5.2203
12462 | 27300.9023 | 5.1592
12463 | 27270.418 | 4.8248
12464 | 27415.9141 | 4.7898
12465 | 27714.1875 | 4.7722
12466 | 28686 | 4.4561
12467 | 28610.2324 | 4.4717
12468 | 28254.3477 | 4.4668
12469 | 27794.1875 | 4.2277
12470 | 27843.1992 | 4.4584
12471 | 27161.5469 | 4.5162
12472 | 26812.7656 | 4.4912
12473 | 25965.5957 | 4.2722
12474 | 24750.7734 | 3.9111
12475 | 24001.7422 | 3.8179
12476 | 23114.0664 | 3.5807
12477 | 21544.9922 | 3.1458
12478 | 20710.1914 | 3.0994
12479 | 19791.3906 | 2.8235
12480 | 17534.8926 | 2.4337
12481 | 15762.6689 | 2.3667
12482 | 14682.8789 | 2.2858
12483 | 14358.8066 | 2.2767
12484 | 13907.6367 | 2.2526
12485 | 13544.7422 | 2.2263
12486 | 13104.4688 | 2.3645
12487 | 12898.0059 | 2.4078
12488 | 12491.0029 | 2.4272
12489 | 12214.2441 | 2.5226
12490 | 12338.6133 | 2.6419
12491 | 12459.5078 | 2.445
12492 | 13070.7715 | 2.1066
12493 | 13393.9199 | 2.2731
12494 | 14535.3633 | 2.5104
12495 | 15464.1426 | 2.8022
12496 | 16952.668 | 3.3733
12497 | 17537.9277 | 3.6506
12498 | 19369.0469 | 3.8197
12499 | 20623.4082 | 3.8748
12500 | 21475.4453 | 3.8119
12501 | 21730.3711 | 3.6623
12502 | 22060.877 | 3.6757
12503 | 21911.5508 | 3.7668
12504 | 21595.2539 | 3.806
12505 | 21354.2969 | 3.6813
12506 | 21141.9375 | 3.5434
12507 | 21084.2539 | 3.5398
12508 | 21275.3594 | 3.575
12509 | 21299.2559 | 3.5137
12510 | 21364.7812 | 3.4294
12511 | 21567.3828 | 3.4423
12512 | 22405.7539 | 3.4459
12513 | 22482.4062 | 3.5202
12514 | 23196.0664 | 3.5774
12515 | 23456.7109 | 3.5585
12516 | 23759.3516 | 3.4842
12517 | 23513.8359 | 3.3878
12518 | 23209.6777 | 3.3851
12519 | 22765.9297 | 3.3669
12520 | 22374.1406 | 3.4033
12521 | 21930.8555 | 3.3009
12522 | 20719.3164 | 2.9681
12523 | 19121.0039 | 2.8641
12524 | 18034.8398 | 2.696
12525 | 17071.7637 | 2.4093
12526 | 16393.4746 | 2.224
12527 | 15888.1836 | 2.0815
12528 | 14942.2979 | 1.9737
12529 | 14129.043 | 1.9413
12530 | 13374.9727 | 1.8725
12531 | 12858.6562 | 1.9228
12532 | 12184.5195 | 1.9115
12533 | 11961.4355 | 2.1682
12534 | 11548.0137 | 2.1071
12535 | 11308.4766 | 2.1016
12536 | 11137.7598 | 2.1061
12537 | 11094.7305 | 2.117
12538 | 11100.6641 | 2.13
12539 | 10994.6836 | 2.2504
12540 | 11512.0645 | 2.2524
12541 | 11873.832 | 2.1988
12542 | 12522.75 | 2.2076
12543 | 13266.6562 | 2.0771
12544 | 14143.3418 | 2.5595
12545 | 14731.8691 | 2.5449
12546 | 15749.6797 | 2.8875
12547 | 16027.8184 | 3.1211
12548 | 17571.9961 | 3.2178
12549 | 18756.7031 | 3.1561
12550 | 20363.0742 | 3.4038
12551 | 21046.791 | 3.5269
12552 | 21551.0645 | 3.551
12553 | 21846.1719 | 3.595
12554 | 22581.3438 | 3.4621
12555 | 21796.0254 | 3.4372
12556 | 21684.3711 | 3.612
12557 | 21826.877 | 3.3167
12558 | 22206.625 | 3.2856
12559 | 22190.2773 | 3.4058
12560 | 22364.4141 | 3.4009
12561 | 23041.5625 | 3.4496
12562 | 24063.8789 | 3.3909
12563 | 23776.0898 | 3.1382
12564 | 22819.6777 | 2.9116
12565 | 21885.6133 | 2.9355
12566 | 20738.6758 | 3.1647
12567 | 20348.791 | 3.2629
12568 | 20139.25 | 3.2055
12569 | 19501.0195 | 3.3495
12570 | 19076.3789 | 2.9923
12571 | 18735.2109 | 2.8499
12572 | 18227.418 | 2.7999
12573 | 17470.0195 | 2.6272
12574 | 17205.5527 | 2.3838
12575 | 15950.1367 | 2.0161
12576 | 15291.5889 | 1.8888
12577 | 15002.7871 | 1.8748
12578 | 13967.2598 | 1.8422
12579 | 13366.6562 | 2.1909
12580 | 13094.793 | 2.1623
12581 | 12959.6152 | 2.1437
12582 | 12708.3301 | 2.1126
12583 | 12569.5518 | 2.1372
12584 | 12342.5391 | 2.1604
12585 | 12122.627 | 2.12
12586 | 12448.3818 | 2.0749
12587 | 12446.6973 | 2.3978
12588 | 13467.2344 | 2.5894
12589 | 15002.1953 | 3.3827
12590 | 18261.8516 | 3.9574
12591 | 20882.5176 | 4.6919
12592 | 23539.3086 | 5.1101
12593 | 25880.4707 | 5.614
12594 | 28229.0527 | 5.6984
12595 | 29155.5156 | 5.7694
12596 | 30505.8535 | 5.7479
12597 | 29783.2852 | 5.7157
12598 | 30995.623 | 5.8989
12599 | 32048.793 | 5.8912
12600 | 31844.5391 | 5.8642
12601 | 31009.623 | 5.8453
12602 | 31275.9922 | 5.7008
12603 | 30986.7285 | 5.468
12604 | 30986.2461 | 5.447
12605 | 31412.6562 | 5.4765
12606 | 30394.3164 | 5.3498
12607 | 30446.9609 | 5.2302
12608 | 30613.6016 | 5.2435
12609 | 30658.8438 | 5.1701
12610 | 29523.5488 | 4.7324
12611 | 29245.1484 | 4.4836
12612 | 28241.8828 | 4.2991
12613 | 27547.5879 | 4.1147
12614 | 28218.084 | 3.9302
12615 | 28517.1055 | 3.7458
12616 | 28025.127 | 3.5613
12617 | 28208.1152 | 3.3769
12618 | 26966.998 | 3.1924
12619 | 26649.3867 | 3.008
12620 | 25726.2188 | 2.8235
12621 | 24095.4883 | 2.6262
12622 | 23040.2988 | 2.5529
12623 | 21242.9688 | 2.5926
12624 | 18776.3145 | 2.2496
12625 | 16769.6074 | 2.1586
12626 | 15732.7129 | 2.1455
12627 | 15264.7549 | 2.1553
12628 | 14723.9316 | 2.128
12629 | 14418.417 | 2.0942
12630 | 13933.2695 | 2.0265
12631 | 13690.5312 | 2.0518
12632 | 13533.5293 | 2.0622
12633 | 13415.6875 | 2.5001
12634 | 13960.2871 | 2.3079
12635 | 14083.3418 | 2.651
12636 | 15054.374 | 2.9285
12637 | 16181.4922 | 3.6803
12638 | 19483.2539 | 4.1188
12639 | 21842.9922 | 4.611
12640 | 24874.6582 | 5.4679
12641 | 27360.7559 | 5.8281
12642 | 29140.3887 | 5.9189
12643 | 30461.2129 | 6.0963
12644 | 32230.3105 | 6.0428
12645 | 31653.8984 | 6.0246
12646 | 31572.2871 | 6.2176
12647 | 33519.5 | 6.0823
12648 | 33002.4688 | 6.2297
12649 | 32102.793 | 6.0597
12650 | 31807.4141 | 5.8765
12651 | 31024.8652 | 5.7464
12652 | 30163.4434 | 5.6492
12653 | 29277.4004 | 5.5636
12654 | 29626.918 | 5.6173
12655 | 29855.4434 | 5.5372
12656 | 29847.5586 | 5.3847
12657 | 29693.7617 | 4.9742
12658 | 29523.582 | 4.745
12659 | 29498.5273 | 4.6159
12660 | 29279.4004 | 4.5439
12661 | 28503.0117 | 4.6764
12662 | 28528.1152 | 4.7942
12663 | 28140.7148 | 4.6931
12664 | 27775.5898 | 4.5116
12665 | 27104.7871 | 4.3548
12666 | 26619.6406 | 4.1433
12667 | 25610.5859 | 3.5608
12668 | 24545.0254 | 3.1507
12669 | 23257.6992 | 2.9304
12670 | 22312.4141 | 2.5435
12671 | 21121.7285 | 2.3256
12672 | 19401.4121 | 2.2212
12673 | 17633.7363 | 2.2194
12674 | 16070.8291 | 2.2184
12675 | 15378.5312 | 2.5208
12676 | 14836.9004 | 2.4872
12677 | 14581.7031 | 2.4899
12678 | 14270.6689 | 2.4426
12679 | 13981.3848 | 2.4464
12680 | 13670.8574 | 2.4758
12681 | 13673.291 | 2.5108
12682 | 13984.71 | 2.4461
12683 | 14284.8359 | 2.9592
12684 | 14809.6367 | 3.0208
12685 | 15672.3955 | 3.7446
12686 | 18499.1777 | 4.3485
12687 | 20449.4219 | 4.9302
12688 | 22727.1719 | 5.5044
12689 | 24580.0898 | 5.9737
12690 | 27178.168 | 6.1938
12691 | 27781.5664 | 6.2267
12692 | 28223.2207 | 6.0464
12693 | 28302.3691 | 6.0918
12694 | 28930 | 6.0213
12695 | 29762.0645 | 6.102
12696 | 29939.9707 | 6.211
12697 | 30290.0645 | 6.0713
12698 | 30346.9805 | 5.9369
12699 | 29817.8125 | 5.8798
12700 | 29369.791 | 5.7386
12701 | 29250.2754 | 5.7424
12702 | 28180.0938 | 5.8181
12703 | 28010.2305 | 5.7946
12704 | 28668.3672 | 5.6891
12705 | 28770.7363 | 5.4237
12706 | 29477.0332 | 5.2237
12707 | 28887.4004 | 5.0782
12708 | 29004.3906 | 5.053
12709 | 28487.4727 | 4.8946
12710 | 28155.082 | 5.0378
12711 | 27970.0723 | 5.0457
12712 | 27123.293 | 4.8553
12713 | 26770.7656 | 4.5319
12714 | 26673.25 | 4.0717
12715 | 25490.4492 | 3.8952
12716 | 24860.0586 | 3.2538
12717 | 23280.5723 | 2.8824
12718 | 22111.4043 | 2.7199
12719 | 20996.9473 | 2.5828
12720 | 18818.082 | 2.2877
12721 | 17896.7988 | 2.2911
12722 | 17390.5254 | 2.2119
12723 | 16958.5254 | 2.269
12724 | 15631.3984 | 2.2153
12725 | 15243.8379 | 2.1848
12726 | 14865.0586 | 2.1819
12727 | 14806.9434 | 2.2285
12728 | 14504.5762 | 2.196
12729 | 14119.457 | 2.369
12730 | 14706.7422 | 2.6433
12731 | 14867.248 | 2.6701
12732 | 15260.1641 | 3.1135
12733 | 16135.4268 | 3.8562
12734 | 18426.1992 | 4.2545
12735 | 20504.5586 | 5.0266
12736 | 23413.2148 | 5.6166
12737 | 26193.4805 | 5.9832
12738 | 28238.9688 | 6.0498
12739 | 28392.2305 | 6.2533
12740 | 28413.5566 | 6.2505
12741 | 27563.1777 | 6.2066
12742 | 27931.082 | 6.0606
12743 | 28259.9785 | 5.9494
12744 | 28111.3359 | 5.9327
12745 | 27860.3242 | 5.9481
12746 | 27648.3242 | 5.7616
12747 | 26852.3984 | 5.8491
12748 | 26781.2715 | 5.6964
12749 | 26549.0195 | 5.681
12750 | 26274.1016 | 5.3938
12751 | 25907.4824 | 5.4133
12752 | 26127.9863 | 5.3529
12753 | 26738.6289 | 5.0226
12754 | 27589.0625 | 4.7534
12755 | 27702.0723 | 4.7698
12756 | 27749.1992 | 4.8874
12757 | 27570.6934 | 5.0281
12758 | 27208.6504 | 5.1256
12759 | 26984.2832 | 5.0323
12760 | 25865.0918 | 4.7877
12761 | 25697.9648 | 4.4558
12762 | 25007.0488 | 4.1638
12763 | 24289.375 | 3.9359
12764 | 23467.0996 | 3.126
12765 | 21864.0039 | 2.9067
12766 | 20837.2031 | 2.6626
12767 | 19827.6406 | 2.436
12768 | 17512.502 | 2.2884
12769 | 15886.5547 | 2.2956
12770 | 14974.1426 | 2.2494
12771 | 14403.1094 | 2.3074
12772 | 15813.7441 | 2.2929
12773 | 15499.1016 | 2.2739
12774 | 13683.7529 | 2.2207
12775 | 13032.5615 | 2.2509
12776 | 12901.2578 | 2.2526
12777 | 12691.4141 | 2.3849
12778 | 12983.2773 | 2.6386
12779 | 13096.8145 | 2.8766
12780 | 13787.0781 | 3.2191
12781 | 14566.0566 | 3.7061
12782 | 16535.7109 | 4.3832
12783 | 17980.8418 | 4.8891
12784 | 19940.7695 | 5.3636
12785 | 21116.8867 | 5.9733
12786 | 22951.6152 | 6.1712
12787 | 23434.4141 | 6.3737
12788 | 24522.6367 | 6.6513
12789 | 24543.543 | 6.7273
12790 | 25678.4707 | 6.6353
12791 | 26638.6504 | 6.5887
12792 | 26795.7773 | 6.4394
12793 | 24886.1738 | 6.4247
12794 | 24657.0488 | 6.0276
12795 | 23731.7422 | 5.7979
12796 | 22561.5625 | 5.7048
12797 | 21765.7715 | 5.6192
12798 | 21261.6133 | 5.3462
12799 | 20863.4551 | 5.1864
12800 | 21264.9922 | 4.994
12801 | 21284.1191 | 4.7947
12802 | 22280.9199 | 4.6421
12803 | 23120.9414 | 4.4648
12804 | 23966.3633 | 4.4228
12805 | 23398.3398 | 4.4338
12806 | 23024.8262 | 4.6864
12807 | 22711.1719 | 4.6203
12808 | 22361.0137 | 4.3259
12809 | 21939.4043 | 4.0371
12810 | 21758.2559 | 3.8515
12811 | 21064.3496 | 3.3911
12812 | 20139.4102 | 2.8607
12813 | 19514.4004 | 2.5663
12814 | 18478.9375 | 2.6743
12815 | 17187.7441 | 2.5038
12816 | 14579.7529 | 2.1562
12817 | 13040.8867 | 2.0972
12818 | 11905.0977 | 2.2815
12819 | 11382.9375 | 2.3746
12820 | 10869.1699 | 2.3292
12821 | 10524.1367 | 2.3158
12822 | 10388.5059 | 2.2652
12823 | 10212.2754 | 2.3348
12824 | 10136.3672 | 2.3238
12825 | 9915.4297 | 2.0737
12826 | 10106.5059 | 2.1246
12827 | 10073.4941 | 2.265
12828 | 10521.6953 | 2.3957
12829 | 10830.1797 | 2.4016
12830 | 11668.5078 | 2.6025
12831 | 12481.3916 | 2.8906
12832 | 13604.6992 | 3.3129
12833 | 14697.6162 | 3.5321
12834 | 16186.3027 | 3.7169
12835 | 16989.4609 | 4.0572
12836 | 18270.2617 | 4.1123
12837 | 18797.0605 | 4.2253
12838 | 19414.4941 | 4.3156
12839 | 19196.5996 | 4.3065
12840 | 19181.3047 | 4.1054
12841 | 19360.875 | 3.9902
12842 | 19924.5918 | 3.9724
12843 | 19822.8125 | 3.9279
12844 | 19162.082 | 3.9188
12845 | 18829.8965 | 4.0158
12846 | 18687.8945 | 3.8966
12847 | 18635.7148 | 3.9161
12848 | 18758.8418 | 3.9782
12849 | 19245.9883 | 3.9093
12850 | 20013.2969 | 3.404
12851 | 20025.0215 | 3.0334
12852 | 19271.9883 | 2.9911
12853 | 18165.1895 | 3.7653
12854 | 17150.7539 | 3.7775
12855 | 16609.2188 | 3.8077
12856 | 15995.4492 | 3.5948
12857 | 15403.1543 | 3.5101
12858 | 14978.1211 | 3.3852
12859 | 14289.8477 | 3.1287
12860 | 13747.9414 | 2.8776
12861 | 13417.5508 | 2.7713
12862 | 12951.1836 | 2.6302
12863 | 12400.2461 | 2.2975
12864 | 11885.0977 | 2.1939
12865 | 11244.3164 | 2.4558
12866 | 10408.2539 | 2.1177
12867 | 10036.6211 | 2.4756
12868 | 9760.6406 | 2.394
12869 | 9398.5488 | 2.3146
12870 | 9175.0117 | 2.2608
12871 | 8776.8516 | 2.2491
12872 | 8627.0098 | 2.2275
12873 | 8591.9473 | 2.1819
12874 | 8620.8203 | 1.9492
12875 | 8512.6289 | 2.2367
12876 | 8648.6738 | 2.4836
12877 | 8834.0957 | 2.3496
12878 | 9115.0957 | 2.4723
12879 | 9498.7695 | 2.522
12880 | 10053.1943 | 2.7043
12881 | 10512.0547 | 2.7434
12882 | 11012.2344 | 3.0846
12883 | 11868.1387 | 3.0575
12884 | 12455.7197 | 3.0957
12885 | 12754.7725 | 3.3141
12886 | 13427.8652 | 3.3786
12887 | 13679.7822 | 3.5253
12888 | 13856.7422 | 3.4392
12889 | 13951.2158 | 3.5767
12890 | 14109.7852 | 3.3712
12891 | 14396.4785 | 3.3782
12892 | 14436.8906 | 3.3277
12893 | 13989.752 | 3.2688
12894 | 13720.4258 | 3.1509
12895 | 13189.4453 | 3.3717
12896 | 12820.9082 | 3.3092
12897 | 12638.2656 | 3.4628
12898 | 13276.0566 | 3.3322
12899 | 13274.2119 | 3.1632
12900 | 12897.8809 | 3.3362
12901 | 12576.0352 | 3.4454
12902 | 12589.623 | 3.3692
12903 | 12550.2656 | 3.4517
12904 | 12569.5293 | 3.427
12905 | 12462.7715 | 3.4642
12906 | 12301.2549 | 3.1243
12907 | 12241.2021 | 3.0262
12908 | 12264.8867 | 2.7677
12909 | 12553.1172 | 2.7361
12910 | 12091.9922 | 2.4341
12911 | 11580.8438 | 2.1288
12912 | 11025.9277 | 2.0032
12913 | 10489.1484 | 1.998
12914 | 10315.9277 | 2.2125
12915 | 10006.2227 | 2.1475
12916 | 9833.9062 | 2.0914
12917 | 9563.7461 | 1.9529
12918 | 9342.1367 | 1.9107
12919 | 9196.7812 | 1.9226
12920 | 9104.4219 | 1.9486
12921 | 8931.1465 | 2.3167
12922 | 9021.084 | 2.2998
12923 | 8996.1875 | 2.7623
12924 | 9794.582 | 3.1236
12925 | 10060.2773 | 3.7857
12926 | 10777.1016 | 4.2758
12927 | 11380.3008 | 4.8045
12928 | 12623.8379 | 5.6402
12929 | 13744.8418 | 6.2833
12930 | 14776.3359 | 6.4833
12931 | 15516.6426 | 6.4863
12932 | 16467.6562 | 6.5315
12933 | 17079.4258 | 6.458
12934 | 17489.0137 | 6.3354
12935 | 17628.2129 | 6.2165
12936 | 17855.1523 | 6.146
12937 | 17652.75 | 6.0677
12938 | 17979.6582 | 6.0053
12939 | 18273.5 | 5.9667
12940 | 18674.9297 | 5.7494
12941 | 17880.6172 | 5.7265
12942 | 17891.3594 | 5.7603
12943 | 17891.6055 | 5.6909
12944 | 18101.0547 | 5.4532
12945 | 18498.9609 | 5.2656
12946 | 19681.5312 | 5.1706
12947 | 20144.0605 | 5.0227
12948 | 20231.4375 | 4.845
12949 | 19700.1523 | 4.6687
12950 | 19246.5 | 5.0103
12951 | 18921.2383 | 4.7963
12952 | 18794.752 | 4.5124
12953 | 18227.0566 | 4.3967
12954 | 17073.0117 | 4.1317
12955 | 15830.4951 | 3.9511
12956 | 14646.6182 | 3.5635
12957 | 14014.46 | 3.1879
12958 | 13571.9316 | 2.9068
12959 | 12850.6484 | 2.4335
12960 | 12020.3535 | 2.5557
12961 | 11518.1289 | 2.5455
12962 | 10841.9727 | 2.5252
12963 | 10639.7812 | 2.6126
12964 | 10256.2656 | 2.5863
12965 | 9906.2852 | 2.5852
12966 | 9701.5508 | 2.5474
12967 | 9572.7725 | 2.5599
12968 | 9397.8008 | 2.551
12969 | 9320.5703 | 2.4703
12970 | 9535.6328 | 2.4861
12971 | 9555.916 | 2.8251
12972 | 9941.5391 | 3.2467
12973 | 10262.1797 | 3.9173
12974 | 11343.8359 | 4.434
12975 | 11879.0576 | 4.7956
12976 | 13049.3223 | 5.4578
12977 | 14547.7773 | 6.0229
12978 | 16091.1719 | 6.0769
12979 | 16713.8164 | 5.9884
12980 | 17650.7012 | 6.2346
12981 | 18144.1406 | 6.4659
12982 | 18724.4121 | 6.2307
12983 | 18888.8984 | 6.1669
12984 | 19085.4004 | 6.05
12985 | 19172.9082 | 5.9698
12986 | 19345.623 | 5.9187
12987 | 19391.0234 | 5.7974
12988 | 19415.6426 | 5.7728
12989 | 19324.9062 | 5.8305
12990 | 19461.1055 | 5.8092
12991 | 19785.5898 | 5.7432
12992 | 20056.834 | 5.6412
12993 | 20177.2012 | 5.3668
12994 | 21342.0977 | 5.2362
12995 | 21878.875 | 5.0469
12996 | 22117.3809 | 4.8881
12997 | 21791.4961 | 5.0229
12998 | 21432.8555 | 5.2265
12999 | 21120.3496 | 4.9052
13000 | 20608.2109 | 4.6156
13001 | 20361.4082 | 4.4601
13002 | 18934.2969 | 4.1893
13003 | 17335.6562 | 4.0175
13004 | 16294.1484 | 3.6608
13005 | 15214.5312 | 3.4174
13006 | 14580.8145 | 3.154
13007 | 13794.6992 | 2.4853
13008 | 12939.3926 | 2.3292
13009 | 12219.1172 | 2.3214
13010 | 11570.2227 | 2.2927
13011 | 11116.3809 | 2.3707
13012 | 10869.498 | 2.3245
13013 | 10613.5273 | 2.2792
13014 | 10399.2754 | 2.2165
13015 | 10222.9824 | 2.214
13016 | 10088.4004 | 2.2468
13017 | 10067.1729 | 2.3252
13018 | 10343.334 | 2.664
13019 | 10436.0557 | 2.967
13020 | 10889.4648 | 3.2194
13021 | 11558.707 | 3.8307
13022 | 13068.8047 | 4.6387
13023 | 14274.4541 | 5.1168
13024 | 15315.3203 | 5.7024
13025 | 16339.6689 | 6.2288
13026 | 18084.123 | 6.4082
13027 | 19107.1133 | 6.4095
13028 | 20628.8633 | 6.5314
13029 | 20516.8535 | 6.5094
13030 | 20361.7891 | 6.4021
13031 | 21175.7461 | 6.3095
13032 | 20808.1055 | 6.3237
13033 | 21203 | 6.415
13034 | 21119.4004 | 6.2089
13035 | 19747.748 | 6.0304
13036 | 20100.1074 | 5.8924
13037 | 20335.8262 | 5.925
13038 | 20909.4434 | 5.8595
13039 | 21531 | 5.8102
13040 | 20890 | 5.753
13041 | 21239.6328 | 5.7311
13042 | 21947.5371 | 5.5544
13043 | 21987.6523 | 5.3873
13044 | 22121.0547 | 5.2265
13045 | 22992.6211 | 5.2511
13046 | 21188.252 | 5.2254
13047 | 21188.5059 | 5.0873
13048 | 20834.8516 | 4.9394
13049 | 20960.252 | 4.6025
13050 | 21198.873 | 4.3448
13051 | 21160.5996 | 4.0483
13052 | 20152.9258 | 3.9779
13053 | 19241.5469 | 3.6413
13054 | 17025.6699 | 3.1581
13055 | 14948.2988 | 2.6405
13056 | 13485.8008 | 2.3326
13057 | 12775.4541 | 2.3435
13058 | 12273.6846 | 2.3054
13059 | 11950.3926 | 2.3886
13060 | 11608.877 | 2.357
13061 | 11121.7275 | 2.4749
13062 | 10861.6338 | 2.5429
13063 | 10731.2021 | 2.5649
13064 | 10621.5273 | 2.5756
13065 | 10568.1074 | 2.6262
13066 | 10830.5596 | 2.5345
13067 | 10892.7607 | 2.9172
13068 | 11405.6445 | 3.1711
13069 | 12011.4248 | 3.9032
13070 | 13216.4629 | 4.3075
13071 | 13987.0215 | 4.7922
13072 | 15302.4111 | 5.3277
13073 | 16349.2422 | 5.8412
13074 | 17552.293 | 5.9412
13075 | 18552.1875 | 5.7513
13076 | 20134.0742 | 5.8757
13077 | 20753.1387 | 5.9472
13078 | 21429.0859 | 5.8882
13079 | 21637.9102 | 5.8198
13080 | 21457.0059 | 5.821
13081 | 21867.0508 | 5.7664
13082 | 21953.8379 | 5.5992
13083 | 22105.1055 | 5.6795
13084 | 21874.3145 | 5.6396
13085 | 21664.0078 | 5.8677
13086 | 21585.0176 | 5.6426
13087 | 21089.8789 | 5.6444
13088 | 21216.5508 | 5.7028
13089 | 21527.4453 | 5.4176
13090 | 22589.9336 | 5.2014
13091 | 23880.1133 | 5.0607
13092 | 23527.5742 | 5.0326
13093 | 23410.1016 | 5.134
13094 | 22825.5645 | 5.2373
13095 | 23298.7578 | 5.1605
13096 | 22979.8418 | 4.9864
13097 | 22271.293 | 4.7076
13098 | 22062.9043 | 4.4216
13099 | 21187.7109 | 4.0819
13100 | 20107.6914 | 3.8743
13101 | 20768.2812 | 3.6731
13102 | 20075.957 | 3.2316
13103 | 17082.4062 | 2.7216
13104 | 13850.7178 | 2.6045
13105 | 13189.2656 | 2.6115
13106 | 12222.0967 | 2.2895
13107 | 11777.6846 | 2.3664
13108 | 11397.917 | 2.3571
13109 | 11006.1475 | 2.2987
13110 | 10807.6211 | 2.2303
13111 | 10480.7988 | 2.263
13112 | 10256.9141 | 2.284
13113 | 10303.9258 | 2.3772
13114 | 10455.9873 | 2.6772
13115 | 10620.4844 | 2.9178
13116 | 11167.4434 | 3.2128
13117 | 11605.832 | 3.8708
13118 | 12976.8848 | 4.5297
13119 | 13799.7266 | 5.0231
13120 | 15167.1016 | 5.4201
13121 | 16361.5352 | 5.9157
13122 | 17324.5781 | 6.1056
13123 | 18393.5801 | 6.1233
13124 | 19463.377 | 6.2177
13125 | 20459.3594 | 6.2747
13126 | 20985.6562 | 6.2807
13127 | 20782.9492 | 6.0486
13128 | 21034.5469 | 6.0144
13129 | 20906.0137 | 5.9835
13130 | 21137.1074 | 5.8497
13131 | 21201.4473 | 5.7433
13132 | 21402.8398 | 5.5166
13133 | 21105.0215 | 5.5003
13134 | 21048.7148 | 5.3789
13135 | 20899.0723 | 5.1862
13136 | 20114.0215 | 5.1643
13137 | 20090.2539 | 5.0549
13138 | 20349.1465 | 4.9806
13139 | 21937.2344 | 4.8534
13140 | 21701.7188 | 4.6159
13141 | 21254.1582 | 4.1722
13142 | 21492.4766 | 4.1633
13143 | 20613.5371 | 4.1397
13144 | 20838.918 | 3.9051
13145 | 19529.1055 | 3.7216
13146 | 20117.127 | 3.4509
13147 | 19902 | 3.2229
13148 | 19052.0723 | 2.8377
13149 | 18423.8496 | 2.6942
13150 | 16874.7676 | 2.5036
13151 | 14707.9219 | 2.4454
13152 | 13227.4463 | 2.414
13153 | 12383.6338 | 2.3711
13154 | 11723.8652 | 2.353
13155 | 11183.917 | 2.1835
13156 | 10992.2773 | 2.0131
13157 | 10664.2559 | 1.9854
13158 | 10540.9199 | 1.9259
13159 | 10017.0752 | 2.0297
13160 | 9773.4844 | 1.9766
13161 | 9687.1807 | 2.0107
13162 | 9759.0723 | 2.1192
13163 | 9742.1035 | 2.5031
13164 | 10254.2959 | 2.5409
13165 | 10588.9141 | 2.4389
13166 | 11466.2803 | 2.5337
13167 | 11853.3555 | 3.0039
13168 | 12665.9648 | 3.5358
13169 | 13774.0107 | 3.8495
13170 | 15559.4141 | 3.9973
13171 | 16331.6689 | 4.2145
13172 | 17800.2383 | 4.2002
13173 | 18331.6406 | 4.1889
13174 | 19351.5996 | 4.2119
13175 | 19411.4004 | 4.0177
13176 | 19092.0098 | 3.8791
13177 | 18880.4023 | 3.8803
13178 | 19245.6855 | 4.0134
13179 | 18979.2129 | 3.9447
13180 | 19117.6973 | 4.0736
13181 | 18644.1602 | 3.9306
13182 | 18874.2148 | 3.9331
13183 | 19144.2812 | 3.936
13184 | 19747.9375 | 3.8971
13185 | 20246.7031 | 3.7643
13186 | 20017.125 | 3.7825
13187 | 19155.2031 | 3.7253
13188 | 18161.8555 | 3.5818
13189 | 17781.834 | 3.756
13190 | 17031.5586 | 3.982
13191 | 16441.1699 | 3.6762
13192 | 16029.126 | 3.3843
13193 | 15873.6104 | 3.2352
13194 | 14653.9355 | 3.1155
13195 | 16000 | 2.8718
13196 | 15809.126 | 2.9096
13197 | 15341.1055 | 2.7726
13198 | 12979.4395 | 2.4219
13199 | 12434.0586 | 2.2852
13200 | 11889.7852 | 2.1039
13201 | 11379.1533 | 2.0948
13202 | 11133.1211 | 2.2439
13203 | 10906.4678 | 2.0788
13204 | 10561.415 | 2.0419
13205 | 10175.3301 | 1.9591
13206 | 9786.6445 | 1.9456
13207 | 9545.6348 | 1.9262
13208 | 9375.5723 | 1.9626
13209 | 9192.4541 | 1.9844
13210 | 9186.3291 | 2.0088
13211 | 9167.5928 | 2.2485
13212 | 9469.2041 | 2.5524
13213 | 9908.6367 | 2.5286
13214 | 11292.6367 | 2.4103
13215 | 11609.7637 | 2.518
13216 | 11912.9111 | 2.4242
13217 | 12280.4072 | 2.7724
13218 | 13205.8496 | 2.8459
13219 | 13568.0078 | 3.0275
13220 | 14489.7988 | 3.1
13221 | 14928.5781 | 3.205
13222 | 17095.4648 | 3.2411
13223 | 17994.6133 | 3.2784
13224 | 18772.9082 | 3.5223
13225 | 19291.5508 | 3.586
13226 | 20154.668 | 3.3163
13227 | 20303.3633 | 3.3113
13228 | 20354.4141 | 3.3687
13229 | 19911.4688 | 3.3497
13230 | 19479.0156 | 2.9766
13231 | 19383.8047 | 3.0861
13232 | 19430.6992 | 3.4561
13233 | 19354.9297 | 3.666
13234 | 20143.6152 | 3.2225
13235 | 20473.8672 | 3.1312
13236 | 19313.3203 | 3.1976
13237 | 17658.7285 | 3.5804
13238 | 16839.4219 | 3.6552
13239 | 16292.6641 | 3.651
13240 | 16037.5166 | 3.3501
13241 | 15815.3789 | 3.3053
13242 | 15487.2422 | 3.2267
13243 | 15515.1055 | 3.034
13244 | 14787.4512 | 2.5696
13245 | 15189.083 | 2.55
13246 | 15659.6318 | 2.4791
13247 | 14237.3867 | 2.4153
13248 | 12817.3945 | 2.0522
13249 | 12172.6152 | 1.9576
13250 | 11195.2656 | 1.9409
13251 | 10801.0352 | 2.0389
13252 | 10612.5 | 1.9919
13253 | 10383.9951 | 2.0091
13254 | 10099.3311 | 1.9616
13255 | 10145.2578 | 1.9719
13256 | 10020.3408 | 1.9904
13257 | 9961.4473 | 2.1129
13258 | 10142.8252 | 2.3988
13259 | 10007.5625 | 2.714
13260 | 10706.4785 | 3.1255
13261 | 11049.2363 | 3.5919
13262 | 11914.7959 | 4.2788
13263 | 12273.1328 | 5.0707
13264 | 12915.207 | 5.5461
13265 | 13636.2402 | 6.1162
13266 | 14382.3564 | 6.2979
13267 | 15490.9893 | 6.2
13268 | 17562.957 | 6.0542
13269 | 18806.1055 | 6.3267
13270 | 19457.8379 | 6.5041
13271 | 19666.8281 | 6.4689
13272 | 19754.0391 | 6.253
13273 | 20231.8438 | 6.1211
13274 | 20847.8164 | 6.003
13275 | 20620.8789 | 6.1338
13276 | 20366.9727 | 5.9447
13277 | 20730.3809 | 5.8745
13278 | 20909.8672 | 5.823
13279 | 21002.9512 | 5.7613
13280 | 21335.4512 | 5.6653
13281 | 21837.0469 | 5.4764
13282 | 23051.4082 | 5.1331
13283 | 23433.6113 | 4.9245
13284 | 23884.9902 | 4.8275
13285 | 23003.2422 | 5.0712
13286 | 23688.7363 | 5.1144
13287 | 23521.7266 | 4.8945
13288 | 23214.5996 | 4.5817
13289 | 21182.0352 | 4.4359
13290 | 19156.9824 | 4.242
13291 | 18724.707 | 3.9191
13292 | 17937.5371 | 3.2609
13293 | 16022.1895 | 2.8402
13294 | 17051.6094 | 2.6481
13295 | 16502.3477 | 2.6435
13296 | 14357.5752 | 2.3366
13297 | 13464.0605 | 2.3354
13298 | 12868.7529 | 2.3007
13299 | 12479.6992 | 2.4156
13300 | 12247.2363 | 2.386
13301 | 11939.4062 | 2.3624
13302 | 11668.0459 | 2.2515
13303 | 11451.1094 | 2.2898
13304 | 11492.0674 | 2.316
13305 | 11468.2559 | 2.4506
13306 | 11700.3926 | 2.6018
13307 | 11709.0859 | 2.9931
13308 | 12983.1318 | 3.2859
13309 | 14871.3037 | 3.8724
13310 | 16568.7266 | 4.3318
13311 | 20304.3066 | 5.0665
13312 | 23260.2031 | 5.8095
13313 | 27157.293 | 6.1687
13314 | 29779.6914 | 6.3764
13315 | 29847.4922 | 6.3312
13316 | 30949.0801 | 6.4777
13317 | 31470.1523 | 6.5323
13318 | 32656.7559 | 6.4608
13319 | 33883.5391 | 6.5215
13320 | 33552.9336 | 6.5374
13321 | 33478.4258 | 6.3874
13322 | 35431.8945 | 6.1837
13323 | 34653.25 | 6.1154
13324 | 33856.0781 | 6.0144
13325 | 32480.0156 | 5.9744
13326 | 32735.5312 | 5.9495
13327 | 33069.9219 | 5.9747
13328 | 33303.4375 | 5.8591
13329 | 32888.0938 | 5.6686
13330 | 31555.2441 | 5.3457
13331 | 31799.2441 | 5.0296
13332 | 30949.6953 | 5.0765
13333 | 29877.0098 | 5.1551
13334 | 29541.875 | 5.0431
13335 | 29122.1055 | 4.7907
13336 | 28715.1875 | 4.5252
13337 | 28275.8086 | 4.4678
13338 | 27649.6426 | 4.2236
13339 | 26747 | 3.7661
13340 | 24498.3438 | 3.1135
13341 | 20877.5293 | 2.7468
13342 | 19855.4434 | 2.6172
13343 | 19620.5703 | 2.3629
13344 | 19278.4336 | 2.2502
13345 | 17754.6426 | 2.2408
13346 | 16807.957 | 2.2648
13347 | 16298.4619 | 2.5949
13348 | 16306.9678 | 2.5208
13349 | 15697.3877 | 2.2255
13350 | 15226.8604 | 2.4284
13351 | 14986.8818 | 2.17
13352 | 15070.333 | 2.1709
13353 | 14756.6367 | 2.5906
13354 | 15196.9336 | 2.4963
13355 | 15600.3877 | 2.8344
13356 | 16129.3682 | 3.1448
13357 | 16553.9375 | 3.8688
13358 | 20383.6992 | 4.3409
13359 | 23693.6387 | 4.8475
13360 | 26364.5156 | 5.7166
13361 | 30250.4766 | 6.1682
13362 | 31471.3945 | 6.275
13363 | 31333.5938 | 6.5151
13364 | 32841.6172 | 6.5259
13365 | 33583.207 | 6.5728
13366 | 35240.8711 | 6.5831
13367 | 34681.5312 | 6.4405
13368 | 34349.7422 | 6.4624
13369 | 33100.9141 | 6.1533
13370 | 33401.6914 | 5.9434
13371 | 33641.4141 | 5.7831
13372 | 34063.7344 | 5.7272
13373 | 33509.0469 | 5.7118
13374 | 32804.6367 | 5.6419
13375 | 32340.7734 | 5.6611
13376 | 33175.7656 | 5.6829
13377 | 32368.3418 | 5.5918
13378 | 30164.002 | 5.1652
13379 | 30407.8652 | 5.0429
13380 | 30284.6445 | 4.9977
13381 | 29087.4746 | 5.3231
13382 | 29423.4121 | 5.2154
13383 | 29383.5898 | 5.0026
13384 | 31278.1836 | 4.7161
13385 | 30706.668 | 4.5023
13386 | 28716.8828 | 4.2047
13387 | 27623.1445 | 3.9727
13388 | 26361.291 | 3.2579
13389 | 22706.6426 | 2.906
13390 | 20855.0898 | 2.6653
13391 | 19494.4277 | 2.5041
13392 | 18979.8789 | 2.5574
13393 | 17253.9414 | 2.5649
13394 | 16773.2891 | 2.543
13395 | 16500.9609 | 2.6352
13396 | 16250.8047 | 2.6022
13397 | 15771.2656 | 2.5713
13398 | 15498.6445 | 2.518
13399 | 15135.8652 | 2.5126
13400 | 15262.4961 | 2.5164
13401 | 15295.8838 | 2.5866
13402 | 15762.0322 | 2.7348
13403 | 16161.9004 | 3.0254
13404 | 17285.4941 | 3.2772
13405 | 18355.1055 | 3.9681
13406 | 21125.8555 | 4.3521
13407 | 24425.4902 | 4.7807
13408 | 28039.9062 | 5.5728
13409 | 31376.4023 | 6.0313
13410 | 34056.125 | 6.093
13411 | 34395.7852 | 5.9524
13412 | 35646.6445 | 6.1737
13413 | 35073.293 | 6.1902
13414 | 36027.9766 | 6.4878
13415 | 34964.9961 | 6.5372
13416 | 34660.8594 | 6.5705
13417 | 33983.5781 | 6.1916
13418 | 33867.7109 | 6.065
13419 | 33632.8164 | 5.9704
13420 | 33359.8047 | 5.8679
13421 | 33052.543 | 6.0524
13422 | 33546.0078 | 5.9857
13423 | 32803.0234 | 5.7967
13424 | 32993.2812 | 5.6967
13425 | 31490.9609 | 5.3295
13426 | 31051.1504 | 5.0165
13427 | 30734.6582 | 4.8892
13428 | 29573.0762 | 5.0939
13429 | 28715.002 | 5.4677
13430 | 28974.0156 | 5.3409
13431 | 29394.1484 | 5.2103
13432 | 29959.3477 | 4.9745
13433 | 29628.8418 | 4.4456
13434 | 29041.3477 | 4.0732
13435 | 28341.418 | 3.6845
13436 | 26617.1758 | 3.2239
13437 | 23050.6133 | 2.9081
13438 | 20948.2539 | 2.8755
13439 | 20253.082 | 2.4795
13440 | 18967.6602 | 2.2521
13441 | 18023.9785 | 2.2881
13442 | 16841.4941 | 2.255
13443 | 15934.3691 | 2.3535
13444 | 16874.3242 | 2.3359
13445 | 16515.7773 | 2.2847
13446 | 16524.3984 | 2.2121
13447 | 16102.0518 | 2.1963
13448 | 16172.1348 | 2.4869
13449 | 16251.3467 | 2.3753
13450 | 16119.6201 | 2.6867
13451 | 16367.5566 | 2.7996
13452 | 17580.9453 | 3.233
13453 | 18233.5273 | 4.0475
13454 | 21191.1074 | 4.5481
13455 | 24618.1855 | 5.1961
13456 | 27773.8008 | 5.7134
13457 | 31116.4141 | 6.3048
13458 | 33573.4375 | 6.4182
13459 | 34039.207 | 6.3623
13460 | 35079.25 | 6.2867
13461 | 33966.9766 | 6.503
13462 | 34983.8906 | 6.6229
13463 | 34631.7539 | 6.505
13464 | 34546.4922 | 6.5016
13465 | 34252.418 | 6.4618
13466 | 32865.8984 | 6.2568
13467 | 32418.2461 | 5.964
13468 | 32275.0039 | 5.8799
13469 | 31703.2148 | 5.7478
13470 | 30800.5508 | 5.4949
13471 | 30880.7812 | 5.2101
13472 | 30751.793 | 5.059
13473 | 30377.1504 | 5.0106
13474 | 30984.4355 | 4.9219
13475 | 31278.0664 | 4.9207
13476 | 30350.3926 | 4.9811
13477 | 28877.0645 | 5.185
13478 | 28332.6836 | 5.1743
13479 | 28046.5547 | 4.8884
13480 | 27420.1562 | 4.6789
13481 | 26767.4629 | 4.3315
13482 | 25713.8828 | 4.0646
13483 | 24800.2285 | 3.7821
13484 | 22076.4453 | 2.9982
13485 | 19864.9375 | 2.8819
13486 | 18577.3789 | 2.6232
13487 | 18473.3359 | 2.276
13488 | 17340.8398 | 2.1185
13489 | 16307.0273 | 2.311
13490 | 15715.0273 | 2.0679
13491 | 15865.0195 | 2.1622
13492 | 14913.8066 | 2.0776
13493 | 14370.0156 | 2.0286
13494 | 14039.8789 | 1.9894
13495 | 14143.1855 | 2.3308
13496 | 13621.2656 | 2.3941
13497 | 13464.876 | 2.4029
13498 | 13516.3496 | 2.216
13499 | 13267.2021 | 2.4002
13500 | 13499.6338 | 2.7735
13501 | 13641.8447 | 2.6723
13502 | 15041.6455 | 2.7175
13503 | 15999.248 | 3.0417
13504 | 16936.6914 | 3.535
13505 | 18510.9258 | 3.7627
13506 | 20191.2734 | 3.8419
13507 | 20443.0215 | 3.9868
13508 | 21195.4219 | 4.0813
13509 | 22430.3711 | 4.0432
13510 | 22434.75 | 4.0642
13511 | 22779.1172 | 4.1447
13512 | 22829.4141 | 4.1561
13513 | 22393.4648 | 4.2013
13514 | 22413.7383 | 4.014
13515 | 22693.877 | 3.9951
13516 | 22457.1289 | 3.8445
13517 | 22091.4316 | 3.9432
13518 | 22305.0742 | 3.9654
13519 | 21581.9062 | 3.9365
13520 | 21414.873 | 3.8326
13521 | 22271.2129 | 3.8653
13522 | 23080.5918 | 3.7756
13523 | 23465.5078 | 3.6947
13524 | 22812.5918 | 3.8691
13525 | 22260.5684 | 4.1298
13526 | 21403.8848 | 3.8051
13527 | 22047.4219 | 3.544
13528 | 21050.9883 | 3.4034
13529 | 21207.5156 | 3.3135
13530 | 19805.2422 | 3.1132
13531 | 18829.5469 | 2.8726
13532 | 17151.3008 | 2.8987
13533 | 16156.4785 | 2.56
13534 | 15562.8027 | 2.3901
13535 | 15080.0674 | 2.3362
13536 | 14204.0244 | 2.301
13537 | 13503.5908 | 2.0912
13538 | 13105.2012 | 2.0277
13539 | 12744.2559 | 2.1395
13540 | 12379.3594 | 2.2296
13541 | 11924.8125 | 2.2557
13542 | 11777.9395 | 2.2831
13543 | 11390.8984 | 1.926
13544 | 11296.0547 | 2.1414
13545 | 11092.1182 | 2.0163
13546 | 11184.3711 | 1.99
13547 | 11042.6348 | 2.132
13548 | 11361.8945 | 2.1509
13549 | 11684.5166 | 2.2154
13550 | 12522.9492 | 2.2774
13551 | 13132.2021 | 2.2887
13552 | 13836.2549 | 2.5784
13553 | 14442.3301 | 2.5796
13554 | 15627.6152 | 3.0126
13555 | 16489.5215 | 3.161
13556 | 18034.8086 | 3.0085
13557 | 18707.6191 | 3.1445
13558 | 20087.7266 | 3.4601
13559 | 20555.7578 | 3.5941
13560 | 21678.8945 | 3.5319
13561 | 20816.2539 | 3.6842
13562 | 22023.3379 | 3.3725
13563 | 21235.3379 | 3.3177
13564 | 21824.1191 | 3.4101
13565 | 22169.9707 | 3.1916
13566 | 22019.2129 | 3.1669
13567 | 21598.3164 | 3.4622
13568 | 21792.5488 | 3.5144
13569 | 21745.8125 | 3.7099
13570 | 22943.0664 | 3.4584
13571 | 23211.9922 | 2.5822
13572 | 21708.7793 | 2.8144
13573 | 21274 | 2.7839
13574 | 20669.3574 | 2.7216
13575 | 19617.4414 | 2.8235
13576 | 19803.4297 | 2.8583
13577 | 20057.2422 | 2.7428
13578 | 19353.7266 | 2.5757
13579 | 18367.6836 | 2.1517
13580 | 17893.8926 | 1.7807
13581 | 17408.9961 | 1.6082
13582 | 16154.9111 | 1.5046
13583 | 15342.2471 | 1.3899
13584 | 14574.5938 | 1.2911
13585 | 14164.2041 | 2.0808
13586 | 14031.1426 | 2.0058
13587 | 13841.3438 | 2.1325
13588 | 13671.0703 | 2.0943
13589 | 13538.0293 | 2.3493
13590 | 12999.293 | 2.3673
13591 | 12828.6514 | 2.3919
13592 | 12479.1846 | 2.2339
13593 | 12525.626 | 2.1698
13594 | 12742.7637 | 2.4238
13595 | 12866.9111 | 2.7626
13596 | 13275.1104 | 2.9588
13597 | 15197.5234 | 3.8757
13598 | 19739.0723 | 4.4605
13599 | 22029.6953 | 5.1012
13600 | 25890.8281 | 5.7911
13601 | 29097.8301 | 6.376
13602 | 30446.2109 | 6.6063
13603 | 30583.6855 | 6.6061
13604 | 31738.832 | 6.7719
13605 | 31667.4746 | 6.7409
13606 | 32930.6641 | 6.6868
13607 | 34856.1523 | 6.5245
13608 | 35187.9453 | 6.5171
13609 | 34797.625 | 6.5087
13610 | 35335.9922 | 6.2452
13611 | 34548.8203 | 6.1058
13612 | 34476.1094 | 5.9653
13613 | 33526.668 | 5.8951
13614 | 34115.0977 | 5.7641
13615 | 34168.2031 | 5.5993
13616 | 33419.0781 | 5.6455
13617 | 33147.2656 | 5.5504
13618 | 32261.6328 | 4.9625
13619 | 32678.3496 | 4.535
13620 | 31900.6035 | 4.4119
13621 | 30570.2852 | 4.5085
13622 | 30207.252 | 5.1668
13623 | 29874.0312 | 5.0838
13624 | 29424.4512 | 4.7978
13625 | 29401.6934 | 4.6192
13626 | 28432.7539 | 4.3906
13627 | 27305.9258 | 3.9964
13628 | 24658.6348 | 3.4374
13629 | 23109.4727 | 2.9726
13630 | 20568.334 | 2.6494
13631 | 19062.7539 | 2.4484
13632 | 17746.9609 | 2.3298
13633 | 17055.0781 | 2.6447
13634 | 16986.8164 | 2.5931
13635 | 17053.3574 | 2.7786
13636 | 16317.4727 | 2.7313
13637 | 15956.4414 | 2.8192
13638 | 15258.4492 | 2.7543
13639 | 15005.8145 | 2.7185
13640 | 15019.1797 | 2.723
13641 | 14971.665 | 2.8486
13642 | 15204.791 | 2.8803
13643 | 15043.2305 | 3.1386
13644 | 16271.917 | 3.2651
13645 | 18221.5195 | 4.1695
13646 | 21202.7969 | 4.7236
13647 | 24222.7148 | 5.5116
13648 | 27029.3711 | 6.1162
13649 | 30827.0801 | 6.5067
13650 | 33048.1992 | 6.6058
13651 | 33721.3438 | 6.511
13652 | 34188.2188 | 6.7752
13653 | 34171.7578 | 6.679
13654 | 34501.9609 | 6.6958
13655 | 35617.1016 | 6.7754
13656 | 34375.9062 | 6.6306
13657 | 33557.75 | 6.789
13658 | 33971.5 | 6.373
13659 | 34502.4062 | 6.953
13660 | 33566.8086 | 6.0986
13661 | 32978.9219 | 5.9612
13662 | 34827.6094 | 5.7255
13663 | 35249.1797 | 5.6706
13664 | 34012.5859 | 5.6251
13665 | 33180.7539 | 5.6242
13666 | 31748.6328 | 5.3996
13667 | 31747.875 | 5.2818
13668 | 31426.6094 | 5.3951
13669 | 30352.8203 | 5.3491
13670 | 29984.4082 | 5.211
13671 | 29818.3867 | 5.0983
13672 | 29238.5039 | 4.7324
13673 | 28599.9746 | 4.5178
13674 | 27989.543 | 4.2856
13675 | 24749.625 | 3.985
13676 | 26061.3184 | 3.5042
13677 | 23316.0645 | 2.9392
13678 | 20529.1562 | 2.86
13679 | 19285.3438 | 2.6131
13680 | 17598.8672 | 2.2746
13681 | 16984.9844 | 2.2987
13682 | 16211.9512 | 2.2832
13683 | 15963.2881 | 2.4064
13684 | 15369.4844 | 2.5748
13685 | 14907.7266 | 2.3314
13686 | 14456.0859 | 2.2901
13687 | 14426.1367 | 2.3084
13688 | 14353.1377 | 2.3401
13689 | 15262.1348 | 2.4209
13690 | 15537.7979 | 2.6655
13691 | 15231.1133 | 2.9683
13692 | 15957.5723 | 3.3128
13693 | 17271.4062 | 4.2288
13694 | 21640.5781 | 4.7268
13695 | 22926.8945 | 5.2056
13696 | 27066.4277 | 5.8845
13697 | 30119.3027 | 6.4628
13698 | 31629.2305 | 6.5227
13699 | 31774.5156 | 6.5731
13700 | 33065.707 | 6.4483
13701 | 33057.8203 | 6.3444
13702 | 34018.5078 | 6.3083
13703 | 34440.918 | 6.1739
13704 | 34420.4844 | 6.1862
13705 | 33778.0312 | 6.1869
13706 | 33218.5703 | 6.0706
13707 | 33625.2305 | 5.8999
13708 | 33218.4297 | 6.2234
13709 | 32228.4102 | 5.8018
13710 | 32095.2812 | 5.8637
13711 | 31712.5977 | 5.8278
13712 | 31116.4609 | 5.8504
13713 | 31955.8594 | 5.6543
13714 | 30850.6055 | 5.3962
13715 | 31235.8398 | 5.1603
13716 | 31340.7227 | 5.3151
13717 | 31220.459 | 5.5819
13718 | 31142.5977 | 5.4598
13719 | 31085.9551 | 5.0672
13720 | 30349.6602 | 4.9418
13721 | 30156.1641 | 4.664
13722 | 27973.5293 | 4.4969
13723 | 27579.3926 | 4.1703
13724 | 25245.0312 | 3.5777
13725 | 22819.1348 | 2.8953
13726 | 20402.5 | 2.7738
13727 | 19267.8359 | 2.513
13728 | 18407.3828 | 2.2997
13729 | 17564.3477 | 2.3525
13730 | 16934.2539 | 2.3503
13731 | 16359.4746 | 2.4714
13732 | 16005.3389 | 2.4686
13733 | 15794.6953 | 2.4434
13734 | 15324.6016 | 2.3845
13735 | 15210.8613 | 2.4036
13736 | 15532.8848 | 2.4738
13737 | 15392.1914 | 2.5908
13738 | 15664.0459 | 2.6928
13739 | 15828.8848 | 2.998
13740 | 16437.8008 | 3.2504
13741 | 17817.8672 | 4.198
13742 | 21378.9551 | 4.4499
13743 | 24130.5781 | 4.8988
13744 | 27457.002 | 5.4223
13745 | 30769.5645 | 5.8716
13746 | 32643.0508 | 6.1523
13747 | 32683.418 | 6.3576
13748 | 34234.2422 | 6.5853
13749 | 34383.2539 | 6.5601
13750 | 35398.1875 | 6.5024
13751 | 35630.1875 | 6.4373
13752 | 34661.1406 | 6.4213
13753 | 34412.6328 | 6.4644
13754 | 34700.2031 | 6.3701
13755 | 34485.8203 | 6.1367
13756 | 34198.418 | 5.9908
13757 | 33672.4688 | 5.9806
13758 | 33449.0469 | 5.9675
13759 | 32981.375 | 5.8821
13760 | 32587.2793 | 5.9917
13761 | 32347.1426 | 5.8195
13762 | 31659.7715 | 5.5936
13763 | 31590.5586 | 5.463
13764 | 30653.8848 | 5.653
13765 | 29258.3359 | 5.7387
13766 | 28669.6406 | 5.5504
13767 | 29788.2422 | 5.361
13768 | 31121.5469 | 5.166
13769 | 30452.4004 | 4.8007
13770 | 29608.5664 | 4.4642
13771 | 28653.375 | 4.0232
13772 | 26220.5117 | 3.6592
13773 | 23415.9277 | 2.9518
13774 | 21656.9453 | 2.7669
13775 | 20686.9023 | 2.4658
13776 | 20174.2617 | 2.5664
13777 | 18744.0391 | 2.6826
13778 | 17381.4883 | 2.653
13779 | 16853.2363 | 2.7582
13780 | 16458.5938 | 2.5457
13781 | 15993.9297 | 2.3817
13782 | 15305.6338 | 2.3211
13783 | 15238.7822 | 2.3866
13784 | 15638.6953 | 2.4295
13785 | 15584.0752 | 2.4802
13786 | 15556.0527 | 2.8577
13787 | 15640.9473 | 3.1458
13788 | 16595.2461 | 3.5184
13789 | 17786.2051 | 4.2503
13790 | 22251.4082 | 4.6443
13791 | 25856.2441 | 5.3866
13792 | 29546.9648 | 6.0622
13793 | 32076.0625 | 6.4738
13794 | 33243.0234 | 6.5047
13795 | 32855.5078 | 6.6498
13796 | 34398.2109 | 6.789
13797 | 34329.9609 | 6.7656
13798 | 34696.0977 | 6.7468
13799 | 34077.9375 | 6.4141
13800 | 33567.043 | 6.383
13801 | 33529.5273 | 6.2454
13802 | 33530.9062 | 6.2993
13803 | 33530.7695 | 6.0149
13804 | 32959.5039 | 5.8385
13805 | 31530.5449 | 5.7991
13806 | 30140.8711 | 5.5964
13807 | 29879.5645 | 5.4141
13808 | 29705.7012 | 5.4454
13809 | 29881.332 | 5.2271
13810 | 30281.8594 | 5.1994
13811 | 30582.1328 | 5.1651
13812 | 30546.4219 | 5.4364
13813 | 29522.8555 | 5.622
13814 | 29078.8242 | 5.441
13815 | 28889.4453 | 5.1088
13816 | 28370.0234 | 5.0438
13817 | 27458.5449 | 4.4598
13818 | 26525.8828 | 4.1732
13819 | 25601.3984 | 4.0515
13820 | 22842.3008 | 3.5021
13821 | 20986.3945 | 2.7129
13822 | 19555.8242 | 2.567
13823 | 17477.9707 | 2.3875
13824 | 17564.873 | 2.3861
13825 | 16690.8672 | 2.5515
13826 | 16525.5527 | 2.4742
13827 | 16134.3037 | 2.603
13828 | 15453.957 | 2.5898
13829 | 15325.6826 | 2.4512
13830 | 14692.3252 | 2.2139
13831 | 14672.4189 | 2.2358
13832 | 14546.9766 | 2.2347
13833 | 14133.9004 | 2.3207
13834 | 13835.5107 | 2.3493
13835 | 13599.4893 | 2.4496
13836 | 13857.5117 | 2.6259
13837 | 14096.7734 | 2.7254
13838 | 15869.7344 | 3.0699
13839 | 16993.293 | 3.452
13840 | 17736.5781 | 3.7883
13841 | 18371.4941 | 4.1376
13842 | 19324.0645 | 4.3046
13843 | 21761.4355 | 4.5298
13844 | 23808.4375 | 4.498
13845 | 24726.5234 | 4.6199
13846 | 23703.4355 | 4.6415
13847 | 23916.6895 | 4.7231
13848 | 23735.7969 | 4.5564
13849 | 23303.6602 | 4.5638
13850 | 22411.5938 | 4.5651
13851 | 22636.4688 | 4.5049
13852 | 22099.9492 | 4.271
13853 | 21290.9805 | 4.2325
13854 | 21136.0996 | 4.1772
13855 | 21694.9316 | 4.0897
13856 | 22306.9062 | 4.0166
13857 | 22561.0703 | 4.0746
13858 | 23071.1074 | 4.0011
13859 | 24126.9434 | 4.0049
13860 | 24654.5977 | 4.1931
13861 | 24745.4688 | 4.2062
13862 | 23965.7949 | 4.1725
13863 | 23843.543 | 3.8502
13864 | 23303.3848 | 3.7907
13865 | 22426.0566 | 3.5953
13866 | 20714.0996 | 3.3707
13867 | 18775.918 | 3.1822
13868 | 17300.9609 | 2.9284
13869 | 16913.4219 | 2.7241
13870 | 16526.8516 | 2.5419
13871 | 17650.4102 | 2.6536
13872 | 16766.6211 | 2.4625
13873 | 15846.3252 | 2.2838
13874 | 15432.377 | 2.2347
13875 | 13502.0371 | 2.3615
13876 | 12795.0059 | 2.2955
13877 | 12251.4893 | 2.2066
13878 | 11883.626 | 2.1534
13879 | 12886.1758 | 2.1014
13880 | 13533.9951 | 2.1311
13881 | 13490.752 | 2.1419
13882 | 13706.7529 | 2.1985
13883 | 13681.6992 | 2.3053
13884 | 14153.0273 | 2.3981
13885 | 14707.3232 | 2.5089
13886 | 16138.9766 | 2.5317
13887 | 16870.9258 | 2.5865
13888 | 17306.3242 | 2.8603
13889 | 17445.3359 | 2.8259
13890 | 18237.9785 | 3.1471
13891 | 19363.834 | 3.2248
13892 | 19892.3398 | 3.2652
13893 | 20896.3828 | 3.4256
13894 | 22270.584 | 3.7515
13895 | 24286.8906 | 3.8496
13896 | 26208.293 | 3.868
13897 | 26179.5352 | 3.9757
13898 | 26277.7891 | 3.8061
13899 | 25989.8086 | 3.5971
13900 | 26444.6934 | 3.696
13901 | 25891.6504 | 3.6144
13902 | 25585.1445 | 3.4251
13903 | 24581.332 | 3.4733
13904 | 23929.6367 | 3.6041
13905 | 24775.1016 | 3.5862
13906 | 25223.9961 | 3.6103
13907 | 25788.8926 | 3.5842
13908 | 24735.2188 | 3.9561
13909 | 23240.625 | 3.9865
13910 | 21003.3711 | 3.6696
13911 | 19497.9277 | 3.5712
13912 | 18855.2852 | 3.4051
13913 | 18427.2637 | 3.2257
13914 | 18418.6211 | 3.2685
13915 | 17868.5781 | 2.908
13916 | 17207.1992 | 2.9447
13917 | 16779.293 | 2.5366
13918 | 16368.7656 | 2.3271
13919 | 15654.8594 | 2.1762
13920 | 14619.5098 | 2.0988
13921 | 14065.1426 | 2.1482
13922 | 13754.1543 | 2.0781
13923 | 13860.7529 | 2.3517
13924 | 13984.7021 | 2.298
13925 | 13595.8066 | 2.1521
13926 | 13097.3965 | 2.128
13927 | 13882.2178 | 2.1927
13928 | 13577.1855 | 2.4985
13929 | 14045.0908 | 2.6909
13930 | 13552.4062 | 2.714
13931 | 13722.1309 | 2.7517
13932 | 14747.0488 | 3.0814
13933 | 16705.1562 | 4.0154
13934 | 19110.6211 | 4.5231
13935 | 23127.4355 | 5.1191
13936 | 26669.332 | 5.7625
13937 | 29790.3359 | 6.0649
13938 | 31344.0742 | 6.3437
13939 | 32283.0137 | 6.558
13940 | 32951.4062 | 6.6662
13941 | 34710.7969 | 6.5865
13942 | 35277.668 | 6.64
13943 | 35050.75 | 6.5151
13944 | 33724.1797 | 6.5479
13945 | 33754.0859 | 6.3484
13946 | 33670.9609 | 6.1631
13947 | 34061.793 | 5.9994
13948 | 33862.4766 | 5.9026
13949 | 33617.7422 | 6.0694
13950 | 33983.0977 | 6.1439
13951 | 33515.6953 | 6.0477
13952 | 32959.75 | 5.8086
13953 | 32069.043 | 5.7939
13954 | 31093.0078 | 5.5824
13955 | 30875.2383 | 5.3834
13956 | 29374.0898 | 5.5799
13957 | 28277.248 | 5.528
13958 | 29333.1016 | 5.3481
13959 | 29351 | 4.9355
13960 | 29945.4961 | 4.9546
13961 | 29325.0859 | 4.7029
13962 | 28817.6426 | 4.3702
13963 | 27398.4512 | 3.8481
13964 | 25001.3555 | 3.2243
13965 | 22595.1602 | 2.8969
13966 | 21063.3281 | 2.7965
13967 | 19867.2637 | 2.4709
13968 | 19470.7148 | 2.5889
13969 | 18844.4414 | 2.6362
13970 | 17672.5566 | 2.5718
13971 | 17100.8086 | 2.4886
13972 | 16646.5352 | 2.5204
13973 | 16060.7227 | 2.5623
13974 | 15805.6406 | 2.4965
13975 | 14972.7734 | 2.5137
13976 | 14994.3633 | 2.543
13977 | 15221.0049 | 2.6233
13978 | 16988.8398 | 2.7617
13979 | 16359.0703 | 3.1741
13980 | 17799.7539 | 3.2983
13981 | 18968.4629 | 4.2297
13982 | 22227.5078 | 4.8311
13983 | 26086.3945 | 5.2202
13984 | 28665.2812 | 5.9134
13985 | 31070.5391 | 6.2934
13986 | 33060.7383 | 6.4398
13987 | 33183.7734 | 6.6171
13988 | 33406.918 | 6.7371
13989 | 33097.2656 | 6.5833
13990 | 34435.1602 | 6.4586
13991 | 36246.6797 | 6.4116
13992 | 36336.9336 | 6.5335
13993 | 33868.6875 | 6.2916
13994 | 33975.1953 | 6.1247
13995 | 33524.5078 | 5.9351
13996 | 33537.6797 | 5.825
13997 | 33363.4258 | 5.815
13998 | 32778.2578 | 5.807
13999 | 33686.5508 | 6.0116
14000 | 33206.6445 | 5.9901
14001 | 33210.5312 | 5.4901
14002 | 31373.3164 | 5.3235
14003 | 30613.8945 | 5.458
14004 | 29723.7539 | 5.7477
14005 | 28405.0918 | 5.6416
14006 | 29459.6094 | 5.4218
14007 | 29677.3184 | 5.2685
14008 | 29599.707 | 4.975
14009 | 29258.5156 | 4.8185
14010 | 28745.7148 | 4.6098
14011 | 28291.9453 | 4.1554
14012 | 26442.1133 | 3.4319
14013 | 23049.1836 | 3.0851
14014 | 21332.959 | 2.6532
14015 | 20261.8848 | 2.4316
14016 | 19204.0938 | 2.2979
14017 | 18255.0391 | 2.3771
14018 | 17312.5566 | 2.3398
14019 | 16824.8516 | 2.5295
14020 | 16497.4512 | 2.5416
14021 | 15922.0508 | 2.5251
14022 | 15832.0938 | 2.5267
14023 | 15954.167 | 2.4902
14024 | 15527.8789 | 2.752
14025 | 15561.2998 | 2.6447
14026 | 16334.1445 | 2.7716
14027 | 16330.3984 | 3.2819
14028 | 17086.9258 | 3.452
14029 | 17819.4941 | 4.1753
14030 | 20319.2852 | 4.6921
14031 | 24353.4141 | 5.3317
14032 | 27957.5645 | 5.933
14033 | 30021.166 | 6.4078
14034 | 31629.1152 | 6.3755
14035 | 32785.0625 | 6.416
14036 | 33488.9688 | 6.4577
14037 | 33368.832 | 6.5304
14038 | 33528.0977 | 6.3607
14039 | 33912.7383 | 6.3177
14040 | 34201.2656 | 6.2395
14041 | 33636.3516 | 6.2289
14042 | 35368.3438 | 5.98
14043 | 34955.0547 | 5.8926
14044 | 34721.0352 | 5.8477
14045 | 32954.6719 | 5.9498
14046 | 33791.6133 | 5.9416
14047 | 33584.0938 | 5.9356
14048 | 33364.2109 | 6.0613
14049 | 33643.7266 | 5.864
14050 | 31737.8008 | 5.6041
14051 | 30337.9004 | 5.4944
14052 | 29597.4355 | 5.7938
14053 | 28601.668 | 5.863
14054 | 30147.8594 | 5.6987
14055 | 30031.0039 | 5.4115
14056 | 29869.7637 | 5.2999
14057 | 29468.1113 | 4.8151
14058 | 28877.0781 | 4.5172
14059 | 27804.0234 | 4.2097
14060 | 26125.5703 | 3.3644
14061 | 23861.9453 | 2.977
14062 | 22090.4609 | 2.7879
14063 | 20477.752 | 2.7588
14064 | 18296.1289 | 2.4022
14065 | 17169.582 | 2.4223
14066 | 14928.4619 | 2.3973
14067 | 15852.874 | 2.5727
14068 | 15623.126 | 2.5444
14069 | 15776 | 2.7064
14070 | 15684 | 2.7327
14071 | 15708 | 2.8741
14072 | 15830 | 2.8103
14073 | 15662 | 2.7823
14074 | 15356.874 | 2.9926
14075 | 15842 | 3.0892
14076 | 15772.3896 | 3.509
14077 | 15744 | 4.4299
14078 | 21134.668 | 4.8074
14079 | 24184.082 | 5.3574
14080 | 27650.1406 | 6.0248
14081 | 31001.9434 | 6.4845
14082 | 32038.123 | 6.6112
14083 | 33371.8203 | 6.6042
14084 | 35171.4219 | 6.5565
14085 | 34992.4844 | 6.5176
14086 | 37625.1133 | 6.5632
14087 | 38281.3672 | 6.4604
14088 | 38169.8516 | 6.3075
14089 | 36980.0391 | 6.2587
14090 | 37950.2188 | 5.9448
14091 | 38446.2383 | 5.9787
14092 | 38507.3672 | 5.9424
14093 | 37305.4375 | 5.8529
14094 | 33092.0742 | 5.9415
14095 | 32895.8203 | 5.8951
14096 | 32890.2109 | 5.7581
14097 | 33123.4531 | 5.7483
14098 | 30884.5938 | 5.5578
14099 | 30368.3633 | 5.4204
14100 | 29157.5508 | 5.748
14101 | 28328.1387 | 5.5276
14102 | 28095.0977 | 5.4213
14103 | 29556.0059 | 5.284
14104 | 29688.7305 | 5.1565
14105 | 29799.627 | 4.6639
14106 | 30066.6367 | 4.2574
14107 | 29353.2363 | 4.0217
14108 | 27504.4863 | 3.5396
14109 | 25664.1484 | 3.1692
14110 | 22825.9961 | 2.7568
14111 | 21028.418 | 2.6251
14112 | 18870.2891 | 2.451
14113 | 18729.9277 | 2.4719
14114 | 18198.873 | 2.5484
14115 | 17831.127 | 2.8492
14116 | 17192 | 2.873
14117 | 17176.6211 | 2.9321
14118 | 16970 | 2.8678
14119 | 16731.8633 | 2.9577
14120 | 16666 | 2.9664
14121 | 16188 | 2.7491
14122 | 16822 | 2.8234
14123 | 17270.873 | 3.1531
14124 | 17308.1367 | 3.4745
14125 | 17912.6641 | 4.4618
14126 | 23076.6895 | 5.0901
14127 | 25524.4512 | 5.6871
14128 | 28223.3613 | 6.2283
14129 | 30250.9609 | 6.6318
14130 | 32159.7637 | 6.9122
14131 | 33275.1211 | 6.9096
14132 | 34208.7031 | 6.9985
14133 | 34014.9531 | 7.0364
14134 | 34182.4688 | 7.0928
14135 | 33879.0469 | 6.8856
14136 | 34089.9922 | 6.7462
14137 | 33860.0469 | 6.487
14138 | 33168.3711 | 6.3764
14139 | 32565.2441 | 6.3276
14140 | 32855.8438 | 6.0137
14141 | 30997.0938 | 5.9876
14142 | 29728.6406 | 5.7623
14143 | 28184.3867 | 5.8022
14144 | 28269.2676 | 5.5699
14145 | 28177.8145 | 5.392
14146 | 28331.793 | 5.3371
14147 | 29077.584 | 5.431
14148 | 28916.0684 | 5.5068
14149 | 28246.0449 | 5.3826
14150 | 28054.1836 | 5.2826
14151 | 27656.623 | 5.1314
14152 | 27206.7168 | 4.8017
14153 | 26257.8613 | 4.5797
14154 | 25346.2227 | 4.2609
14155 | 24408.043 | 3.865
14156 | 22744.6934 | 3.1597
14157 | 21123.6387 | 2.8023
14158 | 19125.3945 | 2.8181
14159 | 17941.9297 | 2.6824
14160 | 16818.2539 | 2.3645
14161 | 16128.6016 | 2.2337
14162 | 15356.3496 | 2.1395
14163 | 14832.9062 | 2.317
14164 | 14210.4229 | 2.271
14165 | 14010.6318 | 2.1915
14166 | 13982.0312 | 2.2182
14167 | 13670.1484 | 2.2104
14168 | 13737.4121 | 2.1936
14169 | 13710.9062 | 2.2347
14170 | 13582.7344 | 2.3496
14171 | 13191.8477 | 2.4855
14172 | 13635.1328 | 2.7745
14173 | 13990.0273 | 2.8394
14174 | 15587.7441 | 3.015
14175 | 16549.9023 | 3.3763
14176 | 17422.6523 | 3.6195
14177 | 19055.9648 | 3.9114
14178 | 20411.8848 | 4.2336
14179 | 20732.043 | 4.5364
14180 | 22168.8223 | 4.5005
14181 | 22582.2441 | 4.7813
14182 | 23100.793 | 4.7935
14183 | 23374.6348 | 4.7357
14184 | 23740.8145 | 4.6919
14185 | 24058.5742 | 4.5647
14186 | 24685.0938 | 4.4419
14187 | 24643.4609 | 4.5048
14188 | 24503.8516 | 4.2308
14189 | 23968.0625 | 4.0787
14190 | 23578.1758 | 4.1392
14191 | 23532.1562 | 4.1846
14192 | 23603.0508 | 4.1307
14193 | 23982.6836 | 4.2139
14194 | 24238.7031 | 4.4173
14195 | 24812.8633 | 4.297
14196 | 25085 | 4.4607
14197 | 24805.4844 | 4.4245
14198 | 24414.3359 | 4.1554
14199 | 23713.4199 | 3.7936
14200 | 23129.8828 | 3.7335
14201 | 22667.125 | 3.5099
14202 | 20826.3945 | 3.5455
14203 | 18588.4023 | 3.1734
14204 | 17438.8438 | 3.0037
14205 | 16766.1797 | 2.7629
14206 | 16239.3789 | 2.7858
14207 | 15698.6211 | 2.4171
14208 | 15453.3584 | 2.2897
14209 | 14320.0508 | 2.5016
14210 | 14090.21 | 2.5557
14211 | 13609.1768 | 2.7153
14212 | 13348.2822 | 2.6952
14213 | 13071.7773 | 2.6675
14214 | 12767.5459 | 2.622
14215 | 12838.9971 | 2.3354
14216 | 12375.1855 | 2.3281
14217 | 12108.4277 | 2.5653
14218 | 12195.0479 | 2.5749
14219 | 12048.7949 | 2.3911
14220 | 12406.8164 | 2.2805
14221 | 12568.4707 | 2.3998
14222 | 13775.3867 | 2.7391
14223 | 14235.4092 | 2.7722
14224 | 14882.3252 | 2.6534
14225 | 15633.4941 | 3.0077
14226 | 16319.5381 | 3.2526
14227 | 18132.3828 | 3.3139
14228 | 19249.3203 | 3.6083
14229 | 20729.2168 | 3.7753
14230 | 22426.6816 | 3.8422
14231 | 23848.9336 | 3.8141
14232 | 24464.3574 | 3.8882
14233 | 24625.9902 | 3.8132
14234 | 24997.7988 | 3.7655
14235 | 25129.6426 | 3.7872
14236 | 25168.0215 | 3.6625
14237 | 25140.6328 | 3.6868
14238 | 25202.6328 | 3.5984
14239 | 24698.3574 | 3.7382
14240 | 24753.5977 | 3.6906
14241 | 24816.3574 | 3.8187
14242 | 24811.7363 | 3.6744
14243 | 24815.8516 | 3.8728
14244 | 23814.6836 | 3.9519
14245 | 22420.25 | 3.8961
14246 | 21288.0469 | 3.7618
14247 | 20859.5215 | 3.7462
14248 | 20482.3516 | 3.7283
14249 | 20280.625 | 3.6243
14250 | 19726.332 | 3.2888
14251 | 18611.5293 | 3.1872
14252 | 17569.7188 | 2.7987
14253 | 16425.5586 | 2.5967
14254 | 16005.6318 | 2.6254
14255 | 16108 | 2.272
14256 | 16036.7656 | 2.1643
14257 | 15199.2285 | 2.2033
14258 | 14364.6592 | 2.11
14259 | 13949.7627 | 2.3104
14260 | 13714.5 | 2.3424
14261 | 13594.7734 | 2.3733
14262 | 13430.1523 | 2.3735
14263 | 13349.5332 | 2.4031
14264 | 13216.6367 | 2.4408
14265 | 13866.2178 | 2.6558
14266 | 13588.9844 | 2.8659
14267 | 13582.8682 | 2.929
14268 | 14354.0176 | 3.172
14269 | 15744.7012 | 4.1367
14270 | 18123.9785 | 4.6964
14271 | 23709.543 | 5.3686
14272 | 26906.9277 | 6.1564
14273 | 29637.5117 | 6.6351
14274 | 33468.125 | 6.8689
14275 | 34110.3555 | 6.8796
14276 | 35924.3242 | 6.8912
14277 | 35905.9375 | 6.6686
14278 | 35238.7891 | 6.5947
14279 | 35950.4414 | 6.6929
14280 | 35108.3984 | 6.8312
14281 | 34312.9766 | 6.8522
14282 | 34833.9844 | 6.7183
14283 | 34663.3672 | 6.5527
14284 | 35103.6406 | 6.4994
14285 | 35568.1875 | 6.5967
14286 | 34460.2383 | 6.5384
14287 | 34863.1328 | 6.3692
14288 | 34056.6094 | 6.242
14289 | 33861.7109 | 5.9882
14290 | 33587.418 | 5.8856
14291 | 33327.9102 | 5.6496
14292 | 32387.2734 | 5.8966
14293 | 29751.9004 | 5.8038
14294 | 29438.6484 | 5.3968
14295 | 30506.4492 | 5.0423
14296 | 31429.5039 | 4.8342
14297 | 30724.9922 | 4.6665
14298 | 29754.4648 | 4.467
14299 | 29095.8008 | 4.1854
14300 | 26495.0156 | 3.634
14301 | 23505.082 | 3.1432
14302 | 21621.3945 | 2.7378
14303 | 20488.1621 | 2.7229
14304 | 19410.0957 | 2.4095
14305 | 19020.1191 | 2.4513
14306 | 17615.6855 | 2.6695
14307 | 17239.4531 | 2.9771
14308 | 16742.4219 | 2.9042
14309 | 16416.9277 | 2.9421
14310 | 16296.4004 | 2.9038
14311 | 16155.6416 | 2.8142
14312 | 16323.5586 | 2.6705
14313 | 16328.084 | 2.7163
14314 | 17106.748 | 2.9694
14315 | 17163.7578 | 3.3925
14316 | 17943.5703 | 3.5633
14317 | 19085.6348 | 4.4898
14318 | 22650.5859 | 5.1114
14319 | 25750.8965 | 5.8062
14320 | 29831.5215 | 6.6749
14321 | 32449.0293 | 7.1962
14322 | 33206.8203 | 7.3026
14323 | 33809.9688 | 7.4636
14324 | 35892.0977 | 7.4306
14325 | 36288.7383 | 7.3721
14326 | 37247.0156 | 7.3357
14327 | 37734.9922 | 7.2319
14328 | 35970.8008 | 7.1983
14329 | 34812.5469 | 7.0438
14330 | 35706.5469 | 6.8256
14331 | 33974.2266 | 6.6606
14332 | 34023.332 | 6.5337
14333 | 34362.8125 | 6.5297
14334 | 34519.0625 | 6.4362
14335 | 34401.707 | 6.2699
14336 | 34046.0391 | 6.2751
14337 | 33208.8047 | 5.9269
14338 | 30095.623 | 5.7025
14339 | 30443.8555 | 5.7485
14340 | 30014.9492 | 5.8917
14341 | 29404.834 | 5.6771
14342 | 29566.6445 | 5.333
14343 | 29964.8652 | 5.154
14344 | 31581.2031 | 5.018
14345 | 29193.9492 | 4.5666
14346 | 28059.0098 | 4.4376
14347 | 27594.6211 | 4.0749
14348 | 25272.8398 | 3.84
14349 | 23108.3848 | 3.0656
14350 | 21507.4453 | 2.7624
14351 | 19767.3164 | 2.6056
14352 | 18335.873 | 2.4829
14353 | 17524.6094 | 2.4898
14354 | 16751.4336 | 2.5032
14355 | 16598.2539 | 2.7413
14356 | 16190.4004 | 2.7727
14357 | 15687.873 | 2.913
14358 | 15597.5059 | 2.7204
14359 | 15548.9785 | 2.6135
14360 | 15543.333 | 2.6232
14361 | 15615.5645 | 2.8029
14362 | 15570.3008 | 2.909
14363 | 15658.1855 | 3.3124
14364 | 16609.6074 | 3.4977
14365 | 18005.8301 | 4.555
14366 | 21569.9492 | 5.2068
14367 | 24393.416 | 5.5695
14368 | 28500.2148 | 6.2795
14369 | 31821.0508 | 6.7442
14370 | 33811.2812 | 6.9014
14371 | 34978.9766 | 6.7471
14372 | 36137.6406 | 6.8457
14373 | 35166.6094 | 6.8549
14374 | 36185.5469 | 6.8625
14375 | 36197.7578 | 6.7446
14376 | 34805.9688 | 6.5522
14377 | 35148.8398 | 6.4942
14378 | 36050.8633 | 6.346
14379 | 34788.2734 | 6.181
14380 | 34926.4219 | 6.3313
14381 | 34069.7578 | 6.1698
14382 | 33967.4102 | 6.0389
14383 | 32370.6914 | 5.8834
14384 | 31727.0391 | 5.7997
14385 | 31624.1641 | 5.7031
14386 | 31186.4883 | 5.5309
14387 | 32243.6797 | 5.5317
14388 | 32508.5742 | 5.8582
14389 | 32274.4102 | 5.7809
14390 | 31377.6055 | 5.43
14391 | 31011.9297 | 5.0958
14392 | 30578.4512 | 4.9423
14393 | 28924.6777 | 4.8772
14394 | 28656.75 | 4.5355
14395 | 27781.9492 | 4.2198
14396 | 25886.8301 | 3.7965
14397 | 23557.5254 | 3.1259
14398 | 20837.9727 | 2.7014
14399 | 20061.0352 | 2.5408
14400 | 18706.4648 | 2.4332
14401 | 17957.2969 | 2.5033
14402 | 17341.3906 | 2.3862
14403 | 17087.8223 | 2.6021
14404 | 16650.4434 | 2.5662
14405 | 16159 | 2.519
14406 | 15853.4844 | 2.4339
14407 | 16002.8203 | 2.4139
14408 | 16308.0625 | 2.4275
14409 | 15843.1465 | 2.5972
14410 | 16009.9971 | 2.8041
14411 | 16182.25 | 3.17
14412 | 17199.0527 | 3.4649
14413 | 18553.3672 | 4.3835
14414 | 22246.3203 | 4.9177
14415 | 24431.9434 | 5.4327
14416 | 28089.127 | 6.0335
14417 | 31354.3086 | 6.495
14418 | 33547.1758 | 6.8236
14419 | 34398.1328 | 6.9387
14420 | 35782.8828 | 6.894
14421 | 35408.9766 | 6.7044
14422 | 36251.7539 | 6.7419
14423 | 36809.2539 | 6.7629
14424 | 38889.1406 | 6.7697
14425 | 39403.9844 | 6.5486
14426 | 39085.2578 | 6.5062
14427 | 39169.3281 | 6.3766
14428 | 38837.7734 | 6.3419
14429 | 37985.4141 | 6.2834
14430 | 36994.8203 | 6.1847
14431 | 35974.6797 | 6.0672
14432 | 35443.8203 | 6.1782
14433 | 35412.2734 | 5.9267
14434 | 34867.4531 | 5.6526
14435 | 33455.6641 | 5.7079
14436 | 32676.8184 | 5.7433
14437 | 31712.3516 | 5.4752
14438 | 31457.373 | 5.4045
14439 | 31936.25 | 5.2257
14440 | 31369.4199 | 5.1671
14441 | 30628.7109 | 4.7369
14442 | 30131.7539 | 4.3907
14443 | 29721.6875 | 4.0016
14444 | 26847.1699 | 3.7352
14445 | 24091.6172 | 3.1266
14446 | 21556.5 | 2.8639
14447 | 20497.6992 | 2.9149
14448 | 19467.8652 | 2.496
14449 | 18643.0859 | 2.5152
14450 | 17834.2852 | 2.4822
14451 | 17330.3066 | 2.6129
14452 | 16835.6855 | 2.5807
14453 | 16327.1377 | 2.547
14454 | 16172.8848 | 2.5022
14455 | 16247.3184 | 2.4916
14456 | 16285.6416 | 2.5178
14457 | 16340.1992 | 2.8401
14458 | 16339.3252 | 2.8573
14459 | 16341.4619 | 3.0338
14460 | 17522.791 | 3.3546
14461 | 18564.8965 | 4.3043
14462 | 21760.5059 | 4.9569
14463 | 25097.4297 | 5.5401
14464 | 27911.5586 | 6.1071
14465 | 30756.4883 | 6.585
14466 | 32341.7012 | 6.7321
14467 | 33137.0586 | 6.8671
14468 | 35290.9141 | 6.8487
14469 | 35117.6484 | 6.88
14470 | 36177.8281 | 6.8796
14471 | 36452.7266 | 6.7493
14472 | 35742.9336 | 6.6916
14473 | 35434.7969 | 6.5113
14474 | 35570.1758 | 6.2214
14475 | 34705.375 | 6.0278
14476 | 33820.9648 | 5.8869
14477 | 32620.7617 | 5.6166
14478 | 32210.373 | 5.4317
14479 | 31486.8359 | 5.3832
14480 | 31837.2266 | 5.3109
14481 | 31063.668 | 5.1484
14482 | 30608.0332 | 5.1104
14483 | 31329.8477 | 5.2514
14484 | 30450.9082 | 5.2829
14485 | 29704.3613 | 5.2719
14486 | 29484.9805 | 5.0216
14487 | 29493.2129 | 4.9504
14488 | 28987.3281 | 4.6759
14489 | 28137.5371 | 4.1848
14490 | 26564.5781 | 3.9407
14491 | 25740.5352 | 3.6558
14492 | 23289.3945 | 3.2639
14493 | 21121.6777 | 3.064
14494 | 19832.0977 | 2.6485
14495 | 18870.168 | 2.4508
14496 | 17733.4824 | 2.2299
14497 | 16899.4414 | 2.2356
14498 | 16158.9131 | 2.2173
14499 | 15611.3047 | 2.6291
14500 | 15319.2109 | 2.5429
14501 | 15332.5566 | 2.4959
14502 | 15050.8818 | 2.2864
14503 | 14262.7324 | 2.162
14504 | 13551.7969 | 2.1772
14505 | 13290.1211 | 2.2146
14506 | 13414.1426 | 2.3875
14507 | 13752.5117 | 2.5356
14508 | 15211.417 | 2.6501
14509 | 16161.207 | 2.9296
14510 | 18681.0488 | 3.0805
14511 | 19710.2773 | 3.3278
14512 | 20863.9531 | 3.8067
14513 | 22030.0156 | 4.0013
14514 | 22846.0605 | 4.3316
14515 | 23726.9766 | 4.1499
14516 | 25272.8086 | 4.2721
14517 | 26027.6094 | 4.4364
14518 | 26334.7578 | 4.4001
14519 | 26221.8418 | 4.318
14520 | 25946.8516 | 4.3901
14521 | 24996.0938 | 4.2582
14522 | 24937.3457 | 4.2689
14523 | 24980.7363 | 4.3692
14524 | 24204.6914 | 4.2653
14525 | 23636.0078 | 4.2507
14526 | 22830.4062 | 4.1599
14527 | 23306.0801 | 4.1259
14528 | 23642.4922 | 4.2013
14529 | 24429.0391 | 4.3527
14530 | 23464.2168 | 4.2651
14531 | 24095.8926 | 4.1942
14532 | 24989.6602 | 4.2316
14533 | 25118.9258 | 4.2893
14534 | 24789.9141 | 4.1593
14535 | 24369.2715 | 3.8341
14536 | 23871.25 | 3.5727
14537 | 22454.6582 | 3.4027
14538 | 20390.8047 | 3.2786
14539 | 18694.2129 | 3.2064
14540 | 17574.4004 | 2.8664
14541 | 16928.8418 | 2.6858
14542 | 16272.8633 | 2.5657
14543 | 15550.9375 | 2.414
14544 | 15032.6387 | 2.2591
14545 | 14217.4922 | 2.2515
14546 | 13567.7012 | 2.1782
14547 | 13050.7344 | 2.3052
14548 | 12727.6074 | 2.2587
14549 | 12458.9434 | 2.1976
14550 | 12137.9551 | 2.1259
14551 | 11869.0703 | 2.1465
14552 | 11477.9766 | 2.076
14553 | 11338.334 | 2.0839
14554 | 11454.6504 | 2.1554
14555 | 11384.6699 | 2.2241
14556 | 11850.3955 | 2.2145
14557 | 12450.7402 | 2.3487
14558 | 13646.9766 | 2.6382
14559 | 14381.8916 | 2.5769
14560 | 14969.7041 | 2.4995
14561 | 14998.6406 | 2.4241
14562 | 16353.7383 | 2.6648
14563 | 17127.2441 | 2.9463
14564 | 18986.1172 | 3.0788
14565 | 19947.7734 | 3.3817
14566 | 21199.291 | 3.3244
14567 | 22096.627 | 3.5364
14568 | 21926.0781 | 3.6223
14569 | 22704.3438 | 3.6726
14570 | 23595.8691 | 3.8485
14571 | 24419.4609 | 3.8194
14572 | 23950.3242 | 3.5792
14573 | 24111.166 | 3.407
14574 | 23428.9434 | 3.4661
14575 | 22985.1406 | 3.3366
14576 | 23135.8574 | 3.2848
14577 | 23504.0391 | 3.5273
14578 | 23533.6465 | 3.6099
14579 | 23999.8262 | 4.0284
14580 | 23551.6172 | 4.2556
14581 | 21536.9609 | 3.9057
14582 | 21050.0273 | 3.6812
14583 | 20687.0156 | 3.5505
14584 | 19922.6992 | 3.5831
14585 | 19219.5508 | 3.4291
14586 | 18870.7871 | 3.3174
14587 | 18476.5293 | 3.1697
14588 | 17888.3496 | 3.1244
14589 | 17360.3496 | 3.0767
14590 | 16606.3066 | 2.8889
14591 | 15968.0537 | 2.5986
14592 | 14551.3262 | 2.4292
14593 | 14284.3574 | 2.5681
14594 | 13325.9453 | 2.5445
14595 | 13158.6836 | 2.7138
14596 | 13183.0352 | 2.4887
14597 | 12499.4043 | 2.2671
14598 | 12133.6562 | 2.2485
14599 | 12291.9805 | 2.2537
14600 | 12060.9922 | 2.2468
14601 | 12019.9668 | 2.2849
14602 | 12399.1445 | 2.2729
14603 | 12371.3135 | 2.4308
14604 | 13760.7051 | 2.4929
14605 | 15933.9053 | 2.6503
14606 | 19371.9609 | 2.9702
14607 | 22881.7461 | 3.646
14608 | 25406.3496 | 4.1383
14609 | 27971.9883 | 4.3973
14610 | 30544.7383 | 4.9267
14611 | 32338.7383 | 5.3585
14612 | 34336.6875 | 5.7135
14613 | 34521.6016 | 5.8538
14614 | 36659.3359 | 6.0393
14615 | 37664.3906 | 6.0906
14616 | 36332.6953 | 6.2687
14617 | 35528.6484 | 6.2228
14618 | 37061.3555 | 6.2318
14619 | 35503.5234 | 6.0675
14620 | 35503.5234 | 5.9662
14621 | 34397.9648 | 5.9922
14622 | 34322.5859 | 5.9556
14623 | 34624.1016 | 5.9085
14624 | 34774.8594 | 5.8605
14625 | 34498.4727 | 5.724
14626 | 32990.8906 | 5.8967
14627 | 33191.8984 | 6.1828
14628 | 33292.4062 | 5.755
14629 | 32488.3633 | 5.5081
14630 | 32237.0996 | 5.107
14631 | 31910.457 | 5.0655
14632 | 32161.7227 | 4.8903
14633 | 31206.918 | 4.6416
14634 | 29598.832 | 4.6068
14635 | 28518.3984 | 4.3632
14636 | 26332.4102 | 4.1228
14637 | 24096.1641 | 3.9644
14638 | 21910.1719 | 3.4466
14639 | 20854.8633 | 2.9269
14640 | 19648.8008 | 2.6995
14641 | 18694 | 2.4968
14642 | 17764.3242 | 2.477
14643 | 17236.6719 | 2.7251
14644 | 17060.7871 | 2.6861
14645 | 16935.1562 | 2.6713
14646 | 16683.8945 | 2.7391
14647 | 16734.1445 | 2.8384
14648 | 16885.1016 | 2.8327
14649 | 16692.8926 | 2.8354
14650 | 17010.5352 | 2.8103
14651 | 16910.2305 | 2.7283
14652 | 17864.8301 | 2.858
14653 | 19523.1699 | 3.1774
14654 | 23317.248 | 3.2698
14655 | 25779.6289 | 3.9224
14656 | 28292.2637 | 4.1029
14657 | 30729.5176 | 4.5909
14658 | 31784.8242 | 5.1431
14659 | 33016.0156 | 5.621
14660 | 35604.0312 | 5.7059
14661 | 35277.3867 | 5.8657
14662 | 35729.6641 | 6.1224
14663 | 36031.1797 | 6.159
14664 | 36332.6953 | 6.0353
14665 | 36458.3281 | 5.9511
14666 | 37463.3789 | 5.9375
14667 | 36960.8516 | 5.9619
14668 | 36257.3125 | 5.914
14669 | 36784.9688 | 5.9493
14670 | 36131.6875 | 5.7963
14671 | 35453.2695 | 5.6449
14672 | 33870.3125 | 5.7268
14673 | 33970.8164 | 5.8369
14674 | 33217.0234 | 6.0071
14675 | 33116.5234 | 6.2412
14676 | 32639.1191 | 6.1249
14677 | 31608.9414 | 5.734
14678 | 30880.2773 | 5.6116
14679 | 30603.8867 | 5.5427
14680 | 30051.1055 | 5.3946
14681 | 30880.2773 | 5.0024
14682 | 31031.0352 | 4.7706
14683 | 29020.9277 | 4.5554
14684 | 27086.1992 | 4.4966
14685 | 25101.2188 | 4.1516
14686 | 23669.0156 | 3.3534
14687 | 22387.5742 | 2.8859
14688 | 21181.5078 | 2.8351
14689 | 20226.707 | 2.5967
14690 | 19498.043 | 2.6011
14691 | 19271.9062 | 2.7934
14692 | 18895.0098 | 2.8547
14693 | 18668.873 | 3.0485
14694 | 18417.6094 | 2.8932
14695 | 17839.7031 | 2.847
14696 | 17663.8203 | 2.8099
14697 | 17864.832 | 2.8241
14698 | 17663.8203 | 2.7807
14699 | 17563.3145 | 2.5573
14700 | 18417.6094 | 2.8456
14701 | 20126.2031 | 3.178
14702 | 23945.4062 | 3.4941
14703 | 26533.418 | 4.0063
14704 | 28819.916 | 4.53
14705 | 31156.668 | 4.8679
14706 | 31960.7109 | 5.6062
14707 | 32764.75 | 6.0658
14708 | 34448.2188 | 6.3593
14709 | 35453.2695 | 6.2748
14710 | 34624.1016 | 6.3636
14711 | 34875.3672 | 6.4268
14712 | 34096.4492 | 6.3857
14713 | 34423.0938 | 6.33
14714 | 35176.8789 | 6.3076
14715 | 35101.5 | 6.1666
14716 | 34297.4609 | 6.1054
14717 | 33921.7617 | 6.0075
14718 | 34071.3242 | 5.9905
14719 | 34649.2305 | 5.9002
14720 | 33794.9336 | 5.8788
14721 | 32287.3535 | 5.9302
14722 | 31332.5508 | 6.2054
14723 | 31910.457 | 6.3768
14724 | 32463.2383 | 6.1559
14725 | 31935.582 | 6.023
14726 | 30905.4023 | 5.7929
14727 | 30503.3828 | 5.8205
14728 | 30151.6113 | 5.4781
14729 | 29573.707 | 5.1287
14730 | 30151.6113 | 4.911
14731 | 29146.5586 | 4.4678
14732 | 27136.4492 | 4.2045
14733 | 24799.7012 | 4.0597
14734 | 22462.9531 | 3.4577
14735 | 21282.0117 | 3.0144
14736 | 20276.959 | 2.8818
14737 | 19347.2852 | 2.627
14738 | 18291.9805 | 2.5084
14739 | 17688.9453 | 2.6888
14740 | 17387.4297 | 2.6986
14741 | 17035.6621 | 2.6401
14742 | 16834.6504 | 2.5707
14743 | 16960.2812 | 2.6552
14744 | 16809.5234 | 2.5901
14745 | 16709.0195 | 2.5796
14746 | 16759.2715 | 2.597
14747 | 17161.293 | 2.662
14748 | 18668.873 | 2.7633
14749 | 20251.832 | 3.1982
14750 | 23593.6367 | 3.2815
14751 | 25679.125 | 4.2009
14752 | 28417.8945 | 4.4896
14753 | 31332.5508 | 5.195
14754 | 32764.75 | 5.9857
14755 | 34196.9531 | 6.3551
14756 | 34473.3438 | 6.3346
14757 | 33945.6914 | 6.4014
14758 | 35101.5 | 6.5061
14759 | 34372.8398 | 6.6815
14760 | 33568.7969 | 6.5908
14761 | 34498.4688 | 6.5322
14762 | 33970.8164 | 6.5409
14763 | 34222.0781 | 6.4308
14764 | 34523.5977 | 6.1128
14765 | 33518.543 | 6.0839
14766 | 32990.8906 | 6.0428
14767 | 32488.3613 | 6.0103
14768 | 31759.6992 | 6.0567
14769 | 31684.3203 | 6.1325
14770 | 30955.6562 | 6.4004
14771 | 31232.0469 | 6.3747
14772 | 31985.8359 | 5.9603
14773 | 31031.0352 | 5.9429
14774 | 30804.8984 | 5.9034
14775 | 30327.4961 | 5.7223
14776 | 29649.0859 | 5.5628
14777 | 29598.832 | 5.3552
14778 | 29046.0547 | 5.2327
14779 | 30025.9805 | 4.6245
14780 | 26684.1758 | 4.4916
14781 | 23141.3633 | 4.1243
14782 | 21533.2773 | 3.5977
14783 | 20176.4531 | 2.9905
14784 | 18920.1367 | 2.864
14785 | 18166.3477 | 2.5092
14786 | 17538.1875 | 2.5038
14787 | 17111.0391 | 2.7714
14788 | 16558.2617 | 2.7049
14789 | 16030.6074 | 2.6364
14790 | 15829.5977 | 2.5907
14791 | 15854.7246 | 2.6392
14792 | 15379.7236 | 2.5948
14793 | 15230.3652 | 2.7711
14794 | 15502.9541 | 2.8868
14795 | 15406.6494 | 2.9063
14796 | 16615.7109 | 2.9746
14797 | 18259.9258 | 3.0719
14798 | 22268.9414 | 3.54
14799 | 24648.2168 | 4.2267
14800 | 27437.4395 | 4.2868
14801 | 28595.3789 | 4.9783
14802 | 29448.0762 | 5.5924
14803 | 30453.1289 | 6.1463
14804 | 31533.5625 | 6.2804
14805 | 31232.0449 | 6.3425
14806 | 32186.8477 | 6.4163
14807 | 32211.9746 | 6.4513
14808 | 31985.8359 | 6.2824
14809 | 31659.1953 | 6.2967
14810 | 31785.0234 | 6.2742
14811 | 31056.1602 | 6.1109
14812 | 30428.2031 | 6.0739
14813 | 29649.2852 | 6.0202
14814 | 29221.9375 | 5.8064
14815 | 29096.3086 | 5.7767
14816 | 28845.043 | 5.7919
14817 | 28719.4102 | 5.7429
14818 | 28669.1582 | 5.9103
14819 | 28895.2969 | 5.959
14820 | 29548.582 | 5.808
14821 | 29196.8125 | 5.6404
14822 | 28392.7676 | 5.5252
14823 | 28041 | 5.5121
14824 | 27287.209 | 5.4387
14825 | 26633.9219 | 5.1949
14826 | 25729.375 | 5.012
14827 | 24774.5742 | 4.4695
14828 | 23769.5195 | 4.2945
14829 | 23091.1094 | 4.0144
14830 | 21181.5078 | 3.4586
14831 | 20251.832 | 2.8567
14832 | 19246.7793 | 2.7533
14833 | 18543.2422 | 2.4754
14834 | 17864.8301 | 2.4388
14835 | 17412.5566 | 2.735
14836 | 17010.5352 | 2.7511
14837 | 16784.3984 | 2.8407
14838 | 16558.2617 | 2.4236
14839 | 16256.7441 | 2.4001
14840 | 15930.1016 | 2.3629
14841 | 15804.4707 | 2.4807
14842 | 15879.8496 | 2.5731
14843 | 15176.3105 | 2.3996
14844 | 15754.2188 | 2.4186
14845 | 15980.3555 | 2.7128
14846 | 17412.5566 | 2.919
14847 | 18543.2422 | 3.2047
14848 | 19699.0547 | 3.3032
14849 | 20628.7266 | 3.393
14850 | 22086.2559 | 3.8286
14851 | 22866.9727 | 4.3182
14852 | 23798.0469 | 4.4583
14853 | 24402.2793 | 4.5274
14854 | 24601.6914 | 4.6744
14855 | 24526.9121 | 4.6054
14856 | 23902.752 | 4.639
14857 | 23601.2363 | 4.5677
14858 | 23924.877 | 4.4989
14859 | 23697.3398 | 4.5117
14860 | 23298.1211 | 4.5683
14861 | 23045.459 | 4.455
14862 | 22841.4473 | 4.3435
14863 | 22742.7422 | 4.2036
14864 | 22719.6152 | 4.2564
14865 | 22640.6387 | 4.3609
14866 | 23191.6152 | 4.6541
14867 | 24121.2891 | 4.9565
14868 | 25302.2285 | 4.9757
14869 | 25402.7324 | 4.7467
14870 | 25151.4707 | 4.5666
14871 | 25176.5957 | 4.4524
14872 | 24900.207 | 4.1888
14873 | 24473.0586 | 3.9425
14874 | 22789.5938 | 3.7586
14875 | 21407.6445 | 3.6682
14876 | 20075.9492 | 3.4249
14877 | 19347.2852 | 3.2078
14878 | 20477.9688 | 3.2358
14879 | 19447.7891 | 3.1234
14880 | 18040.7148 | 2.7788
14881 | 17286.9258 | 2.5502
14882 | 16859.7773 | 2.5506
14883 | 16859.7773 | 3.0469
14884 | 16432.6289 | 3.067
14885 | 13752.1113 | 2.6705
14886 | 13178.2041 | 2.6283
14887 | 12923.0566 | 2.7449
14888 | 12752.7812 | 2.6309
14889 | 12455.4619 | 2.5855
14890 | 11866.8008 | 2.5497
14891 | 12052.9336 | 2.3556
14892 | 12333.0703 | 2.2789
14893 | 12313.5918 | 2.3492
14894 | 13205.709 | 2.4907
14895 | 13865.7598 | 2.4901
14896 | 14437.5732 | 2.4529
14897 | 14827.3418 | 2.5889
14898 | 16077.5215 | 2.7992
14899 | 17140.9648 | 3.0321
14900 | 18629.0352 | 3.1731
14901 | 19115.0625 | 3.3243
14902 | 20433.5664 | 3.5849
14903 | 21210.3223 | 3.8608
14904 | 21863.7383 | 3.9812
14905 | 22014.3066 | 3.8199
14906 | 21975.6328 | 4.1034
14907 | 22069.3281 | 4.0714
14908 | 22163.3398 | 3.9253
14909 | 21783.2852 | 3.9093
14910 | 21698.0645 | 3.8652
14911 | 21928.8047 | 3.894
14912 | 22010.9258 | 3.7035
14913 | 21923.8828 | 3.7823
14914 | 21717.6934 | 4.046
14915 | 21524.5781 | 4.5921
14916 | 20916.3047 | 4.6034
14917 | 20679.0625 | 4.4162
14918 | 19895.6914 | 4.2813
14919 | 19234.8984 | 4.0588
14920 | 18762.6953 | 3.9593
14921 | 18165.1367 | 3.8886
14922 | 17944.7461 | 3.7719
14923 | 17491.3672 | 3.5307
14924 | 16894.6113 | 3.3324
14925 | 16144.7031 | 3.1936
14926 | 15514.5156 | 3.1729
14927 | 15603.9902 | 2.9833
14928 | 16028.7695 | 2.6662
14929 | 15496.4941 | 2.5303
14930 | 15096.3574 | 2.5079
14931 | 13882.3867 | 2.7428
14932 | 12691.0811 | 2.744
14933 | 12502.5547 | 2.8182
14934 | 12105.4785 | 2.5724
14935 | 12155.9844 | 2.5321
14936 | 11992.0254 | 2.5184
14937 | 11991.1504 | 2.5285
14938 | 12289.0664 | 2.5239
14939 | 12359.0117 | 2.6514
14940 | 13203.6562 | 2.8212
14941 | 14743.5312 | 3.2253
14942 | 19271.918 | 3.5546
14943 | 24495.8359 | 4.3312
14944 | 27375.6816 | 4.9427
14945 | 28121.6836 | 5.4432
14946 | 29277.2637 | 6.0124
14947 | 31035.8555 | 6.7993
14948 | 32666.3086 | 6.8822
14949 | 33164.4688 | 6.9485
14950 | 33905.8906 | 6.707
14951 | 34322.6484 | 6.8906
14952 | 35003.5625 | 6.8517
14953 | 35412.8281 | 6.8409
14954 | 36528.6602 | 6.8257
14955 | 35586.9688 | 6.6938
14956 | 35526.7227 | 6.5454
14957 | 35201.043 | 6.6164
14958 | 34049.2695 | 6.4659
14959 | 33660.375 | 6.5411
14960 | 33471.8672 | 6.5261
14961 | 32894.8125 | 6.6346
14962 | 30701.4648 | 6.6815
14963 | 30819.3496 | 6.5283
14964 | 31019.6035 | 6.2366
14965 | 30811.2129 | 6.0396
14966 | 30424.8223 | 5.7311
14967 | 30196.0645 | 5.6517
14968 | 30423.5801 | 5.4678
14969 | 29925.6543 | 4.8985
14970 | 28693.9785 | 4.7022
14971 | 27739.4297 | 4.6668
14972 | 26153.3438 | 4.361
14973 | 23296.9199 | 4.0833
14974 | 21146.5586 | 3.7631
14975 | 20008.1484 | 3.1248
14976 | 18546.9355 | 2.7722
14977 | 17700.7539 | 2.6328
14978 | 16851.7441 | 2.6584
14979 | 16503.1445 | 2.9348
14980 | 16209.7656 | 2.9209
14981 | 15735.1016 | 2.8928
14982 | 15292.5762 | 2.7409
14983 | 15177.0811 | 2.7972
14984 | 15434.7637 | 2.7898
14985 | 15479.5215 | 2.708
14986 | 15677.29 | 2.6967
14987 | 15818.5332 | 2.9684
14988 | 16998.3652 | 3.111
14989 | 18636.1777 | 3.2788
14990 | 22195.0117 | 3.6244
14991 | 24642.8906 | 4.4415
14992 | 28089.1777 | 5.1394
14993 | 30863.4648 | 5.5618
14994 | 32562.5625 | 6.2706
14995 | 33773.5 | 7.1206
14996 | 33668.375 | 7.227
14997 | 34234.0039 | 7.2514
14998 | 35009.4492 | 7.4093
14999 | 35004.4609 | 7.2836
15000 | 34944.3203 | 7.3158
15001 | 32989.1836 | 7.2676
15002 | 33316.7188 | 7.3609
15003 | 33925.2891 | 7.2734
15004 | 32943.5508 | 6.9953
15005 | 32995.4258 | 7.0068
15006 | 32814.2539 | 6.9123
15007 | 32448.9297 | 6.8799
15008 | 31686.2656 | 6.9282
15009 | 31208.1074 | 6.9953
15010 | 30403.6973 | 6.8846
15011 | 29815.6758 | 6.8312
15012 | 30130.5488 | 6.4538
15013 | 30111.6738 | 6.2117
15014 | 29839.0547 | 6.0985
15015 | 29701.0547 | 5.9671
15016 | 28218.3047 | 5.694
15017 | 27833.9355 | 5.2622
15018 | 27367.0391 | 4.9687
15019 | 27040.375 | 4.8571
15020 | 24438.6172 | 4.6553
15021 | 21848.7402 | 4.1839
15022 | 20001 | 3.6316
15023 | 18920.3359 | 3.3711
15024 | 17494.25 | 3.1026
15025 | 16790.1133 | 2.7937
15026 | 16078.4805 | 2.8715
15027 | 15789.2383 | 3.1814
15028 | 15307.4492 | 3.0887
15029 | 14869.4492 | 2.8647
15030 | 14602.7861 | 2.8621
15031 | 14729.4785 | 2.9771
15032 | 14711.8691 | 2.9595
15033 | 14679.2266 | 2.9717
15034 | 14581.9629 | 2.886
15035 | 14742.3516 | 2.9974
15036 | 16018.0703 | 3.1254
15037 | 17498.4824 | 3.5669
15038 | 21495.8438 | 3.7111
15039 | 23662.457 | 4.6205
15040 | 27002.2598 | 5.253
15041 | 31008.7285 | 5.6747
15042 | 32674.3086 | 6.3373
15043 | 32438.9531 | 6.9068
15044 | 33550.6055 | 7.0143
15045 | 33658.1211 | 7.1122
15046 | 35489.9766 | 7.1211
15047 | 35443.9766 | 7.0453
15048 | 34678.8047 | 6.9644
15049 | 34185.1523 | 6.8486
15050 | 34992.9414 | 7.0541
15051 | 35360.7109 | 7.0099
15052 | 36062.25 | 6.7757
15053 | 34607.1719 | 6.7433
15054 | 33873.8906 | 6.6505
15055 | 34262.4141 | 6.7623
15056 | 34310.5977 | 6.625
15057 | 33171.6367 | 6.4463
15058 | 30442.4531 | 6.5476
15059 | 30302.3164 | 6.501
15060 | 30872.9609 | 6.3162
15061 | 30531.2129 | 6.0603
15062 | 30022.0645 | 5.9499
15063 | 29738.1797 | 5.8526
15064 | 28825.7266 | 5.7476
15065 | 28290.2109 | 5.2791
15066 | 27812.1875 | 4.9308
15067 | 26844.7441 | 4.7532
15068 | 24401.1211 | 4.6417
15069 | 21993.2461 | 4.1463
15070 | 20244.5156 | 3.8161
15071 | 19356.1055 | 3.1193
15072 | 17883.6504 | 2.924
15073 | 16675.7031 | 2.667
15074 | 16303.1016 | 2.6605
15075 | 15941.123 | 2.9918
15076 | 15554.0918 | 2.9678
15077 | 15324.1123 | 2.9667
15078 | 14830.6387 | 2.9782
15079 | 14716.5117 | 3.0852
15080 | 14784.5537 | 2.9014
15081 | 15165.5 | 2.8226
15082 | 15008.2363 | 2.744
15083 | 15019.248 | 2.8616
15084 | 16212.1855 | 3.0781
15085 | 17597.0723 | 3.3077
15086 | 20663.5801 | 3.6221
15087 | 23495.9531 | 4.6766
15088 | 27580.9258 | 5.0724
15089 | 29630.6426 | 5.4078
15090 | 31626.5195 | 5.9654
15091 | 34552.0703 | 6.6809
15092 | 36204.25 | 7.0657
15093 | 35288.0938 | 7.1215
15094 | 36624.0391 | 7.3212
15095 | 37856.6094 | 7.2938
15096 | 36422.0391 | 7.1283
15097 | 35582.8477 | 6.8618
15098 | 35676.8711 | 6.9491
15099 | 35241.332 | 6.7231
15100 | 34487.4258 | 6.5118
15101 | 34204.7852 | 6.4059
15102 | 33013.8242 | 6.2844
15103 | 32501.0664 | 6.259
15104 | 31824.7715 | 6.2566
15105 | 31919.541 | 6.1539
15106 | 31044.1504 | 6.2901
15107 | 31943.8867 | 6.4059
15108 | 30969.4434 | 6.2477
15109 | 29233.6113 | 6.1079
15110 | 28835.0625 | 5.8831
15111 | 28687.2305 | 5.8734
15112 | 28778.4609 | 5.7644
15113 | 28727.4941 | 5.3091
15114 | 27803.0625 | 5.0715
15115 | 27252.2832 | 4.7008
15116 | 25063.1641 | 4.569
15117 | 22383.8867 | 4.0334
15118 | 20515.043 | 3.6522
15119 | 19567.2305 | 3.1642
15120 | 18545.3242 | 2.8741
15121 | 18838.9785 | 3.0519
15122 | 17758.957 | 3.0477
15123 | 17378.0625 | 3.0978
15124 | 16836.7988 | 3.088
15125 | 16312.8926 | 2.9855
15126 | 15943.0078 | 2.9293
15127 | 15458.7842 | 3.1051
15128 | 15584.7852 | 3.072
15129 | 15597.4062 | 3.0806
15130 | 15495.8896 | 3.059
15131 | 15601.6582 | 3
15132 | 16849.7227 | 3.1051
15133 | 18501.6934 | 3.4507
15134 | 21769.7266 | 3.7521
15135 | 24600.0156 | 4.5832
15136 | 28386.0938 | 5.1851
15137 | 31384.8887 | 5.6976
15138 | 33474.2578 | 6.2578
15139 | 33860.3945 | 7.097
15140 | 34830.5547 | 7.3
15141 | 34761.8164 | 7.3636
15142 | 35921.0078 | 7.454
15143 | 36091.5156 | 7.3275
15144 | 34931.5625 | 7.3289
15145 | 33302.4883 | 7.3707
15146 | 32968.8594 | 7.2524
15147 | 32277.9199 | 7.1025
15148 | 32055.0469 | 6.7473
15149 | 31939.5293 | 6.5619
15150 | 30811.1172 | 6.4289
15151 | 30093.3066 | 6.396
15152 | 29752.043 | 6.2426
15153 | 29415.7695 | 6.1753
15154 | 29335.9062 | 6.3729
15155 | 28598.4844 | 6.2359
15156 | 28490.9688 | 5.8259
15157 | 28191.5898 | 5.6578
15158 | 27889.1992 | 5.55
15159 | 27654.1875 | 5.4917
15160 | 27490.168 | 5.3579
15161 | 26821.7773 | 5.1173
15162 | 25276.7969 | 4.8949
15163 | 24324.752 | 4.5028
15164 | 22564.5293 | 4.3156
15165 | 20459.4121 | 3.9722
15166 | 18765.209 | 3.604
15167 | 17834.9141 | 2.9518
15168 | 16774.8496 | 2.7361
15169 | 16895.3555 | 2.632
15170 | 15974.2285 | 2.7478
15171 | 15693.1035 | 2.8114
15172 | 14574.417 | 2.6995
15173 | 14110.0254 | 2.6256
15174 | 14005.29 | 2.6302
15175 | 13586.7002 | 2.6496
15176 | 13511.498 | 2.5969
15177 | 13369.0254 | 2.6569
15178 | 13357.1602 | 2.5559
15179 | 13438.4258 | 2.7796
15180 | 14050.6973 | 2.6827
15181 | 14575.2266 | 2.5558
15182 | 16048.3027 | 2.6928
15183 | 17930.5469 | 3.0979
15184 | 19118.9785 | 3.2644
15185 | 20125.1602 | 3.7355
15186 | 21818.2344 | 4.0932
15187 | 23592.0898 | 4.3825
15188 | 26311.3652 | 4.5512
15189 | 27142.2812 | 4.6701
15190 | 28144.9688 | 5.0303
15191 | 27534.168 | 4.9002
15192 | 26915.5234 | 4.8185
15193 | 27545.3145 | 4.771
15194 | 27560.9258 | 4.7616
15195 | 26888.1445 | 4.6656
15196 | 26589.3867 | 4.574
15197 | 25864.4473 | 4.4687
15198 | 25742.9746 | 4.3528
15199 | 25735.0918 | 4.36
15200 | 25724.8379 | 4.3356
15201 | 25861.8711 | 4.3864
15202 | 25996.2383 | 4.8251
15203 | 26082.3555 | 5.069
15204 | 26554.2598 | 4.9866
15205 | 26474.6289 | 4.8038
15206 | 25867.8496 | 4.5282
15207 | 25066.0605 | 4.5482
15208 | 24296.1309 | 4.593
15209 | 23702.2461 | 3.9688
15210 | 21844.002 | 3.6929
15211 | 20293.4336 | 3.3838
15212 | 19075.9883 | 3.1577
15213 | 18542.2207 | 3.1328
15214 | 17746.6602 | 2.8729
15215 | 17115.9043 | 2.5745
15216 | 16679.7246 | 2.4577
15217 | 16089.8398 | 2.2259
15218 | 15493.6582 | 2.1055
15219 | 15230.416 | 2.1865
15220 | 14896.9434 | 2.4168
15221 | 14141.543 | 2.6583
15222 | 13823.8906 | 2.5776
15223 | 13779.6582 | 2.8213
15224 | 13421.7529 | 2.7692
15225 | 13509.6875 | 2.7468
15226 | 13479.4141 | 2.6872
15227 | 13327.1826 | 2.6803
15228 | 14022.4238 | 2.6728
15229 | 14242.584 | 2.4024
15230 | 14598.8574 | 2.5276
15231 | 14892.5107 | 2.6025
15232 | 15808.4395 | 2.5522
15233 | 16619.9766 | 2.5979
15234 | 17542.7539 | 3.0707
15235 | 18445.5566 | 3.472
15236 | 20231.7812 | 3.3947
15237 | 21939.8867 | 3.53
15238 | 22426.5293 | 3.7184
15239 | 23698.7305 | 3.9665
15240 | 24479.2793 | 4.0868
15241 | 24635.7637 | 3.9298
15242 | 25930.9746 | 4.1816
15243 | 26516.8828 | 4.4024
15244 | 26237.9648 | 4.1354
15245 | 26495.1348 | 4.0384
15246 | 26510.5137 | 4.0276
15247 | 25998.2188 | 4.1448
15248 | 26117.9863 | 4.1454
15249 | 25748.9551 | 4.2201
15250 | 25404.8184 | 4.4055
15251 | 25350.6797 | 4.6518
15252 | 24148.5 | 4.4418
15253 | 22859.9316 | 4.2357
15254 | 21669.3613 | 4.1645
15255 | 20896.3281 | 3.9762
15256 | 20476.6758 | 3.8327
15257 | 19833.2539 | 3.6938
15258 | 19564.7461 | 3.5417
15259 | 18868.4512 | 3.4207
15260 | 18376.5664 | 3.306
15261 | 17572.6406 | 3.0857
15262 | 17024.4805 | 2.9344
15263 | 16219.5645 | 2.6846
15264 | 15518.7842 | 2.495
15265 | 14860.7637 | 2.4149
15266 | 14384.7861 | 2.5868
15267 | 13943.7734 | 2.8822
15268 | 13757.501 | 2.8355
15269 | 13823.1318 | 2.7689
15270 | 13531.0156 | 2.7193
15271 | 13147.5293 | 2.7582
15272 | 12742.1504 | 2.722
15273 | 12927.0029 | 2.7786
15274 | 13132.541 | 2.7376
15275 | 13177.666 | 2.7646
15276 | 14514.2363 | 2.7493
15277 | 16838.7344 | 3.1066
15278 | 20809.0645 | 3.3019
15279 | 23314.9609 | 4.1133
15280 | 25940.7227 | 4.7542
15281 | 28589.3574 | 5.357
15282 | 30912.7285 | 5.7644
15283 | 34216.9219 | 6.4386
15284 | 35919.2617 | 6.6336
15285 | 37609.4609 | 6.7295
15286 | 37934.4961 | 6.9644
15287 | 37457.7148 | 6.9837
15288 | 37030.4297 | 6.8896
15289 | 36286.293 | 6.7565
15290 | 36678.5469 | 6.7507
15291 | 35650.1133 | 6.7309
15292 | 35287.2188 | 6.5672
15293 | 34813.7031 | 6.5427
15294 | 33607.5234 | 6.4902
15295 | 34305.4062 | 6.505
15296 | 33640.6484 | 6.5847
15297 | 33029.1094 | 6.5636
15298 | 32360.8145 | 6.7487
15299 | 31378.3828 | 6.6171
15300 | 31415.6445 | 6.2758
15301 | 30900.3613 | 5.9515
15302 | 30358.4531 | 5.7048
15303 | 30370.5703 | 5.5338
15304 | 30364.6855 | 5.4443
15305 | 29356.5273 | 4.8859
15306 | 28390.4629 | 4.6654
15307 | 27289.0391 | 4.5556
15308 | 24551.2578 | 4.3198
15309 | 22545.2871 | 3.903
15310 | 20671.1797 | 3.6999
15311 | 19338.7266 | 3.5184
15312 | 18364.7988 | 2.9191
15313 | 17340.1328 | 2.7049
15314 | 16740.1348 | 2.7929
15315 | 16249.3984 | 2.7677
15316 | 15867.2617 | 2.7415
15317 | 15398.5977 | 2.677
15318 | 15194.4805 | 2.6108
15319 | 15181.6797 | 2.8633
15320 | 15360.3945 | 2.7464
15321 | 15331.1543 | 2.6745
15322 | 15480.7852 | 2.6228
15323 | 15591.6582 | 2.7333
15324 | 16728.7344 | 3.094
15325 | 18307.3047 | 3.1572
15326 | 22028.7617 | 3.5336
15327 | 24714.8906 | 4.2672
15328 | 27510.6719 | 4.6969
15329 | 29459.0312 | 5.347
15330 | 31957.666 | 6.2991
15331 | 33918.8984 | 6.7368
15332 | 34175.4062 | 6.8492
15333 | 35036.0703 | 7.03
15334 | 37325.2109 | 6.9308
15335 | 36315.2617 | 6.6879
15336 | 35214.9844 | 6.6167
15337 | 34520.8047 | 6.6166
15338 | 34360.1641 | 6.7096
15339 | 34133.707 | 6.7088
15340 | 33819.2031 | 6.3749
15341 | 33428.3945 | 6.1229
15342 | 33550.5078 | 6.0635
15343 | 33480.9961 | 6.147
15344 | 32430.0566 | 6.3102
15345 | 31541.6445 | 6.42
15346 | 31068.8652 | 6.8061
15347 | 30649.3496 | 6.7825
15348 | 31075.9922 | 6.2401
15349 | 30842.2227 | 5.8465
15350 | 30394.5703 | 5.8837
15351 | 30030.1797 | 5.8011
15352 | 29232.0215 | 5.5584
15353 | 28482.5996 | 5.1692
15354 | 27595.9355 | 4.8787
15355 | 26743.502 | 4.9607
15356 | 24410.1328 | 4.4409
15357 | 22312.3906 | 4.1968
15358 | 20534.4434 | 3.8657
15359 | 19422.7266 | 3.6808
15360 | 18143.0527 | 3.0678
15361 | 17121.4922 | 2.6484
15362 | 16245.124 | 2.6079
15363 | 15803.4922 | 2.8746
15364 | 15522.7344 | 2.9394
15365 | 15090.8281 | 3.0025
15366 | 14984.4824 | 2.6786
15367 | 14924.7842 | 2.6487
15368 | 14871.248 | 2.6272
15369 | 14657.3633 | 2.6569
15370 | 14776.2363 | 2.6403
15371 | 15202.8799 | 2.7258
15372 | 15547.7959 | 2.8766
15373 | 16903.4688 | 3.2226
15374 | 21624.1172 | 3.4565
15375 | 24142.1094 | 4.3599
15376 | 26804.5137 | 5.0917
15377 | 28343.5898 | 5.5024
15378 | 29611.6738 | 6.1399
15379 | 30992.7715 | 6.7432
15380 | 32109.8047 | 6.7821
15381 | 32744.332 | 6.8074
15382 | 33103.7539 | 6.864
15383 | 34349.4062 | 7.0443
15384 | 33838.375 | 7.0367
15385 | 34139.0391 | 6.8653
15386 | 34227.0391 | 6.813
15387 | 33923.7734 | 6.5786
15388 | 34229.9336 | 6.4905
15389 | 33835.1328 | 6.5223
15390 | 33510.0039 | 6.6966
15391 | 32543.9629 | 6.6464
15392 | 30830.8652 | 6.6832
15393 | 31780.0352 | 6.7579
15394 | 29981.3066 | 6.9435
15395 | 29915.3066 | 6.9618
15396 | 29747.9277 | 6.5261
15397 | 30049.4434 | 6.1737
15398 | 30007.9277 | 6.0024
15399 | 30096.1797 | 5.8812
15400 | 29256.2734 | 5.9243
15401 | 28490.5996 | 5.3534
15402 | 27734.4414 | 5.2204
15403 | 26307.2285 | 4.8591
15404 | 23897.7188 | 4.5203
15405 | 21811.6133 | 4.3105
15406 | 20135.3906 | 3.8592
15407 | 18747.5781 | 3.699
15408 | 17639.6289 | 3.1334
15409 | 17084.25 | 2.8852
15410 | 16028.8711 | 2.8834
15411 | 15670.9648 | 3.1099
15412 | 15425.4492 | 3.1178
15413 | 15246.5742 | 3.0238
15414 | 14982.7344 | 2.7382
15415 | 14765.8906 | 2.6715
15416 | 14682.4688 | 2.5892
15417 | 14299.8477 | 2.6259
15418 | 14225.5508 | 2.5689
15419 | 14487.0889 | 2.6544
15420 | 15669.9111 | 2.8966
15421 | 17347.6289 | 3.1797
15422 | 20936.2539 | 3.4933
15423 | 23494.7715 | 4.5026
15424 | 25330.543 | 5.0897
15425 | 28707.4727 | 5.6466
15426 | 30347.5586 | 6.664
15427 | 31934.793 | 7.2283
15428 | 32754.0781 | 7.4843
15429 | 31775.7617 | 7.5876
15430 | 32230.0566 | 7.5364
15431 | 33902.0273 | 7.5622
15432 | 33204.8555 | 7.4373
15433 | 32075.668 | 7.3573
15434 | 31968.793 | 7.3235
15435 | 31889.0234 | 7.2629
15436 | 34086.7852 | 7.196
15437 | 33372.8594 | 7.0019
15438 | 33002.9727 | 6.9239
15439 | 33433.8672 | 6.9073
15440 | 31824.6562 | 6.9065
15441 | 30858.2461 | 6.9427
15442 | 29488.8965 | 7.1772
15443 | 29062.252 | 7.0965
15444 | 28949.3574 | 6.7884
15445 | 29241.7461 | 6.6625
15446 | 28362.5996 | 6.4069
15447 | 28720.4629 | 6.2685
15448 | 27891.8203 | 6.2131
15449 | 27874.5566 | 5.8531
15450 | 26752.125 | 5.5749
15451 | 25788.5645 | 5.1879
15452 | 23984.7305 | 4.8452
15453 | 21411.9609 | 4.5085
15454 | 19615.7578 | 3.9571
15455 | 18204.1562 | 3.5258
15456 | 17149.1016 | 3.0576
15457 | 16355.0811 | 2.7621
15458 | 15770.0918 | 2.7611
15459 | 15241.7012 | 3.0399
15460 | 14875.6797 | 3.0189
15461 | 14214.5312 | 3.0571
15462 | 14073.4609 | 3.0772
15463 | 14090.9307 | 2.8569
15464 | 13996.1406 | 2.7843
15465 | 13999.6875 | 2.7808
15466 | 14249.0664 | 2.7333
15467 | 14162.6992 | 2.8861
15468 | 15027.6162 | 3.1279
15469 | 16278.5859 | 3.5424
15470 | 20132.5156 | 3.9073
15471 | 22483.3594 | 4.6915
15472 | 24604.3848 | 5.2943
15473 | 25797.207 | 5.799
15474 | 28103.4297 | 6.757
15475 | 28293.5879 | 7.3166
15476 | 29584.8945 | 7.4907
15477 | 29609.5371 | 7.5813
15478 | 29959.2852 | 7.7721
15479 | 30220.5703 | 7.6982
15480 | 29873.6758 | 7.6522
15481 | 29899.2852 | 7.5948
15482 | 29093.2637 | 7.4718
15483 | 26690.6289 | 7.4805
15484 | 27433.4082 | 7.143
15485 | 27932.6934 | 6.9114
15486 | 26851.6406 | 6.9168
15487 | 26663.4082 | 6.9215
15488 | 26631.7559 | 6.8065
15489 | 26593.2715 | 7.0057
15490 | 26690.375 | 7.0076
15491 | 26876.1445 | 6.93
15492 | 27042.2832 | 6.619
15493 | 27379.5234 | 6.2539
15494 | 27138.0293 | 5.8413
15495 | 26759.0195 | 5.3937
15496 | 26235.7344 | 5.1167
15497 | 25172.0391 | 4.8919
15498 | 23977.9961 | 4.6137
15499 | 22867.4258 | 4.2497
15500 | 20990.3281 | 3.9058
15501 | 18900.1992 | 3.6009
15502 | 17558.1562 | 3.496
15503 | 16500.9434 | 3.051
15504 | 15454.3945 | 2.8689
15505 | 14762.7422 | 2.7925
15506 | 14148.374 | 2.7212
15507 | 13630.7637 | 3.0256
15508 | 13760.8789 | 2.9864
15509 | 13903.5 | 2.8938
15510 | 13789.4062 | 2.9574
15511 | 13708.4355 | 2.9459
15512 | 13734.0781 | 2.8976
15513 | 13103.1602 | 2.9399
15514 | 13975.4355 | 2.7029
15515 | 13932.3105 | 2.6965
15516 | 14460.0996 | 2.626
15517 | 14839.3633 | 2.932
15518 | 16323.9551 | 3.0274
15519 | 17826.2715 | 3.4181
15520 | 18503.5566 | 3.8841
15521 | 19524.2422 | 4.2218
15522 | 21158.7812 | 4.5728
15523 | 22410.1172 | 5.1277
15524 | 23680.3945 | 5.3555
15525 | 24176.1758 | 5.5903
15526 | 24316.248 | 5.7006
15527 | 24269.4375 | 5.6375
15528 | 23897.7422 | 5.644
15529 | 24260.1641 | 5.6495
15530 | 23561.2578 | 5.4454
15531 | 23069.5078 | 5.2182
15532 | 22566.8555 | 5.3812
15533 | 22055.5918 | 5.2895
15534 | 22192.4453 | 4.8121
15535 | 21916.1504 | 4.6003
15536 | 21897.8652 | 4.5916
15537 | 21975.9492 | 4.857
15538 | 22242.8984 | 5.2774
15539 | 21278.7188 | 5.5313
15540 | 21861.8672 | 5.3251
15541 | 22812.3184 | 4.9738
15542 | 22804.918 | 4.8679
15543 | 22468.4141 | 4.8668
15544 | 22055.6133 | 4.6381
15545 | 21472.9707 | 4.3125
15546 | 19112.2422 | 4.2066
15547 | 17185.2383 | 3.975
15548 | 16291.7012 | 3.7249
15549 | 15561.29 | 3.6565
15550 | 15125.7734 | 3.4906
15551 | 14403.71 | 3.311
15552 | 13549.8047 | 3.1291
15553 | 12809.877 | 3.054
15554 | 12322.6777 | 3.0388
15555 | 11802.7715 | 3.3105
15556 | 11259.9395 | 3.2922
15557 | 11219.1504 | 2.9333
15558 | 11195.5293 | 2.8378
15559 | 10657.7695 | 2.7461
15560 | 10334.0645 | 2.7213
15561 | 10257.7676 | 2.8774
15562 | 10263.5996 | 2.8316
15563 | 10274.8008 | 2.8687
15564 | 10615.2754 | 2.7989
15565 | 10965.9277 | 2.6832
15566 | 12145.8984 | 2.6968
15567 | 12861.4541 | 3.0048
15568 | 13166.1719 | 2.7978
15569 | 13785.4355 | 2.8569
15570 | 15043.7529 | 2.9792
15571 | 15902.3633 | 3.3307
15572 | 17152.7012 | 3.5652
15573 | 17808.1777 | 3.9372
15574 | 19136.8086 | 4.0165
15575 | 19991.3691 | 3.9407
15576 | 20333.9473 | 4.1325
15577 | 20300.5391 | 4.2386
15578 | 21271.707 | 4.245
15579 | 21896.3281 | 4.2711
15580 | 21300.0859 | 4.432
15581 | 21339.8438 | 4.2455
15582 | 21403.4219 | 4.1702
15583 | 20989.6875 | 4.1114
15584 | 20708.3066 | 4.1322
15585 | 20860.0742 | 4.3032
15586 | 20845.8242 | 4.7735
15587 | 20453.1816 | 5.031
15588 | 19570.125 | 4.9385
15589 | 19081.0938 | 4.728
15590 | 18553.0723 | 4.531
15591 | 17969.0508 | 4.486
15592 | 17725.0293 | 4.4568
15593 | 17318.25 | 4.1451
15594 | 17027.3555 | 3.9264
15595 | 16644.0918 | 3.7499
15596 | 16172.8281 | 3.9084
15597 | 15413.6367 | 3.5922
15598 | 15013.1309 | 3.3412
15599 | 14407.4785 | 3.0095
15600 | 13618.0566 | 2.7585
15601 | 12987.2988 | 2.8818
15602 | 12471.9414 | 2.898
15603 | 12211.1836 | 3.1496
15604 | 11721.1074 | 3.1169
15605 | 11691.7383 | 3.0533
15606 | 11712.8145 | 2.9558
15607 | 11761.5801 | 2.7048
15608 | 11602.8438 | 2.7106
15609 | 11349.9707 | 2.8696
15610 | 11697.0742 | 2.9468
15611 | 11758.7285 | 2.9785
15612 | 12695.5723 | 2.9864
15613 | 14393.0371 | 3.2178
15614 | 18765.1055 | 3.6196
15615 | 20967.5898 | 4.615
15616 | 22780.2988 | 5.2045
15617 | 23827.0996 | 5.6978
15618 | 27225.0625 | 6.5092
15619 | 28442.2305 | 7.5035
15620 | 30317.5801 | 7.8171
15621 | 30933.0039 | 7.8191
15622 | 30800.4961 | 7.9297
15623 | 30123.4648 | 7.8399
15624 | 30578.2461 | 7.8806
15625 | 31527.4355 | 7.7824
15626 | 32168.4688 | 7.7746
15627 | 32028.1934 | 7.6053
15628 | 31940.3086 | 7.4172
15629 | 31420.9082 | 7.3036
15630 | 30124.5918 | 7.206
15631 | 29224.6641 | 7.1598
15632 | 28256.3672 | 7.1848
15633 | 29020.0215 | 7.2008
15634 | 26775.6816 | 7.2954
15635 | 26663.8203 | 7.09
15636 | 27110.8594 | 6.7349
15637 | 27307.3145 | 6.3855
15638 | 27384.8809 | 6.2581
15639 | 27534.2305 | 6.2394
15640 | 27165.6602 | 6.1568
15641 | 26977.7773 | 5.6919
15642 | 26197.3652 | 5.5005
15643 | 24961.668 | 5.223
15644 | 23113.3086 | 4.983
15645 | 20708.4434 | 4.6015
15646 | 18925.3477 | 4.1388
15647 | 18047.0527 | 4.0031
15648 | 16731.6074 | 3.5916
15649 | 15992.5762 | 3.071
15650 | 15432.3438 | 3.0353
15651 | 15157.8379 | 3.3469
15652 | 14712.5527 | 3.1683
15653 | 14162.7842 | 3.0647
15654 | 14012.4375 | 2.9757
15655 | 14003.9629 | 2.9446
15656 | 13906.4453 | 2.9729
15657 | 13575.5527 | 2.9207
15658 | 13529.0449 | 2.8666
15659 | 13599.1836 | 3.0618
15660 | 14834.627 | 3.2849
15661 | 15821.0156 | 3.3715
15662 | 18899.3262 | 3.7359
15663 | 21438.3477 | 4.5713
15664 | 22976.0469 | 5.1691
15665 | 25195.9219 | 5.7468
15666 | 27062.6504 | 6.2679
15667 | 29452.6641 | 7.1642
15668 | 30760.5918 | 7.4712
15669 | 32059.1836 | 7.4583
15670 | 33586.4883 | 7.6558
15671 | 32870.0977 | 7.635
15672 | 33709.2695 | 7.5853
15673 | 32185.2988 | 7.5521
15674 | 33471.8672 | 7.4626
15675 | 32617.4785 | 7.2865
15676 | 32721.0879 | 6.9324
15677 | 31799.8984 | 6.7911
15678 | 31306.1504 | 6.8258
15679 | 30532.707 | 6.758
15680 | 30738.6133 | 6.8898
15681 | 29793.8125 | 7.0073
15682 | 28361.7266 | 7.221
15683 | 28150.4629 | 7.0422
15684 | 28797.6309 | 6.6247
15685 | 28290.7363 | 6.3693
15686 | 28034.209 | 6.2333
15687 | 27631.5684 | 6.2426
15688 | 27298.3047 | 5.9514
15689 | 27127.9141 | 5.4487
15690 | 26096.0078 | 5.2789
15691 | 25135.3008 | 5.0322
15692 | 23018.3203 | 4.7757
15693 | 20936.834 | 4.4214
15694 | 18885.9688 | 4.2419
15695 | 17791.6738 | 3.9976
15696 | 16498.5977 | 3.5632
15697 | 15667.543 | 2.7737
15698 | 15185.291 | 2.7452
15699 | 14829.7227 | 3.0302
15700 | 14399.543 | 3.0067
15701 | 14122.0703 | 3.0006
15702 | 13939.1758 | 2.9282
15703 | 13954.417 | 3.171
15704 | 14010.2363 | 3.2155
15705 | 13822.8359 | 3.0002
15706 | 13581.2051 | 2.8975
15707 | 13870.583 | 3.0574
15708 | 15339.9844 | 3.1178
15709 | 16423.1973 | 3.4325
15710 | 19437 | 3.7585
15711 | 21084.2109 | 4.7081
15712 | 22999.7617 | 5.5657
15713 | 25905.4805 | 5.9039
15714 | 27782.6934 | 6.3445
15715 | 29120.3906 | 6.9847
15716 | 29343.791 | 7.2291
15717 | 29460.5273 | 7.3403
15718 | 28885.7676 | 7.5858
15719 | 29433.4219 | 7.5592
15720 | 29922.959 | 7.4438
15721 | 29085.3281 | 7.3207
15722 | 29714.4336 | 7.2814
15723 | 28274.4512 | 7.1662
15724 | 31028.582 | 7.037
15725 | 29390.8105 | 7.0206
15726 | 28941.7695 | 6.8867
15727 | 28608.875 | 6.774
15728 | 27811.5898 | 6.9104
15729 | 27418.1875 | 6.9586
15730 | 27019.3867 | 7.2654
15731 | 27261.293 | 7.1108
15732 | 27566.0723 | 6.8722
15733 | 28386.7148 | 6.5346
15734 | 27971.3145 | 6.4709
15735 | 28077.2207 | 6.3261
15736 | 27129.2715 | 6.0873
15737 | 26933.4707 | 5.7323
15738 | 25918.9551 | 5.5229
15739 | 24610.1543 | 5.2004
15740 | 22873.541 | 4.9296
15741 | 20686.5586 | 4.6016
15742 | 19268.9785 | 4.2355
15743 | 18719.1875 | 4.0384
15744 | 17248.3867 | 3.5349
15745 | 16289.6797 | 2.9816
15746 | 15830.7119 | 2.981
15747 | 15876.1348 | 3.3136
15748 | 16162.1348 | 3.2536
15749 | 16160.6387 | 3.1668
15750 | 15802.6387 | 3.053
15751 | 15869.7441 | 3.2037
15752 | 15740.9219 | 3.2259
15753 | 15634.0488 | 3.2498
15754 | 15454.8066 | 3.2271
15755 | 15684.5527 | 3.2939
15756 | 16960.9863 | 3.1984
15757 | 18039.5566 | 3.5539
15758 | 21379.6133 | 3.8841
15759 | 23310.8242 | 4.943
15760 | 25334.9336 | 5.6246
15761 | 28042.2109 | 6.2114
15762 | 29675.9277 | 6.655
15763 | 30707.3496 | 7.4463
15764 | 32793.8477 | 7.729
15765 | 33473.3828 | 7.8515
15766 | 33993.1523 | 7.994
15767 | 34248.7852 | 8.0111
15768 | 33388.9414 | 8.014
15769 | 34622.0156 | 7.8492
15770 | 33888.7852 | 7.7717
15771 | 33484.7188 | 7.5064
15772 | 34329.2891 | 7.3008
15773 | 35534.0312 | 7.3115
15774 | 35329.7461 | 7.2035
15775 | 33969.5 | 7.3054
15776 | 33583.3828 | 7.2248
15777 | 32857.8477 | 7.3703
15778 | 30947.8555 | 7.5885
15779 | 30610.0859 | 7.4475
15780 | 30553.3496 | 7.169
15781 | 30497.5801 | 6.8133
15782 | 30881.9922 | 6.684
15783 | 31098.3828 | 6.6196
15784 | 30320.8008 | 6.3843
15785 | 30034.043 | 6.3584
15786 | 28659.8633 | 6.0647
15787 | 28161.1992 | 5.4715
15788 | 25920.7227 | 5.1054
15789 | 23194.5508 | 4.6738
15790 | 21337.2227 | 4.3558
15791 | 20461.0645 | 4.032
15792 | 19392.3789 | 3.5333
15793 | 18854.4531 | 3.1988
15794 | 18105.4414 | 3.2327
15795 | 17938.7695 | 3.513
15796 | 17474.2402 | 3.4797
15797 | 17000.0625 | 3.3948
15798 | 16549.6719 | 3.2924
15799 | 16715.9258 | 3.2702
15800 | 16601.5859 | 3.2683
15801 | 16584.0898 | 3.0708
15802 | 16660.8496 | 2.9798
15803 | 16925.9766 | 3.1025
15804 | 18402.6836 | 3.4815
15805 | 19643.1367 | 3.5987
15806 | 23234.5508 | 3.8677
15807 | 25122.8184 | 4.7605
15808 | 27760.4414 | 5.5877
15809 | 30244.4531 | 6.1335
15810 | 31549.7598 | 6.8592
15811 | 32711.3184 | 7.3347
15812 | 32677.3203 | 7.6916
15813 | 32739.2266 | 7.9448
15814 | 33181.9609 | 7.7216
15815 | 34089.7969 | 7.7323
15816 | 33495.7539 | 7.8718
15817 | 32898.457 | 7.9625
15818 | 32454.6445 | 7.8646
15819 | 31245.3926 | 7.742
15820 | 29761.3066 | 7.3598
15821 | 28067.084 | 7.0514
15822 | 27036.2812 | 6.9048
15823 | 26846.2812 | 6.9425
15824 | 26168.6074 | 7.0165
15825 | 26475.6406 | 7.0469
15826 | 26522.0098 | 7.2483
15827 | 26537.8926 | 7.2359
15828 | 26766.5137 | 6.8472
15829 | 27001.5469 | 6.5528
15830 | 27215.5234 | 6.1857
15831 | 27846.3242 | 5.5256
15832 | 27806.4629 | 5.3861
15833 | 27323.6602 | 4.9559
15834 | 26794.1445 | 4.7973
15835 | 25870.1016 | 4.4279
15836 | 23334.9609 | 4.1875
15837 | 21512.4863 | 3.8112
15838 | 19767.6426 | 3.7417
15839 | 19164.8848 | 3.315
15840 | 17883.6738 | 3.0762
15841 | 17057.2617 | 3.0577
15842 | 16259.9971 | 3.0504
15843 | 14526.3223 | 3.3716
15844 | 13677.2695 | 3.2721
15845 | 13336.0059 | 3.0025
15846 | 13039.3848 | 2.8379
15847 | 12815.7109 | 2.7784
15848 | 12867.4121 | 2.7555
15849 | 12840.1504 | 2.7558
15850 | 12980.9082 | 2.7267
15851 | 13055.8984 | 2.81
15852 | 13608.3086 | 2.8831
15853 | 14119.9629 | 3.005
15854 | 15491.0371 | 3.1327
15855 | 16234.8281 | 3.3998
15856 | 16960.3652 | 3.8512
15857 | 17213.123 | 4.0352
15858 | 19081.2305 | 4.3677
15859 | 20268.0547 | 4.825
15860 | 21799.7285 | 4.9134
15861 | 22655.3086 | 5.169
15862 | 22560.668 | 5.2449
15863 | 22270.4141 | 5.2912
15864 | 22152.3926 | 5.2684
15865 | 22657.8047 | 5.3503
15866 | 23031.2559 | 5.1672
15867 | 22963.1406 | 5.1573
15868 | 22591.1719 | 5.2254
15869 | 21823.875 | 5.1742
15870 | 21464.9492 | 5.1232
15871 | 21497.4453 | 4.9017
15872 | 21238.5703 | 5.0632
15873 | 21144.1602 | 5.1906
15874 | 21596.4883 | 5.3703
15875 | 21668.9922 | 5.3181
15876 | 21564.8555 | 5.1522
15877 | 22189.2656 | 4.8876
15878 | 22240.8984 | 4.7402
15879 | 22175.6348 | 4.8547
15880 | 21684.625 | 4.7482
15881 | 21039.5918 | 4.1877
15882 | 19296.6328 | 4.0179
15883 | 17662.4082 | 3.8878
15884 | 16301.8398 | 3.7249
15885 | 15734.6914 | 3.6368
15886 | 15225.7734 | 3.4292
15887 | 14513.8682 | 3.1879
15888 | 13464.793 | 3.1577
15889 | 12923.4121 | 3.07
15890 | 12362.8145 | 3.0244
15891 | 12272.0566 | 3.337
15892 | 12070.0566 | 3.3548
15893 | 11929.1836 | 3.213
15894 | 11588.4473 | 3.103
15895 | 11562.1094 | 3.0443
15896 | 11330.0859 | 2.8227
15897 | 11245.0762 | 2.6701
15898 | 11367.0762 | 2.6087
15899 | 10991.9258 | 2.8568
15900 | 11223.0762 | 2.6114
15901 | 11390.1797 | 2.8169
15902 | 12284.4961 | 2.9516
15903 | 12582.3809 | 3.0473
15904 | 12792.0127 | 2.8384
15905 | 13411.666 | 2.7968
15906 | 14790.375 | 3.0352
15907 | 15691.4053 | 3.3075
15908 | 16694.7969 | 3.4559
15909 | 17802.293 | 3.7739
15910 | 19080.1992 | 3.9841
15911 | 19961.1055 | 4.1281
15912 | 20708.4434 | 4.1609
15913 | 20856.9492 | 4.4224
15914 | 21486.4238 | 4.6608
15915 | 21561.5586 | 4.6618
15916 | 21496.875 | 4.6139
15917 | 20750.9707 | 4.4273
15918 | 20599.8008 | 4.4451
15919 | 20720.6973 | 4.345
15920 | 20852.1074 | 4.4065
15921 | 20834.1074 | 4.4446
15922 | 20796.0977 | 4.8076
15923 | 20815.2031 | 4.9614
15924 | 19920.0312 | 4.74
15925 | 19528.125 | 4.5603
15926 | 19190.4941 | 4.4534
15927 | 18936.9785 | 4.3863
15928 | 18813.8516 | 4.2397
15929 | 18309.0723 | 4.0267
15930 | 18161.5566 | 3.6979
15931 | 17386.25 | 3.6249
15932 | 16999.7441 | 3.7215
15933 | 16060.1855 | 3.522
15934 | 15586.417 | 3.0886
15935 | 14736.2578 | 2.8715
15936 | 14095.5947 | 2.6179
15937 | 13202.1934 | 2.5756
15938 | 12473.6875 | 2.5851
15939 | 12272.9512 | 2.9271
15940 | 12428.4688 | 2.9138
15941 | 12799.2266 | 2.8183
15942 | 12617.6367 | 2.7738
15943 | 12178.0137 | 2.7653
15944 | 11871.2344 | 2.7126
15945 | 12254.6133 | 2.7507
15946 | 12911.6445 | 2.6437
15947 | 12008.4766 | 2.6714
15948 | 13512.3086 | 3.1348
15949 | 15669.4277 | 3.2281
15950 | 20786.6973 | 3.5236
15951 | 23472.7109 | 4.5124
15952 | 25788.4707 | 5.0431
15953 | 28231.7266 | 5.6939
15954 | 28862.2539 | 6.4025
15955 | 30106.8223 | 7.2099
15956 | 33150.4922 | 7.3879
15957 | 32892.7188 | 7.6255
15958 | 33176.8594 | 7.7223
15959 | 34790.3203 | 7.5693
15960 | 33894.6484 | 7.5993
15961 | 34924.5977 | 7.7289
15962 | 35141.9766 | 7.6987
15963 | 35467.2188 | 7.2701
15964 | 34209.2891 | 7.0301
15965 | 32948.7188 | 7.1198
15966 | 32503.2031 | 7.1506
15967 | 32141.6875 | 7.1917
15968 | 31398.5195 | 7.0363
15969 | 32011.918 | 7.0381
15970 | 29908.9375 | 7.2581
15971 | 29861.3066 | 7.0889
15972 | 30268.2012 | 6.6049
15973 | 30325.4434 | 6.2058
15974 | 30256.2012 | 6.2409
15975 | 29669.8125 | 5.9852
15976 | 28784.1152 | 5.8205
15977 | 28359.3574 | 5.2058
15978 | 27557.9355 | 5.0526
15979 | 26599.8711 | 4.9751
15980 | 24561.9004 | 4.7745
15981 | 22094.7617 | 4.4378
15982 | 20653.5703 | 4.2353
15983 | 19349.6211 | 3.7497
15984 | 18160.9141 | 3.1388
15985 | 17207.2598 | 2.7609
15986 | 16249.7227 | 2.7678
15987 | 15956.7549 | 3.0257
15988 | 15775.123 | 2.9989
15989 | 15299.333 | 3.0119
15990 | 15286.25 | 2.9907
15991 | 15211.3555 | 3.2384
15992 | 14993.8896 | 3.181
15993 | 14912.8789 | 3.1752
15994 | 15037.1533 | 3.1063
15995 | 15199.7754 | 3.1218
15996 | 16245.7012 | 3.1323
15997 | 17712.9141 | 3.4027
15998 | 21505.3613 | 3.8289
15999 | 23827.9727 | 4.6955
16000 | 26171.7344 | 5.526
16001 | 28575.3789 | 5.9297
16002 | 29835.0547 | 6.4847
16003 | 32467.3398 | 7.0385
16004 | 34003.1523 | 7.2129
16005 | 33658.9023 | 7.4056
16006 | 33379.6367 | 7.6298
16007 | 33203.0586 | 7.5735
16008 | 33546.0898 | 7.4815
16009 | 33998.2461 | 7.4906
16010 | 34688.7656 | 7.3931
16011 | 33730.1523 | 7.3195
16012 | 32807.9102 | 6.8935
16013 | 33065.9961 | 6.8863
16014 | 34215.4258 | 6.908
16015 | 32548.4688 | 6.9342
16016 | 29957.3066 | 6.9401
16017 | 29904.9375 | 6.9823
16018 | 29125.6543 | 7.249
16019 | 29080.6426 | 7.1621
16020 | 28872.7578 | 6.6914
16021 | 28862.3691 | 6.2765
16022 | 28917.127 | 6.0687
16023 | 28850.1152 | 6.0284
16024 | 28480.4844 | 5.7928
16025 | 28373.9785 | 5.6074
16026 | 27802.9453 | 5.1747
16027 | 26731.3867 | 4.9528
16028 | 24239.9219 | 4.722
16029 | 22243.0352 | 4.3848
16030 | 20376.2129 | 4.0237
16031 | 19426.0117 | 3.5891
16032 | 18542.4512 | 3.0373
16033 | 17512.5254 | 2.7529
16034 | 16837.3984 | 2.8315
16035 | 16306.1562 | 3.0928
16036 | 15797.124 | 3.0623
16037 | 15501.7451 | 2.9913
16038 | 15123.6074 | 2.899
16039 | 15148.5977 | 2.8934
16040 | 15327.6592 | 2.8113
16041 | 15347.1533 | 2.835
16042 | 15301.7754 | 2.774
16043 | 15165.1104 | 2.8452
16044 | 16291.2695 | 3.0351
16045 | 17536.2812 | 3.4354
16046 | 21397.9805 | 3.7845
16047 | 23360.9609 | 4.6724
16048 | 25783.2832 | 5.5279
16049 | 27990.5996 | 5.7562
16050 | 30357.0957 | 6.5716
16051 | 32084.6758 | 7.155
16052 | 33079.2266 | 7.276
16053 | 32841.9844 | 7.2973
16054 | 34065.1523 | 7.5916
16055 | 34467.3125 | 7.5227
16056 | 33420.375 | 7.5259
16057 | 32109.4355 | 7.3928
16058 | 33090.1094 | 7.0807
16059 | 32881.0898 | 6.8109
16060 | 32758.2891 | 6.6565
16061 | 30873.5508 | 6.5787
16062 | 31327.7617 | 6.6979
16063 | 31346.834 | 6.797
16064 | 29236.918 | 6.8609
16065 | 28222.3477 | 7.2101
16066 | 27311.293 | 7.3535
16067 | 27401.7988 | 7.1139
16068 | 28422.2324 | 6.6727
16069 | 28470.7363 | 6.1577
16070 | 29382.2734 | 6.1648
16071 | 29308.918 | 5.9998
16072 | 28657.6094 | 5.7033
16073 | 28208.7148 | 5.4133
16074 | 27458.166 | 5.3014
16075 | 26403.6172 | 4.965
16076 | 24126.1094 | 4.7584
16077 | 22026.0234 | 4.3411
16078 | 20434.1699 | 4.0017
16079 | 19424.4941 | 3.5778
16080 | 17786.5469 | 3.1741
16081 | 17170.1133 | 3.0971
16082 | 17204.1797 | 2.9201
16083 | 17363.209 | 3.1686
16084 | 16919.0742 | 3.0334
16085 | 16528.1562 | 2.9268
16086 | 16743.7148 | 2.8753
16087 | 16684.3867 | 2.9102
16088 | 16460.207 | 2.951
16089 | 16341.5859 | 2.9221
16090 | 16298.0918 | 2.8357
16091 | 16507.082 | 2.8523
16092 | 17272.7539 | 3.0632
16093 | 18564.8398 | 3.3423
16094 | 21748.625 | 3.7382
16095 | 23959.4883 | 4.7812
16096 | 27207.6602 | 5.5686
16097 | 30630.0859 | 5.9565
16098 | 32946.0977 | 6.7397
16099 | 33904.9023 | 7.3711
16100 | 35839.7461 | 7.5096
16101 | 35187.6094 | 7.5012
16102 | 34685.5664 | 7.6295
16103 | 34409.8789 | 7.5982
16104 | 33878.2383 | 7.5393
16105 | 33583.0391 | 7.5396
16106 | 33545.3281 | 7.4881
16107 | 31433.5293 | 7.497
16108 | 31379.8027 | 7.1338
16109 | 31169.834 | 6.975
16110 | 31083.3203 | 6.913
16111 | 30291.1602 | 7.012
16112 | 32271.3184 | 7.0468
16113 | 30324.959 | 7.06
16114 | 29880.3164 | 7.1958
16115 | 28805.2852 | 6.7911
16116 | 29297.916 | 6.4395
16117 | 28913.3164 | 6.3507
16118 | 29367.7734 | 6.1608
16119 | 28886.2754 | 5.9648
16120 | 28340.3477 | 5.8374
16121 | 27877.3145 | 5.6226
16122 | 27517.293 | 5.3782
16123 | 26969.4082 | 4.974
16124 | 24153.375 | 4.5931
16125 | 21752.625 | 4.2148
16126 | 19973.5273 | 3.9011
16127 | 18887.2109 | 3.6003
16128 | 17920.5469 | 3.2421
16129 | 18387.3242 | 2.8963
16130 | 16377.1445 | 2.831
16131 | 15879.124 | 3.1813
16132 | 15344.5977 | 3.1647
16133 | 14872.7119 | 3.0732
16134 | 14685.2188 | 2.9476
16135 | 14791.3848 | 2.971
16136 | 14816.9941 | 2.9273
16137 | 14539.8691 | 2.9289
16138 | 14385.8467 | 2.9322
16139 | 14556.2363 | 3.0836
16140 | 15595.8066 | 3.1841
16141 | 17190.3867 | 3.3923
16142 | 20788.9277 | 3.695
16143 | 22387.8359 | 4.7225
16144 | 25168.543 | 5.522
16145 | 28520.7363 | 5.9038
16146 | 30371.0742 | 6.4473
16147 | 30900.1074 | 6.9747
16148 | 32506.332 | 7.2912
16149 | 31476.5195 | 7.3783
16150 | 32507.2031 | 7.5104
16151 | 33386.4883 | 7.6322
16152 | 33022.1211 | 7.704
16153 | 33711.8203 | 7.6207
16154 | 32213.8477 | 7.5387
16155 | 32072.2656 | 7.3773
16156 | 32692.6777 | 7.1026
16157 | 31503.9922 | 6.911
16158 | 30911.8535 | 6.6247
16159 | 30462.1074 | 6.6227
16160 | 29966.3184 | 6.6432
16161 | 30057.0742 | 6.6609
16162 | 28997.5156 | 6.7785
16163 | 29248.3906 | 6.6077
16164 | 28534.8516 | 6.1978
16165 | 28115.3359 | 6.0038
16166 | 27927.7031 | 5.5256
16167 | 27413.4297 | 5.1366
16168 | 26714.7656 | 5.0265
16169 | 25950.3535 | 4.6254
16170 | 24813.8066 | 4.4584
16171 | 23543.9512 | 4.1474
16172 | 21543.2461 | 3.8052
16173 | 19594.0117 | 3.5702
16174 | 18135.5566 | 3.4479
16175 | 17523.5352 | 3.2021
16176 | 16345.4707 | 2.9658
16177 | 16130.9434 | 2.8257
16178 | 15233.5645 | 2.6242
16179 | 14112.9238 | 2.9349
16180 | 13809.6387 | 3.0009
16181 | 13471.6367 | 2.995
16182 | 13422.2793 | 2.9221
16183 | 13180.5605 | 2.9502
16184 | 13536.084 | 2.8871
16185 | 13272.1309 | 2.8786
16186 | 12775.5566 | 2.8552
16187 | 12998.374 | 2.952
16188 | 13499.4355 | 2.991
16189 | 13889.0664 | 2.9426
16190 | 14960.8789 | 2.9022
16191 | 15790.6689 | 3.3489
16192 | 16734.3438 | 3.569
16193 | 17620.7773 | 3.7784
16194 | 19863.0312 | 4.0724
16195 | 20820.4551 | 4.4522
16196 | 22419.3516 | 4.5857
16197 | 22912.4668 | 4.6445
16198 | 23008.0664 | 4.727
16199 | 22199.498 | 4.9242
16200 | 21703.4023 | 5.0511
16201 | 21318.8438 | 4.8815
16202 | 21344.0039 | 4.8539
16203 | 21002.5918 | 4.8205
16204 | 20512.5488 | 4.9582
16205 | 20366.6211 | 4.8018
16206 | 19909.0859 | 4.7379
16207 | 19856.8008 | 4.7723
16208 | 19745.4102 | 4.8257
16209 | 20458.9883 | 5.0575
16210 | 20846.0977 | 5.3097
16211 | 21266.4648 | 5.3368
16212 | 21704.2559 | 5.27
16213 | 22227.2656 | 5.09
16214 | 22459.1504 | 4.8242
16215 | 22278.2773 | 4.6724
16216 | 21758.623 | 4.4839
16217 | 21284.9707 | 4.2397
16218 | 19589.8945 | 4.0927
16219 | 18318.127 | 3.7384
16220 | 17385.1992 | 3.8041
16221 | 16319.4893 | 3.5803
16222 | 15852.208 | 3.458
16223 | 15326.2793 | 3.2445
16224 | 14571.4785 | 2.8267
16225 | 14086.7207 | 2.7323
16226 | 14702.374 | 2.856
16227 | 13302.0566 | 3.2422
16228 | 12692.0996 | 3.1717
16229 | 12416.4258 | 3.0994
16230 | 12274.4258 | 2.9964
16231 | 12054.584 | 2.9802
16232 | 11855.1406 | 2.7136
16233 | 11840.4531 | 2.5525
16234 | 12074.3594 | 2.4969
16235 | 12044.0859 | 2.5181
16236 | 12418.8867 | 2.4969
16237 | 12142.6133 | 2.5273
16238 | 12788.8867 | 2.7545
16239 | 13082.0127 | 3.002
16240 | 13790.8359 | 2.8566
16241 | 14524.4473 | 2.7928
16242 | 15716.1758 | 2.9606
16243 | 16720.2285 | 3.2703
16244 | 17755.0391 | 3.7082
16245 | 18709.8926 | 3.688
16246 | 20104.2656 | 3.8597
16247 | 21573.3711 | 4.0032
16248 | 22506.9824 | 4.1127
16249 | 22793.5723 | 4.2814
16250 | 23496.1719 | 4.4468
16251 | 23676.7188 | 4.5413
16252 | 23715.4785 | 4.406
16253 | 23351.332 | 4.2062
16254 | 23324.6875 | 4.0738
16255 | 23151.9531 | 4.11
16256 | 23014.5742 | 4.0924
16257 | 22776.666 | 4.4656
16258 | 22617.793 | 4.7534
16259 | 22301.1504 | 4.9426
16260 | 20839.4336 | 4.7001
16261 | 20170.1699 | 4.3843
16262 | 19923.3672 | 4.2594
16263 | 19477.873 | 4.2066
16264 | 19333.7285 | 4.0305
16265 | 18800.7793 | 4.0239
16266 | 18224.873 | 3.8419
16267 | 17456.0234 | 3.6379
16268 | 17046.3359 | 3.5434
16269 | 16414.207 | 3.4393
16270 | 15803.1758 | 3.0869
16271 | 15079.5 | 2.7904
16272 | 14304.7207 | 2.5742
16273 | 13677.9189 | 2.551
16274 | 13488.1934 | 2.5837
16275 | 13670.9941 | 2.9218
16276 | 12354.4258 | 2.8432
16277 | 12301.1816 | 2.7599
16278 | 12368.1211 | 2.6782
16279 | 12215.1172 | 2.6625
16280 | 12179.4883 | 2.6531
16281 | 12215.3711 | 2.6943
16282 | 12439.876 | 2.6347
16283 | 12767.7607 | 2.8187
16284 | 14306.8574 | 2.8909
16285 | 16189.7021 | 3.0948
16286 | 21135.3164 | 3.5188
16287 | 23655.9727 | 4.4591
16288 | 26409.8711 | 5.2825
16289 | 27805.5664 | 5.9179
16290 | 29526.5273 | 6.5947
16291 | 31319.3926 | 7.4803
16292 | 31639.2773 | 7.6909
16293 | 31906.1719 | 7.6725
16294 | 32247.6348 | 7.6143
16295 | 33147.1406 | 7.7567
16296 | 33507.9102 | 7.7442
16297 | 32957.8672 | 7.7133
16298 | 32356.3828 | 7.7128
16299 | 30517.75 | 7.5202
16300 | 30393.2012 | 7.2869
16301 | 30843.2227 | 7.3266
16302 | 30967.4863 | 7.136
16303 | 31594.0352 | 7.2361
16304 | 30885.1172 | 7.2493
16305 | 30105.0957 | 7.3522
16306 | 28080.3262 | 7.4136
16307 | 28036.2109 | 7.1106
16308 | 27750.3047 | 6.6971
16309 | 28195.2207 | 6.429
16310 | 28987.8848 | 6.0918
16311 | 29187.3926 | 6.0514
16312 | 28114.2363 | 5.8599
16313 | 28399.8691 | 5.5687
16314 | 27581.6543 | 5.4189
16315 | 27095.1562 | 5.1275
16316 | 24575.373 | 4.87
16317 | 23190.7246 | 4.4072
16318 | 21589.6172 | 4.0694
16319 | 19806.6152 | 3.8058
16320 | 18672.9062 | 3.3414
16321 | 18077.0508 | 2.7659
16322 | 17458.0625 | 2.9066
16323 | 16988.957 | 3.1905
16324 | 16770.0391 | 3.1117
16325 | 16284.1338 | 3.1001
16326 | 15952.293 | 3.0388
16327 | 15872.4375 | 3.1446
16328 | 15837.1973 | 3.137
16329 | 15721.1533 | 3.1787
16330 | 15558.2793 | 3.1271
16331 | 15832.6699 | 3.1845
16332 | 16673.6074 | 3.2552
16333 | 17890.9141 | 3.271
16334 | 20998.5801 | 3.7243
16335 | 22828.668 | 4.503
16336 | 26683.8711 | 5.1625
16337 | 29964.5703 | 5.9458
16338 | 31130.498 | 6.5767
16339 | 32191.6875 | 7.2395
16340 | 32906.6055 | 7.4661
16341 | 31844.2891 | 7.4196
16342 | 31717.8672 | 7.4699
16343 | 31870.5078 | 7.3937
16344 | 33120.1211 | 7.2762
16345 | 32809.3438 | 7.1662
16346 | 33292.375 | 7.4524
16347 | 30859.3184 | 7.4018
16348 | 30858.2441 | 7.0337
16349 | 29941.7578 | 7.1777
16350 | 31174.1504 | 7.2563
16351 | 31487.7617 | 7.1301
16352 | 30963.877 | 7.1162
16353 | 29754.4336 | 7.3768
16354 | 28590.4844 | 7.3702
16355 | 28247.7266 | 7.1804
16356 | 28158.0938 | 6.5756
16357 | 27889.4512 | 6.2925
16358 | 28924.9883 | 6.2205
16359 | 28366.2305 | 6.0213
16360 | 28805.8848 | 5.8376
16361 | 29585.2852 | 5.4781
16362 | 28807.8633 | 5.3476
16363 | 27497.9355 | 5.1589
16364 | 25900.2188 | 4.8712
16365 | 23779.0996 | 4.4552
16366 | 21507.4746 | 4.1402
16367 | 20168.5391 | 3.9404
16368 | 18646.3359 | 3.4083
16369 | 18059.3047 | 2.7094
16370 | 17072.6621 | 2.6797
16371 | 16803.2812 | 3.1476
16372 | 16841.0078 | 3.0174
16373 | 15963.7656 | 2.744
16374 | 15723.6074 | 2.7111
16375 | 15693.7441 | 2.9582
16376 | 15577.7656 | 2.9336
16377 | 15618.8281 | 2.9347
16378 | 15401.29 | 2.8847
16379 | 15578.7861 | 3.1431
16380 | 16729.1016 | 3.0787
16381 | 18219.6934 | 3.2305
16382 | 21417.4766 | 3.4679
16383 | 23063.4453 | 4.3763
16384 | 26206.2383 | 4.9981
16385 | 28220.8516 | 5.7343
16386 | 30746.3594 | 6.2655
16387 | 31259.6445 | 6.8243
16388 | 33269.1094 | 6.8935
16389 | 32319.457 | 6.883
16390 | 32979.7305 | 7.0999
16391 | 32820.6055 | 7.1988
16392 | 32981.9844 | 7.0775
16393 | 32345.2031 | 6.9401
16394 | 32594.4668 | 6.868
16395 | 31914.9297 | 6.7576
16396 | 32061.2129 | 6.5645
16397 | 30635.9297 | 6.5873
16398 | 30145.7168 | 6.6486
16399 | 29701.5078 | 6.6665
16400 | 28854.2734 | 6.8246
16401 | 27947.6094 | 6.9328
16402 | 27226.0293 | 7.1271
16403 | 27257.4297 | 6.9088
16404 | 27393.5449 | 6.5779
16405 | 27845.4512 | 6.2902
16406 | 28364.6211 | 6.1928
16407 | 28291.082 | 6.1161
16408 | 27918.2109 | 6.0016
16409 | 28101.2207 | 5.5625
16410 | 27434.418 | 5.3047
16411 | 26789.7773 | 5.1051
16412 | 24300.248 | 4.8404
16413 | 21901.6348 | 4.4724
16414 | 20475.5703 | 4.1491
16415 | 19245.6211 | 3.8571
16416 | 17799.8105 | 3.5539
16417 | 17210.8926 | 2.8257
16418 | 16775.2383 | 2.665
16419 | 16399.5352 | 2.8961
16420 | 16030.7559 | 2.8198
16421 | 15784.7773 | 2.9638
16422 | 15312.7559 | 2.8876
16423 | 15305.2695 | 2.7447
16424 | 15292.417 | 2.744
16425 | 15230.8789 | 2.7775
16426 | 14978.374 | 2.7596
16427 | 15237.6582 | 3.0362
16428 | 16269.8379 | 3.161
16429 | 17733.832 | 3.1158
16430 | 20961.2031 | 3.5519
16431 | 22559.9102 | 4.2979
16432 | 25077.1855 | 5.0451
16433 | 27730.2109 | 5.6995
16434 | 27935.957 | 6.2102
16435 | 30512.0918 | 6.7997
16436 | 31113.0781 | 6.8821
16437 | 30421.4258 | 7.0276
16438 | 30344.0039 | 7.1828
16439 | 29862.5059 | 7.093
16440 | 30447.0547 | 7.146
16441 | 31889.6992 | 7.0013
16442 | 31512.3203 | 6.7809
16443 | 29457.1582 | 6.7973
16444 | 31033.8438 | 6.575
16445 | 29895.6953 | 6.5617
16446 | 28665.1914 | 6.5507
16447 | 29423.043 | 6.5973
16448 | 28954.2734 | 6.6327
16449 | 28880 | 6.8422
16450 | 27778.9883 | 7.0305
16451 | 27191.2715 | 6.9033
16452 | 27370.9258 | 6.5442
16453 | 27665.6836 | 6.4041
16454 | 28008.3262 | 6.0509
16455 | 28154.2109 | 6.0628
16456 | 27498.5566 | 5.947
16457 | 27668.9473 | 5.8086
16458 | 27329.293 | 5.5384
16459 | 26606.0078 | 5.1064
16460 | 24021.625 | 4.7764
16461 | 21579.2227 | 4.3747
16462 | 19816.2637 | 4.1756
16463 | 18759.0957 | 4.0515
16464 | 17539.2617 | 3.7069
16465 | 16957.6074 | 2.9327
16466 | 16119.9766 | 2.6452
16467 | 15771.123 | 2.8542
16468 | 15313.9766 | 2.7905
16469 | 14781.1738 | 2.6857
16470 | 14652.5977 | 2.68
16471 | 14567.0381 | 2.7296
16472 | 15083.4062 | 2.7044
16473 | 15225.9111 | 2.8096
16474 | 14650.8574 | 2.7397
16475 | 15384.6484 | 2.6747
16476 | 16623.7227 | 3.1081
16477 | 17966.1562 | 3.2094
16478 | 21057.2031 | 3.4904
16479 | 22822.2969 | 4.3283
16480 | 25256.5645 | 5.1906
16481 | 27554.6719 | 5.6777
16482 | 29462.5488 | 6.3326
16483 | 29886.4316 | 6.9425
16484 | 31988.793 | 7.0157
16485 | 33220.7422 | 7.145
16486 | 33234.7422 | 7.2322
16487 | 33347.1094 | 7.2328
16488 | 33294.7422 | 7.3614
16489 | 31801.918 | 7.2682
16490 | 31534.5391 | 7.2778
16491 | 30700.2227 | 7.0532
16492 | 30200.8555 | 6.8722
16493 | 27725.9043 | 6.7263
16494 | 26846.2812 | 6.5747
16495 | 26654.5352 | 6.4276
16496 | 26891.9141 | 6.5257
16497 | 26658.0293 | 6.3705
16498 | 26545.9531 | 6.6288
16499 | 26497.6934 | 6.6233
16500 | 25631.0039 | 6.1197
16501 | 25062.6855 | 6.0357
16502 | 26008.3477 | 5.7825
16503 | 26304.8828 | 5.0806
16504 | 25708.2168 | 4.7689
16505 | 25283.4395 | 4.5241
16506 | 24516.6367 | 4.3573
16507 | 23671.1211 | 3.9025
16508 | 21519.6133 | 3.6165
16509 | 19359.6211 | 3.3554
16510 | 17819.6719 | 3.2983
16511 | 16794.9863 | 3.1733
16512 | 15475.4277 | 2.7673
16513 | 14780.4902 | 2.5957
16514 | 14340.2578 | 2.4795
16515 | 13931.4062 | 2.6982
16516 | 13277.7529 | 2.6096
16517 | 12874.2148 | 2.4851
16518 | 12706.6055 | 2.4374
16519 | 12462.1934 | 2.5053
16520 | 12142.6133 | 2.5418
16521 | 12015.1172 | 2.8484
16522 | 12328.3594 | 2.7402
16523 | 12483.1172 | 2.6865
16524 | 12925.5293 | 2.4106
16525 | 13262.1719 | 2.5355
16526 | 14193.709 | 2.9321
16527 | 14856.5117 | 3.1316
16528 | 15537.7959 | 3.2839
16529 | 16554.4609 | 3.6434
16530 | 18697.4629 | 4.1414
16531 | 19780.1367 | 4.3761
16532 | 21224.2852 | 4.5172
16533 | 21348.6562 | 4.7346
16534 | 21446.9375 | 4.8395
16535 | 21179.3379 | 4.9999
16536 | 21139.4023 | 5.0206
16537 | 21040.3926 | 4.8752
16538 | 21160.6973 | 4.8988
16539 | 20851.5391 | 4.9755
16540 | 20643.3184 | 4.9624
16541 | 20545.9395 | 4.8593
16542 | 20340.4219 | 4.5778
16543 | 20270.1914 | 4.343
16544 | 20235.6855 | 4.3398
16545 | 20154.3066 | 4.7214
16546 | 20335.1816 | 5.0649
16547 | 20472.3066 | 5.2337
16548 | 20772.9707 | 4.9911
16549 | 20727.6855 | 4.8463
16550 | 21530.3496 | 4.6231
16551 | 21687.3809 | 4.5922
16552 | 21306.8555 | 4.4548
16553 | 20573.9375 | 4.1672
16554 | 18901.832 | 3.8867
16555 | 17282.7754 | 3.789
16556 | 16201.1953 | 3.5407
16557 | 15548.6699 | 3.3566
16558 | 15079.8906 | 3.3338
16559 | 14486.5117 | 3.1426
16560 | 13681.2041 | 3.0456
16561 | 12929.5293 | 2.9621
16562 | 12376.3828 | 2.846
16563 | 12023.2559 | 3.023
16564 | 11823.0459 | 2.9579
16565 | 11473.7812 | 2.8492
16566 | 11217.3711 | 2.4585
16567 | 10796.3828 | 2.5756
16568 | 10556.5918 | 2.4813
16569 | 10419.1484 | 2.4707
16570 | 10638.2754 | 2.3969
16571 | 10750.4121 | 2.4047
16572 | 11180.9375 | 2.4115
16573 | 11391.6953 | 2.6741
16574 | 12036.2227 | 2.7272
16575 | 12081.7168 | 2.8074
16576 | 12632.5195 | 3.1109
16577 | 13196.1504 | 2.995
16578 | 14639.0156 | 3.2225
16579 | 15509.4492 | 3.3113
16580 | 16707.1973 | 3.6156
16581 | 17574.5352 | 3.8184
16582 | 18708.748 | 3.9324
16583 | 19521.2109 | 4.0494
16584 | 19772.7891 | 4.1751
16585 | 20128.5801 | 4.4487
16586 | 20341 | 4.5307
16587 | 20162.3672 | 4.6319
16588 | 20275.834 | 4.6434
16589 | 19820.9785 | 4.7235
16590 | 19708.3789 | 4.45
16591 | 19563.1797 | 4.2678
16592 | 19348.6094 | 4.3453
16593 | 19120.2637 | 4.6206
16594 | 19284.9062 | 4.7908
16595 | 19507.8965 | 4.8327
16596 | 18683.9688 | 4.7827
16597 | 17697.5352 | 4.579
16598 | 18093.4199 | 4.3788
16599 | 18339.3047 | 4.3147
16600 | 18187.6719 | 3.9363
16601 | 17654.6406 | 3.7476
16602 | 17170.7559 | 3.7827
16603 | 16727.334 | 3.6653
16604 | 16303.7012 | 3.5285
16605 | 15434.1426 | 3.4662
16606 | 15035.0176 | 3.2729
16607 | 14242.8359 | 3.0393
16608 | 13705.5508 | 2.9143
16609 | 13291.9199 | 2.8622
16610 | 12524.1709 | 2.5793
16611 | 12363.666 | 2.6954
16612 | 12039.4121 | 2.6597
16613 | 11467.0254 | 2.5604
16614 | 11382.4248 | 2.4698
16615 | 11497.9492 | 2.5851
16616 | 11517.9492 | 2.7882
16617 | 11519.1895 | 2.812
16618 | 11896.4766 | 2.7914
16619 | 11997.0977 | 2.8561
16620 | 13126.3086 | 2.9631
16621 | 14972.0234 | 3.0207
16622 | 18745.6953 | 3.3757
16623 | 22903.2891 | 4.2911
16624 | 25628.5859 | 4.7917
16625 | 26837.9258 | 5.5032
16626 | 27768.8633 | 6.0271
16627 | 28446.4004 | 6.8664
16628 | 30382.2559 | 7.2107
16629 | 29930.2324 | 7.1329
16630 | 31067.2754 | 7.274
16631 | 30704.7109 | 7.3894
16632 | 29877.7715 | 7.2976
16633 | 29376.3066 | 7.3585
16634 | 30072.875 | 7.3139
16635 | 29036.3574 | 7.3015
16636 | 31020.5176 | 7.0802
16637 | 29377.2109 | 6.9416
16638 | 28773.6641 | 6.818
16639 | 29612.6523 | 6.7748
16640 | 29676.916 | 6.9501
16641 | 28052.3477 | 7.1208
16642 | 26216.2383 | 7.1571
16643 | 26519.5039 | 6.9381
16644 | 26131.8711 | 6.5739
16645 | 26117.2285 | 6.3236
16646 | 26922.418 | 6.1137
16647 | 27239.1562 | 5.9475
16648 | 26933.041 | 5.6805
16649 | 26937.7559 | 5.383
16650 | 26334.7441 | 5.2949
16651 | 24892.9102 | 5.1043
16652 | 22664.918 | 4.8185
16653 | 20559.4336 | 4.59
16654 | 19056.4727 | 4.2542
16655 | 17922.5449 | 3.7478
16656 | 16852.2285 | 3.1871
16657 | 15715.4277 | 2.8701
16658 | 15093.1738 | 2.8246
16659 | 14705.8398 | 3.0163
16660 | 14400.0273 | 2.9854
16661 | 13890.9004 | 2.9061
16662 | 13941.9336 | 2.8483
16663 | 13738.5508 | 2.9445
16664 | 13987.793 | 2.9609
16665 | 13921.1816 | 2.9676
16666 | 14292.0996 | 2.8809
16667 | 14427.8682 | 3.0822
16668 | 15123.0059 | 3.1739
16669 | 16579.0801 | 3.2452
16670 | 19845.1484 | 3.7455
16671 | 21467.3594 | 4.3991
16672 | 23180.0664 | 5.0895
16673 | 25822.2188 | 6.0194
16674 | 28572.5059 | 6.7636
16675 | 29869.4434 | 7.3665
16676 | 31084.1504 | 7.2633
16677 | 29850.5703 | 7.3554
16678 | 31397.3926 | 7.4197
16679 | 35878.2734 | 7.319
16680 | 35521.375 | 7.397
16681 | 33902.8047 | 7.3745
16682 | 33973.4805 | 7.3519
16683 | 32422.7305 | 7.1028
16684 | 32064.6777 | 6.8563
16685 | 30963.4355 | 6.7978
16686 | 30405.3711 | 6.7819
16687 | 31092.0352 | 6.7571
16688 | 31487.918 | 6.8167
16689 | 30560.2461 | 7.1431
16690 | 27219.1992 | 7.4452
16691 | 26632.7656 | 7.1536
16692 | 26019.3867 | 6.6873
16693 | 26431.8711 | 6.3677
16694 | 28767.0117 | 6.2299
16695 | 28512.6211 | 6.054
16696 | 27911.5898 | 5.9818
16697 | 27039.2715 | 5.5855
16698 | 26635.1562 | 5.2709
16699 | 25065.1641 | 5.0975
16700 | 24127.0039 | 4.8965
16701 | 22817.9316 | 4.6174
16702 | 20962.0742 | 4.1478
16703 | 19584.0117 | 3.8253
16704 | 18661.2109 | 3.2445
16705 | 17413.2812 | 3.0481
16706 | 15002.5762 | 2.9379
16707 | 14489.543 | 3.138
16708 | 14210.165 | 3.1191
16709 | 13678.0898 | 3.0597
16710 | 13547.5117 | 3.0257
16711 | 13549.9297 | 3.1433
16712 | 13707.5723 | 2.8754
16713 | 13523.9414 | 2.8157
16714 | 13722.9316 | 2.7614
16715 | 13816.5938 | 2.8658
16716 | 14618.543 | 2.9589
16717 | 16230.3965 | 3.2815
16718 | 20069.3477 | 3.7188
16719 | 22112.4141 | 4.3841
16720 | 24128.2461 | 5.0645
16721 | 25292.3125 | 5.9291
16722 | 27179.7988 | 6.7103
16723 | 28995.2109 | 7.1761
16724 | 30731.6016 | 7.329
16725 | 30465.1172 | 7.4435
16726 | 30450.7715 | 7.5236
16727 | 31306.4258 | 7.3984
16728 | 30496.1699 | 7.4039
16729 | 30100.4121 | 7.3718
16730 | 29609.7168 | 7.2405
16731 | 27098.1348 | 7.3151
16732 | 27371 | 7.109
16733 | 27151.8633 | 7.1018
16734 | 26987.6934 | 6.9853
16735 | 27084.9473 | 6.9386
16736 | 26632.5977 | 6.9719
16737 | 26129.7539 | 7.0475
16738 | 25593.2285 | 7.2425
16739 | 25412.8398 | 6.9004
16740 | 24942.9961 | 6.5782
16741 | 25093.8066 | 6.2568
16742 | 26284.998 | 6.1715
16743 | 26987.9141 | 6.1301
16744 | 26622.3984 | 6.0391
16745 | 26155.2285 | 5.6081
16746 | 25454.3125 | 5.3865
16747 | 24483.1426 | 5.097
16748 | 22612.8047 | 4.9576
16749 | 20448.2852 | 4.7108
16750 | 18510.7031 | 4.3052
16751 | 17437.6289 | 3.6003
16752 | 16674.4805 | 3.3149
16753 | 15914.5762 | 2.8709
16754 | 38.1426 | 2.9124
16755 | 337.5645 | 3.2193
16756 | -118.9609 | 3.2683
16757 | -395.7939 | 3.1961
16758 | -568.2676 | 3.0417
16759 | -501.3828 | 3.1156
16760 | -1417.9121 | 3.1301
16761 | -1103.1113 | 3.1797
16762 | -1640.9766 | 3.0896
16763 | -1158.4277 | 3.059
16764 | -579.6484 | 3.0575
16765 | 775.1221 | 3.4426
16766 | 4146.5156 | 3.6691
16767 | 7388.583 | 4.625
16768 | 10343.2188 | 5.3776
16769 | 12712.168 | 5.8545
16770 | 13850.7578 | 6.4673
16771 | 14638.1797 | 7.0563
16772 | 14681.5479 | 7.3326
16773 | 13612.1162 | 7.3963
16774 | 14174.1484 | 7.3562
16775 | 14215.5059 | 7.364
16776 | 13980.8428 | 7.2583
16777 | 13028.957 | 7.147
16778 | 14211.832 | 7.2041
16779 | 14111.4854 | 7.004
16780 | 16932.1719 | 6.8743
16781 | 16291.624 | 6.8473
16782 | 14473.3691 | 6.7934
16783 | 14182.6641 | 6.6525
16784 | 13690.5059 | 6.7419
16785 | 13153.1035 | 6.9422
16786 | 12320.8086 | 7.2666
16787 | 12275.1777 | 6.8922
16788 | 11095.7344 | 6.532
16789 | 11003.7344 | 6.4454
16790 | 11620.7656 | 6.1602
16791 | 11889.4092 | 6.137
16792 | 11690.7656 | 6.0155
16793 | 11189.7344 | 5.7226
16794 | 10334.8184 | 5.4533
16795 | 9481.1426 | 5.1205
16796 | 7515.0352 | 4.8444
16797 | 5190.1689 | 4.5555
16798 | 3319.8105 | 4.3181
16799 | 2001.9961 | 3.8936
16800 | 1010.6914 | 3.363
16801 | 361.6592 | 2.8453
16802 | 36.0254 | 2.7277
16803 | 134.4375 | 3.185
16804 | -810.9209 | 3.1497
16805 | -1168.9424 | 3.1175
16806 | -220.1719 | 3.0712
16807 | -1017.9004 | 2.9388
16808 | -1495.1123 | 2.8876
16809 | -1904.1953 | 2.8918
16810 | -1645.9766 | 2.8291
16811 | -1400.5127 | 2.8911
16812 | -625.9736 | 3.138
16813 | 1427.4189 | 3.4649
16814 | 3718.7783 | 3.8104
16815 | 6508.7612 | 4.5554
16816 | 8896.8359 | 5.1688
16817 | 11465.6504 | 6.011
16818 | 13277.4512 | 6.5797
16819 | 14626.5273 | 7.1713
16820 | 16877.5508 | 7.3583
16821 | 17471.8242 | 7.3187
16822 | 18037.6152 | 7.5474
16823 | 17094.2344 | 7.4554
16824 | 16446.5195 | 7.5025
16825 | 16068.4971 | 7.2976
16826 | 16210.8867 | 7.2465
16827 | 14825.3066 | 7.0119
16828 | 14498.6641 | 6.8135
16829 | 13561.4941 | 6.7779
16830 | 11765.8926 | 6.5498
16831 | 11438.0088 | 6.4584
16832 | 11290.9971 | 6.4283
16833 | 11176.7451 | 6.5862
16834 | 11389.502 | 6.9306
16835 | 10953.5967 | 6.6843
16836 | 11443.7559 | 6.5523
16837 | 11619.6387 | 6.4804
16838 | 12456.2305 | 5.7227
16839 | 14143.4131 | 5.173
16840 | 11359.8916 | 5.0806
16841 | 10407.5762 | 4.9217
16842 | 9402.8887 | 4.7084
16843 | 7948.0669 | 4.2841
16844 | 5752.0762 | 4.1312
16845 | 3560.7031 | 3.731
16846 | 2734.041 | 3.5455
16847 | 1849.2383 | 3.3241
16848 | 954.0703 | 3.1992
16849 | 294.5332 | 2.9685
16850 | -303.8574 | 2.7975
16851 | -336.3418 | 3.1556
16852 | -1192.3848 | 3.2262
16853 | -1864.1426 | 3.0994
16854 | -1343.0049 | 3.0176
16855 | -1689.5322 | 3.0137
16856 | -2436.9746 | 2.7221
16857 | -3160.9756 | 2.7104
16858 | -3146.5967 | 2.6492
16859 | -3074.3027 | 2.66
16860 | -2676.7451 | 2.7529
16861 | -2444.292 | 2.9287
16862 | -1304.5752 | 3.2456
16863 | -712.8066 | 3.3523
16864 | 549.9443 | 3.8207
16865 | 1558.8594 | 4.0166
16866 | 3184.7568 | 4.4503
16867 | 4898.3594 | 4.7255
16868 | 6127.0654 | 4.83
16869 | 6559.1289 | 4.9437
16870 | 6392.5278 | 5.1224
16871 | 6484.561 | 5.1567
16872 | 6729.1807 | 5.1608
16873 | 6792.3076 | 5.2066
16874 | 7868.6665 | 5.1519
16875 | 6589.1289 | 5.1184
16876 | 5640.0654 | 4.9879
16877 | 5685.9395 | 5.0124
16878 | 5415.9395 | 4.9387
16879 | 5162.5381 | 4.752
16880 | 5080.4238 | 4.8444
16881 | 4913.7793 | 4.9452
16882 | 5384.1909 | 5.2193
16883 | 5571.8232 | 5.4417
16884 | 5447.4336 | 5.2578
16885 | 5526.0752 | 4.9555
16886 | 5752.0752 | 4.8867
16887 | 6065.5913 | 4.7242
16888 | 6125.729 | 4.5344
16889 | 5704.3281 | 4.4217
16890 | 4064.3574 | 4.151
16891 | 2188.0195 | 3.9169
16892 | 1256.9648 | 3.9076
16893 | 633.6797 | 3.5566
16894 | 369.7969 | 3.4304
16895 | -666.5215 | 3.0346
16896 | -1047.9004 | 2.9249
16897 | -1144.5215 | 2.9407
16898 | -1341.0479 | 2.7881
16899 | -1608.1758 | 2.9338
16900 | -1908.0371 | 2.8895
16901 | -2216.3125 | 2.7763
16902 | -2594.334 | 2.6746
16903 | 10731.2607 | 2.6829
16904 | 13065.6992 | 2.6254
16905 | 12839.5625 | 2.5895
16906 | 12563.1719 | 2.5104
16907 | 12236.5293 | 2.4975
16908 | 12438.3398 | 2.4508
16909 | 12814.4355 | 2.1572
16910 | 13417.4688 | 2.0476
16911 | 15377.3232 | 2.5338
16912 | 16558.4609 | 2.4699
16913 | 17261.9961 | 2.472
16914 | 18568.5664 | 2.557
16915 | 19574.0215 | 2.793
16916 | 20629.7285 | 3.185
16917 | 21509.1523 | 3.3012
16918 | 22815.9219 | 3.6007
16919 | 23646.2891 | 3.6871
16920 | 24351.0293 | 3.6924
16921 | 24636.418 | 3.755
16922 | 24343.3008 | 3.9354
16923 | 22333.1934 | 3.9824
16924 | 21658.1816 | 3.6979
16925 | 21752.0859 | 3.8141
16926 | 21803.5391 | 3.7954
16927 | 21477.2988 | 3.7366
16928 | 21648.3809 | 3.7644
16929 | 21870.1172 | 3.9333
16930 | 22068.5293 | 4.2357
16931 | 22139.709 | 4.8921
16932 | 21005.8242 | 4.81
16933 | 20327.2109 | 4.6325
16934 | 20603.6016 | 4.4177
16935 | 20804.6133 | 4.2807
16936 | 20729.2324 | 3.8921
16937 | 20201.5801 | 3.7853
16938 | 20000.5703 | 3.9371
16939 | 19673.9277 | 3.6386
16940 | 18869.8848 | 3.5337
16941 | 18116.0938 | 3.2837
16942 | 17462.8086 | 3.1792
16943 | 16281.8711 | 3.0715
16944 | 15955.2285 | 2.689
16945 | 15528.0811 | 2.8474
16946 | 15176.3125 | 2.806
16947 | 14849.6689 | 3.087
16948 | 14749.1641 | 3.0377
16949 | 15000.4277 | 2.8021
16950 | 15000.4277 | 2.5647
16951 | 14347.1426 | 2.6055
16952 | 14073.752 | 2.6357
16953 | 14030.0996 | 2.6397
16954 | 14222.1113 | 2.5999
16955 | 14749.1641 | 2.8433
16956 | 15502.9541 | 2.7812
16957 | 17136.166 | 3.2665
16958 | 20382.2656 | 3.5224
16959 | 22466.9531 | 4.4311
16960 | 24900.6074 | 5.0158
16961 | 28141.5039 | 5.7854
16962 | 30478.2539 | 6.4028
16963 | 32412.9844 | 7.1686
16964 | 35101.5039 | 7.3825
16965 | 33769.8086 | 7.4771
16966 | 33619.0469 | 7.339
16967 | 35051.2461 | 7.3698
16968 | 35830.168 | 7.2664
16969 | 35453.2734 | 7.1374
16970 | 35126.6289 | 7.2077
16971 | 34699.4805 | 7.1891
16972 | 34523.5938 | 6.8995
16973 | 33066.2695 | 6.7439
16974 | 32668.8457 | 6.6525
16975 | 32842.3281 | 6.5928
16976 | 31960.9121 | 6.6382
16977 | 32161.7207 | 6.6747
16978 | 30327.4961 | 7.0815
16979 | 30252.1172 | 6.9602
16980 | 29724.4648 | 6.4904
16981 | 29020.9258 | 6.2946
16982 | 29247.0645 | 6.1865
16983 | 30176.7383 | 6.1814
16984 | 30076.2324 | 6.0595
16985 | 29674.2109 | 5.7912
16986 | 28568.6523 | 5.6747
16987 | 27865.1172 | 5.5193
16988 | 25704.25 | 5.2202
16989 | 23794.6484 | 4.6346
16990 | 22663.9629 | 4.1793
16991 | 17224.3535 | 3.6347
16992 | 15471.0986 | 3.494
16993 | 14725.9297 | 3.2897
16994 | 12150.3359 | 3.1992
16995 | 6981.8418 | 3.4633
16996 | 2477.2734 | 3.446
16997 | -177.2363 | 3.4192
16998 | -748.7949 | 3.2771
16999 | -740.543 | 3.0194
17000 | -666.9121 | 2.9815
17001 | -859.9219 | 3.0049
17002 | -760.291 | 3.0933
17003 | -558.1533 | 3.1748
17004 | 383.7754 | 3.3489
17005 | 1423.8271 | 3.4624
17006 | 4338.8633 | 3.7952
17007 | 6234.2954 | 4.7301
17008 | 9605.5215 | 5.2119
17009 | 11512.8184 | 5.9537
17010 | 12600.4102 | 6.815
17011 | 13907.9053 | 7.2776
17012 | 16667.0879 | 7.4752
17013 | 17414.4141 | 7.6557
17014 | 16408.0254 | 7.8021
17015 | 16017.4453 | 7.5309
17016 | 16120.3594 | 7.6137
17017 | 15147.9912 | 7.6246
17018 | 15473.1396 | 7.5364
17019 | 30584.4219 | 7.6591
17020 | 32720.6992 | 7.4562
17021 | 32995.6914 | 7.4667
17022 | 31485.9102 | 7.3302
17023 | 32061.2148 | 7.425
17024 | 31156.666 | 7.3605
17025 | 31357.6797 | 7.4694
17026 | 30352.625 | 7.5555
17027 | 30000.8555 | 7.2885
17028 | 29473.2012 | 6.9421
17029 | 28819.916 | 6.5571
17030 | 29121.4336 | 6.2395
17031 | 29850.0957 | 6.1214
17032 | 30201.8633 | 6.1618
17033 | 29548.5801 | 5.8791
17034 | 29196.8125 | 5.6126
17035 | 28166.6328 | 5.3942
17036 | 26231.9023 | 5.2654
17037 | 23568.5117 | 4.743
17038 | 21508.1484 | 4.3024
17039 | 20025.6953 | 3.403
17040 | 19020.6445 | 3.3064
17041 | 18241.7266 | 2.9731
17042 | 17437.6836 | 2.9669
17043 | 17387.4297 | 3.4124
17044 | 17513.0625 | 3.4033
17045 | 17085.9121 | 3.3093
17046 | 17337.1777 | 3.2315
17047 | 17412.5586 | 3.1999
17048 | 17035.6602 | 3.2458
17049 | 16849.0508 | 3.1462
17050 | 16771.8711 | 2.8995
17051 | 16883.5762 | 3.0153
17052 | 18267.6523 | 3.0873
17053 | 19397.5391 | 3.5002
17054 | 23091.1094 | 3.8112
17055 | 24900.2051 | 4.712
17056 | 27790.1367 | 5.3955
17057 | 29473.2031 | 5.9446
17058 | 30603.8867 | 6.4528
17059 | 31608.9414 | 7.0419
17060 | 32463.2344 | 7.2346
17061 | 34121.5742 | 7.3235
17062 | 35679.4062 | 7.3055
17063 | 36860.3438 | 7.2174
17064 | 35980.9219 | 7.1892
17065 | 34322.5859 | 6.883
17066 | 35553.7773 | 6.9614
17067 | 35704.5312 | 7.0343
17068 | 35478.3984 | 6.8216
17069 | 34900.4883 | 6.7844
17070 | 34900.4883 | 6.7242
17071 | 35327.6367 | 6.6775
17072 | 35202.0078 | 6.5437
17073 | 35101.5 | 6.6903
17074 | 32789.8789 | 7.0783
17075 | 32010.9629 | 6.954
17076 | 31885.3301 | 6.6106
17077 | 31483.3086 | 6.4889
17078 | 31056.1602 | 6.3111
17079 | 31056.1602 | 6.2231
17080 | 30804.8984 | 6.1714
17081 | 30226.9922 | 6.0827
17082 | 29272.1895 | 5.779
17083 | 28719.4102 | 5.4823
17084 | 26458.041 | 5.3069
17085 | 24397.6797 | 4.763
17086 | 23040.8574 | 4.4668
17087 | 21859.918 | 3.4094
17088 | 20628.7305 | 3.0797
17089 | 19347.2852 | 3.021
17090 | 18166.3457 | 3.1245
17091 | 17538.1895 | 3.2673
17092 | 17312.0508 | 3.2629
17093 | 17186.418 | 3.2908
17094 | 16784.3984 | 3.3119
17095 | 16608.5137 | 3.3228
17096 | 16533.1348 | 3.2646
17097 | 16206.4922 | 3.2277
17098 | 16105.9873 | 3.0787
17099 | 16206.4922 | 3.0352
17100 | 17563.3145 | 3.0752
17101 | 19070.8965 | 3.4114
17102 | 21985.5508 | 3.6765
17103 | 24146.416 | 4.7024
17104 | 27337.6621 | 5.2648
17105 | 30779.7695 | 5.8017
17106 | 31407.9297 | 6.3198
17107 | 32061.2148 | 7.4036
17108 | 32639.1211 | 8.2843
17109 | 31985.8379 | 8.2912
17110 | 33141.8477 | 8.4957
17111 | 33771.0039 | 8.6211
17112 | 32942.4375 | 8.6839
17113 | 32214.5723 | 8.3552
17114 | 31840.6777 | 8.3332
17115 | 31011.709 | 8.2154
17116 | 31187.1914 | 8.0154
17117 | 30656.541 | 7.8992
17118 | 30755.2441 | 7.8888
17119 | 30076.834 | 7.8391
17120 | 29750.1895 | 6.9413
17121 | 28995.8008 | 6.6409
17122 | 29020.9297 | 6.7977
17123 | 29020.9277 | 6.6439
17124 | 28367.6406 | 6.5028
17125 | 27513.3477 | 6.4178
17126 | 28041 | 6.1788
17127 | 29247.0664 | 6.0425
17128 | 29196.8125 | 5.9962
17129 | 28794.7891 | 5.7502
17130 | 28066.127 | 5.4954
17131 | 27638.9805 | 5.2805
17132 | 25327.3555 | 5.0938
17133 | 23040.8555 | 4.6889
17134 | 21885.0469 | 4.1397
17135 | 20276.9609 | 3.2592
17136 | 18769.3789 | 3.015
17137 | 18090.9668 | 2.866
17138 | 17588.4414 | 2.9038
17139 | 17111.0391 | 3.2903
17140 | 16633.6406 | 3.2778
17141 | 15906.9766 | 3.2592
17142 | 15661.1133 | 3.1201
17143 | 15392.9219 | 2.9105
17144 | 15501.4277 | 2.8115
17145 | 15578.332 | 2.8104
17146 | 15414.4492 | 2.7287
17147 | 15450.1738 | 2.8454
17148 | 16776.9453 | 2.8984
17149 | 17597.4629 | 3.3246
17150 | 21249.5078 | 3.4303
17151 | 23948.752 | 4.1353
17152 | 27489.0195 | 4.7866
17153 | 29953.8008 | 4.9896
17154 | 30051.1094 | 5.4654
17155 | 31106.4121 | 5.9581
17156 | 30855.1523 | 6.1853
17157 | 30754.8418 | 6.2921
17158 | 31761.502 | 6.3858
17159 | 31837.2793 | 6.3748
17160 | 30733.7188 | 6.2335
17161 | 31010.1094 | 6.2122
17162 | 30986.9805 | 5.8031
17163 | 29627.7617 | 5.6864
17164 | 29502.3281 | 5.354
17165 | 28447.6191 | 5.1733
17166 | 28371.4434 | 5.1024
17167 | 27439.7695 | 5.149
17168 | 27312.9355 | 5.1922
17169 | 26734.4297 | 5.1514
17170 | 26005.7656 | 5.4554
17171 | 25704.25 | 5.5134
17172 | 25452.9844 | 5.351
17173 | 25050.9648 | 5.3667
17174 | 25503.2383 | 5.2513
17175 | 26483.168 | 5.0868
17176 | 26332.4082 | 4.968
17177 | 25980.6406 | 4.8667
17178 | 25352.4805 | 4.6149
17179 | 24573.5664 | 4.3266
17180 | 22236.8125 | 4.2839
17181 | 20025.6953 | 3.9629
17182 | 18819.6328 | 3.5788
17183 | 18266.8516 | 3.391
17184 | 17563.3145 | 3.0399
17185 | 17060.7871 | 3.1165
17186 | 16332.124 | 2.896
17187 | 16005.4805 | 3.2287
17188 | 15904.9766 | 3.2025
17189 | 16683.8926 | 3.0427
17190 | 16432.6289 | 2.6863
17191 | 16558.2617 | 2.6819
17192 | 16533.1328 | 2.6538
17193 | 15578.332 | 2.5947
17194 | 14347.9424 | 2.5492
17195 | 14130.0059 | 2.617
17196 | 14760.7646 | 2.6203
17197 | 14877.9961 | 2.7049
17198 | 16407.5039 | 3.115
17199 | 17487.9355 | 3.1589
17200 | 19976.8418 | 3.4488
17201 | 20986.4961 | 3.8814
17202 | 22598.3828 | 4.2757
17203 | 22185.8379 | 4.5087
17204 | 23238.543 | 4.7637
17205 | 23536.0586 | 4.8493
17206 | 23886.2266 | 4.9467
17207 | 24313.1758 | 5.035
17208 | 23735.2676 | 5.0886
17209 | 23656.6914 | 5.0522
17210 | 21243.1621 | 5.1123
17211 | 20487.7695 | 5.0631
17212 | 20661.6562 | 4.9557
17213 | 21567.8027 | 4.6507
17214 | 21495.0234 | 4.7023
17215 | 21326.5391 | 4.6544
17216 | 21147.4531 | 4.8423
17217 | 19485.5176 | 5.0134
17218 | 19882.3379 | 5.2307
17219 | 20582.4766 | 5.0258
17220 | 22036.0039 | 4.8272
17221 | 22236.8125 | 4.7556
17222 | 22714.2148 | 4.5693
17223 | 23568.5117 | 4.4057
17224 | 22236.8125 | 4.2278
17225 | 22035.8047 | 3.9887
17226 | 20402.5898 | 3.8697
17227 | 19724.1797 | 3.8096
17228 | 19121.1484 | 3.6536
17229 | 18694 | 3.2953
17230 | 17312.0508 | 3.1411
17231 | 15528.0801 | 2.9969
17232 | 15025.5537 | 2.8693
17233 | 14849.6699 | 2.7058
17234 | 14171.2578 | 2.8145
17235 | 14925.0479 | 2.9751
17236 | 14774.29 | 2.8719
17237 | 14648.6582 | 2.7872
17238 | 13744.1094 | 2.4682
17239 | 12387.2871 | 2.4996
17240 | 12337.0352 | 2.4651
17241 | 12462.667 | 2.4187
17242 | 13241.582 | 2.3523
17243 | 14422.5215 | 2.3708
17244 | 15226.5645 | 2.3516
17245 | 15126.0586 | 2.5877
17246 | 14182.8057 | 2.5372
17247 | 14620.2061 | 2.529
17248 | 15731.8896 | 2.6805
17249 | 16690.8926 | 2.8121
17250 | 18653.5488 | 2.9657
17251 | 19813.1582 | 3.4092
17252 | 21147.6543 | 3.4531
17253 | 22080.7305 | 3.5326
17254 | 20226.7812 | 3.734
17255 | 19923.6621 | 3.5872
17256 | 20302.1602 | 3.5641
17257 | 20704.9824 | 3.6432
17258 | 21961.4961 | 3.7014
17259 | 21608.7285 | 3.7822
17260 | 20500.5684 | 3.6822
17261 | 18964.0645 | 3.6901
17262 | 18838.6328 | 3.604
17263 | 19012.3164 | 3.1975
17264 | 19111.0234 | 3.2226
17265 | 19206.9277 | 3.2257
17266 | 18174.5469 | 3.2876
17267 | 17341.1758 | 3.2047
17268 | 17086.7148 | 3.0132
17269 | 16834.6484 | 3.0123
17270 | 17362.3027 | 3.2137
17271 | 18241.7246 | 3.0132
17272 | 18945.2637 | 3.0099
17273 | 19020.6426 | 3.0052
17274 | 18593.4922 | 3.0426
17275 | 18869.8848 | 2.9353
17276 | 19271.9062 | 2.8416
17277 | 18342.2305 | 2.8675
17278 | 16834.6484 | 2.949
17279 | 15075.8066 | 2.5773
17280 | 15050.6797 | 2.4671
17281 | 14799.416 | 2.4628
17282 | 14598.4072 | 2.4292
17283 | 14799.416 | 2.6616
17284 | 15553.207 | 2.6772
17285 | 15729.0918 | 2.5858
17286 | 15177.5127 | 2.5514
17287 | 13602.2998 | 2.7085
17288 | 13844.6152 | 2.6795
17289 | 14472.7744 | 2.4862
17290 | 15980.3555 | 2.3941
17291 | 18467.8633 | 2.3994
17292 | 21633.7812 | 2.3406
17293 | 23744.3965 | 2.5999
17294 | 25350.8262 | 2.5283
17295 | 28902.0957 | 2.7198
17296 | 30629.0156 | 2.945
17297 | 33317.5312 | 2.9608
17298 | 35553.7734 | 2.8817
17299 | 35779.9141 | 3.0211
17300 | 35076.375 | 3.182
17301 | 34900.4922 | 3.4958
17302 | 34448.2188 | 3.5038
17303 | 33970.8164 | 3.5361
17304 | 33870.3125 | 3.5795
17305 | 34046.1953 | 3.9045
17306 | 33845.1836 | 4.0428
17307 | 32568.543 | 3.9114
17308 | 30862.1484 | 3.9721
17309 | 31361.8789 | 4.0417
17310 | 31488.5098 | 3.8188
17311 | 31361.4805 | 3.7399
17312 | 29750.3945 | 3.7561
17313 | 27839.9883 | 3.9712
17314 | 27638.9805 | 4.2915
17315 | 27186.7031 | 4.2642
17316 | 26985.8945 | 4.166
17317 | 27111.3242 | 4.0829
17318 | 27613.8535 | 3.9728
17319 | 28342.5156 | 3.9194
17320 | 29046.0547 | 3.6738
17321 | 28644.0332 | 3.5422
17322 | 26684.1758 | 3.5189
17323 | 23621.6367 | 3.366
17324 | 19664.7598 | 3.3433
17325 | 17531.5977 | 3.0111
17326 | 16155.8789 | 3.0548
17327 | 12311.8086 | 2.8463
17328 | 5821.1851 | 2.8926
17329 | 2878.9277 | 2.6358
17330 | 453.333 | 2.5217
17331 | -847.5332 | 2.7815
17332 | -580.8906 | 2.8003
17333 | -562.6367 | 2.7076
17334 | -338.752 | 2.6525
17335 | -27.5605 | 2.6395
17336 | -1447.5225 | 2.5721
17337 | -1465.8916 | 2.5212
17338 | -21.6885 | 2.4006
17339 | 909.9121 | 2.4691
17340 | 4776.9287 | 2.4574
17341 | 6742.3711 | 2.7625
17342 | 9252.9307 | 2.9392
17343 | 11285.8926 | 3.2973
17344 | 13064.6094 | 3.4537
17345 | 15169.6973 | 3.4065
17346 | 17065.5508 | 3.4697
17347 | 17403.4355 | 3.9059
17348 | 18165.4785 | 3.9311
17349 | 17807.7109 | 4.2317
17350 | 16870.2871 | 4.3012
17351 | 16373.2549 | 4.3344
17352 | 17552.7832 | 4.4392
17353 | 16092.1182 | 4.3746
17354 | 16571.8242 | 4.429
17355 | 15245.2021 | 4.513
17356 | 14025.748 | 4.4321
17357 | 13971.3691 | 4.4004
17358 | 13553.7471 | 4.2657
17359 | 14606.1797 | 4.2626
17360 | 11840.7549 | 4.2773
17361 | 11227.6816 | 4.6368
17362 | 9898.4268 | 4.8824
17363 | 10630.9746 | 4.9566
17364 | 16054.8711 | 4.8388
17365 | 15831.3535 | 4.7178
17366 | 11992.5049 | 4.4391
17367 | 11877.4297 | 4.4601
17368 | 11831.1777 | 4.3709
17369 | 12006.1895 | 3.8569
17370 | 9278.9121 | 3.8841
17371 | 6918.9199 | 3.5028
17372 | 4884.0547 | 3.4407
17373 | 3602.3574 | 3.1432
17374 | 2475.5566 | 2.9973
17375 | 1567.9971 | 2.8509
17376 | 1172.8721 | 2.834
17377 | 1172.0195 | 2.8073
17378 | 396.3428 | 2.7855
17379 | 219.333 | 3.0411
17380 | 560.6191 | 2.9413
17381 | -50.1836 | 2.6907
17382 | -586.6152 | 2.6048
17383 | -525.2363 | 2.8275
17384 | -137.2148 | 2.8332
17385 | 708.207 | 2.7919
17386 | 1643.6309 | 2.7186
17387 | 2790.8203 | 2.7867
17388 | 6290.7607 | 2.6375
17389 | 8204.6162 | 2.9205
17390 | 9936.1963 | 3.1734
17391 | 12028.6719 | 3.555
17392 | 12961.9785 | 3.7949
17393 | 13629.126 | 3.8005
17394 | 15131.834 | 4.1336
17395 | 15226.3379 | 4.6566
17396 | 15493.7178 | 4.8284
17397 | 16859.1836 | 5.0292
17398 | 16284.6562 | 5.0691
17399 | 16147.8984 | 5.0989
17400 | 16265.5293 | 5.0497
17401 | 14733.3379 | 5.0481
17402 | 14463.6748 | 5.0785
17403 | 14892.6328 | 4.9691
17404 | 13792.9053 | 4.9036
17405 | 14273.0332 | 4.8856
17406 | 15546.7285 | 4.7189
17407 | 15987.0029 | 4.707
17408 | 15661.2344 | 4.7383
17409 | 14270.1582 | 4.8672
17410 | 13817.0107 | 5.2343
17411 | 11548.7656 | 5.3253
17412 | 11540.7656 | 5.0645
17413 | 11498.7656 | 4.7566
17414 | 10926.9756 | 4.7284
17415 | 11101.3652 | 4.67
17416 | 10983.7344 | 4.6148
17417 | 10532.8389 | 4.2553
17418 | 8208.457 | 4.137
17419 | 6108.0972 | 3.945
17420 | 4416.127 | 3.641
17421 | 3591.4629 | 3.4921
17422 | 1888.3652 | 3.1237
17423 | 1456.3457 | 3.0005
17424 | 711.9336 | 2.862
17425 | 709.0801 | 2.6274
17426 | 530.8281 | 2.568
17427 | -197.4355 | 2.8041
17428 | -419.0684 | 2.6924
17429 | -228.4053 | 2.8499
17430 | -773.9941 | 2.8187
17431 | -1183.8906 | 2.9213
17432 | -1083.418 | 2.8896
17433 | -781.1426 | 2.8694
17434 | 2.1426 | 2.8067
17435 | 1063.8701 | 2.9662
17436 | 5509.1919 | 2.9473
17437 | 7084.0239 | 2.9854
17438 | 9076.4785 | 3.109
17439 | 11052.5859 | 3.4045
17440 | 12534.8105 | 3.7736
17441 | 13099.2207 | 4.1888
17442 | 13974.8945 | 4.3817
17443 | 15036.2021 | 4.7488
17444 | 15764.6143 | 5.0029
17445 | 16620.6875 | 5.2233
17446 | 17937.9844 | 5.4361
17447 | 16926.0566 | 5.5029
17448 | 18679.1016 | 5.4744
17449 | 17107.3613 | 5.4691
17450 | 17482.3203 | 5.4552
17451 | 14860.749 | 5.3363
17452 | 14198.3906 | 5.2418
17453 | 14317.1162 | 5.0649
17454 | 13161.3896 | 5.0013
17455 | 13142.957 | 4.9638
17456 | 10985.3975 | 4.9863
17457 | 11931.9766 | 5.1738
17458 | 13354.2529 | 5.5285
17459 | 11963.7988 | 5.4952
17460 | 11348.1445 | 5.2619
17461 | 9790.7959 | 4.8276
17462 | 9789.8066 | 4.7371
17463 | 10342.5859 | 4.641
17464 | 10538.5859 | 4.5621
17465 | 9865.3008 | 4.5023
17466 | 7706.8037 | 4.3826
17467 | 5598.3281 | 3.887
17468 | 3781.5996 | 3.5128
17469 | 2532.1562 | 3.2715
17470 | 1632.9863 | 3.2866
17471 | 662.5547 | 3.1363
17472 | 591.4492 | 2.7801
17473 | 9.1758 | 2.5888
17474 | -600.3633 | 2.4821
17475 | -889.3945 | 2.6874
17476 | 679.2295 | 2.6122
17477 | 4806.4268 | 2.5171
17478 | 2697.1289 | 2.4724
17479 | -1111.2578 | 2.5557
17480 | -850.6152 | 2.5429
17481 | -1480.3438 | 2.5652
17482 | -408.7539 | 2.4743
17483 | 567.9219 | 2.6176
17484 | 3895.0518 | 2.6611
17485 | 5755.6543 | 2.8755
17486 | 8049.8252 | 3.0687
17487 | 10738.4707 | 3.3213
17488 | 11927.1562 | 3.7368
17489 | 11923.6611 | 4.0719
17490 | 13137.1055 | 4.2501
17491 | 13081.4199 | 4.6811
17492 | 14494.5264 | 4.8878
17493 | 14236.085 | 5.0751
17494 | 13750.3047 | 5.0963
17495 | 13701.2842 | 5.2493
17496 | 12741.251 | 5.3385
17497 | 12783.8623 | 5.3344
17498 | 11472.5137 | 5.1754
17499 | 10770.7861 | 5.1869
17500 | 9837.3223 | 5.1709
17501 | 9782.5215 | 4.9359
17502 | 9466.7109 | 4.8682
17503 | 9276.4277 | 4.8641
17504 | 8620.0352 | 4.8759
17505 | 8441.6055 | 5.1753
17506 | 8252.7939 | 5.2485
17507 | 7383.4658 | 5.2422
17508 | 7683.0884 | 5.0693
17509 | 7604.4355 | 4.8561
17510 | 7579.5615 | 4.7545
17511 | 7634.0459 | 4.6183
17512 | 7718.436 | 4.5365
17513 | 7160.2773 | 4.4691
17514 | 5316.9268 | 4.1291
17515 | 3168.9355 | 3.7493
17516 | 1973.2393 | 3.5912
17517 | 1353.5859 | 3.4372
17518 | 153.1543 | 3.3468
17519 | -462.7539 | 3.0347
17520 | -1066.2676 | 2.9473

## Generation Profiles
Profile index | 1 | 3 | 4 | 5
Profile name | DG 1 (kW) | DG 1 (MW) | ES 1 | DG Wind
DNC, MW | 15 | 15 | 1 | 5
User reference | Example DG profile | Example DG profile | Example ES profile | Example DG Wind
Sampling rate (minutes) | 30 | 30 | 30 | 30
Unit conversion factor to MW | 0.001 | 1 | 0.001 | 1
Total export energy, MWh | 113477.5185 | 113477.5185 | 2228.865 | 17847.7095
Total import energy, MWh | 0 | 0 | 2161.7965 | 0
Minimum profile value, MW | 0 | 0 | -1 | 0
Maximum profile value, MW | 15.108 | 15.108 | 1 | 5
Sign | 1 | 1 | 1 | 1
Number of Periods | 17520 | 17520 | 17520 | 17520
Start period | 2015-10-30 | 2015-10-30 | 2015-10-30 | 2011-10-01
1 | 14702 | 14.702 | 649 | 4.968
2 | 14662 | 14.662 | -793 | 4.9255
3 | 14669 | 14.669 | 301 | 4.9785
4 | 14696 | 14.696 | 300 | 4.9575
5 | 14626 | 14.626 | 883 | 4.963
6 | 14731 | 14.731 | -288 | 4.963
7 | 14744 | 14.744 | 60 | 4.814
8 | 14689 | 14.689 | 562 | 3.75
9 | 14594 | 14.594 | 70 | 3.17
10 | 14591 | 14.591 | 933 | 2.548
11 | 14504 | 14.504 | -702 | 2.186
12 | 14623 | 14.623 | 124 | 2.6065
13 | 14817 | 14.817 | -416 | 2.713
14 | 14519 | 14.519 | 425 | 3.1115
15 | 14601 | 14.601 | 316 | 3.1225
16 | 14706 | 14.706 | 555 | 3.2285
17 | 14580 | 14.58 | 877 | 3.9255
18 | 14681 | 14.681 | 650 | 4.133
19 | 14561 | 14.561 | -830 | 4.665
20 | 14367 | 14.367 | -355 | 4.085
21 | 14532 | 14.532 | 864 | 3.92
22 | 14306 | 14.306 | 312 | 4.4785
23 | 14350 | 14.35 | -242 | 3.798
24 | 14378 | 14.378 | -640 | 4.4945
25 | 14194 | 14.194 | 877 | 4.1545
26 | 14091 | 14.091 | -520 | 4.303
27 | 14362 | 14.362 | 445 | 4.101
28 | 14430 | 14.43 | -157 | 3.303
29 | 14336 | 14.336 | -412 | 4.3245
30 | 14334 | 14.334 | 660 | 3.9735
31 | 14227 | 14.227 | -282 | 4.702
32 | 14343 | 14.343 | 7 | 4.3885
33 | 14238 | 14.238 | 877 | 2.5425
34 | 14594 | 14.594 | -640 | 0.702
35 | 14310 | 14.31 | -127 | 2.367
36 | 14435 | 14.435 | -92 | 4.1595
37 | 14393 | 14.393 | 727 | 3.5425
38 | 14287 | 14.287 | 105 | 3
39 | 14525 | 14.525 | 86 | 0.5215
40 | 14471 | 14.471 | -384 | 3.4895
41 | 14174 | 14.174 | -217 | 1.266
42 | 13851 | 13.851 | 851 | 4.867
43 | 13815 | 13.815 | -391 | 2.0745
44 | 13828 | 13.828 | 694 | 4.0215
45 | 13924 | 13.924 | -48 | 4.952
46 | 13676 | 13.676 | -970 | 4.6385
47 | 14073 | 14.073 | -48 | 4.197
48 | 14353 | 14.353 | -1000 | 4.1275
49 | 14559 | 14.559 | 108 | 3.963
50 | 14607 | 14.607 | 927 | 3.8885
51 | 14633 | 14.633 | 460 | 3.8405
52 | 14549 | 14.549 | -633 | 3.7925
53 | 14648 | 14.648 | 582 | 3.1545
54 | 14617 | 14.617 | -611 | 3.1545
55 | 14541 | 14.541 | -873 | 3.8615
56 | 14629 | 14.629 | -296 | 3.931
57 | 14604 | 14.604 | 681 | 3.7235
58 | 14573 | 14.573 | -245 | 3.3405
59 | 14596 | 14.596 | 276 | 2.9895
60 | 14608 | 14.608 | 508 | 2.968
61 | 14689 | 14.689 | -251 | 2.553
62 | 14490 | 14.49 | -350 | 1.6915
63 | 14571 | 14.571 | -624 | 1.2765
64 | 14548 | 14.548 | 10 | 0.7395
65 | 14293 | 14.293 | -82 | 0.718
66 | 14529 | 14.529 | 711 | 0.67
67 | 14352 | 14.352 | 382 | 0.4785
68 | 14505 | 14.505 | 939 | 0.186
69 | 14519 | 14.519 | 392 | 0.2075
70 | 14592 | 14.592 | -623 | 0.149
71 | 14553 | 14.553 | -486 | 0.25
72 | 14651 | 14.651 | -591 | 0.4415
73 | 14575 | 14.575 | 574 | 0.8245
74 | 14595 | 14.595 | -436 | 1.2925
75 | 14565 | 14.565 | -513 | 1.766
76 | 14475 | 14.475 | 164 | 2.5105
77 | 14567 | 14.567 | 30 | 1.734
78 | 14599 | 14.599 | 688 | 2.4735
79 | 14536 | 14.536 | -504 | 2.468
80 | 14625 | 14.625 | 251 | 2.1115
81 | 14624 | 14.624 | -406 | 1.8725
82 | 14539 | 14.539 | 398 | 2.2765
83 | 14578 | 14.578 | 428 | 2.133
84 | 14578 | 14.578 | -618 | 2.165
85 | 14657 | 14.657 | 201 | 2.0215
86 | 14800 | 14.8 | 643 | 2.1275
87 | 14719 | 14.719 | 915 | 2.649
88 | 14698 | 14.698 | -440 | 1.835
89 | 14572 | 14.572 | 259 | 1.7925
90 | 14740 | 14.74 | 679 | 2.101
91 | 14689 | 14.689 | 866 | 2.0955
92 | 14732 | 14.732 | -852 | 2.016
93 | 14104 | 14.104 | 219 | 2.218
94 | 13925 | 13.925 | 732 | 1.7925
95 | 14609 | 14.609 | -315 | 1.7605
96 | 14604 | 14.604 | -148 | 1.8565
97 | 14752 | 14.752 | 393 | 1.7605
98 | 14684 | 14.684 | -479 | 2.0905
99 | 14765 | 14.765 | 44 | 2.383
100 | 14867 | 14.867 | -836 | 1.3455
101 | 14755 | 14.755 | -662 | 1.383
102 | 14755 | 14.755 | -484 | 1.617
103 | 14757 | 14.757 | -139 | 1.4945
104 | 14817 | 14.817 | -877 | 1.75
105 | 14801 | 14.801 | -415 | 1.6385
106 | 14770 | 14.77 | -946 | 1.3615
107 | 14740 | 14.74 | -346 | 1.0745
108 | 14720 | 14.72 | -840 | 0.537
109 | 14723 | 14.723 | -893 | 0.851
110 | 14464 | 14.464 | -583 | 1.0955
111 | 14558 | 14.558 | -19 | 1.1275
112 | 14654 | 14.654 | 430 | 1.484
113 | 14655 | 14.655 | 770 | 1.6755
114 | 14553 | 14.553 | -539 | 1.5265
115 | 14628 | 14.628 | 864 | 1.351
116 | 14621 | 14.621 | -600 | 1.569
117 | 14555 | 14.555 | -356 | 1.9735
118 | 14580 | 14.58 | 21 | 2.367
119 | 14642 | 14.642 | -91 | 2.867
120 | 14639 | 14.639 | 254 | 2.42
121 | 14662 | 14.662 | -812 | 2.548
122 | 14636 | 14.636 | -864 | 2.452
123 | 14441 | 14.441 | -333 | 3.5
124 | 14311 | 14.311 | -283 | 2.713
125 | 14444 | 14.444 | 648 | 2.351
126 | 14622 | 14.622 | -510 | 2.186
127 | 14250 | 14.25 | -632 | 2.1595
128 | 14676 | 14.676 | -379 | 1.952
129 | 14639 | 14.639 | 459 | 1.553
130 | 14544 | 14.544 | 30 | 1.6385
131 | 14573 | 14.573 | 679 | 2.016
132 | 14613 | 14.613 | 643 | 1.4895
133 | 14690 | 14.69 | -75 | 0.915
134 | 14711 | 14.711 | 357 | 1
135 | 14723 | 14.723 | -323 | 1.2075
136 | 14620 | 14.62 | -959 | 1.218
137 | 14700 | 14.7 | -119 | 1.266
138 | 14712 | 14.712 | -690 | 1.3725
139 | 14891 | 14.891 | 894 | 1.2235
140 | 14430 | 14.43 | -156 | 1.5425
141 | 14097 | 14.097 | -843 | 1.537
142 | 14013 | 14.013 | -593 | 2.08
143 | 14074 | 14.074 | -466 | 1.8775
144 | 14233 | 14.233 | 666 | 1.548
145 | 13759 | 13.759 | -529 | 1.7605
146 | 14463 | 14.463 | 389 | 1.3725
147 | 14810 | 14.81 | 950 | 1.0425
148 | 14634 | 14.634 | -773 | 1.1115
149 | 14832 | 14.832 | 321 | 1.5215
150 | 14837 | 14.837 | 783 | 1.569
151 | 14743 | 14.743 | 780 | 1.4575
152 | 14633 | 14.633 | 958 | 1.569
153 | 14853 | 14.853 | 146 | 1.718
154 | 14727 | 14.727 | -216 | 1.7925
155 | 14699 | 14.699 | 438 | 1.463
156 | 14851 | 14.851 | -541 | 1.6915
157 | 14596 | 14.596 | -890 | 1.25
158 | 14757 | 14.757 | 950 | 1.33
159 | 14737 | 14.737 | 586 | 1.5055
160 | 14758 | 14.758 | -383 | 1.303
161 | 14561 | 14.561 | -239 | 1.101
162 | 14688 | 14.688 | 761 | 1.282
163 | 14752 | 14.752 | 653 | 1.2395
164 | 14751 | 14.751 | -693 | 1.6065
165 | 14454 | 14.454 | -317 | 2.1755
166 | 14660 | 14.66 | -789 | 2.4095
167 | 14788 | 14.788 | -169 | 2.25
168 | 14700 | 14.7 | 319 | 1.6115
169 | 14735 | 14.735 | 451 | 1.7605
170 | 14573 | 14.573 | -348 | 1.564
171 | 14827 | 14.827 | -138 | 1.484
172 | 14878 | 14.878 | 869 | 1.4735
173 | 14479 | 14.479 | 11 | 1.6435
174 | 14647 | 14.647 | 933 | 1.218
175 | 14647 | 14.647 | -779 | 0.867
176 | 14508 | 14.508 | 472 | 0.814
177 | 14734 | 14.734 | 777 | 0.5055
178 | 14644 | 14.644 | -712 | 0.4575
179 | 14754 | 14.754 | 64 | 0.383
180 | 14713 | 14.713 | -98 | 0.5745
181 | 14656 | 14.656 | -43 | 0.899
182 | 14631 | 14.631 | 94 | 1.234
183 | 14690 | 14.69 | -112 | 1.25
184 | 14595 | 14.595 | 873 | 1.2765
185 | 14624 | 14.624 | -732 | 1.5215
186 | 14591 | 14.591 | 409 | 1.617
187 | 13880 | 13.88 | 770 | 1.5265
188 | 14381 | 14.381 | 889 | 1.447
189 | 14795 | 14.795 | 337 | 1.2555
190 | 14629 | 14.629 | 944 | 1.133
191 | 14788 | 14.788 | -897 | 1.181
192 | 14687 | 14.687 | 157 | 1.08
193 | 14795 | 14.795 | -482 | 1.2715
194 | 14703 | 14.703 | 706 | 1.0955
195 | 14774 | 14.774 | -196 | 0.92
196 | 14548 | 14.548 | -259 | 1.08
197 | 14724 | 14.724 | 554 | 1.08
198 | 14620 | 14.62 | -603 | 0.968
199 | 14782 | 14.782 | -17 | 1.0955
200 | 14682 | 14.682 | 151 | 1.1065
201 | 14681 | 14.681 | -470 | 1.165
202 | 14768 | 14.768 | -69 | 1.2605
203 | 14515 | 14.515 | -394 | 0.963
204 | 14822 | 14.822 | 900 | 0.9415
205 | 14651 | 14.651 | -539 | 1.181
206 | 14690 | 14.69 | -420 | 1.484
207 | 14739 | 14.739 | 733 | 1.2765
208 | 14677 | 14.677 | -308 | 0.0055
209 | 14660 | 14.66 | -780 | 0
210 | 14837 | 14.837 | -662 | 0
211 | 14413 | 14.413 | 185 | 0
212 | 14612 | 14.612 | -399 | 0
213 | 14732 | 14.732 | -488 | 0
214 | 14642 | 14.642 | -960 | 0
215 | 14742 | 14.742 | 913 | 0
216 | 14636 | 14.636 | -839 | 0
217 | 14488 | 14.488 | 467 | 0
218 | 14571 | 14.571 | 889 | 0
219 | 14460 | 14.46 | -2 | 0
220 | 14666 | 14.666 | -98 | 0
221 | 14718 | 14.718 | -822 | 0
222 | 14577 | 14.577 | 465 | 0
223 | 14627 | 14.627 | -352 | 0
224 | 14571 | 14.571 | -770 | 0
225 | 14702 | 14.702 | -307 | 0
226 | 14555 | 14.555 | 915 | 0
227 | 14745 | 14.745 | 21 | 0
228 | 14637 | 14.637 | 819 | 0
229 | 14543 | 14.543 | -416 | 0
230 | 14645 | 14.645 | 795 | 0
231 | 14532 | 14.532 | -899 | 0
232 | 14712 | 14.712 | -273 | 0
233 | 14665 | 14.665 | 613 | 0
234 | 14078 | 14.078 | 598 | 0
235 | 14005 | 14.005 | -871 | 0
236 | 14110 | 14.11 | -359 | 0
237 | 14080 | 14.08 | 720 | 0
238 | 14227 | 14.227 | 731 | 0
239 | 13772 | 13.772 | 722 | 0
240 | 14558 | 14.558 | 896 | 0
241 | 14801 | 14.801 | -253 | 0
242 | 14589 | 14.589 | -796 | 0
243 | 14897 | 14.897 | -468 | 0
244 | 14664 | 14.664 | -530 | 0
245 | 14732 | 14.732 | -114 | 0
246 | 14751 | 14.751 | -940 | 0
247 | 14716 | 14.716 | -126 | 0
248 | 14654 | 14.654 | -365 | 0
249 | 14593 | 14.593 | 334 | 0
250 | 14628 | 14.628 | -428 | 0
251 | 14644 | 14.644 | -787 | 0
252 | 14772 | 14.772 | 737 | 0
253 | 14730 | 14.73 | 805 | 0
254 | 14674 | 14.674 | -14 | 0
255 | 14730 | 14.73 | -777 | 0
256 | 14635 | 14.635 | 762 | 0
257 | 14606 | 14.606 | -188 | 0
258 | 14819 | 14.819 | -470 | 0
259 | 14534 | 14.534 | 820 | 0
260 | 14627 | 14.627 | -833 | 0
261 | 14640 | 14.64 | -182 | 0
262 | 14739 | 14.739 | -772 | 0
263 | 14764 | 14.764 | -301 | 0
264 | 14430 | 14.43 | 11 | 0
265 | 14616 | 14.616 | -276 | 0
266 | 14678 | 14.678 | 381 | 0
267 | 14558 | 14.558 | 720 | 0
268 | 14610 | 14.61 | -929 | 0
269 | 14546 | 14.546 | 137 | 0
270 | 14557 | 14.557 | -961 | 0
271 | 14690 | 14.69 | 661 | 0
272 | 14604 | 14.604 | -418 | 0
273 | 14459 | 14.459 | -773 | 0
274 | 14753 | 14.753 | 123 | 0
275 | 14417 | 14.417 | -920 | 0
276 | 14593 | 14.593 | -21 | 0
277 | 14707 | 14.707 | 853 | 0
278 | 14655 | 14.655 | -338 | 0
279 | 14557 | 14.557 | 617 | 0
280 | 14741 | 14.741 | 734 | 0
281 | 14473 | 14.473 | 933 | 0
282 | 14032 | 14.032 | -601 | 0
283 | 13789 | 13.789 | -360 | 0
284 | 14732 | 14.732 | -644 | 0
285 | 14614 | 14.614 | 162 | 0
286 | 14603 | 14.603 | -908 | 0
287 | 14720 | 14.72 | -248 | 0
288 | 14656 | 14.656 | 701 | 0
289 | 14606 | 14.606 | -383 | 0
290 | 14673 | 14.673 | 89 | 0
291 | 14649 | 14.649 | 521 | 0
292 | 14587 | 14.587 | 627 | 0
293 | 14711 | 14.711 | 161 | 0
294 | 14692 | 14.692 | -835 | 0
295 | 14549 | 14.549 | -277 | 0
296 | 14715 | 14.715 | 965 | 0
297 | 14619 | 14.619 | 422 | 0
298 | 14585 | 14.585 | 850 | 0
299 | 14704 | 14.704 | 318 | 0
300 | 14615 | 14.615 | 174 | 0
301 | 14718 | 14.718 | 939 | 0
302 | 14589 | 14.589 | 787 | 0
303 | 14833 | 14.833 | -572 | 0
304 | 14535 | 14.535 | -635 | 0
305 | 14563 | 14.563 | 510 | 0
306 | 14752 | 14.752 | -74 | 0
307 | 14372 | 14.372 | -153 | 0
308 | 14582 | 14.582 | 836 | 0
309 | 14571 | 14.571 | 988 | 0
310 | 14638 | 14.638 | -600 | 0
311 | 14435 | 14.435 | 612 | 0
312 | 14751 | 14.751 | -70 | 0
313 | 14458 | 14.458 | -441 | 0
314 | 14394 | 14.394 | -368 | 0
315 | 14593 | 14.593 | -476 | 0
316 | 14508 | 14.508 | 303 | 0
317 | 14595 | 14.595 | 611 | 0
318 | 14527 | 14.527 | -50 | 0
319 | 14640 | 14.64 | -213 | 0
320 | 14205 | 14.205 | -986 | 0
321 | 14556 | 14.556 | -180 | 0
322 | 14618 | 14.618 | 196 | 0
323 | 14520 | 14.52 | 494 | 0
324 | 14474 | 14.474 | 153 | 0
325 | 14538 | 14.538 | -51 | 0
326 | 14590 | 14.59 | -764 | 0
327 | 14565 | 14.565 | 212 | 0
328 | 14499 | 14.499 | 845 | 0
329 | 14099 | 14.099 | 545 | 0
330 | 13827 | 13.827 | -468 | 0
331 | 14040 | 14.04 | -998 | 0
332 | 13994 | 13.994 | 618 | 0
333 | 13803 | 13.803 | 157 | 0
334 | 14001 | 14.001 | -497 | 0
335 | 14512 | 14.512 | 930 | 0
336 | 14525 | 14.525 | 801 | 0
337 | 14542 | 14.542 | 111 | 0
338 | 14707 | 14.707 | -488 | 0
339 | 14574 | 14.574 | 609 | 0
340 | 14619 | 14.619 | -300 | 0
341 | 14579 | 14.579 | -742 | 0
342 | 14399 | 14.399 | 382 | 0
343 | 14513 | 14.513 | -42 | 0
344 | 14483 | 14.483 | -862 | 0
345 | 14576 | 14.576 | 393 | 0
346 | 14491 | 14.491 | -605 | 0
347 | 14451 | 14.451 | 856 | 0
348 | 14625 | 14.625 | -272 | 0
349 | 14364 | 14.364 | 672 | 0
350 | 14421 | 14.421 | 925 | 0
351 | 14646 | 14.646 | -495 | 0
352 | 14587 | 14.587 | -139 | 0
353 | 14449 | 14.449 | 222 | 0
354 | 14507 | 14.507 | -973 | 0
355 | 14412 | 14.412 | -657 | 0
356 | 14549 | 14.549 | -625 | 0
357 | 14271 | 14.271 | -435 | 0
358 | 14580 | 14.58 | 855 | 0
359 | 14497 | 14.497 | 286 | 0
360 | 14373 | 14.373 | 88 | 0
361 | 14505 | 14.505 | -765 | 0
362 | 14434 | 14.434 | 373 | 0
363 | 14558 | 14.558 | 280 | 0
364 | 14429 | 14.429 | -788 | 0
365 | 14439 | 14.439 | -752 | 0
366 | 14317 | 14.317 | -974 | 0
367 | 14428 | 14.428 | 833 | 0
368 | 14327 | 14.327 | -875 | 0
369 | 14444 | 14.444 | -827 | 0
370 | 14235 | 14.235 | 462 | 0
371 | 14476 | 14.476 | 946 | 0
372 | 14544 | 14.544 | -365 | 0
373 | 14438 | 14.438 | -726 | 0
374 | 14443 | 14.443 | 449 | 0
375 | 14537 | 14.537 | 838 | 0
376 | 14587 | 14.587 | 166 | 0
377 | 14077 | 14.077 | -813 | 0
378 | 13669 | 13.669 | 96 | 0
379 | 14659 | 14.659 | 12 | 0
380 | 14659 | 14.659 | -487 | 0
381 | 14593 | 14.593 | -340 | 0
382 | 14672 | 14.672 | -808 | 0
383 | 14593 | 14.593 | 256 | 0
384 | 14721 | 14.721 | -406 | 0
385 | 14546 | 14.546 | 218 | 0
386 | 14654 | 14.654 | 959 | 0
387 | 14673 | 14.673 | -872 | 0
388 | 14540 | 14.54 | -179 | 0
389 | 14615 | 14.615 | 567 | 0
390 | 14743 | 14.743 | 71 | 0
391 | 14678 | 14.678 | -189 | 0
392 | 14705 | 14.705 | 413 | 0
393 | 14733 | 14.733 | -283 | 0
394 | 14548 | 14.548 | 10 | 0
395 | 14661 | 14.661 | 852 | 0
396 | 14643 | 14.643 | 436 | 0
397 | 14568 | 14.568 | 926 | 0
398 | 14587 | 14.587 | 685 | 0
399 | 14621 | 14.621 | -285 | 0
400 | 14528 | 14.528 | 37 | 0
401 | 14638 | 14.638 | 536 | 0
402 | 14560 | 14.56 | 357 | 0
403 | 14454 | 14.454 | -238 | 0
404 | 14258 | 14.258 | -521 | 0
405 | 14232 | 14.232 | 714 | 0
406 | 14479 | 14.479 | -150 | 0
407 | 14117 | 14.117 | -157 | 0
408 | 14472 | 14.472 | 99 | 0
409 | 14373 | 14.373 | 703 | 0
410 | 14107 | 14.107 | -210 | 0
411 | 14323 | 14.323 | 198 | 0
412 | 14447 | 14.447 | -719 | 0
413 | 14328 | 14.328 | 940 | 0
414 | 14232 | 14.232 | -579 | 0
415 | 14335 | 14.335 | 692 | 0
416 | 14371 | 14.371 | -234 | 0
417 | 14666 | 14.666 | -847 | 0
418 | 14536 | 14.536 | -900 | 0
419 | 14457 | 14.457 | -139 | 0
420 | 14569 | 14.569 | 693 | 0
421 | 14462 | 14.462 | -228 | 0
422 | 14603 | 14.603 | 429 | 0
423 | 14509 | 14.509 | 905 | 0
424 | 14557 | 14.557 | -950 | 0
425 | 14592 | 14.592 | 838 | 0
426 | 14689 | 14.689 | 148 | 0
427 | 14603 | 14.603 | -126 | 0
428 | 14721 | 14.721 | 73 | 0
429 | 14241 | 14.241 | -441 | 0
430 | 14069 | 14.069 | -926 | 0
431 | 14077 | 14.077 | 287 | 0
432 | 14232 | 14.232 | 309 | 0
433 | 14055 | 14.055 | -881 | 0
434 | 14293 | 14.293 | -858 | 0
435 | 14681 | 14.681 | 347 | 0
436 | 14745 | 14.745 | -908 | 0
437 | 14858 | 14.858 | -898 | 0
438 | 14815 | 14.815 | -217 | 0
439 | 14764 | 14.764 | 978 | 0
440 | 14900 | 14.9 | 648 | 0
441 | 14640 | 14.64 | -128 | 0
442 | 14794 | 14.794 | -727 | 0
443 | 14767 | 14.767 | 632 | 0
444 | 14751 | 14.751 | -533 | 0
445 | 14750 | 14.75 | 907 | 0
446 | 14741 | 14.741 | 29 | 0
447 | 14706 | 14.706 | -677 | 0
448 | 14847 | 14.847 | -162 | 0
449 | 14747 | 14.747 | -53 | 0
450 | 14760 | 14.76 | 182 | 0
451 | 14616 | 14.616 | 797 | 0
452 | 14603 | 14.603 | -647 | 0
453 | 14929 | 14.929 | 1000 | 0
454 | 14646 | 14.646 | -227 | 0
455 | 14624 | 14.624 | 251 | 0
456 | 14502 | 14.502 | -65 | 0
457 | 14452 | 14.452 | -235 | 0
458 | 14582 | 14.582 | 580 | 0
459 | 14499 | 14.499 | -890 | 1.963
460 | 14393 | 14.393 | -518 | 3.984
461 | 14460 | 14.46 | 945 | 3.6435
462 | 14446 | 14.446 | 374 | 3.399
463 | 14542 | 14.542 | -577 | 3.4255
464 | 14621 | 14.621 | -113 | 3.085
465 | 14359 | 14.359 | 220 | 2.8775
466 | 14395 | 14.395 | -583 | 2.5055
467 | 14614 | 14.614 | -771 | 2.447
468 | 14392 | 14.392 | 336 | 2.4945
469 | 14583 | 14.583 | 563 | 2.1595
470 | 14518 | 14.518 | 197 | 1.9575
471 | 14413 | 14.413 | -561 | 1.9735
472 | 14393 | 14.393 | -208 | 1.585
473 | 14681 | 14.681 | 4 | 1.6385
474 | 14476 | 14.476 | 878 | 1.915
475 | 13946 | 13.946 | -567 | 2.0215
476 | 14053 | 14.053 | -315 | 1.766
477 | 14670 | 14.67 | -690 | 1.9575
478 | 14691 | 14.691 | 366 | 2.2285
479 | 14646 | 14.646 | 242 | 1.952
480 | 14825 | 14.825 | -730 | 2.0215
481 | 14707 | 14.707 | -182 | 1.9415
482 | 14759 | 14.759 | -952 | 1.415
483 | 14771 | 14.771 | -346 | 1.3405
484 | 14564 | 14.564 | 742 | 0.968
485 | 14792 | 14.792 | 832 | 0.963
486 | 14671 | 14.671 | -461 | 0.9735
487 | 14796 | 14.796 | 209 | 1.016
488 | 14625 | 14.625 | 858 | 1.1755
489 | 14679 | 14.679 | 414 | 0.649
490 | 14682 | 14.682 | -489 | 0.6385
491 | 14569 | 14.569 | 607 | 0.516
492 | 14539 | 14.539 | 475 | 0.6225
493 | 14666 | 14.666 | -211 | 0.5105
494 | 14690 | 14.69 | -879 | 0.3245
495 | 14627 | 14.627 | 357 | 0.436
496 | 14689 | 14.689 | 63 | 0.5905
497 | 14654 | 14.654 | 655 | 1.0265
498 | 14661 | 14.661 | 875 | 1.2925
499 | 14454 | 14.454 | 871 | 1.08
500 | 14656 | 14.656 | -691 | 1.266
501 | 14510 | 14.51 | -723 | 1.819
502 | 14538 | 14.538 | 339 | 2.2925
503 | 14745 | 14.745 | 79 | 2.537
504 | 14635 | 14.635 | 544 | 2.814
505 | 14687 | 14.687 | 749 | 2.8615
506 | 14329 | 14.329 | 816 | 2.9785
507 | 14649 | 14.649 | -858 | 2.9045
508 | 14623 | 14.623 | 463 | 3.064
509 | 14555 | 14.555 | -527 | 3.0955
510 | 14602 | 14.602 | 695 | 3.085
511 | 14497 | 14.497 | 129 | 3.2765
512 | 14463 | 14.463 | -710 | 2.4415
513 | 14365 | 14.365 | 486 | 2.1115
514 | 14442 | 14.442 | -608 | 1.8455
515 | 14356 | 14.356 | -615 | 1.7445
516 | 14362 | 14.362 | 383 | 1.447
517 | 14401 | 14.401 | 632 | 1.585
518 | 14441 | 14.441 | -72 | 2.1065
519 | 14450 | 14.45 | -685 | 1.6435
520 | 14212 | 14.212 | -909 | 1.7715
521 | 14176 | 14.176 | 39 | 1.713
522 | 13571 | 13.571 | -283 | 1.782
523 | 13618 | 13.618 | 268 | 1.314
524 | 13761 | 13.761 | 204 | 1.165
525 | 13627 | 13.627 | 31 | 0.4735
526 | 13415 | 13.415 | 329 | 0.713
527 | 14082 | 14.082 | -540 | 0.6595
528 | 14297 | 14.297 | 237 | 0.7925
529 | 14291 | 14.291 | 64 | 1.016
530 | 14339 | 14.339 | -764 | 0.915
531 | 14319 | 14.319 | -31 | 0.718
532 | 14392 | 14.392 | 151 | 1.3085
533 | 14306 | 14.306 | 70 | 0.883
534 | 14423 | 14.423 | -531 | 1.351
535 | 14202 | 14.202 | -840 | 1.202
536 | 14384 | 14.384 | -70 | 1.3885
537 | 14246 | 14.246 | -315 | 1.213
538 | 14284 | 14.284 | -366 | 0.665
539 | 14262 | 14.262 | 599 | 0.713
540 | 14271 | 14.271 | -268 | 0.899
541 | 14257 | 14.257 | 141 | 1.1275
542 | 14431 | 14.431 | -870 | 1.0105
543 | 14309 | 14.309 | -447 | 1.2285
544 | 14448 | 14.448 | -722 | 0.899
545 | 14414 | 14.414 | -605 | 0.117
546 | 14297 | 14.297 | 485 | 0.117
547 | 14199 | 14.199 | -253 | 0.149
548 | 14296 | 14.296 | -131 | 0.0425
549 | 14211 | 14.211 | -600 | 0.101
550 | 14323 | 14.323 | 965 | 0.117
551 | 14064 | 14.064 | -55 | 0.101
552 | 14359 | 14.359 | -819 | 0.0955
553 | 14262 | 14.262 | 570 | 0.2395
554 | 14184 | 14.184 | -999 | 0.5215
555 | 14017 | 14.017 | 442 | 0.899
556 | 14252 | 14.252 | 681 | 0.931
557 | 14320 | 14.32 | -889 | 1.2395
558 | 14197 | 14.197 | -129 | 1.5905
559 | 14172 | 14.172 | 851 | 1.5745
560 | 14197 | 14.197 | -159 | 1.367
561 | 14409 | 14.409 | 790 | 1.2395
562 | 14200 | 14.2 | 395 | 0.9095
563 | 14431 | 14.431 | -7 | 0.9095
564 | 14281 | 14.281 | 889 | 0.8775
565 | 14477 | 14.477 | -172 | 1.601
566 | 14438 | 14.438 | -428 | 1.516
567 | 14390 | 14.39 | -606 | 1.197
568 | 14311 | 14.311 | -257 | 1.1755
569 | 14344 | 14.344 | 125 | 0.7715
570 | 14214 | 14.214 | -25 | 0.7605
571 | 13297 | 13.297 | -817 | 0.9575
572 | 14290 | 14.29 | 489 | 1.186
573 | 14447 | 14.447 | -724 | 1.718
574 | 14366 | 14.366 | 850 | 1.819
575 | 14479 | 14.479 | -631 | 1.436
576 | 14445 | 14.445 | -209 | 0.9575
577 | 14292 | 14.292 | 459 | 0.4095
578 | 14490 | 14.49 | -585 | 0.133
579 | 14266 | 14.266 | -842 | 0.367
580 | 14466 | 14.466 | 767 | 0.5955
581 | 14626 | 14.626 | -118 | 0.8725
582 | 14514 | 14.514 | 650 | 0.665
583 | 14490 | 14.49 | -277 | 0.3405
584 | 14302 | 14.302 | 239 | 0.3245
585 | 14433 | 14.433 | 774 | 0.298
586 | 14484 | 14.484 | -224 | 0.303
587 | 14458 | 14.458 | 982 | 0.3775
588 | 14329 | 14.329 | 269 | 0.3405
589 | 14579 | 14.579 | 687 | 0.4095
590 | 14419 | 14.419 | -888 | 0.2715
591 | 14416 | 14.416 | -533 | 0.3565
592 | 14597 | 14.597 | -379 | 0.266
593 | 14369 | 14.369 | 201 | 0.186
594 | 14460 | 14.46 | -106 | 0.1225
595 | 14400 | 14.4 | -48 | 0.069
596 | 14434 | 14.434 | 282 | 0.037
597 | 14437 | 14.437 | 786 | 0
598 | 14370 | 14.37 | -536 | 0
599 | 14415 | 14.415 | -151 | 0
600 | 14516 | 14.516 | -324 | 0
601 | 14470 | 14.47 | 499 | 0
602 | 14389 | 14.389 | 702 | 0
603 | 14274 | 14.274 | -41 | 0
604 | 14278 | 14.278 | 284 | 0
605 | 14141 | 14.141 | -976 | 0
606 | 14437 | 14.437 | -11 | 0
607 | 14207 | 14.207 | 703 | 0.0105
608 | 14445 | 14.445 | -524 | 0.0955
609 | 14288 | 14.288 | 479 | 0.101
610 | 14328 | 14.328 | -382 | 0.0105
611 | 14709 | 14.709 | -435 | 0.048
612 | 14289 | 14.289 | -34 | 0.0425
613 | 14648 | 14.648 | 283 | 0.048
614 | 14410 | 14.41 | 523 | 0.0745
615 | 14483 | 14.483 | -533 | 0.1115
616 | 14228 | 14.228 | 91 | 0.0955
617 | 13932 | 13.932 | 390 | 0.0955
618 | 13755 | 13.755 | 455 | 0.1065
619 | 14097 | 14.097 | 643 | 0.2555
620 | 13966 | 13.966 | -306 | 0.069
621 | 13814 | 13.814 | 262 | 0.048
622 | 14035 | 14.035 | -723 | 0.0215
623 | 14725 | 14.725 | -988 | 0.0105
624 | 14558 | 14.558 | 623 | 0.0055
625 | 14509 | 14.509 | 354 | 0
626 | 14562 | 14.562 | 48 | 0
627 | 14650 | 14.65 | -169 | 0
628 | 14727 | 14.727 | 193 | 0
629 | 14633 | 14.633 | 775 | 0
630 | 14683 | 14.683 | 571 | 0.0055
631 | 14494 | 14.494 | 32 | 0
632 | 14696 | 14.696 | -416 | 0
633 | 14712 | 14.712 | -901 | 0
634 | 14537 | 14.537 | 28 | 0
635 | 14808 | 14.808 | -90 | 0.08
636 | 14564 | 14.564 | 92 | 0.0955
637 | 14673 | 14.673 | 712 | 0.0265
638 | 14753 | 14.753 | 994 | 0.016
639 | 14538 | 14.538 | -841 | 0.048
640 | 14707 | 14.707 | 852 | 0.1225
641 | 14598 | 14.598 | 372 | 0.2235
642 | 14590 | 14.59 | -319 | 0.1545
643 | 14641 | 14.641 | -641 | 0.181
644 | 14359 | 14.359 | 297 | 0.197
645 | 14439 | 14.439 | 944 | 0.197
646 | 14508 | 14.508 | 631 | 0.1595
647 | 14559 | 14.559 | -600 | 0.351
648 | 14433 | 14.433 | 67 | 0.537
649 | 14502 | 14.502 | -955 | 0.7285
650 | 14500 | 14.5 | 605 | 0.7555
651 | 14370 | 14.37 | -733 | 1.3405
652 | 14371 | 14.371 | -152 | 1.8455
653 | 14473 | 14.473 | 678 | 1.133
654 | 14454 | 14.454 | 885 | 0.6595
655 | 14582 | 14.582 | -723 | 0.713
656 | 14515 | 14.515 | 803 | 1.548
657 | 14474 | 14.474 | -791 | 1.197
658 | 14325 | 14.325 | -155 | 1.6545
659 | 14409 | 14.409 | -539 | 1.883
660 | 14476 | 14.476 | 654 | 1.553
661 | 14573 | 14.573 | -286 | 1.734
662 | 14393 | 14.393 | 639 | 2.0905
663 | 14450 | 14.45 | -438 | 1.947
664 | 14125 | 14.125 | 368 | 1.835
665 | 13822 | 13.822 | 694 | 2.181
666 | 13965 | 13.965 | -952 | 1.9735
667 | 14276 | 14.276 | 42 | 1.92
668 | 14579 | 14.579 | -471 | 1.9415
669 | 14572 | 14.572 | 18 | 1.468
670 | 14566 | 14.566 | 743 | 1.2715
671 | 14635 | 14.635 | -97 | 1.4895
672 | 14509 | 14.509 | 620 | 1.532
673 | 14573 | 14.573 | 132 | 2.4045
674 | 14602 | 14.602 | -268 | 2.266
675 | 14677 | 14.677 | -13 | 2.3085
676 | 14490 | 14.49 | -178 | 1.9785
677 | 14623 | 14.623 | -335 | 1.899
678 | 14783 | 14.783 | -213 | 2
679 | 14692 | 14.692 | 80 | 1.702
680 | 14652 | 14.652 | -757 | 1.6595
681 | 14623 | 14.623 | 827 | 1.6755
682 | 14672 | 14.672 | 130 | 1.6115
683 | 14592 | 14.592 | -830 | 1.0745
684 | 14695 | 14.695 | -429 | 1.186
685 | 14550 | 14.55 | 684 | 1.3565
686 | 14625 | 14.625 | 589 | 1.351
687 | 14856 | 14.856 | -550 | 1.8615
688 | 14705 | 14.705 | 466 | 1.484
689 | 14452 | 14.452 | 672 | 1.7555
690 | 14587 | 14.587 | -708 | 2.266
691 | 14459 | 14.459 | 744 | 3.1755
692 | 14453 | 14.453 | -456 | 2.516
693 | 14509 | 14.509 | 419 | 2.947
694 | 14520 | 14.52 | -392 | 1.5105
695 | 14532 | 14.532 | 88 | 0
696 | 14622 | 14.622 | 662 | 0
697 | 14531 | 14.531 | 945 | 1.213
698 | 14564 | 14.564 | 748 | 3.0425
699 | 14600 | 14.6 | -702 | 3
700 | 14451 | 14.451 | -887 | 3.2395
701 | 14651 | 14.651 | 212 | 2.9575
702 | 14523 | 14.523 | 847 | 1.7235
703 | 14661 | 14.661 | -542 | 1.3775
704 | 14631 | 14.631 | -895 | 2.149
705 | 14588 | 14.588 | -996 | 1.899
706 | 14825 | 14.825 | -552 | 1.58
707 | 14596 | 14.596 | -176 | 1.053
708 | 14549 | 14.549 | -858 | 1.197
709 | 14537 | 14.537 | -75 | 1.468
710 | 14605 | 14.605 | -386 | 1.782
711 | 14690 | 14.69 | -994 | 1.819
712 | 14594 | 14.594 | -857 | 1.383
713 | 14558 | 14.558 | -349 | 1.702
714 | 14418 | 14.418 | 708 | 2.5425
715 | 13733 | 13.733 | -359 | 2.4575
716 | 13867 | 13.867 | 367 | 1.053
717 | 13817 | 13.817 | -453 | 1.4415
718 | 14120 | 14.12 | 568 | 0.968
719 | 13736 | 13.736 | -104 | 0.7765
720 | 14549 | 14.549 | -351 | 0.681
721 | 14583 | 14.583 | 713 | 0.58
722 | 14798 | 14.798 | 11 | 0.58
723 | 14651 | 14.651 | -490 | 1.08
724 | 14669 | 14.669 | 968 | 1.133
725 | 14601 | 14.601 | 388 | 1.0055
726 | 14880 | 14.88 | -592 | 1.1225
727 | 14563 | 14.563 | 418 | 0.9945
728 | 14645 | 14.645 | -221 | 0.899
729 | 14669 | 14.669 | -861 | 0.9735
730 | 14631 | 14.631 | 951 | 0.9255
731 | 14725 | 14.725 | -483 | 0.883
732 | 14819 | 14.819 | 452 | 0.8935
733 | 14607 | 14.607 | 188 | 0.968
734 | 14592 | 14.592 | -791 | 1.3245
735 | 14693 | 14.693 | -97 | 1.468
736 | 14541 | 14.541 | 388 | 1.665
737 | 14738 | 14.738 | 642 | 1.2555
738 | 14682 | 14.682 | 458 | 0.718
739 | 14435 | 14.435 | -229 | 0.2925
740 | 14629 | 14.629 | -400 | 0.266
741 | 14714 | 14.714 | -382 | 0.3085
742 | 14425 | 14.425 | -975 | 0.314
743 | 14768 | 14.768 | 110 | 0.3885
744 | 14459 | 14.459 | 299 | 0.6915
745 | 14671 | 14.671 | 55 | 0.5265
746 | 14388 | 14.388 | 581 | 0.952
747 | 14739 | 14.739 | -300 | 1.6275
748 | 14632 | 14.632 | 758 | 1.1385
749 | 14580 | 14.58 | -619 | 0.8885
750 | 14646 | 14.646 | 609 | 0.468
751 | 14552 | 14.552 | -769 | 0.7715
752 | 14804 | 14.804 | 542 | 1.2715
753 | 14331 | 14.331 | 174 | 1.2285
754 | 14862 | 14.862 | 621 | 1.335
755 | 14484 | 14.484 | -739 | 1.2925
756 | 14632 | 14.632 | 357 | 1.4415
757 | 14601 | 14.601 | -279 | 1.5585
758 | 14692 | 14.692 | -457 | 1.2715
759 | 14714 | 14.714 | -579 | 1.0055
760 | 14634 | 14.634 | -355 | 0.835
761 | 14277 | 14.277 | 200 | 0.7235
762 | 13765 | 13.765 | 756 | 0.447
763 | 14021 | 14.021 | -915 | 0.218
764 | 14561 | 14.561 | 782 | 0.048
765 | 14391 | 14.391 | 606 | 0.037
766 | 14541 | 14.541 | 161 | 0.165
767 | 14468 | 14.468 | 983 | 0.468
768 | 14340 | 14.34 | 718 | 0.569
769 | 14607 | 14.607 | 387 | 0.5055
770 | 14483 | 14.483 | -237 | 0.3565
771 | 14457 | 14.457 | -339 | 0.133
772 | 14436 | 14.436 | -211 | 0.0745
773 | 14542 | 14.542 | 569 | 0.053
774 | 14516 | 14.516 | -485 | 0.1225
775 | 14420 | 14.42 | -914 | 0.1915
776 | 14489 | 14.489 | 480 | 0.1915
777 | 14354 | 14.354 | 548 | 0.2555
778 | 14389 | 14.389 | -630 | 0.399
779 | 14451 | 14.451 | 378 | 0.6915
780 | 14408 | 14.408 | 188 | 0.7605
781 | 14522 | 14.522 | 490 | 0.6545
782 | 14484 | 14.484 | -129 | 0.681
783 | 14429 | 14.429 | -959 | 0.686
784 | 14344 | 14.344 | -729 | 0.6435
785 | 14287 | 14.287 | 743 | 0.713
786 | 14161 | 14.161 | -276 | 0.484
787 | 14403 | 14.403 | -567 | 0.436
788 | 14240 | 14.24 | 109 | 0.42
789 | 14414 | 14.414 | -662 | 0.4415
790 | 14288 | 14.288 | -690 | 0.6275
791 | 14481 | 14.481 | 922 | 0.766
792 | 14181 | 14.181 | 198 | 0.6275
793 | 14052 | 14.052 | 221 | 0.6065
794 | 14153 | 14.153 | -106 | 0.5745
795 | 14409 | 14.409 | -332 | 0.532
796 | 14347 | 14.347 | -997 | 0.468
797 | 14285 | 14.285 | 695 | 0.548
798 | 14348 | 14.348 | -994 | 0.617
799 | 14200 | 14.2 | -346 | 0.6275
800 | 14362 | 14.362 | 872 | 0.718
801 | 14319 | 14.319 | -629 | 1.048
802 | 14364 | 14.364 | 720 | 1.069
803 | 14333 | 14.333 | -128 | 1.1595
804 | 14394 | 14.394 | 757 | 1.5585
805 | 14363 | 14.363 | -133 | 1.702
806 | 14438 | 14.438 | -680 | 1.7285
807 | 14371 | 14.371 | 47 | 1.8615
808 | 14306 | 14.306 | 796 | 2.1275
809 | 14354 | 14.354 | 127 | 2.1275
810 | 14528 | 14.528 | 581 | 2.0425
811 | 14489 | 14.489 | 423 | 2.0055
812 | 14120 | 14.12 | -67 | 1.9785
813 | 13707 | 13.707 | -616 | 2.2235
814 | 13958 | 13.958 | 707 | 2.7555
815 | 13980 | 13.98 | 465 | 2.819
816 | 13981 | 13.981 | -88 | 2.186
817 | 13511 | 13.511 | 185 | 2.165
818 | 14661 | 14.661 | -472 | 2.2605
819 | 14481 | 14.481 | 694 | 2.4415
820 | 14583 | 14.583 | 858 | 1.9415
821 | 14559 | 14.559 | 714 | 1.6595
822 | 14512 | 14.512 | 954 | 1.532
823 | 14397 | 14.397 | -675 | 1.447
824 | 14611 | 14.611 | 542 | 1.537
825 | 14505 | 14.505 | 396 | 2.3725
826 | 14439 | 14.439 | -213 | 1.9415
827 | 14737 | 14.737 | -820 | 2.2555
828 | 14358 | 14.358 | 166 | 2.516
829 | 14670 | 14.67 | -992 | 1.8935
830 | 14528 | 14.528 | 88 | 2.3935
831 | 14485 | 14.485 | -363 | 1.702
832 | 14630 | 14.63 | 746 | 1.5425
833 | 14518 | 14.518 | -851 | 0.851
834 | 14569 | 14.569 | 374 | 0.351
835 | 14490 | 14.49 | -566 | 0.186
836 | 14547 | 14.547 | -557 | 0.234
837 | 14447 | 14.447 | -409 | 0.2555
838 | 14582 | 14.582 | 448 | 0.1915
839 | 14661 | 14.661 | -766 | 0.287
840 | 14429 | 14.429 | -808 | 0.266
841 | 14576 | 14.576 | -628 | 0.181
842 | 14506 | 14.506 | -661 | 0.2075
843 | 14519 | 14.519 | -90 | 0.2285
844 | 14523 | 14.523 | 67 | 0.101
845 | 14588 | 14.588 | -949 | 0.0105
846 | 14630 | 14.63 | -20 | 0.0265
847 | 14467 | 14.467 | -595 | 0.0425
848 | 14568 | 14.568 | -98 | 0.053
849 | 14626 | 14.626 | 887 | 0.0745
850 | 14677 | 14.677 | -402 | 0.197
851 | 14515 | 14.515 | -401 | 0.2555
852 | 14463 | 14.463 | -599 | 0.234
853 | 14758 | 14.758 | 761 | 0.1545
854 | 14517 | 14.517 | 909 | 0.197
855 | 14747 | 14.747 | 526 | 0.383
856 | 14412 | 14.412 | -23 | 0.3085
857 | 14686 | 14.686 | 57 | 0.314
858 | 14722 | 14.722 | 658 | 0.468
859 | 14305 | 14.305 | 206 | 0.5105
860 | 13685 | 13.685 | -30 | 0.718
861 | 14462 | 14.462 | 717 | 0.4895
862 | 14701 | 14.701 | -66 | 0.1755
863 | 14400 | 14.4 | -911 | 0.1115
864 | 14807 | 14.807 | -124 | 0.0585
865 | 14551 | 14.551 | 998 | 0.0905
866 | 14698 | 14.698 | -709 | 0.037
867 | 14543 | 14.543 | -438 | 0.0055
868 | 14666 | 14.666 | -179 | 0
869 | 14604 | 14.604 | 206 | 0
870 | 14643 | 14.643 | 970 | 0
871 | 14746 | 14.746 | -67 | 0
872 | 14621 | 14.621 | 719 | 0.0215
873 | 14642 | 14.642 | 210 | 0.032
874 | 14674 | 14.674 | -119 | 0.085
875 | 14536 | 14.536 | 402 | 0.1275
876 | 14586 | 14.586 | -512 | 0.3085
877 | 14766 | 14.766 | -930 | 0.548
878 | 14553 | 14.553 | -635 | 0.7395
879 | 14611 | 14.611 | -340 | 1.202
880 | 14511 | 14.511 | -144 | 1.037
881 | 14554 | 14.554 | 486 | 1.383
882 | 14653 | 14.653 | 444 | 1.415
883 | 14498 | 14.498 | -266 | 0.899
884 | 14569 | 14.569 | 446 | 0.899
885 | 14547 | 14.547 | 310 | 1.367
886 | 14588 | 14.588 | -976 | 1.8245
887 | 14579 | 14.579 | -728 | 1.947
888 | 14692 | 14.692 | -116 | 2.032
889 | 14515 | 14.515 | -93 | 1.697
890 | 14480 | 14.48 | -938 | 1.117
891 | 14641 | 14.641 | -526 | 1.032
892 | 14531 | 14.531 | 297 | 0
893 | 14531 | 14.531 | -15 | 1.8775
894 | 14539 | 14.539 | -607 | 1.8245
895 | 14461 | 14.461 | -165 | 1.67
896 | 14270 | 14.27 | -706 | 1.5905
897 | 14490 | 14.49 | -516 | 1.298
898 | 14336 | 14.336 | -31 | 2.1915
899 | 14301 | 14.301 | -897 | 2.516
900 | 14327 | 14.327 | 511 | 2.4735
901 | 14292 | 14.292 | 546 | 2.7925
902 | 14507 | 14.507 | -896 | 1.9895
903 | 14400 | 14.4 | 158 | 2.851
904 | 14448 | 14.448 | 94 | 3.085
905 | 13918 | 13.918 | -924 | 2.8935
906 | 13743 | 13.743 | -407 | 3.3455
907 | 13759 | 13.759 | -487 | 2.9255
908 | 13893 | 13.893 | -21 | 2.085
909 | 13723 | 13.723 | 20 | 2.4095
910 | 13608 | 13.608 | 126 | 2.5
911 | 14331 | 14.331 | 648 | 2.335
912 | 14717 | 14.717 | 736 | 2.298
913 | 14500 | 14.5 | -777 | 2.5745
914 | 14487 | 14.487 | 942 | 2.516
915 | 14680 | 14.68 | -236 | 2.7235
916 | 14585 | 14.585 | -787 | 3.1385
917 | 14765 | 14.765 | -83 | 2.803
918 | 14638 | 14.638 | 954 | 2.7925
919 | 14454 | 14.454 | -943 | 3.633
920 | 14401 | 14.401 | -263 | 4.319
921 | 14650 | 14.65 | 137 | 4.3455
922 | 14535 | 14.535 | 603 | 3.867
923 | 14675 | 14.675 | -683 | 3.3085
924 | 14638 | 14.638 | -847 | 3.298
925 | 14648 | 14.648 | 112 | 3.1225
926 | 14656 | 14.656 | -442 | 3.0105
927 | 14482 | 14.482 | 1000 | 2.633
928 | 14687 | 14.687 | -75 | 2.803
929 | 14563 | 14.563 | -66 | 2.4095
930 | 14636 | 14.636 | 404 | 2.2445
931 | 14583 | 14.583 | 617 | 2.0265
932 | 14496 | 14.496 | 353 | 1.617
933 | 14441 | 14.441 | -175 | 1.83
934 | 14296 | 14.296 | 296 | 1.58
935 | 14440 | 14.44 | -396 | 0.8455
936 | 14399 | 14.399 | 643 | 0.8615
937 | 14350 | 14.35 | -843 | 0.6385
938 | 14472 | 14.472 | -863 | 0.6545
939 | 14346 | 14.346 | 624 | 0.431
940 | 14452 | 14.452 | -351 | 0.1545
941 | 14421 | 14.421 | 528 | 0.1545
942 | 14209 | 14.209 | 694 | 0.0745
943 | 14533 | 14.533 | 400 | 0.1065
944 | 14268 | 14.268 | 99 | 0.064
945 | 14417 | 14.417 | 69 | 0.085
946 | 14480 | 14.48 | 936 | 0.17
947 | 14180 | 14.18 | 788 | 0.213
948 | 14540 | 14.54 | 711 | 0.3725
949 | 14462 | 14.462 | 243 | 0.383
950 | 14439 | 14.439 | -909 | 0.25
951 | 14428 | 14.428 | -665 | 0.165
952 | 14490 | 14.49 | -966 | 0.1225
953 | 14448 | 14.448 | -898 | 0.085
954 | 14168 | 14.168 | 218 | 0.181
955 | 13680 | 13.68 | -621 | 0.1435
956 | 14451 | 14.451 | -445 | 0.069
957 | 14409 | 14.409 | 917 | 0.1275
958 | 14396 | 14.396 | 288 | 0.0745
959 | 14517 | 14.517 | 368 | 0.0105
960 | 14546 | 14.546 | 83 | 0.032
961 | 14570 | 14.57 | -937 | 0
962 | 14609 | 14.609 | -833 | 0
963 | 14450 | 14.45 | -619 | 0
964 | 14577 | 14.577 | 391 | 0
965 | 14558 | 14.558 | -640 | 0
966 | 14545 | 14.545 | 500 | 0
967 | 14647 | 14.647 | -860 | 0
968 | 14587 | 14.587 | -358 | 0
969 | 14445 | 14.445 | -504 | 0
970 | 14444 | 14.444 | 568 | 0
971 | 14652 | 14.652 | -215 | 0
972 | 14511 | 14.511 | -373 | 0
973 | 14516 | 14.516 | -931 | 0
974 | 14470 | 14.47 | 76 | 0
975 | 14427 | 14.427 | -572 | 0
976 | 14633 | 14.633 | 901 | 0
977 | 14423 | 14.423 | -733 | 0
978 | 14531 | 14.531 | 605 | 0
979 | 14400 | 14.4 | 797 | 0
980 | 14535 | 14.535 | 245 | 0
981 | 14386 | 14.386 | 217 | 0
982 | 14346 | 14.346 | -133 | 0
983 | 14659 | 14.659 | 107 | 0
984 | 14451 | 14.451 | 608 | 0
985 | 14601 | 14.601 | 474 | 0
986 | 14279 | 14.279 | -440 | 0
987 | 14649 | 14.649 | -946 | 0
988 | 14326 | 14.326 | -632 | 0
989 | 14557 | 14.557 | -370 | 0
990 | 14544 | 14.544 | 121 | 0
991 | 14477 | 14.477 | 550 | 0
992 | 14648 | 14.648 | 5 | 0
993 | 14508 | 14.508 | 409 | 0
994 | 14615 | 14.615 | 754 | 0
995 | 14550 | 14.55 | -798 | 0
996 | 14506 | 14.506 | -689 | 0
997 | 14556 | 14.556 | -543 | 0
998 | 14582 | 14.582 | -60 | 0
999 | 14608 | 14.608 | -149 | 0
1000 | 14482 | 14.482 | 281 | 0
1001 | 14579 | 14.579 | 804 | 0
1002 | 14373 | 14.373 | -399 | 0
1003 | 13763 | 13.763 | -546 | 0
1004 | 14078 | 14.078 | -395 | 0
1005 | 13882 | 13.882 | 720 | 0
1006 | 13914 | 13.914 | -810 | 0
1007 | 13673 | 13.673 | -529 | 0
1008 | 14291 | 14.291 | -618 | 0
1009 | 14424 | 14.424 | 506 | 0.947
1010 | 14850 | 14.85 | 432 | 0.9895
1011 | 14557 | 14.557 | 617 | 0.9095
1012 | 14801 | 14.801 | 368 | 0.931
1013 | 14684 | 14.684 | 564 | 1.0905
1014 | 14585 | 14.585 | -138 | 0.883
1015 | 14812 | 14.812 | -499 | 0.8245
1016 | 14607 | 14.607 | 282 | 0.9945
1017 | 14629 | 14.629 | -966 | 1.0265
1018 | 14690 | 14.69 | 199 | 1.117
1019 | 14645 | 14.645 | 204 | 1.314
1020 | 14602 | 14.602 | 947 | 1.351
1021 | 14695 | 14.695 | 72 | 0.787
1022 | 14653 | 14.653 | -969 | 0.9095
1023 | 14545 | 14.545 | 324 | 0.8935
1024 | 14734 | 14.734 | 288 | 1.1545
1025 | 14429 | 14.429 | -486 | 1.053
1026 | 14615 | 14.615 | -840 | 0.8935
1027 | 14527 | 14.527 | -145 | 0.819
1028 | 14604 | 14.604 | -92 | 0.8085
1029 | 14644 | 14.644 | 223 | 0.984
1030 | 14540 | 14.54 | 873 | 1.181
1031 | 14510 | 14.51 | 372 | 1.0265
1032 | 14684 | 14.684 | -260 | 1.016
1033 | 14465 | 14.465 | 447 | 1.0745
1034 | 14749 | 14.749 | -73 | 0.814
1035 | 14664 | 14.664 | -506 | 0.4575
1036 | 14683 | 14.683 | -293 | 0.2925
1037 | 14641 | 14.641 | 141 | 0.399
1038 | 14513 | 14.513 | -146 | 0.4255
1039 | 14674 | 14.674 | 35 | 0.548
1040 | 14571 | 14.571 | 735 | 0.4895
1041 | 14618 | 14.618 | 940 | 0.463
1042 | 14518 | 14.518 | -166 | 0.234
1043 | 14599 | 14.599 | 914 | 0.303
1044 | 14569 | 14.569 | 785 | 0.069
1045 | 14577 | 14.577 | 889 | 0.016
1046 | 14777 | 14.777 | 708 | 0.0105
1047 | 14362 | 14.362 | 295 | 0
1048 | 14518 | 14.518 | 912 | 0.0745
1049 | 14451 | 14.451 | 732 | 0.2925
1050 | 13847 | 13.847 | 243 | 0.351
1051 | 13884 | 13.884 | 710 | 0.3085
1052 | 13450 | 13.45 | -300 | 0.6115
1053 | 14351 | 14.351 | -556 | 0.697
1054 | 14708 | 14.708 | 813 | 0.5955
1055 | 14738 | 14.738 | 945 | 0.6915
1056 | 14706 | 14.706 | 989 | 0.819
1057 | 14565 | 14.565 | -151 | 0.7395
1058 | 14813 | 14.813 | -603 | 0.899
1059 | 14735 | 14.735 | 796 | 1.266
1060 | 14727 | 14.727 | -114 | 1.7765
1061 | 14707 | 14.707 | -136 | 2.2925
1062 | 14668 | 14.668 | -224 | 1.9735
1063 | 14478 | 14.478 | -440 | 2
1064 | 14800 | 14.8 | -262 | 1.9095
1065 | 14668 | 14.668 | 842 | 1.548
1066 | 14703 | 14.703 | -949 | 1.351
1067 | 14595 | 14.595 | -474 | 1.702
1068 | 14681 | 14.681 | -825 | 1.9785
1069 | 14725 | 14.725 | -164 | 1.0955
1070 | 14657 | 14.657 | -781 | 0.8245
1071 | 14703 | 14.703 | -886 | 0.617
1072 | 14656 | 14.656 | -691 | 0.569
1073 | 14558 | 14.558 | -72 | 0.7285
1074 | 14542 | 14.542 | -948 | 0.7235
1075 | 14606 | 14.606 | -605 | 0.8085
1076 | 14550 | 14.55 | -151 | 0.75
1077 | 14607 | 14.607 | -299 | 0.9095
1078 | 14577 | 14.577 | -238 | 0.8725
1079 | 14508 | 14.508 | 826 | 1.053
1080 | 14632 | 14.632 | -275 | 1.064
1081 | 14574 | 14.574 | -272 | 0.9095
1082 | 14506 | 14.506 | -592 | 1.0215
1083 | 14608 | 14.608 | -903 | 1.553
1084 | 14601 | 14.601 | 400 | 1.266
1085 | 14646 | 14.646 | 660 | 1.298
1086 | 14770 | 14.77 | -614 | 1.165
1087 | 14446 | 14.446 | 254 | 0.9045
1088 | 14522 | 14.522 | -780 | 0.7925
1089 | 14744 | 14.744 | -530 | 0.8885
1090 | 14557 | 14.557 | 859 | 0.734
1091 | 14595 | 14.595 | 538 | 1.1435
1092 | 14672 | 14.672 | 673 | 1.5055
1093 | 14600 | 14.6 | 740 | 2.4785
1094 | 14778 | 14.778 | -661 | 2.186
1095 | 14516 | 14.516 | -841 | 1.8405
1096 | 14621 | 14.621 | 231 | 1.681
1097 | 14427 | 14.427 | -919 | 1.3405
1098 | 14718 | 14.718 | 424 | 1.383
1099 | 14774 | 14.774 | -978 | 1.2765
1100 | 14813 | 14.813 | -495 | 1.2075
1101 | 14184 | 14.184 | 266 | 1.1915
1102 | 13985 | 13.985 | -178 | 1.202
1103 | 14074 | 14.074 | -573 | 1.314
1104 | 14114 | 14.114 | 623 | 1.266
1105 | 14106 | 14.106 | -752 | 1.048
1106 | 13876 | 13.876 | -186 | 1.0585
1107 | 14726 | 14.726 | 895 | 1.149
1108 | 14708 | 14.708 | -958 | 0.984
1109 | 14824 | 14.824 | -413 | 0.947
1110 | 14893 | 14.893 | 815 | 1.165
1111 | 14724 | 14.724 | 467 | 1.314
1112 | 14906 | 14.906 | -786 | 1.133
1113 | 14621 | 14.621 | 565 | 1.1435
1114 | 14805 | 14.805 | -819 | 1.2765
1115 | 14855 | 14.855 | 778 | 1.3245
1116 | 14689 | 14.689 | -952 | 1.484
1117 | 14810 | 14.81 | -419 | 1.5
1118 | 14775 | 14.775 | 168 | 1.5425
1119 | 14548 | 14.548 | -310 | 1.8085
1120 | 14706 | 14.706 | -20 | 1.351
1121 | 14805 | 14.805 | 260 | 1.787
1122 | 14533 | 14.533 | 790 | 1.484
1123 | 14687 | 14.687 | -841 | 1.7075
1124 | 14577 | 14.577 | -345 | 2.3245
1125 | 14543 | 14.543 | 101 | 1.569
1126 | 14539 | 14.539 | -951 | 1.516
1127 | 14723 | 14.723 | -567 | 1.0425
1128 | 14516 | 14.516 | -686 | 1.2555
1129 | 14531 | 14.531 | -561 | 1.5585
1130 | 14734 | 14.734 | 281 | 1.117
1131 | 14195 | 14.195 | -139 | 1.0105
1132 | 12454 | 12.454 | -145 | 0.9415
1133 | 13380 | 13.38 | -803 | 0.968
1134 | 14469 | 14.469 | 10 | 0.617
1135 | 14547 | 14.547 | -905 | 0.5955
1136 | 14650 | 14.65 | -553 | 0.3405
1137 | 14637 | 14.637 | 614 | 0.335
1138 | 14734 | 14.734 | 322 | 0.548
1139 | 14526 | 14.526 | 916 | 0.867
1140 | 14762 | 14.762 | 309 | 0.9735
1141 | 14504 | 14.504 | 66 | 0.947
1142 | 14744 | 14.744 | -321 | 0.8935
1143 | 14798 | 14.798 | 528 | 0.883
1144 | 14607 | 14.607 | -219 | 0.899
1145 | 14702 | 14.702 | 914 | 1.0215
1146 | 14816 | 14.816 | 546 | 0.851
1147 | 14349 | 14.349 | 582 | 0.8405
1148 | 13909 | 13.909 | -304 | 0.6595
1149 | 14372 | 14.372 | -880 | 1.1225
1150 | 14672 | 14.672 | 500 | 1.037
1151 | 14753 | 14.753 | -961 | 0.617
1152 | 14697 | 14.697 | -996 | 0.819
1153 | 14859 | 14.859 | -544 | 0.5
1154 | 14870 | 14.87 | -445 | 0.3935
1155 | 14773 | 14.773 | -409 | 0.516
1156 | 14769 | 14.769 | 556 | 0.5425
1157 | 14842 | 14.842 | 439 | 0.718
1158 | 14834 | 14.834 | -349 | 0.617
1159 | 14608 | 14.608 | -556 | 0.3775
1160 | 14730 | 14.73 | 23 | 0.415
1161 | 14801 | 14.801 | -366 | 0.436
1162 | 14667 | 14.667 | 489 | 0.3775
1163 | 14707 | 14.707 | 231 | 0.197
1164 | 14826 | 14.826 | -665 | 0.399
1165 | 14662 | 14.662 | 627 | 0.399
1166 | 14742 | 14.742 | -648 | 0.6595
1167 | 14665 | 14.665 | 103 | 0.633
1168 | 14732 | 14.732 | 60 | 0.6275
1169 | 14691 | 14.691 | -790 | 0.532
1170 | 14546 | 14.546 | 299 | 0.6545
1171 | 14632 | 14.632 | -819 | 0.516
1172 | 14712 | 14.712 | -781 | 0.7285
1173 | 14545 | 14.545 | 659 | 0.6435
1174 | 14575 | 14.575 | 790 | 0.569
1175 | 14662 | 14.662 | 885 | 0.803
1176 | 14627 | 14.627 | 61 | 0.8935
1177 | 14545 | 14.545 | 132 | 0.9735
1178 | 14574 | 14.574 | -464 | 1.335
1179 | 14601 | 14.601 | 701 | 1.8885
1180 | 14587 | 14.587 | -607 | 2.899
1181 | 14781 | 14.781 | 801 | 1.484
1182 | 14535 | 14.535 | 711 | 1.516
1183 | 14589 | 14.589 | 452 | 0.851
1184 | 14629 | 14.629 | -554 | 0.7235
1185 | 14498 | 14.498 | -431 | 1.298
1186 | 14723 | 14.723 | 88 | 1.0105
1187 | 14586 | 14.586 | 919 | 1.314
1188 | 14549 | 14.549 | -744 | 1.9045
1189 | 14475 | 14.475 | -324 | 2.33
1190 | 14741 | 14.741 | -59 | 2.2765
1191 | 14675 | 14.675 | 794 | 1.9255
1192 | 14568 | 14.568 | -367 | 1.5745
1193 | 14644 | 14.644 | 917 | 1.186
1194 | 14159 | 14.159 | -566 | 2.3775
1195 | 13763 | 13.763 | -494 | 2.633
1196 | 14100 | 14.1 | -780 | 2.899
1197 | 13929 | 13.929 | -738 | 2.899
1198 | 14032 | 14.032 | 167 | 2.8565
1199 | 13616 | 13.616 | -731 | 2.968
1200 | 14680 | 14.68 | -304 | 2.782
1201 | 14627 | 14.627 | 478 | 3.5745
1202 | 14656 | 14.656 | 365 | 3.8935
1203 | 14617 | 14.617 | -634 | 3.383
1204 | 14639 | 14.639 | -802 | 3.4415
1205 | 14754 | 14.754 | -932 | 2.58
1206 | 14639 | 14.639 | 767 | 2.1115
1207 | 14662 | 14.662 | -111 | 2.218
1208 | 14686 | 14.686 | 270 | 2.186
1209 | 14694 | 14.694 | 995 | 2.569
1210 | 14679 | 14.679 | 527 | 3.319
1211 | 14463 | 14.463 | -393 | 2.6595
1212 | 14777 | 14.777 | -246 | 2.367
1213 | 14600 | 14.6 | 324 | 3.2765
1214 | 14543 | 14.543 | 668 | 3.032
1215 | 14794 | 14.794 | -760 | 2.6755
1216 | 14567 | 14.567 | -92 | 2.4895
1217 | 14617 | 14.617 | 813 | 2.9785
1218 | 14530 | 14.53 | -790 | 3.0215
1219 | 14548 | 14.548 | 958 | 2.867
1220 | 14820 | 14.82 | 71 | 2.3725
1221 | 14470 | 14.47 | 337 | 2.9095
1222 | 14750 | 14.75 | -765 | 3.4945
1223 | 14728 | 14.728 | -245 | 3.915
1224 | 14616 | 14.616 | -717 | 4.032
1225 | 14661 | 14.661 | 63 | 4.202
1226 | 14695 | 14.695 | -532 | 4.2075
1227 | 14583 | 14.583 | -873 | 4.6595
1228 | 14743 | 14.743 | -904 | 4.819
1229 | 14690 | 14.69 | -67 | 4.5955
1230 | 14515 | 14.515 | -543 | 4.601
1231 | 14501 | 14.501 | -436 | 4.367
1232 | 14668 | 14.668 | -556 | 4.3565
1233 | 14634 | 14.634 | -475 | 4.5425
1234 | 14700 | 14.7 | 430 | 4.6755
1235 | 14493 | 14.493 | -378 | 3.835
1236 | 14559 | 14.559 | 139 | 3.798
1237 | 14486 | 14.486 | -979 | 4.1545
1238 | 14648 | 14.648 | -385 | 2.3775
1239 | 14542 | 14.542 | 682 | 1.181
1240 | 14389 | 14.389 | 817 | 0.9945
1241 | 14438 | 14.438 | -716 | 1.0425
1242 | 14422 | 14.422 | 708 | 1
1243 | 13750 | 13.75 | -908 | 1.298
1244 | 14280 | 14.28 | 972 | 1.5
1245 | 14740 | 14.74 | 54 | 1.67
1246 | 14572 | 14.572 | -235 | 1.468
1247 | 14567 | 14.567 | -716 | 1.734
1248 | 14546 | 14.546 | -449 | 1.5955
1249 | 14727 | 14.727 | -725 | 1.2235
1250 | 14630 | 14.63 | -903 | 1.3085
1251 | 14763 | 14.763 | -362 | 1.3615
1252 | 14620 | 14.62 | 69 | 1.697
1253 | 14588 | 14.588 | -386 | 1.431
1254 | 14666 | 14.666 | 844 | 1.383
1255 | 14681 | 14.681 | -88 | 1.069
1256 | 14720 | 14.72 | -26 | 1.0425
1257 | 14431 | 14.431 | -767 | 1.0215
1258 | 14807 | 14.807 | 40 | 1.197
1259 | 14687 | 14.687 | 651 | 1.0585
1260 | 14667 | 14.667 | 224 | 1.101
1261 | 14647 | 14.647 | -972 | 1.1225
1262 | 14560 | 14.56 | 793 | 1.0055
1263 | 14663 | 14.663 | 169 | 0.803
1264 | 14536 | 14.536 | -415 | 0.8455
1265 | 14765 | 14.765 | 180 | 0.8405
1266 | 14497 | 14.497 | -509 | 0.867
1267 | 14518 | 14.518 | 89 | 0.766
1268 | 14563 | 14.563 | -678 | 0.4095
1269 | 14515 | 14.515 | -560 | 0.6225
1270 | 14674 | 14.674 | -624 | 0.814
1271 | 14543 | 14.543 | 510 | 1.5055
1272 | 14632 | 14.632 | 830 | 1.367
1273 | 14439 | 14.439 | 242 | 1.064
1274 | 14682 | 14.682 | -183 | 0.936
1275 | 14655 | 14.655 | -185 | 0.9895
1276 | 14527 | 14.527 | -59 | 1.1755
1277 | 14700 | 14.7 | 230 | 1.149
1278 | 14496 | 14.496 | -902 | 1.0585
1279 | 14567 | 14.567 | 408 | 0.968
1280 | 14430 | 14.43 | -477 | 0.8455
1281 | 14650 | 14.65 | 407 | 0.4945
1282 | 14600 | 14.6 | 704 | 0.3565
1283 | 14669 | 14.669 | -160 | 0.5585
1284 | 14565 | 14.565 | -193 | 0.633
1285 | 14635 | 14.635 | 805 | 0.8455
1286 | 14624 | 14.624 | -144 | 0.7765
1287 | 14642 | 14.642 | 176 | 0.9785
1288 | 14670 | 14.67 | 116 | 0.9095
1289 | 14264 | 14.264 | 686 | 1.08
1290 | 13944 | 13.944 | 579 | 1.1595
1291 | 14050 | 14.05 | 784 | 0.947
1292 | 13786 | 13.786 | -555 | 0.83
1293 | 14204 | 14.204 | 987 | 0.8245
1294 | 13779 | 13.779 | -618 | 1.2235
1295 | 14157 | 14.157 | 332 | 1.053
1296 | 14626 | 14.626 | -625 | 0.5585
1297 | 14671 | 14.671 | -71 | 0.4785
1298 | 14489 | 14.489 | 568 | 0.3725
1299 | 14707 | 14.707 | 198 | 0.516
1300 | 14682 | 14.682 | -850 | 0.5425
1301 | 14760 | 14.76 | -405 | 0.468
1302 | 14773 | 14.773 | -235 | 0.548
1303 | 14579 | 14.579 | 36 | 0.4895
1304 | 14741 | 14.741 | -619 | 0.33
1305 | 14492 | 14.492 | -673 | 0.2925
1306 | 14669 | 14.669 | 141 | 0.4945
1307 | 14515 | 14.515 | 724 | 0.585
1308 | 14636 | 14.636 | 396 | 0.718
1309 | 14698 | 14.698 | 605 | 0.564
1310 | 14896 | 14.896 | 381 | 0.5905
1311 | 14709 | 14.709 | 987 | 0.7605
1312 | 14610 | 14.61 | 21 | 0.803
1313 | 14611 | 14.611 | -538 | 0.5905
1314 | 14583 | 14.583 | -877 | 0.3885
1315 | 14704 | 14.704 | 431 | 0.2285
1316 | 14499 | 14.499 | 485 | 0.1545
1317 | 14730 | 14.73 | 625 | 0.202
1318 | 14536 | 14.536 | 389 | 0.197
1319 | 14637 | 14.637 | -899 | 0.2075
1320 | 14457 | 14.457 | -665 | 0.2555
1321 | 14542 | 14.542 | 500 | 0.2715
1322 | 14630 | 14.63 | -641 | 0.282
1323 | 14529 | 14.529 | -17 | 0.2395
1324 | 14454 | 14.454 | 127 | 0.287
1325 | 14539 | 14.539 | 611 | 0.266
1326 | 14450 | 14.45 | -15 | 0.287
1327 | 14537 | 14.537 | -793 | 0.2765
1328 | 14442 | 14.442 | 226 | 0.2555
1329 | 14531 | 14.531 | 225 | 0.0745
1330 | 14521 | 14.521 | -31 | 0.0905
1331 | 14625 | 14.625 | -423 | 0.234
1332 | 14349 | 14.349 | 250 | 0.5
1333 | 14750 | 14.75 | 450 | 0.436
1334 | 14519 | 14.519 | 28 | 0.5585
1335 | 14587 | 14.587 | -656 | 0.447
1336 | 14613 | 14.613 | 308 | 0.383
1337 | 14377 | 14.377 | -173 | 0.4045
1338 | 13670 | 13.67 | -436 | 0.4045
1339 | 14219 | 14.219 | 993 | 0.6385
1340 | 14513 | 14.513 | 711 | 0.8885
1341 | 14514 | 14.514 | -689 | 1.1915
1342 | 14684 | 14.684 | -728 | 1.3615
1343 | 14390 | 14.39 | 732 | 1.931
1344 | 14717 | 14.717 | -548 | 1.569
1345 | 14526 | 14.526 | -593 | 1.564
1346 | 14518 | 14.518 | 801 | 1.234
1347 | 14432 | 14.432 | 292 | 1.1545
1348 | 14627 | 14.627 | -547 | 1.298
1349 | 14500 | 14.5 | -429 | 1.7605
1350 | 14549 | 14.549 | 390 | 1.1385
1351 | 14726 | 14.726 | -377 | 1.6435
1352 | 14445 | 14.445 | 605 | 1.5105
1353 | 14472 | 14.472 | -301 | 1.585
1354 | 14640 | 14.64 | 537 | 1.2765
1355 | 14546 | 14.546 | 565 | 1.2555
1356 | 14557 | 14.557 | -528 | 1.0955
1357 | 14429 | 14.429 | -696 | 1.165
1358 | 14444 | 14.444 | 855 | 1.4415
1359 | 14550 | 14.55 | 456 | 1.782
1360 | 14498 | 14.498 | 973 | 0.8885
1361 | 14489 | 14.489 | 63 | 0
1362 | 14442 | 14.442 | -288 | 0
1363 | 14494 | 14.494 | -258 | 0
1364 | 14477 | 14.477 | -681 | 1.7765
1365 | 14534 | 14.534 | -161 | 1.814
1366 | 14371 | 14.371 | 787 | 1.835
1367 | 14298 | 14.298 | -717 | 1.2715
1368 | 14482 | 14.482 | 475 | 1.4575
1369 | 14572 | 14.572 | -954 | 1.484
1370 | 14359 | 14.359 | 242 | 1.1065
1371 | 14626 | 14.626 | -642 | 1.9785
1372 | 14448 | 14.448 | 64 | 2.463
1373 | 14386 | 14.386 | 901 | 2.452
1374 | 14519 | 14.519 | -287 | 2.1065
1375 | 14560 | 14.56 | -314 | 3.9575
1376 | 14455 | 14.455 | -353 | 3.7715
1377 | 14294 | 14.294 | 239 | 2.6065
1378 | 14702 | 14.702 | -539 | 1.6595
1379 | 14531 | 14.531 | -579 | 1.5955
1380 | 14420 | 14.42 | -772 | 1.6385
1381 | 14664 | 14.664 | -295 | 2.431
1382 | 14625 | 14.625 | 226 | 2.9575
1383 | 14525 | 14.525 | 688 | 3.6275
1384 | 14594 | 14.594 | 343 | 4.202
1385 | 14563 | 14.563 | 847 | 3.7765
1386 | 14758 | 14.758 | -99 | 3.117
1387 | 14481 | 14.481 | -867 | 3.2235
1388 | 14582 | 14.582 | 145 | 3.0215
1389 | 13736 | 13.736 | 679 | 3.569
1390 | 14012 | 14.012 | -112 | 3.5585
1391 | 13859 | 13.859 | -460 | 3.553
1392 | 14218 | 14.218 | 1000 | 3.883
1393 | 13673 | 13.673 | 750 | 3.6755
1394 | 14467 | 14.467 | -267 | 3.686
1395 | 14878 | 14.878 | -240 | 3.968
1396 | 14709 | 14.709 | -444 | 4.1595
1397 | 14666 | 14.666 | 575 | 3.5425
1398 | 14853 | 14.853 | 934 | 3.7285
1399 | 14393 | 14.393 | 631 | 4.016
1400 | 14849 | 14.849 | 789 | 3.8085
1401 | 14683 | 14.683 | 998 | 4.5105
1402 | 14616 | 14.616 | -319 | 4.734
1403 | 14683 | 14.683 | -633 | 4.4945
1404 | 14833 | 14.833 | 736 | 4.7075
1405 | 14472 | 14.472 | 658 | 3.7555
1406 | 14651 | 14.651 | 977 | 3.431
1407 | 14769 | 14.769 | -717 | 3.0955
1408 | 14597 | 14.597 | 959 | 2.9785
1409 | 14718 | 14.718 | -492 | 2.681
1410 | 14546 | 14.546 | -672 | 2.484
1411 | 14626 | 14.626 | -34 | 2.08
1412 | 14465 | 14.465 | -586 | 2.2765
1413 | 14616 | 14.616 | 565 | 2.8725
1414 | 14502 | 14.502 | -302 | 3.2285
1415 | 14601 | 14.601 | 446 | 3.4095
1416 | 14501 | 14.501 | 678 | 3.936
1417 | 14605 | 14.605 | -995 | 3.314
1418 | 14345 | 14.345 | 435 | 4.064
1419 | 14458 | 14.458 | -830 | 4.415
1420 | 14598 | 14.598 | 282 | 4.484
1421 | 14591 | 14.591 | -502 | 3.899
1422 | 14236 | 14.236 | -552 | 4.181
1423 | 14635 | 14.635 | -935 | 3.6915
1424 | 14503 | 14.503 | -262 | 4.0585
1425 | 14448 | 14.448 | -238 | 3.5425
1426 | 14667 | 14.667 | 433 | 3.9255
1427 | 14556 | 14.556 | -994 | 3.3455
1428 | 14702 | 14.702 | 483 | 3
1429 | 14657 | 14.657 | -552 | 2.2715
1430 | 14653 | 14.653 | -631 | 3.803
1431 | 14600 | 14.6 | 334 | 3.936
1432 | 14643 | 14.643 | -755 | 4.585
1433 | 14603 | 14.603 | -504 | 4.58
1434 | 13861 | 13.861 | 590 | 3.8725
1435 | 14021 | 14.021 | -204 | 3.2075
1436 | 14596 | 14.596 | -915 | 3.303
1437 | 14715 | 14.715 | 27 | 3.601
1438 | 14449 | 14.449 | 153 | 3.787
1439 | 14781 | 14.781 | 216 | 4.3775
1440 | 14502 | 14.502 | 742 | 4.4045
1441 | 14641 | 14.641 | -875 | 3.601
1442 | 14689 | 14.689 | -348 | 3.298
1443 | 14549 | 14.549 | 786 | 4.181
1444 | 14719 | 14.719 | 338 | 3.8245
1445 | 14646 | 14.646 | 830 | 3.9895
1446 | 14654 | 14.654 | -575 | 4.1065
1447 | 14611 | 14.611 | -692 | 3.5105
1448 | 14712 | 14.712 | -855 | 1.936
1449 | 14603 | 14.603 | -679 | 2.335
1450 | 14698 | 14.698 | -331 | 3.883
1451 | 14529 | 14.529 | -929 | 4.2445
1452 | 14665 | 14.665 | -359 | 4.5
1453 | 14730 | 14.73 | -314 | 4.713
1454 | 14450 | 14.45 | -810 | 4.899
1455 | 14571 | 14.571 | -981 | 4.968
1456 | 14679 | 14.679 | 181 | 4.7925
1457 | 14643 | 14.643 | 361 | 4.351
1458 | 14604 | 14.604 | -673 | 3.851
1459 | 14589 | 14.589 | 764 | 3.0105
1460 | 14526 | 14.526 | -302 | 3.9735
1461 | 14356 | 14.356 | -811 | 4.5265
1462 | 14474 | 14.474 | -514 | 3.9895
1463 | 14489 | 14.489 | -592 | 4.197
1464 | 14513 | 14.513 | 744 | 4.58
1465 | 14428 | 14.428 | 32 | 4.4045
1466 | 14510 | 14.51 | 890 | 4.7765
1467 | 14252 | 14.252 | 230 | 4.7925
1468 | 14456 | 14.456 | -333 | 4.8935
1469 | 14115 | 14.115 | -441 | 4.782
1470 | 14308 | 14.308 | -41 | 4.3245
1471 | 14494 | 14.494 | -228 | 4.08
1472 | 14325 | 14.325 | -761 | 4.197
1473 | 14550 | 14.55 | 564 | 2.7285
1474 | 14507 | 14.507 | -795 | 2.665
1475 | 14415 | 14.415 | 957 | 1.484
1476 | 14636 | 14.636 | -783 | 1.9945
1477 | 14262 | 14.262 | 577 | 1.3615
1478 | 14575 | 14.575 | -898 | 1.335
1479 | 14571 | 14.571 | -546 | 1.7715
1480 | 14561 | 14.561 | 743 | 1.569
1481 | 14463 | 14.463 | -271 | 1.5265
1482 | 14504 | 14.504 | 437 | 0.1115
1483 | 14462 | 14.462 | -77 | 1.5265
1484 | 14053 | 14.053 | -726 | 1.0955
1485 | 13792 | 13.792 | -849 | 1.2555
1486 | 14068 | 14.068 | 974 | 1.8725
1487 | 14089 | 14.089 | -716 | 1.351
1488 | 13939 | 13.939 | -429 | 1.452
1489 | 14013 | 14.013 | 600 | 1.303
1490 | 14797 | 14.797 | -937 | 1.665
1491 | 14702 | 14.702 | -253 | 1.2075
1492 | 14613 | 14.613 | -660 | 1.4735
1493 | 14818 | 14.818 | 28 | 0.8455
1494 | 14740 | 14.74 | 341 | 0.899
1495 | 14698 | 14.698 | -472 | 1.0585
1496 | 14774 | 14.774 | 721 | 1.1915
1497 | 14606 | 14.606 | 473 | 1.734
1498 | 14669 | 14.669 | -125 | 1.766
1499 | 14731 | 14.731 | -71 | 1.5745
1500 | 14478 | 14.478 | 362 | 1.6225
1501 | 14694 | 14.694 | -938 | 2.165
1502 | 14727 | 14.727 | 281 | 1.9045
1503 | 14612 | 14.612 | -48 | 2.186
1504 | 14493 | 14.493 | 900 | 2.7075
1505 | 14576 | 14.576 | 758 | 2.8405
1506 | 14733 | 14.733 | 343 | 2.1435
1507 | 14577 | 14.577 | 1 | 2.915
1508 | 14564 | 14.564 | -385 | 2.9945
1509 | 14642 | 14.642 | 954 | 3.3935
1510 | 14521 | 14.521 | -276 | 2.532
1511 | 14663 | 14.663 | 767 | 2.33
1512 | 14555 | 14.555 | -837 | 2.516
1513 | 14518 | 14.518 | -272 | 1.08
1514 | 14354 | 14.354 | -433 | 0.2925
1515 | 14579 | 14.579 | -670 | 0.7285
1516 | 14424 | 14.424 | -158 | 0.4945
1517 | 14516 | 14.516 | -544 | 0.3085
1518 | 14290 | 14.29 | -39 | 0.3725
1519 | 14429 | 14.429 | -503 | 0.4735
1520 | 14366 | 14.366 | -233 | 0.718
1521 | 14492 | 14.492 | -10 | 0.9895
1522 | 14539 | 14.539 | -521 | 1.7715
1523 | 14572 | 14.572 | -542 | 1.516
1524 | 14587 | 14.587 | -253 | 2.303
1525 | 14708 | 14.708 | 937 | 2.399
1526 | 14571 | 14.571 | 555 | 1.484
1527 | 14613 | 14.613 | -983 | 1.697
1528 | 14404 | 14.404 | -334 | 1.2925
1529 | 13877 | 13.877 | 816 | 1.08
1530 | 14292 | 14.292 | 343 | 0.7075
1531 | 14759 | 14.759 | -216 | 0.6115
1532 | 14465 | 14.465 | -675 | 0.8725
1533 | 14659 | 14.659 | -391 | 0.7285
1534 | 14659 | 14.659 | 340 | 0.713
1535 | 14717 | 14.717 | -599 | 0.67
1536 | 14617 | 14.617 | 981 | 0.447
1537 | 14693 | 14.693 | 364 | 0.287
1538 | 14579 | 14.579 | -513 | 0.287
1539 | 14865 | 14.865 | 353 | 0.6435
1540 | 14831 | 14.831 | -828 | 0.8935
1541 | 14601 | 14.601 | 227 | 0.7605
1542 | 14873 | 14.873 | 768 | 0.931
1543 | 14528 | 14.528 | -783 | 1.0585
1544 | 14684 | 14.684 | 748 | 0.681
1545 | 14641 | 14.641 | -162 | 0.218
1546 | 14742 | 14.742 | -140 | 0.0425
1547 | 14717 | 14.717 | 252 | 0.0055
1548 | 14611 | 14.611 | 49 | 0.0055
1549 | 14691 | 14.691 | 245 | 0
1550 | 14719 | 14.719 | 578 | 0
1551 | 14591 | 14.591 | 832 | 0
1552 | 14729 | 14.729 | 738 | 0
1553 | 14629 | 14.629 | 597 | 0
1554 | 14622 | 14.622 | -75 | 0
1555 | 14635 | 14.635 | -346 | 0
1556 | 14589 | 14.589 | 631 | 0
1557 | 14655 | 14.655 | -608 | 0.032
1558 | 14342 | 14.342 | -390 | 0.0265
1559 | 14493 | 14.493 | -71 | 0.037
1560 | 14552 | 14.552 | 791 | 0.085
1561 | 14467 | 14.467 | 769 | 0.1545
1562 | 14447 | 14.447 | 585 | 0.1915
1563 | 14455 | 14.455 | -691 | 0.431
1564 | 14478 | 14.478 | -929 | 0.5215
1565 | 14429 | 14.429 | -708 | 0.383
1566 | 14510 | 14.51 | 313 | 0.25
1567 | 14289 | 14.289 | 938 | 0.1915
1568 | 14595 | 14.595 | 624 | 0.218
1569 | 14487 | 14.487 | 105 | 0.17
1570 | 14441 | 14.441 | 48 | 0.17
1571 | 14434 | 14.434 | 384 | 0.1275
1572 | 14411 | 14.411 | -586 | 0.1275
1573 | 14427 | 14.427 | -468 | 0.064
1574 | 14523 | 14.523 | 827 | 0.016
1575 | 14464 | 14.464 | 106 | 0.0105
1576 | 14363 | 14.363 | 563 | 0.016
1577 | 14485 | 14.485 | 632 | 0.0105
1578 | 13935 | 13.935 | -696 | 0.032
1579 | 13671 | 13.671 | -484 | 0.0585
1580 | 13906 | 13.906 | 196 | 0.048
1581 | 13830 | 13.83 | 282 | 0.016
1582 | 13666 | 13.666 | 534 | 0.016
1583 | 13703 | 13.703 | 963 | 0.0265
1584 | 14574 | 14.574 | 47 | 0.0055
1585 | 14460 | 14.46 | -155 | 0.1225
1586 | 14444 | 14.444 | 17 | 0.101
1587 | 14632 | 14.632 | -974 | 0.016
1588 | 14348 | 14.348 | 345 | 0.1385
1589 | 14720 | 14.72 | 466 | 0.0585
1590 | 14548 | 14.548 | 310 | 0.0055
1591 | 14576 | 14.576 | 922 | 0
1592 | 14481 | 14.481 | -629 | 0
1593 | 14603 | 14.603 | 106 | 0
1594 | 14651 | 14.651 | -304 | 0
1595 | 14647 | 14.647 | 217 | 0
1596 | 14598 | 14.598 | 957 | 0
1597 | 14485 | 14.485 | 902 | 0
1598 | 14409 | 14.409 | 158 | 0
1599 | 14701 | 14.701 | 924 | 0
1600 | 14572 | 14.572 | 218 | 0
1601 | 14497 | 14.497 | 534 | 0
1602 | 14617 | 14.617 | 415 | 0
1603 | 14501 | 14.501 | -926 | 0
1604 | 14496 | 14.496 | 676 | 0
1605 | 14582 | 14.582 | 410 | 0.0585
1606 | 14385 | 14.385 | 734 | 0.053
1607 | 14376 | 14.376 | -890 | 0.064
1608 | 14469 | 14.469 | -722 | 0.0265
1609 | 14594 | 14.594 | -456 | 0.032
1610 | 14381 | 14.381 | -913 | 0.0905
1611 | 14546 | 14.546 | -755 | 0.0745
1612 | 14489 | 14.489 | 482 | 0.133
1613 | 14376 | 14.376 | -388 | 0.1755
1614 | 14501 | 14.501 | -989 | 0.2235
1615 | 14476 | 14.476 | 90 | 0.2765
1616 | 14594 | 14.594 | 753 | 0.3935
1617 | 14746 | 14.746 | -167 | 0.58
1618 | 14465 | 14.465 | 731 | 0.718
1619 | 14357 | 14.357 | 964 | 0.8405
1620 | 14435 | 14.435 | -167 | 0.75
1621 | 14543 | 14.543 | 348 | 0.7285
1622 | 14477 | 14.477 | -442 | 0.7235
1623 | 14683 | 14.683 | -734 | 0.8885
1624 | 14581 | 14.581 | -684 | 1.303
1625 | 14468 | 14.468 | -86 | 1.266
1626 | 14517 | 14.517 | 177 | 1.516
1627 | 14510 | 14.51 | -523 | 2.197
1628 | 14632 | 14.632 | -810 | 1.8085
1629 | 14201 | 14.201 | -327 | 2.101
1630 | 13718 | 13.718 | 627 | 2.6275
1631 | 14666 | 14.666 | 883 | 3.2715
1632 | 14618 | 14.618 | 863 | 3.463
1633 | 14715 | 14.715 | 782 | 4.037
1634 | 14511 | 14.511 | -851 | 4.165
1635 | 14788 | 14.788 | 666 | 3.952
1636 | 14692 | 14.692 | 717 | 4.0055
1637 | 14585 | 14.585 | 267 | 4.42
1638 | 14707 | 14.707 | 218 | 4.5905
1639 | 14592 | 14.592 | 396 | 4.585
1640 | 14894 | 14.894 | -600 | 4.6225
1641 | 14530 | 14.53 | -61 | 4.58
1642 | 14669 | 14.669 | 620 | 4.7925
1643 | 14661 | 14.661 | 665 | 4.4045
1644 | 14559 | 14.559 | -123 | 3.0265
1645 | 14833 | 14.833 | 618 | 2.6595
1646 | 14461 | 14.461 | 462 | 2.5425
1647 | 14627 | 14.627 | 923 | 2.3725
1648 | 14577 | 14.577 | -380 | 2.367
1649 | 14586 | 14.586 | 82 | 2.936
1650 | 14668 | 14.668 | 229 | 3.702
1651 | 14444 | 14.444 | 411 | 3.6275
1652 | 14541 | 14.541 | -196 | 3.548
1653 | 14625 | 14.625 | -740 | 4.08
1654 | 14522 | 14.522 | -744 | 3.9255
1655 | 14620 | 14.62 | -492 | 4.0745
1656 | 14625 | 14.625 | 195 | 4.4255
1657 | 14599 | 14.599 | -533 | 4.7715
1658 | 14455 | 14.455 | -435 | 4.532
1659 | 14583 | 14.583 | 434 | 4.8455
1660 | 14528 | 14.528 | 882 | 4.2605
1661 | 14522 | 14.522 | -862 | 4.3615
1662 | 14508 | 14.508 | -640 | 3.835
1663 | 14349 | 14.349 | -796 | 4.149
1664 | 14644 | 14.644 | -67 | 3.17
1665 | 14598 | 14.598 | -305 | 2.202
1666 | 14554 | 14.554 | -266 | 2.0215
1667 | 14522 | 14.522 | -715 | 2.8405
1668 | 14539 | 14.539 | 133 | 2.7285
1669 | 14458 | 14.458 | -467 | 1.7075
1670 | 14630 | 14.63 | -281 | 1.0745
1671 | 14356 | 14.356 | -424 | 1.686
1672 | 14543 | 14.543 | -961 | 2.186
1673 | 14375 | 14.375 | -204 | 2.6385
1674 | 13888 | 13.888 | 14 | 2.8085
1675 | 13832 | 13.832 | -794 | 2.335
1676 | 13830 | 13.83 | 456 | 1.6435
1677 | 14079 | 14.079 | -663 | 1.287
1678 | 13733 | 13.733 | -219 | 1.5105
1679 | 13939 | 13.939 | -752 | 0.9255
1680 | 14590 | 14.59 | 347 | 1.085
1681 | 14697 | 14.697 | 494 | 1.431
1682 | 14786 | 14.786 | 49 | 1.2075
1683 | 14800 | 14.8 | 502 | 1.1435
1684 | 14570 | 14.57 | 690 | 1.1435
1685 | 14855 | 14.855 | 621 | 0.835
1686 | 14710 | 14.71 | 47 | 0.702
1687 | 14684 | 14.684 | -450 | 1.064
1688 | 14554 | 14.554 | -718 | 0.92
1689 | 14685 | 14.685 | 466 | 0.9255
1690 | 14686 | 14.686 | -914 | 1.149
1691 | 14751 | 14.751 | -739 | 1.016
1692 | 14707 | 14.707 | -117 | 0.702
1693 | 14635 | 14.635 | -163 | 1.0585
1694 | 14718 | 14.718 | 871 | 1.33
1695 | 14645 | 14.645 | 377 | 1.5105
1696 | 14628 | 14.628 | -438 | 2.314
1697 | 14626 | 14.626 | 55 | 1.968
1698 | 14634 | 14.634 | 224 | 2.4415
1699 | 14452 | 14.452 | 447 | 3.819
1700 | 14522 | 14.522 | 967 | 4.83
1701 | 14576 | 14.576 | -899 | 4.8455
1702 | 14561 | 14.561 | 479 | 4.9735
1703 | 14558 | 14.558 | 154 | 4.984
1704 | 14673 | 14.673 | 313 | 4.9785
1705 | 14411 | 14.411 | 371 | 4.3935
1706 | 14591 | 14.591 | 658 | 3.9255
1707 | 14577 | 14.577 | 871 | 3.5905
1708 | 14652 | 14.652 | -436 | 3.3935
1709 | 14422 | 14.422 | 731 | 3.0215
1710 | 14532 | 14.532 | -769 | 3.6385
1711 | 14679 | 14.679 | 617 | 4.734
1712 | 14450 | 14.45 | 275 | 4.8935
1713 | 14522 | 14.522 | 686 | 4.9785
1714 | 14534 | 14.534 | 750 | 4.8615
1715 | 14471 | 14.471 | 990 | 4.936
1716 | 14615 | 14.615 | -111 | 4.968
1717 | 14459 | 14.459 | 57 | 4.9735
1718 | 14570 | 14.57 | 979 | 4.9785
1719 | 14626 | 14.626 | 248 | 4.9735
1720 | 14491 | 14.491 | 845 | 4.963
1721 | 14369 | 14.369 | 995 | 4.9785
1722 | 14555 | 14.555 | -966 | 4.9785
1723 | 14366 | 14.366 | -699 | 4.9785
1724 | 13858 | 13.858 | 550 | 4.9735
1725 | 14111 | 14.111 | -377 | 4.9785
1726 | 14545 | 14.545 | -643 | 4.963
1727 | 14475 | 14.475 | 937 | 4.9785
1728 | 14491 | 14.491 | 636 | 4.9785
1729 | 14650 | 14.65 | -933 | 4.963
1730 | 14560 | 14.56 | 35 | 4.4785
1731 | 14548 | 14.548 | 668 | 4.1275
1732 | 14442 | 14.442 | 448 | 4.564
1733 | 14586 | 14.586 | 109 | 4.0425
1734 | 14666 | 14.666 | 984 | 3.0745
1735 | 14620 | 14.62 | 448 | 2.553
1736 | 14442 | 14.442 | -727 | 1.399
1737 | 14486 | 14.486 | -319 | 1.8885
1738 | 14550 | 14.55 | 606 | 1.3775
1739 | 14587 | 14.587 | 616 | 1.5585
1740 | 14572 | 14.572 | -667 | 0.915
1741 | 14440 | 14.44 | -624 | 0.282
1742 | 14497 | 14.497 | -285 | 0.1545
1743 | 14639 | 14.639 | -628 | 0.4575
1744 | 14474 | 14.474 | -904 | 0.8885
1745 | 14516 | 14.516 | -404 | 0.915
1746 | 14340 | 14.34 | -934 | 0.67
1747 | 14655 | 14.655 | -592 | 0.4255
1748 | 14440 | 14.44 | -896 | 0.213
1749 | 14372 | 14.372 | 921 | 0.08
1750 | 14459 | 14.459 | -679 | 0.0265
1751 | 14486 | 14.486 | 702 | 0.0215
1752 | 14352 | 14.352 | 425 | 0.048
1753 | 14539 | 14.539 | -53 | 0.085
1754 | 14568 | 14.568 | -368 | 0.0905
1755 | 14393 | 14.393 | 406 | 0.0955
1756 | 14479 | 14.479 | -780 | 0.037
1757 | 14469 | 14.469 | -490 | 0.0105
1758 | 14389 | 14.389 | -980 | 0.0055
1759 | 14365 | 14.365 | 72 | 0
1760 | 14498 | 14.498 | 955 | 0
1761 | 14432 | 14.432 | 569 | 0
1762 | 14428 | 14.428 | 704 | 0.0055
1763 | 14582 | 14.582 | 327 | 0.0265
1764 | 14576 | 14.576 | 115 | 0.0105
1765 | 14505 | 14.505 | 961 | 0.016
1766 | 14456 | 14.456 | 572 | 0.0425
1767 | 14752 | 14.752 | -287 | 0.069
1768 | 14500 | 14.5 | 802 | 0.08
1769 | 14522 | 14.522 | -967 | 0.101
1770 | 14047 | 14.047 | -186 | 0.0905
1771 | 13903 | 13.903 | 202 | 0.117
1772 | 14007 | 14.007 | -239 | 0.149
1773 | 14047 | 14.047 | 469 | 0.1225
1774 | 13663 | 13.663 | 802 | 0.1115
1775 | 13946 | 13.946 | -978 | 0.085
1776 | 14559 | 14.559 | 128 | 0.0905
1777 | 14715 | 14.715 | 368 | 0.08
1778 | 14538 | 14.538 | 438 | 0.053
1779 | 14448 | 14.448 | 912 | 0.08
1780 | 14764 | 14.764 | 961 | 0.213
1781 | 14576 | 14.576 | -289 | 0.2445
1782 | 14552 | 14.552 | -118 | 0.436
1783 | 14598 | 14.598 | 662 | 0.569
1784 | 14555 | 14.555 | 129 | 0.5585
1785 | 14588 | 14.588 | 192 | 0.681
1786 | 14665 | 14.665 | 416 | 0.7235
1787 | 14496 | 14.496 | -812 | 0.8455
1788 | 14711 | 14.711 | 163 | 0.9415
1789 | 14590 | 14.59 | -198 | 0.9945
1790 | 14390 | 14.39 | -112 | 1.069
1791 | 14515 | 14.515 | 547 | 0.947
1792 | 14396 | 14.396 | -901 | 1.2235
1793 | 14634 | 14.634 | -520 | 1.2715
1794 | 14477 | 14.477 | 490 | 1.25
1795 | 14583 | 14.583 | -875 | 1.335
1796 | 14433 | 14.433 | 42 | 1.537
1797 | 14578 | 14.578 | 326 | 1.032
1798 | 14526 | 14.526 | -496 | 0.718
1799 | 14475 | 14.475 | -357 | 0.4785
1800 | 14474 | 14.474 | 453 | 0.436
1801 | 14638 | 14.638 | -799 | 0.5745
1802 | 14611 | 14.611 | -936 | 0.564
1803 | 14563 | 14.563 | 346 | 0.867
1804 | 14687 | 14.687 | 292 | 0.7075
1805 | 14583 | 14.583 | -120 | 0.6545
1806 | 14779 | 14.779 | 697 | 0.3885
1807 | 14676 | 14.676 | 169 | 0.553
1808 | 14606 | 14.606 | 974 | 0.7555
1809 | 14640 | 14.64 | -315 | 0.883
1810 | 14785 | 14.785 | -457 | 0.867
1811 | 14694 | 14.694 | 405 | 0.7285
1812 | 14655 | 14.655 | 610 | 1.032
1813 | 14700 | 14.7 | 370 | 1.25
1814 | 14926 | 14.926 | 104 | 0.9945
1815 | 14691 | 14.691 | 591 | 0.8935
1816 | 14611 | 14.611 | -762 | 0.9415
1817 | 14555 | 14.555 | 39 | 0.8615
1818 | 13946 | 13.946 | -984 | 0.686
1819 | 14467 | 14.467 | 629 | 0.617
1820 | 14650 | 14.65 | -7 | 0.569
1821 | 14814 | 14.814 | -170 | 0.4895
1822 | 14777 | 14.777 | -303 | 0.4255
1823 | 14752 | 14.752 | 596 | 0.5055
1824 | 14854 | 14.854 | -367 | 0.537
1825 | 14635 | 14.635 | -520 | 0.5585
1826 | 14880 | 14.88 | 567 | 0.532
1827 | 14727 | 14.727 | -792 | 0.516
1828 | 14844 | 14.844 | 966 | 0.3725
1829 | 14806 | 14.806 | -691 | 0.287
1830 | 14759 | 14.759 | 975 | 0.3405
1831 | 14668 | 14.668 | 434 | 0.298
1832 | 14836 | 14.836 | 535 | 0.2075
1833 | 14629 | 14.629 | 79 | 0.101
1834 | 14996 | 14.996 | 474 | 0.0745
1835 | 14819 | 14.819 | 433 | 0.197
1836 | 14732 | 14.732 | 215 | 0.4785
1837 | 14741 | 14.741 | -338 | 0.532
1838 | 14795 | 14.795 | 892 | 0.5105
1839 | 14767 | 14.767 | 975 | 0.2715
1840 | 14641 | 14.641 | -215 | 0.197
1841 | 14780 | 14.78 | -516 | 0.2605
1842 | 14735 | 14.735 | 258 | 0.484
1843 | 14575 | 14.575 | 533 | 0.537
1844 | 14711 | 14.711 | 258 | 0.463
1845 | 14582 | 14.582 | 507 | 0.415
1846 | 14732 | 14.732 | 991 | 0.1755
1847 | 14696 | 14.696 | -686 | 0.085
1848 | 14553 | 14.553 | -763 | 0.1755
1849 | 14522 | 14.522 | -6 | 0.133
1850 | 14557 | 14.557 | 776 | 0.0955
1851 | 14509 | 14.509 | -323 | 0.133
1852 | 14547 | 14.547 | -389 | 0.1545
1853 | 14535 | 14.535 | 362 | 0.1225
1854 | 14464 | 14.464 | 906 | 0.149
1855 | 14445 | 14.445 | -338 | 0.149
1856 | 14831 | 14.831 | 817 | 0.1385
1857 | 14579 | 14.579 | 647 | 0.149
1858 | 14571 | 14.571 | -767 | 0.1595
1859 | 14586 | 14.586 | -736 | 0.0905
1860 | 14498 | 14.498 | -854 | 0.0585
1861 | 14769 | 14.769 | 393 | 0.085
1862 | 14563 | 14.563 | 97 | 0.1545
1863 | 14649 | 14.649 | -456 | 0.2715
1864 | 14420 | 14.42 | 171 | 0.2765
1865 | 14224 | 14.224 | -707 | 0.4095
1866 | 13995 | 13.995 | -380 | 0.3885
1867 | 13946 | 13.946 | -620 | 0.3565
1868 | 14077 | 14.077 | 131 | 0.25
1869 | 13934 | 13.934 | 109 | 0.3405
1870 | 13909 | 13.909 | 273 | 0.2605
1871 | 14744 | 14.744 | 516 | 0.117
1872 | 14607 | 14.607 | 350 | 0.101
1873 | 14771 | 14.771 | -360 | 0.2075
1874 | 14603 | 14.603 | 430 | 0.0745
1875 | 14586 | 14.586 | 954 | 0.0215
1876 | 14715 | 14.715 | 972 | 0.037
1877 | 14589 | 14.589 | 892 | 0.08
1878 | 14715 | 14.715 | 408 | 0.1545
1879 | 14659 | 14.659 | 556 | 0.367
1880 | 14700 | 14.7 | -400 | 0.298
1881 | 14607 | 14.607 | -748 | 0.282
1882 | 14645 | 14.645 | -242 | 0.319
1883 | 14671 | 14.671 | 969 | 0.3085
1884 | 14654 | 14.654 | -619 | 0.298
1885 | 14530 | 14.53 | 913 | 0.3935
1886 | 14582 | 14.582 | 137 | 0.5955
1887 | 14609 | 14.609 | 49 | 0.7235
1888 | 14570 | 14.57 | -998 | 0.782
1889 | 14576 | 14.576 | 456 | 0.681
1890 | 14674 | 14.674 | 515 | 0.6065
1891 | 14409 | 14.409 | 566 | 0.686
1892 | 14646 | 14.646 | 136 | 0.5905
1893 | 14511 | 14.511 | 214 | 0.5745
1894 | 14655 | 14.655 | -256 | 0.617
1895 | 14730 | 14.73 | 186 | 0.569
1896 | 14480 | 14.48 | 621 | 0.3775
1897 | 14661 | 14.661 | -687 | 0.383
1898 | 14417 | 14.417 | -574 | 0.3935
1899 | 14608 | 14.608 | 462 | 0.436
1900 | 14486 | 14.486 | -949 | 0.42
1901 | 14608 | 14.608 | -409 | 0.367
1902 | 14529 | 14.529 | -99 | 0.3565
1903 | 14608 | 14.608 | 113 | 0.5265
1904 | 14499 | 14.499 | -349 | 0.415
1905 | 14668 | 14.668 | 680 | 0.4575
1906 | 14748 | 14.748 | -907 | 0.58
1907 | 14623 | 14.623 | 981 | 0.5745
1908 | 14621 | 14.621 | 423 | 0.415
1909 | 14658 | 14.658 | -434 | 0.2445
1910 | 14681 | 14.681 | 186 | 0.234
1911 | 14659 | 14.659 | -714 | 0.2555
1912 | 14655 | 14.655 | -276 | 0.3405
1913 | 14269 | 14.269 | -318 | 0.33
1914 | 13831 | 13.831 | -546 | 0.2925
1915 | 14586 | 14.586 | 631 | 0.25
1916 | 14621 | 14.621 | 922 | 0.25
1917 | 14715 | 14.715 | -20 | 0.25
1918 | 14757 | 14.757 | -795 | 0.2715
1919 | 14650 | 14.65 | 264 | 0.2555
1920 | 14902 | 14.902 | -355 | 0.2235
1921 | 14543 | 14.543 | 746 | 0.213
1922 | 14780 | 14.78 | -359 | 0.1595
1923 | 14713 | 14.713 | 585 | 0.2555
1924 | 14925 | 14.925 | 109 | 0.2235
1925 | 14727 | 14.727 | 496 | 0.1385
1926 | 14792 | 14.792 | 936 | 0.197
1927 | 14855 | 14.855 | 393 | 0.186
1928 | 14796 | 14.796 | 634 | 0.2605
1929 | 14713 | 14.713 | -665 | 0.197
1930 | 14618 | 14.618 | 428 | 0.133
1931 | 14841 | 14.841 | 420 | 0.2395
1932 | 14693 | 14.693 | -192 | 0.351
1933 | 14797 | 14.797 | 818 | 0.3885
1934 | 14904 | 14.904 | 262 | 0.319
1935 | 14672 | 14.672 | -393 | 0.3085
1936 | 14705 | 14.705 | -717 | 0.303
1937 | 14739 | 14.739 | -328 | 0.314
1938 | 14681 | 14.681 | 36 | 0.303
1939 | 14790 | 14.79 | 227 | 0.287
1940 | 14530 | 14.53 | -758 | 0.2925
1941 | 14727 | 14.727 | -806 | 0.287
1942 | 14561 | 14.561 | 473 | 0.2235
1943 | 14646 | 14.646 | 358 | 0.2285
1944 | 14578 | 14.578 | 116 | 0.197
1945 | 14509 | 14.509 | -557 | 0.101
1946 | 14527 | 14.527 | 499 | 0.085
1947 | 14676 | 14.676 | -150 | 0.1385
1948 | 14462 | 14.462 | 90 | 0.149
1949 | 14550 | 14.55 | -393 | 0.133
1950 | 14614 | 14.614 | -423 | 0.149
1951 | 14492 | 14.492 | 91 | 0.1595
1952 | 14500 | 14.5 | 777 | 0.165
1953 | 14560 | 14.56 | 334 | 0.165
1954 | 14645 | 14.645 | 816 | 0.17
1955 | 14665 | 14.665 | 659 | 0.1595
1956 | 14458 | 14.458 | 932 | 0.1435
1957 | 14629 | 14.629 | -224 | 0.117
1958 | 14535 | 14.535 | 600 | 0.1435
1959 | 14542 | 14.542 | -810 | 0.2395
1960 | 14561 | 14.561 | 692 | 0.282
1961 | 14268 | 14.268 | 446 | 0.399
1962 | 13840 | 13.84 | -180 | 0.4575
1963 | 13928 | 13.928 | 876 | 0.287
1964 | 14046 | 14.046 | -993 | 0.165
1965 | 14077 | 14.077 | 577 | 0.1385
1966 | 13656 | 13.656 | 771 | 0.1435
1967 | 14591 | 14.591 | 485 | 0.202
1968 | 14630 | 14.63 | 142 | 0.0905
1969 | 14390 | 14.39 | 948 | 0.1115
1970 | 14802 | 14.802 | 362 | 0.1915
1971 | 14599 | 14.599 | 288 | 0.303
1972 | 14624 | 14.624 | 773 | 0.4735
1973 | 14633 | 14.633 | 105 | 0.649
1974 | 14589 | 14.589 | 847 | 0.6595
1975 | 14631 | 14.631 | -829 | 0.9415
1976 | 14736 | 14.736 | -461 | 1.181
1977 | 14627 | 14.627 | -518 | 1.1065
1978 | 14583 | 14.583 | -678 | 1.1115
1979 | 14685 | 14.685 | -92 | 0.9895
1980 | 14701 | 14.701 | 632 | 1.2555
1981 | 14641 | 14.641 | 954 | 1.1385
1982 | 14706 | 14.706 | -440 | 1.016
1983 | 14559 | 14.559 | 712 | 1.2075
1984 | 14832 | 14.832 | 563 | 1.1915
1985 | 14446 | 14.446 | 155 | 1.0055
1986 | 14831 | 14.831 | -535 | 0.8775
1987 | 14636 | 14.636 | 128 | 1.016
1988 | 14703 | 14.703 | 568 | 0.9415
1989 | 14668 | 14.668 | -750 | 0.601
1990 | 14683 | 14.683 | -601 | 0.436
1991 | 14602 | 14.602 | -922 | 0.516
1992 | 14775 | 14.775 | -91 | 0.6595
1993 | 14731 | 14.731 | 433 | 0.9255
1994 | 14601 | 14.601 | 785 | 1.4045
1995 | 14709 | 14.709 | 848 | 1.42
1996 | 14770 | 14.77 | -397 | 1.2925
1997 | 14756 | 14.756 | -632 | 1.3615
1998 | 14764 | 14.764 | 988 | 1.4945
1999 | 14708 | 14.708 | 24 | 1.6065
2000 | 14749 | 14.749 | -47 | 1.67
2001 | 14786 | 14.786 | 584 | 1.553
2002 | 14815 | 14.815 | 219 | 1.564
2003 | 14582 | 14.582 | 473 | 1.532
2004 | 14735 | 14.735 | -836 | 1.787
2005 | 14696 | 14.696 | -544 | 1.867
2006 | 14850 | 14.85 | -557 | 1.7445
2007 | 14641 | 14.641 | -290 | 1.8885
2008 | 14701 | 14.701 | 876 | 2.0425
2009 | 14413 | 14.413 | -658 | 2.3085
2010 | 14345 | 14.345 | 530 | 2.6755
2011 | 14214 | 14.214 | -532 | 2.6115
2012 | 14819 | 14.819 | 130 | 2.3615
2013 | 14693 | 14.693 | 953 | 2.553
2014 | 14820 | 14.82 | -313 | 2.3935
2015 | 14681 | 14.681 | 958 | 2.436
2016 | 14803 | 14.803 | -620 | 2.452
2017 | 14875 | 14.875 | 86 | 2.58
2018 | 14827 | 14.827 | -962 | 2.564
2019 | 14693 | 14.693 | 693 | 2.484
2020 | 14888 | 14.888 | -204 | 2.447
2021 | 14798 | 14.798 | -669 | 2.149
2022 | 14871 | 14.871 | 784 | 1.8775
2023 | 14741 | 14.741 | 170 | 2.287
2024 | 14805 | 14.805 | -2 | 2.1385
2025 | 14815 | 14.815 | 13 | 2.048
2026 | 14812 | 14.812 | 711 | 1.92
2027 | 14764 | 14.764 | 160 | 1.8565
2028 | 14740 | 14.74 | 564 | 1.984
2029 | 14880 | 14.88 | -273 | 2.08
2030 | 14781 | 14.781 | 341 | 1.8245
2031 | 14626 | 14.626 | 70 | 1.532
2032 | 14791 | 14.791 | 299 | 1.713
2033 | 14731 | 14.731 | 855 | 1.0055
2034 | 14773 | 14.773 | -194 | 1.069
2035 | 14599 | 14.599 | 631 | 0.867
2036 | 14099 | 14.099 | -894 | 0.585
2037 | 14597 | 14.597 | -485 | 0.7715
2038 | 14507 | 14.507 | -402 | 0.6065
2039 | 14578 | 14.578 | 405 | 0.383
2040 | 14634 | 14.634 | 597 | 0.4095
2041 | 14678 | 14.678 | 366 | 0.3935
2042 | 14638 | 14.638 | 361 | 0.537
2043 | 14645 | 14.645 | 283 | 0.4785
2044 | 14621 | 14.621 | 524 | 0.463
2045 | 14607 | 14.607 | -762 | 0.548
2046 | 14589 | 14.589 | -448 | 0.6545
2047 | 14721 | 14.721 | 914 | 0.649
2048 | 14694 | 14.694 | 487 | 0.7765
2049 | 14665 | 14.665 | -34 | 0.8615
2050 | 14631 | 14.631 | 119 | 0.8935
2051 | 14681 | 14.681 | -898 | 1.298
2052 | 14647 | 14.647 | -968 | 1.287
2053 | 14680 | 14.68 | 409 | 1.3455
2054 | 14678 | 14.678 | 117 | 0.8725
2055 | 14655 | 14.655 | 765 | 1.734
2056 | 14616 | 14.616 | -158 | 1.8935
2057 | 14425 | 14.425 | -614 | 1.9415
2058 | 13980 | 13.98 | 312 | 2.2715
2059 | 14068 | 14.068 | 872 | 1.5745
2060 | 13999 | 13.999 | 504 | 1.415
2061 | 14008 | 14.008 | 429 | 1.447
2062 | 13910 | 13.91 | 234 | 1.7715
2063 | 14586 | 14.586 | 726 | 1.3565
2064 | 14702 | 14.702 | 512 | 0.984
2065 | 14737 | 14.737 | 405 | 1.1275
2066 | 14629 | 14.629 | -324 | 1.1065
2067 | 14892 | 14.892 | 999 | 1.085
2068 | 14669 | 14.669 | -626 | 0.8565
2069 | 14703 | 14.703 | 400 | 1.213
2070 | 14752 | 14.752 | -961 | 0.883
2071 | 14743 | 14.743 | -394 | 0.702
2072 | 14689 | 14.689 | 227 | 0.452
2073 | 14621 | 14.621 | -209 | 0.4785
2074 | 14707 | 14.707 | -508 | 0.734
2075 | 14751 | 14.751 | 506 | 1.234
2076 | 14891 | 14.891 | -424 | 1.2445
2077 | 14690 | 14.69 | 642 | 0.9735
2078 | 14912 | 14.912 | -730 | 1.351
2079 | 14697 | 14.697 | -166 | 1.2925
2080 | 14824 | 14.824 | 594 | 1.2715
2081 | 14729 | 14.729 | 275 | 1.0905
2082 | 14795 | 14.795 | -340 | 2.0265
2083 | 14606 | 14.606 | -993 | 1.335
2084 | 14571 | 14.571 | -784 | 1.1385
2085 | 14545 | 14.545 | -719 | 1.069
2086 | 14958 | 14.958 | -913 | 0.564
2087 | 14919 | 14.919 | 200 | 0.814
2088 | 14734 | 14.734 | 207 | 0.867
2089 | 14770 | 14.77 | -865 | 0.5215
2090 | 14663 | 14.663 | -413 | 1.032
2091 | 14708 | 14.708 | 816 | 1.0265
2092 | 14597 | 14.597 | -610 | 0.686
2093 | 14397 | 14.397 | 710 | 0.787
2094 | 14486 | 14.486 | 473 | 0.718
2095 | 14693 | 14.693 | 659 | 0.5105
2096 | 14513 | 14.513 | -162 | 0.5905
2097 | 14369 | 14.369 | 230 | 0.8935
2098 | 14629 | 14.629 | 595 | 1.0425
2099 | 14827 | 14.827 | 112 | 1.367
2100 | 14773 | 14.773 | -393 | 1.303
2101 | 14805 | 14.805 | -824 | 1.314
2102 | 14765 | 14.765 | -200 | 3.0955
2103 | 14653 | 14.653 | -409 | 3.2765
2104 | 14669 | 14.669 | -960 | 2.8935
2105 | 14710 | 14.71 | -488 | 2.069
2106 | 14776 | 14.776 | -7 | 2.1545
2107 | 14805 | 14.805 | 933 | 2.3885
2108 | 14686 | 14.686 | -542 | 2.1435
2109 | 14817 | 14.817 | 227 | 2.287
2110 | 14789 | 14.789 | -773 | 1.67
2111 | 14854 | 14.854 | -882 | 1.9415
2112 | 14839 | 14.839 | -953 | 1.484
2113 | 14710 | 14.71 | 23 | 1.4415
2114 | 14989 | 14.989 | 102 | 1.5425
2115 | 14870 | 14.87 | -962 | 1.7075
2116 | 14867 | 14.867 | 841 | 1.782
2117 | 14674 | 14.674 | 594 | 1.553
2118 | 14876 | 14.876 | -529 | 1.1435
2119 | 14312 | 14.312 | -42 | 1.016
2120 | 13910 | 13.91 | 278 | 0.867
2121 | 14728 | 14.728 | 925 | 0.835
2122 | 14884 | 14.884 | 379 | 0.8455
2123 | 14818 | 14.818 | -428 | 0.803
2124 | 14882 | 14.882 | -185 | 0.7075
2125 | 14764 | 14.764 | 921 | 0.665
2126 | 14731 | 14.731 | -962 | 0.5425
2127 | 14788 | 14.788 | 390 | 0.3935
2128 | 14742 | 14.742 | -258 | 0.3935
2129 | 14842 | 14.842 | 332 | 0.351
2130 | 14576 | 14.576 | 372 | 0.335
2131 | 14739 | 14.739 | -195 | 0.314
2132 | 14461 | 14.461 | 863 | 0.314
2133 | 14871 | 14.871 | -560 | 0.2075
2134 | 14634 | 14.634 | -802 | 0.213
2135 | 14649 | 14.649 | -943 | 0.2285
2136 | 14776 | 14.776 | 607 | 0.234
2137 | 14763 | 14.763 | 188 | 0.2765
2138 | 14720 | 14.72 | 513 | 0.234
2139 | 14744 | 14.744 | 938 | 0.2285
2140 | 14636 | 14.636 | -901 | 0.186
2141 | 14750 | 14.75 | -356 | 0.2235
2142 | 14720 | 14.72 | 876 | 0.17
2143 | 14614 | 14.614 | -167 | 0.2605
2144 | 14799 | 14.799 | 459 | 0.319
2145 | 14554 | 14.554 | 263 | 0.431
2146 | 14898 | 14.898 | -917 | 0.3565
2147 | 14723 | 14.723 | -284 | 0.3885
2148 | 14758 | 14.758 | 876 | 0.4945
2149 | 14761 | 14.761 | 190 | 0.537
2150 | 14690 | 14.69 | -824 | 0.649
2151 | 14980 | 14.98 | -382 | 0.702
2152 | 14584 | 14.584 | -142 | 0.8775
2153 | 14569 | 14.569 | -502 | 1.0105
2154 | 13837 | 13.837 | 564 | 0.968
2155 | 14127 | 14.127 | 670 | 0.9785
2156 | 14020 | 14.02 | 165 | 0.8725
2157 | 14345 | 14.345 | -726 | 0.92
2158 | 13578 | 13.578 | 671 | 1.101
2159 | 14666 | 14.666 | 765 | 1.0265
2160 | 14683 | 14.683 | 27 | 1.367
2161 | 14841 | 14.841 | 674 | 1.218
2162 | 14772 | 14.772 | -272 | 1.234
2163 | 14839 | 14.839 | -762 | 1.149
2164 | 14754 | 14.754 | -388 | 0.7925
2165 | 14791 | 14.791 | -796 | 0.782
2166 | 14662 | 14.662 | 300 | 0.8455
2167 | 14808 | 14.808 | 740 | 0.6755
2168 | 14838 | 14.838 | -248 | 0.564
2169 | 14789 | 14.789 | 273 | 0.5955
2170 | 14849 | 14.849 | -788 | 0.649
2171 | 14893 | 14.893 | 76 | 0.819
2172 | 14748 | 14.748 | 238 | 0.9045
2173 | 14857 | 14.857 | -387 | 0.9895
2174 | 12566 | 12.566 | -928 | 0.686
2175 | 10028 | 10.028 | -958 | 0.6385
2176 | 13502 | 13.502 | -8 | 0.3405
2177 | 14247 | 14.247 | -465 | 0.2605
2178 | 14120 | 14.12 | 596 | 0.25
2179 | 14659 | 14.659 | -17 | 0.1435
2180 | 14708 | 14.708 | 359 | 0.08
2181 | 14658 | 14.658 | 689 | 0.0955
2182 | 14698 | 14.698 | 994 | 0.149
2183 | 14655 | 14.655 | -523 | 0.314
2184 | 14671 | 14.671 | 419 | 0.564
2185 | 14617 | 14.617 | 950 | 0.5215
2186 | 14715 | 14.715 | -601 | 0.9415
2187 | 14494 | 14.494 | 292 | 1.1275
2188 | 14769 | 14.769 | -39 | 0.537
2189 | 14591 | 14.591 | -747 | 1.2075
2190 | 14668 | 14.668 | -596 | 2.5215
2191 | 14607 | 14.607 | -275 | 0.931
2192 | 14793 | 14.793 | 805 | 2.351
2193 | 14675 | 14.675 | 821 | 2.4785
2194 | 14556 | 14.556 | -338 | 2.436
2195 | 14710 | 14.71 | -708 | 3.0265
2196 | 14935 | 14.935 | 927 | 2.4735
2197 | 14702 | 14.702 | 118 | 2.9735
2198 | 14679 | 14.679 | -497 | 2.303
2199 | 14687 | 14.687 | 359 | 2.234
2200 | 14522 | 14.522 | -601 | 2.234
2201 | 14540 | 14.54 | -606 | 1.9095
2202 | 13820 | 13.82 | 622 | 1.7555
2203 | 14531 | 14.531 | -246 | 1.5955
2204 | 14714 | 14.714 | 455 | 1.702
2205 | 14861 | 14.861 | 638 | 1.7605
2206 | 14802 | 14.802 | 311 | 2.0055
2207 | 14641 | 14.641 | 44 | 1.947
2208 | 14709 | 14.709 | 424 | 2.218
2209 | 15007 | 15.007 | 11 | 2.2445
2210 | 14842 | 14.842 | 491 | 2.3775
2211 | 14705 | 14.705 | -924 | 2.702
2212 | 14813 | 14.813 | 581 | 2.601
2213 | 14792 | 14.792 | 480 | 2.447
2214 | 14726 | 14.726 | -333 | 2.42
2215 | 14720 | 14.72 | 247 | 1.7765
2216 | 14651 | 14.651 | 920 | 1.6115
2217 | 14810 | 14.81 | 532 | 1.4255
2218 | 14758 | 14.758 | -540 | 1.7555
2219 | 14666 | 14.666 | 619 | 1.2395
2220 | 14826 | 14.826 | 760 | 1.202
2221 | 14714 | 14.714 | -493 | 1.1915
2222 | 14763 | 14.763 | -909 | 1.4095
2223 | 14802 | 14.802 | 17 | 1.314
2224 | 14641 | 14.641 | 956 | 1.1065
2225 | 14775 | 14.775 | 985 | 1.452
2226 | 14725 | 14.725 | -17 | 1.25
2227 | 14545 | 14.545 | -771 | 1.149
2228 | 14720 | 14.72 | 914 | 0.9945
2229 | 14727 | 14.727 | -354 | 1.0215
2230 | 14627 | 14.627 | -914 | 0.9945
2231 | 14763 | 14.763 | 525 | 0.8565
2232 | 14747 | 14.747 | 951 | 0.9735
2233 | 14625 | 14.625 | 91 | 0.798
2234 | 14700 | 14.7 | 777 | 0.686
2235 | 14672 | 14.672 | 601 | 0.67
2236 | 14694 | 14.694 | -848 | 0.6755
2237 | 14678 | 14.678 | 464 | 0.814
2238 | 14831 | 14.831 | -661 | 0.702
2239 | 14629 | 14.629 | -859 | 0.7925
2240 | 14651 | 14.651 | 428 | 0.6275
2241 | 14720 | 14.72 | 364 | 0.697
2242 | 14667 | 14.667 | -907 | 0.7235
2243 | 14588 | 14.588 | 10 | 0.548
2244 | 14681 | 14.681 | -621 | 0.548
2245 | 14811 | 14.811 | 519 | 0.42
2246 | 14689 | 14.689 | -200 | 0.4415
2247 | 14624 | 14.624 | -953 | 0.569
2248 | 14658 | 14.658 | 788 | 0.734
2249 | 14794 | 14.794 | 331 | 0.58
2250 | 14618 | 14.618 | -824 | 0.4735
2251 | 14168 | 14.168 | -475 | 0.484
2252 | 13893 | 13.893 | 73 | 0.3725
2253 | 14097 | 14.097 | -497 | 0.484
2254 | 13948 | 13.948 | 952 | 0.287
2255 | 13929 | 13.929 | 9 | 0.314
2256 | 14059 | 14.059 | -557 | 0.351
2257 | 14582 | 14.582 | -87 | 0.537
2258 | 14647 | 14.647 | -790 | 0.5
2259 | 14599 | 14.599 | -329 | 0.532
2260 | 14795 | 14.795 | 867 | 0.33
2261 | 14720 | 14.72 | -447 | 0.3615
2262 | 14601 | 14.601 | -163 | 0.367
2263 | 14633 | 14.633 | -258 | 0.803
2264 | 14577 | 14.577 | 773 | 0.851
2265 | 14662 | 14.662 | -248 | 0.4785
2266 | 14615 | 14.615 | 43 | 0.702
2267 | 14514 | 14.514 | 685 | 0.5055
2268 | 14793 | 14.793 | -231 | 1.814
2269 | 14645 | 14.645 | -233 | 1.6115
2270 | 14527 | 14.527 | 130 | 1.08
2271 | 14578 | 14.578 | -141 | 1.1275
2272 | 14664 | 14.664 | -140 | 1.447
2273 | 14604 | 14.604 | -136 | 0.915
2274 | 14343 | 14.343 | 386 | 3.037
2275 | 14485 | 14.485 | 237 | 1.936
2276 | 14545 | 14.545 | 699 | 2.0955
2277 | 14569 | 14.569 | -584 | 1.532
2278 | 14507 | 14.507 | 518 | 1.9095
2279 | 14508 | 14.508 | 328 | 1.351
2280 | 14403 | 14.403 | -795 | 1.17
2281 | 14499 | 14.499 | 361 | 1.6755
2282 | 14385 | 14.385 | 17 | 0.8615
2283 | 14447 | 14.447 | 343 | 0.468
2284 | 14448 | 14.448 | 236 | 0.67
2285 | 14520 | 14.52 | 154 | 0.5955
2286 | 14513 | 14.513 | 901 | 0.436
2287 | 14414 | 14.414 | 499 | 0.468
2288 | 14724 | 14.724 | 752 | 0.463
2289 | 14558 | 14.558 | -435 | 0.266
2290 | 14506 | 14.506 | 9 | 0.3775
2291 | 14474 | 14.474 | -350 | 0.3565
2292 | 14551 | 14.551 | 642 | 0.2445
2293 | 14470 | 14.47 | 338 | 0.1115
2294 | 14393 | 14.393 | 596 | 0.186
2295 | 14631 | 14.631 | -898 | 0.202
2296 | 14514 | 14.514 | -85 | 0.1595
2297 | 14485 | 14.485 | -654 | 0.17
2298 | 13872 | 13.872 | 121 | 0.1755
2299 | 14068 | 14.068 | -821 | 0.0585
2300 | 14440 | 14.44 | -570 | 0.0585
2301 | 14576 | 14.576 | 449 | 0.085
2302 | 14722 | 14.722 | 125 | 0.069
2303 | 14600 | 14.6 | -905 | 0.0425
2304 | 14471 | 14.471 | -741 | 0.048
2305 | 14860 | 14.86 | -674 | 0.101
2306 | 14461 | 14.461 | -25 | 0.202
2307 | 14729 | 14.729 | 254 | 0.1385
2308 | 14671 | 14.671 | -354 | 0.1595
2309 | 14541 | 14.541 | 684 | 0.133
2310 | 14360 | 14.36 | -270 | 0.303
2311 | 14675 | 14.675 | -968 | 0.436
2312 | 14442 | 14.442 | -850 | 0.149
2313 | 14573 | 14.573 | 92 | 0.165
2314 | 14667 | 14.667 | -321 | 0.101
2315 | 14529 | 14.529 | 104 | 0.085
2316 | 14572 | 14.572 | -368 | 0.399
2317 | 14618 | 14.618 | 876 | 0.335
2318 | 14576 | 14.576 | 21 | 0.133
2319 | 14568 | 14.568 | 541 | 0.213
2320 | 14530 | 14.53 | 187 | 0.4895
2321 | 14466 | 14.466 | 993 | 0.6545
2322 | 14573 | 14.573 | 61 | 0.3085
2323 | 14529 | 14.529 | 456 | 0.452
2324 | 14470 | 14.47 | -891 | 0.2555
2325 | 14534 | 14.534 | -147 | 0.314
2326 | 14539 | 14.539 | -924 | 0.5215
2327 | 14543 | 14.543 | 0 | 0.2285
2328 | 14410 | 14.41 | -929 | 0.42
2329 | 14435 | 14.435 | -89 | 0.569
2330 | 14590 | 14.59 | 902 | 0.351
2331 | 14262 | 14.262 | -441 | 0.2395
2332 | 14648 | 14.648 | 210 | 0.17
2333 | 14374 | 14.374 | -574 | 0.218
2334 | 14497 | 14.497 | 570 | 0.149
2335 | 14378 | 14.378 | -535 | 0.1275
2336 | 14497 | 14.497 | 280 | 0.197
2337 | 14528 | 14.528 | -543 | 0.287
2338 | 14361 | 14.361 | 516 | 0.282
2339 | 14524 | 14.524 | -874 | 0.186
2340 | 14561 | 14.561 | 91 | 0.1225
2341 | 14408 | 14.408 | -639 | 0.117
2342 | 14708 | 14.708 | 433 | 0.149
2343 | 14570 | 14.57 | 66 | 0.33
2344 | 14665 | 14.665 | -687 | 0.4045
2345 | 14291 | 14.291 | 600 | 0.3405
2346 | 13851 | 13.851 | 74 | 0.4095
2347 | 13918 | 13.918 | -496 | 0.4095
2348 | 14011 | 14.011 | 969 | 0.4045
2349 | 13979 | 13.979 | 130 | 0.431
2350 | 13587 | 13.587 | 919 | 0.42
2351 | 14429 | 14.429 | 832 | 0.3405
2352 | 14553 | 14.553 | 567 | 0.4735
2353 | 14698 | 14.698 | -166 | 0.6225
2354 | 14691 | 14.691 | 956 | 0.4945
2355 | 14622 | 14.622 | 363 | 0.6385
2356 | 14578 | 14.578 | -286 | 0.931
2357 | 14575 | 14.575 | -910 | 0.968
2358 | 14785 | 14.785 | 246 | 0.835
2359 | 14578 | 14.578 | 189 | 0.8775
2360 | 14581 | 14.581 | -866 | 0.633
2361 | 14595 | 14.595 | 637 | 0.6595
2362 | 14699 | 14.699 | -971 | 0.548
2363 | 14596 | 14.596 | 826 | 0.665
2364 | 14659 | 14.659 | -29 | 0.67
2365 | 14610 | 14.61 | 770 | 0.713
2366 | 14616 | 14.616 | -869 | 0.6385
2367 | 14712 | 14.712 | 138 | 0.553
2368 | 14704 | 14.704 | 912 | 0.9255
2369 | 14616 | 14.616 | -269 | 0.947
2370 | 14565 | 14.565 | -577 | 1.9095
2371 | 14533 | 14.533 | 735 | 1.734
2372 | 14707 | 14.707 | 322 | 0.9945
2373 | 14582 | 14.582 | 977 | 0.8615
2374 | 14800 | 14.8 | -646 | 1.1065
2375 | 14709 | 14.709 | 220 | 1.298
2376 | 14646 | 14.646 | 595 | 1.4415
2377 | 14658 | 14.658 | 60 | 1.298
2378 | 14473 | 14.473 | -268 | 1.3615
2379 | 14537 | 14.537 | -873 | 1.2445
2380 | 14560 | 14.56 | -946 | 1.463
2381 | 14687 | 14.687 | -138 | 1.298
2382 | 14453 | 14.453 | 977 | 1.516
2383 | 14377 | 14.377 | 731 | 1.782
2384 | 14708 | 14.708 | -939 | 1.537
2385 | 14455 | 14.455 | 599 | 1.314
2386 | 14504 | 14.504 | -344 | 1.2765
2387 | 14558 | 14.558 | 128 | 1.835
2388 | 14579 | 14.579 | 984 | 1.468
2389 | 14514 | 14.514 | 510 | 1.303
2390 | 14616 | 14.616 | -781 | 1.3615
2391 | 14541 | 14.541 | -916 | 1.0955
2392 | 14599 | 14.599 | -978 | 2.3405
2393 | 14569 | 14.569 | -969 | 4.5425
2394 | 14499 | 14.499 | -597 | 4.947
2395 | 13678 | 13.678 | 925 | 4.6435
2396 | 14235 | 14.235 | 622 | 4.9045
2397 | 14542 | 14.542 | 739 | 4.92
2398 | 14494 | 14.494 | -521 | 4.452
2399 | 14576 | 14.576 | -174 | 4.6755
2400 | 14618 | 14.618 | -550 | 4.803
2401 | 14514 | 14.514 | 842 | 4.4785
2402 | 14523 | 14.523 | -515 | 3.7925
2403 | 14517 | 14.517 | -722 | 2.665
2404 | 14694 | 14.694 | -287 | 2.319
2405 | 14490 | 14.49 | -967 | 2.282
2406 | 14687 | 14.687 | -748 | 2.053
2407 | 14512 | 14.512 | -24 | 2.766
2408 | 14606 | 14.606 | 289 | 3.33
2409 | 14409 | 14.409 | 830 | 2.553
2410 | 14521 | 14.521 | -438 | 2.3405
2411 | 14493 | 14.493 | 399 | 2.1275
2412 | 14418 | 14.418 | -664 | 1.713
2413 | 14387 | 14.387 | -616 | 1.5265
2414 | 14441 | 14.441 | -947 | 1.5585
2415 | 14371 | 14.371 | -537 | 1.0265
2416 | 14403 | 14.403 | 351 | 0.9895
2417 | 14415 | 14.415 | 616 | 0.601
2418 | 14435 | 14.435 | 710 | 0.3405
2419 | 14371 | 14.371 | 898 | 0.197
2420 | 14474 | 14.474 | -244 | 0.3085
2421 | 14463 | 14.463 | -784 | 0.165
2422 | 14316 | 14.316 | -693 | 0.303
2423 | 14525 | 14.525 | 375 | 0.213
2424 | 14508 | 14.508 | -290 | 0.58
2425 | 14426 | 14.426 | -942 | 0.681
2426 | 14524 | 14.524 | 115 | 0.5905
2427 | 14349 | 14.349 | 907 | 0.537
2428 | 14637 | 14.637 | -812 | 0.7445
2429 | 14450 | 14.45 | 618 | 1.0105
2430 | 14495 | 14.495 | 25 | 0.899
2431 | 14385 | 14.385 | 52 | 0.8405
2432 | 14474 | 14.474 | -29 | 0.718
2433 | 14269 | 14.269 | 17 | 1.032
2434 | 14614 | 14.614 | 251 | 1.234
2435 | 14518 | 14.518 | 898 | 1.42
2436 | 14447 | 14.447 | -375 | 1.4735
2437 | 14477 | 14.477 | 607 | 1.7605
2438 | 14472 | 14.472 | 139 | 2.3775
2439 | 14604 | 14.604 | -590 | 2.819
2440 | 14408 | 14.408 | -979 | 2.782
2441 | 14041 | 14.041 | -68 | 2.968
2442 | 13683 | 13.683 | 509 | 2.5585
2443 | 13889 | 13.889 | 961 | 2.484
2444 | 13852 | 13.852 | 806 | 2.67
2445 | 13970 | 13.97 | 547 | 2.4045
2446 | 13705 | 13.705 | 495 | 2.963
2447 | 14359 | 14.359 | 541 | 3.33
2448 | 14551 | 14.551 | 222 | 3.686
2449 | 14557 | 14.557 | -712 | 3.8405
2450 | 14411 | 14.411 | -514 | 4.314
2451 | 14471 | 14.471 | -117 | 4.585
2452 | 14438 | 14.438 | -420 | 4.303
2453 | 14545 | 14.545 | 525 | 4.3245
2454 | 14499 | 14.499 | -826 | 4.165
2455 | 14541 | 14.541 | -312 | 3.8565
2456 | 14535 | 14.535 | -361 | 3.9415
2457 | 14459 | 14.459 | 514 | 3.9095
2458 | 14583 | 14.583 | 694 | 3.9575
2459 | 14649 | 14.649 | 305 | 4.133
2460 | 14623 | 14.623 | 758 | 3.9785
2461 | 14594 | 14.594 | 258 | 3.8245
2462 | 14536 | 14.536 | 1 | 3.6435
2463 | 14643 | 14.643 | 853 | 4.1225
2464 | 14635 | 14.635 | -771 | 4.303
2465 | 14728 | 14.728 | 189 | 4.218
2466 | 14624 | 14.624 | -191 | 4
2467 | 14654 | 14.654 | 212 | 3.984
2468 | 14511 | 14.511 | -456 | 4.069
2469 | 14803 | 14.803 | -364 | 4.048
2470 | 14686 | 14.686 | -958 | 4.2075
2471 | 14510 | 14.51 | -110 | 3.8615
2472 | 14577 | 14.577 | -230 | 3.782
2473 | 14779 | 14.779 | 601 | 3.867
2474 | 14576 | 14.576 | -993 | 4.633
2475 | 14695 | 14.695 | -69 | 4.697
2476 | 14482 | 14.482 | -579 | 4.798
2477 | 14611 | 14.611 | -973 | 4.5425
2478 | 14582 | 14.582 | -336 | 4.415
2479 | 14643 | 14.643 | 266 | 3.9255
2480 | 14640 | 14.64 | -652 | 3.016
2481 | 14569 | 14.569 | -898 | 2.734
2482 | 14540 | 14.54 | 482 | 3.4045
2483 | 14704 | 14.704 | 461 | 4.282
2484 | 14699 | 14.699 | 158 | 3.7395
2485 | 14595 | 14.595 | -699 | 2.2765
2486 | 14668 | 14.668 | 352 | 2.665
2487 | 14661 | 14.661 | 808 | 3.5215
2488 | 14157 | 14.157 | -116 | 4.149
2489 | 14077 | 14.077 | -986 | 4.452
2490 | 14791 | 14.791 | 187 | 3.032
2491 | 14650 | 14.65 | -406 | 2.7605
2492 | 14723 | 14.723 | -631 | 1.202
2493 | 14859 | 14.859 | 378 | 3.447
2494 | 14661 | 14.661 | 808 | 4.1755
2495 | 14686 | 14.686 | -811 | 3.399
2496 | 14852 | 14.852 | -753 | 3.5055
2497 | 14763 | 14.763 | 987 | 2.7925
2498 | 14765 | 14.765 | 297 | 3.3405
2499 | 14763 | 14.763 | -8 | 3.1915
2500 | 14790 | 14.79 | 127 | 2.1595
2501 | 14772 | 14.772 | 198 | 2.686
2502 | 14780 | 14.78 | -74 | 4.3405
2503 | 14848 | 14.848 | -320 | 3.851
2504 | 14636 | 14.636 | 950 | 3.8085
2505 | 14820 | 14.82 | 149 | 3.431
2506 | 14830 | 14.83 | -59 | 3.069
2507 | 14870 | 14.87 | -191 | 3.2605
2508 | 14650 | 14.65 | -253 | 2.367
2509 | 14796 | 14.796 | -406 | 2.218
2510 | 14576 | 14.576 | 407 | 3.899
2511 | 14750 | 14.75 | -303 | 3.351
2512 | 14818 | 14.818 | -334 | 3.3885
2513 | 14767 | 14.767 | -699 | 2.9045
2514 | 14655 | 14.655 | 187 | 2.3885
2515 | 14716 | 14.716 | -58 | 0.58
2516 | 14663 | 14.663 | -691 | 1.835
2517 | 14775 | 14.775 | 868 | 4.5265
2518 | 14665 | 14.665 | 600 | 1.6065
2519 | 14655 | 14.655 | -263 | 3.2445
2520 | 14637 | 14.637 | 201 | 1.2285
2521 | 14677 | 14.677 | 642 | 1.6115
2522 | 14727 | 14.727 | 228 | 4.5905
2523 | 14556 | 14.556 | 824 | 4.963
2524 | 14652 | 14.652 | 728 | 4.819
2525 | 14581 | 14.581 | -751 | 4.617
2526 | 14519 | 14.519 | -160 | 4.9785
2527 | 14615 | 14.615 | -560 | 4.9575
2528 | 14348 | 14.348 | 739 | 4.947
2529 | 14642 | 14.642 | -36 | 4.8405
2530 | 14492 | 14.492 | 775 | 4.0215
2531 | 14690 | 14.69 | 398 | 3.67
2532 | 14627 | 14.627 | 106 | 4.319
2533 | 14545 | 14.545 | -895 | 3.851
2534 | 14563 | 14.563 | 630 | 3.484
2535 | 14715 | 14.715 | 320 | 3.0585
2536 | 14421 | 14.421 | 229 | 3.25
2537 | 14826 | 14.826 | -241 | 2.2605
2538 | 14383 | 14.383 | 576 | 3.0745
2539 | 13831 | 13.831 | -152 | 3.75
2540 | 14027 | 14.027 | 864 | 2.0585
2541 | 14006 | 14.006 | -563 | 2.7555
2542 | 14044 | 14.044 | 990 | 3.218
2543 | 13435 | 13.435 | 806 | 2.2445
2544 | 14594 | 14.594 | -207 | 1.5215
2545 | 14705 | 14.705 | -299 | 0.9415
2546 | 14556 | 14.556 | 36 | 2.5
2547 | 14604 | 14.604 | 669 | 2.1915
2548 | 14887 | 14.887 | 578 | 1.2925
2549 | 14688 | 14.688 | 695 | 1.4785
2550 | 14736 | 14.736 | 690 | 2.3405
2551 | 14638 | 14.638 | -884 | 2.165
2552 | 14720 | 14.72 | 395 | 1.33
2553 | 14713 | 14.713 | -816 | 1.0215
2554 | 14636 | 14.636 | -120 | 0.9415
2555 | 14669 | 14.669 | 656 | 0.718
2556 | 14629 | 14.629 | -595 | 0.314
2557 | 14484 | 14.484 | 988 | 0.133
2558 | 14505 | 14.505 | 740 | 0.0585
2559 | 14582 | 14.582 | 354 | 0.0055
2560 | 14441 | 14.441 | -333 | 0
2561 | 14416 | 14.416 | -594 | 0.064
2562 | 14337 | 14.337 | 730 | 0.1435
2563 | 14548 | 14.548 | -337 | 0.101
2564 | 14435 | 14.435 | 633 | 0.2555
2565 | 14577 | 14.577 | -923 | 0.181
2566 | 14368 | 14.368 | -719 | 0.218
2567 | 14436 | 14.436 | 136 | 0.218
2568 | 14617 | 14.617 | -303 | 0.2285
2569 | 14577 | 14.577 | -20 | 0.1915
2570 | 14531 | 14.531 | -884 | 0.3615
2571 | 14619 | 14.619 | 1000 | 0.5265
2572 | 14495 | 14.495 | 307 | 0.436
2573 | 14760 | 14.76 | 373 | 0.537
2574 | 14622 | 14.622 | -526 | 0.83
2575 | 14548 | 14.548 | -428 | 1.1225
2576 | 14681 | 14.681 | -131 | 1.0905
2577 | 14407 | 14.407 | -966 | 1.3885
2578 | 14707 | 14.707 | -891 | 1.383
2579 | 14568 | 14.568 | -30 | 1.314
2580 | 14685 | 14.685 | 99 | 1.6755
2581 | 14689 | 14.689 | -44 | 1.8565
2582 | 14658 | 14.658 | 318 | 2.4045
2583 | 14751 | 14.751 | 853 | 2.681
2584 | 14622 | 14.622 | 97 | 3.165
2585 | 14578 | 14.578 | -811 | 3.2925
2586 | 14063 | 14.063 | -351 | 3.6435
2587 | 13895 | 13.895 | -755 | 3.75
2588 | 14702 | 14.702 | -130 | 3.287
2589 | 14645 | 14.645 | -240 | 3.1545
2590 | 14602 | 14.602 | -143 | 3.42
2591 | 14954 | 14.954 | -114 | 3.8245
2592 | 14484 | 14.484 | -356 | 4
2593 | 14716 | 14.716 | -326 | 4.218
2594 | 14737 | 14.737 | 45 | 3.9045
2595 | 14837 | 14.837 | 184 | 4.149
2596 | 14652 | 14.652 | 691 | 4.213
2597 | 14759 | 14.759 | -424 | 3.8935
2598 | 14689 | 14.689 | 354 | 4.2075
2599 | 14635 | 14.635 | 475 | 3.633
2600 | 14776 | 14.776 | 86 | 3.351
2601 | 14882 | 14.882 | -93 | 3.6545
2602 | 14598 | 14.598 | 293 | 3.5425
2603 | 14761 | 14.761 | -198 | 3.4255
2604 | 14780 | 14.78 | -632 | 3.6755
2605 | 14692 | 14.692 | 901 | 3.7075
2606 | 14664 | 14.664 | -472 | 3.5745
2607 | 14831 | 14.831 | 376 | 3.266
2608 | 14694 | 14.694 | -320 | 3.3615
2609 | 14817 | 14.817 | 382 | 3.032
2610 | 14599 | 14.599 | 564 | 2.798
2611 | 14892 | 14.892 | -289 | 2.713
2612 | 14760 | 14.76 | 547 | 3.064
2613 | 14638 | 14.638 | 549 | 2.8935
2614 | 14736 | 14.736 | -489 | 3.5905
2615 | 14766 | 14.766 | 475 | 4.0745
2616 | 14754 | 14.754 | -228 | 4.1275
2617 | 14511 | 14.511 | -466 | 3.3935
2618 | 14557 | 14.557 | -751 | 4.0585
2619 | 14562 | 14.562 | -625 | 4.4895
2620 | 14793 | 14.793 | -793 | 3.803
2621 | 14611 | 14.611 | -436 | 4.3085
2622 | 14808 | 14.808 | -398 | 4.17
2623 | 14536 | 14.536 | 176 | 4.032
2624 | 14904 | 14.904 | -201 | 3.6435
2625 | 14669 | 14.669 | -686 | 4.1225
2626 | 14659 | 14.659 | -683 | 4.601
2627 | 14813 | 14.813 | 620 | 4.867
2628 | 14696 | 14.696 | 380 | 4.548
2629 | 14802 | 14.802 | 429 | 4.782
2630 | 14810 | 14.81 | 245 | 4.782
2631 | 14702 | 14.702 | 907 | 4.814
2632 | 14730 | 14.73 | -180 | 4.867
2633 | 14813 | 14.813 | 538 | 4.8885
2634 | 14790 | 14.79 | -437 | 4.931
2635 | 14661 | 14.661 | 875 | 4.9045
2636 | 14428 | 14.428 | -772 | 4.8565
2637 | 13823 | 13.823 | 965 | 4.718
2638 | 14127 | 14.127 | -139 | 4.569
2639 | 14153 | 14.153 | 212 | 4.867
2640 | 13896 | 13.896 | -270 | 4.537
2641 | 13929 | 13.929 | 274 | 4.4415
2642 | 14726 | 14.726 | 578 | 4.282
2643 | 14715 | 14.715 | -604 | 4.2235
2644 | 14731 | 14.731 | 336 | 4.1385
2645 | 14738 | 14.738 | 866 | 3.83
2646 | 14545 | 14.545 | 755 | 3.782
2647 | 14770 | 14.77 | 495 | 3.266
2648 | 14748 | 14.748 | -90 | 2.3245
2649 | 14843 | 14.843 | -452 | 1.3935
2650 | 14594 | 14.594 | 816 | 1.383
2651 | 14659 | 14.659 | -793 | 0.718
2652 | 14767 | 14.767 | -486 | 0.5055
2653 | 14669 | 14.669 | -637 | 0.8885
2654 | 14750 | 14.75 | -407 | 1.0055
2655 | 14639 | 14.639 | 337 | 0.9255
2656 | 14572 | 14.572 | -717 | 1.032
2657 | 14634 | 14.634 | 345 | 0.8615
2658 | 14547 | 14.547 | -410 | 0.984
2659 | 14601 | 14.601 | 140 | 1.0105
2660 | 14460 | 14.46 | 32 | 1.0905
2661 | 14565 | 14.565 | 105 | 2
2662 | 14873 | 14.873 | -112 | 2.213
2663 | 14592 | 14.592 | -512 | 2.1115
2664 | 14727 | 14.727 | -393 | 3.053
2665 | 14666 | 14.666 | -729 | 3.2925
2666 | 14700 | 14.7 | -328 | 2.984
2667 | 14705 | 14.705 | -498 | 3.67
2668 | 14571 | 14.571 | -337 | 3.7555
2669 | 14717 | 14.717 | 774 | 2.9255
2670 | 14677 | 14.677 | 283 | 3.5
2671 | 14794 | 14.794 | 338 | 4.75
2672 | 14808 | 14.808 | -595 | 4.7715
2673 | 14792 | 14.792 | -646 | 4.7765
2674 | 14678 | 14.678 | -169 | 4.8085
2675 | 14641 | 14.641 | 912 | 3.7925
2676 | 14891 | 14.891 | -451 | 4.1435
2677 | 14756 | 14.756 | 817 | 4.564
2678 | 14833 | 14.833 | 452 | 4.08
2679 | 14793 | 14.793 | 800 | 4.085
2680 | 14812 | 14.812 | 660 | 3.213
2681 | 14825 | 14.825 | 958 | 3.4735
2682 | 14630 | 14.63 | -137 | 2.7285
2683 | 14022 | 14.022 | -445 | 2.7765
2684 | 14264 | 14.264 | -248 | 2.7555
2685 | 14514 | 14.514 | 717 | 3.0955
2686 | 14925 | 14.925 | -381 | 2.6915
2687 | 14826 | 14.826 | -722 | 2.2235
2688 | 14796 | 14.796 | 724 | 1.58
2689 | 14678 | 14.678 | -608 | 2.1915
2690 | 14858 | 14.858 | -777 | 2.0215
2691 | 14657 | 14.657 | 488 | 2.1275
2692 | 14954 | 14.954 | -224 | 2.5745
2693 | 14779 | 14.779 | -717 | 2.484
2694 | 14572 | 14.572 | -552 | 2.5055
2695 | 14944 | 14.944 | -271 | 2.5955
2696 | 14864 | 14.864 | -992 | 2.186
2697 | 14833 | 14.833 | 850 | 2.1065
2698 | 14829 | 14.829 | 275 | 2.516
2699 | 14939 | 14.939 | -415 | 3.048
2700 | 14709 | 14.709 | 88 | 2.9945
2701 | 14933 | 14.933 | 410 | 3
2702 | 14782 | 14.782 | -506 | 2.4785
2703 | 14923 | 14.923 | -298 | 2.42
2704 | 14729 | 14.729 | 596 | 3.069
2705 | 14880 | 14.88 | -649 | 3.0055
2706 | 14890 | 14.89 | 69 | 2.734
2707 | 14774 | 14.774 | 160 | 2.383
2708 | 14891 | 14.891 | 987 | 2.5585
2709 | 14875 | 14.875 | 408 | 3.0905
2710 | 14866 | 14.866 | 883 | 2.149
2711 | 14820 | 14.82 | -144 | 3.1595
2712 | 14805 | 14.805 | 813 | 2.9045
2713 | 14959 | 14.959 | -1 | 2.3885
2714 | 14838 | 14.838 | 519 | 2.8565
2715 | 14909 | 14.909 | 528 | 3.6915
2716 | 14849 | 14.849 | -892 | 3.8245
2717 | 14807 | 14.807 | 419 | 3.0745
2718 | 14788 | 14.788 | -292 | 2.6545
2719 | 14854 | 14.854 | -42 | 1.6595
2720 | 14791 | 14.791 | -886 | 2.2445
2721 | 14799 | 14.799 | -369 | 1.553
2722 | 14846 | 14.846 | 25 | 1.83
2723 | 14845 | 14.845 | 853 | 1.335
2724 | 14624 | 14.624 | -452 | 1.2555
2725 | 14839 | 14.839 | -922 | 0.9735
2726 | 14679 | 14.679 | 647 | 1.9255
2727 | 14648 | 14.648 | -335 | 1.9095
2728 | 14571 | 14.571 | 966 | 2.7395
2729 | 14712 | 14.712 | 651 | 2.213
2730 | 14544 | 14.544 | 836 | 1.6065
2731 | 14673 | 14.673 | -503 | 1.649
2732 | 14494 | 14.494 | -868 | 0.9575
2733 | 14146 | 14.146 | -803 | 0.867
2734 | 13934 | 13.934 | 54 | 0.9575
2735 | 13915 | 13.915 | -727 | 1.415
2736 | 14130 | 14.13 | -79 | 1.0425
2737 | 13802 | 13.802 | 490 | 0.9095
2738 | 14151 | 14.151 | -932 | 1.2445
2739 | 14558 | 14.558 | 139 | 1.048
2740 | 14820 | 14.82 | 403 | 1.1915
2741 | 14586 | 14.586 | -478 | 1.5745
2742 | 14865 | 14.865 | -630 | 2
2743 | 14523 | 14.523 | -653 | 2.2075
2744 | 14632 | 14.632 | -263 | 2.6435
2745 | 14743 | 14.743 | 168 | 2.42
2746 | 14738 | 14.738 | -280 | 2.7605
2747 | 14707 | 14.707 | -742 | 2.8615
2748 | 14706 | 14.706 | 669 | 2.931
2749 | 14464 | 14.464 | -658 | 2.734
2750 | 14701 | 14.701 | -534 | 3.4785
2751 | 14695 | 14.695 | -346 | 4.1545
2752 | 14558 | 14.558 | 70 | 3.9045
2753 | 14516 | 14.516 | 405 | 4.1385
2754 | 14617 | 14.617 | -355 | 3.968
2755 | 14535 | 14.535 | -336 | 3.436
2756 | 14597 | 14.597 | -897 | 2.6755
2757 | 14617 | 14.617 | -942 | 3.367
2758 | 14454 | 14.454 | 379 | 2.7605
2759 | 14573 | 14.573 | 987 | 2.4785
2760 | 14534 | 14.534 | 407 | 3.463
2761 | 14599 | 14.599 | 106 | 2.936
2762 | 14516 | 14.516 | 739 | 3.431
2763 | 14332 | 14.332 | 965 | 2.7445
2764 | 14483 | 14.483 | -167 | 2.569
2765 | 14538 | 14.538 | -15 | 2.383
2766 | 14504 | 14.504 | 981 | 2.186
2767 | 14337 | 14.337 | 249 | 2.2235
2768 | 14494 | 14.494 | -298 | 2.2285
2769 | 14541 | 14.541 | 619 | 2.016
2770 | 14508 | 14.508 | -654 | 2.1755
2771 | 14399 | 14.399 | 193 | 2.1435
2772 | 14542 | 14.542 | 21 | 1.649
2773 | 14628 | 14.628 | 881 | 2.1115
2774 | 14502 | 14.502 | -810 | 2.468
2775 | 14548 | 14.548 | 870 | 2.9255
2776 | 14484 | 14.484 | 608 | 3.016
2777 | 14619 | 14.619 | -353 | 2.8935
2778 | 13982 | 13.982 | 778 | 2.883
2779 | 13836 | 13.836 | -997 | 3.0425
2780 | 14649 | 14.649 | 479 | 2.803
2781 | 14697 | 14.697 | -409 | 2.213
2782 | 14571 | 14.571 | -320 | 2.915
2783 | 14814 | 14.814 | -513 | 2.734
2784 | 14850 | 14.85 | -237 | 3.5215
2785 | 14874 | 14.874 | 626 | 3.8455
2786 | 14752 | 14.752 | 596 | 2.9255
2787 | 14964 | 14.964 | 29 | 3.5955
2788 | 14593 | 14.593 | 677 | 2.835
2789 | 14928 | 14.928 | -435 | 2.6915
2790 | 14929 | 14.929 | -247 | 3.835
2791 | 14777 | 14.777 | -885 | 4.4045
2792 | 14869 | 14.869 | 288 | 4.5955
2793 | 14755 | 14.755 | 167 | 4.8245
2794 | 14857 | 14.857 | 93 | 4.7555
2795 | 14923 | 14.923 | -25 | 4.7395
2796 | 14677 | 14.677 | -139 | 4.713
2797 | 14755 | 14.755 | 164 | 4.2445
2798 | 14920 | 14.92 | -145 | 4.5425
2799 | 14882 | 14.882 | -916 | 4.968
2800 | 14868 | 14.868 | 310 | 4.9735
2801 | 14769 | 14.769 | 270 | 4.9735
2802 | 14768 | 14.768 | 176 | 4.968
2803 | 14712 | 14.712 | 140 | 4.9735
2804 | 14681 | 14.681 | -852 | 4.9735
2805 | 14845 | 14.845 | -854 | 4.963
2806 | 14700 | 14.7 | -581 | 2.3245
2807 | 14650 | 14.65 | -603 | 4.25
2808 | 14736 | 14.736 | 364 | 3.25
2809 | 14699 | 14.699 | -581 | 3.75
2810 | 14529 | 14.529 | -95 | 0.6275
2811 | 14701 | 14.701 | -88 | 2.9575
2812 | 14815 | 14.815 | -138 | 4.984
2813 | 14749 | 14.749 | 592 | 4.9785
2814 | 14640 | 14.64 | 789 | 4.9785
2815 | 14673 | 14.673 | -633 | 4.9785
2816 | 14771 | 14.771 | 305 | 4.9785
2817 | 14709 | 14.709 | 351 | 4.968
2818 | 14784 | 14.784 | -899 | 4.968
2819 | 14585 | 14.585 | 97 | 4.7605
2820 | 14675 | 14.675 | 710 | 4.6595
2821 | 14866 | 14.866 | -507 | 4.537
2822 | 14821 | 14.821 | -757 | 4.0585
2823 | 14857 | 14.857 | -660 | 3.5425
2824 | 14702 | 14.702 | 28 | 2.7715
2825 | 14612 | 14.612 | 411 | 2.6755
2826 | 14285 | 14.285 | 39 | 2.282
2827 | 14080 | 14.08 | -365 | 1.7555
2828 | 14244 | 14.244 | 921 | 1.734
2829 | 14207 | 14.207 | 127 | 2.298
2830 | 14042 | 14.042 | 773 | 2.117
2831 | 14295 | 14.295 | -240 | 1.83
2832 | 14807 | 14.807 | -904 | 1.1385
2833 | 14816 | 14.816 | 846 | 1.0585
2834 | 14745 | 14.745 | -656 | 0.9045
2835 | 14845 | 14.845 | 385 | 0.952
2836 | 14701 | 14.701 | -573 | 0.92
2837 | 14805 | 14.805 | 745 | 0.649
2838 | 14901 | 14.901 | -826 | 0.6915
2839 | 14702 | 14.702 | -490 | 0.5105
2840 | 14796 | 14.796 | -484 | 0.463
2841 | 14826 | 14.826 | -824 | 0.484
2842 | 14751 | 14.751 | -130 | 0.585
2843 | 14796 | 14.796 | 295 | 0.601
2844 | 14863 | 14.863 | 690 | 0.7285
2845 | 14705 | 14.705 | -358 | 0.468
2846 | 14692 | 14.692 | 884 | 0.2555
2847 | 14749 | 14.749 | 511 | 0.202
2848 | 14671 | 14.671 | -138 | 0.101
2849 | 14746 | 14.746 | 329 | 0.2395
2850 | 14754 | 14.754 | -441 | 0.303
2851 | 14743 | 14.743 | -583 | 0.2235
2852 | 14682 | 14.682 | -225 | 0.4045
2853 | 14739 | 14.739 | 786 | 0.3885
2854 | 14718 | 14.718 | -652 | 0.399
2855 | 14814 | 14.814 | -47 | 0.2395
2856 | 14621 | 14.621 | -287 | 0.3455
2857 | 14677 | 14.677 | -128 | 0.5215
2858 | 14679 | 14.679 | -438 | 1.069
2859 | 14809 | 14.809 | 97 | 3.7715
2860 | 14724 | 14.724 | -858 | 2.2765
2861 | 14814 | 14.814 | -291 | 3.1915
2862 | 14616 | 14.616 | -591 | 1.1755
2863 | 14809 | 14.809 | 183 | 0.2555
2864 | 14647 | 14.647 | 976 | 0.3615
2865 | 14697 | 14.697 | 351 | 0.7765
2866 | 14913 | 14.913 | 678 | 1.5105
2867 | 14694 | 14.694 | -379 | 1.734
2868 | 14537 | 14.537 | -61 | 2
2869 | 14865 | 14.865 | -520 | 1.814
2870 | 14798 | 14.798 | 795 | 1.585
2871 | 14645 | 14.645 | 784 | 1.0905
2872 | 14813 | 14.813 | -26 | 2.032
2873 | 14717 | 14.717 | -992 | 2.0905
2874 | 14574 | 14.574 | 704 | 1.569
2875 | 13826 | 13.826 | -562 | 1.67
2876 | 14467 | 14.467 | -88 | 1.8245
2877 | 14729 | 14.729 | -825 | 1.936
2878 | 14660 | 14.66 | 675 | 2.197
2879 | 14789 | 14.789 | 829 | 1.9575
2880 | 14708 | 14.708 | 183 | 2.1545
2881 | 14732 | 14.732 | -360 | 2.4095
2882 | 14729 | 14.729 | -794 | 2.0905
2883 | 14570 | 14.57 | 642 | 2.1115
2884 | 14676 | 14.676 | -110 | 2.5905
2885 | 14480 | 14.48 | -71 | 2.4945
2886 | 14772 | 14.772 | 156 | 2.75
2887 | 14720 | 14.72 | 585 | 2.234
2888 | 14743 | 14.743 | -883 | 2.4095
2889 | 14572 | 14.572 | 569 | 2.3615
2890 | 14504 | 14.504 | 626 | 2.0265
2891 | 14822 | 14.822 | 307 | 1.287
2892 | 14639 | 14.639 | -638 | 2.1225
2893 | 14723 | 14.723 | 258 | 1.6225
2894 | 14656 | 14.656 | 486 | 1.8245
2895 | 14739 | 14.739 | 348 | 1.6115
2896 | 14709 | 14.709 | 394 | 1.42
2897 | 14782 | 14.782 | -705 | 1.149
2898 | 14642 | 14.642 | -43 | 1.0265
2899 | 14808 | 14.808 | -244 | 1.0055
2900 | 14564 | 14.564 | 199 | 1.0425
2901 | 14676 | 14.676 | 137 | 1.0105
2902 | 14697 | 14.697 | 70 | 1.1755
2903 | 14825 | 14.825 | 448 | 1.1595
2904 | 14717 | 14.717 | 871 | 0.952
2905 | 14554 | 14.554 | -460 | 0.83
2906 | 14755 | 14.755 | -113 | 0.681
2907 | 14586 | 14.586 | 304 | 0.867
2908 | 14670 | 14.67 | -885 | 0.564
2909 | 14638 | 14.638 | 437 | 0.6385
2910 | 14694 | 14.694 | 711 | 0.484
2911 | 14701 | 14.701 | -345 | 0.2555
2912 | 14685 | 14.685 | -367 | 0.25
2913 | 14707 | 14.707 | -867 | 0.3085
2914 | 14754 | 14.754 | 931 | 0.463
2915 | 14580 | 14.58 | 262 | 0.2285
2916 | 14820 | 14.82 | 307 | 0.319
2917 | 14797 | 14.797 | -475 | 0.436
2918 | 14709 | 14.709 | 195 | 0.713
2919 | 14626 | 14.626 | 205 | 1.0585
2920 | 14550 | 14.55 | -321 | 0.2605
2921 | 14517 | 14.517 | 157 | 2.702
2922 | 13885 | 13.885 | 45 | 0.6385
2923 | 14056 | 14.056 | 803 | 0.383
2924 | 14037 | 14.037 | -150 | 0.282
2925 | 14073 | 14.073 | -195 | 0.8615
2926 | 13482 | 13.482 | -145 | 0.218
2927 | 14570 | 14.57 | 796 | 0.1915
2928 | 14553 | 14.553 | -805 | 0.3565
2929 | 14624 | 14.624 | 621 | 0.3405
2930 | 14740 | 14.74 | 915 | 0.3085
2931 | 14613 | 14.613 | -72 | 0.42
2932 | 14514 | 14.514 | 658 | 1.681
2933 | 14632 | 14.632 | 813 | 2.484
2934 | 14605 | 14.605 | 587 | 1.803
2935 | 14433 | 14.433 | 845 | 1.468
2936 | 14601 | 14.601 | -57 | 2.0265
2937 | 14606 | 14.606 | 681 | 1.7765
2938 | 14370 | 14.37 | 222 | 1.58
2939 | 14435 | 14.435 | -992 | 1.58
2940 | 14731 | 14.731 | -393 | 1.6065
2941 | 14389 | 14.389 | -702 | 3.67
2942 | 14531 | 14.531 | 697 | 4.2765
2943 | 14431 | 14.431 | -320 | 2.6595
2944 | 14416 | 14.416 | 414 | 2.202
2945 | 14512 | 14.512 | -277 | 1.2925
2946 | 14513 | 14.513 | 206 | 0.697
2947 | 14476 | 14.476 | 776 | 0.2285
2948 | 14410 | 14.41 | -474 | 0.101
2949 | 14638 | 14.638 | -656 | 0.516
2950 | 14490 | 14.49 | 534 | 0.452
2951 | 14662 | 14.662 | 709 | 0.5905
2952 | 14559 | 14.559 | 48 | 1.4575
2953 | 14361 | 14.361 | -855 | 0.165
2954 | 14446 | 14.446 | -668 | 0.2715
2955 | 14503 | 14.503 | 158 | 0.6595
2956 | 14543 | 14.543 | -877 | 0.5425
2957 | 14805 | 14.805 | -499 | 0.564
2958 | 14555 | 14.555 | 696 | 0.814
2959 | 14468 | 14.468 | -53 | 1.048
2960 | 14788 | 14.788 | 956 | 1.1275
2961 | 14622 | 14.622 | 949 | 1.3455
2962 | 14735 | 14.735 | 480 | 1.447
2963 | 14552 | 14.552 | -25 | 1.335
2964 | 14612 | 14.612 | 411 | 1.5055
2965 | 14814 | 14.814 | 245 | 1.202
2966 | 14766 | 14.766 | -539 | 0.9895
2967 | 14680 | 14.68 | -8 | 0.9045
2968 | 14877 | 14.877 | -23 | 1.0585
2969 | 14294 | 14.294 | -189 | 1.0585
2970 | 13711 | 13.711 | 413 | 1.181
2971 | 14605 | 14.605 | 905 | 1.4895
2972 | 14957 | 14.957 | -533 | 1.665
2973 | 14616 | 14.616 | 554 | 1.1225
2974 | 14714 | 14.714 | 994 | 1.165
2975 | 14910 | 14.91 | 497 | 1.2925
2976 | 14716 | 14.716 | -977 | 0.8775
2977 | 14779 | 14.779 | 936 | 0.617
2978 | 14889 | 14.889 | 848 | 0.7555
2979 | 14674 | 14.674 | -922 | 0.968
2980 | 14790 | 14.79 | 740 | 1.069
2981 | 14770 | 14.77 | -4 | 1.298
2982 | 14712 | 14.712 | 20 | 0.83
2983 | 14817 | 14.817 | -636 | 1.117
2984 | 14760 | 14.76 | 378 | 1.197
2985 | 14713 | 14.713 | 636 | 1.298
2986 | 14749 | 14.749 | 431 | 0.952
2987 | 14614 | 14.614 | 189 | 1.1225
2988 | 14716 | 14.716 | -653 | 1.218
2989 | 14871 | 14.871 | -743 | 1.3885
2990 | 14705 | 14.705 | 863 | 1.33
2991 | 14764 | 14.764 | 486 | 1.6065
2992 | 14660 | 14.66 | -344 | 1.213
2993 | 14676 | 14.676 | 673 | 1.532
2994 | 14950 | 14.95 | -85 | 1.6595
2995 | 14529 | 14.529 | -975 | 1.782
2996 | 14696 | 14.696 | 681 | 1.6435
2997 | 14562 | 14.562 | -115 | 1.42
2998 | 14679 | 14.679 | -314 | 1.463
2999 | 14841 | 14.841 | 808 | 0.92
3000 | 14730 | 14.73 | 450 | 0.6545
3001 | 14614 | 14.614 | 27 | 0.383
3002 | 14651 | 14.651 | -554 | 0.2235
3003 | 14614 | 14.614 | -487 | 0.234
3004 | 14735 | 14.735 | -86 | 0.33
3005 | 14704 | 14.704 | 185 | 0.4945
3006 | 14557 | 14.557 | -654 | 0.569
3007 | 14661 | 14.661 | 875 | 0.617
3008 | 14569 | 14.569 | -45 | 0.548
3009 | 14616 | 14.616 | -852 | 0.436
3010 | 14730 | 14.73 | -40 | 0.58
3011 | 14847 | 14.847 | 795 | 0.787
3012 | 14738 | 14.738 | -833 | 0.75
3013 | 14743 | 14.743 | -77 | 0.8775
3014 | 14875 | 14.875 | -465 | 1.697
3015 | 14744 | 14.744 | -360 | 1.564
3016 | 14820 | 14.82 | 387 | 1.1545
3017 | 14697 | 14.697 | 189 | 1.3405
3018 | 14824 | 14.824 | 941 | 1.617
3019 | 14156 | 14.156 | -515 | 1.2285
3020 | 14160 | 14.16 | 476 | 1.2075
3021 | 14040 | 14.04 | 295 | 0.9945
3022 | 14092 | 14.092 | 573 | 0.803
3023 | 14245 | 14.245 | -70 | 1.2445
3024 | 14031 | 14.031 | -702 | 1.686
3025 | 14742 | 14.742 | -642 | 1.8615
3026 | 14736 | 14.736 | -576 | 1.8725
3027 | 14882 | 14.882 | -37 | 1.016
3028 | 14850 | 14.85 | -464 | 0.5
3029 | 14603 | 14.603 | 975 | 0.367
3030 | 14897 | 14.897 | -494 | 0.3565
3031 | 14790 | 14.79 | -696 | 0.186
3032 | 14791 | 14.791 | -553 | 0.101
3033 | 14916 | 14.916 | -44 | 0.069
3034 | 14768 | 14.768 | 898 | 0.0425
3035 | 14958 | 14.958 | 396 | 0.186
3036 | 14846 | 14.846 | 66 | 0.2715
3037 | 14853 | 14.853 | -129 | 0.303
3038 | 14851 | 14.851 | -932 | 0.2395
3039 | 14923 | 14.923 | 733 | 0.2555
3040 | 14772 | 14.772 | 528 | 0.298
3041 | 14772 | 14.772 | 22 | 0.303
3042 | 13900 | 13.9 | -934 | 0.2445
3043 | 14698 | 14.698 | 839 | 0.2715
3044 | 14672 | 14.672 | -25 | 0.6065
3045 | 14772 | 14.772 | 756 | 0.5905
3046 | 14886 | 14.886 | 436 | 0.83
3047 | 14903 | 14.903 | 816 | 0.8615
3048 | 14761 | 14.761 | -724 | 0.7395
3049 | 14729 | 14.729 | -964 | 0.766
3050 | 14744 | 14.744 | 368 | 0.8885
3051 | 14794 | 14.794 | -421 | 0.936
3052 | 14754 | 14.754 | 376 | 1.367
3053 | 14877 | 14.877 | -496 | 1.851
3054 | 14675 | 14.675 | -966 | 2.0265
3055 | 14810 | 14.81 | 757 | 1.931
3056 | 14943 | 14.943 | -722 | 1.803
3057 | 14611 | 14.611 | -163 | 2.2395
3058 | 14722 | 14.722 | 924 | 2.266
3059 | 14804 | 14.804 | -547 | 2.6115
3060 | 14844 | 14.844 | 785 | 2.8245
3061 | 14768 | 14.768 | 668 | 3.5215
3062 | 14595 | 14.595 | 171 | 3.367
3063 | 14761 | 14.761 | 424 | 2.548
3064 | 14773 | 14.773 | 712 | 2.303
3065 | 14786 | 14.786 | 208 | 2.835
3066 | 14577 | 14.577 | -190 | 3.0105
3067 | 13703 | 13.703 | 294 | 2.9735
3068 | 14708 | 14.708 | 141 | 2.8085
3069 | 14755 | 14.755 | -734 | 3.287
3070 | 14764 | 14.764 | 722 | 3.915
3071 | 14821 | 14.821 | -327 | 3.92
3072 | 14833 | 14.833 | 151 | 3.9735
3073 | 14791 | 14.791 | 852 | 3.899
3074 | 14902 | 14.902 | 993 | 4.2395
3075 | 14711 | 14.711 | 996 | 4.58
3076 | 14867 | 14.867 | 298 | 4.4735
3077 | 14645 | 14.645 | 819 | 4.165
3078 | 14784 | 14.784 | 34 | 4.75
3079 | 14750 | 14.75 | 818 | 4
3080 | 14752 | 14.752 | -986 | 4.0265
3081 | 14798 | 14.798 | 917 | 3.867
3082 | 14673 | 14.673 | 216 | 3.8615
3083 | 14851 | 14.851 | 619 | 4.4415
3084 | 14585 | 14.585 | -535 | 4.931
3085 | 14725 | 14.725 | -984 | 4.436
3086 | 14734 | 14.734 | -597 | 4.6385
3087 | 14768 | 14.768 | -565 | 4.032
3088 | 14636 | 14.636 | -289 | 4.569
3089 | 14717 | 14.717 | -875 | 3.3885
3090 | 14695 | 14.695 | -838 | 3.8085
3091 | 14600 | 14.6 | 755 | 4.0425
3092 | 14521 | 14.521 | -266 | 3.851
3093 | 14714 | 14.714 | -27 | 3.58
3094 | 14743 | 14.743 | -853 | 4.367
3095 | 14636 | 14.636 | -223 | 3.58
3096 | 14602 | 14.602 | 684 | 2.915
3097 | 14684 | 14.684 | -362 | 3.7075
3098 | 14699 | 14.699 | 544 | 2.6435
3099 | 14666 | 14.666 | 173 | 2.718
3100 | 14542 | 14.542 | -517 | 2.6545
3101 | 14685 | 14.685 | 267 | 2.463
3102 | 14618 | 14.618 | -251 | 3.016
3103 | 14691 | 14.691 | 264 | 3.0215
3104 | 14606 | 14.606 | -257 | 3.686
3105 | 14688 | 14.688 | 61 | 3.9945
3106 | 14592 | 14.592 | -603 | 3.3615
3107 | 14696 | 14.696 | 311 | 3
3108 | 14431 | 14.431 | 182 | 3.0215
3109 | 14772 | 14.772 | 226 | 2.9095
3110 | 14469 | 14.469 | -836 | 3.8935
3111 | 14688 | 14.688 | -715 | 4.053
3112 | 14637 | 14.637 | 241 | 3.298
3113 | 14375 | 14.375 | 838 | 2.9415
3114 | 13851 | 13.851 | -322 | 2.936
3115 | 13991 | 13.991 | -15 | 3.367
3116 | 14004 | 14.004 | -675 | 2.6225
3117 | 14070 | 14.07 | 499 | 1.8775
3118 | 13854 | 13.854 | 125 | 1.649
3119 | 14286 | 14.286 | 55 | 1.6275
3120 | 14618 | 14.618 | -983 | 2.2555
3121 | 14685 | 14.685 | 854 | 2.2605
3122 | 14773 | 14.773 | 249 | 2.2765
3123 | 14650 | 14.65 | -782 | 3.181
3124 | 14801 | 14.801 | -484 | 3.101
3125 | 14627 | 14.627 | -398 | 2.7555
3126 | 14753 | 14.753 | -167 | 2.8455
3127 | 14803 | 14.803 | -900 | 2.617
3128 | 14839 | 14.839 | 612 | 2.7395
3129 | 14628 | 14.628 | 135 | 2.6435
3130 | 14863 | 14.863 | 1 | 2.814
3131 | 14577 | 14.577 | -75 | 2.2765
3132 | 14788 | 14.788 | 368 | 1.851
3133 | 14781 | 14.781 | -662 | 2.282
3134 | 14741 | 14.741 | 909 | 1.819
3135 | 14706 | 14.706 | -509 | 2.2235
3136 | 14761 | 14.761 | -269 | 2.2075
3137 | 14627 | 14.627 | -714 | 2.053
3138 | 14866 | 14.866 | -822 | 2.2235
3139 | 14603 | 14.603 | -122 | 2.303
3140 | 14603 | 14.603 | -638 | 2.3405
3141 | 14761 | 14.761 | 435 | 2.1545
3142 | 14782 | 14.782 | 522 | 2.532
3143 | 14798 | 14.798 | 656 | 1.8775
3144 | 14808 | 14.808 | -166 | 1.6595
3145 | 14701 | 14.701 | 347 | 2.213
3146 | 14776 | 14.776 | 250 | 1.415
3147 | 14517 | 14.517 | 934 | 1.2395
3148 | 14754 | 14.754 | 461 | 1.5105
3149 | 14780 | 14.78 | -587 | 1.287
3150 | 14732 | 14.732 | 772 | 1.1545
3151 | 14568 | 14.568 | -927 | 0.915
3152 | 14650 | 14.65 | 641 | 0.8725
3153 | 14707 | 14.707 | -723 | 1.1275
3154 | 14778 | 14.778 | -13 | 1.2715
3155 | 14803 | 14.803 | -162 | 1.33
3156 | 14775 | 14.775 | -910 | 1.415
3157 | 14726 | 14.726 | -732 | 1.5215
3158 | 14791 | 14.791 | 71 | 1.149
3159 | 14832 | 14.832 | -496 | 0.8245
3160 | 14693 | 14.693 | -25 | 0.686
3161 | 14716 | 14.716 | 941 | 0.3935
3162 | 14237 | 14.237 | 794 | 0.4735
3163 | 13949 | 13.949 | -902 | 0.3775
3164 | 14927 | 14.927 | -335 | 0.4785
3165 | 14752 | 14.752 | -168 | 0.463
3166 | 14880 | 14.88 | 983 | 0.564
3167 | 14816 | 14.816 | -988 | 0.7445
3168 | 14871 | 14.871 | -531 | 0.5105
3169 | 14724 | 14.724 | -509 | 0.516
3170 | 14770 | 14.77 | 589 | 0.6545
3171 | 14904 | 14.904 | -486 | 0.7395
3172 | 14822 | 14.822 | -657 | 0.9255
3173 | 14734 | 14.734 | 834 | 1.25
3174 | 14846 | 14.846 | -76 | 1.447
3175 | 14763 | 14.763 | -445 | 1.6435
3176 | 14782 | 14.782 | -428 | 1.415
3177 | 14868 | 14.868 | -636 | 1.4255
3178 | 14832 | 14.832 | -535 | 1.2395
3179 | 14739 | 14.739 | 33 | 0.984
3180 | 14879 | 14.879 | -801 | 0.8615
3181 | 14576 | 14.576 | 421 | 0.8245
3182 | 14851 | 14.851 | -482 | 0.92
3183 | 14696 | 14.696 | 552 | 1.0425
3184 | 14801 | 14.801 | 922 | 1.2075
3185 | 14566 | 14.566 | -954 | 1.1435
3186 | 14557 | 14.557 | -206 | 1.282
3187 | 14840 | 14.84 | -718 | 0.899
3188 | 13659 | 13.659 | 597 | 1.3245
3189 | 0 | 0 | 810 | 1.3085
3190 | 0 | 0 | -398 | 1.3775
3191 | 0 | 0 | 112 | 0.8885
3192 | 0 | 0 | -790 | 0.484
3193 | 0 | 0 | -265 | 0.5265
3194 | 0 | 0 | 690 | 0.447
3195 | 0 | 0 | -997 | 0.4045
3196 | 0 | 0 | -578 | 0.335
3197 | 2137 | 2.137 | 304 | 0.4945
3198 | 8346 | 8.346 | 479 | 0.601
3199 | 10352 | 10.352 | -735 | 0.5905
3200 | 12706 | 12.706 | 528 | 0.58
3201 | 14053 | 14.053 | 689 | 0.6435
3202 | 13765 | 13.765 | -657 | 0.7235
3203 | 13625 | 13.625 | 544 | 0.8615
3204 | 13664 | 13.664 | -262 | 0.8615
3205 | 14367 | 14.367 | -905 | 0.9095
3206 | 14405 | 14.405 | -978 | 0.649
3207 | 14469 | 14.469 | 62 | 0.734
3208 | 14459 | 14.459 | -327 | 0.7925
3209 | 13972 | 13.972 | 830 | 0.9575
3210 | 13990 | 13.99 | 170 | 0.8565
3211 | 13935 | 13.935 | -137 | 0.9415
3212 | 13964 | 13.964 | 569 | 0.766
3213 | 14019 | 14.019 | 487 | 0.814
3214 | 13732 | 13.732 | -91 | 0.718
3215 | 14105 | 14.105 | -211 | 0.5745
3216 | 14694 | 14.694 | 755 | 0.42
3217 | 14730 | 14.73 | -704 | 0.3775
3218 | 14654 | 14.654 | 530 | 0.367
3219 | 14708 | 14.708 | 142 | 0.2075
3220 | 14769 | 14.769 | -787 | 0.2925
3221 | 14586 | 14.586 | -899 | 0.447
3222 | 14663 | 14.663 | -68 | 0.3935
3223 | 14692 | 14.692 | 448 | 0.3565
3224 | 14623 | 14.623 | 24 | 0.1595
3225 | 14601 | 14.601 | 438 | 0.1275
3226 | 14684 | 14.684 | 174 | 0.069
3227 | 14908 | 14.908 | -819 | 0.032
3228 | 14714 | 14.714 | 123 | 0.0105
3229 | 14618 | 14.618 | 25 | 0.0265
3230 | 14739 | 14.739 | 446 | 0
3231 | 14498 | 14.498 | 342 | 0.016
3232 | 14722 | 14.722 | -175 | 0.032
3233 | 14679 | 14.679 | -637 | 0.0105
3234 | 14464 | 14.464 | -583 | 0
3235 | 14632 | 14.632 | 664 | 0
3236 | 14455 | 14.455 | 442 | 0
3237 | 14462 | 14.462 | -769 | 0.0055
3238 | 14585 | 14.585 | -296 | 0.037
3239 | 14679 | 14.679 | 102 | 0.0425
3240 | 14583 | 14.583 | -529 | 0.0585
3241 | 14544 | 14.544 | 374 | 0.053
3242 | 14567 | 14.567 | -931 | 0.016
3243 | 14634 | 14.634 | 683 | 0
3244 | 14553 | 14.553 | 912 | 0.0055
3245 | 14524 | 14.524 | -346 | 0.016
3246 | 14720 | 14.72 | 874 | 0.0105
3247 | 14489 | 14.489 | -719 | 0.0105
3248 | 14586 | 14.586 | -447 | 0.048
3249 | 14663 | 14.663 | 59 | 0.037
3250 | 14680 | 14.68 | 90 | 0.1115
3251 | 14636 | 14.636 | 459 | 0.165
3252 | 14643 | 14.643 | -665 | 0.117
3253 | 14649 | 14.649 | 872 | 0.0745
3254 | 14661 | 14.661 | 967 | 0.101
3255 | 14602 | 14.602 | 362 | 0.1065
3256 | 14773 | 14.773 | 554 | 0.0425
3257 | 14594 | 14.594 | -477 | 0.0055
3258 | 13997 | 13.997 | -935 | 0.037
3259 | 14110 | 14.11 | -325 | 0.08
3260 | 14532 | 14.532 | -771 | 0.1115
3261 | 14817 | 14.817 | 669 | 0.0585
3262 | 14597 | 14.597 | 502 | 0.2715
3263 | 14786 | 14.786 | -991 | 0.367
3264 | 14631 | 14.631 | 375 | 0.266
3265 | 14816 | 14.816 | -182 | 0.234
3266 | 14634 | 14.634 | 310 | 0
3267 | 14698 | 14.698 | -650 | 0
3268 | 14525 | 14.525 | -666 | 0
3269 | 13598 | 13.598 | -86 | 0
3270 | 13521 | 13.521 | 922 | 0
3271 | 13547 | 13.547 | 551 | 0
3272 | 14519 | 14.519 | -481 | 0
3273 | 14647 | 14.647 | 574 | 0
3274 | 14712 | 14.712 | -374 | 0
3275 | 14657 | 14.657 | 973 | 0
3276 | 14853 | 14.853 | 647 | 0
3277 | 14723 | 14.723 | -122 | 0
3278 | 14625 | 14.625 | 612 | 0
3279 | 14841 | 14.841 | -690 | 0
3280 | 14657 | 14.657 | -178 | 0
3281 | 14662 | 14.662 | 376 | 0
3282 | 14754 | 14.754 | 640 | 0
3283 | 14486 | 14.486 | 461 | 0
3284 | 14706 | 14.706 | 734 | 0
3285 | 14614 | 14.614 | -183 | 0
3286 | 14700 | 14.7 | -846 | 0
3287 | 14797 | 14.797 | 836 | 0.0055
3288 | 14523 | 14.523 | 619 | 0.0105
3289 | 14817 | 14.817 | 944 | 0
3290 | 14515 | 14.515 | -940 | 0.0055
3291 | 14727 | 14.727 | 646 | 0.0105
3292 | 14494 | 14.494 | 930 | 0
3293 | 14526 | 14.526 | -1 | 0
3294 | 14734 | 14.734 | -866 | 0
3295 | 14759 | 14.759 | -993 | 0
3296 | 14578 | 14.578 | 458 | 0
3297 | 14696 | 14.696 | 924 | 0
3298 | 14750 | 14.75 | -97 | 0
3299 | 14530 | 14.53 | 182 | 0
3300 | 14765 | 14.765 | -995 | 0
3301 | 14703 | 14.703 | -359 | 0
3302 | 14688 | 14.688 | 265 | 0
3303 | 14666 | 14.666 | -391 | 0
3304 | 14604 | 14.604 | 970 | 0
3305 | 14666 | 14.666 | -672 | 0
3306 | 14618 | 14.618 | 706 | 0
3307 | 14192 | 14.192 | -698 | 0
3308 | 13933 | 13.933 | -392 | 0
3309 | 14068 | 14.068 | -46 | 0
3310 | 13963 | 13.963 | 396 | 0
3311 | 14135 | 14.135 | -547 | 0.0055
3312 | 13870 | 13.87 | 470 | 0
3313 | 14569 | 14.569 | -846 | 0
3314 | 14865 | 14.865 | -185 | 0
3315 | 14704 | 14.704 | 398 | 0
3316 | 14662 | 14.662 | 343 | 0
3317 | 14729 | 14.729 | -280 | 0
3318 | 14726 | 14.726 | -828 | 0
3319 | 14671 | 14.671 | 735 | 0
3320 | 14669 | 14.669 | 473 | 0
3321 | 14538 | 14.538 | 828 | 0
3322 | 14715 | 14.715 | -320 | 0
3323 | 14589 | 14.589 | -245 | 0
3324 | 14677 | 14.677 | 898 | 0
3325 | 14681 | 14.681 | 277 | 0.032
3326 | 14489 | 14.489 | -497 | 0.0215
3327 | 14704 | 14.704 | 487 | 0.0055
3328 | 14765 | 14.765 | -462 | 0.0105
3329 | 14693 | 14.693 | -916 | 0.0905
3330 | 14453 | 14.453 | 621 | 0.1545
3331 | 14691 | 14.691 | 339 | 0.649
3332 | 14691 | 14.691 | 735 | 0.3725
3333 | 14598 | 14.598 | 412 | 0
3334 | 14517 | 14.517 | -859 | 0
3335 | 14857 | 14.857 | -716 | 0
3336 | 14593 | 14.593 | 223 | 0
3337 | 14548 | 14.548 | -905 | 0
3338 | 14662 | 14.662 | -96 | 0
3339 | 14608 | 14.608 | -915 | 0
3340 | 14525 | 14.525 | -247 | 0
3341 | 14610 | 14.61 | 203 | 0
3342 | 14691 | 14.691 | -197 | 0
3343 | 14560 | 14.56 | 998 | 0
3344 | 14564 | 14.564 | -737 | 0.149
3345 | 14747 | 14.747 | -322 | 0.2445
3346 | 14559 | 14.559 | -925 | 0.2285
3347 | 14701 | 14.701 | -964 | 0.266
3348 | 14693 | 14.693 | -961 | 0.303
3349 | 14628 | 14.628 | 186 | 0.303
3350 | 14644 | 14.644 | 555 | 0.351
3351 | 14650 | 14.65 | 945 | 0.234
3352 | 14682 | 14.682 | 370 | 0.2395
3353 | 14676 | 14.676 | -576 | 0.1435
3354 | 14741 | 14.741 | -420 | 0.282
3355 | 14672 | 14.672 | -274 | 0.468
3356 | 14415 | 14.415 | -177 | 0.4945
3357 | 13659 | 13.659 | 142 | 0.335
3358 | 14550 | 14.55 | -484 | 0.1915
3359 | 14614 | 14.614 | -868 | 0.1115
3360 | 14628 | 14.628 | -778 | 0.1275
3361 | 14754 | 14.754 | 535 | 0.1545
3362 | 14722 | 14.722 | -871 | 0.08
3363 | 14724 | 14.724 | -377 | 0.1065
3364 | 14779 | 14.779 | -261 | 0.1115
3365 | 14783 | 14.783 | 996 | 0.1275
3366 | 14677 | 14.677 | 568 | 0.1755
3367 | 14728 | 14.728 | -576 | 0.0955
3368 | 14642 | 14.642 | 362 | 0.085
3369 | 14827 | 14.827 | -180 | 0.064
3370 | 14644 | 14.644 | -104 | 0.048
3371 | 14731 | 14.731 | 224 | 0.101
3372 | 14744 | 14.744 | -208 | 0.149
3373 | 14588 | 14.588 | 639 | 0.1115
3374 | 14701 | 14.701 | 604 | 0.1755
3375 | 14701 | 14.701 | -23 | 0.117
3376 | 14752 | 14.752 | -444 | 0.0425
3377 | 14728 | 14.728 | 616 | 0.08
3378 | 14544 | 14.544 | -350 | 0.101
3379 | 14756 | 14.756 | -27 | 0.1545
3380 | 14564 | 14.564 | -640 | 0.053
3381 | 14756 | 14.756 | 976 | 0.037
3382 | 14658 | 14.658 | 463 | 0.1755
3383 | 14626 | 14.626 | 239 | 0.149
3384 | 14609 | 14.609 | -510 | 0.33
3385 | 14693 | 14.693 | 329 | 0.3085
3386 | 14682 | 14.682 | -547 | 0.3405
3387 | 14612 | 14.612 | -701 | 0.4255
3388 | 14752 | 14.752 | 477 | 0.5215
3389 | 14693 | 14.693 | -684 | 0.516
3390 | 14662 | 14.662 | -976 | 0.713
3391 | 14624 | 14.624 | 441 | 0.8405
3392 | 14730 | 14.73 | -193 | 0.968
3393 | 14689 | 14.689 | -113 | 1.133
3394 | 14602 | 14.602 | 496 | 0.92
3395 | 14661 | 14.661 | -564 | 1.069
3396 | 14604 | 14.604 | -352 | 1.383
3397 | 14701 | 14.701 | -643 | 1.452
3398 | 14649 | 14.649 | -653 | 1.3775
3399 | 14697 | 14.697 | -409 | 1.1915
3400 | 14556 | 14.556 | 59 | 0.9575
3401 | 14797 | 14.797 | -344 | 1.117
3402 | 14246 | 14.246 | -222 | 1.3085
3403 | 13842 | 13.842 | -166 | 1.5955
3404 | 14072 | 14.072 | -460 | 1.5265
3405 | 14111 | 14.111 | -109 | 0.83
3406 | 14153 | 14.153 | -448 | 0.6225
3407 | 13848 | 13.848 | 465 | 0.4895
3408 | 14696 | 14.696 | 717 | 0.553
3409 | 14699 | 14.699 | 957 | 0.516
3410 | 14933 | 14.933 | -603 | 0.4255
3411 | 14764 | 14.764 | 544 | 0.5055
3412 | 14694 | 14.694 | -413 | 0.2765
3413 | 14754 | 14.754 | 281 | 0.3935
3414 | 14876 | 14.876 | 177 | 0.681
3415 | 14896 | 14.896 | -824 | 0.7715
3416 | 14694 | 14.694 | 841 | 0.6275
3417 | 14865 | 14.865 | 953 | 0.5905
3418 | 14670 | 14.67 | 538 | 0.713
3419 | 14887 | 14.887 | 600 | 0.6275
3420 | 14771 | 14.771 | -330 | 0.5425
3421 | 14856 | 14.856 | -219 | 0.4575
3422 | 14740 | 14.74 | 198 | 0.6225
3423 | 14588 | 14.588 | 768 | 0.7285
3424 | 14787 | 14.787 | -160 | 0.6065
3425 | 14781 | 14.781 | -228 | 0.9045
3426 | 14517 | 14.517 | -845 | 1
3427 | 14868 | 14.868 | 743 | 0.564
3428 | 14666 | 14.666 | 512 | 0.649
3429 | 14689 | 14.689 | 459 | 0.4045
3430 | 14732 | 14.732 | 898 | 0.2445
3431 | 14775 | 14.775 | 340 | 0.2445
3432 | 14735 | 14.735 | -703 | 0.133
3433 | 14666 | 14.666 | -636 | 0.2925
3434 | 14657 | 14.657 | -402 | 0.314
3435 | 14584 | 14.584 | 645 | 0.08
3436 | 14733 | 14.733 | 804 | 0.032
3437 | 14503 | 14.503 | 953 | 0.1595
3438 | 14756 | 14.756 | -823 | 0.2605
3439 | 14530 | 14.53 | 145 | 0.383
3440 | 14731 | 14.731 | 909 | 0.3615
3441 | 14652 | 14.652 | -225 | 0.5425
3442 | 14722 | 14.722 | 325 | 0.2925
3443 | 14638 | 14.638 | 92 | 0.2605
3444 | 14672 | 14.672 | 620 | 0.133
3445 | 14608 | 14.608 | 817 | 0.213
3446 | 14808 | 14.808 | 539 | 0.197
3447 | 14517 | 14.517 | -673 | 0.335
3448 | 14068 | 14.068 | 241 | 0.553
3449 | 13928 | 13.928 | -829 | 0.6225
3450 | 14761 | 14.761 | -565 | 0.516
3451 | 14645 | 14.645 | 506 | 0.617
3452 | 14599 | 14.599 | 702 | 0.6065
3453 | 14687 | 14.687 | 410 | 0.4255
3454 | 14632 | 14.632 | 825 | 0.7715
3455 | 14813 | 14.813 | 591 | 0.798
3456 | 14651 | 14.651 | 228 | 0.8085
3457 | 14883 | 14.883 | -985 | 0.8455
3458 | 14635 | 14.635 | -834 | 0.686
3459 | 14874 | 14.874 | -648 | 0.936
3460 | 14642 | 14.642 | -408 | 0.7445
3461 | 14818 | 14.818 | 657 | 0.7285
3462 | 14701 | 14.701 | 750 | 0.2395
3463 | 14695 | 14.695 | -879 | 0.266
3464 | 14738 | 14.738 | 483 | 0.436
3465 | 14736 | 14.736 | 749 | 0.4945
3466 | 14772 | 14.772 | 959 | 0.4095
3467 | 14716 | 14.716 | -295 | 0.399
3468 | 14788 | 14.788 | -814 | 0.548
3469 | 14753 | 14.753 | -532 | 0.5905
3470 | 14811 | 14.811 | -717 | 0.484
3471 | 14721 | 14.721 | 654 | 0.532
3472 | 14802 | 14.802 | 536 | 0.569
3473 | 14683 | 14.683 | 655 | 0.585
3474 | 14724 | 14.724 | 783 | 0.697
3475 | 14676 | 14.676 | -286 | 0.947
3476 | 14736 | 14.736 | -818 | 0.697
3477 | 14881 | 14.881 | 211 | 0.899
3478 | 14674 | 14.674 | 161 | 0.968
3479 | 14750 | 14.75 | -18 | 0.9045
3480 | 14705 | 14.705 | 109 | 1.665
3481 | 14577 | 14.577 | -324 | 1.3885
3482 | 14491 | 14.491 | -764 | 1.085
3483 | 14728 | 14.728 | -245 | 1.1115
3484 | 14656 | 14.656 | 276 | 0.649
3485 | 14651 | 14.651 | -105 | 0.883
3486 | 14724 | 14.724 | -643 | 0.6115
3487 | 14591 | 14.591 | -426 | 0.787
3488 | 14725 | 14.725 | -977 | 0.8775
3489 | 14489 | 14.489 | 568 | 1.186
3490 | 14815 | 14.815 | 550 | 1.0265
3491 | 14438 | 14.438 | -764 | 0.835
3492 | 14903 | 14.903 | 273 | 0.787
3493 | 14635 | 14.635 | 894 | 1.2395
3494 | 14774 | 14.774 | 791 | 1.0425
3495 | 14786 | 14.786 | 657 | 0.9255
3496 | 14731 | 14.731 | 215 | 0.532
3497 | 14497 | 14.497 | 862 | 0.537
3498 | 13970 | 13.97 | 60 | 0.67
3499 | 14067 | 14.067 | 406 | 0.6385
3500 | 14103 | 14.103 | 909 | 0.6755
3501 | 14208 | 14.208 | -289 | 0.7555
3502 | 13791 | 13.791 | -590 | 0.9255
3503 | 14716 | 14.716 | -51 | 1.0055
3504 | 14806 | 14.806 | -79 | 1.0215
3505 | 14782 | 14.782 | -288 | 1.048
3506 | 14958 | 14.958 | -319 | 1.0955
3507 | 14834 | 14.834 | 166 | 1.133
3508 | 14844 | 14.844 | 356 | 1.25
3509 | 14861 | 14.861 | -781 | 1.42
3510 | 14895 | 14.895 | 841 | 1.282
3511 | 14787 | 14.787 | 371 | 1.032
3512 | 14842 | 14.842 | -476 | 1.197
3513 | 14643 | 14.643 | -35 | 1.2605
3514 | 14890 | 14.89 | 926 | 0.9415
3515 | 14928 | 14.928 | 800 | 0.9945
3516 | 14861 | 14.861 | 858 | 0.9415
3517 | 14929 | 14.929 | 634 | 1.1435
3518 | 14599 | 14.599 | 20 | 1.197
3519 | 14632 | 14.632 | -625 | 1.3085
3520 | 14870 | 14.87 | 587 | 1.165
3521 | 14766 | 14.766 | -821 | 1
3522 | 14506 | 14.506 | 901 | 1.266
3523 | 14566 | 14.566 | 774 | 1.1755
3524 | 14645 | 14.645 | -660 | 0.8405
3525 | 14623 | 14.623 | 108 | 0.6755
3526 | 14806 | 14.806 | 994 | 0.835
3527 | 14909 | 14.909 | 797 | 0.766
3528 | 14513 | 14.513 | 976 | 0.718
3529 | 14678 | 14.678 | 292 | 0.6595
3530 | 14539 | 14.539 | 87 | 0.697
3531 | 14747 | 14.747 | 795 | 0.6065
3532 | 14716 | 14.716 | -48 | 0.532
3533 | 14832 | 14.832 | 877 | 0.718
3534 | 14732 | 14.732 | 638 | 0.7285
3535 | 14738 | 14.738 | 386 | 0.9045
3536 | 14681 | 14.681 | -319 | 1.053
3537 | 14884 | 14.884 | -421 | 1.564
3538 | 14628 | 14.628 | 575 | 1.697
3539 | 14855 | 14.855 | -831 | 2.5955
3540 | 14587 | 14.587 | -68 | 2.75
3541 | 14649 | 14.649 | -453 | 2.1115
3542 | 14817 | 14.817 | 531 | 2.8615
3543 | 14756 | 14.756 | 756 | 2.7395
3544 | 14730 | 14.73 | -583 | 2.3405
3545 | 14703 | 14.703 | -572 | 1.936
3546 | 14284 | 14.284 | 533 | 2.0905
3547 | 13721 | 13.721 | 366 | 2.936
3548 | 14697 | 14.697 | 806 | 2.17
3549 | 14671 | 14.671 | -341 | 1.6065
3550 | 14661 | 14.661 | -546 | 2.835
3551 | 14699 | 14.699 | 494 | 3.4095
3552 | 14756 | 14.756 | 817 | 3.064
3553 | 14689 | 14.689 | -269 | 3.2925
3554 | 14730 | 14.73 | 295 | 2.803
3555 | 14738 | 14.738 | 873 | 3.069
3556 | 14669 | 14.669 | 166 | 2.9415
3557 | 14706 | 14.706 | -118 | 2.181
3558 | 14761 | 14.761 | -779 | 2.2765
3559 | 14724 | 14.724 | 929 | 2.5585
3560 | 14691 | 14.691 | -726 | 2.2765
3561 | 14695 | 14.695 | -24 | 2.085
3562 | 14638 | 14.638 | 502 | 2.415
3563 | 14750 | 14.75 | 555 | 2.7395
3564 | 14625 | 14.625 | 604 | 2.0425
3565 | 14709 | 14.709 | 664 | 1.447
3566 | 14782 | 14.782 | -901 | 1.5745
3567 | 14690 | 14.69 | 5 | 1.585
3568 | 14844 | 14.844 | 555 | 1.2395
3569 | 14801 | 14.801 | -517 | 1.1115
3570 | 14605 | 14.605 | -533 | 1.0585
3571 | 14669 | 14.669 | 549 | 1.165
3572 | 14631 | 14.631 | 681 | 0.952
3573 | 14661 | 14.661 | -642 | 0.7605
3574 | 14684 | 14.684 | 246 | 0.5745
3575 | 14754 | 14.754 | -982 | 0.8615
3576 | 14802 | 14.802 | -725 | 0.8085
3577 | 14678 | 14.678 | -816 | 0.787
3578 | 14734 | 14.734 | 287 | 0.835
3579 | 14663 | 14.663 | -275 | 0.7605
3580 | 14653 | 14.653 | -731 | 0.463
3581 | 14717 | 14.717 | -317 | 0.5265
3582 | 14737 | 14.737 | 611 | 0.6275
3583 | 14704 | 14.704 | -824 | 0.569
3584 | 14889 | 14.889 | -673 | 0.8405
3585 | 14646 | 14.646 | 523 | 0.75
3586 | 14839 | 14.839 | 220 | 0.915
3587 | 14682 | 14.682 | -557 | 0.9785
3588 | 14718 | 14.718 | -475 | 0.9945
3589 | 14721 | 14.721 | -823 | 0.6115
3590 | 14766 | 14.766 | 580 | 0.569
3591 | 14777 | 14.777 | -214 | 0.75
3592 | 14734 | 14.734 | 710 | 0.569
3593 | 14731 | 14.731 | -268 | 0.6385
3594 | 14622 | 14.622 | -997 | 0.782
3595 | 14319 | 14.319 | 730 | 0.9045
3596 | 13706 | 13.706 | -640 | 0.58
3597 | 14284 | 14.284 | -269 | 0.484
3598 | 14040 | 14.04 | 136 | 0.5905
3599 | 14088 | 14.088 | 525 | 0.6755
3600 | 13675 | 13.675 | -964 | 0.83
3601 | 14808 | 14.808 | -454 | 0.601
3602 | 14822 | 14.822 | -734 | 0.75
3603 | 14744 | 14.744 | -387 | 0.7765
3604 | 14862 | 14.862 | -799 | 0.6545
3605 | 14705 | 14.705 | 174 | 0.585
3606 | 14859 | 14.859 | -838 | 0.4575
3607 | 14772 | 14.772 | 993 | 0.4045
3608 | 14797 | 14.797 | -553 | 0.537
3609 | 14699 | 14.699 | 143 | 0.5585
3610 | 14767 | 14.767 | -416 | 0.5105
3611 | 14745 | 14.745 | -402 | 0.3775
3612 | 14557 | 14.557 | 881 | 0.351
3613 | 14947 | 14.947 | 554 | 0.4255
3614 | 14710 | 14.71 | 476 | 0.3565
3615 | 15041 | 15.041 | 464 | 0.447
3616 | 14649 | 14.649 | -149 | 0.452
3617 | 14735 | 14.735 | 557 | 0.5055
3618 | 14671 | 14.671 | -626 | 0.819
3619 | 14649 | 14.649 | 219 | 0.9895
3620 | 14718 | 14.718 | -20 | 0.984
3621 | 14732 | 14.732 | -306 | 0.9045
3622 | 14635 | 14.635 | -344 | 0.984
3623 | 14751 | 14.751 | -779 | 1.1915
3624 | 14554 | 14.554 | -644 | 1.697
3625 | 14612 | 14.612 | -413 | 1.617
3626 | 14743 | 14.743 | -410 | 1.069
3627 | 14776 | 14.776 | 576 | 0.8405
3628 | 14599 | 14.599 | -432 | 1.165
3629 | 14735 | 14.735 | 896 | 0.883
3630 | 14680 | 14.68 | -13 | 1.0425
3631 | 14713 | 14.713 | 371 | 1.0105
3632 | 14901 | 14.901 | 921 | 1.5215
3633 | 14659 | 14.659 | -520 | 1.6435
3634 | 14672 | 14.672 | 311 | 2.1435
3635 | 14812 | 14.812 | -102 | 1.936
3636 | 14776 | 14.776 | -14 | 2.053
3637 | 14681 | 14.681 | 203 | 2.532
3638 | 14672 | 14.672 | -132 | 3.117
3639 | 14792 | 14.792 | -608 | 2.6755
3640 | 14783 | 14.783 | -41 | 2.3615
3641 | 14585 | 14.585 | -380 | 2.3565
3642 | 14527 | 14.527 | -454 | 2.037
3643 | 14039 | 14.039 | -859 | 1.5955
3644 | 14449 | 14.449 | 810 | 1.569
3645 | 14658 | 14.658 | 200 | 1.4575
3646 | 14815 | 14.815 | 898 | 1.3775
3647 | 14773 | 14.773 | -200 | 1.298
3648 | 14699 | 14.699 | 332 | 1.2445
3649 | 14881 | 14.881 | 189 | 1.101
3650 | 14806 | 14.806 | 498 | 0.883
3651 | 14734 | 14.734 | -79 | 0.7765
3652 | 14959 | 14.959 | -990 | 0.8085
3653 | 14644 | 14.644 | -609 | 0.67
3654 | 14854 | 14.854 | 391 | 0.431
3655 | 14713 | 14.713 | -605 | 0.351
3656 | 14588 | 14.588 | -542 | 0.4255
3657 | 14872 | 14.872 | -171 | 0.351
3658 | 14769 | 14.769 | -929 | 0.335
3659 | 14738 | 14.738 | -440 | 0.5425
3660 | 14755 | 14.755 | -983 | 0.569
3661 | 14579 | 14.579 | -968 | 0.5905
3662 | 14791 | 14.791 | 539 | 1.085
3663 | 14646 | 14.646 | 568 | 0.734
3664 | 14698 | 14.698 | -784 | 1.0265
3665 | 14637 | 14.637 | -269 | 0.649
3666 | 14722 | 14.722 | -763 | 0.431
3667 | 14613 | 14.613 | -665 | 0.33
3668 | 14661 | 14.661 | 333 | 0.25
3669 | 14686 | 14.686 | 918 | 0.2395
3670 | 14617 | 14.617 | 967 | 0.298
3671 | 14493 | 14.493 | 28 | 0.351
3672 | 14735 | 14.735 | 42 | 0.1545
3673 | 14644 | 14.644 | -71 | 0.165
3674 | 14454 | 14.454 | 343 | 0.197
3675 | 14847 | 14.847 | 501 | 0.3565
3676 | 14690 | 14.69 | -421 | 0.2925
3677 | 14758 | 14.758 | -905 | 0.3085
3678 | 14452 | 14.452 | 698 | 0.17
3679 | 14453 | 14.453 | -71 | 0.165
3680 | 14539 | 14.539 | -272 | 0.2445
3681 | 14365 | 14.365 | -185 | 0.2285
3682 | 14643 | 14.643 | 929 | 0.2075
3683 | 14685 | 14.685 | 272 | 0.1115
3684 | 14502 | 14.502 | -158 | 0.548
3685 | 14590 | 14.59 | -525 | 1.0585
3686 | 14663 | 14.663 | 674 | 0.963
3687 | 14544 | 14.544 | -283 | 0.83
3688 | 14648 | 14.648 | 1000 | 0.819
3689 | 14576 | 14.576 | -325 | 1.0585
3690 | 14030 | 14.03 | 499 | 0.9945
3691 | 13877 | 13.877 | 785 | 0.75
3692 | 13811 | 13.811 | 487 | 0.8565
3693 | 14177 | 14.177 | -67 | 0.8085
3694 | 13819 | 13.819 | -69 | 1.101
3695 | 13857 | 13.857 | 177 | 1.186
3696 | 14726 | 14.726 | -268 | 1.2235
3697 | 14561 | 14.561 | -275 | 1.1385
3698 | 14714 | 14.714 | 906 | 1.149
3699 | 14763 | 14.763 | 517 | 1.415
3700 | 14713 | 14.713 | -983 | 1.303
3701 | 14645 | 14.645 | -652 | 1.282
3702 | 14739 | 14.739 | 734 | 1.1225
3703 | 14672 | 14.672 | 924 | 1.2605
3704 | 14777 | 14.777 | 32 | 1.4255
3705 | 14728 | 14.728 | 118 | 1.2285
3706 | 14736 | 14.736 | -379 | 1.053
3707 | 14691 | 14.691 | 736 | 0.8725
3708 | 14797 | 14.797 | -195 | 0.9095
3709 | 14685 | 14.685 | 150 | 0.67
3710 | 14685 | 14.685 | -77 | 0.713
3711 | 14770 | 14.77 | -541 | 0.851
3712 | 14626 | 14.626 | -801 | 0.9735
3713 | 14786 | 14.786 | -728 | 0.9415
3714 | 14782 | 14.782 | -223 | 1.3725
3715 | 14602 | 14.602 | -188 | 1.3885
3716 | 14709 | 14.709 | 640 | 0.9415
3717 | 14668 | 14.668 | -678 | 0.819
3718 | 14685 | 14.685 | 682 | 0.5905
3719 | 14741 | 14.741 | -667 | 0.431
3720 | 14706 | 14.706 | 518 | 0.3775
3721 | 14477 | 14.477 | 174 | 0.6115
3722 | 14800 | 14.8 | 178 | 0.553
3723 | 14717 | 14.717 | -733 | 0.782
3724 | 14699 | 14.699 | 138 | 0.9735
3725 | 14587 | 14.587 | -417 | 0.883
3726 | 14710 | 14.71 | 214 | 0.9255
3727 | 14552 | 14.552 | -745 | 1.053
3728 | 14812 | 14.812 | -946 | 0.9255
3729 | 14664 | 14.664 | 655 | 1.0215
3730 | 14501 | 14.501 | -224 | 1.085
3731 | 14798 | 14.798 | 230 | 1.0905
3732 | 14546 | 14.546 | 788 | 1.2445
3733 | 14809 | 14.809 | 481 | 1.447
3734 | 14644 | 14.644 | 902 | 1.197
3735 | 14732 | 14.732 | 579 | 1.4415
3736 | 14748 | 14.748 | -673 | 1.213
3737 | 14393 | 14.393 | -813 | 1.415
3738 | 13855 | 13.855 | 481 | 1.3245
3739 | 14452 | 14.452 | -753 | 1.5425
3740 | 14552 | 14.552 | 686 | 1.569
3741 | 14679 | 14.679 | -103 | 1.633
3742 | 14645 | 14.645 | 569 | 1.463
3743 | 14884 | 14.884 | 994 | 1.2235
3744 | 14688 | 14.688 | 645 | 1.3085
3745 | 14680 | 14.68 | 40 | 0.92
3746 | 14757 | 14.757 | 880 | 0.9945
3747 | 14802 | 14.802 | 74 | 1.037
3748 | 14710 | 14.71 | -207 | 1.2395
3749 | 14863 | 14.863 | 895 | 1.4895
3750 | 14620 | 14.62 | -966 | 1.8405
3751 | 14707 | 14.707 | -841 | 1.7715
3752 | 14879 | 14.879 | 792 | 1.6755
3753 | 14616 | 14.616 | -127 | 1.3935
3754 | 14735 | 14.735 | 222 | 1.766
3755 | 14836 | 14.836 | -67 | 1.8565
3756 | 14739 | 14.739 | 489 | 1.6755
3757 | 14760 | 14.76 | 844 | 1.3885
3758 | 14815 | 14.815 | -185 | 1.4045
3759 | 14705 | 14.705 | -589 | 1.4785
3760 | 14709 | 14.709 | -776 | 1.9415
3761 | 14734 | 14.734 | 70 | 2.798
3762 | 14493 | 14.493 | -946 | 2.7715
3763 | 14843 | 14.843 | -736 | 2.3935
3764 | 14602 | 14.602 | -695 | 1.782
3765 | 14807 | 14.807 | 973 | 2.1275
3766 | 14669 | 14.669 | -597 | 1.9895
3767 | 14615 | 14.615 | 778 | 2.7765
3768 | 14804 | 14.804 | -545 | 3.2605
3769 | 14590 | 14.59 | -965 | 2.8725
3770 | 14799 | 14.799 | -78 | 2.3935
3771 | 14529 | 14.529 | 808 | 2.399
3772 | 14904 | 14.904 | -71 | 2.42
3773 | 14773 | 14.773 | -304 | 3.1115
3774 | 14539 | 14.539 | -748 | 3.0055
3775 | 14692 | 14.692 | 501 | 2.298
3776 | 14786 | 14.786 | 554 | 2.048
3777 | 14776 | 14.776 | -53 | 1.9045
3778 | 14613 | 14.613 | 914 | 1.7395
3779 | 14690 | 14.69 | 906 | 1.5955
3780 | 14626 | 14.626 | 927 | 1.4895
3781 | 14696 | 14.696 | -727 | 0.697
3782 | 14737 | 14.737 | 184 | 0.5055
3783 | 14628 | 14.628 | -725 | 0.5955
3784 | 14798 | 14.798 | 80 | 0.8455
3785 | 14691 | 14.691 | 215 | 0.883
3786 | 14636 | 14.636 | -214 | 1.1915
3787 | 14385 | 14.385 | -199 | 1.303
3788 | 13904 | 13.904 | -744 | 1.4045
3789 | 14164 | 14.164 | 401 | 0.8245
3790 | 13965 | 13.965 | -954 | 0.899
3791 | 14240 | 14.24 | 222 | 1.165
3792 | 13729 | 13.729 | 257 | 1.2605
3793 | 14778 | 14.778 | 883 | 0.9415
3794 | 14733 | 14.733 | -691 | 1.085
3795 | 14925 | 14.925 | 258 | 1.133
3796 | 14649 | 14.649 | -447 | 1.117
3797 | 15040 | 15.04 | -45 | 0.968
3798 | 14743 | 14.743 | 789 | 1.181
3799 | 14980 | 14.98 | -592 | 1.186
3800 | 14865 | 14.865 | 219 | 1.287
3801 | 14835 | 14.835 | -923 | 1.4045
3802 | 14735 | 14.735 | 486 | 1.516
3803 | 14873 | 14.873 | 48 | 1.6065
3804 | 14746 | 14.746 | -498 | 1.649
3805 | 14691 | 14.691 | 727 | 1.67
3806 | 14928 | 14.928 | -727 | 0.9415
3807 | 14774 | 14.774 | 104 | 1.1435
3808 | 14602 | 14.602 | 995 | 1.069
3809 | 14861 | 14.861 | -225 | 0.798
3810 | 14777 | 14.777 | -143 | 0.9575
3811 | 14744 | 14.744 | -862 | 0.7285
3812 | 14744 | 14.744 | 573 | 0.3245
3813 | 14588 | 14.588 | -325 | 0.287
3814 | 14824 | 14.824 | 210 | 0.2715
3815 | 14726 | 14.726 | 148 | 0.1545
3816 | 14656 | 14.656 | -298 | 0.1385
3817 | 14606 | 14.606 | 417 | 0.1385
3818 | 14670 | 14.67 | -23 | 0.298
3819 | 14730 | 14.73 | -883 | 0.2925
3820 | 14708 | 14.708 | 578 | 0.5215
3821 | 14750 | 14.75 | -900 | 0.814
3822 | 14781 | 14.781 | 803 | 0.83
3823 | 14693 | 14.693 | -796 | 0.9735
3824 | 14707 | 14.707 | 108 | 1.0215
3825 | 14758 | 14.758 | -444 | 1.5745
3826 | 14715 | 14.715 | 832 | 1.8775
3827 | 14744 | 14.744 | 165 | 2.516
3828 | 14825 | 14.825 | -130 | 3
3829 | 14800 | 14.8 | -513 | 2.2445
3830 | 14835 | 14.835 | -473 | 2.601
3831 | 14804 | 14.804 | -159 | 3.8565
3832 | 14481 | 14.481 | -523 | 4.064
3833 | 14912 | 14.912 | -795 | 3.867
3834 | 14406 | 14.406 | -600 | 3.6275
3835 | 13665 | 13.665 | 61 | 3.8245
3836 | 14723 | 14.723 | -290 | 4.1545
3837 | 14870 | 14.87 | 452 | 4.0425
3838 | 14790 | 14.79 | -263 | 3.8085
3839 | 14717 | 14.717 | 674 | 3.9735
3840 | 14737 | 14.737 | 408 | 3.9045
3841 | 14884 | 14.884 | 802 | 3.6275
3842 | 14834 | 14.834 | -578 | 3.1385
3843 | 14817 | 14.817 | -687 | 2.516
3844 | 14719 | 14.719 | -299 | 2.569
3845 | 14829 | 14.829 | -524 | 2.564
3846 | 14840 | 14.84 | 657 | 2.9095
3847 | 14793 | 14.793 | -774 | 3.468
3848 | 14724 | 14.724 | -221 | 3.314
3849 | 13121 | 13.121 | 823 | 2.803
3850 | 8906 | 8.906 | -622 | 2.697
3851 | 8231 | 8.231 | -618 | 2.5585
3852 | 9080 | 9.08 | 169 | 3.415
3853 | 10609 | 10.609 | -848 | 2.984
3854 | 8481 | 8.481 | 3 | 3.4095
3855 | 8029 | 8.029 | -568 | 2.915
3856 | 8756 | 8.756 | -139 | 2.883
3857 | 13070 | 13.07 | -74 | 3.415
3858 | 14399 | 14.399 | 250 | 3.787
3859 | 14542 | 14.542 | 299 | 3.484
3860 | 14672 | 14.672 | -958 | 3.9945
3861 | 14830 | 14.83 | -355 | 3.447
3862 | 14723 | 14.723 | 324 | 2.5215
3863 | 14598 | 14.598 | 694 | 2.2715
3864 | 14574 | 14.574 | 501 | 2.4945
3865 | 14531 | 14.531 | -585 | 2.4095
3866 | 14365 | 14.365 | 887 | 3.6435
3867 | 14808 | 14.808 | 985 | 3.6755
3868 | 14581 | 14.581 | 693 | 4.3775
3869 | 14615 | 14.615 | -856 | 3.5905
3870 | 14622 | 14.622 | 814 | 3.3725
3871 | 14374 | 14.374 | 421 | 2.484
3872 | 14747 | 14.747 | 740 | 1.3245
3873 | 14572 | 14.572 | -267 | 1.75
3874 | 14601 | 14.601 | -299 | 1.7765
3875 | 14661 | 14.661 | 274 | 2.085
3876 | 14649 | 14.649 | 35 | 2.048
3877 | 14445 | 14.445 | 42 | 2.463
3878 | 14719 | 14.719 | -781 | 2.6595
3879 | 14626 | 14.626 | 837 | 2.016
3880 | 14306 | 14.306 | 172 | 2.2075
3881 | 13636 | 13.636 | -67 | 2.33
3882 | 14023 | 14.023 | -957 | 2.1545
3883 | 13852 | 13.852 | -807 | 2.601
3884 | 14184 | 14.184 | -77 | 3.069
3885 | 13735 | 13.735 | 719 | 2.532
3886 | 14463 | 14.463 | -45 | 2.1545
3887 | 14691 | 14.691 | 344 | 2.3245
3888 | 14558 | 14.558 | -68 | 2.069
3889 | 14615 | 14.615 | -554 | 2.25
3890 | 14743 | 14.743 | -556 | 2.181
3891 | 14606 | 14.606 | 781 | 2.048
3892 | 14670 | 14.67 | -101 | 1.3885
3893 | 14728 | 14.728 | 647 | 1.548
3894 | 14834 | 14.834 | -459 | 2.6065
3895 | 14707 | 14.707 | -300 | 2.266
3896 | 14771 | 14.771 | -66 | 2.218
3897 | 14749 | 14.749 | 406 | 1.8885
3898 | 14597 | 14.597 | 977 | 1.4895
3899 | 14735 | 14.735 | 32 | 2.468
3900 | 14670 | 14.67 | 436 | 2.6545
3901 | 14685 | 14.685 | -457 | 2.803
3902 | 14828 | 14.828 | 806 | 3.1545
3903 | 14744 | 14.744 | -399 | 2.92
3904 | 14773 | 14.773 | -948 | 4.5955
3905 | 14752 | 14.752 | -641 | 4.686
3906 | 14610 | 14.61 | 238 | 4.6545
3907 | 14673 | 14.673 | 886 | 4.601
3908 | 14572 | 14.572 | -668 | 4.4945
3909 | 14647 | 14.647 | 591 | 4.782
3910 | 14795 | 14.795 | 160 | 4.952
3911 | 14354 | 14.354 | 630 | 4.9735
3912 | 14645 | 14.645 | -428 | 4.968
3913 | 14552 | 14.552 | 284 | 4.963
3914 | 14788 | 14.788 | 904 | 4.9785
3915 | 14523 | 14.523 | -657 | 4.9785
3916 | 14640 | 14.64 | -982 | 4.9735
3917 | 14643 | 14.643 | 271 | 4.963
3918 | 14667 | 14.667 | 356 | 4.9045
3919 | 14699 | 14.699 | 437 | 4.92
3920 | 14728 | 14.728 | -235 | 4.83
3921 | 14714 | 14.714 | 870 | 4.787
3922 | 14601 | 14.601 | 993 | 3.681
3923 | 14480 | 14.48 | 507 | 3.516
3924 | 14802 | 14.802 | -893 | 3.7075
3925 | 14604 | 14.604 | -190 | 3.5585
3926 | 14713 | 14.713 | -417 | 3.202
3927 | 14566 | 14.566 | 116 | 2.4785
3928 | 14686 | 14.686 | -172 | 2.766
3929 | 14649 | 14.649 | 684 | 3.947
3930 | 14329 | 14.329 | 265 | 4.931
3931 | 13716 | 13.716 | -659 | 4.5905
3932 | 14545 | 14.545 | 777 | 3.2605
3933 | 14561 | 14.561 | -203 | 2.9895
3934 | 14651 | 14.651 | 807 | 3.9255
3935 | 14809 | 14.809 | 342 | 3.4895
3936 | 14709 | 14.709 | 557 | 2.9945
3937 | 14651 | 14.651 | 595 | 2.3935
3938 | 14814 | 14.814 | -835 | 3.032
3939 | 14791 | 14.791 | 500 | 3.83
3940 | 14736 | 14.736 | 381 | 2.447
3941 | 14745 | 14.745 | -6 | 2.553
3942 | 14937 | 14.937 | 186 | 3.266
3943 | 14656 | 14.656 | 628 | 3.133
3944 | 14793 | 14.793 | 833 | 3.17
3945 | 14694 | 14.694 | -762 | 2.516
3946 | 14793 | 14.793 | -19 | 2.4095
3947 | 14740 | 14.74 | 304 | 2.734
3948 | 14791 | 14.791 | 114 | 3.085
3949 | 14660 | 14.66 | -565 | 2.9255
3950 | 14820 | 14.82 | -778 | 3.2285
3951 | 14817 | 14.817 | -753 | 3.048
3952 | 14763 | 14.763 | -396 | 3.25
3953 | 14720 | 14.72 | -941 | 3.0215
3954 | 14715 | 14.715 | 549 | 2.718
3955 | 14701 | 14.701 | -404 | 2.1065
3956 | 14627 | 14.627 | -274 | 2.5745
3957 | 14634 | 14.634 | 592 | 2.899
3958 | 14634 | 14.634 | -106 | 3.6755
3959 | 14643 | 14.643 | 426 | 2.8615
3960 | 14612 | 14.612 | 965 | 3.9735
3961 | 14616 | 14.616 | -656 | 4.0955
3962 | 14617 | 14.617 | -487 | 3.9095
3963 | 14516 | 14.516 | 815 | 3.8935
3964 | 14609 | 14.609 | -933 | 3.133
3965 | 14583 | 14.583 | 371 | 3.2605
3966 | 14612 | 14.612 | 259 | 3.053
3967 | 14594 | 14.594 | 388 | 3.766
3968 | 14665 | 14.665 | -461 | 3.3455
3969 | 14625 | 14.625 | -637 | 4.1545
3970 | 14579 | 14.579 | 152 | 3.266
3971 | 14646 | 14.646 | 427 | 3.0745
3972 | 14555 | 14.555 | 945 | 3.5265
3973 | 14611 | 14.611 | 214 | 2.968
3974 | 14450 | 14.45 | -97 | 3.5745
3975 | 14725 | 14.725 | 558 | 3.463
3976 | 14656 | 14.656 | -813 | 4.468
3977 | 14615 | 14.615 | 998 | 3.963
3978 | 14483 | 14.483 | -572 | 3.5105
3979 | 14055 | 14.055 | -204 | 4.4045
3980 | 13884 | 13.884 | 13 | 4.3565
3981 | 14004 | 14.004 | -574 | 3.963
3982 | 13955 | 13.955 | 181 | 3.4785
3983 | 13843 | 13.843 | -916 | 4.3405
3984 | 14054 | 14.054 | 4 | 3.564
3985 | 14691 | 14.691 | -979 | 3.399
3986 | 14689 | 14.689 | -536 | 3.3615
3987 | 14829 | 14.829 | 121 | 3.7285
3988 | 14765 | 14.765 | 776 | 3.447
3989 | 14574 | 14.574 | -56 | 3.186
3990 | 14876 | 14.876 | -311 | 3.6755
3991 | 14713 | 14.713 | 260 | 3.186
3992 | 14717 | 14.717 | 174 | 3.0055
3993 | 14839 | 14.839 | -659 | 3.1115
3994 | 14792 | 14.792 | -457 | 3.5425
3995 | 14769 | 14.769 | -368 | 3.3405
3996 | 14590 | 14.59 | 330 | 3.2605
3997 | 14830 | 14.83 | -636 | 2.9255
3998 | 14746 | 14.746 | -721 | 3.069
3999 | 14671 | 14.671 | 939 | 3.234
4000 | 14768 | 14.768 | -211 | 3.7445
4001 | 14571 | 14.571 | 333 | 2.984
4002 | 14617 | 14.617 | 230 | 3.1545
4003 | 14587 | 14.587 | 107 | 3.516
4004 | 14751 | 14.751 | 982 | 3.048
4005 | 14589 | 14.589 | -67 | 3.133
4006 | 14442 | 14.442 | -166 | 4.0055
4007 | 14751 | 14.751 | -905 | 4.1915
4008 | 14494 | 14.494 | -878 | 4.1385
4009 | 14538 | 14.538 | -181 | 4.617
4010 | 14789 | 14.789 | -327 | 4.037
4011 | 14643 | 14.643 | 370 | 3.181
4012 | 14548 | 14.548 | -401 | 3.3085
4013 | 14664 | 14.664 | -796 | 3.048
4014 | 14562 | 14.562 | 829 | 4.4255
4015 | 14626 | 14.626 | 621 | 3.814
4016 | 14700 | 14.7 | 720 | 4.1595
4017 | 14582 | 14.582 | 167 | 2.452
4018 | 14413 | 14.413 | -617 | 3.6275
4019 | 14723 | 14.723 | 274 | 1.069
4020 | 14479 | 14.479 | 835 | 1.92
4021 | 14762 | 14.762 | 832 | 3.399
4022 | 14639 | 14.639 | -60 | 2.5055
4023 | 14543 | 14.543 | 852 | 1.936
4024 | 14758 | 14.758 | 463 | 2.6755
4025 | 14805 | 14.805 | 643 | 3.6115
4026 | 14203 | 14.203 | -710 | 4.08
4027 | 13762 | 13.762 | 477 | 4.5105
4028 | 14625 | 14.625 | -229 | 4.6225
4029 | 14563 | 14.563 | 762 | 3.314
4030 | 14818 | 14.818 | 749 | 3.7285
4031 | 14737 | 14.737 | 519 | 3.1385
4032 | 14562 | 14.562 | 33 | 2
4033 | 14849 | 14.849 | -351 | 2.101
4034 | 14670 | 14.67 | -155 | 2.617
4035 | 14802 | 14.802 | -137 | 2.968
4036 | 14660 | 14.66 | 849 | 2.883
4037 | 14785 | 14.785 | 87 | 2.75
4038 | 14787 | 14.787 | -836 | 3.431
4039 | 14581 | 14.581 | 403 | 3.1595
4040 | 14674 | 14.674 | 115 | 3.213
4041 | 14628 | 14.628 | -117 | 2.6435
4042 | 14674 | 14.674 | 201 | 3.0745
4043 | 14695 | 14.695 | -679 | 3.7925
4044 | 14713 | 14.713 | -73 | 3.633
4045 | 14787 | 14.787 | 199 | 2.8085
4046 | 14628 | 14.628 | 404 | 2.463
4047 | 14718 | 14.718 | -683 | 2.9575
4048 | 14745 | 14.745 | 337 | 3.037
4049 | 14541 | 14.541 | -947 | 3.1065
4050 | 14682 | 14.682 | -458 | 3.1275
4051 | 14498 | 14.498 | 573 | 3.9415
4052 | 14605 | 14.605 | 0 | 4.2925
4053 | 14660 | 14.66 | 660 | 4.569
4054 | 14686 | 14.686 | 300 | 4.766
4055 | 14659 | 14.659 | -744 | 4.67
4056 | 14674 | 14.674 | -729 | 4.5585
4057 | 14564 | 14.564 | 596 | 4.532
4058 | 14733 | 14.733 | 696 | 4.436
4059 | 14499 | 14.499 | 711 | 4.314
4060 | 14387 | 14.387 | -737 | 4.2075
4061 | 14684 | 14.684 | 453 | 4.1065
4062 | 14527 | 14.527 | -974 | 4.0055
4063 | 14607 | 14.607 | -396 | 4.319
4064 | 14499 | 14.499 | -784 | 3.835
4065 | 14616 | 14.616 | -72 | 4.4045
4066 | 14473 | 14.473 | -180 | 4.484
4067 | 14525 | 14.525 | -154 | 4.4575
4068 | 14575 | 14.575 | -65 | 4.734
4069 | 14572 | 14.572 | 150 | 4.766
4070 | 14585 | 14.585 | -847 | 4.915
4071 | 14683 | 14.683 | -89 | 4.947
4072 | 14585 | 14.585 | 423 | 4.7925
4073 | 14480 | 14.48 | -875 | 4.766
4074 | 14392 | 14.392 | 160 | 4.7075
4075 | 13815 | 13.815 | 854 | 4.7235
4076 | 13890 | 13.89 | 62 | 4.8935
4077 | 13985 | 13.985 | 320 | 4.6385
4078 | 14091 | 14.091 | -910 | 3.952
4079 | 13556 | 13.556 | 967 | 3.9785
4080 | 14572 | 14.572 | 811 | 3.968
4081 | 14687 | 14.687 | 316 | 2.9575
4082 | 14662 | 14.662 | 711 | 3.2445
4083 | 14761 | 14.761 | 175 | 3.3725
4084 | 14748 | 14.748 | -415 | 2.947
4085 | 14704 | 14.704 | 452 | 1.617
4086 | 14795 | 14.795 | 468 | 1.117
4087 | 14865 | 14.865 | -859 | 0.697
4088 | 14571 | 14.571 | 39 | 0.7075
4089 | 14798 | 14.798 | 792 | 1.234
4090 | 14674 | 14.674 | -565 | 1.883
4091 | 14684 | 14.684 | -170 | 2.3615
4092 | 14768 | 14.768 | -877 | 3.186
4093 | 14678 | 14.678 | -237 | 3.3085
4094 | 14628 | 14.628 | -358 | 4.5
4095 | 14777 | 14.777 | 207 | 4.048
4096 | 14692 | 14.692 | -1 | 2.8085
4097 | 14540 | 14.54 | -894 | 1.1755
4098 | 14588 | 14.588 | 704 | 0
4099 | 14788 | 14.788 | -971 | 0
4100 | 14688 | 14.688 | 343 | 0
4101 | 14718 | 14.718 | 990 | 0
4102 | 14644 | 14.644 | -84 | 0.0055
4103 | 14535 | 14.535 | 721 | 0
4104 | 14763 | 14.763 | -968 | 0
4105 | 14758 | 14.758 | 686 | 0
4106 | 14554 | 14.554 | -311 | 0
4107 | 14558 | 14.558 | -162 | 0
4108 | 14670 | 14.67 | 675 | 0
4109 | 14691 | 14.691 | 461 | 0
4110 | 14507 | 14.507 | -283 | 0
4111 | 14698 | 14.698 | 196 | 0
4112 | 14748 | 14.748 | 159 | 0
4113 | 14589 | 14.589 | -164 | 0
4114 | 14758 | 14.758 | -514 | 0
4115 | 14610 | 14.61 | -875 | 0.25
4116 | 14677 | 14.677 | 257 | 0.1225
4117 | 14598 | 14.598 | -536 | 0.431
4118 | 14796 | 14.796 | 162 | 1.952
4119 | 14683 | 14.683 | -723 | 1.117
4120 | 14516 | 14.516 | -456 | 0.9785
4121 | 14901 | 14.901 | 700 | 1.1545
4122 | 14591 | 14.591 | 530 | 1.2605
4123 | 14802 | 14.802 | -897 | 1.1435
4124 | 14293 | 14.293 | -975 | 1.697
4125 | 13774 | 13.774 | -125 | 2.149
4126 | 14650 | 14.65 | 114 | 1.5265
4127 | 14739 | 14.739 | 43 | 1.2765
4128 | 14828 | 14.828 | -400 | 1.3455
4129 | 14760 | 14.76 | 448 | 1.085
4130 | 14679 | 14.679 | 375 | 1.064
4131 | 14921 | 14.921 | -947 | 0.8405
4132 | 14629 | 14.629 | -905 | 0.8455
4133 | 14745 | 14.745 | 66 | 1.1435
4134 | 14688 | 14.688 | -282 | 0.952
4135 | 14766 | 14.766 | 567 | 0.798
4136 | 14625 | 14.625 | -230 | 1.2395
4137 | 14661 | 14.661 | 642 | 0.787
4138 | 14820 | 14.82 | 301 | 0.6385
4139 | 14535 | 14.535 | -7 | 0.633
4140 | 14697 | 14.697 | -919 | 0.4785
4141 | 14592 | 14.592 | 795 | 0.2285
4142 | 14557 | 14.557 | 486 | 0.3245
4143 | 14704 | 14.704 | 234 | 0.1275
4144 | 14373 | 14.373 | -231 | 0.0215
4145 | 14650 | 14.65 | -119 | 0.0265
4146 | 14618 | 14.618 | 784 | 0.101
4147 | 14484 | 14.484 | 179 | 0.3085
4148 | 14670 | 14.67 | 487 | 0.564
4149 | 14623 | 14.623 | 993 | 0.7235
4150 | 14449 | 14.449 | -234 | 1.149
4151 | 14594 | 14.594 | 346 | 1.0905
4152 | 14381 | 14.381 | -927 | 1.351
4153 | 14572 | 14.572 | 871 | 1.713
4154 | 14456 | 14.456 | -864 | 2.2605
4155 | 14579 | 14.579 | -462 | 2.532
4156 | 14436 | 14.436 | -323 | 2.5265
4157 | 14381 | 14.381 | 62 | 2.5585
4158 | 14698 | 14.698 | 593 | 4.1545
4159 | 14475 | 14.475 | -815 | 4.8725
4160 | 14419 | 14.419 | 875 | 4.867
4161 | 14304 | 14.304 | 61 | 3.25
4162 | 14586 | 14.586 | -252 | 4.814
4163 | 14546 | 14.546 | 663 | 4.5585
4164 | 14615 | 14.615 | -287 | 4.7445
4165 | 14579 | 14.579 | 578 | 4.4785
4166 | 14592 | 14.592 | -50 | 4.7235
4167 | 14599 | 14.599 | -784 | 4.734
4168 | 14594 | 14.594 | 884 | 4.8775
4169 | 14599 | 14.599 | 945 | 4.936
4170 | 14167 | 14.167 | 715 | 4.899
4171 | 13782 | 13.782 | -819 | 4.814
4172 | 14100 | 14.1 | 453 | 4.8935
4173 | 13898 | 13.898 | -134 | 4.851
4174 | 13976 | 13.976 | -981 | 4.803
4175 | 13672 | 13.672 | 822 | 4.867
4176 | 14588 | 14.588 | -60 | 4.9255
4177 | 14589 | 14.589 | 312 | 4.8775
4178 | 14611 | 14.611 | -372 | 4.963
4179 | 14653 | 14.653 | -68 | 4.952
4180 | 14772 | 14.772 | 367 | 4.968
4181 | 14634 | 14.634 | -487 | 4.8085
4182 | 14836 | 14.836 | 157 | 4.766
4183 | 14631 | 14.631 | 876 | 4.8405
4184 | 14542 | 14.542 | 471 | 4.814
4185 | 14691 | 14.691 | 626 | 4.7075
4186 | 14625 | 14.625 | -672 | 4.7445
4187 | 14701 | 14.701 | -155 | 3.617
4188 | 14684 | 14.684 | -763 | 3.633
4189 | 14519 | 14.519 | -125 | 3.7715
4190 | 14593 | 14.593 | -822 | 4.069
4191 | 14648 | 14.648 | -877 | 4.4415
4192 | 14563 | 14.563 | 161 | 3.835
4193 | 14878 | 14.878 | 337 | 4.287
4194 | 14608 | 14.608 | 975 | 4.8405
4195 | 14697 | 14.697 | 464 | 4.883
4196 | 14681 | 14.681 | 670 | 4.952
4197 | 14576 | 14.576 | -7 | 4.8405
4198 | 14710 | 14.71 | -519 | 4.8725
4199 | 14591 | 14.591 | -534 | 4.33
4200 | 14519 | 14.519 | -207 | 4.952
4201 | 14551 | 14.551 | -427 | 4.798
4202 | 14509 | 14.509 | -291 | 4.383
4203 | 14392 | 14.392 | 896 | 4.452
4204 | 14723 | 14.723 | -656 | 3.564
4205 | 14476 | 14.476 | 344 | 4.952
4206 | 14461 | 14.461 | 169 | 4.9785
4207 | 14597 | 14.597 | 359 | 4.835
4208 | 14430 | 14.43 | 613 | 4.1275
4209 | 14666 | 14.666 | 280 | 3.963
4210 | 14370 | 14.37 | 832 | 4.202
4211 | 14626 | 14.626 | -844 | 4.6755
4212 | 14562 | 14.562 | 754 | 4.697
4213 | 14552 | 14.552 | -109 | 4.6115
4214 | 14640 | 14.64 | -510 | 3.75
4215 | 14545 | 14.545 | -222 | 3.484
4216 | 14539 | 14.539 | 785 | 3.6595
4217 | 14629 | 14.629 | -498 | 4.0055
4218 | 14005 | 14.005 | 97 | 3.016
4219 | 14060 | 14.06 | -380 | 3.713
4220 | 14672 | 14.672 | -928 | 4.048
4221 | 14726 | 14.726 | -913 | 4.468
4222 | 14762 | 14.762 | -452 | 3.867
4223 | 14691 | 14.691 | 614 | 3.883
4224 | 14798 | 14.798 | 644 | 4.537
4225 | 14660 | 14.66 | 611 | 0
4226 | 14913 | 14.913 | 20 | 0
4227 | 14655 | 14.655 | -448 | 0
4228 | 14745 | 14.745 | -877 | 0
4229 | 14538 | 14.538 | -386 | 0
4230 | 14807 | 14.807 | 613 | 0
4231 | 14719 | 14.719 | 764 | 0
4232 | 14578 | 14.578 | 870 | 0
4233 | 14751 | 14.751 | -70 | 0
4234 | 14706 | 14.706 | -211 | 0
4235 | 14721 | 14.721 | 683 | 0
4236 | 14688 | 14.688 | -802 | 0
4237 | 14702 | 14.702 | -942 | 0
4238 | 14628 | 14.628 | 977 | 0
4239 | 14596 | 14.596 | 883 | 0
4240 | 14562 | 14.562 | 818 | 0
4241 | 14694 | 14.694 | -842 | 0
4242 | 14551 | 14.551 | 312 | 0
4243 | 14522 | 14.522 | -786 | 0
4244 | 14765 | 14.765 | -898 | 0
4245 | 14593 | 14.593 | -545 | 0
4246 | 14634 | 14.634 | -524 | 0
4247 | 14534 | 14.534 | -271 | 0
4248 | 14504 | 14.504 | 103 | 0
4249 | 14642 | 14.642 | -136 | 0
4250 | 14342 | 14.342 | -564 | 0
4251 | 14637 | 14.637 | 654 | 0
4252 | 14671 | 14.671 | -109 | 0
4253 | 14513 | 14.513 | -653 | 0
4254 | 14476 | 14.476 | 932 | 0
4255 | 14609 | 14.609 | 284 | 0
4256 | 14437 | 14.437 | -761 | 0
4257 | 14351 | 14.351 | 656 | 0
4258 | 14561 | 14.561 | 189 | 0
4259 | 14523 | 14.523 | -225 | 0
4260 | 14402 | 14.402 | 147 | 0
4261 | 14530 | 14.53 | 902 | 0
4262 | 14314 | 14.314 | -498 | 0
4263 | 14680 | 14.68 | -736 | 0
4264 | 13969 | 13.969 | 679 | 0
4265 | 13867 | 13.867 | -645 | 0
4266 | 14056 | 14.056 | -19 | 0
4267 | 13945 | 13.945 | 749 | 0
4268 | 13963 | 13.963 | 280 | 0
4269 | 13815 | 13.815 | -871 | 0
4270 | 14493 | 14.493 | 347 | 0
4271 | 14569 | 14.569 | -661 | 0
4272 | 14542 | 14.542 | -798 | 0
4273 | 14548 | 14.548 | -573 | 4.92
4274 | 14568 | 14.568 | -782 | 4.963
4275 | 14637 | 14.637 | -777 | 4.7445
4276 | 14525 | 14.525 | 498 | 4.7075
4277 | 14458 | 14.458 | 891 | 4.8725
4278 | 14597 | 14.597 | 676 | 4.963
4279 | 14589 | 14.589 | 481 | 4.963
4280 | 14445 | 14.445 | 876 | 4.867
4281 | 14495 | 14.495 | -512 | 4.8775
4282 | 14456 | 14.456 | -522 | 4.8455
4283 | 14410 | 14.41 | 265 | 2.936
4284 | 14629 | 14.629 | 242 | 4.0265
4285 | 14418 | 14.418 | 837 | 4.5215
4286 | 14555 | 14.555 | 579 | 4.1915
4287 | 14424 | 14.424 | 667 | 4.936
4288 | 14599 | 14.599 | 536 | 4.8775
4289 | 14469 | 14.469 | -528 | 4.963
4290 | 14595 | 14.595 | 658 | 4.9785
4291 | 14428 | 14.428 | 175 | 4.9735
4292 | 14512 | 14.512 | -892 | 4.9785
4293 | 14497 | 14.497 | 474 | 2.548
4294 | 14459 | 14.459 | 868 | 4.9785
4295 | 14415 | 14.415 | 531 | 4.984
4296 | 14459 | 14.459 | 248 | 4.968
4297 | 14367 | 14.367 | 973 | 2.319
4298 | 14460 | 14.46 | -652 | 2.649
4299 | 14429 | 14.429 | 798 | 2.197
4300 | 14432 | 14.432 | -180 | 4.9785
4301 | 14387 | 14.387 | 800 | 4.037
4302 | 14534 | 14.534 | -148 | 3.6545
4303 | 14595 | 14.595 | -321 | 4.9945
4304 | 14598 | 14.598 | 749 | 4.968
4305 | 14619 | 14.619 | 507 | 4.9735
4306 | 14697 | 14.697 | 942 | 4.3085
4307 | 14554 | 14.554 | 361 | 4.984
4308 | 14493 | 14.493 | -787 | 4.9785
4309 | 14731 | 14.731 | 576 | 4.9735
4310 | 14750 | 14.75 | 78 | 4.9785
4311 | 14614 | 14.614 | -830 | 4.42
4312 | 14792 | 14.792 | -222 | 4.3615
4313 | 14309 | 14.309 | -727 | 2.33
4314 | 13761 | 13.761 | -712 | 2.7925
4315 | 14507 | 14.507 | -991 | 4.8245
4316 | 14621 | 14.621 | 503 | 4.9895
4317 | 14735 | 14.735 | 545 | 4.9095
4318 | 14706 | 14.706 | -285 | 4.899
4319 | 14707 | 14.707 | 831 | 4.633
4320 | 14723 | 14.723 | 897 | 4.6915
4321 | 14679 | 14.679 | -341 | 3.931
4322 | 14768 | 14.768 | -728 | 3.697
4323 | 14754 | 14.754 | -589 | 3.537
4324 | 14679 | 14.679 | 95 | 3.92
4325 | 14716 | 14.716 | -189 | 4.3935
4326 | 14750 | 14.75 | -634 | 4.3085
4327 | 14600 | 14.6 | -13 | 2.1755
4328 | 14859 | 14.859 | 803 | 3.4735
4329 | 14659 | 14.659 | -222 | 3.468
4330 | 14702 | 14.702 | -315 | 3.0905
4331 | 14875 | 14.875 | -330 | 3.9095
4332 | 14743 | 14.743 | -473 | 4.532
4333 | 14568 | 14.568 | 254 | 4.665
4334 | 14876 | 14.876 | 286 | 3.713
4335 | 14656 | 14.656 | 742 | 1.3935
4336 | 14776 | 14.776 | 713 | 2.3405
4337 | 14758 | 14.758 | 319 | 2.3775
4338 | 14679 | 14.679 | 721 | 2.9045
4339 | 14618 | 14.618 | 409 | 2.7925
4340 | 14732 | 14.732 | -366 | 2.42
4341 | 14656 | 14.656 | 491 | 3.197
4342 | 14602 | 14.602 | -686 | 3.6435
4343 | 14750 | 14.75 | 35 | 3.0055
4344 | 14594 | 14.594 | -350 | 2.633
4345 | 14754 | 14.754 | -404 | 2.0955
4346 | 14649 | 14.649 | -972 | 2.452
4347 | 14553 | 14.553 | -790 | 2.7285
4348 | 14695 | 14.695 | -798 | 3.032
4349 | 14600 | 14.6 | 402 | 2.8885
4350 | 14685 | 14.685 | -127 | 2.181
4351 | 14735 | 14.735 | 854 | 1.7395
4352 | 14618 | 14.618 | 420 | 1.899
4353 | 14501 | 14.501 | -211 | 2.17
4354 | 14849 | 14.849 | -766 | 1.351
4355 | 14726 | 14.726 | -277 | 1.564
4356 | 14708 | 14.708 | 82 | 1.2235
4357 | 14829 | 14.829 | -776 | 0.8405
4358 | 14705 | 14.705 | -320 | 1.7605
4359 | 14645 | 14.645 | -682 | 2.468
4360 | 14778 | 14.778 | 839 | 1.8085
4361 | 14446 | 14.446 | -159 | 2.101
4362 | 14011 | 14.011 | -851 | 2.9045
4363 | 13946 | 13.946 | -753 | 2.537
4364 | 13856 | 13.856 | 584 | 1.681
4365 | 14258 | 14.258 | 561 | 1.298
4366 | 13707 | 13.707 | -769 | 0.564
4367 | 14157 | 14.157 | 802 | 0.484
4368 | 14747 | 14.747 | 692 | 0.335
4369 | 14551 | 14.551 | -876 | 1.037
4370 | 14643 | 14.643 | -380 | 1.117
4371 | 14690 | 14.69 | 832 | 0.936
4372 | 14562 | 14.562 | 508 | 1.282
4373 | 14611 | 14.611 | 496 | 1.4945
4374 | 14747 | 14.747 | 568 | 1.537
4375 | 14538 | 14.538 | -662 | 1.3935
4376 | 14397 | 14.397 | 270 | 1.2285
4377 | 14648 | 14.648 | 688 | 1.181
4378 | 14545 | 14.545 | -558 | 1.8245
4379 | 14585 | 14.585 | 522 | 1.9095
4380 | 14517 | 14.517 | -851 | 2.181
4381 | 14572 | 14.572 | 246 | 2.4045
4382 | 14524 | 14.524 | -48 | 2.1915
4383 | 14657 | 14.657 | 592 | 2.2605
4384 | 14402 | 14.402 | 481 | 2.1275
4385 | 14532 | 14.532 | -237 | 1.6915
4386 | 14456 | 14.456 | 948 | 1.931
4387 | 14282 | 14.282 | 677 | 2.963
4388 | 14542 | 14.542 | 932 | 3.0055
4389 | 14501 | 14.501 | 339 | 3.133
4390 | 14506 | 14.506 | -21 | 3.314
4391 | 14496 | 14.496 | -472 | 3.42
4392 | 14492 | 14.492 | -442 | 2.681
4393 | 14577 | 14.577 | 952 | 2.298
4394 | 14593 | 14.593 | -283 | 2.548
4395 | 14593 | 14.593 | 468 | 2.415
4396 | 14480 | 14.48 | 523 | 2.963
4397 | 14746 | 14.746 | 101 | 2.101
4398 | 14567 | 14.567 | -733 | 2.6755
4399 | 14602 | 14.602 | -930 | 2.814
4400 | 14629 | 14.629 | 879 | 1.67
4401 | 14590 | 14.59 | 563 | 1.9735
4402 | 14541 | 14.541 | -456 | 1.5425
4403 | 14768 | 14.768 | -582 | 1.452
4404 | 14630 | 14.63 | 137 | 0.7445
4405 | 14667 | 14.667 | 461 | 0.5055
4406 | 14689 | 14.689 | -565 | 1.702
4407 | 14518 | 14.518 | -612 | 2.037
4408 | 13840 | 13.84 | 788 | 2.3085
4409 | 14199 | 14.199 | 249 | 1.303
4410 | 14561 | 14.561 | 124 | 1.2765
4411 | 14491 | 14.491 | 779 | 1.2715
4412 | 14776 | 14.776 | 272 | 1.202
4413 | 14550 | 14.55 | -742 | 0.915
4414 | 14678 | 14.678 | 846 | 1.165
4415 | 14700 | 14.7 | -399 | 1.463
4416 | 14635 | 14.635 | 788 | 1.6115
4417 | 14758 | 14.758 | -616 | 1.8565
4418 | 14662 | 14.662 | -617 | 1.835
4419 | 14570 | 14.57 | -513 | 2.75
4420 | 14860 | 14.86 | 275 | 2.915
4421 | 14666 | 14.666 | 396 | 2.6385
4422 | 14708 | 14.708 | -565 | 4.048
4423 | 14702 | 14.702 | -240 | 4.5955
4424 | 14607 | 14.607 | -390 | 4.3885
4425 | 14614 | 14.614 | -634 | 4.7925
4426 | 14779 | 14.779 | -73 | 4.117
4427 | 14719 | 14.719 | -540 | 4.085
4428 | 14835 | 14.835 | -704 | 3.8935
4429 | 14636 | 14.636 | 22 | 2.447
4430 | 14786 | 14.786 | 487 | 1.6755
4431 | 14652 | 14.652 | -736 | 1.697
4432 | 14768 | 14.768 | 436 | 2.5425
4433 | 14645 | 14.645 | 863 | 2.4945
4434 | 14604 | 14.604 | 13 | 3.367
4435 | 14723 | 14.723 | 561 | 3.016
4436 | 14631 | 14.631 | -385 | 2.766
4437 | 14683 | 14.683 | -705 | 2.213
4438 | 14592 | 14.592 | 84 | 2.383
4439 | 14685 | 14.685 | 705 | 2.649
4440 | 14668 | 14.668 | 80 | 1.968
4441 | 14612 | 14.612 | 300 | 2.053
4442 | 14582 | 14.582 | 759 | 2.431
4443 | 14720 | 14.72 | -198 | 2.234
4444 | 14633 | 14.633 | 989 | 2.2235
4445 | 14609 | 14.609 | 842 | 3.016
4446 | 14551 | 14.551 | -954 | 2.5905
4447 | 14590 | 14.59 | -978 | 2.7925
4448 | 14884 | 14.884 | 821 | 3.3455
4449 | 14523 | 14.523 | 100 | 4.0055
4450 | 14783 | 14.783 | 733 | 4.4735
4451 | 14760 | 14.76 | 226 | 4.766
4452 | 14633 | 14.633 | -273 | 4.9045
4453 | 14723 | 14.723 | 241 | 4.968
4454 | 14662 | 14.662 | -585 | 4.9735
4455 | 14706 | 14.706 | -56 | 4.963
4456 | 14474 | 14.474 | 798 | 4.436
4457 | 14734 | 14.734 | -976 | 4.947
4458 | 14364 | 14.364 | -75 | 4.9045
4459 | 13714 | 13.714 | -532 | 4.6065
4460 | 14156 | 14.156 | -925 | 4.6115
4461 | 14081 | 14.081 | -393 | 4.75
4462 | 14095 | 14.095 | -351 | 3.6065
4463 | 13487 | 13.487 | 443 | 2.814
4464 | 14783 | 14.783 | 62 | 2.0955
4465 | 14988 | 14.988 | -166 | 2.037
4466 | 14755 | 14.755 | -313 | 2.1435
4467 | 14755 | 14.755 | 913 | 2.133
4468 | 14774 | 14.774 | -111 | 1.6385
4469 | 14922 | 14.922 | 486 | 1.335
4470 | 14707 | 14.707 | 430 | 1.9045
4471 | 14711 | 14.711 | -196 | 2.835
4472 | 14829 | 14.829 | 812 | 2.6915
4473 | 14640 | 14.64 | 439 | 2.5105
4474 | 14727 | 14.727 | 522 | 3.1115
4475 | 14921 | 14.921 | 318 | 3.516
4476 | 14846 | 14.846 | -418 | 3.186
4477 | 14689 | 14.689 | -746 | 3.3455
4478 | 14804 | 14.804 | -74 | 3.3935
4479 | 14714 | 14.714 | -476 | 3.1065
4480 | 14713 | 14.713 | -537 | 3.734
4481 | 14721 | 14.721 | -962 | 4.553
4482 | 14694 | 14.694 | 613 | 4.8245
4483 | 14751 | 14.751 | -71 | 4.915
4484 | 14731 | 14.731 | 344 | 4.963
4485 | 14690 | 14.69 | 74 | 4.952
4486 | 14770 | 14.77 | -361 | 4.9785
4487 | 14752 | 14.752 | -863 | 4.9735
4488 | 14639 | 14.639 | 867 | 4.915
4489 | 14751 | 14.751 | 211 | 4.9735
4490 | 14718 | 14.718 | 58 | 4.9785
4491 | 14684 | 14.684 | -264 | 4.9785
4492 | 14740 | 14.74 | -650 | 4.984
4493 | 14604 | 14.604 | -902 | 4.9785
4494 | 14752 | 14.752 | -688 | 4.984
4495 | 14527 | 14.527 | -46 | 4.9785
4496 | 14720 | 14.72 | 386 | 4.9735
4497 | 14621 | 14.621 | -696 | 4.963
4498 | 14591 | 14.591 | -611 | 4.936
4499 | 14688 | 14.688 | 743 | 4.9785
4500 | 14457 | 14.457 | 252 | 4.9785
4501 | 14798 | 14.798 | -814 | 4.9735
4502 | 14490 | 14.49 | -227 | 4.984
4503 | 14743 | 14.743 | 2 | 4.9735
4504 | 14725 | 14.725 | 213 | 4.984
4505 | 14548 | 14.548 | -872 | 4.9785
4506 | 14271 | 14.271 | 851 | 4.9785
4507 | 13719 | 13.719 | -94 | 4.9785
4508 | 14573 | 14.573 | 830 | 4.9785
4509 | 14519 | 14.519 | 160 | 4.9735
4510 | 14634 | 14.634 | -456 | 4.9785
4511 | 14719 | 14.719 | -257 | 4.931
4512 | 14553 | 14.553 | 628 | 4.9095
4513 | 14596 | 14.596 | -985 | 4.9415
4514 | 14582 | 14.582 | 640 | 4.9785
4515 | 14486 | 14.486 | 784 | 4.984
4516 | 14387 | 14.387 | 213 | 4.9735
4517 | 14503 | 14.503 | 344 | 4.92
4518 | 14584 | 14.584 | 443 | 4.9785
4519 | 14425 | 14.425 | -834 | 4.9045
4520 | 14570 | 14.57 | -918 | 4.915
4521 | 14593 | 14.593 | 424 | 4.984
4522 | 14691 | 14.691 | 660 | 4.9045
4523 | 14545 | 14.545 | 901 | 4.633
4524 | 14651 | 14.651 | -307 | 4.335
4525 | 14610 | 14.61 | -631 | 4.266
4526 | 14574 | 14.574 | -244 | 3.8775
4527 | 14749 | 14.749 | -519 | 3.803
4528 | 14596 | 14.596 | -532 | 4.202
4529 | 14544 | 14.544 | -856 | 4.548
4530 | 14534 | 14.534 | 807 | 4.702
4531 | 14320 | 14.32 | -366 | 4.7285
4532 | 14455 | 14.455 | 772 | 4.75
4533 | 14637 | 14.637 | -62 | 4.6385
4534 | 14369 | 14.369 | 861 | 4.1545
4535 | 14553 | 14.553 | -523 | 4.5905
4536 | 14467 | 14.467 | -197 | 4.213
4537 | 14403 | 14.403 | 30 | 4.3565
4538 | 14270 | 14.27 | 595 | 4.484
4539 | 14377 | 14.377 | 955 | 3.1755
4540 | 14352 | 14.352 | 711 | 3.5265
4541 | 14336 | 14.336 | 251 | 4.3245
4542 | 14415 | 14.415 | 942 | 3.58
4543 | 14285 | 14.285 | 75 | 2.8245
4544 | 14449 | 14.449 | -456 | 4.532
4545 | 14539 | 14.539 | -4 | 4.6385
4546 | 14339 | 14.339 | 633 | 4.8775
4547 | 14566 | 14.566 | -642 | 4.8725
4548 | 14589 | 14.589 | -139 | 4.7285
4549 | 14428 | 14.428 | 233 | 4.3775
4550 | 14639 | 14.639 | 396 | 4.25
4551 | 14532 | 14.532 | -121 | 4.702
4552 | 14570 | 14.57 | -369 | 4.835
4553 | 14375 | 14.375 | 236 | 4.963
4554 | 13852 | 13.852 | 524 | 4.915
4555 | 13926 | 13.926 | 781 | 4.8245
4556 | 13888 | 13.888 | 966 | 4.7555
4557 | 14094 | 14.094 | -822 | 4.1385
4558 | 13731 | 13.731 | 546 | 3.2715
4559 | 14199 | 14.199 | 914 | 2.7395
4560 | 14721 | 14.721 | -948 | 1.936
4561 | 14620 | 14.62 | -218 | 0
4562 | 14466 | 14.466 | 697 | 0
4563 | 14779 | 14.779 | 76 | 0
4564 | 14529 | 14.529 | 122 | 0
4565 | 14666 | 14.666 | 831 | 0
4566 | 14785 | 14.785 | -642 | 0
4567 | 14617 | 14.617 | 800 | 0
4568 | 14685 | 14.685 | -746 | 0
4569 | 14762 | 14.762 | -360 | 0
4570 | 14565 | 14.565 | 473 | 0
4571 | 14660 | 14.66 | 330 | 0
4572 | 14803 | 14.803 | -830 | 0
4573 | 14653 | 14.653 | 527 | 0
4574 | 14737 | 14.737 | -888 | 0
4575 | 14662 | 14.662 | 35 | 0
4576 | 14637 | 14.637 | 157 | 0
4577 | 14755 | 14.755 | 979 | 0
4578 | 14580 | 14.58 | -585 | 0
4579 | 14687 | 14.687 | 73 | 0
4580 | 14676 | 14.676 | 424 | 0
4581 | 14611 | 14.611 | -923 | 0
4582 | 14669 | 14.669 | -929 | 0
4583 | 14590 | 14.59 | -526 | 0
4584 | 14554 | 14.554 | -911 | 0
4585 | 14533 | 14.533 | 50 | 0
4586 | 14693 | 14.693 | -966 | 0
4587 | 14612 | 14.612 | 335 | 0
4588 | 14609 | 14.609 | 926 | 0
4589 | 14704 | 14.704 | 812 | 0
4590 | 14636 | 14.636 | 285 | 0
4591 | 14715 | 14.715 | 551 | 0
4592 | 14549 | 14.549 | -990 | 0
4593 | 14601 | 14.601 | 301 | 0
4594 | 14842 | 14.842 | 387 | 0
4595 | 14577 | 14.577 | 939 | 0
4596 | 14669 | 14.669 | -871 | 0
4597 | 14758 | 14.758 | 696 | 0
4598 | 14590 | 14.59 | 316 | 0
4599 | 14697 | 14.697 | -299 | 0
4600 | 14826 | 14.826 | -498 | 0
4601 | 14660 | 14.66 | -939 | 0
4602 | 14504 | 14.504 | 324 | 0
4603 | 13827 | 13.827 | 749 | 0
4604 | 14473 | 14.473 | -810 | 0
4605 | 14635 | 14.635 | 560 | 0
4606 | 14717 | 14.717 | -568 | 0
4607 | 14746 | 14.746 | -391 | 0
4608 | 14742 | 14.742 | -798 | 0
4609 | 14685 | 14.685 | 328 | 1.133
4610 | 14792 | 14.792 | -963 | 1.2285
4611 | 14661 | 14.661 | -792 | 2.6065
4612 | 14780 | 14.78 | -708 | 3.649
4613 | 14666 | 14.666 | 45 | 4.282
4614 | 14849 | 14.849 | 711 | 3.9045
4615 | 14676 | 14.676 | 55 | 3.4575
4616 | 14798 | 14.798 | 999 | 2.835
4617 | 14850 | 14.85 | 554 | 1.601
4618 | 14620 | 14.62 | -486 | 1.149
4619 | 14847 | 14.847 | -20 | 1.1545
4620 | 14744 | 14.744 | 565 | 0.6385
4621 | 14645 | 14.645 | -483 | 0.814
4622 | 14810 | 14.81 | 275 | 1.537
4623 | 14919 | 14.919 | 641 | 1.0905
4624 | 14734 | 14.734 | 7 | 2.037
4625 | 14634 | 14.634 | 142 | 2.2765
4626 | 14601 | 14.601 | 492 | 1.6435
4627 | 14630 | 14.63 | 586 | 1.564
4628 | 14672 | 14.672 | 782 | 2.133
4629 | 14683 | 14.683 | -329 | 1.9785
4630 | 14799 | 14.799 | 437 | 1.8405
4631 | 14717 | 14.717 | -48 | 1.7285
4632 | 14623 | 14.623 | -633 | 1.7925
4633 | 14690 | 14.69 | -330 | 2.197
4634 | 14658 | 14.658 | -981 | 3.149
4635 | 14666 | 14.666 | -472 | 3.4895
4636 | 14737 | 14.737 | -379 | 4.4735
4637 | 14754 | 14.754 | 647 | 4.952
4638 | 14581 | 14.581 | -282 | 4.4785
4639 | 14646 | 14.646 | 678 | 4.9895
4640 | 14622 | 14.622 | -578 | 4.984
4641 | 14506 | 14.506 | -56 | 4.9785
4642 | 14744 | 14.744 | 139 | 4.9785
4643 | 14658 | 14.658 | 688 | 4.9785
4644 | 14801 | 14.801 | 375 | 4.9735
4645 | 14690 | 14.69 | 823 | 4.9785
4646 | 14697 | 14.697 | -687 | 4.9735
4647 | 14721 | 14.721 | -543 | 4.9785
4648 | 14855 | 14.855 | -791 | 4.9735
4649 | 14505 | 14.505 | -615 | 4.9735
4650 | 14063 | 14.063 | 135 | 4.936
4651 | 14018 | 14.018 | -399 | 4.92
4652 | 14065 | 14.065 | -881 | 4.931
4653 | 14050 | 14.05 | -880 | 4.899
4654 | 13848 | 13.848 | 107 | 4.8565
4655 | 14126 | 14.126 | 535 | 4.814
4656 | 14856 | 14.856 | 353 | 4.803
4657 | 14718 | 14.718 | 744 | 4.8245
4658 | 14808 | 14.808 | -531 | 4.367
4659 | 14736 | 14.736 | -882 | 4.0215
4660 | 14826 | 14.826 | 811 | 3.1755
4661 | 14727 | 14.727 | -858 | 3.234
4662 | 14730 | 14.73 | -560 | 4.2235
4663 | 14865 | 14.865 | -48 | 3.7605
4664 | 14650 | 14.65 | -637 | 3.3455
4665 | 14671 | 14.671 | 483 | 2.9415
4666 | 14881 | 14.881 | 400 | 2.415
4667 | 14707 | 14.707 | 43 | 3.149
4668 | 14679 | 14.679 | 231 | 3.8085
4669 | 14636 | 14.636 | -968 | 3.431
4670 | 14576 | 14.576 | 531 | 3.1595
4671 | 14603 | 14.603 | -922 | 2.9255
4672 | 14738 | 14.738 | 167 | 3.032
4673 | 14619 | 14.619 | -302 | 3.319
4674 | 14500 | 14.5 | 613 | 3.2605
4675 | 14619 | 14.619 | 388 | 2.952
4676 | 14582 | 14.582 | 942 | 2.766
4677 | 14747 | 14.747 | -899 | 2.899
4678 | 14643 | 14.643 | 798 | 3.1915
4679 | 14610 | 14.61 | 392 | 2.984
4680 | 14591 | 14.591 | -488 | 3.2765
4681 | 14735 | 14.735 | 735 | 2.5055
4682 | 14575 | 14.575 | 242 | 1.867
4683 | 14636 | 14.636 | -175 | 2.1595
4684 | 14639 | 14.639 | -598 | 0.537
4685 | 14541 | 14.541 | 947 | 2.2235
4686 | 14625 | 14.625 | -451 | 3.963
4687 | 14479 | 14.479 | -857 | 2.851
4688 | 14633 | 14.633 | 645 | 3.218
4689 | 14760 | 14.76 | -431 | 3.7925
4690 | 14599 | 14.599 | 444 | 4.569
4691 | 14736 | 14.736 | -979 | 3.58
4692 | 14601 | 14.601 | 450 | 3.548
4693 | 14611 | 14.611 | 533 | 3.798
4694 | 14640 | 14.64 | -222 | 3.282
4695 | 14746 | 14.746 | 556 | 2.9575
4696 | 14508 | 14.508 | 747 | 3.2925
4697 | 14775 | 14.775 | -52 | 2.8725
4698 | 14336 | 14.336 | 349 | 2.4895
4699 | 13160 | 13.16 | 644 | 2.3885
4700 | 14333 | 14.333 | -398 | 2.6065
4701 | 14523 | 14.523 | 358 | 3.383
4702 | 14732 | 14.732 | -79 | 2.952
4703 | 14645 | 14.645 | 877 | 2.6595
4704 | 14817 | 14.817 | 895 | 2.649
4705 | 14568 | 14.568 | -75 | 2.42
4706 | 14465 | 14.465 | -26 | 2.234
4707 | 14776 | 14.776 | 90 | 2.069
4708 | 14689 | 14.689 | -424 | 2.1385
4709 | 14778 | 14.778 | 809 | 2.3245
4710 | 14616 | 14.616 | 676 | 2.101
4711 | 14697 | 14.697 | 946 | 2
4712 | 14666 | 14.666 | 629 | 1.936
4713 | 14607 | 14.607 | 510 | 1.782
4714 | 14733 | 14.733 | -41 | 2.3245
4715 | 14728 | 14.728 | 239 | 2.681
4716 | 14637 | 14.637 | -460 | 2.8455
4717 | 14827 | 14.827 | 699 | 2.3775
4718 | 14631 | 14.631 | 388 | 2.5055
4719 | 14744 | 14.744 | -794 | 2.7075
4720 | 14628 | 14.628 | 567 | 2.463
4721 | 14637 | 14.637 | 283 | 2.7395
4722 | 14640 | 14.64 | 155 | 3.4095
4723 | 14680 | 14.68 | 18 | 2.5
4724 | 14501 | 14.501 | -352 | 0.1595
4725 | 14760 | 14.76 | -330 | 0.101
4726 | 14600 | 14.6 | 991 | 0.569
4727 | 14427 | 14.427 | -896 | 0.3565
4728 | 14775 | 14.775 | 767 | 0.532
4729 | 14485 | 14.485 | 542 | 2.537
4730 | 14461 | 14.461 | 240 | 0.064
4731 | 14675 | 14.675 | 524 | 1.787
4732 | 14666 | 14.666 | -270 | 4.7765
4733 | 14614 | 14.614 | 10 | 4.835
4734 | 14457 | 14.457 | -635 | 2.7075
4735 | 14800 | 14.8 | -176 | 1.968
4736 | 14525 | 14.525 | 365 | 1.1915
4737 | 14513 | 14.513 | 980 | 2.287
4738 | 14619 | 14.619 | -157 | 2.6545
4739 | 14740 | 14.74 | 139 | 1.6275
4740 | 14631 | 14.631 | -891 | 2.2075
4741 | 14571 | 14.571 | 804 | 1.4735
4742 | 14645 | 14.645 | -174 | 1.5955
4743 | 14682 | 14.682 | 887 | 1.218
4744 | 14422 | 14.422 | 305 | 1.718
4745 | 14216 | 14.216 | 889 | 1.335
4746 | 13637 | 13.637 | 130 | 2.2765
4747 | 13797 | 13.797 | -381 | 2.617
4748 | 13910 | 13.91 | 969 | 1.968
4749 | 13958 | 13.958 | 270 | 1.383
4750 | 13029 | 13.029 | 629 | 1.33
4751 | 14453 | 14.453 | 164 | 1.2605
4752 | 14619 | 14.619 | -939 | 0.92
4753 | 14708 | 14.708 | -117 | 1.1275
4754 | 14779 | 14.779 | -943 | 1.1755
4755 | 14649 | 14.649 | -601 | 1.085
4756 | 14915 | 14.915 | -917 | 0.851
4757 | 14742 | 14.742 | -369 | 0.8405
4758 | 14704 | 14.704 | -706 | 0.984
4759 | 14832 | 14.832 | 299 | 1.2765
4760 | 14719 | 14.719 | 41 | 1.314
4761 | 14682 | 14.682 | -196 | 1.2075
4762 | 14737 | 14.737 | -21 | 1.037
4763 | 14750 | 14.75 | 749 | 0.8775
4764 | 14827 | 14.827 | -712 | 0.899
4765 | 14804 | 14.804 | -584 | 0.915
4766 | 14687 | 14.687 | 950 | 0.718
4767 | 14752 | 14.752 | 464 | 0.782
4768 | 14706 | 14.706 | -120 | 1.0105
4769 | 14790 | 14.79 | 892 | 0.9415
4770 | 14578 | 14.578 | -180 | 1.2235
4771 | 14751 | 14.751 | 505 | 1.064
4772 | 14666 | 14.666 | -976 | 1.415
4773 | 14935 | 14.935 | 755 | 2.287
4774 | 14670 | 14.67 | 768 | 2.633
4775 | 14742 | 14.742 | -575 | 3.702
4776 | 14728 | 14.728 | 447 | 3.83
4777 | 14536 | 14.536 | 682 | 4.617
4778 | 14598 | 14.598 | -48 | 4.7445
4779 | 14701 | 14.701 | -145 | 4.8935
4780 | 14580 | 14.58 | -938 | 4.915
4781 | 14410 | 14.41 | 190 | 4.8885
4782 | 14481 | 14.481 | -652 | 4.883
4783 | 14425 | 14.425 | -929 | 4.83
4784 | 14642 | 14.642 | -948 | 4.963
4785 | 14553 | 14.553 | 435 | 4.75
4786 | 14690 | 14.69 | -8 | 4.367
4787 | 14508 | 14.508 | -967 | 4.266
4788 | 14594 | 14.594 | 135 | 3.383
4789 | 14721 | 14.721 | -706 | 2.734
4790 | 14549 | 14.549 | 824 | 3.3935
4791 | 14707 | 14.707 | -60 | 2.601
4792 | 14582 | 14.582 | 862 | 2.234
4793 | 14642 | 14.642 | -556 | 1.5
4794 | 14102 | 14.102 | -10 | 1.7765
4795 | 13257 | 13.257 | -575 | 2.686
4796 | 14441 | 14.441 | 70 | 2.197
4797 | 14760 | 14.76 | -34 | 1.4575
4798 | 14689 | 14.689 | 561 | 1.266
4799 | 14748 | 14.748 | -391 | 1.883
4800 | 14561 | 14.561 | 547 | 1.314
4801 | 14822 | 14.822 | -664 | 1.9095
4802 | 14851 | 14.851 | 66 | 1.58
4803 | 14720 | 14.72 | 168 | 1.8085
4804 | 14810 | 14.81 | -458 | 1.048
4805 | 14748 | 14.748 | 468 | 1.6065
4806 | 14794 | 14.794 | 253 | 1.4785
4807 | 14773 | 14.773 | -888 | 0.553
4808 | 14655 | 14.655 | -963 | 0.5585
4809 | 14780 | 14.78 | -175 | 0.548
4810 | 14750 | 14.75 | 505 | 0.117
4811 | 14640 | 14.64 | -136 | 0.399
4812 | 14809 | 14.809 | 218 | 0.149
4813 | 14659 | 14.659 | -73 | 0.0905
4814 | 14727 | 14.727 | 536 | 0.17
4815 | 14648 | 14.648 | -965 | 0.447
4816 | 14780 | 14.78 | -774 | 0.782
4817 | 14308 | 14.308 | -768 | 0.6225
4818 | 14766 | 14.766 | 79 | 0.7075
4819 | 14745 | 14.745 | 425 | 0.702
4820 | 14619 | 14.619 | -150 | 0.702
4821 | 14549 | 14.549 | 764 | 1.032
4822 | 14744 | 14.744 | 438 | 1.569
4823 | 14708 | 14.708 | -279 | 3.463
4824 | 14586 | 14.586 | 590 | 2.83
4825 | 14585 | 14.585 | -545 | 2.1755
4826 | 14729 | 14.729 | 692 | 2.25
4827 | 14672 | 14.672 | 546 | 1.6545
4828 | 14556 | 14.556 | -747 | 1.2715
4829 | 14612 | 14.612 | -815 | 1.0105
4830 | 14667 | 14.667 | -442 | 1.4735
4831 | 14646 | 14.646 | -77 | 1.9735
4832 | 14611 | 14.611 | 460 | 2.8405
4833 | 14645 | 14.645 | 433 | 3.4045
4834 | 14675 | 14.675 | 252 | 3.053
4835 | 14502 | 14.502 | 721 | 3.319
4836 | 14767 | 14.767 | -177 | 3.303
4837 | 14637 | 14.637 | 103 | 3.0585
4838 | 14755 | 14.755 | 708 | 4.3885
4839 | 14673 | 14.673 | 499 | 4.8615
4840 | 14047 | 14.047 | 237 | 4.6755
4841 | 13693 | 13.693 | -348 | 4.0265
4842 | 13883 | 13.883 | -543 | 3.8775
4843 | 14001 | 14.001 | -268 | 3.835
4844 | 13766 | 13.766 | 302 | 4.314
4845 | 13231 | 13.231 | -89 | 4.8565
4846 | 14558 | 14.558 | 888 | 4.335
4847 | 14650 | 14.65 | 988 | 4.6275
4848 | 14798 | 14.798 | 593 | 4.633
4849 | 14763 | 14.763 | 640 | 4.883
4850 | 14871 | 14.871 | -125 | 4.8615
4851 | 14829 | 14.829 | -114 | 4.9735
4852 | 14687 | 14.687 | 854 | 4.952
4853 | 14807 | 14.807 | -901 | 4.67
4854 | 14870 | 14.87 | 569 | 4.734
4855 | 14797 | 14.797 | -923 | 4.463
4856 | 14703 | 14.703 | 582 | 3.984
4857 | 14803 | 14.803 | -33 | 4.8885
4858 | 14683 | 14.683 | -903 | 4.9255
4859 | 14754 | 14.754 | 206 | 4.314
4860 | 14697 | 14.697 | 627 | 4.936
4861 | 14872 | 14.872 | -798 | 4.9785
4862 | 14716 | 14.716 | -735 | 4.851
4863 | 14685 | 14.685 | -564 | 4.899
4864 | 14726 | 14.726 | -566 | 4.936
4865 | 14580 | 14.58 | -210 | 4.415
4866 | 14537 | 14.537 | 786 | 3.58
4867 | 14715 | 14.715 | -903 | 4.787
4868 | 14761 | 14.761 | -312 | 4.8935
4869 | 14588 | 14.588 | 284 | 4.8565
4870 | 14725 | 14.725 | -361 | 4.915
4871 | 14612 | 14.612 | 255 | 4.7925
4872 | 14539 | 14.539 | 874 | 4.718
4873 | 14745 | 14.745 | -139 | 4.5
4874 | 14578 | 14.578 | 151 | 4.6595
4875 | 14515 | 14.515 | 795 | 4.6115
4876 | 14678 | 14.678 | -584 | 4.803
4877 | 14441 | 14.441 | 572 | 4.9415
4878 | 14743 | 14.743 | -32 | 4.9255
4879 | 14579 | 14.579 | -62 | 4.6755
4880 | 14727 | 14.727 | -823 | 4.6225
4881 | 14725 | 14.725 | 168 | 3.947
4882 | 14575 | 14.575 | 804 | 3.686
4883 | 14696 | 14.696 | 179 | 3.9415
4884 | 14432 | 14.432 | -273 | 3.415
4885 | 14754 | 14.754 | 922 | 3.564
4886 | 14625 | 14.625 | -641 | 3.697
4887 | 14269 | 14.269 | -222 | 3.4415
4888 | 13382 | 13.382 | -391 | 4.3935
4889 | 14040 | 14.04 | -542 | 4.633
4890 | 14642 | 14.642 | 826 | 4.234
4891 | 14579 | 14.579 | -717 | 3.899
4892 | 14626 | 14.626 | -118 | 3.5
4893 | 14709 | 14.709 | 211 | 3.702
4894 | 14573 | 14.573 | -705 | 3.665
4895 | 14745 | 14.745 | 249 | 2.4255
4896 | 14743 | 14.743 | 158 | 1.899
4897 | 14669 | 14.669 | 521 | 2.117
4898 | 14798 | 14.798 | 704 | 2.4045
4899 | 14678 | 14.678 | -624 | 2.5215
4900 | 14686 | 14.686 | -618 | 2.782
4901 | 14778 | 14.778 | -409 | 2.3775
4902 | 14620 | 14.62 | 517 | 2.4575
4903 | 14828 | 14.828 | -639 | 1.3405
4904 | 14777 | 14.777 | -403 | 1.383
4905 | 14737 | 14.737 | 853 | 3.085
4906 | 14734 | 14.734 | 140 | 3.213
4907 | 14658 | 14.658 | 647 | 3.3085
4908 | 14756 | 14.756 | -84 | 3.6275
4909 | 14745 | 14.745 | -435 | 3.0105
4910 | 14688 | 14.688 | 574 | 3.037
4911 | 14735 | 14.735 | -417 | 3.3725
4912 | 14748 | 14.748 | 51 | 3.2925
4913 | 14774 | 14.774 | 833 | 3.17
4914 | 14548 | 14.548 | 871 | 3
4915 | 14601 | 14.601 | -378 | 3.0745
4916 | 14825 | 14.825 | -492 | 3.3565
4917 | 14631 | 14.631 | 417 | 3.915
4918 | 14755 | 14.755 | 395 | 4.213
4919 | 14693 | 14.693 | 701 | 3.6385
4920 | 14623 | 14.623 | -667 | 3.5265
4921 | 14707 | 14.707 | 675 | 4.2605
4922 | 14678 | 14.678 | 843 | 3.8885
4923 | 14602 | 14.602 | -58 | 2.8725
4924 | 14483 | 14.483 | -103 | 2.8245
4925 | 14737 | 14.737 | -928 | 2.234
4926 | 14743 | 14.743 | -567 | 1.6065
4927 | 14611 | 14.611 | 377 | 1.9735
4928 | 14597 | 14.597 | -908 | 1.9945
4929 | 14789 | 14.789 | -779 | 3.149
4930 | 14487 | 14.487 | -118 | 3.42
4931 | 14778 | 14.778 | -595 | 3.4255
4932 | 14680 | 14.68 | 916 | 4.1435
4933 | 14696 | 14.696 | 633 | 4.5745
4934 | 14637 | 14.637 | 164 | 4.5
4935 | 14657 | 14.657 | 216 | 4.2445
4936 | 14747 | 14.747 | -711 | 2.915
4937 | 14683 | 14.683 | 629 | 4.0105
4938 | 14490 | 14.49 | 227 | 4.186
4939 | 13883 | 13.883 | 667 | 4.0265
4940 | 13725 | 13.725 | -824 | 4
4941 | 13867 | 13.867 | 657 | 4.1275
4942 | 14147 | 14.147 | -320 | 4.1595
4943 | 13452 | 13.452 | -886 | 4.2075
4944 | 14157 | 14.157 | -781 | 4.181
4945 | 14663 | 14.663 | 832 | 4.2235
4946 | 14691 | 14.691 | 518 | 4.6385
4947 | 14795 | 14.795 | -105 | 4.5
4948 | 14650 | 14.65 | 330 | 4.9045
4949 | 14785 | 14.785 | -940 | 4.8565
4950 | 14721 | 14.721 | -886 | 4.9045
4951 | 14880 | 14.88 | 337 | 4.968
4952 | 14763 | 14.763 | -89 | 4.984
4953 | 14669 | 14.669 | 913 | 3.08
4954 | 14834 | 14.834 | 974 | 4.9785
4955 | 14637 | 14.637 | -654 | 4.9575
4956 | 14857 | 14.857 | -139 | 4.947
4957 | 14816 | 14.816 | -889 | 4.936
4958 | 14641 | 14.641 | -720 | 4.899
4959 | 14839 | 14.839 | 203 | 4.899
4960 | 14838 | 14.838 | -573 | 4.963
4961 | 14615 | 14.615 | 409 | 4.9785
4962 | 14578 | 14.578 | 260 | 4.9735
4963 | 14727 | 14.727 | 617 | 4.963
4964 | 14722 | 14.722 | 618 | 4.984
4965 | 14596 | 14.596 | 487 | 4.936
4966 | 14821 | 14.821 | -515 | 4.9735
4967 | 14572 | 14.572 | 503 | 4.8085
4968 | 14628 | 14.628 | 334 | 4.947
4969 | 14624 | 14.624 | -51 | 4.952
4970 | 14714 | 14.714 | -914 | 4.936
4971 | 14726 | 14.726 | 970 | 4.883
4972 | 14409 | 14.409 | 855 | 4.681
4973 | 14738 | 14.738 | 681 | 3.4735
4974 | 14657 | 14.657 | -98 | 4.3565
4975 | 14642 | 14.642 | 894 | 3.7395
4976 | 14654 | 14.654 | 643 | 4.165
4977 | 14568 | 14.568 | -547 | 4.516
4978 | 14641 | 14.641 | 867 | 4.314
4979 | 14646 | 14.646 | -867 | 3.7075
4980 | 14771 | 14.771 | 249 | 2.6595
4981 | 14733 | 14.733 | -658 | 0.7765
4982 | 14768 | 14.768 | 20 | 0.452
4983 | 14622 | 14.622 | -144 | 1.75
4984 | 14899 | 14.899 | -803 | 3.117
4985 | 14711 | 14.711 | 780 | 3.1435
4986 | 14718 | 14.718 | 912 | 4.8615
4987 | 14686 | 14.686 | -404 | 4.8935
4988 | 14778 | 14.778 | -42 | 4.7445
4989 | 14782 | 14.782 | 594 | 4.5425
4990 | 14558 | 14.558 | 598 | 4.303
4991 | 14820 | 14.82 | -248 | 4.537
4992 | 14583 | 14.583 | 367 | 4.6115
4993 | 14797 | 14.797 | 364 | 4.782
4994 | 14799 | 14.799 | 667 | 4.83
4995 | 14695 | 14.695 | -454 | 4.7395
4996 | 14657 | 14.657 | -125 | 4.803
4997 | 14829 | 14.829 | -843 | 4.883
4998 | 14789 | 14.789 | 731 | 4.8405
4999 | 14790 | 14.79 | -662 | 2.5905
5000 | 14701 | 14.701 | 201 | 0.665
5001 | 14739 | 14.739 | 61 | 0.0745
5002 | 14851 | 14.851 | -808 | 3.968
5003 | 14694 | 14.694 | 861 | 4.915
5004 | 14774 | 14.774 | 289 | 4.8775
5005 | 14856 | 14.856 | 962 | 4.9045
5006 | 14769 | 14.769 | -277 | 4.931
5007 | 14751 | 14.751 | 76 | 4.9575
5008 | 14759 | 14.759 | -654 | 3.6385
5009 | 14744 | 14.744 | 816 | 2.6435
5010 | 14458 | 14.458 | -737 | 4.867
5011 | 14786 | 14.786 | -55 | 4.8935
5012 | 14616 | 14.616 | 865 | 4.9735
5013 | 14773 | 14.773 | 555 | 4.936
5014 | 14662 | 14.662 | 497 | 4.883
5015 | 14643 | 14.643 | -346 | 4.984
5016 | 14840 | 14.84 | 147 | 4.931
5017 | 14618 | 14.618 | 828 | 4.9945
5018 | 14657 | 14.657 | -158 | 4.5105
5019 | 14665 | 14.665 | 626 | 4.3775
5020 | 14667 | 14.667 | 5 | 4.1435
5021 | 14696 | 14.696 | 834 | 3.4095
5022 | 14721 | 14.721 | -29 | 3.6915
5023 | 14546 | 14.546 | -12 | 2.484
5024 | 14705 | 14.705 | -968 | 1.835
5025 | 14530 | 14.53 | -572 | 1.2285
5026 | 14772 | 14.772 | 458 | 2.08
5027 | 14688 | 14.688 | -947 | 0.83
5028 | 14774 | 14.774 | -891 | 1.287
5029 | 14654 | 14.654 | -414 | 1.6385
5030 | 14697 | 14.697 | -700 | 1.484
5031 | 14515 | 14.515 | 304 | 0.984
5032 | 14861 | 14.861 | -462 | 0.686
5033 | 14662 | 14.662 | 95 | 0.6595
5034 | 14751 | 14.751 | 343 | 0.6385
5035 | 14614 | 14.614 | 0 | 0.585
5036 | 14799 | 14.799 | -166 | 0.2925
5037 | 14730 | 14.73 | -1000 | 0.484
5038 | 14639 | 14.639 | 512 | 0.186
5039 | 14838 | 14.838 | -290 | 0.564
5040 | 14721 | 14.721 | 404 | 0.6275
5041 | 14582 | 14.582 | 48 | 0.5585
5042 | 14732 | 14.732 | -786 | 0.4575
5043 | 14875 | 14.875 | 556 | 0.5905
5044 | 14222 | 14.222 | -944 | 0.8245
5045 | 13630 | 13.63 | -353 | 0.75
5046 | 13814 | 13.814 | -806 | 0.7715
5047 | 13988 | 13.988 | -166 | 0.7075
5048 | 13989 | 13.989 | 177 | 0.803
5049 | 13190 | 13.19 | 203 | 0.718
5050 | 14532 | 14.532 | 293 | 0.7235
5051 | 14669 | 14.669 | 137 | 0.6065
5052 | 14749 | 14.749 | 965 | 0.67
5053 | 14689 | 14.689 | -330 | 0.7235
5054 | 14740 | 14.74 | -578 | 0.5265
5055 | 14741 | 14.741 | -56 | 0.6595
5056 | 14767 | 14.767 | 861 | 0.3615
5057 | 14892 | 14.892 | 246 | 0.181
5058 | 14573 | 14.573 | 256 | 0.202
5059 | 14734 | 14.734 | 716 | 0.1225
5060 | 14637 | 14.637 | 484 | 0.0745
5061 | 14722 | 14.722 | 551 | 0.0055
5062 | 14734 | 14.734 | -28 | 0.069
5063 | 14715 | 14.715 | -242 | 0.0905
5064 | 14682 | 14.682 | 100 | 0.1435
5065 | 14532 | 14.532 | 140 | 0.287
5066 | 14678 | 14.678 | 948 | 0.3085
5067 | 14575 | 14.575 | 257 | 0.3455
5068 | 14712 | 14.712 | 158 | 0.415
5069 | 14763 | 14.763 | 508 | 0.25
5070 | 14706 | 14.706 | -302 | 0.58
5071 | 14714 | 14.714 | -947 | 1.5955
5072 | 14734 | 14.734 | -910 | 2.718
5073 | 14607 | 14.607 | 581 | 1.968
5074 | 14729 | 14.729 | -989 | 1.8405
5075 | 14736 | 14.736 | 368 | 1.936
5076 | 14664 | 14.664 | 362 | 1.633
5077 | 14684 | 14.684 | 319 | 2.42
5078 | 14815 | 14.815 | -370 | 3.1915
5079 | 14787 | 14.787 | 167 | 3.6275
5080 | 14656 | 14.656 | -188 | 3.213
5081 | 14442 | 14.442 | -117 | 3.75
5082 | 13834 | 13.834 | -409 | 4.165
5083 | 13878 | 13.878 | 352 | 3.6275
5084 | 14714 | 14.714 | -955 | 3.2395
5085 | 14625 | 14.625 | 698 | 3.431
5086 | 14694 | 14.694 | 641 | 2.0585
5087 | 14794 | 14.794 | -604 | 3.197
5088 | 14727 | 14.727 | -827 | 2.58
5089 | 14823 | 14.823 | -996 | 2.553
5090 | 14770 | 14.77 | -502 | 3.0425
5091 | 14637 | 14.637 | -445 | 2.3935
5092 | 14901 | 14.901 | -191 | 2.6545
5093 | 14805 | 14.805 | 19 | 2.713
5094 | 14760 | 14.76 | -952 | 3.202
5095 | 14738 | 14.738 | -555 | 2.617
5096 | 14910 | 14.91 | -541 | 2.9415
5097 | 14595 | 14.595 | -241 | 3.1065
5098 | 14784 | 14.784 | -190 | 2.2285
5099 | 14910 | 14.91 | -28 | 2.266
5100 | 14704 | 14.704 | 448 | 1.6595
5101 | 14609 | 14.609 | -46 | 1.931
5102 | 14678 | 14.678 | -152 | 2.08
5103 | 14800 | 14.8 | -712 | 2.016
5104 | 14709 | 14.709 | 450 | 1.9415
5105 | 14723 | 14.723 | 701 | 2.697
5106 | 14625 | 14.625 | -595 | 2.367
5107 | 14657 | 14.657 | 443 | 1.8935
5108 | 14709 | 14.709 | -572 | 1.8455
5109 | 14744 | 14.744 | 423 | 1.798
5110 | 14591 | 14.591 | -674 | 1.4785
5111 | 14573 | 14.573 | 904 | 1.0905
5112 | 14700 | 14.7 | 178 | 1.415
5113 | 14570 | 14.57 | 92 | 1.7605
5114 | 14499 | 14.499 | 915 | 1.6435
5115 | 14596 | 14.596 | 341 | 1.5745
5116 | 14529 | 14.529 | 944 | 1.1275
5117 | 14562 | 14.562 | 670 | 1.0955
5118 | 14639 | 14.639 | -912 | 0.9895
5119 | 14462 | 14.462 | -54 | 1.0905
5120 | 14539 | 14.539 | -285 | 1.085
5121 | 14706 | 14.706 | 909 | 0.867
5122 | 14582 | 14.582 | 870 | 0.984
5123 | 14599 | 14.599 | -445 | 0.7925
5124 | 14765 | 14.765 | -20 | 0.7235
5125 | 14686 | 14.686 | -695 | 0.58
5126 | 14535 | 14.535 | 100 | 0.681
5127 | 14729 | 14.729 | -540 | 0.585
5128 | 14652 | 14.652 | -743 | 0.585
5129 | 14624 | 14.624 | 545 | 0.5
5130 | 14361 | 14.361 | -514 | 0.5105
5131 | 13619 | 13.619 | -893 | 0.4735
5132 | 13728 | 13.728 | 778 | 0.6225
5133 | 13911 | 13.911 | -377 | 0.4945
5134 | 14108 | 14.108 | -316 | 0.553
5135 | 13119 | 13.119 | 634 | 0.5
5136 | 14196 | 14.196 | -92 | 0.314
5137 | 14721 | 14.721 | 791 | 0.303
5138 | 14873 | 14.873 | -126 | 0.2395
5139 | 14809 | 14.809 | -761 | 0.218
5140 | 14806 | 14.806 | -253 | 0.218
5141 | 14750 | 14.75 | -499 | 0.186
5142 | 14806 | 14.806 | 750 | 0.181
5143 | 14780 | 14.78 | -875 | 0.197
5144 | 14808 | 14.808 | -789 | 0.335
5145 | 14885 | 14.885 | 556 | 0.399
5146 | 14706 | 14.706 | -580 | 0.3085
5147 | 14661 | 14.661 | 874 | 0.218
5148 | 14899 | 14.899 | 452 | 0.1755
5149 | 14783 | 14.783 | 130 | 0.218
5150 | 14571 | 14.571 | -193 | 0.186
5151 | 14758 | 14.758 | 584 | 0.149
5152 | 14693 | 14.693 | 888 | 0.0905
5153 | 14630 | 14.63 | -342 | 0.053
5154 | 14586 | 14.586 | 531 | 0.053
5155 | 14354 | 14.354 | -493 | 0.032
5156 | 14610 | 14.61 | -653 | 0
5157 | 14530 | 14.53 | -133 | 0
5158 | 14529 | 14.529 | -564 | 0.1065
5159 | 14594 | 14.594 | 609 | 0.069
5160 | 14567 | 14.567 | -996 | 0.2605
5161 | 14644 | 14.644 | 953 | 0.25
5162 | 14535 | 14.535 | 958 | 0.1065
5163 | 14536 | 14.536 | -870 | 0.2075
5164 | 14771 | 14.771 | 559 | 0.202
5165 | 14631 | 14.631 | -4 | 0.0585
5166 | 14601 | 14.601 | 206 | 0.0905
5167 | 14561 | 14.561 | -749 | 0.085
5168 | 14748 | 14.748 | 29 | 0.0955
5169 | 14620 | 14.62 | 587 | 0.0585
5170 | 14603 | 14.603 | -170 | 0.069
5171 | 14419 | 14.419 | 819 | 0.0745
5172 | 14794 | 14.794 | -385 | 0.08
5173 | 14866 | 14.866 | 144 | 0.0955
5174 | 14738 | 14.738 | 247 | 0.1225
5175 | 14810 | 14.81 | 756 | 0.0745
5176 | 14712 | 14.712 | 489 | 0.064
5177 | 14540 | 14.54 | 990 | 0.053
5178 | 13834 | 13.834 | -714 | 0.069
5179 | 13755 | 13.755 | -342 | 0.1065
5180 | 14715 | 14.715 | -439 | 0.0955
5181 | 14810 | 14.81 | -720 | 0.2235
5182 | 14818 | 14.818 | -213 | 0.2395
5183 | 14893 | 14.893 | 887 | 0.165
5184 | 14760 | 14.76 | 916 | 0.186
5185 | 14778 | 14.778 | 218 | 0.17
5186 | 14866 | 14.866 | -783 | 0.1385
5187 | 14844 | 14.844 | -383 | 0.1275
5188 | 14816 | 14.816 | 344 | 0.1115
5189 | 14727 | 14.727 | -430 | 0.069
5190 | 14723 | 14.723 | -172 | 0.101
5191 | 14748 | 14.748 | -159 | 0.1275
5192 | 14692 | 14.692 | -639 | 0.1595
5193 | 14833 | 14.833 | 247 | 0.165
5194 | 14699 | 14.699 | 933 | 0.133
5195 | 14825 | 14.825 | -575 | 0.202
5196 | 14662 | 14.662 | 276 | 0.1595
5197 | 14776 | 14.776 | 88 | 0.133
5198 | 14663 | 14.663 | -761 | 0.1225
5199 | 14682 | 14.682 | 663 | 0.117
5200 | 14865 | 14.865 | -141 | 0.0585
5201 | 14626 | 14.626 | -246 | 0.08
5202 | 14773 | 14.773 | -169 | 0.08
5203 | 14731 | 14.731 | -521 | 0.069
5204 | 14678 | 14.678 | -610 | 0.08
5205 | 14797 | 14.797 | 246 | 0.069
5206 | 14736 | 14.736 | -173 | 0.0215
5207 | 14726 | 14.726 | -574 | 0.0425
5208 | 14688 | 14.688 | -772 | 0.037
5209 | 14608 | 14.608 | 233 | 0.037
5210 | 14823 | 14.823 | 359 | 0.0955
5211 | 14582 | 14.582 | 147 | 0.0585
5212 | 14697 | 14.697 | 546 | 0.064
5213 | 14612 | 14.612 | 177 | 0.0585
5214 | 14703 | 14.703 | -275 | 0.08
5215 | 14619 | 14.619 | -815 | 0.1385
5216 | 14715 | 14.715 | 475 | 0.1275
5217 | 14701 | 14.701 | -200 | 0.085
5218 | 14608 | 14.608 | -991 | 0.117
5219 | 14763 | 14.763 | -615 | 0.117
5220 | 14554 | 14.554 | -151 | 0.08
5221 | 14852 | 14.852 | -9 | 0.037
5222 | 14713 | 14.713 | -131 | 0.0215
5223 | 14618 | 14.618 | 939 | 0.0055
5224 | 14720 | 14.72 | -902 | 0.0265
5225 | 14763 | 14.763 | 241 | 0.016
5226 | 14828 | 14.828 | 490 | 0.0055
5227 | 14759 | 14.759 | -279 | 0
5228 | 14640 | 14.64 | 904 | 0
5229 | 14853 | 14.853 | 276 | 0.0055
5230 | 14670 | 14.67 | 809 | 0
5231 | 14735 | 14.735 | -527 | 0
5232 | 14747 | 14.747 | 175 | 0
5233 | 14746 | 14.746 | -698 | 0
5234 | 14767 | 14.767 | -9 | 0
5235 | 14773 | 14.773 | 317 | 0
5236 | 14836 | 14.836 | 342 | 0
5237 | 14733 | 14.733 | 828 | 0.048
5238 | 14844 | 14.844 | 889 | 0.1225
5239 | 14798 | 14.798 | -195 | 0.25
5240 | 14737 | 14.737 | 657 | 0.303
5241 | 14802 | 14.802 | 487 | 0.431
5242 | 14708 | 14.708 | -520 | 0.6225
5243 | 14726 | 14.726 | 495 | 0.5055
5244 | 14869 | 14.869 | -141 | 0.2555
5245 | 14812 | 14.812 | -837 | 0.335
5246 | 14753 | 14.753 | -52 | 0.314
5247 | 14675 | 14.675 | -760 | 0.367
5248 | 14938 | 14.938 | 850 | 0.2075
5249 | 14633 | 14.633 | -311 | 0.149
5250 | 14632 | 14.632 | 872 | 0.1915
5251 | 14501 | 14.501 | 668 | 0.303
5252 | 14792 | 14.792 | 393 | 0.314
5253 | 14642 | 14.642 | -285 | 0.303
5254 | 14626 | 14.626 | 861 | 0.181
5255 | 14737 | 14.737 | -711 | 0.2235
5256 | 14688 | 14.688 | -995 | 0.3455
5257 | 14727 | 14.727 | -84 | 0.564
5258 | 14790 | 14.79 | -616 | 0.6435
5259 | 14437 | 14.437 | 22 | 0.4095
5260 | 14664 | 14.664 | -485 | 0.287
5261 | 14469 | 14.469 | 883 | 0.3885
5262 | 14853 | 14.853 | 428 | 0.5055
5263 | 14632 | 14.632 | 68 | 0.484
5264 | 14827 | 14.827 | -101 | 0.601
5265 | 14621 | 14.621 | 379 | 0.6065
5266 | 14568 | 14.568 | -267 | 0.516
5267 | 14808 | 14.808 | -234 | 0.5215
5268 | 14715 | 14.715 | 322 | 0.819
5269 | 14493 | 14.493 | 793 | 1.0585
5270 | 14746 | 14.746 | -488 | 0.814
5271 | 14712 | 14.712 | 444 | 0.9045
5272 | 14608 | 14.608 | -942 | 1.048
5273 | 14795 | 14.795 | -806 | 1.1435
5274 | 14788 | 14.788 | -751 | 1.1275
5275 | 14482 | 14.482 | -500 | 1.069
5276 | 14804 | 14.804 | 62 | 1.0215
5277 | 14812 | 14.812 | 438 | 0.968
5278 | 14672 | 14.672 | -710 | 0.963
5279 | 14797 | 14.797 | -35 | 0.8565
5280 | 14672 | 14.672 | 650 | 0.9045
5281 | 14762 | 14.762 | -972 | 0.931
5282 | 14718 | 14.718 | -114 | 0.6755
5283 | 14788 | 14.788 | 638 | 0.6275
5284 | 14709 | 14.709 | 896 | 0.75
5285 | 14786 | 14.786 | 423 | 0.819
5286 | 14670 | 14.67 | -14 | 0.9945
5287 | 14535 | 14.535 | 411 | 0.8885
5288 | 14844 | 14.844 | -651 | 0.9095
5289 | 13905 | 13.905 | 33 | 0.92
5290 | 13786 | 13.786 | 521 | 1.032
5291 | 13840 | 13.84 | -784 | 1.016
5292 | 14035 | 14.035 | -712 | 1.085
5293 | 13968 | 13.968 | 326 | 1.1595
5294 | 13186 | 13.186 | -834 | 1.3565
5295 | 14593 | 14.593 | 414 | 1.2285
5296 | 14740 | 14.74 | 217 | 1.037
5297 | 14718 | 14.718 | -284 | 1.3455
5298 | 14541 | 14.541 | 676 | 1.633
5299 | 14677 | 14.677 | -548 | 0.963
5300 | 14805 | 14.805 | -785 | 0.814
5301 | 14635 | 14.635 | 733 | 2.947
5302 | 14775 | 14.775 | 813 | 3.697
5303 | 14651 | 14.651 | 429 | 3.798
5304 | 14690 | 14.69 | -100 | 3.702
5305 | 14792 | 14.792 | -738 | 3.4255
5306 | 14668 | 14.668 | -450 | 3.3085
5307 | 14619 | 14.619 | -617 | 3.383
5308 | 14778 | 14.778 | -505 | 3.117
5309 | 14779 | 14.779 | -684 | 2.7605
5310 | 14685 | 14.685 | 972 | 3.463
5311 | 14661 | 14.661 | -512 | 3.314
5312 | 14781 | 14.781 | 537 | 2.287
5313 | 14687 | 14.687 | 306 | 2.1435
5314 | 14738 | 14.738 | -811 | 2.1595
5315 | 14704 | 14.704 | -648 | 1.7715
5316 | 14801 | 14.801 | 718 | 1.681
5317 | 14575 | 14.575 | 732 | 2.117
5318 | 14745 | 14.745 | 761 | 1.8405
5319 | 14804 | 14.804 | -124 | 1.5055
5320 | 14452 | 14.452 | -29 | 1.484
5321 | 13829 | 13.829 | -172 | 1.8455
5322 | 13563 | 13.563 | 361 | 1.984
5323 | 14657 | 14.657 | -447 | 2.899
5324 | 14692 | 14.692 | -234 | 3.25
5325 | 14705 | 14.705 | 676 | 3.3405
5326 | 14748 | 14.748 | -102 | 3.936
5327 | 14836 | 14.836 | 497 | 3.798
5328 | 14573 | 14.573 | -889 | 4.553
5329 | 14787 | 14.787 | 126 | 4.7395
5330 | 14685 | 14.685 | -326 | 4.883
5331 | 14813 | 14.813 | 376 | 4.931
5332 | 14788 | 14.788 | 550 | 4.9095
5333 | 14833 | 14.833 | 108 | 4.9785
5334 | 14840 | 14.84 | -938 | 3.25
5335 | 14740 | 14.74 | 524 | 0.314
5336 | 14844 | 14.844 | 177 | 0.9255
5337 | 14652 | 14.652 | 956 | 0.0585
5338 | 14787 | 14.787 | 911 | 1.484
5339 | 14784 | 14.784 | -581 | 0.0585
5340 | 14779 | 14.779 | 136 | 0.7555
5341 | 14834 | 14.834 | -571 | 4.2235
5342 | 14726 | 14.726 | 106 | 4.915
5343 | 14753 | 14.753 | -12 | 4.899
5344 | 14750 | 14.75 | -471 | 4.8565
5345 | 14658 | 14.658 | 764 | 4.2445
5346 | 14673 | 14.673 | 605 | 3.92
5347 | 14654 | 14.654 | -470 | 3.9735
5348 | 14556 | 14.556 | 235 | 3.016
5349 | 14946 | 14.946 | -943 | 2.6915
5350 | 14550 | 14.55 | 629 | 2.798
5351 | 14792 | 14.792 | 476 | 2.0955
5352 | 14658 | 14.658 | 740 | 2.1115
5353 | 14733 | 14.733 | 763 | 1.197
5354 | 14655 | 14.655 | 959 | 0.649
5355 | 14686 | 14.686 | -5 | 0.181
5356 | 14611 | 14.611 | -838 | 0.149
5357 | 14846 | 14.846 | 331 | 0.149
5358 | 14653 | 14.653 | 264 | 0.25
5359 | 14727 | 14.727 | -992 | 0.6065
5360 | 14628 | 14.628 | 202 | 0.649
5361 | 14676 | 14.676 | 940 | 0.3615
5362 | 14661 | 14.661 | -867 | 0.6435
5363 | 14759 | 14.759 | 839 | 0.9095
5364 | 14661 | 14.661 | -438 | 1.5905
5365 | 14727 | 14.727 | -553 | 2.5425
5366 | 14608 | 14.608 | 820 | 3.3885
5367 | 14832 | 14.832 | 17 | 3.564
5368 | 14666 | 14.666 | -767 | 3.7285
5369 | 14368 | 14.368 | 569 | 4.548
5370 | 13763 | 13.763 | 129 | 3.5585
5371 | 13704 | 13.704 | 575 | 1.75
5372 | 14065 | 14.065 | -307 | 4.963
5373 | 14159 | 14.159 | 358 | 4.92
5374 | 13185 | 13.185 | 363 | 4.7445
5375 | 14196 | 14.196 | 209 | 0.3245
5376 | 14657 | 14.657 | -420 | 4.9575
5377 | 14796 | 14.796 | -439 | 4.9895
5378 | 14830 | 14.83 | -196 | 4.9735
5379 | 14709 | 14.709 | -685 | 4.984
5380 | 14741 | 14.741 | 254 | 4.7925
5381 | 14631 | 14.631 | 285 | 4.819
5382 | 14964 | 14.964 | 457 | 4.4045
5383 | 14854 | 14.854 | -573 | 1.399
5384 | 14736 | 14.736 | 621 | 2.814
5385 | 14769 | 14.769 | -154 | 1.4415
5386 | 14733 | 14.733 | 934 | 2.3085
5387 | 14761 | 14.761 | -101 | 3.0745
5388 | 14834 | 14.834 | 998 | 4.351
5389 | 14742 | 14.742 | 23 | 4.3885
5390 | 14682 | 14.682 | -96 | 2.702
5391 | 14854 | 14.854 | -869 | 3.0905
5392 | 14789 | 14.789 | 966 | 2.9945
5393 | 14961 | 14.961 | 853 | 3.1065
5394 | 14756 | 14.756 | 343 | 3.915
5395 | 14668 | 14.668 | 460 | 4.2555
5396 | 14622 | 14.622 | 630 | 4.6275
5397 | 14714 | 14.714 | -716 | 4.17
5398 | 14728 | 14.728 | 923 | 4.633
5399 | 14793 | 14.793 | 448 | 2.7235
5400 | 14579 | 14.579 | 766 | 3.319
5401 | 14474 | 14.474 | -146 | 4.8455
5402 | 14759 | 14.759 | -359 | 4.5905
5403 | 14733 | 14.733 | -799 | 4.1385
5404 | 14661 | 14.661 | -229 | 3.6755
5405 | 14607 | 14.607 | 841 | 3.6115
5406 | 14648 | 14.648 | 199 | 2.936
5407 | 14639 | 14.639 | -128 | 4.3455
5408 | 14724 | 14.724 | -115 | 3.4895
5409 | 14536 | 14.536 | 424 | 4.016
5410 | 14578 | 14.578 | -177 | 4.0105
5411 | 14805 | 14.805 | -449 | 3.681
5412 | 14496 | 14.496 | 918 | 3.9945
5413 | 14675 | 14.675 | -649 | 4.984
5414 | 14680 | 14.68 | -864 | 4.963
5415 | 14516 | 14.516 | 607 | 1.814
5416 | 14491 | 14.491 | 57 | 0.1115
5417 | 14711 | 14.711 | -62 | 0.1435
5418 | 14433 | 14.433 | -521 | 2.569
5419 | 13366 | 13.366 | 831 | 5
5420 | 14017 | 14.017 | -259 | 5
5421 | 14577 | 14.577 | 901 | 4.9945
5422 | 14534 | 14.534 | -772 | 4.9895
5423 | 14708 | 14.708 | -772 | 4.9945
5424 | 14552 | 14.552 | 752 | 4.9895
5425 | 14545 | 14.545 | 911 | 1.3935
5426 | 14643 | 14.643 | 402 | 4.9945
5427 | 14651 | 14.651 | 191 | 4.9945
5428 | 14589 | 14.589 | 309 | 2.149
5429 | 14679 | 14.679 | -881 | 0.1065
5430 | 14637 | 14.637 | -490 | 1.686
5431 | 14805 | 14.805 | 354 | 0.0905
5432 | 14520 | 14.52 | 120 | 1.7605
5433 | 14681 | 14.681 | 525 | 0.697
5434 | 14794 | 14.794 | 914 | 1.7555
5435 | 14500 | 14.5 | 428 | 1.984
5436 | 14786 | 14.786 | 186 | 3.101
5437 | 14571 | 14.571 | -716 | 2.899
5438 | 14786 | 14.786 | 978 | 1.564
5439 | 14572 | 14.572 | 137 | 0.6115
5440 | 14686 | 14.686 | -320 | 0.3565
5441 | 14506 | 14.506 | 218 | 0.335
5442 | 14784 | 14.784 | -681 | 0.516
5443 | 14535 | 14.535 | -172 | 0.1225
5444 | 14534 | 14.534 | -972 | 0
5445 | 14668 | 14.668 | 257 | 0.0215
5446 | 14589 | 14.589 | 119 | 0.149
5447 | 14688 | 14.688 | -734 | 0.197
5448 | 14459 | 14.459 | -5 | 0.399
5449 | 14640 | 14.64 | -900 | 0.4575
5450 | 14548 | 14.548 | 841 | 0.548
5451 | 14830 | 14.83 | -288 | 1.0905
5452 | 14615 | 14.615 | -281 | 1.3775
5453 | 14663 | 14.663 | 295 | 1.5215
5454 | 14561 | 14.561 | 68 | 2.335
5455 | 14708 | 14.708 | 849 | 2.314
5456 | 14640 | 14.64 | 335 | 2.1065
5457 | 14688 | 14.688 | 669 | 2.734
5458 | 14628 | 14.628 | -47 | 2.5105
5459 | 14696 | 14.696 | 538 | 3.165
5460 | 14602 | 14.602 | 564 | 3.67
5461 | 14589 | 14.589 | -552 | 3.6065
5462 | 14602 | 14.602 | -798 | 1.197
5463 | 14652 | 14.652 | -813 | 3.851
5464 | 14546 | 14.546 | -139 | 1.3245
5465 | 14800 | 14.8 | -504 | 4.9945
5466 | 14315 | 14.315 | 803 | 4.9785
5467 | 13685 | 13.685 | -99 | 4.9895
5468 | 13821 | 13.821 | 760 | 4.9895
5469 | 13917 | 13.917 | -459 | 4.9785
5470 | 13847 | 13.847 | -99 | 4.9735
5471 | 13507 | 13.507 | -143 | 4.2925
5472 | 14594 | 14.594 | 920 | 2.032
5473 | 14596 | 14.596 | 462 | 4.2285
5474 | 14770 | 14.77 | -112 | 1.7715
5475 | 14786 | 14.786 | -250 | 4.9255
5476 | 14622 | 14.622 | 43 | 4.8885
5477 | 14766 | 14.766 | -647 | 4.4735
5478 | 14603 | 14.603 | -40 | 4.5055
5479 | 14924 | 14.924 | 94 | 1.8775
5480 | 14835 | 14.835 | -714 | 0.064
5481 | 14726 | 14.726 | 388 | 0.2925
5482 | 14861 | 14.861 | 606 | 0.5585
5483 | 14809 | 14.809 | -195 | 3.649
5484 | 14680 | 14.68 | 434 | 2.867
5485 | 14809 | 14.809 | 890 | 3.282
5486 | 14645 | 14.645 | 948 | 4.7445
5487 | 14776 | 14.776 | -3 | 0.7925
5488 | 14668 | 14.668 | 274 | 4.548
5489 | 14574 | 14.574 | 229 | 3.702
5490 | 14788 | 14.788 | 25 | 4.4255
5491 | 14382 | 14.382 | 743 | 4.399
5492 | 14630 | 14.63 | 901 | 4.3775
5493 | 14534 | 14.534 | -641 | 4.181
5494 | 14479 | 14.479 | -230 | 4.335
5495 | 14682 | 14.682 | 279 | 4.8565
5496 | 14512 | 14.512 | -582 | 4.585
5497 | 14513 | 14.513 | 884 | 4.1385
5498 | 14474 | 14.474 | 900 | 4.3245
5499 | 14497 | 14.497 | 793 | 4.08
5500 | 14341 | 14.341 | 946 | 3.633
5501 | 14422 | 14.422 | -915 | 4.9095
5502 | 14463 | 14.463 | -260 | 3.931
5503 | 14501 | 14.501 | 779 | 4.2555
5504 | 14462 | 14.462 | -5 | 4.5425
5505 | 14466 | 14.466 | -836 | 4.1065
5506 | 14461 | 14.461 | -409 | 4.6595
5507 | 14374 | 14.374 | -601 | 4.83
5508 | 14606 | 14.606 | 251 | 4.8615
5509 | 14675 | 14.675 | 372 | 4.415
5510 | 14568 | 14.568 | -573 | 4.4045
5511 | 14804 | 14.804 | -729 | 3.303
5512 | 14627 | 14.627 | -689 | 2.367
5513 | 14688 | 14.688 | -635 | 4.5585
5514 | 14267 | 14.267 | -148 | 4.1545
5515 | 13707 | 13.707 | 823 | 4.5955
5516 | 13965 | 13.965 | -220 | 4.266
5517 | 14636 | 14.636 | 569 | 4.6595
5518 | 14972 | 14.972 | -761 | 4.617
5519 | 14820 | 14.82 | 404 | 4.1275
5520 | 14625 | 14.625 | -373 | 3.8565
5521 | 14890 | 14.89 | 806 | 3.9945
5522 | 14840 | 14.84 | -979 | 4.33
5523 | 14786 | 14.786 | -971 | 3.67
5524 | 14679 | 14.679 | -901 | 3.713
5525 | 14907 | 14.907 | 777 | 4.1915
5526 | 14732 | 14.732 | 451 | 3.665
5527 | 14761 | 14.761 | -727 | 2.8615
5528 | 14867 | 14.867 | -471 | 3.665
5529 | 14747 | 14.747 | -981 | 4.3885
5530 | 14871 | 14.871 | 509 | 3.287
5531 | 14695 | 14.695 | -632 | 3.686
5532 | 14626 | 14.626 | 759 | 3.7285
5533 | 14950 | 14.95 | 692 | 3.585
5534 | 14773 | 14.773 | 957 | 3.5215
5535 | 14805 | 14.805 | -346 | 3.6275
5536 | 14820 | 14.82 | -774 | 2.681
5537 | 14581 | 14.581 | 559 | 3.516
5538 | 14627 | 14.627 | -259 | 4.3085
5539 | 14774 | 14.774 | 159 | 4.553
5540 | 14640 | 14.64 | 576 | 4.702
5541 | 14635 | 14.635 | -367 | 4.6275
5542 | 14758 | 14.758 | -484 | 4.3935
5543 | 14676 | 14.676 | -536 | 4.8085
5544 | 14635 | 14.635 | -342 | 4.9415
5545 | 14567 | 14.567 | -62 | 4.803
5546 | 14800 | 14.8 | -225 | 4.4095
5547 | 14634 | 14.634 | 679 | 4.516
5548 | 14741 | 14.741 | -601 | 4.75
5549 | 14622 | 14.622 | 819 | 4.5585
5550 | 14724 | 14.724 | -925 | 4.734
5551 | 14708 | 14.708 | -992 | 4.734
5552 | 14666 | 14.666 | -8 | 4.9095
5553 | 14605 | 14.605 | -944 | 4.3565
5554 | 14827 | 14.827 | 404 | 3.8565
5555 | 14537 | 14.537 | -74 | 2.814
5556 | 14700 | 14.7 | 94 | 2.351
5557 | 14449 | 14.449 | 623 | 2.053
5558 | 14822 | 14.822 | -108 | 2.032
5559 | 14696 | 14.696 | -133 | 2.218
5560 | 14500 | 14.5 | -44 | 2.819
5561 | 14873 | 14.873 | 519 | 3.702
5562 | 14329 | 14.329 | 230 | 3.819
5563 | 14000 | 14 | -801 | 4.431
5564 | 13679 | 13.679 | 123 | 4.5955
5565 | 14039 | 14.039 | -66 | 4.8615
5566 | 14039 | 14.039 | 977 | 4.952
5567 | 13706 | 13.706 | -935 | 4.9735
5568 | 14155 | 14.155 | -915 | 4.8935
5569 | 14503 | 14.503 | 175 | 0
5570 | 14812 | 14.812 | -369 | 0
5571 | 14681 | 14.681 | 912 | 0
5572 | 14825 | 14.825 | -226 | 0
5573 | 14758 | 14.758 | 613 | 0
5574 | 14385 | 14.385 | -475 | 0
5575 | 14772 | 14.772 | -212 | 0
5576 | 14741 | 14.741 | 974 | 0
5577 | 14712 | 14.712 | 975 | 0
5578 | 14733 | 14.733 | 640 | 0
5579 | 14672 | 14.672 | 764 | 0
5580 | 14772 | 14.772 | 226 | 0
5581 | 14785 | 14.785 | 895 | 0
5582 | 14744 | 14.744 | -337 | 0
5583 | 14711 | 14.711 | -780 | 0
5584 | 14646 | 14.646 | -513 | 0
5585 | 14774 | 14.774 | 134 | 0
5586 | 14740 | 14.74 | 508 | 0
5587 | 14522 | 14.522 | -786 | 0
5588 | 14864 | 14.864 | -873 | 0
5589 | 14748 | 14.748 | -821 | 0
5590 | 14609 | 14.609 | 752 | 0
5591 | 14727 | 14.727 | -815 | 0
5592 | 14791 | 14.791 | 584 | 0
5593 | 14659 | 14.659 | 389 | 0
5594 | 14693 | 14.693 | 43 | 0
5595 | 14665 | 14.665 | -316 | 0
5596 | 14782 | 14.782 | 370 | 0
5597 | 14711 | 14.711 | -215 | 0
5598 | 14539 | 14.539 | -507 | 0
5599 | 14848 | 14.848 | -234 | 0
5600 | 14727 | 14.727 | 142 | 0
5601 | 14744 | 14.744 | -35 | 0
5602 | 14657 | 14.657 | 784 | 0
5603 | 14693 | 14.693 | -770 | 0
5604 | 14433 | 14.433 | -670 | 0
5605 | 14768 | 14.768 | -959 | 0
5606 | 14642 | 14.642 | 796 | 0
5607 | 14695 | 14.695 | 185 | 0
5608 | 14708 | 14.708 | 292 | 0
5609 | 14734 | 14.734 | 158 | 0
5610 | 14072 | 14.072 | 464 | 0
5611 | 13595 | 13.595 | -680 | 0
5612 | 14326 | 14.326 | -929 | 0
5613 | 14750 | 14.75 | 309 | 0
5614 | 14693 | 14.693 | -64 | 0
5615 | 14755 | 14.755 | 947 | 0
5616 | 14664 | 14.664 | 674 | 0
5617 | 14913 | 14.913 | -345 | 0.037
5618 | 14827 | 14.827 | -158 | 0.0265
5619 | 14772 | 14.772 | -66 | 0.0215
5620 | 14812 | 14.812 | 440 | 0
5621 | 14673 | 14.673 | -526 | 0
5622 | 14801 | 14.801 | 614 | 0
5623 | 14877 | 14.877 | 149 | 0
5624 | 14723 | 14.723 | -246 | 0
5625 | 14872 | 14.872 | 253 | 0
5626 | 14789 | 14.789 | 778 | 0
5627 | 14729 | 14.729 | 409 | 0
5628 | 14813 | 14.813 | 566 | 0.0055
5629 | 14548 | 14.548 | -193 | 0
5630 | 14905 | 14.905 | -508 | 0.0105
5631 | 14692 | 14.692 | 284 | 0.0905
5632 | 14827 | 14.827 | 79 | 0.1595
5633 | 14652 | 14.652 | -692 | 0.2715
5634 | 14706 | 14.706 | -416 | 0.2395
5635 | 14796 | 14.796 | 926 | 0.2395
5636 | 14628 | 14.628 | 190 | 0.447
5637 | 14528 | 14.528 | -694 | 0.5955
5638 | 14654 | 14.654 | -263 | 0.819
5639 | 14793 | 14.793 | -502 | 1.351
5640 | 14731 | 14.731 | 476 | 1.601
5641 | 14698 | 14.698 | -53 | 1.5
5642 | 14708 | 14.708 | -166 | 1.8615
5643 | 14606 | 14.606 | 38 | 1.9255
5644 | 14878 | 14.878 | -40 | 2.4415
5645 | 14665 | 14.665 | -394 | 2.8615
5646 | 14631 | 14.631 | -815 | 3.553
5647 | 14832 | 14.832 | -874 | 4.287
5648 | 14481 | 14.481 | 758 | 4.314
5649 | 14846 | 14.846 | -638 | 4.601
5650 | 14607 | 14.607 | -240 | 4.8405
5651 | 14811 | 14.811 | 140 | 4.787
5652 | 14626 | 14.626 | -925 | 4.7285
5653 | 14863 | 14.863 | -799 | 4.8615
5654 | 14575 | 14.575 | 71 | 4.8245
5655 | 14546 | 14.546 | -408 | 4.133
5656 | 14863 | 14.863 | -724 | 4.266
5657 | 14601 | 14.601 | 296 | 3.4575
5658 | 13896 | 13.896 | -684 | 2.436
5659 | 13788 | 13.788 | -456 | 1.553
5660 | 13807 | 13.807 | -914 | 1.266
5661 | 14064 | 14.064 | -449 | 1.516
5662 | 13743 | 13.743 | -252 | 1.351
5663 | 13461 | 13.461 | 791 | 1.4895
5664 | 14599 | 14.599 | -805 | 1.7285
5665 | 14687 | 14.687 | -948 | 1.787
5666 | 14882 | 14.882 | -746 | 1.915
5667 | 14693 | 14.693 | 520 | 2.0955
5668 | 14881 | 14.881 | -229 | 2.67
5669 | 14736 | 14.736 | 821 | 3.431
5670 | 14914 | 14.914 | -635 | 4.032
5671 | 14766 | 14.766 | 331 | 3.3085
5672 | 14746 | 14.746 | 252 | 4.5585
5673 | 14919 | 14.919 | -330 | 4.6275
5674 | 14716 | 14.716 | 18 | 4.686
5675 | 14636 | 14.636 | 680 | 4.681
5676 | 14828 | 14.828 | -757 | 3.468
5677 | 14891 | 14.891 | 805 | 4.9785
5678 | 14827 | 14.827 | 426 | 0.33
5679 | 14787 | 14.787 | -203 | 1.133
5680 | 14801 | 14.801 | 196 | 2.319
5681 | 14591 | 14.591 | -396 | 0.032
5682 | 14807 | 14.807 | 86 | 0.1385
5683 | 14695 | 14.695 | 376 | 0.0055
5684 | 14751 | 14.751 | 661 | 0.1755
5685 | 14681 | 14.681 | -549 | 0
5686 | 14868 | 14.868 | 37 | 2.553
5687 | 14667 | 14.667 | 828 | 1.186
5688 | 14773 | 14.773 | 31 | 0.0905
5689 | 14805 | 14.805 | 707 | 1.697
5690 | 14694 | 14.694 | -342 | 2.298
5691 | 14800 | 14.8 | -491 | 3.3885
5692 | 14555 | 14.555 | -90 | 4.1385
5693 | 14799 | 14.799 | -504 | 4.9045
5694 | 14717 | 14.717 | 59 | 4.899
5695 | 14815 | 14.815 | 834 | 4.0215
5696 | 14741 | 14.741 | 183 | 2.42
5697 | 14669 | 14.669 | 938 | 4.2395
5698 | 14553 | 14.553 | 770 | 3.218
5699 | 14822 | 14.822 | 26 | 3.314
5700 | 14580 | 14.58 | 956 | 3.3405
5701 | 14498 | 14.498 | -811 | 3.4785
5702 | 14610 | 14.61 | 759 | 2.6275
5703 | 14552 | 14.552 | -95 | 1.8405
5704 | 13944 | 13.944 | 261 | 1.4895
5705 | 12877 | 12.877 | -829 | 1.782
5706 | 14080 | 14.08 | -484 | 2.649
5707 | 14677 | 14.677 | 64 | 1.2555
5708 | 14679 | 14.679 | 757 | 4.0955
5709 | 14766 | 14.766 | 803 | 2.4895
5710 | 14815 | 14.815 | -82 | 1.601
5711 | 14630 | 14.63 | 805 | 2.213
5712 | 14755 | 14.755 | 795 | 2.213
5713 | 14782 | 14.782 | -564 | 3.452
5714 | 14862 | 14.862 | 860 | 3.968
5715 | 14713 | 14.713 | -208 | 4.463
5716 | 14783 | 14.783 | -672 | 4.6065
5717 | 14732 | 14.732 | -202 | 4.67
5718 | 14864 | 14.864 | -262 | 4.6115
5719 | 14869 | 14.869 | 445 | 4.101
5720 | 14810 | 14.81 | -948 | 1.1435
5721 | 14766 | 14.766 | 739 | 0.053
5722 | 14721 | 14.721 | 368 | 0.0585
5723 | 14670 | 14.67 | 191 | 0.1385
5724 | 14727 | 14.727 | 12 | 0.787
5725 | 14778 | 14.778 | -711 | 1.585
5726 | 14778 | 14.778 | 995 | 4.8615
5727 | 14786 | 14.786 | -431 | 4.601
5728 | 14809 | 14.809 | -345 | 4.2715
5729 | 14674 | 14.674 | -940 | 4.5
5730 | 14622 | 14.622 | 143 | 4.58
5731 | 14663 | 14.663 | 129 | 4.399
5732 | 14508 | 14.508 | -110 | 4.718
5733 | 14792 | 14.792 | 280 | 4.867
5734 | 14685 | 14.685 | -244 | 4.83
5735 | 14748 | 14.748 | -566 | 4.665
5736 | 14655 | 14.655 | 752 | 4.798
5737 | 14537 | 14.537 | -357 | 4.899
5738 | 14685 | 14.685 | 464 | 4.814
5739 | 14756 | 14.756 | 744 | 4.8085
5740 | 14663 | 14.663 | 403 | 4.931
5741 | 14636 | 14.636 | -680 | 4.5905
5742 | 14881 | 14.881 | 499 | 4.085
5743 | 14483 | 14.483 | -32 | 4.6385
5744 | 14747 | 14.747 | -671 | 4.367
5745 | 14720 | 14.72 | 695 | 4.101
5746 | 14496 | 14.496 | 671 | 3.0105
5747 | 14782 | 14.782 | -338 | 2.186
5748 | 14628 | 14.628 | 173 | 1.8935
5749 | 14552 | 14.552 | 841 | 3.048
5750 | 14827 | 14.827 | -637 | 3.085
5751 | 14692 | 14.692 | -5 | 2.6275
5752 | 14508 | 14.508 | -579 | 2.4735
5753 | 14023 | 14.023 | 885 | 2.367
5754 | 13678 | 13.678 | 180 | 2.1595
5755 | 14080 | 14.08 | -724 | 1.9045
5756 | 14016 | 14.016 | 646 | 2.5585
5757 | 14079 | 14.079 | -407 | 2.7075
5758 | 13466 | 13.466 | 989 | 2.9415
5759 | 14579 | 14.579 | -909 | 3.7555
5760 | 14722 | 14.722 | -769 | 3.202
5761 | 14613 | 14.613 | -759 | 3.33
5762 | 14856 | 14.856 | -65 | 3.5425
5763 | 14955 | 14.955 | 433 | 3.7925
5764 | 14718 | 14.718 | 536 | 3.4575
5765 | 14822 | 14.822 | -272 | 3.186
5766 | 14759 | 14.759 | 91 | 2.8775
5767 | 14773 | 14.773 | 833 | 1.2445
5768 | 14843 | 14.843 | 983 | 2.564
5769 | 14778 | 14.778 | 778 | 1.8455
5770 | 14822 | 14.822 | 700 | 2.08
5771 | 14774 | 14.774 | 643 | 1.5745
5772 | 14692 | 14.692 | -979 | 1.2925
5773 | 14749 | 14.749 | -374 | 1.3725
5774 | 14727 | 14.727 | 827 | 1.7075
5775 | 14697 | 14.697 | -294 | 1.0055
5776 | 14825 | 14.825 | 230 | 1.0425
5777 | 14733 | 14.733 | 343 | 1.037
5778 | 14684 | 14.684 | -223 | 1.1115
5779 | 14694 | 14.694 | 367 | 1.665
5780 | 14776 | 14.776 | -442 | 1.6115
5781 | 14704 | 14.704 | -449 | 1.436
5782 | 14608 | 14.608 | 892 | 1.3615
5783 | 14678 | 14.678 | -22 | 1.564
5784 | 14736 | 14.736 | 91 | 1.814
5785 | 14666 | 14.666 | -829 | 2.7715
5786 | 14732 | 14.732 | -380 | 2.718
5787 | 14720 | 14.72 | -553 | 3.117
5788 | 14631 | 14.631 | -72 | 3.4045
5789 | 14561 | 14.561 | -260 | 2.6435
5790 | 14851 | 14.851 | -304 | 2.803
5791 | 14725 | 14.725 | -893 | 2.1065
5792 | 14612 | 14.612 | 548 | 1.8725
5793 | 14692 | 14.692 | 790 | 1.0905
5794 | 14542 | 14.542 | -582 | 0.7925
5795 | 14673 | 14.673 | -351 | 0.883
5796 | 14761 | 14.761 | -442 | 0.7445
5797 | 14705 | 14.705 | 138 | 0.4895
5798 | 14747 | 14.747 | -54 | 0.718
5799 | 14784 | 14.784 | -444 | 0.931
5800 | 14455 | 14.455 | 691 | 1.149
5801 | 14004 | 14.004 | 533 | 1.1435
5802 | 14245 | 14.245 | 906 | 1.1915
5803 | 14678 | 14.678 | 14 | 0.963
5804 | 14822 | 14.822 | -861 | 0.42
5805 | 14800 | 14.8 | -864 | 0.17
5806 | 14805 | 14.805 | 274 | 0.213
5807 | 14908 | 14.908 | -911 | 0.149
5808 | 14659 | 14.659 | -71 | 0.101
5809 | 14779 | 14.779 | -334 | 0.0585
5810 | 14890 | 14.89 | -916 | 0.0905
5811 | 14791 | 14.791 | 347 | 0.2395
5812 | 14851 | 14.851 | -915 | 0.17
5813 | 14779 | 14.779 | 0 | 0.101
5814 | 14931 | 14.931 | 220 | 0.1385
5815 | 14947 | 14.947 | 26 | 0.0745
5816 | 14811 | 14.811 | -255 | 0.085
5817 | 14887 | 14.887 | -993 | 0.016
5818 | 14766 | 14.766 | 748 | 0.069
5819 | 14758 | 14.758 | 261 | 0.1225
5820 | 14851 | 14.851 | 614 | 0.782
5821 | 14779 | 14.779 | 590 | 1.319
5822 | 14750 | 14.75 | -355 | 1.8935
5823 | 14684 | 14.684 | -708 | 1.053
5824 | 14737 | 14.737 | 18 | 0.33
5825 | 14655 | 14.655 | 324 | 0.3565
5826 | 14603 | 14.603 | 668 | 1
5827 | 14703 | 14.703 | -492 | 1.032
5828 | 14642 | 14.642 | -653 | 0.798
5829 | 14764 | 14.764 | 757 | 0.6385
5830 | 14681 | 14.681 | -586 | 1.1275
5831 | 14708 | 14.708 | 2 | 1.351
5832 | 14739 | 14.739 | -551 | 1.298
5833 | 14708 | 14.708 | -361 | 1.053
5834 | 14839 | 14.839 | 336 | 1.1435
5835 | 14699 | 14.699 | -655 | 1.282
5836 | 14484 | 14.484 | 99 | 0.883
5837 | 14883 | 14.883 | -647 | 1.0425
5838 | 14698 | 14.698 | 370 | 0.9895
5839 | 14673 | 14.673 | -811 | 0.814
5840 | 14874 | 14.874 | 202 | 0.6385
5841 | 14717 | 14.717 | -890 | 0.585
5842 | 14600 | 14.6 | 478 | 0.697
5843 | 14428 | 14.428 | 280 | 0.867
5844 | 14440 | 14.44 | 295 | 0.7925
5845 | 14700 | 14.7 | 599 | 1.0265
5846 | 14622 | 14.622 | -602 | 0.984
5847 | 14742 | 14.742 | -180 | 0.867
5848 | 14505 | 14.505 | -578 | 0.92
5849 | 13857 | 13.857 | -524 | 1.037
5850 | 13689 | 13.689 | 126 | 0.7925
5851 | 14139 | 14.139 | 264 | 0.7765
5852 | 14047 | 14.047 | 117 | 0.697
5853 | 13431 | 13.431 | -747 | 0.564
5854 | 13965 | 13.965 | -106 | 0.314
5855 | 14895 | 14.895 | 57 | 0.2605
5856 | 14841 | 14.841 | 867 | 0.1275
5857 | 14896 | 14.896 | -946 | 0.117
5858 | 14725 | 14.725 | 353 | 0.213
5859 | 15034 | 15.034 | 469 | 0.2765
5860 | 14916 | 14.916 | 361 | 0.266
5861 | 14774 | 14.774 | -238 | 0.3245
5862 | 15025 | 15.025 | -563 | 0.287
5863 | 14902 | 14.902 | 827 | 0.1435
5864 | 14767 | 14.767 | 132 | 0.367
5865 | 14944 | 14.944 | 530 | 0.202
5866 | 14852 | 14.852 | -127 | 0.101
5867 | 14921 | 14.921 | -891 | 0.2555
5868 | 14796 | 14.796 | 801 | 0.399
5869 | 14763 | 14.763 | 114 | 0.697
5870 | 14814 | 14.814 | -660 | 1.0265
5871 | 14797 | 14.797 | -861 | 1.234
5872 | 14684 | 14.684 | 620 | 0.7395
5873 | 14712 | 14.712 | -626 | 0.5215
5874 | 14762 | 14.762 | -771 | 0.351
5875 | 14738 | 14.738 | -643 | 0.447
5876 | 14779 | 14.779 | 246 | 0.5265
5877 | 14763 | 14.763 | 481 | 0.436
5878 | 14819 | 14.819 | -926 | 0.5955
5879 | 14712 | 14.712 | 627 | 1.314
5880 | 14752 | 14.752 | 70 | 1.2445
5881 | 14639 | 14.639 | -445 | 1.1915
5882 | 14883 | 14.883 | 250 | 1.053
5883 | 14743 | 14.743 | -305 | 0.968
5884 | 14804 | 14.804 | -257 | 1.1545
5885 | 14657 | 14.657 | -847 | 1.048
5886 | 14696 | 14.696 | -970 | 1.181
5887 | 14714 | 14.714 | 830 | 0.947
5888 | 14804 | 14.804 | 948 | 0.5905
5889 | 14692 | 14.692 | 391 | 0.4045
5890 | 14715 | 14.715 | -727 | 0.3455
5891 | 14747 | 14.747 | -4 | 0.3085
5892 | 14703 | 14.703 | 150 | 0.2445
5893 | 14673 | 14.673 | -771 | 0.25
5894 | 14725 | 14.725 | -628 | 0.2285
5895 | 14664 | 14.664 | 283 | 0.1065
5896 | 14484 | 14.484 | 788 | 0.0585
5897 | 14930 | 14.93 | 870 | 0.1385
5898 | 14431 | 14.431 | 394 | 0.1275
5899 | 13255 | 13.255 | -526 | 0.1545
5900 | 14179 | 14.179 | 120 | 0.202
5901 | 14783 | 14.783 | -842 | 0.3405
5902 | 14734 | 14.734 | 675 | 0.2605
5903 | 14817 | 14.817 | -453 | 0.2715
5904 | 14698 | 14.698 | -808 | 0.2445
5905 | 14712 | 14.712 | 794 | 0.3565
5906 | 14792 | 14.792 | -983 | 0.3935
5907 | 14550 | 14.55 | 117 | 0.4575
5908 | 15057 | 15.057 | 15 | 0.383
5909 | 14847 | 14.847 | -99 | 0.5
5910 | 14724 | 14.724 | 989 | 0.601
5911 | 14683 | 14.683 | -992 | 0.649
5912 | 14696 | 14.696 | 946 | 0.6275
5913 | 14798 | 14.798 | 66 | 0.585
5914 | 14533 | 14.533 | -955 | 0.585
5915 | 14787 | 14.787 | -698 | 0.617
5916 | 14746 | 14.746 | 651 | 0.9735
5917 | 14650 | 14.65 | 104 | 0.8615
5918 | 14865 | 14.865 | 852 | 0.931
5919 | 14587 | 14.587 | -495 | 0.9945
5920 | 14661 | 14.661 | -227 | 0.6595
5921 | 14708 | 14.708 | 513 | 0.58
5922 | 14530 | 14.53 | -715 | 0.5055
5923 | 14675 | 14.675 | 935 | 0.33
5924 | 14652 | 14.652 | 542 | 0.2765
5925 | 14637 | 14.637 | 410 | 0.2925
5926 | 14563 | 14.563 | -234 | 0.2925
5927 | 14535 | 14.535 | 764 | 0.351
5928 | 14701 | 14.701 | -519 | 0.6225
5929 | 14431 | 14.431 | 241 | 0.6385
5930 | 14605 | 14.605 | -943 | 0.9095
5931 | 14313 | 14.313 | -138 | 1.0585
5932 | 14633 | 14.633 | -914 | 1.1385
5933 | 14331 | 14.331 | 801 | 0.7765
5934 | 14393 | 14.393 | 416 | 0.553
5935 | 14454 | 14.454 | 526 | 0.4785
5936 | 14383 | 14.383 | 872 | 0.4255
5937 | 14595 | 14.595 | 393 | 0.6755
5938 | 14430 | 14.43 | 228 | 0.7765
5939 | 14506 | 14.506 | 513 | 0.702
5940 | 14711 | 14.711 | -965 | 0.697
5941 | 14615 | 14.615 | -68 | 0.5745
5942 | 14519 | 14.519 | 88 | 0.548
5943 | 14741 | 14.741 | 301 | 0.702
5944 | 14692 | 14.692 | -181 | 0.553
5945 | 14538 | 14.538 | -487 | 0.601
5946 | 14710 | 14.71 | -188 | 0.734
5947 | 14088 | 14.088 | -580 | 0.7445
5948 | 13617 | 13.617 | -538 | 0.7445
5949 | 13899 | 13.899 | -160 | 0.468
5950 | 13994 | 13.994 | 12 | 0.6115
5951 | 14001 | 14.001 | -13 | 0.713
5952 | 13280 | 13.28 | 734 | 0.537
5953 | 14602 | 14.602 | -514 | 0.617
5954 | 14727 | 14.727 | -341 | 0.6275
5955 | 14782 | 14.782 | -815 | 0.6545
5956 | 14792 | 14.792 | 934 | 0.6755
5957 | 14870 | 14.87 | 189 | 0.7765
5958 | 14867 | 14.867 | 858 | 0.984
5959 | 14722 | 14.722 | 880 | 1.3615
5960 | 14719 | 14.719 | -925 | 0.9735
5961 | 14801 | 14.801 | 29 | 0.782
5962 | 14591 | 14.591 | 819 | 0.8615
5963 | 14769 | 14.769 | -29 | 0.819
5964 | 14807 | 14.807 | -285 | 0.8565
5965 | 14808 | 14.808 | -18 | 0.835
5966 | 14828 | 14.828 | -184 | 0.463
5967 | 14672 | 14.672 | -655 | 0.5
5968 | 14673 | 14.673 | -442 | 0.4895
5969 | 14824 | 14.824 | 74 | 0.3775
5970 | 14483 | 14.483 | 480 | 0.3455
5971 | 14679 | 14.679 | -565 | 0.25
5972 | 14560 | 14.56 | -534 | 0.2395
5973 | 14434 | 14.434 | -180 | 0.2605
5974 | 14720 | 14.72 | 918 | 0.2555
5975 | 14648 | 14.648 | -328 | 0.3245
5976 | 14513 | 14.513 | -786 | 0.431
5977 | 14723 | 14.723 | 695 | 0.4255
5978 | 14515 | 14.515 | 666 | 0.335
5979 | 14726 | 14.726 | 702 | 0.399
5980 | 14522 | 14.522 | 892 | 0.3885
5981 | 14228 | 14.228 | -197 | 0.431
5982 | 12346 | 12.346 | 443 | 0.2715
5983 | 14132 | 14.132 | 525 | 0.2395
5984 | 14614 | 14.614 | -850 | 0.069
5985 | 14793 | 14.793 | 831 | 0.3085
5986 | 14681 | 14.681 | 882 | 0.8455
5987 | 14845 | 14.845 | -740 | 0.8775
5988 | 14600 | 14.6 | -587 | 0.702
5989 | 14862 | 14.862 | 546 | 0.649
5990 | 14600 | 14.6 | 178 | 0.537
5991 | 14702 | 14.702 | -322 | 0.803
5992 | 14593 | 14.593 | 344 | 0.8935
5993 | 14222 | 14.222 | 181 | 0.4945
5994 | 13607 | 13.607 | -423 | 0.3935
5995 | 14211 | 14.211 | -858 | 0.2555
5996 | 14649 | 14.649 | -358 | 0.186
5997 | 14684 | 14.684 | -135 | 0.234
5998 | 14664 | 14.664 | -972 | 0.2445
5999 | 14670 | 14.67 | 752 | 0.2445
6000 | 14645 | 14.645 | -564 | 0.282
6001 | 14640 | 14.64 | -719 | 0.266
6002 | 14800 | 14.8 | 745 | 0.2445
6003 | 14754 | 14.754 | -336 | 0.3615
6004 | 14813 | 14.813 | 229 | 0.4735
6005 | 14604 | 14.604 | -883 | 0.6915
6006 | 14742 | 14.742 | -242 | 0.8935
6007 | 14695 | 14.695 | -217 | 0.803
6008 | 14785 | 14.785 | -751 | 0.516
6009 | 14679 | 14.679 | 380 | 0.4785
6010 | 14697 | 14.697 | -149 | 0.431
6011 | 14702 | 14.702 | 631 | 0.548
6012 | 14800 | 14.8 | -316 | 0.463
6013 | 14715 | 14.715 | 585 | 0.351
6014 | 14759 | 14.759 | -661 | 0.266
6015 | 14672 | 14.672 | -878 | 0.234
6016 | 14882 | 14.882 | -217 | 0.25
6017 | 14732 | 14.732 | -928 | 0.2075
6018 | 14571 | 14.571 | 695 | 0.2075
6019 | 14707 | 14.707 | 615 | 0.1545
6020 | 14675 | 14.675 | -488 | 0.287
6021 | 14765 | 14.765 | 908 | 0.6595
6022 | 14629 | 14.629 | 244 | 0.5425
6023 | 14554 | 14.554 | 864 | 0.3455
6024 | 14816 | 14.816 | 233 | 0.282
6025 | 14627 | 14.627 | 515 | 0.335
6026 | 14724 | 14.724 | -119 | 0.3245
6027 | 14582 | 14.582 | 318 | 0.2765
6028 | 14703 | 14.703 | -999 | 0.399
6029 | 14615 | 14.615 | 779 | 0.601
6030 | 14758 | 14.758 | 832 | 0.5215
6031 | 14784 | 14.784 | -269 | 0.4255
6032 | 14637 | 14.637 | -228 | 0.5215
6033 | 14738 | 14.738 | 711 | 0.4575
6034 | 14585 | 14.585 | 563 | 0.537
6035 | 14675 | 14.675 | -123 | 0.6225
6036 | 14737 | 14.737 | -501 | 0.5265
6037 | 14718 | 14.718 | 37 | 0.3885
6038 | 14610 | 14.61 | 172 | 0.3725
6039 | 14768 | 14.768 | -10 | 0.649
6040 | 14719 | 14.719 | -347 | 0.7445
6041 | 14335 | 14.335 | -938 | 1.101
6042 | 13721 | 13.721 | -768 | 1.101
6043 | 13954 | 13.954 | 858 | 1.303
6044 | 13897 | 13.897 | 764 | 1.5265
6045 | 14148 | 14.148 | 987 | 1.351
6046 | 13470 | 13.47 | 214 | 1.436
6047 | 14207 | 14.207 | -327 | 1.4785
6048 | 14554 | 14.554 | -495 | 2.1385
6049 | 14846 | 14.846 | -197 | 2.1595
6050 | 14583 | 14.583 | 237 | 1.452
6051 | 14914 | 14.914 | -23 | 1.617
6052 | 14846 | 14.846 | -711 | 2.463
6053 | 14822 | 14.822 | 376 | 3.181
6054 | 14747 | 14.747 | -249 | 2.6915
6055 | 14687 | 14.687 | -432 | 3.2235
6056 | 14834 | 14.834 | 548 | 3.1435
6057 | 14712 | 14.712 | 659 | 2.9735
6058 | 14685 | 14.685 | -828 | 3.2765
6059 | 14751 | 14.751 | 975 | 3.5905
6060 | 14763 | 14.763 | 201 | 4.085
6061 | 14703 | 14.703 | 558 | 3.8615
6062 | 14800 | 14.8 | 930 | 4.2445
6063 | 14816 | 14.816 | 504 | 3.8885
6064 | 14788 | 14.788 | -875 | 4.7555
6065 | 14773 | 14.773 | 219 | 4.5265
6066 | 14582 | 14.582 | 298 | 4.1115
6067 | 14502 | 14.502 | 536 | 4.053
6068 | 14686 | 14.686 | -25 | 3.5
6069 | 14770 | 14.77 | 846 | 3.7555
6070 | 14648 | 14.648 | -651 | 3.9045
6071 | 14591 | 14.591 | -389 | 4.1385
6072 | 14808 | 14.808 | 104 | 4.734
6073 | 14590 | 14.59 | 383 | 3.787
6074 | 14709 | 14.709 | 469 | 4.0055
6075 | 14684 | 14.684 | 743 | 3.9045
6076 | 14757 | 14.757 | -337 | 2.899
6077 | 14649 | 14.649 | 161 | 3.383
6078 | 14666 | 14.666 | -329 | 4.298
6079 | 14950 | 14.95 | -881 | 3.9415
6080 | 14794 | 14.794 | 630 | 3.2925
6081 | 14562 | 14.562 | 872 | 2.915
6082 | 14730 | 14.73 | -285 | 2.8565
6083 | 14709 | 14.709 | -546 | 2.702
6084 | 14728 | 14.728 | -152 | 3.2765
6085 | 14622 | 14.622 | -885 | 4.0105
6086 | 14844 | 14.844 | -392 | 4.287
6087 | 14756 | 14.756 | 637 | 3.202
6088 | 14751 | 14.751 | 168 | 3.463
6089 | 14207 | 14.207 | -450 | 3.287
6090 | 13214 | 13.214 | -779 | 3.33
6091 | 14461 | 14.461 | -471 | 3.1225
6092 | 14741 | 14.741 | -143 | 3.665
6093 | 14671 | 14.671 | -35 | 4.3405
6094 | 14674 | 14.674 | 131 | 4.1915
6095 | 14729 | 14.729 | -776 | 4.5215
6096 | 14804 | 14.804 | -855 | 4.6545
6097 | 14644 | 14.644 | -502 | 4.6755
6098 | 14776 | 14.776 | -904 | 4.782
6099 | 14742 | 14.742 | -850 | 3.6915
6100 | 14778 | 14.778 | 874 | 3.6275
6101 | 14755 | 14.755 | 97 | 3.1915
6102 | 14851 | 14.851 | 656 | 2.92
6103 | 14840 | 14.84 | -149 | 2.5585
6104 | 14759 | 14.759 | -749 | 2.7445
6105 | 14754 | 14.754 | -471 | 2.5905
6106 | 14714 | 14.714 | -142 | 3.1225
6107 | 14832 | 14.832 | -631 | 4.899
6108 | 14801 | 14.801 | 909 | 4.335
6109 | 14808 | 14.808 | 842 | 3.867
6110 | 14737 | 14.737 | 922 | 4.6225
6111 | 14825 | 14.825 | -848 | 1.782
6112 | 14729 | 14.729 | 489 | 1.936
6113 | 14757 | 14.757 | 546 | 4.6385
6114 | 14618 | 14.618 | -684 | 4.351
6115 | 14666 | 14.666 | 458 | 4.564
6116 | 14648 | 14.648 | -274 | 4.42
6117 | 14717 | 14.717 | -300 | 4.7235
6118 | 14838 | 14.838 | 186 | 4.553
6119 | 14592 | 14.592 | -674 | 4.633
6120 | 14647 | 14.647 | -291 | 3.819
6121 | 14777 | 14.777 | 366 | 4.92
6122 | 14612 | 14.612 | 417 | 3.819
6123 | 14799 | 14.799 | 734 | 2.7285
6124 | 14597 | 14.597 | -777 | 4.3245
6125 | 14716 | 14.716 | 371 | 4.4945
6126 | 14679 | 14.679 | 598 | 4.0055
6127 | 14582 | 14.582 | -87 | 4.3615
6128 | 14710 | 14.71 | 211 | 3.3885
6129 | 14732 | 14.732 | 762 | 3.569
6130 | 14681 | 14.681 | 919 | 2.7235
6131 | 14585 | 14.585 | -287 | 2.415
6132 | 14532 | 14.532 | -470 | 1.984
6133 | 14639 | 14.639 | -994 | 1.633
6134 | 14575 | 14.575 | -273 | 1.702
6135 | 14852 | 14.852 | 68 | 1.1595
6136 | 14134 | 14.134 | -880 | 1.1915
6137 | 13607 | 13.607 | -839 | 1.319
6138 | 13674 | 13.674 | -161 | 1.463
6139 | 14134 | 14.134 | 7 | 1.2395
6140 | 13901 | 13.901 | 464 | 1.314
6141 | 13133 | 13.133 | 765 | 1.3405
6142 | 14489 | 14.489 | -716 | 1.3245
6143 | 14685 | 14.685 | 430 | 1.016
6144 | 14874 | 14.874 | 828 | 1.3725
6145 | 14788 | 14.788 | 120 | 1.2235
6146 | 14769 | 14.769 | -690 | 1.2395
6147 | 14857 | 14.857 | -484 | 1.564
6148 | 14787 | 14.787 | 596 | 1.6275
6149 | 14616 | 14.616 | -39 | 1.3935
6150 | 14932 | 14.932 | 807 | 1.33
6151 | 14673 | 14.673 | 59 | 1.1915
6152 | 14792 | 14.792 | 843 | 0.883
6153 | 14925 | 14.925 | 350 | 0.548
6154 | 14795 | 14.795 | -160 | 0.8085
6155 | 14568 | 14.568 | -710 | 0.7765
6156 | 14802 | 14.802 | 137 | 0.9045
6157 | 14859 | 14.859 | -849 | 0.8775
6158 | 14881 | 14.881 | -492 | 1.2075
6159 | 14519 | 14.519 | -253 | 0.9045
6160 | 14898 | 14.898 | 392 | 1.2235
6161 | 14736 | 14.736 | -299 | 1.452
6162 | 14452 | 14.452 | 195 | 1.431
6163 | 14708 | 14.708 | -934 | 1.2075
6164 | 14361 | 14.361 | 723 | 0.8725
6165 | 14594 | 14.594 | -870 | 1.1275
6166 | 14629 | 14.629 | -902 | 1.314
6167 | 14684 | 14.684 | 949 | 2.4735
6168 | 14608 | 14.608 | -495 | 2.6275
6169 | 14714 | 14.714 | 880 | 3.2555
6170 | 14643 | 14.643 | 139 | 2.6115
6171 | 14541 | 14.541 | -556 | 3
6172 | 14692 | 14.692 | 368 | 2.8615
6173 | 14769 | 14.769 | 625 | 3.1225
6174 | 14705 | 14.705 | 675 | 2
6175 | 14698 | 14.698 | 577 | 2.3885
6176 | 14575 | 14.575 | -352 | 2.83
6177 | 14611 | 14.611 | -477 | 1.7235
6178 | 14662 | 14.662 | -402 | 1.7765
6179 | 14380 | 14.38 | 751 | 1.9095
6180 | 14562 | 14.562 | -566 | 1.33
6181 | 14616 | 14.616 | -334 | 1.532
6182 | 14729 | 14.729 | 369 | 1.1915
6183 | 14623 | 14.623 | 368 | 1.548
6184 | 14673 | 14.673 | -136 | 2.718
6185 | 14743 | 14.743 | 859 | 2.8455
6186 | 14831 | 14.831 | 472 | 2.75
6187 | 14380 | 14.38 | -325 | 2.3245
6188 | 13797 | 13.797 | -728 | 2.5955
6189 | 13608 | 13.608 | -896 | 2.2715
6190 | 14668 | 14.668 | 439 | 2.2605
6191 | 14621 | 14.621 | -1 | 2.3725
6192 | 14696 | 14.696 | 412 | 2.713
6193 | 14740 | 14.74 | -193 | 2.649
6194 | 14781 | 14.781 | 838 | 2.452
6195 | 14696 | 14.696 | 134 | 2.899
6196 | 14718 | 14.718 | -451 | 0.952
6197 | 14719 | 14.719 | -486 | 1.399
6198 | 14708 | 14.708 | -168 | 1.484
6199 | 14706 | 14.706 | 936 | 1.2555
6200 | 14768 | 14.768 | 70 | 0.936
6201 | 14765 | 14.765 | 83 | 0.883
6202 | 14726 | 14.726 | 355 | 1.0745
6203 | 14798 | 14.798 | 630 | 0.702
6204 | 14659 | 14.659 | 270 | 0.766
6205 | 14731 | 14.731 | 675 | 1.032
6206 | 14635 | 14.635 | 413 | 0.8725
6207 | 14700 | 14.7 | 389 | 0.9735
6208 | 14698 | 14.698 | -477 | 0.7555
6209 | 14692 | 14.692 | -692 | 0.4255
6210 | 14721 | 14.721 | 393 | 0.463
6211 | 14588 | 14.588 | 578 | 0.3565
6212 | 14565 | 14.565 | 670 | 1
6213 | 14673 | 14.673 | 887 | 2.213
6214 | 14662 | 14.662 | 264 | 2.851
6215 | 14650 | 14.65 | 290 | 2.1435
6216 | 14597 | 14.597 | -252 | 3.447
6217 | 14728 | 14.728 | 222 | 4.782
6218 | 14584 | 14.584 | 573 | 4.819
6219 | 14614 | 14.614 | 63 | 4.899
6220 | 14683 | 14.683 | 816 | 4.9415
6221 | 14594 | 14.594 | 227 | 4.984
6222 | 14553 | 14.553 | 391 | 2.452
6223 | 14760 | 14.76 | -992 | 0.7555
6224 | 14615 | 14.615 | -268 | 0.0265
6225 | 14335 | 14.335 | 781 | 0.0055
6226 | 14862 | 14.862 | -660 | 0
6227 | 14757 | 14.757 | -872 | 0
6228 | 14541 | 14.541 | -79 | 2.7285
6229 | 14678 | 14.678 | -914 | 4.5745
6230 | 14637 | 14.637 | -247 | 4.697
6231 | 14755 | 14.755 | 412 | 4.681
6232 | 14762 | 14.762 | 832 | 3.4045
6233 | 14172 | 14.172 | 588 | 3
6234 | 13785 | 13.785 | 130 | 2.3565
6235 | 13816 | 13.816 | 927 | 2.319
6236 | 14041 | 14.041 | 229 | 1.3245
6237 | 14136 | 14.136 | 429 | 1.4735
6238 | 13221 | 13.221 | -197 | 1.197
6239 | 14323 | 14.323 | -461 | 1.5055
6240 | 14707 | 14.707 | 194 | 1.4575
6241 | 14667 | 14.667 | 533 | 1.5585
6242 | 14799 | 14.799 | -195 | 1.484
6243 | 14803 | 14.803 | 186 | 1.266
6244 | 14764 | 14.764 | 519 | 1.516
6245 | 14776 | 14.776 | 361 | 1.3245
6246 | 14733 | 14.733 | 982 | 1.0585
6247 | 14880 | 14.88 | -909 | 0.92
6248 | 14744 | 14.744 | -850 | 0.7605
6249 | 14728 | 14.728 | 237 | 1.181
6250 | 14893 | 14.893 | 685 | 0.899
6251 | 14738 | 14.738 | 723 | 1.1755
6252 | 14519 | 14.519 | -989 | 0.952
6253 | 14888 | 14.888 | -411 | 1.181
6254 | 14654 | 14.654 | -593 | 1.367
6255 | 14728 | 14.728 | 889 | 1.3455
6256 | 14862 | 14.862 | -842 | 1.5425
6257 | 14761 | 14.761 | -786 | 2.4945
6258 | 14454 | 14.454 | 612 | 3.213
6259 | 14472 | 14.472 | 514 | 4.032
6260 | 14715 | 14.715 | 509 | 4.016
6261 | 14838 | 14.838 | 744 | 4.5
6262 | 14632 | 14.632 | -643 | 4.899
6263 | 14595 | 14.595 | 708 | 4.8775
6264 | 14748 | 14.748 | 295 | 4.681
6265 | 14609 | 14.609 | 164 | 4.0955
6266 | 14671 | 14.671 | -912 | 4.787
6267 | 14629 | 14.629 | -648 | 4.8565
6268 | 14571 | 14.571 | 509 | 4.915
6269 | 14601 | 14.601 | 992 | 4.9045
6270 | 14752 | 14.752 | 362 | 4.947
6271 | 14622 | 14.622 | 704 | 4.92
6272 | 14629 | 14.629 | -853 | 4.9095
6273 | 14775 | 14.775 | -174 | 4.83
6274 | 14797 | 14.797 | 718 | 4.8615
6275 | 14704 | 14.704 | -386 | 4.718
6276 | 14533 | 14.533 | -201 | 4.4735
6277 | 14794 | 14.794 | 990 | 4.58
6278 | 14511 | 14.511 | 775 | 4.532
6279 | 14756 | 14.756 | 366 | 4.2605
6280 | 14720 | 14.72 | -972 | 2.213
6281 | 14058 | 14.058 | -791 | 2.787
6282 | 13342 | 13.342 | 490 | 3.6435
6283 | 14050 | 14.05 | -715 | 3.585
6284 | 14763 | 14.763 | 902 | 3.649
6285 | 14761 | 14.761 | 39 | 2.436
6286 | 14779 | 14.779 | -230 | 2.67
6287 | 14737 | 14.737 | -602 | 2.415
6288 | 14729 | 14.729 | 489 | 2.734
6289 | 14751 | 14.751 | -856 | 2.835
6290 | 14715 | 14.715 | 105 | 2.9945
6291 | 14752 | 14.752 | 64 | 2.601
6292 | 14680 | 14.68 | 295 | 2.33
6293 | 14769 | 14.769 | 667 | 1.649
6294 | 14631 | 14.631 | -10 | 1.782
6295 | 14659 | 14.659 | 250 | 2.0055
6296 | 14676 | 14.676 | -683 | 1.9945
6297 | 14812 | 14.812 | 770 | 1.6065
6298 | 14662 | 14.662 | 825 | 1.037
6299 | 14728 | 14.728 | -33 | 0.9415
6300 | 14810 | 14.81 | -638 | 0.67
6301 | 14629 | 14.629 | -717 | 0.6385
6302 | 14835 | 14.835 | -484 | 0.883
6303 | 14615 | 14.615 | 940 | 1.032
6304 | 14736 | 14.736 | -584 | 1.0215
6305 | 14725 | 14.725 | -56 | 0.947
6306 | 14629 | 14.629 | 36 | 0.9785
6307 | 14352 | 14.352 | -604 | 0.984
6308 | 14676 | 14.676 | -266 | 1.085
6309 | 14627 | 14.627 | -81 | 1.17
6310 | 14720 | 14.72 | 223 | 1.3085
6311 | 14503 | 14.503 | 284 | 0.633
6312 | 14666 | 14.666 | -396 | 0.7235
6313 | 14611 | 14.611 | 994 | 0.851
6314 | 14762 | 14.762 | -41 | 0.7715
6315 | 14581 | 14.581 | -936 | 1.048
6316 | 14560 | 14.56 | -491 | 1.4945
6317 | 14556 | 14.556 | -524 | 1.431
6318 | 14714 | 14.714 | 705 | 1.7075
6319 | 14788 | 14.788 | 327 | 1.314
6320 | 14585 | 14.585 | 245 | 1.2445
6321 | 14710 | 14.71 | 644 | 0.468
6322 | 14655 | 14.655 | 807 | 0.149
6323 | 14712 | 14.712 | -711 | 0.601
6324 | 14665 | 14.665 | 864 | 0.9895
6325 | 14742 | 14.742 | -280 | 0.686
6326 | 14647 | 14.647 | 80 | 0.4575
6327 | 14668 | 14.668 | -678 | 0.351
6328 | 14679 | 14.679 | 162 | 0.42
6329 | 14655 | 14.655 | 296 | 0.452
6330 | 14584 | 14.584 | 810 | 0.468
6331 | 14668 | 14.668 | 865 | 0.5105
6332 | 14222 | 14.222 | -307 | 0.5425
6333 | 13580 | 13.58 | 437 | 0.5745
6334 | 13724 | 13.724 | -637 | 0.548
6335 | 14052 | 14.052 | 691 | 0.431
6336 | 13760 | 13.76 | -164 | 0.3455
6337 | 13509 | 13.509 | 699 | 0.617
6338 | 14429 | 14.429 | 951 | 0.6915
6339 | 14742 | 14.742 | -654 | 0.67
6340 | 14826 | 14.826 | 233 | 0.468
6341 | 14680 | 14.68 | 771 | 0.3455
6342 | 14680 | 14.68 | 750 | 0.2715
6343 | 14746 | 14.746 | 891 | 0.1915
6344 | 14751 | 14.751 | -351 | 0.165
6345 | 14555 | 14.555 | -464 | 0.133
6346 | 14630 | 14.63 | -511 | 0.0905
6347 | 14852 | 14.852 | -555 | 0.0425
6348 | 14781 | 14.781 | 173 | 0.08
6349 | 14688 | 14.688 | -798 | 0.0585
6350 | 14747 | 14.747 | -340 | 0
6351 | 14786 | 14.786 | 286 | 0.0745
6352 | 14671 | 14.671 | 483 | 0.1115
6353 | 14749 | 14.749 | 585 | 0.181
6354 | 14566 | 14.566 | 210 | 0.1595
6355 | 14642 | 14.642 | -347 | 0.085
6356 | 14640 | 14.64 | 438 | 0.064
6357 | 14629 | 14.629 | -432 | 0.064
6358 | 14600 | 14.6 | 832 | 0.064
6359 | 14640 | 14.64 | -115 | 0.0905
6360 | 14582 | 14.582 | 861 | 0.0955
6361 | 14670 | 14.67 | -474 | 0.101
6362 | 14749 | 14.749 | -792 | 0.069
6363 | 14772 | 14.772 | 620 | 0.0265
6364 | 14640 | 14.64 | -328 | 0.0215
6365 | 14635 | 14.635 | 254 | 0.037
6366 | 14781 | 14.781 | 569 | 0.032
6367 | 14650 | 14.65 | -176 | 0.085
6368 | 14700 | 14.7 | 222 | 0.085
6369 | 14657 | 14.657 | 359 | 0.1385
6370 | 14665 | 14.665 | 742 | 0.335
6371 | 14679 | 14.679 | -398 | 0.537
6372 | 14797 | 14.797 | 587 | 0.553
6373 | 14586 | 14.586 | -896 | 0.5425
6374 | 14762 | 14.762 | 86 | 0.569
6375 | 14610 | 14.61 | -852 | 0.6115
6376 | 14669 | 14.669 | -202 | 0.617
6377 | 14695 | 14.695 | 101 | 0.7445
6378 | 14515 | 14.515 | -632 | 1.213
6379 | 13694 | 13.694 | -731 | 1.0905
6380 | 13581 | 13.581 | 642 | 0.915
6381 | 14578 | 14.578 | 302 | 1.25
6382 | 14688 | 14.688 | -674 | 1.4785
6383 | 14792 | 14.792 | -799 | 1.4785
6384 | 14736 | 14.736 | 407 | 1.3245
6385 | 14767 | 14.767 | -810 | 0.803
6386 | 14666 | 14.666 | -526 | 0.6115
6387 | 14774 | 14.774 | -475 | 0.718
6388 | 14750 | 14.75 | -343 | 0.819
6389 | 14795 | 14.795 | -226 | 1.3725
6390 | 14645 | 14.645 | -132 | 1.4575
6391 | 14713 | 14.713 | 921 | 1.537
6392 | 14694 | 14.694 | -152 | 1.42
6393 | 14783 | 14.783 | -373 | 1.8885
6394 | 14789 | 14.789 | 175 | 2.2075
6395 | 14762 | 14.762 | 628 | 1.766
6396 | 14692 | 14.692 | -822 | 2.1225
6397 | 14614 | 14.614 | 678 | 2.5
6398 | 14644 | 14.644 | 500 | 2.3245
6399 | 14813 | 14.813 | 672 | 2.0215
6400 | 14531 | 14.531 | -405 | 1.9735
6401 | 14800 | 14.8 | 430 | 2.101
6402 | 14624 | 14.624 | 289 | 1.798
6403 | 14680 | 14.68 | -828 | 1.702
6404 | 14745 | 14.745 | -516 | 1.8615
6405 | 14745 | 14.745 | -772 | 1.8565
6406 | 14733 | 14.733 | 303 | 1.8455
6407 | 14601 | 14.601 | 759 | 1.968
6408 | 14568 | 14.568 | 22 | 1.564
6409 | 14643 | 14.643 | 264 | 1.681
6410 | 14622 | 14.622 | 22 | 1.7075
6411 | 14697 | 14.697 | 1000 | 1.7075
6412 | 14808 | 14.808 | 364 | 1.8565
6413 | 14542 | 14.542 | -42 | 1.8615
6414 | 14706 | 14.706 | 471 | 1.553
6415 | 14627 | 14.627 | -749 | 2.0055
6416 | 14592 | 14.592 | 73 | 1.649
6417 | 14535 | 14.535 | 871 | 1.8085
6418 | 14530 | 14.53 | 123 | 1.8885
6419 | 14508 | 14.508 | 736 | 1.83
6420 | 14620 | 14.62 | -338 | 2.287
6421 | 14500 | 14.5 | 814 | 2.436
6422 | 14553 | 14.553 | 20 | 2.468
6423 | 14495 | 14.495 | 878 | 2.4045
6424 | 14468 | 14.468 | -324 | 2.053
6425 | 14721 | 14.721 | 385 | 2.633
6426 | 14661 | 14.661 | 90 | 2.766
6427 | 14564 | 14.564 | -76 | 2.8405
6428 | 14736 | 14.736 | -464 | 3.335
6429 | 14655 | 14.655 | 785 | 2.963
6430 | 14693 | 14.693 | -974 | 2.819
6431 | 14759 | 14.759 | -863 | 2.5
6432 | 14643 | 14.643 | 106 | 2.287
6433 | 14471 | 14.471 | 296 | 2.585
6434 | 14112 | 14.112 | 103 | 2.5215
6435 | 13753 | 13.753 | 471 | 2.484
6436 | 13865 | 13.865 | -92 | 2.649
6437 | 14027 | 14.027 | 784 | 2.947
6438 | 13650 | 13.65 | 715 | 2.8405
6439 | 13354 | 13.354 | 651 | 3.1115
6440 | 14671 | 14.671 | -378 | 2.2075
6441 | 14742 | 14.742 | 741 | 1.08
6442 | 14732 | 14.732 | -232 | 3.4045
6443 | 14721 | 14.721 | -972 | 3.218
6444 | 14733 | 14.733 | 817 | 3.548
6445 | 14664 | 14.664 | 696 | 3.516
6446 | 14789 | 14.789 | 47 | 4.0745
6447 | 14704 | 14.704 | 848 | 3.947
6448 | 14758 | 14.758 | -73 | 4.053
6449 | 14721 | 14.721 | 200 | 4.399
6450 | 14620 | 14.62 | -152 | 3.9255
6451 | 14746 | 14.746 | 909 | 4.3615
6452 | 14655 | 14.655 | 815 | 4.585
6453 | 14728 | 14.728 | 2 | 4.532
6454 | 14668 | 14.668 | -119 | 4.5905
6455 | 14638 | 14.638 | 309 | 4.713
6456 | 14613 | 14.613 | -25 | 4.665
6457 | 14638 | 14.638 | 612 | 4.6545
6458 | 14593 | 14.593 | -816 | 4.697
6459 | 14707 | 14.707 | -167 | 4.702
6460 | 14595 | 14.595 | 957 | 4.569
6461 | 14691 | 14.691 | 490 | 4.7395
6462 | 14585 | 14.585 | 641 | 4.713
6463 | 14659 | 14.659 | 613 | 4.931
6464 | 14618 | 14.618 | 631 | 4.9255
6465 | 14766 | 14.766 | 785 | 4.9785
6466 | 14596 | 14.596 | -74 | 4.9735
6467 | 14421 | 14.421 | 445 | 4.984
6468 | 14609 | 14.609 | -160 | 4.984
6469 | 14789 | 14.789 | -489 | 4.984
6470 | 14591 | 14.591 | 600 | 4.9785
6471 | 14743 | 14.743 | -340 | 2.3405
6472 | 14528 | 14.528 | 742 | 5
6473 | 14882 | 14.882 | 498 | 3.766
6474 | 14650 | 14.65 | -476 | 3.452
6475 | 14699 | 14.699 | 658 | 4.9945
6476 | 14738 | 14.738 | 847 | 4.9945
6477 | 14736 | 14.736 | 559 | 4.9945
6478 | 14508 | 14.508 | 495 | 4.9945
6479 | 14686 | 14.686 | 672 | 4.9945
6480 | 14628 | 14.628 | 96 | 4.9945
6481 | 14707 | 14.707 | -156 | 4.984
6482 | 13955 | 13.955 | -829 | 4.984
6483 | 13310 | 13.31 | 985 | 4.9735
6484 | 14714 | 14.714 | -427 | 4.984
6485 | 14806 | 14.806 | -657 | 4.984
6486 | 14832 | 14.832 | -984 | 4.984
6487 | 14877 | 14.877 | 690 | 4.9785
6488 | 14750 | 14.75 | 230 | 4.984
6489 | 14833 | 14.833 | 898 | 4.984
6490 | 14699 | 14.699 | 339 | 4.984
6491 | 14869 | 14.869 | 504 | 4.963
6492 | 14674 | 14.674 | 943 | 4.9785
6493 | 14702 | 14.702 | 233 | 4.835
6494 | 14761 | 14.761 | -285 | 4.9575
6495 | 14657 | 14.657 | -649 | 4.883
6496 | 14660 | 14.66 | -541 | 4.3725
6497 | 14812 | 14.812 | -565 | 4.899
6498 | 14705 | 14.705 | -460 | 4.7605
6499 | 14504 | 14.504 | 738 | 4.75
6500 | 14745 | 14.745 | 653 | 4.702
6501 | 14656 | 14.656 | -155 | 4.734
6502 | 14788 | 14.788 | 13 | 4.681
6503 | 14662 | 14.662 | 141 | 4.75
6504 | 14629 | 14.629 | 782 | 4.787
6505 | 14733 | 14.733 | -379 | 4.67
6506 | 14608 | 14.608 | 794 | 4.67
6507 | 14648 | 14.648 | 858 | 4.415
6508 | 14653 | 14.653 | 729 | 4.4415
6509 | 14740 | 14.74 | -322 | 4.383
6510 | 14666 | 14.666 | 881 | 4.1115
6511 | 14671 | 14.671 | -352 | 3.803
6512 | 14609 | 14.609 | 294 | 2.947
6513 | 14714 | 14.714 | -336 | 3.1275
6514 | 14634 | 14.634 | -989 | 2.814
6515 | 14865 | 14.865 | 699 | 3.101
6516 | 14720 | 14.72 | -954 | 2.665
6517 | 14590 | 14.59 | -985 | 2.2285
6518 | 14546 | 14.546 | 502 | 2.016
6519 | 14690 | 14.69 | 527 | 2.3615
6520 | 14588 | 14.588 | -531 | 2.4255
6521 | 14771 | 14.771 | -716 | 2.2395
6522 | 14740 | 14.74 | 883 | 2.1225
6523 | 14611 | 14.611 | 629 | 1.8245
6524 | 14879 | 14.879 | 786 | 1.6595
6525 | 14768 | 14.768 | -420 | 1.0265
6526 | 14802 | 14.802 | -768 | 0.569
6527 | 14710 | 14.71 | 202 | 0.4785
6528 | 14864 | 14.864 | 670 | 0.5055
6529 | 14853 | 14.853 | 656 | 0.7715
6530 | 14171 | 14.171 | -431 | 0.952
6531 | 13654 | 13.654 | 251 | 1.0215
6532 | 13959 | 13.959 | 359 | 0.7235
6533 | 14061 | 14.061 | -49 | 0.83
6534 | 14069 | 14.069 | -16 | 0.867
6535 | 13262 | 13.262 | 473 | 0.8885
6536 | 14432 | 14.432 | 168 | 0.931
6537 | 14744 | 14.744 | 266 | 0.867
6538 | 14748 | 14.748 | 574 | 0.5955
6539 | 14813 | 14.813 | 579 | 0.4895
6540 | 14855 | 14.855 | -236 | 0.537
6541 | 14667 | 14.667 | 789 | 0.3935
6542 | 14716 | 14.716 | -71 | 0.5265
6543 | 14738 | 14.738 | 501 | 0.585
6544 | 14723 | 14.723 | -975 | 0.5745
6545 | 14660 | 14.66 | -749 | 0.9895
6546 | 14657 | 14.657 | -885 | 0.867
6547 | 14743 | 14.743 | -234 | 0.553
6548 | 14592 | 14.592 | -140 | 0.803
6549 | 14764 | 14.764 | 648 | 0.67
6550 | 14699 | 14.699 | -714 | 0.2715
6551 | 14639 | 14.639 | 732 | 0.3245
6552 | 14743 | 14.743 | -624 | 0.1915
6553 | 14493 | 14.493 | 705 | 0.218
6554 | 14818 | 14.818 | -70 | 0.617
6555 | 14596 | 14.596 | -858 | 1.1755
6556 | 14681 | 14.681 | 562 | 0.9945
6557 | 14575 | 14.575 | -945 | 0.4895
6558 | 14757 | 14.757 | -673 | 0.3615
6559 | 14458 | 14.458 | -553 | 0.399
6560 | 14650 | 14.65 | 870 | 0.4575
6561 | 14663 | 14.663 | 853 | 0.436
6562 | 14602 | 14.602 | 473 | 0.3775
6563 | 14633 | 14.633 | -483 | 0.314
6564 | 14650 | 14.65 | -673 | 0.3455
6565 | 14663 | 14.663 | 57 | 0.5425
6566 | 14711 | 14.711 | -306 | 0.798
6567 | 14787 | 14.787 | -949 | 0.798
6568 | 14709 | 14.709 | -977 | 0.681
6569 | 14643 | 14.643 | -5 | 1.101
6570 | 14852 | 14.852 | -43 | 0.798
6571 | 14624 | 14.624 | -271 | 0.5
6572 | 14869 | 14.869 | 705 | 0.314
6573 | 14832 | 14.832 | -27 | 0
6574 | 14751 | 14.751 | -884 | 0.0585
6575 | 14798 | 14.798 | 534 | 0.085
6576 | 14753 | 14.753 | 679 | 0.213
6577 | 14783 | 14.783 | 457 | 0.3775
6578 | 14303 | 14.303 | 16 | 0.2285
6579 | 13586 | 13.586 | 451 | 0.149
6580 | 14445 | 14.445 | -112 | 0.0055
6581 | 14796 | 14.796 | 918 | 0
6582 | 14817 | 14.817 | 572 | 0.016
6583 | 14739 | 14.739 | 447 | 0.17
6584 | 14764 | 14.764 | -561 | 0.0585
6585 | 14746 | 14.746 | 647 | 0.069
6586 | 14816 | 14.816 | -591 | 0.0055
6587 | 14647 | 14.647 | -690 | 0
6588 | 14856 | 14.856 | 9 | 0.0425
6589 | 14839 | 14.839 | 52 | 0.186
6590 | 14599 | 14.599 | 578 | 0.2075
6591 | 14783 | 14.783 | 856 | 0.165
6592 | 14756 | 14.756 | -72 | 0.1545
6593 | 14703 | 14.703 | -446 | 0.2445
6594 | 14730 | 14.73 | 576 | 0.2285
6595 | 14711 | 14.711 | 965 | 0.282
6596 | 14652 | 14.652 | 535 | 0.367
6597 | 14739 | 14.739 | -391 | 0.697
6598 | 14702 | 14.702 | 929 | 0.6755
6599 | 14625 | 14.625 | 322 | 0.601
6600 | 14945 | 14.945 | 727 | 0.7395
6601 | 14686 | 14.686 | -162 | 1.2285
6602 | 14695 | 14.695 | -211 | 1.436
6603 | 14662 | 14.662 | -322 | 1.2285
6604 | 14867 | 14.867 | 110 | 0.8885
6605 | 14466 | 14.466 | -971 | 0.9945
6606 | 14623 | 14.623 | 838 | 0.92
6607 | 14577 | 14.577 | -476 | 0.9735
6608 | 14633 | 14.633 | -591 | 0.7395
6609 | 14626 | 14.626 | -714 | 1.0265
6610 | 14638 | 14.638 | 880 | 1.2605
6611 | 14591 | 14.591 | 976 | 1.181
6612 | 14715 | 14.715 | 723 | 1.5
6613 | 14721 | 14.721 | -891 | 1.6385
6614 | 14641 | 14.641 | 809 | 1.2765
6615 | 14628 | 14.628 | -680 | 1.5055
6616 | 14708 | 14.708 | -737 | 1.2445
6617 | 14576 | 14.576 | 484 | 0.8615
6618 | 14635 | 14.635 | -261 | 0.984
6619 | 14869 | 14.869 | 549 | 1.048
6620 | 14744 | 14.744 | 514 | 0.803
6621 | 14614 | 14.614 | 442 | 0.787
6622 | 14883 | 14.883 | 223 | 0.947
6623 | 14763 | 14.763 | -700 | 0.8885
6624 | 14780 | 14.78 | 630 | 0.9415
6625 | 14792 | 14.792 | 55 | 1.0585
6626 | 14072 | 14.072 | -350 | 1.08
6627 | 13823 | 13.823 | 173 | 1.186
6628 | 13883 | 13.883 | 719 | 0.984
6629 | 14006 | 14.006 | -816 | 0.798
6630 | 14060 | 14.06 | 979 | 0.6915
6631 | 13469 | 13.469 | -754 | 0.8455
6632 | 14347 | 14.347 | -521 | 0.7765
6633 | 14802 | 14.802 | 783 | 0.963
6634 | 14549 | 14.549 | -134 | 0.8615
6635 | 14849 | 14.849 | 947 | 0.92
6636 | 14724 | 14.724 | 736 | 0.7395
6637 | 14689 | 14.689 | 905 | 0.6915
6638 | 14689 | 14.689 | -444 | 0.447
6639 | 14718 | 14.718 | 560 | 0.463
6640 | 14641 | 14.641 | -519 | 0.702
6641 | 14621 | 14.621 | 762 | 1.186
6642 | 14693 | 14.693 | 250 | 1.117
6643 | 14547 | 14.547 | -184 | 1.3405
6644 | 14480 | 14.48 | 937 | 1.3405
6645 | 14793 | 14.793 | -225 | 1.835
6646 | 14630 | 14.63 | -410 | 2.436
6647 | 14532 | 14.532 | 20 | 2.7555
6648 | 14732 | 14.732 | -807 | 3.032
6649 | 14543 | 14.543 | -658 | 3.7715
6650 | 14514 | 14.514 | 329 | 4.149
6651 | 14614 | 14.614 | 561 | 4.819
6652 | 14410 | 14.41 | -781 | 4.931
6653 | 14759 | 14.759 | -885 | 4.8615
6654 | 14604 | 14.604 | 652 | 4.4945
6655 | 14564 | 14.564 | -273 | 3.835
6656 | 14679 | 14.679 | 265 | 4.2445
6657 | 14541 | 14.541 | -637 | 2.633
6658 | 14597 | 14.597 | 766 | 2.6065
6659 | 14458 | 14.458 | -444 | 3.032
6660 | 14664 | 14.664 | 416 | 3.0905
6661 | 14636 | 14.636 | 661 | 3.787
6662 | 14670 | 14.67 | -620 | 3.149
6663 | 14509 | 14.509 | -580 | 2.463
6664 | 14866 | 14.866 | -222 | 2.6545
6665 | 14578 | 14.578 | 344 | 2.8565
6666 | 14745 | 14.745 | -393 | 2.5425
6667 | 14712 | 14.712 | 512 | 2.3245
6668 | 14638 | 14.638 | 135 | 2.08
6669 | 14674 | 14.674 | 405 | 3.0105
6670 | 14751 | 14.751 | 648 | 3.1595
6671 | 14717 | 14.717 | 462 | 2.1065
6672 | 14724 | 14.724 | 953 | 3.1275
6673 | 14425 | 14.425 | -485 | 3.1385
6674 | 13897 | 13.897 | 517 | 3.351
6675 | 13773 | 13.773 | -34 | 2.819
6676 | 13750 | 13.75 | 700 | 1.8615
6677 | 14094 | 14.094 | 783 | 1.9095
6678 | 13938 | 13.938 | 732 | 1.9735
6679 | 13443 | 13.443 | -543 | 2.037
6680 | 14558 | 14.558 | -682 | 1.8405
6681 | 14684 | 14.684 | -145 | 1.383
6682 | 14685 | 14.685 | 458 | 1.33
6683 | 14795 | 14.795 | 494 | 1.2235
6684 | 14743 | 14.743 | -574 | 0.9575
6685 | 14741 | 14.741 | -332 | 1.037
6686 | 14854 | 14.854 | -755 | 1.053
6687 | 14660 | 14.66 | 668 | 0.8455
6688 | 14677 | 14.677 | 851 | 0.734
6689 | 14837 | 14.837 | -65 | 0.5425
6690 | 14458 | 14.458 | -329 | 0.537
6691 | 14651 | 14.651 | -441 | 0.7925
6692 | 14659 | 14.659 | -611 | 0.7075
6693 | 14819 | 14.819 | 33 | 0.553
6694 | 14588 | 14.588 | -234 | 0.484
6695 | 14725 | 14.725 | 927 | 0.3615
6696 | 14527 | 14.527 | 426 | 0.4415
6697 | 14760 | 14.76 | 536 | 0.234
6698 | 14591 | 14.591 | 310 | 0.5055
6699 | 14638 | 14.638 | -414 | 0.4415
6700 | 14476 | 14.476 | -861 | 0.6385
6701 | 14791 | 14.791 | -832 | 0.3935
6702 | 14588 | 14.588 | -781 | 0.3775
6703 | 14772 | 14.772 | 147 | 0.2925
6704 | 14556 | 14.556 | -280 | 0.4945
6705 | 14639 | 14.639 | -646 | 0.436
6706 | 14719 | 14.719 | 586 | 0.5265
6707 | 14549 | 14.549 | -603 | 0.8935
6708 | 14634 | 14.634 | 156 | 1.0585
6709 | 14644 | 14.644 | -162 | 0.734
6710 | 14637 | 14.637 | -899 | 0.351
6711 | 14727 | 14.727 | 50 | 0.5
6712 | 14689 | 14.689 | 456 | 0.5215
6713 | 14693 | 14.693 | -242 | 0.5585
6714 | 14754 | 14.754 | 184 | 0.6115
6715 | 14472 | 14.472 | -474 | 0.6755
6716 | 14834 | 14.834 | 932 | 0.3245
6717 | 14707 | 14.707 | 964 | 0.282
6718 | 14694 | 14.694 | -756 | 0.3885
6719 | 14787 | 14.787 | -279 | 0.548
6720 | 14667 | 14.667 | 748 | 0.8085
6721 | 14733 | 14.733 | 763 | 0.8455
6722 | 13855 | 13.855 | -129 | 1.0105
6723 | 13501 | 13.501 | 180 | 0.9785
6724 | 14667 | 14.667 | 991 | 1.649
6725 | 14840 | 14.84 | -684 | 2.048
6726 | 14637 | 14.637 | -653 | 2.0425
6727 | 14584 | 14.584 | -437 | 2.08
6728 | 14783 | 14.783 | 416 | 1.7555
6729 | 14833 | 14.833 | 348 | 1.548
6730 | 14592 | 14.592 | 757 | 1.452
6731 | 14675 | 14.675 | -503 | 1.516
6732 | 14725 | 14.725 | 336 | 1.5905
6733 | 14824 | 14.824 | 783 | 1.681
6734 | 14739 | 14.739 | -713 | 1.4255
6735 | 14756 | 14.756 | -572 | 1.032
6736 | 14571 | 14.571 | 458 | 1.3085
6737 | 14744 | 14.744 | 293 | 1.665
6738 | 14548 | 14.548 | 473 | 2.319
6739 | 14629 | 14.629 | -53 | 2.2765
6740 | 14715 | 14.715 | -84 | 2.1915
6741 | 14560 | 14.56 | 847 | 1.734
6742 | 14777 | 14.777 | 265 | 1.9785
6743 | 14624 | 14.624 | 326 | 1.399
6744 | 14551 | 14.551 | 38 | 0.9095
6745 | 14713 | 14.713 | 529 | 1.048
6746 | 14710 | 14.71 | -701 | 0.803
6747 | 14671 | 14.671 | 246 | 0.415
6748 | 14642 | 14.642 | 220 | 0.697
6749 | 14551 | 14.551 | -164 | 0.5265
6750 | 14706 | 14.706 | 107 | 0.3085
6751 | 14558 | 14.558 | -720 | 0.149
6752 | 14630 | 14.63 | -864 | 0.032
6753 | 14791 | 14.791 | 548 | 0.037
6754 | 14607 | 14.607 | 679 | 0.0055
6755 | 14587 | 14.587 | -183 | 0.0265
6756 | 14670 | 14.67 | -62 | 0.117
6757 | 14544 | 14.544 | -893 | 0.447
6758 | 14626 | 14.626 | -868 | 0.197
6759 | 14669 | 14.669 | -25 | 0.133
6760 | 14642 | 14.642 | 266 | 0.186
6761 | 14744 | 14.744 | -861 | 0.165
6762 | 14728 | 14.728 | -192 | 0.0955
6763 | 14572 | 14.572 | -709 | 0.053
6764 | 14731 | 14.731 | 517 | 0.0745
6765 | 14655 | 14.655 | 816 | 0.165
6766 | 14736 | 14.736 | 551 | 0.202
6767 | 14710 | 14.71 | 529 | 0.1755
6768 | 14669 | 14.669 | -644 | 0.1915
6769 | 14225 | 14.225 | 188 | 0.303
6770 | 13512 | 13.512 | -43 | 0.5215
6771 | 13878 | 13.878 | 302 | 0.2715
6772 | 14072 | 14.072 | 446 | 0.5265
6773 | 13998 | 13.998 | 385 | 0.6755
6774 | 13001 | 13.001 | -589 | 0.6275
6775 | 14509 | 14.509 | -358 | 0.867
6776 | 14727 | 14.727 | 236 | 1.0905
6777 | 14602 | 14.602 | -526 | 1.165
6778 | 14681 | 14.681 | 831 | 1.7605
6779 | 14770 | 14.77 | -592 | 2.681
6780 | 14725 | 14.725 | 10 | 1.713
6781 | 14633 | 14.633 | 335 | 1.936
6782 | 14856 | 14.856 | -271 | 1.7605
6783 | 14605 | 14.605 | 306 | 2.234
6784 | 14814 | 14.814 | 702 | 1.569
6785 | 14593 | 14.593 | 742 | 1.3885
6786 | 14675 | 14.675 | 550 | 1.633
6787 | 14671 | 14.671 | -410 | 1.665
6788 | 14650 | 14.65 | -504 | 1.7765
6789 | 14716 | 14.716 | 542 | 2.048
6790 | 14709 | 14.709 | -674 | 1.92
6791 | 14662 | 14.662 | -703 | 2.234
6792 | 14596 | 14.596 | 3 | 2.1435
6793 | 14646 | 14.646 | -179 | 2.1115
6794 | 14608 | 14.608 | -265 | 2.197
6795 | 14562 | 14.562 | -191 | 2.4575
6796 | 14694 | 14.694 | -621 | 2.234
6797 | 14612 | 14.612 | -712 | 2.3565
6798 | 14607 | 14.607 | 76 | 2.1545
6799 | 14639 | 14.639 | -53 | 2.303
6800 | 14694 | 14.694 | 785 | 2.0105
6801 | 14702 | 14.702 | 194 | 1.7075
6802 | 14672 | 14.672 | 368 | 1.1755
6803 | 14573 | 14.573 | -83 | 1.2555
6804 | 14606 | 14.606 | -747 | 1.4415
6805 | 14689 | 14.689 | -349 | 0.947
6806 | 14575 | 14.575 | -468 | 0.9255
6807 | 14654 | 14.654 | -249 | 0.7075
6808 | 14612 | 14.612 | -765 | 0.7395
6809 | 14843 | 14.843 | 836 | 1.2395
6810 | 14524 | 14.524 | 251 | 1.33
6811 | 14881 | 14.881 | -647 | 0.883
6812 | 14700 | 14.7 | -259 | 0.734
6813 | 14680 | 14.68 | 943 | 1.3565
6814 | 14636 | 14.636 | 467 | 1.335
6815 | 14857 | 14.857 | 99 | 0.9945
6816 | 14649 | 14.649 | 297 | 0.713
6817 | 14724 | 14.724 | 448 | 1.3085
6818 | 13885 | 13.885 | 366 | 1.569
6819 | 13546 | 13.546 | -594 | 1.42
6820 | 14585 | 14.585 | 18 | 1.6755
6821 | 14813 | 14.813 | -406 | 1.6595
6822 | 14639 | 14.639 | -154 | 2.33
6823 | 14732 | 14.732 | -122 | 2.553
6824 | 14793 | 14.793 | -321 | 2.1225
6825 | 14883 | 14.883 | 54 | 2.037
6826 | 14771 | 14.771 | 367 | 1.9895
6827 | 14753 | 14.753 | 812 | 1.963
6828 | 14789 | 14.789 | 149 | 1.8245
6829 | 14730 | 14.73 | -767 | 1.4895
6830 | 14725 | 14.725 | 401 | 1.532
6831 | 14716 | 14.716 | 58 | 1.4735
6832 | 14752 | 14.752 | -313 | 1.181
6833 | 14808 | 14.808 | -985 | 0.9895
6834 | 14693 | 14.693 | -148 | 1.085
6835 | 14568 | 14.568 | 943 | 1.4945
6836 | 14839 | 14.839 | 259 | 1.803
6837 | 14656 | 14.656 | -69 | 2.032
6838 | 14652 | 14.652 | 478 | 1.8245
6839 | 14695 | 14.695 | 343 | 2.431
6840 | 14705 | 14.705 | 463 | 2.0745
6841 | 14599 | 14.599 | 580 | 1.8885
6842 | 14780 | 14.78 | 475 | 1.3935
6843 | 14672 | 14.672 | 973 | 0.8085
6844 | 14676 | 14.676 | 328 | 0.2555
6845 | 14620 | 14.62 | -790 | 0.2555
6846 | 14630 | 14.63 | -269 | 0.431
6847 | 14618 | 14.618 | 949 | 0.4415
6848 | 14604 | 14.604 | 837 | 0.6915
6849 | 14513 | 14.513 | -772 | 0.5585
6850 | 14571 | 14.571 | -460 | 0.1545
6851 | 14514 | 14.514 | 825 | 0.069
6852 | 14829 | 14.829 | 767 | 0.117
6853 | 14570 | 14.57 | 349 | 0.2285
6854 | 14792 | 14.792 | 238 | 0.303
6855 | 14688 | 14.688 | -135 | 0.5055
6856 | 14915 | 14.915 | -190 | 0.335
6857 | 14771 | 14.771 | -795 | 0.2765
6858 | 14752 | 14.752 | -658 | 0.266
6859 | 14827 | 14.827 | -471 | 0.197
6860 | 14769 | 14.769 | -534 | 0.266
6861 | 14742 | 14.742 | 124 | 0.3455
6862 | 14841 | 14.841 | 362 | 0.3615
6863 | 14665 | 14.665 | -371 | 0.335
6864 | 14772 | 14.772 | 383 | 0.25
6865 | 14864 | 14.864 | 822 | 0.314
6866 | 14724 | 14.724 | -898 | 0.3085
6867 | 14208 | 14.208 | 568 | 0.266
6868 | 13624 | 13.624 | -776 | 0.2285
6869 | 14111 | 14.111 | -706 | 0.218
6870 | 14088 | 14.088 | -160 | 0.2715
6871 | 14082 | 14.082 | 271 | 0.2445
6872 | 13629 | 13.629 | -719 | 0.213
6873 | 14564 | 14.564 | 679 | 0.17
6874 | 14803 | 14.803 | -168 | 0.1545
6875 | 14815 | 14.815 | -821 | 0.1595
6876 | 14630 | 14.63 | -218 | 0.133
6877 | 14849 | 14.849 | -27 | 0.202
6878 | 14801 | 14.801 | 722 | 0.218
6879 | 14713 | 14.713 | 728 | 0.0955
6880 | 14649 | 14.649 | -555 | 0.1275
6881 | 14603 | 14.603 | -339 | 0.0955
6882 | 14658 | 14.658 | 245 | 0.1225
6883 | 14549 | 14.549 | 647 | 0.08
6884 | 14754 | 14.754 | 175 | 0.133
6885 | 14666 | 14.666 | 200 | 0.0955
6886 | 14700 | 14.7 | -350 | 0.0955
6887 | 14658 | 14.658 | -779 | 0.069
6888 | 14500 | 14.5 | -760 | 0.0585
6889 | 14575 | 14.575 | -716 | 0.048
6890 | 14791 | 14.791 | -484 | 0.064
6891 | 14366 | 14.366 | 317 | 0.0585
6892 | 14724 | 14.724 | 151 | 0.085
6893 | 14504 | 14.504 | -300 | 0.0905
6894 | 14574 | 14.574 | -864 | 0.0955
6895 | 14642 | 14.642 | 20 | 0.1115
6896 | 14609 | 14.609 | 728 | 0.1385
6897 | 14747 | 14.747 | -14 | 0.1115
6898 | 14725 | 14.725 | 343 | 0.053
6899 | 14575 | 14.575 | -61 | 0.117
6900 | 14520 | 14.52 | 146 | 0.2765
6901 | 14654 | 14.654 | 86 | 0.202
6902 | 14628 | 14.628 | -355 | 0.218
6903 | 14565 | 14.565 | 415 | 0.351
6904 | 14633 | 14.633 | -657 | 0.468
6905 | 14748 | 14.748 | -861 | 0.532
6906 | 14618 | 14.618 | 528 | 0.399
6907 | 14740 | 14.74 | -961 | 0.2395
6908 | 14662 | 14.662 | -639 | 0.298
6909 | 14676 | 14.676 | -578 | 0.3085
6910 | 14811 | 14.811 | 608 | 0.3885
6911 | 14540 | 14.54 | -268 | 0.4255
6912 | 14883 | 14.883 | -43 | 0.431
6913 | 14062 | 14.062 | 325 | 0.601
6914 | 13388 | 13.388 | 716 | 0.4785
6915 | 14411 | 14.411 | -567 | 0.4255
6916 | 14842 | 14.842 | -199 | 0.415
6917 | 14687 | 14.687 | -504 | 0.431
6918 | 14794 | 14.794 | -489 | 0.3615
6919 | 14867 | 14.867 | -702 | 0.287
6920 | 14552 | 14.552 | 133 | 0.351
6921 | 14662 | 14.662 | -773 | 0.319
6922 | 14562 | 14.562 | 218 | 0.2925
6923 | 14980 | 14.98 | -663 | 0.452
6924 | 14668 | 14.668 | -579 | 0.5055
6925 | 14748 | 14.748 | 90 | 0.4735
6926 | 14743 | 14.743 | -106 | 0.4945
6927 | 14662 | 14.662 | -312 | 0.3885
6928 | 14567 | 14.567 | 27 | 0.415
6929 | 14635 | 14.635 | 232 | 0.4415
6930 | 14554 | 14.554 | 253 | 0.4945
6931 | 14567 | 14.567 | -558 | 0.537
6932 | 14583 | 14.583 | -402 | 0.585
6933 | 14740 | 14.74 | 138 | 0.4945
6934 | 14620 | 14.62 | -841 | 0.4895
6935 | 14643 | 14.643 | -581 | 0.5215
6936 | 14449 | 14.449 | -277 | 0.564
6937 | 14675 | 14.675 | -57 | 0.6225
6938 | 14857 | 14.857 | -97 | 0.617
6939 | 14436 | 14.436 | -30 | 0.766
6940 | 14777 | 14.777 | 495 | 0.952
6941 | 14581 | 14.581 | 482 | 0.8245
6942 | 14577 | 14.577 | 375 | 0.564
6943 | 14724 | 14.724 | 42 | 0.564
6944 | 14415 | 14.415 | -302 | 0.6435
6945 | 14687 | 14.687 | 518 | 0.6915
6946 | 14733 | 14.733 | -394 | 0.6755
6947 | 14577 | 14.577 | 739 | 0.697
6948 | 14735 | 14.735 | -544 | 0.7925
6949 | 14646 | 14.646 | -91 | 0.7075
6950 | 14722 | 14.722 | 318 | 0.6385
6951 | 14640 | 14.64 | 30 | 0.5265
6952 | 14598 | 14.598 | 208 | 0.6435
6953 | 14742 | 14.742 | 73 | 0.58
6954 | 14680 | 14.68 | -326 | 0.718
6955 | 14633 | 14.633 | -712 | 0.585
6956 | 14773 | 14.773 | 572 | 0.3615
6957 | 14631 | 14.631 | 122 | 0.4415
6958 | 14696 | 14.696 | -884 | 0.5425
6959 | 14621 | 14.621 | -683 | 0.3725
6960 | 14700 | 14.7 | 43 | 0.1435
6961 | 14577 | 14.577 | -774 | 0.303
6962 | 13827 | 13.827 | 706 | 0.2555
6963 | 13791 | 13.791 | 197 | 0.1545
6964 | 14047 | 14.047 | -306 | 0.218
6965 | 13881 | 13.881 | -649 | 0.2285
6966 | 13876 | 13.876 | 980 | 0.2715
6967 | 13461 | 13.461 | 265 | 0.2715
6968 | 14500 | 14.5 | -739 | 0.2555
6969 | 14781 | 14.781 | 465 | 0.25
6970 | 14593 | 14.593 | 426 | 0.2765
6971 | 14838 | 14.838 | 63 | 0.266
6972 | 14635 | 14.635 | 696 | 0.33
6973 | 14743 | 14.743 | 251 | 0.303
6974 | 14672 | 14.672 | 388 | 0.282
6975 | 14791 | 14.791 | -396 | 0.218
6976 | 14622 | 14.622 | -590 | 0.1915
6977 | 14707 | 14.707 | -542 | 0.1595
6978 | 14489 | 14.489 | -608 | 0.117
6979 | 14780 | 14.78 | 844 | 0.133
6980 | 14554 | 14.554 | 612 | 0.133
6981 | 14774 | 14.774 | -665 | 0.17
6982 | 14743 | 14.743 | -533 | 0.133
6983 | 14644 | 14.644 | 5 | 0.1545
6984 | 14711 | 14.711 | 427 | 0.282
6985 | 14611 | 14.611 | -130 | 0.42
6986 | 14696 | 14.696 | -181 | 0.2715
6987 | 14735 | 14.735 | -329 | 0.181
6988 | 14414 | 14.414 | 320 | 0.2075
6989 | 14649 | 14.649 | 643 | 0.287
6990 | 14579 | 14.579 | -472 | 0.2765
6991 | 14765 | 14.765 | 556 | 0.298
6992 | 14520 | 14.52 | -905 | 0.2925
6993 | 14677 | 14.677 | -394 | 0.25
6994 | 14656 | 14.656 | -691 | 0.186
6995 | 14648 | 14.648 | 604 | 0.1435
6996 | 14682 | 14.682 | 686 | 0.197
6997 | 14583 | 14.583 | 70 | 0.197
6998 | 14524 | 14.524 | -737 | 0.234
6999 | 14664 | 14.664 | 807 | 0.303
7000 | 14676 | 14.676 | 393 | 0.213
7001 | 14667 | 14.667 | 782 | 0.234
7002 | 14661 | 14.661 | 70 | 0.25
7003 | 14731 | 14.731 | 533 | 0.3885
7004 | 14626 | 14.626 | 249 | 0.367
7005 | 14709 | 14.709 | -22 | 0.415
7006 | 14625 | 14.625 | 704 | 0.3885
7007 | 14763 | 14.763 | -737 | 0.202
7008 | 14678 | 14.678 | 401 | 0.1755
7009 | 14229 | 14.229 | -589 | 0.17
7010 | 13406 | 13.406 | 604 | 0.2715
7011 | 13964 | 13.964 | 44 | 0.7235
7012 | 14754 | 14.754 | -172 | 1.335
7013 | 14735 | 14.735 | 585 | 1.6115
7014 | 14705 | 14.705 | -444 | 1.3775
7015 | 14778 | 14.778 | -140 | 1.282
7016 | 14563 | 14.563 | -293 | 1.016
7017 | 14765 | 14.765 | 975 | 1.0105
7018 | 14574 | 14.574 | -811 | 1.4945
7019 | 14719 | 14.719 | -615 | 1.266
7020 | 14704 | 14.704 | -208 | 1.17
7021 | 14631 | 14.631 | -874 | 1.3455
7022 | 14768 | 14.768 | 234 | 1.2285
7023 | 14687 | 14.687 | -297 | 2.0905
7024 | 14725 | 14.725 | -368 | 2.3405
7025 | 14678 | 14.678 | 876 | 2.165
7026 | 14409 | 14.409 | -264 | 2.101
7027 | 14597 | 14.597 | 252 | 1.7605
7028 | 14584 | 14.584 | 358 | 1.6595
7029 | 14606 | 14.606 | 934 | 1.6065
7030 | 14645 | 14.645 | -893 | 1.6915
7031 | 14609 | 14.609 | 988 | 1.5905
7032 | 14599 | 14.599 | 689 | 1.2925
7033 | 14582 | 14.582 | 383 | 1.3245
7034 | 14628 | 14.628 | 305 | 1.931
7035 | 14564 | 14.564 | 337 | 1.7075
7036 | 14557 | 14.557 | -511 | 1.9095
7037 | 14617 | 14.617 | 487 | 2.048
7038 | 14543 | 14.543 | -367 | 2.0905
7039 | 14488 | 14.488 | -42 | 1.7765
7040 | 14678 | 14.678 | 402 | 1.484
7041 | 14470 | 14.47 | -810 | 1.218
7042 | 14529 | 14.529 | -916 | 0.92
7043 | 14657 | 14.657 | -787 | 1.101
7044 | 14534 | 14.534 | 280 | 0.8615
7045 | 14544 | 14.544 | 41 | 0.7445
7046 | 14657 | 14.657 | -323 | 0.5425
7047 | 14571 | 14.571 | 733 | 0.431
7048 | 14502 | 14.502 | 329 | 0.3935
7049 | 14616 | 14.616 | -732 | 0.468
7050 | 14539 | 14.539 | 137 | 0.3085
7051 | 14759 | 14.759 | -557 | 0.218
7052 | 14613 | 14.613 | -204 | 0.197
7053 | 14656 | 14.656 | -966 | 0.1545
7054 | 14532 | 14.532 | 44 | 0.1225
7055 | 14797 | 14.797 | 721 | 0.0055
7056 | 14649 | 14.649 | -843 | 0.037
7057 | 14603 | 14.603 | 992 | 0.0585
7058 | 7261 | 7.261 | 100 | 0.069
7059 | 7161 | 7.161 | 404 | 0.0955
7060 | 7194 | 7.194 | 379 | 0.1065
7061 | 14030 | 14.03 | 724 | 0.08
7062 | 7287 | 7.287 | 532 | 0.1225
7063 | 6953 | 6.953 | -974 | 0.0905
7064 | 7589 | 7.589 | 625 | 0.0745
7065 | 7648 | 7.648 | 412 | 0.048
7066 | 7694 | 7.694 | 505 | 0.037
7067 | 7647 | 7.647 | 647 | 0.048
7068 | 14794 | 14.794 | 819 | 0.0585
7069 | 7631 | 7.631 | -215 | 0.1225
7070 | 7736 | 7.736 | -45 | 0.117
7071 | 7752 | 7.752 | 937 | 0.048
7072 | 7669 | 7.669 | 523 | 0.0585
7073 | 7642 | 7.642 | 514 | 0.0425
7074 | 14619 | 14.619 | -133 | 0.037
7075 | 7604 | 7.604 | -690 | 0.032
7076 | 7581 | 7.581 | 994 | 0.069
7077 | 7645 | 7.645 | 234 | 0.064
7078 | 7695 | 7.695 | 352 | 0.117
7079 | 7598 | 7.598 | 489 | 0.197
7080 | 14495 | 14.495 | -517 | 0.2235
7081 | 7642 | 7.642 | -937 | 0.298
7082 | 7619 | 7.619 | 433 | 0.287
7083 | 7637 | 7.637 | 458 | 0.2445
7084 | 7508 | 7.508 | 663 | 0.33
7085 | 7542 | 7.542 | -944 | 0.3935
7086 | 14526 | 14.526 | 870 | 0.3885
7087 | 7603 | 7.603 | 457 | 0.33
7088 | 7529 | 7.529 | -704 | 0.2715
7089 | 14644 | 14.644 | -427 | 0.1915
7090 | 14528 | 14.528 | 560 | 0.2075
7091 | 7526 | 7.526 | 979 | 0.1545
7092 | 7614 | 7.614 | -401 | 0.0905
7093 | 14521 | 14.521 | -415 | 0.133
7094 | 7551 | 7.551 | -601 | 0.165
7095 | 7653 | 7.653 | -812 | 0.2395
7096 | 7662 | 7.662 | 376 | 0.2715
7097 | 7690 | 7.69 | 784 | 0.33
7098 | 7659 | 7.659 | 780 | 0.2765
7099 | 7679 | 7.679 | -56 | 0.2555
7100 | 7670 | 7.67 | -371 | 0.3405
7101 | 7687 | 7.687 | -901 | 0.415
7102 | 7591 | 7.591 | -387 | 0.6225
7103 | 7697 | 7.697 | 821 | 0.6595
7104 | 7722 | 7.722 | -614 | 0.7075
7105 | 14645 | 14.645 | 158 | 0.713
7106 | 14086 | 14.086 | 135 | 0.6545
7107 | 13202 | 13.202 | 61 | 0.553
7108 | 14547 | 14.547 | 361 | 0.649
7109 | 14779 | 14.779 | -487 | 0.5585
7110 | 14844 | 14.844 | 148 | 0.5745
7111 | 14685 | 14.685 | 128 | 0.6385
7112 | 14695 | 14.695 | -523 | 0.569
7113 | 14798 | 14.798 | -988 | 0.468
7114 | 14721 | 14.721 | -391 | 0.447
7115 | 14603 | 14.603 | 334 | 0.335
7116 | 14548 | 14.548 | -364 | 0.266
7117 | 14654 | 14.654 | -236 | 0.2395
7118 | 14640 | 14.64 | 999 | 0.202
7119 | 14602 | 14.602 | -747 | 0.1385
7120 | 14682 | 14.682 | -665 | 0.0905
7121 | 14673 | 14.673 | -681 | 0.202
7122 | 14465 | 14.465 | -272 | 0.2235
7123 | 14622 | 14.622 | 916 | 0.2715
7124 | 14671 | 14.671 | -903 | 0.2605
7125 | 14613 | 14.613 | -752 | 0.266
7126 | 14489 | 14.489 | -418 | 0.3405
7127 | 14603 | 14.603 | 466 | 0.3935
7128 | 14465 | 14.465 | 574 | 0.5055
7129 | 14637 | 14.637 | -42 | 0.5745
7130 | 14430 | 14.43 | 214 | 0.6275
7131 | 14504 | 14.504 | 889 | 0.5105
7132 | 14702 | 14.702 | 530 | 0.516
7133 | 14518 | 14.518 | -813 | 0.601
7134 | 14390 | 14.39 | 546 | 0.5215
7135 | 14476 | 14.476 | 984 | 0.3455
7136 | 14356 | 14.356 | 160 | 0.3455
7137 | 14412 | 14.412 | 731 | 0.314
7138 | 14441 | 14.441 | -119 | 0.3565
7139 | 14490 | 14.49 | 171 | 0.3455
7140 | 14414 | 14.414 | 75 | 0.4575
7141 | 14574 | 14.574 | 759 | 0.8775
7142 | 14648 | 14.648 | 824 | 0.798
7143 | 14530 | 14.53 | -665 | 0.6595
7144 | 14712 | 14.712 | 604 | 0.803
7145 | 14533 | 14.533 | 494 | 0.899
7146 | 14725 | 14.725 | 634 | 1.048
7147 | 14675 | 14.675 | 877 | 1.234
7148 | 14643 | 14.643 | 13 | 1.835
7149 | 14670 | 14.67 | 62 | 1.9945
7150 | 14569 | 14.569 | 428 | 1.702
7151 | 14538 | 14.538 | 130 | 1.2605
7152 | 14726 | 14.726 | 539 | 1.3245
7153 | 14657 | 14.657 | 604 | 1.5
7154 | 7453 | 7.453 | -481 | 1.5585
7155 | 7197 | 7.197 | 741 | 1.314
7156 | 7209 | 7.209 | 190 | 1.0585
7157 | 7259 | 7.259 | -72 | 1.133
7158 | 7362 | 7.362 | 692 | 0.8455
7159 | 7058 | 7.058 | -932 | 0.5055
7160 | 7277 | 7.277 | -225 | 0.553
7161 | 7717 | 7.717 | -197 | 0.5745
7162 | 7608 | 7.608 | 643 | 0.5425
7163 | 7670 | 7.67 | 813 | 0.3885
7164 | 7705 | 7.705 | 130 | 0.4415
7165 | 7648 | 7.648 | -284 | 0.6545
7166 | 7659 | 7.659 | 403 | 0.633
7167 | 7676 | 7.676 | 854 | 0.537
7168 | 7673 | 7.673 | 606 | 0.6385
7169 | 7660 | 7.66 | 451 | 0.5905
7170 | 7529 | 7.529 | -930 | 0.3085
7171 | 7665 | 7.665 | -392 | 0.165
7172 | 7585 | 7.585 | 857 | 0.165
7173 | 7636 | 7.636 | 978 | 0.2555
7174 | 7661 | 7.661 | -552 | 0.351
7175 | 7532 | 7.532 | -245 | 0.351
7176 | 7613 | 7.613 | 837 | 0.5215
7177 | 7605 | 7.605 | 903 | 0.431
7178 | 7595 | 7.595 | -460 | 0.133
7179 | 7668 | 7.668 | -632 | 0.0905
7180 | 7608 | 7.608 | 386 | 0.149
7181 | 7584 | 7.584 | -942 | 0.1225
7182 | 14526 | 14.526 | -799 | 0.298
7183 | 7615 | 7.615 | 943 | 0.5105
7184 | 7689 | 7.689 | -68 | 0.6225
7185 | 7729 | 7.729 | -864 | 0.3775
7186 | 7669 | 7.669 | -220 | 0.2555
7187 | 7650 | 7.65 | -90 | 0.17
7188 | 7707 | 7.707 | 212 | 0.1435
7189 | 7664 | 7.664 | 307 | 0.266
7190 | 7615 | 7.615 | 955 | 0.3405
7191 | 7692 | 7.692 | -228 | 0.4735
7192 | 7670 | 7.67 | 81 | 0.718
7193 | 7692 | 7.692 | 729 | 0.7925
7194 | 7650 | 7.65 | 246 | 0.718
7195 | 7727 | 7.727 | 186 | 0.6915
7196 | 7774 | 7.774 | -910 | 0.867
7197 | 7571 | 7.571 | 953 | 1.2285
7198 | 14847 | 14.847 | 564 | 1.431
7199 | 14869 | 14.869 | -273 | 1.42
7200 | 13981 | 13.981 | -375 | 1.3615
7201 | 13212 | 13.212 | -983 | 1.383
7202 | 14674 | 14.674 | -421 | 1.0055
7203 | 14739 | 14.739 | 132 | 0.936
7204 | 14681 | 14.681 | 945 | 1.064
7205 | 14949 | 14.949 | 623 | 1.016
7206 | 14712 | 14.712 | 32 | 1.1385
7207 | 14772 | 14.772 | 484 | 1.617
7208 | 14754 | 14.754 | 97 | 1.8775
7209 | 14785 | 14.785 | 673 | 1.7925
7210 | 14705 | 14.705 | 851 | 1.085
7211 | 14670 | 14.67 | 95 | 0.6435
7212 | 14736 | 14.736 | 197 | 0.5745
7213 | 14603 | 14.603 | -168 | 0.33
7214 | 14792 | 14.792 | -699 | 0.1755
7215 | 14763 | 14.763 | 815 | 0.149
7216 | 14645 | 14.645 | 181 | 0.4045
7217 | 14600 | 14.6 | 683 | 0.5955
7218 | 14671 | 14.671 | 352 | 0.303
7219 | 14508 | 14.508 | 720 | 0.1545
7220 | 14583 | 14.583 | 182 | 0.1065
7221 | 14555 | 14.555 | -520 | 0.303
7222 | 14734 | 14.734 | 554 | 0.2555
7223 | 14576 | 14.576 | 698 | 0.319
7224 | 14706 | 14.706 | -670 | 0.447
7225 | 14594 | 14.594 | -829 | 0.4575
7226 | 14472 | 14.472 | 676 | 0.5215
7227 | 14674 | 14.674 | -545 | 1.436
7228 | 14413 | 14.413 | -547 | 1.303
7229 | 14537 | 14.537 | -731 | 1.133
7230 | 14642 | 14.642 | 972 | 1.0585
7231 | 14363 | 14.363 | -757 | 0.8885
7232 | 14673 | 14.673 | -680 | 1.149
7233 | 14542 | 14.542 | -218 | 1.133
7234 | 14677 | 14.677 | 138 | 0.117
7235 | 14585 | 14.585 | 367 | 0.181
7236 | 14773 | 14.773 | -458 | 0.3245
7237 | 14644 | 14.644 | 782 | 0.4895
7238 | 14725 | 14.725 | 734 | 0.963
7239 | 14758 | 14.758 | 416 | 1.1115
7240 | 14790 | 14.79 | 831 | 1.415
7241 | 14755 | 14.755 | 894 | 0.782
7242 | 14746 | 14.746 | -583 | 0.782
7243 | 14718 | 14.718 | -680 | 0.8455
7244 | 14819 | 14.819 | -589 | 0.9255
7245 | 14800 | 14.8 | -935 | 1.2395
7246 | 14691 | 14.691 | 972 | 1.819
7247 | 14427 | 14.427 | -609 | 1.718
7248 | 14068 | 14.068 | 483 | 1.697
7249 | 13733 | 13.733 | -740 | 1.2445
7250 | 13942 | 13.942 | -527 | 1.037
7251 | 14251 | 14.251 | -136 | 1.037
7252 | 13633 | 13.633 | -748 | 1.117
7253 | 13795 | 13.795 | 188 | 1.4575
7254 | 14800 | 14.8 | 824 | 1.5
7255 | 14857 | 14.857 | 677 | 0.9895
7256 | 14630 | 14.63 | -314 | 0.7605
7257 | 14775 | 14.775 | -446 | 0.851
7258 | 14745 | 14.745 | -487 | 0.8245
7259 | 14699 | 14.699 | -842 | 0.803
7260 | 14669 | 14.669 | 579 | 1.064
7261 | 14781 | 14.781 | 781 | 1
7262 | 14744 | 14.744 | -783 | 0.915
7263 | 14707 | 14.707 | 674 | 0.6275
7264 | 14630 | 14.63 | 145 | 0.399
7265 | 14723 | 14.723 | -507 | 0.3405
7266 | 14429 | 14.429 | 341 | 0.431
7267 | 14665 | 14.665 | -688 | 0.287
7268 | 14628 | 14.628 | -289 | 0.202
7269 | 14736 | 14.736 | 528 | 0.287
7270 | 14565 | 14.565 | -504 | 0.431
7271 | 14557 | 14.557 | -680 | 1.516
7272 | 14676 | 14.676 | 605 | 1.6545
7273 | 14462 | 14.462 | 940 | 2.213
7274 | 14669 | 14.669 | -134 | 1.5
7275 | 14540 | 14.54 | 807 | 1.915
7276 | 14569 | 14.569 | -464 | 1.6385
7277 | 14658 | 14.658 | -213 | 1.431
7278 | 14689 | 14.689 | -640 | 1.7555
7279 | 14460 | 14.46 | 875 | 1.6115
7280 | 14615 | 14.615 | -805 | 1.431
7281 | 14551 | 14.551 | -157 | 1.2445
7282 | 14607 | 14.607 | 340 | 1.0585
7283 | 14741 | 14.741 | 380 | 0.92
7284 | 14724 | 14.724 | 525 | 0.601
7285 | 14600 | 14.6 | -299 | 0.734
7286 | 14751 | 14.751 | 615 | 0.782
7287 | 14508 | 14.508 | 130 | 0.9575
7288 | 14848 | 14.848 | 903 | 0.8725
7289 | 14497 | 14.497 | 43 | 0.8085
7290 | 14788 | 14.788 | 111 | 0.867
7291 | 14761 | 14.761 | 557 | 0.819
7292 | 14633 | 14.633 | 903 | 0.9095
7293 | 14696 | 14.696 | 54 | 1.0055
7294 | 14744 | 14.744 | -960 | 0.8725
7295 | 14436 | 14.436 | -682 | 0.851
7296 | 14052 | 14.052 | 129 | 0.7445
7297 | 13491 | 13.491 | 313 | 0.165
7298 | 14581 | 14.581 | 206 | 0.452
7299 | 14713 | 14.713 | 815 | 0.601
7300 | 14859 | 14.859 | 351 | 0.8935
7301 | 14852 | 14.852 | 303 | 0.947
7302 | 14772 | 14.772 | 891 | 0.936
7303 | 14472 | 14.472 | 739 | 0.9045
7304 | 14868 | 14.868 | -346 | 1.0955
7305 | 14823 | 14.823 | -688 | 0.9095
7306 | 14575 | 14.575 | -234 | 1.037
7307 | 14735 | 14.735 | -852 | 1.2925
7308 | 14552 | 14.552 | -299 | 1.7075
7309 | 14713 | 14.713 | -370 | 1.7765
7310 | 14584 | 14.584 | 58 | 1.5425
7311 | 12227 | 12.227 | 305 | 1.2925
7312 | 10074 | 10.074 | 988 | 1.3615
7313 | 11247 | 11.247 | -840 | 1.399
7314 | 11620 | 11.62 | -650 | 0.7605
7315 | 12521 | 12.521 | 717 | 0.7715
7316 | 14090 | 14.09 | -458 | 0.452
7317 | 14613 | 14.613 | -674 | 0.3615
7318 | 14486 | 14.486 | -921 | 0.085
7319 | 14581 | 14.581 | 444 | 0.266
7320 | 14737 | 14.737 | 495 | 0.447
7321 | 14541 | 14.541 | -839 | 0.1915
7322 | 14594 | 14.594 | 168 | 0.1435
7323 | 14737 | 14.737 | 872 | 0.2075
7324 | 14504 | 14.504 | 993 | 0.165
7325 | 14605 | 14.605 | 719 | 0.447
7326 | 14631 | 14.631 | -440 | 0.58
7327 | 14587 | 14.587 | -651 | 0.5585
7328 | 14618 | 14.618 | -487 | 0.048
7329 | 14634 | 14.634 | -352 | 0
7330 | 14667 | 14.667 | 210 | 0
7331 | 14588 | 14.588 | -709 | 0
7332 | 14719 | 14.719 | 629 | 0
7333 | 14574 | 14.574 | -487 | 0
7334 | 14669 | 14.669 | 481 | 0
7335 | 14735 | 14.735 | -58 | 0
7336 | 14685 | 14.685 | 536 | 0.1545
7337 | 14738 | 14.738 | -247 | 0.3245
7338 | 14699 | 14.699 | 752 | 0.069
7339 | 14708 | 14.708 | 491 | 0.0215
7340 | 14683 | 14.683 | -416 | 0.1435
7341 | 14537 | 14.537 | 290 | 0.3565
7342 | 14828 | 14.828 | 862 | 0.33
7343 | 14394 | 14.394 | 310 | 0.5585
7344 | 14079 | 14.079 | -497 | 0.5265
7345 | 13668 | 13.668 | -715 | 0.5955
7346 | 14001 | 14.001 | 58 | 0.3725
7347 | 14136 | 14.136 | -132 | 0.6065
7348 | 13660 | 13.66 | 502 | 1.3405
7349 | 13754 | 13.754 | -686 | 1.436
7350 | 14633 | 14.633 | 656 | 1.7445
7351 | 14788 | 14.788 | -45 | 2.4095
7352 | 14702 | 14.702 | -182 | 2.064
7353 | 14664 | 14.664 | -705 | 2.17
7354 | 14894 | 14.894 | 770 | 2.17
7355 | 14632 | 14.632 | -96 | 2.1915
7356 | 14785 | 14.785 | 276 | 2.6065
7357 | 14810 | 14.81 | 682 | 1.9785
7358 | 14859 | 14.859 | 953 | 2.032
7359 | 14545 | 14.545 | -898 | 1.319
7360 | 14914 | 14.914 | 458 | 2.0215
7361 | 14771 | 14.771 | 847 | 2.681
7362 | 14476 | 14.476 | 45 | 2.532
7363 | 14694 | 14.694 | -193 | 2.7605
7364 | 14615 | 14.615 | 706 | 2.4045
7365 | 14711 | 14.711 | 984 | 2.2075
7366 | 14644 | 14.644 | 456 | 2.25
7367 | 14731 | 14.731 | -703 | 3.1385
7368 | 14654 | 14.654 | 886 | 3.3085
7369 | 14725 | 14.725 | 492 | 3.314
7370 | 14711 | 14.711 | -518 | 2.9095
7371 | 14581 | 14.581 | -565 | 3.064
7372 | 14725 | 14.725 | -890 | 3.2765
7373 | 14542 | 14.542 | -998 | 3.2285
7374 | 14687 | 14.687 | -353 | 3.303
7375 | 14547 | 14.547 | 276 | 3.0905
7376 | 14620 | 14.62 | -665 | 2.5955
7377 | 14712 | 14.712 | 29 | 3.117
7378 | 14668 | 14.668 | -803 | 2.484
7379 | 14567 | 14.567 | 760 | 2.5265
7380 | 14606 | 14.606 | 148 | 2.5265
7381 | 14668 | 14.668 | -642 | 2.553
7382 | 14734 | 14.734 | -542 | 1.431
7383 | 14553 | 14.553 | -1 | 1.3405
7384 | 14765 | 14.765 | 940 | 1.447
7385 | 14702 | 14.702 | 993 | 0.436
7386 | 14691 | 14.691 | -173 | 0.6065
7387 | 14727 | 14.727 | -406 | 0.4415
7388 | 14556 | 14.556 | -432 | 0.819
7389 | 14860 | 14.86 | 60 | 0.9415
7390 | 14680 | 14.68 | 955 | 1.282
7391 | 14621 | 14.621 | 596 | 0.7605
7392 | 13937 | 13.937 | 822 | 0.633
7393 | 13534 | 13.534 | 722 | 0.383
7394 | 14675 | 14.675 | -636 | 0.7715
7395 | 14691 | 14.691 | -697 | 0.6385
7396 | 14775 | 14.775 | -622 | 1.0905
7397 | 14861 | 14.861 | -433 | 0.9045
7398 | 14752 | 14.752 | 861 | 0.8885
7399 | 14794 | 14.794 | 647 | 1.4095
7400 | 14644 | 14.644 | -673 | 0.6755
7401 | 14928 | 14.928 | -678 | 1.0425
7402 | 14658 | 14.658 | -415 | 1
7403 | 14907 | 14.907 | -377 | 1.798
7404 | 14777 | 14.777 | 245 | 1.633
7405 | 14789 | 14.789 | 828 | 1.569
7406 | 14867 | 14.867 | -251 | 1.1435
7407 | 14792 | 14.792 | -80 | 1.298
7408 | 14632 | 14.632 | 692 | 1.431
7409 | 14761 | 14.761 | 728 | 1.303
7410 | 14598 | 14.598 | -49 | 1.33
7411 | 14682 | 14.682 | 51 | 1.5425
7412 | 14638 | 14.638 | -466 | 2.335
7413 | 14663 | 14.663 | -457 | 2.7395
7414 | 14623 | 14.623 | -940 | 2.5215
7415 | 14694 | 14.694 | 676 | 2.415
7416 | 14557 | 14.557 | -998 | 2.6115
7417 | 14537 | 14.537 | -349 | 3.213
7418 | 14687 | 14.687 | -979 | 3.2555
7419 | 14577 | 14.577 | -278 | 3.117
7420 | 14647 | 14.647 | -508 | 2.984
7421 | 14587 | 14.587 | 295 | 2.6225
7422 | 14517 | 14.517 | 808 | 2.7285
7423 | 14464 | 14.464 | 528 | 2.351
7424 | 14527 | 14.527 | -550 | 1.851
7425 | 14584 | 14.584 | -813 | 2.468
7426 | 14541 | 14.541 | -239 | 2.58
7427 | 14611 | 14.611 | -457 | 2.5585
7428 | 14540 | 14.54 | 613 | 2.197
7429 | 14564 | 14.564 | -296 | 2.782
7430 | 14494 | 14.494 | -488 | 2.782
7431 | 14713 | 14.713 | 375 | 2.835
7432 | 14610 | 14.61 | -758 | 2.218
7433 | 14481 | 14.481 | -285 | 1.0905
7434 | 14642 | 14.642 | -323 | 0.564
7435 | 14676 | 14.676 | 951 | 0.0425
7436 | 14585 | 14.585 | 125 | 0.3935
7437 | 14656 | 14.656 | -810 | 0
7438 | 14691 | 14.691 | 899 | 0.0955
7439 | 14112 | 14.112 | 789 | 0.0585
7440 | 13715 | 13.715 | -395 | 0.037
7441 | 13781 | 13.781 | -613 | 0.202
7442 | 13948 | 13.948 | -181 | 0.447
7443 | 13978 | 13.978 | -659 | 0.734
7444 | 13448 | 13.448 | 712 | 0.9255
7445 | 14059 | 14.059 | 182 | 0.8615
7446 | 14545 | 14.545 | 822 | 0.4045
7447 | 14712 | 14.712 | -135 | 0.0105
7448 | 14707 | 14.707 | 947 | 0.1275
7449 | 14593 | 14.593 | -709 | 0.117
7450 | 14534 | 14.534 | -628 | 0.484
7451 | 14696 | 14.696 | -757 | 0.963
7452 | 14717 | 14.717 | -654 | 1.4735
7453 | 14608 | 14.608 | 654 | 1.213
7454 | 14713 | 14.713 | 510 | 1.553
7455 | 14711 | 14.711 | 845 | 0.5105
7456 | 14553 | 14.553 | 321 | 0.6435
7457 | 14858 | 14.858 | 955 | 1.314
7458 | 14556 | 14.556 | 911 | 2.0055
7459 | 14734 | 14.734 | -333 | 2.67
7460 | 14543 | 14.543 | -62 | 3.2715
7461 | 14747 | 14.747 | 262 | 3.2925
7462 | 14598 | 14.598 | -755 | 3.2555
7463 | 14690 | 14.69 | -104 | 3.2715
7464 | 14510 | 14.51 | -637 | 3.2235
7465 | 14574 | 14.574 | 841 | 3.266
7466 | 14787 | 14.787 | 317 | 3.213
7467 | 14596 | 14.596 | 864 | 3.3455
7468 | 14626 | 14.626 | 441 | 3.399
7469 | 14706 | 14.706 | 288 | 3.3405
7470 | 14606 | 14.606 | -313 | 3.3935
7471 | 14552 | 14.552 | 363 | 3.298
7472 | 14509 | 14.509 | -313 | 3.383
7473 | 14692 | 14.692 | -584 | 3.3935
7474 | 14643 | 14.643 | 474 | 3.335
7475 | 14581 | 14.581 | 218 | 3.213
7476 | 14705 | 14.705 | -926 | 3.314
7477 | 14688 | 14.688 | 425 | 3.4415
7478 | 14604 | 14.604 | 400 | 3.447
7479 | 14653 | 14.653 | -800 | 3.447
7480 | 14655 | 14.655 | 624 | 3.4415
7481 | 14695 | 14.695 | 728 | 3.431
7482 | 14633 | 14.633 | 283 | 3.436
7483 | 14650 | 14.65 | -28 | 3.4415
7484 | 14586 | 14.586 | 694 | 3.436
7485 | 14659 | 14.659 | 282 | 3.431
7486 | 14811 | 14.811 | 574 | 3.436
7487 | 14677 | 14.677 | 989 | 3.447
7488 | 14427 | 14.427 | -388 | 3.4415
7489 | 13100 | 13.1 | 944 | 3.436
7490 | 14362 | 14.362 | -885 | 3.436
7491 | 14654 | 14.654 | 767 | 3.436
7492 | 14784 | 14.784 | -564 | 3.431
7493 | 14606 | 14.606 | -798 | 3.436
7494 | 14598 | 14.598 | -953 | 3.431
7495 | 14865 | 14.865 | -34 | 3.4255
7496 | 14637 | 14.637 | -707 | 3.436
7497 | 14796 | 14.796 | -73 | 3.4415
7498 | 14738 | 14.738 | -305 | 3.4415
7499 | 14605 | 14.605 | 716 | 3.4415
7500 | 14793 | 14.793 | 855 | 3.4415
7501 | 14750 | 14.75 | 770 | 3.4415
7502 | 14700 | 14.7 | -791 | 3.436
7503 | 14663 | 14.663 | -153 | 3.4415
7504 | 14672 | 14.672 | 547 | 3.431
7505 | 14836 | 14.836 | 193 | 3.431
7506 | 14652 | 14.652 | 184 | 3.4415
7507 | 14478 | 14.478 | 796 | 3.4415
7508 | 14536 | 14.536 | 183 | 3.4415
7509 | 14617 | 14.617 | -910 | 3.447
7510 | 14691 | 14.691 | 648 | 3.4415
7511 | 14761 | 14.761 | 919 | 3.447
7512 | 14494 | 14.494 | 347 | 3.4415
7513 | 14630 | 14.63 | -291 | 3.436
7514 | 14473 | 14.473 | 807 | 3.436
7515 | 14667 | 14.667 | 527 | 3.436
7516 | 14487 | 14.487 | 157 | 3.431
7517 | 14386 | 14.386 | 525 | 3.4095
7518 | 14502 | 14.502 | 910 | 3.42
7519 | 14564 | 14.564 | 867 | 3.298
7520 | 14398 | 14.398 | -137 | 3.2555
7521 | 14634 | 14.634 | -338 | 3.4255
7522 | 14687 | 14.687 | -962 | 3.4255
7523 | 14631 | 14.631 | -157 | 3.399
7524 | 14527 | 14.527 | 843 | 3.282
7525 | 14658 | 14.658 | -23 | 3.101
7526 | 14585 | 14.585 | 482 | 3.218
7527 | 14723 | 14.723 | -57 | 3.2555
7528 | 14578 | 14.578 | -333 | 3.218
7529 | 14683 | 14.683 | -175 | 3.431
7530 | 14690 | 14.69 | -526 | 3.4415
7531 | 14828 | 14.828 | -701 | 3.447
7532 | 14682 | 14.682 | -610 | 3.4415
7533 | 14724 | 14.724 | 653 | 3.447
7534 | 14718 | 14.718 | -925 | 3.4415
7535 | 14885 | 14.885 | -432 | 3.415
7536 | 14279 | 14.279 | -300 | 3.4095
7537 | 13671 | 13.671 | 664 | 3.2605
7538 | 13860 | 13.86 | 253 | 2.67
7539 | 13969 | 13.969 | 419 | 2.7605
7540 | 14230 | 14.23 | -872 | 2.5905
7541 | 13317 | 13.317 | -187 | 2.7925
7542 | 14392 | 14.392 | -712 | 2.8565
7543 | 14713 | 14.713 | 274 | 3.2445
7544 | 14735 | 14.735 | -942 | 3.1915
7545 | 14757 | 14.757 | 32 | 3.1545
7546 | 14583 | 14.583 | 387 | 3.436
7547 | 14736 | 14.736 | -82 | 3.133
7548 | 14668 | 14.668 | 618 | 3.2925
7549 | 14694 | 14.694 | 406 | 3.3245
7550 | 14721 | 14.721 | -283 | 2.947
7551 | 14675 | 14.675 | -814 | 2.952
7552 | 14674 | 14.674 | 513 | 2.6595
7553 | 14710 | 14.71 | -421 | 3.1755
7554 | 14554 | 14.554 | -434 | 2.7395
7555 | 14742 | 14.742 | 564 | 3.0425
7556 | 14647 | 14.647 | 13 | 3.383
7557 | 14502 | 14.502 | -840 | 2.564
7558 | 14619 | 14.619 | 852 | 2.431
7559 | 14596 | 14.596 | 286 | 2.952
7560 | 14757 | 14.757 | -608 | 1.947
7561 | 14535 | 14.535 | -929 | 2.1065
7562 | 14736 | 14.736 | -6 | 2.2075
7563 | 14636 | 14.636 | 365 | 1.3405
7564 | 14574 | 14.574 | 639 | 1.4735
7565 | 14605 | 14.605 | 795 | 1.117
7566 | 14630 | 14.63 | -580 | 1.314
7567 | 14576 | 14.576 | 241 | 0.899
7568 | 14660 | 14.66 | -273 | 1.319
7569 | 14609 | 14.609 | -446 | 0.819
7570 | 14693 | 14.693 | 578 | 1.4785
7571 | 14669 | 14.669 | 818 | 0.633
7572 | 14501 | 14.501 | 800 | 1.2555
7573 | 14712 | 14.712 | 520 | 1.5745
7574 | 14728 | 14.728 | 566 | 1.633
7575 | 14817 | 14.817 | 14 | 1.436
7576 | 14637 | 14.637 | 250 | 0.6115
7577 | 14676 | 14.676 | -41 | 0.3885
7578 | 14719 | 14.719 | 339 | 0.2075
7579 | 14714 | 14.714 | -668 | 0.1915
7580 | 14762 | 14.762 | -223 | 0.0955
7581 | 14747 | 14.747 | -819 | 0.0055
7582 | 14717 | 14.717 | 241 | 0
7583 | 14726 | 14.726 | -314 | 0
7584 | 14359 | 14.359 | -186 | 0.1275
7585 | 13143 | 13.143 | -995 | 0.0265
7586 | 14771 | 14.771 | 120 | 1.085
7587 | 14819 | 14.819 | 272 | 0.6435
7588 | 14761 | 14.761 | 182 | 0.2395
7589 | 14632 | 14.632 | 651 | 0.9255
7590 | 14742 | 14.742 | 549 | 0.6225
7591 | 14867 | 14.867 | 665 | 0.9735
7592 | 14482 | 14.482 | 709 | 1.968
7593 | 14582 | 14.582 | -497 | 2.0055
7594 | 14847 | 14.847 | -555 | 2.0425
7595 | 14592 | 14.592 | 634 | 0.963
7596 | 14717 | 14.717 | -922 | 1.133
7597 | 14747 | 14.747 | 380 | 1.431
7598 | 14616 | 14.616 | -750 | 1.8455
7599 | 14707 | 14.707 | -701 | 2.17
7600 | 14554 | 14.554 | -157 | 3.0105
7601 | 14614 | 14.614 | -734 | 3.2715
7602 | 14827 | 14.827 | 572 | 3.0745
7603 | 14662 | 14.662 | 769 | 2.8085
7604 | 14669 | 14.669 | 475 | 2.7075
7605 | 14590 | 14.59 | -948 | 2.697
7606 | 14731 | 14.731 | -133 | 2.9095
7607 | 14637 | 14.637 | 695 | 3.053
7608 | 14547 | 14.547 | 260 | 3.25
7609 | 14654 | 14.654 | 707 | 3.2075
7610 | 14522 | 14.522 | -147 | 2.936
7611 | 14638 | 14.638 | 108 | 3.2445
7612 | 14426 | 14.426 | 635 | 3.3725
7613 | 14607 | 14.607 | -866 | 3.351
7614 | 14536 | 14.536 | 648 | 3.2555
7615 | 14592 | 14.592 | 709 | 3.303
7616 | 14554 | 14.554 | -638 | 3.415
7617 | 14457 | 14.457 | -317 | 3.4415
7618 | 14723 | 14.723 | 521 | 3.4415
7619 | 14483 | 14.483 | -125 | 3.447
7620 | 14620 | 14.62 | -310 | 3.4415
7621 | 14619 | 14.619 | -266 | 3.3565
7622 | 14574 | 14.574 | -395 | 2.463
7623 | 14625 | 14.625 | 203 | 0.984
7624 | 14563 | 14.563 | 612 | 1.181
7625 | 14734 | 14.734 | 184 | 0.9255
7626 | 14590 | 14.59 | 251 | 1.17
7627 | 14699 | 14.699 | -496 | 1.8775
7628 | 14676 | 14.676 | -964 | 2.9415
7629 | 14658 | 14.658 | -699 | 3.431
7630 | 14699 | 14.699 | 528 | 3.319
7631 | 14661 | 14.661 | -501 | 3.436
7632 | 14396 | 14.396 | 799 | 3.048
7633 | 13541 | 13.541 | 991 | 2.734
7634 | 13731 | 13.731 | -998 | 2.133
7635 | 14389 | 14.389 | 610 | 1.399
7636 | 14780 | 14.78 | -191 | 0.92
7637 | 14768 | 14.768 | 910 | 1.1595
7638 | 14631 | 14.631 | -473 | 1.7925
7639 | 14728 | 14.728 | -94 | 1.016
7640 | 14568 | 14.568 | 647 | 1.0105
7641 | 14118 | 14.118 | -521 | 1.67
7642 | 14073 | 14.073 | -365 | 1.787
7643 | 14011 | 14.011 | -892 | 1.5425
7644 | 13914 | 13.914 | 687 | 0.718
7645 | 13305 | 13.305 | -759 | 0.1915
7646 | 14487 | 14.487 | 113 | 0.319
7647 | 14548 | 14.548 | 257 | 0.165
7648 | 14795 | 14.795 | -340 | 0.3405
7649 | 14673 | 14.673 | 699 | 0.4095
7650 | 14535 | 14.535 | -132 | 0
7651 | 14616 | 14.616 | -182 | 0
7652 | 14676 | 14.676 | -921 | 0
7653 | 14513 | 14.513 | -361 | 0
7654 | 14658 | 14.658 | -86 | 0
7655 | 14692 | 14.692 | -835 | 0
7656 | 14642 | 14.642 | -533 | 0
7657 | 14356 | 14.356 | 962 | 0
7658 | 14603 | 14.603 | 375 | 0
7659 | 14577 | 14.577 | -935 | 0
7660 | 14444 | 14.444 | 887 | 0.0585
7661 | 14539 | 14.539 | -464 | 0.319
7662 | 14578 | 14.578 | -375 | 0.92
7663 | 14548 | 14.548 | 760 | 0.8775
7664 | 14798 | 14.798 | 659 | 1.431
7665 | 14475 | 14.475 | 204 | 2.08
7666 | 14688 | 14.688 | 754 | 2.4895
7667 | 14523 | 14.523 | 535 | 3.1065
7668 | 14751 | 14.751 | -121 | 2.7445
7669 | 14527 | 14.527 | 3 | 2.266
7670 | 14556 | 14.556 | -402 | 1.2555
7671 | 14694 | 14.694 | -331 | 0.883
7672 | 14669 | 14.669 | 9 | 2.7395
7673 | 14637 | 14.637 | 322 | 2.33
7674 | 14488 | 14.488 | 244 | 1.7075
7675 | 14760 | 14.76 | 492 | 1.33
7676 | 14592 | 14.592 | -209 | 1.0745
7677 | 14724 | 14.724 | -580 | 1.436
7678 | 14740 | 14.74 | -149 | 1.7445
7679 | 14626 | 14.626 | 9 | 0.8775
7680 | 14403 | 14.403 | -641 | 0.7765
7681 | 13674 | 13.674 | -599 | 0.7445
7682 | 13697 | 13.697 | 917 | 1.1435
7683 | 14831 | 14.831 | -342 | 0.936
7684 | 14556 | 14.556 | -392 | 0.2395
7685 | 14755 | 14.755 | 351 | 0.3615
7686 | 14706 | 14.706 | 742 | 0.2605
7687 | 14670 | 14.67 | -283 | 0.037
7688 | 14673 | 14.673 | 648 | 0.186
7689 | 14580 | 14.58 | 490 | 0.8885
7690 | 14757 | 14.757 | 612 | 1.266
7691 | 14714 | 14.714 | 801 | 2.1755
7692 | 14740 | 14.74 | -95 | 3.0955
7693 | 14658 | 14.658 | 685 | 2.936
7694 | 14644 | 14.644 | -28 | 2.367
7695 | 14586 | 14.586 | -313 | 3.1755
7696 | 14804 | 14.804 | -624 | 3.3935
7697 | 14555 | 14.555 | 125 | 3.447
7698 | 14651 | 14.651 | 978 | 3.436
7699 | 14626 | 14.626 | 472 | 3.436
7700 | 14485 | 14.485 | 176 | 2.6595
7701 | 14659 | 14.659 | 482 | 0.25
7702 | 14655 | 14.655 | -977 | 0.3085
7703 | 14632 | 14.632 | -161 | 1.8245
7704 | 14558 | 14.558 | -852 | 2.0215
7705 | 14623 | 14.623 | 736 | 3.3615
7706 | 14571 | 14.571 | -838 | 1.947
7707 | 14510 | 14.51 | -185 | 2.9945
7708 | 14552 | 14.552 | 297 | 3.436
7709 | 14689 | 14.689 | 141 | 3.436
7710 | 14388 | 14.388 | 748 | 3.431
7711 | 14411 | 14.411 | 452 | 3.431
7712 | 14518 | 14.518 | 289 | 3.4095
7713 | 14400 | 14.4 | 962 | 3.4255
7714 | 14596 | 14.596 | 711 | 3.436
7715 | 14636 | 14.636 | -486 | 3.399
7716 | 14499 | 14.499 | -265 | 3.415
7717 | 14539 | 14.539 | 665 | 1.915
7718 | 14715 | 14.715 | -704 | 1.931
7719 | 14671 | 14.671 | -497 | 2.601
7720 | 14640 | 14.64 | 149 | 2.649
7721 | 14543 | 14.543 | -812 | 3
7722 | 14693 | 14.693 | -372 | 2.9415
7723 | 14684 | 14.684 | 265 | 2.8455
7724 | 14563 | 14.563 | -834 | 3.1385
7725 | 14618 | 14.618 | -467 | 2.9895
7726 | 14692 | 14.692 | 359 | 2.197
7727 | 14461 | 14.461 | -361 | 2.351
7728 | 14107 | 14.107 | 627 | 2.4575
7729 | 13627 | 13.627 | 717 | 2.447
7730 | 13899 | 13.899 | 587 | 2.303
7731 | 13990 | 13.99 | -101 | 2.1065
7732 | 13863 | 13.863 | -390 | 2.4415
7733 | 13425 | 13.425 | 843 | 2.165
7734 | 14407 | 14.407 | 51 | 1.8455
7735 | 14750 | 14.75 | 987 | 2.452
7736 | 14611 | 14.611 | 541 | 2.5
7737 | 14566 | 14.566 | 954 | 2.1435
7738 | 14735 | 14.735 | -592 | 1.718
7739 | 14664 | 14.664 | -704 | 1.1385
7740 | 14581 | 14.581 | -114 | 1.452
7741 | 14807 | 14.807 | 909 | 2.1595
7742 | 14559 | 14.559 | 710 | 2.1275
7743 | 14748 | 14.748 | -802 | 2.4255
7744 | 14732 | 14.732 | 715 | 2.7445
7745 | 14510 | 14.51 | -285 | 2.6065
7746 | 14648 | 14.648 | -312 | 2.931
7747 | 14787 | 14.787 | -760 | 2.9095
7748 | 14589 | 14.589 | 526 | 2.92
7749 | 14654 | 14.654 | -630 | 2.8085
7750 | 14678 | 14.678 | 806 | 3.1435
7751 | 14633 | 14.633 | 454 | 3.0105
7752 | 14581 | 14.581 | -477 | 2.9045
7753 | 14549 | 14.549 | 657 | 2.8935
7754 | 14745 | 14.745 | -477 | 3.064
7755 | 14484 | 14.484 | -757 | 2.803
7756 | 14688 | 14.688 | 380 | 3.1115
7757 | 14669 | 14.669 | -466 | 3.1435
7758 | 14604 | 14.604 | -733 | 3.0585
7759 | 14576 | 14.576 | -28 | 3.048
7760 | 14579 | 14.579 | -868 | 3.0105
7761 | 14503 | 14.503 | -194 | 2.9575
7762 | 14586 | 14.586 | 517 | 2.8885
7763 | 14575 | 14.575 | 615 | 2.4095
7764 | 14505 | 14.505 | -172 | 2.287
7765 | 14561 | 14.561 | -461 | 2.7765
7766 | 14676 | 14.676 | -202 | 2.6755
7767 | 14600 | 14.6 | 435 | 2.5745
7768 | 14632 | 14.632 | -838 | 2.681
7769 | 14721 | 14.721 | 475 | 2.9255
7770 | 14697 | 14.697 | -688 | 1.952
7771 | 14665 | 14.665 | -567 | 1.6595
7772 | 14652 | 14.652 | -183 | 1.484
7773 | 14570 | 14.57 | -143 | 2.133
7774 | 14741 | 14.741 | -346 | 2.266
7775 | 14566 | 14.566 | 593 | 1.415
7776 | 14295 | 14.295 | 490 | 0.7555
7777 | 13198 | 13.198 | -848 | 0.7285
7778 | 14287 | 14.287 | -526 | 0.3935
7779 | 14610 | 14.61 | 162 | 0.3085
7780 | 14698 | 14.698 | 223 | 0.83
7781 | 14773 | 14.773 | 885 | 0.963
7782 | 14592 | 14.592 | -537 | 0.931
7783 | 14689 | 14.689 | -481 | 0.165
7784 | 14601 | 14.601 | -594 | 0.069
7785 | 14832 | 14.832 | -892 | 0.3615
7786 | 14600 | 14.6 | 522 | 0.798
7787 | 14547 | 14.547 | -456 | 0.617
7788 | 14735 | 14.735 | 962 | 0.484
7789 | 14708 | 14.708 | 402 | 0.447
7790 | 14652 | 14.652 | 56 | 0.681
7791 | 14632 | 14.632 | 620 | 0.436
7792 | 14659 | 14.659 | -450 | 0.5585
7793 | 14723 | 14.723 | -991 | 0.0215
7794 | 14723 | 14.723 | -335 | 0.0425
7795 | 14575 | 14.575 | -891 | 0.25
7796 | 14638 | 14.638 | -456 | 0.7715
7797 | 14749 | 14.749 | 987 | 0.4095
7798 | 14474 | 14.474 | -707 | 0.1915
7799 | 14708 | 14.708 | -191 | 0.3725
7800 | 14597 | 14.597 | 467 | 0.319
7801 | 14643 | 14.643 | 423 | 0.213
7802 | 14669 | 14.669 | 246 | 0.064
7803 | 14609 | 14.609 | 212 | 0
7804 | 14500 | 14.5 | -219 | 0
7805 | 14679 | 14.679 | 572 | 0.2285
7806 | 14572 | 14.572 | 292 | 0.1115
7807 | 14579 | 14.579 | 282 | 0.2765
7808 | 14517 | 14.517 | 859 | 1.069
7809 | 14655 | 14.655 | -862 | 0.835
7810 | 14498 | 14.498 | -878 | 0.58
7811 | 14761 | 14.761 | 103 | 0.17
7812 | 14639 | 14.639 | -716 | 0.2605
7813 | 14784 | 14.784 | -103 | 0.1385
7814 | 14642 | 14.642 | 515 | 0.3615
7815 | 14814 | 14.814 | 773 | 0.2395
7816 | 14755 | 14.755 | 20 | 0.1275
7817 | 14807 | 14.807 | -598 | 0.069
7818 | 14684 | 14.684 | 679 | 0.197
7819 | 14906 | 14.906 | 321 | 0.186
7820 | 14783 | 14.783 | 870 | 0.1115
7821 | 14684 | 14.684 | -65 | 0.0265
7822 | 14840 | 14.84 | -597 | 0.1065
7823 | 14546 | 14.546 | 597 | 0.181
7824 | 13945 | 13.945 | 600 | 0.2235
7825 | 13859 | 13.859 | -857 | 0.133
7826 | 13935 | 13.935 | -790 | 0.085
7827 | 14158 | 14.158 | -200 | 0.048
7828 | 13803 | 13.803 | 498 | 0.1595
7829 | 13596 | 13.596 | 182 | 0.3405
7830 | 14762 | 14.762 | 82 | 0.3775
7831 | 14727 | 14.727 | 382 | 0.2765
7832 | 14805 | 14.805 | -259 | 0.2075
7833 | 14732 | 14.732 | 694 | 0.2075
7834 | 14826 | 14.826 | -749 | 0.069
7835 | 14628 | 14.628 | -702 | 0.048
7836 | 14815 | 14.815 | -563 | 0.0215
7837 | 14785 | 14.785 | -909 | 0.181
7838 | 14669 | 14.669 | 888 | 0.0425
7839 | 14892 | 14.892 | 270 | 0.0105
7840 | 14670 | 14.67 | 589 | 0
7841 | 14674 | 14.674 | 444 | 0
7842 | 14606 | 14.606 | 306 | 0
7843 | 14556 | 14.556 | -760 | 0
7844 | 14486 | 14.486 | 428 | 0
7845 | 14551 | 14.551 | -85 | 0
7846 | 14783 | 14.783 | 221 | 0
7847 | 14741 | 14.741 | -503 | 0
7848 | 14641 | 14.641 | 465 | 0
7849 | 14681 | 14.681 | 253 | 0.016
7850 | 14601 | 14.601 | -218 | 0
7851 | 14610 | 14.61 | -412 | 0.0105
7852 | 14647 | 14.647 | 436 | 0
7853 | 14474 | 14.474 | -221 | 0.0055
7854 | 14569 | 14.569 | -25 | 0.0055
7855 | 14589 | 14.589 | -607 | 0.053
7856 | 14609 | 14.609 | -611 | 0.0265
7857 | 14691 | 14.691 | -851 | 0.0105
7858 | 14278 | 14.278 | 853 | 0.064
7859 | 14531 | 14.531 | 881 | 0.2445
7860 | 14763 | 14.763 | -749 | 0.899
7861 | 14647 | 14.647 | 919 | 0.718
7862 | 14685 | 14.685 | -131 | 0.798
7863 | 14583 | 14.583 | 664 | 1.0425
7864 | 14596 | 14.596 | 783 | 0.3615
7865 | 14674 | 14.674 | -354 | 0.367
7866 | 14721 | 14.721 | -764 | 0.5425
7867 | 14782 | 14.782 | 887 | 0.42
7868 | 14639 | 14.639 | 922 | 0.335
7869 | 14807 | 14.807 | -946 | 0.1065
7870 | 14860 | 14.86 | 433 | 0.213
7871 | 14704 | 14.704 | 437 | 0.234
7872 | 14888 | 14.888 | -506 | 0.08
7873 | 14793 | 14.793 | 316 | 0.367
7874 | 14709 | 14.709 | 535 | 0.3885
7875 | 14539 | 14.539 | 916 | 0
7876 | 13662 | 13.662 | -543 | 0.069
7877 | 13815 | 13.815 | 985 | 0.367
7878 | 14689 | 14.689 | 345 | 0.303
7879 | 14775 | 14.775 | -616 | 0.053
7880 | 14815 | 14.815 | 258 | 0.0055
7881 | 14579 | 14.579 | 144 | 0
7882 | 14731 | 14.731 | -304 | 0
7883 | 14708 | 14.708 | 752 | 0
7884 | 14618 | 14.618 | -361 | 0.287
7885 | 14647 | 14.647 | -211 | 0.1275
7886 | 14823 | 14.823 | 72 | 0.085
7887 | 14496 | 14.496 | 936 | 0.569
7888 | 14614 | 14.614 | 518 | 1.2925
7889 | 14556 | 14.556 | 708 | 1.133
7890 | 14702 | 14.702 | -387 | 2.0215
7891 | 14566 | 14.566 | 962 | 1.33
7892 | 14569 | 14.569 | -911 | 1.149
7893 | 14460 | 14.46 | 537 | 1.1595
7894 | 14488 | 14.488 | 18 | 1.1225
7895 | 14442 | 14.442 | -499 | 1.399
7896 | 14367 | 14.367 | 381 | 1.782
7897 | 14321 | 14.321 | 725 | 2.053
7898 | 14475 | 14.475 | -669 | 3.1115
7899 | 14295 | 14.295 | 915 | 3
7900 | 14270 | 14.27 | 904 | 2.3085
7901 | 14641 | 14.641 | -895 | 2.75
7902 | 14584 | 14.584 | 970 | 2.968
7903 | 14495 | 14.495 | 226 | 2.681
7904 | 14560 | 14.56 | 941 | 2.67
7905 | 14493 | 14.493 | -975 | 2.202
7906 | 14523 | 14.523 | 914 | 1.58
7907 | 14584 | 14.584 | -871 | 1.367
7908 | 14616 | 14.616 | -264 | 1.5265
7909 | 14554 | 14.554 | 269 | 0.8885
7910 | 14576 | 14.576 | -787 | 0.7605
7911 | 14699 | 14.699 | 194 | 1.2285
7912 | 14461 | 14.461 | 679 | 1.931
7913 | 14685 | 14.685 | -584 | 2.819
7914 | 14557 | 14.557 | 172 | 2.75
7915 | 14708 | 14.708 | -727 | 3.2075
7916 | 14754 | 14.754 | 547 | 3
7917 | 14731 | 14.731 | -273 | 3.016
7918 | 14640 | 14.64 | 407 | 2.83
7919 | 14675 | 14.675 | 346 | 2.7235
7920 | 14793 | 14.793 | 390 | 3.33
7921 | 14169 | 14.169 | -491 | 3.3725
7922 | 13645 | 13.645 | -824 | 3.149
7923 | 13905 | 13.905 | -436 | 3.2715
7924 | 13988 | 13.988 | -249 | 3.181
7925 | 14109 | 14.109 | -297 | 3.053
7926 | 13355 | 13.355 | -843 | 3.2285
7927 | 14340 | 14.34 | -923 | 3.2765
7928 | 14678 | 14.678 | -616 | 3.2555
7929 | 14656 | 14.656 | -726 | 3.1595
7930 | 14730 | 14.73 | 59 | 2.9785
7931 | 14703 | 14.703 | 141 | 2.8935
7932 | 14543 | 14.543 | 206 | 3.335
7933 | 14811 | 14.811 | -781 | 3.4255
7934 | 14636 | 14.636 | -275 | 3.436
7935 | 14597 | 14.597 | 861 | 3.133
7936 | 14627 | 14.627 | -739 | 3.0215
7937 | 14732 | 14.732 | -314 | 2.7395
7938 | 14515 | 14.515 | -95 | 3.3615
7939 | 14589 | 14.589 | -39 | 3.431
7940 | 14648 | 14.648 | -27 | 3.399
7941 | 14612 | 14.612 | -25 | 3.3615
7942 | 14675 | 14.675 | -664 | 3.3455
7943 | 14668 | 14.668 | 489 | 3.367
7944 | 14506 | 14.506 | -16 | 3.4095
7945 | 14760 | 14.76 | 723 | 3.383
7946 | 14482 | 14.482 | -183 | 3.4045
7947 | 14627 | 14.627 | -931 | 3.42
7948 | 14543 | 14.543 | -993 | 3.431
7949 | 14520 | 14.52 | 221 | 2.931
7950 | 14682 | 14.682 | -164 | 2.686
7951 | 14692 | 14.692 | 322 | 2.713
7952 | 14676 | 14.676 | -315 | 3.0215
7953 | 14602 | 14.602 | -277 | 2.181
7954 | 14492 | 14.492 | 802 | 2.037
7955 | 14619 | 14.619 | -556 | 1.319
7956 | 14607 | 14.607 | -910 | 1.282
7957 | 14496 | 14.496 | 502 | 1.0055
7958 | 14713 | 14.713 | -945 | 0.963
7959 | 14655 | 14.655 | -442 | 0.7395
7960 | 14736 | 14.736 | 488 | 0.2395
7961 | 14670 | 14.67 | 363 | 0.3085
7962 | 14649 | 14.649 | 29 | 0.2555
7963 | 14551 | 14.551 | 89 | 0.17
7964 | 14835 | 14.835 | -194 | 0.2395
7965 | 14488 | 14.488 | -344 | 0.2715
7966 | 14880 | 14.88 | -785 | 0.1115
7967 | 14290 | 14.29 | 133 | 0.8615
7968 | 13482 | 13.482 | 307 | 0.3085
7969 | 13841 | 13.841 | 577 | 0.048
7970 | 14686 | 14.686 | -161 | 0.2285
7971 | 14716 | 14.716 | 122 | 0
7972 | 14612 | 14.612 | -432 | 0.718
7973 | 14878 | 14.878 | 39 | 0.383
7974 | 14659 | 14.659 | -481 | 0.6115
7975 | 14691 | 14.691 | 398 | 0.686
7976 | 14717 | 14.717 | -121 | 0.67
7977 | 14726 | 14.726 | 643 | 0.452
7978 | 14621 | 14.621 | -230 | 0.835
7979 | 14716 | 14.716 | -530 | 0.6595
7980 | 14729 | 14.729 | -348 | 0.702
7981 | 14657 | 14.657 | -337 | 0.6915
7982 | 14646 | 14.646 | -164 | 0.7075
7983 | 14673 | 14.673 | 986 | 0.814
7984 | 14640 | 14.64 | 184 | 0.5215
7985 | 14718 | 14.718 | -453 | 0.218
7986 | 14518 | 14.518 | 901 | 0.3935
7987 | 14809 | 14.809 | 797 | 0.197
7988 | 14577 | 14.577 | -838 | 0.718
7989 | 14579 | 14.579 | 858 | 0.3775
7990 | 14646 | 14.646 | -963 | 0.101
7991 | 14451 | 14.451 | -697 | 0.6755
7992 | 14421 | 14.421 | 537 | 0.9735
7993 | 14595 | 14.595 | -165 | 0.686
7994 | 14464 | 14.464 | -863 | 0.633
7995 | 14546 | 14.546 | -857 | 0.1065
7996 | 14419 | 14.419 | -28 | 0.181
7997 | 14374 | 14.374 | -313 | 0.165
7998 | 14506 | 14.506 | 196 | 0
7999 | 14509 | 14.509 | -992 | 0.1545
8000 | 14435 | 14.435 | 370 | 0.0105
8001 | 14522 | 14.522 | -276 | 0
8002 | 14604 | 14.604 | 832 | 0.0215
8003 | 14588 | 14.588 | 946 | 0.0055
8004 | 14694 | 14.694 | -371 | 0.08
8005 | 14458 | 14.458 | -17 | 0.0425
8006 | 14746 | 14.746 | 90 | 0.1065
8007 | 14559 | 14.559 | -97 | 0.0425
8008 | 14693 | 14.693 | -520 | 0.0265
8009 | 14591 | 14.591 | -846 | 0.053
8010 | 14730 | 14.73 | 304 | 0.2075
8011 | 14493 | 14.493 | 369 | 0.2235
8012 | 14727 | 14.727 | -183 | 0.1385
8013 | 14836 | 14.836 | 957 | 0.1915
8014 | 14604 | 14.604 | 1 | 0
8015 | 14730 | 14.73 | -546 | 0
8016 | 14202 | 14.202 | -818 | 0
8017 | 13500 | 13.5 | -910 | 0.0905
8018 | 13980 | 13.98 | 558 | 0.383
8019 | 13978 | 13.978 | -804 | 0.3725
8020 | 14119 | 14.119 | 54 | 0.367
8021 | 13260 | 13.26 | -70 | 0.0105
8022 | 14445 | 14.445 | -9 | 0
8023 | 14730 | 14.73 | 937 | 0
8024 | 14698 | 14.698 | 534 | 0
8025 | 14717 | 14.717 | -789 | 0.0425
8026 | 14618 | 14.618 | 252 | 0.447
8027 | 14705 | 14.705 | 278 | 0.0955
8028 | 14632 | 14.632 | 712 | 0.053
8029 | 14706 | 14.706 | -392 | 0.101
8030 | 14831 | 14.831 | 614 | 0.016
8031 | 14654 | 14.654 | -720 | 0.6275
8032 | 14706 | 14.706 | -524 | 0.6435
8033 | 14674 | 14.674 | 877 | 0.197
8034 | 14746 | 14.746 | 551 | 0.117
8035 | 14611 | 14.611 | -130 | 0.101
8036 | 14723 | 14.723 | 196 | 0.149
8037 | 14591 | 14.591 | -470 | 0.415
8038 | 14689 | 14.689 | 718 | 0.016
8039 | 14766 | 14.766 | 189 | 0.08
8040 | 14655 | 14.655 | 752 | 0.6435
8041 | 14500 | 14.5 | -391 | 0.564
8042 | 14617 | 14.617 | 381 | 0.6545
8043 | 14628 | 14.628 | 274 | 0.9785
8044 | 14632 | 14.632 | -774 | 0.5905
8045 | 14644 | 14.644 | 477 | 0.314
8046 | 14504 | 14.504 | -196 | 1.202
8047 | 14893 | 14.893 | -511 | 0.335
8048 | 14619 | 14.619 | -329 | 0.5955
8049 | 14518 | 14.518 | 237 | 0.484
8050 | 14712 | 14.712 | 610 | 0.298
8051 | 14683 | 14.683 | 401 | 0.6755
8052 | 14742 | 14.742 | 309 | 0.782
8053 | 14587 | 14.587 | -229 | 0.814
8054 | 14581 | 14.581 | -42 | 0.585
8055 | 14599 | 14.599 | 753 | 0.5215
8056 | 14704 | 14.704 | 666 | 0.5955
8057 | 14617 | 14.617 | -71 | 1.085
8058 | 14744 | 14.744 | 610 | 1.181
8059 | 14615 | 14.615 | 39 | 0.3615
8060 | 14662 | 14.662 | 173 | 0.0215
8061 | 14623 | 14.623 | 260 | 0.633
8062 | 14680 | 14.68 | 943 | 0.484
8063 | 14612 | 14.612 | -546 | 1.5265
8064 | 14156 | 14.156 | -479 | 0.564
8065 | 13087 | 13.087 | -103 | 0.133
8066 | 14758 | 14.758 | 23 | 0.1225
8067 | 14610 | 14.61 | -401 | 0.1115
8068 | 14776 | 14.776 | 528 | 0.0105
8069 | 14658 | 14.658 | -454 | 0
8070 | 14714 | 14.714 | -928 | 0.181
8071 | 14549 | 14.549 | -974 | 0.0425
8072 | 14833 | 14.833 | -98 | 0.0265
8073 | 14644 | 14.644 | 716 | 0
8074 | 14709 | 14.709 | -192 | 0
8075 | 14625 | 14.625 | 197 | 0
8076 | 14682 | 14.682 | -878 | 0
8077 | 14704 | 14.704 | -451 | 0
8078 | 14693 | 14.693 | -903 | 0.016
8079 | 14634 | 14.634 | 971 | 0.282
8080 | 14766 | 14.766 | -669 | 0.1435
8081 | 14522 | 14.522 | 896 | 0.048
8082 | 14734 | 14.734 | 708 | 0
8083 | 14620 | 14.62 | 310 | 0
8084 | 14612 | 14.612 | 34 | 0.0055
8085 | 14593 | 14.593 | -692 | 0
8086 | 14675 | 14.675 | -113 | 0
8087 | 14658 | 14.658 | 532 | 0.0425
8088 | 14627 | 14.627 | 899 | 0.048
8089 | 14637 | 14.637 | 821 | 0
8090 | 14653 | 14.653 | -476 | 0.0055
8091 | 14638 | 14.638 | -206 | 0
8092 | 14611 | 14.611 | 904 | 0.0105
8093 | 14706 | 14.706 | -630 | 0.3935
8094 | 14558 | 14.558 | -240 | 0.25
8095 | 14679 | 14.679 | 420 | 0.3935
8096 | 14723 | 14.723 | -99 | 0.08
8097 | 14762 | 14.762 | 771 | 0.0585
8098 | 14606 | 14.606 | -180 | 0
8099 | 14695 | 14.695 | -6 | 0.037
8100 | 14573 | 14.573 | 343 | 0.037
8101 | 14761 | 14.761 | -978 | 0
8102 | 14344 | 14.344 | 15 | 0
8103 | 14843 | 14.843 | -222 | 0
8104 | 14486 | 14.486 | -132 | 0
8105 | 14745 | 14.745 | -602 | 0
8106 | 14670 | 14.67 | -905 | 0
8107 | 14578 | 14.578 | 808 | 0
8108 | 14634 | 14.634 | 292 | 0
8109 | 14641 | 14.641 | 518 | 0
8110 | 14788 | 14.788 | 829 | 0
8111 | 14735 | 14.735 | 188 | 0
8112 | 14475 | 14.475 | 119 | 0
8113 | 13786 | 13.786 | 232 | 0.1385
8114 | 13653 | 13.653 | 401 | 0.4895
8115 | 13978 | 13.978 | -276 | 0.6115
8116 | 13913 | 13.913 | 545 | 0.4945
8117 | 13750 | 13.75 | 646 | 0.367
8118 | 13355 | 13.355 | 362 | 0.5215
8119 | 14651 | 14.651 | -92 | 0.8455
8120 | 14551 | 14.551 | -700 | 0.665
8121 | 14619 | 14.619 | -170 | 0.4945
8122 | 14691 | 14.691 | -352 | 0.0425
8123 | 14754 | 14.754 | -576 | 0.213
8124 | 14822 | 14.822 | -409 | 0.1755
8125 | 14500 | 14.5 | 670 | 0.117
8126 | 14735 | 14.735 | 794 | 0.0105
8127 | 14591 | 14.591 | -446 | 0
8128 | 14757 | 14.757 | -455 | 0
8129 | 14702 | 14.702 | 440 | 0.085
8130 | 14643 | 14.643 | 395 | 0.186
8131 | 14589 | 14.589 | 333 | 0.0265
8132 | 14866 | 14.866 | -304 | 0.0215
8133 | 14562 | 14.562 | -781 | 0.1435
8134 | 14594 | 14.594 | -417 | 0.2075
8135 | 14725 | 14.725 | 831 | 0.181
8136 | 14559 | 14.559 | 901 | 0.282
8137 | 14594 | 14.594 | 893 | 0.33
8138 | 14744 | 14.744 | -479 | 0.7605
8139 | 14615 | 14.615 | 185 | 1.335
8140 | 14798 | 14.798 | 435 | 0.7285
8141 | 14578 | 14.578 | 785 | 0.8885
8142 | 14642 | 14.642 | -346 | 1.133
8143 | 14531 | 14.531 | -985 | 0.7285
8144 | 14679 | 14.679 | -741 | 0.4095
8145 | 14767 | 14.767 | 498 | 1.048
8146 | 14538 | 14.538 | -561 | 0.564
8147 | 14634 | 14.634 | -279 | 0.553
8148 | 14775 | 14.775 | 268 | 0.5585
8149 | 14734 | 14.734 | 466 | 0.3085
8150 | 14749 | 14.749 | -580 | 0.2285
8151 | 14830 | 14.83 | -811 | 0.282
8152 | 14693 | 14.693 | -311 | 0.0265
8153 | 14826 | 14.826 | -266 | 0
8154 | 14678 | 14.678 | 536 | 0
8155 | 14733 | 14.733 | -357 | 0
8156 | 14701 | 14.701 | 859 | 0
8157 | 14608 | 14.608 | 0 | 0
8158 | 14794 | 14.794 | -739 | 0
8159 | 14575 | 14.575 | -855 | 0
8160 | 14768 | 14.768 | -221 | 0
8161 | 14106 | 14.106 | -502 | 0
8162 | 13418 | 13.418 | -52 | 0
8163 | 14524 | 14.524 | -186 | 0
8164 | 14885 | 14.885 | 153 | 0
8165 | 14669 | 14.669 | 787 | 0
8166 | 14754 | 14.754 | -656 | 0
8167 | 14818 | 14.818 | 803 | 0
8168 | 14818 | 14.818 | -194 | 0
8169 | 14643 | 14.643 | -819 | 0
8170 | 14674 | 14.674 | 705 | 0
8171 | 14816 | 14.816 | -675 | 0
8172 | 14748 | 14.748 | 254 | 0
8173 | 14745 | 14.745 | 96 | 0
8174 | 14719 | 14.719 | -568 | 0
8175 | 14674 | 14.674 | 123 | 0
8176 | 14744 | 14.744 | -271 | 0
8177 | 14642 | 14.642 | 43 | 0.0055
8178 | 14638 | 14.638 | -90 | 0.0585
8179 | 14743 | 14.743 | 270 | 0.0955
8180 | 14515 | 14.515 | -354 | 0.351
8181 | 14752 | 14.752 | 777 | 0.7555
8182 | 14726 | 14.726 | 949 | 0.9785
8183 | 14670 | 14.67 | -13 | 0.7605
8184 | 14678 | 14.678 | 567 | 0.234
8185 | 14738 | 14.738 | 756 | 0.08
8186 | 14714 | 14.714 | 859 | 0.3775
8187 | 14544 | 14.544 | 488 | 0.367
8188 | 14639 | 14.639 | 505 | 0.064
8189 | 14573 | 14.573 | -893 | 0
8190 | 14647 | 14.647 | 415 | 0
8191 | 14714 | 14.714 | -814 | 0
8192 | 14493 | 14.493 | 178 | 0
8193 | 14518 | 14.518 | 8 | 0
8194 | 14538 | 14.538 | -784 | 0
8195 | 14655 | 14.655 | 496 | 0
8196 | 14635 | 14.635 | 355 | 0
8197 | 14593 | 14.593 | -586 | 0
8198 | 14710 | 14.71 | -174 | 0
8199 | 14800 | 14.8 | 396 | 0
8200 | 14695 | 14.695 | 939 | 0
8201 | 14822 | 14.822 | -759 | 0
8202 | 14113 | 14.113 | 863 | 0
8203 | 13756 | 13.756 | -281 | 0.016
8204 | 13945 | 13.945 | -913 | 0.6115
8205 | 14048 | 14.048 | -252 | 2.702
8206 | 14039 | 14.039 | -448 | 3.1065
8207 | 13422 | 13.422 | 564 | 2.8405
8208 | 14487 | 14.487 | 886 | 2.6595
8209 | 14680 | 14.68 | -284 | 2.697
8210 | 14844 | 14.844 | 729 | 2.7765
8211 | 14806 | 14.806 | 809 | 2.2715
8212 | 14773 | 14.773 | -228 | 2.681
8213 | 14837 | 14.837 | 842 | 2.5955
8214 | 14698 | 14.698 | 681 | 2.484
8215 | 14786 | 14.786 | 254 | 2.303
8216 | 14844 | 14.844 | 801 | 1.952
8217 | 14760 | 14.76 | -669 | 2.931
8218 | 14830 | 14.83 | -654 | 2.6115
8219 | 14642 | 14.642 | -2 | 2.5215
8220 | 14684 | 14.684 | -820 | 2.3885
8221 | 14617 | 14.617 | 293 | 2.085
8222 | 14462 | 14.462 | 328 | 2.0105
8223 | 14710 | 14.71 | 602 | 2.335
8224 | 14770 | 14.77 | 230 | 2.9095
8225 | 14477 | 14.477 | -227 | 3.2395
8226 | 14668 | 14.668 | -189 | 3.3615
8227 | 14636 | 14.636 | -789 | 3.447
8228 | 14555 | 14.555 | -491 | 3.4415
8229 | 14612 | 14.612 | 667 | 3.431
8230 | 14498 | 14.498 | -284 | 3.4095
8231 | 14466 | 14.466 | 423 | 3.1275
8232 | 14662 | 14.662 | 416 | 2.3935
8233 | 14542 | 14.542 | -522 | 2.6755
8234 | 14510 | 14.51 | 115 | 3.2395
8235 | 14461 | 14.461 | -331 | 3.085
8236 | 14598 | 14.598 | 226 | 3.2715
8237 | 14576 | 14.576 | 813 | 3.1115
8238 | 14528 | 14.528 | -12 | 3.048
8239 | 14405 | 14.405 | -810 | 2.548
8240 | 14709 | 14.709 | -384 | 2.1115
8241 | 14643 | 14.643 | -332 | 1.963
8242 | 14648 | 14.648 | -871 | 1.5265
8243 | 14455 | 14.455 | -835 | 1.0905
8244 | 14656 | 14.656 | -775 | 0.7925
8245 | 14542 | 14.542 | -361 | 0.5955
8246 | 14475 | 14.475 | 132 | 0.2715
8247 | 14760 | 14.76 | -573 | 0.931
8248 | 14827 | 14.827 | 141 | 1.5
8249 | 14638 | 14.638 | -943 | 1.851
8250 | 14499 | 14.499 | -522 | 2.1065
8251 | 14606 | 14.606 | -989 | 2.351
8252 | 14613 | 14.613 | -214 | 2.1275
8253 | 14684 | 14.684 | 195 | 1.6065
8254 | 14699 | 14.699 | 758 | 0.8455
8255 | 14668 | 14.668 | -823 | 0.819
8256 | 14204 | 14.204 | 144 | 0.5
8257 | 13540 | 13.54 | -152 | 0.4095
8258 | 13781 | 13.781 | -226 | 0.282
8259 | 14720 | 14.72 | -970 | 0.367
8260 | 14781 | 14.781 | 313 | 0.2075
8261 | 14775 | 14.775 | 798 | 0.585
8262 | 14732 | 14.732 | -947 | 0.697
8263 | 14776 | 14.776 | -482 | 0.532
8264 | 14598 | 14.598 | -566 | 0.447
8265 | 14792 | 14.792 | 689 | 0.42
8266 | 14695 | 14.695 | -33 | 0.415
8267 | 14694 | 14.694 | 961 | 0.2605
8268 | 14656 | 14.656 | -811 | 0.149
8269 | 14861 | 14.861 | 705 | 0.282
8270 | 14620 | 14.62 | 25 | 0.2765
8271 | 14631 | 14.631 | 633 | 0.367
8272 | 14733 | 14.733 | -219 | 0.181
8273 | 14704 | 14.704 | -108 | 0.0105
8274 | 14580 | 14.58 | -955 | 0
8275 | 14680 | 14.68 | 188 | 0
8276 | 14665 | 14.665 | -160 | 0
8277 | 14650 | 14.65 | 110 | 0.0215
8278 | 14564 | 14.564 | 770 | 0
8279 | 14534 | 14.534 | 456 | 0
8280 | 14590 | 14.59 | -104 | 0
8281 | 14623 | 14.623 | 311 | 0
8282 | 14590 | 14.59 | 315 | 0
8283 | 14616 | 14.616 | 198 | 0
8284 | 14682 | 14.682 | 351 | 0
8285 | 14471 | 14.471 | -260 | 0.1275
8286 | 14565 | 14.565 | -890 | 0.303
8287 | 14497 | 14.497 | -848 | 0.1065
8288 | 14618 | 14.618 | 372 | 0
8289 | 14552 | 14.552 | 278 | 0.2235
8290 | 14606 | 14.606 | 626 | 0.314
8291 | 14482 | 14.482 | 761 | 0.213
8292 | 14690 | 14.69 | 366 | 0.0955
8293 | 14628 | 14.628 | -173 | 0
8294 | 14622 | 14.622 | -758 | 0.303
8295 | 14562 | 14.562 | -979 | 0.5105
8296 | 14657 | 14.657 | -847 | 0.7235
8297 | 14619 | 14.619 | -185 | 0.8725
8298 | 14760 | 14.76 | -474 | 0.6225
8299 | 14758 | 14.758 | 897 | 0.7395
8300 | 14661 | 14.661 | -734 | 0.697
8301 | 14682 | 14.682 | -147 | 0.4735
8302 | 14781 | 14.781 | 154 | 0.4095
8303 | 14531 | 14.531 | 100 | 0.3455
8304 | 13888 | 13.888 | -129 | 0.282
8305 | 13694 | 13.694 | 316 | 0.415
8306 | 13909 | 13.909 | 101 | 0.6225
8307 | 13981 | 13.981 | -501 | 0.7715
8308 | 13941 | 13.941 | -506 | 0.617
8309 | 10781 | 10.781 | -8 | 0.8725
8310 | 12028 | 12.028 | 280 | 0.8455
8311 | 13531 | 13.531 | -446 | 0.9575
8312 | 14766 | 14.766 | -576 | 0.713
8313 | 14747 | 14.747 | 483 | 0.4575
8314 | 15016 | 15.016 | 600 | 0.5055
8315 | 14725 | 14.725 | -949 | 0.787
8316 | 14816 | 14.816 | 140 | 0.915
8317 | 14805 | 14.805 | 406 | 0.819
8318 | 14797 | 14.797 | -590 | 0.9095
8319 | 14762 | 14.762 | -41 | 1.069
8320 | 14809 | 14.809 | -839 | 0.617
8321 | 14593 | 14.593 | -855 | 0.2445
8322 | 14510 | 14.51 | -50 | 0.2925
8323 | 14603 | 14.603 | 249 | 0.202
8324 | 14561 | 14.561 | -775 | 0.2605
8325 | 14560 | 14.56 | 616 | 0.335
8326 | 14547 | 14.547 | -116 | 0.3245
8327 | 14500 | 14.5 | -584 | 0.303
8328 | 14676 | 14.676 | -86 | 0.649
8329 | 14487 | 14.487 | -425 | 0.7395
8330 | 14577 | 14.577 | -918 | 0.5955
8331 | 14514 | 14.514 | 375 | 0.415
8332 | 14693 | 14.693 | 72 | 0.367
8333 | 14267 | 14.267 | 633 | 0.3245
8334 | 14545 | 14.545 | -364 | 0.2235
8335 | 14494 | 14.494 | -336 | 0.0905
8336 | 14420 | 14.42 | 548 | 0
8337 | 14332 | 14.332 | 880 | 0
8338 | 14490 | 14.49 | 741 | 0
8339 | 14361 | 14.361 | -26 | 0
8340 | 14463 | 14.463 | 327 | 0
8341 | 14520 | 14.52 | 84 | 0
8342 | 14374 | 14.374 | 635 | 0
8343 | 14492 | 14.492 | 19 | 0
8344 | 14592 | 14.592 | 442 | 0
8345 | 14313 | 14.313 | 431 | 0
8346 | 14518 | 14.518 | -368 | 0
8347 | 14431 | 14.431 | 983 | 0
8348 | 14548 | 14.548 | -938 | 0.0585
8349 | 14672 | 14.672 | -708 | 0.234
8350 | 14635 | 14.635 | -419 | 0.085
8351 | 14350 | 14.35 | 99 | 0.298
8352 | 13725 | 13.725 | 121 | 0.25
8353 | 13509 | 13.509 | -931 | 0.186
8354 | 14544 | 14.544 | 92 | 0.2445
8355 | 14497 | 14.497 | 611 | 0.2555
8356 | 14647 | 14.647 | -59 | 0.4575
8357 | 14691 | 14.691 | 239 | 0.5265
8358 | 14567 | 14.567 | -214 | 0.5905
8359 | 14553 | 14.553 | 185 | 0.5585
8360 | 14756 | 14.756 | 969 | 0.4045
8361 | 14456 | 14.456 | -549 | 0.351
8362 | 14683 | 14.683 | 677 | 0.415
8363 | 14616 | 14.616 | 506 | 0.314
8364 | 14625 | 14.625 | 766 | 0.0215
8365 | 14713 | 14.713 | -695 | 0.1595
8366 | 14549 | 14.549 | -242 | 0.234
8367 | 14778 | 14.778 | -674 | 0.4785
8368 | 14686 | 14.686 | -18 | 0.032
8369 | 14697 | 14.697 | 759 | 0
8370 | 14503 | 14.503 | -499 | 0
8371 | 14642 | 14.642 | 459 | 0.064
8372 | 14769 | 14.769 | 544 | 0.4575
8373 | 14590 | 14.59 | -697 | 0.431
8374 | 14786 | 14.786 | 809 | 0.202
8375 | 14550 | 14.55 | -440 | 0.5745
8376 | 14579 | 14.579 | 869 | 1.085
8377 | 14532 | 14.532 | -925 | 0.516
8378 | 14487 | 14.487 | -451 | 0.0425
8379 | 14632 | 14.632 | -510 | 0.0215
8380 | 14343 | 14.343 | -504 | 0.0215
8381 | 14512 | 14.512 | 157 | 0
8382 | 14432 | 14.432 | -817 | 0
8383 | 14321 | 14.321 | -831 | 0
8384 | 14524 | 14.524 | 682 | 0
8385 | 14410 | 14.41 | -366 | 0.165
8386 | 14438 | 14.438 | 527 | 0.9095
8387 | 14334 | 14.334 | 345 | 0.564
8388 | 14562 | 14.562 | 289 | 0
8389 | 14518 | 14.518 | 725 | 0
8390 | 14484 | 14.484 | 574 | 0.032
8391 | 14577 | 14.577 | -526 | 0.585
8392 | 14674 | 14.674 | -833 | 0.4095
8393 | 14635 | 14.635 | -426 | 0.218
8394 | 14679 | 14.679 | 453 | 0.399
8395 | 14575 | 14.575 | -62 | 0.537
8396 | 14623 | 14.623 | -257 | 0.314
8397 | 14590 | 14.59 | -139 | 0.67
8398 | 14686 | 14.686 | 540 | 0.5105
8399 | 14722 | 14.722 | 774 | 0.319
8400 | 13978 | 13.978 | 234 | 0.447
8401 | 13534 | 13.534 | 876 | 1.3085
8402 | 14062 | 14.062 | -869 | 1.4255
8403 | 14026 | 14.026 | 643 | 0.8885
8404 | 14082 | 14.082 | -615 | 1.282
8405 | 13474 | 13.474 | -401 | 2.0425
8406 | 14559 | 14.559 | 685 | 1.585
8407 | 14714 | 14.714 | -17 | 1.1595
8408 | 14657 | 14.657 | -468 | 0.585
8409 | 14573 | 14.573 | 494 | 0.702
8410 | 14843 | 14.843 | 504 | 0.686
8411 | 14677 | 14.677 | -932 | 0.1595
8412 | 14722 | 14.722 | 9 | 0.3455
8413 | 14695 | 14.695 | 722 | 0
8414 | 14737 | 14.737 | 85 | 0
8415 | 14662 | 14.662 | 775 | 0
8416 | 14740 | 14.74 | 91 | 0
8417 | 14664 | 14.664 | 499 | 0.2605
8418 | 14606 | 14.606 | -513 | 0.3455
8419 | 14771 | 14.771 | 792 | 0.367
8420 | 14478 | 14.478 | 471 | 0.537
8421 | 14691 | 14.691 | -422 | 0.5265
8422 | 14615 | 14.615 | -647 | 0.67
8423 | 14508 | 14.508 | 576 | 0.7235
8424 | 14746 | 14.746 | 53 | 1.0955
8425 | 14590 | 14.59 | -689 | 1.101
8426 | 14620 | 14.62 | 455 | 1.5745
8427 | 14711 | 14.711 | -697 | 1.2235
8428 | 14681 | 14.681 | 946 | 1.569
8429 | 14563 | 14.563 | -763 | 1.25
8430 | 14614 | 14.614 | -907 | 0.9945
8431 | 14535 | 14.535 | -60 | 0.7445
8432 | 14486 | 14.486 | 171 | 1.032
8433 | 14638 | 14.638 | 861 | 0.7605
8434 | 14550 | 14.55 | -315 | 0.436
8435 | 14590 | 14.59 | 275 | 0.3565
8436 | 14745 | 14.745 | -362 | 0.463
8437 | 14642 | 14.642 | 100 | 0.6225
8438 | 14571 | 14.571 | -198 | 1.0265
8439 | 14760 | 14.76 | -294 | 1.0585
8440 | 14535 | 14.535 | -381 | 0.8725
8441 | 14672 | 14.672 | 81 | 0.548
8442 | 14783 | 14.783 | 15 | 0.117
8443 | 14521 | 14.521 | 809 | 0
8444 | 14706 | 14.706 | -568 | 0.08
8445 | 14775 | 14.775 | 476 | 0.048
8446 | 14681 | 14.681 | -278 | 0.452
8447 | 14688 | 14.688 | 258 | 0.1065
8448 | 14091 | 14.091 | -87 | 0
8449 | 13124 | 13.124 | 481 | 0
8450 | 14200 | 14.2 | 256 | 0
8451 | 14549 | 14.549 | -599 | 0
8452 | 14894 | 14.894 | -367 | 0
8453 | 14721 | 14.721 | -475 | 0
8454 | 14609 | 14.609 | 310 | 0
8455 | 14890 | 14.89 | -620 | 0
8456 | 14517 | 14.517 | 875 | 0
8457 | 14742 | 14.742 | 75 | 0
8458 | 14762 | 14.762 | -585 | 0
8459 | 14675 | 14.675 | 891 | 0
8460 | 14636 | 14.636 | 264 | 0
8461 | 14838 | 14.838 | -301 | 0
8462 | 14671 | 14.671 | 371 | 0
8463 | 14625 | 14.625 | -145 | 0
8464 | 14686 | 14.686 | 741 | 0
8465 | 14704 | 14.704 | -845 | 0
8466 | 14610 | 14.61 | -227 | 0
8467 | 14638 | 14.638 | 374 | 0
8468 | 14636 | 14.636 | 3 | 0
8469 | 14649 | 14.649 | 24 | 0
8470 | 14671 | 14.671 | -580 | 0
8471 | 14597 | 14.597 | -464 | 0
8472 | 14547 | 14.547 | -96 | 0
8473 | 14718 | 14.718 | 705 | 0
8474 | 14624 | 14.624 | 982 | 0
8475 | 14693 | 14.693 | 846 | 0
8476 | 14671 | 14.671 | 802 | 0
8477 | 14622 | 14.622 | -974 | 0.048
8478 | 14682 | 14.682 | -964 | 0.2715
8479 | 14679 | 14.679 | -813 | 0.298
8480 | 14779 | 14.779 | 337 | 0.42
8481 | 14661 | 14.661 | 291 | 0.1275
8482 | 14684 | 14.684 | 597 | 0.016
8483 | 14733 | 14.733 | 992 | 0
8484 | 14569 | 14.569 | -510 | 0
8485 | 14793 | 14.793 | 932 | 0
8486 | 14592 | 14.592 | -452 | 0
8487 | 14846 | 14.846 | -273 | 0
8488 | 14721 | 14.721 | -256 | 0
8489 | 14770 | 14.77 | 329 | 0.032
8490 | 14653 | 14.653 | 113 | 0.0055
8491 | 14485 | 14.485 | -162 | 0
8492 | 14770 | 14.77 | 305 | 0
8493 | 14623 | 14.623 | 243 | 0
8494 | 14749 | 14.749 | 141 | 0.0055
8495 | 14476 | 14.476 | -352 | 0
8496 | 14158 | 14.158 | -154 | 0
8497 | 13696 | 13.696 | 807 | 0
8498 | 14199 | 14.199 | 748 | 0
8499 | 14089 | 14.089 | -352 | 0
8500 | 14021 | 14.021 | 760 | 0
8501 | 13727 | 13.727 | -928 | 0
8502 | 14723 | 14.723 | 904 | 0
8503 | 14671 | 14.671 | -262 | 0
8504 | 14841 | 14.841 | 124 | 0
8505 | 14724 | 14.724 | 827 | 0.314
8506 | 14684 | 14.684 | -229 | 0.713
8507 | 14692 | 14.692 | -755 | 0.032
8508 | 14696 | 14.696 | -971 | 0.069
8509 | 14769 | 14.769 | 565 | 0
8510 | 14784 | 14.784 | 9 | 0.0425
8511 | 14695 | 14.695 | -511 | 0.0745
8512 | 14681 | 14.681 | -204 | 0.0265
8513 | 14689 | 14.689 | 257 | 0
8514 | 14640 | 14.64 | 767 | 0
8515 | 14649 | 14.649 | 729 | 0.8085
8516 | 14795 | 14.795 | -974 | 1.8455
8517 | 14706 | 14.706 | -924 | 1.7925
8518 | 14695 | 14.695 | -314 | 1.6755
8519 | 14596 | 14.596 | 263 | 1.9415
8520 | 14611 | 14.611 | -43 | 2.2555
8521 | 14528 | 14.528 | -421 | 2.1065
8522 | 14854 | 14.854 | -583 | 2.4735
8523 | 14592 | 14.592 | -23 | 2.282
8524 | 14685 | 14.685 | 583 | 2.085
8525 | 14609 | 14.609 | 430 | 2.3245
8526 | 14636 | 14.636 | -488 | 1.9575
8527 | 14689 | 14.689 | 164 | 1.5905
8528 | 14715 | 14.715 | -700 | 1.2235
8529 | 14636 | 14.636 | 408 | 1.4575
8530 | 14650 | 14.65 | 300 | 1.532
8531 | 14417 | 14.417 | -736 | 0.984
8532 | 14734 | 14.734 | -822 | 0.7235
8533 | 14766 | 14.766 | -252 | 0.484
8534 | 14512 | 14.512 | 229 | 0.5215
8535 | 14918 | 14.918 | 638 | 0.149
8536 | 14690 | 14.69 | -860 | 0.101
8537 | 14735 | 14.735 | -467 | 0.4735
8538 | 14722 | 14.722 | -725 | 0.1115
8539 | 14881 | 14.881 | -353 | 0.1275
8540 | 14740 | 14.74 | 503 | 0.0425
8541 | 14486 | 14.486 | 893 | 0
8542 | 14984 | 14.984 | -278 | 0
8543 | 14737 | 14.737 | 737 | 0
8544 | 14768 | 14.768 | 808 | 0
8545 | 14098 | 14.098 | -523 | 0
8546 | 13287 | 13.287 | 174 | 0
8547 | 14220 | 14.22 | 288 | 0
8548 | 14848 | 14.848 | 246 | 0
8549 | 14780 | 14.78 | 393 | 0
8550 | 14785 | 14.785 | 492 | 0
8551 | 14683 | 14.683 | -55 | 0
8552 | 14790 | 14.79 | 156 | 0
8553 | 14572 | 14.572 | -399 | 0
8554 | 14674 | 14.674 | -754 | 0
8555 | 14733 | 14.733 | -263 | 0
8556 | 14743 | 14.743 | -225 | 0
8557 | 14636 | 14.636 | 380 | 0
8558 | 14671 | 14.671 | 707 | 0
8559 | 14708 | 14.708 | -888 | 0
8560 | 14693 | 14.693 | 892 | 0
8561 | 14571 | 14.571 | -770 | 0
8562 | 14538 | 14.538 | -459 | 0
8563 | 14662 | 14.662 | 901 | 0
8564 | 14730 | 14.73 | 244 | 0
8565 | 14608 | 14.608 | 376 | 0
8566 | 14714 | 14.714 | -628 | 0
8567 | 14627 | 14.627 | -613 | 0
8568 | 14641 | 14.641 | -800 | 0
8569 | 14637 | 14.637 | -363 | 0
8570 | 14757 | 14.757 | 295 | 0
8571 | 14630 | 14.63 | -985 | 0
8572 | 14563 | 14.563 | 40 | 0.037
8573 | 14635 | 14.635 | 876 | 0
8574 | 14714 | 14.714 | -27 | 0
8575 | 14624 | 14.624 | -759 | 0.0425
8576 | 14691 | 14.691 | 260 | 0.0265
8577 | 14427 | 14.427 | 297 | 0
8578 | 14761 | 14.761 | -42 | 0
8579 | 14633 | 14.633 | 502 | 0
8580 | 14861 | 14.861 | -844 | 0
8581 | 14652 | 14.652 | 591 | 0
8582 | 14664 | 14.664 | -346 | 0
8583 | 14822 | 14.822 | 206 | 0
8584 | 14695 | 14.695 | -837 | 0
8585 | 14838 | 14.838 | 948 | 0
8586 | 14598 | 14.598 | 385 | 0
8587 | 14631 | 14.631 | -282 | 0
8588 | 14736 | 14.736 | -996 | 0
8589 | 14694 | 14.694 | 19 | 0
8590 | 14611 | 14.611 | -465 | 0
8591 | 14774 | 14.774 | 845 | 0
8592 | 13846 | 13.846 | -103 | 0.085
8593 | 13550 | 13.55 | 775 | 0.2235
8594 | 13808 | 13.808 | -246 | 0.2765
8595 | 13963 | 13.963 | 651 | 0.314
8596 | 14017 | 14.017 | -130 | 0.0055
8597 | 13267 | 13.267 | -485 | 0
8598 | 14527 | 14.527 | -220 | 0
8599 | 14637 | 14.637 | 140 | 0
8600 | 14825 | 14.825 | 391 | 0.0585
8601 | 14717 | 14.717 | 511 | 0.085
8602 | 14590 | 14.59 | 342 | 0
8603 | 14665 | 14.665 | -915 | 0
8604 | 14595 | 14.595 | 372 | 0
8605 | 14700 | 14.7 | 698 | 0
8606 | 14693 | 14.693 | 856 | 0
8607 | 14686 | 14.686 | 926 | 0
8608 | 14618 | 14.618 | 236 | 0
8609 | 14661 | 14.661 | -161 | 0
8610 | 14639 | 14.639 | -436 | 0
8611 | 14675 | 14.675 | 145 | 0
8612 | 14668 | 14.668 | 697 | 0
8613 | 14571 | 14.571 | -927 | 0
8614 | 14576 | 14.576 | -263 | 0
8615 | 14436 | 14.436 | 220 | 0
8616 | 14633 | 14.633 | 104 | 0
8617 | 14616 | 14.616 | 575 | 0
8618 | 14564 | 14.564 | 121 | 0
8619 | 14733 | 14.733 | 955 | 0
8620 | 14534 | 14.534 | -288 | 0
8621 | 14870 | 14.87 | -327 | 0
8622 | 14630 | 14.63 | 113 | 0
8623 | 14652 | 14.652 | -52 | 0.0055
8624 | 14540 | 14.54 | 295 | 0
8625 | 14807 | 14.807 | -384 | 0
8626 | 14416 | 14.416 | -555 | 0
8627 | 14655 | 14.655 | -114 | 0
8628 | 14647 | 14.647 | -76 | 0
8629 | 14629 | 14.629 | -199 | 0
8630 | 14708 | 14.708 | 240 | 0
8631 | 14665 | 14.665 | 557 | 0
8632 | 14781 | 14.781 | -831 | 0
8633 | 14663 | 14.663 | -864 | 0
8634 | 14654 | 14.654 | -200 | 0
8635 | 14641 | 14.641 | -493 | 0
8636 | 14591 | 14.591 | -485 | 0
8637 | 14722 | 14.722 | 494 | 0
8638 | 14667 | 14.667 | 80 | 0
8639 | 14550 | 14.55 | 10 | 0
8640 | 13731 | 13.731 | -628 | 0
8641 | 13457 | 13.457 | -460 | 0
8642 | 14680 | 14.68 | -154 | 0
8643 | 14614 | 14.614 | -385 | 0
8644 | 14855 | 14.855 | -618 | 0
8645 | 14610 | 14.61 | 7 | 0
8646 | 14778 | 14.778 | -639 | 0
8647 | 14678 | 14.678 | -156 | 0.069
8648 | 14657 | 14.657 | -108 | 0.037
8649 | 14706 | 14.706 | 795 | 0.0265
8650 | 14579 | 14.579 | -845 | 0
8651 | 14772 | 14.772 | -339 | 0
8652 | 14729 | 14.729 | 612 | 0
8653 | 14647 | 14.647 | -132 | 0
8654 | 14712 | 14.712 | -16 | 0
8655 | 14624 | 14.624 | -639 | 0.0055
8656 | 14625 | 14.625 | 477 | 0.0265
8657 | 14631 | 14.631 | 744 | 0.064
8658 | 14665 | 14.665 | -145 | 0
8659 | 14605 | 14.605 | 744 | 0
8660 | 14521 | 14.521 | -918 | 0
8661 | 12340 | 12.34 | 483 | 0
8662 | 14453 | 14.453 | 81 | 0.2395
8663 | 14106 | 14.106 | -588 | 0.718
8664 | 12629 | 12.629 | 476 | 0.67
8665 | 10952 | 10.952 | 74 | 1.1115
8666 | 11959 | 11.959 | 159 | 0.952
8667 | 14592 | 14.592 | -991 | 1.032
8668 | 14778 | 14.778 | -369 | 1.053
8669 | 14906 | 14.906 | -86 | 0.899
8670 | 14674 | 14.674 | 837 | 1.0105
8671 | 14574 | 14.574 | 75 | 0.787
8672 | 14585 | 14.585 | 236 | 0.5265
8673 | 14311 | 14.311 | -382 | 0.8775
8674 | 14594 | 14.594 | -685 | 0.8725
8675 | 14640 | 14.64 | 941 | 0.6225
8676 | 14640 | 14.64 | -509 | 0.3935
8677 | 14722 | 14.722 | -449 | 0.33
8678 | 14827 | 14.827 | 679 | 0.3935
8679 | 14736 | 14.736 | -537 | 0.0215
8680 | 14615 | 14.615 | -721 | 0
8681 | 14708 | 14.708 | 963 | 0.016
8682 | 14581 | 14.581 | 346 | 0
8683 | 14720 | 14.72 | -921 | 0
8684 | 14782 | 14.782 | 129 | 0
8685 | 14540 | 14.54 | 73 | 0.1275
8686 | 14613 | 14.613 | -525 | 0.2925
8687 | 14816 | 14.816 | 712 | 0.686
8688 | 14618 | 14.618 | -658 | 0.383
8689 | 14772 | 14.772 | 23 | 0.048
8690 | 14625 | 14.625 | 771 | 0.202
8691 | 14689 | 14.689 | 519 | 0.665
8692 | 14750 | 14.75 | -224 | 0.3615
8693 | 14680 | 14.68 | 599 | 0.4785
8694 | 14697 | 14.697 | 103 | 0.1915
8695 | 14711 | 14.711 | 387 | 0.0905
8696 | 14607 | 14.607 | -358 | 0
8697 | 14737 | 14.737 | -470 | 0
8698 | 14700 | 14.7 | -852 | 0.0585
8699 | 14688 | 14.688 | 911 | 0.133
8700 | 14707 | 14.707 | 673 | 0.516
8701 | 14809 | 14.809 | -568 | 0.25
8702 | 14734 | 14.734 | 395 | 0.0585
8703 | 14761 | 14.761 | 737 | 0.383
8704 | 13768 | 13.768 | 569 | 1.037
8705 | 13715 | 13.715 | -124 | 0.819
8706 | 13727 | 13.727 | -102 | 0.782
8707 | 14007 | 14.007 | -335 | 0.8615
8708 | 13822 | 13.822 | 550 | 0.803
8709 | 13352 | 13.352 | -84 | 0.718
8710 | 14550 | 14.55 | -455 | 0.3775
8711 | 14569 | 14.569 | -690 | 0.6385
8712 | 14765 | 14.765 | -943 | 1.101
8713 | 14592 | 14.592 | 472 | 1.032
8714 | 14690 | 14.69 | 576 | 0.851
8715 | 14648 | 14.648 | -412 | 1.117
8716 | 14558 | 14.558 | 86 | 0.9735
8717 | 14600 | 14.6 | 942 | 0.7715
8718 | 14683 | 14.683 | 1 | 1.702
8719 | 14589 | 14.589 | -168 | 1.7605
8720 | 14641 | 14.641 | -317 | 1.681
8721 | 14580 | 14.58 | -344 | 1.2715
8722 | 14596 | 14.596 | -881 | 1.266
8723 | 14790 | 14.79 | -84 | 0.9575
8724 | 14646 | 14.646 | -605 | 0.0215
8725 | 14676 | 14.676 | 805 | 0.0745
8726 | 14629 | 14.629 | -842 | 0.0215
8727 | 14668 | 14.668 | -570 | 0.0265
8728 | 14601 | 14.601 | 851 | 0.3885
8729 | 14617 | 14.617 | -312 | 0.5905
8730 | 14661 | 14.661 | 326 | 0.564
8731 | 14566 | 14.566 | -25 | 0.016
8732 | 14563 | 14.563 | 72 | 0.08
8733 | 14754 | 14.754 | 889 | 0.303
8734 | 14468 | 14.468 | -918 | 0.335
8735 | 14601 | 14.601 | 270 | 0
8736 | 13923 | 13.923 | -708 | 0
8737 | 12994 | 12.994 | -385 | 1.85
8738 | 14444 | 14.444 | 77 | 2.15
8739 | 14622 | 14.622 | -445 | 4.9
8740 | 14750 | 14.75 | 61 | 1.15
8741 | 14508 | 14.508 | 47 | 2.4
8742 | 14707 | 14.707 | 407 | 4.85
8743 | 14655 | 14.655 | 401 | 3.9
8744 | 14700 | 14.7 | 302 | 2.05
8745 | 14642 | 14.642 | -96 | 3.8
8746 | 14686 | 14.686 | 344 | 2.8
8747 | 14681 | 14.681 | 109 | 4.35
8748 | 14685 | 14.685 | -150 | 1.05
8749 | 14655 | 14.655 | 900 | 4.75
8750 | 14602 | 14.602 | 910 | 0.8
8751 | 14726 | 14.726 | 630 | 2.05
8752 | 14692 | 14.692 | 892 | 0.05
8753 | 14694 | 14.694 | 149 | 2.95
8754 | 14528 | 14.528 | -675 | 1.6
8755 | 14660 | 14.66 | -551 | 2.05
8756 | 14644 | 14.644 | -16 | 3.65
8757 | 14553 | 14.553 | -236 | 1.9
8758 | 14691 | 14.691 | 801 | 1
8759 | 14614 | 14.614 | 571 | 0.6
8760 | 14665 | 14.665 | 451 | 4.05
8761 | 14518 | 14.518 | -452 | 4.2
8762 | 14513 | 14.513 | -514 | 2.55
8763 | 14502 | 14.502 | 666 | 2.55
8764 | 14599 | 14.599 | -215 | 2.55
8765 | 14624 | 14.624 | -239 | 0.55
8766 | 14462 | 14.462 | 739 | 4.65
8767 | 14435 | 14.435 | 118 | 4.9
8768 | 14671 | 14.671 | -239 | 1.65
8769 | 14579 | 14.579 | -107 | 2.75
8770 | 14514 | 14.514 | -68 | 1.85
8771 | 14591 | 14.591 | -486 | 0.5
8772 | 14585 | 14.585 | -552 | 2.6
8773 | 14632 | 14.632 | -851 | 4.55
8774 | 14675 | 14.675 | -47 | 4
8775 | 14562 | 14.562 | -961 | 0.35
8776 | 14661 | 14.661 | 649 | 3.15
8777 | 14699 | 14.699 | -969 | 3.45
8778 | 14675 | 14.675 | -562 | 3.95
8779 | 14678 | 14.678 | -116 | 1.6
8780 | 14618 | 14.618 | 631 | 0.35
8781 | 14767 | 14.767 | 520 | 4.5
8782 | 14638 | 14.638 | 889 | 4.95
8783 | 13914 | 13.914 | 106 | 2.15
8784 | 13614 | 13.614 | -671 | 1.7
8785 | 13744 | 13.744 | -766 | 1.25
8786 | 13789 | 13.789 | 834 | 2.25
8787 | 14157 | 14.157 | 247 | 3.4
8788 | 13361 | 13.361 | 47 | 4.65
8789 | 13996 | 13.996 | -397 | 3.3
8790 | 14648 | 14.648 | 385 | 0.35
8791 | 14631 | 14.631 | 12 | 4.25
8792 | 14653 | 14.653 | -161 | 0.15
8793 | 14758 | 14.758 | 670 | 2.9
8794 | 14745 | 14.745 | -755 | 2.4
8795 | 14732 | 14.732 | -265 | 2.6
8796 | 14670 | 14.67 | 629 | 0.45
8797 | 14653 | 14.653 | 179 | 4.1
8798 | 14705 | 14.705 | 1000 | 0.95
8799 | 14484 | 14.484 | -519 | 0.85
8800 | 14792 | 14.792 | -197 | 1.95
8801 | 14604 | 14.604 | 58 | 1.25
8802 | 14677 | 14.677 | 878 | 1.85
8803 | 14605 | 14.605 | 655 | 1.15
8804 | 14775 | 14.775 | 255 | 0.3
8805 | 14474 | 14.474 | -88 | 3.65
8806 | 14744 | 14.744 | 377 | 0.8
8807 | 14487 | 14.487 | -398 | 4.4
8808 | 14622 | 14.622 | -610 | 3.85
8809 | 14709 | 14.709 | -716 | 2.4
8810 | 14523 | 14.523 | 310 | 3.2
8811 | 14663 | 14.663 | 918 | 0.85
8812 | 14561 | 14.561 | 779 | 3.3
8813 | 14614 | 14.614 | -544 | 3.6
8814 | 14649 | 14.649 | 187 | 4.25
8815 | 14645 | 14.645 | -663 | 1.95
8816 | 14603 | 14.603 | -257 | 0.85
8817 | 14593 | 14.593 | 692 | 2.5
8818 | 14530 | 14.53 | -50 | 4.6
8819 | 14592 | 14.592 | -119 | 1.3
8820 | 14664 | 14.664 | 655 | 2.35
8821 | 14550 | 14.55 | -478 | 3.7
8822 | 14705 | 14.705 | -342 | 1.6
8823 | 14662 | 14.662 | 797 | 2.85
8824 | 14792 | 14.792 | -769 | 0.25
8825 | 14605 | 14.605 | 126 | 1.15
8826 | 14750 | 14.75 | -405 | 4.55
8827 | 14652 | 14.652 | -482 | 3.85
8828 | 14601 | 14.601 | -60 | 0.85
8829 | 14625 | 14.625 | -165 | 1.9
8830 | 14775 | 14.775 | -631 | 0.6
8831 | 14530 | 14.53 | 676 | 2.05
8832 | 13704 | 13.704 | 436 | 2.6
8833 | 13171 | 13.171 | -64 | 0.85
8834 | 14558 | 14.558 | 434 | 4.4
8835 | 14750 | 14.75 | -599 | 2.7
8836 | 14738 | 14.738 | -502 | 2.85
8837 | 14811 | 14.811 | -658 | 1.3
8838 | 14889 | 14.889 | 964 | 3.1
8839 | 14764 | 14.764 | 965 | 2.8
8840 | 14645 | 14.645 | 894 | 3.5
8841 | 14842 | 14.842 | -834 | 0.55
8842 | 14618 | 14.618 | -534 | 0.6
8843 | 14665 | 14.665 | 615 | 1.35
8844 | 14732 | 14.732 | 441 | 2.25
8845 | 14693 | 14.693 | -840 | 2.8
8846 | 14761 | 14.761 | 996 | 4.95
8847 | 14713 | 14.713 | -622 | 1.35
8848 | 14698 | 14.698 | 12 | 1.55
8849 | 14625 | 14.625 | 332 | 1.9
8850 | 14554 | 14.554 | 347 | 2.55
8851 | 14580 | 14.58 | 273 | 4.75
8852 | 14539 | 14.539 | -666 | 0.35
8853 | 14598 | 14.598 | -493 | 4.3
8854 | 14628 | 14.628 | 396 | 4.35
8855 | 14631 | 14.631 | 148 | 4.15
8856 | 14575 | 14.575 | 775 | 3.35
8857 | 14527 | 14.527 | 638 | 3.1
8858 | 14483 | 14.483 | 56 | 4.55
8859 | 14514 | 14.514 | -952 | 1.6
8860 | 14547 | 14.547 | 162 | 2.4
8861 | 14550 | 14.55 | 46 | 3.9
8862 | 14551 | 14.551 | 804 | 0
8863 | 14550 | 14.55 | -948 | 3.1
8864 | 14599 | 14.599 | -642 | 4.2
8865 | 14588 | 14.588 | -730 | 3.65
8866 | 14520 | 14.52 | 728 | 3.7
8867 | 14560 | 14.56 | 6 | 4.5
8868 | 14720 | 14.72 | 411 | 2.7
8869 | 14601 | 14.601 | -127 | 4.6
8870 | 14696 | 14.696 | -913 | 1.9
8871 | 14722 | 14.722 | 296 | 3.85
8872 | 14595 | 14.595 | -761 | 4.8
8873 | 14687 | 14.687 | 279 | 0.15
8874 | 14469 | 14.469 | 29 | 1.5
8875 | 14731 | 14.731 | 398 | 4.65
8876 | 14471 | 14.471 | 919 | 2
8877 | 14707 | 14.707 | 477 | 1.75
8878 | 14619 | 14.619 | 98 | 1.3
8879 | 14637 | 14.637 | -10 | 3.85
8880 | 14174 | 14.174 | 677 | 3.65
8881 | 13579 | 13.579 | 294 | 2.4
8882 | 13701 | 13.701 | 12 | 4.7
8883 | 14091 | 14.091 | -510 | 1.95
8884 | 13863 | 13.863 | 195 | 0.1
8885 | 13256 | 13.256 | 71 | 4
8886 | 14358 | 14.358 | 430 | 4.95
8887 | 14599 | 14.599 | -182 | 0.15
8888 | 14459 | 14.459 | -144 | 0.7
8889 | 14727 | 14.727 | -738 | 2.45
8890 | 14579 | 14.579 | 339 | 2.05
8891 | 14585 | 14.585 | -547 | 0.65
8892 | 14517 | 14.517 | -511 | 0.15
8893 | 14574 | 14.574 | 322 | 0.9
8894 | 14528 | 14.528 | 466 | 0.85
8895 | 14484 | 14.484 | -602 | 2.9
8896 | 14583 | 14.583 | 81 | 2.25
8897 | 14346 | 14.346 | -355 | 0.4
8898 | 14469 | 14.469 | -118 | 3.6
8899 | 14540 | 14.54 | 329 | 0.85
8900 | 14412 | 14.412 | 132 | 1.6
8901 | 14528 | 14.528 | -78 | 0.95
8902 | 14425 | 14.425 | -677 | 1.15
8903 | 14450 | 14.45 | -346 | 2.05
8904 | 14320 | 14.32 | 803 | 0.8
8905 | 14440 | 14.44 | -224 | 1.1
8906 | 14468 | 14.468 | 977 | 2.4
8907 | 14555 | 14.555 | -950 | 2.2
8908 | 14723 | 14.723 | 823 | 4.1
8909 | 14476 | 14.476 | 732 | 1.6
8910 | 14408 | 14.408 | 140 | 5
8911 | 14487 | 14.487 | 219 | 2
8912 | 14342 | 14.342 | 953 | 2.7
8913 | 14577 | 14.577 | 826 | 4.55
8914 | 14495 | 14.495 | -928 | 4.55
8915 | 14383 | 14.383 | 100 | 0.65
8916 | 14606 | 14.606 | 464 | 0.65
8917 | 14550 | 14.55 | -732 | 1.6
8918 | 14525 | 14.525 | 121 | 3.85
8919 | 14511 | 14.511 | 428 | 4.6
8920 | 14678 | 14.678 | -201 | 4.65
8921 | 14700 | 14.7 | -663 | 1.35
8922 | 14788 | 14.788 | 332 | 2.65
8923 | 14725 | 14.725 | -856 | 0.55
8924 | 14643 | 14.643 | 884 | 1.65
8925 | 14725 | 14.725 | 459 | 4.2
8926 | 14545 | 14.545 | 218 | 0.45
8927 | 14783 | 14.783 | 245 | 4.7
8928 | 14658 | 14.658 | -275 | 1.55
8929 | 14758 | 14.758 | -562 | 0.85
8930 | 13668 | 13.668 | -159 | 2.5
8931 | 13700 | 13.7 | 243 | 4.65
8932 | 14579 | 14.579 | 16 | 3.7
8933 | 14725 | 14.725 | -716 | 0.6
8934 | 14766 | 14.766 | -202 | 4.3
8935 | 14794 | 14.794 | 604 | 1.35
8936 | 14619 | 14.619 | 629 | 0.35
8937 | 14716 | 14.716 | 817 | 0.9
8938 | 14549 | 14.549 | 248 | 4.15
8939 | 14836 | 14.836 | -524 | 0.2
8940 | 14732 | 14.732 | 738 | 1.1
8941 | 14789 | 14.789 | -150 | 1.5
8942 | 14646 | 14.646 | 695 | 2.3
8943 | 14723 | 14.723 | -243 | 0.75
8944 | 14605 | 14.605 | 251 | 3.25
8945 | 14731 | 14.731 | -31 | 3.45
8946 | 14614 | 14.614 | -572 | 2.6
8947 | 14580 | 14.58 | 918 | 2.85
8948 | 14510 | 14.51 | -957 | 0.9
8949 | 14582 | 14.582 | 413 | 2.75
8950 | 14461 | 14.461 | 648 | 1.75
8951 | 14669 | 14.669 | -536 | 0.2
8952 | 14726 | 14.726 | 449 | 4.95
8953 | 14432 | 14.432 | 176 | 3.5
8954 | 14526 | 14.526 | -471 | 2.65
8955 | 14369 | 14.369 | -178 | 4.45
8956 | 14477 | 14.477 | -92 | 2.5
8957 | 14459 | 14.459 | 416 | 0.9
8958 | 14711 | 14.711 | -464 | 1.15
8959 | 14500 | 14.5 | 183 | 3.9
8960 | 14343 | 14.343 | -880 | 4.55
8961 | 14334 | 14.334 | -538 | 0.9
8962 | 14302 | 14.302 | 510 | 1.7
8963 | 14555 | 14.555 | 550 | 3.2
8964 | 14433 | 14.433 | 153 | 1.55
8965 | 14539 | 14.539 | -193 | 1.35
8966 | 14482 | 14.482 | -474 | 3.15
8967 | 14652 | 14.652 | -216 | 0.1
8968 | 14628 | 14.628 | -425 | 1.7
8969 | 14526 | 14.526 | 220 | 0.15
8970 | 14728 | 14.728 | -455 | 0.15
8971 | 14641 | 14.641 | 796 | 0.95
8972 | 14665 | 14.665 | 916 | 1.4
8973 | 14551 | 14.551 | 764 | 1.55
8974 | 14634 | 14.634 | -78 | 0.3
8975 | 14684 | 14.684 | -426 | 3.65
8976 | 14287 | 14.287 | 630 | 4.6
8977 | 13481 | 13.481 | 912 | 2.75
8978 | 13841 | 13.841 | 975 | 4.5
8979 | 12996 | 12.996 | 992 | 4
8980 | 4 | 0.004 | -456 | 4.25
8981 | 0 | 0 | 177 | 3.35
8982 | 0 | 0 | -431 | 2.9
8983 | 0 | 0 | 844 | 3.05
8984 | 0 | 0 | 676 | 2.85
8985 | 0 | 0 | -680 | 1.05
8986 | 0 | 0 | 961 | 1.2
8987 | 0 | 0 | 646 | 0.3
8988 | 0 | 0 | 340 | 2.4
8989 | 0 | 0 | 595 | 3.2
8990 | 0 | 0 | -625 | 3.1
8991 | 0 | 0 | -646 | 1.9
8992 | 1386 | 1.386 | 277 | 0.05
8993 | 4340 | 4.34 | -303 | 1.55
8994 | 12239 | 12.239 | 91 | 3.6
8995 | 14436 | 14.436 | -356 | 0.4
8996 | 14626 | 14.626 | -614 | 1.25
8997 | 14657 | 14.657 | 994 | 4.6
8998 | 14515 | 14.515 | 559 | 1.95
8999 | 14622 | 14.622 | -705 | 1.65
9000 | 14377 | 14.377 | 832 | 3.3
9001 | 14467 | 14.467 | -308 | 4.65
9002 | 14454 | 14.454 | -406 | 4.55
9003 | 14585 | 14.585 | 123 | 1.65
9004 | 14691 | 14.691 | -581 | 2.75
9005 | 14390 | 14.39 | 121 | 2.1
9006 | 14034 | 14.034 | -404 | 1.3
9007 | 14362 | 14.362 | 624 | 3
9008 | 14389 | 14.389 | -9 | 3.7
9009 | 14243 | 14.243 | -334 | 3.6
9010 | 14664 | 14.664 | 804 | 1.7
9011 | 14204 | 14.204 | -401 | 4
9012 | 14239 | 14.239 | 560 | 3.1
9013 | 14365 | 14.365 | 36 | 3.7
9014 | 14247 | 14.247 | -528 | 4.65
9015 | 14141 | 14.141 | -361 | 0.55
9016 | 14435 | 14.435 | 202 | 4.5
9017 | 14279 | 14.279 | 747 | 3.3
9018 | 14471 | 14.471 | 85 | 2.65
9019 | 14561 | 14.561 | -750 | 1.85
9020 | 14356 | 14.356 | -766 | 0.5
9021 | 14418 | 14.418 | -638 | 0.55
9022 | 14706 | 14.706 | 98 | 3.3
9023 | 14344 | 14.344 | 196 | 4.4
9024 | 13631 | 13.631 | -605 | 2.95
9025 | 13656 | 13.656 | -238 | 4.85
9026 | 13809 | 13.809 | -619 | 0.8
9027 | 13923 | 13.923 | -443 | 0
9028 | 13627 | 13.627 | 743 | 0
9029 | 13384 | 13.384 | -556 | 1.95
9030 | 14588 | 14.588 | -904 | 2.95
9031 | 14719 | 14.719 | 778 | 0.65
9032 | 14657 | 14.657 | -923 | 3.6
9033 | 14690 | 14.69 | -737 | 2.15
9034 | 14637 | 14.637 | -613 | 1.5
9035 | 14626 | 14.626 | 365 | 2.05
9036 | 14570 | 14.57 | -115 | 4.55
9037 | 14876 | 14.876 | 741 | 1.6
9038 | 14626 | 14.626 | 117 | 3.75
9039 | 14695 | 14.695 | -256 | 1.95
9040 | 14623 | 14.623 | -596 | 2
9041 | 14452 | 14.452 | 804 | 2.4
9042 | 14589 | 14.589 | -82 | 4.25
9043 | 14535 | 14.535 | -139 | 2.5
9044 | 14440 | 14.44 | 510 | 3.8
9045 | 14462 | 14.462 | 796 | 0
9046 | 14413 | 14.413 | -335 | 3.7
9047 | 14358 | 14.358 | -860 | 1.25
9048 | 14480 | 14.48 | -225 | 2.9
9049 | 14184 | 14.184 | -892 | 4.8
9050 | 14324 | 14.324 | -854 | 0.8
9051 | 14247 | 14.247 | 231 | 1.45
9052 | 14197 | 14.197 | -639 | 3.5
9053 | 14183 | 14.183 | 389 | 2.1
9054 | 14088 | 14.088 | 67 | 3.65
9055 | 14278 | 14.278 | -535 | 1.1
9056 | 14089 | 14.089 | 236 | 1.3
9057 | 14203 | 14.203 | -858 | 2.35
9058 | 14222 | 14.222 | -727 | 4.2
9059 | 14197 | 14.197 | -609 | 0.15
9060 | 14382 | 14.382 | -535 | 4.8
9061 | 14252 | 14.252 | -831 | 1.1
9062 | 14229 | 14.229 | 917 | 1.25
9063 | 14258 | 14.258 | 842 | 0.45
9064 | 14392 | 14.392 | 320 | 2.9
9065 | 14406 | 14.406 | -541 | 1.8
9066 | 14447 | 14.447 | -218 | 0.6
9067 | 14312 | 14.312 | 331 | 1.15
9068 | 14513 | 14.513 | -669 | 1.45
9069 | 14513 | 14.513 | 947 | 3.25
9070 | 14548 | 14.548 | -237 | 5
9071 | 14610 | 14.61 | -69 | 0.8
9072 | 14043 | 14.043 | -310 | 0.2
9073 | 13404 | 13.404 | -396 | 1.3
9074 | 14220 | 14.22 | -209 | 3.65
9075 | 14714 | 14.714 | 666 | 2.05
9076 | 14702 | 14.702 | -292 | 3.4
9077 | 14662 | 14.662 | -233 | 4.65
9078 | 14717 | 14.717 | 596 | 0.25
9079 | 14684 | 14.684 | -215 | 1.05
9080 | 14634 | 14.634 | 518 | 0
9081 | 14655 | 14.655 | -525 | 4.6
9082 | 14716 | 14.716 | -720 | 4.5
9083 | 14835 | 14.835 | -252 | 4.35
9084 | 14628 | 14.628 | 794 | 3.95
9085 | 14661 | 14.661 | -923 | 1.95
9086 | 14527 | 14.527 | 624 | 1.75
9087 | 14704 | 14.704 | 566 | 0.25
9088 | 14677 | 14.677 | 139 | 0.1
9089 | 14637 | 14.637 | 561 | 1.5
9090 | 14632 | 14.632 | 932 | 0.5
9091 | 14560 | 14.56 | 456 | 0.35
9092 | 14615 | 14.615 | 699 | 3.2
9093 | 14617 | 14.617 | 403 | 4.7
9094 | 14537 | 14.537 | 958 | 1.2
9095 | 14564 | 14.564 | 600 | 2.1
9096 | 14424 | 14.424 | 711 | 3.5
9097 | 14422 | 14.422 | 969 | 4.3
9098 | 14354 | 14.354 | 520 | 0.15
9099 | 14218 | 14.218 | -615 | 5
9100 | 14339 | 14.339 | 325 | 0.55
9101 | 14211 | 14.211 | -981 | 0.5
9102 | 14220 | 14.22 | -958 | 3.75
9103 | 14287 | 14.287 | 799 | 1.3
9104 | 14283 | 14.283 | -231 | 0.05
9105 | 14212 | 14.212 | -176 | 3.4
9106 | 14265 | 14.265 | -557 | 1
9107 | 14126 | 14.126 | 593 | 4
9108 | 14260 | 14.26 | 884 | 2.6
9109 | 14408 | 14.408 | -460 | 0.55
9110 | 14309 | 14.309 | -699 | 4.95
9111 | 14469 | 14.469 | 352 | 4.65
9112 | 14495 | 14.495 | -225 | 1.8
9113 | 14424 | 14.424 | -552 | 4.4
9114 | 14432 | 14.432 | 86 | 0.5
9115 | 14539 | 14.539 | -287 | 0.2
9116 | 14557 | 14.557 | -225 | 2
9117 | 14630 | 14.63 | 651 | 1.9
9118 | 14640 | 14.64 | -85 | 2.2
9119 | 14581 | 14.581 | 79 | 3.6
9120 | 14434 | 14.434 | 629 | 4.75
9121 | 14042 | 14.042 | 720 | 4.1
9122 | 13671 | 13.671 | 932 | 0.4
9123 | 13895 | 13.895 | 310 | 0.35
9124 | 13910 | 13.91 | 771 | 3.15
9125 | 14000 | 14 | -587 | 2.25
9126 | 13124 | 13.124 | 709 | 4.7
9127 | 14472 | 14.472 | 337 | 4.1
9128 | 14718 | 14.718 | 878 | 2.1
9129 | 14604 | 14.604 | -837 | 0.4
9130 | 14712 | 14.712 | -411 | 3.35
9131 | 14758 | 14.758 | -987 | 4.5
9132 | 14618 | 14.618 | -281 | 4.25
9133 | 14727 | 14.727 | -644 | 4.35
9134 | 14593 | 14.593 | -499 | 3.95
9135 | 14760 | 14.76 | 961 | 0.4
9136 | 14654 | 14.654 | 515 | 1.05
9137 | 14702 | 14.702 | -499 | 4.35
9138 | 14536 | 14.536 | 809 | 1.1
9139 | 14571 | 14.571 | -670 | 3.4
9140 | 14623 | 14.623 | 162 | 0.6
9141 | 14572 | 14.572 | -192 | 1.45
9142 | 14501 | 14.501 | -527 | 3.55
9143 | 14412 | 14.412 | 254 | 0.35
9144 | 14402 | 14.402 | -868 | 2.6
9145 | 14344 | 14.344 | -712 | 4.6
9146 | 14295 | 14.295 | -725 | 3.6
9147 | 14233 | 14.233 | -872 | 2.05
9148 | 14212 | 14.212 | -924 | 4.4
9149 | 14168 | 14.168 | -55 | 2
9150 | 14085 | 14.085 | 249 | 1.25
9151 | 14125 | 14.125 | 177 | 1.65
9152 | 14057 | 14.057 | 30 | 0.95
9153 | 14268 | 14.268 | 908 | 4.3
9154 | 14141 | 14.141 | 528 | 0
9155 | 14330 | 14.33 | 152 | 1.8
9156 | 14310 | 14.31 | -88 | 2
9157 | 14447 | 14.447 | 94 | 4.95
9158 | 14413 | 14.413 | 957 | 1.7
9159 | 14546 | 14.546 | -872 | 0.85
9160 | 14455 | 14.455 | -629 | 2.1
9161 | 14558 | 14.558 | 0 | 0.4
9162 | 14536 | 14.536 | -172 | 1.85
9163 | 14668 | 14.668 | -982 | 3.5
9164 | 14522 | 14.522 | 906 | 2.3
9165 | 14669 | 14.669 | 59 | 3.3
9166 | 14629 | 14.629 | -946 | 2.55
9167 | 14714 | 14.714 | -367 | 2.8
9168 | 14665 | 14.665 | 328 | 3.1
9169 | 13851 | 13.851 | 122 | 4.5
9170 | 13191 | 13.191 | -600 | 4.65
9171 | 14469 | 14.469 | 383 | 2.65
9172 | 14629 | 14.629 | -515 | 2.65
9173 | 14779 | 14.779 | -225 | 0.8
9174 | 14761 | 14.761 | -904 | 2.9
9175 | 14656 | 14.656 | 5 | 0.15
9176 | 14762 | 14.762 | 717 | 4
9177 | 14594 | 14.594 | -211 | 4.25
9178 | 14663 | 14.663 | 199 | 4.75
9179 | 14683 | 14.683 | 220 | 1.35
9180 | 14721 | 14.721 | -758 | 0.25
9181 | 14577 | 14.577 | 104 | 1.95
9182 | 14398 | 14.398 | -302 | 1.25
9183 | 14773 | 14.773 | -935 | 3.65
9184 | 14587 | 14.587 | -265 | 3.9
9185 | 14715 | 14.715 | -670 | 4.15
9186 | 14664 | 14.664 | -405 | 3.9
9187 | 14552 | 14.552 | 384 | 2.4
9188 | 14579 | 14.579 | 443 | 1.25
9189 | 14383 | 14.383 | 94 | 0.05
9190 | 14503 | 14.503 | -142 | 3.55
9191 | 14241 | 14.241 | 204 | 2.8
9192 | 14260 | 14.26 | -536 | 4.8
9193 | 14187 | 14.187 | 179 | 4.45
9194 | 14117 | 14.117 | -620 | 3.35
9195 | 14042 | 14.042 | 795 | 3.15
9196 | 13968 | 13.968 | -565 | 3.75
9197 | 13611 | 13.611 | 888 | 3.15
9198 | 13802 | 13.802 | -614 | 1.85
9199 | 13890 | 13.89 | -983 | 0.15
9200 | 13599 | 13.599 | -357 | 3.2
9201 | 13627 | 13.627 | 736 | 3.8
9202 | 13902 | 13.902 | -867 | 3.2
9203 | 13855 | 13.855 | 161 | 2.95
9204 | 13922 | 13.922 | -705 | 1.5
9205 | 13868 | 13.868 | 57 | 4.5
9206 | 14065 | 14.065 | -529 | 4.1
9207 | 14007 | 14.007 | 783 | 4.95
9208 | 14239 | 14.239 | -749 | 1.6
9209 | 14057 | 14.057 | -692 | 5
9210 | 14390 | 14.39 | 245 | 4.55
9211 | 14314 | 14.314 | 300 | 0.2
9212 | 14418 | 14.418 | 951 | 4.6
9213 | 14422 | 14.422 | 96 | 4.7
9214 | 14315 | 14.315 | 737 | 4.75
9215 | 14685 | 14.685 | 856 | 3.75
9216 | 14615 | 14.615 | 757 | 3.85
9217 | 13875 | 13.875 | 52 | 3.6
9218 | 13684 | 13.684 | 897 | 3.15
9219 | 13732 | 13.732 | 364 | 2.3
9220 | 14121 | 14.121 | 429 | 1.55
9221 | 13848 | 13.848 | 857 | 4.65
9222 | 13584 | 13.584 | -536 | 4.6
9223 | 14452 | 14.452 | -531 | 1.6
9224 | 14629 | 14.629 | 613 | 0.9
9225 | 14743 | 14.743 | -946 | 3.05
9226 | 14579 | 14.579 | -485 | 1.85
9227 | 14605 | 14.605 | 911 | 2.4
9228 | 14548 | 14.548 | -917 | 1.4
9229 | 14784 | 14.784 | -483 | 4.75
9230 | 14627 | 14.627 | 775 | 4.2
9231 | 14602 | 14.602 | -777 | 1
9232 | 14478 | 14.478 | -939 | 0.9
9233 | 14592 | 14.592 | 193 | 0.5
9234 | 14281 | 14.281 | 188 | 1.85
9235 | 14443 | 14.443 | -833 | 3.65
9236 | 14431 | 14.431 | 871 | 1.75
9237 | 14373 | 14.373 | 286 | 4.9
9238 | 14256 | 14.256 | 698 | 3.45
9239 | 14217 | 14.217 | 627 | 0.55
9240 | 14020 | 14.02 | -263 | 4.9
9241 | 13838 | 13.838 | 936 | 4.75
9242 | 13702 | 13.702 | 267 | 2.05
9243 | 13730 | 13.73 | -532 | 4.75
9244 | 13624 | 13.624 | 664 | 2.9
9245 | 13610 | 13.61 | -460 | 2.1
9246 | 13656 | 13.656 | -523 | 2.05
9247 | 13753 | 13.753 | -875 | 2.3
9248 | 13884 | 13.884 | 219 | 4.4
9249 | 13779 | 13.779 | 875 | 1.35
9250 | 13936 | 13.936 | 994 | 4.35
9251 | 13966 | 13.966 | -463 | 4.1
9252 | 13914 | 13.914 | -671 | 4.35
9253 | 13975 | 13.975 | 183 | 1.35
9254 | 14024 | 14.024 | 99 | 1.9
9255 | 14250 | 14.25 | 42 | 0.05
9256 | 14332 | 14.332 | 44 | 1.15
9257 | 14432 | 14.432 | -296 | 0.45
9258 | 14339 | 14.339 | 76 | 1.2
9259 | 14581 | 14.581 | -468 | 3.2
9260 | 14297 | 14.297 | -399 | 0
9261 | 14552 | 14.552 | -140 | 3.3
9262 | 14612 | 14.612 | 986 | 1.25
9263 | 14436 | 14.436 | -195 | 4.9
9264 | 13564 | 13.564 | 554 | 1.3
9265 | 13591 | 13.591 | -450 | 4.15
9266 | 14365 | 14.365 | -881 | 0.3
9267 | 14697 | 14.697 | -539 | 1.7
9268 | 14627 | 14.627 | 850 | 4.5
9269 | 14431 | 14.431 | -185 | 2.9
9270 | 14720 | 14.72 | -665 | 4.45
9271 | 14703 | 14.703 | 869 | 1.9
9272 | 14418 | 14.418 | 155 | 0.25
9273 | 14579 | 14.579 | 852 | 3.55
9274 | 14629 | 14.629 | 168 | 0.4
9275 | 14609 | 14.609 | -32 | 2.25
9276 | 14713 | 14.713 | -765 | 2
9277 | 14645 | 14.645 | -157 | 0.8
9278 | 14438 | 14.438 | -950 | 1.2
9279 | 14733 | 14.733 | -588 | 4.85
9280 | 14591 | 14.591 | -156 | 2.7
9281 | 14567 | 14.567 | -796 | 4.65
9282 | 14609 | 14.609 | -460 | 1.95
9283 | 14448 | 14.448 | 621 | 1.15
9284 | 14571 | 14.571 | -320 | 2.1
9285 | 14409 | 14.409 | -200 | 3.3
9286 | 14462 | 14.462 | 432 | 0.85
9287 | 14570 | 14.57 | -531 | 4.5
9288 | 14426 | 14.426 | 304 | 2.8
9289 | 14397 | 14.397 | -59 | 0.8
9290 | 14566 | 14.566 | -225 | 0.05
9291 | 14350 | 14.35 | 256 | 3.45
9292 | 14434 | 14.434 | -578 | 0.45
9293 | 14510 | 14.51 | 718 | 0.9
9294 | 14351 | 14.351 | -873 | 4.85
9295 | 14345 | 14.345 | -359 | 3.85
9296 | 14381 | 14.381 | 126 | 2.95
9297 | 14305 | 14.305 | 872 | 3.55
9298 | 14441 | 14.441 | -590 | 0.3
9299 | 14486 | 14.486 | -117 | 3.45
9300 | 14481 | 14.481 | -420 | 1.55
9301 | 14465 | 14.465 | -562 | 4.8
9302 | 14368 | 14.368 | 768 | 1.15
9303 | 14521 | 14.521 | -934 | 2.35
9304 | 14554 | 14.554 | 493 | 0.4
9305 | 14610 | 14.61 | 222 | 3.15
9306 | 14517 | 14.517 | -808 | 0.4
9307 | 14464 | 14.464 | 620 | 2.75
9308 | 14675 | 14.675 | 546 | 4.1
9309 | 14615 | 14.615 | -97 | 3.15
9310 | 14771 | 14.771 | -707 | 0.6
9311 | 14539 | 14.539 | 860 | 0.9
9312 | 13868 | 13.868 | 275 | 0.05
9313 | 13851 | 13.851 | 700 | 4.95
9314 | 13893 | 13.893 | -847 | 1.85
9315 | 13984 | 13.984 | 800 | 2.9
9316 | 13930 | 13.93 | 38 | 1.15
9317 | 13194 | 13.194 | -797 | 4.65
9318 | 14212 | 14.212 | 44 | 4.15
9319 | 14734 | 14.734 | 368 | 4.45
9320 | 14600 | 14.6 | -776 | 3.1
9321 | 14670 | 14.67 | 531 | 2.1
9322 | 14576 | 14.576 | -623 | 4.35
9323 | 14550 | 14.55 | -759 | 2.1
9324 | 14751 | 14.751 | -868 | 2.7
9325 | 14660 | 14.66 | 248 | 3.7
9326 | 14632 | 14.632 | 20 | 4.2
9327 | 14466 | 14.466 | -754 | 2.95
9328 | 14638 | 14.638 | 335 | 3.7
9329 | 14532 | 14.532 | -854 | 3.95
9330 | 14670 | 14.67 | 176 | 4.3
9331 | 14542 | 14.542 | 781 | 3.55
9332 | 14682 | 14.682 | 384 | 0.5
9333 | 14490 | 14.49 | 701 | 3.25
9334 | 14403 | 14.403 | -21 | 1.15
9335 | 14619 | 14.619 | 600 | 2.05
9336 | 14486 | 14.486 | 856 | 0.25
9337 | 14440 | 14.44 | 533 | 1.95
9338 | 14423 | 14.423 | -411 | 0.2
9339 | 14263 | 14.263 | -499 | 3.95
9340 | 14410 | 14.41 | 341 | 1.85
9341 | 14335 | 14.335 | -260 | 1.3
9342 | 14245 | 14.245 | 18 | 0.8
9343 | 14257 | 14.257 | -637 | 4.8
9344 | 14376 | 14.376 | -106 | 4.25
9345 | 14266 | 14.266 | 727 | 1.55
9346 | 14324 | 14.324 | 169 | 2.65
9347 | 14335 | 14.335 | -272 | 5
9348 | 14381 | 14.381 | -588 | 0.9
9349 | 14571 | 14.571 | -352 | 1.75
9350 | 14520 | 14.52 | 744 | 2.75
9351 | 14349 | 14.349 | -233 | 2.1
9352 | 14295 | 14.295 | 306 | 2.2
9353 | 14430 | 14.43 | -110 | 3.7
9354 | 14617 | 14.617 | 756 | 1.8
9355 | 14496 | 14.496 | -622 | 3.3
9356 | 14276 | 14.276 | 349 | 2.7
9357 | 14721 | 14.721 | 965 | 0.4
9358 | 14560 | 14.56 | -716 | 0.05
9359 | 14633 | 14.633 | 188 | 0.1
9360 | 14034 | 14.034 | -205 | 2
9361 | 12968 | 12.968 | 583 | 2.95
9362 | 14207 | 14.207 | 556 | 2.9
9363 | 14531 | 14.531 | 372 | 1.1
9364 | 14464 | 14.464 | 442 | 4.4
9365 | 14628 | 14.628 | 473 | 1.1
9366 | 14664 | 14.664 | 643 | 1.25
9367 | 14658 | 14.658 | -681 | 4.75
9368 | 14603 | 14.603 | -529 | 0.8
9369 | 14649 | 14.649 | -725 | 3.2
9370 | 14589 | 14.589 | -101 | 4.9
9371 | 14680 | 14.68 | -985 | 4.1
9372 | 14527 | 14.527 | 629 | 1.55
9373 | 14587 | 14.587 | 957 | 0.15
9374 | 14541 | 14.541 | 900 | 1.15
9375 | 14517 | 14.517 | 500 | 0.15
9376 | 14640 | 14.64 | 45 | 0
9377 | 14438 | 14.438 | -662 | 3.15
9378 | 14608 | 14.608 | -190 | 3.55
9379 | 14340 | 14.34 | 233 | 4.7
9380 | 14609 | 14.609 | 144 | 1.45
9381 | 14349 | 14.349 | 348 | 2
9382 | 14274 | 14.274 | 900 | 1.35
9383 | 14370 | 14.37 | 235 | 0.7
9384 | 14010 | 14.01 | -881 | 0.8
9385 | 14253 | 14.253 | -402 | 1.85
9386 | 13960 | 13.96 | 311 | 1.95
9387 | 14006 | 14.006 | -755 | 2.3
9388 | 13759 | 13.759 | -959 | 2.85
9389 | 14165 | 14.165 | -873 | 0.45
9390 | 13930 | 13.93 | -240 | 0
9391 | 14079 | 14.079 | 553 | 2.75
9392 | 13935 | 13.935 | 34 | 3.85
9393 | 13836 | 13.836 | 488 | 4.8
9394 | 14078 | 14.078 | -290 | 0.7
9395 | 13892 | 13.892 | 242 | 4.55
9396 | 14155 | 14.155 | 432 | 0.2
9397 | 14061 | 14.061 | 343 | 4.85
9398 | 14220 | 14.22 | 198 | 3.4
9399 | 14438 | 14.438 | 762 | 2.5
9400 | 14352 | 14.352 | 796 | 0.05
9401 | 14582 | 14.582 | 689 | 0.35
9402 | 14646 | 14.646 | -395 | 4.75
9403 | 14553 | 14.553 | -559 | 1.15
9404 | 14395 | 14.395 | 516 | 3.15
9405 | 14621 | 14.621 | 502 | 0.2
9406 | 14704 | 14.704 | 852 | 1.65
9407 | 14539 | 14.539 | -278 | 3.35
9408 | 14172 | 14.172 | 709 | 3.8
9409 | 13631 | 13.631 | 709 | 4.05
9410 | 13663 | 13.663 | -969 | 3.25
9411 | 14026 | 14.026 | 374 | 2.6
9412 | 13854 | 13.854 | -225 | 4.3
9413 | 13137 | 13.137 | -617 | 4.15
9414 | 14413 | 14.413 | -739 | 1.9
9415 | 14716 | 14.716 | 118 | 1.1
9416 | 14569 | 14.569 | 874 | 4.05
9417 | 14693 | 14.693 | -925 | 2.35
9418 | 14549 | 14.549 | 154 | 2.15
9419 | 14784 | 14.784 | 63 | 1.55
9420 | 14578 | 14.578 | 787 | 3.2
9421 | 14613 | 14.613 | 433 | 1.75
9422 | 14633 | 14.633 | 259 | 3.65
9423 | 14676 | 14.676 | 336 | 3.2
9424 | 14612 | 14.612 | 517 | 2.6
9425 | 14640 | 14.64 | -830 | 1.5
9426 | 14648 | 14.648 | -702 | 4.45
9427 | 14603 | 14.603 | 917 | 1.85
9428 | 14551 | 14.551 | -140 | 1.6
9429 | 14565 | 14.565 | -652 | 2.25
9430 | 14478 | 14.478 | -8 | 2.5
9431 | 14463 | 14.463 | -276 | 1.3
9432 | 14584 | 14.584 | 946 | 2.55
9433 | 14323 | 14.323 | 597 | 3.05
9434 | 14644 | 14.644 | 53 | 1.05
9435 | 14478 | 14.478 | -346 | 4.5
9436 | 14633 | 14.633 | -922 | 1.4
9437 | 14607 | 14.607 | -298 | 4.85
9438 | 14518 | 14.518 | -756 | 2.25
9439 | 14564 | 14.564 | 790 | 3.85
9440 | 14593 | 14.593 | 906 | 3.6
9441 | 14706 | 14.706 | -934 | 2.55
9442 | 14610 | 14.61 | 149 | 2.7
9443 | 14479 | 14.479 | 480 | 4.55
9444 | 14642 | 14.642 | 379 | 1.05
9445 | 14457 | 14.457 | 779 | 4
9446 | 14763 | 14.763 | 597 | 3.25
9447 | 14654 | 14.654 | -150 | 3.1
9448 | 14524 | 14.524 | -542 | 0.75
9449 | 14666 | 14.666 | -682 | 1.35
9450 | 14643 | 14.643 | 87 | 1.6
9451 | 14591 | 14.591 | 140 | 3
9452 | 14621 | 14.621 | -12 | 0.2
9453 | 14671 | 14.671 | -462 | 0.1
9454 | 14450 | 14.45 | -380 | 2.5
9455 | 14640 | 14.64 | -520 | 2.35
9456 | 14013 | 14.013 | 657 | 2.65
9457 | 13051 | 13.051 | 961 | 1.45
9458 | 14474 | 14.474 | -937 | 0.45
9459 | 14436 | 14.436 | -577 | 4.25
9460 | 14905 | 14.905 | -518 | 3.55
9461 | 14756 | 14.756 | -202 | 0.8
9462 | 14748 | 14.748 | 798 | 2
9463 | 14686 | 14.686 | 890 | 3.25
9464 | 14621 | 14.621 | -60 | 4.05
9465 | 14861 | 14.861 | -353 | 4.35
9466 | 14696 | 14.696 | -455 | 3.8
9467 | 14599 | 14.599 | 408 | 1.05
9468 | 14782 | 14.782 | 704 | 3.95
9469 | 14714 | 14.714 | -30 | 0.05
9470 | 14608 | 14.608 | 438 | 1.35
9471 | 14585 | 14.585 | -866 | 3.75
9472 | 14686 | 14.686 | -974 | 4.4
9473 | 14652 | 14.652 | -996 | 1.2
9474 | 14707 | 14.707 | -676 | 2.15
9475 | 14608 | 14.608 | 924 | 4.5
9476 | 14565 | 14.565 | -569 | 4.95
9477 | 14737 | 14.737 | 23 | 4.7
9478 | 14600 | 14.6 | -359 | 4.7
9479 | 14635 | 14.635 | 167 | 1.2
9480 | 14668 | 14.668 | 141 | 2.95
9481 | 14475 | 14.475 | -927 | 2.9
9482 | 14697 | 14.697 | 663 | 3.2
9483 | 14598 | 14.598 | -923 | 2.85
9484 | 14566 | 14.566 | 145 | 0
9485 | 14594 | 14.594 | -719 | 0.65
9486 | 14487 | 14.487 | 390 | 0.05
9487 | 14583 | 14.583 | 95 | 2
9488 | 14460 | 14.46 | -899 | 2.35
9489 | 14731 | 14.731 | 276 | 4.9
9490 | 14491 | 14.491 | 956 | 4.9
9491 | 14552 | 14.552 | 182 | 2.65
9492 | 14526 | 14.526 | -574 | 4.15
9493 | 14730 | 14.73 | -924 | 3.7
9494 | 14699 | 14.699 | 120 | 4.65
9495 | 14543 | 14.543 | 607 | 3.75
9496 | 14681 | 14.681 | -950 | 3.75
9497 | 14619 | 14.619 | 703 | 4.55
9498 | 14781 | 14.781 | -76 | 1
9499 | 14735 | 14.735 | 402 | 2.15
9500 | 14472 | 14.472 | 430 | 4.2
9501 | 14821 | 14.821 | -759 | 4.65
9502 | 14725 | 14.725 | 492 | 2.9
9503 | 14623 | 14.623 | 192 | 3.8
9504 | 14413 | 14.413 | -482 | 3.2
9505 | 13690 | 13.69 | 293 | 3.7
9506 | 14029 | 14.029 | 378 | 2.9
9507 | 14011 | 14.011 | 707 | 2.45
9508 | 14089 | 14.089 | 501 | 4.65
9509 | 13432 | 13.432 | 686 | 1.55
9510 | 14445 | 14.445 | 718 | 0.6
9511 | 14887 | 14.887 | 31 | 2.25
9512 | 14786 | 14.786 | -918 | 2.95
9513 | 14733 | 14.733 | -793 | 1.95
9514 | 14591 | 14.591 | -671 | 4.5
9515 | 14758 | 14.758 | 203 | 0.9
9516 | 14782 | 14.782 | 291 | 2.15
9517 | 14626 | 14.626 | -102 | 3.2
9518 | 14771 | 14.771 | 580 | 2.05
9519 | 14542 | 14.542 | -538 | 1.35
9520 | 14665 | 14.665 | -631 | 0
9521 | 14727 | 14.727 | 94 | 1.65
9522 | 14642 | 14.642 | -465 | 3.9
9523 | 14515 | 14.515 | 90 | 4.75
9524 | 14639 | 14.639 | 367 | 4.65
9525 | 14655 | 14.655 | 233 | 1.9
9526 | 14533 | 14.533 | -272 | 1.75
9527 | 14666 | 14.666 | -684 | 4.4
9528 | 14593 | 14.593 | -220 | 2.5
9529 | 14481 | 14.481 | -969 | 4.25
9530 | 14703 | 14.703 | -218 | 0.4
9531 | 14536 | 14.536 | 570 | 1.7
9532 | 14499 | 14.499 | -860 | 3.75
9533 | 14442 | 14.442 | 483 | 2.65
9534 | 14562 | 14.562 | 42 | 2.75
9535 | 14520 | 14.52 | 54 | 1.1
9536 | 14549 | 14.549 | 12 | 2.15
9537 | 14391 | 14.391 | 332 | 2.2
9538 | 14597 | 14.597 | 856 | 4.75
9539 | 14577 | 14.577 | -275 | 3.2
9540 | 14514 | 14.514 | 115 | 3.8
9541 | 14431 | 14.431 | 847 | 2.3
9542 | 14683 | 14.683 | -485 | 4.45
9543 | 14605 | 14.605 | -328 | 3.4
9544 | 14597 | 14.597 | 817 | 0.75
9545 | 14593 | 14.593 | 152 | 0.7
9546 | 14718 | 14.718 | -251 | 4.1
9547 | 14564 | 14.564 | 444 | 1.25
9548 | 14710 | 14.71 | -296 | 2.5
9549 | 14700 | 14.7 | -6 | 2.3
9550 | 14717 | 14.717 | -992 | 4.35
9551 | 14641 | 14.641 | 7 | 0.45
9552 | 13924 | 13.924 | -416 | 0.35
9553 | 13197 | 13.197 | -768 | 1.25
9554 | 14404 | 14.404 | 0 | 0.45
9555 | 14708 | 14.708 | 879 | 3.35
9556 | 14776 | 14.776 | -958 | 4.6
9557 | 14766 | 14.766 | 445 | 1.45
9558 | 14747 | 14.747 | 980 | 3.15
9559 | 14659 | 14.659 | -389 | 1.75
9560 | 14875 | 14.875 | 374 | 1.05
9561 | 14643 | 14.643 | -366 | 3.4
9562 | 14836 | 14.836 | 604 | 0.8
9563 | 14713 | 14.713 | -516 | 3.85
9564 | 14685 | 14.685 | -836 | 4.65
9565 | 14695 | 14.695 | -933 | 1.15
9566 | 14566 | 14.566 | -748 | 0.95
9567 | 14713 | 14.713 | -210 | 2.15
9568 | 14611 | 14.611 | 389 | 2.9
9569 | 14632 | 14.632 | -399 | 4.7
9570 | 14649 | 14.649 | 126 | 2.85
9571 | 14502 | 14.502 | 848 | 0.8
9572 | 14756 | 14.756 | -51 | 1.8
9573 | 14491 | 14.491 | -265 | 4.7
9574 | 14477 | 14.477 | -748 | 2.15
9575 | 14497 | 14.497 | -272 | 3.9
9576 | 14533 | 14.533 | 619 | 3.1
9577 | 14465 | 14.465 | -71 | 0.7
9578 | 14418 | 14.418 | 571 | 2.5
9579 | 14679 | 14.679 | 283 | 4.4
9580 | 14241 | 14.241 | -160 | 1.5
9581 | 14439 | 14.439 | 972 | 2.85
9582 | 14383 | 14.383 | 986 | 0.85
9583 | 14429 | 14.429 | -604 | 4.4
9584 | 14560 | 14.56 | -935 | 0.1
9585 | 14432 | 14.432 | -230 | 2.35
9586 | 14608 | 14.608 | -863 | 1.2
9587 | 14220 | 14.22 | 723 | 0.4
9588 | 14554 | 14.554 | 717 | 1.4
9589 | 14397 | 14.397 | 377 | 2.8
9590 | 14441 | 14.441 | 292 | 4.15
9591 | 14509 | 14.509 | -171 | 3.15
9592 | 14486 | 14.486 | 672 | 4.5
9593 | 14671 | 14.671 | 547 | 2.35
9594 | 14667 | 14.667 | 519 | 3.25
9595 | 14682 | 14.682 | 130 | 0.1
9596 | 14628 | 14.628 | -783 | 1.95
9597 | 14562 | 14.562 | -993 | 3.9
9598 | 14533 | 14.533 | 595 | 2.75
9599 | 14645 | 14.645 | -42 | 4.1
9600 | 13661 | 13.661 | 140 | 4.8
9601 | 13818 | 13.818 | 529 | 4.6
9602 | 13757 | 13.757 | -845 | 0.6
9603 | 14017 | 14.017 | 659 | 3.75
9604 | 13800 | 13.8 | 784 | 3.1
9605 | 13487 | 13.487 | -645 | 4.55
9606 | 14449 | 14.449 | 528 | 0.9
9607 | 14740 | 14.74 | 777 | 3.1
9608 | 14621 | 14.621 | 957 | 2.3
9609 | 14733 | 14.733 | 41 | 0.2
9610 | 14724 | 14.724 | 126 | 1.65
9611 | 14711 | 14.711 | -431 | 1.9
9612 | 14655 | 14.655 | -327 | 3.4
9613 | 14630 | 14.63 | 586 | 4.85
9614 | 14691 | 14.691 | -34 | 3.6
9615 | 14623 | 14.623 | 551 | 5
9616 | 14437 | 14.437 | -823 | 0.85
9617 | 14726 | 14.726 | -922 | 0.1
9618 | 14563 | 14.563 | -129 | 3.8
9619 | 14587 | 14.587 | 590 | 4.75
9620 | 14438 | 14.438 | -606 | 1.7
9621 | 14470 | 14.47 | -651 | 2.85
9622 | 14465 | 14.465 | -338 | 2.15
9623 | 14468 | 14.468 | 395 | 4.55
9624 | 14304 | 14.304 | -148 | 4.85
9625 | 14215 | 14.215 | -688 | 2.45
9626 | 14332 | 14.332 | 239 | 3.1
9627 | 14220 | 14.22 | 377 | 4.8
9628 | 14194 | 14.194 | 513 | 0.5
9629 | 14103 | 14.103 | 871 | 1.7
9630 | 14123 | 14.123 | 512 | 3.2
9631 | 14160 | 14.16 | 150 | 3.55
9632 | 14244 | 14.244 | -795 | 0.15
9633 | 14151 | 14.151 | 689 | 4.9
9634 | 14020 | 14.02 | -688 | 2.65
9635 | 13981 | 13.981 | -176 | 2.5
9636 | 14247 | 14.247 | -791 | 4.55
9637 | 14149 | 14.149 | -99 | 4
9638 | 14066 | 14.066 | 761 | 2.85
9639 | 14329 | 14.329 | 126 | 1.95
9640 | 14319 | 14.319 | -969 | 3.4
9641 | 14268 | 14.268 | -283 | 4.15
9642 | 14388 | 14.388 | 197 | 3.4
9643 | 14301 | 14.301 | 507 | 0.7
9644 | 14256 | 14.256 | -37 | 4.1
9645 | 14454 | 14.454 | -1 | 3.15
9646 | 14431 | 14.431 | -148 | 3.3
9647 | 14236 | 14.236 | 211 | 4.45
9648 | 13510 | 13.51 | 68 | 0.8
9649 | 13109 | 13.109 | 393 | 4.3
9650 | 14323 | 14.323 | -966 | 4.8
9651 | 14522 | 14.522 | 551 | 4.45
9652 | 14461 | 14.461 | 535 | 4.15
9653 | 14438 | 14.438 | 385 | 0.65
9654 | 14645 | 14.645 | 439 | 4
9655 | 14314 | 14.314 | 743 | 3.65
9656 | 14525 | 14.525 | -589 | 0.9
9657 | 14421 | 14.421 | 780 | 4.15
9658 | 14423 | 14.423 | 91 | 2.95
9659 | 14423 | 14.423 | -768 | 2.6
9660 | 14512 | 14.512 | -879 | 2.6
9661 | 14533 | 14.533 | 492 | 4.95
9662 | 14606 | 14.606 | 705 | 0.15
9663 | 14563 | 14.563 | 27 | 4.05
9664 | 14464 | 14.464 | -957 | 3
9665 | 14593 | 14.593 | 868 | 1.95
9666 | 14529 | 14.529 | -558 | 5
9667 | 14552 | 14.552 | 142 | 1.2
9668 | 14522 | 14.522 | -243 | 2.95
9669 | 14535 | 14.535 | -678 | 1.5
9670 | 14422 | 14.422 | 613 | 3.2
9671 | 14456 | 14.456 | 444 | 0.9
9672 | 14521 | 14.521 | -674 | 1.8
9673 | 14462 | 14.462 | -922 | 4.6
9674 | 14441 | 14.441 | -257 | 0.75
9675 | 14495 | 14.495 | 476 | 2.55
9676 | 14499 | 14.499 | -667 | 0.2
9677 | 14450 | 14.45 | 988 | 4.8
9678 | 14378 | 14.378 | -379 | 1.9
9679 | 14459 | 14.459 | -847 | 3.45
9680 | 14483 | 14.483 | -728 | 3.1
9681 | 14532 | 14.532 | 171 | 0.5
9682 | 14452 | 14.452 | 945 | 4.3
9683 | 14376 | 14.376 | 707 | 0.2
9684 | 14506 | 14.506 | -273 | 0.2
9685 | 14664 | 14.664 | -113 | 3.75
9686 | 14599 | 14.599 | 724 | 1.95
9687 | 14425 | 14.425 | 643 | 2.95
9688 | 14615 | 14.615 | 594 | 4.35
9689 | 14531 | 14.531 | 582 | 1.8
9690 | 14546 | 14.546 | -7 | 5
9691 | 14597 | 14.597 | -189 | 1.1
9692 | 14595 | 14.595 | 125 | 0.15
9693 | 14690 | 14.69 | -785 | 2.8
9694 | 14439 | 14.439 | -151 | 4.75
9695 | 14531 | 14.531 | -646 | 2.05
9696 | 13673 | 13.673 | -769 | 0.85
9697 | 13653 | 13.653 | -860 | 3.4
9698 | 13901 | 13.901 | -340 | 3.6
9699 | 13861 | 13.861 | -995 | 3.6
9700 | 13353 | 13.353 | 733 | 0.35
9701 | 13761 | 13.761 | 11 | 4.65
9702 | 14604 | 14.604 | 410 | 0.9
9703 | 14541 | 14.541 | -4 | 0.65
9704 | 14627 | 14.627 | -629 | 1.1
9705 | 14674 | 14.674 | 676 | 4.85
9706 | 14581 | 14.581 | -697 | 3
9707 | 14689 | 14.689 | -669 | 1.95
9708 | 14652 | 14.652 | 694 | 1.25
9709 | 14558 | 14.558 | -25 | 0.6
9710 | 14750 | 14.75 | 230 | 4.2
9711 | 14637 | 14.637 | 979 | 3.55
9712 | 14424 | 14.424 | -660 | 2.7
9713 | 14398 | 14.398 | 512 | 4.5
9714 | 14524 | 14.524 | 555 | 0.65
9715 | 14480 | 14.48 | 200 | 2.3
9716 | 14392 | 14.392 | 246 | 0.55
9717 | 14363 | 14.363 | -828 | 3.75
9718 | 14426 | 14.426 | -129 | 2.2
9719 | 14268 | 14.268 | -379 | 1.4
9720 | 14362 | 14.362 | -293 | 4.4
9721 | 14106 | 14.106 | 409 | 1.1
9722 | 14269 | 14.269 | 381 | 1.45
9723 | 14177 | 14.177 | -831 | 2
9724 | 14147 | 14.147 | 388 | 0.55
9725 | 14122 | 14.122 | 929 | 2.75
9726 | 14088 | 14.088 | 39 | 2.8
9727 | 14194 | 14.194 | -446 | 3.05
9728 | 14091 | 14.091 | -899 | 0.95
9729 | 14323 | 14.323 | 742 | 1.25
9730 | 14377 | 14.377 | -202 | 1
9731 | 14469 | 14.469 | -604 | 0.9
9732 | 14270 | 14.27 | -845 | 1.8
9733 | 14519 | 14.519 | 348 | 1.7
9734 | 14504 | 14.504 | 979 | 1.9
9735 | 14443 | 14.443 | -459 | 4.2
9736 | 14427 | 14.427 | 456 | 1.6
9737 | 14418 | 14.418 | -243 | 0.25
9738 | 14430 | 14.43 | -631 | 0
9739 | 14422 | 14.422 | 866 | 1.55
9740 | 14411 | 14.411 | -81 | 0.9
9741 | 14338 | 14.338 | 939 | 4.9
9742 | 14401 | 14.401 | 823 | 2.15
9743 | 14380 | 14.38 | -242 | 0
9744 | 13984 | 13.984 | -425 | 3.3
9745 | 13335 | 13.335 | 685 | 1.45
9746 | 13624 | 13.624 | -943 | 2.1
9747 | 14446 | 14.446 | 339 | 2.85
9748 | 14379 | 14.379 | 706 | 2.95
9749 | 14319 | 14.319 | 796 | 0.55
9750 | 14575 | 14.575 | -194 | 4.75
9751 | 14380 | 14.38 | -88 | 2.35
9752 | 14519 | 14.519 | 349 | 4.3
9753 | 14334 | 14.334 | 330 | 4.1
9754 | 14452 | 14.452 | 996 | 4.2
9755 | 14359 | 14.359 | -637 | 0.65
9756 | 14501 | 14.501 | -147 | 1.45
9757 | 14374 | 14.374 | -193 | 2.9
9758 | 14510 | 14.51 | 130 | 3.8
9759 | 14368 | 14.368 | 840 | 2.85
9760 | 14462 | 14.462 | 590 | 3.4
9761 | 14325 | 14.325 | -736 | 1.95
9762 | 14204 | 14.204 | 3 | 4.6
9763 | 14165 | 14.165 | 740 | 3
9764 | 14309 | 14.309 | -473 | 2.25
9765 | 14242 | 14.242 | 771 | 4.15
9766 | 14199 | 14.199 | 862 | 3.35
9767 | 14274 | 14.274 | 784 | 3.8
9768 | 14279 | 14.279 | -952 | 4.1
9769 | 14268 | 14.268 | 303 | 4.3
9770 | 14152 | 14.152 | 254 | 2.5
9771 | 14162 | 14.162 | -495 | 1.85
9772 | 14072 | 14.072 | 178 | 2.7
9773 | 14135 | 14.135 | 847 | 2.65
9774 | 14181 | 14.181 | 435 | 2.95
9775 | 14028 | 14.028 | 211 | 4.6
9776 | 13979 | 13.979 | -903 | 1.4
9777 | 14100 | 14.1 | 945 | 4.55
9778 | 14052 | 14.052 | 650 | 2.35
9779 | 14115 | 14.115 | 559 | 3.85
9780 | 14210 | 14.21 | 922 | 3.95
9781 | 14153 | 14.153 | -89 | 1.45
9782 | 14321 | 14.321 | 217 | 1.25
9783 | 14293 | 14.293 | 726 | 0.7
9784 | 14224 | 14.224 | 523 | 3.8
9785 | 14350 | 14.35 | 678 | 3.55
9786 | 14339 | 14.339 | 852 | 4.25
9787 | 14448 | 14.448 | 263 | 3.85
9788 | 14499 | 14.499 | -477 | 2.1
9789 | 14363 | 14.363 | -854 | 2.5
9790 | 14531 | 14.531 | 772 | 1.15
9791 | 13544 | 13.544 | 550 | 1.7
9792 | 13600 | 13.6 | 192 | 1.8
9793 | 13691 | 13.691 | 951 | 4.5
9794 | 13734 | 13.734 | 260 | 2.85
9795 | 13609 | 13.609 | 847 | 1.45
9796 | 13374 | 13.374 | -628 | 2.9
9797 | 14153 | 14.153 | 14 | 3.6
9798 | 9605 | 9.605 | 322 | 2.2
9799 | 2687 | 2.687 | 286 | 3.8
9800 | 2201 | 2.201 | -215 | 3.15
9801 | 4260 | 4.26 | -522 | 1.45
9802 | 4919 | 4.919 | 221 | 1.45
9803 | 3040 | 3.04 | -965 | 2.5
9804 | 0 | 0 | -373 | 1.1
9805 | 0 | 0 | -886 | 3.05
9806 | 0 | 0 | 891 | 0.5
9807 | 0 | 0 | -631 | 0
9808 | 0 | 0 | -284 | 1.7
9809 | 0 | 0 | 386 | 0.7
9810 | 0 | 0 | 990 | 3.25
9811 | 0 | 0 | -954 | 1.4
9812 | 0 | 0 | 4 | 1
9813 | 0 | 0 | -128 | 0.1
9814 | 0 | 0 | -802 | 1.5
9815 | 0 | 0 | 376 | 4.4
9816 | 0 | 0 | 529 | 3.75
9817 | 0 | 0 | 288 | 4.8
9818 | 0 | 0 | 833 | 0.9
9819 | 0 | 0 | -4 | 4.65
9820 | 0 | 0 | 565 | 4.4
9821 | 795 | 0.795 | -339 | 4.25
9822 | 9952 | 9.952 | -432 | 2
9823 | 12658 | 12.658 | 741 | 3.6
9824 | 13331 | 13.331 | -220 | 0.85
9825 | 13960 | 13.96 | 505 | 1.1
9826 | 14331 | 14.331 | 270 | 2.55
9827 | 14461 | 14.461 | -290 | 4.15
9828 | 14428 | 14.428 | -282 | 3.4
9829 | 14431 | 14.431 | -903 | 4.5
9830 | 14521 | 14.521 | 852 | 0.7
9831 | 14551 | 14.551 | 871 | 2.85
9832 | 14422 | 14.422 | 164 | 2.25
9833 | 14602 | 14.602 | -860 | 2.85
9834 | 14717 | 14.717 | 309 | 3.6
9835 | 14760 | 14.76 | 33 | 1
9836 | 14764 | 14.764 | -898 | 2.45
9837 | 14744 | 14.744 | 51 | 1.4
9838 | 14896 | 14.896 | -550 | 0
9839 | 14787 | 14.787 | 840 | 2.65
9840 | 14141 | 14.141 | -900 | 0.55
9841 | 14053 | 14.053 | 972 | 1.75
9842 | 14887 | 14.887 | -915 | 1.75
9843 | 14758 | 14.758 | 917 | 4.65
9844 | 15031 | 15.031 | -494 | 1.75
9845 | 14905 | 14.905 | -658 | 3.35
9846 | 14977 | 14.977 | -138 | 3.6
9847 | 15108 | 15.108 | -60 | 4.45
9848 | 14936 | 14.936 | -458 | 3
9849 | 15017 | 15.017 | -794 | 1.5
9850 | 14898 | 14.898 | 449 | 0.8
9851 | 14905 | 14.905 | 556 | 2.2
9852 | 14945 | 14.945 | -497 | 3.1
9853 | 14783 | 14.783 | 683 | 3.9
9854 | 14783 | 14.783 | 637 | 0.45
9855 | 14295 | 14.295 | 952 | 0.05
9856 | 14510 | 14.51 | 942 | 4.75
9857 | 14375 | 14.375 | -19 | 3.3
9858 | 14436 | 14.436 | 441 | 3.35
9859 | 14370 | 14.37 | -669 | 0.95
9860 | 14286 | 14.286 | 360 | 1.65
9861 | 14417 | 14.417 | -922 | 0
9862 | 14199 | 14.199 | -57 | 1.8
9863 | 14129 | 14.129 | -758 | 1
9864 | 14072 | 14.072 | 870 | 4.35
9865 | 14377 | 14.377 | 239 | 1.95
9866 | 14079 | 14.079 | 68 | 1.5
9867 | 14350 | 14.35 | -849 | 1.25
9868 | 14062 | 14.062 | 784 | 3.8
9869 | 14085 | 14.085 | 382 | 4.95
9870 | 14163 | 14.163 | -275 | 4.7
9871 | 13978 | 13.978 | 209 | 0.95
9872 | 14150 | 14.15 | 73 | 0.2
9873 | 14308 | 14.308 | 536 | 2.2
9874 | 14297 | 14.297 | 722 | 1.3
9875 | 14448 | 14.448 | 453 | 3.75
9876 | 14297 | 14.297 | 425 | 0.3
9877 | 14255 | 14.255 | -646 | 3.7
9878 | 14278 | 14.278 | -232 | 1.95
9879 | 14341 | 14.341 | -690 | 0
9880 | 14517 | 14.517 | 359 | 1.1
9881 | 14492 | 14.492 | -974 | 4.05
9882 | 14499 | 14.499 | -77 | 4.9
9883 | 14525 | 14.525 | -112 | 0.65
9884 | 14518 | 14.518 | 869 | 0.15
9885 | 14628 | 14.628 | 0 | 3.45
9886 | 14575 | 14.575 | -225 | 3.65
9887 | 14637 | 14.637 | 174 | 1
9888 | 13847 | 13.847 | 681 | 3.65
9889 | 13716 | 13.716 | 455 | 0.15
9890 | 13906 | 13.906 | -321 | 3.1
9891 | 13943 | 13.943 | 982 | 0.2
9892 | 13722 | 13.722 | 296 | 2.3
9893 | 13525 | 13.525 | 215 | 3.45
9894 | 14791 | 14.791 | -436 | 3.3
9895 | 14525 | 14.525 | -88 | 5
9896 | 14590 | 14.59 | 459 | 3.2
9897 | 14535 | 14.535 | -375 | 2.45
9898 | 14654 | 14.654 | -234 | 2.2
9899 | 14535 | 14.535 | 491 | 3.8
9900 | 14636 | 14.636 | -814 | 4.65
9901 | 14491 | 14.491 | 720 | 3.3
9902 | 14564 | 14.564 | -136 | 1.5
9903 | 14467 | 14.467 | 584 | 1.65
9904 | 14521 | 14.521 | 499 | 1.45
9905 | 14345 | 14.345 | 959 | 4.25
9906 | 14355 | 14.355 | 46 | 0.85
9907 | 14406 | 14.406 | -956 | 0
9908 | 14318 | 14.318 | 116 | 1.05
9909 | 14421 | 14.421 | -488 | 3.35
9910 | 14340 | 14.34 | -52 | 4.55
9911 | 14288 | 14.288 | 299 | 2.95
9912 | 14264 | 14.264 | 918 | 4.1
9913 | 14412 | 14.412 | 987 | 2
9914 | 14264 | 14.264 | -716 | 1.75
9915 | 14146 | 14.146 | -919 | 4
9916 | 14422 | 14.422 | -712 | 4.55
9917 | 14158 | 14.158 | -710 | 2.95
9918 | 14306 | 14.306 | 178 | 2.55
9919 | 14175 | 14.175 | -505 | 3.5
9920 | 14279 | 14.279 | -328 | 4.55
9921 | 14122 | 14.122 | -473 | 1.05
9922 | 14334 | 14.334 | -568 | 3.65
9923 | 14212 | 14.212 | 2 | 0.55
9924 | 14325 | 14.325 | 600 | 0.3
9925 | 14269 | 14.269 | 325 | 2.05
9926 | 14451 | 14.451 | 108 | 0.1
9927 | 14439 | 14.439 | 112 | 3.05
9928 | 14556 | 14.556 | 733 | 4.25
9929 | 14523 | 14.523 | 227 | 4.3
9930 | 14548 | 14.548 | 873 | 0.65
9931 | 14395 | 14.395 | -664 | 4.95
9932 | 14671 | 14.671 | -732 | 0.85
9933 | 14461 | 14.461 | 995 | 0
9934 | 14454 | 14.454 | 31 | 3.5
9935 | 14672 | 14.672 | -59 | 2.2
9936 | 13886 | 13.886 | -799 | 1.7
9937 | 12915 | 12.915 | 281 | 2.7
9938 | 14453 | 14.453 | 294 | 0.05
9939 | 14401 | 14.401 | -775 | 1.75
9940 | 14755 | 14.755 | 692 | 2.45
9941 | 14758 | 14.758 | -994 | 1.95
9942 | 14643 | 14.643 | -708 | 0.4
9943 | 14519 | 14.519 | -306 | 0.9
9944 | 14654 | 14.654 | -629 | 4.45
9945 | 14544 | 14.544 | 428 | 0.85
9946 | 14749 | 14.749 | 993 | 0.5
9947 | 14585 | 14.585 | 93 | 0.05
9948 | 14684 | 14.684 | 571 | 3.9
9949 | 14678 | 14.678 | -73 | 1.3
9950 | 14573 | 14.573 | 299 | 1.7
9951 | 14571 | 14.571 | -695 | 1.25
9952 | 14574 | 14.574 | -190 | 2.35
9953 | 14537 | 14.537 | 621 | 1.65
9954 | 14357 | 14.357 | -247 | 2.55
9955 | 14465 | 14.465 | -837 | 4.75
9956 | 7812 | 7.812 | -740 | 3.8
9957 | 0 | 0 | -5 | 2.45
9958 | 0 | 0 | -374 | 3.35
9959 | 0 | 0 | -63 | 5
9960 | 0 | 0 | 547 | 2.2
9961 | 0 | 0 | 434 | 2.05
9962 | 0 | 0 | -652 | 0.85
9963 | 0 | 0 | 919 | 0
9964 | 307 | 0.307 | -117 | 4.35
9965 | 4944 | 4.944 | -465 | 3.25
9966 | 10600 | 10.6 | -904 | 5
9967 | 12832 | 12.832 | -718 | 3
9968 | 14168 | 14.168 | -510 | 0.15
9969 | 14238 | 14.238 | -609 | 0.05
9970 | 14280 | 14.28 | 774 | 2.3
9971 | 14190 | 14.19 | -142 | 4.05
9972 | 14260 | 14.26 | 715 | 3.8
9973 | 14317 | 14.317 | 146 | 0.25
9974 | 14305 | 14.305 | 702 | 1.9
9975 | 14319 | 14.319 | -652 | 0.45
9976 | 14539 | 14.539 | -422 | 3.7
9977 | 14428 | 14.428 | -130 | 4.65
9978 | 14515 | 14.515 | 627 | 0.1
9979 | 14494 | 14.494 | 504 | 1.25
9980 | 14552 | 14.552 | 241 | 3.2
9981 | 14462 | 14.462 | 65 | 4.55
9982 | 14408 | 14.408 | 804 | 0.85
9983 | 13856 | 13.856 | -476 | 0.45
9984 | 13350 | 13.35 | 535 | 2.35
9985 | 13228 | 13.228 | -363 | 2.4
9986 | 13727 | 13.727 | -257 | 2.9
9987 | 13523 | 13.523 | 522 | 1.45
9988 | 13088 | 13.088 | 191 | 1.6
9989 | 13874 | 13.874 | 483 | 3.8
9990 | 14620 | 14.62 | 169 | 4
9991 | 14739 | 14.739 | -672 | 3.55
9992 | 14432 | 14.432 | -432 | 4.05
9993 | 14542 | 14.542 | 283 | 3.3
9994 | 14767 | 14.767 | -656 | 3.5
9995 | 14516 | 14.516 | -515 | 0
9996 | 14562 | 14.562 | 0 | 2.95
9997 | 14552 | 14.552 | -873 | 3.2
9998 | 14550 | 14.55 | 671 | 0.85
9999 | 14414 | 14.414 | 337 | 2.95
10000 | 14445 | 14.445 | -336 | 4
10001 | 14756 | 14.756 | -435 | 4.95
10002 | 14470 | 14.47 | -398 | 1.5
10003 | 14672 | 14.672 | 771 | 4.15
10004 | 14561 | 14.561 | 0 | 4.25
10005 | 14426 | 14.426 | -178 | 2.3
10006 | 14606 | 14.606 | 911 | 0.25
10007 | 14613 | 14.613 | 514 | 0.5
10008 | 14433 | 14.433 | 869 | 1.15
10009 | 14380 | 14.38 | -417 | 1.55
10010 | 14446 | 14.446 | -526 | 4.05
10011 | 14616 | 14.616 | -47 | 2.75
10012 | 14589 | 14.589 | -42 | 3.15
10013 | 14468 | 14.468 | -146 | 1
10014 | 14552 | 14.552 | 899 | 4.85
10015 | 14485 | 14.485 | -64 | 2.05
10016 | 14559 | 14.559 | 404 | 2.3
10017 | 14441 | 14.441 | -343 | 1.5
10018 | 14586 | 14.586 | 423 | 4.55
10019 | 14560 | 14.56 | -20 | 1
10020 | 14552 | 14.552 | -999 | 0.35
10021 | 14542 | 14.542 | -317 | 3.45
10022 | 14502 | 14.502 | 668 | 4.45
10023 | 14615 | 14.615 | -291 | 0.8
10024 | 14521 | 14.521 | 521 | 5
10025 | 14617 | 14.617 | 456 | 0.9
10026 | 14600 | 14.6 | -397 | 3.25
10027 | 14610 | 14.61 | -705 | 4.95
10028 | 14525 | 14.525 | -459 | 4.1
10029 | 14604 | 14.604 | -481 | 4.05
10030 | 14635 | 14.635 | -469 | 0.05
10031 | 14496 | 14.496 | -946 | 4.45
10032 | 13582 | 13.582 | -826 | 0.15
10033 | 12868 | 12.868 | -587 | 2.25
10034 | 14075 | 14.075 | 636 | 3.8
10035 | 14401 | 14.401 | -102 | 1.45
10036 | 14230 | 14.23 | 398 | 2.7
10037 | 14224 | 14.224 | 784 | 3.05
10038 | 14362 | 14.362 | -313 | 3.55
10039 | 14180 | 14.18 | -229 | 3.4
10040 | 14382 | 14.382 | 582 | 4.8
10041 | 14245 | 14.245 | 962 | 4.65
10042 | 14553 | 14.553 | -845 | 2.1
10043 | 14534 | 14.534 | 76 | 3.8
10044 | 14686 | 14.686 | -181 | 3.55
10045 | 14482 | 14.482 | 495 | 3.25
10046 | 14508 | 14.508 | -827 | 4.3
10047 | 14589 | 14.589 | 480 | 2.9
10048 | 14524 | 14.524 | 876 | 1.6
10049 | 14453 | 14.453 | 103 | 2.55
10050 | 14589 | 14.589 | 126 | 0.2
10051 | 14423 | 14.423 | -690 | 4.85
10052 | 14457 | 14.457 | 551 | 0.55
10053 | 14504 | 14.504 | 809 | 0.15
10054 | 14571 | 14.571 | 587 | 4.75
10055 | 14442 | 14.442 | 662 | 2.55
10056 | 14519 | 14.519 | 945 | 2.7
10057 | 14338 | 14.338 | 752 | 3.55
10058 | 14391 | 14.391 | -587 | 2.5
10059 | 14507 | 14.507 | -418 | 4.1
10060 | 14406 | 14.406 | 833 | 4.7
10061 | 14328 | 14.328 | -761 | 3.7
10062 | 14418 | 14.418 | -34 | 1.8
10063 | 14394 | 14.394 | -925 | 3.8
10064 | 14338 | 14.338 | -349 | 1.05
10065 | 14405 | 14.405 | -591 | 4.8
10066 | 14424 | 14.424 | 263 | 4.35
10067 | 14302 | 14.302 | 656 | 3.4
10068 | 14295 | 14.295 | -270 | 0.35
10069 | 14167 | 14.167 | 763 | 4.45
10070 | 14519 | 14.519 | -10 | 0.35
10071 | 14373 | 14.373 | 109 | 0.5
10072 | 14424 | 14.424 | 83 | 2.45
10073 | 14432 | 14.432 | -136 | 4.2
10074 | 14452 | 14.452 | -788 | 1.4
10075 | 14364 | 14.364 | 230 | 1.7
10076 | 14542 | 14.542 | 590 | 2.6
10077 | 14477 | 14.477 | -71 | 0.6
10078 | 14585 | 14.585 | 465 | 4.05
10079 | 14380 | 14.38 | 618 | 2.8
10080 | 13996 | 13.996 | 183 | 2.5
10081 | 13593 | 13.593 | -464 | 2.35
10082 | 13396 | 13.396 | -947 | 1.2
10083 | 13537 | 13.537 | 364 | 2.4
10084 | 13292 | 13.292 | 867 | 1.8
10085 | 13208 | 13.208 | -95 | 0.85
10086 | 14240 | 14.24 | -181 | 3.4
10087 | 14543 | 14.543 | -808 | 3.8
10088 | 14464 | 14.464 | 478 | 2.45
10089 | 14215 | 14.215 | 952 | 3.8
10090 | 14599 | 14.599 | -682 | 4.75
10091 | 14458 | 14.458 | -603 | 4.3
10092 | 14636 | 14.636 | -274 | 1.85
10093 | 14726 | 14.726 | 748 | 0.6
10094 | 14605 | 14.605 | 253 | 0.15
10095 | 14617 | 14.617 | 218 | 1.2
10096 | 14671 | 14.671 | 720 | 0.35
10097 | 14609 | 14.609 | -724 | 2.35
10098 | 14535 | 14.535 | -87 | 0.75
10099 | 14491 | 14.491 | -966 | 3.15
10100 | 14467 | 14.467 | -731 | 1.35
10101 | 14480 | 14.48 | -75 | 3.3
10102 | 14394 | 14.394 | -986 | 2.9
10103 | 14507 | 14.507 | -315 | 4.65
10104 | 14445 | 14.445 | -828 | 4.55
10105 | 14288 | 14.288 | 275 | 1.25
10106 | 14407 | 14.407 | -925 | 0.05
10107 | 14387 | 14.387 | 225 | 0.05
10108 | 14293 | 14.293 | 199 | 0
10109 | 14469 | 14.469 | -332 | 0.75
10110 | 14252 | 14.252 | 449 | 4
10111 | 14317 | 14.317 | 469 | 1.55
10112 | 14241 | 14.241 | -650 | 2.75
10113 | 14192 | 14.192 | -445 | 3
10114 | 14266 | 14.266 | 536 | 2.3
10115 | 14290 | 14.29 | 878 | 4.85
10116 | 14402 | 14.402 | 886 | 1.05
10117 | 14406 | 14.406 | -481 | 0.95
10118 | 14334 | 14.334 | 886 | 4.9
10119 | 14415 | 14.415 | 226 | 3.45
10120 | 14509 | 14.509 | 838 | 2.9
10121 | 14381 | 14.381 | 207 | 2.9
10122 | 14454 | 14.454 | -469 | 2.65
10123 | 14472 | 14.472 | -685 | 4.8
10124 | 14547 | 14.547 | -450 | 4.05
10125 | 14415 | 14.415 | -867 | 2.75
10126 | 14556 | 14.556 | -519 | 0.35
10127 | 14575 | 14.575 | -854 | 2.6
10128 | 13918 | 13.918 | -288 | 0.55
10129 | 13172 | 13.172 | 187 | 3.45
10130 | 14313 | 14.313 | 167 | 3.2
10131 | 14682 | 14.682 | -778 | 0
10132 | 14522 | 14.522 | -775 | 3.95
10133 | 14753 | 14.753 | -891 | 4.95
10134 | 14595 | 14.595 | 498 | 4.65
10135 | 14634 | 14.634 | 11 | 1.6
10136 | 14556 | 14.556 | -766 | 4.4
10137 | 14763 | 14.763 | 657 | 1.15
10138 | 14591 | 14.591 | 485 | 0.2
10139 | 14546 | 14.546 | -807 | 2.95
10140 | 14766 | 14.766 | -533 | 3.15
10141 | 14539 | 14.539 | 837 | 4.35
10142 | 14511 | 14.511 | -932 | 3.2
10143 | 14823 | 14.823 | -646 | 2.9
10144 | 14529 | 14.529 | -402 | 4.95
10145 | 14503 | 14.503 | -80 | 2.95
10146 | 14575 | 14.575 | -937 | 0.45
10147 | 14279 | 14.279 | -350 | 2.05
10148 | 14689 | 14.689 | 290 | 0.5
10149 | 14363 | 14.363 | 241 | 3.5
10150 | 14529 | 14.529 | 957 | 3
10151 | 14327 | 14.327 | 878 | 1.45
10152 | 14305 | 14.305 | 378 | 3.75
10153 | 14484 | 14.484 | 122 | 4.55
10154 | 14224 | 14.224 | 243 | 2.2
10155 | 14355 | 14.355 | -549 | 3.05
10156 | 14256 | 14.256 | 852 | 4.9
10157 | 14187 | 14.187 | -827 | 3.75
10158 | 14414 | 14.414 | -304 | 0.3
10159 | 14186 | 14.186 | 833 | 1.6
10160 | 14348 | 14.348 | 0 | 0.85
10161 | 14029 | 14.029 | -380 | 1.85
10162 | 14377 | 14.377 | 973 | 1.3
10163 | 14380 | 14.38 | -938 | 0.4
10164 | 14219 | 14.219 | 201 | 2.6
10165 | 14341 | 14.341 | -263 | 0.5
10166 | 14310 | 14.31 | -582 | 3.85
10167 | 14285 | 14.285 | 330 | 4.3
10168 | 14271 | 14.271 | 916 | 4.6
10169 | 14350 | 14.35 | -620 | 1.05
10170 | 14481 | 14.481 | 102 | 1.7
10171 | 14491 | 14.491 | -528 | 2.95
10172 | 14412 | 14.412 | 342 | 4.2
10173 | 14420 | 14.42 | -738 | 4.95
10174 | 14731 | 14.731 | 787 | 4.4
10175 | 14510 | 14.51 | 341 | 4.5
10176 | 14037 | 14.037 | 66 | 3.4
10177 | 13491 | 13.491 | 55 | 0.35
10178 | 13994 | 13.994 | -665 | 2.7
10179 | 13988 | 13.988 | -564 | 0.75
10180 | 13741 | 13.741 | 25 | 0.75
10181 | 13419 | 13.419 | -93 | 0.85
10182 | 14479 | 14.479 | -75 | 2.3
10183 | 14785 | 14.785 | -492 | 4.5
10184 | 14584 | 14.584 | 902 | 1.1
10185 | 14526 | 14.526 | 785 | 3.25
10186 | 14643 | 14.643 | 776 | 4.35
10187 | 14691 | 14.691 | -610 | 1.65
10188 | 14636 | 14.636 | -510 | 4.55
10189 | 14599 | 14.599 | 515 | 4.2
10190 | 14694 | 14.694 | 566 | 4.85
10191 | 14550 | 14.55 | 615 | 1.7
10192 | 14574 | 14.574 | -800 | 1.2
10193 | 14879 | 14.879 | 521 | 3.85
10194 | 14525 | 14.525 | 246 | 4.9
10195 | 14400 | 14.4 | 10 | 1.6
10196 | 14500 | 14.5 | -806 | 4.9
10197 | 14570 | 14.57 | -637 | 1.15
10198 | 14465 | 14.465 | 10 | 2.95
10199 | 14351 | 14.351 | -111 | 0.35
10200 | 14496 | 14.496 | -715 | 1.8
10201 | 14222 | 14.222 | 573 | 3.45
10202 | 14309 | 14.309 | -79 | 1.85
10203 | 14467 | 14.467 | 97 | 0.25
10204 | 14264 | 14.264 | -910 | 0
10205 | 14436 | 14.436 | -893 | 1.15
10206 | 14176 | 14.176 | -625 | 3.1
10207 | 14291 | 14.291 | 801 | 4.05
10208 | 14121 | 14.121 | -417 | 0.75
10209 | 14221 | 14.221 | -880 | 1.15
10210 | 14237 | 14.237 | -658 | 4.3
10211 | 14065 | 14.065 | -126 | 1.7
10212 | 14337 | 14.337 | 874 | 4.15
10213 | 14242 | 14.242 | -779 | 0.05
10214 | 14091 | 14.091 | 504 | 4.6
10215 | 14270 | 14.27 | 900 | 4.75
10216 | 14322 | 14.322 | -361 | 4.95
10217 | 14288 | 14.288 | -512 | 3
10218 | 14385 | 14.385 | 828 | 0.7
10219 | 14271 | 14.271 | -508 | 2.25
10220 | 14444 | 14.444 | -252 | 4.6
10221 | 14426 | 14.426 | -808 | 4.9
10222 | 14581 | 14.581 | 397 | 0.95
10223 | 3761 | 3.761 | -777 | 4.45
10224 | 0 | 0 | 881 | 4.35
10225 | 0 | 0 | -646 | 1
10226 | 0 | 0 | 755 | 3.75
10227 | 0 | 0 | 313 | 2.2
10228 | 0 | 0 | 562 | 3.45
10229 | 0 | 0 | -354 | 3.75
10230 | 0 | 0 | -500 | 3.75
10231 | 0 | 0 | -754 | 1.2
10232 | 0 | 0 | -731 | 2.6
10233 | 0 | 0 | 149 | 0.4
10234 | 0 | 0 | -274 | 3.05
10235 | 0 | 0 | 625 | 0.05
10236 | 0 | 0 | -533 | 2.6
10237 | 0 | 0 | -52 | 4.7
10238 | 0 | 0 | 463 | 2.05
10239 | 0 | 0 | -641 | 3.9
10240 | 0 | 0 | 578 | 3.65
10241 | 0 | 0 | -693 | 1.35
10242 | 0 | 0 | 230 | 0.35
10243 | 0 | 0 | 468 | 4.3
10244 | 0 | 0 | -397 | 4.75
10245 | 0 | 0 | -660 | 1.3
10246 | 0 | 0 | 975 | 2.6
10247 | 0 | 0 | 664 | 4.65
10248 | 0 | 0 | 192 | 0.85
10249 | 0 | 0 | -357 | 2.95
10250 | 0 | 0 | -177 | 1.9
10251 | 0 | 0 | 294 | 4.2
10252 | 0 | 0 | 922 | 4.5
10253 | 0 | 0 | 82 | 1.45
10254 | 0 | 0 | -797 | 3.55
10255 | 0 | 0 | -96 | 4
10256 | 0 | 0 | 706 | 3.25
10257 | 0 | 0 | 202 | 1.15
10258 | 0 | 0 | 967 | 0.2
10259 | 0 | 0 | -182 | 1.95
10260 | 0 | 0 | 886 | 4.55
10261 | 0 | 0 | -446 | 4.75
10262 | 0 | 0 | 58 | 4.65
10263 | 0 | 0 | -703 | 4.7
10264 | 0 | 0 | 474 | 3.15
10265 | 0 | 0 | 930 | 0.45
10266 | 0 | 0 | -547 | 1.85
10267 | 0 | 0 | 67 | 4.55
10268 | 0 | 0 | 71 | 3.9
10269 | 0 | 0 | -366 | 5
10270 | 0 | 0 | -629 | 3.75
10271 | 0 | 0 | 879 | 4.8
10272 | 0 | 0 | 370 | 4.95
10273 | 0 | 0 | -330 | 0.35
10274 | 0 | 0 | -851 | 2.8
10275 | 0 | 0 | -291 | 1.3
10276 | 0 | 0 | 284 | 1.35
10277 | 0 | 0 | -956 | 2.95
10278 | 0 | 0 | 682 | 1.8
10279 | 0 | 0 | 256 | 2.7
10280 | 0 | 0 | 868 | 2.15
10281 | 0 | 0 | 904 | 2.2
10282 | 0 | 0 | 779 | 4.35
10283 | 0 | 0 | -2 | 0
10284 | 0 | 0 | -126 | 4.1
10285 | 0 | 0 | 798 | 0.2
10286 | 0 | 0 | 451 | 3.65
10287 | 0 | 0 | 469 | 2.75
10288 | 0 | 0 | -659 | 3.1
10289 | 0 | 0 | -487 | 2
10290 | 0 | 0 | -191 | 3.75
10291 | 511 | 0.511 | -653 | 3.1
10292 | 2983 | 2.983 | -64 | 0.85
10293 | 7984 | 7.984 | 816 | 2.45
10294 | 9075 | 9.075 | 644 | 2.15
10295 | 10171 | 10.171 | -870 | 4
10296 | 11702 | 11.702 | -998 | 5
10297 | 13309 | 13.309 | 383 | 0.35
10298 | 14349 | 14.349 | -981 | 4.2
10299 | 14716 | 14.716 | 482 | 1.6
10300 | 14513 | 14.513 | -167 | 2.2
10301 | 14374 | 14.374 | 73 | 0.2
10302 | 14594 | 14.594 | 859 | 3.35
10303 | 14377 | 14.377 | -247 | 0.25
10304 | 14561 | 14.561 | -854 | 3.35
10305 | 14492 | 14.492 | 918 | 4.2
10306 | 14563 | 14.563 | 70 | 1.55
10307 | 14529 | 14.529 | -82 | 2
10308 | 14337 | 14.337 | -713 | 1.1
10309 | 14315 | 14.315 | 506 | 2.1
10310 | 14469 | 14.469 | -940 | 2.4
10311 | 14318 | 14.318 | -165 | 3.2
10312 | 14546 | 14.546 | -223 | 4.35
10313 | 14492 | 14.492 | -547 | 3.65
10314 | 14576 | 14.576 | -554 | 2.9
10315 | 14589 | 14.589 | -527 | 0.25
10316 | 14336 | 14.336 | -861 | 1.3
10317 | 14475 | 14.475 | -12 | 0.5
10318 | 14268 | 14.268 | 335 | 3.25
10319 | 14521 | 14.521 | -122 | 3.2
10320 | 13772 | 13.772 | 68 | 3.35
10321 | 13562 | 13.562 | 36 | 4.2
10322 | 13593 | 13.593 | 809 | 2.8
10323 | 13890 | 13.89 | 56 | 3.6
10324 | 13975 | 13.975 | -834 | 3.3
10325 | 13383 | 13.383 | 605 | 3.35
10326 | 13901 | 13.901 | 1000 | 1.35
10327 | 14483 | 14.483 | -142 | 0.9
10328 | 14670 | 14.67 | -392 | 3.35
10329 | 14491 | 14.491 | -774 | 3.45
10330 | 14507 | 14.507 | -540 | 1.15
10331 | 14601 | 14.601 | 625 | 4.05
10332 | 14404 | 14.404 | 455 | 0.75
10333 | 14720 | 14.72 | -966 | 3.35
10334 | 14658 | 14.658 | -557 | 1.45
10335 | 14345 | 14.345 | 529 | 2.65
10336 | 14217 | 14.217 | 316 | 1.7
10337 | 14432 | 14.432 | -325 | 3.1
10338 | 14378 | 14.378 | 991 | 3.95
10339 | 14375 | 14.375 | -930 | 3.3
10340 | 14342 | 14.342 | 994 | 2.45
10341 | 14409 | 14.409 | 87 | 4.35
10342 | 14366 | 14.366 | -457 | 2.7
10343 | 14488 | 14.488 | -936 | 0.4
10344 | 14386 | 14.386 | 777 | 4.6
10345 | 14405 | 14.405 | -924 | 4.65
10346 | 14358 | 14.358 | -120 | 3.4
10347 | 14582 | 14.582 | -124 | 0.75
10348 | 14485 | 14.485 | -211 | 1.35
10349 | 14391 | 14.391 | -806 | 1.2
10350 | 14350 | 14.35 | -335 | 0.55
10351 | 14418 | 14.418 | -373 | 4.7
10352 | 14357 | 14.357 | -431 | 2.6
10353 | 14511 | 14.511 | -192 | 2.05
10354 | 14413 | 14.413 | -251 | 4.8
10355 | 14286 | 14.286 | -166 | 3.95
10356 | 14468 | 14.468 | -843 | 4.7
10357 | 14292 | 14.292 | -933 | 2.2
10358 | 14543 | 14.543 | 136 | 3.9
10359 | 14397 | 14.397 | -142 | 1.15
10360 | 14467 | 14.467 | 91 | 2.8
10361 | 14556 | 14.556 | -627 | 1.15
10362 | 14378 | 14.378 | -49 | 2.75
10363 | 14379 | 14.379 | -393 | 2.75
10364 | 14473 | 14.473 | -286 | 2.3
10365 | 14401 | 14.401 | 935 | 0.55
10366 | 14545 | 14.545 | -945 | 0.7
10367 | 14425 | 14.425 | 636 | 3.85
10368 | 14262 | 14.262 | 417 | 2.25
10369 | 13586 | 13.586 | -487 | 1.3
10370 | 13404 | 13.404 | -698 | 0.85
10371 | 14428 | 14.428 | -786 | 1.1
10372 | 14624 | 14.624 | -432 | 4.65
10373 | 14456 | 14.456 | 570 | 1.05
10374 | 14613 | 14.613 | 893 | 3.35
10375 | 14542 | 14.542 | 792 | 2.45
10376 | 14474 | 14.474 | 116 | 3.6
10377 | 14470 | 14.47 | 931 | 0.35
10378 | 14595 | 14.595 | 592 | 0.95
10379 | 14489 | 14.489 | -654 | 0.9
10380 | 14555 | 14.555 | -988 | 4.1
10381 | 14467 | 14.467 | -154 | 2.05
10382 | 14538 | 14.538 | -466 | 4.6
10383 | 14721 | 14.721 | 324 | 3.85
10384 | 14473 | 14.473 | -270 | 1.9
10385 | 14572 | 14.572 | -946 | 1.6
10386 | 14467 | 14.467 | -936 | 4.15
10387 | 14497 | 14.497 | 641 | 2
10388 | 14590 | 14.59 | -179 | 4.8
10389 | 14551 | 14.551 | -373 | 3.95
10390 | 14439 | 14.439 | -81 | 0.9
10391 | 14482 | 14.482 | -587 | 3.45
10392 | 14613 | 14.613 | 659 | 4.95
10393 | 14648 | 14.648 | 501 | 1.85
10394 | 14399 | 14.399 | 160 | 3.15
10395 | 14571 | 14.571 | -229 | 4.65
10396 | 14596 | 14.596 | 996 | 0.1
10397 | 14455 | 14.455 | 898 | 2.3
10398 | 14521 | 14.521 | -308 | 2.15
10399 | 14580 | 14.58 | 259 | 4.15
10400 | 14493 | 14.493 | -42 | 2.75
10401 | 14523 | 14.523 | -698 | 0.75
10402 | 14513 | 14.513 | 953 | 4.8
10403 | 14500 | 14.5 | 396 | 1.6
10404 | 14445 | 14.445 | -253 | 4.65
10405 | 14398 | 14.398 | -367 | 1.45
10406 | 14423 | 14.423 | 223 | 3.25
10407 | 14470 | 14.47 | -685 | 1.65
10408 | 14410 | 14.41 | 18 | 4.9
10409 | 14493 | 14.493 | 426 | 3.95
10410 | 14551 | 14.551 | 286 | 1.7
10411 | 14568 | 14.568 | -386 | 0.7
10412 | 14580 | 14.58 | -162 | 3.75
10413 | 14590 | 14.59 | -713 | 3.55
10414 | 14686 | 14.686 | 407 | 1.6
10415 | 14609 | 14.609 | 983 | 4
10416 | 14338 | 14.338 | 694 | 1.1
10417 | 13785 | 13.785 | -566 | 0
10418 | 13780 | 13.78 | -132 | 4.75
10419 | 14031 | 14.031 | -648 | 0.75
10420 | 13941 | 13.941 | 417 | 2.65
10421 | 13425 | 13.425 | 965 | 4.6
10422 | 13740 | 13.74 | 945 | 3.1
10423 | 14892 | 14.892 | -854 | 2.6
10424 | 14528 | 14.528 | -919 | 3.55
10425 | 14621 | 14.621 | -850 | 0.5
10426 | 14616 | 14.616 | 797 | 2.8
10427 | 14642 | 14.642 | 185 | 4.4
10428 | 14648 | 14.648 | 653 | 1.85
10429 | 14600 | 14.6 | 987 | 1.35
10430 | 14618 | 14.618 | -380 | 4.45
10431 | 14594 | 14.594 | 266 | 1.45
10432 | 14540 | 14.54 | 68 | 0.55
10433 | 14615 | 14.615 | -290 | 4.15
10434 | 14634 | 14.634 | 650 | 2
10435 | 14500 | 14.5 | 243 | 3.6
10436 | 14521 | 14.521 | -49 | 4.8
10437 | 14468 | 14.468 | 375 | 1.7
10438 | 14832 | 14.832 | -432 | 2.7
10439 | 14374 | 14.374 | -154 | 0.25
10440 | 14364 | 14.364 | -241 | 0.95
10441 | 14411 | 14.411 | 983 | 1.75
10442 | 14400 | 14.4 | 655 | 0.35
10443 | 14401 | 14.401 | 710 | 0.95
10444 | 14494 | 14.494 | 482 | 2.3
10445 | 14198 | 14.198 | -710 | 0.5
10446 | 14385 | 14.385 | 135 | 2
10447 | 14309 | 14.309 | 920 | 4.7
10448 | 14300 | 14.3 | 342 | 2.15
10449 | 14166 | 14.166 | -373 | 3.95
10450 | 14353 | 14.353 | -604 | 2.9
10451 | 14367 | 14.367 | 461 | 3.6
10452 | 14138 | 14.138 | -838 | 1.95
10453 | 14190 | 14.19 | 631 | 2.7
10454 | 14146 | 14.146 | -309 | 2.65
10455 | 14246 | 14.246 | 979 | 3.25
10456 | 14283 | 14.283 | -541 | 1.1
10457 | 14117 | 14.117 | 311 | 4.5
10458 | 14293 | 14.293 | 358 | 3.25
10459 | 14424 | 14.424 | 221 | 4.4
10460 | 14301 | 14.301 | 429 | 1.7
10461 | 14240 | 14.24 | -964 | 0.85
10462 | 14532 | 14.532 | -778 | 4.3
10463 | 13965 | 13.965 | 277 | 3.65
10464 | 13411 | 13.411 | -68 | 2.85
10465 | 13130 | 13.13 | -536 | 0.1
10466 | 14240 | 14.24 | 227 | 4.2
10467 | 14406 | 14.406 | 978 | 2.3
10468 | 14414 | 14.414 | 510 | 0.9
10469 | 14312 | 14.312 | 841 | 2.65
10470 | 14351 | 14.351 | 16 | 2.85
10471 | 14483 | 14.483 | -718 | 2.2
10472 | 14421 | 14.421 | 368 | 3.15
10473 | 14390 | 14.39 | 157 | 3.75
10474 | 14453 | 14.453 | -763 | 3.4
10475 | 14438 | 14.438 | 449 | 2.45
10476 | 14316 | 14.316 | 289 | 3.85
10477 | 14439 | 14.439 | 69 | 3.15
10478 | 14638 | 14.638 | -758 | 2.45
10479 | 14372 | 14.372 | 520 | 3.15
10480 | 14266 | 14.266 | 129 | 4.4
10481 | 14522 | 14.522 | -48 | 2.1
10482 | 14269 | 14.269 | 475 | 2.15
10483 | 14412 | 14.412 | -450 | 1.45
10484 | 14394 | 14.394 | 640 | 4.25
10485 | 14224 | 14.224 | -300 | 0.5
10486 | 14347 | 14.347 | 385 | 0.95
10487 | 14159 | 14.159 | 581 | 0.5
10488 | 14097 | 14.097 | 53 | 1.7
10489 | 14243 | 14.243 | 94 | 1.35
10490 | 14028 | 14.028 | 582 | 3.75
10491 | 14134 | 14.134 | -200 | 2.05
10492 | 14036 | 14.036 | -380 | 3.1
10493 | 13929 | 13.929 | -672 | 3.25
10494 | 13958 | 13.958 | -448 | 2.3
10495 | 13996 | 13.996 | 372 | 3.25
10496 | 13890 | 13.89 | 837 | 3.15
10497 | 13964 | 13.964 | -300 | 2
10498 | 13790 | 13.79 | -71 | 0.3
10499 | 13974 | 13.974 | -369 | 2.4
10500 | 13945 | 13.945 | -653 | 3.05
10501 | 14051 | 14.051 | -483 | 4.65
10502 | 14024 | 14.024 | 565 | 1.45
10503 | 14018 | 14.018 | -354 | 1.7
10504 | 13952 | 13.952 | -872 | 2.3
10505 | 14211 | 14.211 | -789 | 2.55
10506 | 14076 | 14.076 | -570 | 3.8
10507 | 14131 | 14.131 | -522 | 1.45
10508 | 14197 | 14.197 | -382 | 4
10509 | 14249 | 14.249 | -351 | 4.7
10510 | 14383 | 14.383 | 123 | 1.75
10511 | 14421 | 14.421 | -387 | 4.65
10512 | 14379 | 14.379 | -45 | 2.65
10513 | 14216 | 14.216 | -437 | 3.4
10514 | 13550 | 13.55 | -694 | 0.6
10515 | 13292 | 13.292 | 522 | 2.55
10516 | 13461 | 13.461 | -633 | 1.5
10517 | 13532 | 13.532 | 419 | 3.95
10518 | 13576 | 13.576 | -539 | 1.8
10519 | 12842 | 12.842 | 56 | 1.3
10520 | 14102 | 14.102 | -557 | 4.6
10521 | 14545 | 14.545 | -148 | 3.85
10522 | 14592 | 14.592 | 143 | 3.8
10523 | 14047 | 14.047 | -682 | 3.25
10524 | 14594 | 14.594 | 138 | 2.6
10525 | 14374 | 14.374 | 964 | 4.4
10526 | 50 | 0.05 | -995 | 1.8
10527 | 0 | 0 | -529 | 2.9
10528 | 0 | 0 | 172 | 2.9
10529 | 0 | 0 | 789 | 4.65
10530 | 0 | 0 | 813 | 1.9
10531 | 0 | 0 | -403 | 0.1
10532 | 0 | 0 | 537 | 0.7
10533 | 0 | 0 | -789 | 1.7
10534 | 0 | 0 | 217 | 2.65
10535 | 0 | 0 | -230 | 2.85
10536 | 0 | 0 | -952 | 0.15
10537 | 0 | 0 | -519 | 4.9
10538 | 0 | 0 | -444 | 4.85
10539 | 0 | 0 | 128 | 4.4
10540 | 0 | 0 | -663 | 1.85
10541 | 0 | 0 | -413 | 4.05
10542 | 0 | 0 | 442 | 3.85
10543 | 0 | 0 | 527 | 2.85
10544 | 0 | 0 | 490 | 3.15
10545 | 0 | 0 | -243 | 0.45
10546 | 0 | 0 | -926 | 4.9
10547 | 0 | 0 | 258 | 1.9
10548 | 0 | 0 | 728 | 3.65
10549 | 0 | 0 | -556 | 4.8
10550 | 0 | 0 | 758 | 3.35
10551 | 0 | 0 | 899 | 0.4
10552 | 0 | 0 | 761 | 3.3
10553 | 0 | 0 | -97 | 0.85
10554 | 0 | 0 | -945 | 4.7
10555 | 0 | 0 | 148 | 2.95
10556 | 0 | 0 | -733 | 0.25
10557 | 0 | 0 | 590 | 2.9
10558 | 0 | 0 | 405 | 1.65
10559 | 0 | 0 | 271 | 3.6
10560 | 0 | 0 | 852 | 2.25
10561 | 0 | 0 | -524 | 3.8
10562 | 0 | 0 | 739 | 0.2
10563 | 0 | 0 | -740 | 3.05
10564 | 0 | 0 | 954 | 1.8
10565 | 0 | 0 | 624 | 1.4
10566 | 0 | 0 | 738 | 4.8
10567 | 0 | 0 | -539 | 0
10568 | 0 | 0 | 240 | 0.35
10569 | 1052 | 1.052 | 909 | 4.9
10570 | 1722 | 1.722 | -858 | 1.2
10571 | 2290 | 2.29 | -967 | 3.15
10572 | 6398 | 6.398 | 595 | 1.05
10573 | 9766 | 9.766 | 191 | 4.2
10574 | 10476 | 10.476 | -756 | 0.85
10575 | 12304 | 12.304 | 525 | 1.85
10576 | 13689 | 13.689 | -697 | 0.4
10577 | 14520 | 14.52 | -245 | 1.5
10578 | 14501 | 14.501 | 236 | 2.6
10579 | 14292 | 14.292 | -696 | 2.5
10580 | 14281 | 14.281 | 813 | 0.15
10581 | 14188 | 14.188 | -118 | 2.25
10582 | 14132 | 14.132 | -180 | 2.85
10583 | 14284 | 14.284 | -912 | 3.1
10584 | 14106 | 14.106 | 479 | 1.25
10585 | 14161 | 14.161 | -841 | 1.1
10586 | 14036 | 14.036 | -693 | 0.45
10587 | 14062 | 14.062 | -889 | 4.3
10588 | 13932 | 13.932 | -123 | 3.7
10589 | 13906 | 13.906 | 551 | 4.75
10590 | 13715 | 13.715 | -509 | 2.55
10591 | 13761 | 13.761 | 652 | 1.3
10592 | 13908 | 13.908 | -338 | 1.65
10593 | 13669 | 13.669 | -406 | 4.7
10594 | 13757 | 13.757 | -48 | 3.95
10595 | 13817 | 13.817 | -765 | 3.35
10596 | 13750 | 13.75 | -717 | 4.8
10597 | 13875 | 13.875 | -849 | 1.2
10598 | 13637 | 13.637 | 342 | 0.5
10599 | 13846 | 13.846 | 630 | 4.45
10600 | 13930 | 13.93 | 903 | 0.6
10601 | 13818 | 13.818 | 109 | 1.25
10602 | 13970 | 13.97 | -295 | 3.35
10603 | 13972 | 13.972 | -272 | 4.65
10604 | 13945 | 13.945 | 648 | 3.85
10605 | 14083 | 14.083 | 895 | 2.7
10606 | 14113 | 14.113 | 371 | 1.8
10607 | 14240 | 14.24 | -338 | 4.9
10608 | 13717 | 13.717 | -697 | 1.2
10609 | 13375 | 13.375 | 528 | 1.45
10610 | 13433 | 13.433 | 92 | 1.75
10611 | 13591 | 13.591 | -318 | 0.2
10612 | 13756 | 13.756 | -986 | 1.8
10613 | 13310 | 13.31 | -442 | 4.95
10614 | 13585 | 13.585 | -443 | 4
10615 | 14379 | 14.379 | -617 | 3.75
10616 | 14498 | 14.498 | 736 | 0.95
10617 | 14464 | 14.464 | -866 | 0.35
10618 | 14537 | 14.537 | 427 | 3.7
10619 | 14489 | 14.489 | 976 | 2.35
10620 | 14331 | 14.331 | 943 | 4.35
10621 | 14373 | 14.373 | -188 | 4.75
10622 | 14300 | 14.3 | 973 | 2.05
10623 | 14208 | 14.208 | 860 | 3.05
10624 | 14290 | 14.29 | 918 | 2
10625 | 14105 | 14.105 | -493 | 1.05
10626 | 14130 | 14.13 | 811 | 4.45
10627 | 13975 | 13.975 | 528 | 4.55
10628 | 13922 | 13.922 | 692 | 1.6
10629 | 13865 | 13.865 | 197 | 1.95
10630 | 13686 | 13.686 | -43 | 2.9
10631 | 13689 | 13.689 | -134 | 2.25
10632 | 13609 | 13.609 | 187 | 0.95
10633 | 13505 | 13.505 | 365 | 0.75
10634 | 13600 | 13.6 | -289 | 0.2
10635 | 13481 | 13.481 | -831 | 1.5
10636 | 13401 | 13.401 | -104 | 0.05
10637 | 13579 | 13.579 | 846 | 4.3
10638 | 13435 | 13.435 | -871 | 1.7
10639 | 13657 | 13.657 | -82 | 3.9
10640 | 13492 | 13.492 | 646 | 3.95
10641 | 13446 | 13.446 | 886 | 3.55
10642 | 13471 | 13.471 | 19 | 4.05
10643 | 13499 | 13.499 | -844 | 0
10644 | 13288 | 13.288 | -584 | 1.3
10645 | 13348 | 13.348 | -417 | 2.2
10646 | 13461 | 13.461 | 856 | 0.75
10647 | 13533 | 13.533 | 792 | 2.9
10648 | 13696 | 13.696 | 270 | 3.25
10649 | 13718 | 13.718 | 167 | 2.05
10650 | 13905 | 13.905 | -280 | 4.05
10651 | 13832 | 13.832 | -576 | 1.6
10652 | 13866 | 13.866 | -817 | 3.45
10653 | 13866 | 13.866 | -752 | 1.65
10654 | 13912 | 13.912 | 77 | 1.75
10655 | 13923 | 13.923 | -225 | 0.95
10656 | 13343 | 13.343 | -994 | 4
10657 | 12714 | 12.714 | 212 | 3.1
10658 | 13781 | 13.781 | 3 | 3.35
10659 | 14071 | 14.071 | 348 | 2.3
10660 | 14067 | 14.067 | -960 | 3.85
10661 | 14004 | 14.004 | -904 | 4.75
10662 | 14270 | 14.27 | 196 | 4.05
10663 | 14167 | 14.167 | -145 | 1
10664 | 14274 | 14.274 | 520 | 2.55
10665 | 14348 | 14.348 | 396 | 2.8
10666 | 14105 | 14.105 | 302 | 2.85
10667 | 14108 | 14.108 | -35 | 0.1
10668 | 14092 | 14.092 | -17 | 2.6
10669 | 14181 | 14.181 | 779 | 2.65
10670 | 14068 | 14.068 | -59 | 2.15
10671 | 14159 | 14.159 | 35 | 4.7
10672 | 14046 | 14.046 | -459 | 1.2
10673 | 14083 | 14.083 | -861 | 0.1
10674 | 13966 | 13.966 | 235 | 1.45
10675 | 13860 | 13.86 | 369 | 4.3
10676 | 13931 | 13.931 | 44 | 0.7
10677 | 13909 | 13.909 | 741 | 1.8
10678 | 13970 | 13.97 | -134 | 1.8
10679 | 13940 | 13.94 | 845 | 4.35
10680 | 13947 | 13.947 | 898 | 4.1
10681 | 13812 | 13.812 | 431 | 1.6
10682 | 13956 | 13.956 | 243 | 3.55
10683 | 13691 | 13.691 | 270 | 0.05
10684 | 13907 | 13.907 | -272 | 3.65
10685 | 13808 | 13.808 | 576 | 1.35
10686 | 13883 | 13.883 | 973 | 3.5
10687 | 13891 | 13.891 | -620 | 4.4
10688 | 13817 | 13.817 | 76 | 1.45
10689 | 13782 | 13.782 | 13 | 0.9
10690 | 13803 | 13.803 | -57 | 2.85
10691 | 13792 | 13.792 | -997 | 4.8
10692 | 13860 | 13.86 | -866 | 3.8
10693 | 13843 | 13.843 | -604 | 3.75
10694 | 14022 | 14.022 | -950 | 0.95
10695 | 13900 | 13.9 | 228 | 3.9
10696 | 14113 | 14.113 | -977 | 0.35
10697 | 14021 | 14.021 | -614 | 2.5
10698 | 14151 | 14.151 | -896 | 2.25
10699 | 14339 | 14.339 | -326 | 1.5
10700 | 14268 | 14.268 | -67 | 1.8
10701 | 14189 | 14.189 | 834 | 4.25
10702 | 14510 | 14.51 | -224 | 0.1
10703 | 14464 | 14.464 | 97 | 0.8
10704 | 14406 | 14.406 | 351 | 4.25
10705 | 14244 | 14.244 | -782 | 4.1
10706 | 13642 | 13.642 | -494 | 1.75
10707 | 13437 | 13.437 | -149 | 1.15
10708 | 13619 | 13.619 | -156 | 0.85
10709 | 13757 | 13.757 | -632 | 0.35
10710 | 13683 | 13.683 | -831 | 1.8
10711 | 13311 | 13.311 | 749 | 4.55
10712 | 14405 | 14.405 | -619 | 3.25
10713 | 14346 | 14.346 | -406 | 4.65
10714 | 14564 | 14.564 | 844 | 3.6
10715 | 14504 | 14.504 | -493 | 3.75
10716 | 14490 | 14.49 | 178 | 4.4
10717 | 14443 | 14.443 | -952 | 4.35
10718 | 14570 | 14.57 | 864 | 2.35
10719 | 14471 | 14.471 | 907 | 2.95
10720 | 14478 | 14.478 | 225 | 4.85
10721 | 14422 | 14.422 | 734 | 3.9
10722 | 14356 | 14.356 | -82 | 4.45
10723 | 14410 | 14.41 | 216 | 4.95
10724 | 14420 | 14.42 | -264 | 2.35
10725 | 14288 | 14.288 | -885 | 3.9
10726 | 14243 | 14.243 | -844 | 1.3
10727 | 14299 | 14.299 | 370 | 3.1
10728 | 14088 | 14.088 | 91 | 0.65
10729 | 14012 | 14.012 | -827 | 2.85
10730 | 13941 | 13.941 | -514 | 2.5
10731 | 13981 | 13.981 | -747 | 0.3
10732 | 13850 | 13.85 | -992 | 1.7
10733 | 13876 | 13.876 | 118 | 1.8
10734 | 13681 | 13.681 | 739 | 0.45
10735 | 13506 | 13.506 | 797 | 0.45
10736 | 13686 | 13.686 | -545 | 3.35
10737 | 13609 | 13.609 | 250 | 2.05
10738 | 13750 | 13.75 | -987 | 0.7
10739 | 13790 | 13.79 | -209 | 3
10740 | 13625 | 13.625 | 287 | 2.9
10741 | 13697 | 13.697 | 296 | 1.95
10742 | 13720 | 13.72 | 127 | 0.6
10743 | 13735 | 13.735 | -379 | 0
10744 | 13778 | 13.778 | 377 | 2.6
10745 | 13841 | 13.841 | -774 | 0.65
10746 | 13841 | 13.841 | 9 | 0.75
10747 | 13919 | 13.919 | 553 | 1.7
10748 | 14019 | 14.019 | 369 | 4.6
10749 | 13914 | 13.914 | 954 | 3.4
10750 | 14004 | 14.004 | -548 | 1.75
10751 | 13870 | 13.87 | 926 | 1.9
10752 | 12753 | 12.753 | -569 | 3.2
10753 | 12141 | 12.141 | 108 | 1.25
10754 | 13321 | 13.321 | 7 | 1.75
10755 | 13619 | 13.619 | 704 | 4.25
10756 | 14207 | 14.207 | -679 | 0.95
10757 | 14255 | 14.255 | -532 | 2.8
10758 | 14179 | 14.179 | -393 | 1.5
10759 | 14241 | 14.241 | -417 | 1.8
10760 | 14303 | 14.303 | -501 | 3.55
10761 | 14180 | 14.18 | 726 | 4.4
10762 | 14181 | 14.181 | -837 | 0.3
10763 | 14130 | 14.13 | -309 | 4.25
10764 | 14272 | 14.272 | 516 | 0.7
10765 | 14102 | 14.102 | -179 | 3.6
10766 | 14225 | 14.225 | 414 | 1.05
10767 | 14141 | 14.141 | 161 | 3.1
10768 | 14145 | 14.145 | 691 | 3.55
10769 | 14108 | 14.108 | -288 | 2.45
10770 | 13926 | 13.926 | -38 | 4.75
10771 | 13928 | 13.928 | -513 | 2.95
10772 | 14049 | 14.049 | 821 | 0.8
10773 | 14095 | 14.095 | 765 | 0.25
10774 | 13795 | 13.795 | -926 | 3.7
10775 | 13883 | 13.883 | 584 | 3.75
10776 | 13653 | 13.653 | 789 | 2
10777 | 13761 | 13.761 | 411 | 1.4
10778 | 13802 | 13.802 | -641 | 3.55
10779 | 13780 | 13.78 | -230 | 3.9
10780 | 13728 | 13.728 | 574 | 2.65
10781 | 13725 | 13.725 | -281 | 2.8
10782 | 13664 | 13.664 | 729 | 3.35
10783 | 13717 | 13.717 | -783 | 2.75
10784 | 13906 | 13.906 | 376 | 3.05
10785 | 14023 | 14.023 | 941 | 3.85
10786 | 13980 | 13.98 | -390 | 0.65
10787 | 14229 | 14.229 | -227 | 2.45
10788 | 14118 | 14.118 | -84 | 2.3
10789 | 14117 | 14.117 | 824 | 3.15
10790 | 14067 | 14.067 | -319 | 2.7
10791 | 13972 | 13.972 | 360 | 3.3
10792 | 14202 | 14.202 | -434 | 2.35
10793 | 13905 | 13.905 | 281 | 3.95
10794 | 13551 | 13.551 | 209 | 2.1
10795 | 13607 | 13.607 | -161 | 3.5
10796 | 13539 | 13.539 | -206 | 2.95
10797 | 13501 | 13.501 | -202 | 3.65
10798 | 13665 | 13.665 | -239 | 0.25
10799 | 14244 | 14.244 | 776 | 3.45
10800 | 13428 | 13.428 | -798 | 4
10801 | 12658 | 12.658 | 722 | 3.25
10802 | 12588 | 12.588 | 346 | 0.2
10803 | 12748 | 12.748 | -417 | 0.95
10804 | 12759 | 12.759 | -889 | 2.95
10805 | 12906 | 12.906 | -719 | 3.05
10806 | 13627 | 13.627 | -363 | 1.9
10807 | 14049 | 14.049 | 890 | 1.6
10808 | 13711 | 13.711 | 448 | 2.3
10809 | 13876 | 13.876 | 28 | 4.7
10810 | 13688 | 13.688 | 994 | 1.95
10811 | 14530 | 14.53 | 8 | 2.25
10812 | 14525 | 14.525 | -711 | 1.25
10813 | 14553 | 14.553 | 447 | 0.9
10814 | 14529 | 14.529 | -707 | 1.6
10815 | 14433 | 14.433 | 316 | 2.6
10816 | 14587 | 14.587 | 532 | 1.1
10817 | 14543 | 14.543 | -412 | 0.65
10818 | 14465 | 14.465 | -914 | 0.9
10819 | 14458 | 14.458 | -516 | 1.4
10820 | 14504 | 14.504 | 611 | 0.75
10821 | 14478 | 14.478 | -556 | 0.25
10822 | 14522 | 14.522 | -950 | 4.4
10823 | 14389 | 14.389 | 928 | 2.35
10824 | 14595 | 14.595 | -336 | 1.2
10825 | 14418 | 14.418 | 430 | 3.3
10826 | 14330 | 14.33 | 6 | 4.75
10827 | 14351 | 14.351 | 954 | 1
10828 | 14352 | 14.352 | -730 | 2.55
10829 | 14188 | 14.188 | -531 | 0.75
10830 | 14357 | 14.357 | 805 | 2.95
10831 | 14374 | 14.374 | 64 | 4.9
10832 | 14125 | 14.125 | -337 | 3.15
10833 | 14257 | 14.257 | 857 | 2.75
10834 | 14225 | 14.225 | 791 | 2.75
10835 | 14329 | 14.329 | 790 | 4.35
10836 | 14274 | 14.274 | -436 | 2.65
10837 | 14456 | 14.456 | 890 | 2.6
10838 | 14327 | 14.327 | -946 | 3.45
10839 | 14389 | 14.389 | -300 | 4.35
10840 | 14386 | 14.386 | -906 | 3.05
10841 | 14404 | 14.404 | -458 | 0.95
10842 | 14387 | 14.387 | -146 | 4.45
10843 | 14468 | 14.468 | 672 | 4.05
10844 | 14475 | 14.475 | 141 | 2.35
10845 | 14365 | 14.365 | 154 | 1.3
10846 | 14403 | 14.403 | 120 | 0.25
10847 | 14301 | 14.301 | -746 | 1.2
10848 | 13881 | 13.881 | -659 | 2.35
10849 | 13157 | 13.157 | -19 | 0.2
10850 | 13683 | 13.683 | -621 | 2.4
10851 | 14471 | 14.471 | 863 | 3.65
10852 | 14639 | 14.639 | 12 | 4.1
10853 | 14568 | 14.568 | -277 | 0.6
10854 | 14564 | 14.564 | 143 | 4.9
10855 | 14570 | 14.57 | -839 | 1.7
10856 | 14608 | 14.608 | -901 | 3.45
10857 | 14471 | 14.471 | 800 | 0.85
10858 | 14702 | 14.702 | 990 | 2.7
10859 | 14444 | 14.444 | 781 | 4.95
10860 | 14492 | 14.492 | -239 | 1.25
10861 | 14472 | 14.472 | -14 | 3.75
10862 | 14498 | 14.498 | -784 | 3.65
10863 | 14596 | 14.596 | -158 | 0.2
10864 | 14509 | 14.509 | -14 | 0.3
10865 | 14358 | 14.358 | -905 | 1.6
10866 | 14463 | 14.463 | -522 | 3.15
10867 | 14394 | 14.394 | -727 | 1.4
10868 | 14275 | 14.275 | 995 | 3.8
10869 | 14300 | 14.3 | -165 | 1.7
10870 | 14341 | 14.341 | 71 | 1.75
10871 | 14270 | 14.27 | -511 | 3
10872 | 14298 | 14.298 | -905 | 2.85
10873 | 14383 | 14.383 | -555 | 1.8
10874 | 14299 | 14.299 | -33 | 3.65
10875 | 14405 | 14.405 | 397 | 0.95
10876 | 14460 | 14.46 | -853 | 2.05
10877 | 14352 | 14.352 | 644 | 2.3
10878 | 14309 | 14.309 | 199 | 2.4
10879 | 14395 | 14.395 | -171 | 1.8
10880 | 14158 | 14.158 | 443 | 0.7
10881 | 13997 | 13.997 | -574 | 4.95
10882 | 14357 | 14.357 | -972 | 1.25
10883 | 14289 | 14.289 | 237 | 3.1
10884 | 14254 | 14.254 | 67 | 2.65
10885 | 14258 | 14.258 | 893 | 2.4
10886 | 14301 | 14.301 | 204 | 2.45
10887 | 14291 | 14.291 | -617 | 4.2
10888 | 14320 | 14.32 | 464 | 2.2
10889 | 14491 | 14.491 | 66 | 4.45
10890 | 14313 | 14.313 | -180 | 4.55
10891 | 14517 | 14.517 | -818 | 1.8
10892 | 14470 | 14.47 | 618 | 3.65
10893 | 14332 | 14.332 | -323 | 2.55
10894 | 13936 | 13.936 | 718 | 3.25
10895 | 13938 | 13.938 | 517 | 2.9
10896 | 13577 | 13.577 | 453 | 3.75
10897 | 13305 | 13.305 | 388 | 0.75
10898 | 13635 | 13.635 | 784 | 2.15
10899 | 13679 | 13.679 | 35 | 0.45
10900 | 13815 | 13.815 | -629 | 4.75
10901 | 12791 | 12.791 | -176 | 2.6
10902 | 14352 | 14.352 | 805 | 0.05
10903 | 14635 | 14.635 | -88 | 3.45
10904 | 14664 | 14.664 | 259 | 1.5
10905 | 14628 | 14.628 | -501 | 4.2
10906 | 14492 | 14.492 | -801 | 1.95
10907 | 14636 | 14.636 | -319 | 1.45
10908 | 14520 | 14.52 | -214 | 3.4
10909 | 14546 | 14.546 | -785 | 3.05
10910 | 14522 | 14.522 | -17 | 4
10911 | 14613 | 14.613 | -472 | 1
10912 | 14569 | 14.569 | -825 | 3.1
10913 | 14567 | 14.567 | 928 | 1.1
10914 | 14512 | 14.512 | 400 | 3.25
10915 | 14638 | 14.638 | -671 | 1.85
10916 | 14415 | 14.415 | -403 | 4.95
10917 | 14376 | 14.376 | -745 | 1.25
10918 | 14641 | 14.641 | -560 | 3.2
10919 | 14531 | 14.531 | -391 | 2.5
10920 | 14436 | 14.436 | -102 | 1.15
10921 | 14427 | 14.427 | 811 | 0.55
10922 | 14605 | 14.605 | 785 | 5
10923 | 14376 | 14.376 | -516 | 3.8
10924 | 14445 | 14.445 | 683 | 3.65
10925 | 14405 | 14.405 | -8 | 1.9
10926 | 14413 | 14.413 | -580 | 3.65
10927 | 14374 | 14.374 | -981 | 1.8
10928 | 14365 | 14.365 | -260 | 4.9
10929 | 14144 | 14.144 | -5 | 1.85
10930 | 14460 | 14.46 | 999 | 2.5
10931 | 14346 | 14.346 | -653 | 1.15
10932 | 14341 | 14.341 | -25 | 4.45
10933 | 14586 | 14.586 | 372 | 2.6
10934 | 14423 | 14.423 | -773 | 2.55
10935 | 14421 | 14.421 | 891 | 3.8
10936 | 14538 | 14.538 | 209 | 3.45
10937 | 14491 | 14.491 | -799 | 0.4
10938 | 14484 | 14.484 | -864 | 2.85
10939 | 14469 | 14.469 | 173 | 2.45
10940 | 14413 | 14.413 | -945 | 0
10941 | 14524 | 14.524 | -410 | 4.65
10942 | 14466 | 14.466 | 900 | 3.25
10943 | 14567 | 14.567 | 992 | 3.35
10944 | 13941 | 13.941 | 312 | 4.7
10945 | 13043 | 13.043 | -669 | 3.35
10946 | 14307 | 14.307 | -632 | 1.7
10947 | 14488 | 14.488 | 481 | 2.15
10948 | 14538 | 14.538 | 113 | 0.6
10949 | 14480 | 14.48 | -229 | 0.6
10950 | 14466 | 14.466 | 509 | 4.75
10951 | 14790 | 14.79 | 322 | 0.95
10952 | 14431 | 14.431 | 879 | 3.9
10953 | 14497 | 14.497 | 935 | 3.55
10954 | 14564 | 14.564 | -233 | 0.1
10955 | 14507 | 14.507 | -598 | 0.8
10956 | 14711 | 14.711 | 77 | 4.25
10957 | 14473 | 14.473 | 290 | 3.8
10958 | 14551 | 14.551 | -71 | 4.9
10959 | 14567 | 14.567 | 271 | 0.25
10960 | 14516 | 14.516 | -458 | 1.5
10961 | 14476 | 14.476 | 188 | 1.15
10962 | 14616 | 14.616 | 111 | 4.1
10963 | 14434 | 14.434 | -689 | 2.8
10964 | 14483 | 14.483 | 4 | 1.35
10965 | 14587 | 14.587 | 972 | 1.3
10966 | 14539 | 14.539 | 555 | 1.9
10967 | 14488 | 14.488 | -967 | 3.15
10968 | 14465 | 14.465 | 540 | 0.3
10969 | 14591 | 14.591 | 534 | 2.4
10970 | 14557 | 14.557 | 283 | 1.5
10971 | 14483 | 14.483 | -89 | 2.95
10972 | 14541 | 14.541 | 886 | 0
10973 | 14376 | 14.376 | -110 | 3.05
10974 | 14396 | 14.396 | 985 | 2.45
10975 | 14522 | 14.522 | 371 | 4.6
10976 | 14384 | 14.384 | 630 | 1.25
10977 | 14472 | 14.472 | 956 | 1.9
10978 | 14382 | 14.382 | -121 | 3.3
10979 | 14444 | 14.444 | 832 | 1.3
10980 | 14320 | 14.32 | -304 | 1.85
10981 | 14457 | 14.457 | 696 | 0
10982 | 14342 | 14.342 | -978 | 0.95
10983 | 14368 | 14.368 | -203 | 0.65
10984 | 14467 | 14.467 | -907 | 4.25
10985 | 14456 | 14.456 | 145 | 2
10986 | 14322 | 14.322 | 48 | 1.05
10987 | 14526 | 14.526 | -51 | 4.5
10988 | 14406 | 14.406 | -286 | 3.3
10989 | 14456 | 14.456 | -828 | 3.6
10990 | 14490 | 14.49 | 754 | 4.6
10991 | 14314 | 14.314 | 976 | 3.2
10992 | 13627 | 13.627 | 45 | 4.6
10993 | 13435 | 13.435 | -734 | 2.5
10994 | 13797 | 13.797 | 995 | 4.65
10995 | 13815 | 13.815 | -852 | 1.85
10996 | 13827 | 13.827 | -491 | 3.95
10997 | 13341 | 13.341 | -645 | 2.7
10998 | 14464 | 14.464 | -735 | 4.1
10999 | 14595 | 14.595 | 794 | 4.65
11000 | 14503 | 14.503 | 1 | 2.35
11001 | 14643 | 14.643 | 987 | 5
11002 | 14546 | 14.546 | -211 | 4.45
11003 | 14542 | 14.542 | 41 | 3.15
11004 | 14689 | 14.689 | -244 | 2.45
11005 | 14523 | 14.523 | 607 | 1.6
11006 | 14496 | 14.496 | -164 | 3.3
11007 | 14597 | 14.597 | 921 | 0.95
11008 | 14510 | 14.51 | -670 | 3.05
11009 | 14574 | 14.574 | -274 | 2.25
11010 | 14536 | 14.536 | 743 | 0.6
11011 | 14533 | 14.533 | 376 | 1.9
11012 | 14478 | 14.478 | -421 | 3.3
11013 | 14617 | 14.617 | -304 | 3.45
11014 | 14478 | 14.478 | -600 | 2.2
11015 | 14673 | 14.673 | 561 | 3.15
11016 | 14350 | 14.35 | -174 | 2.65
11017 | 14522 | 14.522 | 687 | 1.1
11018 | 14426 | 14.426 | 443 | 1.25
11019 | 14402 | 14.402 | 172 | 1.65
11020 | 14509 | 14.509 | -211 | 1.55
11021 | 14324 | 14.324 | 284 | 4.4
11022 | 14461 | 14.461 | -223 | 1.25
11023 | 14385 | 14.385 | -203 | 1.4
11024 | 14305 | 14.305 | 879 | 4.8
11025 | 14361 | 14.361 | -830 | 4.55
11026 | 14419 | 14.419 | -411 | 2.25
11027 | 14150 | 14.15 | 730 | 1.25
11028 | 14386 | 14.386 | -359 | 2.85
11029 | 14469 | 14.469 | 50 | 0.9
11030 | 14473 | 14.473 | -559 | 1.85
11031 | 14470 | 14.47 | 193 | 1.6
11032 | 14427 | 14.427 | 733 | 3.15
11033 | 14610 | 14.61 | 288 | 2.75
11034 | 12392 | 12.392 | -835 | 4.1
11035 | 10 | 0.01 | 338 | 1.75
11036 | 0 | 0 | 34 | 1.7
11037 | 0 | 0 | 166 | 2.6
11038 | 0 | 0 | 811 | 2.85
11039 | 0 | 0 | 350 | 3.8
11040 | 0 | 0 | -677 | 0.15
11041 | 1586 | 1.586 | -383 | 4.8
11042 | 8642 | 8.642 | 497 | 2.15
11043 | 12912 | 12.912 | 321 | 4.55
11044 | 14660 | 14.66 | -265 | 1.05
11045 | 14649 | 14.649 | -993 | 0.65
11046 | 14490 | 14.49 | -6 | 1.15
11047 | 14582 | 14.582 | 336 | 4.05
11048 | 14712 | 14.712 | 150 | 0.6
11049 | 14559 | 14.559 | 985 | 3.05
11050 | 14587 | 14.587 | -47 | 3.55
11051 | 14598 | 14.598 | 526 | 1.25
11052 | 14620 | 14.62 | 636 | 2.65
11053 | 14510 | 14.51 | 537 | 2.05
11054 | 14623 | 14.623 | -650 | 1.45
11055 | 14291 | 14.291 | -987 | 4.5
11056 | 14603 | 14.603 | -866 | 2.15
11057 | 14375 | 14.375 | -708 | 4.05
11058 | 14359 | 14.359 | 591 | 2.35
11059 | 14491 | 14.491 | 931 | 2.9
11060 | 14556 | 14.556 | -161 | 3.35
11061 | 14407 | 14.407 | 703 | 2.5
11062 | 14382 | 14.382 | -529 | 0.35
11063 | 14392 | 14.392 | -694 | 3.6
11064 | 14310 | 14.31 | -60 | 2.6
11065 | 14289 | 14.289 | 278 | 3.1
11066 | 14545 | 14.545 | 670 | 3.65
11067 | 14091 | 14.091 | -864 | 1.1
11068 | 14519 | 14.519 | 578 | 4.3
11069 | 14365 | 14.365 | -634 | 2.65
11070 | 14401 | 14.401 | -557 | 4.7
11071 | 14192 | 14.192 | -909 | 2.05
11072 | 14534 | 14.534 | 993 | 1.3
11073 | 14288 | 14.288 | -68 | 0.1
11074 | 14253 | 14.253 | -894 | 3.95
11075 | 14325 | 14.325 | -415 | 3.45
11076 | 14516 | 14.516 | -55 | 2.6
11077 | 14390 | 14.39 | 823 | 2.9
11078 | 14431 | 14.431 | -670 | 1.65
11079 | 14549 | 14.549 | -173 | 3.3
11080 | 14352 | 14.352 | -904 | 1.55
11081 | 14528 | 14.528 | -575 | 4.6
11082 | 14454 | 14.454 | 699 | 2.85
11083 | 14515 | 14.515 | 712 | 4.9
11084 | 14549 | 14.549 | -831 | 4.9
11085 | 14468 | 14.468 | -868 | 1.8
11086 | 14361 | 14.361 | 983 | 4.1
11087 | 14107 | 14.107 | 964 | 3.65
11088 | 13704 | 13.704 | -172 | 0.35
11089 | 13575 | 13.575 | -15 | 1.8
11090 | 13689 | 13.689 | 580 | 0.7
11091 | 13904 | 13.904 | 38 | 3.9
11092 | 13200 | 13.2 | -425 | 2.85
11093 | 13669 | 13.669 | 346 | 4.3
11094 | 14587 | 14.587 | -616 | 3.75
11095 | 14457 | 14.457 | 232 | 1.45
11096 | 14640 | 14.64 | -47 | 1.4
11097 | 14462 | 14.462 | -56 | 0.8
11098 | 14512 | 14.512 | 210 | 2.85
11099 | 14705 | 14.705 | 941 | 4.25
11100 | 14464 | 14.464 | 455 | 2.45
11101 | 14521 | 14.521 | 646 | 2.55
11102 | 14583 | 14.583 | 56 | 2.5
11103 | 14502 | 14.502 | -315 | 1.75
11104 | 14556 | 14.556 | 969 | 2.4
11105 | 14448 | 14.448 | -116 | 4.65
11106 | 14627 | 14.627 | 531 | 0.3
11107 | 14464 | 14.464 | -178 | 2.75
11108 | 14495 | 14.495 | -510 | 4.45
11109 | 14511 | 14.511 | -894 | 1.6
11110 | 14510 | 14.51 | 529 | 1.8
11111 | 14395 | 14.395 | 710 | 4.75
11112 | 14427 | 14.427 | -495 | 4
11113 | 14522 | 14.522 | -507 | 2.95
11114 | 14542 | 14.542 | 725 | 2.4
11115 | 14209 | 14.209 | 45 | 4.65
11116 | 14396 | 14.396 | -913 | 1.35
11117 | 14221 | 14.221 | -305 | 2.15
11118 | 14294 | 14.294 | -233 | 0.7
11119 | 14396 | 14.396 | -697 | 3.15
11120 | 14450 | 14.45 | -225 | 2.75
11121 | 14376 | 14.376 | -944 | 0.1
11122 | 14425 | 14.425 | -850 | 1.25
11123 | 14439 | 14.439 | 813 | 0.5
11124 | 14252 | 14.252 | -359 | 0.85
11125 | 14501 | 14.501 | 186 | 3.2
11126 | 14414 | 14.414 | 884 | 2.4
11127 | 14548 | 14.548 | 54 | 1.5
11128 | 14517 | 14.517 | 940 | 1.55
11129 | 14453 | 14.453 | -139 | 5
11130 | 14451 | 14.451 | -80 | 3.35
11131 | 14550 | 14.55 | 158 | 2.05
11132 | 14570 | 14.57 | -87 | 0.4
11133 | 14468 | 14.468 | -385 | 4.6
11134 | 14475 | 14.475 | -27 | 2.15
11135 | 14508 | 14.508 | 509 | 0.5
11136 | 14577 | 14.577 | 273 | 2.45
11137 | 13761 | 13.761 | -85 | 3.95
11138 | 13482 | 13.482 | 717 | 1.3
11139 | 14228 | 14.228 | -896 | 0.05
11140 | 14539 | 14.539 | -738 | 0.05
11141 | 14642 | 14.642 | 377 | 1.85
11142 | 14647 | 14.647 | 279 | 1.7
11143 | 14516 | 14.516 | -155 | 2.1
11144 | 14595 | 14.595 | -935 | 4.6
11145 | 14649 | 14.649 | -22 | 0.8
11146 | 14658 | 14.658 | -739 | 0.65
11147 | 14468 | 14.468 | -689 | 2.3
11148 | 14566 | 14.566 | -72 | 0.75
11149 | 14435 | 14.435 | 393 | 1.9
11150 | 14709 | 14.709 | -146 | 1.2
11151 | 14577 | 14.577 | -543 | 0.7
11152 | 14490 | 14.49 | -40 | 0.5
11153 | 14652 | 14.652 | -531 | 0.9
11154 | 14556 | 14.556 | -41 | 1.9
11155 | 14566 | 14.566 | -530 | 4.35
11156 | 14518 | 14.518 | 557 | 1.1
11157 | 14431 | 14.431 | -962 | 0.15
11158 | 14504 | 14.504 | 266 | 4.4
11159 | 14502 | 14.502 | 152 | 0.3
11160 | 14589 | 14.589 | 422 | 4.15
11161 | 14239 | 14.239 | -637 | 1.05
11162 | 14560 | 14.56 | 816 | 1.2
11163 | 14338 | 14.338 | 305 | 3.05
11164 | 14601 | 14.601 | -314 | 3
11165 | 14559 | 14.559 | 866 | 4.6
11166 | 14408 | 14.408 | 726 | 3.9
11167 | 14402 | 14.402 | -33 | 2.2
11168 | 14571 | 14.571 | -523 | 1.45
11169 | 14440 | 14.44 | -499 | 1.2
11170 | 14479 | 14.479 | 973 | 2.4
11171 | 14473 | 14.473 | -1000 | 3.7
11172 | 14200 | 14.2 | 25 | 0.6
11173 | 14508 | 14.508 | -642 | 2.25
11174 | 14563 | 14.563 | -722 | 0
11175 | 14372 | 14.372 | -461 | 1.3
11176 | 14390 | 14.39 | 787 | 4.85
11177 | 14409 | 14.409 | -467 | 4
11178 | 14424 | 14.424 | 765 | 3.2
11179 | 14514 | 14.514 | 687 | 3.4
11180 | 14440 | 14.44 | 88 | 4.05
11181 | 14486 | 14.486 | -368 | 3.05
11182 | 14518 | 14.518 | -14 | 1.3
11183 | 14336 | 14.336 | 666 | 0.65
11184 | 13892 | 13.892 | 47 | 2.6
11185 | 13752 | 13.752 | 307 | 4.95
11186 | 13912 | 13.912 | -243 | 3.65
11187 | 13766 | 13.766 | 478 | 3.7
11188 | 13992 | 13.992 | -522 | 2.85
11189 | 13673 | 13.673 | -267 | 1.05
11190 | 14311 | 14.311 | 694 | 3.45
11191 | 14770 | 14.77 | 64 | 0.05
11192 | 14558 | 14.558 | 447 | 2.05
11193 | 14793 | 14.793 | -240 | 1.3
11194 | 14608 | 14.608 | -47 | 0.95
11195 | 14551 | 14.551 | -270 | 3.3
11196 | 14605 | 14.605 | -168 | 2.7
11197 | 14653 | 14.653 | 464 | 1.75
11198 | 14514 | 14.514 | -565 | 1.6
11199 | 14585 | 14.585 | 556 | 1.8
11200 | 14193 | 14.193 | 37 | 3.85
11201 | 14591 | 14.591 | 17 | 0.3
11202 | 14361 | 14.361 | 826 | 4.35
11203 | 14341 | 14.341 | -955 | 0.45
11204 | 14304 | 14.304 | 604 | 0.25
11205 | 14452 | 14.452 | 247 | 0.6
11206 | 14259 | 14.259 | 109 | 3.95
11207 | 14313 | 14.313 | -823 | 3.9
11208 | 14213 | 14.213 | 738 | 2.1
11209 | 14495 | 14.495 | -674 | 3.35
11210 | 14311 | 14.311 | 232 | 2.7
11211 | 14392 | 14.392 | 48 | 0.35
11212 | 14294 | 14.294 | -647 | 0.2
11213 | 14442 | 14.442 | 555 | 0.35
11214 | 14260 | 14.26 | 84 | 1.75
11215 | 14181 | 14.181 | -976 | 4.3
11216 | 14208 | 14.208 | 320 | 0.7
11217 | 13935 | 13.935 | 216 | 1
11218 | 14562 | 14.562 | -37 | 3.8
11219 | 14293 | 14.293 | -373 | 3.55
11220 | 14022 | 14.022 | 752 | 1
11221 | 14279 | 14.279 | 174 | 0
11222 | 14158 | 14.158 | 391 | 2.85
11223 | 13967 | 13.967 | 115 | 1
11224 | 14358 | 14.358 | 519 | 0.1
11225 | 14309 | 14.309 | 583 | 2
11226 | 14368 | 14.368 | -558 | 1.2
11227 | 14248 | 14.248 | -355 | 1.3
11228 | 14390 | 14.39 | 869 | 1.6
11229 | 14393 | 14.393 | 728 | 1.05
11230 | 14252 | 14.252 | -538 | 1.55
11231 | 14300 | 14.3 | 361 | 0.5
11232 | 13222 | 13.222 | -157 | 1.75
11233 | 13007 | 13.007 | 395 | 1.45
11234 | 14308 | 14.308 | -27 | 3.85
11235 | 14303 | 14.303 | -629 | 4.5
11236 | 14318 | 14.318 | -209 | 2.3
11237 | 14372 | 14.372 | -202 | 3.5
11238 | 14463 | 14.463 | -671 | 4.25
11239 | 14297 | 14.297 | -143 | 3.25
11240 | 14414 | 14.414 | 985 | 4.85
11241 | 14397 | 14.397 | 173 | 0.2
11242 | 14247 | 14.247 | 371 | 3.4
11243 | 14406 | 14.406 | -148 | 3.1
11244 | 14314 | 14.314 | 52 | 0.2
11245 | 14367 | 14.367 | -600 | 2.6
11246 | 14271 | 14.271 | -907 | 1.05
11247 | 14229 | 14.229 | -671 | 2.35
11248 | 14377 | 14.377 | 637 | 2.75
11249 | 14339 | 14.339 | 113 | 0.45
11250 | 14298 | 14.298 | 788 | 3.85
11251 | 14299 | 14.299 | 962 | 3.15
11252 | 14497 | 14.497 | -89 | 3.75
11253 | 14158 | 14.158 | -177 | 0.15
11254 | 14424 | 14.424 | -104 | 0.85
11255 | 13985 | 13.985 | -368 | 0.45
11256 | 14371 | 14.371 | -825 | 3.9
11257 | 14320 | 14.32 | -820 | 2.25
11258 | 14340 | 14.34 | 975 | 1.85
11259 | 14239 | 14.239 | -565 | 1.95
11260 | 14396 | 14.396 | 759 | 4
11261 | 14180 | 14.18 | -238 | 1.2
11262 | 14178 | 14.178 | -290 | 3.6
11263 | 14148 | 14.148 | -146 | 2.55
11264 | 13993 | 13.993 | -11 | 2.7
11265 | 14171 | 14.171 | 982 | 1.8
11266 | 14159 | 14.159 | 99 | 1.95
11267 | 14146 | 14.146 | 373 | 4.9
11268 | 14038 | 14.038 | -472 | 2.5
11269 | 14209 | 14.209 | -298 | 1
11270 | 14107 | 14.107 | -764 | 3.5
11271 | 14370 | 14.37 | -278 | 3.2
11272 | 14421 | 14.421 | 151 | 0.45
11273 | 14348 | 14.348 | -157 | 4.4
11274 | 14361 | 14.361 | -97 | 4.5
11275 | 14360 | 14.36 | -833 | 0.45
11276 | 14409 | 14.409 | 337 | 4.95
11277 | 14562 | 14.562 | 706 | 2.4
11278 | 14262 | 14.262 | -144 | 0.7
11279 | 14489 | 14.489 | 794 | 2.25
11280 | 14138 | 14.138 | 911 | 2.85
11281 | 13609 | 13.609 | 862 | 1.05
11282 | 13599 | 13.599 | 647 | 4.05
11283 | 13799 | 13.799 | -317 | 3.15
11284 | 13826 | 13.826 | -868 | 4.6
11285 | 13232 | 13.232 | 330 | 3.45
11286 | 13793 | 13.793 | 879 | 4.95
11287 | 14269 | 14.269 | 605 | 0.65
11288 | 14470 | 14.47 | 483 | 3.95
11289 | 14520 | 14.52 | -191 | 1.5
11290 | 14666 | 14.666 | 163 | 3.5
11291 | 14642 | 14.642 | -762 | 3.25
11292 | 14568 | 14.568 | -152 | 2.5
11293 | 14564 | 14.564 | -907 | 3.7
11294 | 14504 | 14.504 | 264 | 3.8
11295 | 14450 | 14.45 | -579 | 4.5
11296 | 14361 | 14.361 | 365 | 5
11297 | 14434 | 14.434 | -899 | 4.2
11298 | 14171 | 14.171 | 422 | 2.15
11299 | 14287 | 14.287 | 740 | 4.8
11300 | 14217 | 14.217 | -44 | 3.55
11301 | 14054 | 14.054 | 599 | 0.15
11302 | 14237 | 14.237 | 578 | 1.75
11303 | 14017 | 14.017 | 513 | 2.55
11304 | 14239 | 14.239 | 549 | 0.3
11305 | 13648 | 13.648 | -128 | 1.4
11306 | 10788 | 10.788 | -121 | 3.65
11307 | 12279 | 12.279 | -370 | 3.2
11308 | 14208 | 14.208 | 566 | 4.25
11309 | 12834 | 12.834 | 991 | 4.7
11310 | 12811 | 12.811 | -248 | 4
11311 | 14064 | 14.064 | -597 | 2.65
11312 | 14099 | 14.099 | -337 | 4.75
11313 | 14153 | 14.153 | -685 | 4.45
11314 | 14118 | 14.118 | -502 | 4.7
11315 | 13970 | 13.97 | -631 | 0.9
11316 | 14002 | 14.002 | 964 | 3.8
11317 | 14304 | 14.304 | 45 | 4.2
11318 | 13956 | 13.956 | -200 | 3.45
11319 | 14121 | 14.121 | 327 | 3.15
11320 | 14252 | 14.252 | 868 | 0.3
11321 | 14247 | 14.247 | 592 | 0.25
11322 | 14250 | 14.25 | 78 | 0.6
11323 | 14275 | 14.275 | -470 | 3.6
11324 | 14220 | 14.22 | 98 | 1.3
11325 | 14267 | 14.267 | 615 | 2.25
11326 | 14288 | 14.288 | -749 | 2.1
11327 | 14261 | 14.261 | 453 | 0.35
11328 | 14119 | 14.119 | 828 | 3.5
11329 | 13205 | 13.205 | 924 | 4.4
11330 | 13586 | 13.586 | 779 | 3.65
11331 | 14334 | 14.334 | -300 | 1.45
11332 | 14460 | 14.46 | 266 | 2.6
11333 | 14480 | 14.48 | -871 | 0.45
11334 | 14410 | 14.41 | 237 | 3.95
11335 | 14530 | 14.53 | -855 | 0.25
11336 | 14428 | 14.428 | 505 | 1.9
11337 | 14610 | 14.61 | -762 | 1.1
11338 | 14679 | 14.679 | 262 | 2.1
11339 | 14547 | 14.547 | 819 | 4.85
11340 | 14553 | 14.553 | 922 | 0.35
11341 | 14501 | 14.501 | 179 | 3.4
11342 | 14505 | 14.505 | 378 | 0.05
11343 | 14452 | 14.452 | 201 | 0.5
11344 | 14279 | 14.279 | 352 | 2.8
11345 | 14435 | 14.435 | 122 | 3.2
11346 | 14487 | 14.487 | -161 | 4.2
11347 | 14228 | 14.228 | -840 | 3.65
11348 | 14144 | 14.144 | -583 | 1.6
11349 | 14220 | 14.22 | 819 | 1.85
11350 | 14380 | 14.38 | -792 | 3.5
11351 | 14179 | 14.179 | 506 | 0.95
11352 | 14181 | 14.181 | -244 | 3.85
11353 | 14252 | 14.252 | -197 | 4.15
11354 | 14141 | 14.141 | 548 | 2.75
11355 | 14132 | 14.132 | 155 | 1.55
11356 | 14110 | 14.11 | 655 | 2.25
11357 | 14054 | 14.054 | -940 | 2.3
11358 | 13987 | 13.987 | 673 | 4.65
11359 | 14367 | 14.367 | 627 | 2.75
11360 | 14165 | 14.165 | -722 | 1.9
11361 | 14104 | 14.104 | 655 | 0.55
11362 | 14189 | 14.189 | 803 | 3.75
11363 | 14001 | 14.001 | -134 | 3.85
11364 | 14229 | 14.229 | -187 | 3.75
11365 | 13947 | 13.947 | -897 | 1.85
11366 | 13992 | 13.992 | 808 | 4.25
11367 | 14067 | 14.067 | -202 | 0.05
11368 | 13988 | 13.988 | 47 | 2.7
11369 | 14138 | 14.138 | -293 | 2.5
11370 | 14133 | 14.133 | 527 | 3.5
11371 | 14314 | 14.314 | -342 | 3.55
11372 | 14308 | 14.308 | -891 | 4.95
11373 | 14422 | 14.422 | -10 | 4.1
11374 | 14262 | 14.262 | 812 | 3.75
11375 | 13793 | 13.793 | 619 | 0.95
11376 | 13459 | 13.459 | 455 | 0.1
11377 | 13743 | 13.743 | -674 | 1.75
11378 | 13810 | 13.81 | -995 | 5
11379 | 13739 | 13.739 | 567 | 0.95
11380 | 13085 | 13.085 | 431 | 1.25
11381 | 13673 | 13.673 | -265 | 3.75
11382 | 14236 | 14.236 | 90 | 3.45
11383 | 14539 | 14.539 | -871 | 3.1
11384 | 14512 | 14.512 | -191 | 0.4
11385 | 14491 | 14.491 | 131 | 3.55
11386 | 14435 | 14.435 | 340 | 0.9
11387 | 14586 | 14.586 | 363 | 1.1
11388 | 14446 | 14.446 | -156 | 3.25
11389 | 14369 | 14.369 | 424 | 0.05
11390 | 14422 | 14.422 | 184 | 2.3
11391 | 14522 | 14.522 | -460 | 0.65
11392 | 14474 | 14.474 | 978 | 1.8
11393 | 14451 | 14.451 | 934 | 1.05
11394 | 14358 | 14.358 | 567 | 3.65
11395 | 14383 | 14.383 | -514 | 1.95
11396 | 14244 | 14.244 | 328 | 1.45
11397 | 14272 | 14.272 | 345 | 4.3
11398 | 14250 | 14.25 | -609 | 3.25
11399 | 14224 | 14.224 | -235 | 1.05
11400 | 14192 | 14.192 | 639 | 3.6
11401 | 14292 | 14.292 | 613 | 0.15
11402 | 14345 | 14.345 | 170 | 1.5
11403 | 14238 | 14.238 | 90 | 0.7
11404 | 14190 | 14.19 | 78 | 3.3
11405 | 14186 | 14.186 | -7 | 3.55
11406 | 14240 | 14.24 | -387 | 2
11407 | 14105 | 14.105 | -758 | 2.45
11408 | 14108 | 14.108 | -693 | 0.65
11409 | 14012 | 14.012 | -716 | 3.65
11410 | 14042 | 14.042 | 560 | 3.2
11411 | 14023 | 14.023 | 921 | 0.4
11412 | 14074 | 14.074 | -158 | 1.4
11413 | 13976 | 13.976 | 523 | 4.1
11414 | 14079 | 14.079 | 881 | 1.8
11415 | 13911 | 13.911 | 451 | 3
11416 | 14151 | 14.151 | -572 | 0.75
11417 | 14169 | 14.169 | -754 | 0.95
11418 | 14072 | 14.072 | -430 | 0.35
11419 | 14196 | 14.196 | -126 | 1.05
11420 | 14260 | 14.26 | -443 | 4.6
11421 | 14142 | 14.142 | -470 | 4
11422 | 14300 | 14.3 | -604 | 3.05
11423 | 14205 | 14.205 | 917 | 2.75
11424 | 13715 | 13.715 | 655 | 2.8
11425 | 13678 | 13.678 | 57 | 0.1
11426 | 13626 | 13.626 | 655 | 0
11427 | 13888 | 13.888 | 513 | 3.75
11428 | 13703 | 13.703 | 218 | 4.45
11429 | 13250 | 13.25 | 340 | 3.1
11430 | 14406 | 14.406 | -109 | 2.1
11431 | 14621 | 14.621 | 335 | 3.8
11432 | 14558 | 14.558 | 680 | 2.75
11433 | 14236 | 14.236 | -751 | 4.45
11434 | 14445 | 14.445 | 69 | 4.25
11435 | 14529 | 14.529 | -699 | 3
11436 | 11844 | 11.844 | -585 | 0.2
11437 | 11599 | 11.599 | -608 | 2.35
11438 | 10126 | 10.126 | -469 | 0.6
11439 | 10696 | 10.696 | 983 | 2.75
11440 | 10374 | 10.374 | -51 | 4.15
11441 | 10077 | 10.077 | 790 | 0.35
11442 | 10300 | 10.3 | 577 | 2.6
11443 | 9665 | 9.665 | 850 | 1.9
11444 | 8577 | 8.577 | -317 | 3.4
11445 | 8047 | 8.047 | -673 | 4.95
11446 | 7792 | 7.792 | -129 | 1.4
11447 | 8154 | 8.154 | -403 | 1.75
11448 | 7944 | 7.944 | -543 | 4.9
11449 | 8104 | 8.104 | 841 | 2.1
11450 | 8265 | 8.265 | 631 | 0.75
11451 | 9689 | 9.689 | -167 | 1.05
11452 | 12031 | 12.031 | 340 | 3.6
11453 | 13081 | 13.081 | -498 | 1.45
11454 | 13491 | 13.491 | 977 | 2.2
11455 | 12999 | 12.999 | -24 | 4.15
11456 | 12007 | 12.007 | -798 | 1.2
11457 | 11721 | 11.721 | 742 | 4.45
11458 | 10327 | 10.327 | 855 | 0.25
11459 | 12226 | 12.226 | -873 | 0.3
11460 | 12649 | 12.649 | 241 | 3.4
11461 | 12191 | 12.191 | -814 | 4.3
11462 | 11832 | 11.832 | 50 | 1
11463 | 10990 | 10.99 | -567 | 1.45
11464 | 1980 | 1.98 | 347 | 3.05
11465 | 0 | 0 | 904 | 0.65
11466 | 0 | 0 | -731 | 0.15
11467 | 0 | 0 | -22 | 3.2
11468 | 0 | 0 | -700 | 1.5
11469 | 0 | 0 | -896 | 3.75
11470 | 0 | 0 | -403 | 0.5
11471 | 0 | 0 | -403 | 2.55
11472 | 0 | 0 | -841 | 4.95
11473 | 0 | 0 | 624 | 4.65
11474 | 0 | 0 | 18 | 0.05
11475 | 0 | 0 | 795 | 4.65
11476 | 0 | 0 | -109 | 4.1
11477 | 0 | 0 | 88 | 1.3
11478 | 0 | 0 | 105 | 1.2
11479 | 0 | 0 | 278 | 2.1
11480 | 0 | 0 | -692 | 3.7
11481 | 0 | 0 | -630 | 2.65
11482 | 0 | 0 | -686 | 2.9
11483 | 0 | 0 | 48 | 2.65
11484 | 0 | 0 | -35 | 4.9
11485 | 0 | 0 | -295 | 2.05
11486 | 0 | 0 | -904 | 2.45
11487 | 0 | 0 | -282 | 0.65
11488 | 0 | 0 | -844 | 2.3
11489 | 0 | 0 | 126 | 1
11490 | 0 | 0 | -136 | 3.75
11491 | 0 | 0 | -318 | 0.25
11492 | 0 | 0 | -206 | 0.75
11493 | 0 | 0 | -5 | 2.75
11494 | 0 | 0 | 408 | 4
11495 | 0 | 0 | 384 | 2.85
11496 | 0 | 0 | -965 | 2.35
11497 | 0 | 0 | -366 | 1.05
11498 | 0 | 0 | 56 | 4.05
11499 | 0 | 0 | 646 | 1.35
11500 | 0 | 0 | -86 | 2.65
11501 | 0 | 0 | 802 | 2.05
11502 | 0 | 0 | 737 | 1.2
11503 | 0 | 0 | 738 | 4.8
11504 | 0 | 0 | -499 | 4.35
11505 | 0 | 0 | -946 | 2.6
11506 | 0 | 0 | 569 | 4.3
11507 | 0 | 0 | 41 | 0.55
11508 | 0 | 0 | -963 | 1.4
11509 | 0 | 0 | -106 | 2.35
11510 | 0 | 0 | -837 | 2.9
11511 | 0 | 0 | -207 | 4.85
11512 | 0 | 0 | 758 | 0.05
11513 | 0 | 0 | 83 | 2.6
11514 | 0 | 0 | -451 | 2.05
11515 | 0 | 0 | 869 | 1.2
11516 | 0 | 0 | -787 | 4.2
11517 | 0 | 0 | -10 | 1.1
11518 | 0 | 0 | 357 | 2.45
11519 | 0 | 0 | -627 | 0.3
11520 | 0 | 0 | -240 | 4.5
11521 | 0 | 0 | -727 | 3.25
11522 | 0 | 0 | -231 | 2.2
11523 | 0 | 0 | -346 | 0.9
11524 | 0 | 0 | -484 | 2.5
11525 | 0 | 0 | -247 | 4.9
11526 | 0 | 0 | -988 | 4.4
11527 | 0 | 0 | -408 | 5
11528 | 0 | 0 | -246 | 3.3
11529 | 0 | 0 | 784 | 2.7
11530 | 0 | 0 | 868 | 0.7
11531 | 0 | 0 | 759 | 2.25
11532 | 0 | 0 | -412 | 2.05
11533 | 0 | 0 | 876 | 2.3
11534 | 0 | 0 | -836 | 3.9
11535 | 0 | 0 | 323 | 0.15
11536 | 0 | 0 | -840 | 4.55
11537 | 0 | 0 | 713 | 0.2
11538 | 0 | 0 | 239 | 1.05
11539 | 0 | 0 | 540 | 4.05
11540 | 0 | 0 | 179 | 3.55
11541 | 0 | 0 | 517 | 2.7
11542 | 0 | 0 | 29 | 2.55
11543 | 0 | 0 | -689 | 4.7
11544 | 0 | 0 | 910 | 4.55
11545 | 0 | 0 | 823 | 0.95
11546 | 0 | 0 | 129 | 0.65
11547 | 0 | 0 | -415 | 1.85
11548 | 0 | 0 | 516 | 2.75
11549 | 0 | 0 | 41 | 0
11550 | 0 | 0 | 847 | 4.2
11551 | 0 | 0 | -679 | 2.25
11552 | 0 | 0 | -223 | 0.95
11553 | 0 | 0 | -103 | 4.05
11554 | 0 | 0 | -719 | 3.35
11555 | 0 | 0 | 400 | 3.7
11556 | 0 | 0 | -621 | 0.1
11557 | 0 | 0 | -121 | 0.7
11558 | 0 | 0 | 901 | 0.7
11559 | 0 | 0 | -990 | 0.6
11560 | 0 | 0 | -736 | 3.35
11561 | 0 | 0 | 959 | 4.7
11562 | 0 | 0 | -261 | 1.6
11563 | 0 | 0 | -137 | 4.3
11564 | 0 | 0 | -497 | 3.35
11565 | 0 | 0 | 119 | 1.15
11566 | 0 | 0 | 6 | 0.35
11567 | 0 | 0 | -72 | 2.15
11568 | 0 | 0 | -935 | 4.4
11569 | 0 | 0 | 817 | 0.6
11570 | 0 | 0 | 547 | 5
11571 | 0 | 0 | -929 | 2.05
11572 | 0 | 0 | 993 | 1.7
11573 | 0 | 0 | -276 | 4.45
11574 | 0 | 0 | 1000 | 2.2
11575 | 0 | 0 | 352 | 0.1
11576 | 0 | 0 | -265 | 3.3
11577 | 0 | 0 | 832 | 0.5
11578 | 0 | 0 | 52 | 1.15
11579 | 0 | 0 | -800 | 3.2
11580 | 0 | 0 | -266 | 3.3
11581 | 0 | 0 | 408 | 4.05
11582 | 0 | 0 | -48 | 2.35
11583 | 0 | 0 | 82 | 3.55
11584 | 0 | 0 | -6 | 2.95
11585 | 0 | 0 | -227 | 4.85
11586 | 0 | 0 | 577 | 4.15
11587 | 0 | 0 | -940 | 2.9
11588 | 0 | 0 | 659 | 4.05
11589 | 0 | 0 | 601 | 4.75
11590 | 0 | 0 | 808 | 1.4
11591 | 0 | 0 | 684 | 3.5
11592 | 0 | 0 | 835 | 2.35
11593 | 0 | 0 | -529 | 2.2
11594 | 0 | 0 | -530 | 3.9
11595 | 0 | 0 | -556 | 2.1
11596 | 0 | 0 | -21 | 1.05
11597 | 0 | 0 | 499 | 0.6
11598 | 0 | 0 | -96 | 1.6
11599 | 0 | 0 | 880 | 4.2
11600 | 0 | 0 | 143 | 3.3
11601 | 0 | 0 | 919 | 2.55
11602 | 0 | 0 | 334 | 1.9
11603 | 0 | 0 | 824 | 4.9
11604 | 0 | 0 | 277 | 3.75
11605 | 0 | 0 | -639 | 0.8
11606 | 0 | 0 | -264 | 4.95
11607 | 0 | 0 | 849 | 2.5
11608 | 0 | 0 | -723 | 3.05
11609 | 0 | 0 | -258 | 3.35
11610 | 0 | 0 | 714 | 1.9
11611 | 0 | 0 | -390 | 1.05
11612 | 0 | 0 | -402 | 2.9
11613 | 0 | 0 | -254 | 2.4
11614 | 0 | 0 | 454 | 1.45
11615 | 0 | 0 | 598 | 0.5
11616 | 0 | 0 | 528 | 0.85
11617 | 0 | 0 | -462 | 1
11618 | 0 | 0 | 495 | 0.8
11619 | 0 | 0 | 610 | 4.65
11620 | 0 | 0 | 523 | 1.8
11621 | 0 | 0 | 290 | 3.25
11622 | 0 | 0 | -802 | 1.7
11623 | 0 | 0 | -988 | 2.95
11624 | 0 | 0 | -252 | 3.1
11625 | 0 | 0 | -761 | 3.65
11626 | 0 | 0 | 736 | 2.7
11627 | 0 | 0 | 545 | 0.4
11628 | 0 | 0 | -421 | 1
11629 | 0 | 0 | 180 | 0
11630 | 0 | 0 | 548 | 2.05
11631 | 0 | 0 | 91 | 2
11632 | 0 | 0 | -854 | 0.3
11633 | 0 | 0 | 323 | 1.5
11634 | 0 | 0 | -722 | 3.25
11635 | 0 | 0 | -31 | 1.6
11636 | 0 | 0 | 747 | 4.3
11637 | 0 | 0 | -396 | 2.25
11638 | 0 | 0 | 373 | 2.4
11639 | 0 | 0 | 286 | 3.7
11640 | 0 | 0 | -368 | 4.15
11641 | 0 | 0 | -284 | 4.15
11642 | 0 | 0 | 700 | 2.35
11643 | 0 | 0 | -67 | 3.25
11644 | 0 | 0 | 635 | 1.6
11645 | 0 | 0 | -480 | 4.35
11646 | 0 | 0 | -616 | 4.6
11647 | 0 | 0 | 656 | 3.1
11648 | 0 | 0 | -68 | 3.9
11649 | 0 | 0 | -453 | 4.85
11650 | 0 | 0 | 714 | 3.45
11651 | 0 | 0 | -55 | 5
11652 | 0 | 0 | -39 | 0.6
11653 | 0 | 0 | 927 | 4.4
11654 | 0 | 0 | 289 | 3.7
11655 | 0 | 0 | 852 | 3.45
11656 | 0 | 0 | -975 | 1.85
11657 | 0 | 0 | -619 | 0.15
11658 | 0 | 0 | -823 | 0.5
11659 | 0 | 0 | -322 | 0
11660 | 0 | 0 | 273 | 0.75
11661 | 0 | 0 | -475 | 4.7
11662 | 0 | 0 | 93 | 2.3
11663 | 0 | 0 | -63 | 4.7
11664 | 0 | 0 | -160 | 3.1
11665 | 0 | 0 | 444 | 2.9
11666 | 0 | 0 | -799 | 1.3
11667 | 0 | 0 | -46 | 2.45
11668 | 0 | 0 | -468 | 0.55
11669 | 0 | 0 | 461 | 4.1
11670 | 0 | 0 | 347 | 3.5
11671 | 0 | 0 | -201 | 4.25
11672 | 0 | 0 | 744 | 4
11673 | 0 | 0 | 639 | 2
11674 | 0 | 0 | 878 | 0.4
11675 | 0 | 0 | -656 | 3.25
11676 | 0 | 0 | -497 | 2.4
11677 | 0 | 0 | -740 | 3
11678 | 0 | 0 | -186 | 1.9
11679 | 0 | 0 | 935 | 0.4
11680 | 0 | 0 | 330 | 0.65
11681 | 0 | 0 | 126 | 2.8
11682 | 0 | 0 | 824 | 4.65
11683 | 0 | 0 | -659 | 4.1
11684 | 0 | 0 | -310 | 0.75
11685 | 0 | 0 | 1 | 0.95
11686 | 0 | 0 | 837 | 3.3
11687 | 0 | 0 | 893 | 1.55
11688 | 0 | 0 | -878 | 1.1
11689 | 0 | 0 | -334 | 4.6
11690 | 0 | 0 | -545 | 0.85
11691 | 0 | 0 | -347 | 3.9
11692 | 0 | 0 | 776 | 4
11693 | 0 | 0 | -925 | 4.4
11694 | 0 | 0 | 131 | 0.6
11695 | 0 | 0 | 653 | 0.1
11696 | 0 | 0 | -121 | 0.2
11697 | 0 | 0 | 76 | 1.95
11698 | 0 | 0 | 774 | 4.85
11699 | 0 | 0 | 55 | 0.65
11700 | 0 | 0 | 679 | 2.65
11701 | 0 | 0 | -765 | 3.8
11702 | 0 | 0 | 508 | 2
11703 | 0 | 0 | 818 | 3
11704 | 0 | 0 | 806 | 0.55
11705 | 0 | 0 | -605 | 1.5
11706 | 0 | 0 | -136 | 3.25
11707 | 0 | 0 | 359 | 0.2
11708 | 0 | 0 | -63 | 2.9
11709 | 0 | 0 | -608 | 0.45
11710 | 0 | 0 | -167 | 4
11711 | 0 | 0 | -781 | 1.75
11712 | 0 | 0 | -613 | 4.7
11713 | 0 | 0 | 724 | 4.5
11714 | 0 | 0 | 91 | 0.95
11715 | 0 | 0 | 615 | 1.95
11716 | 0 | 0 | 492 | 0
11717 | 0 | 0 | -496 | 0.4
11718 | 0 | 0 | 677 | 2
11719 | 0 | 0 | 813 | 0
11720 | 0 | 0 | 429 | 3.75
11721 | 0 | 0 | 34 | 1.25
11722 | 0 | 0 | -117 | 4.3
11723 | 0 | 0 | 990 | 4.6
11724 | 0 | 0 | 196 | 1.4
11725 | 0 | 0 | 563 | 3
11726 | 0 | 0 | 52 | 4.85
11727 | 0 | 0 | -733 | 4.85
11728 | 0 | 0 | 758 | 4.05
11729 | 0 | 0 | -380 | 2.65
11730 | 0 | 0 | 614 | 1.9
11731 | 0 | 0 | 687 | 1.5
11732 | 0 | 0 | 822 | 3.65
11733 | 0 | 0 | -861 | 0.5
11734 | 0 | 0 | -913 | 2.05
11735 | 0 | 0 | 309 | 4.8
11736 | 0 | 0 | 75 | 2.55
11737 | 0 | 0 | -169 | 4.7
11738 | 0 | 0 | 758 | 3.9
11739 | 0 | 0 | -534 | 1.35
11740 | 0 | 0 | -992 | 2.75
11741 | 0 | 0 | -174 | 0.3
11742 | 0 | 0 | -910 | 1.1
11743 | 0 | 0 | -737 | 4.9
11744 | 0 | 0 | 893 | 1.1
11745 | 0 | 0 | -746 | 3.6
11746 | 0 | 0 | 435 | 3.2
11747 | 0 | 0 | -825 | 3.35
11748 | 0 | 0 | 325 | 0.6
11749 | 0 | 0 | -338 | 0.7
11750 | 0 | 0 | 678 | 4.4
11751 | 0 | 0 | 896 | 1.45
11752 | 0 | 0 | -402 | 1.15
11753 | 0 | 0 | 333 | 3
11754 | 0 | 0 | -840 | 0.5
11755 | 0 | 0 | -625 | 0.5
11756 | 0 | 0 | 870 | 2.05
11757 | 0 | 0 | -683 | 4.35
11758 | 0 | 0 | 766 | 1
11759 | 0 | 0 | 205 | 4.1
11760 | 0 | 0 | 835 | 1.8
11761 | 0 | 0 | -103 | 2.5
11762 | 0 | 0 | -116 | 1.6
11763 | 0 | 0 | -888 | 1.9
11764 | 0 | 0 | 755 | 2.45
11765 | 0 | 0 | 278 | 2.3
11766 | 0 | 0 | -534 | 0
11767 | 0 | 0 | 698 | 2.7
11768 | 0 | 0 | 233 | 0.5
11769 | 0 | 0 | 65 | 4.65
11770 | 0 | 0 | -22 | 3.65
11771 | 0 | 0 | -460 | 1
11772 | 0 | 0 | 708 | 2.25
11773 | 0 | 0 | -44 | 2.05
11774 | 0 | 0 | -387 | 3.9
11775 | 0 | 0 | -642 | 2
11776 | 0 | 0 | -918 | 4.6
11777 | 0 | 0 | -592 | 3.2
11778 | 0 | 0 | -281 | 4
11779 | 0 | 0 | -144 | 3.2
11780 | 0 | 0 | 285 | 4.1
11781 | 0 | 0 | -508 | 1.3
11782 | 0 | 0 | 700 | 3.4
11783 | 0 | 0 | -151 | 0.45
11784 | 0 | 0 | 398 | 0.8
11785 | 0 | 0 | 482 | 4.6
11786 | 0 | 0 | -526 | 3.95
11787 | 0 | 0 | -630 | 3.65
11788 | 0 | 0 | 706 | 3.45
11789 | 0 | 0 | 610 | 3.05
11790 | 0 | 0 | 157 | 1.4
11791 | 0 | 0 | -659 | 4.75
11792 | 0 | 0 | -75 | 1.1
11793 | 0 | 0 | 792 | 3.1
11794 | 0 | 0 | 100 | 1.25
11795 | 0 | 0 | 318 | 0.15
11796 | 0 | 0 | -714 | 3.05
11797 | 0 | 0 | -798 | 4.55
11798 | 0 | 0 | -868 | 4.6
11799 | 0 | 0 | -527 | 4.15
11800 | 0 | 0 | 101 | 4.8
11801 | 0 | 0 | 89 | 0.15
11802 | 0 | 0 | 801 | 0
11803 | 0 | 0 | -203 | 0.65
11804 | 0 | 0 | 450 | 3
11805 | 0 | 0 | -64 | 3.1
11806 | 0 | 0 | -547 | 1.8
11807 | 0 | 0 | -799 | 3.55
11808 | 0 | 0 | 798 | 1.4
11809 | 0 | 0 | -806 | 0.4
11810 | 0 | 0 | -71 | 0.75
11811 | 0 | 0 | 103 | 0.9
11812 | 0 | 0 | 536 | 1.1
11813 | 0 | 0 | 408 | 0.15
11814 | 0 | 0 | 161 | 4.1
11815 | 0 | 0 | -429 | 1.2
11816 | 0 | 0 | 601 | 1.85
11817 | 0 | 0 | 347 | 2.55
11818 | 0 | 0 | -527 | 2.4
11819 | 0 | 0 | 468 | 2.6
11820 | 0 | 0 | 965 | 1.15
11821 | 0 | 0 | -970 | 3.1
11822 | 0 | 0 | -247 | 4.5
11823 | 0 | 0 | 702 | 0.65
11824 | 0 | 0 | 983 | 1.35
11825 | 0 | 0 | -790 | 2.2
11826 | 0 | 0 | -126 | 5
11827 | 0 | 0 | -186 | 3.35
11828 | 0 | 0 | -729 | 2.85
11829 | 0 | 0 | 840 | 3.15
11830 | 0 | 0 | -564 | 3.65
11831 | 0 | 0 | 318 | 0.65
11832 | 0 | 0 | -537 | 2
11833 | 0 | 0 | 96 | 3.65
11834 | 0 | 0 | -357 | 4.25
11835 | 0 | 0 | 980 | 4.25
11836 | 0 | 0 | 813 | 3.15
11837 | 0 | 0 | -119 | 3.9
11838 | 0 | 0 | 898 | 3.7
11839 | 0 | 0 | -981 | 0.45
11840 | 0 | 0 | 816 | 2.55
11841 | 0 | 0 | 839 | 4.8
11842 | 0 | 0 | 147 | 1.4
11843 | 0 | 0 | -157 | 4.6
11844 | 0 | 0 | -610 | 4.55
11845 | 0 | 0 | 233 | 4.4
11846 | 0 | 0 | 22 | 0.75
11847 | 0 | 0 | -405 | 3.15
11848 | 0 | 0 | -169 | 3.3
11849 | 0 | 0 | -75 | 2.4
11850 | 0 | 0 | 897 | 4.6
11851 | 0 | 0 | -724 | 1.7
11852 | 0 | 0 | 121 | 1.95
11853 | 0 | 0 | -945 | 4.5
11854 | 0 | 0 | -922 | 1.2
11855 | 0 | 0 | 546 | 1.2
11856 | 0 | 0 | 277 | 1.85
11857 | 0 | 0 | -383 | 2.7
11858 | 0 | 0 | -935 | 3.1
11859 | 0 | 0 | 720 | 0.7
11860 | 0 | 0 | 116 | 0.6
11861 | 0 | 0 | -622 | 4.95
11862 | 0 | 0 | -190 | 0.35
11863 | 0 | 0 | -907 | 4.1
11864 | 0 | 0 | 841 | 2.8
11865 | 0 | 0 | 375 | 4.3
11866 | 0 | 0 | 789 | 0.7
11867 | 0 | 0 | -737 | 2.2
11868 | 0 | 0 | -291 | 2.45
11869 | 0 | 0 | 978 | 1.75
11870 | 0 | 0 | -91 | 1.95
11871 | 0 | 0 | 301 | 3.3
11872 | 0 | 0 | -641 | 3.35
11873 | 0 | 0 | 523 | 1.5
11874 | 0 | 0 | -220 | 0.5
11875 | 0 | 0 | 500 | 0.4
11876 | 0 | 0 | 426 | 3.05
11877 | 0 | 0 | 663 | 4.85
11878 | 0 | 0 | 815 | 1.3
11879 | 0 | 0 | 992 | 1
11880 | 0 | 0 | 280 | 3.15
11881 | 0 | 0 | 967 | 2.35
11882 | 0 | 0 | 773 | 1.45
11883 | 0 | 0 | 105 | 1.65
11884 | 0 | 0 | -265 | 3.7
11885 | 0 | 0 | 385 | 3.65
11886 | 0 | 0 | -334 | 1.65
11887 | 0 | 0 | -867 | 1.25
11888 | 0 | 0 | 517 | 0.05
11889 | 0 | 0 | 12 | 1.15
11890 | 0 | 0 | -502 | 1.4
11891 | 0 | 0 | -232 | 1.45
11892 | 0 | 0 | -424 | 4.6
11893 | 0 | 0 | 970 | 0.5
11894 | 0 | 0 | 527 | 4.65
11895 | 0 | 0 | -813 | 2.15
11896 | 0 | 0 | -63 | 0.25
11897 | 0 | 0 | -729 | 0.05
11898 | 0 | 0 | -808 | 0.2
11899 | 0 | 0 | 770 | 0.05
11900 | 0 | 0 | 950 | 0.6
11901 | 0 | 0 | -127 | 1.5
11902 | 0 | 0 | 47 | 1.05
11903 | 0 | 0 | 42 | 1.2
11904 | 0 | 0 | 820 | 4.65
11905 | 0 | 0 | -589 | 2.25
11906 | 0 | 0 | -65 | 4.05
11907 | 0 | 0 | -799 | 1.05
11908 | 0 | 0 | -195 | 4.25
11909 | 0 | 0 | -740 | 4.15
11910 | 0 | 0 | -503 | 0.85
11911 | 0 | 0 | -860 | 3.85
11912 | 0 | 0 | 472 | 4.35
11913 | 0 | 0 | 537 | 4.1
11914 | 0 | 0 | 291 | 0.95
11915 | 0 | 0 | -239 | 2.65
11916 | 0 | 0 | -234 | 1.7
11917 | 0 | 0 | 478 | 0.1
11918 | 0 | 0 | 353 | 0.6
11919 | 0 | 0 | 670 | 1.65
11920 | 0 | 0 | -324 | 3.85
11921 | 0 | 0 | 1 | 3.25
11922 | 0 | 0 | 80 | 0.15
11923 | 0 | 0 | -113 | 2.2
11924 | 0 | 0 | -120 | 4.05
11925 | 0 | 0 | 762 | 1.55
11926 | 0 | 0 | 787 | 3.4
11927 | 0 | 0 | -444 | 4.95
11928 | 0 | 0 | -15 | 2.8
11929 | 0 | 0 | 529 | 4.75
11930 | 0 | 0 | -389 | 2.1
11931 | 0 | 0 | -96 | 4.9
11932 | 0 | 0 | 595 | 0.4
11933 | 0 | 0 | 614 | 0.85
11934 | 0 | 0 | 905 | 2.25
11935 | 0 | 0 | -693 | 0.25
11936 | 0 | 0 | -841 | 3.75
11937 | 0 | 0 | -704 | 1.45
11938 | 0 | 0 | 971 | 4.3
11939 | 0 | 0 | 284 | 1.9
11940 | 0 | 0 | -16 | 2.45
11941 | 0 | 0 | 51 | 2.5
11942 | 0 | 0 | 133 | 1.95
11943 | 0 | 0 | 749 | 1.5
11944 | 0 | 0 | 605 | 4.25
11945 | 0 | 0 | 153 | 3.5
11946 | 0 | 0 | 216 | 3.9
11947 | 0 | 0 | 493 | 4.2
11948 | 0 | 0 | -618 | 4.4
11949 | 0 | 0 | 464 | 2.45
11950 | 0 | 0 | 460 | 3.8
11951 | 0 | 0 | 650 | 2.55
11952 | 0 | 0 | 844 | 4.55
11953 | 0 | 0 | -910 | 4.1
11954 | 0 | 0 | 305 | 4.45
11955 | 0 | 0 | -258 | 2.1
11956 | 0 | 0 | -858 | 0.85
11957 | 0 | 0 | -470 | 0.55
11958 | 0 | 0 | -876 | 3.1
11959 | 0 | 0 | 57 | 3.6
11960 | 0 | 0 | -890 | 2.8
11961 | 0 | 0 | 632 | 3.1
11962 | 0 | 0 | 85 | 1
11963 | 0 | 0 | 544 | 3
11964 | 0 | 0 | -120 | 4.9
11965 | 0 | 0 | 81 | 2.8
11966 | 0 | 0 | -962 | 2.45
11967 | 0 | 0 | -756 | 1.3
11968 | 0 | 0 | -32 | 1.9
11969 | 0 | 0 | -933 | 1.35
11970 | 0 | 0 | 383 | 4.5
11971 | 0 | 0 | 403 | 0.5
11972 | 0 | 0 | -810 | 1.35
11973 | 0 | 0 | 860 | 3.4
11974 | 0 | 0 | -250 | 1.2
11975 | 0 | 0 | 428 | 3.15
11976 | 0 | 0 | 920 | 1.5
11977 | 0 | 0 | 931 | 1.5
11978 | 0 | 0 | 515 | 1.1
11979 | 0 | 0 | 619 | 4.05
11980 | 0 | 0 | -771 | 2.4
11981 | 0 | 0 | -15 | 0.6
11982 | 0 | 0 | 744 | 1.4
11983 | 0 | 0 | 368 | 3.1
11984 | 0 | 0 | -768 | 0.5
11985 | 0 | 0 | 569 | 4.4
11986 | 0 | 0 | -987 | 1.65
11987 | 0 | 0 | -845 | 3.15
11988 | 0 | 0 | 197 | 1.95
11989 | 0 | 0 | -627 | 3.35
11990 | 0 | 0 | 363 | 4.75
11991 | 0 | 0 | 165 | 4.9
11992 | 0 | 0 | -134 | 1.2
11993 | 0 | 0 | -910 | 2.7
11994 | 0 | 0 | 681 | 1.15
11995 | 0 | 0 | 491 | 2.75
11996 | 0 | 0 | -435 | 2.45
11997 | 0 | 0 | 549 | 4.2
11998 | 0 | 0 | -537 | 4.25
11999 | 0 | 0 | 612 | 1.65
12000 | 0 | 0 | -541 | 0.6
12001 | 0 | 0 | 294 | 2.9
12002 | 0 | 0 | 969 | 0.2
12003 | 0 | 0 | -182 | 0.85
12004 | 0 | 0 | 145 | 4.95
12005 | 0 | 0 | -432 | 3.5
12006 | 0 | 0 | 106 | 2.3
12007 | 0 | 0 | 583 | 4.6
12008 | 0 | 0 | 230 | 1.65
12009 | 0 | 0 | -934 | 3.25
12010 | 0 | 0 | -303 | 0.25
12011 | 0 | 0 | -903 | 1
12012 | 0 | 0 | 341 | 3.45
12013 | 0 | 0 | -785 | 0.2
12014 | 0 | 0 | 585 | 1.1
12015 | 0 | 0 | -916 | 2.6
12016 | 0 | 0 | -374 | 3.6
12017 | 0 | 0 | 143 | 3.9
12018 | 0 | 0 | -803 | 0.5
12019 | 0 | 0 | 372 | 1.15
12020 | 0 | 0 | 453 | 0.75
12021 | 0 | 0 | -272 | 1.35
12022 | 0 | 0 | -182 | 0.3
12023 | 0 | 0 | 534 | 2.95
12024 | 0 | 0 | -608 | 2.15
12025 | 0 | 0 | -165 | 1.45
12026 | 0 | 0 | 520 | 3.4
12027 | 0 | 0 | 319 | 1.25
12028 | 0 | 0 | 408 | 3.65
12029 | 0 | 0 | 819 | 0.75
12030 | 0 | 0 | -547 | 2.75
12031 | 0 | 0 | -568 | 4.5
12032 | 0 | 0 | 467 | 3.65
12033 | 0 | 0 | -950 | 2.9
12034 | 0 | 0 | -723 | 0.95
12035 | 0 | 0 | -890 | 0.3
12036 | 0 | 0 | -201 | 3.1
12037 | 0 | 0 | -507 | 0
12038 | 0 | 0 | -472 | 2.55
12039 | 0 | 0 | -688 | 0.55
12040 | 0 | 0 | 811 | 0.25
12041 | 0 | 0 | 118 | 0.85
12042 | 0 | 0 | 875 | 2.25
12043 | 0 | 0 | 888 | 0.3
12044 | 0 | 0 | 675 | 2.65
12045 | 0 | 0 | -477 | 1.25
12046 | 0 | 0 | -822 | 0.25
12047 | 0 | 0 | 643 | 3.25
12048 | 0 | 0 | -813 | 3.15
12049 | 0 | 0 | 32 | 2.8
12050 | 0 | 0 | -941 | 2.4
12051 | 0 | 0 | -735 | 4
12052 | 0 | 0 | -604 | 0.4
12053 | 0 | 0 | 957 | 4.1
12054 | 0 | 0 | -56 | 4.2
12055 | 0 | 0 | -413 | 4.35
12056 | 0 | 0 | -248 | 4.2
12057 | 0 | 0 | 481 | 1.45
12058 | 0 | 0 | 51 | 3.1
12059 | 0 | 0 | 861 | 1.65
12060 | 0 | 0 | -52 | 2.75
12061 | 0 | 0 | -647 | 4.2
12062 | 0 | 0 | 478 | 2.45
12063 | 0 | 0 | -387 | 4.75
12064 | 0 | 0 | -378 | 4.25
12065 | 0 | 0 | 475 | 2.15
12066 | 0 | 0 | 836 | 0.05
12067 | 0 | 0 | 336 | 3.9
12068 | 0 | 0 | 310 | 2.45
12069 | 0 | 0 | -817 | 1.2
12070 | 0 | 0 | -366 | 1.05
12071 | 0 | 0 | 401 | 5
12072 | 0 | 0 | 933 | 2.3
12073 | 0 | 0 | 99 | 1.5
12074 | 0 | 0 | -872 | 0.45
12075 | 0 | 0 | 82 | 4.25
12076 | 0 | 0 | 989 | 1
12077 | 0 | 0 | 163 | 2.1
12078 | 0 | 0 | -369 | 2.6
12079 | 0 | 0 | 23 | 2.8
12080 | 0 | 0 | -899 | 1.45
12081 | 0 | 0 | 803 | 3.85
12082 | 0 | 0 | -642 | 1.75
12083 | 0 | 0 | -958 | 4.6
12084 | 0 | 0 | -559 | 4.7
12085 | 0 | 0 | 39 | 4.75
12086 | 0 | 0 | -562 | 1.85
12087 | 0 | 0 | 372 | 0.1
12088 | 0 | 0 | -555 | 0.35
12089 | 0 | 0 | -459 | 2.3
12090 | 0 | 0 | 345 | 4.55
12091 | 0 | 0 | 213 | 0.95
12092 | 0 | 0 | -633 | 1.95
12093 | 0 | 0 | 579 | 1.4
12094 | 0 | 0 | -406 | 4.3
12095 | 0 | 0 | 258 | 1.5
12096 | 0 | 0 | -886 | 1.7
12097 | 0 | 0 | -296 | 3.45
12098 | 0 | 0 | 984 | 0.15
12099 | 0 | 0 | 36 | 3.8
12100 | 0 | 0 | 433 | 1.8
12101 | 0 | 0 | -574 | 1.4
12102 | 0 | 0 | -602 | 4.65
12103 | 0 | 0 | 640 | 2.3
12104 | 0 | 0 | -43 | 2.55
12105 | 0 | 0 | -593 | 4.6
12106 | 0 | 0 | 933 | 3.4
12107 | 0 | 0 | 240 | 0.75
12108 | 0 | 0 | 86 | 0.6
12109 | 0 | 0 | 498 | 0.3
12110 | 0 | 0 | -675 | 4
12111 | 0 | 0 | 904 | 1.45
12112 | 0 | 0 | 391 | 1.95
12113 | 0 | 0 | -984 | 2.1
12114 | 0 | 0 | 698 | 1.7
12115 | 0 | 0 | 406 | 1.5
12116 | 0 | 0 | -417 | 2.9
12117 | 0 | 0 | 655 | 1.3
12118 | 0 | 0 | -53 | 0.6
12119 | 0 | 0 | -807 | 4.45
12120 | 0 | 0 | -783 | 0.45
12121 | 0 | 0 | -251 | 3.05
12122 | 0 | 0 | 399 | 0.15
12123 | 0 | 0 | -799 | 2.6
12124 | 0 | 0 | -644 | 4.7
12125 | 0 | 0 | 399 | 0.55
12126 | 0 | 0 | 801 | 4.7
12127 | 0 | 0 | -716 | 4.6
12128 | 0 | 0 | -952 | 3.65
12129 | 0 | 0 | 511 | 1.2
12130 | 0 | 0 | 369 | 0.55
12131 | 0 | 0 | -736 | 0.85
12132 | 0 | 0 | 784 | 5
12133 | 0 | 0 | 26 | 1.2
12134 | 0 | 0 | -568 | 0.35
12135 | 0 | 0 | 130 | 3.3
12136 | 0 | 0 | 365 | 3
12137 | 0 | 0 | -68 | 4.3
12138 | 0 | 0 | -180 | 1.4
12139 | 0 | 0 | 119 | 4.4
12140 | 0 | 0 | -99 | 4.3
12141 | 0 | 0 | -167 | 4.1
12142 | 0 | 0 | 642 | 1.85
12143 | 0 | 0 | 406 | 1.8
12144 | 0 | 0 | 845 | 4
12145 | 0 | 0 | -799 | 3.9
12146 | 0 | 0 | 402 | 4.45
12147 | 0 | 0 | -668 | 1.55
12148 | 0 | 0 | -334 | 1.45
12149 | 0 | 0 | 401 | 0.85
12150 | 0 | 0 | -443 | 5
12151 | 0 | 0 | 149 | 2.25
12152 | 0 | 0 | -710 | 0.45
12153 | 0 | 0 | -961 | 1.1
12154 | 0 | 0 | -951 | 4.75
12155 | 0 | 0 | -860 | 0.95
12156 | 0 | 0 | -463 | 1
12157 | 0 | 0 | -634 | 2.85
12158 | 0 | 0 | -504 | 2.95
12159 | 0 | 0 | -897 | 0.65
12160 | 0 | 0 | -794 | 4.1
12161 | 0 | 0 | -148 | 3.55
12162 | 0 | 0 | -112 | 3.15
12163 | 0 | 0 | -930 | 4.75
12164 | 0 | 0 | 951 | 1.75
12165 | 0 | 0 | -946 | 4.25
12166 | 0 | 0 | -24 | 3.2
12167 | 0 | 0 | 156 | 0
12168 | 0 | 0 | 615 | 0.45
12169 | 0 | 0 | 259 | 3.6
12170 | 0 | 0 | -139 | 1.75
12171 | 0 | 0 | -526 | 4.7
12172 | 0 | 0 | 474 | 2.25
12173 | 0 | 0 | 330 | 3.95
12174 | 0 | 0 | 227 | 2.8
12175 | 0 | 0 | -553 | 2.4
12176 | 0 | 0 | 297 | 2.85
12177 | 0 | 0 | 991 | 3.8
12178 | 0 | 0 | -758 | 0.05
12179 | 0 | 0 | -635 | 2.9
12180 | 0 | 0 | -446 | 2
12181 | 0 | 0 | 665 | 3.1
12182 | 0 | 0 | 744 | 1.7
12183 | 0 | 0 | 345 | 4.7
12184 | 0 | 0 | -177 | 1.8
12185 | 0 | 0 | 543 | 1.4
12186 | 0 | 0 | -456 | 4.1
12187 | 0 | 0 | -461 | 2
12188 | 0 | 0 | -384 | 3.4
12189 | 0 | 0 | -432 | 4
12190 | 0 | 0 | 12 | 4.3
12191 | 0 | 0 | 442 | 1.1
12192 | 0 | 0 | 245 | 0.6
12193 | 0 | 0 | -220 | 4.1
12194 | 0 | 0 | -885 | 2
12195 | 0 | 0 | 288 | 1.8
12196 | 0 | 0 | -68 | 0.7
12197 | 0 | 0 | 922 | 4.45
12198 | 0 | 0 | 999 | 4.95
12199 | 0 | 0 | 67 | 4.85
12200 | 0 | 0 | -524 | 3.5
12201 | 0 | 0 | 453 | 3.05
12202 | 0 | 0 | -542 | 4.9
12203 | 0 | 0 | 548 | 3.5
12204 | 0 | 0 | 664 | 2.45
12205 | 0 | 0 | -179 | 0.1
12206 | 0 | 0 | 130 | 0.8
12207 | 0 | 0 | 193 | 4.2
12208 | 0 | 0 | 853 | 0.15
12209 | 0 | 0 | 540 | 1.25
12210 | 0 | 0 | -466 | 1.95
12211 | 0 | 0 | -823 | 0.45
12212 | 0 | 0 | 18 | 0.25
12213 | 0 | 0 | -843 | 3.1
12214 | 0 | 0 | -96 | 0.05
12215 | 0 | 0 | 285 | 3
12216 | 0 | 0 | 138 | 4.6
12217 | 0 | 0 | -230 | 2.6
12218 | 0 | 0 | -822 | 1.45
12219 | 0 | 0 | 892 | 0.55
12220 | 0 | 0 | -383 | 1.7
12221 | 0 | 0 | -761 | 3.35
12222 | 0 | 0 | 394 | 0.65
12223 | 0 | 0 | 119 | 3.55
12224 | 0 | 0 | 360 | 3.5
12225 | 0 | 0 | 359 | 1.4
12226 | 0 | 0 | -834 | 3.85
12227 | 0 | 0 | 815 | 3.9
12228 | 0 | 0 | -486 | 1.15
12229 | 0 | 0 | 774 | 4.2
12230 | 0 | 0 | -619 | 3.3
12231 | 0 | 0 | 991 | 3.65
12232 | 0 | 0 | 544 | 4.9
12233 | 0 | 0 | 156 | 1.35
12234 | 0 | 0 | -668 | 3.7
12235 | 0 | 0 | 52 | 1.9
12236 | 0 | 0 | 202 | 3.6
12237 | 0 | 0 | 178 | 2.45
12238 | 0 | 0 | -915 | 3.3
12239 | 0 | 0 | -312 | 1.9
12240 | 0 | 0 | 786 | 0.15
12241 | 0 | 0 | -759 | 1.65
12242 | 0 | 0 | -443 | 4.7
12243 | 0 | 0 | 678 | 1.8
12244 | 0 | 0 | -336 | 0.55
12245 | 0 | 0 | 341 | 2.7
12246 | 0 | 0 | 915 | 1.5
12247 | 0 | 0 | 718 | 4.45
12248 | 0 | 0 | -528 | 4.4
12249 | 0 | 0 | 584 | 0.95
12250 | 0 | 0 | 355 | 3.95
12251 | 0 | 0 | 162 | 1.65
12252 | 0 | 0 | -474 | 3.25
12253 | 0 | 0 | 165 | 1.05
12254 | 0 | 0 | -93 | 2.95
12255 | 0 | 0 | 886 | 1.7
12256 | 0 | 0 | -478 | 3.85
12257 | 0 | 0 | -60 | 0.85
12258 | 0 | 0 | -815 | 4.55
12259 | 0 | 0 | -347 | 3.25
12260 | 0 | 0 | -745 | 4
12261 | 0 | 0 | 708 | 2.6
12262 | 0 | 0 | -48 | 0.75
12263 | 0 | 0 | -653 | 1.35
12264 | 0 | 0 | 209 | 0.55
12265 | 0 | 0 | 853 | 1.15
12266 | 0 | 0 | 18 | 0.3
12267 | 0 | 0 | -537 | 0.95
12268 | 0 | 0 | 318 | 1.7
12269 | 0 | 0 | 141 | 0
12270 | 0 | 0 | -517 | 1.1
12271 | 0 | 0 | 1000 | 4.45
12272 | 0 | 0 | 927 | 3.1
12273 | 0 | 0 | 778 | 3.2
12274 | 0 | 0 | 608 | 0.3
12275 | 0 | 0 | 449 | 0.05
12276 | 0 | 0 | -252 | 2.05
12277 | 0 | 0 | -95 | 3.6
12278 | 0 | 0 | 742 | 4.2
12279 | 0 | 0 | -633 | 2.75
12280 | 0 | 0 | -78 | 3.1
12281 | 0 | 0 | 967 | 3.3
12282 | 0 | 0 | -341 | 0
12283 | 0 | 0 | -14 | 0.8
12284 | 0 | 0 | 887 | 4.6
12285 | 0 | 0 | 927 | 0.95
12286 | 0 | 0 | -736 | 5
12287 | 0 | 0 | -616 | 4.1
12288 | 0 | 0 | -764 | 4.1
12289 | 0 | 0 | -136 | 2.6
12290 | 0 | 0 | 746 | 3.15
12291 | 0 | 0 | -271 | 1.55
12292 | 0 | 0 | -95 | 4.85
12293 | 0 | 0 | 868 | 1.35
12294 | 0 | 0 | 246 | 1.1
12295 | 0 | 0 | 308 | 0.05
12296 | 0 | 0 | 796 | 0.7
12297 | 0 | 0 | 253 | 4.9
12298 | 0 | 0 | 796 | 4.25
12299 | 0 | 0 | 717 | 1.3
12300 | 0 | 0 | -915 | 5
12301 | 0 | 0 | 583 | 1.8
12302 | 0 | 0 | -827 | 3.1
12303 | 0 | 0 | 25 | 1.5
12304 | 0 | 0 | 654 | 3.6
12305 | 0 | 0 | -128 | 2.5
12306 | 0 | 0 | -601 | 0.55
12307 | 0 | 0 | 645 | 1.05
12308 | 0 | 0 | -221 | 2.5
12309 | 0 | 0 | 220 | 4.65
12310 | 0 | 0 | 456 | 0.55
12311 | 0 | 0 | 627 | 1.15
12312 | 0 | 0 | -268 | 3.65
12313 | 0 | 0 | -645 | 4.4
12314 | 0 | 0 | 176 | 1.05
12315 | 0 | 0 | 381 | 3.85
12316 | 0 | 0 | -191 | 4.4
12317 | 0 | 0 | 903 | 4.35
12318 | 0 | 0 | -748 | 4.85
12319 | 0 | 0 | 516 | 3.9
12320 | 0 | 0 | 286 | 4.5
12321 | 0 | 0 | 522 | 4.3
12322 | 0 | 0 | -791 | 3.8
12323 | 0 | 0 | -548 | 3.5
12324 | 0 | 0 | 183 | 1.3
12325 | 0 | 0 | -292 | 2.65
12326 | 0 | 0 | 843 | 4.35
12327 | 0 | 0 | 573 | 3.2
12328 | 0 | 0 | 65 | 2.65
12329 | 0 | 0 | 307 | 4.95
12330 | 0 | 0 | 901 | 3.35
12331 | 0 | 0 | 909 | 0.35
12332 | 0 | 0 | -867 | 2.2
12333 | 0 | 0 | -353 | 0.9
12334 | 0 | 0 | -782 | 1.5
12335 | 0 | 0 | -459 | 0.85
12336 | 0 | 0 | 923 | 3.75
12337 | 0 | 0 | 966 | 1.7
12338 | 0 | 0 | 339 | 1.5
12339 | 0 | 0 | -691 | 4.15
12340 | 0 | 0 | -102 | 4.1
12341 | 0 | 0 | 537 | 5
12342 | 0 | 0 | -565 | 1.8
12343 | 0 | 0 | -316 | 0.65
12344 | 0 | 0 | 848 | 2.85
12345 | 251 | 0.251 | 171 | 2.4
12346 | 696 | 0.696 | -574 | 4.85
12347 | 1297 | 1.297 | -570 | 3.85
12348 | 2946 | 2.946 | 442 | 4.4
12349 | 7320 | 7.32 | -576 | 0.2
12350 | 9323 | 9.323 | -80 | 4
12351 | 9613 | 9.613 | -86 | 2.3
12352 | 11263 | 11.263 | 259 | 1.55
12353 | 13334 | 13.334 | 760 | 4
12354 | 14509 | 14.509 | -358 | 1.4
12355 | 14350 | 14.35 | 39 | 0.4
12356 | 14241 | 14.241 | 1000 | 2.9
12357 | 14167 | 14.167 | 257 | 0.3
12358 | 14253 | 14.253 | -980 | 3.1
12359 | 14248 | 14.248 | 574 | 1.85
12360 | 14388 | 14.388 | 326 | 3.25
12361 | 14330 | 14.33 | 634 | 1.5
12362 | 14446 | 14.446 | 250 | 3.5
12363 | 14261 | 14.261 | -13 | 4.1
12364 | 14308 | 14.308 | -884 | 4.3
12365 | 14157 | 14.157 | -283 | 0.95
12366 | 14242 | 14.242 | 168 | 2.35
12367 | 14214 | 14.214 | 843 | 1.4
12368 | 14260 | 14.26 | -248 | 1.65
12369 | 14330 | 14.33 | -480 | 0.7
12370 | 14530 | 14.53 | 496 | 4.25
12371 | 14286 | 14.286 | -855 | 2.05
12372 | 14468 | 14.468 | 905 | 1.8
12373 | 14533 | 14.533 | -693 | 2.5
12374 | 14604 | 14.604 | 889 | 0.7
12375 | 14448 | 14.448 | -691 | 0.3
12376 | 14576 | 14.576 | 529 | 1.5
12377 | 14441 | 14.441 | -139 | 1.6
12378 | 14580 | 14.58 | -959 | 4.65
12379 | 14596 | 14.596 | 774 | 3.6
12380 | 14618 | 14.618 | 7 | 2.65
12381 | 14592 | 14.592 | -13 | 1.25
12382 | 14608 | 14.608 | -51 | 1.55
12383 | 14497 | 14.497 | -715 | 4
12384 | 14654 | 14.654 | 771 | 0.35
12385 | 13784 | 13.784 | -9 | 2.3
12386 | 13787 | 13.787 | 100 | 2.8
12387 | 14589 | 14.589 | 562 | 3
12388 | 14730 | 14.73 | 380 | 0.8
12389 | 14639 | 14.639 | 855 | 4.8
12390 | 14853 | 14.853 | 249 | 4.05
12391 | 14455 | 14.455 | -615 | 4.2
12392 | 14804 | 14.804 | 755 | 0.5
12393 | 14792 | 14.792 | 552 | 1.75
12394 | 14660 | 14.66 | 238 | 1.3
12395 | 14703 | 14.703 | 345 | 2.65
12396 | 14693 | 14.693 | 989 | 3.05
12397 | 14636 | 14.636 | 976 | 2.65
12398 | 14632 | 14.632 | -614 | 2.95
12399 | 14657 | 14.657 | 220 | 3.6
12400 | 14508 | 14.508 | -21 | 4.35
12401 | 14632 | 14.632 | -246 | 0.65
12402 | 14450 | 14.45 | 108 | 3.35
12403 | 14452 | 14.452 | -70 | 1.05
12404 | 14472 | 14.472 | -443 | 3.4
12405 | 14359 | 14.359 | -765 | 0.45
12406 | 14470 | 14.47 | -235 | 4.65
12407 | 14434 | 14.434 | 567 | 1.9
12408 | 14468 | 14.468 | 135 | 2.2
12409 | 14458 | 14.458 | -899 | 4.9
12410 | 14438 | 14.438 | -420 | 3.4
12411 | 14530 | 14.53 | -990 | 0.1
12412 | 14304 | 14.304 | -694 | 4
12413 | 14258 | 14.258 | 595 | 1.4
12414 | 14332 | 14.332 | 555 | 4.55
12415 | 14101 | 14.101 | -180 | 0.35
12416 | 14231 | 14.231 | -493 | 1.1
12417 | 14094 | 14.094 | -394 | 3.7
12418 | 14129 | 14.129 | -315 | 3.85
12419 | 14153 | 14.153 | -532 | 4.15
12420 | 14133 | 14.133 | 860 | 4.3
12421 | 14221 | 14.221 | -312 | 1
12422 | 14352 | 14.352 | 60 | 3.5
12423 | 14352 | 14.352 | 571 | 1.35
12424 | 14517 | 14.517 | 873 | 0.95
12425 | 14461 | 14.461 | -232 | 1.6
12426 | 14624 | 14.624 | -519 | 1.1
12427 | 14568 | 14.568 | -990 | 2.7
12428 | 14558 | 14.558 | 181 | 1.4
12429 | 14512 | 14.512 | 180 | 1.4
12430 | 14494 | 14.494 | -335 | 3.1
12431 | 14710 | 14.71 | 324 | 1.7
12432 | 14207 | 14.207 | -347 | 0.15
12433 | 13875 | 13.875 | 391 | 0.65
12434 | 13830 | 13.83 | -750 | 2.95
12435 | 14148 | 14.148 | -959 | 4.45
12436 | 14134 | 14.134 | -979 | 4.6
12437 | 13502 | 13.502 | 236 | 1.3
12438 | 14172 | 14.172 | 815 | 4.75
12439 | 14545 | 14.545 | 531 | 2.85
12440 | 14696 | 14.696 | -696 | 3.4
12441 | 14693 | 14.693 | 655 | 3.65
12442 | 14597 | 14.597 | 134 | 4.8
12443 | 14658 | 14.658 | -700 | 4.95
12444 | 14590 | 14.59 | -646 | 3.25
12445 | 14650 | 14.65 | -943 | 3.75
12446 | 14547 | 14.547 | 85 | 2.1
12447 | 14525 | 14.525 | -784 | 2.2
12448 | 14489 | 14.489 | -658 | 2.65
12449 | 14558 | 14.558 | 619 | 0.85
12450 | 14542 | 14.542 | 786 | 3.75
12451 | 14578 | 14.578 | -200 | 2.8
12452 | 14385 | 14.385 | 987 | 4.5
12453 | 14515 | 14.515 | -325 | 3.1
12454 | 14258 | 14.258 | -446 | 3.55
12455 | 14474 | 14.474 | -616 | 0.7
12456 | 14430 | 14.43 | 364 | 3.9
12457 | 14338 | 14.338 | -519 | 2.55
12458 | 14503 | 14.503 | -738 | 2.6
12459 | 14370 | 14.37 | 746 | 1.9
12460 | 14510 | 14.51 | 357 | 3.45
12461 | 14325 | 14.325 | -706 | 0.75
12462 | 14420 | 14.42 | 268 | 4.1
12463 | 14316 | 14.316 | -691 | 1.45
12464 | 13936 | 13.936 | 337 | 1.95
12465 | 14236 | 14.236 | 800 | 0.3
12466 | 14230 | 14.23 | -875 | 1.95
12467 | 14124 | 14.124 | 979 | 0.35
12468 | 14043 | 14.043 | 950 | 2.65
12469 | 14069 | 14.069 | -985 | 0.35
12470 | 14197 | 14.197 | 443 | 2.4
12471 | 13935 | 13.935 | 101 | 1.25
12472 | 14279 | 14.279 | 103 | 3.55
12473 | 14114 | 14.114 | 31 | 1.1
12474 | 14269 | 14.269 | 321 | 1.6
12475 | 14244 | 14.244 | 201 | 4.3
12476 | 14287 | 14.287 | 203 | 0.9
12477 | 14157 | 14.157 | 513 | 3.95
12478 | 14296 | 14.296 | -305 | 1.95
12479 | 14270 | 14.27 | 62 | 4.9
12480 | 14361 | 14.361 | 963 | 4.45
12481 | 14156 | 14.156 | -150 | 1.45
12482 | 14368 | 14.368 | 869 | 0.3
12483 | 14162 | 14.162 | -583 | 1
12484 | 14297 | 14.297 | 543 | 2.45
12485 | 14107 | 14.107 | 841 | 0.25
12486 | 14252 | 14.252 | 187 | 3.75
12487 | 14222 | 14.222 | -585 | 3.9
12488 | 14251 | 14.251 | 246 | 1.1
12489 | 14184 | 14.184 | 844 | 0.15
12490 | 14210 | 14.21 | -803 | 3.5
12491 | 14187 | 14.187 | 86 | 4.6
12492 | 14214 | 14.214 | -555 | 3.2
12493 | 14278 | 14.278 | -633 | 4.8
12494 | 14150 | 14.15 | -171 | 3.85
12495 | 14345 | 14.345 | -843 | 1.95
12496 | 14232 | 14.232 | -681 | 1.7
12497 | 14229 | 14.229 | -646 | 2.75
12498 | 14301 | 14.301 | -406 | 4.95
12499 | 14365 | 14.365 | 324 | 3.9
12500 | 14354 | 14.354 | -294 | 0.75
12501 | 14402 | 14.402 | -414 | 3.55
12502 | 14255 | 14.255 | 612 | 3.55
12503 | 14308 | 14.308 | -166 | 2.05
12504 | 14340 | 14.34 | 947 | 1.45
12505 | 14354 | 14.354 | -951 | 5
12506 | 14187 | 14.187 | 97 | 2.45
12507 | 14160 | 14.16 | -376 | 0.95
12508 | 14031 | 14.031 | 897 | 3.35
12509 | 14042 | 14.042 | -917 | 4.45
12510 | 14221 | 14.221 | -37 | 4.8
12511 | 14152 | 14.152 | 966 | 3.1
12512 | 14190 | 14.19 | -248 | 3.5
12513 | 14044 | 14.044 | -122 | 2
12514 | 14118 | 14.118 | -741 | 3.75
12515 | 14369 | 14.369 | 838 | 0.35
12516 | 14124 | 14.124 | 380 | 3
12517 | 14227 | 14.227 | -271 | 4.9
12518 | 14182 | 14.182 | -796 | 4.8
12519 | 14272 | 14.272 | -17 | 1.05
12520 | 14120 | 14.12 | -192 | 2.25
12521 | 14457 | 14.457 | 211 | 3.3
12522 | 14291 | 14.291 | -646 | 2.45
12523 | 14458 | 14.458 | -40 | 3.5
12524 | 14347 | 14.347 | -171 | 4.2
12525 | 14431 | 14.431 | -147 | 0.15
12526 | 14585 | 14.585 | 934 | 1.05
12527 | 14200 | 14.2 | -46 | 3.3
12528 | 13900 | 13.9 | -498 | 3.55
12529 | 14122 | 14.122 | 100 | 2.7
12530 | 13875 | 13.875 | 414 | 0.25
12531 | 13559 | 13.559 | 277 | 4.35
12532 | 14250 | 14.25 | -863 | 1.95
12533 | 14613 | 14.613 | -517 | 3.45
12534 | 14379 | 14.379 | 178 | 0.7
12535 | 14683 | 14.683 | -640 | 4.3
12536 | 14553 | 14.553 | -223 | 0.1
12537 | 14552 | 14.552 | -349 | 0.85
12538 | 14333 | 14.333 | 925 | 3.5
12539 | 14504 | 14.504 | -233 | 1.5
12540 | 14521 | 14.521 | 459 | 0.45
12541 | 14427 | 14.427 | -163 | 1.5
12542 | 14551 | 14.551 | -258 | 3.65
12543 | 14153 | 14.153 | -341 | 2.9
12544 | 14561 | 14.561 | -810 | 2
12545 | 14176 | 14.176 | 674 | 5
12546 | 14217 | 14.217 | -260 | 4.4
12547 | 14352 | 14.352 | -33 | 3.7
12548 | 14104 | 14.104 | 731 | 3.4
12549 | 14290 | 14.29 | -181 | 1.1
12550 | 14182 | 14.182 | 220 | 1.3
12551 | 14080 | 14.08 | 219 | 2.2
12552 | 14226 | 14.226 | -139 | 0.6
12553 | 14111 | 14.111 | -518 | 2.6
12554 | 14006 | 14.006 | 403 | 3.5
12555 | 14027 | 14.027 | 261 | 3.7
12556 | 13851 | 13.851 | -994 | 1
12557 | 13996 | 13.996 | 97 | 4.8
12558 | 13853 | 13.853 | 529 | 3.5
12559 | 13830 | 13.83 | 862 | 4.1
12560 | 13940 | 13.94 | 968 | 0
12561 | 13924 | 13.924 | 794 | 3.95
12562 | 13870 | 13.87 | 808 | 3.55
12563 | 14060 | 14.06 | -215 | 2.55
12564 | 13882 | 13.882 | -410 | 4.05
12565 | 14032 | 14.032 | -841 | 0.9
12566 | 13917 | 13.917 | -555 | 0.6
12567 | 13956 | 13.956 | 957 | 5
12568 | 14236 | 14.236 | 209 | 3.2
12569 | 14285 | 14.285 | 363 | 4.5
12570 | 14260 | 14.26 | -937 | 4.7
12571 | 14330 | 14.33 | 70 | 1.65
12572 | 14275 | 14.275 | -391 | 4.85
12573 | 14444 | 14.444 | 638 | 3.5
12574 | 14482 | 14.482 | 801 | 1.9
12575 | 14688 | 14.688 | -496 | 1.35
12576 | 14052 | 14.052 | 187 | 2.95
12577 | 13139 | 13.139 | -176 | 1.95
12578 | 14239 | 14.239 | -559 | 3.05
12579 | 14552 | 14.552 | 574 | 3.65
12580 | 14617 | 14.617 | -224 | 1.7
12581 | 14641 | 14.641 | -541 | 0.8
12582 | 14631 | 14.631 | 817 | 3.95
12583 | 14523 | 14.523 | 926 | 2.55
12584 | 14682 | 14.682 | -170 | 4.85
12585 | 14606 | 14.606 | -389 | 2.2
12586 | 14478 | 14.478 | -415 | 4.3
12587 | 14569 | 14.569 | -681 | 2.2
12588 | 14487 | 14.487 | -203 | 0.9
12589 | 14523 | 14.523 | 417 | 2.65
12590 | 14324 | 14.324 | -771 | 3.2
12591 | 14515 | 14.515 | 890 | 1.75
12592 | 14231 | 14.231 | -495 | 3.75
12593 | 14314 | 14.314 | -263 | 4.35
12594 | 14187 | 14.187 | -227 | 2
12595 | 14192 | 14.192 | 596 | 0.4
12596 | 13976 | 13.976 | 951 | 4
12597 | 13996 | 13.996 | -496 | 0.2
12598 | 13767 | 13.767 | -174 | 1.65
12599 | 13984 | 13.984 | -55 | 4.75
12600 | 13779 | 13.779 | 552 | 1.75
12601 | 13808 | 13.808 | -808 | 2.85
12602 | 13806 | 13.806 | -378 | 4.35
12603 | 13900 | 13.9 | -546 | 0.3
12604 | 13816 | 13.816 | 154 | 0.65
12605 | 13698 | 13.698 | 174 | 4
12606 | 13674 | 13.674 | 425 | 0
12607 | 13537 | 13.537 | -154 | 0.6
12608 | 13796 | 13.796 | -442 | 3.25
12609 | 13597 | 13.597 | -451 | 0.2
12610 | 13623 | 13.623 | 449 | 2
12611 | 13565 | 13.565 | 469 | 1.3
12612 | 13545 | 13.545 | 688 | 1.1
12613 | 13795 | 13.795 | 162 | 3.9
12614 | 13726 | 13.726 | -904 | 0.85
12615 | 13570 | 13.57 | 66 | 1.2
12616 | 13825 | 13.825 | 122 | 1.35
12617 | 13801 | 13.801 | 10 | 1.3
12618 | 13867 | 13.867 | 700 | 2.6
12619 | 13928 | 13.928 | 14 | 2.6
12620 | 13787 | 13.787 | -131 | 4.35
12621 | 14216 | 14.216 | 700 | 5
12622 | 14161 | 14.161 | 109 | 0.65
12623 | 14049 | 14.049 | -731 | 0.6
12624 | 13464 | 13.464 | 888 | 2.15
12625 | 13239 | 13.239 | -913 | 2.75
12626 | 13527 | 13.527 | 816 | 3.55
12627 | 13653 | 13.653 | -691 | 3.95
12628 | 13358 | 13.358 | -413 | 1.5
12629 | 13041 | 13.041 | 434 | 3.1
12630 | 13905 | 13.905 | -669 | 0.5
12631 | 14233 | 14.233 | -512 | 0.55
12632 | 14544 | 14.544 | 827 | 4.85
12633 | 14462 | 14.462 | -151 | 4.9
12634 | 14340 | 14.34 | 697 | 0.95
12635 | 14472 | 14.472 | 823 | 4.15
12636 | 14361 | 14.361 | 664 | 3.65
12637 | 14259 | 14.259 | 455 | 2.6
12638 | 14269 | 14.269 | -104 | 4.1
12639 | 14220 | 14.22 | -298 | 3
12640 | 14177 | 14.177 | -143 | 2.85
12641 | 14026 | 14.026 | -562 | 1.4
12642 | 13878 | 13.878 | 235 | 4.4
12643 | 13699 | 13.699 | -972 | 1.65
12644 | 13718 | 13.718 | 938 | 3.25
12645 | 13919 | 13.919 | 692 | 2.85
12646 | 13763 | 13.763 | 932 | 3.2
12647 | 13587 | 13.587 | -780 | 4.8
12648 | 13660 | 13.66 | -54 | 2.8
12649 | 13414 | 13.414 | 300 | 0.65
12650 | 13618 | 13.618 | 955 | 0.85
12651 | 13613 | 13.613 | -65 | 2.8
12652 | 13457 | 13.457 | -12 | 3.35
12653 | 13517 | 13.517 | 264 | 0.1
12654 | 13417 | 13.417 | 412 | 1.6
12655 | 13415 | 13.415 | 261 | 3.2
12656 | 13292 | 13.292 | -417 | 3.45
12657 | 13420 | 13.42 | 767 | 3.6
12658 | 13273 | 13.273 | 880 | 2.6
12659 | 13398 | 13.398 | 215 | 3.5
12660 | 13381 | 13.381 | 100 | 1.6
12661 | 13352 | 13.352 | 680 | 4.2
12662 | 13259 | 13.259 | 663 | 2.75
12663 | 13409 | 13.409 | 404 | 0.05
12664 | 13532 | 13.532 | -65 | 3.45
12665 | 13490 | 13.49 | -827 | 0.8
12666 | 13642 | 13.642 | 135 | 0.95
12667 | 13742 | 13.742 | 465 | 4.95
12668 | 13658 | 13.658 | 172 | 1.85
12669 | 13912 | 13.912 | -310 | 2.85
12670 | 13789 | 13.789 | -893 | 1.85
12671 | 13998 | 13.998 | -443 | 4.75
12672 | 13422 | 13.422 | -194 | 3.85
12673 | 12741 | 12.741 | -564 | 2.2
12674 | 13484 | 13.484 | -251 | 1.25
12675 | 13998 | 13.998 | 313 | 2.05
12676 | 14219 | 14.219 | -33 | 1.7
12677 | 14271 | 14.271 | 366 | 1
12678 | 14200 | 14.2 | 574 | 3.6
12679 | 14083 | 14.083 | -798 | 1.85
12680 | 14161 | 14.161 | 96 | 4.5
12681 | 14203 | 14.203 | 519 | 1
12682 | 14174 | 14.174 | 46 | 1.05
12683 | 14123 | 14.123 | -322 | 4.7
12684 | 14199 | 14.199 | -988 | 2.6
12685 | 14139 | 14.139 | 143 | 2.8
12686 | 14268 | 14.268 | 747 | 3.85
12687 | 14092 | 14.092 | -903 | 0.3
12688 | 13943 | 13.943 | -247 | 0
12689 | 14057 | 14.057 | -411 | 0.05
12690 | 14002 | 14.002 | 38 | 2.45
12691 | 13928 | 13.928 | -152 | 3.1
12692 | 14015 | 14.015 | 49 | 4.95
12693 | 13804 | 13.804 | 697 | 2.35
12694 | 13733 | 13.733 | 418 | 3.8
12695 | 13833 | 13.833 | 333 | 4.45
12696 | 13668 | 13.668 | 603 | 0.35
12697 | 13706 | 13.706 | 827 | 4.9
12698 | 13820 | 13.82 | 617 | 3.55
12699 | 13737 | 13.737 | -873 | 3.4
12700 | 13732 | 13.732 | -833 | 0.45
12701 | 13509 | 13.509 | 977 | 0.75
12702 | 13603 | 13.603 | 618 | 4.7
12703 | 13657 | 13.657 | 605 | 4.8
12704 | 13497 | 13.497 | -710 | 4.05
12705 | 13597 | 13.597 | -853 | 0.45
12706 | 13648 | 13.648 | -885 | 4.35
12707 | 13627 | 13.627 | -108 | 2.25
12708 | 13528 | 13.528 | -946 | 1
12709 | 13712 | 13.712 | -64 | 3.15
12710 | 13688 | 13.688 | 879 | 2.45
12711 | 13996 | 13.996 | 376 | 1.25
12712 | 14059 | 14.059 | -708 | 4.3
12713 | 14034 | 14.034 | 899 | 3.9
12714 | 13980 | 13.98 | -109 | 0.4
12715 | 14263 | 14.263 | -310 | 3.9
12716 | 14096 | 14.096 | -647 | 0.05
12717 | 14048 | 14.048 | -919 | 4.85
12718 | 14330 | 14.33 | -160 | 1.2
12719 | 14268 | 14.268 | 952 | 2.05
12720 | 14264 | 14.264 | 37 | 2.55
12721 | 13893 | 13.893 | -87 | 4.15
12722 | 13404 | 13.404 | 144 | 0.95
12723 | 13503 | 13.503 | 196 | 1.4
12724 | 13630 | 13.63 | -243 | 2.55
12725 | 13548 | 13.548 | -161 | 1.25
12726 | 12958 | 12.958 | 761 | 0
12727 | 14532 | 14.532 | -356 | 1.4
12728 | 14520 | 14.52 | 475 | 1.05
12729 | 14594 | 14.594 | -982 | 1
12730 | 14439 | 14.439 | 882 | 2.95
12731 | 14374 | 14.374 | 787 | 3.25
12732 | 14621 | 14.621 | 420 | 0.75
12733 | 14419 | 14.419 | 837 | 1.3
12734 | 14198 | 14.198 | 466 | 2
12735 | 14255 | 14.255 | 371 | 0.15
12736 | 14394 | 14.394 | 940 | 1.3
12737 | 14398 | 14.398 | 356 | 1.35
12738 | 14260 | 14.26 | -673 | 0.9
12739 | 14204 | 14.204 | 366 | 3
12740 | 14240 | 14.24 | 739 | 4.5
12741 | 14268 | 14.268 | 495 | 1.55
12742 | 14137 | 14.137 | -50 | 2.75
12743 | 13986 | 13.986 | 650 | 1.8
12744 | 13809 | 13.809 | -248 | 2.15
12745 | 13974 | 13.974 | -459 | 0.65
12746 | 14061 | 14.061 | 965 | 1.3
12747 | 13849 | 13.849 | 802 | 0.75
12748 | 14021 | 14.021 | 10 | 3.15
12749 | 13950 | 13.95 | 824 | 3.2
12750 | 14040 | 14.04 | -477 | 0.6
12751 | 13960 | 13.96 | 427 | 3.8
12752 | 13965 | 13.965 | -655 | 4.25
12753 | 13936 | 13.936 | 272 | 2.75
12754 | 13975 | 13.975 | 954 | 4.7
12755 | 14051 | 14.051 | -63 | 2.2
12756 | 13841 | 13.841 | 87 | 0.75
12757 | 14122 | 14.122 | -591 | 0.2
12758 | 14099 | 14.099 | -728 | 0.3
12759 | 13969 | 13.969 | -438 | 1.1
12760 | 14019 | 14.019 | 371 | 0.5
12761 | 14219 | 14.219 | -751 | 1.75
12762 | 14200 | 14.2 | -42 | 1.1
12763 | 14383 | 14.383 | 249 | 2.4
12764 | 14106 | 14.106 | 619 | 3.95
12765 | 14313 | 14.313 | 929 | 3.75
12766 | 14331 | 14.331 | -405 | 3.9
12767 | 14183 | 14.183 | 556 | 0.2
12768 | 13719 | 13.719 | 615 | 2.3
12769 | 12646 | 12.646 | -304 | 3.15
12770 | 13663 | 13.663 | 597 | 0.05
12771 | 14315 | 14.315 | 955 | 3.25
12772 | 14239 | 14.239 | -590 | 1.05
12773 | 14459 | 14.459 | -927 | 2.15
12774 | 14454 | 14.454 | -562 | 1.9
12775 | 14470 | 14.47 | 964 | 4.8
12776 | 14358 | 14.358 | 912 | 1.7
12777 | 14550 | 14.55 | 453 | 4.95
12778 | 14205 | 14.205 | 628 | 3.75
12779 | 14511 | 14.511 | -945 | 4.9
12780 | 14392 | 14.392 | 840 | 3.5
12781 | 14394 | 14.394 | -756 | 1.05
12782 | 14376 | 14.376 | 189 | 2.9
12783 | 14330 | 14.33 | 832 | 3.7
12784 | 14318 | 14.318 | -784 | 0.8
12785 | 14195 | 14.195 | 207 | 2.75
12786 | 14258 | 14.258 | -801 | 1.7
12787 | 14333 | 14.333 | -88 | 4.55
12788 | 14264 | 14.264 | -378 | 1.2
12789 | 14185 | 14.185 | 357 | 0.2
12790 | 14102 | 14.102 | 90 | 2.5
12791 | 13984 | 13.984 | 116 | 0.8
12792 | 13859 | 13.859 | -280 | 3.95
12793 | 14126 | 14.126 | 750 | 2.05
12794 | 13963 | 13.963 | -947 | 1.6
12795 | 14111 | 14.111 | 938 | 4.75
12796 | 13990 | 13.99 | 226 | 3.05
12797 | 13899 | 13.899 | -429 | 3.55
12798 | 13984 | 13.984 | -682 | 2.3
12799 | 14043 | 14.043 | -906 | 4.6
12800 | 13809 | 13.809 | -134 | 3.65
12801 | 14042 | 14.042 | 597 | 3.05
12802 | 13932 | 13.932 | 105 | 4.1
12803 | 13864 | 13.864 | -868 | 2.3
12804 | 13936 | 13.936 | -525 | 0.3
12805 | 13917 | 13.917 | 857 | 0.45
12806 | 13947 | 13.947 | -833 | 3.9
12807 | 13996 | 13.996 | 476 | 2.4
12808 | 14109 | 14.109 | -327 | 4.4
12809 | 13938 | 13.938 | -954 | 0.75
12810 | 14214 | 14.214 | 12 | 1.25
12811 | 14149 | 14.149 | 240 | 1.25
12812 | 14096 | 14.096 | 949 | 2.55
12813 | 14171 | 14.171 | 289 | 3.35
12814 | 14213 | 14.213 | -56 | 1.5
12815 | 14059 | 14.059 | 699 | 4.6
12816 | 14292 | 14.292 | 73 | 0.05
12817 | 14184 | 14.184 | -40 | 2.75
12818 | 14230 | 14.23 | -56 | 1.1
12819 | 14124 | 14.124 | 612 | 1.25
12820 | 13844 | 13.844 | 900 | 4.05
12821 | 13339 | 13.339 | 507 | 2.4
12822 | 13471 | 13.471 | -41 | 2
12823 | 10598 | 10.598 | -422 | 2.2
12824 | 11955 | 11.955 | 568 | 0
12825 | 13469 | 13.469 | 267 | 4.5
12826 | 13616 | 13.616 | 337 | 1.8
12827 | 14362 | 14.362 | 743 | 4.5
12828 | 14368 | 14.368 | 390 | 4.9
12829 | 14562 | 14.562 | -549 | 1.6
12830 | 14451 | 14.451 | -11 | 2.8
12831 | 14415 | 14.415 | -408 | 1.85
12832 | 14292 | 14.292 | -339 | 0.95
12833 | 14376 | 14.376 | 656 | 3.95
12834 | 14172 | 14.172 | 766 | 3.95
12835 | 14210 | 14.21 | -120 | 5
12836 | 14116 | 14.116 | -101 | 0.85
12837 | 14180 | 14.18 | -293 | 1.45
12838 | 14127 | 14.127 | 366 | 3.35
12839 | 14146 | 14.146 | 418 | 4.2
12840 | 14039 | 14.039 | -856 | 2.4
12841 | 14180 | 14.18 | -390 | 1.4
12842 | 13950 | 13.95 | -647 | 2.1
12843 | 13908 | 13.908 | -352 | 2.8
12844 | 13812 | 13.812 | 106 | 4.8
12845 | 13831 | 13.831 | -750 | 4.25
12846 | 13955 | 13.955 | 178 | 1.5
12847 | 13869 | 13.869 | -78 | 3.75
12848 | 13884 | 13.884 | -549 | 4.4
12849 | 13745 | 13.745 | -807 | 0.3
12850 | 13887 | 13.887 | -191 | 1.45
12851 | 13889 | 13.889 | 172 | 4.3
12852 | 13770 | 13.77 | 493 | 1.85
12853 | 14006 | 14.006 | -86 | 0.3
12854 | 13840 | 13.84 | 984 | 2.9
12855 | 14049 | 14.049 | 161 | 4.3
12856 | 13913 | 13.913 | 490 | 3.9
12857 | 13977 | 13.977 | 518 | 1.8
12858 | 14160 | 14.16 | 272 | 4.5
12859 | 14128 | 14.128 | 946 | 3.7
12860 | 14145 | 14.145 | -797 | 0
12861 | 14222 | 14.222 | -573 | 0.8
12862 | 14247 | 14.247 | 67 | 2.45
12863 | 14031 | 14.031 | 103 | 4.4
12864 | 13299 | 13.299 | -457 | 4.1
12865 | 13300 | 13.3 | 507 | 4.55
12866 | 14446 | 14.446 | 883 | 5
12867 | 14451 | 14.451 | -326 | 1
12868 | 14426 | 14.426 | -306 | 2.7
12869 | 14440 | 14.44 | -664 | 1.7
12870 | 14403 | 14.403 | 810 | 0.8
12871 | 14399 | 14.399 | 181 | 3.55
12872 | 14468 | 14.468 | 746 | 3.15
12873 | 14399 | 14.399 | -525 | 3.2
12874 | 14593 | 14.593 | 649 | 2.2
12875 | 14445 | 14.445 | -402 | 1.45
12876 | 14458 | 14.458 | 564 | 4.8
12877 | 14484 | 14.484 | 199 | 1.8
12878 | 14496 | 14.496 | -271 | 2.2
12879 | 14402 | 14.402 | -598 | 2.5
12880 | 14463 | 14.463 | 397 | 1.1
12881 | 14276 | 14.276 | 910 | 2.2
12882 | 14351 | 14.351 | -3 | 2.5
12883 | 14194 | 14.194 | -803 | 3
12884 | 14200 | 14.2 | 476 | 4.05
12885 | 14094 | 14.094 | -558 | 2.95
12886 | 13862 | 13.862 | -727 | 0.9
12887 | 13988 | 13.988 | -752 | 2
12888 | 14066 | 14.066 | -315 | 0.25
12889 | 13938 | 13.938 | -203 | 1.55
12890 | 14131 | 14.131 | -831 | 0.1
12891 | 14058 | 14.058 | -318 | 0.15
12892 | 13871 | 13.871 | 605 | 2.85
12893 | 13994 | 13.994 | 872 | 1.25
12894 | 14049 | 14.049 | 317 | 3.6
12895 | 14014 | 14.014 | 412 | 3.1
12896 | 13984 | 13.984 | 743 | 2.5
12897 | 13888 | 13.888 | -639 | 1.9
12898 | 13908 | 13.908 | 313 | 1.7
12899 | 13918 | 13.918 | -249 | 0.85
12900 | 14037 | 14.037 | 394 | 2.15
12901 | 14030 | 14.03 | 590 | 3.75
12902 | 14060 | 14.06 | 491 | 4.55
12903 | 13989 | 13.989 | 58 | 0.1
12904 | 14220 | 14.22 | 613 | 3.45
12905 | 14259 | 14.259 | 72 | 4.35
12906 | 14208 | 14.208 | 821 | 4
12907 | 14152 | 14.152 | -554 | 2.85
12908 | 14212 | 14.212 | -288 | 2.9
12909 | 14259 | 14.259 | 284 | 1.95
12910 | 14257 | 14.257 | 417 | 4.65
12911 | 14300 | 14.3 | -101 | 2.85
12912 | 14293 | 14.293 | -769 | 3
12913 | 14056 | 14.056 | 254 | 0.45
12914 | 13692 | 13.692 | 272 | 1.55
12915 | 13583 | 13.583 | -918 | 2.75
12916 | 13575 | 13.575 | 627 | 3.1
12917 | 13785 | 13.785 | -253 | 2.45
12918 | 13227 | 13.227 | 489 | 4.8
12919 | 13598 | 13.598 | 281 | 4.05
12920 | 14322 | 14.322 | -947 | 2.95
12921 | 14408 | 14.408 | -23 | 1.8
12922 | 14659 | 14.659 | -826 | 3
12923 | 13426 | 13.426 | 203 | 0.05
12924 | 13345 | 13.345 | 881 | 2.95
12925 | 13241 | 13.241 | -929 | 1.05
12926 | 14131 | 14.131 | -514 | 4.8
12927 | 14087 | 14.087 | 642 | 2.95
12928 | 9736 | 9.736 | 608 | 4.05
12929 | 8918 | 8.918 | 38 | 1.55
12930 | 11753 | 11.753 | -768 | 2.25
12931 | 14163 | 14.163 | -657 | 1.55
12932 | 14161 | 14.161 | -702 | 0.15
12933 | 14110 | 14.11 | -545 | 2.4
12934 | 14207 | 14.207 | -760 | 1.05
12935 | 14136 | 14.136 | 34 | 0.95
12936 | 14148 | 14.148 | -556 | 3.15
12937 | 14327 | 14.327 | -322 | 4.6
12938 | 14173 | 14.173 | 744 | 0.05
12939 | 14094 | 14.094 | 582 | 1.55
12940 | 14172 | 14.172 | 875 | 0.55
12941 | 14243 | 14.243 | 980 | 1.2
12942 | 14106 | 14.106 | 171 | 0.75
12943 | 14150 | 14.15 | -685 | 4.85
12944 | 14267 | 14.267 | -594 | 0.45
12945 | 14321 | 14.321 | 440 | 0.15
12946 | 14277 | 14.277 | -428 | 0.45
12947 | 14284 | 14.284 | 699 | 0.7
12948 | 14239 | 14.239 | -73 | 2.85
12949 | 14406 | 14.406 | 765 | 0
12950 | 14336 | 14.336 | -797 | 2.9
12951 | 14298 | 14.298 | -3 | 4.8
12952 | 14346 | 14.346 | -669 | 3.95
12953 | 14455 | 14.455 | 144 | 3.2
12954 | 14415 | 14.415 | 418 | 4.45
12955 | 14431 | 14.431 | 97 | 2.6
12956 | 14537 | 14.537 | -801 | 3.25
12957 | 14473 | 14.473 | 182 | 0.8
12958 | 14543 | 14.543 | -665 | 0.55
12959 | 14172 | 14.172 | -570 | 2.35
12960 | 13285 | 13.285 | 106 | 3.5
12961 | 13878 | 13.878 | -337 | 0.95
12962 | 14389 | 14.389 | 42 | 4.9
12963 | 14509 | 14.509 | -477 | 3.7
12964 | 14607 | 14.607 | -514 | 0.95
12965 | 14435 | 14.435 | 132 | 0
12966 | 14605 | 14.605 | -902 | 1.05
12967 | 14335 | 14.335 | -650 | 2.45
12968 | 14531 | 14.531 | -361 | 1.9
12969 | 14470 | 14.47 | -70 | 4.8
12970 | 14498 | 14.498 | 584 | 1.25
12971 | 14609 | 14.609 | 516 | 4.15
12972 | 14465 | 14.465 | 486 | 2.55
12973 | 14658 | 14.658 | 409 | 0.95
12974 | 14532 | 14.532 | -394 | 3.85
12975 | 14436 | 14.436 | 303 | 1.55
12976 | 14397 | 14.397 | 824 | 4.15
12977 | 14279 | 14.279 | -949 | 3.15
12978 | 14477 | 14.477 | -354 | 4
12979 | 14268 | 14.268 | 141 | 4.15
12980 | 14216 | 14.216 | 362 | 4.7
12981 | 14213 | 14.213 | -500 | 1
12982 | 14155 | 14.155 | -790 | 0.65
12983 | 13977 | 13.977 | 885 | 4.4
12984 | 13961 | 13.961 | 382 | 3.7
12985 | 14099 | 14.099 | -680 | 0.7
12986 | 14130 | 14.13 | 76 | 2.8
12987 | 14130 | 14.13 | 708 | 3.45
12988 | 14067 | 14.067 | 789 | 4.45
12989 | 14137 | 14.137 | 639 | 2.5
12990 | 14090 | 14.09 | -953 | 1.65
12991 | 13911 | 13.911 | -812 | 2.75
12992 | 13973 | 13.973 | 668 | 3.65
12993 | 14302 | 14.302 | -463 | 1.2
12994 | 14159 | 14.159 | 401 | 0.3
12995 | 14246 | 14.246 | -256 | 1.9
12996 | 14267 | 14.267 | 64 | 1.8
12997 | 14282 | 14.282 | -389 | 4.5
12998 | 14210 | 14.21 | 4 | 0.3
12999 | 14003 | 14.003 | -855 | 3.65
13000 | 14318 | 14.318 | 195 | 0.25
13001 | 14050 | 14.05 | 386 | 0.25
13002 | 14223 | 14.223 | -618 | 0.95
13003 | 14287 | 14.287 | -872 | 5
13004 | 14272 | 14.272 | -584 | 3.5
13005 | 14389 | 14.389 | 300 | 4.4
13006 | 14211 | 14.211 | 463 | 2.95
13007 | 14328 | 14.328 | 109 | 0.6
13008 | 13762 | 13.762 | 852 | 5
13009 | 13288 | 13.288 | 540 | 5
13010 | 13287 | 13.287 | 346 | 3.35
13011 | 8681 | 8.681 | -976 | 4.1
13012 | 9088 | 9.088 | 822 | 3.2
13013 | 11428 | 11.428 | 555 | 0.05
13014 | 14057 | 14.057 | 395 | 3.95
13015 | 14255 | 14.255 | -75 | 2.15
13016 | 14242 | 14.242 | 219 | 2.05
13017 | 14380 | 14.38 | -368 | 0.65
13018 | 14286 | 14.286 | -20 | 3.5
13019 | 14337 | 14.337 | -592 | 2.85
13020 | 14371 | 14.371 | -427 | 1.9
13021 | 14217 | 14.217 | 824 | 4.5
13022 | 14351 | 14.351 | 245 | 0.75
13023 | 14112 | 14.112 | 224 | 4.45
13024 | 14116 | 14.116 | 297 | 3.85
13025 | 14237 | 14.237 | 535 | 3.7
13026 | 14104 | 14.104 | -822 | 4.5
13027 | 14121 | 14.121 | 505 | 2.85
13028 | 14227 | 14.227 | 207 | 1.55
13029 | 14063 | 14.063 | 312 | 3.25
13030 | 14117 | 14.117 | 621 | 1
13031 | 14020 | 14.02 | 649 | 1.95
13032 | 14035 | 14.035 | 342 | 3.2
13033 | 13934 | 13.934 | 5 | 2.75
13034 | 13914 | 13.914 | -966 | 2.25
13035 | 14049 | 14.049 | -35 | 1.65
13036 | 13936 | 13.936 | 593 | 1
13037 | 14015 | 14.015 | -683 | 4.3
13038 | 14090 | 14.09 | -718 | 4.95
13039 | 14020 | 14.02 | -824 | 1.25
13040 | 14021 | 14.021 | 530 | 4.25
13041 | 14096 | 14.096 | -201 | 1.35
13042 | 14076 | 14.076 | -702 | 3.7
13043 | 14005 | 14.005 | 761 | 0.25
13044 | 14064 | 14.064 | 508 | 4.5
13045 | 11783 | 11.783 | -316 | 3.25
13046 | 8181 | 8.181 | 605 | 0.1
13047 | 10287 | 10.287 | 8 | 2.55
13048 | 14235 | 14.235 | -938 | 1.3
13049 | 14420 | 14.42 | -743 | 1.4
13050 | 14448 | 14.448 | 746 | 2.8
13051 | 14467 | 14.467 | 847 | 3.2
13052 | 14532 | 14.532 | -459 | 1.85
13053 | 14545 | 14.545 | 271 | 2.25
13054 | 14469 | 14.469 | -208 | 3.75
13055 | 14276 | 14.276 | -53 | 1.4
13056 | 13357 | 13.357 | -473 | 1.45
13057 | 13661 | 13.661 | 101 | 0.35
13058 | 14506 | 14.506 | 347 | 0.4
13059 | 14624 | 14.624 | -346 | 1.1
13060 | 14561 | 14.561 | -679 | 0.1
13061 | 14517 | 14.517 | 467 | 1.05
13062 | 14540 | 14.54 | -229 | 3.75
13063 | 14672 | 14.672 | -919 | 3.85
13064 | 14427 | 14.427 | -929 | 1.9
13065 | 14671 | 14.671 | -285 | 0.75
13066 | 14588 | 14.588 | 584 | 4.45
13067 | 14628 | 14.628 | -304 | 2.25
13068 | 14526 | 14.526 | 455 | 3
13069 | 14562 | 14.562 | -734 | 3.2
13070 | 14516 | 14.516 | -921 | 0.25
13071 | 14498 | 14.498 | -54 | 3.1
13072 | 14587 | 14.587 | -976 | 4.65
13073 | 14467 | 14.467 | 632 | 4.55
13074 | 14558 | 14.558 | 630 | 4.15
13075 | 14224 | 14.224 | 856 | 4.25
13076 | 14309 | 14.309 | 871 | 1.5
13077 | 14214 | 14.214 | -711 | 4.85
13078 | 14299 | 14.299 | 478 | 4.1
13079 | 14398 | 14.398 | -648 | 2.5
13080 | 14253 | 14.253 | -623 | 3.4
13081 | 14392 | 14.392 | 985 | 0.3
13082 | 14366 | 14.366 | -622 | 2.9
13083 | 14376 | 14.376 | -964 | 3.6
13084 | 14379 | 14.379 | 303 | 2.8
13085 | 14536 | 14.536 | -673 | 0
13086 | 14523 | 14.523 | 662 | 0.5
13087 | 14455 | 14.455 | -539 | 4.5
13088 | 14635 | 14.635 | 38 | 4.25
13089 | 14550 | 14.55 | 508 | 1.8
13090 | 14603 | 14.603 | 96 | 2.7
13091 | 14478 | 14.478 | 495 | 4.85
13092 | 14446 | 14.446 | -585 | 0
13093 | 14330 | 14.33 | 85 | 1.15
13094 | 14335 | 14.335 | 166 | 3.35
13095 | 14362 | 14.362 | -458 | 0.45
13096 | 14337 | 14.337 | -987 | 3.7
13097 | 14307 | 14.307 | 676 | 1.75
13098 | 14213 | 14.213 | -149 | 2.25
13099 | 14298 | 14.298 | -134 | 3.8
13100 | 14345 | 14.345 | -910 | 1.1
13101 | 14371 | 14.371 | 471 | 4.75
13102 | 14323 | 14.323 | 128 | 2
13103 | 14252 | 14.252 | 682 | 3.25
13104 | 13783 | 13.783 | -330 | 0.15
13105 | 9721 | 9.721 | 616 | 0.8
13106 | 7703 | 7.703 | -701 | 2.1
13107 | 10461 | 10.461 | 308 | 4.5
13108 | 14278 | 14.278 | -25 | 2
13109 | 14490 | 14.49 | -568 | 2.5
13110 | 14454 | 14.454 | 141 | 1
13111 | 14615 | 14.615 | 983 | 0.8
13112 | 14388 | 14.388 | -604 | 3
13113 | 14386 | 14.386 | 667 | 1.45
13114 | 14441 | 14.441 | 528 | 1.15
13115 | 14532 | 14.532 | 83 | 3.5
13116 | 14229 | 14.229 | 40 | 1.35
13117 | 14510 | 14.51 | 735 | 4.95
13118 | 14213 | 14.213 | -590 | 3.3
13119 | 14349 | 14.349 | 49 | 2.7
13120 | 14302 | 14.302 | 275 | 3.95
13121 | 14339 | 14.339 | -659 | 3.95
13122 | 14251 | 14.251 | -613 | 0.8
13123 | 14191 | 14.191 | 534 | 0.05
13124 | 14239 | 14.239 | -693 | 4.75
13125 | 14186 | 14.186 | 220 | 2.95
13126 | 14051 | 14.051 | 886 | 4.4
13127 | 14099 | 14.099 | -49 | 3.95
13128 | 14050 | 14.05 | -239 | 4.9
13129 | 14225 | 14.225 | -551 | 3.5
13130 | 14305 | 14.305 | 952 | 3.45
13131 | 14339 | 14.339 | -454 | 2.35
13132 | 14300 | 14.3 | 748 | 0.25
13133 | 14238 | 14.238 | -923 | 1.45
13134 | 14246 | 14.246 | -763 | 2
13135 | 14339 | 14.339 | -316 | 1.25
13136 | 14362 | 14.362 | -737 | 4.45
13137 | 14413 | 14.413 | -60 | 0.6
13138 | 14317 | 14.317 | -850 | 2.1
13139 | 14350 | 14.35 | 332 | 4.15
13140 | 14303 | 14.303 | 416 | 3.75
13141 | 14417 | 14.417 | -913 | 4.6
13142 | 14324 | 14.324 | 771 | 0.85
13143 | 14384 | 14.384 | 821 | 2.5
13144 | 14351 | 14.351 | 755 | 1.6
13145 | 14295 | 14.295 | 341 | 1.65
13146 | 14363 | 14.363 | -341 | 3.6
13147 | 14340 | 14.34 | -283 | 0.15
13148 | 14354 | 14.354 | 790 | 2
13149 | 14460 | 14.46 | 877 | 3.1
13150 | 14547 | 14.547 | 989 | 0.6
13151 | 14005 | 14.005 | 247 | 0.75
13152 | 13257 | 13.257 | 182 | 0.25
13153 | 13806 | 13.806 | 517 | 0.55
13154 | 13795 | 13.795 | 915 | 0.65
13155 | 13713 | 13.713 | -916 | 2.1
13156 | 13193 | 13.193 | -402 | 4.3
13157 | 14441 | 14.441 | 98 | 0.6
13158 | 14646 | 14.646 | -488 | 4.25
13159 | 14743 | 14.743 | 79 | 3.6
13160 | 14391 | 14.391 | 679 | 1.55
13161 | 14565 | 14.565 | -741 | 4.75
13162 | 14682 | 14.682 | -273 | 2.6
13163 | 14521 | 14.521 | 631 | 4
13164 | 14702 | 14.702 | 143 | 0.35
13165 | 14487 | 14.487 | 109 | 3.75
13166 | 14576 | 14.576 | -774 | 1.2
13167 | 14468 | 14.468 | 299 | 4.05
13168 | 14404 | 14.404 | -551 | 4.35
13169 | 14377 | 14.377 | -551 | 2.85
13170 | 14552 | 14.552 | 487 | 3.95
13171 | 14343 | 14.343 | 48 | 2.25
13172 | 14242 | 14.242 | 921 | 2.05
13173 | 14250 | 14.25 | -729 | 0.9
13174 | 14117 | 14.117 | 884 | 4.95
13175 | 14269 | 14.269 | -899 | 3.85
13176 | 14210 | 14.21 | 828 | 4.7
13177 | 14295 | 14.295 | 764 | 4.8
13178 | 14318 | 14.318 | 549 | 2.6
13179 | 14159 | 14.159 | -282 | 3.25
13180 | 14225 | 14.225 | -569 | 2.15
13181 | 13935 | 13.935 | -161 | 2.3
13182 | 14217 | 14.217 | -20 | 0.2
13183 | 14083 | 14.083 | -121 | 1.6
13184 | 14003 | 14.003 | 260 | 1.8
13185 | 14233 | 14.233 | 105 | 0.3
13186 | 14269 | 14.269 | -107 | 2.2
13187 | 14267 | 14.267 | -100 | 1.85
13188 | 14180 | 14.18 | 404 | 2.75
13189 | 14333 | 14.333 | 36 | 3.4
13190 | 14250 | 14.25 | -9 | 3.15
13191 | 11635 | 11.635 | 690 | 3.95
13192 | 13245 | 13.245 | 186 | 1.1
13193 | 14456 | 14.456 | -460 | 4.25
13194 | 14382 | 14.382 | -180 | 2.95
13195 | 14413 | 14.413 | 172 | 0.8
13196 | 14372 | 14.372 | 616 | 1.4
13197 | 14474 | 14.474 | -227 | 2.45
13198 | 14506 | 14.506 | -349 | 1.35
13199 | 14443 | 14.443 | 658 | 1.05
13200 | 14472 | 14.472 | 420 | 3.8
13201 | 13875 | 13.875 | 810 | 0.5
13202 | 13050 | 13.05 | 565 | 2.7
13203 | 14273 | 14.273 | -909 | 2.35
13204 | 14583 | 14.583 | -608 | 4.45
13205 | 14521 | 14.521 | 58 | 1.15
13206 | 14522 | 14.522 | 403 | 1.4
13207 | 14519 | 14.519 | 793 | 1.35
13208 | 14416 | 14.416 | 512 | 4.75
13209 | 14497 | 14.497 | 225 | 3.75
13210 | 14463 | 14.463 | 611 | 2.05
13211 | 14432 | 14.432 | -257 | 3.3
13212 | 14509 | 14.509 | 635 | 4.95
13213 | 14579 | 14.579 | -512 | 1.5
13214 | 14561 | 14.561 | -654 | 2.05
13215 | 14358 | 14.358 | -217 | 1.95
13216 | 14130 | 14.13 | -459 | 3.5
13217 | 14327 | 14.327 | -577 | 2.75
13218 | 14340 | 14.34 | 651 | 1.25
13219 | 14400 | 14.4 | -859 | 4.3
13220 | 14241 | 14.241 | 760 | 2.75
13221 | 14222 | 14.222 | -646 | 2.05
13222 | 14048 | 14.048 | 21 | 2.15
13223 | 13965 | 13.965 | 584 | 2.85
13224 | 14113 | 14.113 | 700 | 1.5
13225 | 14146 | 14.146 | -631 | 1.45
13226 | 14128 | 14.128 | 445 | 3.8
13227 | 14092 | 14.092 | -942 | 2.65
13228 | 14157 | 14.157 | 866 | 3.25
13229 | 14365 | 14.365 | -353 | 4.9
13230 | 14187 | 14.187 | 669 | 2.1
13231 | 14107 | 14.107 | 105 | 0.25
13232 | 14186 | 14.186 | -626 | 1.5
13233 | 14216 | 14.216 | -892 | 3.95
13234 | 14043 | 14.043 | -679 | 1.4
13235 | 14237 | 14.237 | -911 | 0.3
13236 | 14193 | 14.193 | -581 | 4
13237 | 14306 | 14.306 | -971 | 2.4
13238 | 13441 | 13.441 | 899 | 1.15
13239 | 9201 | 9.201 | -598 | 1.6
13240 | 11137 | 11.137 | -439 | 3.4
13241 | 12610 | 12.61 | 690 | 3.8
13242 | 14185 | 14.185 | 755 | 4.95
13243 | 14454 | 14.454 | -849 | 2.1
13244 | 14403 | 14.403 | -845 | 3.1
13245 | 14497 | 14.497 | 136 | 1.9
13246 | 14464 | 14.464 | -22 | 0.2
13247 | 14463 | 14.463 | -691 | 4.4
13248 | 14027 | 14.027 | -748 | 4.5
13249 | 13424 | 13.424 | 701 | 0.35
13250 | 13959 | 13.959 | -29 | 1.4
13251 | 13837 | 13.837 | 460 | 4.55
13252 | 13816 | 13.816 | -391 | 4.6
13253 | 13341 | 13.341 | -568 | 0.45
13254 | 14405 | 14.405 | -149 | 2
13255 | 14576 | 14.576 | -217 | 3.4
13256 | 14628 | 14.628 | 527 | 4.75
13257 | 14488 | 14.488 | -901 | 4.3
13258 | 14681 | 14.681 | 939 | 1.3
13259 | 14540 | 14.54 | 886 | 0.45
13260 | 14540 | 14.54 | 91 | 0.7
13261 | 14507 | 14.507 | -152 | 1.15
13262 | 14546 | 14.546 | 485 | 0.65
13263 | 14504 | 14.504 | 855 | 2.65
13264 | 14319 | 14.319 | 793 | 2.35
13265 | 14477 | 14.477 | 403 | 2.75
13266 | 14397 | 14.397 | -863 | 4.6
13267 | 14276 | 14.276 | 142 | 4.05
13268 | 14257 | 14.257 | 929 | 2.85
13269 | 14126 | 14.126 | 665 | 4.45
13270 | 14145 | 14.145 | 632 | 2.45
13271 | 13961 | 13.961 | -552 | 2.3
13272 | 14223 | 14.223 | 833 | 5
13273 | 14172 | 14.172 | 229 | 4.35
13274 | 14230 | 14.23 | 365 | 0.85
13275 | 14159 | 14.159 | 994 | 0.45
13276 | 14109 | 14.109 | -654 | 2.25
13277 | 14267 | 14.267 | -241 | 3.05
13278 | 14233 | 14.233 | -630 | 3.5
13279 | 14236 | 14.236 | 44 | 1.1
13280 | 11679 | 11.679 | -148 | 3.2
13281 | 8797 | 8.797 | -295 | 4
13282 | 8577 | 8.577 | 830 | 1.35
13283 | 8853 | 8.853 | -890 | 3.05
13284 | 8909 | 8.909 | 303 | 2.15
13285 | 8872 | 8.872 | 674 | 3.4
13286 | 9423 | 9.423 | -394 | 1.9
13287 | 10173 | 10.173 | -975 | 4.7
13288 | 10453 | 10.453 | 336 | 3.7
13289 | 10396 | 10.396 | 91 | 1.25
13290 | 10815 | 10.815 | -167 | 4.65
13291 | 10648 | 10.648 | 908 | 4.3
13292 | 10741 | 10.741 | -873 | 2.55
13293 | 10868 | 10.868 | -186 | 3.8
13294 | 10783 | 10.783 | -73 | 2.2
13295 | 10851 | 10.851 | -455 | 0.85
13296 | 10743 | 10.743 | -891 | 1.95
13297 | 10954 | 10.954 | -299 | 1.65
13298 | 10869 | 10.869 | 278 | 2.5
13299 | 10575 | 10.575 | -662 | 0.45
13300 | 10596 | 10.596 | 785 | 0.3
13301 | 10773 | 10.773 | -176 | 0.2
13302 | 10806 | 10.806 | -106 | 2.65
13303 | 10297 | 10.297 | -243 | 2.3
13304 | 10947 | 10.947 | -811 | 2.85
13305 | 11046 | 11.046 | 254 | 0.5
13306 | 10543 | 10.543 | -642 | 4.4
13307 | 10423 | 10.423 | -224 | 2.3
13308 | 10868 | 10.868 | -408 | 4.9
13309 | 10802 | 10.802 | 57 | 2.5
13310 | 10641 | 10.641 | -429 | 3.25
13311 | 10761 | 10.761 | -634 | 2.3
13312 | 11498 | 11.498 | -10 | 3
13313 | 11456 | 11.456 | 358 | 1.1
13314 | 11323 | 11.323 | -116 | 2.55
13315 | 11492 | 11.492 | 610 | 3.85
13316 | 11431 | 11.431 | 89 | 2.3
13317 | 11534 | 11.534 | -214 | 2.5
13318 | 11280 | 11.28 | 245 | 1.65
13319 | 11210 | 11.21 | -287 | 0.85
13320 | 11296 | 11.296 | 354 | 3
13321 | 11275 | 11.275 | 992 | 1.95
13322 | 11561 | 11.561 | -716 | 2.3
13323 | 11291 | 11.291 | 152 | 0.1
13324 | 11355 | 11.355 | 393 | 1.75
13325 | 10984 | 10.984 | -1 | 4.45
13326 | 11258 | 11.258 | 201 | 0.25
13327 | 11285 | 11.285 | 895 | 4.65
13328 | 11413 | 11.413 | 413 | 0.7
13329 | 11135 | 11.135 | -81 | 0
13330 | 11358 | 11.358 | -129 | 1.15
13331 | 11283 | 11.283 | -586 | 3.15
13332 | 11064 | 11.064 | 284 | 2.15
13333 | 11343 | 11.343 | 131 | 3.4
13334 | 11470 | 11.47 | 904 | 3.25
13335 | 11171 | 11.171 | -565 | 2.35
13336 | 11060 | 11.06 | -193 | 3
13337 | 11349 | 11.349 | -679 | 4.2
13338 | 11173 | 11.173 | -167 | 3.3
13339 | 11186 | 11.186 | 846 | 3.8
13340 | 11301 | 11.301 | 914 | 3.7
13341 | 11188 | 11.188 | 877 | 0.15
13342 | 11338 | 11.338 | 698 | 1.05
13343 | 11580 | 11.58 | -7 | 4.5
13344 | 11578 | 11.578 | -481 | 0.4
13345 | 10879 | 10.879 | 26 | 3.9
13346 | 11064 | 11.064 | 13 | 3.65
13347 | 11209 | 11.209 | -453 | 3.55
13348 | 11214 | 11.214 | -871 | 2.8
13349 | 10520 | 10.52 | 449 | 2.2
13350 | 11642 | 11.642 | -990 | 3.8
13351 | 11888 | 11.888 | -223 | 1.8
13352 | 11838 | 11.838 | -195 | 3.7
13353 | 11830 | 11.83 | -889 | 4.75
13354 | 11815 | 11.815 | -309 | 2.25
13355 | 11865 | 11.865 | 535 | 2.95
13356 | 11828 | 11.828 | 503 | 1
13357 | 11802 | 11.802 | -525 | 2.35
13358 | 11749 | 11.749 | -449 | 3.9
13359 | 11843 | 11.843 | -111 | 2.9
13360 | 11777 | 11.777 | -142 | 3.65
13361 | 11668 | 11.668 | -805 | 1.25
13362 | 11898 | 11.898 | 465 | 3.2
13363 | 12185 | 12.185 | -778 | 3.15
13364 | 13027 | 13.027 | 979 | 4.25
13365 | 13778 | 13.778 | 664 | 1.25
13366 | 13806 | 13.806 | 248 | 0.6
13367 | 13785 | 13.785 | -663 | 1.7
13368 | 14107 | 14.107 | -241 | 2.35
13369 | 13870 | 13.87 | -227 | 4.45
13370 | 13848 | 13.848 | 146 | 0.7
13371 | 14213 | 14.213 | 640 | 4.4
13372 | 13816 | 13.816 | 406 | 4.75
13373 | 13984 | 13.984 | -933 | 4.4
13374 | 13787 | 13.787 | -692 | 5
13375 | 13966 | 13.966 | 512 | 3.7
13376 | 13950 | 13.95 | -770 | 1.85
13377 | 13973 | 13.973 | 921 | 2.7
13378 | 14100 | 14.1 | -175 | 2.7
13379 | 14168 | 14.168 | -858 | 2.4
13380 | 13986 | 13.986 | -266 | 0.55
13381 | 14284 | 14.284 | 631 | 2.95
13382 | 13939 | 13.939 | -453 | 1.25
13383 | 14069 | 14.069 | 270 | 1.7
13384 | 14123 | 14.123 | -702 | 2.15
13385 | 14164 | 14.164 | -30 | 4.6
13386 | 14142 | 14.142 | 545 | 1.8
13387 | 14149 | 14.149 | 823 | 2.9
13388 | 14218 | 14.218 | -820 | 4.1
13389 | 14080 | 14.08 | 933 | 1.4
13390 | 14314 | 14.314 | 55 | 0.4
13391 | 14234 | 14.234 | 280 | 0.05
13392 | 11141 | 11.141 | -890 | 2.95
13393 | 10639 | 10.639 | 692 | 5
13394 | 11198 | 11.198 | 217 | 2.9
13395 | 14176 | 14.176 | -460 | 3.6
13396 | 13354 | 13.354 | 169 | 1.05
13397 | 12739 | 12.739 | 112 | 2.4
13398 | 14027 | 14.027 | 223 | 0.35
13399 | 14282 | 14.282 | -901 | 2.5
13400 | 14291 | 14.291 | 176 | 2.95
13401 | 14294 | 14.294 | 120 | 2
13402 | 14305 | 14.305 | -855 | 0.65
13403 | 14295 | 14.295 | 916 | 2
13404 | 14343 | 14.343 | 378 | 3.15
13405 | 14388 | 14.388 | -545 | 4
13406 | 13967 | 13.967 | 120 | 0.75
13407 | 13342 | 13.342 | -715 | 2.15
13408 | 11041 | 11.041 | -8 | 3.3
13409 | 14008 | 14.008 | -159 | 1.25
13410 | 14109 | 14.109 | 637 | 3.25
13411 | 14302 | 14.302 | -583 | 3.25
13412 | 13722 | 13.722 | -962 | 3.85
13413 | 14379 | 14.379 | 906 | 2
13414 | 14147 | 14.147 | 788 | 4.55
13415 | 13972 | 13.972 | -930 | 4.15
13416 | 14268 | 14.268 | 483 | 1.6
13417 | 13757 | 13.757 | -852 | 3.55
13418 | 14174 | 14.174 | -162 | 4.6
13419 | 13841 | 13.841 | 646 | 2.6
13420 | 14017 | 14.017 | 229 | 2.25
13421 | 13999 | 13.999 | 705 | 2.9
13422 | 13988 | 13.988 | 530 | 2.15
13423 | 13832 | 13.832 | 129 | 3.85
13424 | 13900 | 13.9 | -837 | 3.65
13425 | 13992 | 13.992 | -923 | 4.65
13426 | 13965 | 13.965 | 329 | 2.25
13427 | 13888 | 13.888 | -289 | 0.1
13428 | 13909 | 13.909 | 271 | 2.25
13429 | 14092 | 14.092 | 603 | 1.3
13430 | 14187 | 14.187 | 163 | 1.05
13431 | 14270 | 14.27 | -741 | 4.3
13432 | 14449 | 14.449 | 174 | 1.05
13433 | 13729 | 13.729 | -947 | 1.85
13434 | 14469 | 14.469 | 141 | 1.4
13435 | 14240 | 14.24 | -87 | 0.3
13436 | 14283 | 14.283 | -372 | 0.05
13437 | 14242 | 14.242 | -782 | 2.3
13438 | 14225 | 14.225 | -667 | 3.4
13439 | 14634 | 14.634 | -676 | 0.7
13440 | 14467 | 14.467 | -882 | 4.8
13441 | 13858 | 13.858 | -658 | 0.15
13442 | 13274 | 13.274 | -107 | 3.9
13443 | 13592 | 13.592 | 54 | 4.75
13444 | 13676 | 13.676 | 573 | 1.15
13445 | 13763 | 13.763 | -946 | 1.25
13446 | 13168 | 13.168 | 246 | 3
13447 | 14106 | 14.106 | -879 | 2.85
13448 | 14439 | 14.439 | 581 | 1
13449 | 14414 | 14.414 | -779 | 1.5
13450 | 14508 | 14.508 | -720 | 0.6
13451 | 14466 | 14.466 | 493 | 2.95
13452 | 14283 | 14.283 | -582 | 3.4
13453 | 14401 | 14.401 | 709 | 0.95
13454 | 14236 | 14.236 | -173 | 2.45
13455 | 14502 | 14.502 | 495 | 0.5
13456 | 14344 | 14.344 | -996 | 0
13457 | 14349 | 14.349 | -440 | 3.2
13458 | 14303 | 14.303 | 198 | 3
13459 | 14440 | 14.44 | -311 | 1.05
13460 | 14197 | 14.197 | 220 | 1.55
13461 | 14131 | 14.131 | 994 | 4.8
13462 | 14078 | 14.078 | 301 | 3.3
13463 | 14209 | 14.209 | 879 | 1.8
13464 | 14072 | 14.072 | 174 | 1.4
13465 | 14102 | 14.102 | -339 | 2.3
13466 | 13957 | 13.957 | 273 | 3.45
13467 | 3658 | 3.658 | -676 | 3.9
13468 | 0 | 0 | 131 | 3.35
13469 | 0 | 0 | 742 | 0.3
13470 | 0 | 0 | -185 | 3.05
13471 | 0 | 0 | 334 | 2.1
13472 | 0 | 0 | 572 | 1
13473 | 5202 | 5.202 | -812 | 0.4
13474 | 13541 | 13.541 | -3 | 0.05
13475 | 14194 | 14.194 | -527 | 0.9
13476 | 14249 | 14.249 | -209 | 2.4
13477 | 13989 | 13.989 | 153 | 0.95
13478 | 14239 | 14.239 | 781 | 2.05
13479 | 14048 | 14.048 | 643 | 3.55
13480 | 14222 | 14.222 | -424 | 1.55
13481 | 14240 | 14.24 | 145 | 4.5
13482 | 14173 | 14.173 | -995 | 1.95
13483 | 14322 | 14.322 | 5 | 3.35
13484 | 14143 | 14.143 | -351 | 2.15
13485 | 14246 | 14.246 | 613 | 2.2
13486 | 14213 | 14.213 | -494 | 1.75
13487 | 14204 | 14.204 | 966 | 4.95
13488 | 13395 | 13.395 | -413 | 1.2
13489 | 13167 | 13.167 | -160 | 0.6
13490 | 14232 | 14.232 | -85 | 0.55
13491 | 14507 | 14.507 | 120 | 2.1
13492 | 14390 | 14.39 | 975 | 1.85
13493 | 14325 | 14.325 | -34 | 3.8
13494 | 14342 | 14.342 | 531 | 1.3
13495 | 14583 | 14.583 | -272 | 2.9
13496 | 14358 | 14.358 | 99 | 0.2
13497 | 14402 | 14.402 | -682 | 3.5
13498 | 14506 | 14.506 | 653 | 3.95
13499 | 14492 | 14.492 | -975 | 2.4
13500 | 14561 | 14.561 | -800 | 3.55
13501 | 14372 | 14.372 | -618 | 3
13502 | 14283 | 14.283 | -409 | 3.85
13503 | 14477 | 14.477 | 261 | 2.05
13504 | 14021 | 14.021 | -619 | 0.05
13505 | 12129 | 12.129 | 130 | 2.1
13506 | 14258 | 14.258 | 46 | 3.45
13507 | 14262 | 14.262 | -483 | 2.05
13508 | 14184 | 14.184 | -326 | 0.55
13509 | 14143 | 14.143 | 257 | 4.1
13510 | 14123 | 14.123 | 205 | 0.75
13511 | 13996 | 13.996 | 73 | 1.9
13512 | 13919 | 13.919 | -847 | 2.9
13513 | 13972 | 13.972 | 505 | 4.6
13514 | 14033 | 14.033 | -263 | 4.95
13515 | 13880 | 13.88 | -73 | 0.3
13516 | 13845 | 13.845 | -309 | 4.3
13517 | 13969 | 13.969 | 898 | 3.5
13518 | 13748 | 13.748 | -28 | 3.05
13519 | 13843 | 13.843 | -300 | 1.3
13520 | 13748 | 13.748 | 281 | 0.5
13521 | 13856 | 13.856 | -139 | 1.9
13522 | 13785 | 13.785 | 18 | 0.15
13523 | 13724 | 13.724 | 227 | 0.6
13524 | 13709 | 13.709 | -489 | 4.55
13525 | 13764 | 13.764 | -849 | 0.45
13526 | 13800 | 13.8 | 636 | 2.5
13527 | 13706 | 13.706 | -763 | 5
13528 | 13882 | 13.882 | 858 | 3.5
13529 | 13838 | 13.838 | -135 | 2.2
13530 | 13901 | 13.901 | 204 | 3.2
13531 | 13839 | 13.839 | -363 | 4.5
13532 | 14033 | 14.033 | 796 | 5
13533 | 14022 | 14.022 | 6 | 2
13534 | 13937 | 13.937 | 422 | 3
13535 | 14018 | 14.018 | -840 | 0.05
13536 | 13428 | 13.428 | 86 | 0.6
13537 | 12850 | 12.85 | -162 | 0.5
13538 | 10599 | 10.599 | -667 | 2.95
13539 | 13104 | 13.104 | -260 | 1.85
13540 | 13366 | 13.366 | 17 | 2.7
13541 | 12855 | 12.855 | 575 | 0.5
13542 | 13665 | 13.665 | 766 | 1.95
13543 | 13930 | 13.93 | 313 | 3.8
13544 | 13997 | 13.997 | -4 | 2
13545 | 13957 | 13.957 | 108 | 0.45
13546 | 13904 | 13.904 | 647 | 4.2
13547 | 14020 | 14.02 | 573 | 2.35
13548 | 14227 | 14.227 | -517 | 3.5
13549 | 14211 | 14.211 | -69 | 3.15
13550 | 14229 | 14.229 | -881 | 3.3
13551 | 14108 | 14.108 | 87 | 3.05
13552 | 13987 | 13.987 | 845 | 3.15
13553 | 14092 | 14.092 | -168 | 1.85
13554 | 14023 | 14.023 | 891 | 3.75
13555 | 14047 | 14.047 | -643 | 1.9
13556 | 14041 | 14.041 | 207 | 3.25
13557 | 13900 | 13.9 | -501 | 4.5
13558 | 13872 | 13.872 | 946 | 2.5
13559 | 13769 | 13.769 | -852 | 3.2
13560 | 13881 | 13.881 | 445 | 3.35
13561 | 13927 | 13.927 | 681 | 3.3
13562 | 13715 | 13.715 | -69 | 1.05
13563 | 13903 | 13.903 | 458 | 1.25
13564 | 13888 | 13.888 | -517 | 2.1
13565 | 13891 | 13.891 | -19 | 0.55
13566 | 13791 | 13.791 | 829 | 1.75
13567 | 13911 | 13.911 | -673 | 2.75
13568 | 13889 | 13.889 | -298 | 0.25
13569 | 13584 | 13.584 | 300 | 3.95
13570 | 13821 | 13.821 | 886 | 0.85
13571 | 14021 | 14.021 | 857 | 0.4
13572 | 13909 | 13.909 | 800 | 3.65
13573 | 13846 | 13.846 | -921 | 4.85
13574 | 13917 | 13.917 | 952 | 4.2
13575 | 13944 | 13.944 | 488 | 2.45
13576 | 14019 | 14.019 | -242 | 0.4
13577 | 14072 | 14.072 | 565 | 0.1
13578 | 14084 | 14.084 | -227 | 3.45
13579 | 14061 | 14.061 | -867 | 4.75
13580 | 14159 | 14.159 | 560 | 2.85
13581 | 14178 | 14.178 | 829 | 2.3
13582 | 14282 | 14.282 | 467 | 2.3
13583 | 14254 | 14.254 | 280 | 0.45
13584 | 13608 | 13.608 | 772 | 0.1
13585 | 12834 | 12.834 | -634 | 3.9
13586 | 13885 | 13.885 | -401 | 3.75
13587 | 14139 | 14.139 | -809 | 2.7
13588 | 14410 | 14.41 | 559 | 2.2
13589 | 14383 | 14.383 | -161 | 1.1
13590 | 14510 | 14.51 | 739 | 4.5
13591 | 14529 | 14.529 | -773 | 5
13592 | 14469 | 14.469 | -318 | 1.8
13593 | 14308 | 14.308 | -321 | 4
13594 | 14375 | 14.375 | -82 | 3.4
13595 | 14484 | 14.484 | 509 | 0.6
13596 | 14506 | 14.506 | 287 | 2
13597 | 14299 | 14.299 | 111 | 2.7
13598 | 14409 | 14.409 | -626 | 4.75
13599 | 14227 | 14.227 | -863 | 1.35
13600 | 14546 | 14.546 | 918 | 2.65
13601 | 14285 | 14.285 | -24 | 3.6
13602 | 14335 | 14.335 | -472 | 2.5
13603 | 14212 | 14.212 | -338 | 1.55
13604 | 14316 | 14.316 | 649 | 2.9
13605 | 14164 | 14.164 | 257 | 1.9
13606 | 14087 | 14.087 | -461 | 3.05
13607 | 14173 | 14.173 | 413 | 0.9
13608 | 14195 | 14.195 | -178 | 1.75
13609 | 13979 | 13.979 | 122 | 5
13610 | 14154 | 14.154 | 141 | 1.25
13611 | 14105 | 14.105 | -718 | 1.45
13612 | 14100 | 14.1 | -670 | 3.7
13613 | 14188 | 14.188 | 34 | 1.75
13614 | 14181 | 14.181 | 950 | 2.65
13615 | 14212 | 14.212 | -797 | 3
13616 | 14225 | 14.225 | -542 | 0.4
13617 | 14223 | 14.223 | 759 | 3
13618 | 10690 | 10.69 | -60 | 4
13619 | 13389 | 13.389 | -902 | 4.5
13620 | 14175 | 14.175 | -880 | 3.25
13621 | 14330 | 14.33 | -268 | 0.95
13622 | 14209 | 14.209 | -550 | 0.75
13623 | 14187 | 14.187 | -76 | 2.05
13624 | 14491 | 14.491 | -804 | 3.75
13625 | 14238 | 14.238 | 418 | 2.45
13626 | 14512 | 14.512 | 471 | 0.7
13627 | 14288 | 14.288 | 59 | 0.5
13628 | 14425 | 14.425 | 908 | 2
13629 | 14308 | 14.308 | -22 | 2.25
13630 | 14508 | 14.508 | 756 | 1
13631 | 14525 | 14.525 | -538 | 4.25
13632 | 14387 | 14.387 | 610 | 2.3
13633 | 13594 | 13.594 | 27 | 3.15
13634 | 13778 | 13.778 | -35 | 0.6
13635 | 13759 | 13.759 | -632 | 3.85
13636 | 14021 | 14.021 | 19 | 4.25
13637 | 13587 | 13.587 | 854 | 1.55
13638 | 13336 | 13.336 | -699 | 1.7
13639 | 14470 | 14.47 | -388 | 0.25
13640 | 14536 | 14.536 | -895 | 1.5
13641 | 14540 | 14.54 | 873 | 2.15
13642 | 14493 | 14.493 | 808 | 2.05
13643 | 14689 | 14.689 | 259 | 1.75
13644 | 14595 | 14.595 | -681 | 2.4
13645 | 14758 | 14.758 | -941 | 0.65
13646 | 14726 | 14.726 | 168 | 2.45
13647 | 14603 | 14.603 | -692 | 0.5
13648 | 14503 | 14.503 | 359 | 4.3
13649 | 14435 | 14.435 | 63 | 3.45
13650 | 14390 | 14.39 | -291 | 1.8
13651 | 14349 | 14.349 | 74 | 4.55
13652 | 14387 | 14.387 | -133 | 1.15
13653 | 14363 | 14.363 | 594 | 3.65
13654 | 14591 | 14.591 | -695 | 4.5
13655 | 14351 | 14.351 | 736 | 1.45
13656 | 14345 | 14.345 | 769 | 4.75
13657 | 14365 | 14.365 | 250 | 0.45
13658 | 14481 | 14.481 | -378 | 4.7
13659 | 14297 | 14.297 | -636 | 3.85
13660 | 14165 | 14.165 | 301 | 2.25
13661 | 14155 | 14.155 | -338 | 2.3
13662 | 14156 | 14.156 | -191 | 2.4
13663 | 14215 | 14.215 | 784 | 3.85
13664 | 14211 | 14.211 | 33 | 0.9
13665 | 14220 | 14.22 | -289 | 1.85
13666 | 14318 | 14.318 | 364 | 1.2
13667 | 14261 | 14.261 | -881 | 4.4
13668 | 14411 | 14.411 | -410 | 0.05
13669 | 14293 | 14.293 | 644 | 1.95
13670 | 14393 | 14.393 | 59 | 1.1
13671 | 14348 | 14.348 | 168 | 4.75
13672 | 14450 | 14.45 | -871 | 3.5
13673 | 14440 | 14.44 | -190 | 2.55
13674 | 14435 | 14.435 | 792 | 3.7
13675 | 14475 | 14.475 | 316 | 1.35
13676 | 14560 | 14.56 | -537 | 2.25
13677 | 14564 | 14.564 | 367 | 3.2
13678 | 14408 | 14.408 | -449 | 3.2
13679 | 14573 | 14.573 | 307 | 4.8
13680 | 13970 | 13.97 | -150 | 1.55
13681 | 13063 | 13.063 | -510 | 4.7
13682 | 14228 | 14.228 | -364 | 3.45
13683 | 14509 | 14.509 | 24 | 1.25
13684 | 14537 | 14.537 | 738 | 0.8
13685 | 14542 | 14.542 | 853 | 3.45
13686 | 14436 | 14.436 | 303 | 3.65
13687 | 14495 | 14.495 | -709 | 1.45
13688 | 14578 | 14.578 | 692 | 3.7
13689 | 14670 | 14.67 | -836 | 0
13690 | 14530 | 14.53 | 327 | 4.45
13691 | 14672 | 14.672 | 959 | 4.55
13692 | 14600 | 14.6 | -754 | 2.95
13693 | 14679 | 14.679 | -634 | 2.1
13694 | 14546 | 14.546 | -416 | 1
13695 | 14512 | 14.512 | -543 | 0.05
13696 | 14531 | 14.531 | -464 | 0.05
13697 | 14590 | 14.59 | 869 | 3.05
13698 | 14561 | 14.561 | 142 | 4.15
13699 | 14686 | 14.686 | 672 | 0.85
13700 | 14541 | 14.541 | 202 | 4.95
13701 | 14444 | 14.444 | 123 | 5
13702 | 14347 | 14.347 | 978 | 1.8
13703 | 14364 | 14.364 | 739 | 1.35
13704 | 14379 | 14.379 | -410 | 2.55
13705 | 14280 | 14.28 | -804 | 3.4
13706 | 14329 | 14.329 | -949 | 4.55
13707 | 14322 | 14.322 | -816 | 0.2
13708 | 14286 | 14.286 | 810 | 3.45
13709 | 14247 | 14.247 | 109 | 1.25
13710 | 14197 | 14.197 | -585 | 2.65
13711 | 14226 | 14.226 | 254 | 0.15
13712 | 14255 | 14.255 | -865 | 1.05
13713 | 14198 | 14.198 | 649 | 1.25
13714 | 14222 | 14.222 | 385 | 1.85
13715 | 14249 | 14.249 | -616 | 3.1
13716 | 14370 | 14.37 | 669 | 3.95
13717 | 14338 | 14.338 | -734 | 2.65
13718 | 14422 | 14.422 | -530 | 4.9
13719 | 14510 | 14.51 | -828 | 1.35
13720 | 14436 | 14.436 | 197 | 0.45
13721 | 14406 | 14.406 | -727 | 1.2
13722 | 14408 | 14.408 | -380 | 0.8
13723 | 14397 | 14.397 | 800 | 4.2
13724 | 14481 | 14.481 | 221 | 4.65
13725 | 14405 | 14.405 | -370 | 0.2
13726 | 14400 | 14.4 | 958 | 1
13727 | 14392 | 14.392 | -144 | 4.1
13728 | 13797 | 13.797 | -985 | 4.3
13729 | 13179 | 13.179 | 514 | 0.65
13730 | 13757 | 13.757 | 676 | 1.2
13731 | 13826 | 13.826 | 644 | 3.5
13732 | 13970 | 13.97 | -706 | 2.6
13733 | 13153 | 13.153 | -499 | 2.8
13734 | 14126 | 14.126 | -179 | 3.75
13735 | 14561 | 14.561 | -136 | 0.05
13736 | 14445 | 14.445 | -877 | 0.35
13737 | 14402 | 14.402 | 233 | 0.95
13738 | 14458 | 14.458 | 451 | 2.25
13739 | 14315 | 14.315 | -494 | 1.15
13740 | 14419 | 14.419 | -349 | 1.55
13741 | 14529 | 14.529 | 496 | 3.7
13742 | 14505 | 14.505 | 128 | 2.3
13743 | 14429 | 14.429 | -412 | 1.85
13744 | 14374 | 14.374 | -243 | 2.1
13745 | 14371 | 14.371 | 640 | 2
13746 | 14435 | 14.435 | -880 | 0.15
13747 | 14312 | 14.312 | 308 | 2.35
13748 | 14376 | 14.376 | 805 | 4.95
13749 | 14316 | 14.316 | 149 | 1.55
13750 | 14138 | 14.138 | 654 | 3.3
13751 | 14307 | 14.307 | 794 | 1.25
13752 | 14248 | 14.248 | -988 | 0.9
13753 | 14220 | 14.22 | -8 | 1
13754 | 14063 | 14.063 | -756 | 4.9
13755 | 14013 | 14.013 | 363 | 4.95
13756 | 14080 | 14.08 | -176 | 3.25
13757 | 14155 | 14.155 | 433 | 0.8
13758 | 14065 | 14.065 | -821 | 4.45
13759 | 14106 | 14.106 | 89 | 4.7
13760 | 13988 | 13.988 | -508 | 3.5
13761 | 14013 | 14.013 | 875 | 2.65
13762 | 14102 | 14.102 | -20 | 0.55
13763 | 14246 | 14.246 | 773 | 1.8
13764 | 14090 | 14.09 | 435 | 2.25
13765 | 14321 | 14.321 | 312 | 1.75
13766 | 14000 | 14 | 136 | 4.4
13767 | 14262 | 14.262 | -704 | 4.3
13768 | 14056 | 14.056 | 703 | 0.75
13769 | 14178 | 14.178 | -114 | 2.9
13770 | 14126 | 14.126 | -36 | 4.55
13771 | 14083 | 14.083 | 147 | 4.95
13772 | 14131 | 14.131 | 59 | 4.2
13773 | 14240 | 14.24 | 465 | 0.7
13774 | 14112 | 14.112 | -594 | 1.3
13775 | 14134 | 14.134 | -702 | 2.8
13776 | 13316 | 13.316 | 682 | 0.35
13777 | 12897 | 12.897 | 677 | 2
13778 | 13847 | 13.847 | -597 | 2.25
13779 | 14212 | 14.212 | 707 | 3
13780 | 14243 | 14.243 | 53 | 4.1
13781 | 14245 | 14.245 | -519 | 3.3
13782 | 14190 | 14.19 | 100 | 3.85
13783 | 14138 | 14.138 | -826 | 4.7
13784 | 14160 | 14.16 | -303 | 3.15
13785 | 14130 | 14.13 | 498 | 2.2
13786 | 14334 | 14.334 | -865 | 0.35
13787 | 14278 | 14.278 | -840 | 3.5
13788 | 14185 | 14.185 | 89 | 1.15
13789 | 14171 | 14.171 | -35 | 1.15
13790 | 14346 | 14.346 | -291 | 0.55
13791 | 14255 | 14.255 | -496 | 1.9
13792 | 14352 | 14.352 | 530 | 4.65
13793 | 14162 | 14.162 | -699 | 3.3
13794 | 14028 | 14.028 | -135 | 4.35
13795 | 14219 | 14.219 | 158 | 5
13796 | 14277 | 14.277 | 648 | 0.65
13797 | 14048 | 14.048 | 248 | 0.8
13798 | 13972 | 13.972 | -862 | 3.45
13799 | 13990 | 13.99 | -750 | 1.4
13800 | 13912 | 13.912 | -77 | 4.35
13801 | 13878 | 13.878 | -344 | 2.9
13802 | 13722 | 13.722 | 439 | 3.7
13803 | 13808 | 13.808 | -339 | 3.35
13804 | 13709 | 13.709 | -887 | 0.35
13805 | 13747 | 13.747 | -161 | 4.8
13806 | 13735 | 13.735 | 169 | 0.75
13807 | 13800 | 13.8 | 475 | 3.8
13808 | 13800 | 13.8 | -485 | 4.95
13809 | 13844 | 13.844 | 351 | 0.55
13810 | 13993 | 13.993 | -720 | 1.35
13811 | 13982 | 13.982 | 343 | 0.35
13812 | 13964 | 13.964 | -71 | 1.35
13813 | 14142 | 14.142 | 339 | 2.4
13814 | 14115 | 14.115 | -110 | 3.9
13815 | 13970 | 13.97 | 901 | 2.65
13816 | 14128 | 14.128 | 249 | 4.05
13817 | 14263 | 14.263 | 858 | 0.8
13818 | 14276 | 14.276 | 144 | 0.15
13819 | 14121 | 14.121 | -160 | 1.75
13820 | 14434 | 14.434 | 943 | 3.55
13821 | 14339 | 14.339 | 69 | 1.55
13822 | 14235 | 14.235 | -410 | 1
13823 | 14183 | 14.183 | -309 | 1.85
13824 | 14199 | 14.199 | -673 | 5
13825 | 14067 | 14.067 | -614 | 0.1
13826 | 14284 | 14.284 | 547 | 2.8
13827 | 14056 | 14.056 | 698 | 3
13828 | 14145 | 14.145 | 610 | 2.6
13829 | 14152 | 14.152 | 575 | 1.95
13830 | 13540 | 13.54 | 325 | 0.2
13831 | 13189 | 13.189 | -845 | 5
13832 | 13664 | 13.664 | -3 | 2.5
13833 | 13574 | 13.574 | 856 | 0.1
13834 | 13732 | 13.732 | -946 | 2.5
13835 | 13081 | 13.081 | -952 | 2.9
13836 | 13722 | 13.722 | -244 | 2.7
13837 | 14328 | 14.328 | -602 | 0.3
13838 | 14297 | 14.297 | 143 | 3.15
13839 | 14413 | 14.413 | 908 | 4.9
13840 | 14259 | 14.259 | -16 | 4.2
13841 | 14198 | 14.198 | -980 | 0.55
13842 | 14159 | 14.159 | 445 | 2.1
13843 | 14153 | 14.153 | -432 | 4.85
13844 | 14051 | 14.051 | 314 | 1.85
13845 | 14319 | 14.319 | 423 | 3.75
13846 | 14082 | 14.082 | 1000 | 2.6
13847 | 14218 | 14.218 | 476 | 2.7
13848 | 14056 | 14.056 | 532 | 0.1
13849 | 14120 | 14.12 | -805 | 4.4
13850 | 13918 | 13.918 | -825 | 1.7
13851 | 13963 | 13.963 | -677 | 1.2
13852 | 13954 | 13.954 | 705 | 0.45
13853 | 14056 | 14.056 | 738 | 4.2
13854 | 14122 | 14.122 | -819 | 4.2
13855 | 14089 | 14.089 | 380 | 2.3
13856 | 14221 | 14.221 | -966 | 1.2
13857 | 14115 | 14.115 | 384 | 1.25
13858 | 14270 | 14.27 | -448 | 4.8
13859 | 14080 | 14.08 | -503 | 4.1
13860 | 14219 | 14.219 | 287 | 4.75
13861 | 14198 | 14.198 | 548 | 2.75
13862 | 14251 | 14.251 | -476 | 0.55
13863 | 14294 | 14.294 | 710 | 1.05
13864 | 14276 | 14.276 | 111 | 3
13865 | 14321 | 14.321 | 538 | 4.2
13866 | 14241 | 14.241 | 913 | 4.4
13867 | 14291 | 14.291 | -197 | 0.3
13868 | 14379 | 14.379 | 302 | 4.05
13869 | 14332 | 14.332 | 61 | 0
13870 | 14469 | 14.469 | -155 | 1.65
13871 | 14204 | 14.204 | -403 | 1.5
13872 | 13362 | 13.362 | 520 | 1.55
13873 | 13228 | 13.228 | 728 | 0.75
13874 | 14266 | 14.266 | 27 | 2
13875 | 14395 | 14.395 | -683 | 2.1
13876 | 14323 | 14.323 | -115 | 2.75
13877 | 14490 | 14.49 | 490 | 3.35
13878 | 14485 | 14.485 | -449 | 3.5
13879 | 14339 | 14.339 | -257 | 0.35
13880 | 14387 | 14.387 | 525 | 4.7
13881 | 14400 | 14.4 | -578 | 1.25
13882 | 14348 | 14.348 | -502 | 1.6
13883 | 14530 | 14.53 | -57 | 1.6
13884 | 14404 | 14.404 | 557 | 3.55
13885 | 14494 | 14.494 | 898 | 3.7
13886 | 14343 | 14.343 | 486 | 4.95
13887 | 14460 | 14.46 | 802 | 0.9
13888 | 14314 | 14.314 | -967 | 3.05
13889 | 14250 | 14.25 | -462 | 3.25
13890 | 14273 | 14.273 | -48 | 0.85
13891 | 14476 | 14.476 | 394 | 1.7
13892 | 14217 | 14.217 | 231 | 2
13893 | 14197 | 14.197 | 470 | 4.25
13894 | 14203 | 14.203 | -260 | 1.25
13895 | 14189 | 14.189 | -458 | 1.55
13896 | 14124 | 14.124 | 296 | 1.4
13897 | 14188 | 14.188 | 54 | 0.4
13898 | 14122 | 14.122 | -248 | 3.4
13899 | 14155 | 14.155 | 466 | 1.15
13900 | 14192 | 14.192 | 16 | 3.35
13901 | 14120 | 14.12 | 580 | 2.2
13902 | 14048 | 14.048 | -272 | 3.55
13903 | 14123 | 14.123 | 383 | 0.6
13904 | 14137 | 14.137 | -728 | 3.65
13905 | 13967 | 13.967 | 90 | 2.55
13906 | 14078 | 14.078 | -919 | 0.45
13907 | 14164 | 14.164 | 303 | 2.2
13908 | 14194 | 14.194 | -126 | 4.7
13909 | 14181 | 14.181 | -823 | 3.45
13910 | 14236 | 14.236 | 669 | 4.5
13911 | 14263 | 14.263 | 474 | 3.95
13912 | 14403 | 14.403 | 453 | 1.85
13913 | 14422 | 14.422 | 818 | 3.45
13914 | 14411 | 14.411 | 503 | 2.8
13915 | 14423 | 14.423 | 354 | 3.9
13916 | 14541 | 14.541 | 588 | 2.55
13917 | 14469 | 14.469 | -819 | 2.3
13918 | 14621 | 14.621 | 688 | 1.7
13919 | 14570 | 14.57 | -379 | 0.95
13920 | 13894 | 13.894 | -91 | 4.3
13921 | 13539 | 13.539 | 115 | 3.25
13922 | 13917 | 13.917 | 65 | 0.35
13923 | 13978 | 13.978 | 770 | 4.85
13924 | 13893 | 13.893 | -191 | 2.95
13925 | 13095 | 13.095 | 695 | 2.55
13926 | 14513 | 14.513 | -386 | 0.5
13927 | 14552 | 14.552 | -120 | 4.3
13928 | 14469 | 14.469 | 783 | 3.8
13929 | 14653 | 14.653 | -857 | 2.25
13930 | 14742 | 14.742 | -801 | 0.7
13931 | 14608 | 14.608 | 979 | 2.8
13932 | 14540 | 14.54 | -238 | 1.15
13933 | 14565 | 14.565 | 168 | 5
13934 | 14598 | 14.598 | 673 | 3.15
13935 | 14575 | 14.575 | 625 | 1.65
13936 | 14491 | 14.491 | -490 | 4.9
13937 | 14559 | 14.559 | -416 | 4
13938 | 14409 | 14.409 | -537 | 4.8
13939 | 14396 | 14.396 | 705 | 4.15
13940 | 14426 | 14.426 | -10 | 1.55
13941 | 14200 | 14.2 | 436 | 1.4
13942 | 14194 | 14.194 | 861 | 1.05
13943 | 14274 | 14.274 | -354 | 1.6
13944 | 14145 | 14.145 | 754 | 4.6
13945 | 14103 | 14.103 | 724 | 1.95
13946 | 14021 | 14.021 | -275 | 4.2
13947 | 14016 | 14.016 | 901 | 4.95
13948 | 13993 | 13.993 | 741 | 2.2
13949 | 13957 | 13.957 | -533 | 1.6
13950 | 13930 | 13.93 | 174 | 0.2
13951 | 14015 | 14.015 | 638 | 0.6
13952 | 13915 | 13.915 | -478 | 0.75
13953 | 14000 | 14 | 451 | 2.65
13954 | 13877 | 13.877 | -623 | 0.8
13955 | 13890 | 13.89 | -337 | 1.35
13956 | 14022 | 14.022 | 27 | 0
13957 | 14057 | 14.057 | -595 | 3.35
13958 | 14032 | 14.032 | -280 | 0.05
13959 | 13926 | 13.926 | 956 | 1.8
13960 | 14210 | 14.21 | -613 | 4.95
13961 | 14260 | 14.26 | 203 | 4.4
13962 | 14228 | 14.228 | -85 | 1.45
13963 | 14394 | 14.394 | 318 | 1.7
13964 | 14393 | 14.393 | 296 | 1.55
13965 | 14555 | 14.555 | 888 | 2.5
13966 | 14348 | 14.348 | 124 | 2.75
13967 | 14328 | 14.328 | -286 | 4.95
13968 | 14065 | 14.065 | 862 | 4.95
13969 | 13066 | 13.066 | 600 | 1.1
13970 | 14248 | 14.248 | 333 | 3.85
13971 | 14396 | 14.396 | -558 | 0.8
13972 | 14600 | 14.6 | -866 | 2.5
13973 | 14534 | 14.534 | -713 | 0.1
13974 | 14652 | 14.652 | -226 | 3.95
13975 | 14531 | 14.531 | -957 | 2.75
13976 | 14630 | 14.63 | -838 | 4.75
13977 | 14635 | 14.635 | -454 | 4.85
13978 | 14612 | 14.612 | 356 | 0.95
13979 | 14522 | 14.522 | 232 | 2.85
13980 | 14514 | 14.514 | 368 | 3.7
13981 | 14560 | 14.56 | -921 | 3.65
13982 | 14609 | 14.609 | -612 | 4.3
13983 | 14274 | 14.274 | 775 | 4.3
13984 | 14497 | 14.497 | 167 | 1.4
13985 | 14379 | 14.379 | 251 | 4.3
13986 | 14414 | 14.414 | 632 | 3.9
13987 | 14337 | 14.337 | 444 | 0
13988 | 14299 | 14.299 | -674 | 2.1
13989 | 14181 | 14.181 | 28 | 2.95
13990 | 14110 | 14.11 | 245 | 4.45
13991 | 14173 | 14.173 | -500 | 2.65
13992 | 14057 | 14.057 | -695 | 0.3
13993 | 14122 | 14.122 | -722 | 2.45
13994 | 13775 | 13.775 | -250 | 3.9
13995 | 14033 | 14.033 | 215 | 1.9
13996 | 14089 | 14.089 | -314 | 0.4
13997 | 14025 | 14.025 | 771 | 3.55
13998 | 13939 | 13.939 | 329 | 0.25
13999 | 14012 | 14.012 | -226 | 4.15
14000 | 14002 | 14.002 | -968 | 0.25
14001 | 13984 | 13.984 | 666 | 0.85
14002 | 13936 | 13.936 | 767 | 4.7
14003 | 13911 | 13.911 | -975 | 3.3
14004 | 14059 | 14.059 | 645 | 4.9
14005 | 13975 | 13.975 | 331 | 2.25
14006 | 14070 | 14.07 | 374 | 0.95
14007 | 14111 | 14.111 | -581 | 2.7
14008 | 14225 | 14.225 | -750 | 2.75
14009 | 14312 | 14.312 | 612 | 0.65
14010 | 14222 | 14.222 | -747 | 1.6
14011 | 14336 | 14.336 | -705 | 0.5
14012 | 14380 | 14.38 | -892 | 4.05
14013 | 14416 | 14.416 | 35 | 2.6
14014 | 14454 | 14.454 | 418 | 5
14015 | 14342 | 14.342 | 435 | 3.35
14016 | 14029 | 14.029 | -943 | 1.6
14017 | 13317 | 13.317 | -906 | 5
14018 | 0 | 0 | -242 | 2.65
14019 | 0 | 0 | -433 | 3.75
14020 | 0 | 0 | -988 | 4.15
14021 | 0 | 0 | -430 | 0.6
14022 | 0 | 0 | 18 | 4.35
14023 | 0 | 0 | 116 | 2.3
14024 | 0 | 0 | 373 | 1.6
14025 | 0 | 0 | -153 | 2.6
14026 | 0 | 0 | -276 | 3.45
14027 | 0 | 0 | 593 | 3.75
14028 | 0 | 0 | 155 | 0.4
14029 | 0 | 0 | 756 | 2.2
14030 | 0 | 0 | 290 | 1.3
14031 | 0 | 0 | -421 | 4.8
14032 | 0 | 0 | -106 | 4.5
14033 | 0 | 0 | 472 | 1.9
14034 | 0 | 0 | -806 | 2.15
14035 | 0 | 0 | 929 | 1.9
14036 | 0 | 0 | 526 | 0.85
14037 | 0 | 0 | 237 | 0.15
14038 | 0 | 0 | 36 | 4.25
14039 | 0 | 0 | -87 | 3.95
14040 | 0 | 0 | 743 | 1.95
14041 | 0 | 0 | 686 | 1.25
14042 | 0 | 0 | 835 | 1.85
14043 | 0 | 0 | 302 | 4.4
14044 | 0 | 0 | 370 | 4.5
14045 | 0 | 0 | 122 | 4.2
14046 | 0 | 0 | 311 | 4.35
14047 | 0 | 0 | -958 | 3.15
14048 | 0 | 0 | -638 | 3.75
14049 | 0 | 0 | 669 | 1.85
14050 | 0 | 0 | 389 | 3.15
14051 | 0 | 0 | -869 | 3.1
14052 | 0 | 0 | -316 | 0.15
14053 | 0 | 0 | 675 | 4.15
14054 | 0 | 0 | 979 | 0.05
14055 | 0 | 0 | 948 | 1.15
14056 | 0 | 0 | 884 | 2.95
14057 | 0 | 0 | -72 | 5
14058 | 0 | 0 | 901 | 3.05
14059 | 0 | 0 | 741 | 4.15
14060 | 0 | 0 | 832 | 1.4
14061 | 0 | 0 | 143 | 1.85
14062 | 0 | 0 | 401 | 2.25
14063 | 0 | 0 | 263 | 4.75
14064 | 0 | 0 | -239 | 0.1
14065 | 0 | 0 | 208 | 4.65
14066 | 0 | 0 | 167 | 0.95
14067 | 0 | 0 | 603 | 3.85
14068 | 0 | 0 | -245 | 2.9
14069 | 0 | 0 | -210 | 0.5
14070 | 0 | 0 | 107 | 1.3
14071 | 0 | 0 | 660 | 1.45
14072 | 0 | 0 | 769 | 1.4
14073 | 0 | 0 | -187 | 2.2
14074 | 0 | 0 | 265 | 0.45
14075 | 0 | 0 | -57 | 3.2
14076 | 0 | 0 | 901 | 3
14077 | 0 | 0 | -515 | 3.45
14078 | 0 | 0 | 844 | 2.95
14079 | 0 | 0 | 453 | 3.35
14080 | 0 | 0 | 840 | 3.3
14081 | 0 | 0 | 920 | 3.4
14082 | 0 | 0 | 20 | 1.95
14083 | 0 | 0 | -985 | 0.05
14084 | 0 | 0 | -414 | 0.9
14085 | 0 | 0 | 156 | 0.1
14086 | 0 | 0 | -912 | 4.6
14087 | 0 | 0 | 177 | 4.5
14088 | 0 | 0 | 804 | 0.2
14089 | 0 | 0 | 627 | 4.45
14090 | 0 | 0 | -832 | 4.9
14091 | 0 | 0 | 58 | 0.1
14092 | 0 | 0 | -506 | 3.1
14093 | 0 | 0 | 28 | 1
14094 | 0 | 0 | 320 | 0.05
14095 | 0 | 0 | -126 | 3.15
14096 | 0 | 0 | -740 | 3.2
14097 | 0 | 0 | -993 | 4.8
14098 | 0 | 0 | 163 | 3.25
14099 | 0 | 0 | 430 | 4.95
14100 | 0 | 0 | 126 | 2.6
14101 | 0 | 0 | 757 | 4.8
14102 | 0 | 0 | -941 | 2.35
14103 | 0 | 0 | -906 | 2.45
14104 | 0 | 0 | 588 | 1.4
14105 | 0 | 0 | 172 | 3.45
14106 | 0 | 0 | 480 | 4.6
14107 | 0 | 0 | -571 | 4.95
14108 | 0 | 0 | -407 | 4.75
14109 | 0 | 0 | -300 | 4.8
14110 | 0 | 0 | -97 | 0
14111 | 0 | 0 | 452 | 4.85
14112 | 0 | 0 | 324 | 2.4
14113 | 0 | 0 | -593 | 0.25
14114 | 0 | 0 | 975 | 3.2
14115 | 0 | 0 | 364 | 1.95
14116 | 0 | 0 | -491 | 3.25
14117 | 0 | 0 | 59 | 3.35
14118 | 0 | 0 | 665 | 2.45
14119 | 0 | 0 | -1 | 2.65
14120 | 0 | 0 | 596 | 3.65
14121 | 0 | 0 | 244 | 4.6
14122 | 0 | 0 | 618 | 0.1
14123 | 0 | 0 | 696 | 1.05
14124 | 0 | 0 | 513 | 4.4
14125 | 0 | 0 | -42 | 0.85
14126 | 0 | 0 | -44 | 0.65
14127 | 0 | 0 | 41 | 4.5
14128 | 0 | 0 | -784 | 0.3
14129 | 0 | 0 | -735 | 3.35
14130 | 0 | 0 | -446 | 2.85
14131 | 0 | 0 | -442 | 3.15
14132 | 0 | 0 | -5 | 4.05
14133 | 0 | 0 | -96 | 1.2
14134 | 0 | 0 | 61 | 4.9
14135 | 0 | 0 | -386 | 2.5
14136 | 0 | 0 | -915 | 4.75
14137 | 0 | 0 | 541 | 4.4
14138 | 0 | 0 | -79 | 4.4
14139 | 0 | 0 | -307 | 1.9
14140 | 0 | 0 | 904 | 4.95
14141 | 0 | 0 | 997 | 4.6
14142 | 0 | 0 | 790 | 3.65
14143 | 0 | 0 | 526 | 4
14144 | 0 | 0 | 685 | 1.55
14145 | 0 | 0 | 430 | 0.75
14146 | 0 | 0 | 192 | 4.2
14147 | 0 | 0 | 322 | 2.6
14148 | 0 | 0 | 346 | 4.1
14149 | 0 | 0 | -253 | 0.2
14150 | 0 | 0 | -280 | 4.75
14151 | 0 | 0 | -713 | 2.55
14152 | 0 | 0 | 128 | 4
14153 | 0 | 0 | 614 | 2.95
14154 | 0 | 0 | -124 | 3.95
14155 | 0 | 0 | -576 | 3.5
14156 | 0 | 0 | 205 | 2.75
14157 | 0 | 0 | -724 | 4.65
14158 | 0 | 0 | 783 | 1.1
14159 | 0 | 0 | -294 | 4.95
14160 | 0 | 0 | -58 | 3.5
14161 | 0 | 0 | 435 | 3.25
14162 | 0 | 0 | -921 | 2.95
14163 | 0 | 0 | -641 | 3.4
14164 | 0 | 0 | -388 | 3.75
14165 | 0 | 0 | -990 | 3.35
14166 | 0 | 0 | 366 | 1.4
14167 | 0 | 0 | -832 | 3
14168 | 0 | 0 | -898 | 1.6
14169 | 0 | 0 | 256 | 4.35
14170 | 0 | 0 | -342 | 1.15
14171 | 0 | 0 | 137 | 2.55
14172 | 0 | 0 | -52 | 1.95
14173 | 0 | 0 | 797 | 0.4
14174 | 0 | 0 | -33 | 1.1
14175 | 0 | 0 | 53 | 2.4
14176 | 0 | 0 | -565 | 4.65
14177 | 0 | 0 | -143 | 3.6
14178 | 0 | 0 | 110 | 1
14179 | 0 | 0 | 608 | 0.15
14180 | 0 | 0 | 665 | 4.95
14181 | 0 | 0 | -33 | 2.15
14182 | 0 | 0 | 495 | 3.3
14183 | 0 | 0 | 239 | 2
14184 | 0 | 0 | -526 | 1.85
14185 | 0 | 0 | -150 | 4.35
14186 | 0 | 0 | -67 | 0.4
14187 | 0 | 0 | 628 | 4.75
14188 | 0 | 0 | -23 | 3.5
14189 | 0 | 0 | -295 | 3.45
14190 | 0 | 0 | 796 | 3
14191 | 0 | 0 | 97 | 1.05
14192 | 0 | 0 | 767 | 3.7
14193 | 0 | 0 | -847 | 0.5
14194 | 0 | 0 | -627 | 4.6
14195 | 0 | 0 | 393 | 0.15
14196 | 0 | 0 | 934 | 3.2
14197 | 0 | 0 | -777 | 0.1
14198 | 0 | 0 | 677 | 0.5
14199 | 0 | 0 | -516 | 4.75
14200 | 0 | 0 | -940 | 1.8
14201 | 0 | 0 | 952 | 2.2
14202 | 0 | 0 | -440 | 2.3
14203 | 0 | 0 | -105 | 0.8
14204 | 0 | 0 | -416 | 0.85
14205 | 0 | 0 | -141 | 0.1
14206 | 0 | 0 | -947 | 0.8
14207 | 0 | 0 | 104 | 3.95
14208 | 0 | 0 | 118 | 3.45
14209 | 0 | 0 | -474 | 1.7
14210 | 0 | 0 | -677 | 3.5
14211 | 0 | 0 | 922 | 2.45
14212 | 0 | 0 | -132 | 1.5
14213 | 0 | 0 | -926 | 3
14214 | 0 | 0 | 914 | 0.75
14215 | 0 | 0 | -333 | 2.55
14216 | 0 | 0 | -650 | 1.15
14217 | 0 | 0 | 8 | 2.8
14218 | 0 | 0 | 899 | 3.95
14219 | 0 | 0 | 528 | 4.6
14220 | 0 | 0 | 967 | 1.15
14221 | 0 | 0 | 246 | 2.5
14222 | 0 | 0 | 341 | 0.45
14223 | 0 | 0 | -875 | 2.85
14224 | 0 | 0 | -575 | 4.3
14225 | 0 | 0 | -121 | 1.6
14226 | 0 | 0 | 272 | 1.7
14227 | 0 | 0 | -241 | 1.65
14228 | 0 | 0 | -315 | 3.05
14229 | 0 | 0 | 680 | 1.75
14230 | 0 | 0 | -151 | 2.1
14231 | 0 | 0 | 632 | 0.95
14232 | 0 | 0 | -19 | 3.7
14233 | 0 | 0 | 501 | 0.75
14234 | 0 | 0 | -497 | 3.3
14235 | 0 | 0 | 960 | 4.5
14236 | 0 | 0 | 768 | 4.3
14237 | 0 | 0 | 39 | 2.2
14238 | 0 | 0 | -662 | 4
14239 | 0 | 0 | -267 | 4.8
14240 | 0 | 0 | 319 | 0.25
14241 | 0 | 0 | 729 | 1
14242 | 0 | 0 | -139 | 3.25
14243 | 0 | 0 | 376 | 0.4
14244 | 0 | 0 | -334 | 3.4
14245 | 0 | 0 | 453 | 1.15
14246 | 0 | 0 | -950 | 4.45
14247 | 0 | 0 | 216 | 1
14248 | 0 | 0 | 469 | 4.6
14249 | 0 | 0 | -260 | 1.7
14250 | 0 | 0 | 990 | 1.5
14251 | 0 | 0 | -671 | 4.8
14252 | 0 | 0 | 147 | 4.8
14253 | 0 | 0 | -806 | 0.35
14254 | 0 | 0 | 481 | 3.35
14255 | 0 | 0 | -396 | 4.8
14256 | 0 | 0 | 926 | 5
14257 | 0 | 0 | 175 | 1.9
14258 | 0 | 0 | -642 | 3.4
14259 | 0 | 0 | 805 | 0.8
14260 | 0 | 0 | 444 | 4.2
14261 | 0 | 0 | -6 | 4.3
14262 | 0 | 0 | 706 | 2.05
14263 | 0 | 0 | 511 | 3.45
14264 | 0 | 0 | 642 | 2
14265 | 0 | 0 | 948 | 3.35
14266 | 0 | 0 | 100 | 0.65
14267 | 0 | 0 | 370 | 3.2
14268 | 0 | 0 | 563 | 2.45
14269 | 0 | 0 | -958 | 0.1
14270 | 0 | 0 | 913 | 3.25
14271 | 0 | 0 | -886 | 3.15
14272 | 0 | 0 | -536 | 0.15
14273 | 0 | 0 | 451 | 1.95
14274 | 0 | 0 | 924 | 2.25
14275 | 0 | 0 | -949 | 1.45
14276 | 0 | 0 | -868 | 1.5
14277 | 0 | 0 | -966 | 0.9
14278 | 0 | 0 | -852 | 3.55
14279 | 0 | 0 | -3 | 4.35
14280 | 0 | 0 | 247 | 3.25
14281 | 0 | 0 | -919 | 0
14282 | 0 | 0 | -3 | 3.85
14283 | 0 | 0 | -848 | 4.25
14284 | 0 | 0 | -743 | 4
14285 | 0 | 0 | -569 | 4.25
14286 | 0 | 0 | 548 | 0.95
14287 | 0 | 0 | -960 | 1.75
14288 | 0 | 0 | -138 | 1.4
14289 | 0 | 0 | -908 | 3.15
14290 | 0 | 0 | -984 | 2.75
14291 | 0 | 0 | 919 | 4.45
14292 | 0 | 0 | -803 | 4.8
14293 | 0 | 0 | -196 | 2.15
14294 | 0 | 0 | -328 | 3.3
14295 | 0 | 0 | 481 | 2.8
14296 | 0 | 0 | 507 | 1.2
14297 | 0 | 0 | 56 | 2.25
14298 | 0 | 0 | 362 | 3.1
14299 | 0 | 0 | 949 | 4
14300 | 0 | 0 | -264 | 2.7
14301 | 0 | 0 | -490 | 0.55
14302 | 0 | 0 | 949 | 2.8
14303 | 0 | 0 | 455 | 1.3
14304 | 0 | 0 | -603 | 1.95
14305 | 0 | 0 | -616 | 2.8
14306 | 0 | 0 | -203 | 1.55
14307 | 0 | 0 | 42 | 0.1
14308 | 0 | 0 | 478 | 2.05
14309 | 0 | 0 | -175 | 4.55
14310 | 0 | 0 | 756 | 4.35
14311 | 0 | 0 | 901 | 0.45
14312 | 0 | 0 | -599 | 3.5
14313 | 0 | 0 | -567 | 2.7
14314 | 0 | 0 | -505 | 4.6
14315 | 0 | 0 | -523 | 4.35
14316 | 0 | 0 | -349 | 3.95
14317 | 0 | 0 | 116 | 1.4
14318 | 0 | 0 | 640 | 1.6
14319 | 0 | 0 | -824 | 3.1
14320 | 0 | 0 | 426 | 3.2
14321 | 0 | 0 | -152 | 0.45
14322 | 0 | 0 | -580 | 4.1
14323 | 0 | 0 | -921 | 0.1
14324 | 0 | 0 | -747 | 4.1
14325 | 0 | 0 | 260 | 1.7
14326 | 0 | 0 | 323 | 1.85
14327 | 0 | 0 | 75 | 1.85
14328 | 0 | 0 | 737 | 0.4
14329 | 0 | 0 | 70 | 4.35
14330 | 0 | 0 | -586 | 2
14331 | 0 | 0 | -412 | 3.8
14332 | 0 | 0 | 904 | 1.75
14333 | 0 | 0 | 993 | 3.35
14334 | 0 | 0 | -989 | 1.35
14335 | 0 | 0 | 760 | 2.1
14336 | 0 | 0 | -644 | 2.85
14337 | 0 | 0 | 335 | 2.3
14338 | 0 | 0 | 14 | 2.85
14339 | 0 | 0 | 335 | 4.1
14340 | 0 | 0 | -186 | 2.95
14341 | 0 | 0 | -912 | 4.7
14342 | 0 | 0 | -255 | 3.2
14343 | 0 | 0 | -952 | 0.7
14344 | 0 | 0 | -208 | 0.6
14345 | 0 | 0 | 340 | 3.85
14346 | 0 | 0 | 257 | 4.85
14347 | 0 | 0 | -269 | 1.6
14348 | 0 | 0 | -534 | 2.4
14349 | 0 | 0 | 16 | 3.25
14350 | 0 | 0 | 38 | 4.9
14351 | 0 | 0 | 799 | 1
14352 | 0 | 0 | 866 | 4.7
14353 | 0 | 0 | 810 | 0.2
14354 | 0 | 0 | -238 | 3.65
14355 | 0 | 0 | -218 | 1
14356 | 0 | 0 | 136 | 4.5
14357 | 0 | 0 | -776 | 0.75
14358 | 0 | 0 | -454 | 0.15
14359 | 0 | 0 | 968 | 5
14360 | 0 | 0 | -625 | 1.55
14361 | 0 | 0 | 643 | 4.1
14362 | 0 | 0 | -664 | 3.35
14363 | 0 | 0 | -864 | 3.1
14364 | 0 | 0 | 830 | 2.75
14365 | 0 | 0 | -241 | 4.45
14366 | 0 | 0 | 707 | 2.7
14367 | 0 | 0 | -464 | 0.85
14368 | 0 | 0 | -918 | 3.95
14369 | 0 | 0 | 589 | 2.3
14370 | 0 | 0 | 23 | 1.15
14371 | 0 | 0 | -226 | 1.25
14372 | 0 | 0 | 176 | 4.15
14373 | 0 | 0 | -36 | 0.95
14374 | 0 | 0 | 584 | 4.9
14375 | 0 | 0 | 173 | 2.25
14376 | 0 | 0 | -780 | 4.1
14377 | 0 | 0 | 520 | 3.8
14378 | 0 | 0 | 170 | 0.9
14379 | 0 | 0 | 116 | 2.75
14380 | 0 | 0 | 205 | 0.4
14381 | 0 | 0 | -576 | 0.15
14382 | 0 | 0 | -320 | 4
14383 | 0 | 0 | -217 | 2.75
14384 | 0 | 0 | -396 | 4.4
14385 | 0 | 0 | 809 | 3.1
14386 | 0 | 0 | 864 | 4.15
14387 | 0 | 0 | 13 | 2.05
14388 | 0 | 0 | 650 | 4.05
14389 | 0 | 0 | 23 | 3.05
14390 | 0 | 0 | 314 | 0.75
14391 | 0 | 0 | 146 | 0.3
14392 | 0 | 0 | 650 | 4.05
14393 | 0 | 0 | 283 | 2.25
14394 | 0 | 0 | 741 | 1.35
14395 | 0 | 0 | -227 | 0.4
14396 | 0 | 0 | 376 | 4.2
14397 | 0 | 0 | -915 | 2.75
14398 | 0 | 0 | -418 | 3.85
14399 | 0 | 0 | 498 | 2.65
14400 | 0 | 0 | -305 | 2.85
14401 | 0 | 0 | 982 | 4.5
14402 | 0 | 0 | 619 | 3.85
14403 | 0 | 0 | 723 | 4.5
14404 | 0 | 0 | 217 | 3.4
14405 | 0 | 0 | -125 | 2.85
14406 | 0 | 0 | 588 | 1.6
14407 | 0 | 0 | 195 | 0.95
14408 | 0 | 0 | -768 | 3.5
14409 | 0 | 0 | -912 | 4.85
14410 | 0 | 0 | 323 | 1.6
14411 | 0 | 0 | -636 | 4.3
14412 | 0 | 0 | -515 | 0.45
14413 | 0 | 0 | 50 | 3.15
14414 | 0 | 0 | 785 | 3.05
14415 | 0 | 0 | 621 | 3.1
14416 | 0 | 0 | -563 | 0.45
14417 | 0 | 0 | 762 | 3.7
14418 | 0 | 0 | -993 | 3.8
14419 | 0 | 0 | 52 | 4.8
14420 | 0 | 0 | -5 | 3.8
14421 | 0 | 0 | -713 | 2.75
14422 | 0 | 0 | 765 | 3.7
14423 | 0 | 0 | -267 | 0.25
14424 | 0 | 0 | -335 | 2.95
14425 | 0 | 0 | -505 | 2.05
14426 | 0 | 0 | -535 | 4.9
14427 | 0 | 0 | -288 | 1.75
14428 | 0 | 0 | -140 | 4.2
14429 | 0 | 0 | 953 | 1.3
14430 | 0 | 0 | 792 | 1.15
14431 | 0 | 0 | -468 | 4.8
14432 | 0 | 0 | 93 | 4.6
14433 | 0 | 0 | 997 | 3.75
14434 | 0 | 0 | 498 | 1.05
14435 | 0 | 0 | 765 | 0.05
14436 | 0 | 0 | -880 | 4.4
14437 | 0 | 0 | 122 | 4.45
14438 | 0 | 0 | -563 | 0.75
14439 | 0 | 0 | 251 | 3.45
14440 | 0 | 0 | 472 | 0.9
14441 | 0 | 0 | 201 | 2.95
14442 | 0 | 0 | -229 | 0.8
14443 | 0 | 0 | 202 | 4.05
14444 | 0 | 0 | -850 | 0.6
14445 | 0 | 0 | -249 | 0.8
14446 | 0 | 0 | -311 | 0.85
14447 | 0 | 0 | -238 | 3.35
14448 | 0 | 0 | -700 | 2.45
14449 | 0 | 0 | 766 | 4.05
14450 | 0 | 0 | -2 | 1.05
14451 | 0 | 0 | 39 | 0.4
14452 | 0 | 0 | 115 | 2.65
14453 | 0 | 0 | -294 | 1.25
14454 | 0 | 0 | -299 | 0.55
14455 | 0 | 0 | -321 | 3.8
14456 | 0 | 0 | -897 | 1.05
14457 | 0 | 0 | -507 | 3.55
14458 | 0 | 0 | -19 | 1.3
14459 | 0 | 0 | 930 | 3.25
14460 | 0 | 0 | 431 | 3.65
14461 | 0 | 0 | 173 | 2.25
14462 | 0 | 0 | -972 | 3.35
14463 | 0 | 0 | 600 | 0.4
14464 | 0 | 0 | -990 | 3.55
14465 | 0 | 0 | 414 | 3.8
14466 | 0 | 0 | 390 | 1.2
14467 | 0 | 0 | -861 | 0.35
14468 | 0 | 0 | -133 | 1.3
14469 | 0 | 0 | -557 | 2.35
14470 | 0 | 0 | -808 | 1.5
14471 | 0 | 0 | -898 | 4.35
14472 | 0 | 0 | -249 | 2.3
14473 | 0 | 0 | 758 | 2.25
14474 | 0 | 0 | -962 | 1.2
14475 | 0 | 0 | 495 | 1.1
14476 | 0 | 0 | -556 | 2.65
14477 | 0 | 0 | 699 | 3.45
14478 | 0 | 0 | -493 | 2.35
14479 | 0 | 0 | 112 | 2
14480 | 0 | 0 | -512 | 0.8
14481 | 0 | 0 | 29 | 4.3
14482 | 0 | 0 | 330 | 3.7
14483 | 0 | 0 | -400 | 2.05
14484 | 0 | 0 | -530 | 3.2
14485 | 0 | 0 | 447 | 3.6
14486 | 0 | 0 | 346 | 1.95
14487 | 0 | 0 | 533 | 4.6
14488 | 0 | 0 | 680 | 0.5
14489 | 0 | 0 | 163 | 1.1
14490 | 0 | 0 | -61 | 1.35
14491 | 0 | 0 | -641 | 0.55
14492 | 0 | 0 | 305 | 0.25
14493 | 0 | 0 | -634 | 3.9
14494 | 0 | 0 | -330 | 3.75
14495 | 0 | 0 | -154 | 0.2
14496 | 0 | 0 | 266 | 2.5
14497 | 0 | 0 | 603 | 4.35
14498 | 0 | 0 | -911 | 4.8
14499 | 0 | 0 | 586 | 1.35
14500 | 0 | 0 | -520 | 4.2
14501 | 0 | 0 | 681 | 0.15
14502 | 0 | 0 | -769 | 4.45
14503 | 0 | 0 | 962 | 1.65
14504 | 0 | 0 | -323 | 1.3
14505 | 0 | 0 | -959 | 3.9
14506 | 0 | 0 | -410 | 3.15
14507 | 0 | 0 | -421 | 4
14508 | 0 | 0 | -413 | 4.9
14509 | 0 | 0 | 256 | 4.7
14510 | 0 | 0 | -829 | 3.5
14511 | 0 | 0 | -696 | 0.2
14512 | 0 | 0 | 925 | 4.6
14513 | 0 | 0 | -504 | 3.1
14514 | 0 | 0 | -557 | 2
14515 | 0 | 0 | -25 | 4.65
14516 | 0 | 0 | -956 | 1.2
14517 | 0 | 0 | 157 | 0.9
14518 | 0 | 0 | 65 | 0.4
14519 | 0 | 0 | -271 | 3.2
14520 | 0 | 0 | -149 | 0.3
14521 | 0 | 0 | -50 | 0.95
14522 | 0 | 0 | -621 | 1.15
14523 | 0 | 0 | -398 | 4.1
14524 | 0 | 0 | 842 | 3.2
14525 | 0 | 0 | 859 | 3.4
14526 | 0 | 0 | 884 | 1
14527 | 0 | 0 | 407 | 0.55
14528 | 0 | 0 | 176 | 0.35
14529 | 0 | 0 | -469 | 2.7
14530 | 0 | 0 | -50 | 3.25
14531 | 0 | 0 | -491 | 0.15
14532 | 0 | 0 | -876 | 0.7
14533 | 0 | 0 | 882 | 1.7
14534 | 0 | 0 | 444 | 0
14535 | 0 | 0 | 589 | 3.45
14536 | 0 | 0 | 770 | 4.75
14537 | 0 | 0 | 778 | 1.85
14538 | 0 | 0 | -238 | 2
14539 | 0 | 0 | 853 | 2.8
14540 | 0 | 0 | 805 | 2.6
14541 | 0 | 0 | -217 | 2.15
14542 | 0 | 0 | 775 | 1.2
14543 | 0 | 0 | 685 | 4.85
14544 | 0 | 0 | -443 | 1.3
14545 | 0 | 0 | 689 | 0.85
14546 | 0 | 0 | 782 | 1.7
14547 | 0 | 0 | 26 | 2.6
14548 | 0 | 0 | -150 | 3.45
14549 | 0 | 0 | -211 | 2.3
14550 | 0 | 0 | -616 | 4.6
14551 | 0 | 0 | 964 | 0.95
14552 | 0 | 0 | 698 | 4.05
14553 | 0 | 0 | -350 | 4.65
14554 | 0 | 0 | -277 | 1.4
14555 | 0 | 0 | 705 | 3.85
14556 | 0 | 0 | -901 | 3.05
14557 | 0 | 0 | 485 | 2.65
14558 | 0 | 0 | -35 | 3.05
14559 | 0 | 0 | 308 | 3.2
14560 | 0 | 0 | 337 | 0
14561 | 0 | 0 | 917 | 0.75
14562 | 0 | 0 | -898 | 3.15
14563 | 0 | 0 | -808 | 3.15
14564 | 0 | 0 | -893 | 1.8
14565 | 0 | 0 | 296 | 4.05
14566 | 0 | 0 | -224 | 3.85
14567 | 0 | 0 | -731 | 2.15
14568 | 0 | 0 | -603 | 3.55
14569 | 0 | 0 | -583 | 1.4
14570 | 0 | 0 | -474 | 4
14571 | 0 | 0 | 748 | 4.9
14572 | 0 | 0 | -960 | 4.45
14573 | 0 | 0 | -614 | 1.75
14574 | 0 | 0 | 907 | 0.4
14575 | 0 | 0 | -598 | 0.6
14576 | 0 | 0 | -466 | 4.25
14577 | 0 | 0 | 327 | 0.75
14578 | 0 | 0 | -307 | 4.5
14579 | 0 | 0 | 432 | 4.1
14580 | 0 | 0 | -41 | 3.9
14581 | 0 | 0 | -868 | 1.95
14582 | 0 | 0 | 938 | 2.05
14583 | 0 | 0 | 538 | 0.7
14584 | 0 | 0 | -764 | 0.7
14585 | 0 | 0 | 134 | 0.8
14586 | 0 | 0 | -366 | 0.9
14587 | 0 | 0 | 186 | 0.65
14588 | 0 | 0 | 715 | 3.8
14589 | 0 | 0 | 676 | 2.65
14590 | 0 | 0 | 190 | 3.9
14591 | 0 | 0 | -576 | 2.7
14592 | 0 | 0 | -670 | 4.7
14593 | 0 | 0 | -474 | 4.7
14594 | 0 | 0 | -317 | 3.65
14595 | 0 | 0 | -329 | 1.15
14596 | 0 | 0 | 101 | 4.05
14597 | 0 | 0 | -273 | 4.5
14598 | 0 | 0 | 149 | 2.6
14599 | 0 | 0 | 311 | 2.4
14600 | 0 | 0 | 224 | 1.4
14601 | 0 | 0 | -414 | 4.85
14602 | 0 | 0 | -205 | 0.45
14603 | 0 | 0 | 1 | 4.55
14604 | 0 | 0 | 8 | 3.7
14605 | 0 | 0 | -130 | 0.4
14606 | 0 | 0 | -433 | 3.8
14607 | 0 | 0 | -452 | 0.6
14608 | 0 | 0 | -474 | 0.6
14609 | 0 | 0 | 538 | 0.4
14610 | 0 | 0 | 919 | 3.7
14611 | 0 | 0 | 419 | 1.7
14612 | 0 | 0 | 448 | 3.5
14613 | 0 | 0 | -664 | 2.9
14614 | 0 | 0 | -711 | 1.95
14615 | 0 | 0 | -157 | 1.4
14616 | 0 | 0 | 843 | 0.25
14617 | 0 | 0 | 125 | 2.05
14618 | 0 | 0 | 541 | 2.65
14619 | 0 | 0 | 365 | 0.8
14620 | 0 | 0 | -1 | 4.25
14621 | 0 | 0 | -126 | 2.9
14622 | 0 | 0 | 495 | 0.05
14623 | 0 | 0 | -928 | 4.6
14624 | 0 | 0 | 551 | 2.25
14625 | 0 | 0 | 887 | 2.3
14626 | 0 | 0 | 279 | 0.7
14627 | 0 | 0 | -955 | 2.1
14628 | 0 | 0 | 285 | 2.7
14629 | 0 | 0 | -558 | 2.25
14630 | 0 | 0 | -276 | 2.4
14631 | 0 | 0 | -217 | 1.1
14632 | 0 | 0 | -62 | 3.1
14633 | 0 | 0 | -194 | 2.35
14634 | 0 | 0 | -801 | 3.6
14635 | 0 | 0 | 315 | 4.1
14636 | 0 | 0 | -456 | 1.55
14637 | 0 | 0 | -259 | 3.8
14638 | 0 | 0 | 745 | 1.9
14639 | 0 | 0 | -278 | 2.3
14640 | 14229 | 14.229 | -705 | 0.7
14641 | 14436 | 14.436 | -81 | 2.05
14642 | 14185 | 14.185 | 563 | 2.25
14643 | 14164 | 14.164 | 533 | 4.95
14644 | 11198 | 11.198 | 330 | 0.75
14645 | 10342 | 10.342 | 510 | 4.7
14646 | 8902 | 8.902 | -752 | 1.2
14647 | 10817 | 10.817 | -281 | 3.55
14648 | 14063 | 14.063 | -585 | 1.55
14649 | 14633 | 14.633 | 688 | 1.65
14650 | 14516 | 14.516 | 568 | 4.15
14651 | 14397 | 14.397 | 50 | 0.35
14652 | 14300 | 14.3 | -28 | 2.9
14653 | 14423 | 14.423 | -941 | 1.7
14654 | 14307 | 14.307 | -619 | 4
14655 | 14502 | 14.502 | -69 | 1.9
14656 | 14406 | 14.406 | -463 | 4.2
14657 | 13456 | 13.456 | 49 | 0.35
14658 | 12013 | 12.013 | -713 | 1.65
14659 | 13291 | 13.291 | -473 | 1.65
14660 | 14149 | 14.149 | 461 | 4.55
14661 | 14015 | 14.015 | -22 | 2.9
14662 | 13806 | 13.806 | -101 | 0.75
14663 | 13917 | 13.917 | 188 | 0.65
14664 | 13775 | 13.775 | -685 | 4.6
14665 | 14042 | 14.042 | -764 | 2.85
14666 | 14029 | 14.029 | 275 | 2.65
14667 | 13786 | 13.786 | -900 | 1.6
14668 | 13792 | 13.792 | 28 | 4.65
14669 | 13829 | 13.829 | -563 | 0.2
14670 | 13666 | 13.666 | 954 | 3.45
14671 | 13773 | 13.773 | 845 | 3.4
14672 | 13726 | 13.726 | 113 | 1.55
14673 | 13718 | 13.718 | -232 | 4.8
14674 | 13827 | 13.827 | 601 | 1.3
14675 | 13740 | 13.74 | -90 | 3.25
14676 | 13867 | 13.867 | -282 | 4.1
14677 | 13833 | 13.833 | 76 | 3.6
14678 | 13918 | 13.918 | 47 | 4.95
14679 | 13887 | 13.887 | 712 | 2.8
14680 | 13945 | 13.945 | -883 | 2.9
14681 | 13953 | 13.953 | -865 | 2.35
14682 | 14045 | 14.045 | 817 | 0.8
14683 | 14182 | 14.182 | -763 | 2.65
14684 | 14151 | 14.151 | 51 | 3.9
14685 | 14173 | 14.173 | -534 | 4.45
14686 | 14113 | 14.113 | 553 | 1.45
14687 | 14302 | 14.302 | -566 | 4.1
14688 | 13939 | 13.939 | -813 | 4.8
14689 | 13476 | 13.476 | 164 | 3.4
14690 | 13502 | 13.502 | 94 | 1.9
14691 | 13783 | 13.783 | 911 | 3.4
14692 | 13620 | 13.62 | 170 | 2.5
14693 | 13368 | 13.368 | -424 | 0.15
14694 | 13972 | 13.972 | 159 | 2.2
14695 | 14076 | 14.076 | 395 | 0.1
14696 | 14334 | 14.334 | 684 | 4.95
14697 | 14309 | 14.309 | -118 | 3.15
14698 | 13157 | 13.157 | -986 | 3.1
14699 | 14318 | 14.318 | -235 | 0.3
14700 | 14331 | 14.331 | -153 | 2.95
14701 | 14379 | 14.379 | 49 | 1
14702 | 14354 | 14.354 | 847 | 0.1
14703 | 14182 | 14.182 | 198 | 4.95
14704 | 14329 | 14.329 | -540 | 1.55
14705 | 14120 | 14.12 | -464 | 3.6
14706 | 14110 | 14.11 | 898 | 0.9
14707 | 14159 | 14.159 | 725 | 2.65
14708 | 14143 | 14.143 | -796 | 2.15
14709 | 14108 | 14.108 | 459 | 3.85
14710 | 13914 | 13.914 | -590 | 2.25
14711 | 13940 | 13.94 | -358 | 2.65
14712 | 14066 | 14.066 | -446 | 1.65
14713 | 13872 | 13.872 | -635 | 4.4
14714 | 12194 | 12.194 | -624 | 4.25
14715 | 11466 | 11.466 | -791 | 2.6
14716 | 12678 | 12.678 | -224 | 4.1
14717 | 13909 | 13.909 | 901 | 1.35
14718 | 13925 | 13.925 | 164 | 4.4
14719 | 13842 | 13.842 | 298 | 1.5
14720 | 13776 | 13.776 | -421 | 0.45
14721 | 13692 | 13.692 | -786 | 1
14722 | 13999 | 13.999 | -489 | 4.8
14723 | 14032 | 14.032 | 742 | 1.7
14724 | 13977 | 13.977 | 807 | 0.25
14725 | 13984 | 13.984 | 60 | 2.1
14726 | 14108 | 14.108 | -470 | 2.2
14727 | 14136 | 14.136 | -118 | 0.2
14728 | 14153 | 14.153 | 699 | 0.8
14729 | 14276 | 14.276 | -837 | 3.35
14730 | 14157 | 14.157 | -377 | 4.5
14731 | 14218 | 14.218 | -836 | 4.45
14732 | 14095 | 14.095 | -364 | 1.1
14733 | 14185 | 14.185 | -110 | 3
14734 | 14278 | 14.278 | 842 | 4.3
14735 | 14134 | 14.134 | 508 | 3
14736 | 13710 | 13.71 | -766 | 4.65
14737 | 13628 | 13.628 | 378 | 4.6
14738 | 13745 | 13.745 | -968 | 1.4
14739 | 13690 | 13.69 | 633 | 3.4
14740 | 13393 | 13.393 | -562 | 1.2
14741 | 13656 | 13.656 | 946 | 2.35
14742 | 14374 | 14.374 | -921 | 3.95
14743 | 14211 | 14.211 | -432 | 2.15
14744 | 14314 | 14.314 | 752 | 4.9
14745 | 14330 | 14.33 | 202 | 0.5
14746 | 14360 | 14.36 | 15 | 0.15
14747 | 14464 | 14.464 | 315 | 3.9
14748 | 14359 | 14.359 | -901 | 1.05
14749 | 14446 | 14.446 | -630 | 0.15
14750 | 14377 | 14.377 | 335 | 1.2
14751 | 14289 | 14.289 | -967 | 2.15
14752 | 14275 | 14.275 | 477 | 1.9
14753 | 14325 | 14.325 | 286 | 0.8
14754 | 14224 | 14.224 | -54 | 2.6
14755 | 14277 | 14.277 | -612 | 0.05
14756 | 14238 | 14.238 | -924 | 4.45
14757 | 14194 | 14.194 | 819 | 3.7
14758 | 14194 | 14.194 | 889 | 4.3
14759 | 14077 | 14.077 | 838 | 4.45
14760 | 14032 | 14.032 | 319 | 3.95
14761 | 14057 | 14.057 | -246 | 4.3
14762 | 14014 | 14.014 | 6 | 0.55
14763 | 13900 | 13.9 | 967 | 3.95
14764 | 13868 | 13.868 | -495 | 0.3
14765 | 13858 | 13.858 | -254 | 5
14766 | 14066 | 14.066 | 657 | 4.2
14767 | 13943 | 13.943 | -899 | 0
14768 | 13990 | 13.99 | -825 | 3.65
14769 | 13833 | 13.833 | 853 | 3.1
14770 | 13976 | 13.976 | -494 | 2.95
14771 | 13894 | 13.894 | 23 | 2.75
14772 | 14007 | 14.007 | -731 | 2.45
14773 | 14109 | 14.109 | -795 | 3.65
14774 | 14039 | 14.039 | 287 | 0.2
14775 | 14076 | 14.076 | 600 | 4.1
14776 | 14031 | 14.031 | -88 | 4.4
14777 | 14070 | 14.07 | 137 | 4.75
14778 | 14090 | 14.09 | -584 | 2.05
14779 | 14106 | 14.106 | -889 | 1.9
14780 | 14244 | 14.244 | -266 | 1.3
14781 | 14217 | 14.217 | -310 | 1.05
14782 | 14214 | 14.214 | -74 | 4.65
14783 | 13913 | 13.913 | -212 | 2.9
14784 | 13386 | 13.386 | 150 | 2.45
14785 | 13973 | 13.973 | -801 | 0.2
14786 | 14266 | 14.266 | -63 | 2.5
14787 | 14263 | 14.263 | -313 | 2.4
14788 | 14248 | 14.248 | 259 | 2.8
14789 | 14262 | 14.262 | -264 | 0.45
14790 | 14313 | 14.313 | 349 | 0
14791 | 14245 | 14.245 | 976 | 1.55
14792 | 14346 | 14.346 | 414 | 0.4
14793 | 14226 | 14.226 | -348 | 3.3
14794 | 14255 | 14.255 | -347 | 3.55
14795 | 14319 | 14.319 | -227 | 3.05
14796 | 14340 | 14.34 | 362 | 2.9
14797 | 14294 | 14.294 | -194 | 0.2
14798 | 14242 | 14.242 | 290 | 2.95
14799 | 14310 | 14.31 | 530 | 3.05
14800 | 14335 | 14.335 | 648 | 3.15
14801 | 14286 | 14.286 | 122 | 4.75
14802 | 14240 | 14.24 | -45 | 0.35
14803 | 10771 | 10.771 | 862 | 3.25
14804 | 11561 | 11.561 | 418 | 1.45
14805 | 13083 | 13.083 | -892 | 4
14806 | 13509 | 13.509 | -680 | 2.5
14807 | 14003 | 14.003 | 119 | 2.2
14808 | 13960 | 13.96 | 506 | 1.5
14809 | 14045 | 14.045 | -132 | 3
14810 | 14120 | 14.12 | 901 | 0.15
14811 | 14160 | 14.16 | -409 | 0.85
14812 | 14010 | 14.01 | 641 | 4.65
14813 | 13962 | 13.962 | -935 | 0.85
14814 | 14133 | 14.133 | 61 | 4.45
14815 | 13917 | 13.917 | -830 | 3.35
14816 | 13929 | 13.929 | 858 | 3.35
14817 | 14017 | 14.017 | 931 | 2.8
14818 | 13963 | 13.963 | 746 | 2.75
14819 | 14000 | 14 | 245 | 1.35
14820 | 13977 | 13.977 | -972 | 0.1
14821 | 13930 | 13.93 | 941 | 2
14822 | 14037 | 14.037 | 521 | 0.25
14823 | 14066 | 14.066 | 698 | 1.75
14824 | 14132 | 14.132 | -264 | 0.85
14825 | 14241 | 14.241 | 174 | 2.5
14826 | 14217 | 14.217 | -144 | 2.5
14827 | 14272 | 14.272 | -378 | 2.1
14828 | 14158 | 14.158 | 788 | 1.7
14829 | 14216 | 14.216 | -762 | 0.55
14830 | 14203 | 14.203 | 471 | 0.75
14831 | 14116 | 14.116 | -778 | 3.4
14832 | 13380 | 13.38 | 246 | 2.3
14833 | 14157 | 14.157 | 729 | 3.4
14834 | 14333 | 14.333 | 484 | 2.75
14835 | 14349 | 14.349 | -369 | 4.6
14836 | 14228 | 14.228 | 444 | 0.7
14837 | 14388 | 14.388 | 128 | 0.45
14838 | 14334 | 14.334 | -69 | 2.35
14839 | 14303 | 14.303 | -132 | 2.6
14840 | 14340 | 14.34 | -18 | 0.3
14841 | 14275 | 14.275 | 823 | 1.9
14842 | 14464 | 14.464 | -675 | 4.05
14843 | 14302 | 14.302 | -97 | 1.15
14844 | 14368 | 14.368 | -662 | 0
14845 | 14340 | 14.34 | -932 | 4.5
14846 | 14357 | 14.357 | 556 | 4
14847 | 14431 | 14.431 | -174 | 0.15
14848 | 14362 | 14.362 | 555 | 4.4
14849 | 14313 | 14.313 | -650 | 1.3
14850 | 14379 | 14.379 | 340 | 1.2
14851 | 14256 | 14.256 | -879 | 2.2
14852 | 14235 | 14.235 | 395 | 4.05
14853 | 14285 | 14.285 | 811 | 4.8
14854 | 14294 | 14.294 | -200 | 4.35
14855 | 14303 | 14.303 | -8 | 1.55
14856 | 14363 | 14.363 | 949 | 2.7
14857 | 14288 | 14.288 | 984 | 1.6
14858 | 14345 | 14.345 | -480 | 3.65
14859 | 14353 | 14.353 | 326 | 3.25
14860 | 14393 | 14.393 | -342 | 2.05
14861 | 14269 | 14.269 | 709 | 2.7
14862 | 14340 | 14.34 | 76 | 1
14863 | 14207 | 14.207 | -519 | 4.1
14864 | 14404 | 14.404 | 39 | 1.9
14865 | 14227 | 14.227 | -297 | 2.35
14866 | 14102 | 14.102 | -779 | 2.95
14867 | 14002 | 14.002 | 41 | 1.7
14868 | 14066 | 14.066 | 239 | 1
14869 | 13954 | 13.954 | 598 | 1.85
14870 | 13991 | 13.991 | -376 | 3.55
14871 | 13944 | 13.944 | 403 | 4.7
14872 | 14079 | 14.079 | -255 | 4.65
14873 | 14102 | 14.102 | -928 | 3.85
14874 | 14105 | 14.105 | -390 | 3.3
14875 | 14070 | 14.07 | 924 | 2.85
14876 | 13987 | 13.987 | -808 | 1.7
14877 | 13969 | 13.969 | 921 | 0.3
14878 | 14151 | 14.151 | 0 | 1.2
14879 | 14071 | 14.071 | 236 | 1.25
14880 | 13963 | 13.963 | -22 | 2.05
14881 | 13926 | 13.926 | 9 | 1.1
14882 | 13651 | 13.651 | 549 | 3.4
14883 | 13331 | 13.331 | 592 | 1
14884 | 13466 | 13.466 | 960 | 4.9
14885 | 13421 | 13.421 | 26 | 3.75
14886 | 13486 | 13.486 | 966 | 2.35
14887 | 13380 | 13.38 | -459 | 2.3
14888 | 14166 | 14.166 | 969 | 2.15
14889 | 14223 | 14.223 | 761 | 4.05
14890 | 14246 | 14.246 | -7 | 1.3
14891 | 14250 | 14.25 | 801 | 1.65
14892 | 14369 | 14.369 | -935 | 0.95
14893 | 14263 | 14.263 | -451 | 4
14894 | 14349 | 14.349 | 407 | 0.4
14895 | 14243 | 14.243 | -959 | 3.8
14896 | 14140 | 14.14 | -899 | 2.55
14897 | 14260 | 14.26 | -633 | 2.65
14898 | 14142 | 14.142 | 474 | 3.4
14899 | 14030 | 14.03 | -636 | 2.25
14900 | 13886 | 13.886 | 13 | 1.15
14901 | 14041 | 14.041 | 163 | 1.05
14902 | 13984 | 13.984 | 501 | 0
14903 | 13948 | 13.948 | -59 | 4.9
14904 | 13924 | 13.924 | 506 | 0.25
14905 | 13980 | 13.98 | -179 | 1.35
14906 | 13860 | 13.86 | 724 | 2.9
14907 | 13972 | 13.972 | 702 | 1.2
14908 | 13966 | 13.966 | 918 | 0.35
14909 | 14026 | 14.026 | 419 | 4.7
14910 | 13941 | 13.941 | 985 | 1.6
14911 | 13845 | 13.845 | -809 | 3.35
14912 | 13961 | 13.961 | -343 | 2.65
14913 | 14007 | 14.007 | -503 | 1.85
14914 | 13983 | 13.983 | 641 | 2.4
14915 | 13999 | 13.999 | 886 | 3.75
14916 | 14075 | 14.075 | -862 | 5
14917 | 14173 | 14.173 | 615 | 0.05
14918 | 14171 | 14.171 | -401 | 4.3
14919 | 14177 | 14.177 | 44 | 0.05
14920 | 14235 | 14.235 | -647 | 3.7
14921 | 14385 | 14.385 | 245 | 2.55
14922 | 13945 | 13.945 | -573 | 4.5
14923 | 10823 | 10.823 | 621 | 3
14924 | 10601 | 10.601 | 448 | 3.35
14925 | 14254 | 14.254 | -362 | 2.85
14926 | 14332 | 14.332 | 172 | 1.1
14927 | 14452 | 14.452 | -70 | 0.9
14928 | 13966 | 13.966 | -45 | 1.85
14929 | 13406 | 13.406 | -960 | 1.55
14930 | 14033 | 14.033 | -923 | 4.85
14931 | 14135 | 14.135 | 733 | 2.75
14932 | 14295 | 14.295 | 938 | 1.95
14933 | 14343 | 14.343 | 721 | 3
14934 | 14485 | 14.485 | -219 | 3.3
14935 | 14406 | 14.406 | 333 | 1.05
14936 | 14460 | 14.46 | 129 | 4.6
14937 | 14520 | 14.52 | 107 | 4.9
14938 | 14379 | 14.379 | -87 | 3.85
14939 | 14416 | 14.416 | -341 | 4
14940 | 14361 | 14.361 | -362 | 0.45
14941 | 14342 | 14.342 | 487 | 3.25
14942 | 14271 | 14.271 | -897 | 2.55
14943 | 14333 | 14.333 | 499 | 4.25
14944 | 14265 | 14.265 | -370 | 3.35
14945 | 14152 | 14.152 | -518 | 0.8
14946 | 14290 | 14.29 | 197 | 4.05
14947 | 14189 | 14.189 | -572 | 3.65
14948 | 14233 | 14.233 | 910 | 2.7
14949 | 14159 | 14.159 | -195 | 1.25
14950 | 14104 | 14.104 | -667 | 3.85
14951 | 14168 | 14.168 | -340 | 2.2
14952 | 13955 | 13.955 | -43 | 0.5
14953 | 14062 | 14.062 | -710 | 2.5
14954 | 13963 | 13.963 | 246 | 2.4
14955 | 13812 | 13.812 | 224 | 1.85
14956 | 13948 | 13.948 | -564 | 4.4
14957 | 13953 | 13.953 | -133 | 1.5
14958 | 14040 | 14.04 | 9 | 1.85
14959 | 14029 | 14.029 | 60 | 0.15
14960 | 13821 | 13.821 | -494 | 0.9
14961 | 13910 | 13.91 | -721 | 0.8
14962 | 13762 | 13.762 | -799 | 1
14963 | 14065 | 14.065 | 68 | 3.45
14964 | 13887 | 13.887 | 640 | 0.05
14965 | 13920 | 13.92 | -843 | 3.75
14966 | 14104 | 14.104 | -269 | 2.85
14967 | 13987 | 13.987 | 651 | 3.2
14968 | 14051 | 14.051 | -934 | 2.25
14969 | 13949 | 13.949 | -581 | 4.7
14970 | 14014 | 14.014 | -865 | 0.5
14971 | 14141 | 14.141 | -948 | 4.15
14972 | 14040 | 14.04 | -874 | 2.5
14973 | 14095 | 14.095 | -785 | 4.25
14974 | 14024 | 14.024 | -826 | 1.1
14975 | 13679 | 13.679 | 806 | 2.25
14976 | 13125 | 13.125 | 209 | 0
14977 | 13421 | 13.421 | -84 | 3.7
14978 | 13500 | 13.5 | 394 | 3.4
14979 | 13536 | 13.536 | 181 | 0.45
14980 | 13045 | 13.045 | 396 | 0.8
14981 | 14214 | 14.214 | 78 | 2.35
14982 | 14087 | 14.087 | 888 | 1.1
14983 | 13980 | 13.98 | -809 | 4.1
14984 | 13688 | 13.688 | -541 | 0.3
14985 | 13929 | 13.929 | -462 | 4.3
14986 | 13940 | 13.94 | -264 | 0.5
14987 | 14029 | 14.029 | -957 | 3.7
14988 | 13852 | 13.852 | -281 | 2.55
14989 | 14030 | 14.03 | 183 | 2.25
14990 | 13952 | 13.952 | 666 | 4.2
14991 | 13931 | 13.931 | -512 | 3.2
14992 | 13800 | 13.8 | 573 | 0.95
14993 | 13784 | 13.784 | 928 | 2.15
14994 | 13763 | 13.763 | -12 | 1.1
14995 | 13775 | 13.775 | -154 | 3.45
14996 | 13576 | 13.576 | 230 | 1.1
14997 | 13542 | 13.542 | -754 | 4.9
14998 | 13588 | 13.588 | -524 | 1.7
14999 | 13445 | 13.445 | -874 | 3.55
15000 | 13446 | 13.446 | -661 | 2.25
15001 | 13284 | 13.284 | 893 | 0.2
15002 | 13427 | 13.427 | 975 | 0.25
15003 | 13271 | 13.271 | 998 | 3.8
15004 | 13426 | 13.426 | -239 | 4.05
15005 | 13440 | 13.44 | 669 | 1.45
15006 | 13315 | 13.315 | -939 | 2.5
15007 | 13812 | 13.812 | 365 | 4.8
15008 | 13400 | 13.4 | -173 | 0.6
15009 | 13522 | 13.522 | 290 | 0.5
15010 | 13669 | 13.669 | -393 | 3.7
15011 | 13652 | 13.652 | -856 | 1.65
15012 | 13314 | 13.314 | -418 | 3.9
15013 | 13679 | 13.679 | -716 | 1.1
15014 | 13758 | 13.758 | -856 | 2.25
15015 | 13818 | 13.818 | -62 | 3.65
15016 | 13769 | 13.769 | 81 | 4.65
15017 | 13866 | 13.866 | -989 | 0.8
15018 | 13861 | 13.861 | 130 | 4.05
15019 | 13928 | 13.928 | 303 | 3.75
15020 | 13986 | 13.986 | 95 | 3.05
15021 | 13987 | 13.987 | 148 | 3.65
15022 | 13820 | 13.82 | -38 | 0.6
15023 | 13676 | 13.676 | 724 | 3.65
15024 | 13436 | 13.436 | 947 | 0.2
15025 | 13256 | 13.256 | -214 | 4.3
15026 | 13422 | 13.422 | -731 | 2.95
15027 | 9560 | 9.56 | 233 | 3.75
15028 | 7355 | 7.355 | 764 | 3.4
15029 | 11576 | 11.576 | -254 | 0.4
15030 | 13930 | 13.93 | -964 | 0.8
15031 | 14079 | 14.079 | 975 | 3.8
15032 | 14067 | 14.067 | -818 | 3.05
15033 | 14021 | 14.021 | -164 | 1.5
15034 | 14009 | 14.009 | 83 | 1.7
15035 | 14019 | 14.019 | 707 | 3.95
15036 | 13972 | 13.972 | -104 | 0
15037 | 14054 | 14.054 | 168 | 0
15038 | 14059 | 14.059 | -497 | 5
15039 | 14084 | 14.084 | 614 | 3.4
15040 | 13897 | 13.897 | 966 | 4.65
15041 | 13965 | 13.965 | 165 | 0.3
15042 | 14039 | 14.039 | 258 | 3.3
15043 | 13903 | 13.903 | -190 | 3.4
15044 | 14018 | 14.018 | 256 | 4.8
15045 | 13848 | 13.848 | -991 | 2.05
15046 | 13669 | 13.669 | 193 | 3.4
15047 | 13867 | 13.867 | -51 | 3.65
15048 | 14036 | 14.036 | 408 | 0.65
15049 | 13775 | 13.775 | 694 | 1.85
15050 | 13966 | 13.966 | 521 | 3.85
15051 | 13650 | 13.65 | -584 | 2.25
15052 | 13715 | 13.715 | -39 | 3.2
15053 | 13784 | 13.784 | 24 | 0
15054 | 13661 | 13.661 | 153 | 0.65
15055 | 13707 | 13.707 | -138 | 0.55
15056 | 13777 | 13.777 | -984 | 1.1
15057 | 13874 | 13.874 | 123 | 3.1
15058 | 13735 | 13.735 | 734 | 2.35
15059 | 13728 | 13.728 | -480 | 4.4
15060 | 13737 | 13.737 | -854 | 0.45
15061 | 13731 | 13.731 | -227 | 3.1
15062 | 13775 | 13.775 | 445 | 1.35
15063 | 13799 | 13.799 | -391 | 4.8
15064 | 13720 | 13.72 | -960 | 3.75
15065 | 14054 | 14.054 | 106 | 0.9
15066 | 13999 | 13.999 | 396 | 1.95
15067 | 13784 | 13.784 | -413 | 1.6
15068 | 13763 | 13.763 | 884 | 2.6
15069 | 14015 | 14.015 | -439 | 0.55
15070 | 13905 | 13.905 | -153 | 3.25
15071 | 14114 | 14.114 | -191 | 2.15
15072 | 13702 | 13.702 | -869 | 1.65
15073 | 13485 | 13.485 | 949 | 2.3
15074 | 13471 | 13.471 | 536 | 2.8
15075 | 13522 | 13.522 | -951 | 0.45
15076 | 13486 | 13.486 | 684 | 4.55
15077 | 13019 | 13.019 | 825 | 2.35
15078 | 14055 | 14.055 | -197 | 2
15079 | 14122 | 14.122 | 125 | 0.05
15080 | 14053 | 14.053 | -11 | 4.1
15081 | 14217 | 14.217 | -840 | 4.45
15082 | 14081 | 14.081 | 722 | 2.65
15083 | 14364 | 14.364 | 776 | 3.7
15084 | 14085 | 14.085 | 930 | 3.7
15085 | 14226 | 14.226 | 128 | 3.5
15086 | 14219 | 14.219 | 591 | 3.2
15087 | 14227 | 14.227 | -362 | 0.55
15088 | 14350 | 14.35 | -955 | 4.5
15089 | 13986 | 13.986 | 39 | 0.95
15090 | 14121 | 14.121 | 545 | 4.15
15091 | 13998 | 13.998 | -769 | 4.95
15092 | 13813 | 13.813 | 716 | 0
15093 | 14000 | 14 | -74 | 1.15
15094 | 13888 | 13.888 | -572 | 2.9
15095 | 13650 | 13.65 | -759 | 1.65
15096 | 13910 | 13.91 | 993 | 2.35
15097 | 13886 | 13.886 | 856 | 4
15098 | 13788 | 13.788 | -292 | 3.95
15099 | 13830 | 13.83 | -209 | 2.75
15100 | 13673 | 13.673 | 322 | 1.2
15101 | 13774 | 13.774 | 254 | 1.4
15102 | 13590 | 13.59 | -756 | 2.4
15103 | 13845 | 13.845 | 605 | 2.65
15104 | 13788 | 13.788 | 330 | 1.1
15105 | 13626 | 13.626 | 341 | 3.2
15106 | 13803 | 13.803 | 965 | 2.65
15107 | 13906 | 13.906 | -520 | 3.75
15108 | 13873 | 13.873 | 973 | 4.75
15109 | 14050 | 14.05 | 6 | 0.7
15110 | 13968 | 13.968 | 217 | 1
15111 | 14214 | 14.214 | -258 | 1.95
15112 | 14101 | 14.101 | -40 | 0.25
15113 | 14232 | 14.232 | -382 | 2.85
15114 | 14287 | 14.287 | 288 | 0.35
15115 | 14242 | 14.242 | 877 | 1.05
15116 | 14286 | 14.286 | 772 | 4.05
15117 | 14272 | 14.272 | 738 | 4.2
15118 | 14356 | 14.356 | -730 | 2.35
15119 | 14277 | 14.277 | 158 | 4.55
15120 | 14223 | 14.223 | -678 | 4.9
15121 | 13714 | 13.714 | 766 | 4.35
15122 | 13537 | 13.537 | -416 | 0.9
15123 | 13642 | 13.642 | -934 | 3.85
15124 | 13508 | 13.508 | -522 | 2.2
15125 | 13612 | 13.612 | -326 | 1.95
15126 | 14200 | 14.2 | 418 | 0.65
15127 | 14121 | 14.121 | -855 | 0.65
15128 | 14187 | 14.187 | 191 | 0.9
15129 | 14457 | 14.457 | 29 | 0.4
15130 | 14323 | 14.323 | 410 | 0.1
15131 | 14233 | 14.233 | 260 | 2.6
15132 | 14147 | 14.147 | 407 | 3.65
15133 | 14234 | 14.234 | 172 | 3.05
15134 | 14292 | 14.292 | 153 | 1.05
15135 | 14010 | 14.01 | -681 | 4.85
15136 | 14056 | 14.056 | -699 | 0.65
15137 | 13777 | 13.777 | 906 | 1.7
15138 | 13866 | 13.866 | -304 | 3.7
15139 | 13984 | 13.984 | 909 | 4.55
15140 | 13818 | 13.818 | 460 | 0.4
15141 | 13779 | 13.779 | -872 | 1.55
15142 | 13887 | 13.887 | -175 | 2.65
15143 | 13721 | 13.721 | 240 | 4.6
15144 | 13748 | 13.748 | 83 | 0.5
15145 | 13757 | 13.757 | 624 | 3.2
15146 | 13781 | 13.781 | -5 | 3.7
15147 | 13797 | 13.797 | -736 | 1.8
15148 | 13748 | 13.748 | 381 | 0.05
15149 | 13697 | 13.697 | 483 | 3.4
15150 | 13752 | 13.752 | -490 | 2.75
15151 | 13827 | 13.827 | -226 | 3.05
15152 | 13599 | 13.599 | -963 | 4.45
15153 | 13616 | 13.616 | -215 | 1.9
15154 | 13730 | 13.73 | -915 | 0.55
15155 | 13794 | 13.794 | 653 | 0.65
15156 | 13638 | 13.638 | 28 | 3.45
15157 | 13654 | 13.654 | 75 | 0.85
15158 | 13779 | 13.779 | -698 | 1.1
15159 | 13757 | 13.757 | -841 | 3.7
15160 | 13791 | 13.791 | -883 | 1
15161 | 13841 | 13.841 | 971 | 4.6
15162 | 13792 | 13.792 | 771 | 1.85
15163 | 13819 | 13.819 | -640 | 4.05
15164 | 13757 | 13.757 | -206 | 1.65
15165 | 13958 | 13.958 | 439 | 0.1
15166 | 13998 | 13.998 | 825 | 1.5
15167 | 13847 | 13.847 | 143 | 2.4
15168 | 13670 | 13.67 | -645 | 2.9
15169 | 13201 | 13.201 | 716 | 3.15
15170 | 13360 | 13.36 | 740 | 3.8
15171 | 13499 | 13.499 | 501 | 4.2
15172 | 13516 | 13.516 | 363 | 0
15173 | 13150 | 13.15 | 346 | 0.1
15174 | 14116 | 14.116 | -179 | 1.45
15175 | 14274 | 14.274 | 176 | 2.4
15176 | 14363 | 14.363 | -80 | 2.95
15177 | 14257 | 14.257 | 245 | 3.2
15178 | 14323 | 14.323 | -691 | 3.95
15179 | 14273 | 14.273 | 352 | 0.85
15180 | 14401 | 14.401 | 825 | 3.55
15181 | 14223 | 14.223 | -328 | 3.6
15182 | 14354 | 14.354 | -157 | 4.4
15183 | 14420 | 14.42 | 250 | 0.85
15184 | 14333 | 14.333 | -426 | 0.4
15185 | 14358 | 14.358 | 0 | 0.35
15186 | 14205 | 14.205 | -933 | 1.75
15187 | 14439 | 14.439 | 607 | 4.55
15188 | 14312 | 14.312 | -687 | 2.8
15189 | 14252 | 14.252 | 874 | 1.6
15190 | 14248 | 14.248 | -493 | 1.05
15191 | 14250 | 14.25 | 440 | 2.45
15192 | 14242 | 14.242 | -263 | 3.45
15193 | 14206 | 14.206 | -799 | 1.4
15194 | 14392 | 14.392 | 382 | 3.65
15195 | 14126 | 14.126 | -766 | 3.5
15196 | 14029 | 14.029 | -368 | 2.15
15197 | 14271 | 14.271 | 982 | 3.55
15198 | 14251 | 14.251 | -232 | 3.7
15199 | 14215 | 14.215 | -479 | 2.65
15200 | 14145 | 14.145 | 807 | 4.35
15201 | 14221 | 14.221 | -413 | 1.85
15202 | 14211 | 14.211 | 540 | 4.5
15203 | 14073 | 14.073 | -614 | 2.2
15204 | 14192 | 14.192 | -445 | 0.6
15205 | 14277 | 14.277 | 481 | 3.35
15206 | 14174 | 14.174 | -192 | 3.1
15207 | 14180 | 14.18 | 51 | 0.8
15208 | 14298 | 14.298 | -37 | 0.45
15209 | 14267 | 14.267 | -207 | 3.05
15210 | 14401 | 14.401 | 916 | 4.8
15211 | 14277 | 14.277 | 416 | 4.15
15212 | 14362 | 14.362 | -519 | 3.35
15213 | 14367 | 14.367 | 597 | 4.6
15214 | 14243 | 14.243 | -505 | 3.65
15215 | 14463 | 14.463 | -653 | 3.85
15216 | 14401 | 14.401 | 414 | 2.1
15217 | 14282 | 14.282 | 121 | 0.05
15218 | 14520 | 14.52 | 4 | 1.9
15219 | 14430 | 14.43 | 656 | 4.15
15220 | 14018 | 14.018 | -571 | 3.95
15221 | 13680 | 13.68 | 808 | 4.65
15222 | 13820 | 13.82 | -760 | 4.65
15223 | 13697 | 13.697 | 233 | 2.35
15224 | 13507 | 13.507 | -191 | 0.05
15225 | 14343 | 14.343 | 799 | 2.05
15226 | 14664 | 14.664 | 499 | 3.6
15227 | 14450 | 14.45 | -568 | 4.35
15228 | 14550 | 14.55 | 592 | 2.75
15229 | 14586 | 14.586 | -701 | 1
15230 | 14519 | 14.519 | 628 | 0.15
15231 | 14420 | 14.42 | -695 | 0.75
15232 | 14183 | 14.183 | -262 | 3.85
15233 | 14548 | 14.548 | -691 | 3.9
15234 | 14338 | 14.338 | 672 | 2.55
15235 | 14159 | 14.159 | -451 | 1.65
15236 | 14111 | 14.111 | -294 | 1.25
15237 | 14127 | 14.127 | 0 | 2.4
15238 | 14052 | 14.052 | 200 | 1.15
15239 | 13959 | 13.959 | -181 | 4.2
15240 | 13855 | 13.855 | -315 | 2.2
15241 | 13959 | 13.959 | -363 | 2.3
15242 | 14176 | 14.176 | 718 | 0.2
15243 | 13951 | 13.951 | 922 | 0.7
15244 | 13928 | 13.928 | 590 | 3.6
15245 | 14026 | 14.026 | 349 | 1.55
15246 | 13876 | 13.876 | 365 | 0.7
15247 | 13835 | 13.835 | 708 | 2.25
15248 | 14030 | 14.03 | -504 | 2.35
15249 | 13970 | 13.97 | 689 | 0.6
15250 | 13908 | 13.908 | -371 | 0
15251 | 14038 | 14.038 | 643 | 0.85
15252 | 14077 | 14.077 | 217 | 4.4
15253 | 14168 | 14.168 | 998 | 4.7
15254 | 14101 | 14.101 | 607 | 1.1
15255 | 14257 | 14.257 | 871 | 1.7
15256 | 14366 | 14.366 | -493 | 4.7
15257 | 14240 | 14.24 | -142 | 3.85
15258 | 14203 | 14.203 | -780 | 0.6
15259 | 14366 | 14.366 | -266 | 0.7
15260 | 14509 | 14.509 | -782 | 1.2
15261 | 14400 | 14.4 | 836 | 1.7
15262 | 14362 | 14.362 | 131 | 0.95
15263 | 14418 | 14.418 | 590 | 3.7
15264 | 14257 | 14.257 | 101 | 2.35
15265 | 13853 | 13.853 | -219 | 1.65
15266 | 13672 | 13.672 | 599 | 2.5
15267 | 13762 | 13.762 | -323 | 2.75
15268 | 13895 | 13.895 | 675 | 0.55
15269 | 13658 | 13.658 | 693 | 1.45
15270 | 13572 | 13.572 | -162 | 3.35
15271 | 14421 | 14.421 | -961 | 3.85
15272 | 14353 | 14.353 | -744 | 0.4
15273 | 14412 | 14.412 | 2 | 4.85
15274 | 14353 | 14.353 | 797 | 3.95
15275 | 14284 | 14.284 | -542 | 3.75
15276 | 14308 | 14.308 | -882 | 1.3
15277 | 14392 | 14.392 | -2 | 4.45
15278 | 14383 | 14.383 | -911 | 1.75
15279 | 14409 | 14.409 | -530 | 0.7
15280 | 14393 | 14.393 | 737 | 0.45
15281 | 14280 | 14.28 | -768 | 3.6
15282 | 14287 | 14.287 | 6 | 2.25
15283 | 14070 | 14.07 | -658 | 4.5
15284 | 14050 | 14.05 | 306 | 1.95
15285 | 13970 | 13.97 | -424 | 4.2
15286 | 13752 | 13.752 | -211 | 3.3
15287 | 13838 | 13.838 | -645 | 2.8
15288 | 13815 | 13.815 | -4 | 3.2
15289 | 13732 | 13.732 | 910 | 0.9
15290 | 13544 | 13.544 | -855 | 1.6
15291 | 13666 | 13.666 | -871 | 0.9
15292 | 13626 | 13.626 | 451 | 3.55
15293 | 13626 | 13.626 | -885 | 4.4
15294 | 13654 | 13.654 | 493 | 0.65
15295 | 13681 | 13.681 | 141 | 0.2
15296 | 13781 | 13.781 | -365 | 0.3
15297 | 13685 | 13.685 | 659 | 2.9
15298 | 13801 | 13.801 | -694 | 2.1
15299 | 13669 | 13.669 | 27 | 3.1
15300 | 13757 | 13.757 | -688 | 0.75
15301 | 13791 | 13.791 | 275 | 2.35
15302 | 13934 | 13.934 | -989 | 1.95
15303 | 13832 | 13.832 | -666 | 4.7
15304 | 13889 | 13.889 | 465 | 5
15305 | 13887 | 13.887 | 90 | 0.75
15306 | 14045 | 14.045 | 968 | 4.35
15307 | 13952 | 13.952 | -819 | 0.6
15308 | 13884 | 13.884 | -289 | 4.95
15309 | 14052 | 14.052 | -459 | 1.15
15310 | 14015 | 14.015 | 528 | 2.15
15311 | 13956 | 13.956 | 938 | 0.45
15312 | 13798 | 13.798 | 56 | 4.7
15313 | 13789 | 13.789 | 749 | 1.5
15314 | 13440 | 13.44 | -646 | 0.4
15315 | 13428 | 13.428 | -667 | 1.35
15316 | 13496 | 13.496 | 49 | 1.3
15317 | 13311 | 13.311 | -902 | 3.2
15318 | 13931 | 13.931 | -294 | 0.15
15319 | 14196 | 14.196 | 978 | 0
15320 | 14175 | 14.175 | -915 | 2.45
15321 | 14371 | 14.371 | -966 | 3.3
15322 | 14232 | 14.232 | -266 | 1.2
15323 | 14185 | 14.185 | -605 | 4.05
15324 | 14138 | 14.138 | -915 | 3.45
15325 | 14449 | 14.449 | 539 | 4.7
15326 | 14366 | 14.366 | -817 | 3.05
15327 | 14164 | 14.164 | -125 | 0.05
15328 | 14212 | 14.212 | -650 | 1.85
15329 | 14287 | 14.287 | 752 | 0.95
15330 | 14029 | 14.029 | -641 | 5
15331 | 14059 | 14.059 | 686 | 4.2
15332 | 13883 | 13.883 | -583 | 3.65
15333 | 13977 | 13.977 | -633 | 0
15334 | 13837 | 13.837 | -496 | 0.75
15335 | 13805 | 13.805 | 693 | 1.45
15336 | 13617 | 13.617 | -17 | 3.85
15337 | 13655 | 13.655 | -353 | 1.55
15338 | 13360 | 13.36 | -430 | 1.25
15339 | 13534 | 13.534 | -718 | 1.2
15340 | 13378 | 13.378 | 645 | 4.4
15341 | 13385 | 13.385 | -363 | 1.35
15342 | 13379 | 13.379 | 792 | 2.1
15343 | 13221 | 13.221 | -309 | 0.85
15344 | 13443 | 13.443 | 922 | 1.5
15345 | 13510 | 13.51 | -817 | 3.45
15346 | 13511 | 13.511 | 237 | 4.05
15347 | 13759 | 13.759 | -772 | 3.35
15348 | 13624 | 13.624 | 608 | 3.4
15349 | 13831 | 13.831 | 688 | 1.35
15350 | 13469 | 13.469 | -544 | 2.25
15351 | 13734 | 13.734 | 466 | 4.4
15352 | 13921 | 13.921 | 556 | 3
15353 | 14097 | 14.097 | -767 | 4.25
15354 | 13894 | 13.894 | 86 | 0.7
15355 | 13952 | 13.952 | -977 | 4.35
15356 | 13866 | 13.866 | 2 | 1.8
15357 | 14105 | 14.105 | 816 | 0.7
15358 | 14289 | 14.289 | 548 | 1.55
15359 | 13983 | 13.983 | 236 | 1.05
15360 | 13774 | 13.774 | -36 | 2.3
15361 | 13377 | 13.377 | -775 | 3.6
15362 | 13559 | 13.559 | -950 | 2.75
15363 | 13566 | 13.566 | -121 | 0.7
15364 | 13594 | 13.594 | -586 | 4.1
15365 | 13332 | 13.332 | -998 | 0.55
15366 | 14161 | 14.161 | -724 | 0.6
15367 | 14097 | 14.097 | -732 | 2.45
15368 | 14117 | 14.117 | -150 | 5
15369 | 14248 | 14.248 | -730 | 4.75
15370 | 14148 | 14.148 | 797 | 0.8
15371 | 14217 | 14.217 | -609 | 4.9
15372 | 14219 | 14.219 | -800 | 3.25
15373 | 14239 | 14.239 | 997 | 4.8
15374 | 14262 | 14.262 | -707 | 3.2
15375 | 14215 | 14.215 | -722 | 3.8
15376 | 14027 | 14.027 | 404 | 1.2
15377 | 14187 | 14.187 | 91 | 2.8
15378 | 14323 | 14.323 | 814 | 3.9
15379 | 13997 | 13.997 | -451 | 3.35
15380 | 14189 | 14.189 | 372 | 0.45
15381 | 14071 | 14.071 | -659 | 0
15382 | 14152 | 14.152 | 130 | 3.45
15383 | 14040 | 14.04 | -281 | 0.85
15384 | 14109 | 14.109 | 685 | 4.5
15385 | 14010 | 14.01 | 141 | 5
15386 | 13895 | 13.895 | -203 | 2.65
15387 | 13942 | 13.942 | -598 | 1.15
15388 | 13768 | 13.768 | 549 | 4.45
15389 | 13920 | 13.92 | 795 | 2.5
15390 | 13809 | 13.809 | -967 | 0.9
15391 | 13871 | 13.871 | 807 | 0.75
15392 | 13983 | 13.983 | 293 | 0.9
15393 | 13787 | 13.787 | 577 | 4.4
15394 | 13770 | 13.77 | -512 | 1
15395 | 13791 | 13.791 | -190 | 3.5
15396 | 14066 | 14.066 | -21 | 2.3
15397 | 13948 | 13.948 | -716 | 4.1
15398 | 11168 | 11.168 | 529 | 2.8
15399 | 12294 | 12.294 | -399 | 4.95
15400 | 13935 | 13.935 | -558 | 2.75
15401 | 14242 | 14.242 | 475 | 1.15
15402 | 14154 | 14.154 | -436 | 2.3
15403 | 14249 | 14.249 | 956 | 0.85
15404 | 14168 | 14.168 | -673 | 3.65
15405 | 14203 | 14.203 | 13 | 2.45
15406 | 14165 | 14.165 | 722 | 0.85
15407 | 14212 | 14.212 | 385 | 1.1
15408 | 14264 | 14.264 | 447 | 2.8
15409 | 14183 | 14.183 | 446 | 2.65
15410 | 13706 | 13.706 | -145 | 1.6
15411 | 13759 | 13.759 | 489 | 2.4
15412 | 13767 | 13.767 | 388 | 4.9
15413 | 13534 | 13.534 | -200 | 3.75
15414 | 13539 | 13.539 | -371 | 4.2
15415 | 14273 | 14.273 | 32 | 4.5
15416 | 14183 | 14.183 | 891 | 4.3
15417 | 14307 | 14.307 | -649 | 3.85
15418 | 14273 | 14.273 | 324 | 0.2
15419 | 14277 | 14.277 | 366 | 2.3
15420 | 14434 | 14.434 | 670 | 0.95
15421 | 14300 | 14.3 | -83 | 2.35
15422 | 14297 | 14.297 | -837 | 3.25
15423 | 14289 | 14.289 | -28 | 1.85
15424 | 14281 | 14.281 | 245 | 0.65
15425 | 14251 | 14.251 | -873 | 2.85
15426 | 14234 | 14.234 | 67 | 4.7
15427 | 14281 | 14.281 | -604 | 3.8
15428 | 14249 | 14.249 | -701 | 1.1
15429 | 14202 | 14.202 | 537 | 1.2
15430 | 14298 | 14.298 | -830 | 4.35
15431 | 14211 | 14.211 | 237 | 1.45
15432 | 14087 | 14.087 | 428 | 1.75
15433 | 14063 | 14.063 | 0 | 2.7
15434 | 13965 | 13.965 | 517 | 1.7
15435 | 13827 | 13.827 | -694 | 4.05
15436 | 13769 | 13.769 | -856 | 3.2
15437 | 13760 | 13.76 | 236 | 1.35
15438 | 13665 | 13.665 | -872 | 1.9
15439 | 13694 | 13.694 | 446 | 0.45
15440 | 13542 | 13.542 | 674 | 4.9
15441 | 13706 | 13.706 | 754 | 2.15
15442 | 13508 | 13.508 | 118 | 4.8
15443 | 13759 | 13.759 | -358 | 1.95
15444 | 13570 | 13.57 | 229 | 2.85
15445 | 13852 | 13.852 | -32 | 1
15446 | 13833 | 13.833 | -537 | 1.35
15447 | 13810 | 13.81 | 735 | 4.95
15448 | 14002 | 14.002 | 364 | 4.7
15449 | 13934 | 13.934 | -786 | 3.5
15450 | 13990 | 13.99 | 246 | 3.7
15451 | 14011 | 14.011 | 799 | 3.35
15452 | 13926 | 13.926 | -742 | 0.55
15453 | 13899 | 13.899 | 803 | 0.55
15454 | 13995 | 13.995 | -295 | 3.65
15455 | 13943 | 13.943 | 133 | 1.45
15456 | 13782 | 13.782 | -954 | 2.2
15457 | 13339 | 13.339 | -395 | 2.9
15458 | 13424 | 13.424 | -665 | 1.3
15459 | 13625 | 13.625 | -475 | 4.1
15460 | 13724 | 13.724 | -856 | 1.3
15461 | 13193 | 13.193 | 593 | 1.9
15462 | 14066 | 14.066 | -574 | 0.05
15463 | 13991 | 13.991 | -871 | 2.15
15464 | 14089 | 14.089 | -560 | 3.95
15465 | 14092 | 14.092 | -502 | 0
15466 | 14060 | 14.06 | 221 | 0.6
15467 | 14248 | 14.248 | 808 | 3.45
15468 | 14241 | 14.241 | -105 | 1.8
15469 | 14194 | 14.194 | 317 | 0.65
15470 | 14235 | 14.235 | 509 | 4.15
15471 | 14396 | 14.396 | -988 | 1.3
15472 | 14273 | 14.273 | 417 | 0.95
15473 | 14262 | 14.262 | -581 | 2.4
15474 | 14257 | 14.257 | 835 | 2.05
15475 | 14169 | 14.169 | 166 | 2.4
15476 | 14349 | 14.349 | -700 | 3.35
15477 | 14368 | 14.368 | -415 | 1.45
15478 | 14159 | 14.159 | 402 | 2.45
15479 | 14241 | 14.241 | -670 | 3.15
15480 | 14385 | 14.385 | 867 | 3.6
15481 | 14205 | 14.205 | -582 | 1.45
15482 | 14033 | 14.033 | -794 | 4.7
15483 | 14275 | 14.275 | -824 | 2.05
15484 | 14137 | 14.137 | -828 | 4.3
15485 | 14253 | 14.253 | 518 | 3.75
15486 | 14073 | 14.073 | 940 | 0.2
15487 | 14085 | 14.085 | -756 | 4.55
15488 | 14085 | 14.085 | -423 | 2.8
15489 | 14111 | 14.111 | -575 | 2.15
15490 | 14183 | 14.183 | -921 | 0.7
15491 | 14019 | 14.019 | -453 | 0.6
15492 | 14280 | 14.28 | -465 | 0.8
15493 | 14258 | 14.258 | -62 | 0
15494 | 14374 | 14.374 | 793 | 1.85
15495 | 14040 | 14.04 | -546 | 2.2
15496 | 14222 | 14.222 | 920 | 4.45
15497 | 14272 | 14.272 | -708 | 0.7
15498 | 14410 | 14.41 | 947 | 4.9
15499 | 14231 | 14.231 | -800 | 0.55
15500 | 14230 | 14.23 | -717 | 2.3
15501 | 14364 | 14.364 | 781 | 4.8
15502 | 14304 | 14.304 | -256 | 0.4
15503 | 14421 | 14.421 | 319 | 3.35
15504 | 14088 | 14.088 | 137 | 2.7
15505 | 13885 | 13.885 | 678 | 1.65
15506 | 13819 | 13.819 | -551 | 3.25
15507 | 13761 | 13.761 | 848 | 4.15
15508 | 13264 | 13.264 | 726 | 1.3
15509 | 14102 | 14.102 | 977 | 4.85
15510 | 14255 | 14.255 | -725 | 3.7
15511 | 14457 | 14.457 | 628 | 2.75
15512 | 14352 | 14.352 | 672 | 2.8
15513 | 14245 | 14.245 | 141 | 4.9
15514 | 14334 | 14.334 | -169 | 4.35
15515 | 14392 | 14.392 | 939 | 4.65
15516 | 14397 | 14.397 | -714 | 3.8
15517 | 14364 | 14.364 | -14 | 2.5
15518 | 14322 | 14.322 | -128 | 2.6
15519 | 14240 | 14.24 | 284 | 4.25
15520 | 12027 | 12.027 | -532 | 3.1
15521 | 9407 | 9.407 | 982 | 0.25
15522 | 13217 | 13.217 | -999 | 2.1
15523 | 14000 | 14 | -203 | 0.6
15524 | 14532 | 14.532 | 748 | 3.7
15525 | 14106 | 14.106 | 772 | 2.9
15526 | 14607 | 14.607 | 122 | 4.45
15527 | 14266 | 14.266 | -464 | 2.7
15528 | 14119 | 14.119 | 446 | 4.45
15529 | 14106 | 14.106 | 421 | 4.55
15530 | 14201 | 14.201 | -706 | 4.6
15531 | 14108 | 14.108 | 124 | 2.8
15532 | 14047 | 14.047 | 574 | 0.4
15533 | 14071 | 14.071 | 777 | 0.35
15534 | 14083 | 14.083 | 389 | 3.35
15535 | 14048 | 14.048 | -524 | 4.15
15536 | 14028 | 14.028 | 942 | 0.65
15537 | 12889 | 12.889 | -60 | 4.45
15538 | 10574 | 10.574 | 760 | 5
15539 | 10572 | 10.572 | 403 | 1.4
15540 | 11632 | 11.632 | -195 | 2.5
15541 | 13456 | 13.456 | -306 | 2.1
15542 | 14240 | 14.24 | 294 | 3.4
15543 | 14090 | 14.09 | 658 | 2.2
15544 | 14364 | 14.364 | -576 | 0.3
15545 | 14227 | 14.227 | 264 | 4.85
15546 | 14307 | 14.307 | 24 | 0.2
15547 | 14244 | 14.244 | -152 | 2
15548 | 14290 | 14.29 | 142 | 3.6
15549 | 14490 | 14.49 | 994 | 0.05
15550 | 14408 | 14.408 | 718 | 0.85
15551 | 14413 | 14.413 | 927 | 1.05
15552 | 14345 | 14.345 | -119 | 0.6
15553 | 14446 | 14.446 | 763 | 1.6
15554 | 14360 | 14.36 | 193 | 0.65
15555 | 13777 | 13.777 | 436 | 3.05
15556 | 13663 | 13.663 | 800 | 1.35
15557 | 13751 | 13.751 | -65 | 4.6
15558 | 13817 | 13.817 | 43 | 1.15
15559 | 13723 | 13.723 | 783 | 1.7
15560 | 13722 | 13.722 | -9 | 2.5
15561 | 14309 | 14.309 | 940 | 1.5
15562 | 14344 | 14.344 | 681 | 4.9
15563 | 14430 | 14.43 | -474 | 3.6
15564 | 14549 | 14.549 | 171 | 1.7
15565 | 14509 | 14.509 | -78 | 2.8
15566 | 14397 | 14.397 | 438 | 4.8
15567 | 14477 | 14.477 | 391 | 1.35
15568 | 14418 | 14.418 | -501 | 5
15569 | 14396 | 14.396 | 237 | 3.95
15570 | 14306 | 14.306 | 501 | 1.55
15571 | 14232 | 14.232 | 330 | 2.9
15572 | 14455 | 14.455 | -260 | 3.2
15573 | 14074 | 14.074 | 130 | 0.95
15574 | 13623 | 13.623 | -883 | 4.3
15575 | 13944 | 13.944 | -823 | 4.3
15576 | 13991 | 13.991 | 30 | 2.25
15577 | 14012 | 14.012 | -166 | 1.5
15578 | 14009 | 14.009 | -850 | 2.15
15579 | 13941 | 13.941 | 778 | 4.1
15580 | 14176 | 14.176 | -512 | 0.6
15581 | 13727 | 13.727 | 708 | 5
15582 | 13970 | 13.97 | -980 | 4.7
15583 | 13854 | 13.854 | -763 | 4.5
15584 | 14040 | 14.04 | -266 | 4.5
15585 | 13841 | 13.841 | -807 | 0.95
15586 | 13841 | 13.841 | 250 | 0.8
15587 | 13860 | 13.86 | 1000 | 3.2
15588 | 13974 | 13.974 | 47 | 3.9
15589 | 14134 | 14.134 | 943 | 4.45
15590 | 14285 | 14.285 | -392 | 2.4
15591 | 14200 | 14.2 | -1000 | 1.35
15592 | 14105 | 14.105 | 113 | 0.4
15593 | 14236 | 14.236 | -877 | 1.55
15594 | 14225 | 14.225 | 552 | 2.85
15595 | 14091 | 14.091 | 506 | 1.1
15596 | 14294 | 14.294 | 397 | 0.65
15597 | 14310 | 14.31 | 323 | 3.55
15598 | 14338 | 14.338 | -549 | 2.7
15599 | 14203 | 14.203 | 239 | 4.35
15600 | 14146 | 14.146 | 139 | 0.6
15601 | 14231 | 14.231 | 659 | 3.5
15602 | 14170 | 14.17 | 803 | 0.65
15603 | 14167 | 14.167 | -15 | 2.8
15604 | 14338 | 14.338 | -726 | 1.8
15605 | 14256 | 14.256 | -325 | 0.2
15606 | 14141 | 14.141 | 284 | 4.75
15607 | 14176 | 14.176 | -803 | 1.45
15608 | 14210 | 14.21 | -90 | 1.1
15609 | 14243 | 14.243 | -859 | 1.4
15610 | 14201 | 14.201 | -119 | 4.5
15611 | 14248 | 14.248 | 55 | 0.1
15612 | 14098 | 14.098 | -185 | 3.65
15613 | 14244 | 14.244 | 958 | 1
15614 | 14329 | 14.329 | -833 | 4.8
15615 | 14293 | 14.293 | 327 | 3.85
15616 | 14263 | 14.263 | -659 | 0.5
15617 | 14278 | 14.278 | 316 | 3.25
15618 | 14282 | 14.282 | 772 | 4.6
15619 | 14160 | 14.16 | -984 | 3.5
15620 | 14227 | 14.227 | -62 | 4.25
15621 | 14249 | 14.249 | 474 | 1.05
15622 | 14144 | 14.144 | -477 | 0.4
15623 | 14256 | 14.256 | 790 | 4.1
15624 | 14191 | 14.191 | 131 | 3.9
15625 | 14229 | 14.229 | -31 | 1.75
15626 | 14043 | 14.043 | 223 | 4.65
15627 | 14259 | 14.259 | -405 | 1.1
15628 | 14244 | 14.244 | -276 | 1.8
15629 | 14279 | 14.279 | 615 | 4.05
15630 | 14206 | 14.206 | 657 | 1.7
15631 | 14069 | 14.069 | -455 | 0.3
15632 | 13902 | 13.902 | -65 | 1.25
15633 | 14094 | 14.094 | 502 | 1.45
15634 | 14160 | 14.16 | -109 | 1.1
15635 | 14267 | 14.267 | 750 | 4.45
15636 | 14210 | 14.21 | -928 | 0.8
15637 | 14060 | 14.06 | -831 | 4.9
15638 | 14127 | 14.127 | -500 | 0.8
15639 | 14328 | 14.328 | 447 | 0
15640 | 14214 | 14.214 | 480 | 4.05
15641 | 14283 | 14.283 | -293 | 4.55
15642 | 14205 | 14.205 | -973 | 2.35
15643 | 14304 | 14.304 | 863 | 3.8
15644 | 14299 | 14.299 | 428 | 2.85
15645 | 14319 | 14.319 | 556 | 2.95
15646 | 14271 | 14.271 | 921 | 3.65
15647 | 14321 | 14.321 | -108 | 2.95
15648 | 14181 | 14.181 | 83 | 3.65
15649 | 13693 | 13.693 | -105 | 2
15650 | 13650 | 13.65 | -435 | 4.15
15651 | 13827 | 13.827 | 510 | 0.6
15652 | 13672 | 13.672 | -72 | 0
15653 | 13612 | 13.612 | 7 | 0.05
15654 | 13919 | 13.919 | 143 | 3
15655 | 14251 | 14.251 | -110 | 1.1
15656 | 14365 | 14.365 | 937 | 2.55
15657 | 14302 | 14.302 | -644 | 3.6
15658 | 14284 | 14.284 | 866 | 2.75
15659 | 14385 | 14.385 | 555 | 2.1
15660 | 14344 | 14.344 | 297 | 0.15
15661 | 14262 | 14.262 | 432 | 1.95
15662 | 14253 | 14.253 | 872 | 0.05
15663 | 14351 | 14.351 | 512 | 3
15664 | 14344 | 14.344 | 136 | 4.2
15665 | 14295 | 14.295 | 410 | 2.4
15666 | 14318 | 14.318 | -419 | 2.6
15667 | 14337 | 14.337 | 941 | 3.8
15668 | 14166 | 14.166 | 489 | 2.25
15669 | 14232 | 14.232 | 561 | 3.4
15670 | 14124 | 14.124 | -710 | 2.9
15671 | 14098 | 14.098 | -534 | 1.85
15672 | 14124 | 14.124 | 719 | 0.5
15673 | 14022 | 14.022 | -384 | 1.6
15674 | 14205 | 14.205 | -254 | 0.5
15675 | 14121 | 14.121 | 955 | 1.35
15676 | 14135 | 14.135 | 184 | 4.85
15677 | 14211 | 14.211 | 895 | 4.5
15678 | 14107 | 14.107 | -935 | 2.8
15679 | 14161 | 14.161 | 357 | 0.4
15680 | 14120 | 14.12 | 639 | 4.35
15681 | 14116 | 14.116 | -516 | 3.15
15682 | 14259 | 14.259 | 442 | 3.45
15683 | 14148 | 14.148 | 386 | 4.25
15684 | 14223 | 14.223 | 310 | 3.35
15685 | 14106 | 14.106 | 161 | 0.25
15686 | 14222 | 14.222 | -582 | 0.6
15687 | 14368 | 14.368 | -602 | 0.85
15688 | 14134 | 14.134 | -562 | 2.1
15689 | 14210 | 14.21 | 740 | 4
15690 | 14235 | 14.235 | -805 | 0.25
15691 | 14155 | 14.155 | -120 | 3.55
15692 | 14334 | 14.334 | -269 | 2.8
15693 | 14486 | 14.486 | -705 | 1.15
15694 | 14374 | 14.374 | 521 | 2.45
15695 | 14395 | 14.395 | 41 | 2.75
15696 | 14308 | 14.308 | -234 | 4.35
15697 | 14022 | 14.022 | -599 | 1.95
15698 | 13670 | 13.67 | 433 | 3.85
15699 | 13828 | 13.828 | 300 | 2.8
15700 | 13697 | 13.697 | 88 | 0.6
15701 | 13462 | 13.462 | 921 | 4.2
15702 | 14304 | 14.304 | 746 | 1.75
15703 | 14420 | 14.42 | -542 | 3.2
15704 | 14323 | 14.323 | -128 | 4.95
15705 | 14297 | 14.297 | -545 | 2.65
15706 | 14393 | 14.393 | -683 | 2.4
15707 | 14472 | 14.472 | -130 | 2.8
15708 | 14357 | 14.357 | 921 | 4.3
15709 | 14312 | 14.312 | -445 | 4.55
15710 | 14301 | 14.301 | -639 | 4.2
15711 | 14305 | 14.305 | -728 | 0.65
15712 | 14440 | 14.44 | -976 | 2.95
15713 | 14334 | 14.334 | -831 | 0.25
15714 | 14268 | 14.268 | -312 | 0.25
15715 | 14296 | 14.296 | 320 | 3.2
15716 | 14158 | 14.158 | 400 | 3.5
15717 | 14249 | 14.249 | 710 | 0.5
15718 | 14106 | 14.106 | 963 | 2.9
15719 | 14002 | 14.002 | -876 | 3.95
15720 | 14014 | 14.014 | 944 | 1.95
15721 | 13977 | 13.977 | -514 | 3.4
15722 | 14045 | 14.045 | -233 | 1.1
15723 | 13916 | 13.916 | -178 | 0.6
15724 | 13976 | 13.976 | -804 | 4
15725 | 13970 | 13.97 | 557 | 2.25
15726 | 13993 | 13.993 | -758 | 2.1
15727 | 13877 | 13.877 | -955 | 0.1
15728 | 13960 | 13.96 | 157 | 1.2
15729 | 13859 | 13.859 | 163 | 4.25
15730 | 14165 | 14.165 | -34 | 1.3
15731 | 13993 | 13.993 | 677 | 2.5
15732 | 14143 | 14.143 | 188 | 3.25
15733 | 14123 | 14.123 | -140 | 2.1
15734 | 14047 | 14.047 | 12 | 3.8
15735 | 14136 | 14.136 | -786 | 1.8
15736 | 14110 | 14.11 | -274 | 4.1
15737 | 14144 | 14.144 | 351 | 0.9
15738 | 14048 | 14.048 | 164 | 4.65
15739 | 14140 | 14.14 | 703 | 1.6
15740 | 14169 | 14.169 | 835 | 2.7
15741 | 14082 | 14.082 | -348 | 1.6
15742 | 14095 | 14.095 | -162 | 4.65
15743 | 13908 | 13.908 | -930 | 2.6
15744 | 13304 | 13.304 | -186 | 4.25
15745 | 13553 | 13.553 | 163 | 1.5
15746 | 13617 | 13.617 | -979 | 1.25
15747 | 13569 | 13.569 | -194 | 4
15748 | 13399 | 13.399 | -620 | 2.8
15749 | 13982 | 13.982 | -186 | 1.1
15750 | 14256 | 14.256 | 723 | 3.1
15751 | 14288 | 14.288 | 773 | 4.7
15752 | 14301 | 14.301 | 131 | 0.15
15753 | 14196 | 14.196 | -399 | 3.3
15754 | 14235 | 14.235 | -674 | 2.35
15755 | 14274 | 14.274 | 803 | 3.75
15756 | 14254 | 14.254 | 953 | 2.85
15757 | 14364 | 14.364 | -786 | 1.4
15758 | 14156 | 14.156 | 627 | 2.75
15759 | 14181 | 14.181 | 673 | 3.3
15760 | 14167 | 14.167 | 446 | 2.45
15761 | 14096 | 14.096 | -384 | 0.65
15762 | 14220 | 14.22 | 280 | 3.9
15763 | 14244 | 14.244 | -192 | 2.7
15764 | 14176 | 14.176 | 25 | 1.95
15765 | 14087 | 14.087 | -370 | 2.15
15766 | 14075 | 14.075 | 193 | 0.1
15767 | 14147 | 14.147 | -239 | 1.8
15768 | 14144 | 14.144 | -309 | 2.8
15769 | 14085 | 14.085 | 838 | 3.85
15770 | 14090 | 14.09 | -140 | 1.15
15771 | 14061 | 14.061 | -759 | 0
15772 | 13918 | 13.918 | 475 | 0.5
15773 | 14011 | 14.011 | -97 | 0.7
15774 | 14088 | 14.088 | 547 | 0.3
15775 | 14027 | 14.027 | 799 | 3.15
15776 | 14056 | 14.056 | -41 | 2.3
15777 | 14065 | 14.065 | 737 | 2.05
15778 | 14077 | 14.077 | -110 | 0.15
15779 | 14139 | 14.139 | 189 | 2.15
15780 | 14084 | 14.084 | -989 | 2.55
15781 | 14144 | 14.144 | 268 | 4.65
15782 | 14213 | 14.213 | 905 | 0.55
15783 | 14169 | 14.169 | 690 | 1.15
15784 | 14114 | 14.114 | -947 | 3.4
15785 | 14267 | 14.267 | 437 | 3.45
15786 | 14336 | 14.336 | -553 | 2
15787 | 14251 | 14.251 | -937 | 2.05
15788 | 14256 | 14.256 | 604 | 0.2
15789 | 14341 | 14.341 | 33 | 1.7
15790 | 14200 | 14.2 | -469 | 2.85
15791 | 14293 | 14.293 | -140 | 0.5
15792 | 14405 | 14.405 | -186 | 1.5
15793 | 14288 | 14.288 | -108 | 4.45
15794 | 14278 | 14.278 | -529 | 0.55
15795 | 13843 | 13.843 | 212 | 2.95
15796 | 13738 | 13.738 | 804 | 1.95
15797 | 13861 | 13.861 | 180 | 0.25
15798 | 13524 | 13.524 | -783 | 1.55
15799 | 13631 | 13.631 | -455 | 1.15
15800 | 14337 | 14.337 | -970 | 2.1
15801 | 14442 | 14.442 | -654 | 3.85
15802 | 14341 | 14.341 | -125 | 3
15803 | 14424 | 14.424 | 10 | 2.4
15804 | 14445 | 14.445 | 244 | 2.35
15805 | 14313 | 14.313 | -431 | 0.85
15806 | 14455 | 14.455 | -106 | 2.35
15807 | 14341 | 14.341 | -229 | 4.9
15808 | 14303 | 14.303 | -993 | 4.6
15809 | 14466 | 14.466 | -731 | 3.05
15810 | 14124 | 14.124 | 649 | 0.7
15811 | 13954 | 13.954 | -51 | 3.75
15812 | 14159 | 14.159 | 869 | 4.05
15813 | 14052 | 14.052 | -317 | 1.4
15814 | 14000 | 14 | 837 | 2
15815 | 14055 | 14.055 | -762 | 2.95
15816 | 14038 | 14.038 | 764 | 3
15817 | 14078 | 14.078 | -382 | 2.25
15818 | 13934 | 13.934 | -266 | 4.6
15819 | 13983 | 13.983 | 692 | 0.4
15820 | 13852 | 13.852 | -175 | 1.9
15821 | 14007 | 14.007 | 619 | 1.85
15822 | 13974 | 13.974 | 597 | 1.9
15823 | 13897 | 13.897 | -456 | 4.1
15824 | 14015 | 14.015 | 747 | 2.4
15825 | 14029 | 14.029 | 800 | 0.5
15826 | 14151 | 14.151 | -917 | 4.9
15827 | 14097 | 14.097 | 993 | 4.9
15828 | 14027 | 14.027 | -179 | 1.9
15829 | 13983 | 13.983 | 300 | 1.85
15830 | 14221 | 14.221 | 129 | 2.5
15831 | 14138 | 14.138 | 557 | 4.95
15832 | 14196 | 14.196 | 998 | 2.6
15833 | 14232 | 14.232 | 309 | 4.95
15834 | 14246 | 14.246 | -549 | 0.1
15835 | 14360 | 14.36 | -395 | 4.2
15836 | 14241 | 14.241 | -939 | 3.6
15837 | 14234 | 14.234 | 479 | 4.6
15838 | 14263 | 14.263 | -688 | 3.15
15839 | 14328 | 14.328 | 884 | 3.6
15840 | 14150 | 14.15 | 807 | 3.8
15841 | 13627 | 13.627 | -988 | 5
15842 | 13823 | 13.823 | -549 | 3.45
15843 | 13792 | 13.792 | 912 | 4.6
15844 | 13798 | 13.798 | 982 | 2.45
15845 | 13563 | 13.563 | 267 | 4.8
15846 | 14055 | 14.055 | 77 | 1.8
15847 | 14474 | 14.474 | -213 | 4.45
15848 | 14426 | 14.426 | 661 | 4.45
15849 | 14312 | 14.312 | 705 | 3.2
15850 | 14386 | 14.386 | -187 | 4.55
15851 | 14363 | 14.363 | 685 | 1.4
15852 | 14349 | 14.349 | 443 | 0.7
15853 | 14370 | 14.37 | 637 | 2.35
15854 | 14300 | 14.3 | 895 | 0.2
15855 | 14370 | 14.37 | 53 | 0.3
15856 | 14212 | 14.212 | 884 | 0.35
15857 | 14185 | 14.185 | 612 | 3.25
15858 | 14093 | 14.093 | 459 | 4
15859 | 14081 | 14.081 | 213 | 0.55
15860 | 14123 | 14.123 | -639 | 2
15861 | 14087 | 14.087 | -482 | 2.3
15862 | 14006 | 14.006 | -317 | 0.9
15863 | 14015 | 14.015 | 714 | 4.2
15864 | 13999 | 13.999 | 823 | 0.3
15865 | 13957 | 13.957 | 859 | 1.05
15866 | 13843 | 13.843 | 278 | 4.05
15867 | 13870 | 13.87 | -526 | 1.15
15868 | 13758 | 13.758 | 969 | 3.75
15869 | 13816 | 13.816 | 959 | 0.8
15870 | 13655 | 13.655 | -433 | 1.15
15871 | 13792 | 13.792 | 788 | 4.35
15872 | 13760 | 13.76 | 159 | 0.6
15873 | 13794 | 13.794 | -855 | 4.75
15874 | 13838 | 13.838 | -629 | 0.4
15875 | 13846 | 13.846 | -757 | 1.35
15876 | 13885 | 13.885 | 922 | 2.45
15877 | 14020 | 14.02 | 442 | 0.5
15878 | 13876 | 13.876 | -731 | 3.35
15879 | 14054 | 14.054 | -759 | 4.95
15880 | 13758 | 13.758 | -624 | 5
15881 | 13876 | 13.876 | 282 | 1.1
15882 | 13956 | 13.956 | -816 | 2.75
15883 | 13991 | 13.991 | 385 | 2.35
15884 | 13935 | 13.935 | -626 | 1.25
15885 | 14030 | 14.03 | 855 | 2.8
15886 | 14005 | 14.005 | -876 | 4.85
15887 | 14116 | 14.116 | 229 | 4
15888 | 14005 | 14.005 | -276 | 0.65
15889 | 13754 | 13.754 | 144 | 0.95
15890 | 13368 | 13.368 | 434 | 2.2
15891 | 13573 | 13.573 | 512 | 2.85
15892 | 13660 | 13.66 | 294 | 4.85
15893 | 13599 | 13.599 | 209 | 0.3
15894 | 13316 | 13.316 | 690 | 0.5
15895 | 14282 | 14.282 | -459 | 4.25
15896 | 14276 | 14.276 | -69 | 4.85
15897 | 14284 | 14.284 | 202 | 4.2
15898 | 14346 | 14.346 | 925 | 1
15899 | 14299 | 14.299 | 691 | 0.5
15900 | 14204 | 14.204 | -374 | 3.4
15901 | 14238 | 14.238 | -651 | 1.15
15902 | 14267 | 14.267 | -13 | 2.05
15903 | 14171 | 14.171 | -732 | 1.8
15904 | 14349 | 14.349 | 867 | 3.85
15905 | 14030 | 14.03 | 949 | 2.75
15906 | 14275 | 14.275 | 155 | 3.4
15907 | 14213 | 14.213 | 748 | 0.55
15908 | 14140 | 14.14 | 942 | 4.4
15909 | 14069 | 14.069 | -604 | 4.65
15910 | 14019 | 14.019 | 538 | 1.65
15911 | 14017 | 14.017 | -723 | 0.7
15912 | 14188 | 14.188 | -939 | 2.35
15913 | 14145 | 14.145 | -179 | 2.55
15914 | 13922 | 13.922 | 968 | 1.8
15915 | 13876 | 13.876 | -413 | 1.5
15916 | 13976 | 13.976 | -548 | 3.95
15917 | 13964 | 13.964 | 110 | 0.6
15918 | 13952 | 13.952 | 538 | 2.25
15919 | 13890 | 13.89 | -847 | 0.8
15920 | 13988 | 13.988 | -443 | 4
15921 | 14146 | 14.146 | -572 | 3.6
15922 | 14127 | 14.127 | -332 | 4.35
15923 | 14404 | 14.404 | -619 | 0.15
15924 | 14161 | 14.161 | -191 | 3.55
15925 | 14280 | 14.28 | -292 | 1.5
15926 | 14198 | 14.198 | -569 | 3.5
15927 | 14245 | 14.245 | -694 | 2.55
15928 | 14306 | 14.306 | 893 | 0.4
15929 | 14348 | 14.348 | 841 | 2.3
15930 | 14433 | 14.433 | 753 | 2.4
15931 | 14416 | 14.416 | 238 | 2.15
15932 | 14410 | 14.41 | -446 | 1.75
15933 | 14337 | 14.337 | 389 | 2.45
15934 | 14411 | 14.411 | 631 | 4.45
15935 | 14420 | 14.42 | 833 | 0.55
15936 | 14459 | 14.459 | -758 | 3.65
15937 | 13964 | 13.964 | 781 | 3
15938 | 13706 | 13.706 | 226 | 4.7
15939 | 13799 | 13.799 | 676 | 0.65
15940 | 13908 | 13.908 | -221 | 2.95
15941 | 13898 | 13.898 | -357 | 1.35
15942 | 13763 | 13.763 | -899 | 3.7
15943 | 14259 | 14.259 | -193 | 1.45
15944 | 14278 | 14.278 | -250 | 1.05
15945 | 14457 | 14.457 | -826 | 2.85
15946 | 14369 | 14.369 | -343 | 1.75
15947 | 14439 | 14.439 | -290 | 2.4
15948 | 14345 | 14.345 | -72 | 0.5
15949 | 14378 | 14.378 | -211 | 3.8
15950 | 14442 | 14.442 | -5 | 1.8
15951 | 14433 | 14.433 | -848 | 5
15952 | 14326 | 14.326 | 742 | 3.95
15953 | 14409 | 14.409 | -745 | 1.05
15954 | 14372 | 14.372 | 597 | 3.15
15955 | 14457 | 14.457 | -211 | 2.85
15956 | 14353 | 14.353 | -148 | 0.2
15957 | 14355 | 14.355 | -639 | 4.05
15958 | 14289 | 14.289 | 27 | 1.95
15959 | 14378 | 14.378 | -130 | 1.5
15960 | 14272 | 14.272 | 891 | 2
15961 | 14348 | 14.348 | 271 | 4.3
15962 | 14253 | 14.253 | 589 | 2.85
15963 | 14252 | 14.252 | -896 | 0.05
15964 | 14312 | 14.312 | -633 | 4.3
15965 | 14201 | 14.201 | 925 | 5
15966 | 14322 | 14.322 | -689 | 0.05
15967 | 14266 | 14.266 | 389 | 0.3
15968 | 14292 | 14.292 | -409 | 4.75
15969 | 14227 | 14.227 | -905 | 3.35
15970 | 14299 | 14.299 | 362 | 3.05
15971 | 14198 | 14.198 | 522 | 2.95
15972 | 14158 | 14.158 | -635 | 4.6
15973 | 14094 | 14.094 | -864 | 3.15
15974 | 14354 | 14.354 | 643 | 1.35
15975 | 14329 | 14.329 | -992 | 1.2
15976 | 14260 | 14.26 | 580 | 2.4
15977 | 14296 | 14.296 | -52 | 3.95
15978 | 14261 | 14.261 | -980 | 2.85
15979 | 14274 | 14.274 | 164 | 4.4
15980 | 14198 | 14.198 | 983 | 2
15981 | 14260 | 14.26 | 671 | 1.2
15982 | 14099 | 14.099 | -106 | 0.75
15983 | 14344 | 14.344 | 321 | 3.55
15984 | 14293 | 14.293 | 896 | 4.65
15985 | 13561 | 13.561 | -467 | 1.8
15986 | 13414 | 13.414 | 827 | 3.55
15987 | 13725 | 13.725 | -909 | 2.85
15988 | 13666 | 13.666 | -513 | 3.45
15989 | 13753 | 13.753 | -713 | 3.65
15990 | 13514 | 13.514 | 825 | 4.55
15991 | 14247 | 14.247 | 18 | 3.7
15992 | 14125 | 14.125 | -622 | 1
15993 | 14337 | 14.337 | -237 | 1
15994 | 14349 | 14.349 | -258 | 4.8
15995 | 14229 | 14.229 | 653 | 3.2
15996 | 14248 | 14.248 | -155 | 1.05
15997 | 14293 | 14.293 | -790 | 4.5
15998 | 14209 | 14.209 | 781 | 2.4
15999 | 14206 | 14.206 | -773 | 2.3
16000 | 14131 | 14.131 | -62 | 2.1
16001 | 14177 | 14.177 | 543 | 2.3
16002 | 14046 | 14.046 | 358 | 4.45
16003 | 14123 | 14.123 | -216 | 0.05
16004 | 14150 | 14.15 | -931 | 1.5
16005 | 14140 | 14.14 | 397 | 0.4
16006 | 14123 | 14.123 | -550 | 2.2
16007 | 14076 | 14.076 | 586 | 2.5
16008 | 13981 | 13.981 | -175 | 0.55
16009 | 13965 | 13.965 | -957 | 3.8
16010 | 14003 | 14.003 | -649 | 2.9
16011 | 13902 | 13.902 | 837 | 2.6
16012 | 13838 | 13.838 | -32 | 2.15
16013 | 13750 | 13.75 | -767 | 2.75
16014 | 13926 | 13.926 | 154 | 2.75
16015 | 13812 | 13.812 | 505 | 3.95
16016 | 13793 | 13.793 | -213 | 1.75
16017 | 13728 | 13.728 | -231 | 3.55
16018 | 13976 | 13.976 | -317 | 3.3
16019 | 13987 | 13.987 | 488 | 3.3
16020 | 13969 | 13.969 | 652 | 3.8
16021 | 13992 | 13.992 | -948 | 0.1
16022 | 14009 | 14.009 | 557 | 0.75
16023 | 14145 | 14.145 | 451 | 2.55
16024 | 14243 | 14.243 | -151 | 1.6
16025 | 14153 | 14.153 | -686 | 4.25
16026 | 14157 | 14.157 | -529 | 1.5
16027 | 14173 | 14.173 | 463 | 0.55
16028 | 14092 | 14.092 | -188 | 3.05
16029 | 14216 | 14.216 | 825 | 4.1
16030 | 14022 | 14.022 | 588 | 4.4
16031 | 14248 | 14.248 | 888 | 0
16032 | 13874 | 13.874 | 264 | 0.8
16033 | 13628 | 13.628 | -717 | 4.95
16034 | 13580 | 13.58 | -348 | 2.3
16035 | 13593 | 13.593 | -647 | 1.35
16036 | 13272 | 13.272 | 976 | 1.85
16037 | 13899 | 13.899 | -83 | 4.6
16038 | 14182 | 14.182 | -478 | 3.15
16039 | 14159 | 14.159 | 756 | 3.1
16040 | 14043 | 14.043 | 405 | 1.4
16041 | 14108 | 14.108 | 910 | 4.6
16042 | 14151 | 14.151 | -793 | 3.5
16043 | 14212 | 14.212 | -178 | 4.85
16044 | 14263 | 14.263 | 420 | 4.5
16045 | 13611 | 13.611 | -503 | 2.7
16046 | 14281 | 14.281 | -233 | 4.55
16047 | 14153 | 14.153 | -897 | 4.15
16048 | 14180 | 14.18 | -243 | 4.15
16049 | 14192 | 14.192 | -812 | 1.1
16050 | 14092 | 14.092 | -379 | 0.8
16051 | 14103 | 14.103 | -695 | 4.4
16052 | 14187 | 14.187 | 341 | 0.6
16053 | 13841 | 13.841 | -857 | 1.5
16054 | 13860 | 13.86 | -487 | 5
16055 | 13728 | 13.728 | 645 | 0.3
16056 | 13738 | 13.738 | 516 | 4.65
16057 | 13787 | 13.787 | -493 | 2.4
16058 | 13569 | 13.569 | 452 | 0.8
16059 | 13737 | 13.737 | -6 | 3.05
16060 | 13579 | 13.579 | -858 | 1.2
16061 | 13487 | 13.487 | -431 | 4.3
16062 | 13583 | 13.583 | 880 | 0.5
16063 | 13481 | 13.481 | -442 | 3.45
16064 | 13470 | 13.47 | 974 | 0.55
16065 | 13470 | 13.47 | -305 | 3.35
16066 | 13626 | 13.626 | -258 | 0.7
16067 | 13689 | 13.689 | 214 | 3.25
16068 | 13760 | 13.76 | 95 | 4.5
16069 | 13642 | 13.642 | 972 | 4.65
16070 | 13631 | 13.631 | 303 | 4.75
16071 | 13842 | 13.842 | -61 | 4.95
16072 | 13786 | 13.786 | 772 | 2.95
16073 | 13884 | 13.884 | -485 | 0.45
16074 | 13724 | 13.724 | -738 | 5
16075 | 13803 | 13.803 | -591 | 3.35
16076 | 13796 | 13.796 | 746 | 2.5
16077 | 13893 | 13.893 | -669 | 4.2
16078 | 13902 | 13.902 | 348 | 2.95
16079 | 13784 | 13.784 | 664 | 2.35
16080 | 13601 | 13.601 | 381 | 2.35
16081 | 13277 | 13.277 | 255 | 0.25
16082 | 13283 | 13.283 | 385 | 2.3
16083 | 13393 | 13.393 | -454 | 3.55
16084 | 13468 | 13.468 | 672 | 1.85
16085 | 13031 | 13.031 | -788 | 2.45
16086 | 13826 | 13.826 | -690 | 4.3
16087 | 14030 | 14.03 | 373 | 2.4
16088 | 13711 | 13.711 | 664 | 4.85
16089 | 14109 | 14.109 | 384 | 4.95
16090 | 13982 | 13.982 | 278 | 4.6
16091 | 13989 | 13.989 | 363 | 0.1
16092 | 13832 | 13.832 | -912 | 0.55
16093 | 14185 | 14.185 | -541 | 0.65
16094 | 14120 | 14.12 | 545 | 0.2
16095 | 14204 | 14.204 | -569 | 3.65
16096 | 14075 | 14.075 | 321 | 1.05
16097 | 14145 | 14.145 | 128 | 3.95
16098 | 14220 | 14.22 | 941 | 2.8
16099 | 14004 | 14.004 | 453 | 3.1
16100 | 14031 | 14.031 | 238 | 4.3
16101 | 13978 | 13.978 | 438 | 3.2
16102 | 13874 | 13.874 | 234 | 1.75
16103 | 13909 | 13.909 | 613 | 1.95
16104 | 13845 | 13.845 | -391 | 4.15
16105 | 13895 | 13.895 | 802 | 3.35
16106 | 13886 | 13.886 | 213 | 2
16107 | 13967 | 13.967 | 263 | 4.05
16108 | 13864 | 13.864 | 614 | 1.15
16109 | 13927 | 13.927 | -363 | 1.05
16110 | 13913 | 13.913 | -516 | 0.25
16111 | 13996 | 13.996 | -354 | 1.2
16112 | 13951 | 13.951 | -366 | 1.4
16113 | 13992 | 13.992 | -747 | 0.35
16114 | 14027 | 14.027 | 986 | 0.45
16115 | 14044 | 14.044 | -617 | 3.15
16116 | 14151 | 14.151 | 896 | 4.15
16117 | 14286 | 14.286 | 373 | 3.7
16118 | 14148 | 14.148 | 543 | 0.95
16119 | 14180 | 14.18 | 486 | 3.05
16120 | 14174 | 14.174 | 80 | 2.6
16121 | 14130 | 14.13 | -732 | 4.4
16122 | 14381 | 14.381 | 19 | 2.35
16123 | 14246 | 14.246 | 235 | 3.25
16124 | 14230 | 14.23 | 310 | 4.25
16125 | 14170 | 14.17 | 327 | 4.15
16126 | 14226 | 14.226 | -252 | 0.15
16127 | 14290 | 14.29 | 452 | 4.35
16128 | 14036 | 14.036 | -637 | 3.35
16129 | 13783 | 13.783 | -179 | 0.9
16130 | 13778 | 13.778 | 99 | 2.75
16131 | 13755 | 13.755 | 430 | 3.05
16132 | 13393 | 13.393 | -176 | 0.45
16133 | 14130 | 14.13 | 152 | 3.95
16134 | 14320 | 14.32 | -106 | 1.75
16135 | 14383 | 14.383 | 196 | 4.4
16136 | 14382 | 14.382 | -312 | 1.8
16137 | 14415 | 14.415 | 571 | 0.45
16138 | 14388 | 14.388 | 935 | 3.35
16139 | 14340 | 14.34 | 738 | 1.15
16140 | 14428 | 14.428 | 680 | 4.25
16141 | 14384 | 14.384 | -807 | 4.75
16142 | 14396 | 14.396 | 989 | 0.15
16143 | 14253 | 14.253 | 7 | 0.1
16144 | 14369 | 14.369 | 792 | 1.1
16145 | 14477 | 14.477 | -612 | 1.85
16146 | 14238 | 14.238 | 550 | 2.85
16147 | 14260 | 14.26 | 437 | 1.85
16148 | 14294 | 14.294 | -902 | 4.5
16149 | 14160 | 14.16 | 957 | 4.4
16150 | 14252 | 14.252 | 439 | 4.6
16151 | 14163 | 14.163 | -741 | 3.6
16152 | 14042 | 14.042 | 769 | 4.1
16153 | 14148 | 14.148 | -616 | 1.7
16154 | 14065 | 14.065 | 506 | 4.05
16155 | 14185 | 14.185 | 800 | 3.85
16156 | 14057 | 14.057 | -366 | 0.25
16157 | 14074 | 14.074 | -247 | 2.05
16158 | 14077 | 14.077 | -444 | 4.9
16159 | 14032 | 14.032 | 950 | 2.05
16160 | 13982 | 13.982 | 740 | 2.15
16161 | 14110 | 14.11 | 348 | 0.9
16162 | 14049 | 14.049 | -633 | 1.55
16163 | 14095 | 14.095 | -229 | 1.25
16164 | 14176 | 14.176 | -545 | 1.95
16165 | 14089 | 14.089 | -294 | 1.25
16166 | 14244 | 14.244 | 968 | 4.75
16167 | 14297 | 14.297 | -184 | 2.2
16168 | 14129 | 14.129 | 452 | 4.45
16169 | 14391 | 14.391 | 969 | 0.15
16170 | 14373 | 14.373 | 55 | 0.8
16171 | 14344 | 14.344 | 884 | 4
16172 | 14300 | 14.3 | 528 | 0.75
16173 | 14326 | 14.326 | 382 | 4.15
16174 | 14370 | 14.37 | -591 | 0.2
16175 | 14385 | 14.385 | -697 | 0.35
16176 | 14287 | 14.287 | 225 | 2.2
16177 | 14427 | 14.427 | -392 | 1.4
16178 | 13848 | 13.848 | 541 | 4.75
16179 | 13749 | 13.749 | 378 | 3.1
16180 | 13845 | 13.845 | -783 | 4.55
16181 | 13895 | 13.895 | 597 | 3.75
16182 | 13626 | 13.626 | 412 | 1.65
16183 | 13725 | 13.725 | 133 | 2.15
16184 | 14286 | 14.286 | 826 | 4.15
16185 | 14476 | 14.476 | 675 | 4.55
16186 | 14504 | 14.504 | 151 | 4.5
16187 | 14456 | 14.456 | -686 | 2.4
16188 | 14477 | 14.477 | 876 | 3.75
16189 | 14491 | 14.491 | 157 | 1.1
16190 | 14497 | 14.497 | 62 | 1
16191 | 14476 | 14.476 | 343 | 3.45
16192 | 14485 | 14.485 | -55 | 4.5
16193 | 14550 | 14.55 | -357 | 4.05
16194 | 14457 | 14.457 | -224 | 0.45
16195 | 14345 | 14.345 | 384 | 0.55
16196 | 14388 | 14.388 | 85 | 3.05
16197 | 14362 | 14.362 | -639 | 4.9
16198 | 14357 | 14.357 | -918 | 3.85
16199 | 14310 | 14.31 | -861 | 1.8
16200 | 14365 | 14.365 | -671 | 1.05
16201 | 14333 | 14.333 | 525 | 4
16202 | 14336 | 14.336 | -506 | 4.2
16203 | 14374 | 14.374 | -607 | 0.4
16204 | 14184 | 14.184 | 269 | 1.3
16205 | 14350 | 14.35 | 835 | 3.95
16206 | 14372 | 14.372 | -188 | 3.55
16207 | 14284 | 14.284 | -971 | 2.4
16208 | 14356 | 14.356 | 406 | 0.75
16209 | 14421 | 14.421 | -679 | 3.85
16210 | 14243 | 14.243 | -826 | 0.7
16211 | 14475 | 14.475 | -993 | 4.25
16212 | 14364 | 14.364 | 227 | 1.15
16213 | 14439 | 14.439 | 667 | 4
16214 | 14456 | 14.456 | 880 | 1.45
16215 | 14430 | 14.43 | 345 | 4.35
16216 | 14434 | 14.434 | 347 | 0.25
16217 | 14483 | 14.483 | -634 | 0.05
16218 | 14440 | 14.44 | -928 | 2.85
16219 | 14378 | 14.378 | 275 | 3.65
16220 | 14455 | 14.455 | -257 | 4.05
16221 | 14486 | 14.486 | 577 | 1.55
16222 | 14579 | 14.579 | -917 | 3.1
16223 | 14473 | 14.473 | 452 | 1.45
16224 | 14321 | 14.321 | -352 | 3.8
16225 | 13961 | 13.961 | 704 | 3.65
16226 | 13927 | 13.927 | -371 | 4.6
16227 | 13971 | 13.971 | 838 | 0.25
16228 | 13594 | 13.594 | -661 | 3.7
16229 | 13867 | 13.867 | -60 | 2.35
16230 | 14408 | 14.408 | -261 | 3.5
16231 | 14548 | 14.548 | 678 | 2.8
16232 | 14328 | 14.328 | -221 | 2.3
16233 | 14400 | 14.4 | 308 | 1.3
16234 | 14402 | 14.402 | 83 | 0.75
16235 | 14285 | 14.285 | -295 | 2.1
16236 | 14517 | 14.517 | 484 | 3.2
16237 | 14313 | 14.313 | -29 | 2.95
16238 | 14479 | 14.479 | 813 | 3.45
16239 | 14485 | 14.485 | -771 | 0.1
16240 | 14373 | 14.373 | 88 | 1.25
16241 | 14337 | 14.337 | -894 | 0.35
16242 | 14546 | 14.546 | -533 | 3.4
16243 | 14384 | 14.384 | -685 | 0.75
16244 | 14363 | 14.363 | 13 | 2.2
16245 | 14205 | 14.205 | 517 | 4.35
16246 | 14424 | 14.424 | -695 | 2.35
16247 | 14166 | 14.166 | -936 | 0.85
16248 | 14257 | 14.257 | 637 | 1.5
16249 | 14033 | 14.033 | -407 | 4
16250 | 14026 | 14.026 | -382 | 0.35
16251 | 14285 | 14.285 | 215 | 4.1
16252 | 14221 | 14.221 | 439 | 1.8
16253 | 14282 | 14.282 | -37 | 3.8
16254 | 14136 | 14.136 | -406 | 0.25
16255 | 14281 | 14.281 | -930 | 1.6
16256 | 14202 | 14.202 | 191 | 4
16257 | 14356 | 14.356 | 344 | 3.4
16258 | 14260 | 14.26 | -593 | 0.45
16259 | 14372 | 14.372 | -845 | 3.6
16260 | 14323 | 14.323 | 947 | 3.05
16261 | 14379 | 14.379 | -141 | 2.45
16262 | 14437 | 14.437 | -269 | 1.95
16263 | 14413 | 14.413 | -975 | 0.15
16264 | 14403 | 14.403 | 417 | 1.7
16265 | 14494 | 14.494 | 379 | 0.3
16266 | 14454 | 14.454 | 479 | 1.2
16267 | 14583 | 14.583 | 8 | 3.75
16268 | 14485 | 14.485 | 541 | 0.95
16269 | 14541 | 14.541 | 626 | 1.55
16270 | 14527 | 14.527 | -42 | 0.6
16271 | 14372 | 14.372 | 807 | 1
16272 | 14336 | 14.336 | -49 | 0
16273 | 14302 | 14.302 | -223 | 2.05
16274 | 13553 | 13.553 | -660 | 0.55
16275 | 14446 | 14.446 | -54 | 1.8
16276 | 14558 | 14.558 | 308 | 3.55
16277 | 14693 | 14.693 | 998 | 3.15
16278 | 14588 | 14.588 | 845 | 4.7
16279 | 14492 | 14.492 | -119 | 1.1
16280 | 14611 | 14.611 | -155 | 2.7
16281 | 14532 | 14.532 | -655 | 2.2
16282 | 14548 | 14.548 | 261 | 4.25
16283 | 14595 | 14.595 | 564 | 2.45
16284 | 14611 | 14.611 | 673 | 3.8
16285 | 14644 | 14.644 | 513 | 1.85
16286 | 14389 | 14.389 | -952 | 3.2
16287 | 14538 | 14.538 | 428 | 4.7
16288 | 14530 | 14.53 | -415 | 1.3
16289 | 14465 | 14.465 | -973 | 2.65
16290 | 14444 | 14.444 | -321 | 0.65
16291 | 14503 | 14.503 | 47 | 3
16292 | 14618 | 14.618 | -241 | 2.15
16293 | 14278 | 14.278 | 802 | 4.65
16294 | 14305 | 14.305 | -707 | 3
16295 | 14348 | 14.348 | 306 | 2.05
16296 | 14275 | 14.275 | -996 | 1.75
16297 | 14305 | 14.305 | 542 | 2.3
16298 | 14181 | 14.181 | 315 | 4.35
16299 | 14103 | 14.103 | 471 | 0.15
16300 | 14135 | 14.135 | 836 | 1
16301 | 14256 | 14.256 | -931 | 1.7
16302 | 14176 | 14.176 | 577 | 0.25
16303 | 14127 | 14.127 | -848 | 1.15
16304 | 14194 | 14.194 | -136 | 4.95
16305 | 14214 | 14.214 | 144 | 1.4
16306 | 14249 | 14.249 | 422 | 2.6
16307 | 14227 | 14.227 | 647 | 0.05
16308 | 14224 | 14.224 | -874 | 3.25
16309 | 14232 | 14.232 | 747 | 1.35
16310 | 14200 | 14.2 | 155 | 2.4
16311 | 14304 | 14.304 | -169 | 4.7
16312 | 14347 | 14.347 | 66 | 0.1
16313 | 14448 | 14.448 | 772 | 3.25
16314 | 14280 | 14.28 | -188 | 3.1
16315 | 14474 | 14.474 | -958 | 2.4
16316 | 14288 | 14.288 | 752 | 3.4
16317 | 14621 | 14.621 | 561 | 3.75
16318 | 14425 | 14.425 | -534 | 0
16319 | 14256 | 14.256 | -220 | 1.55
16320 | 14096 | 14.096 | 38 | 4.75
16321 | 13566 | 13.566 | -273 | 3.65
16322 | 13898 | 13.898 | 438 | 2
16323 | 13932 | 13.932 | -874 | 0.7
16324 | 13804 | 13.804 | -449 | 2.85
16325 | 13548 | 13.548 | -455 | 1.25
16326 | 14148 | 14.148 | 316 | 1.5
16327 | 14407 | 14.407 | -623 | 1.3
16328 | 14391 | 14.391 | -804 | 3.1
16329 | 14396 | 14.396 | -509 | 4
16330 | 14497 | 14.497 | -310 | 3.4
16331 | 14305 | 14.305 | 337 | 2.15
16332 | 14403 | 14.403 | 985 | 2.45
16333 | 14339 | 14.339 | 268 | 4.05
16334 | 14402 | 14.402 | -904 | 0.1
16335 | 14409 | 14.409 | 746 | 1.45
16336 | 14398 | 14.398 | 83 | 2.85
16337 | 14394 | 14.394 | 205 | 1.6
16338 | 14369 | 14.369 | -989 | 2.6
16339 | 14306 | 14.306 | 417 | 0.2
16340 | 14254 | 14.254 | 703 | 3.65
16341 | 14320 | 14.32 | 297 | 1.4
16342 | 14169 | 14.169 | -545 | 1.5
16343 | 14083 | 14.083 | 128 | 3.5
16344 | 14180 | 14.18 | 294 | 4.8
16345 | 14016 | 14.016 | -471 | 4.95
16346 | 14099 | 14.099 | -10 | 1.75
16347 | 13981 | 13.981 | 70 | 0.6
16348 | 14023 | 14.023 | -41 | 4.2
16349 | 14025 | 14.025 | -525 | 0.15
16350 | 14005 | 14.005 | 184 | 0.25
16351 | 13955 | 13.955 | -173 | 1.65
16352 | 13992 | 13.992 | -722 | 2.85
16353 | 14097 | 14.097 | -88 | 3.95
16354 | 14099 | 14.099 | 351 | 1.25
16355 | 14006 | 14.006 | -548 | 0
16356 | 14082 | 14.082 | 149 | 1.05
16357 | 14152 | 14.152 | 619 | 4.75
16358 | 14178 | 14.178 | -556 | 2.45
16359 | 14258 | 14.258 | 92 | 3.5
16360 | 14186 | 14.186 | -838 | 0.6
16361 | 14300 | 14.3 | 49 | 2.6
16362 | 14234 | 14.234 | -283 | 0.35
16363 | 14231 | 14.231 | 328 | 3.45
16364 | 14203 | 14.203 | -979 | 3.45
16365 | 14116 | 14.116 | -153 | 0.35
16366 | 14292 | 14.292 | 641 | 1.7
16367 | 14174 | 14.174 | 137 | 2.6
16368 | 14156 | 14.156 | 800 | 0.2
16369 | 13724 | 13.724 | 86 | 4
16370 | 13554 | 13.554 | -187 | 1.9
16371 | 14091 | 14.091 | -212 | 2.15
16372 | 14083 | 14.083 | -503 | 0.05
16373 | 14210 | 14.21 | 509 | 4.05
16374 | 14277 | 14.277 | 200 | 3
16375 | 14287 | 14.287 | -904 | 0.55
16376 | 14224 | 14.224 | 677 | 2.35
16377 | 14303 | 14.303 | 723 | 4.55
16378 | 14345 | 14.345 | 594 | 1.95
16379 | 14222 | 14.222 | 198 | 2.7
16380 | 14366 | 14.366 | 654 | 0.75
16381 | 14255 | 14.255 | -179 | 1.2
16382 | 14263 | 14.263 | 621 | 3.1
16383 | 14320 | 14.32 | -570 | 0.45
16384 | 14271 | 14.271 | 149 | 1.7
16385 | 14185 | 14.185 | -309 | 1.2
16386 | 14249 | 14.249 | 451 | 1.15
16387 | 14230 | 14.23 | -699 | 3.8
16388 | 14244 | 14.244 | 359 | 1.85
16389 | 14035 | 14.035 | -439 | 0.5
16390 | 14305 | 14.305 | -405 | 3.15
16391 | 14318 | 14.318 | 668 | 1.95
16392 | 14029 | 14.029 | -999 | 4.55
16393 | 14131 | 14.131 | -146 | 1.4
16394 | 14040 | 14.04 | 115 | 0.45
16395 | 13985 | 13.985 | -605 | 3
16396 | 13978 | 13.978 | -372 | 0.55
16397 | 14031 | 14.031 | 401 | 3.3
16398 | 14020 | 14.02 | 96 | 2.1
16399 | 14113 | 14.113 | 428 | 0.1
16400 | 14091 | 14.091 | -411 | 2.25
16401 | 14289 | 14.289 | -691 | 4.3
16402 | 14248 | 14.248 | -644 | 1.55
16403 | 14264 | 14.264 | 329 | 0.65
16404 | 14289 | 14.289 | -487 | 3.55
16405 | 14226 | 14.226 | 696 | 0.95
16406 | 14389 | 14.389 | -868 | 1.75
16407 | 14336 | 14.336 | -757 | 1.15
16408 | 14357 | 14.357 | -972 | 0.95
16409 | 14340 | 14.34 | 465 | 3.8
16410 | 14484 | 14.484 | -443 | 3.2
16411 | 14326 | 14.326 | -384 | 1.45
16412 | 14344 | 14.344 | 213 | 3.1
16413 | 14400 | 14.4 | 99 | 4.3
16414 | 14350 | 14.35 | -51 | 2.7
16415 | 14325 | 14.325 | -459 | 4.85
16416 | 14273 | 14.273 | -694 | 4.1
16417 | 13706 | 13.706 | -904 | 4
16418 | 13812 | 13.812 | -539 | 0.8
16419 | 13818 | 13.818 | -678 | 0.7
16420 | 13866 | 13.866 | -736 | 2.2
16421 | 13393 | 13.393 | 657 | 0.55
16422 | 14028 | 14.028 | -831 | 2.7
16423 | 14355 | 14.355 | -739 | 2.2
16424 | 14480 | 14.48 | 231 | 2.15
16425 | 14413 | 14.413 | -965 | 4.15
16426 | 14444 | 14.444 | 212 | 0.9
16427 | 14470 | 14.47 | -691 | 1.2
16428 | 14354 | 14.354 | -938 | 1.25
16429 | 14364 | 14.364 | 199 | 3.05
16430 | 14410 | 14.41 | -357 | 0
16431 | 14465 | 14.465 | 409 | 1.8
16432 | 14161 | 14.161 | -88 | 0
16433 | 14422 | 14.422 | -133 | 2.45
16434 | 14364 | 14.364 | 670 | 1.35
16435 | 14256 | 14.256 | -439 | 0.35
16436 | 14200 | 14.2 | 97 | 2.95
16437 | 14197 | 14.197 | 595 | 1.6
16438 | 14256 | 14.256 | -121 | 1.7
16439 | 14075 | 14.075 | -211 | 0.4
16440 | 14152 | 14.152 | -820 | 4.95
16441 | 14092 | 14.092 | -309 | 4.2
16442 | 14167 | 14.167 | -459 | 1.5
16443 | 14105 | 14.105 | 262 | 3.2
16444 | 14161 | 14.161 | -806 | 4.6
16445 | 14081 | 14.081 | -144 | 1.4
16446 | 14093 | 14.093 | -536 | 4.4
16447 | 14186 | 14.186 | 546 | 0.7
16448 | 14143 | 14.143 | -682 | 0.65
16449 | 14111 | 14.111 | -898 | 2.45
16450 | 14159 | 14.159 | -448 | 4.65
16451 | 14164 | 14.164 | 274 | 1.45
16452 | 14299 | 14.299 | -201 | 0.95
16453 | 14246 | 14.246 | -140 | 0.5
16454 | 14193 | 14.193 | -392 | 1.25
16455 | 14242 | 14.242 | 795 | 4
16456 | 14375 | 14.375 | 395 | 1.8
16457 | 14282 | 14.282 | 811 | 3
16458 | 14278 | 14.278 | 127 | 2.75
16459 | 14359 | 14.359 | -862 | 4.85
16460 | 14305 | 14.305 | 676 | 0.65
16461 | 14340 | 14.34 | 550 | 1.25
16462 | 14308 | 14.308 | 334 | 1.9
16463 | 14334 | 14.334 | 800 | 2.85
16464 | 13947 | 13.947 | -754 | 2.6
16465 | 13400 | 13.4 | 60 | 4.7
16466 | 14262 | 14.262 | 86 | 0.7
16467 | 14502 | 14.502 | 989 | 4.9
16468 | 14327 | 14.327 | 561 | 0.7
16469 | 14347 | 14.347 | 644 | 3.65
16470 | 14365 | 14.365 | 4 | 2.15
16471 | 14291 | 14.291 | -50 | 0.25
16472 | 14351 | 14.351 | -879 | 1.2
16473 | 14315 | 14.315 | 835 | 3.6
16474 | 14289 | 14.289 | -738 | 2.5
16475 | 14334 | 14.334 | 688 | 4.2
16476 | 14217 | 14.217 | -785 | 3
16477 | 14388 | 14.388 | 551 | 1
16478 | 14325 | 14.325 | -301 | 3.3
16479 | 14294 | 14.294 | -929 | 3.4
16480 | 14351 | 14.351 | -430 | 3.8
16481 | 14350 | 14.35 | -674 | 2.65
16482 | 14295 | 14.295 | 105 | 1.15
16483 | 14381 | 14.381 | -527 | 2.9
16484 | 14288 | 14.288 | -91 | 3.95
16485 | 14329 | 14.329 | 757 | 4.8
16486 | 14293 | 14.293 | 840 | 4.15
16487 | 14210 | 14.21 | -888 | 3.2
16488 | 14360 | 14.36 | 651 | 3.8
16489 | 14225 | 14.225 | 470 | 2.05
16490 | 14343 | 14.343 | -606 | 1.5
16491 | 14175 | 14.175 | -528 | 0.1
16492 | 14385 | 14.385 | 453 | 4.75
16493 | 14128 | 14.128 | -863 | 3.85
16494 | 14120 | 14.12 | -872 | 2.05
16495 | 14223 | 14.223 | 538 | 3.3
16496 | 14192 | 14.192 | 206 | 2.65
16497 | 14298 | 14.298 | -120 | 3.5
16498 | 14236 | 14.236 | 591 | 2.05
16499 | 14347 | 14.347 | 627 | 3.5
16500 | 14179 | 14.179 | 40 | 0.4
16501 | 14293 | 14.293 | -946 | 4.05
16502 | 14216 | 14.216 | -25 | 4.05
16503 | 14181 | 14.181 | 938 | 0.5
16504 | 14072 | 14.072 | -85 | 4.65
16505 | 14104 | 14.104 | 440 | 0
16506 | 14432 | 14.432 | 352 | 1.25
16507 | 14316 | 14.316 | -225 | 0.55
16508 | 14310 | 14.31 | 494 | 4.8
16509 | 14326 | 14.326 | -155 | 4.8
16510 | 14310 | 14.31 | 708 | 3.3
16511 | 14224 | 14.224 | -635 | 1.55
16512 | 13700 | 13.7 | -836 | 2.5
16513 | 13515 | 13.515 | 942 | 4.85
16514 | 13557 | 13.557 | -260 | 0.6
16515 | 13774 | 13.774 | 87 | 0.65
16516 | 13570 | 13.57 | -870 | 3
16517 | 13602 | 13.602 | 293 | 3.75
16518 | 14494 | 14.494 | 700 | 2.35
16519 | 14285 | 14.285 | 274 | 2.55
16520 | 14472 | 14.472 | -980 | 4.5
16521 | 14369 | 14.369 | 103 | 1.8
16522 | 14323 | 14.323 | -948 | 3.35
16523 | 14495 | 14.495 | 306 | 2.15
16524 | 14469 | 14.469 | 483 | 1.9
16525 | 14348 | 14.348 | 798 | 4.6
16526 | 14465 | 14.465 | -377 | 0.85
16527 | 14452 | 14.452 | 773 | 1.05
16528 | 14470 | 14.47 | -384 | 1.05
16529 | 14418 | 14.418 | 474 | 2.7
16530 | 14335 | 14.335 | -263 | 0.2
16531 | 14412 | 14.412 | -83 | 2.55
16532 | 14275 | 14.275 | -229 | 5
16533 | 14442 | 14.442 | -966 | 4.85
16534 | 14230 | 14.23 | -544 | 0.3
16535 | 14353 | 14.353 | 947 | 1.65
16536 | 14249 | 14.249 | -571 | 0.5
16537 | 14376 | 14.376 | 162 | 0
16538 | 14237 | 14.237 | -984 | 2.75
16539 | 14408 | 14.408 | -62 | 3.7
16540 | 14379 | 14.379 | -175 | 1.3
16541 | 14281 | 14.281 | 987 | 3.8
16542 | 14396 | 14.396 | 504 | 3.75
16543 | 14336 | 14.336 | 98 | 0.55
16544 | 14318 | 14.318 | -107 | 2.65
16545 | 14336 | 14.336 | 421 | 0.4
16546 | 14365 | 14.365 | -864 | 2.65
16547 | 14493 | 14.493 | -732 | 4.1
16548 | 14364 | 14.364 | -51 | 0.75
16549 | 14352 | 14.352 | -169 | 0.85
16550 | 14334 | 14.334 | -304 | 1.7
16551 | 14360 | 14.36 | 915 | 2.15
16552 | 14471 | 14.471 | 987 | 1.65
16553 | 14398 | 14.398 | -246 | 1.95
16554 | 14359 | 14.359 | -263 | 0.9
16555 | 14491 | 14.491 | 643 | 4.95
16556 | 14375 | 14.375 | 345 | 3.9
16557 | 14340 | 14.34 | -532 | 1.65
16558 | 14414 | 14.414 | -976 | 2.45
16559 | 14454 | 14.454 | -392 | 0.4
16560 | 14450 | 14.45 | 139 | 2.85
16561 | 14365 | 14.365 | 781 | 1.35
16562 | 14148 | 14.148 | -662 | 1.7
16563 | 13800 | 13.8 | 712 | 1.95
16564 | 13404 | 13.404 | 858 | 4.8
16565 | 14187 | 14.187 | -976 | 1.2
16566 | 14239 | 14.239 | -455 | 2.75
16567 | 14153 | 14.153 | 775 | 2.1
16568 | 14410 | 14.41 | -508 | 4.05
16569 | 14370 | 14.37 | -993 | 2.85
16570 | 14454 | 14.454 | -251 | 4.1
16571 | 14585 | 14.585 | -220 | 2.8
16572 | 14393 | 14.393 | -95 | 2.75
16573 | 14388 | 14.388 | -670 | 2
16574 | 14582 | 14.582 | 497 | 2.55
16575 | 14435 | 14.435 | 765 | 0
16576 | 14565 | 14.565 | 66 | 2.15
16577 | 14464 | 14.464 | -34 | 0.35
16578 | 14508 | 14.508 | -462 | 4.85
16579 | 14517 | 14.517 | -810 | 0.15
16580 | 14477 | 14.477 | -597 | 1.55
16581 | 14411 | 14.411 | -105 | 4.85
16582 | 14330 | 14.33 | 703 | 0.35
16583 | 14293 | 14.293 | -878 | 3.8
16584 | 14244 | 14.244 | -774 | 0.1
16585 | 14375 | 14.375 | 706 | 0.1
16586 | 14342 | 14.342 | 433 | 2.1
16587 | 14311 | 14.311 | -564 | 3.8
16588 | 14311 | 14.311 | -789 | 3.45
16589 | 14412 | 14.412 | -849 | 1.8
16590 | 14309 | 14.309 | 475 | 1.85
16591 | 14345 | 14.345 | -453 | 4.3
16592 | 14512 | 14.512 | -746 | 1.4
16593 | 14324 | 14.324 | -573 | 1.3
16594 | 14376 | 14.376 | 581 | 3.75
16595 | 14387 | 14.387 | -291 | 0.75
16596 | 14432 | 14.432 | 789 | 2.8
16597 | 14503 | 14.503 | -863 | 2.95
16598 | 14536 | 14.536 | -304 | 0.15
16599 | 14548 | 14.548 | -937 | 1.15
16600 | 14402 | 14.402 | -976 | 0.8
16601 | 14575 | 14.575 | -739 | 2.6
16602 | 14460 | 14.46 | 190 | 1.75
16603 | 14507 | 14.507 | -871 | 2.45
16604 | 14524 | 14.524 | -102 | 2.2
16605 | 14519 | 14.519 | 331 | 4.75
16606 | 14616 | 14.616 | 989 | 1.65
16607 | 14279 | 14.279 | 648 | 3.8
16608 | 13710 | 13.71 | -172 | 3.5
16609 | 13961 | 13.961 | 916 | 3.1
16610 | 13972 | 13.972 | 17 | 1.9
16611 | 13997 | 13.997 | -222 | 4.9
16612 | 13359 | 13.359 | 628 | 3.55
16613 | 14331 | 14.331 | -527 | 3.7
16614 | 14552 | 14.552 | -147 | 0.05
16615 | 14587 | 14.587 | 200 | 0.1
16616 | 14513 | 14.513 | 652 | 3.7
16617 | 14492 | 14.492 | 456 | 1.2
16618 | 14644 | 14.644 | 915 | 1
16619 | 14580 | 14.58 | -116 | 4.95
16620 | 14476 | 14.476 | 579 | 0.15
16621 | 14649 | 14.649 | 693 | 0.2
16622 | 14502 | 14.502 | -495 | 4.15
16623 | 14368 | 14.368 | 574 | 2
16624 | 14652 | 14.652 | 998 | 3.75
16625 | 14520 | 14.52 | -964 | 0.3
16626 | 14561 | 14.561 | -453 | 2.75
16627 | 14541 | 14.541 | -46 | 1.2
16628 | 14345 | 14.345 | -875 | 4.1
16629 | 14357 | 14.357 | 220 | 2.05
16630 | 14568 | 14.568 | 587 | 1.85
16631 | 14354 | 14.354 | 548 | 4.35
16632 | 14286 | 14.286 | 102 | 4
16633 | 14523 | 14.523 | -847 | 4.45
16634 | 14418 | 14.418 | 745 | 0.15
16635 | 14362 | 14.362 | 556 | 0.15
16636 | 14480 | 14.48 | 837 | 4.6
16637 | 14477 | 14.477 | 971 | 0.55
16638 | 14373 | 14.373 | -788 | 0.9
16639 | 14484 | 14.484 | -533 | 0.6
16640 | 14456 | 14.456 | -464 | 0.65
16641 | 14332 | 14.332 | 476 | 0.75
16642 | 14526 | 14.526 | -105 | 0.45
16643 | 14463 | 14.463 | 386 | 3.9
16644 | 14438 | 14.438 | -276 | 3.75
16645 | 14445 | 14.445 | -648 | 4.15
16646 | 14489 | 14.489 | 572 | 1.2
16647 | 14404 | 14.404 | 887 | 3.3
16648 | 14311 | 14.311 | -377 | 2.9
16649 | 14473 | 14.473 | 722 | 4.5
16650 | 14400 | 14.4 | 529 | 0.25
16651 | 14353 | 14.353 | -189 | 0.5
16652 | 14655 | 14.655 | 128 | 4
16653 | 14499 | 14.499 | 741 | 4.55
16654 | 14302 | 14.302 | -497 | 4.35
16655 | 13743 | 13.743 | -564 | 3.25
16656 | 13772 | 13.772 | 955 | 3.1
16657 | 14357 | 14.357 | 734 | 2.35
16658 | 14355 | 14.355 | 431 | 0.25
16659 | 14451 | 14.451 | -201 | 0.2
16660 | 14354 | 14.354 | 0 | 1.7
16661 | 14419 | 14.419 | 254 | 3.25
16662 | 14449 | 14.449 | -880 | 0.15
16663 | 14445 | 14.445 | -57 | 2.1
16664 | 14203 | 14.203 | 805 | 3.05
16665 | 14286 | 14.286 | 281 | 3.2
16666 | 14404 | 14.404 | -843 | 2.7
16667 | 14423 | 14.423 | 150 | 5
16668 | 14339 | 14.339 | -120 | 2.85
16669 | 14607 | 14.607 | 255 | 4.65
16670 | 14377 | 14.377 | -431 | 2.05
16671 | 14413 | 14.413 | 179 | 4.25
16672 | 13491 | 13.491 | 236 | 1.65
16673 | 13562 | 13.562 | 271 | 2.7
16674 | 13503 | 13.503 | 889 | 4.9
16675 | 13610 | 13.61 | -32 | 1.8
16676 | 13477 | 13.477 | 301 | 2.9
16677 | 13451 | 13.451 | -31 | 0.75
16678 | 13421 | 13.421 | -873 | 0.8
16679 | 13492 | 13.492 | -542 | 2.7
16680 | 14113 | 14.113 | -610 | 0.75
16681 | 14336 | 14.336 | -492 | 2
16682 | 14362 | 14.362 | -361 | 5
16683 | 14448 | 14.448 | -629 | 0.9
16684 | 14342 | 14.342 | 623 | 1.55
16685 | 14253 | 14.253 | 389 | 0.35
16686 | 14268 | 14.268 | -4 | 2.95
16687 | 14220 | 14.22 | -198 | 3.85
16688 | 14290 | 14.29 | -850 | 1.7
16689 | 14261 | 14.261 | 306 | 2.55
16690 | 14362 | 14.362 | -689 | 0.4
16691 | 14283 | 14.283 | -442 | 4
16692 | 14219 | 14.219 | 532 | 1.35
16693 | 14267 | 14.267 | 325 | 4.85
16694 | 14350 | 14.35 | -294 | 1.2
16695 | 14319 | 14.319 | -213 | 4.9
16696 | 14384 | 14.384 | 377 | 1.6
16697 | 14418 | 14.418 | -583 | 1
16698 | 14270 | 14.27 | 124 | 2.9
16699 | 14403 | 14.403 | 636 | 4.2
16700 | 14298 | 14.298 | -63 | 0.85
16701 | 14220 | 14.22 | -647 | 1.4
16702 | 14533 | 14.533 | 607 | 4.8
16703 | 14058 | 14.058 | -862 | 3.15
16704 | 13825 | 13.825 | 281 | 0.65
16705 | 13223 | 13.223 | 20 | 0.5
16706 | 13339 | 13.339 | -333 | 2.75
16707 | 13451 | 13.451 | 914 | 1.6
16708 | 13567 | 13.567 | -378 | 0.6
16709 | 13573 | 13.573 | 99 | 2.45
16710 | 14429 | 14.429 | 371 | 4.65
16711 | 14407 | 14.407 | -884 | 0.8
16712 | 14325 | 14.325 | 647 | 2.5
16713 | 14514 | 14.514 | 342 | 1.35
16714 | 14312 | 14.312 | -408 | 3.25
16715 | 14402 | 14.402 | -97 | 2.25
16716 | 14507 | 14.507 | -714 | 2.35
16717 | 14422 | 14.422 | -88 | 2.9
16718 | 14472 | 14.472 | -480 | 3.25
16719 | 14445 | 14.445 | -599 | 4.2
16720 | 14481 | 14.481 | -687 | 4.15
16721 | 14394 | 14.394 | 881 | 4.95
16722 | 14430 | 14.43 | 611 | 1.9
16723 | 14467 | 14.467 | -636 | 1.45
16724 | 14330 | 14.33 | 733 | 4.8
16725 | 14381 | 14.381 | 944 | 3.6
16726 | 14270 | 14.27 | -916 | 0.95
16727 | 14359 | 14.359 | 877 | 4.8
16728 | 14473 | 14.473 | 606 | 4.65
16729 | 14304 | 14.304 | 253 | 0.85
16730 | 14261 | 14.261 | 15 | 0.8
16731 | 14284 | 14.284 | 362 | 3.35
16732 | 14424 | 14.424 | 104 | 4.3
16733 | 14401 | 14.401 | 717 | 0.85
16734 | 14308 | 14.308 | -590 | 2.5
16735 | 14421 | 14.421 | -991 | 1.8
16736 | 14398 | 14.398 | -345 | 0.55
16737 | 14398 | 14.398 | -763 | 1.55
16738 | 14289 | 14.289 | 672 | 0.6
16739 | 14245 | 14.245 | 159 | 3.25
16740 | 14542 | 14.542 | -338 | 3.3
16741 | 14163 | 14.163 | 556 | 0.3
16742 | 14285 | 14.285 | 940 | 1.9
16743 | 14420 | 14.42 | -523 | 2.05
16744 | 14373 | 14.373 | 213 | 0.95
16745 | 14435 | 14.435 | -640 | 1
16746 | 14408 | 14.408 | 582 | 4.75
16747 | 14275 | 14.275 | -882 | 2.05
16748 | 14461 | 14.461 | -559 | 1.7
16749 | 14404 | 14.404 | -464 | 0.55
16750 | 14387 | 14.387 | -814 | 3.6
16751 | 14301 | 14.301 | -186 | 4.35
16752 | 14019 | 14.019 | 934 | 0.65
16753 | 13526 | 13.526 | -765 | 0.45
16754 | 14248 | 14.248 | -521 | 0.85
16755 | 14273 | 14.273 | -786 | 3.2
16756 | 14322 | 14.322 | 370 | 1.2
16757 | 14293 | 14.293 | -924 | 3.85
16758 | 14171 | 14.171 | 139 | 3.65
16759 | 13983 | 13.983 | -740 | 4.85
16760 | 14376 | 14.376 | -187 | 3.3
16761 | 14373 | 14.373 | -299 | 1.45
16762 | 14421 | 14.421 | 637 | 4.65
16763 | 14452 | 14.452 | 999 | 3.15
16764 | 14431 | 14.431 | 494 | 4.8
16765 | 14516 | 14.516 | 607 | 4.95
16766 | 14492 | 14.492 | 548 | 3.4
16767 | 14401 | 14.401 | 180 | 4.05
16768 | 14475 | 14.475 | 516 | 3.05
16769 | 14622 | 14.622 | -698 | 4.35
16770 | 14631 | 14.631 | 738 | 4
16771 | 14418 | 14.418 | 575 | 1.55
16772 | 14542 | 14.542 | 213 | 2.7
16773 | 14412 | 14.412 | -493 | 0
16774 | 14396 | 14.396 | 760 | 4.15
16775 | 14407 | 14.407 | 910 | 3.2
16776 | 14434 | 14.434 | -254 | 4.15
16777 | 14364 | 14.364 | -450 | 3.2
16778 | 14424 | 14.424 | 741 | 3.75
16779 | 14387 | 14.387 | -706 | 2.65
16780 | 13228 | 13.228 | -216 | 0.75
16781 | 13665 | 13.665 | 822 | 0.05
16782 | 14357 | 14.357 | -937 | 4
16783 | 14452 | 14.452 | -346 | 1.6
16784 | 14412 | 14.412 | 161 | 0.8
16785 | 14440 | 14.44 | -218 | 4.5
16786 | 14448 | 14.448 | 0 | 2.65
16787 | 14538 | 14.538 | 747 | 1
16788 | 14431 | 14.431 | 441 | 0.95
16789 | 14438 | 14.438 | -1000 | 4.55
16790 | 14482 | 14.482 | 501 | 3.45
16791 | 14366 | 14.366 | 182 | 0.65
16792 | 14459 | 14.459 | -659 | 4.25
16793 | 14459 | 14.459 | -268 | 2
16794 | 14524 | 14.524 | -367 | 0.8
16795 | 14351 | 14.351 | 619 | 2.95
16796 | 14480 | 14.48 | -79 | 3.8
16797 | 14454 | 14.454 | -568 | 2.5
16798 | 14566 | 14.566 | 390 | 2.45
16799 | 14524 | 14.524 | -604 | 1.3
16800 | 14433 | 14.433 | -434 | 3.55
16801 | 14405 | 14.405 | 862 | 3.35
16802 | 14395 | 14.395 | -283 | 3.1
16803 | 14062 | 14.062 | -89 | 3
16804 | 13999 | 13.999 | -479 | 0.05
16805 | 14136 | 14.136 | -658 | 0.45
16806 | 14411 | 14.411 | -120 | 1.3
16807 | 14409 | 14.409 | 123 | 0.45
16808 | 14424 | 14.424 | 704 | 3.9
16809 | 14393 | 14.393 | -992 | 3.4
16810 | 14399 | 14.399 | -780 | 2.7
16811 | 14350 | 14.35 | 958 | 1.65
16812 | 14397 | 14.397 | -150 | 2.85
16813 | 14330 | 14.33 | 659 | 0.75
16814 | 14536 | 14.536 | 952 | 0.5
16815 | 14518 | 14.518 | -386 | 4.35
16816 | 14415 | 14.415 | -919 | 4.55
16817 | 14533 | 14.533 | -511 | 3.8
16818 | 14504 | 14.504 | 932 | 0.55
16819 | 14423 | 14.423 | 856 | 4.75
16820 | 14523 | 14.523 | -466 | 4.45
16821 | 14311 | 14.311 | 216 | 2.05
16822 | 14554 | 14.554 | 995 | 1.15
16823 | 14603 | 14.603 | 884 | 2.9
16824 | 14471 | 14.471 | -461 | 1.7
16825 | 14413 | 14.413 | -536 | 1.05
16826 | 14519 | 14.519 | -132 | 0.25
16827 | 14646 | 14.646 | 475 | 0.75
16828 | 14353 | 14.353 | -566 | 1.45
16829 | 14406 | 14.406 | -505 | 2.85
16830 | 14358 | 14.358 | 317 | 1.9
16831 | 14315 | 14.315 | -131 | 0.65
16832 | 14307 | 14.307 | 367 | 0.65
16833 | 14375 | 14.375 | 819 | 4.7
16834 | 14422 | 14.422 | -704 | 1.2
16835 | 14327 | 14.327 | -691 | 3.65
16836 | 14316 | 14.316 | 78 | 4.95
16837 | 14312 | 14.312 | 375 | 3.7
16838 | 14193 | 14.193 | -601 | 2.1
16839 | 14411 | 14.411 | 77 | 1.25
16840 | 14333 | 14.333 | -207 | 2.9
16841 | 14351 | 14.351 | -804 | 0.3
16842 | 14357 | 14.357 | 721 | 1.4
16843 | 14427 | 14.427 | 832 | 0.35
16844 | 14454 | 14.454 | 250 | 1.35
16845 | 14446 | 14.446 | 257 | 4.55
16846 | 14364 | 14.364 | 521 | 1.45
16847 | 14369 | 14.369 | 905 | 2.1
16848 | 14277 | 14.277 | -379 | 2.9
16849 | 14225 | 14.225 | 719 | 3.35
16850 | 14203 | 14.203 | -580 | 0.5
16851 | 14363 | 14.363 | -12 | 1.4
16852 | 14381 | 14.381 | 473 | 0.75
16853 | 14484 | 14.484 | -717 | 3.75
16854 | 14377 | 14.377 | 611 | 2.95
16855 | 14470 | 14.47 | 55 | 1.15
16856 | 14342 | 14.342 | -625 | 3
16857 | 14520 | 14.52 | 22 | 3
16858 | 14463 | 14.463 | 73 | 0.1
16859 | 14426 | 14.426 | 483 | 3.1
16860 | 14369 | 14.369 | -187 | 3.6
16861 | 14365 | 14.365 | 663 | 0.75
16862 | 14470 | 14.47 | -521 | 3.55
16863 | 14428 | 14.428 | -697 | 0.05
16864 | 14332 | 14.332 | 76 | 2.35
16865 | 14434 | 14.434 | -956 | 0.75
16866 | 14506 | 14.506 | -23 | 2.55
16867 | 14442 | 14.442 | -780 | 4.5
16868 | 14377 | 14.377 | 366 | 1.55
16869 | 14385 | 14.385 | 376 | 0.55
16870 | 14392 | 14.392 | -979 | 2
16871 | 14220 | 14.22 | 956 | 3.95
16872 | 14311 | 14.311 | 888 | 0.75
16873 | 14361 | 14.361 | 821 | 0.7
16874 | 14329 | 14.329 | -277 | 0.6
16875 | 14284 | 14.284 | 694 | 2.45
16876 | 14272 | 14.272 | -233 | 4.9
16877 | 14255 | 14.255 | -190 | 4.65
16878 | 14292 | 14.292 | -878 | 2.55
16879 | 14442 | 14.442 | 440 | 4.75
16880 | 14326 | 14.326 | 384 | 1
16881 | 14330 | 14.33 | -918 | 4.3
16882 | 14247 | 14.247 | -424 | 3.45
16883 | 14394 | 14.394 | 730 | 3.6
16884 | 14481 | 14.481 | -511 | 3.25
16885 | 14453 | 14.453 | 777 | 4.5
16886 | 14441 | 14.441 | 567 | 1.4
16887 | 14523 | 14.523 | 864 | 2
16888 | 14343 | 14.343 | 665 | 2.2
16889 | 14226 | 14.226 | 452 | 1.3
16890 | 14283 | 14.283 | 33 | 3.2
16891 | 12382 | 12.382 | -4 | 1.05
16892 | 11760 | 11.76 | 768 | 1.45
16893 | 12232 | 12.232 | 327 | 1
16894 | 12096 | 12.096 | 658 | 4.6
16895 | 12000 | 12 | -501 | 4.1
16896 | 11967 | 11.967 | 570 | 3.95
16897 | 11986 | 11.986 | 954 | 0.5
16898 | 11929 | 11.929 | 431 | 4.1
16899 | 11969 | 11.969 | -544 | 1.15
16900 | 12074 | 12.074 | 40 | 4.95
16901 | 11945 | 11.945 | 498 | 1.45
16902 | 12054 | 12.054 | -928 | 1.85
16903 | 11988 | 11.988 | -535 | 2.25
16904 | 11954 | 11.954 | 229 | 1.05
16905 | 11996 | 11.996 | -955 | 1.15
16906 | 12122 | 12.122 | 922 | 4.9
16907 | 11971 | 11.971 | -557 | 0.4
16908 | 11980 | 11.98 | -268 | 3.75
16909 | 11930 | 11.93 | 726 | 0.3
16910 | 12075 | 12.075 | -770 | 1.5
16911 | 12107 | 12.107 | -758 | 1.45
16912 | 11976 | 11.976 | 698 | 2.05
16913 | 11725 | 11.725 | -78 | 0.25
16914 | 11867 | 11.867 | 979 | 1.8
16915 | 11898 | 11.898 | -111 | 4.6
16916 | 11709 | 11.709 | -881 | 1
16917 | 11768 | 11.768 | 883 | 2.25
16918 | 11888 | 11.888 | -248 | 0.75
16919 | 11843 | 11.843 | -882 | 0.05
16920 | 11614 | 11.614 | -931 | 1.55
16921 | 11188 | 11.188 | -149 | 3
16922 | 10805 | 10.805 | 374 | 3.5
16923 | 10612 | 10.612 | 30 | 3.95
16924 | 11128 | 11.128 | 111 | 0.2
16925 | 12091 | 12.091 | -63 | 2.3
16926 | 12395 | 12.395 | -23 | 1.95
16927 | 12542 | 12.542 | 477 | 4.8
16928 | 13710 | 13.71 | 608 | 3.55
16929 | 14291 | 14.291 | -595 | 0.25
16930 | 14108 | 14.108 | 748 | 3.8
16931 | 14288 | 14.288 | -392 | 4.7
16932 | 14398 | 14.398 | -589 | 4.6
16933 | 14295 | 14.295 | -318 | 4.95
16934 | 14355 | 14.355 | 583 | 3
16935 | 14367 | 14.367 | -768 | 3.1
16936 | 14391 | 14.391 | 586 | 1.35
16937 | 14357 | 14.357 | -950 | 0.25
16938 | 14411 | 14.411 | -442 | 4.45
16939 | 14485 | 14.485 | -352 | 4.5
16940 | 14377 | 14.377 | 724 | 2
16941 | 14476 | 14.476 | 145 | 0.25
16942 | 14478 | 14.478 | 243 | 0.35
16943 | 14330 | 14.33 | 691 | 3.9
16944 | 14507 | 14.507 | -780 | 3.15
16945 | 14406 | 14.406 | -499 | 3.5
16946 | 14381 | 14.381 | 858 | 2.75
16947 | 14536 | 14.536 | 574 | 3.8
16948 | 14405 | 14.405 | -418 | 3.1
16949 | 14452 | 14.452 | 396 | 1.25
16950 | 14457 | 14.457 | -707 | 3
16951 | 14537 | 14.537 | 874 | 0.65
16952 | 14394 | 14.394 | -25 | 3.75
16953 | 14607 | 14.607 | -232 | 1.75
16954 | 14489 | 14.489 | 554 | 0.7
16955 | 14405 | 14.405 | -902 | 1.55
16956 | 14393 | 14.393 | 660 | 2.25
16957 | 14300 | 14.3 | -537 | 0.2
16958 | 14415 | 14.415 | -83 | 1.4
16959 | 14229 | 14.229 | -984 | 3.4
16960 | 14238 | 14.238 | 254 | 4.55
16961 | 14348 | 14.348 | 716 | 2.8
16962 | 14387 | 14.387 | 117 | 1.65
16963 | 14036 | 14.036 | -479 | 0.75
16964 | 13667 | 13.667 | 282 | 2.05
16965 | 13856 | 13.856 | 692 | 0.15
16966 | 14321 | 14.321 | -121 | 2.55
16967 | 14249 | 14.249 | 153 | 5
16968 | 14171 | 14.171 | -715 | 1
16969 | 13713 | 13.713 | 179 | 2.25
16970 | 13433 | 13.433 | 306 | 2.1
16971 | 13734 | 13.734 | 368 | 2.35
16972 | 13691 | 13.691 | -688 | 3
16973 | 13464 | 13.464 | -149 | 3.4
16974 | 13689 | 13.689 | -888 | 2.7
16975 | 14224 | 14.224 | -445 | 4.4
16976 | 14135 | 14.135 | -771 | 4.95
16977 | 14346 | 14.346 | -812 | 0.45
16978 | 14343 | 14.343 | 830 | 1.5
16979 | 14171 | 14.171 | -505 | 3
16980 | 14281 | 14.281 | -175 | 3.35
16981 | 14366 | 14.366 | -909 | 1.85
16982 | 14321 | 14.321 | 760 | 4.8
16983 | 14309 | 14.309 | 395 | 2.25
16984 | 14431 | 14.431 | 177 | 1.3
16985 | 14270 | 14.27 | -851 | 1.8
16986 | 14323 | 14.323 | -74 | 2.45
16987 | 14442 | 14.442 | 459 | 4.85
16988 | 14507 | 14.507 | 453 | 0.95
16989 | 14394 | 14.394 | -753 | 2.45
16990 | 14415 | 14.415 | 32 | 3.85
16991 | 14412 | 14.412 | -57 | 5
16992 | 14128 | 14.128 | -833 | 4.15
16993 | 13507 | 13.507 | -970 | 1.8
16994 | 13866 | 13.866 | 918 | 3.5
16995 | 13805 | 13.805 | -536 | 4.35
16996 | 13939 | 13.939 | 693 | 4.55
16997 | 13251 | 13.251 | -328 | 2.85
16998 | 14350 | 14.35 | 569 | 4.95
16999 | 14390 | 14.39 | -813 | 4.95
17000 | 14437 | 14.437 | -690 | 0.95
17001 | 14431 | 14.431 | 363 | 0.45
17002 | 14334 | 14.334 | 211 | 3.6
17003 | 14329 | 14.329 | 829 | 4.95
17004 | 14278 | 14.278 | 429 | 3.35
17005 | 14480 | 14.48 | 285 | 1.4
17006 | 14473 | 14.473 | 692 | 0.9
17007 | 14245 | 14.245 | 148 | 1.95
17008 | 14336 | 14.336 | 67 | 2.9
17009 | 14433 | 14.433 | 72 | 0.85
17010 | 14448 | 14.448 | 161 | 1.25
17011 | 14379 | 14.379 | -760 | 1.2
17012 | 14500 | 14.5 | -783 | 4.95
17013 | 14435 | 14.435 | 401 | 1.75
17014 | 14388 | 14.388 | -82 | 2.5
17015 | 14316 | 14.316 | -248 | 0.85
17016 | 14357 | 14.357 | 689 | 4.05
17017 | 14243 | 14.243 | -38 | 4.1
17018 | 14317 | 14.317 | 655 | 2.2
17019 | 14348 | 14.348 | -54 | 4.1
17020 | 14295 | 14.295 | 841 | 1.15
17021 | 14500 | 14.5 | -804 | 3
17022 | 14449 | 14.449 | 433 | 2.55
17023 | 14225 | 14.225 | -425 | 3.5
17024 | 14242 | 14.242 | -745 | 3.85
17025 | 14384 | 14.384 | -969 | 4.4
17026 | 14347 | 14.347 | -974 | 1.6
17027 | 14202 | 14.202 | -805 | 5
17028 | 14417 | 14.417 | 30 | 2.1
17029 | 14242 | 14.242 | -177 | 2.55
17030 | 14470 | 14.47 | 589 | 0.75
17031 | 14291 | 14.291 | -257 | 1.6
17032 | 14455 | 14.455 | 347 | 0.05
17033 | 14413 | 14.413 | -969 | 3.45
17034 | 14378 | 14.378 | -167 | 3.3
17035 | 14447 | 14.447 | -215 | 4
17036 | 14259 | 14.259 | 986 | 3.05
17037 | 14363 | 14.363 | -297 | 0.95
17038 | 14158 | 14.158 | 609 | 1.9
17039 | 14485 | 14.485 | -213 | 3.1
17040 | 13954 | 13.954 | 71 | 3.1
17041 | 13334 | 13.334 | 430 | 1.2
17042 | 14242 | 14.242 | -39 | 0.85
17043 | 14426 | 14.426 | -45 | 1.55
17044 | 14275 | 14.275 | -784 | 1.85
17045 | 14190 | 14.19 | -410 | 3.25
17046 | 14229 | 14.229 | -30 | 4.9
17047 | 14588 | 14.588 | 593 | 0.05
17048 | 14440 | 14.44 | 796 | 3.4
17049 | 14398 | 14.398 | -281 | 3.1
17050 | 14323 | 14.323 | 791 | 1.8
17051 | 14438 | 14.438 | 774 | 2.2
17052 | 14381 | 14.381 | -455 | 3.1
17053 | 14410 | 14.41 | -692 | 3.85
17054 | 14288 | 14.288 | -968 | 0.6
17055 | 14522 | 14.522 | -94 | 0.1
17056 | 14397 | 14.397 | 970 | 0.4
17057 | 14293 | 14.293 | 622 | 0.8
17058 | 14337 | 14.337 | 50 | 3.4
17059 | 14357 | 14.357 | -403 | 1.25
17060 | 14429 | 14.429 | 209 | 2.1
17061 | 14290 | 14.29 | -857 | 1.85
17062 | 14356 | 14.356 | 167 | 0.1
17063 | 14291 | 14.291 | 532 | 2.4
17064 | 14303 | 14.303 | 923 | 1.5
17065 | 14233 | 14.233 | 858 | 1.85
17066 | 14404 | 14.404 | 413 | 3.5
17067 | 14431 | 14.431 | -95 | 2.1
17068 | 14246 | 14.246 | -471 | 4.5
17069 | 14300 | 14.3 | 821 | 2.8
17070 | 14404 | 14.404 | 752 | 3.3
17071 | 14318 | 14.318 | 869 | 0.75
17072 | 14334 | 14.334 | 389 | 1.85
17073 | 14427 | 14.427 | -992 | 3.35
17074 | 14355 | 14.355 | -494 | 5
17075 | 14397 | 14.397 | -540 | 3.35
17076 | 14261 | 14.261 | -605 | 2.75
17077 | 14415 | 14.415 | 241 | 4.55
17078 | 14297 | 14.297 | 400 | 4.2
17079 | 14361 | 14.361 | 332 | 2.6
17080 | 14348 | 14.348 | -795 | 4
17081 | 14292 | 14.292 | -222 | 0.6
17082 | 14303 | 14.303 | -461 | 2.95
17083 | 14385 | 14.385 | -16 | 1.05
17084 | 14498 | 14.498 | 117 | 2.95
17085 | 14276 | 14.276 | -429 | 4.35
17086 | 14433 | 14.433 | 103 | 2.95
17087 | 14381 | 14.381 | 423 | 1.6
17088 | 14268 | 14.268 | 720 | 1.75
17089 | 13969 | 13.969 | -655 | 0.5
17090 | 13639 | 13.639 | 731 | 3.85
17091 | 13649 | 13.649 | -834 | 1
17092 | 13735 | 13.735 | -94 | 2.35
17093 | 13647 | 13.647 | 161 | 1.35
17094 | 13877 | 13.877 | 646 | 4.25
17095 | 14366 | 14.366 | -655 | 0.7
17096 | 14368 | 14.368 | -146 | 2.45
17097 | 14408 | 14.408 | 575 | 2
17098 | 14527 | 14.527 | 873 | 4.9
17099 | 14442 | 14.442 | 765 | 3.45
17100 | 14376 | 14.376 | -794 | 1.15
17101 | 14439 | 14.439 | 929 | 5
17102 | 14367 | 14.367 | 464 | 3.6
17103 | 14387 | 14.387 | -892 | 0.7
17104 | 14488 | 14.488 | 0 | 3
17105 | 14338 | 14.338 | 717 | 2.9
17106 | 14362 | 14.362 | 376 | 1
17107 | 14297 | 14.297 | 845 | 2.5
17108 | 14383 | 14.383 | -798 | 4.9
17109 | 14411 | 14.411 | 788 | 0.4
17110 | 14343 | 14.343 | -907 | 0.6
17111 | 14174 | 14.174 | 403 | 4
17112 | 14412 | 14.412 | 241 | 0.65
17113 | 14292 | 14.292 | -887 | 2.2
17114 | 14372 | 14.372 | -661 | 2.4
17115 | 14127 | 14.127 | 96 | 0.65
17116 | 14345 | 14.345 | -119 | 2.75
17117 | 14327 | 14.327 | -485 | 3.25
17118 | 14279 | 14.279 | -991 | 3.25
17119 | 14288 | 14.288 | 28 | 2.95
17120 | 14202 | 14.202 | 18 | 0.6
17121 | 14444 | 14.444 | 586 | 0.25
17122 | 14212 | 14.212 | -488 | 1.65
17123 | 14387 | 14.387 | -440 | 4.45
17124 | 14382 | 14.382 | -536 | 4.3
17125 | 14373 | 14.373 | -682 | 4.25
17126 | 14441 | 14.441 | -607 | 3.3
17127 | 14356 | 14.356 | 550 | 1.4
17128 | 14513 | 14.513 | 683 | 4
17129 | 14403 | 14.403 | 795 | 1.7
17130 | 14442 | 14.442 | -784 | 1.35
17131 | 14269 | 14.269 | -981 | 0.7
17132 | 14564 | 14.564 | 582 | 2.1
17133 | 14410 | 14.41 | 160 | 0.8
17134 | 14431 | 14.431 | -603 | 1.95
17135 | 14286 | 14.286 | -542 | 2.15
17136 | 13702 | 13.702 | -824 | 0.15
17137 | 13905 | 13.905 | -726 | 1.7
17138 | 14446 | 14.446 | -689 | 2.25
17139 | 14575 | 14.575 | 205 | 1.65
17140 | 14452 | 14.452 | -754 | 2.55
17141 | 14510 | 14.51 | 451 | 0.5
17142 | 14461 | 14.461 | -798 | 0.75
17143 | 14385 | 14.385 | 989 | 2.25
17144 | 14413 | 14.413 | -180 | 1.8
17145 | 14427 | 14.427 | 53 | 4.75
17146 | 14428 | 14.428 | -742 | 1.05
17147 | 14326 | 14.326 | -974 | 1.3
17148 | 14422 | 14.422 | -822 | 4.2
17149 | 14381 | 14.381 | 2 | 0.45
17150 | 14455 | 14.455 | 881 | 4.7
17151 | 14439 | 14.439 | -136 | 4.8
17152 | 14375 | 14.375 | -246 | 2.5
17153 | 14496 | 14.496 | -115 | 4.6
17154 | 14420 | 14.42 | 644 | 0.6
17155 | 14470 | 14.47 | -490 | 3.6
17156 | 14341 | 14.341 | 97 | 4.7
17157 | 14444 | 14.444 | 568 | 0.85
17158 | 14552 | 14.552 | -428 | 3.45
17159 | 14352 | 14.352 | -650 | 3.25
17160 | 14327 | 14.327 | 984 | 0.2
17161 | 14276 | 14.276 | 738 | 3
17162 | 14448 | 14.448 | -523 | 0.6
17163 | 14330 | 14.33 | 831 | 1.6
17164 | 14457 | 14.457 | 595 | 1.05
17165 | 14367 | 14.367 | -88 | 3.4
17166 | 14330 | 14.33 | -386 | 0.8
17167 | 14336 | 14.336 | 825 | 2.65
17168 | 14380 | 14.38 | -133 | 0.4
17169 | 14356 | 14.356 | 62 | 2.6
17170 | 14418 | 14.418 | 783 | 0.85
17171 | 14427 | 14.427 | 507 | 4.15
17172 | 11845 | 11.845 | -613 | 4.2
17173 | 11035 | 11.035 | -165 | 1.55
17174 | 13271 | 13.271 | -683 | 3.4
17175 | 14368 | 14.368 | -846 | 0.45
17176 | 14407 | 14.407 | -212 | 2.8
17177 | 14385 | 14.385 | -983 | 0
17178 | 14462 | 14.462 | -874 | 4.95
17179 | 14589 | 14.589 | 310 | 1.45
17180 | 14412 | 14.412 | 156 | 2.9
17181 | 14446 | 14.446 | 118 | 2.1
17182 | 14455 | 14.455 | -164 | 0
17183 | 14458 | 14.458 | -507 | 3.8
17184 | 13903 | 13.903 | -415 | 1.35
17185 | 13751 | 13.751 | -924 | 4.6
17186 | 13870 | 13.87 | 551 | 0.35
17187 | 13965 | 13.965 | -252 | 4.75
17188 | 13486 | 13.486 | 9 | 4.65
17189 | 13769 | 13.769 | 221 | 1.45
17190 | 14407 | 14.407 | 384 | 1.9
17191 | 14604 | 14.604 | 891 | 1.75
17192 | 14409 | 14.409 | -767 | 2.55
17193 | 14507 | 14.507 | -285 | 4.95
17194 | 14477 | 14.477 | 466 | 3.9
17195 | 14521 | 14.521 | 597 | 1.05
17196 | 14435 | 14.435 | 540 | 3.15
17197 | 14452 | 14.452 | 807 | 3.4
17198 | 14364 | 14.364 | 977 | 4.6
17199 | 14433 | 14.433 | 702 | 1.35
17200 | 14431 | 14.431 | 97 | 3.9
17201 | 14577 | 14.577 | 869 | 1.85
17202 | 14451 | 14.451 | -829 | 4.4
17203 | 14450 | 14.45 | 8 | 4
17204 | 14357 | 14.357 | -559 | 4.55
17205 | 14488 | 14.488 | -405 | 3.1
17206 | 14414 | 14.414 | 562 | 1.75
17207 | 14157 | 14.157 | -541 | 1.1
17208 | 14400 | 14.4 | -59 | 2.5
17209 | 14302 | 14.302 | 840 | 3.95
17210 | 14254 | 14.254 | -143 | 1.95
17211 | 14180 | 14.18 | 247 | 0.05
17212 | 14234 | 14.234 | -164 | 3.65
17213 | 14355 | 14.355 | 343 | 2.35
17214 | 14342 | 14.342 | -895 | 3.8
17215 | 14427 | 14.427 | -389 | 4
17216 | 14383 | 14.383 | 887 | 4.7
17217 | 14360 | 14.36 | -770 | 2.7
17218 | 14377 | 14.377 | 882 | 4.15
17219 | 14363 | 14.363 | 601 | 4.95
17220 | 14486 | 14.486 | -393 | 4.9
17221 | 14375 | 14.375 | 549 | 0.3
17222 | 14342 | 14.342 | 246 | 2.6
17223 | 14501 | 14.501 | 550 | 2.5
17224 | 14387 | 14.387 | -677 | 2.25
17225 | 14422 | 14.422 | 530 | 1.3
17226 | 14244 | 14.244 | 611 | 4.8
17227 | 14441 | 14.441 | -581 | 3
17228 | 14380 | 14.38 | -243 | 2.85
17229 | 14455 | 14.455 | -514 | 1.15
17230 | 14686 | 14.686 | -798 | 4.3
17231 | 13721 | 13.721 | -598 | 4.25
17232 | 13765 | 13.765 | -372 | 0.35
17233 | 13957 | 13.957 | 161 | 2.45
17234 | 14014 | 14.014 | -302 | 3
17235 | 13737 | 13.737 | -136 | 4.9
17236 | 13898 | 13.898 | 384 | 4.95
17237 | 14582 | 14.582 | -958 | 2.8
17238 | 14252 | 14.252 | -521 | 2.55
17239 | 14590 | 14.59 | 800 | 3.5
17240 | 14505 | 14.505 | -655 | 1.65
17241 | 14505 | 14.505 | 868 | 4.4
17242 | 14391 | 14.391 | 89 | 4.8
17243 | 14550 | 14.55 | 681 | 3.1
17244 | 14353 | 14.353 | -194 | 4.05
17245 | 14346 | 14.346 | -27 | 1
17246 | 14526 | 14.526 | 7 | 2.85
17247 | 14458 | 14.458 | -214 | 1.6
17248 | 14586 | 14.586 | 931 | 3.4
17249 | 14440 | 14.44 | 155 | 4
17250 | 14482 | 14.482 | 617 | 2.35
17251 | 14426 | 14.426 | -274 | 4.3
17252 | 14277 | 14.277 | -780 | 4.65
17253 | 14539 | 14.539 | -671 | 2.8
17254 | 14275 | 14.275 | 81 | 2.45
17255 | 14475 | 14.475 | -735 | 0.1
17256 | 14331 | 14.331 | 295 | 4.6
17257 | 14380 | 14.38 | -469 | 4.55
17258 | 14319 | 14.319 | 589 | 0.15
17259 | 14267 | 14.267 | 140 | 4.7
17260 | 13902 | 13.902 | 907 | 2.3
17261 | 14226 | 14.226 | -369 | 3.25
17262 | 14364 | 14.364 | -875 | 1.45
17263 | 14357 | 14.357 | 146 | 0
17264 | 14385 | 14.385 | -716 | 1.6
17265 | 14455 | 14.455 | 483 | 2.75
17266 | 14517 | 14.517 | -429 | 5
17267 | 14441 | 14.441 | 815 | 3.9
17268 | 14400 | 14.4 | 387 | 0.2
17269 | 14460 | 14.46 | -786 | 0.45
17270 | 14543 | 14.543 | 291 | 1.95
17271 | 14461 | 14.461 | -864 | 0.3
17272 | 14382 | 14.382 | 776 | 4.9
17273 | 14539 | 14.539 | -623 | 1.75
17274 | 14624 | 14.624 | -152 | 3.2
17275 | 14517 | 14.517 | 564 | 4.9
17276 | 14549 | 14.549 | 337 | 1.5
17277 | 14553 | 14.553 | 895 | 1.55
17278 | 14508 | 14.508 | 776 | 3.3
17279 | 14300 | 14.3 | -73 | 3.9
17280 | 13825 | 13.825 | -348 | 1.8
17281 | 13848 | 13.848 | -635 | 0.25
17282 | 14310 | 14.31 | -546 | 1.6
17283 | 14408 | 14.408 | -120 | 4
17284 | 14461 | 14.461 | 300 | 0.1
17285 | 14462 | 14.462 | -516 | 4.3
17286 | 14567 | 14.567 | -643 | 1.5
17287 | 14499 | 14.499 | 544 | 0.2
17288 | 14407 | 14.407 | -403 | 3.6
17289 | 14447 | 14.447 | 218 | 3.55
17290 | 14462 | 14.462 | -653 | 4.1
17291 | 14456 | 14.456 | 615 | 0.55
17292 | 14628 | 14.628 | -244 | 1.75
17293 | 14475 | 14.475 | 41 | 0.4
17294 | 14530 | 14.53 | 652 | 4.3
17295 | 14467 | 14.467 | 905 | 2.05
17296 | 14345 | 14.345 | -213 | 1.65
17297 | 14470 | 14.47 | -688 | 2.2
17298 | 14508 | 14.508 | -812 | 1
17299 | 14449 | 14.449 | -97 | 4.2
17300 | 14377 | 14.377 | -914 | 3.95
17301 | 14507 | 14.507 | -124 | 0.45
17302 | 14270 | 14.27 | 394 | 2.8
17303 | 14468 | 14.468 | 852 | 0.7
17304 | 14350 | 14.35 | -593 | 3.15
17305 | 14493 | 14.493 | 159 | 1.85
17306 | 14457 | 14.457 | 645 | 1.5
17307 | 14406 | 14.406 | -405 | 3.8
17308 | 14334 | 14.334 | 607 | 1
17309 | 14404 | 14.404 | 542 | 3.05
17310 | 14462 | 14.462 | 747 | 1
17311 | 14250 | 14.25 | -59 | 3.2
17312 | 14405 | 14.405 | 844 | 2.1
17313 | 14337 | 14.337 | -90 | 5
17314 | 14405 | 14.405 | -776 | 3.95
17315 | 14268 | 14.268 | -673 | 2
17316 | 14402 | 14.402 | 253 | 4.5
17317 | 14412 | 14.412 | -294 | 0.3
17318 | 14379 | 14.379 | 400 | 3.6
17319 | 14618 | 14.618 | -631 | 0.55
17320 | 14682 | 14.682 | 971 | 4.15
17321 | 14218 | 14.218 | -302 | 3.65
17322 | 14461 | 14.461 | 322 | 2.2
17323 | 14545 | 14.545 | -118 | 0.75
17324 | 14438 | 14.438 | 985 | 0.35
17325 | 14381 | 14.381 | -720 | 3
17326 | 14390 | 14.39 | 200 | 2.4
17327 | 14296 | 14.296 | 553 | 0.2
17328 | 13755 | 13.755 | 599 | 0.95
17329 | 13726 | 13.726 | -833 | 0.05
17330 | 13906 | 13.906 | 804 | 2.6
17331 | 13849 | 13.849 | 962 | 3.4
17332 | 13626 | 13.626 | -161 | 2.1
17333 | 13646 | 13.646 | -88 | 3.6
17334 | 14477 | 14.477 | -738 | 2.05
17335 | 14344 | 14.344 | 183 | 0.95
17336 | 14418 | 14.418 | -461 | 0.45
17337 | 14539 | 14.539 | 1 | 2.35
17338 | 14493 | 14.493 | -597 | 3.85
17339 | 14478 | 14.478 | 650 | 1.45
17340 | 14513 | 14.513 | -232 | 1.75
17341 | 14568 | 14.568 | -315 | 4
17342 | 14464 | 14.464 | 441 | 2.15
17343 | 14460 | 14.46 | -129 | 2.7
17344 | 14426 | 14.426 | 585 | 1.05
17345 | 14533 | 14.533 | -619 | 1.15
17346 | 14447 | 14.447 | -248 | 2.5
17347 | 14317 | 14.317 | -237 | 1.25
17348 | 14474 | 14.474 | -10 | 1
17349 | 14476 | 14.476 | -331 | 3.4
17350 | 14441 | 14.441 | 781 | 0.85
17351 | 14355 | 14.355 | 220 | 4.65
17352 | 14328 | 14.328 | -407 | 3.3
17353 | 14566 | 14.566 | 938 | 2.2
17354 | 14351 | 14.351 | -659 | 3.1
17355 | 14377 | 14.377 | 422 | 4.25
17356 | 14440 | 14.44 | -432 | 4.75
17357 | 14434 | 14.434 | -473 | 0.9
17358 | 14283 | 14.283 | -129 | 2.85
17359 | 14361 | 14.361 | -579 | 0.05
17360 | 14401 | 14.401 | -952 | 1.3
17361 | 14334 | 14.334 | 905 | 0
17362 | 14284 | 14.284 | -329 | 0.35
17363 | 14302 | 14.302 | 798 | 1.4
17364 | 14287 | 14.287 | 725 | 2.75
17365 | 14502 | 14.502 | -119 | 4.05
17366 | 14185 | 14.185 | -495 | 0.05
17367 | 14329 | 14.329 | 253 | 1.95
17368 | 14491 | 14.491 | -230 | 4.25
17369 | 14384 | 14.384 | -869 | 1.9
17370 | 14388 | 14.388 | 24 | 3.65
17371 | 14368 | 14.368 | -290 | 2.3
17372 | 14379 | 14.379 | -668 | 1.25
17373 | 14460 | 14.46 | 980 | 3.7
17374 | 14280 | 14.28 | -250 | 1.55
17375 | 14362 | 14.362 | -288 | 1.45
17376 | 13769 | 13.769 | 243 | 1.35
17377 | 13778 | 13.778 | 994 | 3.85
17378 | 14386 | 14.386 | -99 | 1.55
17379 | 14335 | 14.335 | -859 | 0.6
17380 | 14311 | 14.311 | 700 | 3.25
17381 | 14291 | 14.291 | 44 | 3.6
17382 | 14402 | 14.402 | 827 | 1.4
17383 | 14365 | 14.365 | -960 | 3.15
17384 | 14374 | 14.374 | -339 | 1.5
17385 | 14481 | 14.481 | 442 | 4.85
17386 | 14318 | 14.318 | -450 | 0.55
17387 | 14333 | 14.333 | 218 | 2.05
17388 | 14362 | 14.362 | -214 | 0.3
17389 | 14432 | 14.432 | 941 | 1.8
17390 | 14286 | 14.286 | -569 | 2.25
17391 | 14320 | 14.32 | -610 | 3.5
17392 | 14410 | 14.41 | 386 | 3.85
17393 | 14365 | 14.365 | 623 | 0.6
17394 | 14278 | 14.278 | -497 | 2.15
17395 | 14181 | 14.181 | 642 | 0.95
17396 | 14174 | 14.174 | 880 | 1
17397 | 14166 | 14.166 | 754 | 4.45
17398 | 14365 | 14.365 | 410 | 0
17399 | 14237 | 14.237 | 79 | 0.95
17400 | 14157 | 14.157 | -139 | 4.1
17401 | 13165 | 13.165 | 249 | 2.25
17402 | 8967 | 8.967 | -437 | 3.7
17403 | 9643 | 9.643 | 534 | 0
17404 | 11714 | 11.714 | 883 | 3.2
17405 | 13723 | 13.723 | 651 | 2.55
17406 | 14303 | 14.303 | 735 | 3.85
17407 | 14131 | 14.131 | 427 | 3.4
17408 | 14121 | 14.121 | -704 | 4.75
17409 | 14221 | 14.221 | -28 | 3.45
17410 | 14086 | 14.086 | -666 | 3.55
17411 | 14122 | 14.122 | 840 | 0.8
17412 | 14293 | 14.293 | 754 | 2.8
17413 | 14229 | 14.229 | 557 | 1.95
17414 | 14272 | 14.272 | -214 | 2.6
17415 | 14188 | 14.188 | -414 | 2.55
17416 | 14278 | 14.278 | 619 | 1.6
17417 | 14409 | 14.409 | -485 | 3.2
17418 | 14254 | 14.254 | 929 | 2.85
17419 | 14339 | 14.339 | 862 | 3.65
17420 | 14264 | 14.264 | 156 | 2
17421 | 14389 | 14.389 | -550 | 4.7
17422 | 14107 | 14.107 | -670 | 1.1
17423 | 14152 | 14.152 | -487 | 0.65
17424 | 13513 | 13.513 | 309 | 2.5
17425 | 13878 | 13.878 | -795 | 1.5
17426 | 13725 | 13.725 | -913 | 2.8
17427 | 13918 | 13.918 | -410 | 0
17428 | 13636 | 13.636 | 504 | 4.15
17429 | 13942 | 13.942 | -486 | 2.2
17430 | 14212 | 14.212 | 450 | 3.4
17431 | 14235 | 14.235 | 248 | 3.05
17432 | 14160 | 14.16 | -833 | 3.4
17433 | 14451 | 14.451 | 773 | 4.05
17434 | 14379 | 14.379 | -9 | 1.1
17435 | 14519 | 14.519 | 690 | 1.95
17436 | 14351 | 14.351 | -349 | 4.25
17437 | 14255 | 14.255 | 264 | 4.65
17438 | 14371 | 14.371 | 800 | 2.2
17439 | 14374 | 14.374 | -116 | 2.25
17440 | 14387 | 14.387 | 424 | 2.95
17441 | 14399 | 14.399 | -987 | 0
17442 | 14360 | 14.36 | -592 | 2.1
17443 | 14280 | 14.28 | 194 | 1
17444 | 14343 | 14.343 | 139 | 0.9
17445 | 14096 | 14.096 | -710 | 2.45
17446 | 14302 | 14.302 | -713 | 3.7
17447 | 14228 | 14.228 | 730 | 4.4
17448 | 13529 | 13.529 | -100 | 3.95
17449 | 13535 | 13.535 | -196 | 1.65
17450 | 14209 | 14.209 | 983 | 4
17451 | 14164 | 14.164 | 985 | 4.8
17452 | 14206 | 14.206 | -267 | 2.6
17453 | 14200 | 14.2 | 940 | 1.3
17454 | 14223 | 14.223 | -48 | 4.15
17455 | 14205 | 14.205 | -615 | 4.75
17456 | 14317 | 14.317 | -534 | 0.95
17457 | 14192 | 14.192 | -964 | 3.7
17458 | 14383 | 14.383 | -909 | 4.05
17459 | 14359 | 14.359 | -605 | 1.6
17460 | 14245 | 14.245 | 724 | 1.45
17461 | 14359 | 14.359 | -771 | 2.1
17462 | 14271 | 14.271 | -492 | 3
17463 | 14372 | 14.372 | -230 | 1.9
17464 | 14220 | 14.22 | -182 | 0.3
17465 | 14368 | 14.368 | 578 | 1.5
17466 | 14270 | 14.27 | -902 | 2.6
17467 | 14383 | 14.383 | -715 | 4.65
17468 | 14178 | 14.178 | -969 | 4.7
17469 | 14443 | 14.443 | 75 | 0.15
17470 | 14277 | 14.277 | 546 | 1.7
17471 | 14213 | 14.213 | -128 | 2.1
17472 | 13768 | 13.768 | -106 | 1.6
17473 | 13665 | 13.665 | -643 | 1.35
17474 | 14253 | 14.253 | 889 | 3.25
17475 | 14226 | 14.226 | 621 | 2.65
17476 | 14375 | 14.375 | 65 | 3.7
17477 | 14270 | 14.27 | 431 | 0.3
17478 | 14276 | 14.276 | 836 | 2.1
17479 | 14232 | 14.232 | 996 | 1.25
17480 | 14354 | 14.354 | 295 | 4.45
17481 | 14435 | 14.435 | 942 | 1
17482 | 14252 | 14.252 | -108 | 3.05
17483 | 14369 | 14.369 | -316 | 4.05
17484 | 14350 | 14.35 | 374 | 0.2
17485 | 14237 | 14.237 | 78 | 4.65
17486 | 14199 | 14.199 | -517 | 1.2
17487 | 14261 | 14.261 | 78 | 2.4
17488 | 14359 | 14.359 | -610 | 4.6
17489 | 14353 | 14.353 | -988 | 2.85
17490 | 14332 | 14.332 | -301 | 2.7
17491 | 14335 | 14.335 | -947 | 0.95
17492 | 14371 | 14.371 | 561 | 4.35
17493 | 14235 | 14.235 | 179 | 5
17494 | 14218 | 14.218 | -307 | 0.2
17495 | 14414 | 14.414 | 778 | 0.65
17496 | 12539 | 12.539 | -593 | 5
17497 | 14146 | 14.146 | -998 | 4.35
17498 | 14346 | 14.346 | -713 | 0.75
17499 | 14077 | 14.077 | 186 | 4.95
17500 | 13645 | 13.645 | 611 | 2.45
17501 | 14074 | 14.074 | 108 | 3.05
17502 | 14231 | 14.231 | -593 | 1.75
17503 | 14551 | 14.551 | -378 | 1
17504 | 14501 | 14.501 | 374 | 3.8
17505 | 14404 | 14.404 | 548 | 4.8
17506 | 14367 | 14.367 | 292 | 0.15
17507 | 14413 | 14.413 | 825 | 2.1
17508 | 14403 | 14.403 | -488 | 1.05
17509 | 14388 | 14.388 | 339 | 2.7
17510 | 14181 | 14.181 | -311 | 1
17511 | 14376 | 14.376 | -94 | 4.2
17512 | 14286 | 14.286 | -248 | 2.45
17513 | 14269 | 14.269 | -860 | 1.3
17514 | 14533 | 14.533 | 939 | 0.45
17515 | 14339 | 14.339 | 656 | 1.4
17516 | 14429 | 14.429 | 958 | 4.45
17517 | 14356 | 14.356 | -722 | 1.65
17518 | 14471 | 14.471 | -209 | 0.9
17519 | 14298 | 14.298 | -743 | 1.1
17520 | 14055 | 14.055 | -300 | 3.45

## IntermediateResults (hidden)
Capacity Outage Probability Table
State No. | Capacity | Ind. probability | Cum. probability | ENS | EENS
1 | 134.665 | 0.57322 | 1 | 0.24812 | 0.14223
2 | 133.9129 | 0.057311 | 0.42678 | 2.6124 | 0.14972
3 | 133.1609 | 0.0030919 | 0.36947 | 7.4772 | 0.023119
4 | 132.4088 | 0.00033128 | 0.36637 | 14.8426 | 0.004917
5 | 130.1527 | 0.00022085 | 0.36604 | 51.9422 | 0.011472
6 | 128.6486 | 0.00033128 | 0.36582 | 89.1781 | 0.029543
7 | 127.8965 | 0.00055213 | 0.36549 | 111.5469 | 0.061589
8 | 121.8801 | 0.00011043 | 0.36494 | 380.5179 | 0.042019
9 | 120.376 | 0.00088341 | 0.36483 | 472.7663 | 0.41765
10 | 94.665 | 0.27995 | 0.36394 | 17625.624 | 4934.2283
11 | 93.9129 | 0.027989 | 0.083998 | 18918.3951 | 529.5115
12 | 93.1609 | 0.00151 | 0.056008 | 20259.5365 | 30.5922
13 | 92.4088 | 0.00016179 | 0.054498 | 21649.0483 | 3.5025
14 | 90.1527 | 0.00010786 | 0.054337 | 26107.806 | 2.8159
15 | 88.6486 | 0.00016179 | 0.054229 | 29322.163 | 4.744
16 | 87.8965 | 0.00026965 | 0.054067 | 31001.8971 | 8.3595
17 | 81.8801 | 5.3929e-05 | 0.053797 | 46181.1028 | 2.4905
18 | 80.376 | 0.00043143 | 0.053743 | 50459.608 | 21.77
19 | 54.665 | 0.045573 | 0.053312 | 150318.4301 | 6850.4098
20 | 53.9129 | 0.0045564 | 0.0077393 | 153603.3845 | 699.8765
21 | 53.1609 | 0.00024582 | 0.003183 | 156888.3389 | 38.5658
22 | 52.4088 | 2.6337e-05 | 0.0029371 | 160173.2933 | 4.2186
23 | 50.1527 | 1.7558e-05 | 0.0029108 | 170028.1565 | 2.9854
24 | 48.6486 | 2.6337e-05 | 0.0028932 | 176598.0653 | 4.6512
25 | 47.8965 | 4.3896e-05 | 0.0028669 | 179883.0197 | 7.8961
26 | 41.8801 | 8.7792e-06 | 0.002823 | 206162.6549 | 1.8099
27 | 40.376 | 7.0233e-05 | 0.0028142 | 212732.5637 | 14.9409
28 | 14.665 | 0.0024729 | 0.002744 | 325038.4301 | 803.7988
29 | 13.9129 | 0.00024725 | 0.00027107 | 328323.3845 | 81.1766
30 | 13.1609 | 1.3339e-05 | 2.3819e-05 | 331608.3389 | 4.4233
31 | 12.4088 | 1.4292e-06 | 1.0481e-05 | 334893.2933 | 0.47862
32 | 10.1527 | 9.5278e-07 | 9.0514e-06 | 344748.1565 | 0.32847
33 | 8.6486 | 1.4292e-06 | 8.0986e-06 | 351318.0653 | 0.50209
34 | 7.8965 | 2.3819e-06 | 6.6694e-06 | 354603.0197 | 0.84464
35 | 1.8801 | 4.7639e-07 | 4.2875e-06 | 380882.6549 | 0.18145
36 | 0.37602 | 3.8111e-06 | 3.8111e-06 | 387452.5637 | 1.4766
|  |  |  | Total | 14057.4615

## ShiftGeneration (hidden)
Typical Load Profile of a Peak Day |  |  |  | Time of Operation
Time | Demand |  |  | Case |  |  | Start |  | DO NOT DELETE!
| MW | % |  |  | hours |  | Auto or hh:mm |  | Auxiliary data used to draw a chart
0:30 | 35235.7 | 67.22% |  | 1 | 8 |  | auto |  | 0 | 67.22% | Case 1
1:00 | 35588.1 | 67.89% |  | 2 | 12 |  | auto |  | 0.5 | 67.22% | 0.5 | 12 | 89.2%
1:30 | 35680.6 | 68.07% | [6 empty] | 0.5 | 67.89% | 0.83333 | 20 | 89.2%
2:00 | 35296.7 | 67.34% |  |  |  | Please press the Refresh button before reading the results |  |  | 1 | 67.89%
2:30 | 35145.1 | 67.05% | [6 empty] | 1 | 68.07%
3:00 | 35515 | 67.75% | [6 empty] | 1.5 | 68.07%
3:30 | 34828.5 | 66.44% |  | Maximum Additional Contribution |  |  |  |  | 1.5 | 67.34% | Case 2
4:00 | 33973.8 | 64.81% | [6 empty] | 2 | 67.34% | 8:30 | 8.5 | 87.61%
4:30 | 33305.4 | 63.54% | [6 empty] | 2 | 67.05% | 20:30 | 20.5 | 87.61%
5:00 | 33040.5 | 63.03% |  | Duration | Time |  | Maximum contribution |  | 2.5 | 67.05%
5:30 | 33120.2 | 63.19% |  | hours | Start | Stop | of peak | of firm cap. | 2.5 | 67.75%
6:00 | 33742 | 64.37% |  | 8 | 12:00 | 20:00 | 10.8% | 12.11% | 3 | 67.75%
6:30 | 36227.4 | 69.11% |  | 12 | 8:30 | 20:30 | 12.39% | 14.15% | 3 | 66.44%
7:00 | 38997.6 | 74.4% | [6 empty] | 3.5 | 66.44%
7:30 | 42593.3 | 81.26% | [6 empty] | 3.5 | 64.81%
8:00 | 44825.8 | 85.52% | [6 empty] | 4 | 64.81%
8:30 | 45920.9 | 87.61% | [6 empty] | 4 | 63.54%
9:00 | 45930.1 | 87.62% | [6 empty] | 4.5 | 63.54%
9:30 | 46546.1 | 88.8% | [6 empty] | 4.5 | 63.03%
10:00 | 46757.4 | 89.2% | [6 empty] | 5 | 63.03%
10:30 | 46653.5 | 89% | [6 empty] | 5 | 63.19%
11:00 | 46681.8 | 89.06% | [6 empty] | 5.5 | 63.19%
11:30 | 46692.6 | 89.08% | [6 empty] | 5.5 | 64.37%
12:00 | 46661.4 | 89.02% | [6 empty] | 6 | 64.37%
12:30 | 46645.7 | 88.99% | [6 empty] | 6 | 69.11%
13:00 | 46283.4 | 88.3% | [6 empty] | 6.5 | 69.11%
13:30 | 46193.3 | 88.13% | [6 empty] | 6.5 | 74.4%
14:00 | 46108 | 87.96% | [6 empty] | 7 | 74.4%
14:30 | 46363.8 | 88.45% | [6 empty] | 7 | 81.26%
15:00 | 46267.2 | 88.27% | [6 empty] | 7.5 | 81.26%
15:30 | 46472.7 | 88.66% | [6 empty] | 7.5 | 85.52%
16:00 | 47952.2 | 91.48% | [6 empty] | 8 | 85.52%
16:30 | 50128.7 | 95.63% | [6 empty] | 8 | 87.61%
17:00 | 51971 | 99.15% | [6 empty] | 8.5 | 87.61%
17:30 | 52417.7 | 100% | [6 empty] | 8.5 | 87.62%
18:00 | 51887.4 | 98.99% | [6 empty] | 9 | 87.62%
18:30 | 51072.9 | 97.43% | [6 empty] | 9 | 88.8%
19:00 | 50294.6 | 95.95% | [6 empty] | 9.5 | 88.8%
19:30 | 49173 | 93.81% | [6 empty] | 9.5 | 89.2%
20:00 | 47825.7 | 91.24% | [6 empty] | 10 | 89.2%
20:30 | 46564.2 | 88.83% | [6 empty] | 10 | 89%
21:00 | 45256.7 | 86.34% | [6 empty] | 10.5 | 89%
21:30 | 44024.5 | 83.99% | [6 empty] | 10.5 | 89.06%
22:00 | 42123.2 | 80.36% | [6 empty] | 11 | 89.06%
22:30 | 40325.2 | 76.93% | [6 empty] | 11 | 89.08%
23:00 | 38639.6 | 73.71% | [6 empty] | 11.5 | 89.08%
23:30 | 36675.6 | 69.97% | [6 empty] | 11.5 | 89.02%
24:00 | 35594.6 | 67.91% | [6 empty] | 12 | 89.02%
[9 empty] | 12 | 88.99%
Maximum demand |  | 52417.7 | 100% | [5 empty] | 12.5 | 88.99%
Average demand |  | 42817.0917 | 81.68% | [5 empty] | 12.5 | 88.3%
Minimum demand |  | 33040.5 | 63.03% | [5 empty] | 13 | 88.3%
[9 empty] | 13 | 88.13%
[9 empty] | 13.5 | 88.13%
[9 empty] | 13.5 | 87.96%
[9 empty] | 14 | 87.96%
[9 empty] | 14 | 88.45%
[9 empty] | 14.5 | 88.45%
[9 empty] | 14.5 | 88.27%
[9 empty] | 15 | 88.27%
[9 empty] | 15 | 88.66%
[9 empty] | 15.5 | 88.66%
[9 empty] | 15.5 | 91.48%
[9 empty] | 16 | 91.48%
[9 empty] | 16 | 95.63%
[9 empty] | 16.5 | 95.63%
[9 empty] | 16.5 | 99.15%
[9 empty] | 17 | 99.15%
[9 empty] | 17 | 100%
[9 empty] | 17.5 | 100%
[9 empty] | 17.5 | 98.99%
[9 empty] | 18 | 98.99%
[9 empty] | 18 | 97.43%
[9 empty] | 18.5 | 97.43%
[9 empty] | 18.5 | 95.95%
[9 empty] | 19 | 95.95%
[9 empty] | 19 | 93.81%
[9 empty] | 19.5 | 93.81%
[9 empty] | 19.5 | 91.24%
[9 empty] | 20 | 91.24%
[9 empty] | 20 | 88.83%
[9 empty] | 20.5 | 88.83%
[9 empty] | 20.5 | 86.34%
[9 empty] | 21 | 86.34%
[9 empty] | 21 | 83.99%
[9 empty] | 21.5 | 83.99%
[9 empty] | 21.5 | 80.36%
[9 empty] | 22 | 80.36%
[9 empty] | 22 | 76.93%
[9 empty] | 22.5 | 76.93%
[9 empty] | 22.5 | 73.71%
[9 empty] | 23 | 73.71%
[9 empty] | 23 | 69.97%
[9 empty] | 23.5 | 69.97%
[9 empty] | 23.5 | 67.91%
[9 empty] | 24 | 67.91%

## About
P. Djapić, Imperial College of Science, Technology and Medicine, Prototype application for calculating generation capability to security of supply, Version 1.00, November 2003 - June 2006
Based on:
R.N. Allan, G. Strbac, and K. Jarrett, K/EL/00287 Extension: "Security Contribution from Distributed Generation", UMIST, December 2002
P. Djapić, G Strbac, Imperial College London, Prototype application for calculating generation capability to security of supply, Version 2.00, November 2018 - Sep 2019
P. Djapić, G Strbac, Imperial College London, Prototype application for calculating generation capability to security of supply, Issue 3, April 2020