## Slide 1
Guidance for the Performance Monitoring Excel Calculator Tool v2.1

## Slide 2: Summary
The Performance Monitoring Excel Calculator Tool allows to calculate errors and K factors for a single settlement period using 20Hz data (36000 rows of data). The data needed to use the tool: -Contracted Volumes, e.g. P and Q -From performance files: -p_mw -baseline_mw -availability -f_hz There is a new universal Excel calculators for all services:
PerfMon_Excel_ALL_PROTECTED_v2.1.xlsx
This slide pack will demonstrate the usage of this tool.

## Slide 3: Excel sheets
The sheets available within the tools are:
Front: Disclaimer and purpose of the tool, as well as explanatory notes.
DC-DM-DR PerfMon: This is the main calculator sheet where data is added and calculations are performed.
Performance: Graph for total response including performance bounds.
Errors: Low and High error graphs if applicable.
Frequency: Frequency trace graph of the input data.
Frequency Window: Frequency window and frequency trace graph.

## Slide 4: Using Excel formulae
This excel sheet contains four sections:
Section 1: Computation area, this is where all calculations take place.
Section 2: Result area for low and high where applicable.
Section 3: Contract and service information.
Section 4: Output graphs

## Slide 5: Using Excel formulae
Section 1: Computation area.
In this area, the green fields indicate the input data (i.e. f_hz, p_mw, baseline_mw and availability). This is where performance data will be copied for processing. The gray fields will perform the calculations with he provided data and generate results.
A full description of the columns is provided in the Front sheet.
Note that the data is required to be 20Hz, i.e. 50ms time intervals between samplings.
Input data

## Slide 6: Using Excel formulae
Section 2: Result area.
This area shows the results of the calculation for the settlement period data.
The grace period flag can be utilised to apply a 0.55 seconds grace period in the beginning of the settlement period to simulate “start of delivery”. This grace period will be applied when the flag value is set to TRUE, otherwise calculations are performed without grace period. This is the only grace period simulated in the calculator.
Contracted availability checks if the provided availability matches the contracted service. If the availability matches, then YES is displayed.
The SP Results for High displays the results for the High contract side and the SP Results for Low displays the results for the Low contract side. This is formed by:
Error: Maximum rolling minimum error.
K factor: The SP K factor based on the error calculated
Availability: Total availability for the SP.
Final K: This is calculated based on the availability factor F in the service terms, e.g. Final K = F* K factor, where F is 0 if there is any period or periods of unavailability within the SP, otherwise is 1.
Drop down menu to choose grace period at the start of the SP (TRUE or FALSE)
Availability check
Results for Low and High

## Slide 7: Using Excel formulae
Section 3: Contract and service information.
Here is where the information of the contracted service is added, i.e. the contracted volume for low (P) and contracted volume for high (Q).
If single-side service is required, the corresponding volume should be set to zero. For example if a DC Low service is required, the volume for High should be set to zero.
This section also shows the response curve parameters based on frequency points.
Contracted volumes
Drop-down menu for dynamic services
K factor table
Response delivery curve

## Slide 8: Using Excel formulae
Section 4: Output graphs.
This are shows the input and output data for the first 20 seconds, including (from top to bottom):
Errors
Frequency window and frequency trace
K factor graph
Performance bounds, response and availability
Segregated performance bounds, response and availability.

## Slide 9: Performance
Graph including data for the full duration of the settlement period of:
Total response, i.e. r = p_mw - baseline_mw
Performance bounds.

## Slide 10: Low errors
Graph including data for the full duration of the settlement period of:
LF scaled errors: errors scaled by the contracted volume
LF errors rolling: rolling minimum errors

## Slide 11: High errors
Graph including data for the full duration of the settlement period of:
HF scaled errors: errors scaled by the contracted volume
HF errors rolling: rolling minimum errors

## Slide 12: Frequency
Graph including data for the full duration of the settlement period of:
Frequency trace

## Slide 13: Frequency Window
Graph including data for the full duration of the settlement period of:
Frequency trace, i.e. f_hz
Frequency window, i.e. lfw (lower frequency window) and ufw (upper frequency window)