##### ***STCP 06-1 Issue 006 System Restoration***

CM089 – Electricity System Restoration Standard

19 May 2023

##### ***STC Procedure Document Authorisation***

|  |  |  |  |
| --- | --- | --- | --- |
| **Party** | **Name of Party Representative** | **Signature** | **Date** |
| National Grid Electricity System Operator Ltd |  |  |  |
| National Grid Electricity Transmission plc |  |  |  |
| SP Transmission plc |  |  |  |
| Scottish Hydro Electric  Transmission plc |  |  |  |
| Offshore Transmission Owners |  |  |  |

##### ***STC Procedure Change Control History***

|  |  |  |
| --- | --- | --- |
| Issue 001 | 23/12/2004 | BETTA Go-Live Version |
| Issue 002 | 28/07/2005 | Issue 002 incorporating PA028 |
| Issue 003 | 05/10/2005 | Issue 003 incorporating PA035 and PA037 |
| Issue 004 | 30/09/2010 | Issue 004 incorporating Offshore |
| Issue 005 | 19/05/2016 | Issue 005 incorporating PM088 |
| Issue 006 | 01/04/2019 | Issue 006 incorporating National Grid Legal Separation changes |
| Issue 007 | 19/05/2023 | Issue 007 Incorporating changes to facilitate the Electricity System Restoration Standard |

# Introduction

## Scope

### This document describes the planning and procedures required by NGESO and the TOs to manage System Restoration of the Total System in an efficient manner.

### 

### This document covers the restoration of the Total System following a Partial Shutdown or Total Shutdown in accordance with Restoration Plans be they Local Joint Restoration Plans or Distributed Restoration Zone Plans. The restoration process may include aTO carrying out the processes set out in Local Joint Restoration Plans or a Network Operator carrying out the processes set out in a Distribution Restoration Zone Plan. These processes are also described in OC9 of the Grid Code.

### TO network start up plans may be invoked in response to power island operation. Their use is outside the scope of this document. They are considered in STCP 06-2 Power Island Management.

### This procedure applies to NGESO and each TO. For the purposes of this document, the TOs are:

#### NGET as an onshore Transmission Licence holder

#### SPT as an onshore Transmission License holder

#### SHETL as an onshore Transmission License holder

#### Offshore Transmission License holders as appointed by OFGEM.

## Objectives

### The objective of this document is to enable, as far as possible, restoration of the TOs’ Transmission Systems and interfacing Users’ Systems in the shortest possible time using the most effective means following a Total Shutdown or Partial Shutdown.

# Key Definitions

## None

# Procedure

## Responsibilities

### NGESO shall establish the overall System Restoration strategy. This shall require Restoration Contractors to be party to Restoration Plans.

### NGESO shall establish Local Joint Restoration Plans which also includes Offshore Local Joint Restoration Plans. In addition, NGESO shall also instruct relevant Network Operators to establish Distribution Restoration Zone Plans.

### Restoration Plans shall be agreed by NGESO, relevant TOs, relevant Network Operators and Restoration Contractors.

### NGESO shall provide the TO with a signed copy of each Restoration Plan relevant to that TO’s Transmission System as provided for in Grid Code OC9.4.7.6.1.

### Where requested by NGESO, the relevant TO shall assist in the development and production of Restoration Plans.

### The relevant TO and NGESO shall each inform the other party if they become aware of any material change that may invalidate aRestoration Plan. In the case of Distribution Restoration Zone Plans, the Network Operator (in coordination with NGESO) shall inform the TO of any material change that may invalidate a Restoration Plan as specified in Grid Code OC9 and the Restoration Plan.

### NGESO in coordination with relevant Network Operators shall regularly review, update and re-issue Restoration Plans as necessary in accordance with the requirements of Grid Code OC9.

### When a Total or Partial Shutdown exists, NGESO shall notify the relevant TOs and Users of the situation. The Parties shall agree the implementation of those Restoration Plans (taking account of advised Restoration Contractors availabilities, the availability of each TO Transmission System and the availability of Plant to establish Distribution Restoration Zones).

### In Scotland, the relevant onshore TO shall implementLocal Joint Restoration Plans and issue instructions to Network Operators in Scotland to implement Distribution Restoration Zone Plans.

### If there is a failure of the voice communications the procedure described in section 3.5 shall be applied.

### NGESO shall direct and manage System Restoration through:

### agreeing the implementation of the Restoration Plans or other actions with the relevant TO;

### overseeing the coupling of Power Islands; and

### co-ordinating the operation of established parts of the National Electricity Transmission System.

### NGESO shall ensure that Usersshall abide with Restoration Plans.

### NGESO shall periodically carry out System Restoration and remote synchronisation tests and NGESO will advise the TO of these. The relevant TO shall co-operate with NGESO and relevant Network Operators in the case of Distribution Restoration Zones in facilitating these tests including the provision of additional staff and resources when identified as needed by NGESO. NGESO shall procure that relevant Users TOs co-operate in facilitating such tests as provided for in Grid Code OC5.7.2.1(g) or OC5.7.2.3(d) as applicable.

## Local Joint Restoration Plans

### Description of Local Joint Restoration Plans including Offshore Local Joint Restoration Plans

#### Local Joint Restoration Plans (LJRP) shall include the agreed method and procedures for Power Island creation. This may require the relevant TO to issue instructions to Anchor Plant and Top Up Restoration Plant that are party to the relevant Local Joint Restoration Plan. For the avoidance of doubt, the requirements applicable to Distributed Restoration Zones are covered in section 3.3 of this document and are completely separate from Local Joint Restoration Plans.

#### It may be deemed appropriate for a specific restoration option to be developed which prioritises restoration of a site deemed of strategic importance to the Transmission System restoration. Where possible this should be achieved as part of a standard Local Joint Restoration Plan. Should this be the case; an Annex to each relevant LJRP should be developed, discussed and agreed with the relevant TO and Users which will allow one TO to operate a Power Island that encompasses another TO’s area. The Annex will specifically detail the restoration route, equipment to be energised, and load to be supplied. It will also detail the command and communication chain for this Annex to be enacted and the format of instructions that should be issued.

#### NGESO will instruct the enacting of this Annex (if no communications exist then this can be enacted upon communication and agreement between both TOs). Once the Annex is enacted the LJRP will end if the network is extended any further than detailed in the Annex. At this point the LJRP will end and control of the interconnected Power Island will revert to NGESO as per standard LJRP operation. On the day, all parties to the Annex have the right to refuse this operation if deemed it places plant/personnel/restoration at risk.

#### Local Joint Restoration Plans and any Power Islands created under them shall only include sites from within a single Transmission Area (unless an Annex to the LJRP exists for a defined restoration route and is signed, and agreed, by all impacted TOs).

#### Local Joint Restoration Plans shall detail the agreed method and procedures which the TO shall use to restore parts of the Transmission network, and coordinate the actions of Anchor Plant that shall energise parts of the Transmission System and the subsequent synchronisation of Top Up Restoration Plant, and meet complementary demand, so as to form a Power Island.

#### The Local Joint Restoration Plan shall include a record of which TO and which TO sites are covered by the Local Joint Restoration Plan, and shall set out what actions are required by NGESO and the TO should a Total Shutdown or a Partial Shutdown (and the need to implement a Local Joint Restoration Plan) arise.

#### The Local Joint Restoration Plan shall go on to cover the creation of Power Islands within TO Transmission areas and may require the despatch of Top Up Restoration Plant other than Anchor Plant.

#### A Local Joint Restoration Plan shall include the agreed methods and procedures that aTO shall use to restore that TO’s Transmission System and interfacing Users’ Systems. These procedures shall be based on the following:

#### Each User shall make available relevant demand blocks;

#### Anchor Plant shall be available to energise the National Electricity Transmission System and meet demand blocks;

#### Top Up Restoration Plant, shall be able to receive supplies, synchronise to the National Electricity Transmission System and meet demand blocks, and

#### interaction between Restoration Contractors Plant included in the Local Joint Restoration Plan shall be managed by the onshore TO in respect of frequency control and reactive power requirements in a Power Island.

#### The list of Local Joint Restoration Plans is contained in Appendix B. NGESO shall be responsible for proposing amendments to Appendix B of this STCP through the STC Committee so that the list remains current and correct.

### **Creation of a new Local Joint Restoration Plan**

#### When NGESO identifies a requirement for a new Local Joint Restoration Plan (including an Offshore Local Joint Restoration Plan), NGESO shall discuss and agree such a plan with the relevant TO and Users.

#### Each Local Joint Restoration Plan shall be prepared by NGESO to reflect the above discussions and agreement. The TO shall support NGESO in developing the Local Joint Restoration Plans, including the provision of relevant information, data and resources, where necessary as detailed in Grid Code OC9.4.7.6.1.

#### When a Local Joint Restoration Plan has been prepared, it shall be sent by NGESO to the TO for confirmation of the agreement. NGESO shall also send the prepared LJRP to Users involved for confirmation of the agreement

#### The Local Joint Restoration Plan shall then be signed by NGESO and the relevant TO to confirm agreement to the Plan. NGESO shall procure that involved Users also sign to confirm agreement.

#### Once signed by the relevant parties, the Local Joint Restoration shall apply between NGESO and the relevant TO as if it were part of this STCP.

#### NGESO shall distribute a signed copy of the new Local Joint Restoration Plan to each relevant TO and User indicating the date of implementation.

3.2.2.6 The establishment, testing and provisions of the Local Joint Restoration Plan shall be in accordance with OC9.4.7.6 of the Grid Code.

### **Changes to an Existing Local Joint Restoration Plan**

#### If NGESO becomes aware that a change is required to a Local Joint Restoration Plan, NGESO shall initiate discussions with the relevant TO and Users to seek agreement for that change. NGESO shall procure that Users (the Network Operator, relevant Restoration Contractors which NGESO reasonably require and Non Embedded Customers) shall join those discussions.

#### If the TO party to a Local Joint Restoration Plan becomes aware that a change is required to that Local Joint Restoration Plan, it shall contact NGESO who shall then initiate such discussions with the relevant TO, Users and other affected parties to seek agreement for that change. NGESO shall procure that Users (the Network Operator, relevant Restoration Contractors, which NGESO reasonably require and Non Embedded Customers) shall join those discussions.

#### The principles applied in section 3.2.2 shall apply to discussions held under 3.2.3.1 and 3.2.3.2 and to any consequent changes.

When changes to a Local Joint Restoration Plan are agreed, NGESO shall update and reissue that Local Joint Restoration Plan to the relevant TO, Users and other affected parties indicating the issue number and the date that any change takes effect

#### The establishment, testing and provisions of the Local Joint Restoration Plan shall be in accordance with OC9.4.7.6 of the Grid Code.

### **Failure to Agree**

#### If NGESO or the relevant TO do not agree on a Local Joint Restoration Plan, NGESO shall develop and agree its own restoration plan.

## Distribution Restoration Zone Plans

### Description of Distribution Restoration Zone Plans

#### Distribution Restoration Zone Plans (DRZP) shall include the agreed method and procedures for Power Island creation where the Power Island has been initiated through instructions issued by Network Operators to Anchor Restoration Contractors and Top Up Restoration Contractors.

#### The Distribution Restoration Zone Plan shall include a record of which onshore TO, which Network Operator, which onshore TO sites and which Network Operator sites are covered by the Distribution Restoration Zone Plan, and shall set out what actions are required by Network Operators, NGESO and the onshore TO should a Total Shutdown or a Partial Shutdown (and the need to implement a Distribution Restoration Zone Plan) arise. For the avoidance of doubt, any Restoration Plan involving an Offshore Transmission Licensee and Offshore Generator shall be treated under the auspices of an Offshore Local Joint Restoration Plan rather than a Distribution Restoration Zone Plan even where Embedded Offshore Transmission Systems are involved.

#### The Distribution Restoration Zone Plan shall include the provision for the creation of Power Islands within Network Operator’s Systems which may also extend to Onshore TO’s assets and may require the despatch of Top Up Restoration Plant in addition to the despatch of Anchor Plant.

#### A Distribution Restoration Zone Plan shall include the agreed methods and procedures that a Network Operator shall use to restore part of the Network Operator’s System. These procedures shall be based on the following :

#### Each Party covered under the Distribution Restoration Zone Plan shall make available relevant demand blocks;

#### Anchor Plant shall be available to energise the Network Operator’s System and meet demand blocks;

#### Top Up Restoration Plant other than those in respect of Anchor Plant, shall be able to receive supplies, synchronise to the Network Operator’s System and meet demand blocks, and

#### interaction between Anchor Plant and Top Up Restoration Pant included in the Distribution Restoration Zone Plan shall be managed by the Network Operator in respect of frequency control and reactive power requirements in a Power Island.

#### The list of Distribution Restoration Zone Plans is contained in Appendix B. NGESO shall be responsible for proposing amendments to Appendix B of this STCP through the STC Committee so that the list remains current and correct.

### **Creation of a new Distribution Restoration Zone Plan**

#### When NGESO or the relevant Network Operator identifies a requirement for a new Distribution Restoration Zone Plan, the relevant Network Operator shall discuss and agree such a plan with NGESO, the relevant onshore TO and relevant Restoration Contractors.

#### Each Distribution Restoration Zone Plan shall be prepared by the relevant Network Operator to reflect the above discussions and agreement. NGESO and onshore TO shall support the relevant Network Operator in developing the Distribution Restoration Zone Plans, including the provision of relevant information, data and resources, where necessary as detailed in Grid Code OC9.4.7.6.1.

#### When a Distribution Restoration Zone Plan has been prepared, it shall be sent by the relevant Network Operator to NGESO and the onshore TO for confirmation of the agreement. The relevant Network Operator shall also send the prepared Distribution Restoration Zone Plan to Restoration Contractors (including those who own and operate Anchor Plant) involved for confirmation of the agreement.

#### The Distribution Restoration Zone Plan shall then be signed by the relevant Network Operator, NGESO and the relevant onshore TO to confirm agreement to the Plan. The relevant Network Operator in coordination with NGESO, shall procure that those parties involved (including Restoration Contractors) also sign to confirm agreement.

#### Once signed by the relevant parties, the Distribution Restoration Zone Plan shall apply between the relevant Network Operator, NGESO and the relevant TO as if it were part of this STCP.

#### The relevant Network Operator shall distribute a signed copy of the new Distribution Restoration Zone Plan to each relevant party indicating the date of implementation.

3.3.2.6 The establishment, testing and provisions of the Distribution Restoration Zone Plan shall be in accordance with OC9.4.7.6 of the Grid Code.

### **Changes to an Existing Distribution Restoration Zone Plan**

#### If any party to the Distribution Restoration Zone Plan (including NGESO) becomes aware that a change is required to that Distribution Restoration Zone Plan, it shall contact the Network Operator and the Network Operator shall then initiate such discussions with the ESO and TO, and other affected parties to seek agreement for that change. Relevant Network Operators in coordination with the ESO, shall procure in coordination with the ESO that other parties who are signatories to the Distribution Restoration Zone Plan or new parties who need to be party to the Distribution Restoration Zone Plan shall join those discussions.

#### The principles applied in section 3.3.2 shall apply to discussions held under 3.3.3.1 and to any consequent changes.

#### When changes to a Distribution Restoration Zone Plan are agreed, the relevant Network Operator shall update and reissue that Distribution Restoration Zone Plan to the relevant onshore TO, NGESO, and those parties who are signatories to the Plan and other affected parties indicating the issue number and the date that any change takes effect as provided for in OC9.4.7.6.1 of the Grid Code.

## System Restoration Incident Management

### When notified that a Total Shutdown or Partial Shutdown has occurred, all Parties shall establish communications routes and arrangements between Duty Managers or other representatives between NGESO, onshore TO, Generators relevant Users and affected offshore TOs to provide urgent managerial communication channels. Under such conditions, it may also be necessary to invoke the System Incident Management procedures under STCP 06-3.

## System Restoration Procedure

### In the event of a Total Shutdown or Partial Shutdown, NGESO shall, as soon as reasonably practicable, notify the relevant TO, Users, Restoration Contractors, relevant Network Operators and other affected parties that a Total Shutdown or a Partial Shutdown exists and that a Restoration Plan shall be implemented.

### Where voice communication between NGESO and the relevant TO and/or Users is not available and prevents NGESO from invoking System Restoration, the provisions of section 3.5 shall apply.

### **In Scotland**

#### The onshore TO shall request Restoration Contractors party to the Local Joint Restoration Plan (including Offshore Local Joint Restoration Plans) and affected Users to assess the condition of their assets, and report on their capability to carry out their obligations under the Local Joint Restoration Plan. Where a Distribution Restoration Zone Plan is in place, the onshore TO shall request the relevant Network Operator to assess the feasibility of establishing a Distribution Restoration Zone in accordance with the Distribution Restoration Zone Plan. This shall include the Network Operator undertaking an assessment of its System to ensure the network is in a position to establish a Distribution Restoration Zone and that Restoration Contractors Plant are in a sufficient state of readiness to permit the establishment of a Distribution Restoration Zone in accordance with the Distribution Restoration Zone Plan.

#### Where an offshore network connects within an onshore network covered by a Local Joint Restoration Plan (LJRP) the onshore TO shall, as necessary, liaise with the offshore TO to confirm the status of the connection between the onshore and offshore networks. The relevant TO shall gather these reports and feed them back to NGESO as soon as reasonably practicable.

#### Where the availability and capability of the TO’s Transmission System and Users’ Systems, and the availability of Restoration Contractors Plant in the Local Joint Restoration Plan are not significantly different with the Local Joint Restorations Plan’s requirements, NGESO shall give the onshore TO the authority to implement the appropriate Local Joint Restoration Plan or Offshore Local Joint Restoration Plan as appropriate. Where the availability and capability of the onshore TO’s Transmission System and Network Operators’ Systems, and the availability of Anchor Contractor’s Plant in the Distribution Restoration Zone Plan are not significantly different with the Distribution Restoration Zone Plan’s requirements, NGESO shall give the onshore TO the authority to implement the appropriate Distribution Restoration Plan though the issue of instructions to the relevant Network Operator.

#### Where to the extent that the availability and capability of the TO’s Transmission System or Users’ Systems, or the availability of Restoration Contractors Plant in the Local Joint Restoration Plan is significantly different to that set out in the Local Joint Restoration Plan, NGESO may choose to manage the restoration of part of the TO’s Transmission System outside the provisions of the Local Joint Restoration Plan, using STCP 01-1 Operational Switching and normal energy balancing processes as appropriate.

#### When the relevant onshore TO has been given the authority to implement the appropriate Local Joint Restoration Plan, it shall execute and progress the appropriate Local Joint Restoration Plan in accordance with its obligations under that LJRP.

#### When implementing a Local Joint Restoration Plan, the onshore TO shall carry out operational liaison, complete appropriate Operational Switching actions and issue instructions to Users, including Restoration Contractors party to the Local Joint Restoration Plan to establish and control a Power Island in accordance with the provisions of the Local Joint Restoration Plan. When implementing a Distribution Restoration Zone Plan, the onshore TO shall issue instructions to relevant Network Operators to establish a Distribution Restoration Zone. The relevant Network Operator shall then carry out the requirements of the Distribution Restoration Zone Plan together with the relevant requirements of OC9 of the Grid Code and DOC9 of the Distribution Code which will enable the control and establishment of a Power Island.

### **In England and Wales**

#### NGESO has the sole authority to implement the Local Joint Restoration Plans. In the case of Distribution Restoration Zone Plans, NGESO will issue instructions to relevant Network Operators who will then implement the relevant Distribution Restoration Zone Plan.

#### NGESO shall request Restoration Contractors party to the Local Joint Restoration Plan to assess the condition of their assets, and report on their capability to carry out their obligations under the Local Joint Restoration Plan. NGESO shall request Network Operators party to the Local Joint Restoration Plan to assess the condition of their assets and report on their capability to carry out their obligation under the Local Joint Restoration Plan. In addition, and where a Distribution Restoration Zone Plan is in place, NGESO shall request the relevant Network Operator to undertake an assessment of the Distribution Network to ensure the network is in a position to establish a Distribution Restoration Zone and that Restoration Contractor’s Plant is in a sufficient state of readiness to permit the establishment of a Distribution Restoration Zone in accordance with the Distribution Restoration Zone Plan.

#### Where an offshore network connects within an onshore network covered by a Local Joint Restoration Plan (LJRP) NGESO shall as necessary, liaise with the offshore TO to confirm the status of the connection between the onshore and offshore networks.

#### When implementing a Local Joint Restoration Plan, NGESO shall carry out operational liaison, with Restoration Contractors party to the Local Joint Restoration Plan in accordance with the provisions of the Local Joint Restoration Plan. The relevant TO shall carry out operational liaison, direct appropriate Operational Switching actions and issue instructions to relevant Users party to the Local Joint Restoration Plan to establish and control a Power Island in accordance with the provisions of the Local Joint Restoration Plan. When implementing a Distribution Restoration Zone Plan, NGESO shall issue instructions to relevant Network Operators to establish a Distribution Restoration Zone. The relevant Network Operator shall then carry out the requirements of the Distribution Restoration Zone Plan together with the relevant requirements of OC9 of the Grid Code and DOC9 of the Distribution Code which will enable the control and establishment of a Power Island.

### **Power Islands:**

### Where possible, a Power Island (be it established either through a Local Joint Restoration Plan (LJRP) or Distribution Restoration Zone Plan (DRZP)) should be operated in accordance with following frequency and voltage criteria:

* the frequency on the Transmission System shall be nominally 50Hz and shall be controlled within the limits 49.5 – 50.5Hz;
* the voltage on the Transmission System shall normally remain within -/+ 5% of nominal. The minimum voltage is –10% and the maximum is +10% of nominal. Voltages of +10% and –5% should not prevail for more than 15 minutes.
* The voltage on the Distribution System when operated at 110kV or above shall normally remain within the limits of -/+10%. For nominal voltages of below 110kV on the Distribution System the voltage shall normally remain within -/+ 6%.

### During the initial stages of implementing a Local Joint Restoration Plan or Distribution Restoration Zone Plan, normal operational standards may not be appropriate or possible and the TO’s Transmission System may be operated outside normal voltage and frequency standards provided that it does not result in damage to Plant and/or Apparatus, or a safety hazard.

### At any time during the implementation of the Local Joint Restoration Plan or Distribution Restoration Zone Plan, the TO shall advise NGESO (and relevant Network Operator) of any circumstances that may require significant modification to the implementation of the Local Joint Restoration Plan or Distribution Restoration Zone Plan. Where such modifications are required, both parties may agree a new course of action consistent with the aims of the Local Joint Restoration Plan or Distribution Restoration Zone Plan.

### At any time during the implementation of the Local Joint Restoration Plan and where there is good reason, NGESO may choose to terminate operation in accordance with the Local Joint Restoration Plan and manage restoration of that part of the Transmission System without the bounds of the Local Joint Restoration Plan. NGESO shall notify the relevant onshore TO and any other affected parties of the termination of the Local Joint Restoration Plan. In the case of a Distribution Restoration Zone Plan and where there is good reason, the Network Operator may choose to terminate operation in accordance with the Distribution Restoration Zone Plan and manage restoration of that part of the Distribution System without the bounds of the Distribution Restoration Zone Plan. The relevant Network Operator shall notify NGESO, relevant onshore TO and any other affected parties of the termination of the Distribution Restoration Zone Plan.

### At any time during the implementation of the Local Joint Restoration Plan or Distribution Restoration Zone Plan and where there is good reason, the onshore TO may choose to terminate operation in accordance with the Local Joint Restoration Plan or (where relevant) Distribution Restoration Zone Plan having liaised with the relevant Network Operator. The TO will advise NGESO of the termination of the Local Joint Restoration Plan or termination of the Distribution Restoration Zone Plan having held discussions with both the relevant Network Operator and NGESO. Operation and restoration of that part of the National Electricity Transmission System will return to NGESO. NGESO shall notify the relevant affected parties of the termination of the Plan.

### The onshore TO shall keep NGESO informed of progress in establishing the Power Island(s). At any time during establishing Power Islands the onshore TO shall inform NGESO if further resources become available, such that additional Power Islands can be established in accordance with the relevant Local Joint Restoration Plan or Distribution Restoration Zone Plan. NGESO and the onshore TO shall decide if and when additional Local Joint Restoration Plans should be invoked. In the case of Distribution Restoration Zones, NGESO, relevant Network Operators and TO’s shall decide if and when additional Distribution Restoration Zones shall be invoked.

### **Interconnection of Power Islands**

#### NGESO shall agree with the TO to the interconnection of any Power Islands which are not expressly allowed for in a Local Joint Restoration Plan or Distribution Restoration Zone Plan. Local Joint Restoration Plan operation and Distribution Restoration Zone Plan operation shall terminate at this point and NGESO shall take back control of that part of the TO’s Transmission System formed from the interconnected Power Islands irrespective of whether they were formed by a Local Joint Restoration Plan or Distribution Restoration Zone Plan. TOs shall not operate a Power Island that contains part of more than one TO’s Transmission System unless through a prescribed Local Joint Restoration Plan Annex.

#### NGESO shall coordinate the interconnection of sub-systems created from the interconnection of Power Islands irrespective of whether they were formed from a Local Joint Restoration Plan or Distribution Restoration Zone Plan to form an integrated System. The completion of the integration of sub-systems shall eventually re-establish the TO’s Transmission System or the re-connection of the relevant part of the TO’s Transmission System, completing System Restoration.

#### At any point during the connection of Power Islands or management of sub-systems, NGESO may request the TO to resume Local Joint Restoration Plan operation of part of that onshore TO’s Transmission System, providing its operation would still remain within the bounds of an applicable Local Joint Restoration Plan and would not include more than one TO’s Transmission System unless through a prescribed Local Joint Restoration Plan Annex. Equally at any point during the connection of Power Islands or management of sub-systems, NGESO may request a Network Operator to resume Distribution Restoration Zone Plan operation of part of restoration of the onshore TO’s Transmission System, providing its operation would still remain within the bounds of an applicable Distribution Restoration Zone Plan and would not include more than one Distribution System unless specifically prescribed by a Distribution Restoration Zone Plan.

### **Completion of System Restoration**

#### When the System Restoration is complete, NGESO shall formally notify the TOs and Users that System Restoration is complete and normal operation has been resumed.

## Voice Communication Failure

### In the event of a total communication failure between the TO and NGESO during System Restoration conditions, the TO where possible, may choose to invoke the LJRP(s) for its Transmission System and operate within those provisions

### Where voice communication failure is protracted, the TO, where possible may consider the interconnection of established Power Islands as allowed for in the Local Joint Restoration Plan(s) or Network Operators in the case of Distribution Restoration Zone Pans.

### The TO must seek to inform NGESO as soon as reasonably practicable of all actions they have taken and the status of the restoration after communication is re-established.

## System Restoration Training

### NGESO shall carry out and make available appropriate and regular training for TO staff, to allow them to carry out their roles and responsibilities under a System Restoration condition. The TO shall make available appropriately skilled personnel to complete the prescribed System Restoration training. Training and Assurance shall also be undertaken as provided for in Grid Code OC5.7 in particular OC5.7.4. In addition, training and regular exercises shall be undertaken in accordance with the requirements of OC9.4.7.6.2 of the Grid Code.

## System Restoration Testing

### NGESO shall carry out System Restoration and other related Tests on a routine basis. All System Restoration or related Tests shall be carried out in accordance with the provision of STCP 08-3 Operational Tests and System Tests in addition to the requirements of OC5.7 of the Grid Code and OC9.4.7.6.2 of the Grid Code.

## System Restoration Test Bookings

### System Restoration Tests shall be booked in the Outage database by NGESO for information. Booking requests shall be agreed in accordance with STCP 11-1 Outage Planning.

***Appendix A – Process Diagrams***

Note that the Process Diagrams shown in this Appendix A are for information only. In the event of any contradiction between the process represented in this Appendix and the process described elsewhere in this STCP, then the text elsewhere in this STCP shall prevail.

# *Appendix B – LJRPs and DRZPs*

|  |
| --- |
| This Appendix has been removed from this version of the STCP on the grounds of Confidentiality. In respect of LJRPs, this decision was taken, in accordance with the decision taken by the STC Committee in July 2005 and in respect of DRZPs, this decision was taken in accordance with the decision taken by the STC Committee in XX 2023. **For further information please e-mail STC.Team@nationalgrid.com** |

***Appendix C:– Abbreviations & Definitions***

## Abbreviations

STCP System Operator –Transmission Owner Code Procedure

TO Transmission Owner

TSC Transmission Status Certificate

GC Grid Code

## Definitions

**STC definitions used:**

Committee

Distribution Restoration Zone Plan

Generator

Generating Unit

Local Joint Restoration Plan

Network Operator

NGESO

NGET

Non Embedded Customer

Offshore

Offshore Local Joint Restoration Plan

Offshore Transmission System

Partial Shutdown

Party

Power Station

Restoration Contractor

Restoration Plan

System

System Restoration

Total Shutdown

Total System

User

**Grid Code definitions used:**

Anchor

Anchor Restoration Contractor

Ancillary Services Agreement

Distribution Restoration Zone

Embedded

Plant

Power Island

Top Up Restoration Contractor

Top Up Restoration Plant

**Definitions used from other STCPs:**

|  |  |
| --- | --- |
| Duty Manager | As defined in STCP 06-3 System Incident Management |