# DATA REGISTRATION CODE

# (DRC)

GRID CODE MODIFICATION GC0156

DATED 20 JUNE 2023

Text taken from GC0148 when submitted to Ofgem in October 2022

# CONTENTS

# (This contents page does not form part ofthe Grid Code)

Paragraph No/Title	Page Number

DRC.1   INTRODUCTION	3

DRC.2   OBJECTIVE	3

DRC.3   SCOPE	3

DRC.4   DATA CATEGORIES AND STAGES IN REGISTRATION	4

DRC.4.2   Standard Planning Data	4

DRC.4.3   Detailed Planning Data	4

DRC.4.4   Operational Data	4

DRC.5   PROCEDURES AND RESPONSIBILITIES	4

DRC.5.1   Responsibility For Submission And Updating Of Data	4

DRC.5.2   Methods Of Submitting Data	4

DRC.5.3   Changes To Users Data	6

DRC.5.4   Data Not Supplied	6

DRC.5.5   Substituted Data	6

DRC.6   DATA TO BE REGISTERED	6

SCHEDULE 1 - GENERATING UNIT (OR CCGT MODULE), POWER PARK MODULE AND DC CONVERTER TECHNICAL DATA	12

SCHEDULE 2 - GENERATION PLANNING PARAMETERS	39

SCHEDULE 3 - LARGE POWER STATION OUTAGE PROGRAMMES, OUTPUT USABLE AND INFLEXIBILITY INFORMATION	43

SCHEDULE 4 - LARGE POWER STATION DROOP AND RESPONSE DATA	44

SCHEDULE 5 - USERS SYSTEM DATA	45

SCHEDULE 6 - USERS OUTAGE INFORMATION	57

SCHEDULE 7 - LOAD CHARACTERISTICS AT GRID SUPPLY POINTS	61

SCHEDULE 8 - DATA SUPPLIED BY BM PARTICIPANTS	62

SCHEDULE 9 - DATA SUPPLIED BY NGET TO USERS	63

SCHEDULE 10 - DEMAND PROFILES AND ACTIVE ENERGY DATA	65

SCHEDULE 11 - CONNECTION POINT DATA	67

SCHEDULE 12 - DEMAND CONTROL	74

SCHEDULE 13 - FAULT INFEED DATA	78

SCHEDULE 13 - FAULT INFEED DATA	79

SCHEDULE 14 - FAULT INFEED DATA (GENERATORS INCLUDING UNIT TRANSFORMERS AND STATION TRANSFORMERS)	80

SCHEDULE 16 - SYSTEM RESTORATION INFORMATION	88

SCHEDULE 16 - SYSTEM RESTORATION INFORMATION	89

SCHEDULE 16 - SYSTEM RESTORATION INFORMATION	90

SCHEDULE 16 - SYSTEM RESTORATION INFORMATION	92

SCHEDULE 17 - ACCESS PERIOD DATA	99

SCHEDULE 18 - OFFSHORE TRANSMISSION SYSTEM DATA	100

SCHEDULE 19 - USER DATA FILE STRUCTURE	131

SCHEDULE 19 - USER DATA FILE STRUCTURE	133

DRC.1 	INTRODUCTION

DRC.1.1	The Data Registration Code ("DRC") presents a unified listing of all data required by The Company from Users (including Restoration Contractors where they are not a User) and by Users (including Restoration Contractors where they are not a User) from The Company, from time to time under the Grid Code.  The data which is specified in each section of the Grid Code is collated here in the DRC. Where there is any inconsistency in the data requirements under any particular section of the Grid Code and the Data Registration Code the provisions of the particular section of the Grid Code shall prevail.

DRC.1.2 	The DRC identifies the section of the Grid Code under which each item of data is required.

DRC.1.3	The Code under which any item of data is required specifies procedures and timings for the supply of that data, for routine updating and for recording temporary or permanent changes to that data.  All timetables for the provision of data are repeated in the DRC.

DRC.1.4	Various sections of the Grid Code also specify information which Users will receive from The Company. This information is summarised in a single schedule in the DRC (Schedule 9).

DRC.1.5	The categorisation of data into DPD I and DPD II is indicated in the DRC below.

DRC.1.6	For the purposes of this DRC, if a User is also a Restoration Contractor, they shall only need to submit the data once stating on their data submission  they are also a Restoration Contractor.  If a Restoration Contractor does not have a CUSC Contract then the data required to be submitted shall be pursuant to the terms of the Anchor Plant Contract or Top Up Restoration Contract.

DRC.2	OBJECTIVE

The objective of the DRC is to:

DRC.2.1	List and collate all the data to be provided by each category of User to The Company under the Grid Code.

DRC.2.2	List all the data to be provided by The Company to each category of User under the Grid Code.

DRC.3	SCOPE

DRC.3.1	The DRC applies to The Company, Users and Restoration Contractors, which in this DRC means:-

(a)	Generators (including those undertaking OTSDUW and/or those who own and/or operate DC Connected Power Park Modules);

(b)	Network Operators;

(c)	DC Converter Station owners and HVDC System Owners;

(d)	Suppliers;

(e)	Non-Embedded Customers;

(f)	Externally Interconnected System Operators;

(g)	Interconnector Users;

(h)	BM Participants; and

(i) 	Pumped Storage Generators and Generators in respect of Electricity Storage Modules.

(j)	Restoration Contractors (which would be pursuant to the requirements of their Anchor Restoration Contract or Top Up Restoration Contract).

DRC.3.2	For the avoidance of doubt, the DRC applies to both GB Code Users and EU Code Users.

DRC.4	DATA CATEGORIES AND STAGES IN REGISTRATION

DRC.4.1.1	Within the DRC each data item is allocated to one of the following three categories:

(a)	Standard Planning Data (SPD)

(b)	Detailed Planning Data (DPD)

(c)	Operational Data

DRC.4.2	Standard Planning Data (SPD)

DRC.4.2.1	The Standard Planning Data listed and collated in this DRC is that data listed in Part 1 of the Appendix to the PC.

DRC.4.2.2	Standard Planning Data will be provided to The Company in accordance with PC.4.4 and PC.A.1.2.

DRC.4.3	Detailed Planning Data (DPD)

DRC.4.3.1	The Detailed Planning Data listed and collated in this DRC is categorised as DPD I and DPD II and is that data listed in Part 2 of the Appendix to the PC.

DRC.4.3.2	Detailed Planning Data will be provided to The Company in accordance with PC.4.4, PC.4.5 and PC.A.1.2.

DRC.4.4	Operational Data

DRC.4.4.1	Operational Data is data which is required by the Operating Codes and the Balancing Codes. Within the DRC, Operational Data is sub-categorised according to the Code under which it is required, namely OC1, OC2, BC1 or BC2.

DRC.4.4.2	Operational Data is to be supplied in accordance with timetables set down in the relevant Operating Codes and Balancing Codes and repeated in tabular form in the schedules to the DRC.

DRC.5	PROCEDURES AND RESPONSIBILITIES

DRC.5.1	Responsibility For Submission And Updating Of Data

In accordance with the provisions of the various sections of the Grid Code, each User must submit data as summarised in DRC.6 and listed and collated in the attached schedules.

DRC.5.2	Methods Of Submitting Data

DRC.5.2.1	Wherever possible, the data schedules to the DRC are structured to serve as standard formats for data submission and such format must be used for the written submission of data to The Company.

DRC.5.2.2	Data must be submitted to the Transmission Control Centre notified by The Company, or to such other department or address as The Company may from time to time advise.  The name of the person at the User Site who is submitting each schedule of data must be included.

DRC.5.2.3	Where a computer data link exists between a User and The Company, data may be submitted via this link.  The Company will, in this situation, provide computer files for completion by the User containing all the data in the corresponding DRC schedule.

Data submitted can be in an electronic format using a proforma to be supplied by The Company or other format to be agreed annually in advance with The Company. In all cases the data must be complete and relate to, and relate only to, what is required by the relevant section of the Grid Code.

DRC.5.2.4	Other modes of data transfer, such as magnetic tape, may be utilised if The Company gives its prior written consent.

DRC.5.2.5	Generators, HVDC System Owners and DC Converter Station owners submitting data for a Power Generating Module, Generating Unit, DC Converter, HVDC System, Power Park Module (including DC Connected Power Park Modules) or CCGT Module before the issue of a Final Operational Notification should submit the DRC data schedules and compliance information required under the CP electronically using the User Data File Structure unless otherwise agreed with The Company.  Data required from Restoration Contractors where not provided would be pursuant to the the terms of their Anchor Restoration Contract or Top Up Restoration Contract.

DRC.5.3	Changes To User’s Data

DRC.5.3.1	Whenever a User becomes aware of a change to an item of data which is registered with The Company, the User must notify The Company in accordance with each section of the Grid Code.  The method and timing of the notification to The Company is set out in each section of the Grid Code.  Data required from Restoration Contractors where not provided would be pursuant to the the terms of their Anchor Restoration Contract or Top Up Restoration Contract.

DRC.5.4	Data Not Supplied

DRC.5.4.1	Users and The Company are obliged to supply data as set out in the individual sections of the Grid Code and repeated in the DRC.  If a User fails to supply data when required by any section of the Grid Code, The Company will estimate such data if and when, in The Company's view, it is necessary to do so.  If The Company fails to supply data when required by any section of the Grid Code, the User to whom that data ought to have been supplied, will estimate such data if and when, in that User's view, it is necessary to do so.  Such estimates will, in each case, be based upon data supplied previously for the same Plant or Apparatus or upon corresponding data for similar Plant or Apparatus or upon such other information as The Company or that User, as the case may be, deems appropriate.

DRC.5.4.2	The Company will advise a User in writing of any estimated data it intends to use pursuant to DRC.5.4.1 relating directly to that User's Plant or Apparatus in the event of data not being supplied.

DRC.5.4.3	A User will advise The Company in writing of any estimated data it intends to use pursuant to DRC.5.4.1 in the event of data not being supplied.

DRC.5.4.4	Data requirements defined in DRC5.4.1 – DRC5.4.3 as applicable to a Restoration Contractor where that Restoration Contractor is a not a User, would be pursuantto the the terms of the Anchor Restoration Contract or Top Up Restoration Contract.

DRC.5.5	Substituted Data

DRC.5.5.1	In the case of PC.A.4 only, if the data supplied by a User does not in The Company’s reasonable opinion reflect the equivalent data recorded by The Company, The Company may estimate such data if and when, in the view of The Company, it is necessary to do so.  Such estimates will, in each case, be based upon data supplied previously for the same Plant or Apparatus or upon corresponding data for similar Plant or Apparatus or upon such other information as The Company deems appropriate.

DRC.5.5.2	The Company will advise a User in writing of any estimated data it intends to use pursuant to DRC.5.5.1 relating directly to that User's Plant or Apparatus where it does not in The Company’s reasonable opinion reflect the equivalent data recorded by The Company.  Such estimated data will be used by The Company in place of the appropriate data submitted by the User pursuant to PC.A.4 and as such shall be deemed to accurately represent the User’s submission until such time as the User provides data to The Company’s reasonable satisfaction.

DRC.6	DATA TO BE REGISTERED

DRC.6.1	Schedules 1 to 20 attached cover the following data areas.

DRC.6.1.1	Schedule 1 – Power Generating Module, Generating Unit (or CCGT Module), Power Park Module (including DC Connected Power Park Module and Power Park Unit), HVDC System  and DC Converter Technical Data.

Comprising Power Generating Module, Generating Unit (and CCGT Module), Power Park Module (including DC Connected Power Park Module and Power Park Unit) and DC Converter fixed electrical parameters. Any data required under DRC Schedule 1 from Restoration Contractors where not provided, would be pursuant to the terms of their Anchor Restoration Contract or Top Up Restoration Contract.

DRC.6.1.2 	Schedule 2 - Generation Planning Parameters

Comprising Genset parameters and Restoration Contractors parameters required for Operational Planning studies.

DRC.6.1.3	Schedule 3 -  Power Station Outage Programmes, Output Usable and Inflexibility Information.

Comprising generation and storage outage planning in respect of Large Power Stations, Output Usable and inflexibility information at timescales down to the daily BM Unit Data submission.  In the case of Restoration Contractors, this data needs to only to be provided where such a Resoration Contractor has an Anchor Restoration Contract or Top Up Restoration Contract other than in respect of Large Power Stations where the data will already be required.

DRC.6.1.4	Schedule 4 - Large Power Station Droop and Response Data.

Comprising data on governor Droop settings and Primary, Secondary and High Frequency Response data for Large Power Stations.

DRC.6.1.5	Schedule 5 – User's System Data.

Comprising electrical parameters relating to Plant and Apparatus connected to the National Electricity Transmission System.

DRC.6.1.6	Schedule 6 – Users Outage and Restoration Service Provider Outage Information.

Comprising the information required by The Company for outages on the User’s System, including outages at Power Stations other than outages of Gensets.  Outages of Plant and Apparatus of Restoration Contractors and key Plant and Apparatus of a Network Operator’s System associated with a Distribution Restoration Zone Plan also need to be co-ordinated with outages on the National Electricity Transmission System. The data submitted should therefore also include outages on Restoration Contractors Plant and Apparatus and Network Operator’s Plant and Apparatus which would prevent the operation of a Local Joint Restoration Plan or Distribution Restoration Zone Plan.

DRC.6.1.7 	Schedule 7 - Load Characteristics.

Comprising the estimated parameters of load groups in respect of, for example, harmonic content and response to frequency.

DRC.6.1.8	Schedule 8 -  BM Unit Data.

DRC.6.1.9	Schedule 9 - Data Supplied by The Company to Users.

DRC.6.1.10	Schedule 10 - Demand Profiles and Active Energy Data

Comprising information relating to the Network Operators’ and Non-Embedded Customers’ total Demand and Active Energy taken from the National Electricity Transmission System

DRC.6.1.11	Schedule 11 - Connection Point Data

Comprising information relating to Demand, demand transfer capability and the Small Power Station, Medium Power Station and Customer generation connected to the Connection Point

DRC.6.1.12	Schedule 12 - Demand Control Data

Comprising information related to Demand Control

DRC.6.1.13	Schedule 13 - Fault Infeed Data

Comprising information relating to the short circuit contribution to the National Electricity Transmission System from Users other than Generators, HVDC System Owners  and DC Converter Station owners.

DRC.6.1.14	Schedule 14 - Fault Infeed Data (Generators Including Unit and Station Transformers)

Comprising information relating to the Short Circuit contribution to the National Electricity Transmission System from Generators, HVDC System Owners and DC Converter Station owners.

DRC.6.1.15	Schedule 15 – Mothballed Power Generating Module, Mothballed Generating Unit, Mothballed Power Park Module (including Mothballed DC Connected Power Park Modules), Mothballed HVDC Systems, Mothballed HVDC Converters, Mothballed DC Converters at a DC Converter Station and Alternative Fuel Data

Comprising information relating to estimated return to service times for Mothballed Power Generating Modules, Mothballed Generating Units, Mothballed Power Park Modules (including Mothballed DC Connected Power Park Modules), Mothballed HVDC Systems, Mothballed HVDC Converters and Mothballed DC Converters at a DC Converter Station and the capability of gas-fired Generating Units to operate using alternative fuels.

DRC.6.1.16	Schedule 16 – System Restoration Information

Comprising information relating to System Restoration.

DRC.6.1.17	Schedule 17 – Access Period Schedule

Comprising Access Period information for Transmission Interface Circuits within an Access Group.

DRC.6.1.18	Schedule 18 – Generators Undertaking OTSDUW Arrangements

Comprising electrical parameters relating to OTSDUW Plant and Apparatus between the Offshore Grid Entry Point and Transmission Interface Point.

DRC.6.1.19	Schedule 19 – User Data File Structure

Comprising information relating to the User Data File Structure.

DRC.6.1.20	Schedule 20 – Grid Forming Plant Data

Comprising information relating to Grid Forming Plant

DRC.6.2	The Schedules applicable to each class of User are as follows:

| User | Schedule |
| --- | --- |
| Generators with Large Power Stations | 1, 2, 3, 4, 9, 14, 15, 16, 19 |
| Generators with Medium Power Stations (see notes 2, 3, 4) | 1, 2 (part), 9, 14, 15, 19 |
| Generators with Small Power Stations directly connected to the National Electricity Transmission System | 1, 6, 14, 15, 19 |
| Generators undertaking OTSDUW (see note 5) | 18, 19 |
| All Users connected directly to the National Electricity Transmission System | 5, 6, 9 |
| All Users connected directly to the National Electricity Transmission System other than Generators | 10,11,13,17 |
| All Users connected directly to the National Electricity Transmission System with Demand | 7, 9 |
| A Pumped Storage Generator, a Generator in respect of one or more Electricity Storage Modules and an Externally Interconnected System Operator and Interconnector Users | 12 (as marked) |
| All Suppliers | 12 |
| All Network Operators | 12, 16 |
| All BM Participants | 8 |
| All DC Converter Station owners | 1, 4, 9, 14, 15, 19 |
| Restoration Contractors | 2, 3, 6, 16 |

Notes:

(1)	Network Operators must provide data relating to Small Power Stations and/or Customer Generating Plant Embedded in their Systems when such data is requested by The Company pursuant to PC.A.3.1.4 or PC.A.5.1.4.

(2)	The data in schedules 1, 14 and 15 need not be supplied in relation to Medium Power Stations connected at a voltage level below the voltage level of the Subtransmission System except in connection with a CUSC Contract or unless specifically requested by The Company.

(3)	Each Network Operator within whose System an Embedded Medium Power Station not subject to a Bilateral Agreement or Embedded DC Converter Station not subject to a Bilateral Agreement is situated shall provide the data to The Company in respect of each such Embedded Medium Power Station or Embedded DC Converter Station or HVDC System.

(4)	In the case of Schedule 2, Generators, HVDC System Owners, DC Converter Station owners or Network Operators in the case of Embedded Medium Power Stations not subject to a Bilateral Agreement or Embedded DC Converter Stations not subject to a Bilateral Agreement, would only be expected to submit data in relation to Standard Planning Data as required by the Planning Code.

(5)	In the case of Generators undertaking OTSDUW, the Generator will need to supply User data in accordance with the requirements of Large or Small Power Stations (as defined in DRC.6.2) up to the Offshore Grid Entry Point.  In addition, the User will also need to submit Offshore Transmission System data in between the Interface Point and its Connection Points in accordance with the requirements of Schedule 18.

(6)	In the case of Restoration Contractors, data only needs to be provided by a Restoration Contractor where such a Restoration Contractor is not a CUSC Party and the data has not been submitted.  In this case the data to be submitted would be would be pursuant to the the terms of the Anchor Restoration Contract or Top Up Restoration Contract.

SCHEDULE 1 – POWER GENERATING MODULE, GENERATING UNIT (OR CCGT MODULE), POWER PARK MODULE, DC CONNECTED POWER PARK MODULE, HVDC SYSTEM AND DC CONVERTER TECHNICAL DATA

PAGE 1 OF 19

ABBREVIATIONS:

| SPD = Standard Planning Data | DPD = Detailed Planning Data |
| --- | --- |
| % on MVA = % on Rated MVA | RC = Registered Capacity MC = Maximum Capacity |
| % on 100 = % on 100 MVA | OC1, BC1, etc = Grid Code for which data is required |
| CUSC Contract = User data which may be submitted to the Relevant Transmission Licensees by The Company, following the acceptance by a User of a CUSC Contract. | CUSC App. Form = User data which may be submitted to the Relevant Transmission Licensees by The Company, following an application by a User for a CUSC Contract. |

Note:

All parameters, where applicable, are to be measured at nominal System Frequency

+	these SPD items should only be given in the data supplied with the application for a CUSC Contract.

*	Asterisk items are not required for Small Power Stations and Medium Power Stations

Information is to be given on a Unit basis, unless otherwise stated. Where references to CCGT Modules are made, the columns "G1" etc should be amended to read "M1" etc, as appropriate

□	These data items may be submitted to the Relevant Transmission Licensees from The Company in respect of the National Electricity Transmission System.  The data may be submitted to the Relevant Transmission Licensees in a summarised form e.g. network model; the data transferred will have been originally derived from data submitted by Users to The Company.

■	these data items may be submitted to the Relevant Transmission Licensee from The Company in respect to Relevant Units only.  The data may be submitted to the Relevant Transmission Licensee in a summarised form e.g. network model; the data transferred will have been originally derived from data submitted by Users to The Company.

SCHEDULE 1 – POWER GENERATING MODULE, GENERATING UNIT (OR CCGT MODULE), POWER PARK MODULE, DC CONNECTED POWER PARK MODULE, HVDC SYSTEM AND DC CONVERTER TECHNICAL DATA

PAGE 2 OF 19

POWER STATION NAME: _________________________	DATE: _____________

| DATA DESCRIPTION | UNITS | DATA to RTL |  | DATA CAT. | GENERATING UNIT OR STATION DATA |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | CUSC Cont ract | CUSC App. Form |  | F.Yr. 0 | F.Yr. 1 | F.Yr. 2 | F.Yr. 3 | F.Yr. 4 | F.Yr. 5 | F.Yr. 6 |
| GENERATING STATION DEMANDS: |  |  |  |  |  |  |  |  |  |  |  |
| Demand associated with the Power Station supplied through the National Electricity Transmission System or the Generator's User System (PC.A.5.2) |  |  |  |  |  |  |  |  |  |  |  |
| - The maximum Demand that could occur. | MW MVAr | □ □ |  | DPD I DPD I |  |  |  |  |  |  |  |
| - Demand at specified time of annual peak half hour of National Electricity Transmission System Demand at Annual ACS Conditions. | MW MVAr | □ □ |  | DPD II DPD II |  |  |  |  |  |  |  |
| - Demand at specified time of annual minimum half-hour of National Electricity Transmission System Demand. | MW MVAr | □ □ |  | DPD II DPD II |  |  |  |  |  |  |  |
| (Additional Demand supplied through the unit transformers to be provided below) |  |  |  |  |  |  |  |  |  |  |  |
| INDIVIDUAL GENERATING UNIT (OR AS THE CASE MAY BE, SYNCHRONOUS POWER GENERATING MODULE OR CCGT MODULE) DATA |  |  |  |  | G1 | G2 | G3 | G4 | G5 | G6 | STN |
| Point of connection to the National Electricity Transmission System (or the Total System if embedded) of the Generating Unit or Synchronous Power Generating Module (other than a CCGT Unit) or the CCGT Module, as the case may be in terms of geographical and electrical location and system voltage (PC.A.3.4.1) | Text | □ | ■ | SPD |  |  |  |  |  |  |  |
| If the busbars at the Connection Point are normally run in separate sections identify the section to which the Generating Unit (other than a CCGT Unit) or Synchronous Power Generating Module or CCGT Module, as the case may be is connected (PC.A.3.1.5) | Section Number | □ | ■ | SPD |  |  |  |  |  |  |  |
| Type of Unit (steam, Gas Turbine Combined Cycle Gas Turbine Unit, tidal, wind, storage type etc.) (PC.A.3.2.2 (h), PC.A.3.4.4) |  | □ |  |  |  |  |  |  |  |  |  |

SCHEDULE 1 – POWER GENERATING MODULE, GENERATING UNIT (OR CCGT MODULE), POWER PARK MODULE, DC CONNECTED POWER PARK MODULE, HVDC SYSTEM AND DC CONVERTER TECHNICAL DATA

PAGE 3 OF 19

| INDIVIDUAL SYNCHRONOUS POWER GENERATING MODULE GENERATING UNIT (OR AS THE CASE MAY BE, CCGT MODULE) DATA |  |  |  |  | G1 | G2 | G3 | G4 | G5 | G6 | STN |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| A list of the Generating Units and CCGT Units within a Synchronous Power Generating Module or CCGT Module, identifying each CCGT Unit, and the Power Generating Module or CCGT Module of which it forms part, unambiguously. In the case of a Range CCGT Module, details of the possible configurations should also be submitted. (PC.A.3.2.2 (g)) |  | □ | ■ | SPD |  |  |  |  |  |  |  |

.

SCHEDULE 1 – POWER GENERATING MODULE, GENERATING UNIT (OR CCGT MODULE), POWER PARK MODULE, DC CONNECTED POWER PARK MODULE, HVDC SYSTEM AND DC CONVERTER TECHNICAL DATA

PAGE 4 OF 19

| DATA DESCRIPTION | UNITS | DATA to RTL |  | DATA CAT. | GENERATING UNIT (OR CCGT MODULE, AS THE CASE MAY BE) |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | CUSC Cont ract | CUSC App. Form |  | G1 | G2 | G3 | G4 | G5 | G6 | STN |
| Rated MVA (PC.A.3.3.1) | MVA | □ | ■ | SPD+ |  |  |  |  |  |  |  |
| Rated MW (PC.A.3.3.1) | MW | □ | ■ | SPD+ |  |  |  |  |  |  |  |
| Rated terminal voltage (PC.A.5.3.2.(a) & PC.A.5.4.2 (b)) | kV | □ |  | DPD I |  |  |  |  |  |  |  |
| *Performance Chart at Onshore Synchronous Generating Unit stator terminals (PC.A.3.2.2(f)(i)) * Performance Chart of the Offshore Synchronous Generating Unit at the Offshore Grid Entry Point (PC.A.3.2.2(f)(ii)) * Synchronous Generating Unit Performance Chart (PC.A.3.2.2(f)) * Power Generating Module Performance Chart of the Synchronous Power Generating Module (PC.A.3.2.2(f)) * Maximum terminal voltage set point (PC.A.5.3.2.(a) & PC.A.5.4.2 (b)) * Terminal voltage set point step resolution – if not continuous (PC.A.5.3.2.(a) & PC.A.5.4.2 (b)) | kV kV | □ □ |  | SPD DPD I DPD I | (see OC2 for specification) |  |  |  |  |  |  |
| *Output Usable (on a monthly basis) (PC.A.3.2.2(b)) | MW |  |  | SPD | (except in relation to CCGT Modules when required on a unit basis under the Grid Code, this data item may be supplied under Schedule 3) |  |  |  |  |  |  |
| Turbo-Generator inertia constant (for synchronous machines) (PC.A.5.3.2(a)) | MW secs /MVA | □ | ■ | SPD+ |  |  |  |  |  |  |  |
| Short circuit ratio (synchronous machines) (PC.A.5.3.2(a)) |  | □ | ■ | SPD+ |  |  |  |  |  |  |  |
| Normal auxiliary load supplied by the Generating Unit at rated MW output (PC.A.5.2.1) | MW MVAr | □ □ |  | DPD II DPD II |  |  |  |  |  |  |  |
| Rated field current at rated MW and MVAr output and at rated terminal voltage (PC.A.5.3.2 (a)) | A | □ |  | DPD II |  |  |  |  |  |  |  |
| Field current open circuit saturation curve (as derived from appropriate manufacturers' test certificates): (PC.A.5.3.2 (a)) 120% rated terminal volts 110% rated terminal volts 100% rated terminal volts 90% rated terminal volts 80% rated terminal volts 70% rated terminal volts 60% rated terminal volts 50% rated terminal volts | A A A A A A A A | □ □ □ □ □ □ □ □ |  | DPD II DPD II DPD II DPD II DPD II DPD II DPD II DPD II |  |  |  |  |  |  |  |
| IMPEDANCES: (Unsaturated) |  |  |  |  |  |  |  |  |  |  |  |
| Direct axis synchronous reactance (PC.A.5.3.2(a)) | % on MVA | □ |  | DPD I |  |  |  |  |  |  |  |
| Direct axis transient reactance (PC.A.3.3.1(a)& PC.A.5.3.2(a) | % on MVA | □ | ■ | SPD+ |  |  |  |  |  |  |  |
| Direct axis sub-transient reactance (PC.A.5.3.2(a)) | % on MVA | □ |  | DPD I |  |  |  |  |  |  |  |
| Quad axis synch reactance (PC.A.5.3.2(a)) | % on MVA | □ |  | DPD I |  |  |  |  |  |  |  |
| Quad axis sub-transient reactance (PC.A.5.3.2(a)) | % on MVA | □ |  | DPD I |  |  |  |  |  |  |  |
| Stator leakage reactance (PC.A.5.3.2(a)) | % on MVA | □ |  | DPD I |  |  |  |  |  |  |  |
| Armature winding direct current resistance. (PC.A.5.3.2(a)) | % on MVA | □ |  | DPD I |  |  |  |  |  |  |  |
| In Scotland, negative sequence resistance (PC.A.2.5.6 (a) (iv) | % on MVA | □ |  | DPD I |  |  |  |  |  |  |  |
| Note:- the above data item relating to armature winding direct-current resistance need only be provided by Generators in relation to Generating Units or Synchronous Generating Units within Power Generating Modules commissioned after 1st March 1996 and in cases where, for whatever reason, the Generator is aware of the value of the data item. |  |  |  |  |  |  |  |  |  |  |  |

SCHEDULE 1 – POWER GENERATING MODULE, GENERATING UNIT (OR CCGT MODULE), POWER PARK MODULE DC CONNECTED POWER PARK MODULE, HVDC SYSTEM AND DC CONVERTER TECHNICAL DATA

PAGE 5 OF 19

| DATA DESCRIPTION | UNITS | DATA to RTL |  | DATA CAT. | GENERATING UNIT OR STATION DATA |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | CUSC Contract | CUSC App. Form |  | G1 | G2 | G3 | G4 | G5 | G6 | STN |
| TIME CONSTANTS (Short-circuit and Unsaturated) |  |  |  |  |  |  |  |  |  |  |  |
| Direct axis transient time constant (PC.A.5.3.2(a)) | S | □ |  | DPD I |  |  |  |  |  |  |  |
| Direct axis sub-transient time constant (PC.A.5.3.2(a)) | S | □ |  | DPD I |  |  |  |  |  |  |  |
| Quadrature axis sub-transient time constant (PC.A.5.3.2(a)) | S | □ |  | DPD I |  |  |  |  |  |  |  |
| Stator time constant (PC.A.5.3.2(a)) | S | □ |  | DPD I |  |  |  |  |  |  |  |
| MECHANICAL PARAMETERS (PC.A.5.3.2(a)) |  |  |  |  |  |  |  |  |  |  |  |
| The number of turbine generator masses |  | □ |  | DPD II |  |  |  |  |  |  |  |
| Diagram showing the Inertia and parameters for each turbine generator mass for the complete drive train | Kgm2 | □ |  | DPD II DPD II |  |  |  |  |  |  |  |
| Diagram showing Stiffness constants and parameters between each turbine generator mass for the complete drive train | Nm/rad | □ |  | DPD II DPD II |  |  |  |  |  |  |  |
| Number of poles Relative power applied to different parts of the turbine | % | □ □ |  | DPD II DPD II |  |  |  |  |  |  |  |
| Torsional mode frequencies Modal damping decrement factors for the different mechanical modes | Hz | □ □ |  | DPD II DPD II |  |  |  |  |  |  |  |
| GENERATING UNIT STEP-UP TRANSFORMER |  |  |  |  |  |  |  |  |  |  |  |
| Rated MVA (PC.A.3.3.1 & PC.A.5.3.2) | MVA | □ | ■ | SPD+ |  |  |  |  |  |  |  |
| Voltage Ratio (PC.A.5.3.2) | - | □ |  | DPD I |  |  |  |  |  |  |  |
| Positive sequence reactance: (PC.A.5.3.2) |  |  |  |  |  |  |  |  |  |  |  |
| Max tap | % on MVA | □ | ■ | SPD+ |  |  |  |  |  |  |  |
| Min tap | % on MVA | □ | ■ | SPD+ |  |  |  |  |  |  |  |
| Nominal tap | % on MVA | □ | ■ | SPD+ |  |  |  |  |  |  |  |
| Positive sequence resistance: (PC.A.5.3.2) |  |  |  |  |  |  |  |  |  |  |  |
| Max tap | % on MVA | □ |  | DPD II |  |  |  |  |  |  |  |
| Min tap | % on MVA | □ |  | DPD II |  |  |  |  |  |  |  |
| Nominal tap | % on MVA | □ |  | DPD II |  |  |  |  |  |  |  |
| Zero phase sequence reactance (PC.A.5.3.2) | % on MVA | □ |  | DPD II |  |  |  |  |  |  |  |
| Tap change range (PC.A.5.3.2) | +% / -% | □ |  | DPD II |  |  |  |  |  |  |  |
| Tap change step size (PC.A.5.3.2) | % | □ |  | DPD II |  |  |  |  |  |  |  |
| Tap changer type: on-load or off-circuit (PC.A.5.3.2) | On/Off | □ |  | DPD II |  |  |  |  |  |  |  |

SCHEDULE 1 – POWER GENERATING MODULE, GENERATING UNIT (OR CCGT MODULE), POWER PARK MODULE, DC CONNECTED POWER PARK MODULE, HVDC SYSTEM AND DC CONVERTER TECHNICAL DATA

PAGE 6 OF 19

| DATA DESCRIPTION | UNITS |  | DATA to RTL |  | DATA CAT. | GENERATING UNIT OR STATION DATA |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | CUSC Contract | CUSC App. Form |  | G1 |  |  | G2 |  | G3 |  | G4 | G5 |  | G6 |  | STN |
| EXCITATION: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Note: The data items requested under Option 1 below may continue to be provided by Generators in relation to Generating Units on the System at 9 January 1995 (in this paragraph, the "relevant date") or they may provide the new data items set out under Option 2. Generators must supply the data as set out under Option 2 (and not those under Option 1) for Generating Unit and Synchronous Power Generating Unit excitation control systems commissioned after the relevant date, those Generating Unit or Synchronous Power Generating Unit excitation control systems recommissioned for any reason such as refurbishment after the relevant date and Generating Unit or Synchronous Power Generating Unit excitation control systems where, as a result of testing or other process, the Generator is aware of the data items listed under Option 2 in relation to that Generating Unit or Synchronous Power Generating Unit. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| # Option 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| DC gain of Excitation Loop (PC.A.5.3.2(c)) |  |  | ## □ |  | ## DPD II |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Max field voltage (PC.A.5.3.2(c)) |  | V | □ |  | DPD II |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Min field voltage (PC.A.5.3.2(c)) |  | V | □ |  | DPD II |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Rated field voltage (PC.A.5.3.2(c)) |  | V | □ |  | DPD II |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Max rate of change of field volts: (PC.A.5.3.2(c)) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Rising |  | V/Sec | □ |  | DPD II |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Falling |  | V/Sec | □ |  | DPD II |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Details of Excitation Loop (PC.A.5.3.2(c)) Described in block diagram form showing transfer functions of individual elements |  | Diagram | □ |  | DPD II | (please attach) |  |  |  |  |  |  |  |  |  |  |  |  |
| Dynamic characteristics of over- excitation limiter (PC.A.5.3.2(c)) |  |  | □ |  | DPD II |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Dynamic characteristics of under-excitation limiter (PC.A.5.3.2(c)) |  |  | □ |  | DPD II |  |  |  |  |  |  |  |  |  |  |  |  |  |
| # Option 2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Exciter category, e.g. Rotating Exciter, or Static Exciter etc (PC.A.5.3.2(c)) |  | Text | ## □ | ## ■ | ## SPD |  |  |  |  |  |  |  |  |  |  |  |  |  |
| ### Excitation System Nominal (PC.A.5.3.2(c)) Response VE |  | Sec-1 | □ |  | DPD II |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Rated Field Voltage (PC.A.5.3.2(c)) UfN |  | V | □ |  | DPD II |  |  |  |  |  |  |  |  |  |  |  |  |  |
| No-load Field Voltage (PC.A.5.3.2(c)) UfO |  | V | □ |  | DPD II |  |  |  |  |  |  |  |  |  |  |  |  |  |
| ### Excitation System On-Load (PC.A.5.3.2(c)) Positive Ceiling Voltage UpL+ |  | V | □ |  | DPD II |  |  |  |  |  |  |  |  |  |  |  |  |  |
| ### Excitation System No-Load (PC.A.5.3.2(c)) Positive Ceiling Voltage UpO+ |  | V | □ |  | DPD II |  |  |  |  |  |  |  |  |  |  |  |  |  |
| ### Excitation System No-Load (PC.A.5.3.2(c)) Negative Ceiling Voltage UpO- |  | V | □ |  | DPD II |  |  |  |  |  |  |  |  |  |  |  |  |  |
| ### Power System Stabiliser (PSS) fitted (PC.A.3.4.2) Stator Current Limit (PC.A.5.3.2(c)) |  | Yes/No A | □ □ | ■ | SPD DPD II |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Details of Excitation System (PC.A.5.3.2(c)) (including PSS if fitted) described in block diagram form showing transfer functions of individual elements. |  | Diagram | □ |  | ## DPD II |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Details of Over-excitation Limiter (PC.A.5.3.2(c)) described in block diagram form showing transfer functions of individual elements. |  | Diagram | □ |  | ## DPD II |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Details of Under-excitation Limiter (PC.A.5.3.2(c)) described in block diagram form showing transfer functions of individual elements. |  | Diagram | □ |  | ## DPD II |  |  |  |  |  |  |  |  |  |  |  |  |  |

SCHEDULE 1 – POWER GENERATING MODULE, GENERATING UNIT (OR CCGT MODULE), POWER PARK MODULE, DC CONNECTED POWER PARK MODULE, HVDC SYSTEM AND DC CONVERTER TECHNICAL DATA

PAGE 7 OF 19

| DATA DESCRIPTION | UNITS | DATA to RTL |  | DATA CAT. | GENERATING UNIT OR STATION DATA |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | CUSC Contract | CUSC App. Form |  | G1 | G2 |  | G3 |  | G4 |  |  | G5 |  | G6 |  | STN |
| GOVERNOR AND ASSOCIATED PRIME MOVER PARAMETERS |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Note: The data items requested under Option 1 below may continue to be provided by Generators in relation to Generating Units on the System at 9 January 1995 (in this paragraph, the "relevant date") or they may provide the new data items set out under Option 2. Generators must supply the data as set out under Option 2 (and not those under Option 1) for Generating Unit and Synchronous Power Generating Unit governor control systems commissioned after the relevant date, those Generating Unit and Synchronous Power Generating Unit governor control systems recommissioned for any reason such as refurbishment after the relevant date and Generating Unit and Synchronous Power Generating Unit governor control systems where, as a result of testing or other process, the Generator is aware of the data items listed under Option 2 in relation to that Generating Unit and Synchronous Power Generating Unit. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| # Option 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| GOVERNOR PARAMETERS (REHEAT UNITS) (PC.A.5.3.2(d) – Option 1(i)) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| HP Governor average gain | MW/Hz | □ |  | DPD II |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Speeder motor setting range | Hz | □ |  | DPD II |  |  |  |  |  |  |  |  |  |  |  |  |  |
| HP governor valve time constant | S | □ |  | DPD II |  |  |  |  |  |  |  |  |  |  |  |  |  |
| HP governor valve opening limits |  | □ |  | DPD II |  |  |  |  |  |  |  |  |  |  |  |  |  |
| HP governor valve rate limits |  | □ |  | DPD II |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Re-heat time constant (stored Active Energy in reheater) | S | □ |  | DPD II |  |  |  |  |  |  |  |  |  |  |  |  |  |
| IP governor average gain | MW/Hz | □ |  | DPD II |  |  |  |  |  |  |  |  |  |  |  |  |  |
| IP governor setting range | Hz | □ |  | DPD II |  |  |  |  |  |  |  |  |  |  |  |  |  |
| IP governor time constant | S | □ |  | DPD II |  |  |  |  |  |  |  |  |  |  |  |  |  |
| IP governor valve opening limits |  | □ |  | DPD II |  |  |  |  |  |  |  |  |  |  |  |  |  |
| IP governor valve rate limits |  | □ |  | DPD II |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Details of acceleration sensitive |  | □ |  | DPD II | (please attach) |  |  |  |  |  |  |  |  |  |  |  |  |
| elements HP & IP in governor loop |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Governor block diagram showing |  | □ |  | DPD II | (please attach) |  |  |  |  |  |  |  |  |  |  |  |  |
| transfer functions of individual elements |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| GOVERNOR (Non-reheat steam and Gas |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Turbines) (PC.A.5.3.2(d) – Option 1(ii)) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Governor average gain | MW/Hz | □ |  | DPD II |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Speeder motor setting range |  | □ |  | DPD II |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Time constant of steam or fuel governor valve | S | □ |  | DPD II |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Governor valve opening limits |  | □ |  | DPD II |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Governor valve rate limits |  | □ |  | DPD II |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Time constant of turbine | S | □ |  | DPD II |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Governor block diagram |  | □ |  | DPD II | (please attach) |  |  |  |  |  |  |  |  |  |  |  |  |

SCHEDULE 1 – POWER GENERATING MODULE, GENERATING UNIT (OR CCGT MODULE), POWER PARK MODULE DC CONNECTED POWER PARK MODULE, HVDC SYSTEM AND DC CONVERTER TECHNICAL DATA

PAGE 8 OF 19

| DATA DESCRIPTION | UNITS | DATA to RTL |  | DATA CAT. | GENERATING UNIT OR STATION DATA |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | CUSC Contract | CUSC App. Form |  | G1 | G2 | G3 | G4 | G5 | G6 | STN |
| (PC.A.5.3.2(d) – Option 1(iii)) |  |  |  |  |  |  |  |  |  |  |  |
| BOILER & STEAM TURBINE DATA* |  |  |  |  |  |  |  |  |  |  |  |
| Boiler time constant (Stored Active Energy) | S |  |  | ### DPD II |  |  |  |  |  |  |  |
| HP turbine response ratio: (Proportion of Primary Response arising from HP turbine) | % |  |  | ### DPD II |  |  |  |  |  |  |  |
| HP turbine response ratio: (Proportion of High Frequency Response arising from HP turbine) | % |  |  | DPD II |  |  |  |  |  |  |  |
|  | End of Option 1 |  |  |  |  |  |  |  |  |  |  |
| # Option 2 |  |  |  |  |  |  |  |  |  |  |  |
| All Generating Units and Synchronous Power Generating Units |  |  |  |  |  |  |  |  |  |  |  |
| Governor Block Diagram showing transfer function of individual elements including acceleration sensitive elements |  | ### □ |  | ### DPD II |  |  |  |  |  |  |  |
| Governor Time Constant (PC.A.5.3.2(d) – Option 2(i)) | Sec | ### □ |  | ### DPD II |  |  |  |  |  |  |  |
| Governor Deadband (PC.A.5.3.2(d) – Option 2(i)) - Maximum Setting - Normal Setting - Minimum Setting | Hz Hz Hz |  |  | ### DPD II DPD II DPD II |  |  |  |  |  |  |  |
| Speeder Motor Setting Range (PC.A.5.3.2(d) – Option 2(i)) | % | ### □ |  | ### DPD II |  |  |  |  |  |  |  |
| Average Gain (PC.A.5.3.2(d) – Option 2(i)) | MW/Hz | ### □ |  | ### DPD II |  |  |  |  |  |  |  |
| Steam Units |  |  |  |  |  |  |  |  |  |  |  |
| (PC.A.5.3.2(d) – Option 2(ii)) |  |  |  |  |  |  |  |  |  |  |  |
| HP Valve Time Constant | sec | □ |  | DPD II |  |  |  |  |  |  |  |
| HP Valve Opening Limits | % | □ |  | DPD II |  |  |  |  |  |  |  |
| HP Valve Opening Rate Limits | %/sec | □ |  | DPD II |  |  |  |  |  |  |  |
| HP Valve Closing Rate Limits | %/sec | □ |  | DPD II |  |  |  |  |  |  |  |
| HP Turbine Time Constant | sec | □ |  | DPD II |  |  |  |  |  |  |  |
| (PC.A.5.3.2(d) – Option 2(ii)) |  |  |  |  |  |  |  |  |  |  |  |
| IP Valve Time Constant | sec | □ |  | DPD II |  |  |  |  |  |  |  |
| IP Valve Opening Limits | % | □ |  | DPD II |  |  |  |  |  |  |  |
| IP Valve Opening Rate Limits | %/sec | □ |  | DPD II |  |  |  |  |  |  |  |
| IP Valve Closing Rate Limits | %/sec | □ |  | DPD II |  |  |  |  |  |  |  |
| IP Turbine Time Constant | sec | □ |  | DPD II |  |  |  |  |  |  |  |
| (PC.A.5.3.2(d) – Option 2(ii)) |  |  |  |  |  |  |  |  |  |  |  |
| LP Valve Time Constant | sec | □ |  | DPD II |  |  |  |  |  |  |  |
| LP Valve Opening Limits | % | □ |  | DPD II |  |  |  |  |  |  |  |
| LP Valve Opening Rate Limits | %/sec | □ |  | DPD II |  |  |  |  |  |  |  |
| LP Valve Closing Rate Limits | %/sec | □ |  | DPD II |  |  |  |  |  |  |  |
| LP Turbine Time Constant | sec | □ |  | DPD II |  |  |  |  |  |  |  |
| (PC.A.5.3.2(d) – Option 2(ii)) |  |  |  |  |  |  |  |  |  |  |  |
| Reheater Time Constant | sec |  |  | DPD II |  |  |  |  |  |  |  |
| Boiler Time Constant | sec |  |  | DPD II |  |  |  |  |  |  |  |
| HP Power Fraction | % |  |  | DPD II |  |  |  |  |  |  |  |
| IP Power Fraction | % |  |  | DPD II |  |  |  |  |  |  |  |

#	Where the generating unit or  synchronous power generating unit governor does not have a selectable deadband facility, then the actual value of the deadband need only be provided.

SCHEDULE 1 – POWER GENERATING MODULE, GENERATING UNIT (OR CCGT MODULE), POWER PARK MODULE, DC CONNECTED POWER PARK MODULE, HVDC SYSTEM AND DC CONVERTER TECHNICAL DATA

PAGE 9 OF 19

| DATA DESCRIPTION | UNITS | DATA to RTL |  | DATA CAT. | GENERATING UNIT OR STATION DATA |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | CUSC Contract | CUSC App. Form |  | G1 | G2 | G3 | G4 | G5 | G6 | STN |
| Gas Turbine Units |  |  |  |  |  |  |  |  |  |  |  |
| (PC.A.5.3.2(d) – Option 2(iii)) |  |  |  |  |  |  |  |  |  |  |  |
| Inlet Guide Vane Time Constant | sec | □ |  | DPD II |  |  |  |  |  |  |  |
| Inlet Guide Vane Opening Limits | % | □ |  | DPD II |  |  |  |  |  |  |  |
| Inlet Guide Vane Opening Rate Limits | %/sec | □ |  | DPD II |  |  |  |  |  |  |  |
| Inlet Guide Vane Closing Rate Limits | %/sec | □ |  | DPD II |  |  |  |  |  |  |  |
| (PC.A.5.3.2(d) – Option 2(iii)) |  |  |  |  |  |  |  |  |  |  |  |
| Fuel Valve Time Constant | sec | □ |  | DPD II |  |  |  |  |  |  |  |
| Fuel Valve Opening Limits | % | □ |  | DPD II |  |  |  |  |  |  |  |
| Fuel Valve Opening Rate Limits | %/sec | □ |  | DPD II |  |  |  |  |  |  |  |
| Fuel Valve Closing Rate Limits | %/sec | □ |  | DPD II |  |  |  |  |  |  |  |
| (PC.A.5.3.2(d) – Option 2(iii)) |  |  |  |  |  |  |  |  |  |  |  |
| Waste Heat Recovery Boiler Time Constant |  |  |  |  |  |  |  |  |  |  |  |
| Hydro Generating Units |  |  |  |  |  |  |  |  |  |  |  |
| (PC.A.5.3.2(d) – Option 2(iv)) |  |  |  |  |  |  |  |  |  |  |  |
| Guide Vane Actuator Time Constant | sec | □ |  | DPD II |  |  |  |  |  |  |  |
| Guide Vane Opening Limits | % | □ |  | DPD II |  |  |  |  |  |  |  |
| Guide Vane Opening Rate Limits | %/sec | □ |  | DPD II |  |  |  |  |  |  |  |
| Guide Vane Closing Rate Limits | %/sec | □ |  | DPD II |  |  |  |  |  |  |  |
| Water Time Constant Synchronous Electricity Storage Units and Modules (PC.A.5.3.2(d) – Option 2(v) Valve Actuator Time Constant Valve Opening Limits Valve Opening Rate Limits Valve Closing Rate Limits For Synchronous Electricity Storage Modules which are derived from compressed air energy storage systems the above data should be provided. For other Synchronous Electricity Storage Modules data should be supplied as required by The Company in accordance with PC.A.7. | sec sec % %/sec %/sec | □ □ □ □ □ |  | DPD II DPD II DPD II DPD II DPD II |  |  |  |  |  |  |  |
|  | End of Option 2 |  |  |  |  |  |  |  |  |  |  |
| UNIT CONTROL OPTIONS* |  |  |  |  |  |  |  |  |  |  |  |
| (PC.A.5.3.2(e) |  |  |  |  |  |  |  |  |  |  |  |
| Maximum droop | % |  |  | DPD II |  |  |  |  |  |  |  |
| Normal droop | % | □ |  | DPD II |  |  |  |  |  |  |  |
| Minimum droop | % |  |  | DPD II |  |  |  |  |  |  |  |
| Maximum Governor Deadband Normal Governor Deadband Minimum Governor Deadband |  |  |  | DPD II DPD II |  |  |  |  |  |  |  |
| Maximum Frequency Response Deadband1 | ±Hz |  |  | DPD II |  |  |  |  |  |  |  |
| Normal Frequency Response Deadband1 | ±Hz |  |  | DPD II |  |  |  |  |  |  |  |
| Minimum Frequency Response Deadband1 Maximum Frequency Response Insensitivity1 Normal Frequency Response Insensitivity1 Minimum Frequency Response Insensitivity1 | ±Hz ±Hz ±Hz ±Hz |  |  | DPD II DPDII DPDII DPDII |  |  |  |  |  |  |  |
|  | ±Hz ±Hz ±Hz |  |  |  |  |  |  |  |  |  |  |
| Frequency settings between which Unit Load Controller droop applies: |  |  |  |  |  |  |  |  |  |  |  |
| Maximum | Hz |  |  | DPD II |  |  |  |  |  |  |  |
| Normal | Hz |  |  | DPD II |  |  |  |  |  |  |  |
| Minimum | Hz |  |  | DPD II |  |  |  |  |  |  |  |
| Sustained response normally selected | Yes/No |  |  | DPD II |  |  |  |  |  |  |  |
| 1 Data required only in respect of Large Power Stations comprising Type C and Type D Power Generating Modules owned and operated by EU Code Generators. |  |  |  |  |  |  |  |  |  |  |  |

SCHEDULE 1 – POWER GENERATING MODULE, GENERATING UNIT (OR CCGT MODULE), POWER PARK MODULE, DC CONNECTED POWER PARK MODULE, HVDC SYSTEM AND DC CONVERTER TECHNICAL DATA

PAGE 10 OF 19

| DATA DESCRIPTION | UNITS | DATA to RTL |  | DATA CAT. | POWER PARK UNIT (OR POWER PARK MODULE, AS THE CASE MAY BE) |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | CUSC Contract | CUSC App. Form |  | G1 | G2 | G3 | G4 | G5 | G6 | STN |  |
| Power Park Module Rated MVA (PC.A.3.3.1(a)) | MVA | □ | ■ | SPD+ |  |  |  |  |  |  |  |  |
| Power Park Module Rated MW (PC.A.3.3.1(a)) | MW | □ | ■ | SPD+ |  |  |  |  |  |  |  |  |
| *Performance Chart of a Power Park Module at the connection point (PC.A.3.2.2(f)(ii)) |  |  |  | SPD | (see OC2 for specification) |  |  |  |  |  |  |  |
| *Output Usable (on a monthly basis) (PC.A.3.2.2(b)) | MW |  |  | SPD | (except in relation to CCGT Modules when required on a unit basis under the Grid Code, this data item may be supplied under Schedule 3) |  |  |  |  |  |  |  |
| Number & Type of Power Park Units within each Power Park Module (PC.A.3.2.2(k)) Number & Type of Offshore Power Park Units within each Offshore Power Park String and the number of Offshore Power Park Strings and connection point within each Offshore Power Park Module (PC.A.3.2.2.(k)) |  | □ |  | SPD SPD |  |  |  |  |  |  |  |  |
| In the case where an appropriate Manufacturer’s Data & Performance Report is registered with The Company then subject to The Company’s agreement, the report reference may be given as an alternative to completion of the following sections of this Schedule 1 to the end of page 11 with the exception of the sections marked thus # below. | Reference the Manufacturer’s Data & Performance Report |  |  | SPD |  |  |  |  |  |  |  |  |
| Power Park Unit Model (including Non Synchronous Electricity Storage Units) - A validated mathematical model in accordance with PC.5.4.2 (a) | Transfer function block diagram and algebraic equations, simulation and measured test results | □ |  | DPD II |  |  |  |  |  |  |  |  |

SCHEDULE 1 – POWER GENERATING MODULE, GENERATING UNIT (OR CCGT MODULE), POWER PARK MODULE DC CONNECTED POWER PARK MODULE, HVDC SYSTEM AND DC CONVERTER TECHNICAL DATA

PAGE 11 OF 19

| DATA DESCRIPTION | UNITS | DATA to RTL |  | DATA CAT. | POWER PARK UNIT (OR POWER PARK MODULE, AS THE CASE MAY BE) |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | CUSC Contract | CUSC App. Form |  | G1 | G2 | G3 | G4 | G5 | G6 | STN |
| Power Park Unit Data (where applicable) |  |  |  |  |  |  |  |  |  |  |  |
| Rated MVA (PC.A.3.3.1(e)) | MVA | □ | ■ | SPD+ |  |  |  |  |  |  |  |
| Rated MW (PC.A.3.3.1(e)) | MW | □ | ■ | SPD+ |  |  |  |  |  |  |  |
| Rated terminal voltage (PC.A.3.3.1(e)) | V | □ | ■ | SPD+ |  |  |  |  |  |  |  |
| Site minimum air density (PC.A.5.4.2(b)) | kg/m3 | □ | ■ | DPD II |  |  |  |  |  |  |  |
| Site maximum air density | kg/m3 | □ | ■ | DPD II |  |  |  |  |  |  |  |
| Site average air density | kg/m3 | □ | ■ | DPD II |  |  |  |  |  |  |  |
| Year for which air density data is submitted |  | □ | ■ | DPD II |  |  |  |  |  |  |  |
| Number of pole pairs |  | □ |  | DPD II |  |  |  |  |  |  |  |
| Blade swept area | m2 | □ |  | DPD II |  |  |  |  |  |  |  |
| Gear Box Ratio |  | □ |  | DPD II |  |  |  |  |  |  |  |
| Stator Resistance (PC.A.5.4.2(b)) | % on MVA | □ | ■ | SPD+ |  |  |  |  |  |  |  |
| Stator Reactance (PC.A.3.3.1(e)) | % on MVA | □ | ■ | SPD+ |  |  |  |  |  |  |  |
| Magnetising Reactance (PC.A.3.3.1(e)) | % on MVA | □ | ■ | SPD+ |  |  |  |  |  |  |  |
| Rotor Resistance (at starting). (PC.A.5.4.2(b)) | % on MVA | □ |  | DPD II |  |  |  |  |  |  |  |
| Rotor Resistance (at rated running) (PC.A.3.3.1(e)) | % on MVA | □ | ■ | SPD+ |  |  |  |  |  |  |  |
| Rotor Reactance (at starting). (PC.A.5.4.2(b)) | % on MVA | □ |  | DPD II |  |  |  |  |  |  |  |
| Rotor Reactance (at rated running) (PC.A.3.3.1(e)) | % on MVA | □ | ■ | SPD |  |  |  |  |  |  |  |
| Equivalent inertia constant of the first mass (e.g. wind turbine rotor and blades) at minimum speed (PC.A.5.4.2(b)) | MW secs /MVA | □ | ■ | SPD+ |  |  |  |  |  |  |  |
| Equivalent inertia constant of the first mass (e.g. wind turbine rotor and blades) at synchronous speed (PC.A.5.4.2(b)) | MW secs /MVA | □ | ■ | SPD+ |  |  |  |  |  |  |  |
| Equivalent inertia constant of the first mass (e.g. wind turbine rotor and blades) at rated speed (PC.A.5.4.2(b)) | MW secs /MVA | □ | ■ | SPD+ |  |  |  |  |  |  |  |
| Equivalent inertia constant of the second mass (e.g. generator rotor) at minimum speed (PC.A.5.4.2(b)) | MW secs /MVA | □ | ■ | SPD+ |  |  |  |  |  |  |  |
| Equivalent inertia constant of the second mass (e.g. generator rotor) at synchronous speed (PC.A.5.4.2(b)) | MW secs /MVA | □ | ■ | SPD+ |  |  |  |  |  |  |  |
| Equivalent inertia constant of the second mass (e.g. generator rotor) at rated speed (PC.A.5.4.2(b)) | MW secs /MVA | □ | ■ | SPD+ |  |  |  |  |  |  |  |
| Equivalent shaft stiffness between the two masses (PC.A.5.4.2(b)) | Nm / electrical radian | □ | ■ | SPD+ |  |  |  |  |  |  |  |

SCHEDULE 1 – POWER GENERATING MODULE, GENERATING UNIT (OR CCGT MODULE), POWER PARK MODULE, DC CONNECTED POWER PARK MODULE, HVDC SYSTEM AND DC CONVERTER TECHNICAL DATA

PAGE 12 OF 19

| DATA DESCRIPTION | UNITS | DATA to RTL |  | DATA CAT. | POWER PARK UNIT (OR POWER PARK MODULE, AS THE CASE MAY BE) |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | CUSC Contract | CUSC App. Form |  | G1 | G2 | G3 | G4 |  | G5 |  | G6 |  | STN |
| Minimum generator rotor speed (Doubly Fed Induction Generators) (PC.A.3.3.1(e)) | RPM | □ | ■ | SPD+ |  |  |  |  |  |  |  |  |  |  |
| Maximum generator rotor speed (Doubly Fed Induction Generators) (PC.A.3.3.1(e)) | RPM | □ | ■ | SPD+ |  |  |  |  |  |  |  |  |  |  |
| The optimum generator rotor speed versus wind speed (PC.A.5.4.2(b)) | tabular format | □ |  | DPD II |  |  |  |  |  |  |  |  |  |  |
| Power Converter Rating (Doubly Fed Induction Generators) (PC.A.5.4.2(b)) | MVA | □ | ■ | DPD II |  |  |  |  |  |  |  |  |  |  |
| The rotor power coefficient (Cp) versus tip speed ratio () curves for a range of blade angles (where applicable) (PC.A.5.4.2(b)) | Diagram + tabular format | □ |  | DPD II |  |  |  |  |  |  |  |  |  |  |
| # The electrical power output versus generator rotor speed for a range of wind speeds over the entire operating range of the Power Park Unit. (PC.A.5.4.2(b)) | Diagram + tabular format | □ |  | DPD II |  |  |  |  |  |  |  |  |  |  |
| The blade angle versus wind speed curve (PC.A.5.4.2(b)) | Diagram + tabular format | □ |  | DPD II |  |  |  |  |  |  |  |  |  |  |
| The electrical power output versus wind speed over the entire operating range of the Power Park Unit. (PC.A.5.4.2(b)) | Diagram + tabular format | □ |  | DPD II |  |  |  |  |  |  |  |  |  |  |
| Transfer function block diagram, parameters and description of the operation of the power electronic converter including fault ride though capability (where applicable). (PC.A.5.4.2(b)) | Diagram | □ |  | DPD II |  |  |  |  |  |  |  |  |  |  |
| For a Power Park Unit consisting of a synchronous machine in combination with a back to back DC Converter or HVDC Converter, or for a Power Park Unit not driven by a wind turbine, the data to be supplied shall be agreed with The Company in accordance with PC.A.7. (PC.A.5.4.2(b)) |  | □ |  |  |  |  |  |  |  |  |  |  |  |  |

SCHEDULE 1 – POWER GENERATING MODULE, GENERATING UNIT (OR CCGT MODULE), POWER PARK MODULE, DC CONNECTED POWER PARK MODULE, HVDC SYSTEM AND DC CONVERTER TECHNICAL DATA

PAGE 13 OF 19

| DATA DESCRIPTION | UNITS | DATA to RTL |  |  | DATA CAT. | POWER PARK UNIT (OR POWER PARK MODULE, AS THE CASE MAY BE) |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | CUSC Contract |  | CUSC App. Form |  | G1 | G2 | G3 | G4 | G5 | G6 | STN |
| Torque / Speed and blade angle control systems and parameters (PC.A.5.4.2(c)) For the Power Park Unit, details of the torque / speed controller and blade angle controller in the case of a wind turbine and power limitation functions (where applicable) described in block diagram form showing transfer functions and parameters of individual elements | Diagram | □ |  |  | DPD II |  |  |  |  |  |  |  |
| # Voltage/Reactive Power/Power Factor control system parameters (PC.A.5.4.2(d)) # For the Power Park Unit and Power Park Module details of Voltage/Reactive Power/Power Factor controller (and PSS if fitted) described in block diagram form including parameters showing transfer functions of individual elements. | Diagram | □ |  |  | DPD II |  |  |  |  |  |  |  |
| # Frequency control system parameters (PC.A.5.4.2(e)) # For the Power Park Unit and Power Park Module details of the Frequency controller described in block diagram form showing transfer functions and parameters of individual elements. | Diagram | □ |  |  | DPD II |  |  |  |  |  |  |  |
| As an alternative to PC.A.5.4.2 (a), (b), (c), (d), (e) and (f), is the submission of a single complete model that consists of the full information required under PC.A.5.4.2 (a), (b), (c), (d) (e) and (f) provided that all the information required under PC.A.5.4.2 (a), b), (c), (d), (e) and (f) individually is clearly identifiable. (PC.A.5.4.2(g)) | Diagram | □ |  |  | DPD II |  |  |  |  |  |  |  |
| # Harmonic Assessment Information (PC.A.5.4.2(h)) (as defined in IEC 61400-21 (2001)) for each Power Park Unit:- |  |  |  |  |  |  |  |  |  |  |  |  |
| # Flicker coefficient for continuous operation |  | □ |  |  | DPD I |  |  |  |  |  |  |  |
| # Flicker step factor |  | □ |  |  | DPD I |  |  |  |  |  |  |  |
| # Number of switching operations in a 10 minute window |  | □ |  |  | DPD I |  |  |  |  |  |  |  |
| # Number of switching operations in a 2 hour window |  | □ |  |  | DPD I |  |  |  |  |  |  |  |
| # Voltage change factor |  | □ |  |  | DPD I |  |  |  |  |  |  |  |
| # Current Injection at each harmonic for each Power Park Unit and for each Power Park Module | Tabular format | □ |  |  | DPD I |  |  |  |  |  |  |  |
| Note:- Generators who own or operate DC Connected Power Park Modules shall supply all data for their DC Connected Power Park Modules as applicable to Power Park Modules. |  |  |  |  |  |  |  |  |  |  |  |  |

SCHEDULE 1 – POWER GENERATING MODULE, GENERATING UNIT (OR CCGT MODULE), POWER PARK MODULE, DC CONNECTED POWER PARK MODULE, HVDC SYSTEM AND DC CONVERTER TECHNICAL DATA

PAGE 14 OF 19

HVDC SYSTEM AND DC CONVERTER STATION TECHNICAL DATA

HVDC SYSTEM OR DC CONVERTER STATION NAME					DATE:___________

| Data Description | Units | DATA to RTL |  | Data Category | DC Converter Station Data |
| --- | --- | --- | --- | --- | --- |
| (PC.A.4) |  | CUSC Contract | CUSC App. Form |  |  |
| HVDC SYSTEM AND DC CONVERTER STATION DEMANDS: Demand supplied through Station Transformers associated with the DC Converter Station and HVDC System [PC.A.4.1] - Demand with all DC Converters and HVDC Converters within and HVDc System operating at Rated MW import. - Demand with all DC Converters and HVDC Converters within an HVDC System operating at Rated MW export. Additional Demand associated with the DC Converter Station or HVDC System supplied through the National Electricity Transmission System. [PC.A.4.1] - The maximum Demand that could occur. - Demand at specified time of annual peak half hour of The Company Demand at Annual ACS Conditions. - Demand at specified time of annual minimum half-hour of The Company Demand. DC CONVERTER STATION AND HVDC SYSTEM DATA Number of poles, i.e. number of DC Converters or HVDC Converters within the HVDC System Pole arrangement (e.g. monopole or bipole) Details of each viable operating configuration Configuration 1 Configuration 2 Configuration 3 Configuration 4 Configuration 5 Configuration 6 Remote ac connection arrangement | MW MVAr MW MVAr MW MVAr MW MVAr MW MVAr Text Text Diagram Diagram Diagram Diagram Diagram Diagram Diagram | □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ | ■ ■ ■ ■ ■ ■ ■ ■ ■ | DPD II DPD II DPD II DPD II DPD II DPD II DPD II DPD II DPD II DPD II SPD+ SPD+ SPD+ SPD |  |

SCHEDULE 1 – POWER PARK MODULE, GENERATING UNIT (OR CCGT MODULE), POWER PARK MODULE, DC CONNECTED POWER PARK MODULE, HVDC SYSTEM AND DC CONVERTER TECHNICAL DATA

PAGE 15 OF 19

| Data Description | Units | DATA to RTL |  | Data Category | Operating Configuration |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | CUSC Contract | CUSC App. Form |  | 1 | 2 | 3 | 4 | 5 | 6 |
| DC CONVERTER STATION AND HVDC SYSTEM DATA (PC.A.3.3.1d) DC Converter or HVDC Converter Type (e.g. current or Voltage source) Point of connection to the National Electricity Transmission System (or the Total System if Embedded) of the DC Converter Station or HVDC System configuration in terms of geographical and electrical location and system voltage If the busbars at the Connection Point are normally run in separate sections identify the section to which the DC Converter Station or HVDC System configuration is connected Rated MW import per pole [PC.A.3.3.1] Rated MW export per pole [PC.A.3.3.1] | Text Text Section Number MW MW | □ □ □ □ □ | ■ ■ ■ ■ ■ | SPD SPD SPD SPD + SPD + |  |  |  |  |  |  |
| ACTIVE POWER TRANSFER CAPABILITY (PC.A.3.2.2) Registered Capacity Registered Import Capacity Minimum Generation Minimum Import Capacity Maximum HVDC Active Power Transmission Capacity Minimum Active Power Transmission Capacity Import MW available in excess of Registered Import Capacity and Maximum Active Power Transmission Capacity Time duration for which MW in excess of Registered Import Capacity is available Export MW available in excess of Registered Capacity and Maximum Active Power Transmission Capacity. Time duration for which MW in excess of Registered Capacity is available | MW MW MW MW MW MW MW Min MW Min | □ □ □ □ □ □ □ □ □ □ | ■ ■ ■ ■ | SPD SPD SPD SPD SPD SPD SPD SPD |  |  |  |  |  |  |

SCHEDULE 1 –POWER GENERATING MODULE, GENERATING UNIT (OR CCGT MODULE), POWER PARK MODULE, DC CONNECTED POWER PARK MODULE, HVDC SYSTEM AND DC CONVERTER TECHNICAL DATA

PAGE 16 OF 19

| Data Description | Units | DATA to RTL |  | Data Category | Operating Configuration |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | CUSC Contract | CUSC App. Form |  | 1 | 2 | 3 | 4 | 5 | 6 |
| DC CONVERTER AND HVDC CONVERTER TRANSFORMER [PC.A.5.4.3.1] Rated MVA Winding arrangement Nominal primary voltage Nominal secondary (converter-side) voltage(s) Positive sequence reactance Maximum tap Nominal tap Minimum tap Positive sequence resistance Maximum tap Nominal tap Minimum tap Zero phase sequence reactance Tap change range Number of steps | MVA kV kV % on MVA % on MVA % on MVA % on MVA % on MVA % on MVA % on MVA +% / -% | □ □ □ □ □ □ □ □ □ □ □ □ |  | DPD II DPD II DPD II DPD II DPD II DPD II DPD II DPD II DPD II DPD II DPD II DPD II |  |  |  |  |  |  |

SCHEDULE 1 – POWER GENERATING MODULE, GENERATING UNIT (OR CCGT MODULE), DC CONNECTED POWER PARK MODULE, HVDC SYSTEM, POWER PARK MODULE AND DC CONVERTER TECHNICAL DATA

PAGE 17 OF 19

| Data Description | Units | DATA to RTL |  | Data Category | Operating configuration |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | CUSC Contract | CUSC App. Form |  | 1 | 2 | 3 | 4 | 5 | 6 |
| DC NETWORK [PC.A.5.4.3.1 (c)] Rated DC voltage per pole Rated DC current per pole Details of the DC Network described in diagram form including resistance, inductance and capacitance of all DC cables and/or DC lines. Details of any line reactors (including line reactor resistance), line capacitors, DC filters, earthing electrodes and other conductors that form part of the DC Network should be shown. | kV A Diagram | □ □ □ |  | DPD II DPD II DPD II |  |  |  |  |  |  |
| DC CONVERTER STATION AND HVDC SYSTEM AC HARMONIC FILTER AND REACTIVE COMPENSATION EQUIPMENT [PC.A.5.4.3.1 (d)] For all switched reactive compensation equipment Total number of AC filter banks Diagram of filter connections Type of equipment (e.g. fixed or variable) Capacitive rating; or Inductive rating; or Operating range Reactive Power capability as a function of various MW transfer levels | Diagram Text Diagram Text MVAr MVAr MVAr Table | □ □ □ □ □ □ □ □ | ■ ■ ■ | DPD II DPD II DPD II DPD II DPD II DPD II DPD II DPD II |  |  |  |  |  |  |

SCHEDULE 1 – POWER GENERATING MODULE, GENERATING UNIT (OR CCGT MODULE), POWER PARK MODULE, DC CONNECTED POWER PARK MODULE, HVDC SYSTEM AND DC CONVERTER TECHNICAL DATA

PAGE 18 OF 19

| Data Description | Units | DATA to RTL |  | Data Category | Operating configuration |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | CUSC Contract | CUSC App. Form |  | 1 | 2 | 3 | 4 | 5 | 6 |
| CONTROL SYSTEMS [PC.A.5.4.3.2] Static VDC – PDC (DC voltage – DC power) or Static VDC – IDC (DC voltage – DC current) characteristic (as appropriate) when operating as –Rectifier –Inverter Details of rectifier mode control system, in block diagram form together with parameters showing transfer functions of individual elements. Details of inverter mode control system, in block diagram form showing transfer functions of individual elements including parameters. Details of converter transformer tap changer control system in block diagram form showing transfer functions of individual elements including parameters. (Only required for DC Converters and HVDC Systems connected to the National Electricity Transmission System.) Details of AC filter and reactive compensation equipment control systems in block diagram form showing transfer functions of individual elements including parameters. (Only required for DC Converters and HVDC Systems connected to the National Electricity Transmission System.) Details of any frequency and/or load control systems in block diagram form showing transfer functions of individual elements including parameters. Details of any large or small signal modulating controls, such as power oscillation damping controls or sub-synchronous oscillation damping controls, that have not been submitted as part of the above control system data. Details of HVDC Converter unit models and/or control systems in block diagram form showing transfer functions of individual elements including parameters. Details of AC component models and/or control systems in block diagram form showing transfer functions of individual elements including parameters. Details of DC Grid models and/or control systems in block diagram form showing transfer functions of individual elements including parameters. Details of Voltage and power controller and/or control systems in block diagram form showing transfer functions of individual elements including parameters. Details of Special control features if applicable (e.g., power oscillation damping (POD) function, subsynchronous torsional interaction (SSTI) control and/or control systems in block diagram form showing transfer functions of individual elements including parameters. Details of Multi terminal control, if applicable and/or control systems in block diagram form showing transfer functions of individual elements including parameters. Details of HVDC System protection models as agreed between The Company the HVDC System Owner and/or control systems in block diagram form showing transfer functions of individual elements including parameters. Transfer block diagram representation of the reactive power control at converter ends for a voltage source converter Transfer block diagram representation of the reactive power control at converter ends for a voltage source converter. | Diagram Diagram Diagram Diagram Diagram Diagram Diagram Diagram Diagram Diagram Diagram Diagram Diagram Diagram Diagram | □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ |  | DPD II DPD II DPD II DPD II DPD II DPD II DPD II DPD II DPD II DPD II DPD II DPD II DPD II DPD II DPD II |  |  |  |  |  |  |

SCHEDULE 1 – POWER GENERATING MODULE, GENERATING UNIT (OR CCGT MODULE), POWER PARK MODULE, DC CONNECTED POWER PARK MODULE, HVDC SYSTEM AND DC CONVERTER TECHNICAL DATA

PAGE 19 OF 19

| Data Description | Units | DATA to RTL |  | Data Category | Operating configuration |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | CUSC Contract | CUSC App. Form |  | 1 | 2 | 3 | 4 | 5 | 6 |
| LOADING PARAMETERS [PC.A.5.4.3.3] MW Export Nominal loading rate Maximum (emergency) loading rate MW Import Nominal loading rate Maximum (emergency) loading rate Maximum recovery time, to 90% of pre-fault loading, following an AC system fault or severe voltage depression. Maximum recovery time, to 90% of pre-fault loading, following a transient DC Network fault. | MW/s MW/s MW/s MW/s s s | □ □ |  | DPD I DPD I DPD I DPD I DPD II DPD II |  |  |  |  |  |  |

NOTE:	Users are referred to Schedules 5 & 14 which set down data required for all Users directly connected to the National Electricity Transmission System, including Power Stations.  Generators undertaking OTSDUW Arrangements and are utilising an OTSDUW DC Converter are referred to Schedule 18.

SCHEDULE 2 - GENERATION PLANNING PARAMETERS

PAGE 1 OF 3

This schedule contains the Genset Generation Planning Parameters required by The Company to facilitate studies in Operational Planning timescales.

For a Generating Unit including those within a Power Generating Module (other than a Power Park Unit) at a Large Power Station, the information is to be submitted on a unit basis and for a CCGT Module or Power Park Module at a Large Power Station the information is to be submitted on a module basis, unless otherwise stated.

Where references to CCGT Modules or Power Park Modules at a Large Power Station are made, the columns "G1" etc should be amended to read "M1" etc, as appropriate.

6Contractors, data only needs to be provided by a Restoration Contractor where they are not a CUSC Party and the data has not been submitted.  In this case the data to be submitted would be would be pursant to the the terms of the Anchor Restoration Contract or Top Up Restoration Contract if required.

Power Station: _________________________

Generation Planning Parameters

| DATA DESCRIPTION |  | UNITS | DATA to RTL |  | DATA CAT. | GENSET OR STATION DATA |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | CUSC Contract | CUSC App. Form |  | G1 | G2 | G3 | G4 | G5 | G6 | STN |  |
| OUTPUT CAPABILITY |  |  |  |  |  |  |  |  |  |  |  |  |  |
| (PC.A.3.2.2) |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Registered Capacity on a station and unit basis (on a station and module basis in the case of a CCGT Module or Power Park Module at a Large Power Station) Maximum Capacity on a Power Generating Module basis and Synchronous Generating Unit basis and Registered Capacity on a Power Station basis) | MW MW | □ □ | ■ ■ | SPD SPD |  |  |  |  |  |  |  |
| Minimum Generation (on a module basis in the case of a CCGT Module or Power Park Module at a Large Power Station) Minimum Stable Operating Level (on a module basis in the case of a Power Generating Module at a Large Power Station | MW MW | □ □ | ■ ■ | SPD SPD |  |  |  |  |  |  |  |
| MW available from Power Generating Modules and Generating Units or Power Park Modules in excess of Registered Capacity or Maximum Capacity | MW | □ | ■ | SPD |  |  |  |  |  |  |  |
| REGIME UNAVAILABILITY |  |  |  |  |  |  |  |  |  |  |  |  |  |
| These data blocks are provided to allow fixed periods of unavailability to be registered. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Expected Running Regime. Is Power Station normally available for full output 24 hours per day, 7 days per week? If No please provide details of unavailability below. (PC.A.3.2.2.) |  |  | □ | ■ | SPD |  |  |  |  |  |  |  |  |
| Earliest Synchronising time: OC2.4.2.1(a) |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Monday |  | hr/min | ■ |  | OC2 |  |  |  |  |  |  | - |  |
| Tuesday – Friday |  | hr/min | ■ |  | OC2 |  |  |  |  |  |  | - |  |
| Saturday – Sunday |  | hr/min | ■ |  | OC2 |  |  |  |  |  |  | - |  |
| Latest De-Synchronising time: OC2.4.2.1(a) |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Monday – Thursday |  | hr/min | ■ |  | OC2 |  |  |  |  |  |  | - |  |
| Friday |  | hr/min | ■ |  | OC2 |  |  |  |  |  |  | - |  |
| Saturday – Sunday |  | hr/min | ■ |  | OC2 |  |  |  |  |  |  | - |  |
| SYNCHRONISING PARAMETERS |  |  |  |  |  |  |  |  |  |  |  |  |  |
| OC2.4.2.1(a) |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Notice to Deviate from Zero (NDZ) after 48 hour Shutdown |  | Mins | ■ |  | OC2 |  |  |  |  |  |  |  |  |
| Station Synchronising Intervals (SI) after 48 hour Shutdown |  | Mins | ■ |  |  | - | - | - | - | - | - |  |  |
| Synchronising Group (if applicable) |  | 1 to 4 | ■ |  | OC2 |  |  |  |  |  |  | - |  |

SCHEDULE 2 - GENERATION PLANNING PARAMETERS

PAGE 2 OF 3

| DATA DESCRIPTION | UNITS | DATA to RTL |  | DATA CAT. | GENSET OR STATION DATA |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | CUSC Contract | CUSC App. Form |  | G1 | G2 |  | G3 |  | G4 |  | G5 |  | G6 | STN |
| Synchronising Generation (SYG) after 48 hour Shutdown PC.A.5.3.2(f) & OC2.4.2.1(a) | MW | ■ |  | DPD II & OC2 |  |  |  |  |  |  |  |  |  |  | - |
| De-Synchronising Intervals (Single value) OC2.4.2.1(a) | Mins | ■ |  | OC2 | - | - |  | - |  | - |  | - |  | - |  |
| RUNNING AND SHUTDOWN PERIOD LIMITATIONS: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Minimum Non Zero time (MNZT) after 48 hour Shutdown OC2.4.2.1(a) | Mins | ■ |  | OC2 |  |  |  |  |  |  |  |  |  |  |  |
| Minimum Zero time (MZT) OC2.4.2.1(a) | Mins |  |  | OC2 |  |  |  |  |  |  |  |  |  |  |  |
| Existing AGR Plant Flexibility Limit (Existing AGR Plant only) | No. |  |  | OC2 |  |  |  |  |  |  |  |  |  |  |  |
| 80% Reactor Thermal Power (expressed as Gross-Net MW) (Existing AGR Plant only) | MW |  |  | OC2 |  |  |  |  |  |  |  |  |  |  |  |
| Frequency Sensitive AGR Unit Limit (Frequency Sensitive AGR Units only) | No. |  |  | OC2 |  |  |  |  |  |  |  |  |  |  |  |
| RUN-UP PARAMETERS |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| PC.A.5.3.2(f) & OC2.4.2.1(a) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Run-up rates (RUR) after 48 hour Shutdown: | (Note that for DPD only a single value of run-up rate from Synch Gen to Registered Capacity is required) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| (See note 2 page 3) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| MW Level 1 (MWL1) | MW | ■ |  | DPD II OC2 |  |  |  |  |  |  |  |  |  |  | - |
| MW Level 2 (MWL2) | MW | ■ |  | DPD II OC2 |  |  |  |  |  |  |  |  |  |  | - |
| RUR from Synch. Gen to MWL1 | MW/Mins | ■ |  | DPD II OC2 |  |  |  |  |  |  |  |  |  |  |  |
| RUR from MWL1 to MWL2 | MW/Mins | ■ |  | OC2 |  |  |  |  |  |  |  |  |  |  |  |
| RUR from MWL2 to RC | MW/Mins | ■ |  | OC2 |  |  |  |  |  |  |  |  |  |  |  |
| Run-Down Rates (RDR): | (Note that for DPD only a single value of run-down rate from Registered Capacity to de-synch is required) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| MWL2 | MW | ■ |  | DPD II OC2 |  |  |  |  |  |  |  |  |  |  |  |
| RDR from RC to MWL2 | MW/Min | ■ |  | DPD II OC2 |  |  |  |  |  |  |  |  |  |  |  |
| MWL1 | MW | ■ |  | DPD II OC2 |  |  |  |  |  |  |  |  |  |  |  |
| RDR from MWL2 to MWL1 | MW/Min | ■ |  | DPD II OC2 |  |  |  |  |  |  |  |  |  |  |  |
| RDR from MWL1 to de-synch | MW/Min | ■ |  | DPD II OC2 |  |  |  |  |  |  |  |  |  |  |  |

SCHEDULE 2 - GENERATION PLANNING PARAMETERS

PAGE 3 OF 3

| DATA DESCRIPTION | UNITS | DATA to RTL |  | DATA CAT. | GENSET OR STATION DATA |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | CUSC Contract | CUSC App. Form |  | G1 | G2 | G3 | G4 |  |  | G5 | G6 | STN |
| REGULATION PARAMETERS |  |  |  |  |  |  |  |  |  |  |  |  |  |
| OC2.4.2.1(a) |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Regulating Range | MW | ■ |  | DPD II |  |  |  |  |  |  |  |  |  |
| Load rejection capability while still Synchronised and able to supply Load. | MW | ■ |  | DPD II |  |  |  |  |  |  |  |  |  |
| GAS TURBINE LOADING PARAMETERS: |  |  |  |  |  |  |  |  |  |  |  |  |  |
| OC2.4.2.1(a) |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Fast loading | MW/Min | ■ |  | OC2 |  |  |  |  |  |  |  |  |  |
| Slow loading | MW/Min | ■ |  | OC2 |  |  |  |  |  |  |  |  |  |
| CCGT MODULE PLANNING MATRIX |  |  |  | OC2 | (please attach) |  |  |  |  |  |  |  |  |
| POWER PARK MODULE PLANNING MATRIX |  |  |  | OC2 | (please attach) |  |  |  |  |  |  |  |  |
| Power Park Module Active Power Output/ Intermittent Power Source Curve (e.g., MW output / Wind speed) |  |  |  | OC2 | (please attach) |  |  |  |  |  |  |  |  |

NOTES:

(1)	To allow for different groups of Gensets within a Power Station (e.g., Gensets with the same operator) each Genset may be allocated to one of up to four Synchronising Groups.  Within each such Synchronising Group the single synchronising interval will apply but between Synchronising Groups a zero synchronising interval will be assumed.

(2)	The run-up of a Genset from synchronising block load to Registered Capacity or Maximum Capacity is represented as a three stage characteristic in which the run-up rate changes at two intermediate loads, MWL1 and MWL2.  The values MWL1 & MWL2 can be different for each Genset.

SCHEDULE 3 - LARGE POWER STATION OUTAGE PROGRAMMES, OUTPUT USABLE AND INFLEXIBILITY INFORMATION

PAGE 1 OF 1

(Also outline information on contracts involving External Interconnections)

For a Generating Unit at a Large Power Station the information is to be submitted on a unit basis 	and for a CCGT Module or Power Park Module at a Large Power Station the information is to be 	submitted on a module basis, unless otherwise stated.

In the case of Restoration Contractors, data only needs to be provided by a Restoration Contractor where such a Resoration Contractor is not a CUSC Party and the data has not been submitted previously.  In this case, the data to be submitted would be would be pursant to the the terms of the Anchor Restoration Contract or Top Up Restoration Contract.

| DATA DESCRIPTION | UNITS | TIME COVERED | UPDATE TIME | DATA CAT | DATA to RTL |  |
| --- | --- | --- | --- | --- | --- | --- |
| OUTPUT PROFILES |  |  |  |  |  |  |
|  |  |  |  |  | CUSC Contract | CUSC App. Form |
| In the case of Large Power Stations whose output may be expected to vary in a random manner (e.g., wind power) or to some other pattern (e.g., Tidal) sufficient information is required to enable an understanding of the possible profile | MW | F. yrs 1 - 7 | Week 24 | SPD |  |  |

Notes: 1. The week numbers quoted in the Update Time column refer to standard weeks in the current year.

SCHEDULE 4 - LARGE POWER STATION DROOP AND RESPONSE DATA

PAGE 1 OF 1

GOVERNOR DROOP AND RESPONSE (PC.A.5.5 ■ CUSC Contract)

The Data in this Schedule 4 is to be supplied by Generators with respect to all Large Power Stations, HVDC System Owners and by DC Converter Station owners (where agreed), whether directly connected or Embedded

| Data Description | Normal Value | MW | Data CAT | Droop% |  |  | Response Capability |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  | Unit 1 | Unit 2 | Unit 3 | Primary | Secondary | High Frequency |
| MLP1 | Designed Minimum Operating Level or Minimum Regulating Level (for a CCGT Module or Power Park Module, on a modular basis assuming all units are Synchronised) |  |  |  |  |  |  |  |  |
| MLP2 | Minimum Generation or Minimum Stable Operating Level (for a CCGT Module or Power Park Module, or Power Generating Module on a modular basis assuming all units are Synchronised) |  |  |  |  |  |  |  |  |
| MLP3 | 70% of Registered Capacity or Maximum Capacity |  |  |  |  |  |  |  |  |
| MLP4 | 80% of Registered Capacity or Maximum Capacity |  |  |  |  |  |  |  |  |
| MLP5 | 95% of Registered Capacity or Maximum Capacity |  |  |  |  |  |  |  |  |
| MLP6 | Registered Capacity or Maximum Capacity |  |  |  |  |  |  |  |  |

Notes:

- The data provided in this Schedule 4 is not intended to constrain any Ancillary Services Agreement.

- Registered Capacity or Maximum Capacity should be identical to that provided in Schedule 2.

- The Governor Droop should be provided for each Generating Unit(excluding Power Park Units), Power Park Module, HVDC Converter or DC Converter. The Response Capability should be provided for each Genset or DC Converter.

- Primary, Secondary and High Frequency Response are defined in CC.A.3.2 or ECC.A.3.2 and are based on a frequency ramp of 0.5Hz over 10 seconds. Primary Response is the minimum value of response between 10s and 30s after the frequency ramp starts, Secondary Response between 30s and 30 minutes, and High Frequency Response is the minimum value after 10s on an indefinite basis.

- For plants which have not yet Synchronised, the data values of MLP1 to MLP6 should be as described above. For plants which have already Synchronised, the values of MLP1 to MLP6 can take any value between Designed Operating Minimum Level or Minimum Regulating Level and Registered Capacity or Maximum Capacity. If MLP1 is not provided at the Designed Minimum Operating Level, the value of the Designed Minimum Operating Level should be separately stated.

- For the avoidance of doubt Transmission DC Converters and OTSDUW DC Converters must be capable of providing a continuous signal indicating the real time frequency measured at the Transmission Interface Point to the Offshore Grid Entry Point (as detailed in CC.6.3.7(e)(vii) and CC.6.3.7(e)(viii) or ECC.6.3..3.1.1(f) to enable Offshore Power Generating Modules, Offshore Generating Units, Offshore Power Park Modules and/or Offshore DC Converters to satisfy the frequency response requirements of CC.6.3.7 or ECC.6.3.7.

- Alternative governor settigs shall be supplied by Generators, HVDC System Owners and DC Converter Owners where operation is required as part of System Restoration - as required in CC.6.3.5 orECC.6.3.5.2 and ECC.6.3.5.5(vii)

SCHEDULE 5 - USERS SYSTEM DATA

PAGE 1 OF 11

The data in this Schedule 5 is required from Users who are connected to the National Electricity Transmission System via a Connection Point (or who are seeking such a connection). Generators undertaking OTSDUW should use DRC Schedule 18 although they should still supply data under Schedule 5 in relation to their User’s System up to the Offshore Grid Entry Point.

Table 5 (a)

| DATA DESCRIPTION | UNITS | DATA to RTL |  | DATA CATEGORY |
| --- | --- | --- | --- | --- |
|  |  | CUSC Contract | CUSC App. Form |  |
| USERS SYSTEM LAYOUT (PC.A.2.2) |  |  |  |  |
| A Single Line Diagram showing all or part of the User’s System is required. This diagram shall include:- |  |  |  | SPD |
| - all parts of the User’s System, whether existing or proposed, operating at Supergrid Voltage, and in Scotland and Offshore, also all parts of the User System operating at 110kV and greater, |  | ■ | ■ |  |
| (b) all parts of the User’s System operating at a voltage of 50kV and greater, and in Scotland and Offshore greater than 30kV, or higher which can interconnect Connection Points, or split bus-bars at a single Connection Point, |  | ■ | ■ |  |
| (c) all parts of the User’s System between Embedded Medium Power Stations or Large Power Stations or Offshore Transmission Systems connected to the User’s Subtransmission System and the relevant Connection Point or Interface Point, |  | ■ | ■ |  |
| (d) all parts of the User’s System at a Transmission Site. |  | ■ | ■ |  |
| The Single Line Diagram may also include additional details of the User’s Subtransmission System, and the transformers connecting the User’s Subtransmission System to a lower voltage. With The Company’s agreement, it may also include details of the User’s System at a voltage below the voltage of the Subtransmission System. |  | ■ | ■ |  |
| This Single Line Diagram shall depict the arrangement(s) of all of the existing and proposed load current carrying Apparatus relating to both existing and proposed Connection Points, showing electrical circuitry (i.e., overhead lines, underground cables, power transformers and similar equipment), operating voltages. In addition, for equipment operating at a Supergrid Voltage, and in Scotland and Offshore also at 110kV and greater, circuit breakers and phasing arrangements shall be shown. |  | ■ | ■ |  |

SCHEDULE 5 - USERS SYSTEM DATA

PAGE 2 OF 11

Table 5(b)

| DATA DESCRIPTION | UNITS | DATA EXCH |  | DATA CATEGORY |
| --- | --- | --- | --- | --- |
|  |  | CUSC Contract | CUSC App. Form |  |
| REACTIVE COMPENSATION (PC.A.2.4) For independently switched reactive compensation equipment not owned by a Relevant Transmission Licensee connected to the User's System at 132kV and above, and also in Scotland and Offshore, connected at 33kV and above, other than power factor correction equipment associated with a customer’s Plant or Apparatus: |  |  |  |  |
| Type of equipment (e.g., fixed or variable) | Text | ■ | ■ | SPD |
| Capacitive rating; or | MVAr | ■ | ■ | SPD |
| Inductive rating; or | MVAr | ■ | ■ | SPD |
| Operating range | MVAr | ■ | ■ | SPD |
| Details of automatic control logic to enable operating characteristics to be determined | text and/or diagrams | ■ | ■ | SPD |
| Point of connection to User's System (electrical location and system voltage) | Text | ■ | ■ | SPD |
| SUBSTATION INFRASTRUCTURE (PC.A.2.2.6(b)) |  |  |  |  |
| For the infrastructure associated with any User’s equipment at a Substation owned by a Relevant Transmission Licensee or operated or managed by The Company:- |  |  |  |  |
| Rated 3-phase rms short-circuit withstand current | kA | ■ | ■ | SPD |
| Rated 1-phase rms short-circuit withstand current | kA | ■ | ■ | SPD |
| Rated Duration of short-circuit withstand | s | ■ | ■ | SPD |
| Rated rms continuous current | A | ■ | ■ | SPD |

SCHEDULE 5 – USERS SYSTEM DATA

PAGE 3 OF 11

Table 5 (c)

| DATA DESCRIPTION |  | UNITS | DATA EXCH |  | DATA CATEGORY |
| --- | --- | --- | --- | --- | --- |
|  |  |  | CUSC Contract | CUSC App. Form |  |
| LUMPED SUSCEPTANCES (PC.A.2.3) |  |  |  |  |  |
| Equivalent Lumped Susceptance required for all parts of the User’s Subtransmission System which are not included in the Single Line Diagram. |  |  | ■ | ■ |  |
| This should not include: |  |  | ■ | ■ |  |
| (a) | independently switched reactive compensation equipment identified above. |  | ■ | ■ |  |
| (b) | any susceptance of the User’s System inherent in the Demand (Reactive Power) data provided in Schedule 1 (Generator Data) or Schedule 11 (Connection Point data). |  | ■ | ■ |  |
| Equivalent lumped shunt susceptance at nominal Frequency. |  | % on 100 MVA | ■ | ■ | SPD |

SCHEDULE 5 – USERS SYSTEM DATA

PAGE 4 OF 11

USER’S SYSTEM DATA

Circuit Parameters	(PC.A.2.2.4) (■ CUSC Contract & ■ CUSC Application Form)

The data below is all Standard Planning Data. Details are to be given for all circuits shown on the Single Line Diagram

Table 5 (d)

| Years Valid | Node 1 | Node 2 | Rated Voltage kV | Operating Voltage kV | Positive Phase Sequence % on 100 MVA |  |  | Zero Phase Sequence (self) % on 100 MVA |  |  | Positive Phase Sequence (mutual) % on 100 MVA |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  | R | X | B | R | X | B | R | X | B |

Notes

- Data should be supplied for the current, and each of the seven succeeding Financial Years.  This should be done by showing for which years the data is valid in the first column of the Table.

SCHEDULE 5 – USERS SYSTEM DATA

PAGE 5 OF 11

USERS SYSTEM DATA

# Transformer Data (PC.A.2.2.5) (■ CUSC Contract & ■ CUSC Application Form)

The data below is all Standard Planning Data, and details should be shown below of all transformers shown on the Single Line Diagram.  Details of Winding Arrangement, Tap Changer and earthing details are only required for transformers connecting the User’s higher voltage system with its Primary Voltage System.

Table 5 (e)

| Years valid | Name of Node of Conne-ction | Trans-former | Rating MVA | Voltage Ratio |  | Positive Phase Sequence Reactance % on Rating |  |  | Positive Phase Sequence Resistance % on Rating |  |  | Zero Sequence Reactance % on Rating | Winding Arr | Tap Changer |  |  | Earthing Details (delete as app)* |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  | HV | LV | Max Tap | Min Tap | Nom Tap | Max Tap | Min Tap | Nom Tap |  |  | Range +% to -% | Step size % | Type (delete) |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | ON/ OFF | Direct/ Res/ Rea |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | ON/ OFF | Direct/ Res/ Rea |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | ON/ OFF | Direct/ Res/ Rea |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | ON/ OFF | Direct/ Res/ Rea |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | ON/ OFF | Direct/ Res/ Rea |

*If Resistance or Ractance please give impedance value

Notes

- Data should be supplied for the current, and each of the seven succeeding Financial Years.  This should be done by showing for which years the data is valid in the first column of the Table

2. 	For a transformer with two secondary windings, the positive and zero phase sequence leakage impedances between the HV and LV1, HV and LV2, and LV1 and LV2 windings are required.

SCHEDULE 5 –USERS SYSTEM DATA

PAGE 6 OF 11

USER’S SYSTEM DATA

# Switchgear Data (PC.A.2.2.6(a)) (■ CUSC Contract & CUSC Application Form ■)

The data below is all Standard Planning Data, and should be provided for all switchgear (i.e., circuit breakers, load disconnectors and disconnectors) operating at a Supergrid Voltage, and also in Scotland and Offshore, operating at 132kV. In addition, data should be provided for all circuit breakers irrespective of voltage located at a Connection Site which is owned by a Relevant Transmission Licensee or  operated or managed by The Company.

Table 5(f)

| Years Valid | Connection Point | Switch No | Rated Voltage kV rms | Operating Votage kV rms | Rated short-circuit breaking current |  | Rated short-circuit peak making current |  | Rated rms continuous current (A) | DC time constant at testing of asymmetrical breaking ability (s) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  | 3 phase kA rms | 1 phase ka rms | 3 phase kA rms | 1 phase ka rms |  |  |

# Notes

- Rated Voltage should be as defined by IEC 694.

- Data should be supplied for the current, and each of the seven succeeding Financial Years.  This should be done by showing for which years the data is valid in the first column of the Table

SCHEDULE 5 –USERS SYSTEM DATA

PAGE 7 OF 11

Table 5(g)

| DATA DESCRIPTION | UNITS | DATA to RTL |  | DATA CATEGORY |
| --- | --- | --- | --- | --- |
| PROTECTION SYSTEMS (PC.A.6.3) |  | CUSC Contract | CUSC App. Form |  |
| The following information relates only to Protection equipment which can trip or inter-trip or close any Connection Point circuit breaker or any Transmission circuit breaker. The information need only be supplied once, in accordance with the timing requirements set out in PC.A.1.4 (b) and need not be supplied on a routine annual basis thereafter, although The Company should be notified if any of the information changes. |  |  |  |  |
| (a) A full description, including estimated settings, for all relays and Protection systems installed or to be installed on the User's System; |  | ■ |  | DPD II |
| (b) A full description of any auto-reclose facilities installed or to be installed on the User's System, including type and time delays; |  | ■ |  | DPD II |
| (c) A full description, including estimated settings, for all relays and Protection systems installed or to be installed on the Power Generating Module, Power Park Module or Generating Unit's generator transformer, unit transformer, station transformer and their associated connections; |  | ■ |  | DPD II |
| (d) For Generating Units (other than Power Park Units) having a circuit breaker at the generator terminal voltage clearance times for electrical faults within the Generating Unit zone must be declared. |  | ■ |  | DPD II |
| (e) Fault Clearance Times: |  |  |  |  |
| Most probable fault clearance time for electrical faults on any part of the Users System directly connected to the National Electricity Transmission System. (f) Alternative Protection data as submitted under (a) to (e) abovin respect of System Restoration | msec | ■ ■ |  | DPD II DPD II |

| DATA DESCRIPTION | UNITS | DATA to RTL |  | DATA CATEGORY |
| --- | --- | --- | --- | --- |
| POWER PARK MODULE/UNIT PROTECTION SYSTEMS |  | CUSC Contract | CUSC App. Form |  |
| Details of settings for the Power Park Module/Unit protection relays (to include): (PC.A.5.4.2(f)) |  |  |  |  |
| (a) Under frequency, |  | ■ |  | DPD II |
| (b) Over Frequency, |  | ■ |  | DPD II |
| (c) Under Voltage, Over Voltage, |  | ■ |  | DPD II |
| (d) Rotor Over current, |  | ■ |  | DPD II |
| (e) Stator Over current, |  | ■ |  | DPD II |
| (f) High Wind Speed Shut Down Level, |  | ■ |  | DPD II |
| (g) Rotor Underspeed, |  | ■ |  | DPD II |
| (h) Rotor Overspeed. |  | ■ |  | DPD II |

SCHEDULE 5 - USERS SYSTEM DATA

PAGE 8 OF 11

Information for Transient Overvoltage Assessment (DPD I) (PC.A.6.2 ■ CUSC Contract)

The information listed below may be requested by The Company from each User with respect to any Connection Site between that User and the National Electricity Transmission System.  The impact of any third party Embedded within the Users System should be reflected.

(a)	Busbar layout plan(s), including dimensions and geometry showing positioning of any current and voltage transformers, through bushings, support insulators, disconnectors, circuit breakers, surge arresters, etc.  Electrical parameters of any associated current and voltage transformers, stray capacitances of wall bushings and support insulators, and grading capacitances of circuit breakers;

(b)	Electrical parameters and physical construction details of lines and cables connected at that busbar.  Electrical parameters of all plant e.g., transformers (including neutral earthing impedance or zig-zag transformers if any), series reactors and shunt compensation equipment connected at that busbar (or to the tertiary of a transformer) or by lines or cables to that busbar;

(c)	Basic insulation levels (BIL) of all Apparatus connected directly, by lines or by cables to the busbar;

(d)	Characteristics of overvoltage Protection devices at the busbar and at the termination points of all lines, and all cables connected to the busbar;

(e)	Fault levels at the lower voltage terminals of each transformer connected directly or indirectly to the National Electricity Transmission System without intermediate transformation;

(f)	The following data is required on all transformers operating at Supergrid Voltage throughout Great Britain and, in Scotland and Offshore, also at greater than 110kV: three or five limb cores or single phase units to be specified, and operating peak flux density at nominal voltage.

(g)	An indication of which items of equipment may be out of service simultaneously during Planned Outage conditions.

Harmonic Studies (DPD I) (PC.A.6.4 ■ CUSC Contract)

The information given below, both current and forecast, where not already supplied in this Schedule 5 may be requested by The Company from each User if it is necessary for The Company to evaluate the production/magnification of harmonic distortion on the National Electricity Transmission System and User’s systems.  The impact of any third party Embedded within the User’s System should be reflected:

(a)	Overhead lines and underground cable circuits of the User's Subtransmission System must be differentiated and the following data provided separately for each type:

Positive phase sequence resistance

Positive phase sequence reactance

Positive phase sequence susceptance

(b)	for all transformers connecting the User's Subtransmission System to a lower voltage:

Rated MVA

Voltage Ratio

Positive phase sequence resistance

Positive phase sequence reactance

SCHEDULE 5 – USERS SYSTEM DATA

PAGE 9 OF 11

(c)	at the lower voltage points of those connecting transformers:

Equivalent positive phase sequence susceptance

Connection voltage and MVAr rating of any capacitor bank and component design parameters if configured as a filter

Equivalent positive phase sequence interconnection impedance with other lower voltage points

The minimum and maximum Demand (both MW and MVAr) that could occur

Harmonic current injection sources in Amps at the Connection voltage points

Details of traction loads, e.g., connection phase pairs, continuous variation with time, etc.

(d)	an indication of which items of equipment may be out of service simultaneously during Planned Outage conditions

Voltage Assessment Studies (DPD I) (PC.A.6.5 ■ CUSC Contract)

The information listed below, where not already supplied in this Schedule 5, may be requested by The Company from each User with respect to any Connection Site if it is necessary for The Company to undertake detailed voltage assessment studies (e.g., to examine potential voltage instability, voltage control co-ordination or to calculate voltage step changes). The impact of any third party Embedded within the Users System should be reflected:

(a)	For all circuits of the User’s Subtransmission System:

Positive Phase Sequence Reactance

Positive Phase Sequence Resistance

Positive Phase Sequence Susceptance

MVAr rating of any reactive compensation equipment

(b)	for all transformers connecting the User's Subtransmission System to a lower voltage:

Rated MVA

Voltage Ratio

Positive phase sequence resistance

Positive Phase sequence reactance

Tap-changer range

Number of tap steps

Tap-changer type: on-load or off-circuit

AVC/tap-changer time delay to first tap movement

AVC/tap-changer inter-tap time delay

SCHEDULE 5 – USERS SYSTEM DATA

PAGE 10 OF 11

(c)	at the lower voltage points of those connecting transformers:-

Equivalent positive phase sequence susceptance

MVAr rating of any reactive compensation equipment

Equivalent positive phase sequence interconnection impedance with other lower voltage points

The maximum Demand (both MW and MVAr) that could occur

Estimate of voltage insensitive (constant power) load content in % of total load at both winter peak and 75% off-peak load conditions

Short Circuit Analyses:(DPD I) (PC.A.6.6 ■ CUSC Contract)

The information listed below, both current and forecast, and where not already supplied under this Schedule 5, may be requested by The Company from each User with respect to any Connection Site where prospective short-circuit currents on equipment owned by a Relevant Transmission Licensee or operated or managed by The Company are close to the equipment rating.  The impact of any third party Embedded within the User’s System should be reflected:-

(a)	For all circuits of the User’s Subtransmission System:

Positive phase sequence resistance

Positive phase sequence reactance

Positive phase sequence susceptance

Zero phase sequence resistance (both self and mutuals)

Zero phase sequence reactance (both self and mutuals)

Zero phase sequence susceptance (both self and mutuals)

(b)	for all transformers connecting the User's Subtransmission System to a lower voltage:

Rated MVA

Voltage Ratio

Positive phase sequence resistance (at max, min and nominal tap)

Positive phase sequence reactance (at max, min and nominal tap)

Zero phase sequence reactance (at nominal tap)

Tap changer range

Earthing method: direct, resistance or reactance

Impedance if not directly earthed

(c)	at the lower voltage points of those connecting transformers:-

The maximum Demand (in MW and MVAr) that could occur

Short-circuit infeed data in accordance with PC.A.2.5.6(a) unless the User’s lower voltage network runs in parallel with the Subtransmission System, when to prevent double counting in each node infeed data, a  equivalent comprising the data items of PC.A.2.5.6(a) for each node together with the positive phase sequence interconnection impedance between the nodes shall be submitted.

SCHEDULE 5 – USERS SYSTEM DATA

PAGE 11 OF 11

Dynamic Models:(DPD II) (PC.A.6.7 ■ CUSC Contract)

The information listed below, both current and forecast, and where not already supplied under this Schedule 5, may be requested by The Company from each EU Code User or in respect of each EU Grid Supply Point  with respect to any Connection Site

- Dynamic model structure and block diagrams including parameters, transfer   functions and individual elements (as applicable)

- Power control functions and block diagrams including parameters, 	transfer   functions and individual elements (as applicable)

- Voltage control functions and block diagrams including parameters, 	transfer  functions and individual elements (as applicable)

- Converter control models and block diagrams including parameters, transfer functions and individual elements (as applicable)

SCHEDULE 6 – USERS OUTAGE INFORMATION

PAGE 1 OF 3

| DATA DESCRIPTION | UNITS | DATA to RTL |  | TIMESCALE COVERED | UPDATE TIME | DATA CAT. |
| --- | --- | --- | --- | --- | --- | --- |
|  |  | CUSC Contract | CUSC App. Form |  |  |  |
| Details are required from Network Operators of proposed outages in their User Systems and from Generators with respect to their outages, which may affect the performance of the Total System (e.g., at a Connection Point or constraining Embedded Large Power Stations or constraints to the Maximum Import Capacity or Maximum Export Capacity at an Interface Point) (OC2.4.1.3.2(a) & (b)). Outages of Plant and Apparatus of Restoration Contractors and key Plant and Apparatus of a Network Operator’s System associated with a Distribution Restoration Zone Plan also need to be co-ordinated with outages on the National Electricity Transmission System. Thisincludes data from Network Operators and Restoration Contractors which would impact the ability to operate a Local Joint Restoration Plan or Distribution Restoration Zone Plan. |  | ■ |  | Years 2-5 | Week 8 (Network Operator etc) Week 13 (Generators) | OC2 OC2 PC.A.5.7.2 |
| (The Company advises Network Operators of National Electricity Transmission System outages affecting their Systems) |  |  |  | Years 2-5 | Week 28) |  |
| Network Operator informs The Company if unhappy with proposed outages) |  | ■ |  | " | Week 30 | OC2 |
| (The Company draws up revised National Electricity Transmission System |  |  |  | " | Week 34) |  |
| (outage plan advises Users of operational effects) |  |  |  |  |  |  |
| Generators and Non-Embedded Customers provide Details of Apparatus owned by them (other than Gensets) at each Grid Supply Point (OC2.4.1.3.3) |  | ■ |  | Year 1 | Week 13 | OC2 |
| (The Company advises Network Operators of outages affecting their Systems) (OC2.4.1.3.3) |  |  |  | Year 1 | Week 28) |  |
| Network Operator details of relevant outages affecting the Total System (OC2.4.1.3.3) |  | ■ |  | Year 1 | Week 32 | OC2 |
| Details of:- Maximum Import Capacity for each Interface Point Maximum Export Capacity for each Interface Point Changes to previously declared values of the Interface Point Target Voltage/Power Factor (OC2.4.1.3.3(c )). | MVA / MW MVA / MW V (unless power factor control |  |  | Year 1 | Week 32 | OC2 |
| (The Company informs Users of aspects that may affect their Systems) (OC2.4.1.3.3) |  |  |  | Year 1 | Week 34) |  |
| Users inform The Company if unhappy with aspects as notified (OC2.4.1.3.3) |  | ■ |  | Year 1 | Week 36 | OC2 |
| (The Company issues final National Electricity Transmission System |  | ■ |  | Year 1 | Week 49 | OC2 |
| (outage plan with advice of operational) (OC2.4.1.3.3) (effects on Users System) |  |  |  |  |  |  |
| Generator, Network Operator and Non-Embedded Customers to inform The Company of changes to outages previously requested |  |  |  | Week 8 ahead to year end | As occurring | OC2 |
| Details of load transfer capability of 12MW or more between Grid Supply Points in England and Wales and 10MW or more between Grid Supply Points in Scotland. |  |  |  | Within Yr 0 | As The Company request | OC2 |
| Details of:- Maximum Import Capacity for each Interface Point Maximum Export Capacity for each Interface Point Changes to previously declared values of the Interface Point Target Voltage/Power Factor | MVA / MW MVA / MW V (unless power factor control |  |  | Within Yr 0 | As occurring | OC2 |

Note: Users should refer to OC2 for full details of the procedure summarised above and for the 	information which The Company will provide on the Programming Phase.

SCHEDULE 6 – USERS OUTAGE INFORMATION

PAGE 2 OF 3

The data below is to be provided to The Company as required for compliance with the applicable Retained EU Law (Commission Regulation (EU) No 543/2013 (OC2.4.2.3)).  Data provided under Article Numbers 7.1(a), 7.1(b), 15.1(a), 15.1(b), and 15.1(c) and 15.1(d) is to be provided using MODIS.

| ECR ARTICLE No. | DATA DESCRIPTION | USERS PROVIDING DATA | FREQUENCY OF SUBMISSION |
| --- | --- | --- | --- |
| 7.1(a) | Planned unavailability of the Apparatus belonging to a Non-Embedded Customer where OC2.4.7 (a) applies - Unavailable demand capacity during the event (MW) - Estimated start date and time (dd.mm.yy hh:mm) - Estimated end date and time (dd.mm.yy hh:mm) - Reason for unavailability from the list below: . Maintenance . Failure . Shutdown . Other | Non-Embedded Customer | To be received by The Company as soon as reasonably possible but in any case, to facilitate publication of data no later than 1 hour after a decision has been made by the Non-Embedded Customer regarding the planned unavailability |
| 7.1(b) | Changes in actual availability of the Apparatus belonging to a Non-Embedded Customer where OC2.4.7 (b) applies - Unavailable demand capacity during the event (MW) - Start date and time (dd.mm.yy hh:mm) - Estimated end date and time (dd.mm.yy hh:mm) - Reason for unavailability from the list below : . Maintenance . Failure . Shutdown . Other | Non-Embedded Customer | To be received by The Company as soon as reasonably possible but in any case, to facilitate publication of data no later than 1 hour after the change in actual availability |
| 8.1 | Year Ahead Forecast Margin information as provided in accordance with OC2.4.1.2.2 - Output Usable | Generator | In accordance with OC2.4.1.2.2 |
| 14.1(a) | Registered Capacity or Maximum Capacity for Generating Units or Power Generating Modules with greater than 1 MW Registered Capacity or Maximum Capacity provided in accordance with PC.4.3.1 and PC.A.3.4.3 or PC.A.3.1.4 - Registered Capacity or Maximum Capacity (MW) - Production type (from that listed under PC.A.3.4.3) | Generator | Week 24 |
| 14.1(b) | Power Station Registered Capacity for units with equal or greater than 100 MW Registered Capacity provided in accordance with PC.4.3.1 and PC.A.3.4.3 - Power Station name - Location of Generating Unit - Production type (from that listed under PC.A.3.4.3) - Voltage connection levels - Registered Capacity or Maximum Capacity (MW) | Generator | Week 24 |
| 14.1(c) | Estimated output of Active Power of a BM Unit or Generating Unit for each per Settlement Period of the next Operational Day provided in accordance with BC1.4.2 - Physical Notification | Generator | In accordance with BC1.4.2 |
| 15.1(a) | Planned unavailability of a Generating Unit where OC2.4.7(c) applies - Power Station name - Generating Unit and/or Power Generating Module name - Location of Generating Unit and/or Power Generating Module - Generating Unit Registered Capacity (MW) - Production type (from that listed under PC.A.3.4.3) - Output Usable (MW) during the event - Start date and time (dd.mm.yy hh:mm) - Estimated end date and time (dd.mm.yy hh:mm) - Reason for unavailability from the list below: . Maintenance . Shutdown . Other | Generator | To be received by The Company as soon as reasonably possible but in any case, to facilitate publication of data no later than 1 hour after a decision has been made by the Generator regarding the planned unavailability |
| 15.1(b) | Changes in availability of a Generating Unit and/or Power Generating Module where OC2.4.7 (d) applies - Power Station name - Generating Unit and/or Power Generating Module name - Location of Generating Unit and/or Power Generating Module - Generating Unit Registered Capacity and Power Generating Module Maximum Capacity (MW) - Production type(from that listed under PC.A.3.4.3) - Maximum Export Limit (MW) during the event - Start date and time (dd.mm.yy hh:mm) - Estimated end date and time (dd.mm.yy hh:mm) - Reason for unavailability from the list below: . Maintenance . Shutdown . Other | Generator | To be received by The Company as soon as reasonably possible but in any case, to facilitate publication of data no later than 1 hour after the change in actual availability |
| 15.1(c) | Planned unavailability of a Power Station where OC2.4.7(e) applies - Power Station name - Location of Power Station - Power Station Registered Capacity (MW) - Production type (from that listed under PC.A.3.4.3) - Power Station aggregated Output Usable (MW) during the event - Start date and time (dd.mm.yy hh:mm) - Estimated end date and time (dd.mm.yy hh:mm) - Reason for unavailability from the list below: . Maintenance . Shutdown . Other | Generator | To be received by The Company as soon as reasonably possible but in any case, to facilitate publication of data no later than 1 hour after a decision has been made by the Generator regarding the planned unavailability |
| 15.1(d) | Changes in actual availability of a Power Station where OC2.4.7 (f) applies - Power Station name - Location of Power Station - Power Station Registered Capacity (MW) - Production type (from that listed under PC.A.3.4.3) - Power Station aggregated Maximum Export Limit (MW) during the event - Start date and time (dd.mm.yy hh:mm) - Estimated end date and time (dd.mm.yy hh:mm) - Reason for unavailability from the list below: . Maintenance . Shutdown . Other | Generator | To be received by The Company as soon as reasonably possible but in any case, to facilitate publication of data no later than 1 hour after the change in actual availability |
| 15.1(e) | Outage data from a Network Operator relating to an outage on the Network Operator’s System or an outage of a Restoration Contractor’s Plant and Apparatus (not already supplied) which would prevent the operation of a Restoration Plan.. Outages of Plant and Apparatus of Restoration Contractors and key Plant and Apparatus of a Network Operator’s System associated with a Distribution Restoration Zone Plan also need to be co-ordinated with outages on the National Electricity Transmission System | Network Operators and Restoration Service Contractors | In accordance with the requirements of OC2 |

SCHEDULE 7 - LOAD CHARACTERISTICS AT GRID SUPPLY POINTS

PAGE 1 OF 1

All data in this schedule 7 is categorised as Standard Planning Data (SPD) and is required for existing and agreed future connections.  This data is only required to be updated when requested by The Company.

|  |  |  |  | DATA FOR FUTURE YEARS |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| DATA DESCRIPTION | UNITS | DATA to RTL |  | Yr 1 | Yr 2 | Yr 3 | Yr 4 | Yr 5 |  | Yr 6 | Yr 7 |
|  |  | CUSC Contract | CUSC App. Form |  |  |  |  |  |  |  |  |
| FOR ALL TYPES OF DEMAND FOR EACH GRID SUPPLY POINT |  |  |  |  |  |  |  |  |  |  |  |
| The following information is required infrequently and should only be supplied, wherever possible, when requested by The Company (PC.A.4.7) |  | □ |  |  |  |  |  |  |  |  |  |
| Details of individual loads which have Characteristics significantly different from the typical range of domestic or commercial and industrial load supplied: (PC.A.4.7(a)) |  | □ |  | (Please Attach) |  |  |  |  |  |  |  |
| Sensitivity of demand to fluctuations in voltage And frequency on National Electricity Transmission System at time of peak Connection Point Demand (Active Power) (PC.A.4.7(b)) |  | □ |  |  |  |  |  |  |  |  |  |
| Voltage Sensitivity (PC.A.4.7(b)) | MW/kV MVAr/kV | □ |  |  |  |  |  |  |  |  |  |
| Frequency Sensitivity (PC.A.4.7(b)) | MW/Hz MVAr/Hz | □ |  |  |  |  |  |  |  |  |  |
| Reactive Power sensitivity should relate to the Power Factor information given in Schedule 11 (or for Generators, Schedule 1) and note 6 on Schedule 11 relating to Reactive Power therefore applies: (PC.A.4.7(b)) |  | □ |  |  |  |  |  |  |  |  |  |
| Phase unbalance imposed on the National Electricity Transmission System (PC.A.4.7(d)) |  |  |  |  |  |  |  |  |  |  |  |
| - maximum | % | □ |  |  |  |  |  |  |  |  |  |
| - average | % | □ |  |  |  |  |  |  |  |  |  |
| Maximum Harmonic Content imposed on National Electricity Transmission System (PC.A.4.7(e)) | % | □ |  |  |  |  |  |  |  |  |  |
| Details of any loads which may cause Demand Fluctuations greater than those permitted under Engineering Recommendation P28, Stage 1 at the Point of Common Coupling including Flicker Severity (Short Term) and Flicker Severity (Long Term) (PC.A.4.7(f)) |  | □ |  |  |  |  |  |  |  |  |  |

SCHEDULE 8 - DATA SUPPLIED BY BM PARTICIPANTS

PAGE 1 OF 1

| CODE | DESCRIPTION |
| --- | --- |
| BC1 BC1 & BC2 BC1 BC1 BC2 BC1 & BC2 | Physical Notifications Export and Import Limits Bid-Offer Data Dynamic Parameters (Day Ahead) Dynamic Parameters (For use in Balancing Mechanism) Other Relevant Data |

- No information collated under this Schedule will be transferred to the Relevant Transmission Licensees

SCHEDULE 9 - DATA SUPPLIED BY THE COMPANY TO USERS

PAGE 1 OF 1

(Example of data to be supplied)

| CODE | DESCRIPTION |
| --- | --- |
| CC or ECC | Operation Diagram |
| CC or ECC | Site Responsibility Schedules |
| PC | Day of the peak National Electricity Transmission System Demand |
|  | Day of the minimum National Electricity Transmission System Demand |
| OC1.7 | From 31 December 2026 and during normal system operation, The Company shall publish on a daily basis, 60% and 100% of the peak National Demand, under pre System shutdown conditions for the following day, based on the latest forecast that would feed into the System Restoration Regional targets by means of messages inputted by The Company to the Balancing Mechanism Reporting Service (BMRS). From 31 December 2026 and during System Restoration, The Company shall publish for each System Restoration Region, the Demand that is used to calculate the National Demand on an hourly basis on a reasonable endeavours basis by means of messages inputted by The Company to the Balancing Mechanism Reporting Service (BMRS). |
| OC2 | Surpluses and Output Useable (OU) requirements for each Generator over varying timescales |
|  | Equivalent networks to Users for Outage Planning |
|  | Negative Reserve Active Power Margins (when necessary) |
|  | Operating Reserve information |
| BC1 | Demand Estimates, Indicated Margin and Indicated Imbalance, indicative Synchronising and Desynchronising times of Embedded Power Stations to Network Operators, special actions. |
| BC2 | Bid-Offer Acceptances, Ancillary Services instructions to relevant Users, Emergency Instructions |
| BC3 | Location, amount, and Low Frequency Relay settings of any Low Frequency Relay initiated Demand reduction for Demand which is Embedded. |

- No information collated under this Schedule will be transferred to the Relevant Transmission Licensees

- In respect of OC1, the data would also be supplied to Restoration Contractors

# DATA TO BE SUPPLIED BY THE COMPANY TO USERS

# PURSUANT TO THE TRANSMISSION LICENCE

1.	The Transmission Licence requires The Company to publish annually the Seven Year Statement which is designed to provide Users and potential Users with information to enable them to identify opportunities for continued and further use of the National Electricity Transmission System.

When a User is considering a development at a specific site, certain additional information may be required in relation to that site which is of such a level of detail that it is inappropriate to include it in the Seven Year Statement.  In these circumstances, the  User may contact The Company who will be pleased to arrange a discussion and the provision of such additional information relevant to the site under consideration as the User may reasonably require.

2.	The Transmission Licence also requires The Company to offer terms for an agreement for connection to and use of the National Electricity Transmission System and further information will be given by The Company to the potential User in the course of the discussions of the terms of such an agreement.

SCHEDULE 10 - DEMAND PROFILES AND ACTIVE ENERGY DATA

PAGE 1 OF 2

The following information is required from each Network Operator and from each Non-Embedded Customer. The data should be provided in calendar week 24 each year (although Network Operators may delay the submission until calendar week 28).

| DATA DESCRIPTION | F. Yr. 0 | F. Yr. 1 | F. Yr. 2 | F. Yr. 3 | F. Yr. 4 | F. Yr. 5 | F. Yr. 6 | F. Yr. 7 | UPDATE TIME | DATA CAT |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Demand Profiles | (PC.A.4.2) (■ – CUSC Contract & ■ CUSC Application Form) |  |  |  |  |  |  |  |  |  |
| Total User's system profile (please delete as applicable) | Day of User's annual Maximum demand at Annual ACS Conditions (MW) Day of annual peak of National Electricity Transmission System Demand at Annual ACS Conditions (MW) Day of annual minimum National Electricity Transmission System Demand at average conditions (MW) |  |  |  |  |  |  |  |  |  |
| 0000 : 0030 |  |  |  |  |  |  |  |  | Wk.24 | SPD |
| 0030 : 0100 |  |  |  |  |  |  |  |  | : |  |
| 0100 : 0130 |  |  |  |  |  |  |  |  | : |  |
| 0130 : 0200 |  |  |  |  |  |  |  |  | : | : |
| 0200 : 0230 |  |  |  |  |  |  |  |  | : | : |
| 0230 : 0300 |  |  |  |  |  |  |  |  | : | : |
| 0300 : 0330 |  |  |  |  |  |  |  |  | : | : |
| 0330 : 0400 |  |  |  |  |  |  |  |  | : | : |
| 0400 : 0430 |  |  |  |  |  |  |  |  | : | : |
| 0430 : 0500 |  |  |  |  |  |  |  |  | : | : |
| 0500 : 0530 |  |  |  |  |  |  |  |  | : | : |
| 0530 : 0600 |  |  |  |  |  |  |  |  | : | : |
| 0600 : 0630 |  |  |  |  |  |  |  |  | : | : |
| 0630 : 0700 |  |  |  |  |  |  |  |  | : | : |
| 0700 : 0730 |  |  |  |  |  |  |  |  | : | : |
| 0730 : 0800 |  |  |  |  |  |  |  |  | : | : |
| 0800 : 0830 |  |  |  |  |  |  |  |  | : | : |
| 0830 : 0900 |  |  |  |  |  |  |  |  | : | : |
| 0900 : 0930 |  |  |  |  |  |  |  |  | : | : |
| 0930 : 1000 |  |  |  |  |  |  |  |  | : | : |
| 1000 : 1030 |  |  |  |  |  |  |  |  | : | : |
| 1030 : 1100 |  |  |  |  |  |  |  |  | : | : |
| 1100 : 1130 |  |  |  |  |  |  |  |  | : | : |
| 1130 : 1200 |  |  |  |  |  |  |  |  | : | : |
| 1200 : 1230 |  |  |  |  |  |  |  |  | : | : |
| 1230 : 1300 |  |  |  |  |  |  |  |  | : | : |
| 1300 : 1330 |  |  |  |  |  |  |  |  | : | : |
| 1330 : 1400 |  |  |  |  |  |  |  |  | : | : |
| 1400 : 1430 |  |  |  |  |  |  |  |  | : | : |
| 1430 : 1500 |  |  |  |  |  |  |  |  | : | : |
| 1500 : 1530 |  |  |  |  |  |  |  |  | : | : |
| 1530 : 1600 |  |  |  |  |  |  |  |  | : | : |
| 1600 : 1630 |  |  |  |  |  |  |  |  | : | : |
| 1630 : 1700 |  |  |  |  |  |  |  |  | : | : |
| 1700 : 1730 |  |  |  |  |  |  |  |  | : | : |
| 1730 : 1800 |  |  |  |  |  |  |  |  | : | : |
| 1800 : 1830 |  |  |  |  |  |  |  |  | : | : |
| 1830 : 1900 |  |  |  |  |  |  |  |  | : | : |
| 1900 : 1930 |  |  |  |  |  |  |  |  | : | : |
| 1930 : 2000 |  |  |  |  |  |  |  |  | : | : |
| 2000 : 2030 |  |  |  |  |  |  |  |  | : | : |
| 2030 : 2100 |  |  |  |  |  |  |  |  | : | : |
| 2100 : 2130 |  |  |  |  |  |  |  |  | : | : |
| 2130 : 2200 |  |  |  |  |  |  |  |  | : | : |
| 2200 : 2230 |  |  |  |  |  |  |  |  | : | : |
| 2230 : 2300 |  |  |  |  |  |  |  |  | : | : |
| 2300 : 2330 |  |  |  |  |  |  |  |  | : | : |
| 2330 : 0000 |  |  |  |  |  |  |  |  | : | : |

SCHEDULE 10 - DEMAND PROFILES AND ACTIVE ENERGY DATA

PAGE 2 OF 2

| DATA DESCRIPTION | Out-turn |  | F.Yr. | Update | Data Cat | DATA to RTL |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | Actual | Weather | 0 | Time |  |  |  |
|  |  | Corrected. |  |  |  |  |  |
| (PC.A.4.3) |  |  |  |  |  | CUSC Contract | CUSC App. Form |
| Active Energy Data |  |  |  | Week 24 | SPD | ■ | ■ |
| Total annual Active Energy requirements under average conditions of each Network Operator and each Non-Embedded Customer in the following categories of Customer Tariff:- |  |  |  |  |  | ■ | ■ |
| LV1 |  |  |  |  |  | ■ | ■ |
| LV2 |  |  |  |  |  | ■ | ■ |
| LV3 |  |  |  |  |  | ■ | ■ |
| EHV |  |  |  |  |  | ■ | ■ |
| HV |  |  |  |  |  | ■ | ■ |
| Traction |  |  |  |  |  | ■ | ■ |
| Lighting |  |  |  |  |  | ■ | ■ |
| User System Losses |  |  |  |  |  | ■ | ■ |
| Active Energy from Embedded |  |  |  |  |  | ■ | ■ |
| Small Power Stations and |  |  |  |  |  |  |  |
| Embedded Medium Power Stations |  |  |  |  |  |  |  |

# NOTES:

1.		'F. yr.' means 'Financial Year'

2.	Demand and Active Energy Data (General)

Demand and Active Energy data should relate to the point of connection to the National Electricity Transmission System and should be net of the output (as reasonably considered appropriate by the User) of all Embedded Small Power Stations, Medium Power Stations and Customer Generating Plant. Auxiliary demand of Embedded Power Stations should be included in the demand data submitted by the User at the Connection Point.  Users should refer to the PC for a full definition of the Demand to be included.

3.	Demand profiles and Active Energy data should be for the total System of the Network Operator, including all Connection Points, and for each Non-Embedded Customer. Demand Profiles should give the numerical maximum demand that in the User's opinion could reasonably be imposed on the National Electricity Transmission System.

4.	In addition the demand profile is to be supplied for such days as The Company may specify, but such a request is not to be made more than once per calendar year.

SCHEDULE 11 - CONNECTION POINT DATA

PAGE 1 OF 5

The following information is required from each Network Operator and from each Non-Embedded Customer. The data should be provided in calendar week 24 each year (although Network Operators may delay the submission until calendar week 28).

| Table 11(a) Connection Point: |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Connection Point Demand at the time of - (select each one in turn) (Provide data for each Access Period associated with the Connection Point) |  | a) maximum Demand b) peak National Electricity Transmission System Demand (specified by The Company) c) minimum National Electricity Transmission System Demand (specified by The Company) d) maximum Demand during Access Period e) specified by either The Company or a User |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Name of Transmission Interface Circuit out of service during Access Period (if reqd). |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | PC.A.4.1.4.2 |  |
| DATA DESCRIPTION (CUSC Contract □ & CUSC Application Form ■) |  |  | Outturn | Outturn | F.Yr |  | F.Yr |  |  | F.Yr. |  | F.Yr. |  | F.Yr. |  | F.Yr | F.Yr | F.Yr |  | DATA CAT |
|  |  |  |  | Weather Corrected | 1 |  | 2 |  |  | 3 |  | 4 |  | 5 |  | 6 | 7 | 8 |  |  |
| Date of a), b), c), d) or e) as denoted above. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | PC.A.4.3.3 |
| Time of a), b), c), d) or e) as denoted above. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | PC.A.4.3.3 |
| Connection Point Demand (MW) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | PC.A.4.3.1 |
| Connection Point Demand (MVAr) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | PC.A.4.3.1 |
| Deduction made at Connection Point for Small Power Stations, Medium Power Stations and Customer Generating Plant (MW) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | PC.A.4.3.2(a) |
| Reference to valid Single Line Diagram |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | PC.A.4.3.5 |
| Reference to node and branch data. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | PC.A.2.2 |
| Note: The following data block can be repeated for each post fault network revision that may impact on the Transmission System. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Reference to post-fault revision of Single Line Diagram |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | PC.A.4.5 |  |
| Reference to post-fault revision of the node and branch data associated with the Single Line Diagram |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | PC.A.4.5 |  |
| Reference to the description of the actions and timescales involved in effecting the post-fault actions (e.g. auto-switching, manual, teleswitching, overload protection operation etc) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | PC.A.4.5 |  |
| Access Group: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Note: The following data block to be repeated for each Connection Point with the Access Group. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Name of associated Connection Point within the same Access Group: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | PC.A.4.3.1 |  |
| Demand at associated Connection Point (MW) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | PC.A.4.3.1 |  |
| Demand at associated Connection Point (MVAr) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | PC.A.4.3.1 |  |
| Deduction made at associated Connection Point for Small Power Stations, Medium Power Stations and Customer Generating Plant (MW) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | PC.A.4.3.2(a) |  |

# SCHEDULE 11 - CONNECTION POINT DATA

PAGE 2 OF 5

# Table 11(b)

| Embedded Generation Data |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Connection Point: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| DATA DESCRIPTION | Outturn |  | Outturn | F.Yr | F.Yr | F.Yr. | F.Yr. | F.Yr. | F.Yr | F.Yr | F.Yr | DATA CAT |  |  |
|  |  | Weather Corrected |  | 1 |  |  | 2 | 3 | 4 | 5 | 6 | 7 | 8 |  |
| Small Power Station, Medium Power Station and Customer Generation Summary | For each Connection Point where there are Embedded Small Power Stations, Medium Power Stations or Customer Generating Stations the following information is required: |  |  |  |  |  |  |  |  |  |  |  |  |  |
| No. of Small Power Stations, Medium Power Stations or Customer Power Stations |  |  |  |  |  |  |  |  |  |  |  | PC.A.3.1.4(a) |  |  |
| Number of Generating Units within these stations |  |  |  |  |  |  |  |  |  |  |  | PC.A.3.1.4(a) |  |  |
| Summated Capacity of all these Generating Units |  |  |  |  |  |  |  |  |  |  |  | PC.A.3.1.4(a) |  |  |
| Where the Network Operator’s System places a constraint on the capacity of an Embedded Large Power Station |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Station Name |  |  |  |  |  |  |  |  |  |  |  | PC.A.3.2.2(c) |  |  |
| Generating Unit |  |  |  |  |  |  |  |  |  |  |  | PC.A.3.2.2(c) |  |  |
| System Constrained Capacity |  |  |  |  |  |  |  |  |  |  |  | PC.A.3.2.2(c)(i) |  |  |
| Reactive Despatch Network Restriction |  |  |  |  |  |  |  |  |  |  |  | PC.A.3.2.2(c)(ii) |  |  |

| Where the Network Operator’s System places a constraint on the capacity of an Offshore Transmission System at an Interface Point |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Offshore Transmission System Name |  |  |  |  |  |  |  |  |  |  | PC.A.3.2.2(c) |
| Interface Point Name |  |  |  |  |  |  |  |  |  |  | PC.A.3.2.2(c) |
| Maximum Export Capacity |  |  |  |  |  |  |  |  |  |  | PC.A.3.2.2(c) |
| Maximum Import Capacity |  |  |  |  |  |  |  |  |  |  | PC.A.3.2.2(c) |

# SCHEDULE 11 - CONNECTION POINT DATA

PAGE 3 OF 5

Table 11(c)

| # For each Embedded Small Power Station of 1MW and above, the following information is required, effective 2015 in line with the Week 24 data submissions. |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| # DATA DESCRIPTION | An Embedded Small Power Station reference unique to each Network Operator | # Connection Date (Financial Year for generator connecting after week 24 2015) | # Generator unit Reference | # Technology Type / Production type | # CHP (Y/N) | # Registered capacity in MW (as defined in the Distribution Code) | # Lowest voltage node on the most up-to-date Single Line Diagram to which it connects or where it will export most of its power | # Where it exports electricity from wind PV or storage, the geographical location of the primary or higher voltage substation to which it connects | # Control mode | Control mode voltage target and reactive range or target pf (as appropriate) | Loss of mains protection type | # Loss of mains protection settings |
| # DATA CAT | PC.A.3.1.4 (a) |  | # PC.A.3.1.4 (a) | # PC.A.3.1.4 (a) | # PC.A.3.1.4 | # PC.A.3.1.4 (a) | # PC.A.3.1.4 (a) | # PC.A.3.1.4 (a) | # PC.A.3.1.4 (a) | # PC.A.3.1.4 (a) | # PC.A.3.1.4 (a) | # PC.A.3.1.4 (a) |

Table 11(c)

# SCHEDULE 11 - CONNECTION POINT DATA

PAGE 4 OF 5

NOTES:

1.	'F.Yr.' means 'Financial Year'.  F.Yr. 1 refers to the current financial year.

2.	All Demand data should be net of the output (as reasonably considered appropriate by the User) of all Embedded Small Power Stations, Embedded Medium Power Stations and Customer Generating Plant.  Generation and / or Auxiliary demand of Embedded Large Power Stations should not be included in the demand data submitted by the User.  Users should refer to the PC for a full definition of the Demand to be included.

3.	Peak Demand should relate to each Connection Point individually and should give the maximum demand that in the User's opinion could reasonably be imposed on the National Electricity Transmission System. Users may submit the Demand data at each node on the Single Line Diagram instead of at a Connection Point as long as the User reasonably believes such data relates to the peak (or minimum) at the Connection Point.

In deriving Demand any deduction made by the User (as detailed in note 2 above) to allow for Embedded Small Power Stations, Embedded Medium Power Stations and Customer Generating Plant is to be specifically stated as indicated on the Schedule.

4.	The Company may at its discretion require details of any Embedded Small Power Stations or Embedded Medium Power Stations whose output can be expected to vary in a random manner (e.g. wind power) or according to some other pattern (e.g. tidal power)

5.	Where more than 95% of the total Demand at a Connection Point is taken by synchronous motors, values of the Power Factor at maximum and minimum continuous excitation may be given instead. Power Factor data should allow for series reactive losses on the User's System but exclude reactive compensation network susceptance specified separately in Schedule 5.

- Where a Reactive Despatch Network Restriction is in place which requires the generator to maintain a target voltage set point this should be stated as an alternative to the size of the Reactive Despatch Network Restriction.

SCHEDULE 11 - CONNECTION POINT DATA

PAGE 5 OF 5

Table 11 (d)

Embedded Small Power Stations <1MW

| Network Operator |  |
| --- | --- |

| Fuel Type | Aggregate Registered Capacity Total MW | Number of PGMs | Comments |
| --- | --- | --- | --- |
| Biomass |  |  |  |
| Fossil brown coal/lignite |  |  |  |
| Fossil coal-derived gas |  |  |  |
| Fossil gas |  |  |  |
| Fossil hard coal |  |  |  |
| Fossil oil |  |  |  |
| Fossil oil shale |  |  |  |
| Fossil peat |  |  |  |
| Geothermal |  |  |  |
| Hydro pumped storage |  |  |  |
| Hydro run-of-river and poundage |  |  |  |
| Hydro water reservoir |  |  |  |
| Marine |  |  |  |
| Nuclear |  |  |  |
| Other renewable |  |  |  |
| Solar |  |  |  |
| Waste |  |  |  |
| Wind offshore |  |  |  |
| Wind onshore |  |  |  |
| Other |  |  |  |

SCHEDULE 12 - DEMAND CONTROL

PAGE 1 OF 2

The following information is required from each Network Operator and where indicated with an asterisk from Externally Interconnected System Operators and/or Interconnector Users and a Pumped Storage Generator and Generators in respect of Electricity Storage Modules. Where indicated with a double asterisk, the information is only required from Suppliers.

| DATA DESCRIPTION | UNITS |  | UPDATE TIME |  |
| --- | --- | --- | --- | --- |
| Demand Control |  |  |  |  |
| Demand met or to be relieved by Demand Control (averaging at the Demand Control Notification Level or more over a half hour) at each Connection Point. |  |  |  |  |
| Demand Control at time of National Electricity Transmission System weekly peak demand |  |  |  |  |
| Amount | MW | )F.yrs 0 to 5 | Week 24 | OC1 |
| Duration | Min | ) |  |  |
| For each half hour | MW | Wks 2-8 ahead | 1000 Mon | OC1 |
| For each half hour | MW | Days 2-12 ahead | 1200 Wed | OC1 |
| For each half hour | MW | Previous calendar day | 0600 daily | OC1 |
| **Customer Demand Management (at the Customer Demand Management Notification Level or more at the Connection Point) |  |  |  |  |
| For each half hour | MW | Any time in Control Phase |  | OC1 |
| For each half hour | MW | Remainder of period | When changes occur to previous plan | OC1 |
| For each half hour | MW | Previous calendar day | 0600 daily | OC1 |
| **In Scotland, Load Management Blocks For each block of 5MW or more, for each half hour | MW | For the next day | 11:00 | OC1 |

SCHEDULE 12 - DEMAND CONTROL

PAGE 2 OF 2

| DATA DESCRIPTION | UNITS | TIME COVERED | UPDATE TIME | DATA CAT. |
| --- | --- | --- | --- | --- |
| *Demand Control or Pump Tripping Offered as Reserve |  |  |  |  |
| Magnitude of Demand or pumping load or Electricity Storage charging load which is tripped | MW | Year ahead from week 24 | Week 24 | DPD I |
| System Frequency at which tripping is initiated | Hz | " | " | " |
| Time duration of System Frequency below trip setting for tripping to be initiated | S | " | " | " |
| Time delay from trip initiation to Tripping Electricity Storage Module data Maximum Capacity Maximum Import Power Registered Import Capability Charge Time Discharge time Operating periods | S MW MW MW Min Min Min | " " " " " " “ “ “ | " " " " " " “ “ “ | " " " " " " “ “ “ |
| Emergency Manual Load Disconnection |  |  |  |  |
| Method of achieving load disconnection | Text | Year ahead from week 24 | Annual in week 24 | OC6 |
| Annual ACS Peak Demand (Active Power) at Connection Point (requested under Schedule 11 - repeated here for reference) | MW | " | " | " |
| Cumulative percentage of Connection Point Demand (Active Power) which can be disconnected by the following times from an instruction from The Company |  |  |  |  |
| 5 mins | % | " | " | " |
| 10 mins | % | " | " | " |
| 15 mins | % | " | " | " |
| 20 mins | % | " | " | " |
| 25 mins | % | " | " | " |
| 30 mins | % | " | " | " |

Notes:

1.	Network Operators may delay the submission until calendar week 28.

2.	No information collated under this Schedule will be transferred to the Relevant Transmission Licensees (or Generators undertaking OTSDUW).

SCHEDULE 12A - AUTOMATIC LOW FREQUENCY DEMAND DISCONNECTION

PAGE 1 OF 1

Time Covered:  Year ahead from week 24					Data Category: 	OC6

Update Time:	Annual in week 24

|  | GSP Demand | Low Frequency Demand Disconnection Blocks MW |  |  |  |  |  |  |  |  | Residual |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Grid Supply Point |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | demand |
|  | MW | 48.8Hz | 48.75Hz | 48.7Hz | 48.6Hz | 48.5Hz | 48.4Hz | 48.2Hz | 48.0Hz | 47.8Hz | MW |
| GSP1 |  |  |  |  |  |  |  |  |  |  |  |
| GSP2 |  |  |  |  |  |  |  |  |  |  |  |
| GSP3 |  |  |  |  |  |  |  |  |  |  |  |
| Total demand disconnected MW per block % |  |  |  |  |  |  |  |  |  |  |  |
| Total demand disconnection MW ( % of aggregate demand of MW) |  |  |  |  |  |  |  |  |  |  |  |

Note:	All demand refers to that at the time of forecast National Electricity Transmission System peak demand.

Network Operators may delay the submission until calendar week 28

No information collated under this schedule will be transferred to the Relevant Transmission 	Licensees (or Generators undertaking OTSDUW).

SCHEDULE 13 - FAULT INFEED DATA

PAGE 1 OF 2

The data in this Schedule 13 is all Standard Planning Data, and is required from all Users other than  Generators who are connected to the National Electricity Transmission System via a Connection Point (or who are seeking such a connection).  A data submission is to be made each year in Week 24 (although Network Operators may delay the submission until Week 28).  A separate submission is required for each node included in the Single Line Diagram provided in Schedule 5.

| DATA DESCRIPTION | UNITS | F.Yr 0 | F.Yr. 1 | F.Yr. 2 | F.Yr. 3 | F.Yr. 4 | F.Yr. 5 | F.Yr. 6 | F.Yr. 7 |  | DATA to RTL |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| SHORT CIRCUIT INFEED TO THE NATIONAL ELECTRICITY TRANSMISSION SYSTEM FROM USERS SYSTEM AT A CONNECTION POINT |  |  |  |  |  |  |  |  |  |  | CUSC Contract | CUSC App. Form |  |
| (PC.A.2.5) |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Name of node or Connection Point |  |  |  |  |  |  |  |  |  | □ |  |  | ■ |
| Symmetrical three phase short-circuit current infeed |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - at instant of fault | kA |  |  |  |  |  |  |  |  | □ |  |  | ■ |
| - after subtransient fault current contribution has substantially decayed | Ka |  |  |  |  |  |  |  |  | □ |  |  | ■ |
| Zero sequence source impedances as seen from the Point of Connection or node on the Single Line Diagram (as appropriate) consistent with the maximum infeed above: |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - Resistance | % on 100 |  |  |  |  |  |  |  |  | □ |  |  | ■ |
| - Reactance | % on 100 |  |  |  |  |  |  |  |  | □ |  |  | ■ |
| Positive sequence X/R ratio at instance of fault |  |  |  |  |  |  |  |  |  | □ |  |  | ■ |
| Pre-Fault voltage magnitude at which the maximum fault currents were calculated | p.u. |  |  |  |  |  |  |  |  | □ |  |  | ■ |

SCHEDULE 13 - FAULT INFEED DATA

PAGE 2 OF 2

| DATA DESCRIPTION | UNITS | F.Yr 0 | F.Yr. 1 | F.Yr. 2 | F.Yr. 3 | F.Yr. 4 | F.Yr. 5 | F.Yr. 6 | F.Yr. 7 | DATA to RTL |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| SHORT CIRCUIT INFEED TO THE NATIONAL ELECTRICITY TRANSMISSION SYSTEM FROM USERS SYSTEM AT A CONNECTION POINT |  |  |  |  |  |  |  |  |  | CUSC Contract | CUSC App. Form |
| Negative sequence impedances of User’s System as seen from the Point of Connection or node on the Single Line Diagram (as appropriate). If no data is given, it will be assumed that they are equal to the positive sequence values. |  |  |  |  |  |  |  |  |  |  |  |
| - Resistance | % on 100 |  |  |  |  |  |  |  |  | □ | ■ |
| - Reactance | % on 100 |  |  |  |  |  |  |  |  | □ | ■ |

SCHEDULE 14 - FAULT INFEED DATA (GENERATORS INCLUDING UNIT TRANSFORMERS AND STATION TRANSFORMERS)

PAGE 1 OF 5

The data in this Schedule 14 is all Standard Planning Data, and is to be provided by Generators, with respect to all directly connected Power Stations, all Embedded Large Power Stations and all Embedded Medium Power Stations connected to the Subtransmission System. A data submission is to be made each year in Week 24.

Fault infeeds via Unit Transformers

A submission should be made for each Generating Unit  (including those which are part of a Synchronous Power Generating Module) with an associated Unit Transformer.  Where there is more than one Unit Transformer associated with a Generating Unit, a value for the total infeed through all Unit Transformers should be provided. The infeed through the Unit Transformer(s) should include contributions from all motors normally connected to the Unit Board, together with any generation (e.g. Auxiliary Gas Turbines) which would normally be connected to the Unit Board, and should be expressed as a fault current at the Generating Unit terminals for a fault at that location.

| DATA DESCRIPTION |  |  | UNITS |  | F.Yr. 0 |  | F.Yr. 1 |  |  | F.Yr 2 |  |  | F.Yr. 3 |  |  | F.Yr. 4 |  |  | F.Yr. 5 |  |  | F.Yr. 6 |  |  | F.Yr. 7 | DATA to RTL |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| (PC.A.2.5) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | CUSC Contract |  |  | CUSC App. Form |
| Name of Power Station Number of Unit Transformers |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | □ □ |  |  | ■ ■ |
| Symmetrical three phase short- circuit current infeed through the Unit Transformers(s) for a fault at the Generating Unit terminals |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - at instant of fault |  | kA |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | □ | ■ |  |
| - after subtransient fault current contribution has substantially decayed Positive sequence X/R ratio at instance of fault Subtransient time constant (if significantly different from 40ms) Pre-fault voltage at fault point (if different from 1.0 p.u.) The following data items need only be supplied if the Generating Unit Step-up Transformer can supply zero sequence current from the Generating Unit side to the National Electricity Transmission System |  | kA ms |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | □ □ □ □ | ■ ■ ■ ■ |  |
| Zero sequence source impedances as seen from the Generating Unit terminals consistent with the maximum infeed above: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - Resistance |  | % on 100 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | □ | ■ |  |
| - Reactance |  | % on 100 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | □ | ■ |  |

SCHEDULE 14 - FAULT INFEED DATA (GENERATORS INCLUDING UNIT TRANSFORMERS AND STATION TRANSFORMERS)

PAGE 2 OF 5

Fault infeeds via Station Transformers

A submission is required for each Station Transformer directly connected to the National Electricity Transmission System.  The submission should represent normal operating conditions when the maximum number of Gensets are Synchronised to the System, and should include the fault current from all motors normally connected to the Station Board, together with any Generation (e.g. Auxiliary Gas Turbines) which would normally be connected to the Station Board. The fault infeed should be expressed as a fault current at the hv terminals of the Station Transformer for a fault at that location.

If the submission for normal operating conditions does not represent the worst case, then a separate submission representing the maximum fault infeed that could occur in practice should be made.

| DATA DESCRIPTION | UNITS | F.Yr. 0 | F.Yr. 1 | F.Yr. 2 | F.Yr. 3 | F.Yr. 4 | F.Yr. 5 | F.Yr. 6 | F.Yr. 7 | DATA to RTL |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| (PC.A.2.5) |  |  |  |  |  |  |  |  |  | CUSC Contract | CUSC App. Form |
| Name of Power Station |  |  |  |  |  |  |  |  |  | □ | ■ |
| Number of Station Transformers |  |  |  |  |  |  |  |  |  | □ | ■ |
| Symmetrical three phase short-circuit current infeed for a fault at the Connection Point |  |  |  |  |  |  |  |  |  |  |  |
| - at instant of fault | kA |  |  |  |  |  |  |  |  | □ | ■ |
| - after subtransient fault current contribution has substantially decayed | kA |  |  |  |  |  |  |  |  | □ | ■ |
| Positive sequence X/R ratio At instance of fault |  |  |  |  |  |  |  |  |  | □ | ■ |
| Subtransient time constant (if significantly different from 40ms) | ms |  |  |  |  |  |  |  |  | □ | ■ |
| Pre-fault voltage (if different from 1.0 p.u.) at fault point (See note 1) |  |  |  |  |  |  |  |  |  | □ | ■ |
| Zero sequence source Impedances as seen from the Point of Connection Consistent with the maximum Infeed above: |  |  |  |  |  |  |  |  |  |  |  |
| - Resistance | % on 100 |  |  |  |  |  |  |  |  | □ | ■ |
| - Reactance | % on 100 |  |  |  |  |  |  |  |  | □ | ■ |

Note 1.	The pre-fault voltage provided above should represent the voltage within the range 0.95 to 1.05 that gives the highest fault current

Note 2. 	% on 100 is an abbreviation for % on 100 MVA

SCHEDULE 14 - FAULT INFEED DATA (GENERATORS INCLUDING UNIT TRANSFORMERS AND STATION TRANSFORMERS)

PAGE 3 OF 5

Fault infeeds from Power Park Modules

A submission is required for the whole Power Park Module and for each Power Park Unit type or equivalent. The submission shall represent operating conditions that result in the maximum fault infeed. The fault current from all motors normally connected to the Power Park Unit’s electrical system shall be included. The fault infeed shall be expressed as a fault current at the terminals of the Power Park Unit, or the Common Collection Busbar if an equivalent Single Line Diagram and associated data as described in PC.A.2.2.2 is provided, and the Grid Entry Point, or User System Entry Point if Embedded, for a fault at the Grid Entry Point, or User System Entry Point if Embedded.

Should actual data in respect of fault infeeds be unavailable at the time of the application for a CUSC Contract or Embedded Development Agreement, a limited subset of the data, representing the maximum fault infeed that may result from all of the plant types being considered, shall be submitted. This data will, as a minimum,  represent the root mean square of the positive, negative and zero sequence components of the fault current for both single phase and three phase solid faults at the Grid Entry Point (or User System Entry Point if Embedded) at the time of fault application and 50ms following fault application.  Actual data in respect of fault infeeds shall be submitted to The Company as soon as it is available, in line with PC.A.1.2

| DATA DESCRIPTION | UNITS | F.Yr. 0 |  | F.Yr. 1 | F.Yr. 2 |  | F.Yr. 3 |  | F.Yr. 4 |  | F.Yr. 5 |  | F.Yr. 6 |  | F.Yr. 7 |  | DATA to RTL |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| (PC.A.2.5) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | CUSC Contract | CUSC App. Form |
| Name of Power Station |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | □ | ■ |
| Name of Power Park Module |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | □ | ■ |
| #### Power Park Unit type |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | □ | ■ |
| A submission shall be provided for the contribution of the entire Power Park Module and each type of Power Park Unit or equivalent to the positive, negative and zero sequence components of the short circuit current at the Power Park Unit terminals, or Common Collection Busbar, and Grid Entry Point or User System Entry Point if Embedded for (i) a solid symmetrical three phase short circuit (ii) a solid single phase to earth short circuit (iii) a solid phase to phase short circuit (iv) a solid two phase to earth short circuit at the Grid Entry Point or User System Entry Point if Embedded. If protective controls are used and active for the above conditions, a submission shall be provided in the limiting case where the protective control is not active. This case may require application of a non-solid fault, resulting in a retained voltage at the fault point. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | □ □ □ □ □ | ■ ■ ■ ■ ■ |

SCHEDULE 14 - FAULT INFEED DATA (GENERATORS INCLUDING UNIT TRANSFORMERS AND STATION TRANSFORMERS)

PAGE 4 OF 5

| DATA DESCRIPTION | UNITS | F.Yr. 0 | F.Yr. 1 | F.Yr. 2 | F.Yr. 3 | F.Yr. 4 | F.Yr. 5 | F.Yr. 6 | F.Yr. 7 | DATA to RTL | DATA DESCRIPTION |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  |  |  |  |  | CUSC Contract | CUSC App. Form |
| - A continuous time trace and table showing the root mean square of the positive, negative and zero sequence components of the fault current from the time of fault inception to 140ms after fault inception at 10ms intervals | Graphical and tabular kA versus s |  |  |  |  |  |  |  |  | □ | ■ |
| - A continuous time trace and table showing the positive, negative and zero sequence components of retained voltage at the terminals or Common Collection Busbar, if appropriate | pu versus s |  |  |  |  |  |  |  |  | □ | ■ |
| - A continuous time trace and table showing the root mean square of the positive, negative and zero sequence components of retained voltage at the fault point, if appropriate | pu versus s |  |  |  |  |  |  |  |  | □ | ■ |

SCHEDULE 14 - FAULT INFEED DATA (GENERATORS INCLUDING UNIT TRANSFORMERS AND STATION TRANSFORMERS)

PAGE 5 OF 5

| DATA DESCRIPTION | UNITS | F.Yr. 0 | F.Yr. 1 | F.Yr. 2 | F.Yr. 3 | F.Yr. 4 | F.Yr. 5 | F.Yr. 6 | F.Yr. 7 | DATA to RTL | DATA DESCRIPTION |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  |  |  |  |  | CUSC Contract | CUSC App. Form |
| For Power Park Units that utilise a protective control, such as a crowbar circuit, - additional rotor resistance applied to the Power Park Unit under a fault situation - additional rotor reactance applied to the Power Park Unit under a fault situation. | % on MVA % on MVA |  |  |  |  |  |  |  |  | □ □ | ■ ■ |
| Positive sequence X/R ratio of the equivalent at time of fault at the Common Collection Busbar |  |  |  |  |  |  |  |  |  | □ | ■ |
| Minimum zero sequence impedance of the equivalent at a Common Collection Busbar |  |  |  |  |  |  |  |  |  | □ | ■ |
| Active Power generated pre-fault | MW |  |  |  |  |  |  |  |  | □ | ■ |
| Number of Power Park Units in equivalent generator |  |  |  |  |  |  |  |  |  | □ | ■ |
| Power Factor (lead or lag) |  |  |  |  |  |  |  |  |  | □ | ■ |
| Pre-fault voltage (if different from 1.0 pu) at fault point (See note 1) | pu |  |  |  |  |  |  |  |  | □ | ■ |
| Items of reactive compensation switched in pre-fault |  |  |  |  |  |  |  |  |  | □ | ■ |

Note 1.	The pre-fault voltage provided above should represent the voltage within the range 0.95 pu to 1.05 pu that gives the highest fault current

SCHEDULE 15 – MOTHBALLED POWER GENERATING MODULE, MOTHBALLED GENERATING UNIT, MOTHBALLED POWER PARK MODULE (INCLUDING MOTHBALLED DC CONNECTED POWER PARK MODULES), MOTHBALLED HVDC SYSTEMS, MOTHBALLED HVDC CONVERTERS, MOTHBALLED DC CONVERTERS AT A DC CONVERTER STATION AND ALTERNATIVE FUEL DATA

PAGE 1 OF 3

MOTHBALLED POWER GENERATING MODULES, MOTHBALLED GENERATING UNIT, MOTHBALLED POWER PARK MODULE (INCLUDING MOTHBALLED DC CONNECTED POWER PARK MODULES), MOTHBALLED HVDC SYSTEMS, MOTHBALLED HVDC CONVERTERS OR MOTHBALLED DC CONVERTER  AT A DC CONVERTER STATION  AND ALTERNATIVE FUEL DATA

The following data items must be supplied with respect to each Mothballed Power Generating Module, Mothballed Generating Unit, Mothballed Power Park Module (including Mothballed DC Connected Power Park Modules), Mothballed HVDC Systems, Mothballed HVDC Converters or Mothballed DC Converters at a DC Converter station

Power Station	Generating Unit, Power Park Module or DC Converter Name (e.g. Unit 1)

| Data Description | Units | Data CAT | Generating Unit Data |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | <1 month | 1-2 months | 2-3 months | 3-6 months | 6-12 months | >12 months | Total MW being returned |
| MW output that can be returned to service | MW | DPD II |  |  |  |  |  |  |  |

Notes

- The time periods identified in the above table represent the estimated time it would take to return the Mothballed Power Generating Module, Mothballed Generating Unit, Mothballed Power Park Module (Mothballed DC Connected Power Park Modules), Mothballed HVDC Systems, Mothballed HVDC Converters or Mothballed DC Converter at a DC Converter Station to service once a decision to return has been made.

- Where a Mothballed Power Generating Module, Mothballed Generating Unit, Mothballed Power Park Module (including a Mothballed DC Connected Power Park Module), Mothballed HVDC System, Mothballed HVDC Converter or Mothballed DC Converter at a DC Converter Station can be physically returned in stages covering more than one of the time periods identified in the above table then information should be provided for each applicable time period.

- The estimated notice to physically return MW output to service should be determined in accordance with Good Industry Practice assuming normal working arrangements and normal plant procurement lead times.

- The MW output values in each time period should be incremental MW values, e.g. if 150MW could be returned in 2 – 3 months and an additional 50MW in 3 – 6 months then the values in the columns should be Nil, Nil, 150, 50, Nil, Nil, 200 respectively.

- Significant factors which may prevent the Mothballed Power Generating Module, Mothballed Generating Unit, Mothballed Power Park Module (Mothballed DC Connected Power Park Module). Mothballed HVDC System, Mothballed HVDC Converter or Mothballed DC Converter at a DC Converter Station achieving the estimated values provided in this table, excluding factors relating to Transmission Entry Capacity, should be appended separately.

SCHEDULE 15 – MOTHBALLED POWER GENERATING MODULES, MOTHBALLED GENERATING UNIT, MOTHBALLED POWER PARK MODULE (INCLUDING DC CONNECTED POWER PARK MODULES), MOTHBALLED HVDC SYSTEMS, MOTHBALLED HVDC CONVERTERS, MOTHBALLED DC CONVERTERS AT A DC CONVERTER STATION AND ALTERNATIVE FUEL DATA

PAGE 2 OF 3

ALTERNATIVE FUEL INFORMATION

The following data items for alternative fuels need only be supplied with respect to each Generating Unit whose primary fuel is gas including those which form part of a Power Generating Module.

Power Station	 Generating Unit Name (e.g. Unit 1)

| Data Description | Units | Data CAT | Generating Unit Data |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  |  |  | 1 | 2 | 3 | 4 |
| Alternative Fuel Type (*please specify) | Text | DPD II | Oil distillate | Other gas* | Other* | Other* |
| CHANGEOVER TO ALTERNATIVE FUEL For off-line changeover: |  |  |  |  |  |  |
| Time to carry out off-line fuel changeover | Minutes | DPD II |  |  |  |  |
| Maximum output following off-line changeover | MW | DPD II |  |  |  |  |
| For on-line changeover: |  |  |  |  |  |  |
| Time to carry out on0ine fuel changeover | Minutes | DPD II |  |  |  |  |
| Maximum output during on-line fuel changeover | MW | DPD II |  |  |  |  |
| Maximum output following on-line fuel changeover | MW | DPD II |  |  |  |  |
| Maximum operating time at full load assuing: |  |  |  |  |  |  |
| Typical stock levels | Hours | DPD II |  |  |  |  |
| Maximum possible stock levels | Hours | DPD II |  |  |  |  |
| Maximum rate of replacement of depleted stocks of alternative fuels on the basisi of Good Industry Practice | MWh (electrical)/day | DPD II |  |  |  |  |
| Is changeover to alternative fuel used in normal operating arrangements? | Text | DPD II |  |  |  |  |
| Number of successful changeovers carried out in the last Financial Year (**delete as appropriate) | Text | DPD II | 0 / 1-5 / 6-10 / 11-20 / >20 ** | 0 / 1-5 / 6-10 / 11-20 / >20 ** | 0 / 1-5 / 6-10 / 11-20 / >20 ** | 0 / 1-5 / 6-10 / 11-20 / >20 ** |

SCHEDULE 15 – MOTHBALLED POWER GENERATING MODULES, MOTHBALLED GENERATING UNIT, MOTHBALLED POWER PARK MODULE (INCLUDING MOTHBALLED DC CONNECTED POWER PARK MODULES), MOTHBALLED HVDC SYSTEMS, MOTHBALLED HVDC CONVERTERS MOTHBALLED DC CONVERTERS AT A DC CONVERTER STATION AND ALTERNATIVE FUEL DATA

PAGE 3 OF 3

| Data Description | Units | Data CAT | Generating Unit Data |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  |  |  | 1 | 2 | 3 | 4 |
| CHANGEOVER BACK TO MAIN FUEL |  |  |  |  |  |  |
| For off-line changeover: |  |  |  |  |  |  |
| Time to carry out off-line fuel changeover | Minutes |  |  |  |  |  |
| For on-line changeover |  |  |  |  |  |  |
| Time to carry out on-line fuel changeover | Minutes |  |  |  |  |  |
| Maximum output during on-line fuel changeover | MW |  |  |  |  |  |

Notes

- Where a Generating Unit has the facilities installed to generate using more than one alternative fuel type details of each alternative fuel should be given.

- Significant factors and their effects which may prevent the use of alternative fuels achieving the estimated values provided in this table (e.g. emissions limits, distilled water stocks etc.) should be appended separately.

SCHEDULE 16 – SYSTEM RESTORATION  INFORMATION

PAGE 1 OF 6

PART I

| SYSTEM RESTORATION INFORMATION (EXCLUDING THOSE PARTICIPATING IN DISTRIBUTION RESTORATION ZONES) The following data/text items are required from each Generator for each BM Unit at a Large Power Station as detailed in PC.A.5.7. Data is not required for Restoration Contractor’s Plant and Apparatus or Electricity Storage Modules which have short cycle times. The data should be provided in accordance with PC.A.1.2 and also, where possible, upon request from The Company during a System Restoration. For Restoration Contractors who are party to a Distribution Restoration Zone Plan, the data submitted should be supplied as part of Schedule 6 of this Data Registration Code. |  |  |
| --- | --- | --- |
| Data Description (PC.A.5.7.1) (■ CUSC Contract) | Units | Data Category |
| Site name | Text |  |
| Location | Text |  |
| Identity and size of all BMUs at this location | MW |  |
| Are there personnel on site 24 hours a day? | Yes/No |  |
| If yes what is the minimum number of personnel on site at any time? |  |  |
| Is the site controlled from this location? | Yes/No |  |
| If not where is the Control Point? | Text |  |
| Does the Control Point for this site control any other sites? | Yes/No |  |
| How many sites does the control point cover and what is the total power of all these sites? |  |  |

No information collated under this Schedule will be transferred to the Relevant Transmission Licensees

SCHEDULE 16 – SYSTEM RESTORATION  INFORMATION

PAGE 2 OF 6

PART I

| SYSTEM RESTORATION INFORMATION (EXCLUDING THOSE PARTICIPATING IN DISTRIBUTION RESTORATION ZONES) The following data/text items are required from each Generator for each BM Unit at a Large Power Station as detailed in PC.A.5.7. Data is not required for Restoration Contractor’s Plant and Apparatus or Electricity Storage Modules which have short cycle times. The data should be provided in accordance with PC.A.1.2 and also, where possible, upon request from The Company during a System Restoration. For Restoration Contractors who are party to a Distribution Restoration Zone Plan, the data submitted should be supplied as part of Schedule 6 of this Data Registration Code. |  |  |
| --- | --- | --- |
| Data Description (PC.A.5.7.1) (■ CUSC Contract) | Units | Data Category |
| Site Electrical Supplies and Electrical Resilience |  |  |
| Main Site |  |  |
| Site Connection Points for BMUs & Station transformers | Text |  |
| Does the site have any internal back-up power supplies | Yes/No |  |
| If yes please give details of type, power and duration site can be maintained. | Hours |  |
| What is the time duration the site can be maintained in a state of readiness without external power supplies? | Hours |  |
| What is the time duration the site communication equipment can be maintained in service without external power supplies? | Hours |  |
| Control Point |  |  |
| Where is the Control Point electrical supply connection? Is it onsite via site connection or other please give details and MPAN as required | Text |  |
| Does the Control Point have any internal back-up power supplies | Yes/No |  |
| If yes please give details of type, power and duration site can be maintained. | Hours |  |
| What is the time duration the Control Point can continue to operate without external power supplies? | Hours |  |
| What is the time duration the Control Point communications equipment can be maintained in service without external power supplies? | Hours |  |
| What is the time duration the Control Point to Site operating capability communications equipment can be maintained in service without external power supplies? | Hours |  |
| Other Auxiliary site Electrical supplies |  |  |
| Are there any other locations with other electrical power supplies which are operated by the User which are required for the site to operated eg remote intakes at hydro power station, gas take-off points, CW pumphouses | Yes/No |  |
| Where are the electrical supply connections to these other sites? Is it onsite via site connection or other please give details and MPAN as required | Text |  |
| Do these other sites have any internal back-up power supplies | Yes/No |  |
| If yes please give details of type, power and duration site can be maintained. | Hours |  |
| Other Third Party Supplies which the site needs to operate |  |  |
| Are there any other substances being supplied to site by a third party which if they were not being provided would restrict the site’s ability to restart and remain in service, eg water? | Yes/No |  |
| How long can the site operate without these supplies being restored? | Hours |  |

SCHEDULE 16 – SYSTEM RESTORATION  INFORMATION

PAGE 3 OF 6

PART I

| SYSTEM RESTORATION INFORMATION (EXCLUDING THOSE PARTICIPATING IN DISTRIBUTION RESTORATION ZONES) The following data/text items are required from each Generator for each BM Unit at a Large Power Station as detailed in PC.A.5.7. Data is not required for Restoration Contractor’s Plant and Apparatus or Electricity Storage Modules which have short cycle times. The data should be provided in accordance with PC.A.1.2 and also, where possible, upon request from The Company during a System Restoration. For Restoration Contractors who are party to a Distribution Restoration Zone Plan, the data submitted should be supplied as part of Schedule 6 of this Data Registration Code. |  |  |
| --- | --- | --- |
| Data Description (PC.A.5.7.1) (■ CUSC Contract) | Units | Data Category |
| Primary Fuel Type & Storage |  |  |
| Gas Is there any gas stored on-site or is it completely dependent on the gas mains supply, if there is fuel estimated minimum and maximum generation capacity in MWhrs? | MWhrs |  |
| Oil What are the minimum and maximum oil storage levels in terms of estimated generation capacity in MWhrs? | MWhrs |  |
| Coal What are the minimum and maximum coal storage levels in terms of estimated generation capacity in MWhrs? | MWhrs |  |
| Biomass What are the minimum and maximum biomass storage levels in terms of estimated generation capacity in MWhrs? | MWhrs |  |
| Hydro Is the site run of river or is there on-site water storage, and what is the estimated minimum and maximum generation capacity in MWhrs? | MWhrs |  |
| Battery What are the minimum and maximum battery storage levels in terms of estimated generation capacity in MWhrs? | MWhrs |  |
| Wind |  |  |
| Other | MWhrs |  |

SCHEDULE 16 – SYSTEM RESTORATION  INFORMATION

PAGE 4 OF 6

PART I

| SYSTEM RESTORATION INFORMATION (EXCLUDING THOSE PARTICIPATING IN DISTRIBUTION RESTORATION ZONES) The following data/text items are required from each Generator for each BM Unit at a Large Power Station as detailed in PC.A.5.7. Data is not required for Restoration Contractor’s Plant and Apparatus or Electricity Storage Modules which have short cycle times. The data should be provided in accordance with PC.A.1.2 and also, where possible, upon request from The Company during a System Restoration. For Restoration Contractors who are party to a Distribution Restoration Zone Plan, the data submitted should be supplied as part of Schedule 6 of this Data Registration Code. |  |  |
| --- | --- | --- |
| Data Description (PC.A.5.7.1) (■ CUSC Contract) | Units | Data Category |
| Protection and Electrical Switching |  |  |
| Main Plant |  |  |
| Site Connection Points for BMUs & Station transformers | Text |  |
| How is all the electrical protection reset and does it require to be carried out locally or remotely? | Text |  |
| What are the procedures for resetting protection and who is authorised to reset protection and are they on-site? | Text |  |
| Are there any mechanical protection devices such as overspeed devices and do these need to be reset locally? | Text |  |
| Auxiliary Plant |  |  |
| How is all the electrical protection on the auxiliary plant reset and does it require to be carried out locally or remotely? | Text |  |
| Electrical Switching |  |  |
| Who carries out the electrical switching on-site your employees or contractors? | Text |  |
| Are there staff on this site authorised for electrical switching? | Text |  |
| If authorised personnel are not normally on site what are the arrangements to get them to site? | Text |  |

SCHEDULE 16 – SYSTEM RESTORATION  INFORMATION

PAGE 5 OF 6

PART I

| SYSTEM RESTORATION INFORMATION (EXCLUDING THOSE PARTICIPATING IN DISTRIBUTION RESTORATION ZONES) The following data/text items are required from each Generator for each BM Unit at a Large Power Station as detailed in PC.A.5.7. Data is not required for Restoration Contractor’s Plant and Apparatus or Electricity Storage Modules which have short cycle times. The data should be provided in accordance with PC.A.1.2 and also, where possible, upon request from The Company during a System Restoration. For Restoration Contractors who are party to a Distribution Restoration Zone Plan, the data submitted should be supplied as part of Schedule 6 of this Data Registration Code. |  |  |
| --- | --- | --- |
| Data Description (PC.A.5.7.1) (■ CUSC Contract) | Units | Data Category |
| Assuming all BM Units were running immediately prior to the Total Shutdown or Partial Shutdown and in the event of loss of all external power supplies, provide the following information: |  |  |
| From loss of external site supplies what is the estimated time for this site to be ready to be re-energised? | Hours |  |
| Expected time for the first and subsequent BM Units to be Synchronised, at time intervals of 12 hours, 24 hours, 36 hours, 48 hours and 72 hours from the restoration of external power supplies, assuming external power supplies are not available at the User’s Site for up to 2472hrs | Hours Tabular or Graphical | DPD II |
| Describe any likely issues that would have a significant impact on a BM Units time to be Synchronised arising as a direct consequence of the inherent design or operational practice of the HVDC System or DC Converter Station and/or BM Unit, e.g. time from a Total Shutdown or Partial Shutdown at which batteries would be discharged or the availability of primary fuel. | Text | DPD II |
| Block Loading Capability: |  |  |
| Provide estimated Block Loading Capability from 0MW to Registered Capacity and the time between each incremental step of each BM Unit based on when the unit being ‘hot’ (run prior to shutdown) and also ‘cold’ (not run for 48hrs or more prior to the shutdown). was running immediately prior to the Shutdown) and at time intervals of 12 hours, 24 hours, 36 hours, 48 hours and 72 hours after the BM Unit had been Shutdown. The Block Loading Capability should be valid for a frequency deviation of 49.5Hz – 50.5Hz. The data should identify any required ‘hold’ points. | Tabular or Graphical | DPD II |

SCHEDULE 16 – SYSTEM RESTORATION  INFORMATION

PAGE 1 OF 2

PART I

| SYSTEM RESTORATION INFORMATION (EXCLUDING PARTIES PARTICIPATING IN DISTRIBUTION RESTORATION ZONES) The following data/text items are required from each Generator for each BM Unit at a Large Power Station as detailed in PC.A.5.7. Data is not required for Restoration Contractors Plant and Apparatus. The data should be provided in accordance with PC.A.1.2 and also, where possible, upon request from The Company during a System Restoration. For Restoration Contractors who are party to a Distribution Restoration Zone Plan, the data submitted should be supplied as part of Schedule 16 Part II of this Data Registration Code. |  |  |
| --- | --- | --- |
| Data Description (PC.A.5.7.1) (■ CUSC Contract) | Units | Data Category |
| Assuming all BM Units were running immediately prior to the Total Shutdown or Partial Shutdown and in the event of loss of all external power supplies, provide the following information: |  |  |
| a) Expected time for the first and subsequent BM Units to be Synchronised, at time intervals of 12 hours, 24 hours, 36 hours, 48 hours and 72 hours from the restoration of external power supplies, assuming external power supplies are not available at the User’s Site | Tabular or Graphical | DPD II |
| b) Describe any likely issues that would have a significant impact on a BM Unit’s time to be Synchronised arising as a direct consequence of the inherent design or operational practice of the Power Station and/or BM Unit, e.g. limited barring facilities, time from a Total Shutdown or Partial Shutdown at which batteries would be discharged or the availability of primary fuel supplies. | Text | DPD II |
| Block Loading Capability: |  |  |
| c) Provide estimated Block Loading Capability from 0MW to Registered Capacity and the time between each incremental step of each BM Unit based on when the unit was running immediately prior to the Shutdown) and at time intervals of 12 hours, 24 hours, 36 hours, 48 hours and 72 hours after the BM Unit had been Shutdown. The Block Loading Capability should be valid for a frequency deviation of 49.5Hz – 50.5Hz. The data should identify any required ‘hold’ points. | Tabular or Graphical | DPD II |

SCHEDULE 16 – SYSTEM RESTORATION INFORMATION

PAGE 1 OF 1

PART III

| DISTRIBUTION RESTORATION ZONE INFORMATION (PC.A.5.7.2 – DPD) Where a Network Operator has a Distribution Restoration Zone Plan in place, the following data specified shall be submitted by Network Operators and Restoration Contractors, party to a Distribution Restoration Zone Plan. Restoration Contractors shall, where reasonably practicable, submit the relevant information to the Network Operator who shall then supply that information to The Company. |  |  |
| --- | --- | --- |
| Data Description (PC.A.5.7.2) | Units | Data Category |
| The expected time for each Restoration Contractor’s Plant to connect to the Network Operator’s System following a Total Shutdown or Partial Shutdown. The assessment should include the Restoration Contractor’s ability to reconnect or re-synchronise all their Plant, to the Total System at time intervals of 12 hours, 24 hours, 36 hours, 48 hours and 72 hours from the restoration of external power supplies. | Tabular or Graphical | DPD II |
| Additionally, the data and supporting text should highlight any specific issues (eg those that would affect the time before which the Restoration Contractor’s Plant could be energised) that may arise as time progresses from Shutdown without external supplies being restored or the availability of primary fuel supplies. | Tabular or Graphical | DPD II |
| Block Loading Capability |  |  |
| Provide estimated Block Loading Capability from 0MW to Registered Capacity and the time between each incremental step of each Restoration Contractor’s Plant and Apparatus based on when the Restoration Contractor’s Plant and Apparatus was running immediately prior to the Shutdown) and at time intervals of 12 hours, 24 hours, 36 hours, 48 hours and 72 hours after the Restoration Contractor’s Plant and Apparatus had been Shutdown. The Block Loading Capability should be valid for a frequency deviation of 49.5Hz – 50.5Hz. The data should identify any required ‘hold’ points. | Tabular or Graphical | DPD II |
| Governor Setting Information |  |  |
| From 2025 onwards, Restoration Contractors, Generators, HVDC System Owners and DC Converter owners, shall supply the governor setting information in accordance with the applicable requirements of CC.6.3.7 (h) or ECC.6.3.7.3.8. | Tabular or Graphical | DPD II |

SCHEDULE 16 – SYSTEM RESTORATION INFORMATION

PAGE 1 OF 5

PART III

All Users and Restoration Contractors are required to confirm annually they comply with the applicable requirements of OC5.7.  In the case of Generators, HVDC System Owners, DC Converter owners, Non-Embedded Customers, and Network Operators this confirmation shall be provided in their Week 24 submission.

| Assurance Activity | Grid Code Reference | Parties Involved | Frequency of Assurance Activity | The Company Witness required | Date of test result submission/visit | Annual Statement of Compliance (Y/N/Not applicable) |
| --- | --- | --- | --- | --- | --- | --- |
| System Restoration Power Island review | OC9.4.7.6 OC5.7.4.2(iv) | Relevant Transmission Licensees, Network Operators and The Company | Every 3 years | Not applicable |  |  |
| System Restoration Power Island availability assessment | OC9.4.7.6 OC5.7.4.2(iv) | Relevant Transmission Licensees, Network Operators and The Company | Yearly | Not applicable |  |  |
| Remote Synchronisation test - TO/DNO | OC5.7.2.1(g) OC5.7.2.3 (d) | Relevant Transmission Licensees, relevant Network Operators, Restoration Contractors and The Company | Every 3 years | No |  |  |
| Low Frequency Demand Disconnection Relay test | CC.A.5.4.3 / ECC.A.5.4.3 | Relevant Transmission Licences, relevant Network Operators, Non-Embedded Customers and The Company | Every 3 years although this may be extended to no more than every five years if considered to be required for operational purposes | No |  |  |
| Anchor Restoration Contractor test | OC5.7.2.1 /OC5.7.2.2 / OC5.7.2.3 | Relevant Transmission Licensees, Network Operators, Anchor Restoration Contractors and The Company | Every 3 years | Yes |  |  |
| Assurance Activity | Grid Code Reference | Parties Involved | Frequency of Assurance Activity | The Company Witness required | Date of test result submission/visit | Annual Statement of Compliance (Y/N/Not applicable) |
| Top Up Restoration Contractor test | OC.5.7.2.4 | Relevant Transmission Licensees, Network Operators, Top Up Restoration Contractors and The Company | Every 3 years | Yes |  |  |
| Resilience to Partial Shutdown or Total Shutdown of Restoration Contractor | OC9.4.7.6.2 OC5.7.4.2(iii) CC/ECC.7.11 | Restoration Contractors and The Company | Yearly | No |  |  |
| Quick Resynchronisation Unit Test | OC5.7.2.5 | EU Generators in respect of Type C and Type D Power Generating Modules, relevant Network Operators and The Company | Yearly | Yes |  |  |
| Distribution Restoration Zone Control System test | OC5.7.2.6 | Network Operators, Restoration Contractors and The Company | Every 3 years | Yes |  |  |
| Dead Line Charge test | OC5.7.2.1(g)(a) OC5.7.2.3(d)(a) | Transmission Licensees, relevant Network Operators Anchor Restoration Contractors and The Company | Every 3 years | Yes |  |  |
| Remote Synchronisation test -Restoration Contractor | OC5.7.2.1(g)(b) OC5.7.2.3(d)(b) | Relevant Transmission Licensees, relevant Network Operators, Restoration Contractors and The Company | Every 3 years | Yes |  |  |

PAGE 2 OF 5

PART III

| Assurance Activity | Grid Code Reference | PAGE 3 of 5 PART III Parties Involved | Frequency of Assurance Activity | The Company Witness required | Date of test result submission/visit | Annual Statement of Compliance (Y/N/Not applicable) |
| --- | --- | --- | --- | --- | --- | --- |
| Assurance Visits | OC5.7.4 OC5.7.5 | The Company, Relevant Transmission Licensees, relevant Network Operators to visit Restoration Contractors | Every 3 years | Yes |  |  |
| Voice Systems Resilience test or equivalent | OC5.7.4.2(vi) | CUSC Parties, relevant Network Operators, Relevant Transmission Licensees Restoration Contractors and The Company | Yearly | No |  |  |
| Critical Tools and Facilities control systems resilience demonstration –power resilience including power resilience demonstration & connectivity and alarm event handling | OC.5.7.4.2(iii) OC5.7.4.2(ix) OC5.7.4.3 CC.7.10.7 ECC.7.10.7 | CUSC Parties, relevant Network Operators, Relevant Transmission Licensees, Restoration Contractors and The Company | Every 3 years | No |  |  |
| Control systems resilience demonstration – diagram & topology | OC5.7.2.6 | CUSC Parties, relevant Network Operators, Relevant Transmission Licensees, Restoration Contractors and The Company | Every 3 years (as set out in the DRZCS RES)' | No |  |  |
| Cyber-Security | CC.7.10.6 ECC.7.10.6 OC.5.7.4.2(iii) OC5.7.4.2(x) | CUSC Parties, relevant Network Operators, Relevant Transmission Licensees, Restoration Contractors and The Company | Yearly | No |  |  |
| Assurance Activity | Grid Code Reference | Parties Involved | Frequency of Assurance Activity | The Company Witness required | Date of test result submission/visit | Annual Statement of Compliance (Y/N/Not applicable) |
| Telephony services test as per CC/ECC.6.5.4. | CC.6.5.1 – CC.6.5.5 ECC.6.5.1 – ECC.6.5.5 OC.5.7.4.2(vi) OC5.7.4.2(xi) OC5.7.4.2(xii) | CUSC Parties, relevant Network Operators, relevant Transmission Licensees, Restoration Contractors and The Company | Yearly (or as in accordance with CC/ECC.6.5.4.) | No |  |  |
| Resilience to Partial Shutdown or Total Shutdown of CUSC Parties | OC5.7.4 OC5.7.5 | CUSC Parties and The Company | Yearly | No |  |  |
| Restoration Procedure review | OC9.4.7.6.2 OC5.7.4.2(iv) | The Company, Relevant Transmission Licensees, relevant Network Operators, CUSC Parties and Restoration Contractors | Every 3 years | Not applicable |  |  |
| LJRP & DRZP reviews | OC9.4.7.6 OC5.7.4.2(iv) | The Company, Network Operators, Transmission Licensees and Restoration Plan signatories | Every 3 years | Not applicable |  |  |
| Awareness training for Restoration Contractor and CUSC Parties | OC9.4.7.6.2 OC5.7.4 | The Company, relevant Network Operators, Transmission Licensees, CUSC Parties and Restoration Contractors | Every 3 years | Not applicable |  |  |

PAGE 4 OF 5

PART III

| Assurance Activity | Grid Code Reference | Parties Involved | Frequency of Assurance Activity | The Company Witness required | Date of test result submission/visit | Annual Statement of Compliance (Y/N/Not applicable) |
| --- | --- | --- | --- | --- | --- | --- |
| Cross industry training | OC9.4.7.6.2 OC5.7.4 | The Company, Network Operators, Transmission Licensees, CUSC Parties and Restoration Contractors | Every 3 years | Not applicable |  |  |

PAGE 5 OF 5

PART III

SCHEDULE 17 - ACCESS PERIOD DATA

PAGE 1 OF 1

(PC.A.4 - CUSC Contract ■)

Submissions by Users using this Schedule 17 shall commence in 2011 and shall then continue in each year thereafter

| Access Group |  |
| --- | --- |

| Asset Identifier | Start Week | End Week | Maintenance Year (1, 2 or 3) | Duration | Potential Concurrent Outage (Y/N) |
| --- | --- | --- | --- | --- | --- |

Comments

SCHEDULE 18 - OFFSHORE TRANSMISSION SYSTEM DATA

PAGE 1 OF 24

The data in this Schedule 18 is required from Generators who are undertaking OTSDUW and connecting to a Transmission Interface Point.

| DATA DESCRIPTION | UNITS | DATA to RTL |  | DATA CAT. | GENERATING UNIT OR STATION DATA |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | CUSC Cont ract | CUSC App. Form |  | F.Yr0 | F.Yr1 | F.Yr2 | F.Yr3 | F.Yr4 | F.Yr5 | F.Yr 6 |
| INDIVIDUAL OTSDUW DATA |  |  |  |  |  |  |  |  |  |  |  |
| Interface Point Capacity (PC.A.3.2.2 (a)) Performance Chart at the Transmission Interface Point for OTSDUW Plant and Apparatus (PC.A.3.2.2(f)(iv) | MW MVAr | □ □ | ■ ■ |  |  |  |  |  |  |  |  |
| OTSDUW DEMANDS Demand associated with the OTSDUW Plant and Apparatus (excluding OTSDUW DC Converters – see Note 1)) supplied at each Interface Point. The User should also provide the Demand supplied to each Connection Point on the OTSDUW Plant and Apparatus. (PC.A.5.2.5) |  |  |  |  |  |  |  |  |  |  |  |
| - The maximum Demand that could occur. | MW MVAr | □ □ |  | DPD I DPD I |  |  |  |  |  |  |  |
| - Demand at specified time of annual peak half hour of National Electricity Transmission System Demand at Annual ACS Conditions. | MW MVAr | □ □ |  | DPD II DPD II |  |  |  |  |  |  |  |
| - Demand at specified time of annual minimum half-hour of National Electricity Transmission System Demand. | MW MVAr | □ □ |  | DPD II DPD II |  |  |  |  |  |  |  |
| (Note 1 – Demand required from OTSDUW DC Converters should be supplied under page 2 of Schedule 18). |  |  |  |  |  |  |  |  |  |  |  |

SCHEDULE 18 - OFFSHORE TRANSMISSION SYSTEM DATA

PAGE 2 OF 24

OTSDUW USERS SYSTEM DATA

| DATA DESCRIPTION |  | UNITS | DATA to RTL |  | DATA CATEGORY |
| --- | --- | --- | --- | --- | --- |
|  |  |  | CUSC Contract | CUSC App. Form |  |
| OFFSHORE TRANSMISSION SYSTEM LAYOUT (PC.A.2.2.1, PC.A.2.2.2 and P.C.A.2.2.3) |  |  |  |  |  |
| A Single Line Diagram showing connectivity of all of the Offshore Transmission System including all Plant and Apparatus between the Interface Point and all Connection Points is required. |  |  | ■ | ■ | SPD |
| This Single Line Diagram shall depict the arrangement(s) of all of the existing and proposed load current carrying Apparatus relating to both existing and proposed Interface Points and Connection Points, showing electrical circuitry (i.e. overhead lines, underground cables (including subsea cables), power transformers and similar equipment), operating voltages, circuit breakers and phasing arrangements |  |  | ■ | ■ | SPD |
| Operational Diagrams of all substations within the OTSDUW Plant and Apparatus |  |  | ■ | ■ | SPD |
| SUBSTATION INFRASTRUCTURE (PC.A.2.2.6) |  |  |  |  |  |
| For the infrastructure associated with any OTSDUW Plant and Apparatus |  |  |  |  |  |
| Rated 3-phase rms short-circuit withstand current |  | kA | ■ | ■ | SPD |
| Rated 1-phase rms short-circuit withstand current |  | kA | ■ | ■ | SPD |
| Rated Duration of short-circuit withstand |  | s | ■ | ■ | SPD |
| Rated rms continuous current |  | A | ■ | ■ | SPD |
| LUMPED SUSCEPTANCES (PC.A.2.3) |  |  |  |  |  |
| Equivalent Lumped Susceptance required for all parts of the User’s Subtransmission System (including OTSDUW Plant and Apparatus) which are not included in the Single Line Diagram. |  |  | ■ | ■ |  |
| This should not include: |  |  | ■ | ■ |  |
| (a) | independently switched reactive compensation equipment identified above. |  | ■ | ■ |  |
| (b) | any susceptance of the OTSDUW Plant and Apparatus inherent in the Demand (Reactive Power) data provided on Page 1 and 2 of this Schedule 14. |  | ■ | ■ |  |
| Equivalent lumped shunt susceptance at nominal Frequency. |  | % on 100 MVA | ■ | ■ |  |

SCHEDULE 18 - OFFSHORE TRANSMISSION SYSTEM DATA

PAGE 3 OF 24

OFFSHORE TRANSMISSION SYSTEM DATA

Branch  Data (PC.A.2.2.4)

| Node 1 | Node 2 | Rated Voltage kV | Operating Voltage kV | Circuit | PPS PARAMETERS |  |  | ZPS PARAMETERS |  |  | Maximum Continuous Ratings |  |  | Length (km) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  | R | X | B | R | X | B | R | X | B |  |

Notes

- For information equivalent STC Reference: STCP12-1m Part 3 – 2.1 Branch Data

- In the case where an overhead line exists within the OTSDUW Plant and Apparatus the Mutual inductances should also be provided.

SCHEDULE 18 - OFFSHORE TRANSMISSION SYSTEM DATA

PAGE 4 OF 24

OFFSHORE TRANSMISSION SYSTEM DATA

2 Winding Transformer Data (PC.A.2.2.5)

The data below is Standard Planning Data, and details should be shown below of all transformers shown on the Single Line Diagram

| HV Node | HV (kV) | LV Node | LV (kV) | Rating (MVA) | Transformer | Positive Phase Sequence Reactance % on 100MVA |  |  | Positive Phase Sequence Resistance % on 100MVA |  |  | Tap Changer |  |  | Winding Arr | Earthing method (Direct/ Res/ Reac) | Earthing Impedance method |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  | Max Tap | Min Tap | Nom Tap | Max Tap | Min Tap | Nom Tap | Range +% to -% | Step size % | Type |  |  |  |

Notes

1 For information the corresponding STC Reference is STCP12-1: Part 3 – 2.4 Transformers

SCHEDULE 18 - OFFSHORE TRANSMISSION SYSTEM DATA

PAGE 5 OF 24

USERS SYSTEM DATA (OTSUA)

Auto Transformer Data 3-Winding (PC.A.2.2.5)

The data below is all Standard Planning Data, and details should be shown below of all transformers shown on the Single Line Diagram

| HV Node | HV (kV) | LV Node | LV (kV) | PSS/E Circuit | Rating (MVA) | Trans-former | Positive Phase Sequence Reactance % on 100MVA |  |  | Positive Phase Sequence Resistance % on 100MVA |  |  | Taps |  |  | Win-ding Arr | Earth-ing Impe-dance method |  |  |  |  |  |  | The Com-pany Sheet | The Com-pany Code |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  |  | Max Tap | Min Tap | Nom Tap | Max Tap | Min Tap | Nom Tap | Range +% to -% | Step size % | Type |  |  | ZOH |  | ZOL |  | ZOT Dflt X/R=20 |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | ROH % 100 MVA | XOH % 100 MVA | ROL % 100 MVA | XOL % 100 MVA | ROT % 100 MVA | XOT % 100 MVA |  |  |

Notes

1.For information STC Reference: STCP12-1: Part 3 - 2.4  Transformers

SCHEDULE 18 - OFFSHORE TRANSMISSION SYSTEM DATA

PAGE 6 OF 24

# OFFSHORE TRANSMISSION SYSTEM DATA

# Circuit Breaker Data (PC.A.2.2.6(a))

The data below is all Standard Planning Data, and should be provided for all OTSUA switchgear (i.e. circuit breakers, load disconnectors and disconnectors)

|  | Circuit Breaker Data |  |  |  |  |  |  | Assumed Operating Times |  |  | Conti-nuos Rating | 3 Phase |  |  |  | 1 Phase |  |  |  | DC time constant at testing of asymmetrical breaking ability (s) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Location | Name | Rated Voltage | Oper-ating Voltage | Make | Model | Type | Yr Comm-issioed | Circuit Breaker (ms) | Minimum Protection and Trip Relay (ms) | Total Time |  | Fault Rating (RMS Symmerical) (3 phase MVA) | Fault Break Rating (RMS Symmertrical) (3 phase) (kA) | Fault Break Rating (Peak Asymmetrical) (3 phase) (kA) | Fault Make Rating (Peak Asymmetrical) (3 phase) (kA) | Fault Rating (RMS Symmerical) (1 phase MVA) | Fault Break Rating (RMS Symmertrical) (1 phase) (kA) | Fault Break Rating (Peak Asymmetrical) (1 phase) (kA) | Fault Make Rating (Peak Asymmetrical) (1 phase) (kA) |  |

SCHEDULE 18 - OFFSHORE TRANSMISSION SYSTEM DATA

PAGE 7 OF 24

| # OFFSHORE TRANSMISSION SYSTEM DATA REACTIVE COMPENSATION EQUIPMENT (PC.A.2.4(e)) |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Item | Node | kV | Device No. | Rating (MVAr) | P Loss (kW) | Tap range | Connection Arrangement |
| Notes: 1.For information STC Reference: STCP12-1: Part 3 - 2.5 Reactive Compensation Equipment 2. Data relating to continuously variable reactive compensation equipment (such as statcoms or SVCs) should be entered on the SVC Modelling table. 3. For the avoidance of doubt this includes any AC Reactive Compensation equipment included within the OTSDUW DC Converter other than harmonic filter data which is to be entered in the harmonic filter data table. |  |  |  |  |  |  |  |

| PC.A.2.4.1(e) | A mathematical representation in block diagram format to model the control of any dynamic compensation plant. The model should be suitable for RMS dynamic stability type studies in which the time constants used should not be less than 10ms. |
| --- | --- |

SCHEDULE 18 - OFFSHORE TRANSMISSION SYSTEM DATA

PAGE 8 OF 24

# OFFSHORE TRANSMISSION SYSTEM DATA

REACTIVE COMPENSATION  - SVC Modelling Data (PC.A.2.4.1(e)(iii))

| HV node | LV Node | Control Node | Nominal Voltage (kV) | Target Voltage (kV) | Max MVAr at HV | Min MVAr at HV | Slope % | Voltage Dependent Q Limit | Normal Running Mode | R1 PPS_R | X1 PPS_X | R0 ZPS_R | Z0 ZPS_X | Trasnf Winding Type | Connection (Direct/ Tertiary) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

Notes:

1.For information the equivalent  STC Reference is: STCP12-1: Part 3 - 2.7 SVC Modelling Data

SCHEDULE 18 - OFFSHORE TRANSMISSION SYSTEM DATA

PAGE 9 OF 24

# OFFSHORE TRANSMISSION SYSTEM DATA

Harmonic Filter Data (including OTSDUW DC Converter harmonic Filter Data)

(PC.A.5.4.3.1(d) and PC.A.6.4.2)

| Site Name |  | SLD Reference |  | Point of Filter Connection |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Filter Description |  |  |  |  |  |  |  |  |
| Manufacturer |  | Model |  | Filter Type |  | Filter connection type (Delta/Star, Grounded/ Ungrounded) |  | Notes |
| Bus Voltage |  | Rating |  | Q factor |  | Tuning Frequency |  | Notes |
| Component Parameters (as per SLD) |  |  |  |  |  |  |  |  |
|  | Parameter as applicable |  |  |  |  |  |  |  |
| Filter Component (R, C or L) | Capacitance (micro-Farads) |  | Inductance (milli-Henrys) |  |  | Resistance (Ohms) |  | Notes |
| Filter frequency characteristics (graphs) detailing for frequency range up to 10kHz and higher |  |  |  |  |  |  |  |  |
| 1. Graph of impedance (ohm) against frequency (Hz) |  |  |  |  |  |  |  |  |
| 2. Graph of angle (degree) against frequency (Hz) |  |  |  |  |  |  |  |  |
| 3. Connection diagram of Filter & Elements |  |  |  |  |  |  |  |  |

Notes:

- For information STC Reference: STCP12-1: Part 3 - 2.8 Harmonic Filter Data

SCHEDULE 18 - OFFSHORE TRANSMISSION SYSTEM DATA

PAGE 10 OF 24

# Information for Transient Overvoltage Assessment (DPD I) (PC.A.6.2 ■ CUSC Contract)

The information listed below may be requested by The Company from each User undertaking OTSDUW with respect to any Interface Point or Connection Point to enable The Company to assess transient overvoltage on the National Electricity Transmission System.

(a) 	Busbar layout plan(s), including dimensions and geometry showing positioning of any current and voltage transformers, through bushings, support insulators, disconnectors, circuit breakers, surge arresters, etc.  Electrical parameters of any associated current and voltage transformers, stray capacitances of wall bushings and support insulators, and grading capacitances of circuit breakers;

(b)		Electrical parameters and physical construction details of lines and cables connected at that busbar.  Electrical parameters of all plant e.g., transformers (including neutral earthing impedance or zig-zag transformers if any), series reactors and shunt compensation equipment connected at that busbar (or to the tertiary of a transformer) or by lines or cables to that busbar;

(c)		Basic insulation levels (BIL) of all Apparatus connected directly, by lines or by cables to the busbar;

(d)		Characteristics of overvoltage Protection devices at the busbar and at the termination points of all lines, and all cables connected to the busbar;

(e) 	Fault levels at the lower voltage terminals of each transformer connected to each Interface Point or Connection Point without intermediate transformation;

(f)		The following data is required on all transformers within the OTSDUW Plant and Apparatus.

(g) 	An indication of which items of equipment may be out of service simultaneously during Planned Outage conditions.

# Harmonic Studies (DPD I) (PC.A.6.4 ■ CUSC Contract)

The information given below, both current and forecast, where not already supplied in this Schedule 14 may be requested by The Company from each User if it is necessary for The Company to evaluate the production/magnification of harmonic distortion on National Electricity Transmission System.  The impact of any third party Embedded within the User’s System should be reflected:-

(a)	Overhead lines and underground cable circuits (including subsea cables) of the User's OTSDUW Plant and Apparatus must be differentiated and the following data provided separately for each type:-

Positive phase sequence resistance

Positive phase sequence reactance

Positive phase sequence susceptance

(b)		for all transformers connecting the OTSDUW Plant and Apparatus to a lower voltage:-

Rated MVA

Voltage Ratio

Positive phase sequence resistance

Positive phase sequence reactance

SCHEDULE 18 - OFFSHORE TRANSMISSION SYSTEM DATA

PAGE 11 OF 24

(c)		at the lower voltage points of those connecting transformers:-

Equivalent positive phase sequence susceptance

# Connection voltage and MVAr rating of any capacitor bank and component design parameters if configured as a filter

Equivalent positive phase sequence interconnection impedance with other lower voltage points

The minimum and maximum Demand (both MW and MVAr) that could occur

Harmonic current injection sources in Amps at the Connection Points and Interface Points

(d)	an indication of which items of equipment may be out of service simultaneously during Planned Outage conditions

# Voltage Assessment Studies (DPD I) (PC.A.6.5 ■ CUSC Contract)

The information listed below, where not already supplied in this Schedule 14, may be requested by The Company from each User undertaking OTSDUW with respect to any Connection Point or Interface Point if it is necessary for The Company to undertake detailed voltage assessment studies (e.g. to examine potential voltage instability, voltage control co-ordination or to calculate voltage step changes on the National Electricity Transmission System).

(a)	For all circuits of the User’s OTSDUW Plant and Apparatus:-

Positive Phase Sequence Reactance

Positive Phase Sequence Resistance

Positive Phase Sequence Susceptance

MVAr rating of any reactive compensation equipment

(b) 	for all transformers connecting the User's OTSDUW Plant and Apparatus to a lower voltage:-

Rated MVA

Voltage Ratio

Positive phase sequence resistance

Positive Phase sequence reactance

Tap-changer range

Number of tap steps

Tap-changer type: on-load or off-circuit

AVC/tap-changer time delay to first tap movement

AVC/tap-changer inter-tap time delay

(c) 	at the lower voltage points of those connecting transformers

Equivalent positive phase sequence susceptance

MVAr rating of any reactive compensation equipment

Equivalent positive phase sequence interconnection impedance with other lower voltage points

The maximum Demand (both MW and MVAr) that could occur

Estimate of voltage insensitive (constant power) load content in % of total load at both winter peak and 75% off-peak load conditions

SCHEDULE 18 - OFFSHORE TRANSMISSION SYSTEM DATA

PAGE 12 OF 24

# Short Circuit Analyses:(DPD I) (PC.A.6.6 ■ CUSC Contract)

The information listed below, both current and forecast, and where not already supplied under this Schedule 14, may be requested by The Company from each User undertaking OTSDUW with respect to any Connection Point or Interface Point where prospective short-circuit currents on Transmission equipment are close to the equipment rating.

- For all circuits of the User’s OTSDUW Plant and Apparatus:-

Positive phase sequence resistance

Positive phase sequence reactance

Positive phase sequence susceptance

Zero phase sequence resistance (both self and mutuals)

Zero phase sequence reactance (both self and mutuals)

Zero phase sequence susceptance (both self and mutuals)

- For all transformers connecting the User's OTSDUW Plant and Apparatus to a lower voltage:-

Rated MVA

Voltage Ratio

Positive phase sequence resistance (at max, min and nominal tap)

Positive Phase sequence reactance (at max, min and nominal tap)

Zero phase sequence reactance (at nominal tap)

Tap changer range

Earthing method: direct, resistance or reactance

Impedance if not directly earthed

(c)  	At the lower voltage points of those connecting transformers:-

# The maximum Demand (in MW and MVAr) that could occur

Short-circuit infeed data in accordance with PC.A.2.5.6(a) unless the User’s OTSDUW Plant and Apparatus runs in parallel with the Subtransmission System, when to prevent double counting in each node infeed data, a  equivalent comprising the data items of PC.A.2.5.6(a) for each node together with the positive phase sequence interconnection impedance between the nodes shall be submitted.

SCHEDULE 18 - OFFSHORE TRANSMISSION SYSTEM DATA

PAGE 13 OF 24

# Fault infeed data to be submitted by OTSDUW Plant and Apparatus providing a fault infeed (including OTSDUW DC Converters) (PC.A.2.5.5)

A submission is required for OTSDUW Plant and Apparatus (including OTSDUW DC Converters at each Transmission Interface Point and  Connection Point.  The submission shall represent operating conditions that result in the maximum fault infeed. The fault current from all auxiliaries of the OTSDUW Plant and Apparatus at the Transmission Interface Point and Connection Point shall be included. The fault infeed shall be expressed as a fault current at the Transmission Interface Point and also at each Connection Point.

Should actual data in respect of fault infeeds be unavailable at the time of the application for a CUSC Contract or Embedded Development Agreement, a limited subset of the data, representing the maximum fault infeed that may result from the OTSDUW Plant and Apparatus, shall be submitted. This data will, as a minimum,  represent the root mean square of the positive, negative and zero sequence components of the fault current for both single phase and three phase solid faults at each Connection Point and Interface Point at the time of fault application and 50ms following fault application.  Actual data in respect of fault infeeds shall be submitted to The Company as soon as it is available, in line with PC.A.1.2.

| DATA DESCRIPTION | UNITS | F.Yr. 0 | F.Yr. 1 | F.Yr. 2 | F.Yr. 3 | F.Yr. 4 | F.Yr. 5 | F.Yr. 6 | F.Yr. 7 | DATA to RTL |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| (PC.A.2.5) |  |  |  |  |  |  |  |  |  | CUSC Contract | CUSC App. Form |
| Name of OTSDUW Plant and Apparatus |  |  |  |  |  |  |  |  |  |  |  |
| OTSDUW DC Converter type (i.e. voltage or current source) |  |  |  |  |  |  |  |  |  |  |  |
| A submission shall be provided for the contribution of each OTSDUW Plant and Apparatus to the positive, negative and zero sequence components of the short circuit current at the Interface Point and each Connection Point for (i) a solid symmetrical three phase short circuit (ii) a solid single phase to earth short circuit (iii) a solid phase to phase short circuit (iv) a solid two phase to earth short circuit If protective controls are used and active for the above conditions, a submission shall be provided in the limiting case where the protective control is not active. This case may require application of a non-solid fault, resulting in a retained voltage at the fault point. |  |  |  |  |  |  |  |  |  | □ □ □ □ □ | ■ ■ ■ ■ ■ |

SCHEDULE 18 - OFFSHORE TRANSMISSION SYSTEM DATA

PAGE 14 OF 24

| DATA DESCRIPTION | UNITS | F. Yr. 0 | F. Yr. 1 | F. Yr. 2 | F. Yr. 3 | F. Yr. 4 | F. Yr. 5 | F. Yr. 6 | F. Yr. 7 | DATA to RTL |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  |  |  |  |  | CUSC Contract | CUSC App. Form |
| - A continuous time trace and table showing the root mean square of the positive, negative and zero sequence components of the fault current from the time of fault inception to 140ms after fault inception at 10ms intervals | Graphical and tabular kA versus s |  |  |  |  |  |  |  |  | □ | ■ |
| - A continuous time trace and table showing the positive, negative and zero sequence components of retained voltage at the Interface Point and each Connection Point, if appropriate | p.u. versus s |  |  |  |  |  |  |  |  | □ | ■ |
| - A continuous time trace and table showing the root mean square of the positive, negative and zero sequence components of retained voltage at the fault point, if appropriate | p.u. versus s |  |  |  |  |  |  |  |  | □ | ■ |
| Positive sequence X/R ratio of the equivalent at time of fault at the Interface Point and each Connection Point |  |  |  |  |  |  |  |  |  | □ | ■ |
| Minimum zero sequence impedance of the equivalent at the Interface Point and each Connection Point |  |  |  |  |  |  |  |  |  | □ | ■ |
| Active Power transfer at the Interface Point and each Connection Point pre-fault | MW |  |  |  |  |  |  |  |  | □ | ■ |
| Power Factor (lead or lag) |  |  |  |  |  |  |  |  |  | □ | ■ |
| Pre-fault voltage (if different from 1.0 p.u.) at fault point (See note 1) | p.u. |  |  |  |  |  |  |  |  | □ | ■ |
| Items of reactive compensation switched in pre-fault |  |  |  |  |  |  |  |  |  | □ | ■ |

Note 1.	The pre-fault voltage provided above should represent the voltage within the range 0.95 to 1.05 that gives the highest fault current

SCHEDULE 18 - OFFSHORE TRANSMISSION SYSTEM DATA

PAGE 15 OF 24

Thermal Ratings Data (PC.A.2.2.4)

|  |  |  | CIRCUIT RATING SCHEDULE |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Voltage | Offshore TO Name |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Issue Date |  |  |  |
| 132kV |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| CIRCUIT Name from Site A – Site B |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Winter |  |  |  |  |  |  |  | Spring/Autumn |  |  |  |  |  | Summer |  |  |  |  |  |  |  |
| OVERALL CCT RATINGS |  | %Nom | Limit |  | Amps |  |  | MVA |  | %Nom |  | Limit |  | Amps | MVA | %Nom |  |  | Limit | Amps |  |  | MVA |
| Pre-Fault Continuous |  | 84% | Line |  | 485 |  |  | 111 |  | 84% |  | Line |  | 450 | 103 | 84% |  |  | Line | 390 |  |  | 89 |
| Post-Fault Continuous |  | 100% | Line |  | 580 |  |  | 132 |  | 100% |  | Line |  | 540 | 123 | 100% |  |  | Line | 465 |  |  | 106 |
| Prefault load exceeds line prefault continuous rating | 6hr | 95% | Line |  | 580 |  |  | 132 |  | 95% |  | Line |  | 540 | 123 | 95% |  |  | Line | 465 |  |  | 106 |
|  | 20m |  | Line |  | 580 |  |  | 132 |  |  |  | Line |  | 540 | 123 |  |  |  | Line | 465 |  |  | 106 |
|  | 10m | mva | Line |  | 580 |  |  | 132 |  | mva |  | Line |  | 540 | 123 | mva |  |  | Line | 465 |  |  | 106 |
|  | 5m | 125 | Line |  | 580 |  |  | 132 |  | 116 |  | Line |  | 540 | 123 | 100 |  |  | Line | 465 |  |  | 106 |
|  | 3m |  | Line |  | 580 |  |  | 132 |  |  |  | Line |  | 540 | 123 |  |  |  | Line | 465 |  |  | 106 |
|  | 6hr | 90% | Line |  | 580 |  |  | 132 |  | 90% |  | Line |  | 540 | 123 | 90% |  |  | Line | 465 |  |  | 106 |
|  | 20m |  | Line |  | 580 |  |  | 132 |  |  |  | Line |  | 540 | 123 |  |  |  | Line | 465 |  |  | 106 |
| Short Term | 10m | mva | Line |  | 580 |  |  | 132 |  | mva |  | Line |  | 540 | 123 | mva |  |  | Line | 465 |  |  | 106 |
| Overloads | 5m | 118 | Line |  | 580 |  |  | 132 |  | 110 |  | Line |  | 540 | 123 | 95 |  |  | Line | 465 |  |  | 106 |
|  | 3m |  | Line |  | 580 |  |  | 132 |  |  |  | Line |  | 540 | 123 |  |  |  | Line | 465 |  |  | 106 |
| Limiting Item and permitted overload values for different times and pre-fault loads | 6hr | 84% | Line |  | 580 |  |  | 132 |  | 84% |  | Line |  | 540 | 123 | 84% |  |  | Line | 465 |  |  | 106 |
|  | 20m |  | Line |  | 590 |  |  | 135 |  |  |  | Line |  | 545 | 125 |  |  |  | Line | 470 |  |  | 108 |
|  | 10m | mva | Line |  | 630 |  |  | 144 |  | mva |  | Line |  | 580 | 133 | mva |  |  | Line | 495 |  |  | 113 |
|  | 5m | 110 | Line |  | 710 |  |  | 163 |  | 103 |  | Line |  | 655 | 149 | 89 |  |  | Line | 555 |  |  | 126 |
|  | 3m |  | Line |  | 810 |  |  | 185 |  |  |  | Line |  | 740 | 170 |  |  |  | Line | 625 |  |  | 143 |
|  | 6hr | 75% | Line |  | 580 |  |  | 132 |  | 75% |  | Line |  | 540 | 123 | 75% |  |  | Line | 465 |  |  | 106 |
|  | 20m |  | Line |  | 595 |  |  | 136 |  |  |  | Line |  | 555 | 126 |  |  |  | Line | 475 |  |  | 109 |
|  | 10m | mva | Line |  | 650 |  |  | 149 |  | mva |  | Line |  | 600 | 137 | mva |  |  | Line | 510 |  |  | 116 |
|  | 5m | 99 | Line |  | 760 |  |  | 173 |  | 92 |  | Line |  | 695 | 159 | 79 |  |  | Line | 585 |  |  | 134 |
|  | 3m |  | Line |  | 885 |  |  | 203 |  |  |  | Line |  | 810 | 185 |  |  |  | Line | 685 |  |  | 156 |
|  | 6hr | 60% | Line |  | 580 |  |  | 132 |  | 60% |  | Line |  | 540 | 123 | 60% |  |  | Line | 465 |  |  | 106 |
|  | 20m |  | Line |  | 605 |  |  | 138 |  |  |  | Line |  | 560 | 128 |  |  |  | Line | 480 |  |  | 110 |
|  | 10m | mva | Line |  | 675 |  |  | 155 |  | mva |  | Line |  | 620 | 142 | mva |  |  | Line | 530 |  |  | 121 |
|  | 5m | 79 | Line |  | 820 |  |  | 187 |  | 73 |  | Line |  | 750 | 172 | 63 |  |  | Line | 635 |  |  | 145 |
|  | 3m |  | Line |  | 985 |  |  | 226 |  |  |  | Line |  | 900 | 206 |  |  |  | Line | 755 |  |  | 173 |
|  | 6hr | 30% | Line |  | 580 |  |  | 132 |  | 30% |  | Line |  | 540 | 123 | 30% |  |  | Line | 465 |  |  | 106 |
|  | 20m |  | Line |  | 615 |  |  | 141 |  |  |  | Line |  | 570 | 130 |  |  |  | Line | 490 |  |  | 112 |
|  | 10m | mva | Line |  | 710 |  |  | 163 |  | mva |  | Line |  | 655 | 150 | mva |  |  | Line | 555 |  |  | 127 |
|  | 5m | 39 | Line |  | 895 |  |  | 205 |  | 36 |  | Line |  | 820 | 187 | 31 |  |  | Line | 690 |  |  | 158 |
|  | 3m |  | Line |  | 1110 |  |  | 255 |  |  |  | Line |  | 1010 | 230 |  |  |  | Line | 845 |  |  | 193 |

SCHEDULE 18 - OFFSHORE TRANSMISSION SYSTEM DATA

PAGE 16 OF 24

|  | 6hr |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | 20m |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 10m |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 5m |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 3m |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 6hr |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 20m |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 10m |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 5m |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 3m |  |  |  |  |  |  |  |  |  |  |  |  |
| Notes or Restrictions Detailed |  |  |  |  |  |  |  |  |  |  |  |  |  |

Notes: 	1.  For information the equivalent STC Reference: STCP12-1: Part 3 - 2.6 Thermal Ratings

2. The values shown in the above table is example data.

SCHEDULE 18 - OFFSHORE TRANSMISSION SYSTEM DATA

PAGE 17 OF 24

Protection Policy (PC.A.6.3)

To include details of the protection policy

Protection Schedules(PC.A.6.3)

Data schedules for the protection systems associated with each primary plant item including:

Protection, Intertrip Signalling & operating times

Intertripping and protection unstabilisation initiation

Synchronising facilities

# Delayed Auto Reclose sequence schedules

Automatic Switching Scheme Schedules (PC.A.2.2.7)

# A diagram of  the scheme and an explanation of how the system will operate and what plant will be affected by the scheme’s operation.

SCHEDULE 18 - OFFSHORE TRANSMISSION SYSTEM DATA

PAGE 18 OF 24

# GENERATOR INTERTRIP SCHEMES (PC.A.2.2.7(b))

# Substation: _______________________________

Details of Generator Intertrip Schemes:

A diagram of the scheme and an explanation of how the system will operate and what plant will be effected by the schemes operation.

# DEMAND INTERTRIP SCHEMES (PC.A.2.2.7(b))

# Substation:________________________________

Details of Demand Intertrip Schemes:

# A diagram of the scheme and an explanation of how the system will operate and what plant will be effected by the schemes operation

SCHEDULE 18 - OFFSHORE TRANSMISSION SYSTEM DATA

PAGE 19 OF 24

Specific Operating Requirements (CC.5.2.1 or ECC.5.2.1)

# SUBSTATION OPERATIONAL GUIDE

# Substation: __________________________

Location Details:

| Postal Address: | Telephone Nos. | Map Ref. |
| --- | --- | --- |
| Transmission Interface |  |  |
| Generator Interface |  |  |

- Substation Type:

- Voltage Control: (short description of voltage control system. To include mention of modes i.e. Voltage, manual etc. Plus control step increments i.e. 0.5% or 0.33kV)

- Energisation Switching Information: (The standard energisation switching process from dead.)

- Intertrip Systems:

- Reactive Plant Outage: (A short explanation of any system re-configurations required to facilitate the outage of any reactive plant which form part of the OTSDUW Plant and Apparatus equipment.  Also any generation restrictions required).

- Harmonic Filter Outage: (An explanation as to any OTSDUW Plant and Apparatus reconfigurations required to facilitate the outage and maintain the system within specified Harmonic limits, also any generation restrictions required).

SCHEDULE 18 - OFFSHORE TRANSMISSION SYSTEM DATA

PAGE 20 OF 24

OTSDUW DC CONVERTER TECHNICAL DATA

OTSDUW DC CONVERTER NAME					DATE:___________

| Data Description | Units | DATA to RTL |  | Data Category | DC Converter Station Data |
| --- | --- | --- | --- | --- | --- |
| (PC.A.4 and PC.A.5.2.5) |  | CUSC Contract | CUSC App. Form |  |  |
| OTSDUW DC CONVERTER (CONVERTER DEMANDS): Demand supplied through Station Transformers associated with the OTSDUW DC Converter at each Interface Point and each Offshore Connection Point Grid Entry Point [PC.A.4.1] - Demand with all OTSDUW DC Converters operating at Interface Point Capacity . - Demand with all OTSDUW DC Converters operating at maximum Interface Point flow from the Interface Point to each Offshore Grid Entry Point . - The maximum Demand that could occur. - Demand at specified time of annual peak half hour of The Company Demand at Annual ACS Conditions. - Demand at specified time of annual minimum half-hour of The Company Demand. OTSDUW DC CONVERTER DATA Number of poles, i.e. number of OTSDUW DC Converters Pole arrangement (e.g. monopole or bipole) Return path arrangement Details of each viable operating configuration Configuration 1 Configuration 2 Configuration 3 Configuration 4 Configuration 5 Configuration 6 | MW MVAr MW MVAr MW MVAr MW MVAr MW MVAr Text Text Diagram Diagram Diagram Diagram Diagram Diagram Diagram | □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ | ■ ■ ■ ■ ■ ■ ■ ■ | DPD II DPD II DPD II DPD II DPD II DPD II DPD II DPD II DPD II SPD+ SPD+ SPD+ |  |

SCHEDULE 18 - OFFSHORE TRANSMISSION SYSTEM DATA

PAGE 21 OF 24

| Data Description | Units | DATA to RTL |  | Data Category | Operating Configuration |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | CUSC Contract | CUSC App. Form |  | 1 | 2 | 3 | 4 | 5 | 6 |
| OTSDUW DC CONVERTER DATA (PC.A.3.3.1(d)) OTSDUW DC Converter Type (e.g. current or Voltage source) If the busbars at the Interface Point or Connection Point are normally run in separate sections identify the section to which the OTSDUW DC Converter configuration is connected Rated MW import per pole (PC.A.3.3.1) Rated MW export per pole (PC.A.3.3.1) | Text Section Number MW MW | □ □ □ □ | ■ ■ ■ ■ | SPD SPD SPD+ SPD+ |  |  |  |  |  |  |
| ACTIVE POWER TRANSFER CAPABILITY (PC.A.3.2.2) Interface Point Capacity | MW MVAr | □ □ | ■ ■ | SPD SPD |  |  |  |  |  |  |
| OTSDUW DC CONVERTER TRANSFORMER (PC.A.5.4.3.1) Rated MVA Winding arrangement Nominal primary voltage Nominal secondary (converter-side) voltage(s) Positive sequence reactance Maximum tap Nominal tap Minimum tap Positive sequence resistance Maximum tap Nominal tap Minimum tap Zero phase sequence reactance Tap change range Number of steps | MVA kV kV % on MVA % on MVA % on MVA % on MVA % on MVA % on MVA % on MVA +% / -% | □ □ □ □ □ □ □ □ □ □ □ □ |  | DPD II DPD II DPD II DPD II DPD II DPD II DPD II DPD II DPD II DPD II DPD II DPD II |  |  |  |  |  |  |

SCHEDULE 18 - OFFSHORE TRANSMISSION SYSTEM DATA

PAGE 22 OF 24

| Data Description | Units | DATA to RTL |  | Data Category | Operating configuration |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | CUSC Contract | CUSC App. Form |  | 1 | 2 | 3 | 4 | 5 | 6 |
| OTSDUW DC CONVERTER NETWORK DATA (PC.A.5.4.3.1 (c)) Rated DC voltage per pole Rated DC current per pole Details of the OTSDUW DC Network described in diagram form including resistance, inductance and capacitance of all DC cables and/or DC lines. Details of any line reactors (including line reactor resistance), line capacitors, DC filters, earthing electrodes and other conductors that form part of the OTSDUW DC Network should be shown. | kV A Diagram | □ □ □ |  | DPD II DPD II DPD II |  |  |  |  |  |  |

SCHEDULE 18 - OFFSHORE TRANSMISSION SYSTEM DATA

PAGE 23 OF 24

| Data Description | Units | DATA to RTL |  | Data Category | Operating configuration |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | CUSC Contract | CUSC App. Form |  | 1 | 2 | 3 | 4 | 5 | 6 |
| OTSDUW DC CONVERTER CONTROL SYSTEMS (PC.A.5.4.3.2) Static VDC – PDC (DC voltage – DC power) or Static VDC – IDC (DC voltage – DC current) characteristic (as appropriate) when operating as –Rectifier –Inverter Details of rectifier mode control system, in block diagram form together with parameters showing transfer functions of individual elements. Details of inverter mode control system, in block diagram form showing transfer functions of individual elements including parameters (as applicable). Details of OTSDUW DC Converter transformer tap changer control system in block diagram form showing transfer functions of individual elements including parameters. Details of AC filter control systems in block diagram form showing transfer functions of individual elements including parameters Details of any frequency and/or load control systems in block diagram form showing transfer functions of individual elements including parameters. Details of any large or small signal modulating controls, such as power oscillation damping controls or sub-synchronous oscillation damping controls, that have not been submitted as part of the above control system data. Transfer block diagram representation of the reactive power control at converter ends for a voltage source converter. For Generators in respect of OTSDUW who are also EU Code Users details of OTSDUW DC Converter unit models and/or control systems in block diagram form showing transfer functions of individual elements including parameters. For Generators in respect of OTSDUW who are also EU Code Users details of AC component models and/or control systems in block diagram form showing transfer functions of individual elements including parameters. For Generators in respect of OTSDUW who are also EU Code Users details of DC Grid models and/or control systems in block diagram form showing transfer functions of individual elements including parameters. For Generators in respect of OTSDUW who are also EU Code Users details of Voltage and power controller and/or control systems in block diagram form showing transfer functions of individual elements including parameters. For Generators in respect of OTSDUW who are also EU Code Users details of Special control features if applicable (e.g. power oscillation damping (POD) function, subsynchronous torsional interaction (SSTI) control and/or control systems in block diagram form showing transfer functions of individual elements including parameters. For Generators in respect of OTSDUW who are also EU Code Users details of Multi terminal control, if applicable and/or control systems in block diagram form showing transfer functions of individual elements including parameters. For Generators in respect of OTSDUW who are also EU Code Users details of OTSDUW DC Converter protection models as agreed between The Company and the Generator (in respect of OTSDW) and/or control systems in block diagram form showing transfer functions of individual elements including parameters. | Diagram Diagram Diagram Diagram Diagram Diagram Diagram Diagram Diagram Diagram Diagram Diagram Diagram Diagram Diagram Diagram Diagram | □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ |  | DPD II DPD II DPD II DPD II DPD II DPD II DPD II DPD II DPD II DPD II DPD II DPD II DPD II DPD II DPD II DPD II DPD II |  |  |  |  |  |  |

SCHEDULE 18 - OFFSHORE TRANSMISSION SYSTEM DATA

PAGE 24 OF 24

| Data Description | Units | DATA to RTL |  | Data Category | Operating configuration |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | CUSC Contract | CUSC App. Form |  | 1 | 2 | 3 | 4 | 5 | 6 |
| LOADING PARAMETERS (PC.A.5.4.3.3) MW Export from the Offshore Grid Entry Point to the Transmission Interface Point Nominal loading rate Maximum (emergency) loading rate Maximum recovery time, to 90% of pre-fault loading, following an AC system fault or severe voltage depression. Maximum recovery time, to 90% of pre-fault loading, following a transient DC Network fault. | MW/s MW/s s s | □ □ □ □ |  | DPD I DPD I DPD II DPD II |  |  |  |  |  |  |

SCHEDULE 19 – USER DATA FILE STRUCTURE

PAGE 1 OF 2

The structure of the User Data File Structure is given below.

| i.d. | Folder name | Description of contents |
| --- | --- | --- |
| Part A: Commercial & Legal |  |  |
| A2 | Commissioning | Commissioning & Test Programmes |
| A3 | Statements | Statements of Readiness |
| A9 | AS Monitoring | Ancillary Services Monitoring |
| A10 | Self-Certification | User Self Certification of Compliance |
| A11 | Compliance statements | Compliance Statement |
| Part 1: Safety & System Operation |  |  |
| 1.1 | Interface Agreements | Interface Agreements |
| 1.2 | Safety Rules | Safety Rules |
| 1.3 | Switching Procedures | Local Switching Procedures |
| 1.4 | Earthing | Earthing |
| 1.5 | SRS | Site Responsibility Schedules |
| 1.6 | Diagrams | Operational and Gas Zone Diagrams |
| 1.7 | Drawings | Site Common Drawings |
| 1.8 | Telephony | Control Telephony |
| 1.9 | Safety Procedures | Local Safety Procedures |
| 1.10 | Co-ordinators | Safety Co-ordinators |
| 1.11 | RISSP | Record of Inter System Safety Precautions |
| 1.12 | Tel Numbers | Telephone Numbers for Joint System Incidents |
| 1.13 | Contact Details | Contact Details (fax, tel, email) |
| 1.14 | Restoration Plan | Local Joint Restoration Plan (incl. System Restoration if applicable) |
| 1.15 | Maintenance | Maintenance Standards |
| Part 2: Connection Technical Data |  |  |
| 2.1 | DRC Schedule 5 | DRC Schedule 5 – Users System Data |
| 2.2 | Protection Report | Protection Settings Reports |
| 2.3 | Special Automatic Facilities | Special Automatic Facilities e.g. intertrip |
| 2.4 | Operational Metering | Operational Metering |
| 2.5 | Tariff Metering | Tariff Metering |
| 2.6 | Operational Comms | Operational Communications |
| 2.7 | Monitoring | Performance Monitoring |
| 2.8 | Power Quality | Power Quality Test Results (if required) |

SCHEDULE 19 – USER DATA FILE STRUCTURE

PAGE 2 OF 2

| Part 3: Generator Technical Data |  |  |
| --- | --- | --- |
| 3.1 | DRC Schedule 1 | DRC Schedule 1 - Generating Unit, Power Generating Module, HVDC System and DC Converter Technical Data |
| 3.2 | DRC Schedule 2 | DRC Schedule 2 - Generation Planning Data |
| 3.3 | DRC Schedule 4 | DRC Schedule 4 – Frequency Droop & Response |
| 3.4 | DRC Schedule 14 | DRC Schedule 14 – Fault Infeed Data – Generators |
| 3.5 | Special Generator Protection | Special Generator Protection e.g. Pole slipping; islanding |
| 3.6 | Compliance Tests | Compliance Tests & Evidence |
| 3.7 | Compliance Studies | Compliance Simulation Studies |
| 3.8 | Site Specific | Bilateral Connections Agreement Technical Data & Compliance |
| 3.9 | DRC Schedule 20 | DRC Schedule 20 - Grid Forming Plant Data |
| Part 4: General DRC Schedules |  |  |
| 4.1 | DRC Schedule 3 | DRC Schedule 3 – Large Power Station Outage Information |
| 4.2 | DRC Schedule 6 | DRC Schedule 6 – Users Outage Information |
| 4.3 | DRC Schedule 7 | DRC Schedule 7 – Load Characteristics |
| 4.4 | DRC Schedule 8 | DRC Schedule 8 – BM Unit Data (if applicable) |
| 4.5 | DRC Schedule 10 | DRC Schedule 10 –Demand Profiles |
| 4.6 | DRC Schedule 11 | DRC Schedule 11 – Connection Point Data |
| Part 5: OTSDUW Data and Information (if applicable and prior to OTSUA Transfer Time) |  |  |
|  |  | Diagrams |
|  |  | Circuits Plant and Apparatus |
|  |  | Circuit Parameters |
|  |  | Protection Operation and Autoswitching |
|  |  | Automatic Control Systems |
|  |  | Mathematical model of dynamic compensation plant |

SCHEDULE 20 – GRID FORMING PLANT CAPABILITY DATA

The following data need only be supplied by Users (be they a GB Code User or EU Code User) or Non-CUSC Parties who wish to offer a Grid Forming Capability as provided for ECC.6.3.19.3.  Where such a Grid Forming Capability is provided then the following data items and models are to be supplied in respect of each Grid Forming Plant.

| DATA DESCRIPTION |  | GRID FORMING PLANT DATA |  |  |
| --- | --- | --- | --- | --- |
|  |  | 1 | 2 | 3 |
| Submission of Network Frequency Perturbation Plot and Nichols Chart for each GBGF-I (PC.A.5.8.1) | Graphs |  |  |  |
| High level equivalent architecture diagram of Grid Forming Plant (PC.A.5.8.1) | Diagram |  |  |  |
| GBGF-I Grid Forming Plant Block Diagram (Laplace Operator) in the general form shown in Figure PC.A.5.8.1 or as agreed with The Company. When submitting either Figure PC.A.5.8.1 (a) or Figure PC.A.5.8.1 (b), each User or Non-CUSC Party can use their own design, that may be very different to Figures PC.A.5.8.1 (a) or PC.A.5.8.1 (b), but should contain all relevant functions that can include simulation models and other equivalent data and documentation | Block Diagram (Laplace Operator) Documentation |  |  |  |
| Each User or Non-CUSC Party shall provide a model of their Grid Forming Plant which provides a true and accurate reflection of its Grid Forming Capability. | Model and documentation – format to be agreed with The Company |  |  |  |

In order to participate in the Grid Forming Capability market, User’s and Non-CUSC Parties are required to provide data of their GBGF-I in accordance with Figures PC.A.5.8.1(a) and PC.A.5.8.1(b) Users and Non-CUSC Parties in respect of Grid Forming Plants should indicate if the data is submitted on a unit or aggregated basis.   Table 1 below defines the notation used in Figure PC.5.8.1

| Parameter | Symbol | Units |
| --- | --- | --- |
| The primary reactance of the Grid Forming Unit, in pu. | Xin or Xts | pu on MVA Rating of Grid Forming Unit |
| The additional reactance, in pu, between the terminals of the Grid Forming Unit and the Grid Entry Point or User System Entry Point (if Embedded). | Xtr | pu on MVA Rating of Grid Forming Unit |
| The rated angle between the Internal Voltage Source and the input terminals of the Grid Forming Unit. |  | radians |
| The rated angle between the Internal Voltage Source and Grid Entry Point or User System Entry Point (if Embedded). |  | radians |
| The rated voltage and phase of the Internal Voltage Source of the Grid Forming Unit. |  | Voltage - pu Phase - radians |
| The rated electrical angle between current and voltage at the input to the Grid transformer. |  | radians |

Table 1

In order to participate in a Grid Forming Capability market, User’s and Non-CUSC Parties are also required to provide the data of their GBGF-I in accordance with the Table below to The Company. The details and arrangements for Users and Non-CUSC Parties participating in this market shall be published on The Company’s Website.

| Quantity | Units | Range (where Applicable) | User Defined Parameter |
| --- | --- | --- | --- |
| Type of Grid form Plant (eg Generating Unit, Electricity Storage Module, Dynamic Reactive Compensation Equipment | N/A |  |  |
| Maximum Continuous Rating at Registered Capacity or Maximum Capacity | MVA |  |  |
| Primary reactance Xin or Xts(see Table 1) | pu on MVA |  |  |
| Additional reactance Xtr (See Table 1) | pu on MVA |  |  |
| Maximum Capacity | MW |  |  |
| Active ROCOF Response Power (MW) supplied or absorbed at 1Hz/s System Frequency change (which is the maximum frequency change for linear operation of the Grid Forming Plant) | MW |  |  |
| Phase Jump Angle Withstand | degrees |  | 60 degrees specified |
| Phase Jump Angle limit | degrees |  | 5 degrees recommended |
| Phase Jump Power (MW) at the rated angle | MW |  |  |
| Defined Active Damping Power for a Grid Oscillation Value of 0.05 Hz peak to peak at 1 Hz | MW |  |  |
| The cumulative energy delivered for a 1Hz/s System Frequency fall from 52 Hz to 47 Hz This is the total Active Power transient output of the Grid Forming Plant | MWs or MJ |  |  |
| Inertia Constant (H) using equation 1 or declared in accordance with the simulation results of ECP.A.3.9.4 | MWs/MVA |  |  |
| Inertia Constant (He) using equation 2 or declared in accordance with the simulation results of ECP.A.3.9.4 | MWs/MVA |  |  |
| Continuous Overload Capability | % on MVA |  |  |
| Short Term duration Overload capability |  |  |  |
| Duration of Short Term Overload Capability | s |  |  |
| Peak Current Rating | pu |  |  |
| Nominal Grid Entry Point or User System Entry Point voltage | kV |  |  |
| Grid Entry Point or User System Entry Point | - Location |  |  |
| Continuous or defined time duration MVA Rating | MVA |  |  |
| Continuous or defined time duration MW Rating | MW |  |  |
| For a GBGF-I the inverters maximum Internal Voltage Source (IVS) for the worst case condition – for example operation at maximum exporting Reactive Power at the maximum AC System voltage | pu |  |  |
| Maximum Three Phase Short Circuit Infeed at Grid Entry Point or User System Entry Point | kA |  |  |
| Maximum Single Phase Short Circuit Infeed at Grid Entry Point or User System Entry Point | kA |  |  |
| Will the Grid Forming Plant contribute to any other form of commercial service – for example Dynamic Containment, Firm Frequency Response, | Details to be provided |  |  |
| Equivalent Damping Factor. | ζ |  | 0.2 to 5.0 allowed |

Table 2

H = Installed MWs / Rated installed MVA

(equation 1)

He = (Active ROCOF Response Power at 1 Hz / s x System Frequency) / ( Installed MVA x 2 )

(equation 2)

<END OF DATA REGISTRATION CODE>