Electricity System Restoration (ESR) Competitive Procurement Event - Invitation to the SW & Midlands Tender – ITT Stage 1 Feasibility Study

**F1 Report**

|  |  |
| --- | --- |
| Provider Name | [ Complete ] |
| Site/Asset/Project Name | [ Complete ] |
| Tender Category | [Complete ] |
| Submission Date | [ Complete ] |

Contents

[1.1 ESR Operation 3](#_Toc124515333)

[1.2 Anchor Generator (Primary/Full) Restoration Service Provider 5](#_Toc124515334)

[1.3 Distributed ReStart Projects 9](#_Toc124515335)

[1.4 Top-up Services 16](#_Toc124515336)

[List of Attachments 19](#_Toc124515337)

[Appendices 19](#_Toc124515338)

[Appendix 1 – Anchor Generator (PrimaryFull) Service 20](#_Toc124515339)

[Appendix 2 – Anchor Generator Distributed ReStart 21](#_Toc124515340)

[Appendix 3 – Top Up Service Distributed ReStart 22](#_Toc124515341)

[Appendix 4 – Top Up Service 23](#_Toc124515342)

Instructions

Please populate the front page with your company details and the tender category you are tendering in for. This document contains technical questions for each category, please only complete the category relevant to you. The table below explains what section you are required to complete. Please read this document in conjunction with Appendix 1 – SW & Midlands Tender Technical Requirements & Assessment Criteria

|  |  |
| --- | --- |
| Category | Complete sections |
| Anchor Generator (Primary/Full) Restoration Service Provider | Complete all questions within section 1.1 and 1.2  Complete table on Appendix 1  Please list all attachments in the format provided on page 20 |
| Anchor Generator (Distributed ReStart) | Complete all Questions within section 1.1 and 1.3.1  Complete table on Appendix 2  Please list all attachments in the format provided on page 20 |
| Top-up Services (Distributed ReStart) | Complete all Questions within section 1.1 and 1.3.2  Complete table on Appendix 3  Please list all attachments in the format provided on page 20 |
| Top- up Services | Complete all Questions within section 1.1 and 1.4.1  Complete at least one requirement in section 1.4.2  Complete table on Appendix 4  Please list all attachments in the format provided on page 20 |

Each of the tables below contains the technical requirements for each section and the format for the response. Please note there is a word count (excluding attachments) Please ensure all attachments are labelled clearly to reduce the number of clarifications. Please use the empty ‘Provider Response’ cells for your answer.

If you have any questions relating to the content of this document, please submit them using the Appendix 2 SW & Midlands Tender Query Form.

1.1 ESR Operation

General Description of the Service

|  |  |
| --- | --- |
| Requirement | - The proposed project, including description of assets and their current / expected capability to provide a ESR Service;  - Share the relevant Single Line Diagram of the Plant;  - Number of power generating modules expected to be included in the ESR Service (if applicable);  - High-level start-up sequence from black start up to the Minimum Stable Operating Level and, from that point, up to the contracted output. |
| Response Format | Text (no more than 500 words). For the start-up sequence, share a Table & Graphic highlighting key stages (milestones, hold points, etc.) and expected times. |
| Attachments | *Please include the titles of any attachments associated to this section.* |
| **Response** |  |

Organisation / Site Arrangements

|  |  |
| --- | --- |
| Requirement | Please share how are you as an expecting to deliver the ESR Service (logistics).  Examples:   * How will you guarantee a 24h availability of the ESR Service? * Number of Control Room shift teams? * Staff response arrangements (if required); * ESR expected to be included in the annual Staff’s mandatory training.   Site locations and logistics (telephone calls on site, distance to site) |
| Response Format | Text (no more than 500 words). |
| Attachments | *Please include the titles of any attachments associated to this section.* |
| **Response** |  |

ESR Auxiliary Unit(s)

|  |  |
| --- | --- |
| Requirement | Please share:  - Information around any existing assets (if applicable);  - Potential new needs:   1. Expected House Load / size for the ESR Auxiliary Unit(s) 2. Assessment/comparison of advantages/disadvantages for potential options (different technologies, costs, risks for reliability, environment, site constraints); 3. Preferred option including evidence of initial discussions on relevant environmental permits and planning permissions required.;   - Demonstrate that the final preferred solution involving existing and/or new assets is compliant with the minimum resilience requirement (≥72h). |
| Response Format | Text (no more than 500 words). |
| Attachments | *Please include the titles of any attachments associated to this section.* |
| **Response** |  |

Communication Systems

|  |  |
| --- | --- |
| Requirement | Please share details of any existing telecommunications and systems (telephony, SCADA, text messages, Satellite Phones, etc.) ; particularly related resilience under Black Start conditions. |
| Response Format | Text (no more than 500 words). |
| Attachments | *Please include the titles of any attachments associated to this section.* |
| **Response** |  |

Project Timescales

|  |  |
| --- | --- |
| Requirement | A programme for all provider activities required to achieve the ESR capability.  Please attach a project programme including all provider activities that are necessary between contract award and service commencement date, including for example:   * Construction works (where applicable) * Long lead time procurement (where applicable) * Communication system upgrades (where applicable) * Control System upgrades (where applicable)   A statement confirming ability to deliver the ESR Service earlier than / by August 2027. |
| Response Format | Text (no more than 500 words) + Gantt Chart (or equivalent). |
| Attachments | *Please include the titles of any attachments associated to this section.* |
| **Response** |  |

1.2 Anchor Generator (Primary/Full) Restoration Service Provider

Time to Connect

|  |  |
| --- | --- |
| Requirement | *≤ 2hours. Time taken to start-up the Restoration Station from shutdown without the use of external power supplies, and to energise part of the NETS, within two hours of receiving an instruction from the Electricity System Operator (ESO) or its delegate.* |
| Response Format | Text (no more than 100 words). If applicable, consider effect of warmth – Hot, Warm, Cold. Detail key stages of the Restoration and timings. |
| Attachments | *Please include the titles of any attachments associated to this section.* |
| **Response** |  |

Or Phase 2 Time to Connect

|  |  |
| --- | --- |
| Requirement | *2 - 24hours. Time taken to start-up the Restoration Station from shutdown without the use of external power supplies, and to energise part of the NETS, within two hours of receiving an instruction from the Electricity System Operator (ESO) or its delegate.* |
| Response Format | Text (no more than 100 words). If applicable, consider effect of warmth – Hot, Warm, Cold. Detail key stages of the Restoration and timings. |
| Attachments | *Please include the titles of any attachments associated to this section.* |
| **Response** |  |

Or Phase 3 Time to Connect

|  |  |
| --- | --- |
| Requirement | *24 - 72hours. Time taken to start-up the Restoration Station from shutdown without the use of external power supplies, and to energise part of the NETS, within two hours of receiving an instruction from the Electricity System Operator (ESO) or its delegate.* |
| Response Format | Text (no more than 100 words). If applicable, consider effect of warmth – Hot, Warm, Cold. Detail key stages of the Restoration and timings. |
| Attachments | *Please include the titles of any attachments associated to this section.* |
| **Response** |  |

Service Availability

|  |  |
| --- | --- |
| Requirement | ≥ 80%. *The ability to deliver the contracted ESR Service over 80% of a year. Note: It is the responsibility of the Provider to demonstrate its service availability. By submitting a tender, the provider commits to ensuring availability at least 80% of each year of the service.* |
| Response Format | Text (no more than 300 words). |
| Attachments | *Please include the titles of any attachments associated to this section.* |
| **Response** |  |

Voltage Regulation

|  |  |
| --- | --- |
| Requirement | Existent. *Ability to create a voltage source and remain connected within acceptable limits during energisation/block loading (±10%).* |
| Response Format | Text (no more than 300 words). |
| Attachments | *Please include the titles of any attachments associated to this section.* |
| **Response** |  |

Frequency Regulation

|  |  |
| --- | --- |
| Requirement | Existent. *Ability to manage frequency level when block loading (47.5Hz – 52Hz), at 10MW block load and the maximum block load capability.* |
| Response Format | Text (no more than 300 words). |
| Attachments | *Please include the titles of any attachments associated to this section.* |
| **Response** |  |

Resilience of Supply – ESR Service

|  |  |
| --- | --- |
| Requirement | ≥ 10h. *When instructed, the minimum time the RSP will deliver the contracted service.* |
| Response Format | Text (no more than 300 words). Explain how the Provider will ensure the ESR Auxiliary Unit will have the expected resilience. |
| Attachments | *Please include the titles of any attachments associated to this section.* |
| **Response** |  |

Resilience of Supply – ESR Auxiliary Unit(s)

|  |  |
| --- | --- |
| Requirement | ≥ 72h. *Run continuously at the output required to support / deliver the contracted restoration Service* |
| Response Format | Text (no more than 300 words). Explain how the Provider will ensure the ESR Auxiliary Unit will have the expected resilience. |
| Attachments | *Please include the titles of any attachments associated to this section.* |
| **Response** |  |

Block Loading Capability

|  |  |
| --- | --- |
| Requirement | ≥ 10MW. *Capability to accept instantaneous loading of demand blocks.* |
| Response Format | Text (no more than 300 words) + Table + Graphic. If applicable, explain the impact of temperature (Hot, War, Cold) on the block loading capability. Share the expected block loading profile up to the contracted output, including maximum sizes of each block, time between blocks and any hold/critical load points. |
| Attachments | *Please include the titles of any attachments associated to this section.* |
| **Response** |  |

Reactive Capability

|  |  |
| --- | --- |
| Requirement | ≥ 50MVAr Leading. Ability to energise part of the NETS, managing Voltage with Leading or lagging capability whilst active power is zero. |
| Response Format | Text (no more than 300 words) + Table + Generator Capability Curve. |
| Attachments | *Please include the titles of any attachments associated to this section.* |
| **Response** |  |

Sequential Restoration attempts

|  |  |
| --- | --- |
| Requirement | ≥ 3. *Ability to perform at least three sequential start-ups.* |
| Response Format | Text (no more than 500 words). Explain how you will be able to deliver a minimum of 3 sequential start-ups at any stage of restoration (to allow for possible tripping of the Transmission or Distribution Networks during the re-instatement period, or trips during the ESR Service Provider’s own starting sequence). Demonstrate how all generating units (if applicable) can be safely shutdown without the need for external supplies and can be maintained in a state of readiness for subsequent start-ups. |
| Attachments | *Please include the titles of any attachments associated to this section.* |
| **Response** |  |

Short-circuit Level (following the start of a system disturbance)

|  |  |
| --- | --- |
| Requirement | t≤80ms: I ≥ [kA]; t>80ms: I ≥ [kA], U ≡ connection voltage [kV]  *Injection of reactive current during a disturbance.* |
| Response Format | Text (no more than 500 words). Explain/demonstrate how can you meet the requirement. This can be done from Fault Ride Through test evidence, or in the case of a synchronous generator, Grid code DRC schedule1 modelling data being provided as an alternative. |
| Attachments | *Please include the titles of any attachments associated to this section.* |
| **Response** |  |

Inertia Value

|  |  |
| --- | --- |
| Requirement | ≥400 MVA.s. Stored energy available in the RSP for immediate release in response to changes in power levels and thereby helping to maintain frequency and voltage on the power island within acceptable bounds. (This can be real, physical inertia as in a rotating machine, or virtual inertia as in converter-connected resources with suitable control). |
| Response Format | Text (no more than 500 words). Explain/demonstrate how can you meet the requirement. |
| Attachments | *Please include the titles of any attachments associated to this section.* |
|  |  |

1.3 Distributed ReStart Projects

1.3.1 Anchor Generators (Distributed Restart)

Time to Connect

|  |  |
| --- | --- |
| Requirement | *≤ 8hours. Time taken to start-up the ESR Plant from shutdown without the use of external power supplies, and to energise part of the Network, within eight hours of receiving an instruction from the Electricity System Operator (ESO).* |
| Response Format | Text (no more than 100 words). If applicable, consider effect of warmth – Hot, Warm, Cold. Detail key stages of the Black Start and timings. |
| Attachments | *Please include the titles of any attachments associated to this section.* |
| **Response** |  |

Service Availability

|  |  |
| --- | --- |
| Requirement | ≥ 80%. *The ability to deliver the contracted ESR Service over 80% of a year. Note: It is the responsibility of the Provider to demonstrate its service availability. By submitting a tender, the provider commits to ensuring availability at least 80% of each year of the service.* *We note that planned major maintenance outages may impact the availability for an individual year. Please detail how these have been allowed for.* |
| Response Format | Text (no more than 300 words). |
| Attachments | *Please include the titles of any attachments associated to this section.* |
| **Response** |  |

Voltage Regulation

|  |  |
| --- | --- |
| Requirement | Existent. *Ability to control voltage level within acceptable limits during energisation/block loading (±10%).* |
| Response Format | Text (no more than 300 words). |
| Attachments | *Please include the titles of any attachments associated to this section.* |
| **Response** |  |

Frequency Regulation

|  |  |
| --- | --- |
| Requirement | Existent. *Ability to manage frequency level when block loading (47.5Hz – 52Hz).* |
| Response Format | Text (no more than 300 words). |
| Attachments | *Please include the titles of any attachments associated to this section.* |
| **Response** |  |

Resilience of Supply – ESR Service

|  |  |
| --- | --- |
| Requirement | ≥ 72h. *When instructed to ESR, the minimum time the Provider will deliver the contracted service.* |
| Response Format | Text (no more than 300 words). Explain how the Provider will ensure the ESR Auxiliary Unit will have the expected resilience. |
| Attachments | *Please include the titles of any attachments associated to this section.* |
| **Response** |  |

Resilience of Supply – Auxiliary Unit(s)

|  |  |
| --- | --- |
| Requirement | ≥ 120h. *Run continuously at the output required to support / deliver the contracted restoration service.* |
| Response Format | Text (no more than 300 words). Explain how will the Provider ensure the BS Auxiliary Unit will have the expected resilience. |
| Attachments | *Please include the titles of any attachments associated to this section.* |
| **Response** |  |

Block Loading Capability

|  |  |
| --- | --- |
| Requirement | ≥ 2MW. *Capability to accept instantaneous loading of demand blocks.* |
| Response Format | Text (no more than 300 words) + Table + Graphic. If applicable, explain the impact of temperature (Hot, War, Cold) on the block loading capability. Share the expected block loading profile up to the contracted output, including maximum sizes of each block, time between blocks and any hold/critical load points. |
| Attachments | *Please include the titles of any attachments associated to this section.* |
| **Response** |  |

Reactive Capability

|  |  |
| --- | --- |
| Requirement | Power factor of 0.95 lead/lag at Point of Connection Ability to energise part of the NETS, managing Voltage with Leading or lagging capability whilst active power is zero |
| Response Format | Text (no more than 300 words) + Table + Generator Capability Curve. |
| Attachments | *Please include the titles of any attachments associated to this section.* |
| **Response** |  |

Sequential Start-Ups

|  |  |
| --- | --- |
| Requirement | ≥ 3. *Ability to perform at least three sequential start-ups.* |
| Response Format | Text (no more than 500 words). Explain how will you be able to deliver a minimum of 3 sequential start-ups at any stage of restoration (to allow for possible tripping of the Transmission or Distribution Networks during the re-instatement period, or trips during the ESR Service Provider’s own starting sequence). Demonstrate how all generating units (if applicable) can be safely shutdown without the need for external supplies, and can be maintained in a state of readiness for subsequent start-ups. |
| Attachments | *Please include the titles of any attachments associated to this section.* |
| **Response** |  |

Short-circuit Level (following the start of a system disturbance)

|  |  |
| --- | --- |
| Requirement | *≥ 1x Anchor’s MVA Rating Injection of reactive current during a disturbance.* |
| Response Format | Text (no more than 500 words). Explain/demonstrate how can you meet the requirement. This can be done from Fault Ride Through test evidence, or in the case of a synchronous generator, Grid code DRC schedule1 modelling data being provided as an alternative. |
| Attachments | *Please include the titles of any attachments associated to this section.* |
| **Response** |  |

Inertia Value

|  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Requirement | Stored energy available in the RSP for immediate release in response to changes in power levels and thereby helping to maintain frequency and voltage on the power island within acceptable bounds. (This can be real, physical inertia as in a rotating machine, or virtual inertia as in converter-connected resources with suitable control). Linked to the Block Loading Capability example provided below   |  | | --- | | *2MW, ≥ 80 MVA.s* | | *3MW, ≥ 120 MVA.s* | | *4MW, ≥ 160 MVA.s* | | *5MW, ≥ 200 MVA.s* | | *6MW, ≥ 240 MVA.s* | | *7MW, ≥ 280 MVA.s* | |
| Response Format | Text (no more than 500 words). Explain/demonstrate how can you meet the requirement. |
| Attachments | *Please include the titles of any attachments associated to this section.* |
| **Response** |  |

Earthing

|  |  |
| --- | --- |
| Requirement | *Will depend on the requirements of the network area for which services are being procured. The Provider must have facilities suitable for safe and effective earthing consistent with their proposed role in the restoration process and the earthing design and facilities of the network to which they are connected.* |
| Response Format | Text (no more than 500 words). |
| Attachments | *Please include the titles of any attachments associated to this section.* |
| **Response** |  |

1.3.2 Top-up Services (Distributed ReStart)

Resilience of Supply – ESR Service

|  |  |
| --- | --- |
| Requirement | ≥ 72h. *When instructed to ESR, the minimum time the Provider will deliver the contracted service.* |
| Response Format | Text (no more than 300 words). Explain how the Provider will ensure the ESR Auxiliary Unit will have the expected resilience. |
| Attachments | *Please include the titles of any attachments associated to this section.* |
| **Response** |  |

Service Availability

|  |  |
| --- | --- |
| Requirement | ≥ 80%. *The ability to deliver the contracted ESR Service over 80% of a year. Note: It is the responsibility of the Provider to demonstrate its service availability. By submitting a tender, the provider commits to ensuring availability at least 80% of each year of the service.* *We note that planned major maintenance outages may impact the availability for an individual year. Please detail how these have been allowed for.* |
| Response Format | Text (no more than 300 words). |
| Attachments | *Please include the titles of any attachments associated to this section.* |
| **Response** |  |

Fast MW Control

|  |  |
| --- | --- |
| Requirement | Deliver rapid MW response triggered by a local frequency measurement or on receipt of an external control request (which will change the set point at an agreed ramp rate).  <200ms provide available MW, sustained for at least 15 minutes with gradual reduction toward preferred operating position,  And/Or  <200ms provide available MW, sustained for at least 10 seconds with gradual reduction toward preferred operating position,  And/or  Active power output reduction in response to a change in system frequency above a certain value (value and required rate of reduction to be confirmed)  And/or  Active power output increase in response to a system frequency below a certain value (value and required rate of increase to be confirmed). This will only be required if output has been constrained below the maximum output power. |
| Response Format | Text (no more than 300 words) |
| Attachments | *Please include the titles of any attachments associated to this section.* |
| **Response** |  |

Inertia Value

|  |  |
| --- | --- |
| Requirement | There is no minimum requirement for individual generators/resources, but the service provider should state what inertia is available.  The inertial response should be provided by an inherent response without any measurement delays. |
| Response Format | Text (no more than 500 words). Explain/demonstrate how can you meet the requirement. |
| Attachments | *Please include the titles of any attachments associated to this section.* |
| **Response** |  |

Frequency Control

|  |  |
| --- | --- |
| Requirement | Provide frequency sensitive control of active power.. |
| Response Format | Text (no more than 500 words). Explain/demonstrate how can you meet the requirement. |
| Attachments | *Please include the titles of any attachments associated to this section.* |
| **Response** |  |

Reactive Capability (Voltage Control)

|  |  |
| --- | --- |
| Requirement | Provide continuous steady state control of the voltage at point of connection. Compliant with Engineering Recommendation G99 requirements on reactive capabilities. |
| Response Format | Text (no more than 300 words) + Table + Generator Capability Curve. |
| Attachments | *Please include the titles of any attachments associated to this section.* |
| **Response** |  |

Short-circuit Level (following the start of a system disturbance)

|  |  |
| --- | --- |
| Requirement | *≥ 1 x DER MVA rating (at t≥1s)*  *The maximum equivalent MVA short-circuit infeed that can be sustained as measured at the DNO point of connection for at least one second.* |
| Response Format | Text (no more than 500 words). Explain/demonstrate how can you meet the requirement. This can be done from Fault Ride Through test evidence, or in the case of a synchronous generator, Grid code DRC schedule1 modelling data being provided as an alternative. |
| Attachments | *Please include the titles of any attachments associated to this section.* |
| **Response** |  |

Energy

|  |  |
| --- | --- |
| Requirement | Generate or consume MW on instruction from an external control system, deliver within 10 seconds of request. |
| Response Format | Text (no more than 500 words |
| Attachments | *Please include the titles of any attachments associated to this section.* |
| **Response** |  |

1.4 Top-up Services

**1.4.1 – Mandatory Requirements**

**(Please complete all the questions in this section)**

Resilience of Supply

|  |  |
| --- | --- |
| Requirement | Minimum ≥ 24h. Ability to maintain a state of readiness that will enable the Restoration Service Provider, once external electrical supplies are re-established, to receive an instruction from the ESO and Start-Up in alignment with the expected behaviour under normal operating conditions.  Example: external electrical supplies re-established to a given wind farm 36 hours into a partial or total shutdown. |
| Response Format | Text (no more than 300 words). |
| Attachments | *Please include the titles of any attachments associated to this section.* |
| **Response** |  |

Service Availability

|  |  |
| --- | --- |
| Requirement | Minimum ≥ 80%. The ability to deliver the contracted Restoration Service over 80% of a year.  Note: It is the responsibility of the Provider to demonstrate its service availability. By submitting a tender, the provider commits to ensuring availability at least 80% of each year of the service. |
| Response Format | Text (no more than 300 words). |
| Attachments | *Please include the titles of any attachments associated to this section.* |
| **Response** |  |

Voltage Regulation

|  |  |
| --- | --- |
| Requirement | Minimum requirement - Existent. Ability to manage voltage and remain connected within acceptable limits during energisation/block loading. |
| Response Format | Text (no more than 300 words). |
| Attachments | *Please include the titles of any attachments associated to this section.* |
| **Response** |  |

Frequency Regulation

|  |  |
| --- | --- |
| Requirement | Ability to manage frequency and remain connected within acceptable limits during energisation/block loading. |
| Response Format | Text (no more than 300 words). |
| Attachments | *Please include the titles of any attachments associated to this section.* |
| **Response** |  |

1.4.2 At least one of the Requirements below

Resilience of Supply – ESR Service

|  |  |
| --- | --- |
| Requirement | ≥ 10h. *When instructed to BS, the minimum time the Provider will deliver the contracted service.* |
| Response Format | Text (no more than 300 words). Explain how the Provider will ensure the ESR Auxiliary Unit will have the expected resilience. |
| Attachments | *Please include the titles of any attachments associated to this section.* |
| **Response** |  |

Block Loading Capability

|  |  |
| --- | --- |
| Requirement | ≥ 10MW. *Capability to accept instantaneous loading of demand blocks.* |
| Response Format | Text (no more than 300 words) + Table + Graphic. If applicable, explain the impact of temperature (Hot, War, Cold) on the block loading capability. Share the expected block loading profile up to the contracted output, including maximum sizes of each block, time between blocks and any hold/critical load points. |
| Attachments | *Please include the titles of any attachments associated to this section.* |
| **Response** |  |
| **Response** |  |

Reactive Capability

|  |  |
| --- | --- |
| Requirement | ≥ 50MVAr Leading. *Ability to energise part of the network (MVAr>0, MW=0).* |
| Response Format | Text (no more than 300 words) + Table + Generator Capability Curve. |
| Attachments | *Please include the titles of any attachments associated to this section.* |
| **Response** |  |

Short-circuit Level(following the start of a system disturbance)

|  |  |
| --- | --- |
| Requirement | t≤80ms: I ≥ [kA]; t>80ms: I ≥ [kA], U ≡ connection voltage [kV]  *Injection of reactive current during a disturbance.* |
| Response Format | Text (no more than 500 words). Explain/demonstrate how can you meet the requirement. This can be done from Fault Ride Through test evidence, or in the case of a synchronous generator, Grid code DRC schedule1 modelling data being provided as an alternative. |
| Attachments | *Please include the titles of any attachments associated to this section.* |
| **Response** |  |

Inertia Value

|  |  |
| --- | --- |
| Requirement | ≥400 MVA.s. *Stored rotating energy in the system (real or virtual).* |
| Response Format | Text (no more than 500 words). Explain/demonstrate how can you meet the requirement. |
| Attachments | *Please include the titles of any attachments associated to this section.* |
|  |  |

List of Attachments

|  |  |  |
| --- | --- | --- |
| **Appendix**  **Num.** | Document | File name as submitted |
| **1** |  |  |
| **2** |  |  |
| **3** |  |  |
| **4** |  |  |
| **5** |  |  |
| **6** |  |  |
| **7** |  |  |
| **8** |  |  |
| **9** |  |  |
| **10** |  |  |
| **11** |  |  |
| **12** |  |  |
| **13** |  |  |
| **14** |  |  |
| **15** |  |  |
| **16** |  |  |
| **17** |  |  |
| **18** |  |  |
| **19** |  |  |
| **20** |  |  |

Appendices

Appendix 1 – Anchor Generator (Primary) Service

|  |  |  |  |
| --- | --- | --- | --- |
| Ref | Requirement | Provider Expected Capability following F1 | Reference to F1 section evidencing the requirement |
| 1.01 | Time to Connect |  |  |
|  | Or Phase 2 Time to Connect |  |  |
|  | Or Phase 3 Time to Connect |  |  |
| 1.02 | Service Availability |  |  |
| 1.03a | Voltage Control (Leading) |  |  |
| 1.03b | Voltage Control (Lagging) |  |  |
| 1.04a | Frequency Control (Lower) |  |  |
| 1.04b | Frequency Control (Upper) |  |  |
| 1.05 | Resilience of supply, Black Start Service |  |  |
| 1.06 | Resilience of Supply, BS Auxiliary Unit(s) |  |  |
| 1.07 | Block loading size |  |  |
| 1.08 | Reactive Capability |  |  |
| 1.09 | Sequential Black Starts |  |  |
| 1.10 | Short Circuit Level |  |  |
| 1.11 | Inertia Value |  |  |

.

Appendix 2 – Anchor Generator Distributed ReStart

|  |  |  |  |
| --- | --- | --- | --- |
| Ref | Requirement | Provider Expected Capability following F1 | Reference to F1 section evidencing the requirement |
| 2.01 | Time to Connect |  |  |
| 2.02 | Service Availability |  |  |
| 2.03 | Voltage Regulation |  |  |
| 2.04 | Frequency Regulation |  |  |
| 2.05 | Resilience of supply, Black Start Service |  |  |
| 2.06 | Resilience of Supply, BS Auxiliary Unit(s) |  |  |
| 2.07 | Block loading size |  |  |
| 2.08 | Reactive Capability |  |  |
| 2.09 | Sequential Black Starts |  |  |
| 2.10 | Short-circuit level (following the start of a system disturbance) |  |  |
| 2.11 | Inertia Value |  |  |
| 2.11 | Earthing |  |  |

Appendix 3 – Top Up Service Distributed ReStart

|  |  |  |  |
| --- | --- | --- | --- |
| Ref | Requirement | Provider Expected Capability following F1 | Reference to F1 section evidencing the requirement |
| 3.01 | Resilience of Supply |  |  |
| 3.02 | Service Availability |  |  |
| 3.03 | Fast MW Control |  |  |
| 3.04 | Inertia Value |  |  |
| 3.05 | Frequency Control |  |  |
| 3.06 | Reactive Capability  (Voltage Control) |  |  |
| 3.07 | Short-Circuit Infeed |  |  |
| 3.08 | Energy (MWh) |  |  |

Appendix 4 – Top Up Service

|  |  |  |  |
| --- | --- | --- | --- |
| Ref | Requirement | Provider Expected Capability following F1 | Reference to F1 section evidencing the requirement |
| 4.01 | Resiliance |  |  |
| 4.02 | Service Availability |  |  |
| 4.03 | Voltage Regulation |  |  |
| 4.04 | Frequency Regulation |  |  |

Mandatory

Optional

|  |  |  |  |
| --- | --- | --- | --- |
| Ref | Requirement | Provider Expected Capability following F1 | Reference to F1 section evidencing the requirement |
| 4.05 | Resilience of Supply, Restoration Service |  |  |
| 4.06 | Block Loading Size |  |  |
| 4.07 | Reactive Capability |  |  |
| 4.08 | Short-circuit level (SCL) (following the start of a system disturbance) |  |  |

Faraday House, Warwick Technology Park, Gallows Hill, Warwick, CV346DA

nationalgrideso.com